Unison Networks | 2008 | 2007-04-30 | 0.72439 | 0.009798
Unison Networks | 2008 | 2007-05-01 | 0.69244 | 0.026227
Unison Networks | 2008 | 2007-05-02 | 0.21742 | 0.0093415
Unison Networks | 2008 | 2007-05-03 | 0.026246 | 0.00018354
Unison Networks | 2008 | 2007-05-04 | 0.012459 | 0.0020048
Unison Networks | 2008 | 2007-05-05 | 0.052586 | 0.0014824
Unison Networks | 2008 | 2007-05-06 | 0.0013097 | 0.00064944
Unison Networks | 2008 | 2007-05-07 | 0.20729 | 0.0037884
Unison Networks | 2008 | 2007-05-08
Unison Networks | 2008 | 2007-05-09 | 0.036834 | 0.00022589
Unison Networks | 2008 | 2007-05-10 | 0.020085 | 0.00010353
Unison Networks | 2008 | 2007-05-11 | 0.1773 | 0.00059296
Unison Networks | 2008 | 2007-05-12 | 0.046383 | 0.0010542
Unison Networks | 2008 | 2007-05-13
Unison Networks | 2008 | 2007-05-14 | 0.1015 | 0.00036707
Unison Networks | 2008 | 2007-05-15 | 0.30614 | 0.0033884
Unison Networks | 2008 | 2007-05-16 | 0.018749 | 7.5297e-05
Unison Networks | 2008 | 2007-05-17 | 0.074524 | 0.00042825
Unison Networks | 2008 | 2007-05-18 | 0.6606 | 0.024457
Unison Networks | 2008 | 2007-05-19
Unison Networks | 2008 | 2007-05-20 | 0.033361 | 0.00024001
Unison Networks | 2008 | 2007-05-21
Unison Networks | 2008 | 2007-05-22 | 0.11187 | 0.00048943
Unison Networks | 2008 | 2007-05-23 | 0.73768 | 0.023577
Unison Networks | 2008 | 2007-05-24 | 0.019009 | 0.0057602
Unison Networks | 2008 | 2007-05-25 | 0.022429 | 8.9415e-05
Unison Networks | 2008 | 2007-05-26 | 0.0088756 | 2.8236e-05
Unison Networks | 2008 | 2007-05-27 | 0.3104 | 0.0039249
Unison Networks | 2008 | 2007-05-28
Unison Networks | 2008 | 2007-05-29 | 0.64384 | 0.003459
Unison Networks | 2008 | 2007-05-30 | 0.04956 | 0.0017883
Unison Networks | 2008 | 2007-05-31 | 0.016339 | 0.00013177
Unison Networks | 2008 | 2007-06-01 | 0.025596 | 0.00087533
Unison Networks | 2008 | 2007-06-02 | 1.2509 | 0.011558
Unison Networks | 2008 | 2007-06-03 | 0.50609 | 0.01513
Unison Networks | 2008 | 2007-06-04
Unison Networks | 2008 | 2007-06-05 | 0.097968 | 0.0011859
Unison Networks | 2008 | 2007-06-06 | 0.27062 | 0.0028754
Unison Networks | 2008 | 2007-06-07 | 0.20696 | 0.0038496
Unison Networks | 2008 | 2007-06-08 | 0.093592 | 0.0017507
Unison Networks | 2008 | 2007-06-09 | 0.046957 | 0.0016848
Unison Networks | 2008 | 2007-06-10 | 0.36383 | 0.010259
Unison Networks | 2008 | 2007-06-11
Unison Networks | 2008 | 2007-06-12 | 0.013638 | 8.4709e-05
Unison Networks | 2008 | 2007-06-13 | 0.14899 | 0.00056002
Unison Networks | 2008 | 2007-06-14
Unison Networks | 2008 | 2007-06-15
Unison Networks | 2008 | 2007-06-16 | 0.16535 | 0.0038401
Unison Networks | 2008 | 2007-06-17 | 0.025495 | 0.00022589
Unison Networks | 2008 | 2007-06-18 | 0.36198 | 0.0013318
Unison Networks | 2008 | 2007-06-19
Unison Networks | 2008 | 2007-06-20 | 1.6589 | 0.012636
Unison Networks | 2008 | 2007-06-21 | 0.11866 | 0.00044237
Unison Networks | 2008 | 2007-06-22 | 0.38109 | 0.015535
Unison Networks | 2008 | 2007-06-23 | 1.7239 | 0.06916
Unison Networks | 2008 | 2007-06-24
Unison Networks | 2008 | 2007-06-25 | 0.30995 | 0.0084521
Unison Networks | 2008 | 2007-06-26 | 0.24818 | 0.0050778
Unison Networks | 2008 | 2007-06-27
Unison Networks | 2008 | 2007-06-28 | 0.094733 | 0.00028707
Unison Networks | 2008 | 2007-06-29 | 0.15464 | 0.003779
Unison Networks | 2008 | 2007-06-30
Unison Networks | 2008 | 2007-07-01 | 0.3717 | 0.0024424
Unison Networks | 2008 | 2007-07-02 | 0.035837 | 0.0010306
Unison Networks | 2008 | 2007-07-03
Unison Networks | 2008 | 2007-07-04 | 0.043625 | 0.00014118
Unison Networks | 2008 | 2007-07-05 | 0.1157 | 0.0024848
Unison Networks | 2008 | 2007-07-06 | 0.052623 | 0.0022354
Unison Networks | 2008 | 2007-07-07
Unison Networks | 2008 | 2007-07-08 | 0.10201 | 0.0017318
Unison Networks | 2008 | 2007-07-09 | 0.55307 | 0.003426
Unison Networks | 2008 | 2007-07-10 | 1.0419 | 0.015492
Unison Networks | 2008 | 2007-07-11 | 0.33385 | 0.0091956
Unison Networks | 2008 | 2007-07-12 | 0.35256 | 0.0022824
Unison Networks | 2008 | 2007-07-13 | 0.018358 | 8.4709e-05
Unison Networks | 2008 | 2007-07-14
Unison Networks | 2008 | 2007-07-15 | 0.027007 | 0.0017507
Unison Networks | 2008 | 2007-07-16 | 0.64707 | 0.009911
Unison Networks | 2008 | 2007-07-17 | 0.023535 | 0.00033413
Unison Networks | 2008 | 2007-07-18 | 0.22357 | 0.0065132
Unison Networks | 2008 | 2007-07-19 | 0.064967 | 0.00022118
Unison Networks | 2008 | 2007-07-20 | 0.04258 | 0.00018354
Unison Networks | 2008 | 2007-07-21 | 0.086341 | 0.0014024
Unison Networks | 2008 | 2007-07-22 | 0.11765 | 0.0015483
Unison Networks | 2008 | 2007-07-23 | 0.0014401 | 8.4709e-05
Unison Networks | 2008 | 2007-07-24 | 0.036637 | 0.00035295
Unison Networks | 2008 | 2007-07-25 | 0.86508 | 0.010683
Unison Networks | 2008 | 2007-07-26 | 0.056065 | 0.00029178
Unison Networks | 2008 | 2007-07-27 | 0.10603 | 0.00055061
Unison Networks | 2008 | 2007-07-28 | 0.080659 | 0.00082827
Unison Networks | 2008 | 2007-07-29 | 0.017699 | 3.2942e-05
Unison Networks | 2008 | 2007-07-30 | 0.013478 | 1.8824e-05
Unison Networks | 2008 | 2007-07-31 | 0.072457 | 0.00057885
Unison Networks | 2008 | 2007-08-01 | 0.020227 | 0.00044237
Unison Networks | 2008 | 2007-08-02 | 0.17552 | 0.013681
Unison Networks | 2008 | 2007-08-03 | 0.0066073 | 6.1179e-05
Unison Networks | 2008 | 2007-08-04
Unison Networks | 2008 | 2007-08-05
Unison Networks | 2008 | 2007-08-06 | 0.19153 | 0.0039201
Unison Networks | 2008 | 2007-08-07 | 0.088201 | 0.00058826
Unison Networks | 2008 | 2007-08-08 | 0.0096035 | 9.4121e-05
Unison Networks | 2008 | 2007-08-09 | 0.0064426 | 1.4118e-05
Unison Networks | 2008 | 2007-08-10 | 0.66794 | 0.012843
Unison Networks | 2008 | 2007-08-11 | 0.51176 | 0.011765
Unison Networks | 2008 | 2007-08-12 | 0.19695 | 0.0025601
Unison Networks | 2008 | 2007-08-13 | 0.16918 | 0.0078638
Unison Networks | 2008 | 2007-08-14 | 0.022488 | 0.0021036
Unison Networks | 2008 | 2007-08-15 | 0.23319 | 0.0056096
Unison Networks | 2008 | 2007-08-16 | 0.83098 | 0.0037319
Unison Networks | 2008 | 2007-08-17 | 0.10644 | 0.0015154
Unison Networks | 2008 | 2007-08-18
Unison Networks | 2008 | 2007-08-19 | 0.13197 | 0.0043437
Unison Networks | 2008 | 2007-08-20 | 0.025257 | 0.00035295
Unison Networks | 2008 | 2007-08-21 | 0.088888 | 0.00042355
Unison Networks | 2008 | 2007-08-22 | 0.026462 | 8.0003e-05
Unison Networks | 2008 | 2007-08-23 | 0.48403 | 0.012156
Unison Networks | 2008 | 2007-08-24 | 0.12376 | 0.0014306
Unison Networks | 2008 | 2007-08-25 | 0.24374 | 0.0014683
Unison Networks | 2008 | 2007-08-26 | 0.049291 | 0.00016471
Unison Networks | 2008 | 2007-08-27 | 0.81734 | 0.067673
Unison Networks | 2008 | 2007-08-28 | 0.25113 | 0.0044708
Unison Networks | 2008 | 2007-08-29 | 0.050967 | 0.00032001
Unison Networks | 2008 | 2007-08-30 | 1.2303 | 0.018147
Unison Networks | 2008 | 2007-08-31 | 0.01014 | 0.0015248
Unison Networks | 2008 | 2007-09-01 | 0.17987 | 0.0022542
Unison Networks | 2008 | 2007-09-02 | 0.17191 | 0.00104
Unison Networks | 2008 | 2007-09-03 | 0.055508 | 0.0016989
Unison Networks | 2008 | 2007-09-04 | 0.091085 | 0.002706
Unison Networks | 2008 | 2007-09-05 | 0.045677 | 0.00025883
Unison Networks | 2008 | 2007-09-06 | 0.078328 | 0.00033884
Unison Networks | 2008 | 2007-09-07 | 0.17628 | 0.0014165
Unison Networks | 2008 | 2007-09-08
Unison Networks | 2008 | 2007-09-09
Unison Networks | 2008 | 2007-09-10 | 0.00082827 | 1.8824e-05
Unison Networks | 2008 | 2007-09-11 | 0.04011 | 0.00020236
Unison Networks | 2008 | 2007-09-12 | 0.00050825 | 4.7061e-06
Unison Networks | 2008 | 2007-09-13 | 0.15025 | 0.00059296
Unison Networks | 2008 | 2007-09-14 | 0.27267 | 0.0034778
Unison Networks | 2008 | 2007-09-15 | 0.129 | 0.0017365
Unison Networks | 2008 | 2007-09-16
Unison Networks | 2008 | 2007-09-17 | 0.012273 | 4.2355e-05
Unison Networks | 2008 | 2007-09-18 | 0.36836 | 0.0024377
Unison Networks | 2008 | 2007-09-19 | 0.050658 | 0.00080474
Unison Networks | 2008 | 2007-09-20 | 0.10857 | 0.00032472
Unison Networks | 2008 | 2007-09-21 | 0.55546 | 0.011582
Unison Networks | 2008 | 2007-09-22 | 0.046421 | 0.0029554
Unison Networks | 2008 | 2007-09-23 | 0.060708 | 0.00043296
Unison Networks | 2008 | 2007-09-24 | 0.053757 | 0.00072944
Unison Networks | 2008 | 2007-09-25 | 0.32376 | 0.0014353
Unison Networks | 2008 | 2007-09-26 | 0.49249 | 0.004979
Unison Networks | 2008 | 2007-09-27 | 0.0023201 | 9.4121e-06
Unison Networks | 2008 | 2007-09-28 | 0.72329 | 0.012885
Unison Networks | 2008 | 2007-09-29
Unison Networks | 2008 | 2007-09-30
Unison Networks | 2008 | 2007-10-01 | 0.45318 | 0.0045084
Unison Networks | 2008 | 2007-10-02 | 0.36615 | 0.001906
Unison Networks | 2008 | 2007-10-03 | 0.71225 | 0.0043202
Unison Networks | 2008 | 2007-10-04 | 0.057574 | 0.0015201
Unison Networks | 2008 | 2007-10-05 | 0.73125 | 0.01481
Unison Networks | 2008 | 2007-10-06 | 0.067548 | 0.00076709
Unison Networks | 2008 | 2007-10-07
Unison Networks | 2008 | 2007-10-08
Unison Networks | 2008 | 2007-10-09 | 0.0028236 | 1.8824e-05
Unison Networks | 2008 | 2007-10-10
Unison Networks | 2008 | 2007-10-11 | 0.094224 | 0.0027342
Unison Networks | 2008 | 2007-10-12 | 0.14855 | 0.0016283
Unison Networks | 2008 | 2007-10-13
Unison Networks | 2008 | 2007-10-14 | 1.6102 | 0.03554
Unison Networks | 2008 | 2007-10-15 | 0.029707 | 0.010673
Unison Networks | 2008 | 2007-10-16 | 0.15769 | 0.0096757
Unison Networks | 2008 | 2007-10-17 | 0.40548 | 0.0052567
Unison Networks | 2008 | 2007-10-18 | 3.7073 | 0.03427
Unison Networks | 2008 | 2007-10-19 | 0.082682 | 0.012523
Unison Networks | 2008 | 2007-10-20
Unison Networks | 2008 | 2007-10-21 | 0.11579 | 0.0040754
Unison Networks | 2008 | 2007-10-22 | 0.22924 | 0.0030684
Unison Networks | 2008 | 2007-10-23 | 0.13483 | 0.0040143
Unison Networks | 2008 | 2007-10-24 | 0.0039107 | 1.4118e-05
Unison Networks | 2008 | 2007-10-25 | 0.12835 | 0.00038119
Unison Networks | 2008 | 2007-10-26 | 0.15218 | 0.0065085
Unison Networks | 2008 | 2007-10-27 | 0.39342 | 0.0062591
Unison Networks | 2008 | 2007-10-28 | 0.014791 | 0.00014589
Unison Networks | 2008 | 2007-10-29
Unison Networks | 2008 | 2007-10-30 | 0.3502 | 0.0046025
Unison Networks | 2008 | 2007-10-31 | 0.015704 | 0.00011295
Unison Networks | 2008 | 2007-11-01 | 0.18095 | 0.0020377
Unison Networks | 2008 | 2007-11-02 | 0.67296 | 0.016674
Unison Networks | 2008 | 2007-11-03
Unison Networks | 2008 | 2007-11-04 | 0.20033 | 0.00064002
Unison Networks | 2008 | 2007-11-05 | 0.025366 | 8.9415e-05
Unison Networks | 2008 | 2007-11-06 | 0.0085509 | 2.353e-05
Unison Networks | 2008 | 2007-11-07 | 0.062614 | 0.0010824
Unison Networks | 2008 | 2007-11-08 | 0.51095 | 0.011638
Unison Networks | 2008 | 2007-11-09 | 0.057085 | 0.00018824
Unison Networks | 2008 | 2007-11-10 | 0.039884 | 0.00011765
Unison Networks | 2008 | 2007-11-11 | 0.049962 | 0.0015295
Unison Networks | 2008 | 2007-11-12 | 0.048218 | 0.0018683
Unison Networks | 2008 | 2007-11-13 | 0.028914 | 0.00033884
Unison Networks | 2008 | 2007-11-14 | 0.38098 | 0.0089603
Unison Networks | 2008 | 2007-11-15 | 0.0060285 | 1.4118e-05
Unison Networks | 2008 | 2007-11-16 | 0.79301 | 0.01136
Unison Networks | 2008 | 2007-11-17 | 0.0064473 | 2.353e-05
Unison Networks | 2008 | 2007-11-18 | 0.016372 | 0.0002306
Unison Networks | 2008 | 2007-11-19 | 0.025719 | 0.00082356
Unison Networks | 2008 | 2007-11-20 | 0.090181 | 0.011873
Unison Networks | 2008 | 2007-11-21 | 0.00090356 | 2.8236e-05
Unison Networks | 2008 | 2007-11-22 | 0.14015 | 0.00070591
Unison Networks | 2008 | 2007-11-23 | 0.046177 | 0.00066826
Unison Networks | 2008 | 2007-11-24 | 0.24467 | 0.0026072
Unison Networks | 2008 | 2007-11-25
Unison Networks | 2008 | 2007-11-26 | 0.52698 | 0.021761
Unison Networks | 2008 | 2007-11-27 | 0.061951 | 0.00055061
Unison Networks | 2008 | 2007-11-28 | 0.4465 | 0.0085933
Unison Networks | 2008 | 2007-11-29 | 1.0506 | 0.007012
Unison Networks | 2008 | 2007-11-30 | 0.53588 | 0.0047437
Unison Networks | 2008 | 2007-12-01
Unison Networks | 2008 | 2007-12-02 | 0.077683 | 0.0045696
Unison Networks | 2008 | 2007-12-03 | 0.55328 | 0.005699
Unison Networks | 2008 | 2007-12-04 | 0.26514 | 0.018175
Unison Networks | 2008 | 2007-12-05 | 0.030729 | 0.0033272
Unison Networks | 2008 | 2007-12-06 | 0.80994 | 0.010965
Unison Networks | 2008 | 2007-12-07 | 0.061866 | 0.0019342
Unison Networks | 2008 | 2007-12-08 | 0.36267 | 0.013732
Unison Networks | 2008 | 2007-12-09 | 0.00060238 | 0.00015059
Unison Networks | 2008 | 2007-12-10 | 0.030636 | 0.00030119
Unison Networks | 2008 | 2007-12-11 | 0.35912 | 0.0016189
Unison Networks | 2008 | 2007-12-12 | 0.023027 | 0.00012706
Unison Networks | 2008 | 2007-12-13 | 0.2254 | 0.0025883
Unison Networks | 2008 | 2007-12-14 | 0.17026 | 0.00061179
Unison Networks | 2008 | 2007-12-15 | 0.096143 | 0.0071156
Unison Networks | 2008 | 2007-12-16
Unison Networks | 2008 | 2007-12-17 | 0.49454 | 0.002753
Unison Networks | 2008 | 2007-12-18 | 0.80441 | 0.015092
Unison Networks | 2008 | 2007-12-19 | 0.27733 | 0.0028378
Unison Networks | 2008 | 2007-12-20 | 0.054684 | 0.0003906
Unison Networks | 2008 | 2007-12-21 | 0.053235 | 0.00065885
Unison Networks | 2008 | 2007-12-22
Unison Networks | 2008 | 2007-12-23
Unison Networks | 2008 | 2007-12-24 | 0.065682 | 0.00057885
Unison Networks | 2008 | 2007-12-25 | 1.5058 | 0.012179
Unison Networks | 2008 | 2007-12-26
Unison Networks | 2008 | 2007-12-27
Unison Networks | 2008 | 2007-12-28
Unison Networks | 2008 | 2007-12-29 | 0.23138 | 0.0017412
Unison Networks | 2008 | 2007-12-30 | 0.026126 | 0.0052237
Unison Networks | 2008 | 2007-12-31
Unison Networks | 2008 | 2008-01-01
Unison Networks | 2008 | 2008-01-02 | 0.060792 | 0.0043813
Unison Networks | 2008 | 2008-01-03 | 0.43466 | 0.01905
Unison Networks | 2008 | 2008-01-04 | 4.4435 | 0.027135
Unison Networks | 2008 | 2008-01-05 | 0.52665 | 0.01585
Unison Networks | 2008 | 2008-01-06 | 0.0019038 | 1.8824e-05
Unison Networks | 2008 | 2008-01-07 | 0.064586 | 0.00019765
Unison Networks | 2008 | 2008-01-08 | 0.01216 | 6.1179e-05
Unison Networks | 2008 | 2008-01-09 | 0.008405 | 7.0591e-05
Unison Networks | 2008 | 2008-01-10
Unison Networks | 2008 | 2008-01-11 | 0.60456 | 0.011845
Unison Networks | 2008 | 2008-01-12
Unison Networks | 2008 | 2008-01-13 | 0.069047 | 0.0025977
Unison Networks | 2008 | 2008-01-14 | 0.027813 | 0.00017883
Unison Networks | 2008 | 2008-01-15 | 0.33361 | 0.0064661
Unison Networks | 2008 | 2008-01-16 | 0.06404 | 0.00060238
Unison Networks | 2008 | 2008-01-17 | 0.046345 | 0.00035766
Unison Networks | 2008 | 2008-01-18 | 0.33384 | 0.0022354
Unison Networks | 2008 | 2008-01-19 | 0.45981 | 0.0040002
Unison Networks | 2008 | 2008-01-20
Unison Networks | 2008 | 2008-01-21 | 0.070991 | 0.0011106
Unison Networks | 2008 | 2008-01-22 | 1.3008 | 0.026434
Unison Networks | 2008 | 2008-01-23 | 1.5506 | 0.036486
Unison Networks | 2008 | 2008-01-24 | 0.73893 | 0.015822
Unison Networks | 2008 | 2008-01-25 | 0.074163 | 0.00034354
Unison Networks | 2008 | 2008-01-26 | 0.011061 | 0.0011295
Unison Networks | 2008 | 2008-01-27 | 0.17547 | 0.0017412
Unison Networks | 2008 | 2008-01-28 | 0.097655 | 0.0034542
Unison Networks | 2008 | 2008-01-29 | 0.84737 | 0.010895
Unison Networks | 2008 | 2008-01-30 | 0.096679 | 0.0029836
Unison Networks | 2008 | 2008-01-31 | 0.050534 | 0.00022118
Unison Networks | 2008 | 2008-02-01 | 1.0838 | 0.012085
Unison Networks | 2008 | 2008-02-02 | 0.36192 | 0.019257
Unison Networks | 2008 | 2008-02-03 | 0.014005 | 0.00014589
Unison Networks | 2008 | 2008-02-04 | 0.47982 | 0.0025977
Unison Networks | 2008 | 2008-02-05 | 4.7343 | 0.035855
Unison Networks | 2008 | 2008-02-06 | 0.0017459 | 4.7061e-06
Unison Networks | 2008 | 2008-02-07 | 0.060878 | 0.0001553
Unison Networks | 2008 | 2008-02-08 | 0.0040284 | 0.00014589
Unison Networks | 2008 | 2008-02-09 | 0.025897 | 7.5297e-05
Unison Networks | 2008 | 2008-02-10 | 0.0076473 | 2.353e-05
Unison Networks | 2008 | 2008-02-11 | 0.0098968 | 0.00020236
Unison Networks | 2008 | 2008-02-12 | 0.08381 | 0.0035343
Unison Networks | 2008 | 2008-02-13 | 0.059485 | 0.00022589
Unison Networks | 2008 | 2008-02-14 | 0.11008 | 0.0017742
Unison Networks | 2008 | 2008-02-15 | 0.80863 | 0.0063391
Unison Networks | 2008 | 2008-02-16 | 0.86245 | 0.015699
Unison Networks | 2008 | 2008-02-17 | 0.0249 | 0.00024001
Unison Networks | 2008 | 2008-02-18
Unison Networks | 2008 | 2008-02-19 | 0.11432 | 0.012118
Unison Networks | 2008 | 2008-02-20 | 0.3921 | 0.0022118
Unison Networks | 2008 | 2008-02-21 | 0.063908 | 0.00021177
Unison Networks | 2008 | 2008-02-22 | 0.25098 | 0.0022824
Unison Networks | 2008 | 2008-02-23
Unison Networks | 2008 | 2008-02-24 | 0.54286 | 0.018711
Unison Networks | 2008 | 2008-02-25 | 1.1765 | 0.07405
Unison Networks | 2008 | 2008-02-26 | 0.18279 | 0.0094968
Unison Networks | 2008 | 2008-02-27 | 0.078732 | 0.00024001
Unison Networks | 2008 | 2008-02-28 | 0.22667 | 0.0016754
Unison Networks | 2008 | 2008-02-29 | 0.22105 | 0.018589
Unison Networks | 2008 | 2008-03-01 | 1.077 | 0.015699
Unison Networks | 2008 | 2008-03-02
Unison Networks | 2008 | 2008-03-03 | 0.55324 | 0.0084944
Unison Networks | 2008 | 2008-03-04 | 0.1662 | 0.00090356
Unison Networks | 2008 | 2008-03-05 | 0.063687 | 0.0002306
Unison Networks | 2008 | 2008-03-06 | 0.17715 | 0.011445
Unison Networks | 2008 | 2008-03-07 | 1.9183 | 0.018711
Unison Networks | 2008 | 2008-03-08 | 0.43225 | 0.010062
Unison Networks | 2008 | 2008-03-09 | 0.81396 | 0.0096945
Unison Networks | 2008 | 2008-03-10 | 0.23445 | 0.0010777
Unison Networks | 2008 | 2008-03-11 | 0.44103 | 0.0033507
Unison Networks | 2008 | 2008-03-12 | 0.79271 | 0.016843
Unison Networks | 2008 | 2008-03-13 | 0.0017177 | 4.7061e-06
Unison Networks | 2008 | 2008-03-14 | 0.043686 | 0.00019765
Unison Networks | 2008 | 2008-03-15 | 1.3783 | 0.0054355
Unison Networks | 2008 | 2008-03-16
Unison Networks | 2008 | 2008-03-17 | 0.084394 | 0.00034825
Unison Networks | 2008 | 2008-03-18 | 0.28666 | 0.0013412
Unison Networks | 2008 | 2008-03-19 | 0.16392 | 0.00059767
Unison Networks | 2008 | 2008-03-20 | 0.1212 | 0.0020848
Unison Networks | 2008 | 2008-03-21
Unison Networks | 2008 | 2008-03-22
Unison Networks | 2008 | 2008-03-23 | 0.18889 | 0.0030778
Unison Networks | 2008 | 2008-03-24
Unison Networks | 2008 | 2008-03-25 | 0.82414 | 0.014589
Unison Networks | 2008 | 2008-03-26 | 0.65294 | 0.0058967
Unison Networks | 2008 | 2008-03-27 | 1.5806 | 0.013455
Unison Networks | 2008 | 2008-03-28 | 0.080516 | 0.0032425
Unison Networks | 2008 | 2008-03-29 | 1.671 | 0.057522
Unison Networks | 2008 | 2008-03-30 | 0.0026683 | 4.7061e-06
Unison Networks | 2008 | 2008-03-31 | 0.30119 | 0.01192
Unison Networks | 2009 | 2008-04-01 | 0.0056034 | 0.00011674
Unison Networks | 2009 | 2008-04-02
Unison Networks | 2009 | 2008-04-03 | 0.11411 | 0.0029511
Unison Networks | 2009 | 2008-04-04 | 0.0025776 | 1.4008e-05
Unison Networks | 2009 | 2008-04-05 | 0.00056034 | 4.6695e-06
Unison Networks | 2009 | 2008-04-06 | 0.12724 | 0.0050944
Unison Networks | 2009 | 2008-04-07 | 0.061217 | 0.00078447
Unison Networks | 2009 | 2008-04-08 | 0.16438 | 0.0024515
Unison Networks | 2009 | 2008-04-09 | 0.45366 | 0.01088
Unison Networks | 2009 | 2008-04-10 | 4.6338 | 0.061488
Unison Networks | 2009 | 2008-04-11 | 0.11543 | 0.00048563
Unison Networks | 2009 | 2008-04-12
Unison Networks | 2009 | 2008-04-13
Unison Networks | 2009 | 2008-04-14
Unison Networks | 2009 | 2008-04-15 | 3.1454 | 0.043286
Unison Networks | 2009 | 2008-04-16 | 2.7223 | 0.077403
Unison Networks | 2009 | 2008-04-17 | 4.6187 | 0.045733
Unison Networks | 2009 | 2008-04-18 | 0.030875 | 0.00013542
Unison Networks | 2009 | 2008-04-19 | 0.0064439 | 5.6034e-05
Unison Networks | 2009 | 2008-04-20 | 0.8586 | 0.012897
Unison Networks | 2009 | 2008-04-21
Unison Networks | 2009 | 2008-04-22 | 0.022017 | 0.00045294
Unison Networks | 2009 | 2008-04-23 | 0.06018 | 0.00024281
Unison Networks | 2009 | 2008-04-24 | 0.26621 | 0.00083117
Unison Networks | 2009 | 2008-04-25 | 0.060621 | 0.014363
Unison Networks | 2009 | 2008-04-26
Unison Networks | 2009 | 2008-04-27 | 0.033046 | 9.8059e-05
Unison Networks | 2009 | 2008-04-28 | 0.033548 | 0.00013075
Unison Networks | 2009 | 2008-04-29 | 8.4051e-05 | 9.339e-06
Unison Networks | 2009 | 2008-04-30 | 0.77103 | 0.0085592
Unison Networks | 2009 | 2008-05-01 | 0.00025947 | 0.00018678
Unison Networks | 2009 | 2008-05-02 | 0.040648 | 2.3347e-05
Unison Networks | 2009 | 2008-05-03
Unison Networks | 2009 | 2008-05-04
Unison Networks | 2009 | 2008-05-05 | 0.15979 | 0.0015036
Unison Networks | 2009 | 2008-05-06 | 0.062897 | 0.00077981
Unison Networks | 2009 | 2008-05-07 | 0.33194 | 0.011818
Unison Networks | 2009 | 2008-05-08 | 0.013468 | 0.00067241
Unison Networks | 2009 | 2008-05-09 | 0.049996 | 0.00011207
Unison Networks | 2009 | 2008-05-10 | 0.23989 | 0.0051178
Unison Networks | 2009 | 2008-05-11
Unison Networks | 2009 | 2008-05-12
Unison Networks | 2009 | 2008-05-13
Unison Networks | 2009 | 2008-05-14 | 0.04365 | 0.00012608
Unison Networks | 2009 | 2008-05-15 | 0.074404 | 0.002713
Unison Networks | 2009 | 2008-05-16 | 0.17805 | 0.0034741
Unison Networks | 2009 | 2008-05-17 | 0.76644 | 0.014606
Unison Networks | 2009 | 2008-05-18 | 0.26 | 0.0015269
Unison Networks | 2009 | 2008-05-19 | 0.11372 | 0.0023347
Unison Networks | 2009 | 2008-05-20 | 0.0036982 | 2.8017e-05
Unison Networks | 2009 | 2008-05-21 | 0.52428 | 0.0030072
Unison Networks | 2009 | 2008-05-22 | 0.21167 | 0.0017884
Unison Networks | 2009 | 2008-05-23 | 0.10336 | 0.0014522
Unison Networks | 2009 | 2008-05-24 | 0.06195 | 0.0051925
Unison Networks | 2009 | 2008-05-25 | 0.8515 | 0.020541
Unison Networks | 2009 | 2008-05-26 | 0.0039597 | 3.7356e-05
Unison Networks | 2009 | 2008-05-27 | 0.088543 | 0.0017464
Unison Networks | 2009 | 2008-05-28 | 0.7082 | 0.013397
Unison Networks | 2009 | 2008-05-29 | 0.053877 | 0.00022414
Unison Networks | 2009 | 2008-05-30 | 0.47444 | 0.0031146
Unison Networks | 2009 | 2008-05-31 | 0.075709 | 0.0012561
Unison Networks | 2009 | 2008-06-01 | 0.14995 | 0.00065373
Unison Networks | 2009 | 2008-06-02
Unison Networks | 2009 | 2008-06-03 | 0.029987 | 0.00042959
Unison Networks | 2009 | 2008-06-04 | 0.037459 | 0.00015409
Unison Networks | 2009 | 2008-06-05 | 0.025519 | 9.339e-05
Unison Networks | 2009 | 2008-06-06 | 0.24683 | 0.002232
Unison Networks | 2009 | 2008-06-07 | 0.48055 | 0.013019
Unison Networks | 2009 | 2008-06-08
Unison Networks | 2009 | 2008-06-09 | 0.0083645 | 8.4051e-05
Unison Networks | 2009 | 2008-06-10 | 0.44001 | 0.0067054
Unison Networks | 2009 | 2008-06-11
Unison Networks | 2009 | 2008-06-12 | 0.25703 | 0.0021807
Unison Networks | 2009 | 2008-06-13
Unison Networks | 2009 | 2008-06-14
Unison Networks | 2009 | 2008-06-15
Unison Networks | 2009 | 2008-06-16
Unison Networks | 2009 | 2008-06-17 | 0.24932 | 0.0010133
Unison Networks | 2009 | 2008-06-18 | 0.15372 | 0.0023161
Unison Networks | 2009 | 2008-06-19 | 0.079293 | 0.0006117
Unison Networks | 2009 | 2008-06-20 | 0.28405 | 0.0039364
Unison Networks | 2009 | 2008-06-21 | 0.0019108 | 5.6034e-05
Unison Networks | 2009 | 2008-06-22 | 0.55023 | 0.023506
Unison Networks | 2009 | 2008-06-23
Unison Networks | 2009 | 2008-06-24 | 0.36266 | 0.0034321
Unison Networks | 2009 | 2008-06-25
Unison Networks | 2009 | 2008-06-26 | 0.15394 | 0.00051831
Unison Networks | 2009 | 2008-06-27 | 0.35538 | 0.0018071
Unison Networks | 2009 | 2008-06-28 | 0.00089654 | 9.339e-06
Unison Networks | 2009 | 2008-06-29 | 0.27344 | 0.0068782
Unison Networks | 2009 | 2008-06-30 | 1.2393 | 0.018192
Unison Networks | 2009 | 2008-07-01
Unison Networks | 2009 | 2008-07-02 | 0.099951 | 0.0027363
Unison Networks | 2009 | 2008-07-03 | 0.049753 | 0.00052765
Unison Networks | 2009 | 2008-07-04
Unison Networks | 2009 | 2008-07-05 | 0.04631 | 0.015405
Unison Networks | 2009 | 2008-07-06 | 0.67238 | 0.0079848
Unison Networks | 2009 | 2008-07-07 | 0.049118 | 0.00017277
Unison Networks | 2009 | 2008-07-08 | 0.032981 | 0.00017277
Unison Networks | 2009 | 2008-07-09 | 0.00055567 | 0.00011674
Unison Networks | 2009 | 2008-07-10 | 0.17625 | 0.00065373
Unison Networks | 2009 | 2008-07-11 | 0.04691 | 0.018963
Unison Networks | 2009 | 2008-07-12
Unison Networks | 2009 | 2008-07-13 | 0.73173 | 0.031332
Unison Networks | 2009 | 2008-07-14 | 0.00624 | 0.00017744
Unison Networks | 2009 | 2008-07-15 | 0.15593 | 0.00049497
Unison Networks | 2009 | 2008-07-16 | 0.016588 | 0.00063038
Unison Networks | 2009 | 2008-07-17 | 0.25719 | 0.0029044
Unison Networks | 2009 | 2008-07-18 | 1.4091 | 0.019593
Unison Networks | 2009 | 2008-07-19 | 0.019324 | 0.00012141
Unison Networks | 2009 | 2008-07-20 | 0.20946 | 0.0047816
Unison Networks | 2009 | 2008-07-21 | 0.004945 | 1.8678e-05
Unison Networks | 2009 | 2008-07-22 | 0.60006 | 0.0023488
Unison Networks | 2009 | 2008-07-23 | 0.27501 | 0.0039644
Unison Networks | 2009 | 2008-07-24 | 0.22048 | 0.002699
Unison Networks | 2009 | 2008-07-25 | 0.010471 | 0.0046088
Unison Networks | 2009 | 2008-07-26 | 1.5206 | 0.024445
Unison Networks | 2009 | 2008-07-27 | 0.45103 | 0.014644
Unison Networks | 2009 | 2008-07-28 | 0.024491 | 0.00013542
Unison Networks | 2009 | 2008-07-29 | 0.30349 | 0.0015736
Unison Networks | 2009 | 2008-07-30 | 1.9944 | 0.035866
Unison Networks | 2009 | 2008-07-31 | 0.042068 | 0.00023814
Unison Networks | 2009 | 2008-08-01 | 0.41323 | 0.0045294
Unison Networks | 2009 | 2008-08-02 | 0.73692 | 0.043534
Unison Networks | 2009 | 2008-08-03 | 0.034944 | 0.014765
Unison Networks | 2009 | 2008-08-04 | 0.33456 | 0.0065093
Unison Networks | 2009 | 2008-08-05 | 0.011356 | 0.00020546
Unison Networks | 2009 | 2008-08-06 | 0.019836 | 0.00012608
Unison Networks | 2009 | 2008-08-07 | 0.42349 | 0.0086386
Unison Networks | 2009 | 2008-08-08 | 0.013672 | 5.6034e-05
Unison Networks | 2009 | 2008-08-09 | 0.11339 | 0.0072657
Unison Networks | 2009 | 2008-08-10 | 0.62533 | 0.030837
Unison Networks | 2009 | 2008-08-11 | 0.052508 | 0.00022414
Unison Networks | 2009 | 2008-08-12 | 0.015923 | 3.7356e-05
Unison Networks | 2009 | 2008-08-13 | 0.20291 | 0.0014289
Unison Networks | 2009 | 2008-08-14 | 0.087039 | 0.00035488
Unison Networks | 2009 | 2008-08-15 | 0.45197 | 0.0026476
Unison Networks | 2009 | 2008-08-16
Unison Networks | 2009 | 2008-08-17 | 0.38374 | 0.0012094
Unison Networks | 2009 | 2008-08-18 | 0.017781 | 6.5373e-05
Unison Networks | 2009 | 2008-08-19 | 0.039946 | 0.0025215
Unison Networks | 2009 | 2008-08-20 | 0.46805 | 0.0012187
Unison Networks | 2009 | 2008-08-21 | 0.29517 | 0.020868
Unison Networks | 2009 | 2008-08-22 | 0.079363 | 0.00024281
Unison Networks | 2009 | 2008-08-23
Unison Networks | 2009 | 2008-08-24
Unison Networks | 2009 | 2008-08-25 | 1.179 | 0.018267
Unison Networks | 2009 | 2008-08-26 | 0.074679 | 0.0082883
Unison Networks | 2009 | 2008-08-27 | 0.3298 | 0.0052625
Unison Networks | 2009 | 2008-08-28 | 0.37223 | 0.0010366
Unison Networks | 2009 | 2008-08-29 | 0.11671 | 0.042759
Unison Networks | 2009 | 2008-08-30 | 0.63186 | 0.015199
Unison Networks | 2009 | 2008-08-31 | 0.50234 | 0.0050337
Unison Networks | 2009 | 2008-09-01 | 0.078993 | 0.00054633
Unison Networks | 2009 | 2008-09-02 | 0.026098 | 0.00024748
Unison Networks | 2009 | 2008-09-03 | 0.0042343 | 0.00052765
Unison Networks | 2009 | 2008-09-04 | 0.43123 | 0.013112
Unison Networks | 2009 | 2008-09-05 | 0.048571 | 0.0015783
Unison Networks | 2009 | 2008-09-06 | 0.077663 | 0.00081249
Unison Networks | 2009 | 2008-09-07 | 0.41642 | 0.002699
Unison Networks | 2009 | 2008-09-08 | 0.17956 | 0.025281
Unison Networks | 2009 | 2008-09-09 | 0.055122 | 0.0013075
Unison Networks | 2009 | 2008-09-10 | 0.41569 | 0.0044967
Unison Networks | 2009 | 2008-09-11 | 0.92401 | 0.0080782
Unison Networks | 2009 | 2008-09-12 | 0.2615 | 0.010194
Unison Networks | 2009 | 2008-09-13 | 0.06471 | 0.0033293
Unison Networks | 2009 | 2008-09-14 | 0.085956 | 0.0015689
Unison Networks | 2009 | 2008-09-15 | 0.65642 | 0.019859
Unison Networks | 2009 | 2008-09-16 | 0.18558 | 0.019411
Unison Networks | 2009 | 2008-09-17 | 0.0057715 | 2.8017e-05
Unison Networks | 2009 | 2008-09-18 | 0.29008 | 0.00089654
Unison Networks | 2009 | 2008-09-19 | 0.18942 | 0.0019285
Unison Networks | 2009 | 2008-09-20
Unison Networks | 2009 | 2008-09-21 | 0.40463 | 0.014391
Unison Networks | 2009 | 2008-09-22 | 0.018342 | 3.7356e-05
Unison Networks | 2009 | 2008-09-23 | 0.33018 | 0.0049076
Unison Networks | 2009 | 2008-09-24 | 0.19917 | 0.0010553
Unison Networks | 2009 | 2008-09-25 | 0.16779 | 0.00074245
Unison Networks | 2009 | 2008-09-26 | 0.14432 | 0.00037823
Unison Networks | 2009 | 2008-09-27
Unison Networks | 2009 | 2008-09-28
Unison Networks | 2009 | 2008-09-29 | 0.16157 | 0.00097125
Unison Networks | 2009 | 2008-09-30 | 0.30723 | 0.071186
Unison Networks | 2009 | 2008-10-01 | 0.098087 | 0.00051831
Unison Networks | 2009 | 2008-10-02 | 0.012225 | 5.1364e-05
Unison Networks | 2009 | 2008-10-03 | 0.010483 | 4.2025e-05
Unison Networks | 2009 | 2008-10-04 | 0.069491 | 0.00050431
Unison Networks | 2009 | 2008-10-05 | 0.0031753 | 7.9381e-05
Unison Networks | 2009 | 2008-10-06 | 0.0027036 | 1.4008e-05
Unison Networks | 2009 | 2008-10-07 | 1.3282 | 0.013448
Unison Networks | 2009 | 2008-10-08 | 0.0097561 | 7.4712e-05
Unison Networks | 2009 | 2008-10-09 | 0.14349 | 0.0010226
Unison Networks | 2009 | 2008-10-10 | 0.0068642 | 0.00022881
Unison Networks | 2009 | 2008-10-11
Unison Networks | 2009 | 2008-10-12 | 0.10952 | 0.00092456
Unison Networks | 2009 | 2008-10-13
Unison Networks | 2009 | 2008-10-14 | 0.19315 | 0.0010039
Unison Networks | 2009 | 2008-10-15
Unison Networks | 2009 | 2008-10-16 | 1.4717 | 0.027307
Unison Networks | 2009 | 2008-10-17 | 0.021507 | 0.00029885
Unison Networks | 2009 | 2008-10-18
Unison Networks | 2009 | 2008-10-19
Unison Networks | 2009 | 2008-10-20
Unison Networks | 2009 | 2008-10-21 | 0.015115 | 5.1364e-05
Unison Networks | 2009 | 2008-10-22 | 0.057878 | 0.00023347
Unison Networks | 2009 | 2008-10-23 | 0.21379 | 0.00064906
Unison Networks | 2009 | 2008-10-24 | 0.018659 | 7.4712e-05
Unison Networks | 2009 | 2008-10-25 | 0.8182 | 0.0031099
Unison Networks | 2009 | 2008-10-26 | 0.14443 | 0.0014849
Unison Networks | 2009 | 2008-10-27
Unison Networks | 2009 | 2008-10-28 | 0.012496 | 0.0022834
Unison Networks | 2009 | 2008-10-29 | 0.13017 | 0.0024048
Unison Networks | 2009 | 2008-10-30 | 0.40679 | 0.017539
Unison Networks | 2009 | 2008-10-31 | 0.19216 | 0.0029138
Unison Networks | 2009 | 2008-11-01 | 0.044061 | 0.0028951
Unison Networks | 2009 | 2008-11-02 | 0.15553 | 0.0026056
Unison Networks | 2009 | 2008-11-03 | 0.026686 | 0.0069015
Unison Networks | 2009 | 2008-11-04 | 0.3335 | 0.0030258
Unison Networks | 2009 | 2008-11-05 | 0.5608 | 0.009437
Unison Networks | 2009 | 2008-11-06 | 0.33063 | 0.0026523
Unison Networks | 2009 | 2008-11-07 | 0.32077 | 0.0046181
Unison Networks | 2009 | 2008-11-08
Unison Networks | 2009 | 2008-11-09 | 0.0025636 | 1.4008e-05
Unison Networks | 2009 | 2008-11-10 | 0.070729 | 0.0031519
Unison Networks | 2009 | 2008-11-11 | 0.177 | 0.0042913
Unison Networks | 2009 | 2008-11-12 | 0.10421 | 0.00035021
Unison Networks | 2009 | 2008-11-13 | 0.24583 | 0.00066774
Unison Networks | 2009 | 2008-11-14 | 0.0073731 | 4.2025e-05
Unison Networks | 2009 | 2008-11-15 | 0.31829 | 0.012785
Unison Networks | 2009 | 2008-11-16 | 0.11452 | 0.00035021
Unison Networks | 2009 | 2008-11-17 | 0.48806 | 0.0062945
Unison Networks | 2009 | 2008-11-18 | 0.11336 | 0.0019285
Unison Networks | 2009 | 2008-11-19 | 0.95605 | 0.023291
Unison Networks | 2009 | 2008-11-20 | 0.012145 | 7.9381e-05
Unison Networks | 2009 | 2008-11-21 | 0.10119 | 0.0021666
Unison Networks | 2009 | 2008-11-22 | 0.5197 | 0.0047442
Unison Networks | 2009 | 2008-11-23 | 0.058146 | 0.0026196
Unison Networks | 2009 | 2008-11-24 | 1.0153 | 0.014018
Unison Networks | 2009 | 2008-11-25 | 0.054993 | 0.00070976
Unison Networks | 2009 | 2008-11-26 | 0.20366 | 0.0018865
Unison Networks | 2009 | 2008-11-27 | 2.7115 | 0.0092876
Unison Networks | 2009 | 2008-11-28 | 0.078186 | 0.00024281
Unison Networks | 2009 | 2008-11-29 | 0.05256 | 0.0014849
Unison Networks | 2009 | 2008-11-30 | 0.017036 | 0.00029885
Unison Networks | 2009 | 2008-12-01 | 0.65766 | 0.0075132
Unison Networks | 2009 | 2008-12-02 | 0.37967 | 0.0050244
Unison Networks | 2009 | 2008-12-03 | 0.42393 | 0.0019238
Unison Networks | 2009 | 2008-12-04 | 0.076865 | 0.00038757
Unison Networks | 2009 | 2008-12-05 | 0.055992 | 0.00029418
Unison Networks | 2009 | 2008-12-06 | 0.059001 | 0.019136
Unison Networks | 2009 | 2008-12-07 | 0.53453 | 0.0047068
Unison Networks | 2009 | 2008-12-08 | 0.16213 | 0.0014335
Unison Networks | 2009 | 2008-12-09 | 0.078512 | 0.00070509
Unison Networks | 2009 | 2008-12-10 | 0.13932 | 0.00083117
Unison Networks | 2009 | 2008-12-11 | 0.0052859 | 1.8678e-05
Unison Networks | 2009 | 2008-12-12 | 0.13478 | 0.0014569
Unison Networks | 2009 | 2008-12-13
Unison Networks | 2009 | 2008-12-14
Unison Networks | 2009 | 2008-12-15 | 0.12446 | 0.011305
Unison Networks | 2009 | 2008-12-16 | 0.12719 | 0.00068642
Unison Networks | 2009 | 2008-12-17 | 0.05892 | 0.0053606
Unison Networks | 2009 | 2008-12-18 | 0.090196 | 0.00027083
Unison Networks | 2009 | 2008-12-19 | 0.046732 | 0.0002755
Unison Networks | 2009 | 2008-12-20 | 0.11368 | 0.00097125
Unison Networks | 2009 | 2008-12-21 | 1.9883 | 0.025346
Unison Networks | 2009 | 2008-12-22 | 0.0054764 | 0.00022414
Unison Networks | 2009 | 2008-12-23 | 0.049357 | 0.0001681
Unison Networks | 2009 | 2008-12-24 | 0.27886 | 0.012131
Unison Networks | 2009 | 2008-12-25 | 0.0015689 | 0.0015689
Unison Networks | 2009 | 2008-12-26 | 0.32888 | 0.0017651
Unison Networks | 2009 | 2008-12-27
Unison Networks | 2009 | 2008-12-28 | 0.078027 | 0.0017277
Unison Networks | 2009 | 2008-12-29 | 0.7401 | 0.025972
Unison Networks | 2009 | 2008-12-30 | 0.011702 | 0.0048796
Unison Networks | 2009 | 2008-12-31 | 0.29069 | 0.0080502
Unison Networks | 2009 | 2009-01-01 | 0.0045062 | 0.0020639
Unison Networks | 2009 | 2009-01-02
Unison Networks | 2009 | 2009-01-03 | 0.11064 | 0.0045948
Unison Networks | 2009 | 2009-01-04
Unison Networks | 2009 | 2009-01-05
Unison Networks | 2009 | 2009-01-06
Unison Networks | 2009 | 2009-01-07 | 0.98276 | 0.013626
Unison Networks | 2009 | 2009-01-08
Unison Networks | 2009 | 2009-01-09
Unison Networks | 2009 | 2009-01-10 | 0.27356 | 0.0074338
Unison Networks | 2009 | 2009-01-11
Unison Networks | 2009 | 2009-01-12
Unison Networks | 2009 | 2009-01-13 | 0.012542 | 8.872e-05
Unison Networks | 2009 | 2009-01-14 | 0.26933 | 0.0099507
Unison Networks | 2009 | 2009-01-15 | 0.25397 | 0.0041465
Unison Networks | 2009 | 2009-01-16 | 0.043791 | 0.00024748
Unison Networks | 2009 | 2009-01-17 | 0.0012802 | 9.339e-06
Unison Networks | 2009 | 2009-01-18
Unison Networks | 2009 | 2009-01-19 | 0.021293 | 0.00070976
Unison Networks | 2009 | 2009-01-20 | 0.10698 | 0.00045294
Unison Networks | 2009 | 2009-01-21 | 0.28706 | 0.0041232
Unison Networks | 2009 | 2009-01-22 | 0.27861 | 0.0028017
Unison Networks | 2009 | 2009-01-23 | 0.015423 | 4.2025e-05
Unison Networks | 2009 | 2009-01-24 | 0.2419 | 0.0026102
Unison Networks | 2009 | 2009-01-25 | 0.71776 | 0.020485
Unison Networks | 2009 | 2009-01-26 | 0.15504 | 0.0030212
Unison Networks | 2009 | 2009-01-27 | 0.48055 | 0.01073
Unison Networks | 2009 | 2009-01-28 | 0.21043 | 0.0060843
Unison Networks | 2009 | 2009-01-29 | 0.13791 | 0.00046695
Unison Networks | 2009 | 2009-01-30 | 0.83855 | 0.053564
Unison Networks | 2009 | 2009-01-31
Unison Networks | 2009 | 2009-02-01 | 0.56142 | 0.014914
Unison Networks | 2009 | 2009-02-02 | 0.2833 | 0.0074478
Unison Networks | 2009 | 2009-02-03 | 0.9988 | 0.02967
Unison Networks | 2009 | 2009-02-04 | 0.10836 | 0.0048703
Unison Networks | 2009 | 2009-02-05 | 0.64804 | 0.0078214
Unison Networks | 2009 | 2009-02-06
Unison Networks | 2009 | 2009-02-07
Unison Networks | 2009 | 2009-02-08
Unison Networks | 2009 | 2009-02-09 | 0.28128 | 0.010348
Unison Networks | 2009 | 2009-02-10 | 0.13448 | 0.00044827
Unison Networks | 2009 | 2009-02-11 | 0.099687 | 0.00021947
Unison Networks | 2009 | 2009-02-12 | 0.82238 | 0.01597
Unison Networks | 2009 | 2009-02-13 | 0.20196 | 0.0024281
Unison Networks | 2009 | 2009-02-14 | 0.0012701 | 9.339e-06
Unison Networks | 2009 | 2009-02-15 | 0.75868 | 0.013836
Unison Networks | 2009 | 2009-02-16 | 0.013742 | 4.6695e-05
Unison Networks | 2009 | 2009-02-17 | 0.27397 | 0.0019659
Unison Networks | 2009 | 2009-02-18 | 0.079004 | 0.00070042
Unison Networks | 2009 | 2009-02-19 | 0.14575 | 0.00044827
Unison Networks | 2009 | 2009-02-20 | 0.32822 | 0.01024
Unison Networks | 2009 | 2009-02-21 | 0.60155 | 0.0073685
Unison Networks | 2009 | 2009-02-22 | 0.0054073 | 8.4051e-05
Unison Networks | 2009 | 2009-02-23 | 0.055025 | 0.0030632
Unison Networks | 2009 | 2009-02-24 | 0.064906 | 0.00064906
Unison Networks | 2009 | 2009-02-25 | 0.023077 | 6.5373e-05
Unison Networks | 2009 | 2009-02-26 | 0.63665 | 0.0096145
Unison Networks | 2009 | 2009-02-27 | 0.12015 | 0.0014055
Unison Networks | 2009 | 2009-02-28 | 0.2611 | 0.0054353
Unison Networks | 2009 | 2009-03-01 | 0.066746 | 0.0099273
Unison Networks | 2009 | 2009-03-02 | 0.0041839 | 1.4008e-05
Unison Networks | 2009 | 2009-03-03 | 0.38389 | 0.0052532
Unison Networks | 2009 | 2009-03-04 | 0.34381 | 0.012211
Unison Networks | 2009 | 2009-03-05 | 0.79819 | 1.8678e-05
Unison Networks | 2009 | 2009-03-06 | 0.0037963 | 1.4008e-05
Unison Networks | 2009 | 2009-03-07 | 4.541 | 0.028166
Unison Networks | 2009 | 2009-03-08 | 0.15127 | 0.00041558
Unison Networks | 2009 | 2009-03-09 | 0.23089 | 0.011594
Unison Networks | 2009 | 2009-03-10 | 0.50136 | 0.0077327
Unison Networks | 2009 | 2009-03-11 | 0.30111 | 0.0091989
Unison Networks | 2009 | 2009-03-12 | 0.19362 | 0.0061404
Unison Networks | 2009 | 2009-03-13 | 0.89679 | 0.0071303
Unison Networks | 2009 | 2009-03-14 | 0.056515 | 0.00015409
Unison Networks | 2009 | 2009-03-15
Unison Networks | 2009 | 2009-03-16 | 0.10703 | 0.0034881
Unison Networks | 2009 | 2009-03-17 | 0.27587 | 0.0014475
Unison Networks | 2009 | 2009-03-18 | 1.1814 | 0.026411
Unison Networks | 2009 | 2009-03-19 | 0.13605 | 0.0013075
Unison Networks | 2009 | 2009-03-20 | 0.11779 | 0.0051551
Unison Networks | 2009 | 2009-03-21
Unison Networks | 2009 | 2009-03-22 | 0.20967 | 0.0013728
Unison Networks | 2009 | 2009-03-23 | 0.031099 | 9.339e-05
Unison Networks | 2009 | 2009-03-24 | 0.58458 | 0.0018585
Unison Networks | 2009 | 2009-03-25 | 0.011832 | 5.6034e-05
Unison Networks | 2009 | 2009-03-26 | 0.49709 | 0.0030679
Unison Networks | 2009 | 2009-03-27 | 0.29924 | 0.00088253
Unison Networks | 2009 | 2009-03-28 | 0.0018398 | 0.00070976
Unison Networks | 2009 | 2009-03-29 | 0.0308 | 0.0013542
Unison Networks | 2009 | 2009-03-30 | 0.044902 | 0.00022414
Unison Networks | 2009 | 2009-03-31 | 0.22527 | 0.00068642
Unison Networks | 2010 | 2009-04-01 | 0.15461 | 0.0076265
Unison Networks | 2010 | 2009-04-02 | 0.14318 | 0.0019935
Unison Networks | 2010 | 2009-04-03 | 0.51176 | 0.0022949
Unison Networks | 2010 | 2009-04-04
Unison Networks | 2010 | 2009-04-05
Unison Networks | 2010 | 2009-04-06 | 0.23565 | 0.0022022
Unison Networks | 2010 | 2009-04-07 | 0.042875 | 0.00025962
Unison Networks | 2010 | 2009-04-08 | 0.0057257 | 1.8545e-05
Unison Networks | 2010 | 2009-04-09 | 0.025601 | 6.9542e-05
Unison Networks | 2010 | 2009-04-10
Unison Networks | 2010 | 2009-04-11 | 0.0027817 | 1.8545e-05
Unison Networks | 2010 | 2009-04-12
Unison Networks | 2010 | 2009-04-13
Unison Networks | 2010 | 2009-04-14 | 1.7175 | 0.0072278
Unison Networks | 2010 | 2009-04-15 | 0.2905 | 0.0039361
Unison Networks | 2010 | 2009-04-16 | 0.16807 | 0.00083451
Unison Networks | 2010 | 2009-04-17 | 0.26833 | 0.0036626
Unison Networks | 2010 | 2009-04-18
Unison Networks | 2010 | 2009-04-19 | 0.090488 | 0.00031062
Unison Networks | 2010 | 2009-04-20 | 1.2675 | 0.0097313
Unison Networks | 2010 | 2009-04-21 | 0.97245 | 0.0052296
Unison Networks | 2010 | 2009-04-22 | 0.35714 | 0.0025406
Unison Networks | 2010 | 2009-04-23 | 0.0016968 | 1.3908e-05
Unison Networks | 2010 | 2009-04-24 | 0.28358 | 0.0039407
Unison Networks | 2010 | 2009-04-25
Unison Networks | 2010 | 2009-04-26 | 0.041818 | 0.00019008
Unison Networks | 2010 | 2009-04-27 | 0.65943 | 0.010798
Unison Networks | 2010 | 2009-04-28 | 0.023904 | 0.000102
Unison Networks | 2010 | 2009-04-29 | 0.33342 | 0.0049375
Unison Networks | 2010 | 2009-04-30 | 0.036125 | 0.0003338
Unison Networks | 2010 | 2009-05-01 | 0.014803 | 0.00014372
Unison Networks | 2010 | 2009-05-02 | 0.014405 | 6.027e-05
Unison Networks | 2010 | 2009-05-03 | 0.093187 | 0.002981
Unison Networks | 2010 | 2009-05-04 | 0.025202 | 0.00013445
Unison Networks | 2010 | 2009-05-05 | 1.4188 | 0.021688
Unison Networks | 2010 | 2009-05-06 | 0.042935 | 0.00013445
Unison Networks | 2010 | 2009-05-07 | 0.0053572 | 0.0015253
Unison Networks | 2010 | 2009-05-08 | 0.013561 | 0.00054243
Unison Networks | 2010 | 2009-05-09 | 0.00063979 | 4.6362e-06
Unison Networks | 2010 | 2009-05-10
Unison Networks | 2010 | 2009-05-11 | 0.11289 | 0.0069264
Unison Networks | 2010 | 2009-05-12 | 0.03244 | 0.019082
Unison Networks | 2010 | 2009-05-13 | 0.12161 | 0.0012286
Unison Networks | 2010 | 2009-05-14 | 0.13635 | 0.00034771
Unison Networks | 2010 | 2009-05-15 | 0.36111 | 0.029384
Unison Networks | 2010 | 2009-05-16
Unison Networks | 2010 | 2009-05-17 | 0.062199 | 0.0010478
Unison Networks | 2010 | 2009-05-18
Unison Networks | 2010 | 2009-05-19 | 1.8022 | 0.022722
Unison Networks | 2010 | 2009-05-20 | 0.0067616 | 0.0007047
Unison Networks | 2010 | 2009-05-21 | 0.11496 | 0.00061197
Unison Networks | 2010 | 2009-05-22 | 0.023167 | 8.8087e-05
Unison Networks | 2010 | 2009-05-23 | 0.43046 | 0.0069774
Unison Networks | 2010 | 2009-05-24 | 0.40141 | 0.0030228
Unison Networks | 2010 | 2009-05-25 | 0.50055 | 0.010084
Unison Networks | 2010 | 2009-05-26 | 0.051357 | 0.0032639
Unison Networks | 2010 | 2009-05-27 | 0.074892 | 0.010663
Unison Networks | 2010 | 2009-05-28 | 0.28182 | 0.00092259
Unison Networks | 2010 | 2009-05-29 | 0.5678 | 0.015462
Unison Networks | 2010 | 2009-05-30 | 0.002485 | 9.2723e-06
Unison Networks | 2010 | 2009-05-31 | 0.15649 | 0.0018174
Unison Networks | 2010 | 2009-06-01 | 0.13545 | 0.0012147
Unison Networks | 2010 | 2009-06-02
Unison Networks | 2010 | 2009-06-03 | 0.52081 | 0.010965
Unison Networks | 2010 | 2009-06-04 | 0.31146 | 0.0017339
Unison Networks | 2010 | 2009-06-05 | 0.39229 | 0.013904
Unison Networks | 2010 | 2009-06-06 | 0.32643 | 0.01421
Unison Networks | 2010 | 2009-06-07 | 0.11286 | 0.00031526
Unison Networks | 2010 | 2009-06-08 | 0.13605 | 0.0003848
Unison Networks | 2010 | 2009-06-09 | 0.11418 | 0.0039176
Unison Networks | 2010 | 2009-06-10 | 0.33654 | 0.0052991
Unison Networks | 2010 | 2009-06-11 | 0.18559 | 0.00102
Unison Networks | 2010 | 2009-06-12 | 0.22985 | 0.0023366
Unison Networks | 2010 | 2009-06-13 | 1.0552 | 0.027548
Unison Networks | 2010 | 2009-06-14 | 0.69209 | 0.005123
Unison Networks | 2010 | 2009-06-15 | 0.644 | 0.011535
Unison Networks | 2010 | 2009-06-16 | 0.35809 | 0.007339
Unison Networks | 2010 | 2009-06-17 | 1.6495 | 0.030951
Unison Networks | 2010 | 2009-06-18 | 0.045434 | 0.00016227
Unison Networks | 2010 | 2009-06-19
Unison Networks | 2010 | 2009-06-20 | 0.0013445 | 4.6362e-06
Unison Networks | 2010 | 2009-06-21
Unison Networks | 2010 | 2009-06-22 | 0.060817 | 0.00025499
Unison Networks | 2010 | 2009-06-23 | 0.1099 | 0.00081133
Unison Networks | 2010 | 2009-06-24
Unison Networks | 2010 | 2009-06-25 | 0.35893 | 0.0091379
Unison Networks | 2010 | 2009-06-26 | 0.082677 | 0.004205
Unison Networks | 2010 | 2009-06-27
Unison Networks | 2010 | 2009-06-28 | 0.058861 | 0.0020445
Unison Networks | 2010 | 2009-06-29
Unison Networks | 2010 | 2009-06-30 | 0.48384 | 0.001516
Unison Networks | 2010 | 2009-07-01 | 0.091884 | 0.0030506
Unison Networks | 2010 | 2009-07-02 | 0.011729 | 4.6362e-05
Unison Networks | 2010 | 2009-07-03 | 0.4411 | 0.072305
Unison Networks | 2010 | 2009-07-04 | 0.52143 | 0.0015114
Unison Networks | 2010 | 2009-07-05
Unison Networks | 2010 | 2009-07-06 | 0.040945 | 0.00031989
Unison Networks | 2010 | 2009-07-07 | 0.035341 | 0.0004358
Unison Networks | 2010 | 2009-07-08 | 0.057901 | 0.0011915
Unison Networks | 2010 | 2009-07-09 | 0.064062 | 0.00023644
Unison Networks | 2010 | 2009-07-10 | 0.01351 | 0.0002179
Unison Networks | 2010 | 2009-07-11
Unison Networks | 2010 | 2009-07-12 | 0.67136 | 0.018081
Unison Networks | 2010 | 2009-07-13
Unison Networks | 2010 | 2009-07-14 | 0.605 | 0.018758
Unison Networks | 2010 | 2009-07-15 | 0.0098518 | 0.00028744
Unison Networks | 2010 | 2009-07-16 | 0.045169 | 0.0011961
Unison Networks | 2010 | 2009-07-17 | 0.088008 | 0.00102
Unison Networks | 2010 | 2009-07-18 | 0.62408 | 0.0087809
Unison Networks | 2010 | 2009-07-19 | 0.96534 | 0.013876
Unison Networks | 2010 | 2009-07-20 | 0.010116 | 0.00014372
Unison Networks | 2010 | 2009-07-21 | 0.051086 | 0.00036162
Unison Networks | 2010 | 2009-07-22 | 0.22664 | 0.0021095
Unison Networks | 2010 | 2009-07-23 | 0.82576 | 0.0087299
Unison Networks | 2010 | 2009-07-24 | 0.053835 | 0.01217
Unison Networks | 2010 | 2009-07-25
Unison Networks | 2010 | 2009-07-26
Unison Networks | 2010 | 2009-07-27 | 0.019388 | 7.8815e-05
Unison Networks | 2010 | 2009-07-28 | 0.045522 | 0.0002179
Unison Networks | 2010 | 2009-07-29 | 0.09569 | 0.00037553
Unison Networks | 2010 | 2009-07-30 | 0.12131 | 0.0014279
Unison Networks | 2010 | 2009-07-31
Unison Networks | 2010 | 2009-08-01 | 0.004625 | 0.0032268
Unison Networks | 2010 | 2009-08-02 | 0.071466 | 9.7359e-05
Unison Networks | 2010 | 2009-08-03 | 2.7817e-05 | 4.6362e-06
Unison Networks | 2010 | 2009-08-04 | 0.37302 | 0.008869
Unison Networks | 2010 | 2009-08-05 | 0.0062588 | 4.1725e-05
Unison Networks | 2010 | 2009-08-06 | 0.51823 | 0.0033195
Unison Networks | 2010 | 2009-08-07 | 0.17004 | 0.0011266
Unison Networks | 2010 | 2009-08-08
Unison Networks | 2010 | 2009-08-09
Unison Networks | 2010 | 2009-08-10 | 0.0096339 | 0.00031989
Unison Networks | 2010 | 2009-08-11 | 0.0036672 | 3.2453e-05
Unison Networks | 2010 | 2009-08-12 | 0.011437 | 4.1725e-05
Unison Networks | 2010 | 2009-08-13
Unison Networks | 2010 | 2009-08-14
Unison Networks | 2010 | 2009-08-15
Unison Networks | 2010 | 2009-08-16 | 0.06649 | 0.00077887
Unison Networks | 2010 | 2009-08-17 | 0.12467 | 0.0031711
Unison Networks | 2010 | 2009-08-18 | 0.11618 | 0.00035235
Unison Networks | 2010 | 2009-08-19 | 0.021141 | 9.2723e-05
Unison Networks | 2010 | 2009-08-20 | 0.14163 | 0.0022346
Unison Networks | 2010 | 2009-08-21 | 0.074744 | 0.0003848
Unison Networks | 2010 | 2009-08-22
Unison Networks | 2010 | 2009-08-23
Unison Networks | 2010 | 2009-08-24
Unison Networks | 2010 | 2009-08-25 | 0.15538 | 0.0064489
Unison Networks | 2010 | 2009-08-26 | 0.0033439 | 0.003236
Unison Networks | 2010 | 2009-08-27 | 0.92685 | 0.022198
Unison Networks | 2010 | 2009-08-28 | 0.084104 | 0.0059621
Unison Networks | 2010 | 2009-08-29
Unison Networks | 2010 | 2009-08-30 | 0.018786 | 7.8815e-05
Unison Networks | 2010 | 2009-08-31 | 2.0256 | 0.011665
Unison Networks | 2010 | 2009-09-01
Unison Networks | 2010 | 2009-09-02 | 0.0011822 | 4.6362e-06
Unison Networks | 2010 | 2009-09-03 | 1.0986 | 0.028758
Unison Networks | 2010 | 2009-09-04 | 0.11065 | 0.0018823
Unison Networks | 2010 | 2009-09-05 | 0.0012796 | 0.00030135
Unison Networks | 2010 | 2009-09-06 | 0.19791 | 0.0029208
Unison Networks | 2010 | 2009-09-07 | 0.35396 | 0.0023181
Unison Networks | 2010 | 2009-09-08 | 0.39046 | 0.0012749
Unison Networks | 2010 | 2009-09-09 | 0.2727 | 0.0017339
Unison Networks | 2010 | 2009-09-10 | 0.2184 | 0.00040798
Unison Networks | 2010 | 2009-09-11 | 0.0023644 | 4.6362e-05
Unison Networks | 2010 | 2009-09-12 | 0.69824 | 0.011136
Unison Networks | 2010 | 2009-09-13 | 0.0086511 | 2.7817e-05
Unison Networks | 2010 | 2009-09-14 | 0.00066761 | 9.2723e-06
Unison Networks | 2010 | 2009-09-15 | 0.18906 | 0.0005517
Unison Networks | 2010 | 2009-09-16 | 0.054127 | 0.0029254
Unison Networks | 2010 | 2009-09-17 | 0.14178 | 0.00066761
Unison Networks | 2010 | 2009-09-18 | 0.4908 | 0.01198
Unison Networks | 2010 | 2009-09-19
Unison Networks | 2010 | 2009-09-20
Unison Networks | 2010 | 2009-09-21 | 0.016273 | 6.9542e-05
Unison Networks | 2010 | 2009-09-22 | 0.21974 | 0.0087345
Unison Networks | 2010 | 2009-09-23 | 0.03988 | 0.00015763
Unison Networks | 2010 | 2009-09-24 | 0.0044878 | 4.6362e-05
Unison Networks | 2010 | 2009-09-25 | 0.0059806 | 4.6362e-05
Unison Networks | 2010 | 2009-09-26
Unison Networks | 2010 | 2009-09-27 | 0.047636 | 0.0001159
Unison Networks | 2010 | 2009-09-28 | 0.014159 | 3.2453e-05
Unison Networks | 2010 | 2009-09-29 | 0.1566 | 0.00050998
Unison Networks | 2010 | 2009-09-30 | 0.04428 | 0.00025499
Unison Networks | 2010 | 2009-10-01 | 0.27309 | 0.019889
Unison Networks | 2010 | 2009-10-02
Unison Networks | 2010 | 2009-10-03 | 0.11402 | 0.00084842
Unison Networks | 2010 | 2009-10-04 | 4.541 | 0.040307
Unison Networks | 2010 | 2009-10-05 | 1.8518 | 0.0078722
Unison Networks | 2010 | 2009-10-06 | 0.46908 | 0.0095227
Unison Networks | 2010 | 2009-10-07 | 0.00040335 | 4.6362e-06
Unison Networks | 2010 | 2009-10-08
Unison Networks | 2010 | 2009-10-09
Unison Networks | 2010 | 2009-10-10 | 0.013093 | 0.00027817
Unison Networks | 2010 | 2009-10-11
Unison Networks | 2010 | 2009-10-12
Unison Networks | 2010 | 2009-10-13 | 0.089153 | 0.0043209
Unison Networks | 2010 | 2009-10-14 | 0.024912 | 0.00046362
Unison Networks | 2010 | 2009-10-15 | 0.11818 | 0.0015577
Unison Networks | 2010 | 2009-10-16 | 0.035179 | 0.00030135
Unison Networks | 2010 | 2009-10-17
Unison Networks | 2010 | 2009-10-18 | 0.99059 | 0.015517
Unison Networks | 2010 | 2009-10-19
Unison Networks | 2010 | 2009-10-20
Unison Networks | 2010 | 2009-10-21 | 0.15388 | 0.00046825
Unison Networks | 2010 | 2009-10-22 | 0.021067 | 6.027e-05
Unison Networks | 2010 | 2009-10-23
Unison Networks | 2010 | 2009-10-24
Unison Networks | 2010 | 2009-10-25
Unison Networks | 2010 | 2009-10-26
Unison Networks | 2010 | 2009-10-27 | 0.16104 | 0.0018452
Unison Networks | 2010 | 2009-10-28
Unison Networks | 2010 | 2009-10-29 | 0.53419 | 0.0086742
Unison Networks | 2010 | 2009-10-30
Unison Networks | 2010 | 2009-10-31 | 0.077302 | 0.008665
Unison Networks | 2010 | 2009-11-01
Unison Networks | 2010 | 2009-11-02
Unison Networks | 2010 | 2009-11-03 | 0.15637 | 0.016514
Unison Networks | 2010 | 2009-11-04 | 0.065314 | 0.0001669
Unison Networks | 2010 | 2009-11-05 | 0.069209 | 0.00022254
Unison Networks | 2010 | 2009-11-06 | 0.032703 | 0.00012054
Unison Networks | 2010 | 2009-11-07
Unison Networks | 2010 | 2009-11-08 | 0.90039 | 0.013575
Unison Networks | 2010 | 2009-11-09 | 0.026139 | 0.00012518
Unison Networks | 2010 | 2009-11-10 | 0.10419 | 0.00074178
Unison Networks | 2010 | 2009-11-11 | 0.1399 | 0.00073251
Unison Networks | 2010 | 2009-11-12
Unison Networks | 2010 | 2009-11-13 | 1.0503 | 0.0074503
Unison Networks | 2010 | 2009-11-14 | 0.0001669 | 4.6362e-06
Unison Networks | 2010 | 2009-11-15 | 1.1346 | 0.02638
Unison Networks | 2010 | 2009-11-16 | 0.23748 | 0.0027956
Unison Networks | 2010 | 2009-11-17 | 0.023097 | 0.00011127
Unison Networks | 2010 | 2009-11-18 | 0.070266 | 0.00039871
Unison Networks | 2010 | 2009-11-19 | 0.093142 | 0.0019565
Unison Networks | 2010 | 2009-11-20 | 0.38174 | 0.0019935
Unison Networks | 2010 | 2009-11-21 | 0.19772 | 0.0035977
Unison Networks | 2010 | 2009-11-22 | 0.016101 | 0.00070006
Unison Networks | 2010 | 2009-11-23 | 0.034085 | 0.00052389
Unison Networks | 2010 | 2009-11-24 | 0.11286 | 0.00032453
Unison Networks | 2010 | 2009-11-25 | 0.24633 | 0.0043024
Unison Networks | 2010 | 2009-11-26 | 0.54734 | 0.0085444
Unison Networks | 2010 | 2009-11-27 | 0.034076 | 0.00034771
Unison Networks | 2010 | 2009-11-28
Unison Networks | 2010 | 2009-11-29 | 0.40234 | 0.017988
Unison Networks | 2010 | 2009-11-30 | 1.346 | 0.025332
Unison Networks | 2010 | 2009-12-01 | 0.61726 | 0.0028651
Unison Networks | 2010 | 2009-12-02 | 0.0050015 | 0.0024201
Unison Networks | 2010 | 2009-12-03 | 0.30321 | 0.0042004
Unison Networks | 2010 | 2009-12-04
Unison Networks | 2010 | 2009-12-05
Unison Networks | 2010 | 2009-12-06
Unison Networks | 2010 | 2009-12-07 | 0.034041 | 0.0024201
Unison Networks | 2010 | 2009-12-08 | 0.0024664 | 6.4906e-05
Unison Networks | 2010 | 2009-12-09 | 0.0032731 | 9.2723e-06
Unison Networks | 2010 | 2009-12-10 | 0.031572 | 0.00020863
Unison Networks | 2010 | 2009-12-11
Unison Networks | 2010 | 2009-12-12 | 0.34814 | 0.010292
Unison Networks | 2010 | 2009-12-13 | 0.025627 | 0.00017617
Unison Networks | 2010 | 2009-12-14
Unison Networks | 2010 | 2009-12-15 | 0.89223 | 0.0068244
Unison Networks | 2010 | 2009-12-16 | 0.20892 | 0.0034818
Unison Networks | 2010 | 2009-12-17 | 0.25123 | 0.0013955
Unison Networks | 2010 | 2009-12-18 | 0.022652 | 0.00012054
Unison Networks | 2010 | 2009-12-19 | 0.0033798 | 4.6362e-06
Unison Networks | 2010 | 2009-12-20 | 0.015503 | 0.00017617
Unison Networks | 2010 | 2009-12-21 | 1.0501 | 0.010162
Unison Networks | 2010 | 2009-12-22 | 0.0041626 | 0.0016876
Unison Networks | 2010 | 2009-12-23 | 0.20329 | 0.0012147
Unison Networks | 2010 | 2009-12-24 | 0.44928 | 0.015373
Unison Networks | 2010 | 2009-12-25
Unison Networks | 2010 | 2009-12-26 | 0.4925 | 0.0072973
Unison Networks | 2010 | 2009-12-27 | 0.31942 | 0.010793
Unison Networks | 2010 | 2009-12-28 | 0.12739 | 0.0039593
Unison Networks | 2010 | 2009-12-29 | 0.031589 | 0.0015856
Unison Networks | 2010 | 2009-12-30 | 0.63854 | 0.010876
Unison Networks | 2010 | 2009-12-31 | 0.00021326 | 9.2723e-06
Unison Networks | 2010 | 2010-01-01
Unison Networks | 2010 | 2010-01-02 | 0.0019379 | 4.6362e-06
Unison Networks | 2010 | 2010-01-03 | 0.22617 | 0.001057
Unison Networks | 2010 | 2010-01-04 | 0.24395 | 0.0010292
Unison Networks | 2010 | 2010-01-05 | 0.69653 | 0.028012
Unison Networks | 2010 | 2010-01-06 | 0.49228 | 0.010121
Unison Networks | 2010 | 2010-01-07
Unison Networks | 2010 | 2010-01-08 | 0.0052435 | 1.3908e-05
Unison Networks | 2010 | 2010-01-09 | 0.32543 | 0.021484
Unison Networks | 2010 | 2010-01-10
Unison Networks | 2010 | 2010-01-11 | 0.79162 | 0.012045
Unison Networks | 2010 | 2010-01-12 | 0.0014743 | 1.3908e-05
Unison Networks | 2010 | 2010-01-13 | 0.0080947 | 2.7817e-05
Unison Networks | 2010 | 2010-01-14 | 0.0040566 | 3.2453e-05
Unison Networks | 2010 | 2010-01-15 | 0.0059225 | 0.0053038
Unison Networks | 2010 | 2010-01-16 | 2.0037 | 0.0084888
Unison Networks | 2010 | 2010-01-17
Unison Networks | 2010 | 2010-01-18 | 0.014409 | 0.00051461
Unison Networks | 2010 | 2010-01-19 | 0.0034493 | 5.5634e-05
Unison Networks | 2010 | 2010-01-20 | 0.10291 | 0.0054707
Unison Networks | 2010 | 2010-01-21 | 0.025964 | 0.0032778
Unison Networks | 2010 | 2010-01-22 | 0.92967 | 0.020464
Unison Networks | 2010 | 2010-01-23 | 0.22893 | 0.0030506
Unison Networks | 2010 | 2010-01-24 | 0.12216 | 0.0025406
Unison Networks | 2010 | 2010-01-25 | 0.47961 | 0.019954
Unison Networks | 2010 | 2010-01-26 | 0.29422 | 0.029861
Unison Networks | 2010 | 2010-01-27 | 0.018944 | 0.0096896
Unison Networks | 2010 | 2010-01-28 | 0.29521 | 0.0013213
Unison Networks | 2010 | 2010-01-29 | 0.0098055 | 9.7359e-05
Unison Networks | 2010 | 2010-01-30 | 0.0023181 | 9.2723e-05
Unison Networks | 2010 | 2010-01-31 | 0.28485 | 0.0072695
Unison Networks | 2010 | 2010-02-01 | 0.051383 | 0.00061197
Unison Networks | 2010 | 2010-02-02 | 0.085342 | 0.00039871
Unison Networks | 2010 | 2010-02-03 | 0.19029 | 0.0034168
Unison Networks | 2010 | 2010-02-04 | 0.56328 | 0.016551
Unison Networks | 2010 | 2010-02-05 | 0.33974 | 0.0039639
Unison Networks | 2010 | 2010-02-06
Unison Networks | 2010 | 2010-02-07 | 0.2848 | 0.002981
Unison Networks | 2010 | 2010-02-08 | 0.041104 | 0.00014372
Unison Networks | 2010 | 2010-02-09 | 0.056561 | 0.00033844
Unison Networks | 2010 | 2010-02-10 | 0.047595 | 0.00018545
Unison Networks | 2010 | 2010-02-11 | 0.1364 | 0.0016412
Unison Networks | 2010 | 2010-02-12 | 0.00023181 | 2.3181e-05
Unison Networks | 2010 | 2010-02-13
Unison Networks | 2010 | 2010-02-14 | 0.4019 | 0.077377
Unison Networks | 2010 | 2010-02-15 | 0.13814 | 0.0038944
Unison Networks | 2010 | 2010-02-16 | 0.80031 | 0.0031479
Unison Networks | 2010 | 2010-02-17
Unison Networks | 2010 | 2010-02-18
Unison Networks | 2010 | 2010-02-19 | 0.01071 | 0.0012286
Unison Networks | 2010 | 2010-02-20 | 0.05995 | 0.00023644
Unison Networks | 2010 | 2010-02-21 | 0.081834 | 0.0014094
Unison Networks | 2010 | 2010-02-22 | 0.024474 | 7.4178e-05
Unison Networks | 2010 | 2010-02-23 | 0.032546 | 9.2723e-05
Unison Networks | 2010 | 2010-02-24
Unison Networks | 2010 | 2010-02-25 | 0.24372 | 0.004307
Unison Networks | 2010 | 2010-02-26 | 0.0061661 | 4.6362e-05
Unison Networks | 2010 | 2010-02-27
Unison Networks | 2010 | 2010-02-28 | 0.24213 | 0.0090961
Unison Networks | 2010 | 2010-03-01 | 0.20403 | 0.0042374
Unison Networks | 2010 | 2010-03-02 | 0.00084378 | 5.0998e-05
Unison Networks | 2010 | 2010-03-03
Unison Networks | 2010 | 2010-03-04 | 0.68167 | 0.018925
Unison Networks | 2010 | 2010-03-05 | 0.52058 | 0.01548
Unison Networks | 2010 | 2010-03-06 | 0.078901 | 0.0012147
Unison Networks | 2010 | 2010-03-07 | 0.034982 | 0.000102
Unison Networks | 2010 | 2010-03-08 | 0.092686 | 0.00038944
Unison Networks | 2010 | 2010-03-09 | 0.27986 | 0.0041911
Unison Networks | 2010 | 2010-03-10 | 0.095713 | 0.00046362
Unison Networks | 2010 | 2010-03-11 | 0.25478 | 0.0036765
Unison Networks | 2010 | 2010-03-12 | 0.60868 | 0.020483
Unison Networks | 2010 | 2010-03-13 | 0.016783 | 4.6362e-05
Unison Networks | 2010 | 2010-03-14 | 0.004043 | 1.8545e-05
Unison Networks | 2010 | 2010-03-15 | 0.19058 | 0.0044646
Unison Networks | 2010 | 2010-03-16 | 1.1516 | 0.0013955
Unison Networks | 2010 | 2010-03-17 | 0.56756 | 0.011618
Unison Networks | 2010 | 2010-03-18 | 0.11341 | 0.00037553
Unison Networks | 2010 | 2010-03-19
Unison Networks | 2010 | 2010-03-20 | 0.15446 | 0.0014001
Unison Networks | 2010 | 2010-03-21
Unison Networks | 2010 | 2010-03-22 | 0.19912 | 0.001924
Unison Networks | 2010 | 2010-03-23 | 0.021393 | 0.0015577
Unison Networks | 2010 | 2010-03-24 | 0.05436 | 0.0019008
Unison Networks | 2010 | 2010-03-25 | 0.24124 | 0.00084378
Unison Networks | 2010 | 2010-03-26
Unison Networks | 2010 | 2010-03-27 | 0.083382 | 0.0029625
Unison Networks | 2010 | 2010-03-28
Unison Networks | 2010 | 2010-03-29 | 0.017455 | 0.0010246
Unison Networks | 2010 | 2010-03-30 | 0.48913 | 0.011697
Unison Networks | 2010 | 2010-03-31 | 0.082663 | 0.00060734
Unison Networks | 2011 | 2010-04-01 | 0.24682 | 0.0066931
Unison Networks | 2011 | 2010-04-02 | 0.080576 | 0.00025778
Unison Networks | 2011 | 2010-04-03
Unison Networks | 2011 | 2010-04-04
Unison Networks | 2011 | 2010-04-05 | 0.52874 | 0.012576
Unison Networks | 2011 | 2010-04-06 | 0.44592 | 0.0042626
Unison Networks | 2011 | 2010-04-07 | 0.47152 | 0.0038851
Unison Networks | 2011 | 2010-04-08 | 0.056564 | 0.0010403
Unison Networks | 2011 | 2010-04-09 | 0.037034 | 0.00015651
Unison Networks | 2011 | 2010-04-10 | 0.010095 | 0.0015513
Unison Networks | 2011 | 2010-04-11
Unison Networks | 2011 | 2010-04-12 | 0.010053 | 3.6826e-05
Unison Networks | 2011 | 2010-04-13 | 0.017419 | 7.3652e-05
Unison Networks | 2011 | 2010-04-14 | 0.42431 | 0.014523
Unison Networks | 2011 | 2010-04-15 | 0.097326 | 0.0021451
Unison Networks | 2011 | 2010-04-16 | 0.047897 | 0.0043777
Unison Networks | 2011 | 2010-04-17 | 0.38068 | 0.012281
Unison Networks | 2011 | 2010-04-18 | 0.0083825 | 0.00013349
Unison Networks | 2011 | 2010-04-19 | 0.0037608 | 8.7461e-05
Unison Networks | 2011 | 2010-04-20 | 0.15817 | 0.01183
Unison Networks | 2011 | 2010-04-21 | 0.036972 | 0.012106
Unison Networks | 2011 | 2010-04-22 | 0.138 | 0.00075033
Unison Networks | 2011 | 2010-04-23 | 0.0061062 | 0.0026284
Unison Networks | 2011 | 2010-04-24
Unison Networks | 2011 | 2010-04-25
Unison Networks | 2011 | 2010-04-26 | 0.81185 | 0.0093998
Unison Networks | 2011 | 2010-04-27 | 0.017056 | 0.002808
Unison Networks | 2011 | 2010-04-28 | 0.0088441 | 0.00026699
Unison Networks | 2011 | 2010-04-29 | 0.091613 | 0.00021175
Unison Networks | 2011 | 2010-04-30 | 0.0075161 | 0.00077334
Unison Networks | 2011 | 2010-05-01
Unison Networks | 2011 | 2010-05-02 | 0.12464 | 0.0033235
Unison Networks | 2011 | 2010-05-03 | 0.062641 | 0.00029
Unison Networks | 2011 | 2010-05-04 | 0.047188 | 0.00025318
Unison Networks | 2011 | 2010-05-05 | 0.067483 | 0.00025318
Unison Networks | 2011 | 2010-05-06 | 0.10872 | 0.0022326
Unison Networks | 2011 | 2010-05-07 | 0.0044731 | 2.7619e-05
Unison Networks | 2011 | 2010-05-08 | 0.059601 | 0.010426
Unison Networks | 2011 | 2010-05-09
Unison Networks | 2011 | 2010-05-10 | 0.17747 | 0.00044191
Unison Networks | 2011 | 2010-05-11 | 0.24991 | 0.0010726
Unison Networks | 2011 | 2010-05-12 | 0.06253 | 0.00018413
Unison Networks | 2011 | 2010-05-13 | 0.48736 | 0.012719
Unison Networks | 2011 | 2010-05-14
Unison Networks | 2011 | 2010-05-15 | 0.12261 | 0.0042073
Unison Networks | 2011 | 2010-05-16 | 0.056518 | 0.007959
Unison Networks | 2011 | 2010-05-17 | 0.20225 | 0.014238
Unison Networks | 2011 | 2010-05-18 | 0.14458 | 0.00078255
Unison Networks | 2011 | 2010-05-19 | 0.057324 | 0.00062144
Unison Networks | 2011 | 2010-05-20 | 0.065048 | 0.00048794
Unison Networks | 2011 | 2010-05-21 | 0.54374 | 0.0075769
Unison Networks | 2011 | 2010-05-22 | 0.11782 | 0.001206
Unison Networks | 2011 | 2010-05-23 | 0.18018 | 0.00063985
Unison Networks | 2011 | 2010-05-24 | 0.22675 | 0.0052661
Unison Networks | 2011 | 2010-05-25 | 0.03039 | 0.0019518
Unison Networks | 2011 | 2010-05-26 | 1.0122 | 0.024406
Unison Networks | 2011 | 2010-05-27 | 0.014896 | 0.0015099
Unison Networks | 2011 | 2010-05-28 | 0.30588 | 0.011526
Unison Networks | 2011 | 2010-05-29 | 0.11587 | 0.0029369
Unison Networks | 2011 | 2010-05-30
Unison Networks | 2011 | 2010-05-31
Unison Networks | 2011 | 2010-06-01 | 0.078204 | 0.0014684
Unison Networks | 2011 | 2010-06-02 | 0.16707 | 0.010449
Unison Networks | 2011 | 2010-06-03 | 0.01189 | 9.6668e-05
Unison Networks | 2011 | 2010-06-04 | 0.024305 | 0.00060302
Unison Networks | 2011 | 2010-06-05 | 0.32766 | 0.0051096
Unison Networks | 2011 | 2010-06-06 | 0.78321 | 0.010993
Unison Networks | 2011 | 2010-06-07 | 0.25555 | 0.0012429
Unison Networks | 2011 | 2010-06-08 | 0.29993 | 0.010357
Unison Networks | 2011 | 2010-06-09 | 0.64171 | 0.033198
Unison Networks | 2011 | 2010-06-10 | 1.1312 | 0.015969
Unison Networks | 2011 | 2010-06-11 | 0.32871 | 0.0088106
Unison Networks | 2011 | 2010-06-12 | 1.294 | 0.0048748
Unison Networks | 2011 | 2010-06-13 | 0.010127 | 0.00010127
Unison Networks | 2011 | 2010-06-14 | 0.97198 | 0.024498
Unison Networks | 2011 | 2010-06-15 | 0.082759 | 0.0023338
Unison Networks | 2011 | 2010-06-16 | 0.43098 | 0.0018551
Unison Networks | 2011 | 2010-06-17 | 0.26311 | 0.0038483
Unison Networks | 2011 | 2010-06-18 | 0.0097312 | 4.1429e-05
Unison Networks | 2011 | 2010-06-19 | 0.72991 | 0.0075815
Unison Networks | 2011 | 2010-06-20 | 0.28632 | 0.0027665
Unison Networks | 2011 | 2010-06-21 | 0.28623 | 0.0048104
Unison Networks | 2011 | 2010-06-22 | 0.038193 | 0.00036365
Unison Networks | 2011 | 2010-06-23 | 0.047615 | 0.00023937
Unison Networks | 2011 | 2010-06-24 | 0.43341 | 0.02407
Unison Networks | 2011 | 2010-06-25 | 0.0010772 | 1.381e-05
Unison Networks | 2011 | 2010-06-26
Unison Networks | 2011 | 2010-06-27 | 0.16096 | 0.024121
Unison Networks | 2011 | 2010-06-28 | 0.00040508 | 4.6032e-06
Unison Networks | 2011 | 2010-06-29 | 0.26076 | 0.0012751
Unison Networks | 2011 | 2010-06-30 | 0.027383 | 0.0010818
Unison Networks | 2011 | 2010-07-01 | 0.0068588 | 2.3016e-05
Unison Networks | 2011 | 2010-07-02
Unison Networks | 2011 | 2010-07-03
Unison Networks | 2011 | 2010-07-04 | 0.036255 | 0.00010127
Unison Networks | 2011 | 2010-07-05 | 0.051786 | 0.00034524
Unison Networks | 2011 | 2010-07-06 | 0.54996 | 0.0024029
Unison Networks | 2011 | 2010-07-07
Unison Networks | 2011 | 2010-07-08 | 0.033102 | 0.0016065
Unison Networks | 2011 | 2010-07-09
Unison Networks | 2011 | 2010-07-10
Unison Networks | 2011 | 2010-07-11 | 0.06845 | 0.00030381
Unison Networks | 2011 | 2010-07-12 | 0.050028 | 0.00055699
Unison Networks | 2011 | 2010-07-13 | 0.63957 | 0.016213
Unison Networks | 2011 | 2010-07-14 | 0.01067 | 8.7461e-05
Unison Networks | 2011 | 2010-07-15 | 0.00062604 | 4.6032e-06
Unison Networks | 2011 | 2010-07-16 | 0.0033604 | 5.9842e-05
Unison Networks | 2011 | 2010-07-17 | 0.049383 | 0.00068588
Unison Networks | 2011 | 2010-07-18 | 0.38402 | 0.0055607
Unison Networks | 2011 | 2010-07-19 | 0.096557 | 0.00031762
Unison Networks | 2011 | 2010-07-20 | 0.15555 | 0.0014776
Unison Networks | 2011 | 2010-07-21 | 0.091015 | 0.023343
Unison Networks | 2011 | 2010-07-22 | 0.010587 | 0.0004235
Unison Networks | 2011 | 2010-07-23 | 0.11037 | 0.0045296
Unison Networks | 2011 | 2010-07-24
Unison Networks | 2011 | 2010-07-25 | 0.093542 | 0.00024857
Unison Networks | 2011 | 2010-07-26 | 0.010219 | 9.2065e-05
Unison Networks | 2011 | 2010-07-27 | 0.18946 | 0.0025548
Unison Networks | 2011 | 2010-07-28 | 0.026436 | 0.00010587
Unison Networks | 2011 | 2010-07-29 | 0.096497 | 0.00048794
Unison Networks | 2011 | 2010-07-30 | 0.98206 | 0.020429
Unison Networks | 2011 | 2010-07-31 | 0.20943 | 0.0042994
Unison Networks | 2011 | 2010-08-01 | 1.2259 | 0.0045388
Unison Networks | 2011 | 2010-08-02 | 0.23399 | 0.0010818
Unison Networks | 2011 | 2010-08-03 | 0.0038943 | 1.381e-05
Unison Networks | 2011 | 2010-08-04 | 0.12883 | 0.0010772
Unison Networks | 2011 | 2010-08-05 | 0.018905 | 0.00017032
Unison Networks | 2011 | 2010-08-06 | 0.059547 | 0.00077334
Unison Networks | 2011 | 2010-08-07 | 0.056881 | 0.0031302
Unison Networks | 2011 | 2010-08-08 | 0.27299 | 0.0084976
Unison Networks | 2011 | 2010-08-09
Unison Networks | 2011 | 2010-08-10 | 0.086344 | 0.0021083
Unison Networks | 2011 | 2010-08-11
Unison Networks | 2011 | 2010-08-12 | 0.039358 | 0.0001381
Unison Networks | 2011 | 2010-08-13 | 0.0045434 | 1.381e-05
Unison Networks | 2011 | 2010-08-14 | 0.25317 | 0.0054502
Unison Networks | 2011 | 2010-08-15 | 0.0067603 | 5.0635e-05
Unison Networks | 2011 | 2010-08-16 | 0.015147 | 0.006822
Unison Networks | 2011 | 2010-08-17
Unison Networks | 2011 | 2010-08-18 | 0.043919 | 0.00029921
Unison Networks | 2011 | 2010-08-19 | 0.063014 | 0.00049255
Unison Networks | 2011 | 2010-08-20 | 0.023688 | 0.00016572
Unison Networks | 2011 | 2010-08-21
Unison Networks | 2011 | 2010-08-22
Unison Networks | 2011 | 2010-08-23
Unison Networks | 2011 | 2010-08-24 | 0.059336 | 0.00024857
Unison Networks | 2011 | 2010-08-25 | 0.51201 | 0.0025042
Unison Networks | 2011 | 2010-08-26 | 0.0703 | 0.0002808
Unison Networks | 2011 | 2010-08-27
Unison Networks | 2011 | 2010-08-28 | 0.0039358 | 2.3016e-05
Unison Networks | 2011 | 2010-08-29 | 0.73091 | 0.007135
Unison Networks | 2011 | 2010-08-30 | 1.1792 | 0.0077012
Unison Networks | 2011 | 2010-08-31 | 0.013119 | 6.9048e-05
Unison Networks | 2011 | 2010-09-01
Unison Networks | 2011 | 2010-09-02 | 0.10749 | 0.0046815
Unison Networks | 2011 | 2010-09-03 | 0.0049864 | 0.0022418
Unison Networks | 2011 | 2010-09-04 | 0.11926 | 0.0045526
Unison Networks | 2011 | 2010-09-05 | 0.33336 | 0.0051832
Unison Networks | 2011 | 2010-09-06 | 0.1794 | 0.0027389
Unison Networks | 2011 | 2010-09-07 | 0.093934 | 0.0010864
Unison Networks | 2011 | 2010-09-08 | 0.030496 | 0.00011508
Unison Networks | 2011 | 2010-09-09 | 0.71054 | 0.011913
Unison Networks | 2011 | 2010-09-10 | 0.019831 | 8.2858e-05
Unison Networks | 2011 | 2010-09-11 | 0.30699 | 0.0021313
Unison Networks | 2011 | 2010-09-12
Unison Networks | 2011 | 2010-09-13 | 0.58559 | 0.01009
Unison Networks | 2011 | 2010-09-14 | 0.039611 | 0.00019334
Unison Networks | 2011 | 2010-09-15 | 0.051466 | 0.0022188
Unison Networks | 2011 | 2010-09-16
Unison Networks | 2011 | 2010-09-17 | 4.541 | 0.025889
Unison Networks | 2011 | 2010-09-18 | 0.55337 | 0.0059197
Unison Networks | 2011 | 2010-09-19 | 1.4586 | 0.009363
Unison Networks | 2011 | 2010-09-20 | 0.15672 | 0.0040969
Unison Networks | 2011 | 2010-09-21 | 3.1768 | 0.024457
Unison Networks | 2011 | 2010-09-22 | 0.10924 | 0.0042258
Unison Networks | 2011 | 2010-09-23 | 1.2855 | 0.013262
Unison Networks | 2011 | 2010-09-24
Unison Networks | 2011 | 2010-09-25
Unison Networks | 2011 | 2010-09-26
Unison Networks | 2011 | 2010-09-27 | 0.13868 | 0.019085
Unison Networks | 2011 | 2010-09-28 | 0.0482 | 0.00017032
Unison Networks | 2011 | 2010-09-29
Unison Networks | 2011 | 2010-09-30 | 0.012042 | 5.5239e-05
Unison Networks | 2011 | 2010-10-01 | 0.007692 | 1.381e-05
Unison Networks | 2011 | 2010-10-02 | 0.23785 | 0.0047735
Unison Networks | 2011 | 2010-10-03 | 0.38396 | 0.0047966
Unison Networks | 2011 | 2010-10-04
Unison Networks | 2011 | 2010-10-05 | 0.18144 | 0.0044559
Unison Networks | 2011 | 2010-10-06 | 0.27346 | 0.011195
Unison Networks | 2011 | 2010-10-07 | 0.055984 | 0.00098049
Unison Networks | 2011 | 2010-10-08
Unison Networks | 2011 | 2010-10-09 | 0.14163 | 0.01154
Unison Networks | 2011 | 2010-10-10
Unison Networks | 2011 | 2010-10-11 | 0.89609 | 0.023453
Unison Networks | 2011 | 2010-10-12 | 1.4389 | 0.010601
Unison Networks | 2011 | 2010-10-13 | 0.25216 | 0.0009943
Unison Networks | 2011 | 2010-10-14 | 0.48516 | 0.0080418
Unison Networks | 2011 | 2010-10-15 | 0.40791 | 0.007356
Unison Networks | 2011 | 2010-10-16
Unison Networks | 2011 | 2010-10-17 | 0.0678 | 0.0015467
Unison Networks | 2011 | 2010-10-18 | 0.92715 | 0.012304
Unison Networks | 2011 | 2010-10-19 | 0.0066029 | 0.0030013
Unison Networks | 2011 | 2010-10-20
Unison Networks | 2011 | 2010-10-21 | 0.015545 | 0.00031762
Unison Networks | 2011 | 2010-10-22 | 0.00076874 | 4.6032e-06
Unison Networks | 2011 | 2010-10-23
Unison Networks | 2011 | 2010-10-24 | 0.1169 | 0.0047781
Unison Networks | 2011 | 2010-10-25
Unison Networks | 2011 | 2010-10-26
Unison Networks | 2011 | 2010-10-27 | 0.0078141 | 0.00020715
Unison Networks | 2011 | 2010-10-28
Unison Networks | 2011 | 2010-10-29 | 0.14028 | 0.0010035
Unison Networks | 2011 | 2010-10-30
Unison Networks | 2011 | 2010-10-31 | 0.43918 | 0.0055055
Unison Networks | 2011 | 2010-11-01 | 0.12398 | 0.00063525
Unison Networks | 2011 | 2010-11-02
Unison Networks | 2011 | 2010-11-03 | 0.26236 | 0.0027481
Unison Networks | 2011 | 2010-11-04 | 0.008051 | 1.8413e-05
Unison Networks | 2011 | 2010-11-05
Unison Networks | 2011 | 2010-11-06
Unison Networks | 2011 | 2010-11-07
Unison Networks | 2011 | 2010-11-08 | 0.0090453 | 8.2858e-05
Unison Networks | 2011 | 2010-11-09 | 0.037397 | 0.0001473
Unison Networks | 2011 | 2010-11-10 | 0.0064767 | 0.00013349
Unison Networks | 2011 | 2010-11-11
Unison Networks | 2011 | 2010-11-12 | 0.2343 | 0.0012613
Unison Networks | 2011 | 2010-11-13 | 0.00010127 | 4.6032e-06
Unison Networks | 2011 | 2010-11-14 | 0.25435 | 0.0014086
Unison Networks | 2011 | 2010-11-15 | 0.031004 | 0.0069693
Unison Networks | 2011 | 2010-11-16 | 0.4303 | 0.001358
Unison Networks | 2011 | 2010-11-17 | 0.06045 | 0.00027159
Unison Networks | 2011 | 2010-11-18 | 0.20916 | 0.0010956
Unison Networks | 2011 | 2010-11-19 | 0.09797 | 0.00043731
Unison Networks | 2011 | 2010-11-20 | 0.21561 | 0.0018505
Unison Networks | 2011 | 2010-11-21 | 0.0073972 | 4.6032e-05
Unison Networks | 2011 | 2010-11-22 | 0.41764 | 0.010146
Unison Networks | 2011 | 2010-11-23 | 0.28172 | 0.0014132
Unison Networks | 2011 | 2010-11-24
Unison Networks | 2011 | 2010-11-25 | 0.21951 | 0.00062604
Unison Networks | 2011 | 2010-11-26 | 0.32459 | 0.0027619
Unison Networks | 2011 | 2010-11-27
Unison Networks | 2011 | 2010-11-28 | 0.024278 | 0.0012106
Unison Networks | 2011 | 2010-11-29 | 0.67183 | 0.017791
Unison Networks | 2011 | 2010-11-30 | 0.0077058 | 1.381e-05
Unison Networks | 2011 | 2010-12-01 | 0.08883 | 0.0020668
Unison Networks | 2011 | 2010-12-02 | 0.069969 | 0.00033604
Unison Networks | 2011 | 2010-12-03 | 0.027527 | 0.00010127
Unison Networks | 2011 | 2010-12-04
Unison Networks | 2011 | 2010-12-05 | 0.043639 | 0.011508
Unison Networks | 2011 | 2010-12-06 | 0.45207 | 0.01497
Unison Networks | 2011 | 2010-12-07 | 0.21547 | 0.0015237
Unison Networks | 2011 | 2010-12-08 | 0.0037424 | 1.381e-05
Unison Networks | 2011 | 2010-12-09 | 0.030602 | 0.00011048
Unison Networks | 2011 | 2010-12-10 | 0.039832 | 0.0001427
Unison Networks | 2011 | 2010-12-11
Unison Networks | 2011 | 2010-12-12
Unison Networks | 2011 | 2010-12-13 | 0.001496 | 7.3652e-05
Unison Networks | 2011 | 2010-12-14 | 0.15839 | 0.003434
Unison Networks | 2011 | 2010-12-15 | 0.18784 | 0.0011876
Unison Networks | 2011 | 2010-12-16 | 0.00047874 | 4.6032e-06
Unison Networks | 2011 | 2010-12-17 | 0.09779 | 0.00063985
Unison Networks | 2011 | 2010-12-18
Unison Networks | 2011 | 2010-12-19 | 0.010108 | 0.0001473
Unison Networks | 2011 | 2010-12-20 | 4.5569 | 0.077278
Unison Networks | 2011 | 2010-12-21 | 0.4756 | 0.011384
Unison Networks | 2011 | 2010-12-22 | 0.11241 | 0.0026791
Unison Networks | 2011 | 2010-12-23 | 0.15974 | 0.0027343
Unison Networks | 2011 | 2010-12-24
Unison Networks | 2011 | 2010-12-25
Unison Networks | 2011 | 2010-12-26
Unison Networks | 2011 | 2010-12-27 | 0.20982 | 0.0099522
Unison Networks | 2011 | 2010-12-28 | 4.5604 | 0.077163
Unison Networks | 2011 | 2010-12-29 | 0.24501 | 0.0017861
Unison Networks | 2011 | 2010-12-30
Unison Networks | 2011 | 2010-12-31 | 0.0036685 | 0.00039588
Unison Networks | 2011 | 2011-01-01 | 0.13542 | 0.0031486
Unison Networks | 2011 | 2011-01-02
Unison Networks | 2011 | 2011-01-03
Unison Networks | 2011 | 2011-01-04
Unison Networks | 2011 | 2011-01-05 | 0.067308 | 0.0017354
Unison Networks | 2011 | 2011-01-06
Unison Networks | 2011 | 2011-01-07 | 0.05174 | 0.00068128
Unison Networks | 2011 | 2011-01-08 | 0.1301 | 8.2858e-05
Unison Networks | 2011 | 2011-01-09 | 0.051885 | 0.0007181
Unison Networks | 2011 | 2011-01-10
Unison Networks | 2011 | 2011-01-11 | 0.15669 | 0.00068128
Unison Networks | 2011 | 2011-01-12
Unison Networks | 2011 | 2011-01-13 | 0.15546 | 0.0024811
Unison Networks | 2011 | 2011-01-14 | 0.020948 | 0.0035445
Unison Networks | 2011 | 2011-01-15 | 0.27248 | 0.0026699
Unison Networks | 2011 | 2011-01-16 | 0.25976 | 0.0064491
Unison Networks | 2011 | 2011-01-17 | 0.074997 | 0.0078163
Unison Networks | 2011 | 2011-01-18 | 1.0351 | 0.010974
Unison Networks | 2011 | 2011-01-19 | 1.0109 | 0.024333
Unison Networks | 2011 | 2011-01-20 | 0.29029 | 0.0085114
Unison Networks | 2011 | 2011-01-21 | 0.022798 | 0.00031302
Unison Networks | 2011 | 2011-01-22 | 0.00025348 | 9.2065e-06
Unison Networks | 2011 | 2011-01-23 | 4.541 | 0.029497
Unison Networks | 2011 | 2011-01-24 | 4.6003 | 0.024577
Unison Networks | 2011 | 2011-01-25 | 2.653 | 0.018109
Unison Networks | 2011 | 2011-01-26 | 0.015074 | 0.0015651
Unison Networks | 2011 | 2011-01-27
Unison Networks | 2011 | 2011-01-28 | 0.1167 | 0.0059013
Unison Networks | 2011 | 2011-01-29 | 0.96789 | 0.028291
Unison Networks | 2011 | 2011-01-30
Unison Networks | 2011 | 2011-01-31 | 0.79092 | 0.013156
Unison Networks | 2011 | 2011-02-01 | 0.013326 | 0.00017492
Unison Networks | 2011 | 2011-02-02 | 0.31121 | 0.0021497
Unison Networks | 2011 | 2011-02-03 | 0.73508 | 0.011968
Unison Networks | 2011 | 2011-02-04 | 0.094725 | 0.0019702
Unison Networks | 2011 | 2011-02-05
Unison Networks | 2011 | 2011-02-06
Unison Networks | 2011 | 2011-02-07 | 0.55139 | 0.012318
Unison Networks | 2011 | 2011-02-08 | 0.060763 | 0.00025318
Unison Networks | 2011 | 2011-02-09 | 0.08066 | 0.0016019
Unison Networks | 2011 | 2011-02-10
Unison Networks | 2011 | 2011-02-11 | 0.45977 | 0.074001
Unison Networks | 2011 | 2011-02-12 | 0.054315 | 0.0014638
Unison Networks | 2011 | 2011-02-13 | 0.58905 | 0.01259
Unison Networks | 2011 | 2011-02-14 | 0.0076874 | 0.00052937
Unison Networks | 2011 | 2011-02-15 | 0.0014316 | 4.6032e-06
Unison Networks | 2011 | 2011-02-16 | 0.062654 | 0.00017953
Unison Networks | 2011 | 2011-02-17 | 0.10904 | 0.0040232
Unison Networks | 2011 | 2011-02-18 | 0.00094826 | 9.2065e-06
Unison Networks | 2011 | 2011-02-19
Unison Networks | 2011 | 2011-02-20
Unison Networks | 2011 | 2011-02-21 | 0.0087553 | 2.3016e-05
Unison Networks | 2011 | 2011-02-22 | 0.026248 | 5.9842e-05
Unison Networks | 2011 | 2011-02-23 | 0.17931 | 0.006288
Unison Networks | 2011 | 2011-02-24 | 0.017216 | 5.5239e-05
Unison Networks | 2011 | 2011-02-25 | 0.0288 | 0.0035997
Unison Networks | 2011 | 2011-02-26 | 0.20844 | 0.0022556
Unison Networks | 2011 | 2011-02-27 | 0.00031762 | 4.6032e-06
Unison Networks | 2011 | 2011-02-28
Unison Networks | 2011 | 2011-03-01 | 0.043445 | 0.0001473
Unison Networks | 2011 | 2011-03-02 | 0.0021267 | 0.0007089
Unison Networks | 2011 | 2011-03-03 | 0.16756 | 0.001496
Unison Networks | 2011 | 2011-03-04 | 0.51487 | 0.0079406
Unison Networks | 2011 | 2011-03-05 | 0.46476 | 0.013796
Unison Networks | 2011 | 2011-03-06 | 0.42425 | 0.001648
Unison Networks | 2011 | 2011-03-07 | 0.12082 | 0.00090684
Unison Networks | 2011 | 2011-03-08 | 0.047956 | 0.00019334
Unison Networks | 2011 | 2011-03-09
Unison Networks | 2011 | 2011-03-10 | 0.011922 | 3.2223e-05
Unison Networks | 2011 | 2011-03-11 | 0.3717 | 0.0054226
Unison Networks | 2011 | 2011-03-12 | 0.085571 | 0.0010173
Unison Networks | 2011 | 2011-03-13
Unison Networks | 2011 | 2011-03-14 | 0.13127 | 0.00069048
Unison Networks | 2011 | 2011-03-15 | 0.32914 | 0.0055285
Unison Networks | 2011 | 2011-03-16 | 0.093051 | 0.006044
Unison Networks | 2011 | 2011-03-17
Unison Networks | 2011 | 2011-03-18 | 0.85877 | 0.017414
Unison Networks | 2011 | 2011-03-19 | 0.49161 | 0.003434
Unison Networks | 2011 | 2011-03-20 | 0.13571 | 0.0057172
Unison Networks | 2011 | 2011-03-21 | 0.04411 | 0.0079636
Unison Networks | 2011 | 2011-03-22 | 2.2629 | 0.045144
Unison Networks | 2011 | 2011-03-23 | 0.16247 | 0.00077334
Unison Networks | 2011 | 2011-03-24 | 0.08935 | 0.001961
Unison Networks | 2011 | 2011-03-25 | 0.16065 | 0.0012521
Unison Networks | 2011 | 2011-03-26 | 0.46645 | 0.0071074
Unison Networks | 2011 | 2011-03-27 | 0.40079 | 0.0068864
Unison Networks | 2011 | 2011-03-28 | 0.028968 | 0.00013349
Unison Networks | 2011 | 2011-03-29 | 0.40148 | 0.009073
Unison Networks | 2011 | 2011-03-30 | 0.12479 | 0.0022602
Unison Networks | 2011 | 2011-03-31 | 0.0037194 | 9.2065e-06
Unison Networks | 2012 | 2011-04-01 | 0.00023837 | 1.8336e-05
Unison Networks | 2012 | 2011-04-02 | 0.00095347 | 0.00023837
Unison Networks | 2012 | 2011-04-03 | 0.00011002 | 2.7504e-05
Unison Networks | 2012 | 2011-04-04 | 0.010979 | 0.0010727
Unison Networks | 2012 | 2011-04-05 | 0.14448 | 0.0069952
Unison Networks | 2012 | 2011-04-06 | 0.06369 | 0.00038506
Unison Networks | 2012 | 2011-04-07 | 0.18341 | 0.0028237
Unison Networks | 2012 | 2011-04-08 | 0.00093055 | 4.584e-06
Unison Networks | 2012 | 2011-04-09
Unison Networks | 2012 | 2011-04-10
Unison Networks | 2012 | 2011-04-11 | 1.2852 | 0.078047
Unison Networks | 2012 | 2011-04-12 | 0.13006 | 0.00038506
Unison Networks | 2012 | 2011-04-13 | 0.35688 | 0.012542
Unison Networks | 2012 | 2011-04-14 | 0.27009 | 0.00087554
Unison Networks | 2012 | 2011-04-15 | 0.12842 | 0.00046757
Unison Networks | 2012 | 2011-04-16 | 0.12132 | 0.0014165
Unison Networks | 2012 | 2011-04-17 | 0.90763 | 0.01355
Unison Networks | 2012 | 2011-04-18 | 1.8747 | 0.012537
Unison Networks | 2012 | 2011-04-19 | 0.0032455 | 1.8336e-05
Unison Networks | 2012 | 2011-04-20 | 0.27544 | 0.00093055
Unison Networks | 2012 | 2011-04-21 | 0.19413 | 0.003846
Unison Networks | 2012 | 2011-04-22
Unison Networks | 2012 | 2011-04-23
Unison Networks | 2012 | 2011-04-24 | 0.23448 | 0.0082879
Unison Networks | 2012 | 2011-04-25
Unison Networks | 2012 | 2011-04-26 | 4.541 | 0.077048
Unison Networks | 2012 | 2011-04-27 | 4.9043 | 0.042718
Unison Networks | 2012 | 2011-04-28 | 0.18835 | 0.0032363
Unison Networks | 2012 | 2011-04-29 | 0.10093 | 0.00021086
Unison Networks | 2012 | 2011-04-30
Unison Networks | 2012 | 2011-05-01 | 0.010741 | 0.0032638
Unison Networks | 2012 | 2011-05-02 | 0.20534 | 0.0074536
Unison Networks | 2012 | 2011-05-03 | 0.031446 | 0.00012835
Unison Networks | 2012 | 2011-05-04
Unison Networks | 2012 | 2011-05-05 | 0.0086638 | 0.00012377
Unison Networks | 2012 | 2011-05-06 | 0.0086053 | 0.00041256
Unison Networks | 2012 | 2011-05-07 | 0.42756 | 0.073289
Unison Networks | 2012 | 2011-05-08 | 0.13178 | 0.0093514
Unison Networks | 2012 | 2011-05-09 | 0.00093514 | 0.0006005
Unison Networks | 2012 | 2011-05-10 | 0.17247 | 0.0062342
Unison Networks | 2012 | 2011-05-11 | 0.16457 | 0.0097456
Unison Networks | 2012 | 2011-05-12 | 0.029371 | 0.00028421
Unison Networks | 2012 | 2011-05-13 | 0.035205 | 0.00011002
Unison Networks | 2012 | 2011-05-14
Unison Networks | 2012 | 2011-05-15 | 1.0135 | 0.062837
Unison Networks | 2012 | 2011-05-16 | 2.3793 | 0.034861
Unison Networks | 2012 | 2011-05-17 | 0.62486 | 0.011478
Unison Networks | 2012 | 2011-05-18
Unison Networks | 2012 | 2011-05-19 | 0.001091 | 4.584e-06
Unison Networks | 2012 | 2011-05-20 | 0.019381 | 6.4176e-05
Unison Networks | 2012 | 2011-05-21 | 0.030012 | 9.168e-06
Unison Networks | 2012 | 2011-05-22
Unison Networks | 2012 | 2011-05-23
Unison Networks | 2012 | 2011-05-24 | 0.0056017 | 4.584e-05
Unison Networks | 2012 | 2011-05-25 | 0.37624 | 0.010328
Unison Networks | 2012 | 2011-05-26 | 2.0623 | 0.0070364
Unison Networks | 2012 | 2011-05-27 | 0.099427 | 0.00051799
Unison Networks | 2012 | 2011-05-28
Unison Networks | 2012 | 2011-05-29 | 0.0012579 | 5.5008e-05
Unison Networks | 2012 | 2011-05-30 | 0.21705 | 0.0042081
Unison Networks | 2012 | 2011-05-31
Unison Networks | 2012 | 2011-06-01 | 0.038483 | 0.00018336
Unison Networks | 2012 | 2011-06-02
Unison Networks | 2012 | 2011-06-03 | 0.56676 | 0.0040064
Unison Networks | 2012 | 2011-06-04 | 0.49044 | 0.0098923
Unison Networks | 2012 | 2011-06-05 | 0.30127 | 0.0040064
Unison Networks | 2012 | 2011-06-06 | 0.011139 | 0.0006601
Unison Networks | 2012 | 2011-06-07
Unison Networks | 2012 | 2011-06-08 | 0.65526 | 0.002017
Unison Networks | 2012 | 2011-06-09 | 0.67275 | 0.02446
Unison Networks | 2012 | 2011-06-10 | 0.28177 | 0.0034472
Unison Networks | 2012 | 2011-06-11
Unison Networks | 2012 | 2011-06-12 | 0.18079 | 0.0020078
Unison Networks | 2012 | 2011-06-13 | 0.20537 | 0.0012056
Unison Networks | 2012 | 2011-06-14 | 0.37264 | 0.021852
Unison Networks | 2012 | 2011-06-15 | 0.22251 | 0.00078386
Unison Networks | 2012 | 2011-06-16 | 0.15658 | 0.0049828
Unison Networks | 2012 | 2011-06-17 | 0.048778 | 0.0064314
Unison Networks | 2012 | 2011-06-18 | 0.097383 | 0.0039193
Unison Networks | 2012 | 2011-06-19
Unison Networks | 2012 | 2011-06-20
Unison Networks | 2012 | 2011-06-21 | 0.03714 | 0.00010085
Unison Networks | 2012 | 2011-06-22 | 0.079202 | 0.00098098
Unison Networks | 2012 | 2011-06-23 | 1.0801 | 0.011368
Unison Networks | 2012 | 2011-06-24 | 0.092097 | 0.00033922
Unison Networks | 2012 | 2011-06-25
Unison Networks | 2012 | 2011-06-26 | 0.57666 | 0.0020124
Unison Networks | 2012 | 2011-06-27 | 0.0010818 | 1.8336e-05
Unison Networks | 2012 | 2011-06-28 | 0.0020095 | 0.00021086
Unison Networks | 2012 | 2011-06-29 | 0.064312 | 0.0025945
Unison Networks | 2012 | 2011-06-30
Unison Networks | 2012 | 2011-07-01 | 0.32101 | 0.0014531
Unison Networks | 2012 | 2011-07-02
Unison Networks | 2012 | 2011-07-03
Unison Networks | 2012 | 2011-07-04 | 0.026473 | 0.00015127
Unison Networks | 2012 | 2011-07-05
Unison Networks | 2012 | 2011-07-06 | 0.0047179 | 0.0022828
Unison Networks | 2012 | 2011-07-07
Unison Networks | 2012 | 2011-07-08 | 0.14099 | 0.0070456
Unison Networks | 2012 | 2011-07-09 | 0.39888 | 0.0031263
Unison Networks | 2012 | 2011-07-10 | 0.56753 | 0.011804
Unison Networks | 2012 | 2011-07-11 | 0.087962 | 0.0026587
Unison Networks | 2012 | 2011-07-12 | 0.33768 | 0.010378
Unison Networks | 2012 | 2011-07-13 | 0.076294 | 0.0030529
Unison Networks | 2012 | 2011-07-14 | 0.052601 | 0.00038964
Unison Networks | 2012 | 2011-07-15 | 0.97251 | 0.016645
Unison Networks | 2012 | 2011-07-16 | 1.2375 | 0.03085
Unison Networks | 2012 | 2011-07-17
Unison Networks | 2012 | 2011-07-18 | 0.12727 | 0.0016411
Unison Networks | 2012 | 2011-07-19
Unison Networks | 2012 | 2011-07-20 | 0.079189 | 0.00066468
Unison Networks | 2012 | 2011-07-21 | 0.045052 | 0.0007151
Unison Networks | 2012 | 2011-07-22 | 0.7175 | 0.025065
Unison Networks | 2012 | 2011-07-23 | 0.0034655 | 0.00049507
Unison Networks | 2012 | 2011-07-24 | 0.73137 | 0.012427
Unison Networks | 2012 | 2011-07-25 | 0.00087096 | 9.6264e-05
Unison Networks | 2012 | 2011-07-26 | 0.024084 | 0.00016961
Unison Networks | 2012 | 2011-07-27 | 0.0044464 | 0.00011002
Unison Networks | 2012 | 2011-07-28
Unison Networks | 2012 | 2011-07-29 | 0.09003 | 0.00035755
Unison Networks | 2012 | 2011-07-30 | 2.5212e-05 | 1.8336e-05
Unison Networks | 2012 | 2011-07-31 | 0.4361 | 0.0043365
Unison Networks | 2012 | 2011-08-01 | 0.8642 | 0.037653
Unison Networks | 2012 | 2011-08-02 | 0.0017384 | 0.00033005
Unison Networks | 2012 | 2011-08-03
Unison Networks | 2012 | 2011-08-04 | 0.037873 | 0.0003713
Unison Networks | 2012 | 2011-08-05 | 0.22122 | 0.0085629
Unison Networks | 2012 | 2011-08-06
Unison Networks | 2012 | 2011-08-07 | 0.54593 | 0.012629
Unison Networks | 2012 | 2011-08-08 | 0.035411 | 0.00055925
Unison Networks | 2012 | 2011-08-09 | 0.27833 | 0.0018198
Unison Networks | 2012 | 2011-08-10 | 0.14165 | 0.0059134
Unison Networks | 2012 | 2011-08-11 | 0.18539 | 0.0034197
Unison Networks | 2012 | 2011-08-12 | 0.064946 | 0.0014577
Unison Networks | 2012 | 2011-08-13 | 0.041421 | 0.00016502
Unison Networks | 2012 | 2011-08-14
Unison Networks | 2012 | 2011-08-15 | 0.033252 | 0.00028421
Unison Networks | 2012 | 2011-08-16 | 0.00047674 | 4.584e-06
Unison Networks | 2012 | 2011-08-17 | 0.11836 | 0.0082512
Unison Networks | 2012 | 2011-08-18 | 0.34885 | 0.0029429
Unison Networks | 2012 | 2011-08-19
Unison Networks | 2012 | 2011-08-20 | 0.095919 | 0.0022095
Unison Networks | 2012 | 2011-08-21 | 0.099587 | 0.00025212
Unison Networks | 2012 | 2011-08-22 | 0.0044098 | 5.9592e-05
Unison Networks | 2012 | 2011-08-23 | 0.3538 | 0.0012652
Unison Networks | 2012 | 2011-08-24 | 0.021389 | 0.0035801
Unison Networks | 2012 | 2011-08-25 | 0.35758 | 0.0018519
Unison Networks | 2012 | 2011-08-26 | 0.002072 | 9.168e-06
Unison Networks | 2012 | 2011-08-27 | 0.018473 | 0.00067385
Unison Networks | 2012 | 2011-08-28
Unison Networks | 2012 | 2011-08-29 | 0.034815 | 0.0001421
Unison Networks | 2012 | 2011-08-30 | 0.4728 | 0.0028971
Unison Networks | 2012 | 2011-08-31 | 0.022984 | 0.00018794
Unison Networks | 2012 | 2011-09-01 | 0.28724 | 0.0038826
Unison Networks | 2012 | 2011-09-02 | 0.095505 | 0.0036214
Unison Networks | 2012 | 2011-09-03 | 0.0057208 | 3.6672e-05
Unison Networks | 2012 | 2011-09-04
Unison Networks | 2012 | 2011-09-05 | 1.0229 | 0.0076186
Unison Networks | 2012 | 2011-09-06 | 0.00052716 | 2.292e-05
Unison Networks | 2012 | 2011-09-07
Unison Networks | 2012 | 2011-09-08
Unison Networks | 2012 | 2011-09-09
Unison Networks | 2012 | 2011-09-10
Unison Networks | 2012 | 2011-09-11 | 0.0011139 | 4.584e-06
Unison Networks | 2012 | 2011-09-12 | 0.22054 | 0.0041302
Unison Networks | 2012 | 2011-09-13 | 0.14268 | 0.0027871
Unison Networks | 2012 | 2011-09-14 | 0.53475 | 0.011364
Unison Networks | 2012 | 2011-09-15 | 0.031821 | 2.7504e-05
Unison Networks | 2012 | 2011-09-16 | 0.12718 | 0.00048132
Unison Networks | 2012 | 2011-09-17
Unison Networks | 2012 | 2011-09-18
Unison Networks | 2012 | 2011-09-19
Unison Networks | 2012 | 2011-09-20 | 1.6917 | 0.0078341
Unison Networks | 2012 | 2011-09-21 | 0.017868 | 0.00031171
Unison Networks | 2012 | 2011-09-22
Unison Networks | 2012 | 2011-09-23 | 0.009388 | 9.6264e-05
Unison Networks | 2012 | 2011-09-24
Unison Networks | 2012 | 2011-09-25
Unison Networks | 2012 | 2011-09-26
Unison Networks | 2012 | 2011-09-27 | 0.053833 | 0.0010589
Unison Networks | 2012 | 2011-09-28 | 0.024816 | 0.00036672
Unison Networks | 2012 | 2011-09-29 | 0.059065 | 0.00025212
Unison Networks | 2012 | 2011-09-30
Unison Networks | 2012 | 2011-10-01 | 0.026116 | 0.00065093
Unison Networks | 2012 | 2011-10-02
Unison Networks | 2012 | 2011-10-03 | 0.64124 | 0.010002
Unison Networks | 2012 | 2011-10-04 | 0.11912 | 0.00054091
Unison Networks | 2012 | 2011-10-05 | 0.040189 | 0.00023837
Unison Networks | 2012 | 2011-10-06
Unison Networks | 2012 | 2011-10-07 | 0.61567 | 0.014852
Unison Networks | 2012 | 2011-10-08 | 0.14805 | 0.0017786
Unison Networks | 2012 | 2011-10-09
Unison Networks | 2012 | 2011-10-10 | 0.14344 | 0.0012606
Unison Networks | 2012 | 2011-10-11 | 0.084582 | 0.0032042
Unison Networks | 2012 | 2011-10-12 | 0.089718 | 0.00046757
Unison Networks | 2012 | 2011-10-13 | 0.19115 | 0.0036443
Unison Networks | 2012 | 2011-10-14 | 0.25563 | 0.01102
Unison Networks | 2012 | 2011-10-15 | 0.0010354 | 3.6672e-05
Unison Networks | 2012 | 2011-10-16 | 2.0154 | 0.0076369
Unison Networks | 2012 | 2011-10-17 | 0.001682 | 0.00039422
Unison Networks | 2012 | 2011-10-18 | 0.2103 | 0.0015861
Unison Networks | 2012 | 2011-10-19 | 0.10007 | 0.00056842
Unison Networks | 2012 | 2011-10-20 | 0.021471 | 0.00015586
Unison Networks | 2012 | 2011-10-21 | 0.51526 | 0.01366
Unison Networks | 2012 | 2011-10-22
Unison Networks | 2012 | 2011-10-23 | 0.077036 | 0.0017328
Unison Networks | 2012 | 2011-10-24
Unison Networks | 2012 | 2011-10-25 | 0.033486 | 0.0001421
Unison Networks | 2012 | 2011-10-26 | 0.19947 | 0.0015127
Unison Networks | 2012 | 2011-10-27 | 0.25204 | 0.00064634
Unison Networks | 2012 | 2011-10-28 | 0.10634 | 0.00086179
Unison Networks | 2012 | 2011-10-29
Unison Networks | 2012 | 2011-10-30 | 0.6073 | 0.01102
Unison Networks | 2012 | 2011-10-31
Unison Networks | 2012 | 2011-11-01 | 0.080593 | 0.00028879
Unison Networks | 2012 | 2011-11-02 | 0.05785 | 0.001311
Unison Networks | 2012 | 2011-11-03 | 0.58654 | 0.0092184
Unison Networks | 2012 | 2011-11-04 | 0.017893 | 0.0046298
Unison Networks | 2012 | 2011-11-05 | 0.38799 | 0.011579
Unison Networks | 2012 | 2011-11-06 | 0.0081366 | 4.1256e-05
Unison Networks | 2012 | 2011-11-07 | 0.03419 | 0.00032088
Unison Networks | 2012 | 2011-11-08 | 0.016627 | 0.00016961
Unison Networks | 2012 | 2011-11-09 | 0.0042081 | 1.3752e-05
Unison Networks | 2012 | 2011-11-10 | 0.58689 | 0.021737
Unison Networks | 2012 | 2011-11-11 | 0.0089113 | 0.00033005
Unison Networks | 2012 | 2011-11-12 | 1.7321 | 0.074875
Unison Networks | 2012 | 2011-11-13
Unison Networks | 2012 | 2011-11-14 | 2.4746 | 0.042022
Unison Networks | 2012 | 2011-11-15 | 1.8786 | 0.059775
Unison Networks | 2012 | 2011-11-16 | 0.11336 | 0.0048636
Unison Networks | 2012 | 2011-11-17 | 0.010295 | 0.0015952
Unison Networks | 2012 | 2011-11-18 | 3.3072 | 0.029475
Unison Networks | 2012 | 2011-11-19 | 0.3731 | 0.012303
Unison Networks | 2012 | 2011-11-20 | 0.0026266 | 4.584e-06
Unison Networks | 2012 | 2011-11-21 | 1.0321 | 0.021059
Unison Networks | 2012 | 2011-11-22 | 0.71693 | 0.01086
Unison Networks | 2012 | 2011-11-23 | 0.514 | 0.0063763
Unison Networks | 2012 | 2011-11-24 | 0.031965 | 0.0016915
Unison Networks | 2012 | 2011-11-25 | 1.0562 | 0.0089113
Unison Networks | 2012 | 2011-11-26 | 0.80041 | 0.0043181
Unison Networks | 2012 | 2011-11-27 | 0.015288 | 0.0004309
Unison Networks | 2012 | 2011-11-28
Unison Networks | 2012 | 2011-11-29 | 0.16975 | 0.00062342
Unison Networks | 2012 | 2011-11-30
Unison Networks | 2012 | 2011-12-01
Unison Networks | 2012 | 2011-12-02 | 0.047304 | 0.00030254
Unison Networks | 2012 | 2011-12-03 | 0.00020414 | 9.168e-06
Unison Networks | 2012 | 2011-12-04
Unison Networks | 2012 | 2011-12-05 | 0.014037 | 0.0070777
Unison Networks | 2012 | 2011-12-06 | 0.11947 | 0.0011827
Unison Networks | 2012 | 2011-12-07 | 0.14577 | 0.0040752
Unison Networks | 2012 | 2011-12-08 | 0.38093 | 0.016223
Unison Networks | 2012 | 2011-12-09 | 0.060729 | 0.00063259
Unison Networks | 2012 | 2011-12-10
Unison Networks | 2012 | 2011-12-11 | 0.00054091 | 4.584e-06
Unison Networks | 2012 | 2011-12-12 | 0.25959 | 0.0012606
Unison Networks | 2012 | 2011-12-13 | 0.060156 | 0.0018657
Unison Networks | 2012 | 2011-12-14 | 0.082017 | 0.00019253
Unison Networks | 2012 | 2011-12-15 | 0.072985 | 0.00089388
Unison Networks | 2012 | 2011-12-16 | 0.050241 | 0.0015036
Unison Networks | 2012 | 2011-12-17
Unison Networks | 2012 | 2011-12-18 | 0.004668 | 0.00059592
Unison Networks | 2012 | 2011-12-19 | 0.87906 | 0.011579
Unison Networks | 2012 | 2011-12-20 | 0.31572 | 0.0074169
Unison Networks | 2012 | 2011-12-21 | 0.089008 | 0.00092597
Unison Networks | 2012 | 2011-12-22 | 0.019675 | 0.00010543
Unison Networks | 2012 | 2011-12-23 | 0.00048254 | 9.168e-06
Unison Networks | 2012 | 2011-12-24
Unison Networks | 2012 | 2011-12-25
Unison Networks | 2012 | 2011-12-26
Unison Networks | 2012 | 2011-12-27 | 0.40626 | 0.0062984
Unison Networks | 2012 | 2011-12-28 | 0.00039881 | 1.3752e-05
Unison Networks | 2012 | 2011-12-29 | 0.14016 | 0.0025395
Unison Networks | 2012 | 2011-12-30 | 0.15523 | 0.0031584
Unison Networks | 2012 | 2011-12-31
Unison Networks | 2012 | 2012-01-01 | 0.15067 | 0.017268
Unison Networks | 2012 | 2012-01-02 | 0.21613 | 0.004474
Unison Networks | 2012 | 2012-01-03
Unison Networks | 2012 | 2012-01-04
Unison Networks | 2012 | 2012-01-05 | 0.0025166 | 4.1256e-05
Unison Networks | 2012 | 2012-01-06
Unison Networks | 2012 | 2012-01-07 | 0.33721 | 0.013853
Unison Networks | 2012 | 2012-01-08 | 1.7144 | 0.020105
Unison Networks | 2012 | 2012-01-09 | 0.70507 | 0.015705
Unison Networks | 2012 | 2012-01-10 | 0.72462 | 0.0027779
Unison Networks | 2012 | 2012-01-11 | 0.36106 | 0.047935
Unison Networks | 2012 | 2012-01-12 | 0.014536 | 0.00022462
Unison Networks | 2012 | 2012-01-13 | 1.1484 | 0.021251
Unison Networks | 2012 | 2012-01-14 | 0.19566 | 0.005487
Unison Networks | 2012 | 2012-01-15
Unison Networks | 2012 | 2012-01-16 | 0.18325 | 0.001774
Unison Networks | 2012 | 2012-01-17 | 0.32521 | 0.0021453
Unison Networks | 2012 | 2012-01-18 | 0.0070986 | 0.00073802
Unison Networks | 2012 | 2012-01-19 | 0.041118 | 0.0002292
Unison Networks | 2012 | 2012-01-20 | 0.1195 | 0.00049966
Unison Networks | 2012 | 2012-01-21 | 0.070189 | 0.0029521
Unison Networks | 2012 | 2012-01-22 | 0.019913 | 0.00074261
Unison Networks | 2012 | 2012-01-23 | 0.35428 | 0.0089205
Unison Networks | 2012 | 2012-01-24 | 0.13343 | 0.0017419
Unison Networks | 2012 | 2012-01-25 | 0.080463 | 0.00035297
Unison Networks | 2012 | 2012-01-26 | 0.026144 | 0.0025945
Unison Networks | 2012 | 2012-01-27 | 0.33527 | 0.010947
Unison Networks | 2012 | 2012-01-28 | 0.21556 | 0.009278
Unison Networks | 2012 | 2012-01-29 | 0.46705 | 0.077052
Unison Networks | 2012 | 2012-01-30
Unison Networks | 2012 | 2012-01-31 | 0.036681 | 0.00033005
Unison Networks | 2012 | 2012-02-01 | 0.0082145 | 8.2512e-05
Unison Networks | 2012 | 2012-02-02 | 0.0757 | 0.00027962
Unison Networks | 2012 | 2012-02-03 | 0.080669 | 0.00050424
Unison Networks | 2012 | 2012-02-04
Unison Networks | 2012 | 2012-02-05
Unison Networks | 2012 | 2012-02-06
Unison Networks | 2012 | 2012-02-07 | 0.030323 | 0.00016502
Unison Networks | 2012 | 2012-02-08 | 0.29696 | 0.0057667
Unison Networks | 2012 | 2012-02-09 | 0.34252 | 0.004914
Unison Networks | 2012 | 2012-02-10 | 0.53875 | 0.01124
Unison Networks | 2012 | 2012-02-11 | 0.56965 | 0.018657
Unison Networks | 2012 | 2012-02-12 | 0.015532 | 0.00016502
Unison Networks | 2012 | 2012-02-13 | 0.029457 | 0.00051799
Unison Networks | 2012 | 2012-02-14 | 0.014774 | 5.5008e-05
Unison Networks | 2012 | 2012-02-15 | 0.50873 | 0.014311
Unison Networks | 2012 | 2012-02-16 | 0.096855 | 0.00061426
Unison Networks | 2012 | 2012-02-17 | 0.36069 | 0.016796
Unison Networks | 2012 | 2012-02-18 | 0.44584 | 0.0084162
Unison Networks | 2012 | 2012-02-19
Unison Networks | 2012 | 2012-02-20
Unison Networks | 2012 | 2012-02-21 | 0.00014424 | 3.6672e-05
Unison Networks | 2012 | 2012-02-22
Unison Networks | 2012 | 2012-02-23 | 0.29661 | 0.0033876
Unison Networks | 2012 | 2012-02-24 | 0.0047674 | 2.292e-05
Unison Networks | 2012 | 2012-02-25 | 0.49921 | 0.008838
Unison Networks | 2012 | 2012-02-26 | 0.043227 | 0.0003713
Unison Networks | 2012 | 2012-02-27 | 0.098616 | 0.00032546
Unison Networks | 2012 | 2012-02-28 | 0.21902 | 0.0042585
Unison Networks | 2012 | 2012-02-29 | 0.0044164 | 0.0031996
Unison Networks | 2012 | 2012-03-01 | 0.40335 | 0.0097639
Unison Networks | 2012 | 2012-03-02 | 0.039688 | 0.00017878
Unison Networks | 2012 | 2012-03-03 | 3.1131 | 0.062223
Unison Networks | 2012 | 2012-03-04 | 0.31263 | 0.002567
Unison Networks | 2012 | 2012-03-05 | 0.0012468 | 9.168e-06
Unison Networks | 2012 | 2012-03-06 | 0.006303 | 2.292e-05
Unison Networks | 2012 | 2012-03-07 | 0.022159 | 0.00090305
Unison Networks | 2012 | 2012-03-08 | 0.092303 | 0.0014898
Unison Networks | 2012 | 2012-03-09 | 1.1023 | 0.0023424
Unison Networks | 2012 | 2012-03-10
Unison Networks | 2012 | 2012-03-11 | 0.55948 | 0.013193
Unison Networks | 2012 | 2012-03-12 | 0.59063 | 0.0076094
Unison Networks | 2012 | 2012-03-13 | 0.00014257 | 1.3752e-05
Unison Networks | 2012 | 2012-03-14 | 0.068279 | 0.0023928
Unison Networks | 2012 | 2012-03-15 | 0.31273 | 0.00088013
Unison Networks | 2012 | 2012-03-16 | 0.25408 | 0.0060463
Unison Networks | 2012 | 2012-03-17 | 0.1157 | 0.0006601
Unison Networks | 2012 | 2012-03-18 | 0.14023 | 0.0011093
Unison Networks | 2012 | 2012-03-19 | 4.6045 | 0.077479
Unison Networks | 2012 | 2012-03-20 | 5.0044 | 0.081036
Unison Networks | 2012 | 2012-03-21 | 4.6149 | 0.052675
Unison Networks | 2012 | 2012-03-22 | 1.2538 | 0.0041806
Unison Networks | 2012 | 2012-03-23
Unison Networks | 2012 | 2012-03-24 | 0.0062122 | 0.0044373
Unison Networks | 2012 | 2012-03-25
Unison Networks | 2012 | 2012-03-26
Unison Networks | 2012 | 2012-03-27 | 1.1207 | 0.07708
Unison Networks | 2012 | 2012-03-28 | 0.49804 | 0.014586
Unison Networks | 2012 | 2012-03-29 | 0.26439 | 4.584e-06
Unison Networks | 2012 | 2012-03-30 | 0.24437 | 0.0017052
Unison Networks | 2012 | 2012-03-31 | 0.20446 | 0.0012835
Unison Networks | 2013 | 2012-04-01 | 0.070331 | 0.0048469
Unison Networks | 2013 | 2012-04-02 | 0.88623 | 0.021256
Unison Networks | 2013 | 2012-04-03 | 0.10027 | 0.0040703
Unison Networks | 2013 | 2012-04-04 | 1.4917 | 0.013988
Unison Networks | 2013 | 2012-04-05 | 0.064983 | 0.0015943
Unison Networks | 2013 | 2012-04-06 | 0.0051621 | 0.00015075
Unison Networks | 2013 | 2012-04-07
Unison Networks | 2013 | 2012-04-08
Unison Networks | 2013 | 2012-04-09 | 0.2315 | 0.0061031
Unison Networks | 2013 | 2012-04-10 | 0.23631 | 0.009881
Unison Networks | 2013 | 2012-04-11 | 0.061111 | 0.00049337
Unison Networks | 2013 | 2012-04-12 | 0.61261 | 0.0090633
Unison Networks | 2013 | 2012-04-13 | 0.019387 | 9.1364e-05
Unison Networks | 2013 | 2012-04-14
Unison Networks | 2013 | 2012-04-15 | 0.025498 | 0.00045682
Unison Networks | 2013 | 2012-04-16 | 0.29006 | 0.012019
Unison Networks | 2013 | 2012-04-17 | 0.32825 | 0.0013385
Unison Networks | 2013 | 2012-04-18 | 0.065385 | 0.00046139
Unison Networks | 2013 | 2012-04-19 | 0.3815 | 0.0087801
Unison Networks | 2013 | 2012-04-20 | 0.02655 | 0.00063041
Unison Networks | 2013 | 2012-04-21
Unison Networks | 2013 | 2012-04-22
Unison Networks | 2013 | 2012-04-23 | 0.015674 | 0.00021471
Unison Networks | 2013 | 2012-04-24 | 0.77864 | 0.022188
Unison Networks | 2013 | 2012-04-25
Unison Networks | 2013 | 2012-04-26 | 0.53735 | 0.015486
Unison Networks | 2013 | 2012-04-27 | 0.12087 | 0.00328
Unison Networks | 2013 | 2012-04-28
Unison Networks | 2013 | 2012-04-29
Unison Networks | 2013 | 2012-04-30 | 0.1563 | 0.0030607
Unison Networks | 2013 | 2012-05-01 | 0.00031977 | 3.1977e-05
Unison Networks | 2013 | 2012-05-02 | 0.1176 | 0.00056646
Unison Networks | 2013 | 2012-05-03 | 0.29112 | 0.0036728
Unison Networks | 2013 | 2012-05-04 | 0.11867 | 0.0013933
Unison Networks | 2013 | 2012-05-05 | 0.19119 | 0.0020466
Unison Networks | 2013 | 2012-05-06 | 0.0083461 | 0.0001005
Unison Networks | 2013 | 2012-05-07 | 0.14311 | 0.001809
Unison Networks | 2013 | 2012-05-08 | 0.018804 | 0.0025308
Unison Networks | 2013 | 2012-05-09 | 0.16183 | 0.0072543
Unison Networks | 2013 | 2012-05-10
Unison Networks | 2013 | 2012-05-11
Unison Networks | 2013 | 2012-05-12 | 0.1062 | 0.0004888
Unison Networks | 2013 | 2012-05-13 | 0.0012151 | 8.6796e-05
Unison Networks | 2013 | 2012-05-14 | 0.0030698 | 5.4819e-05
Unison Networks | 2013 | 2012-05-15
Unison Networks | 2013 | 2012-05-16 | 0.098902 | 0.00047509
Unison Networks | 2013 | 2012-05-17 | 0.28431 | 0.019876
Unison Networks | 2013 | 2012-05-18 | 0.16781 | 0.0032115
Unison Networks | 2013 | 2012-05-19
Unison Networks | 2013 | 2012-05-20 | 0.0016446 | 2.2841e-05
Unison Networks | 2013 | 2012-05-21 | 0.018186 | 0.00022384
Unison Networks | 2013 | 2012-05-22 | 0.0014207 | 4.5682e-06
Unison Networks | 2013 | 2012-05-23 | 0.0051733 | 0.0031429
Unison Networks | 2013 | 2012-05-24 | 0.43953 | 0.006327
Unison Networks | 2013 | 2012-05-25 | 0.021384 | 0.00017359
Unison Networks | 2013 | 2012-05-26 | 0.1819 | 0.00066696
Unison Networks | 2013 | 2012-05-27 | 0.33891 | 0.0094653
Unison Networks | 2013 | 2012-05-28 | 0.001114 | 9.1364e-06
Unison Networks | 2013 | 2012-05-29 | 0.0031868 | 0.0019917
Unison Networks | 2013 | 2012-05-30 | 0.21207 | 0.0030561
Unison Networks | 2013 | 2012-05-31 | 0.29491 | 0.015683
Unison Networks | 2013 | 2012-06-01
Unison Networks | 2013 | 2012-06-02
Unison Networks | 2013 | 2012-06-03
Unison Networks | 2013 | 2012-06-04
Unison Networks | 2013 | 2012-06-05 | 0.27417 | 0.017053
Unison Networks | 2013 | 2012-06-06 | 0.22474 | 0.0013887
Unison Networks | 2013 | 2012-06-07 | 0.059821 | 0.0008771
Unison Networks | 2013 | 2012-06-08 | 0.093053 | 0.0042576
Unison Networks | 2013 | 2012-06-09
Unison Networks | 2013 | 2012-06-10 | 0.023873 | 0.00011877
Unison Networks | 2013 | 2012-06-11
Unison Networks | 2013 | 2012-06-12
Unison Networks | 2013 | 2012-06-13 | 0.076527 | 0.0042302
Unison Networks | 2013 | 2012-06-14 | 0.16516 | 0.0030561
Unison Networks | 2013 | 2012-06-15 | 0.0026907 | 8.6796e-05
Unison Networks | 2013 | 2012-06-16
Unison Networks | 2013 | 2012-06-17 | 0.0013339 | 4.5682e-06
Unison Networks | 2013 | 2012-06-18 | 0.37563 | 0.010626
Unison Networks | 2013 | 2012-06-19 | 0.078461 | 0.00026496
Unison Networks | 2013 | 2012-06-20 | 0.21992 | 0.0011923
Unison Networks | 2013 | 2012-06-21 | 1.6026 | 0.0076746
Unison Networks | 2013 | 2012-06-22 | 0.28873 | 0.0090451
Unison Networks | 2013 | 2012-06-23 | 0.42015 | 0.0014801
Unison Networks | 2013 | 2012-06-24 | 0.0061123 | 1.3705e-05
Unison Networks | 2013 | 2012-06-25
Unison Networks | 2013 | 2012-06-26 | 0.1086 | 0.0031749
Unison Networks | 2013 | 2012-06-27 | 0.058931 | 0.0026724
Unison Networks | 2013 | 2012-06-28 | 0.046415 | 0.00015532
Unison Networks | 2013 | 2012-06-29 | 0.015093 | 0.0001005
Unison Networks | 2013 | 2012-06-30
Unison Networks | 2013 | 2012-07-01
Unison Networks | 2013 | 2012-07-02 | 0.38919 | 0.0013065
Unison Networks | 2013 | 2012-07-03 | 0.043801 | 0.0010004
Unison Networks | 2013 | 2012-07-04
Unison Networks | 2013 | 2012-07-05 | 0.10562 | 0.0002878
Unison Networks | 2013 | 2012-07-06 | 0.13777 | 0.0069254
Unison Networks | 2013 | 2012-07-07
Unison Networks | 2013 | 2012-07-08 | 0.0017953 | 4.5682e-06
Unison Networks | 2013 | 2012-07-09 | 0.10677 | 0.0012974
Unison Networks | 2013 | 2012-07-10
Unison Networks | 2013 | 2012-07-11 | 0.14462 | 0.0032982
Unison Networks | 2013 | 2012-07-12 | 0.082136 | 0.0023161
Unison Networks | 2013 | 2012-07-13
Unison Networks | 2013 | 2012-07-14
Unison Networks | 2013 | 2012-07-15 | 0.17483 | 0.001809
Unison Networks | 2013 | 2012-07-16 | 0.31855 | 0.0059021
Unison Networks | 2013 | 2012-07-17 | 0.016181 | 0.00010507
Unison Networks | 2013 | 2012-07-18 | 0.37706 | 0.0015304
Unison Networks | 2013 | 2012-07-19 | 0.0014847 | 3.1977e-05
Unison Networks | 2013 | 2012-07-20 | 0.0005025 | 9.1364e-06
Unison Networks | 2013 | 2012-07-21
Unison Networks | 2013 | 2012-07-22 | 0.17222 | 0.00033348
Unison Networks | 2013 | 2012-07-23 | 0.068706 | 0.0010735
Unison Networks | 2013 | 2012-07-24 | 0.35033 | 0.0099678
Unison Networks | 2013 | 2012-07-25 | 0.25437 | 0.0069071
Unison Networks | 2013 | 2012-07-26
Unison Networks | 2013 | 2012-07-27 | 0.45053 | 0.0095339
Unison Networks | 2013 | 2012-07-28
Unison Networks | 2013 | 2012-07-29
Unison Networks | 2013 | 2012-07-30 | 0.58373 | 0.015459
Unison Networks | 2013 | 2012-07-31 | 0.080305 | 0.00036089
Unison Networks | 2013 | 2012-08-01 | 0.10488 | 0.003079
Unison Networks | 2013 | 2012-08-02
Unison Networks | 2013 | 2012-08-03 | 0.010877 | 5.9387e-05
Unison Networks | 2013 | 2012-08-04
Unison Networks | 2013 | 2012-08-05 | 0.19019 | 0.0044768
Unison Networks | 2013 | 2012-08-06 | 0.023973 | 0.0043763
Unison Networks | 2013 | 2012-08-07 | 0.086166 | 0.00042941
Unison Networks | 2013 | 2012-08-08 | 0.29344 | 0.0011146
Unison Networks | 2013 | 2012-08-09 | 0.0364 | 0.00014618
Unison Networks | 2013 | 2012-08-10 | 0.64041 | 0.009712
Unison Networks | 2013 | 2012-08-11 | 0.10843 | 0.00063498
Unison Networks | 2013 | 2012-08-12 | 0.19735 | 0.0031795
Unison Networks | 2013 | 2012-08-13 | 0.18132 | 0.013622
Unison Networks | 2013 | 2012-08-14
Unison Networks | 2013 | 2012-08-15 | 0.1212 | 0.0042576
Unison Networks | 2013 | 2012-08-16 | 0.056311 | 0.0077066
Unison Networks | 2013 | 2012-08-17 | 0.00038373 | 1.3705e-05
Unison Networks | 2013 | 2012-08-18
Unison Networks | 2013 | 2012-08-19 | 0.1493 | 0.0009776
Unison Networks | 2013 | 2012-08-20 | 0.0059356 | 0.0033759
Unison Networks | 2013 | 2012-08-21 | 0.25951 | 0.021224
Unison Networks | 2013 | 2012-08-22 | 0.0084421 | 0.00029237
Unison Networks | 2013 | 2012-08-23 | 1.3465 | 0.023188
Unison Networks | 2013 | 2012-08-24 | 0.033997 | 0.00034718
Unison Networks | 2013 | 2012-08-25
Unison Networks | 2013 | 2012-08-26 | 0.15503 | 0.0015897
Unison Networks | 2013 | 2012-08-27 | 0.01673 | 0.0032023
Unison Networks | 2013 | 2012-08-28
Unison Networks | 2013 | 2012-08-29 | 0.0021105 | 2.7409e-05
Unison Networks | 2013 | 2012-08-30 | 0.09479 | 0.0082319
Unison Networks | 2013 | 2012-08-31 | 0.039926 | 0.00036546
Unison Networks | 2013 | 2012-09-01 | 0.0041114 | 4.5682e-05
Unison Networks | 2013 | 2012-09-02 | 0.0089263 | 5.025e-05
Unison Networks | 2013 | 2012-09-03 | 0.045175 | 0.00014161
Unison Networks | 2013 | 2012-09-04 | 0.069905 | 0.0062356
Unison Networks | 2013 | 2012-09-05 | 0.457 | 0.0053631
Unison Networks | 2013 | 2012-09-06 | 1.9293 | 0.077477
Unison Networks | 2013 | 2012-09-07 | 0.51089 | 0.011028
Unison Networks | 2013 | 2012-09-08 | 0.90977 | 0.0050981
Unison Networks | 2013 | 2012-09-09 | 0.029631 | 0.0057879
Unison Networks | 2013 | 2012-09-10 | 0.38415 | 0.016167
Unison Networks | 2013 | 2012-09-11 | 0.95629 | 0.010639
Unison Networks | 2013 | 2012-09-12
Unison Networks | 2013 | 2012-09-13 | 0.75432 | 0.0089126
Unison Networks | 2013 | 2012-09-14 | 0.13003 | 0.00092278
Unison Networks | 2013 | 2012-09-15 | 0.082142 | 0.0016628
Unison Networks | 2013 | 2012-09-16 | 3.5142 | 0.030433
Unison Networks | 2013 | 2012-09-17 | 0.0014755 | 3.1977e-05
Unison Networks | 2013 | 2012-09-18 | 0.084216 | 0.00078573
Unison Networks | 2013 | 2012-09-19 | 0.006359 | 0.00010964
Unison Networks | 2013 | 2012-09-20 | 0.050104 | 0.00019643
Unison Networks | 2013 | 2012-09-21 | 0.0021927 | 9.1364e-06
Unison Networks | 2013 | 2012-09-22 | 0.21376 | 0.0098582
Unison Networks | 2013 | 2012-09-23 | 0.011101 | 0.00013705
Unison Networks | 2013 | 2012-09-24 | 0.21663 | 0.011096
Unison Networks | 2013 | 2012-09-25 | 0.071754 | 0.0015715
Unison Networks | 2013 | 2012-09-26 | 4.1114e-05 | 4.5682e-06
Unison Networks | 2013 | 2012-09-27 | 0.66133 | 0.0046139
Unison Networks | 2013 | 2012-09-28 | 0.024029 | 0.00089994
Unison Networks | 2013 | 2012-09-29
Unison Networks | 2013 | 2012-09-30 | 0.0088806 | 4.1114e-05
Unison Networks | 2013 | 2012-10-01 | 0.046897 | 0.00022384
Unison Networks | 2013 | 2012-10-02 | 0.21202 | 0.0042393
Unison Networks | 2013 | 2012-10-03 | 0.0057559 | 2.2841e-05
Unison Networks | 2013 | 2012-10-04 | 0.00011421 | 4.5682e-06
Unison Networks | 2013 | 2012-10-05
Unison Networks | 2013 | 2012-10-06 | 0.14125 | 0.0023435
Unison Networks | 2013 | 2012-10-07 | 0.0025486 | 6.3955e-05
Unison Networks | 2013 | 2012-10-08 | 0.12256 | 0.0031703
Unison Networks | 2013 | 2012-10-09 | 0.19085 | 0.0053676
Unison Networks | 2013 | 2012-10-10 | 0.017441 | 0.00010964
Unison Networks | 2013 | 2012-10-11 | 0.044567 | 0.0028506
Unison Networks | 2013 | 2012-10-12
Unison Networks | 2013 | 2012-10-13 | 4.6711 | 0.035906
Unison Networks | 2013 | 2012-10-14 | 0.052147 | 0.0013659
Unison Networks | 2013 | 2012-10-15 | 0.15208 | 0.0054088
Unison Networks | 2013 | 2012-10-16 | 0.090318 | 0.0012471
Unison Networks | 2013 | 2012-10-17 | 0.06899 | 0.0023389
Unison Networks | 2013 | 2012-10-18 | 0.74985 | 0.012343
Unison Networks | 2013 | 2012-10-19 | 0.77833 | 0.0035723
Unison Networks | 2013 | 2012-10-20 | 0.19396 | 0.0084146
Unison Networks | 2013 | 2012-10-21
Unison Networks | 2013 | 2012-10-22 | 0.62803 | 0.016286
Unison Networks | 2013 | 2012-10-23 | 0.0067016 | 7.3091e-05
Unison Networks | 2013 | 2012-10-24 | 0.015322 | 9.1364e-06
Unison Networks | 2013 | 2012-10-25 | 0.16761 | 0.015888
Unison Networks | 2013 | 2012-10-26 | 0.28111 | 0.004856
Unison Networks | 2013 | 2012-10-27 | 0.00054819 | 1.8273e-05
Unison Networks | 2013 | 2012-10-28
Unison Networks | 2013 | 2012-10-29 | 0.0010827 | 3.1977e-05
Unison Networks | 2013 | 2012-10-30 | 0.11083 | 0.0016857
Unison Networks | 2013 | 2012-10-31 | 0.010387 | 0.0012014
Unison Networks | 2013 | 2012-11-01 | 0.013166 | 5.025e-05
Unison Networks | 2013 | 2012-11-02 | 1.5649 | 0.016519
Unison Networks | 2013 | 2012-11-03 | 0.24616 | 0.014824
Unison Networks | 2013 | 2012-11-04 | 0.074463 | 0.00026496
Unison Networks | 2013 | 2012-11-05 | 0.069996 | 0.00045682
Unison Networks | 2013 | 2012-11-06 | 0.097862 | 0.0048012
Unison Networks | 2013 | 2012-11-07 | 0.016436 | 9.5932e-05
Unison Networks | 2013 | 2012-11-08 | 0.013805 | 2.7409e-05
Unison Networks | 2013 | 2012-11-09 | 0.00012791 | 3.1977e-05
Unison Networks | 2013 | 2012-11-10 | 0.0062128 | 4.5682e-05
Unison Networks | 2013 | 2012-11-11
Unison Networks | 2013 | 2012-11-12 | 0.026827 | 0.00037459
Unison Networks | 2013 | 2012-11-13 | 1.2187 | 0.016697
Unison Networks | 2013 | 2012-11-14 | 0.76597 | 0.010187
Unison Networks | 2013 | 2012-11-15 | 0.0051621 | 2.2841e-05
Unison Networks | 2013 | 2012-11-16 | 0.018011 | 0.0031201
Unison Networks | 2013 | 2012-11-17 | 0.001608 | 5.025e-05
Unison Networks | 2013 | 2012-11-18 | 1.5633 | 0.019652
Unison Networks | 2013 | 2012-11-19
Unison Networks | 2013 | 2012-11-20 | 0.010256 | 0.00031064
Unison Networks | 2013 | 2012-11-21 | 0.0303 | 0.00010964
Unison Networks | 2013 | 2012-11-22 | 0.17402 | 0.0018593
Unison Networks | 2013 | 2012-11-23 | 0.011261 | 7.766e-05
Unison Networks | 2013 | 2012-11-24 | 0.0096481 | 2.7409e-05
Unison Networks | 2013 | 2012-11-25
Unison Networks | 2013 | 2012-11-26 | 0.14633 | 0.0069117
Unison Networks | 2013 | 2012-11-27 | 0.082925 | 0.00026039
Unison Networks | 2013 | 2012-11-28 | 0.051246 | 0.0029556
Unison Networks | 2013 | 2012-11-29 | 0.18744 | 0.002814
Unison Networks | 2013 | 2012-11-30 | 0.0084553 | 0.00061671
Unison Networks | 2013 | 2012-12-01 | 0.0083598 | 4.5682e-05
Unison Networks | 2013 | 2012-12-02 | 0.46603 | 0.0079898
Unison Networks | 2013 | 2012-12-03 | 1.114 | 0.017259
Unison Networks | 2013 | 2012-12-04 | 0.073652 | 0.0024394
Unison Networks | 2013 | 2012-12-05 | 0.0070396 | 0.00030607
Unison Networks | 2013 | 2012-12-06 | 2.0752 | 0.044398
Unison Networks | 2013 | 2012-12-07 | 0.32931 | 0.005523
Unison Networks | 2013 | 2012-12-08 | 0.00039287 | 9.1364e-06
Unison Networks | 2013 | 2012-12-09 | 0.17398 | 0.0071675
Unison Networks | 2013 | 2012-12-10 | 0.18278 | 0.00054819
Unison Networks | 2013 | 2012-12-11
Unison Networks | 2013 | 2012-12-12 | 0.047167 | 0.00015075
Unison Networks | 2013 | 2012-12-13
Unison Networks | 2013 | 2012-12-14 | 0.0237 | 0.00013248
Unison Networks | 2013 | 2012-12-15
Unison Networks | 2013 | 2012-12-16 | 0.0012882 | 9.1364e-06
Unison Networks | 2013 | 2012-12-17 | 0.3441 | 0.0055549
Unison Networks | 2013 | 2012-12-18 | 0.20882 | 0.0042941
Unison Networks | 2013 | 2012-12-19 | 1.1884 | 0.073982
Unison Networks | 2013 | 2012-12-20 | 0.43254 | 0.0029054
Unison Networks | 2013 | 2012-12-21 | 0.021489 | 0.000201
Unison Networks | 2013 | 2012-12-22
Unison Networks | 2013 | 2012-12-23 | 0.047236 | 0.0011969
Unison Networks | 2013 | 2012-12-24 | 0.34751 | 0.0064503
Unison Networks | 2013 | 2012-12-25 | 0.91193 | 0.010466
Unison Networks | 2013 | 2012-12-26 | 0.12815 | 0.0045865
Unison Networks | 2013 | 2012-12-27 | 0.40511 | 0.0077477
Unison Networks | 2013 | 2012-12-28 | 0.022841 | 0.00018273
Unison Networks | 2013 | 2012-12-29 | 0.047152 | 0.00016446
Unison Networks | 2013 | 2012-12-30
Unison Networks | 2013 | 2012-12-31 | 0.012323 | 0.00028323
Unison Networks | 2013 | 2013-01-01 | 0.10028 | 0.0045773
Unison Networks | 2013 | 2013-01-02 | 0.0027492 | 5.4819e-05
Unison Networks | 2013 | 2013-01-03 | 0.015035 | 0.00028323
Unison Networks | 2013 | 2013-01-04 | 0.02183 | 0.00026039
Unison Networks | 2013 | 2013-01-05
Unison Networks | 2013 | 2013-01-06
Unison Networks | 2013 | 2013-01-07 | 0.50504 | 0.0057422
Unison Networks | 2013 | 2013-01-08 | 0.0037551 | 1.8273e-05
Unison Networks | 2013 | 2013-01-09
Unison Networks | 2013 | 2013-01-10 | 0.052988 | 0.00075832
Unison Networks | 2013 | 2013-01-11 | 0.15791 | 0.0061488
Unison Networks | 2013 | 2013-01-12
Unison Networks | 2013 | 2013-01-13 | 0.3419 | 0.014107
Unison Networks | 2013 | 2013-01-14 | 0.026706 | 0.00015989
Unison Networks | 2013 | 2013-01-15 | 0.13359 | 0.0018273
Unison Networks | 2013 | 2013-01-16 | 0.0097303 | 0.00032434
Unison Networks | 2013 | 2013-01-17 | 0.14094 | 0.0023252
Unison Networks | 2013 | 2013-01-18 | 0.65622 | 0.014554
Unison Networks | 2013 | 2013-01-19 | 0.28985 | 0.0017451
Unison Networks | 2013 | 2013-01-20 | 0.0049382 | 0.00041571
Unison Networks | 2013 | 2013-01-21
Unison Networks | 2013 | 2013-01-22 | 0.21458 | 0.0080401
Unison Networks | 2013 | 2013-01-23 | 0.0091273 | 0.0001005
Unison Networks | 2013 | 2013-01-24 | 0.027391 | 9.1364e-05
Unison Networks | 2013 | 2013-01-25 | 0.0016857 | 4.5682e-06
Unison Networks | 2013 | 2013-01-26 | 0.029602 | 7.3091e-05
Unison Networks | 2013 | 2013-01-27
Unison Networks | 2013 | 2013-01-28 | 0.066474 | 0.0092917
Unison Networks | 2013 | 2013-01-29 | 0.10077 | 0.0013705
Unison Networks | 2013 | 2013-01-30 | 0.14887 | 0.0018958
Unison Networks | 2013 | 2013-01-31 | 0.10676 | 0.00073091
Unison Networks | 2013 | 2013-02-01 | 0.020283 | 0.00019186
Unison Networks | 2013 | 2013-02-02 | 0.022166 | 0.00019186
Unison Networks | 2013 | 2013-02-03 | 0.020488 | 0.0008908
Unison Networks | 2013 | 2013-02-04 | 0.54114 | 0.0035723
Unison Networks | 2013 | 2013-02-05 | 1.0372 | 0.027423
Unison Networks | 2013 | 2013-02-06 | 0.0026587 | 2.7409e-05
Unison Networks | 2013 | 2013-02-07 | 0.1252 | 0.004253
Unison Networks | 2013 | 2013-02-08 | 0.19528 | 0.0056463
Unison Networks | 2013 | 2013-02-09 | 0.021073 | 9.5932e-05
Unison Networks | 2013 | 2013-02-10
Unison Networks | 2013 | 2013-02-11 | 0.053307 | 0.0015166
Unison Networks | 2013 | 2013-02-12 | 0.14522 | 0.00042028
Unison Networks | 2013 | 2013-02-13 | 0.062154 | 0.0050616
Unison Networks | 2013 | 2013-02-14 | 0.096933 | 0.0019598
Unison Networks | 2013 | 2013-02-15 | 0.034518 | 0.0007903
Unison Networks | 2013 | 2013-02-16 | 0.0097029 | 4.1114e-05
Unison Networks | 2013 | 2013-02-17 | 0.14421 | 0.0050113
Unison Networks | 2013 | 2013-02-18 | 0.038236 | 8.2228e-05
Unison Networks | 2013 | 2013-02-19 | 0.22346 | 0.0021014
Unison Networks | 2013 | 2013-02-20 | 0.0020785 | 5.9387e-05
Unison Networks | 2013 | 2013-02-21 | 0.028158 | 0.00014161
Unison Networks | 2013 | 2013-02-22 | 0.0014984 | 1.8273e-05
Unison Networks | 2013 | 2013-02-23 | 0.025692 | 6.3955e-05
Unison Networks | 2013 | 2013-02-24 | 0.26613 | 0.0033896
Unison Networks | 2013 | 2013-02-25 | 0.14372 | 0.00063955
Unison Networks | 2013 | 2013-02-26 | 0.057559 | 0.00013705
Unison Networks | 2013 | 2013-02-27 | 0.0086796 | 9.1364e-05
Unison Networks | 2013 | 2013-02-28 | 0.0041845 | 1.8273e-05
Unison Networks | 2013 | 2013-03-01 | 0.25214 | 0.012608
Unison Networks | 2013 | 2013-03-02 | 0.085691 | 0.00053448
Unison Networks | 2013 | 2013-03-03 | 0.19488 | 0.0042896
Unison Networks | 2013 | 2013-03-04 | 0.12649 | 0.0025125
Unison Networks | 2013 | 2013-03-05 | 0.060693 | 0.00047053
Unison Networks | 2013 | 2013-03-06 | 0.19848 | 0.0047555
Unison Networks | 2013 | 2013-03-07 | 0.017912 | 7.766e-05
Unison Networks | 2013 | 2013-03-08 | 0.5436 | 0.0099313
Unison Networks | 2013 | 2013-03-09 | 0.36652 | 0.0024714
Unison Networks | 2013 | 2013-03-10
Unison Networks | 2013 | 2013-03-11 | 0.49473 | 0.013965
Unison Networks | 2013 | 2013-03-12 | 0.31401 | 0.00094562
Unison Networks | 2013 | 2013-03-13 | 0.39408 | 0.0015943
Unison Networks | 2013 | 2013-03-14 | 0.16193 | 0.00052534
Unison Networks | 2013 | 2013-03-15
Unison Networks | 2013 | 2013-03-16 | 0.059998 | 0.00073548
Unison Networks | 2013 | 2013-03-17 | 0.033517 | 0.0022567
Unison Networks | 2013 | 2013-03-18 | 0.58582 | 0.015441
Unison Networks | 2013 | 2013-03-19 | 1.8981 | 0.014728
Unison Networks | 2013 | 2013-03-20 | 0.0038738 | 1.8273e-05
Unison Networks | 2013 | 2013-03-21 | 0.018378 | 6.3955e-05
Unison Networks | 2013 | 2013-03-22 | 0.12151 | 0.00091364
Unison Networks | 2013 | 2013-03-23
Unison Networks | 2013 | 2013-03-24 | 0.17917 | 0.00064869
Unison Networks | 2013 | 2013-03-25 | 0.0017999 | 0.00015989
Unison Networks | 2013 | 2013-03-26 | 1.5022 | 0.0045408
Unison Networks | 2013 | 2013-03-27 | 0.016299 | 0.00024212
Unison Networks | 2013 | 2013-03-28 | 0.0099952 | 8.6796e-05
Unison Networks | 2013 | 2013-03-29
Unison Networks | 2013 | 2013-03-30 | 0.6136 | 0.010233
Unison Networks | 2013 | 2013-03-31 | 0.036395 | 0.0017725
Unison Networks | 2014 | 2013-04-01 | 0.027296 | 0.00059992
Unison Networks | 2014 | 2013-04-02 | 0.10794 | 0.0016316
Unison Networks | 2014 | 2013-04-03
Unison Networks | 2014 | 2013-04-04 | 1.6751 | 0.021279
Unison Networks | 2014 | 2013-04-05 | 0.10427 | 0.00054084
Unison Networks | 2014 | 2013-04-06 | 0.29538 | 0.0013635
Unison Networks | 2014 | 2013-04-07
Unison Networks | 2014 | 2013-04-08 | 0.0077171 | 0.00060901
Unison Networks | 2014 | 2013-04-09 | 0.0072068 | 6.8173e-05
Unison Networks | 2014 | 2013-04-10 | 0.026505 | 0.00010908
Unison Networks | 2014 | 2013-04-11 | 0.050602 | 0.00012726
Unison Networks | 2014 | 2013-04-12
Unison Networks | 2014 | 2013-04-13
Unison Networks | 2014 | 2013-04-14
Unison Networks | 2014 | 2013-04-15 | 0.00027269 | 4.5448e-06
Unison Networks | 2014 | 2013-04-16 | 0.41971 | 0.011417
Unison Networks | 2014 | 2013-04-17 | 0.065691 | 0.00035904
Unison Networks | 2014 | 2013-04-18 | 0.058841 | 0.0045857
Unison Networks | 2014 | 2013-04-19 | 0.097187 | 0.00045903
Unison Networks | 2014 | 2013-04-20 | 0.017468 | 4.5448e-05
Unison Networks | 2014 | 2013-04-21 | 0.0014771 | 2.2724e-05
Unison Networks | 2014 | 2013-04-22 | 0.1295 | 0.00054538
Unison Networks | 2014 | 2013-04-23 | 0.0013907 | 9.0897e-06
Unison Networks | 2014 | 2013-04-24 | 0.23946 | 0.0042312
Unison Networks | 2014 | 2013-04-25
Unison Networks | 2014 | 2013-04-26 | 0.4501 | 0.0096441
Unison Networks | 2014 | 2013-04-27 | 0.91192 | 0.024774
Unison Networks | 2014 | 2013-04-28
Unison Networks | 2014 | 2013-04-29 | 0.055306 | 0.00019543
Unison Networks | 2014 | 2013-04-30 | 0.07149 | 0.00024088
Unison Networks | 2014 | 2013-05-01 | 0.13038 | 0.0022861
Unison Networks | 2014 | 2013-05-02 | 0.49156 | 0.003295
Unison Networks | 2014 | 2013-05-03 | 0.019688 | 7.2717e-05
Unison Networks | 2014 | 2013-05-04 | 0.0070218 | 6.8173e-05
Unison Networks | 2014 | 2013-05-05
Unison Networks | 2014 | 2013-05-06 | 0.071569 | 0.0016998
Unison Networks | 2014 | 2013-05-07 | 0.023797 | 0.00012726
Unison Networks | 2014 | 2013-05-08 | 0.22223 | 0.0038813
Unison Networks | 2014 | 2013-05-09 | 0.033635 | 0.0024769
Unison Networks | 2014 | 2013-05-10 | 0.0078262 | 2.7269e-05
Unison Networks | 2014 | 2013-05-11
Unison Networks | 2014 | 2013-05-12 | 0.073671 | 0.00081353
Unison Networks | 2014 | 2013-05-13
Unison Networks | 2014 | 2013-05-14 | 0.0029269 | 3.1814e-05
Unison Networks | 2014 | 2013-05-15
Unison Networks | 2014 | 2013-05-16 | 0.47006 | 0.0020043
Unison Networks | 2014 | 2013-05-17 | 1.6946 | 0.010639
Unison Networks | 2014 | 2013-05-18 | 0.30647 | 0.010326
Unison Networks | 2014 | 2013-05-19 | 0.045771 | 0.00012271
Unison Networks | 2014 | 2013-05-20 | 0.036295 | 0.00029996
Unison Networks | 2014 | 2013-05-21 | 0.13323 | 0.0011998
Unison Networks | 2014 | 2013-05-22
Unison Networks | 2014 | 2013-05-23 | 0.21936 | 0.0020179
Unison Networks | 2014 | 2013-05-24 | 0.28327 | 0.0059765
Unison Networks | 2014 | 2013-05-25 | 0.54183 | 0.0098259
Unison Networks | 2014 | 2013-05-26 | 0.086125 | 0.0011135
Unison Networks | 2014 | 2013-05-27 | 0.50586 | 0.010221
Unison Networks | 2014 | 2013-05-28 | 0.022988 | 8.1807e-05
Unison Networks | 2014 | 2013-05-29 | 0.47075 | 0.0051175
Unison Networks | 2014 | 2013-05-30 | 0.0035995 | 1.8179e-05
Unison Networks | 2014 | 2013-05-31 | 0.20453 | 0.00066355
Unison Networks | 2014 | 2013-06-01 | 0.049861 | 0.00052266
Unison Networks | 2014 | 2013-06-02
Unison Networks | 2014 | 2013-06-03 | 0.16624 | 0.0055265
Unison Networks | 2014 | 2013-06-04 | 0.25714 | 0.0013316
Unison Networks | 2014 | 2013-06-05 | 0.63743 | 0.00654
Unison Networks | 2014 | 2013-06-06 | 0.47427 | 0.0030723
Unison Networks | 2014 | 2013-06-07 | 0.11992 | 0.0044767
Unison Networks | 2014 | 2013-06-08 | 1.1924 | 0.035813
Unison Networks | 2014 | 2013-06-09 | 0.083694 | 0.004963
Unison Networks | 2014 | 2013-06-10 | 0.031578 | 0.00016361
Unison Networks | 2014 | 2013-06-11 | 0.13285 | 0.00064537
Unison Networks | 2014 | 2013-06-12
Unison Networks | 2014 | 2013-06-13 | 0.3046 | 0.00091806
Unison Networks | 2014 | 2013-06-14 | 0.00047721 | 3.1814e-05
Unison Networks | 2014 | 2013-06-15 | 0.01343 | 0.00021815
Unison Networks | 2014 | 2013-06-16 | 0.060098 | 0.0057674
Unison Networks | 2014 | 2013-06-17
Unison Networks | 2014 | 2013-06-18 | 0.052025 | 0.00014998
Unison Networks | 2014 | 2013-06-19
Unison Networks | 2014 | 2013-06-20 | 0.050993 | 0.00069081
Unison Networks | 2014 | 2013-06-21 | 0.2383 | 0.011208
Unison Networks | 2014 | 2013-06-22 | 0.1687 | 0.005781
Unison Networks | 2014 | 2013-06-23 | 0.030532 | 0.00099077
Unison Networks | 2014 | 2013-06-24 | 0.018766 | 3.1814e-05
Unison Networks | 2014 | 2013-06-25
Unison Networks | 2014 | 2013-06-26
Unison Networks | 2014 | 2013-06-27 | 0.0079444 | 0.0003545
Unison Networks | 2014 | 2013-06-28 | 0.025152 | 0.0020815
Unison Networks | 2014 | 2013-06-29
Unison Networks | 2014 | 2013-06-30 | 0.0031996 | 0.00019997
Unison Networks | 2014 | 2013-07-01
Unison Networks | 2014 | 2013-07-02 | 0.020147 | 0.00014543
Unison Networks | 2014 | 2013-07-03 | 0.53129 | 0.014271
Unison Networks | 2014 | 2013-07-04 | 0.015016 | 6.3628e-05
Unison Networks | 2014 | 2013-07-05 | 0.1646 | 0.00087261
Unison Networks | 2014 | 2013-07-06 | 0.12218 | 0.00086806
Unison Networks | 2014 | 2013-07-07 | 0.24726 | 0.0012362
Unison Networks | 2014 | 2013-07-08
Unison Networks | 2014 | 2013-07-09 | 0.0013316 | 1.3635e-05
Unison Networks | 2014 | 2013-07-10 | 0.40993 | 0.0081216
Unison Networks | 2014 | 2013-07-11 | 0.00060446 | 4.5448e-06
Unison Networks | 2014 | 2013-07-12 | 0.086803 | 0.0026496
Unison Networks | 2014 | 2013-07-13
Unison Networks | 2014 | 2013-07-14 | 4.5491 | 0.015039
Unison Networks | 2014 | 2013-07-15 | 0.64731 | 0.012607
Unison Networks | 2014 | 2013-07-16 | 0.3457 | 0.011117
Unison Networks | 2014 | 2013-07-17 | 0.005881 | 2.2724e-05
Unison Networks | 2014 | 2013-07-18 | 0.066655 | 0.00025906
Unison Networks | 2014 | 2013-07-19
Unison Networks | 2014 | 2013-07-20 | 0.0035859 | 1.3635e-05
Unison Networks | 2014 | 2013-07-21 | 0.038056 | 0.00088624
Unison Networks | 2014 | 2013-07-22 | 0.36102 | 0.0038858
Unison Networks | 2014 | 2013-07-23 | 0.16131 | 0.00098168
Unison Networks | 2014 | 2013-07-24 | 0.55102 | 0.0089215
Unison Networks | 2014 | 2013-07-25 | 0.064628 | 0.00028632
Unison Networks | 2014 | 2013-07-26 | 0.19824 | 0.0011589
Unison Networks | 2014 | 2013-07-27 | 4.5946 | 0.030296
Unison Networks | 2014 | 2013-07-28 | 0.029881 | 0.00020452
Unison Networks | 2014 | 2013-07-29 | 0.075958 | 0.00023179
Unison Networks | 2014 | 2013-07-30 | 0.22666 | 0.00057265
Unison Networks | 2014 | 2013-07-31 | 0.39774 | 0.018402
Unison Networks | 2014 | 2013-08-01 | 0.077267 | 0.00034541
Unison Networks | 2014 | 2013-08-02 | 0.38004 | 0.0021815
Unison Networks | 2014 | 2013-08-03
Unison Networks | 2014 | 2013-08-04 | 0.94842 | 0.0081171
Unison Networks | 2014 | 2013-08-05 | 0.068741 | 0.00024997
Unison Networks | 2014 | 2013-08-06 | 0.075358 | 0.00033632
Unison Networks | 2014 | 2013-08-07 | 0.04264 | 0.0003045
Unison Networks | 2014 | 2013-08-08 | 0.054874 | 0.0015271
Unison Networks | 2014 | 2013-08-09 | 0.00070899 | 9.0897e-06
Unison Networks | 2014 | 2013-08-10
Unison Networks | 2014 | 2013-08-11 | 0.00052266 | 4.5448e-06
Unison Networks | 2014 | 2013-08-12 | 0.0053405 | 0.0034041
Unison Networks | 2014 | 2013-08-13 | 0.27198 | 0.0024815
Unison Networks | 2014 | 2013-08-14 | 0.1233 | 0.00049539
Unison Networks | 2014 | 2013-08-15 | 0.02322 | 0.00012271
Unison Networks | 2014 | 2013-08-16 | 0.0082034 | 5.4538e-05
Unison Networks | 2014 | 2013-08-17 | 0.24736 | 0.001827
Unison Networks | 2014 | 2013-08-18 | 0.74616 | 0.012226
Unison Networks | 2014 | 2013-08-19 | 0.037263 | 0.00053629
Unison Networks | 2014 | 2013-08-20 | 0.27479 | 0.0019543
Unison Networks | 2014 | 2013-08-21
Unison Networks | 2014 | 2013-08-22 | 0.039267 | 0.00023633
Unison Networks | 2014 | 2013-08-23 | 0.039961 | 0.00039995
Unison Networks | 2014 | 2013-08-24 | 0.008667 | 2.7269e-05
Unison Networks | 2014 | 2013-08-25 | 0.27892 | 0.0063628
Unison Networks | 2014 | 2013-08-26 | 0.52537 | 0.015089
Unison Networks | 2014 | 2013-08-27 | 0.13646 | 0.00049539
Unison Networks | 2014 | 2013-08-28 | 0.29251 | 0.0060401
Unison Networks | 2014 | 2013-08-29 | 0.031705 | 0.0003954
Unison Networks | 2014 | 2013-08-30 | 0.15526 | 0.0021452
Unison Networks | 2014 | 2013-08-31
Unison Networks | 2014 | 2013-09-01 | 0.045003 | 0.00015452
Unison Networks | 2014 | 2013-09-02 | 0.0053265 | 1.8179e-05
Unison Networks | 2014 | 2013-09-03 | 0.31123 | 0.0013135
Unison Networks | 2014 | 2013-09-04 | 0.012795 | 0.0021906
Unison Networks | 2014 | 2013-09-05 | 1.2413 | 0.026056
Unison Networks | 2014 | 2013-09-06 | 0.0014998 | 6.8173e-05
Unison Networks | 2014 | 2013-09-07 | 0.15527 | 0.00066809
Unison Networks | 2014 | 2013-09-08 | 0.0091306 | 2.7269e-05
Unison Networks | 2014 | 2013-09-09 | 0.091772 | 0.0017179
Unison Networks | 2014 | 2013-09-10 | 2.0055 | 0.0053765
Unison Networks | 2014 | 2013-09-11 | 4.6937 | 0.026024
Unison Networks | 2014 | 2013-09-12 | 1.1278 | 0.032405
Unison Networks | 2014 | 2013-09-13 | 0.07133 | 0.0011726
Unison Networks | 2014 | 2013-09-14
Unison Networks | 2014 | 2013-09-15 | 0.70443 | 0.013262
Unison Networks | 2014 | 2013-09-16
Unison Networks | 2014 | 2013-09-17 | 0.98421 | 0.034918
Unison Networks | 2014 | 2013-09-18 | 0.015234 | 9.0897e-05
Unison Networks | 2014 | 2013-09-19
Unison Networks | 2014 | 2013-09-20
Unison Networks | 2014 | 2013-09-21 | 0.5682 | 0.0076989
Unison Networks | 2014 | 2013-09-22 | 2.8068 | 0.018279
Unison Networks | 2014 | 2013-09-23 | 0.042062 | 0.00037268
Unison Networks | 2014 | 2013-09-24 | 0.44424 | 0.0060083
Unison Networks | 2014 | 2013-09-25 | 0.12773 | 0.0023497
Unison Networks | 2014 | 2013-09-26 | 0.1674 | 0.0057492
Unison Networks | 2014 | 2013-09-27 | 0.00023633 | 4.5448e-06
Unison Networks | 2014 | 2013-09-28 | 0.65268 | 0.019361
Unison Networks | 2014 | 2013-09-29 | 0.18106 | 0.0027224
Unison Networks | 2014 | 2013-09-30
Unison Networks | 2014 | 2013-10-01 | 0.0039176 | 3.6359e-05
Unison Networks | 2014 | 2013-10-02 | 0.019202 | 9.9986e-05
Unison Networks | 2014 | 2013-10-03 | 0.1646 | 0.00067264
Unison Networks | 2014 | 2013-10-04 | 0.12745 | 0.0027405
Unison Networks | 2014 | 2013-10-05 | 0.015713 | 0.0015861
Unison Networks | 2014 | 2013-10-06
Unison Networks | 2014 | 2013-10-07 | 0.04363 | 0.00010908
Unison Networks | 2014 | 2013-10-08 | 0.15089 | 0.0045357
Unison Networks | 2014 | 2013-10-09 | 0.21639 | 0.0034495
Unison Networks | 2014 | 2013-10-10 | 0.16958 | 0.0074853
Unison Networks | 2014 | 2013-10-11 | 0.013089 | 0.00022724
Unison Networks | 2014 | 2013-10-12 | 0.013789 | 0.00011817
Unison Networks | 2014 | 2013-10-13
Unison Networks | 2014 | 2013-10-14 | 1.9334 | 0.00654
Unison Networks | 2014 | 2013-10-15 | 1.1914 | 0.011153
Unison Networks | 2014 | 2013-10-16 | 0.20014 | 0.0074263
Unison Networks | 2014 | 2013-10-17 | 0.31201 | 0.0097169
Unison Networks | 2014 | 2013-10-18 | 0.050698 | 0.00018634
Unison Networks | 2014 | 2013-10-19 | 1.0935 | 0.049698
Unison Networks | 2014 | 2013-10-20 | 0.014593 | 8.6352e-05
Unison Networks | 2014 | 2013-10-21 | 0.0094942 | 0.0036177
Unison Networks | 2014 | 2013-10-22 | 0.68179 | 0.017834
Unison Networks | 2014 | 2013-10-23 | 0.025842 | 0.0042812
Unison Networks | 2014 | 2013-10-24 | 0.044189 | 0.0011862
Unison Networks | 2014 | 2013-10-25 | 0.0041449 | 8.6352e-05
Unison Networks | 2014 | 2013-10-26 | 0.41807 | 0.0043903
Unison Networks | 2014 | 2013-10-27
Unison Networks | 2014 | 2013-10-28
Unison Networks | 2014 | 2013-10-29 | 0.13647 | 0.00094078
Unison Networks | 2014 | 2013-10-30 | 0.33657 | 0.004763
Unison Networks | 2014 | 2013-10-31 | 0.086756 | 0.0019043
Unison Networks | 2014 | 2013-11-01 | 0.49155 | 0.0033041
Unison Networks | 2014 | 2013-11-02 | 0.10647 | 0.0010044
Unison Networks | 2014 | 2013-11-03 | 0.00019997 | 9.0897e-06
Unison Networks | 2014 | 2013-11-04 | 0.14315 | 0.07354
Unison Networks | 2014 | 2013-11-05 | 0.0027951 | 2.2724e-05
Unison Networks | 2014 | 2013-11-06 | 0.25369 | 0.0046812
Unison Networks | 2014 | 2013-11-07 | 0.14025 | 0.00033177
Unison Networks | 2014 | 2013-11-08 | 0.013356 | 0.00024542
Unison Networks | 2014 | 2013-11-09
Unison Networks | 2014 | 2013-11-10 | 0.0020861 | 7.7262e-05
Unison Networks | 2014 | 2013-11-11 | 0.9021 | 0.0082398
Unison Networks | 2014 | 2013-11-12 | 0.092435 | 0.00078626
Unison Networks | 2014 | 2013-11-13 | 0.10564 | 0.01328
Unison Networks | 2014 | 2013-11-14 | 0.10676 | 0.0024588
Unison Networks | 2014 | 2013-11-15 | 0.00059992 | 1.8179e-05
Unison Networks | 2014 | 2013-11-16
Unison Networks | 2014 | 2013-11-17
Unison Networks | 2014 | 2013-11-18 | 0.016546 | 0.00029996
Unison Networks | 2014 | 2013-11-19 | 0.28463 | 0.0027542
Unison Networks | 2014 | 2013-11-20 | 0.013362 | 9.5442e-05
Unison Networks | 2014 | 2013-11-21 | 0.012153 | 0.00012271
Unison Networks | 2014 | 2013-11-22 | 0.065921 | 0.00051357
Unison Networks | 2014 | 2013-11-23 | 0.34495 | 0.010826
Unison Networks | 2014 | 2013-11-24 | 0.0032041 | 1.3635e-05
Unison Networks | 2014 | 2013-11-25 | 0.035717 | 0.0019952
Unison Networks | 2014 | 2013-11-26 | 0.0045367 | 0.0015043
Unison Networks | 2014 | 2013-11-27 | 0.13174 | 0.0059719
Unison Networks | 2014 | 2013-11-28 | 0.2897 | 0.011953
Unison Networks | 2014 | 2013-11-29 | 0.055215 | 0.00036359
Unison Networks | 2014 | 2013-11-30 | 0.44424 | 0.0041903
Unison Networks | 2014 | 2013-12-01 | 0.004563 | 0.00010453
Unison Networks | 2014 | 2013-12-02 | 0.048493 | 0.00025451
Unison Networks | 2014 | 2013-12-03 | 0.46417 | 0.037109
Unison Networks | 2014 | 2013-12-04 | 0.17215 | 0.0008317
Unison Networks | 2014 | 2013-12-05 | 0.69959 | 0.013044
Unison Networks | 2014 | 2013-12-06 | 0.087656 | 0.001927
Unison Networks | 2014 | 2013-12-07 | 0.32303 | 0.0055811
Unison Networks | 2014 | 2013-12-08 | 0.071534 | 0.0014725
Unison Networks | 2014 | 2013-12-09 | 0.041691 | 0.00066355
Unison Networks | 2014 | 2013-12-10 | 0.09985 | 0.0023769
Unison Networks | 2014 | 2013-12-11 | 0.35487 | 0.011644
Unison Networks | 2014 | 2013-12-12 | 0.18216 | 0.0011998
Unison Networks | 2014 | 2013-12-13 | 0.3025 | 0.0052584
Unison Networks | 2014 | 2013-12-14 | 0.5889 | 0.032287
Unison Networks | 2014 | 2013-12-15 | 0.076471 | 0.0042449
Unison Networks | 2014 | 2013-12-16 | 0.60769 | 0.0096532
Unison Networks | 2014 | 2013-12-17 | 0.70625 | 0.018248
Unison Networks | 2014 | 2013-12-18 | 0.69666 | 0.011139
Unison Networks | 2014 | 2013-12-19 | 0.028769 | 0.00064082
Unison Networks | 2014 | 2013-12-20 | 0.88915 | 0.024233
Unison Networks | 2014 | 2013-12-21 | 0.0033626 | 9.0897e-05
Unison Networks | 2014 | 2013-12-22 | 0.35278 | 0.0043267
Unison Networks | 2014 | 2013-12-23
Unison Networks | 2014 | 2013-12-24
Unison Networks | 2014 | 2013-12-25 | 0.21647 | 0.0014725
Unison Networks | 2014 | 2013-12-26 | 0.55106 | 0.012326
Unison Networks | 2014 | 2013-12-27 | 0.1677 | 0.007499
Unison Networks | 2014 | 2013-12-28
Unison Networks | 2014 | 2013-12-29 | 0.004363 | 0.00013635
Unison Networks | 2014 | 2013-12-30 | 0.093698 | 0.0014771
Unison Networks | 2014 | 2013-12-31 | 0.21751 | 0.0064446
Unison Networks | 2014 | 2014-01-01 | 0.055739 | 0.00066809
Unison Networks | 2014 | 2014-01-02
Unison Networks | 2014 | 2014-01-03 | 0.18556 | 0.0019906
Unison Networks | 2014 | 2014-01-04 | 0.104 | 0.0014816
Unison Networks | 2014 | 2014-01-05 | 0.30476 | 0.0064446
Unison Networks | 2014 | 2014-01-06
Unison Networks | 2014 | 2014-01-07 | 0.28415 | 0.0025451
Unison Networks | 2014 | 2014-01-08 | 0.41229 | 0.019279
Unison Networks | 2014 | 2014-01-09 | 0.28792 | 0.0024997
Unison Networks | 2014 | 2014-01-10 | 0.050143 | 0.00035904
Unison Networks | 2014 | 2014-01-11 | 0.13453 | 0.0016816
Unison Networks | 2014 | 2014-01-12 | 0.050408 | 0.003804
Unison Networks | 2014 | 2014-01-13 | 0.20185 | 0.0064764
Unison Networks | 2014 | 2014-01-14 | 0.10947 | 0.00024997
Unison Networks | 2014 | 2014-01-15 | 0.090902 | 0.0017225
Unison Networks | 2014 | 2014-01-16 | 0.4664 | 0.011844
Unison Networks | 2014 | 2014-01-17 | 0.15437 | 0.0090306
Unison Networks | 2014 | 2014-01-18 | 0.00069695 | 2.2724e-05
Unison Networks | 2014 | 2014-01-19 | 0.11874 | 0.0038268
Unison Networks | 2014 | 2014-01-20 | 0.04308 | 0.00032268
Unison Networks | 2014 | 2014-01-21 | 0.17395 | 0.0097714
Unison Networks | 2014 | 2014-01-22 | 0.032677 | 0.00023633
Unison Networks | 2014 | 2014-01-23 | 0.043349 | 0.00017725
Unison Networks | 2014 | 2014-01-24
Unison Networks | 2014 | 2014-01-25
Unison Networks | 2014 | 2014-01-26 | 0.62732 | 0.0086534
Unison Networks | 2014 | 2014-01-27 | 0.021564 | 0.0036859
Unison Networks | 2014 | 2014-01-28 | 0.14186 | 0.00047721
Unison Networks | 2014 | 2014-01-29 | 0.10909 | 0.00042267
Unison Networks | 2014 | 2014-01-30 | 0.075194 | 0.00024997
Unison Networks | 2014 | 2014-01-31 | 0.081618 | 0.001018
Unison Networks | 2014 | 2014-02-01 | 0.95328 | 0.020452
Unison Networks | 2014 | 2014-02-02
Unison Networks | 2014 | 2014-02-03 | 0.19169 | 0.0030905
Unison Networks | 2014 | 2014-02-04 | 0.20615 | 0.0094487
Unison Networks | 2014 | 2014-02-05 | 0.065829 | 0.0040858
Unison Networks | 2014 | 2014-02-06
Unison Networks | 2014 | 2014-02-07 | 0.39403 | 0.0056629
Unison Networks | 2014 | 2014-02-08 | 0.52081 | 0.013357
Unison Networks | 2014 | 2014-02-09 | 0.011516 | 0.00014089
Unison Networks | 2014 | 2014-02-10 | 0.031712 | 0.011012
Unison Networks | 2014 | 2014-02-11 | 0.12967 | 0.00049084
Unison Networks | 2014 | 2014-02-12 | 0.051334 | 0.00019088
Unison Networks | 2014 | 2014-02-13 | 0.42017 | 0.020015
Unison Networks | 2014 | 2014-02-14 | 0.085763 | 0.0014543
Unison Networks | 2014 | 2014-02-15 | 0.04515 | 0.0018997
Unison Networks | 2014 | 2014-02-16 | 0.0093946 | 6.3628e-05
Unison Networks | 2014 | 2014-02-17 | 0.12009 | 0.0074944
Unison Networks | 2014 | 2014-02-18 | 0.11705 | 0.00095442
Unison Networks | 2014 | 2014-02-19 | 0.0062537 | 1.8179e-05
Unison Networks | 2014 | 2014-02-20 | 0.046098 | 0.00012726
Unison Networks | 2014 | 2014-02-21 | 0.16571 | 0.00066809
Unison Networks | 2014 | 2014-02-22 | 0.13416 | 0.00060901
Unison Networks | 2014 | 2014-02-23 | 0.12496 | 0.0042721
Unison Networks | 2014 | 2014-02-24 | 0.041838 | 0.020147
Unison Networks | 2014 | 2014-02-25 | 0.021837 | 0.0033132
Unison Networks | 2014 | 2014-02-26 | 0.047057 | 4.5448e-06
Unison Networks | 2014 | 2014-02-27
Unison Networks | 2014 | 2014-02-28 | 0.062622 | 0.020261
Unison Networks | 2014 | 2014-03-01 | 0.047393 | 0.0045903
Unison Networks | 2014 | 2014-03-02 | 0.22384 | 0.00079989
Unison Networks | 2014 | 2014-03-03 | 1.439 | 0.027687
Unison Networks | 2014 | 2014-03-04 | 0.0024269 | 2.2724e-05
Unison Networks | 2014 | 2014-03-05 | 0.074968 | 0.0025497
Unison Networks | 2014 | 2014-03-06 | 0.01223 | 3.1814e-05
Unison Networks | 2014 | 2014-03-07 | 0.0051675 | 1.3635e-05
Unison Networks | 2014 | 2014-03-08 | 0.015289 | 0.0002636
Unison Networks | 2014 | 2014-03-09 | 0.80323 | 0.0024088
Unison Networks | 2014 | 2014-03-10 | 0.34589 | 0.0086625
Unison Networks | 2014 | 2014-03-11 | 0.062434 | 0.001877
Unison Networks | 2014 | 2014-03-12 | 0.009076 | 0.00010453
Unison Networks | 2014 | 2014-03-13 | 0.19995 | 0.002586
Unison Networks | 2014 | 2014-03-14 | 0.0056856 | 0.0002227
Unison Networks | 2014 | 2014-03-15 | 3.7224 | 0.01318
Unison Networks | 2014 | 2014-03-16 | 2.4384 | 0.018525
Unison Networks | 2014 | 2014-03-17 | 0.0028087 | 9.0897e-06
Unison Networks | 2014 | 2014-03-18 | 0.11544 | 0.0065809
Unison Networks | 2014 | 2014-03-19 | 0.0023815 | 3.1814e-05
Unison Networks | 2014 | 2014-03-20 | 0.10114 | 0.0015316
Unison Networks | 2014 | 2014-03-21 | 0.22945 | 0.0018907
Unison Networks | 2014 | 2014-03-22 | 0.39147 | 0.0073581
Unison Networks | 2014 | 2014-03-23
Unison Networks | 2014 | 2014-03-24 | 0.26249 | 0.0074808
Unison Networks | 2014 | 2014-03-25 | 0.55512 | 0.0017861
Unison Networks | 2014 | 2014-03-26 | 0.10666 | 0.00065446
Unison Networks | 2014 | 2014-03-27 | 0.43247 | 0.0087079
Unison Networks | 2014 | 2014-03-28 | 0.36153 | 0.0053947
Unison Networks | 2014 | 2014-03-29 | 0.0051038 | 0.00019543
Unison Networks | 2014 | 2014-03-30
Unison Networks | 2014 | 2014-03-31
Vector Lines | 2005 | 2004-04-01 | 0.17353 | 0.0021608
Vector Lines | 2005 | 2004-04-02 | 0.1713 | 0.0034172
Vector Lines | 2005 | 2004-04-03 | 0.34179 | 0.0027829
Vector Lines | 2005 | 2004-04-04 | 0.41939 | 0.0066388
Vector Lines | 2005 | 2004-04-05 | 0.001016 | 9.208e-06
Vector Lines | 2005 | 2004-04-06 | 0.48149 | 0.0052139
Vector Lines | 2005 | 2004-04-07 | 0.11286 | 0.0010316
Vector Lines | 2005 | 2004-04-08 | 0.5872 | 0.0073014
Vector Lines | 2005 | 2004-04-09 | 0.088257 | 0.0016523
Vector Lines | 2005 | 2004-04-10 | 0.004641 | 4.9903e-05
Vector Lines | 2005 | 2004-04-11 | 0.056482 | 0.00065889
Vector Lines | 2005 | 2004-04-12
Vector Lines | 2005 | 2004-04-13
Vector Lines | 2005 | 2004-04-14 | 0.27814 | 0.0092932
Vector Lines | 2005 | 2004-04-15 | 0.43855 | 0.0113
Vector Lines | 2005 | 2004-04-16 | 0.19713 | 0.0039042
Vector Lines | 2005 | 2004-04-17 | 0.31208 | 0.00080315
Vector Lines | 2005 | 2004-04-18 | 0.002124 | 1.2277e-05
Vector Lines | 2005 | 2004-04-19 | 0.48458 | 0.0076304
Vector Lines | 2005 | 2004-04-20 | 0.36953 | 0.026526
Vector Lines | 2005 | 2004-04-21 | 0.061141 | 0.00057869
Vector Lines | 2005 | 2004-04-22 | 0.0067055 | 0.00012073
Vector Lines | 2005 | 2004-04-23 | 0.00042766 | 2.0462e-06
Vector Lines | 2005 | 2004-04-24 | 0.20461 | 0.0027271
Vector Lines | 2005 | 2004-04-25 | 0.21099 | 0.0031492
Vector Lines | 2005 | 2004-04-26 | 0.21934 | 0.0021459
Vector Lines | 2005 | 2004-04-27 | 0.054561 | 0.00044096
Vector Lines | 2005 | 2004-04-28 | 0.30653 | 0.0065554
Vector Lines | 2005 | 2004-04-29 | 0.20352 | 0.0038551
Vector Lines | 2005 | 2004-04-30 | 0.66959 | 0.017984
Vector Lines | 2005 | 2004-05-01 | 0.14198 | 0.0011101
Vector Lines | 2005 | 2004-05-02 | 0.30861 | 0.0092428
Vector Lines | 2005 | 2004-05-03 | 0.23385 | 0.0033221
Vector Lines | 2005 | 2004-05-04 | 0.63692 | 0.0081322
Vector Lines | 2005 | 2004-05-05 | 0.045514 | 0.00047895
Vector Lines | 2005 | 2004-05-06 | 0.01195 | 0.00014937
Vector Lines | 2005 | 2004-05-07 | 0.24796 | 0.0018948
Vector Lines | 2005 | 2004-05-08 | 0.080233 | 0.0019425
Vector Lines | 2005 | 2004-05-09 | 0.20461 | 0.0018273
Vector Lines | 2005 | 2004-05-10
Vector Lines | 2005 | 2004-05-11 | 0.24394 | 0.0029834
Vector Lines | 2005 | 2004-05-12 | 1.0437 | 0.013321
Vector Lines | 2005 | 2004-05-13 | 0.27567 | 0.0018713
Vector Lines | 2005 | 2004-05-14 | 0.00027624 | 2.0462e-06
Vector Lines | 2005 | 2004-05-15 | 0.11392 | 0.0013526
Vector Lines | 2005 | 2004-05-16 | 0.01379 | 7.0595e-05
Vector Lines | 2005 | 2004-05-17 | 0.22192 | 0.0082668
Vector Lines | 2005 | 2004-05-18 | 0.0092766 | 0.00034786
Vector Lines | 2005 | 2004-05-19 | 0.0045181 | 2.4555e-05
Vector Lines | 2005 | 2004-05-20 | 0.098696 | 0.0039852
Vector Lines | 2005 | 2004-05-21 | 0.13499 | 0.0019796
Vector Lines | 2005 | 2004-05-22 | 0.59014 | 0.0030042
Vector Lines | 2005 | 2004-05-23 | 0.23021 | 0.0018621
Vector Lines | 2005 | 2004-05-24 | 0.48648 | 0.0044637
Vector Lines | 2005 | 2004-05-25 | 0.33184 | 0.0058508
Vector Lines | 2005 | 2004-05-26 | 0.26406 | 0.010792
Vector Lines | 2005 | 2004-05-27 | 0.27609 | 0.0041037
Vector Lines | 2005 | 2004-05-28 | 3.3736 | 0.038927
Vector Lines | 2005 | 2004-05-29 | 2.0679 | 0.013727
Vector Lines | 2005 | 2004-05-30 | 0.53456 | 0.0054446
Vector Lines | 2005 | 2004-05-31 | 0.26553 | 0.0092827
Vector Lines | 2005 | 2004-06-01 | 0.096283 | 0.0021883
Vector Lines | 2005 | 2004-06-02 | 0.04963 | 0.00026192
Vector Lines | 2005 | 2004-06-03 | 0.12343 | 0.0018296
Vector Lines | 2005 | 2004-06-04 | 0.42312 | 0.0052366
Vector Lines | 2005 | 2004-06-05 | 0.01976 | 0.00053407
Vector Lines | 2005 | 2004-06-06 | 0.34381 | 0.0054246
Vector Lines | 2005 | 2004-06-07 | 0.060141 | 0.0060262
Vector Lines | 2005 | 2004-06-08 | 0.037982 | 0.00066103
Vector Lines | 2005 | 2004-06-09 | 0.13779 | 0.0024729
Vector Lines | 2005 | 2004-06-10 | 0.44295 | 0.0041702
Vector Lines | 2005 | 2004-06-11 | 0.22854 | 0.0025394
Vector Lines | 2005 | 2004-06-12 | 0.17424 | 0.0021936
Vector Lines | 2005 | 2004-06-13 | 0.060611 | 0.0031901
Vector Lines | 2005 | 2004-06-14 | 0.15645 | 0.0018651
Vector Lines | 2005 | 2004-06-15 | 0.01045 | 0.0016349
Vector Lines | 2005 | 2004-06-16 | 0.0016411 | 6.1387e-06
Vector Lines | 2005 | 2004-06-17 | 0.59482 | 0.0026008
Vector Lines | 2005 | 2004-06-18 | 1.3542 | 0.0059494
Vector Lines | 2005 | 2004-06-19 | 0.071496 | 0.0012236
Vector Lines | 2005 | 2004-06-20 | 0.70264 | 0.011131
Vector Lines | 2005 | 2004-06-21 | 0.057675 | 0.0010088
Vector Lines | 2005 | 2004-06-22 | 1.6575 | 0.029059
Vector Lines | 2005 | 2004-06-23 | 0.26166 | 0.0044168
Vector Lines | 2005 | 2004-06-24 | 0.026059 | 0.0030509
Vector Lines | 2005 | 2004-06-25 | 0.011416 | 0.00018211
Vector Lines | 2005 | 2004-06-26 | 0.30563 | 0.0030857
Vector Lines | 2005 | 2004-06-27 | 0.48173 | 0.0083409
Vector Lines | 2005 | 2004-06-28 | 0.11606 | 0.0026086
Vector Lines | 2005 | 2004-06-29 | 0.26911 | 0.0038014
Vector Lines | 2005 | 2004-06-30 | 2.5664 | 0.038999
Vector Lines | 2005 | 2004-07-01 | 0.51015 | 0.0057049
Vector Lines | 2005 | 2004-07-02 | 1.2935 | 0.023925
Vector Lines | 2005 | 2004-07-03 | 1.1266 | 0.005569
Vector Lines | 2005 | 2004-07-04 | 0.30242 | 0.0041968
Vector Lines | 2005 | 2004-07-05 | 0.25966 | 0.0039646
Vector Lines | 2005 | 2004-07-06 | 0.081557 | 0.00019542
Vector Lines | 2005 | 2004-07-07 | 0.022568 | 0.00021527
Vector Lines | 2005 | 2004-07-08 | 0.0047319 | 2.967e-05
Vector Lines | 2005 | 2004-07-09 | 0.12475 | 0.0019091
Vector Lines | 2005 | 2004-07-10
Vector Lines | 2005 | 2004-07-11 | 0.066936 | 0.00076529
Vector Lines | 2005 | 2004-07-12 | 0.051544 | 0.00074278
Vector Lines | 2005 | 2004-07-13 | 0.55364 | 0.010705
Vector Lines | 2005 | 2004-07-14 | 0.013996 | 5.8318e-05
Vector Lines | 2005 | 2004-07-15 | 0.25682 | 0.004108
Vector Lines | 2005 | 2004-07-16 | 0.51446 | 0.0056823
Vector Lines | 2005 | 2004-07-17 | 0.28466 | 0.0036192
Vector Lines | 2005 | 2004-07-18 | 0.13537 | 0.0016462
Vector Lines | 2005 | 2004-07-19 | 0.064917 | 0.0025783
Vector Lines | 2005 | 2004-07-20 | 0.37859 | 0.005177
Vector Lines | 2005 | 2004-07-21 | 0.066963 | 0.0004338
Vector Lines | 2005 | 2004-07-22 | 0.13065 | 0.0089386
Vector Lines | 2005 | 2004-07-23 | 0.024225 | 0.00012277
Vector Lines | 2005 | 2004-07-24
Vector Lines | 2005 | 2004-07-25 | 0.11422 | 0.0020544
Vector Lines | 2005 | 2004-07-26 | 0.13646 | 0.00094945
Vector Lines | 2005 | 2004-07-27 | 0.029687 | 0.00095764
Vector Lines | 2005 | 2004-07-28 | 0.0097288 | 6.3433e-05
Vector Lines | 2005 | 2004-07-29 | 0.10632 | 0.00061694
Vector Lines | 2005 | 2004-07-30 | 0.2947 | 0.0052036
Vector Lines | 2005 | 2004-07-31 | 0.029865 | 0.00041539
Vector Lines | 2005 | 2004-08-01
Vector Lines | 2005 | 2004-08-02
Vector Lines | 2005 | 2004-08-03 | 0.0054839 | 2.967e-05
Vector Lines | 2005 | 2004-08-04 | 0.23489 | 0.018553
Vector Lines | 2005 | 2004-08-05 | 0.3838 | 0.0089359
Vector Lines | 2005 | 2004-08-06 | 0.49547 | 0.0020544
Vector Lines | 2005 | 2004-08-07 | 0.38532 | 0.0041282
Vector Lines | 2005 | 2004-08-08 | 0.20779 | 0.0080233
Vector Lines | 2005 | 2004-08-09 | 0.62479 | 0.0071142
Vector Lines | 2005 | 2004-08-10 | 0.080012 | 0.0044444
Vector Lines | 2005 | 2004-08-11 | 0.32836 | 0.0023296
Vector Lines | 2005 | 2004-08-12 | 0.02124 | 6.1387e-05
Vector Lines | 2005 | 2004-08-13 | 0.34994 | 0.0043016
Vector Lines | 2005 | 2004-08-14 | 0.003673 | 9.6173e-05
Vector Lines | 2005 | 2004-08-15 | 0.00010333 | 1.0231e-06
Vector Lines | 2005 | 2004-08-16 | 0.073112 | 0.0010477
Vector Lines | 2005 | 2004-08-17 | 0.0063106 | 3.6832e-05
Vector Lines | 2005 | 2004-08-18 | 0.32492 | 0.0043928
Vector Lines | 2005 | 2004-08-19 | 0.31262 | 0.0039462
Vector Lines | 2005 | 2004-08-20 | 0.17811 | 0.0027016
Vector Lines | 2005 | 2004-08-21 | 1.1099 | 0.0093338
Vector Lines | 2005 | 2004-08-22 | 0.00039697 | 2.0462e-06
Vector Lines | 2005 | 2004-08-23 | 0.35943 | 0.0049748
Vector Lines | 2005 | 2004-08-24 | 0.0024555 | 2.4555e-05
Vector Lines | 2005 | 2004-08-25 | 0.044306 | 0.00037139
Vector Lines | 2005 | 2004-08-26 | 0.16079 | 0.0021219
Vector Lines | 2005 | 2004-08-27 | 0.23654 | 0.0051043
Vector Lines | 2005 | 2004-08-28 | 0.0011479 | 6.1387e-06
Vector Lines | 2005 | 2004-08-29 | 0.049904 | 0.00037241
Vector Lines | 2005 | 2004-08-30 | 0.11534 | 0.0024146
Vector Lines | 2005 | 2004-08-31 | 0.10033 | 0.00097298
Vector Lines | 2005 | 2004-09-01 | 0.060634 | 0.0012155
Vector Lines | 2005 | 2004-09-02 | 0.032944 | 0.00018621
Vector Lines | 2005 | 2004-09-03 | 0.18755 | 0.0026049
Vector Lines | 2005 | 2004-09-04 | 0.31867 | 0.0056824
Vector Lines | 2005 | 2004-09-05 | 0.00056783 | 1.0231e-06
Vector Lines | 2005 | 2004-09-06 | 0.00094945 | 8.1849e-06
Vector Lines | 2005 | 2004-09-07 | 0.0089298 | 0.0011653
Vector Lines | 2005 | 2004-09-08 | 0.006727 | 4.1948e-05
Vector Lines | 2005 | 2004-09-09 | 0.17856 | 0.0017096
Vector Lines | 2005 | 2004-09-10 | 0.10151 | 0.0035103
Vector Lines | 2005 | 2004-09-11 | 0.2503 | 0.0095129
Vector Lines | 2005 | 2004-09-12 | 0.039371 | 0.00022713
Vector Lines | 2005 | 2004-09-13 | 0.11032 | 0.0024493
Vector Lines | 2005 | 2004-09-14 | 0.14853 | 0.0026335
Vector Lines | 2005 | 2004-09-15 | 0.21764 | 0.0028881
Vector Lines | 2005 | 2004-09-16 | 0.32437 | 0.0017485
Vector Lines | 2005 | 2004-09-17
Vector Lines | 2005 | 2004-09-18 | 0.056432 | 0.0019316
Vector Lines | 2005 | 2004-09-19
Vector Lines | 2005 | 2004-09-20 | 0.0029057 | 1.0231e-05
Vector Lines | 2005 | 2004-09-21 | 0.22249 | 0.0022905
Vector Lines | 2005 | 2004-09-22 | 0.23172 | 0.0060332
Vector Lines | 2005 | 2004-09-23 | 0.048618 | 0.00023736
Vector Lines | 2005 | 2004-09-24 | 0.13908 | 0.0026601
Vector Lines | 2005 | 2004-09-25 | 0.1184 | 0.00040618
Vector Lines | 2005 | 2004-09-26 | 0.0052916 | 3.0693e-05
Vector Lines | 2005 | 2004-09-27 | 0.1588 | 0.0037951
Vector Lines | 2005 | 2004-09-28 | 0.78832 | 0.012992
Vector Lines | 2005 | 2004-09-29 | 0.20231 | 0.0020585
Vector Lines | 2005 | 2004-09-30 | 0.02026 | 0.00057192
Vector Lines | 2005 | 2004-10-01 | 0.21525 | 0.00063331
Vector Lines | 2005 | 2004-10-02 | 0.25704 | 0.0057714
Vector Lines | 2005 | 2004-10-03
Vector Lines | 2005 | 2004-10-04 | 0.37895 | 0.010935
Vector Lines | 2005 | 2004-10-05 | 0.27742 | 0.0057803
Vector Lines | 2005 | 2004-10-06 | 0.19365 | 0.0027205
Vector Lines | 2005 | 2004-10-07 | 0.055375 | 0.00023839
Vector Lines | 2005 | 2004-10-08 | 0.038873 | 0.00034274
Vector Lines | 2005 | 2004-10-09 | 0.081144 | 0.00036849
Vector Lines | 2005 | 2004-10-10
Vector Lines | 2005 | 2004-10-11 | 0.00017393 | 2.0462e-06
Vector Lines | 2005 | 2004-10-12 | 0.22493 | 0.0038571
Vector Lines | 2005 | 2004-10-13 | 0.00024555 | 1.0231e-06
Vector Lines | 2005 | 2004-10-14 | 0.026137 | 0.0004338
Vector Lines | 2005 | 2004-10-15 | 0.050667 | 0.00087783
Vector Lines | 2005 | 2004-10-16 | 0.89738 | 0.019455
Vector Lines | 2005 | 2004-10-17 | 0.42392 | 0.0064078
Vector Lines | 2005 | 2004-10-18 | 1.2822 | 0.019021
Vector Lines | 2005 | 2004-10-19 | 0.015493 | 0.0021475
Vector Lines | 2005 | 2004-10-20 | 0.7772 | 0.020265
Vector Lines | 2005 | 2004-10-21 | 0.11441 | 0.0027911
Vector Lines | 2005 | 2004-10-22
Vector Lines | 2005 | 2004-10-23 | 0.023999 | 0.00033753
Vector Lines | 2005 | 2004-10-24
Vector Lines | 2005 | 2004-10-25 | 0.4789 | 0.0060712
Vector Lines | 2005 | 2004-10-26 | 0.267 | 0.0045695
Vector Lines | 2005 | 2004-10-27 | 0.11083 | 0.0038367
Vector Lines | 2005 | 2004-10-28 | 0.011443 | 0.00012482
Vector Lines | 2005 | 2004-10-29 | 0.22999 | 0.0016288
Vector Lines | 2005 | 2004-10-30 | 0.0024112 | 6.6977e-05
Vector Lines | 2005 | 2004-10-31 | 0.32742 | 0.0046913
Vector Lines | 2005 | 2004-11-01 | 0.047978 | 0.00057295
Vector Lines | 2005 | 2004-11-02 | 0.038313 | 0.00032433
Vector Lines | 2005 | 2004-11-03 | 0.1329 | 0.0021327
Vector Lines | 2005 | 2004-11-04
Vector Lines | 2005 | 2004-11-05 | 0.0036464 | 3.6832e-05
Vector Lines | 2005 | 2004-11-06 | 0.27173 | 0.0031485
Vector Lines | 2005 | 2004-11-07
Vector Lines | 2005 | 2004-11-08 | 0.044792 | 0.0004737
Vector Lines | 2005 | 2004-11-09 | 0.02649 | 0.00037373
Vector Lines | 2005 | 2004-11-10
Vector Lines | 2005 | 2004-11-11 | 0.74076 | 0.013573
Vector Lines | 2005 | 2004-11-12 | 0.023086 | 0.0023051
Vector Lines | 2005 | 2004-11-13 | 0.099952 | 0.00085533
Vector Lines | 2005 | 2004-11-14 | 1.3041 | 0.015508
Vector Lines | 2005 | 2004-11-15 | 0.60087 | 0.0047664
Vector Lines | 2005 | 2004-11-16 | 0.22123 | 0.0028289
Vector Lines | 2005 | 2004-11-17 | 0.00096991 | 6.1387e-06
Vector Lines | 2005 | 2004-11-18 | 0.46876 | 0.0044751
Vector Lines | 2005 | 2004-11-19
Vector Lines | 2005 | 2004-11-20 | 0.82335 | 0.0021035
Vector Lines | 2005 | 2004-11-21 | 0.00091467 | 6.1387e-06
Vector Lines | 2005 | 2004-11-22 | 0.14626 | 0.0023874
Vector Lines | 2005 | 2004-11-23 | 0.34939 | 0.0061561
Vector Lines | 2005 | 2004-11-24 | 0.40862 | 0.0046235
Vector Lines | 2005 | 2004-11-25 | 0.061224 | 0.00092592
Vector Lines | 2005 | 2004-11-26 | 2.1486 | 0.024495
Vector Lines | 2005 | 2004-11-27 | 0.22466 | 0.0038142
Vector Lines | 2005 | 2004-11-28 | 0.15868 | 0.0014856
Vector Lines | 2005 | 2004-11-29 | 0.10117 | 0.0013362
Vector Lines | 2005 | 2004-11-30 | 0.0084898 | 5.1156e-05
Vector Lines | 2005 | 2004-12-01 | 0.065258 | 0.00096991
Vector Lines | 2005 | 2004-12-02 | 0.20144 | 0.00407
Vector Lines | 2005 | 2004-12-03 | 0.26213 | 0.004117
Vector Lines | 2005 | 2004-12-04 | 0.85316 | 0.0081993
Vector Lines | 2005 | 2004-12-05 | 0.79481 | 0.014624
Vector Lines | 2005 | 2004-12-06 | 0.38531 | 0.0086368
Vector Lines | 2005 | 2004-12-07 | 0.022367 | 0.0022764
Vector Lines | 2005 | 2004-12-08 | 0.45708 | 0.006649
Vector Lines | 2005 | 2004-12-09 | 0.15927 | 0.00312
Vector Lines | 2005 | 2004-12-10 | 0.11795 | 0.0054409
Vector Lines | 2005 | 2004-12-11 | 0.4644 | 0.0052913
Vector Lines | 2005 | 2004-12-12 | 0.4137 | 0.0022785
Vector Lines | 2005 | 2004-12-13 | 0.13723 | 0.0014958
Vector Lines | 2005 | 2004-12-14 | 0.040228 | 0.00013812
Vector Lines | 2005 | 2004-12-15 | 1.3144 | 0.012461
Vector Lines | 2005 | 2004-12-16 | 0.9861 | 0.0052552
Vector Lines | 2005 | 2004-12-17 | 0.27861 | 0.0031328
Vector Lines | 2005 | 2004-12-18 | 1.8085 | 0.015093
Vector Lines | 2005 | 2004-12-19 | 0.64315 | 0.012217
Vector Lines | 2005 | 2004-12-20 | 0.41585 | 0.0067235
Vector Lines | 2005 | 2004-12-21 | 0.19899 | 0.0013052
Vector Lines | 2005 | 2004-12-22 | 0.30165 | 0.0043672
Vector Lines | 2005 | 2004-12-23 | 0.12142 | 0.0020503
Vector Lines | 2005 | 2004-12-24 | 0.002521 | 4.5017e-05
Vector Lines | 2005 | 2004-12-25 | 0.23802 | 0.0031601
Vector Lines | 2005 | 2004-12-26 | 0.33506 | 0.0053625
Vector Lines | 2005 | 2004-12-27 | 0.0864 | 0.0029998
Vector Lines | 2005 | 2004-12-28 | 0.12958 | 0.0056967
Vector Lines | 2005 | 2004-12-29 | 0.31562 | 0.0096214
Vector Lines | 2005 | 2004-12-30 | 1.6657 | 0.018223
Vector Lines | 2005 | 2004-12-31 | 0.48685 | 0.014902
Vector Lines | 2005 | 2005-01-01
Vector Lines | 2005 | 2005-01-02
Vector Lines | 2005 | 2005-01-03 | 0.00021076 | 1.0231e-06
Vector Lines | 2005 | 2005-01-04
Vector Lines | 2005 | 2005-01-05
Vector Lines | 2005 | 2005-01-06 | 0.22068 | 0.0057059
Vector Lines | 2005 | 2005-01-07 | 0.25546 | 0.0026059
Vector Lines | 2005 | 2005-01-08 | 0.023512 | 0.00035093
Vector Lines | 2005 | 2005-01-09 | 0.084648 | 0.002082
Vector Lines | 2005 | 2005-01-10 | 0.00084714 | 5.1156e-06
Vector Lines | 2005 | 2005-01-11 | 0.21426 | 0.0041539
Vector Lines | 2005 | 2005-01-12 | 0.0020698 | 7.1618e-06
Vector Lines | 2005 | 2005-01-13 | 0.030648 | 0.00023736
Vector Lines | 2005 | 2005-01-14 | 0.53959 | 0.0024616
Vector Lines | 2005 | 2005-01-15 | 0.093525 | 0.0024944
Vector Lines | 2005 | 2005-01-16 | 0.18804 | 0.002034
Vector Lines | 2005 | 2005-01-17 | 0.10838 | 0.0038786
Vector Lines | 2005 | 2005-01-18 | 0.019279 | 0.00022918
Vector Lines | 2005 | 2005-01-19 | 0.070945 | 0.00091467
Vector Lines | 2005 | 2005-01-20 | 0.23138 | 0.0031432
Vector Lines | 2005 | 2005-01-21 | 0.0095477 | 0.00015244
Vector Lines | 2005 | 2005-01-22 | 0.11497 | 0.0019429
Vector Lines | 2005 | 2005-01-23 | 0.044982 | 0.00069674
Vector Lines | 2005 | 2005-01-24 | 0.23747 | 0.0034919
Vector Lines | 2005 | 2005-01-25 | 0.046971 | 0.00030693
Vector Lines | 2005 | 2005-01-26 | 0.49936 | 0.0050119
Vector Lines | 2005 | 2005-01-27 | 0.24002 | 0.0020851
Vector Lines | 2005 | 2005-01-28 | 0.19988 | 0.0028329
Vector Lines | 2005 | 2005-01-29 | 0.041919 | 0.00028033
Vector Lines | 2005 | 2005-01-30 | 0.21947 | 0.0033865
Vector Lines | 2005 | 2005-01-31 | 0.83279 | 0.0079598
Vector Lines | 2005 | 2005-02-01 | 0.12024 | 0.00025066
Vector Lines | 2005 | 2005-02-02 | 1.3707 | 0.014365
Vector Lines | 2005 | 2005-02-03 | 0.69352 | 0.0086187
Vector Lines | 2005 | 2005-02-04 | 0.74252 | 0.0075158
Vector Lines | 2005 | 2005-02-05 | 1.3614 | 0.018854
Vector Lines | 2005 | 2005-02-06
Vector Lines | 2005 | 2005-02-07 | 0.056058 | 0.00042357
Vector Lines | 2005 | 2005-02-08 | 0.099145 | 0.0016444
Vector Lines | 2005 | 2005-02-09 | 0.059427 | 0.0022856
Vector Lines | 2005 | 2005-02-10 | 0.0058604 | 0.00073255
Vector Lines | 2005 | 2005-02-11 | 0.24279 | 0.0032177
Vector Lines | 2005 | 2005-02-12 | 0.00016662 | 3.3324e-05
Vector Lines | 2005 | 2005-02-13 | 0.54176 | 0.0042548
Vector Lines | 2005 | 2005-02-14 | 0.21469 | 0.015777
Vector Lines | 2005 | 2005-02-15 | 0.96647 | 0.0051146
Vector Lines | 2005 | 2005-02-16 | 0.27427 | 0.0033364
Vector Lines | 2005 | 2005-02-17 | 0.14407 | 0.0038035
Vector Lines | 2005 | 2005-02-18 | 0.44804 | 0.0062553
Vector Lines | 2005 | 2005-02-19 | 0.00030693 | 1.0231e-06
Vector Lines | 2005 | 2005-02-20
Vector Lines | 2005 | 2005-02-21 | 0.0369 | 0.00067321
Vector Lines | 2005 | 2005-02-22 | 0.46643 | 0.004605
Vector Lines | 2005 | 2005-02-23 | 0.41468 | 0.0075977
Vector Lines | 2005 | 2005-02-24
Vector Lines | 2005 | 2005-02-25 | 0.22089 | 0.0021424
Vector Lines | 2005 | 2005-02-26 | 0.5341 | 0.0056844
Vector Lines | 2005 | 2005-02-27 | 0.17108 | 0.0034663
Vector Lines | 2005 | 2005-02-28 | 0.13666 | 0.0018007
Vector Lines | 2005 | 2005-03-01 | 0.22972 | 0.0040169
Vector Lines | 2005 | 2005-03-02 | 0.35034 | 0.0032475
Vector Lines | 2005 | 2005-03-03 | 0.02453 | 0.0011766
Vector Lines | 2005 | 2005-03-04 | 0.25304 | 0.0040147
Vector Lines | 2005 | 2005-03-05
Vector Lines | 2005 | 2005-03-06 | 0.061127 | 0.00078145
Vector Lines | 2005 | 2005-03-07 | 0.21953 | 0.0036896
Vector Lines | 2005 | 2005-03-08 | 0.056215 | 0.00014835
Vector Lines | 2005 | 2005-03-09 | 0.0014733 | 0.00012277
Vector Lines | 2005 | 2005-03-10 | 0.17761 | 0.0095375
Vector Lines | 2005 | 2005-03-11 | 0.23312 | 0.0022836
Vector Lines | 2005 | 2005-03-12
Vector Lines | 2005 | 2005-03-13 | 0.012732 | 0.00020872
Vector Lines | 2005 | 2005-03-14 | 0.32299 | 0.0054675
Vector Lines | 2005 | 2005-03-15 | 0.080429 | 0.00082259
Vector Lines | 2005 | 2005-03-16 | 0.13671 | 0.0021271
Vector Lines | 2005 | 2005-03-17 | 0.078698 | 0.0017761
Vector Lines | 2005 | 2005-03-18 | 0.12047 | 0.00077661
Vector Lines | 2005 | 2005-03-19 | 0.18541 | 0.0034336
Vector Lines | 2005 | 2005-03-20 | 0.018858 | 0.00026192
Vector Lines | 2005 | 2005-03-21 | 0.081056 | 0.0016508
Vector Lines | 2005 | 2005-03-22 | 0.1888 | 0.0015188
Vector Lines | 2005 | 2005-03-23 | 0.22264 | 0.0050051
Vector Lines | 2005 | 2005-03-24 | 0.42363 | 0.0074707
Vector Lines | 2005 | 2005-03-25 | 0.29283 | 0.0046449
Vector Lines | 2005 | 2005-03-26
Vector Lines | 2005 | 2005-03-27 | 0.11667 | 0.0018252
Vector Lines | 2005 | 2005-03-28 | 0.076022 | 0.00044199
Vector Lines | 2005 | 2005-03-29 | 0.044395 | 0.00023122
Vector Lines | 2005 | 2005-03-30 | 0.032795 | 0.00069777
Vector Lines | 2005 | 2005-03-31
Vector Lines | 2006 | 2005-04-01 | 0.23893 | 0.0024279
Vector Lines | 2006 | 2005-04-02 | 0.00048276 | 1.6092e-05
Vector Lines | 2006 | 2005-04-03
Vector Lines | 2006 | 2005-04-04 | 0.06301 | 0.0012987
Vector Lines | 2006 | 2005-04-05 | 0.00065172 | 2.0115e-06
Vector Lines | 2006 | 2005-04-06 | 0.005957 | 2.9166e-05
Vector Lines | 2006 | 2005-04-07
Vector Lines | 2006 | 2005-04-08 | 0.065381 | 0.0012079
Vector Lines | 2006 | 2005-04-09 | 0.57762 | 0.0050267
Vector Lines | 2006 | 2005-04-10 | 0.01228 | 0.00037212
Vector Lines | 2006 | 2005-04-11 | 0.086783 | 0.0020044
Vector Lines | 2006 | 2005-04-12 | 0.031804 | 0.00093534
Vector Lines | 2006 | 2005-04-13 | 0.4121 | 0.0053068
Vector Lines | 2006 | 2005-04-14 | 0.25476 | 0.0046785
Vector Lines | 2006 | 2005-04-15 | 0.069103 | 0.0008408
Vector Lines | 2006 | 2005-04-16 | 0.11794 | 0.002621
Vector Lines | 2006 | 2005-04-17 | 0.15038 | 0.002623
Vector Lines | 2006 | 2005-04-18 | 0.41418 | 0.0051284
Vector Lines | 2006 | 2005-04-19 | 0.13005 | 0.0013203
Vector Lines | 2006 | 2005-04-20 | 0.30143 | 0.006312
Vector Lines | 2006 | 2005-04-21 | 0.77305 | 0.0068622
Vector Lines | 2006 | 2005-04-22 | 0.011103 | 4.6264e-05
Vector Lines | 2006 | 2005-04-23
Vector Lines | 2006 | 2005-04-24 | 0.62754 | 0.0071166
Vector Lines | 2006 | 2005-04-25 | 0.024651 | 0.00011644
Vector Lines | 2006 | 2005-04-26 | 0.24203 | 0.001806
Vector Lines | 2006 | 2005-04-27 | 0.42867 | 0.005258
Vector Lines | 2006 | 2005-04-28 | 0.40765 | 0.0045037
Vector Lines | 2006 | 2005-04-29 | 0.063734 | 0.0011038
Vector Lines | 2006 | 2005-04-30 | 0.29536 | 0.004604
Vector Lines | 2006 | 2005-05-01 | 0.0088079 | 0.00033645
Vector Lines | 2006 | 2005-05-02 | 2.6091 | 0.038927
Vector Lines | 2006 | 2005-05-03 | 0.59002 | 0.011436
Vector Lines | 2006 | 2005-05-04 | 0.42598 | 0.0048832
Vector Lines | 2006 | 2005-05-05 | 0.44549 | 0.0076559
Vector Lines | 2006 | 2005-05-06 | 0.0039304 | 2.2126e-05
Vector Lines | 2006 | 2005-05-07 | 0.15903 | 0.0017301
Vector Lines | 2006 | 2005-05-08 | 0.16675 | 0.0020286
Vector Lines | 2006 | 2005-05-09 | 0.16976 | 0.0025347
Vector Lines | 2006 | 2005-05-10 | 0.050928 | 0.00064465
Vector Lines | 2006 | 2005-05-11 | 0.017138 | 0.00011164
Vector Lines | 2006 | 2005-05-12 | 0.00055115 | 6.0344e-06
Vector Lines | 2006 | 2005-05-13
Vector Lines | 2006 | 2005-05-14 | 0.026226 | 0.00049482
Vector Lines | 2006 | 2005-05-15 | 0.46571 | 0.0046536
Vector Lines | 2006 | 2005-05-16 | 0.60503 | 0.0049724
Vector Lines | 2006 | 2005-05-17 | 0.45233 | 0.0039405
Vector Lines | 2006 | 2005-05-18 | 0.15463 | 0.0029504
Vector Lines | 2006 | 2005-05-19 | 0.11431 | 0.002724
Vector Lines | 2006 | 2005-05-20
Vector Lines | 2006 | 2005-05-21 | 0.19157 | 0.00066781
Vector Lines | 2006 | 2005-05-22 | 1.3278 | 0.022452
Vector Lines | 2006 | 2005-05-23 | 0.24576 | 0.0011918
Vector Lines | 2006 | 2005-05-24 | 0.85504 | 0.0079343
Vector Lines | 2006 | 2005-05-25 | 0.045024 | 0.00062356
Vector Lines | 2006 | 2005-05-26 | 0.16889 | 0.0017417
Vector Lines | 2006 | 2005-05-27 | 0.41293 | 0.0072412
Vector Lines | 2006 | 2005-05-28 | 0.20964 | 0.0061966
Vector Lines | 2006 | 2005-05-29 | 0.0011184 | 2.0115e-06
Vector Lines | 2006 | 2005-05-30 | 2.2368 | 0.039028
Vector Lines | 2006 | 2005-05-31 | 0.16299 | 0.0032974
Vector Lines | 2006 | 2005-06-01 | 0.35747 | 0.0034718
Vector Lines | 2006 | 2005-06-02 | 0.21347 | 0.003504
Vector Lines | 2006 | 2005-06-03 | 0.53508 | 0.0040199
Vector Lines | 2006 | 2005-06-04 | 0.1934 | 0.0019813
Vector Lines | 2006 | 2005-06-05 | 0.28363 | 0.003683
Vector Lines | 2006 | 2005-06-06 | 0.0014483 | 6.0344e-05
Vector Lines | 2006 | 2005-06-07 | 0.017141 | 6.839e-05
Vector Lines | 2006 | 2005-06-08 | 0.059258 | 0.0005855
Vector Lines | 2006 | 2005-06-09 | 0.0032938 | 0.00033994
Vector Lines | 2006 | 2005-06-10 | 0.14805 | 0.0073057
Vector Lines | 2006 | 2005-06-11 | 0.039646 | 0.0003862
Vector Lines | 2006 | 2005-06-12 | 0.14037 | 0.0010492
Vector Lines | 2006 | 2005-06-13 | 0.19886 | 0.0012763
Vector Lines | 2006 | 2005-06-14 | 0.031843 | 0.010376
Vector Lines | 2006 | 2005-06-15 | 0.017144 | 0.00028664
Vector Lines | 2006 | 2005-06-16 | 0.031904 | 0.00013175
Vector Lines | 2006 | 2005-06-17 | 0.12612 | 0.0014674
Vector Lines | 2006 | 2005-06-18 | 0.33195 | 0.0050488
Vector Lines | 2006 | 2005-06-19 | 0.079415 | 0.0012612
Vector Lines | 2006 | 2005-06-20 | 0.0016896 | 4.2241e-05
Vector Lines | 2006 | 2005-06-21 | 0.27514 | 0.0028985
Vector Lines | 2006 | 2005-06-22 | 1.3222 | 0.021585
Vector Lines | 2006 | 2005-06-23 | 0.41925 | 0.011274
Vector Lines | 2006 | 2005-06-24 | 0.33708 | 0.0035406
Vector Lines | 2006 | 2005-06-25 | 0.79306 | 0.0066474
Vector Lines | 2006 | 2005-06-26 | 0.50178 | 0.0067405
Vector Lines | 2006 | 2005-06-27 | 0.10429 | 0.0016896
Vector Lines | 2006 | 2005-06-28 | 0.091444 | 0.0017248
Vector Lines | 2006 | 2005-06-29 | 0.41938 | 0.0046694
Vector Lines | 2006 | 2005-06-30 | 0.61166 | 0.0087087
Vector Lines | 2006 | 2005-07-01 | 0.32111 | 0.0044101
Vector Lines | 2006 | 2005-07-02 | 0.00059138 | 1.408e-05
Vector Lines | 2006 | 2005-07-03
Vector Lines | 2006 | 2005-07-04 | 0.00095344 | 0.00031781
Vector Lines | 2006 | 2005-07-05 | 0.12789 | 0.0018807
Vector Lines | 2006 | 2005-07-06 | 0.15065 | 0.00099367
Vector Lines | 2006 | 2005-07-07 | 0.1291 | 0.0017631
Vector Lines | 2006 | 2005-07-08 | 0.18454 | 0.0030735
Vector Lines | 2006 | 2005-07-09
Vector Lines | 2006 | 2005-07-10 | 0.25306 | 0.0033129
Vector Lines | 2006 | 2005-07-11 | 0.17978 | 0.004483
Vector Lines | 2006 | 2005-07-12 | 1.8808 | 0.028546
Vector Lines | 2006 | 2005-07-13 | 0.20185 | 0.00081063
Vector Lines | 2006 | 2005-07-14 | 0.14047 | 0.00083577
Vector Lines | 2006 | 2005-07-15 | 0.98083 | 0.021975
Vector Lines | 2006 | 2005-07-16 | 1.4359 | 0.024551
Vector Lines | 2006 | 2005-07-17 | 0.04839 | 0.00097456
Vector Lines | 2006 | 2005-07-18 | 1.4795 | 0.015323
Vector Lines | 2006 | 2005-07-19 | 0.052974 | 0.00069497
Vector Lines | 2006 | 2005-07-20 | 0.016706 | 0.00025244
Vector Lines | 2006 | 2005-07-21 | 0.13772 | 0.020558
Vector Lines | 2006 | 2005-07-22 | 0.6084 | 0.0087087
Vector Lines | 2006 | 2005-07-23 | 0.22989 | 0.0028764
Vector Lines | 2006 | 2005-07-24 | 0.55095 | 0.0062094
Vector Lines | 2006 | 2005-07-25 | 0.73008 | 0.0062939
Vector Lines | 2006 | 2005-07-26 | 0.0988 | 0.0012049
Vector Lines | 2006 | 2005-07-27 | 0.010411 | 0.00011533
Vector Lines | 2006 | 2005-07-28 | 0.030035 | 0.00032314
Vector Lines | 2006 | 2005-07-29 | 0.075131 | 0.00073874
Vector Lines | 2006 | 2005-07-30 | 0.12333 | 0.0052258
Vector Lines | 2006 | 2005-07-31
Vector Lines | 2006 | 2005-08-01 | 0.032163 | 0.002391
Vector Lines | 2006 | 2005-08-02 | 0.04306 | 0.0041708
Vector Lines | 2006 | 2005-08-03 | 0.00090517 | 5.0287e-06
Vector Lines | 2006 | 2005-08-04 | 0.0072625 | 7.7442e-05
Vector Lines | 2006 | 2005-08-05
Vector Lines | 2006 | 2005-08-06 | 0.039171 | 0.00019336
Vector Lines | 2006 | 2005-08-07 | 0.18179 | 0.0011734
Vector Lines | 2006 | 2005-08-08 | 0.0052801 | 3.4195e-05
Vector Lines | 2006 | 2005-08-09 | 0.1201 | 0.0040491
Vector Lines | 2006 | 2005-08-10 | 0.047601 | 0.0012682
Vector Lines | 2006 | 2005-08-11 | 0.081856 | 0.0017751
Vector Lines | 2006 | 2005-08-12 | 0.0051977 | 1.9109e-05
Vector Lines | 2006 | 2005-08-13 | 0.0019139 | 9.0517e-06
Vector Lines | 2006 | 2005-08-14 | 0.076009 | 0.0048115
Vector Lines | 2006 | 2005-08-15 | 0.057026 | 0.0013578
Vector Lines | 2006 | 2005-08-16 | 0.12407 | 0.00036307
Vector Lines | 2006 | 2005-08-17 | 0.1135 | 0.010297
Vector Lines | 2006 | 2005-08-18 | 0.31941 | 0.0034235
Vector Lines | 2006 | 2005-08-19 | 0.12341 | 0.0017681
Vector Lines | 2006 | 2005-08-20 | 0.21551 | 0.0049442
Vector Lines | 2006 | 2005-08-21 | 0.17033 | 0.0026059
Vector Lines | 2006 | 2005-08-22 | 0.13435 | 0.0027537
Vector Lines | 2006 | 2005-08-23 | 0.56055 | 0.010924
Vector Lines | 2006 | 2005-08-24 | 0.040232 | 0.0011519
Vector Lines | 2006 | 2005-08-25 | 0.054523 | 0.0003193
Vector Lines | 2006 | 2005-08-26 | 0.087856 | 0.00027672
Vector Lines | 2006 | 2005-08-27 | 0.34924 | 0.0016937
Vector Lines | 2006 | 2005-08-28 | 0.051962 | 0.001578
Vector Lines | 2006 | 2005-08-29 | 0.29239 | 0.0045972
Vector Lines | 2006 | 2005-08-30 | 0.26015 | 0.0029508
Vector Lines | 2006 | 2005-08-31 | 0.030599 | 0.00016394
Vector Lines | 2006 | 2005-09-01 | 0.37014 | 0.0038351
Vector Lines | 2006 | 2005-09-02 | 0.12603 | 0.0027748
Vector Lines | 2006 | 2005-09-03 | 0.018366 | 0.0004033
Vector Lines | 2006 | 2005-09-04 | 0.0090205 | 5.1293e-05
Vector Lines | 2006 | 2005-09-05 | 0.022368 | 0.00013477
Vector Lines | 2006 | 2005-09-06 | 0.47298 | 0.00543
Vector Lines | 2006 | 2005-09-07 | 0.35611 | 0.0021833
Vector Lines | 2006 | 2005-09-08 | 0.0006477 | 4.023e-06
Vector Lines | 2006 | 2005-09-09 | 0.40878 | 0.0042322
Vector Lines | 2006 | 2005-09-10 | 0.079968 | 0.0013789
Vector Lines | 2006 | 2005-09-11
Vector Lines | 2006 | 2005-09-12 | 0.2893 | 0.0072141
Vector Lines | 2006 | 2005-09-13 | 0.14375 | 0.003302
Vector Lines | 2006 | 2005-09-14 | 0.024956 | 0.00019511
Vector Lines | 2006 | 2005-09-15 | 0.21826 | 0.0025511
Vector Lines | 2006 | 2005-09-16 | 0.99015 | 0.011279
Vector Lines | 2006 | 2005-09-17 | 0.081958 | 0.0013537
Vector Lines | 2006 | 2005-09-18 | 3.4101 | 0.038998
Vector Lines | 2006 | 2005-09-19 | 0.65948 | 0.020779
Vector Lines | 2006 | 2005-09-20 | 0.055588 | 0.0018315
Vector Lines | 2006 | 2005-09-21 | 0.03076 | 0.0001227
Vector Lines | 2006 | 2005-09-22 | 0.044023 | 0.00031379
Vector Lines | 2006 | 2005-09-23 | 0.15917 | 0.0016504
Vector Lines | 2006 | 2005-09-24 | 0.23658 | 0.0040149
Vector Lines | 2006 | 2005-09-25
Vector Lines | 2006 | 2005-09-26 | 0.019345 | 0.0010148
Vector Lines | 2006 | 2005-09-27 | 0.23924 | 0.0033292
Vector Lines | 2006 | 2005-09-28 | 0.19692 | 0.0042044
Vector Lines | 2006 | 2005-09-29 | 0.0022207 | 0.00037011
Vector Lines | 2006 | 2005-09-30 | 0.12525 | 0.0010644
Vector Lines | 2006 | 2005-10-01 | 2.0553 | 0.027658
Vector Lines | 2006 | 2005-10-02 | 0.49008 | 0.0084374
Vector Lines | 2006 | 2005-10-03 | 0.033169 | 0.00039307
Vector Lines | 2006 | 2005-10-04 | 0.0022126 | 1.0057e-05
Vector Lines | 2006 | 2005-10-05 | 0.2041 | 0.005028
Vector Lines | 2006 | 2005-10-06 | 0.34211 | 0.0062278
Vector Lines | 2006 | 2005-10-07 | 0.14763 | 0.0033395
Vector Lines | 2006 | 2005-10-08 | 3.3736 | 0.038927
Vector Lines | 2006 | 2005-10-09 | 1.0267 | 0.012413
Vector Lines | 2006 | 2005-10-10 | 0.70913 | 0.0072194
Vector Lines | 2006 | 2005-10-11 | 0.0036224 | 4.27e-05
Vector Lines | 2006 | 2005-10-12 | 0.4407 | 0.0051363
Vector Lines | 2006 | 2005-10-13 | 0.26988 | 0.0048188
Vector Lines | 2006 | 2005-10-14 | 0.041776 | 0.00032888
Vector Lines | 2006 | 2005-10-15 | 0.013292 | 0.0022162
Vector Lines | 2006 | 2005-10-16 | 0.0028508 | 1.4344e-05
Vector Lines | 2006 | 2005-10-17 | 0.092034 | 0.0016973
Vector Lines | 2006 | 2005-10-18 | 0.044806 | 0.0006135
Vector Lines | 2006 | 2005-10-19 | 0.32946 | 0.0021207
Vector Lines | 2006 | 2005-10-20 | 0.53713 | 0.011902
Vector Lines | 2006 | 2005-10-21 | 0.42935 | 0.0072609
Vector Lines | 2006 | 2005-10-22 | 0.97854 | 0.011374
Vector Lines | 2006 | 2005-10-23 | 0.014392 | 0.00010661
Vector Lines | 2006 | 2005-10-24 | 0.33294 | 0.0053994
Vector Lines | 2006 | 2005-10-25 | 0.237 | 0.00216
Vector Lines | 2006 | 2005-10-26 | 0.23702 | 0.0018621
Vector Lines | 2006 | 2005-10-27 | 0.28853 | 0.0034555
Vector Lines | 2006 | 2005-10-28
Vector Lines | 2006 | 2005-10-29 | 0.012308 | 5.8333e-05
Vector Lines | 2006 | 2005-10-30 | 0.085272 | 0.0017576
Vector Lines | 2006 | 2005-10-31 | 0.022834 | 0.0001361
Vector Lines | 2006 | 2005-11-01 | 0.017866 | 0.00029333
Vector Lines | 2006 | 2005-11-02 | 0.0070023 | 4.0361e-05
Vector Lines | 2006 | 2005-11-03 | 0.26737 | 0.0090004
Vector Lines | 2006 | 2005-11-04 | 0.97863 | 0.0086835
Vector Lines | 2006 | 2005-11-05 | 0.11326 | 0.0084429
Vector Lines | 2006 | 2005-11-06 | 0.1946 | 0.0035519
Vector Lines | 2006 | 2005-11-07 | 0.050525 | 0.00078802
Vector Lines | 2006 | 2005-11-08
Vector Lines | 2006 | 2005-11-09 | 0.15813 | 0.0010022
Vector Lines | 2006 | 2005-11-10 | 0.33071 | 0.0047008
Vector Lines | 2006 | 2005-11-11 | 0.20472 | 0.0016847
Vector Lines | 2006 | 2005-11-12 | 0.41621 | 0.02263
Vector Lines | 2006 | 2005-11-13 | 0.25161 | 0.0032417
Vector Lines | 2006 | 2005-11-14 | 0.037768 | 0.00068793
Vector Lines | 2006 | 2005-11-15 | 0.17254 | 0.0027336
Vector Lines | 2006 | 2005-11-16 | 0.23572 | 0.002283
Vector Lines | 2006 | 2005-11-17 | 0.064987 | 0.00066204
Vector Lines | 2006 | 2005-11-18 | 0.10794 | 0.002464
Vector Lines | 2006 | 2005-11-19 | 0.14607 | 0.0021127
Vector Lines | 2006 | 2005-11-20 | 0.014731 | 3.3189e-05
Vector Lines | 2006 | 2005-11-21 | 0.56339 | 0.0075038
Vector Lines | 2006 | 2005-11-22 | 0.33315 | 0.0045816
Vector Lines | 2006 | 2005-11-23 | 0.070482 | 0.002094
Vector Lines | 2006 | 2005-11-24 | 0.13682 | 0.004472
Vector Lines | 2006 | 2005-11-25 | 0.14787 | 0.0014513
Vector Lines | 2006 | 2005-11-26 | 3.3736 | 0.038927
Vector Lines | 2006 | 2005-11-27 | 0.10698 | 0.0016592
Vector Lines | 2006 | 2005-11-28 | 0.008415 | 7.8448e-05
Vector Lines | 2006 | 2005-11-29 | 0.39798 | 0.0029083
Vector Lines | 2006 | 2005-11-30 | 0.010723 | 6.2356e-05
Vector Lines | 2006 | 2005-12-01 | 0.22326 | 0.0018521
Vector Lines | 2006 | 2005-12-02 | 0.19191 | 0.0021301
Vector Lines | 2006 | 2005-12-03 | 0.00027757 | 1.1376e-06
Vector Lines | 2006 | 2005-12-04 | 0.0095496 | 0.00076651
Vector Lines | 2006 | 2005-12-05 | 0.013506 | 0.0006125
Vector Lines | 2006 | 2005-12-06 | 0.32444 | 0.0060653
Vector Lines | 2006 | 2005-12-07 | 0.0023625 | 8.1465e-05
Vector Lines | 2006 | 2005-12-08 | 0.35563 | 0.0089501
Vector Lines | 2006 | 2005-12-09 | 0.20273 | 0.003158
Vector Lines | 2006 | 2005-12-10 | 0.48256 | 0.0067012
Vector Lines | 2006 | 2005-12-11 | 0.72098 | 0.0072496
Vector Lines | 2006 | 2005-12-12 | 0.31545 | 0.0083285
Vector Lines | 2006 | 2005-12-13 | 0.27565 | 0.0050542
Vector Lines | 2006 | 2005-12-14 | 0.72633 | 0.0076038
Vector Lines | 2006 | 2005-12-15 | 0.15056 | 0.0025454
Vector Lines | 2006 | 2005-12-16 | 0.61451 | 0.0063242
Vector Lines | 2006 | 2005-12-17 | 1.001 | 0.01258
Vector Lines | 2006 | 2005-12-18 | 0.081565 | 0.0013453
Vector Lines | 2006 | 2005-12-19 | 0.2711 | 0.0028613
Vector Lines | 2006 | 2005-12-20 | 0.17575 | 0.0033374
Vector Lines | 2006 | 2005-12-21 | 0.045883 | 0.003805
Vector Lines | 2006 | 2005-12-22 | 0.56579 | 0.0076415
Vector Lines | 2006 | 2005-12-23 | 1.7344 | 0.027053
Vector Lines | 2006 | 2005-12-24 | 0.31206 | 0.0062658
Vector Lines | 2006 | 2005-12-25
Vector Lines | 2006 | 2005-12-26 | 0.079289 | 0.0068169
Vector Lines | 2006 | 2005-12-27 | 0.17347 | 0.0023815
Vector Lines | 2006 | 2005-12-28 | 0.44822 | 0.0050852
Vector Lines | 2006 | 2005-12-29 | 0.56574 | 0.0071112
Vector Lines | 2006 | 2005-12-30 | 0.0027529 | 1.1376e-05
Vector Lines | 2006 | 2005-12-31 | 0.099995 | 0.00087701
Vector Lines | 2006 | 2006-01-01 | 0.33285 | 0.0043979
Vector Lines | 2006 | 2006-01-02 | 0.75808 | 0.010798
Vector Lines | 2006 | 2006-01-03 | 0.099241 | 0.0032536
Vector Lines | 2006 | 2006-01-04 | 0.65453 | 0.0079705
Vector Lines | 2006 | 2006-01-05 | 0.87272 | 0.0086865
Vector Lines | 2006 | 2006-01-06 | 0.22643 | 0.0037675
Vector Lines | 2006 | 2006-01-07
Vector Lines | 2006 | 2006-01-08 | 0.25367 | 0.0016184
Vector Lines | 2006 | 2006-01-09 | 0.0067314 | 3.0172e-05
Vector Lines | 2006 | 2006-01-10 | 0.87159 | 0.009875
Vector Lines | 2006 | 2006-01-11 | 0.169 | 0.0032705
Vector Lines | 2006 | 2006-01-12 | 0.0016293 | 9.0517e-06
Vector Lines | 2006 | 2006-01-13 | 0.15256 | 0.0014094
Vector Lines | 2006 | 2006-01-14
Vector Lines | 2006 | 2006-01-15 | 0.1529 | 0.0025254
Vector Lines | 2006 | 2006-01-16 | 0.74449 | 0.014937
Vector Lines | 2006 | 2006-01-17 | 0.74376 | 0.010299
Vector Lines | 2006 | 2006-01-18 | 0.041007 | 0.00084703
Vector Lines | 2006 | 2006-01-19 | 1.1756 | 0.016465
Vector Lines | 2006 | 2006-01-20 | 0.31116 | 0.00055638
Vector Lines | 2006 | 2006-01-21
Vector Lines | 2006 | 2006-01-22 | 0.0066067 | 1.9109e-05
Vector Lines | 2006 | 2006-01-23 | 0.46443 | 0.0071527
Vector Lines | 2006 | 2006-01-24 | 3.3736 | 0.038927
Vector Lines | 2006 | 2006-01-25 | 0.62844 | 0.022649
Vector Lines | 2006 | 2006-01-26 | 0.40762 | 0.0079373
Vector Lines | 2006 | 2006-01-27 | 0.12132 | 0.002451
Vector Lines | 2006 | 2006-01-28 | 0.46051 | 0.0059801
Vector Lines | 2006 | 2006-01-29 | 0.028621 | 0.00018707
Vector Lines | 2006 | 2006-01-30 | 0.1128 | 0.0012511
Vector Lines | 2006 | 2006-01-31 | 0.18958 | 0.0093783
Vector Lines | 2006 | 2006-02-01 | 0.16895 | 0.00304
Vector Lines | 2006 | 2006-02-02 | 0.99947 | 0.006984
Vector Lines | 2006 | 2006-02-03 | 0.015946 | 0.00015589
Vector Lines | 2006 | 2006-02-04 | 0.27511 | 0.0028667
Vector Lines | 2006 | 2006-02-05 | 0.1655 | 0.0025844
Vector Lines | 2006 | 2006-02-06 | 0.040298 | 0.00038017
Vector Lines | 2006 | 2006-02-07 | 0.33692 | 0.019706
Vector Lines | 2006 | 2006-02-08 | 0.16074 | 0.0017313
Vector Lines | 2006 | 2006-02-09 | 0.094818 | 0.00041101
Vector Lines | 2006 | 2006-02-10 | 0.64242 | 0.0062989
Vector Lines | 2006 | 2006-02-11 | 0.081623 | 0.0011568
Vector Lines | 2006 | 2006-02-12 | 0.0045136 | 1.0321e-05
Vector Lines | 2006 | 2006-02-13
Vector Lines | 2006 | 2006-02-14 | 0.32488 | 0.00387
Vector Lines | 2006 | 2006-02-15 | 0.10194 | 0.0025207
Vector Lines | 2006 | 2006-02-16 | 0.33541 | 0.0058609
Vector Lines | 2006 | 2006-02-17 | 0.035246 | 0.00020845
Vector Lines | 2006 | 2006-02-18
Vector Lines | 2006 | 2006-02-19 | 0.067291 | 0.00024003
Vector Lines | 2006 | 2006-02-20 | 0.0076064 | 0.00068692
Vector Lines | 2006 | 2006-02-21 | 0.0011441 | 1.0321e-05
Vector Lines | 2006 | 2006-02-22 | 0.23175 | 0.0051781
Vector Lines | 2006 | 2006-02-23 | 0.045668 | 0.00048477
Vector Lines | 2006 | 2006-02-24 | 0.13594 | 0.0020808
Vector Lines | 2006 | 2006-02-25 | 0.0097134 | 9.8563e-05
Vector Lines | 2006 | 2006-02-26 | 0.2458 | 0.0029559
Vector Lines | 2006 | 2006-02-27 | 0.1036 | 0.00071408
Vector Lines | 2006 | 2006-02-28 | 0.0089833 | 6.5373e-05
Vector Lines | 2006 | 2006-03-01 | 0.31031 | 0.0051514
Vector Lines | 2006 | 2006-03-02 | 0.13322 | 0.0012366
Vector Lines | 2006 | 2006-03-03 | 0.31856 | 0.0029524
Vector Lines | 2006 | 2006-03-04 | 0.79856 | 0.0029508
Vector Lines | 2006 | 2006-03-05 | 0.15347 | 0.0018387
Vector Lines | 2006 | 2006-03-06 | 0.22419 | 0.0014182
Vector Lines | 2006 | 2006-03-07 | 1.4365 | 0.014595
Vector Lines | 2006 | 2006-03-08 | 1.1757 | 0.021365
Vector Lines | 2006 | 2006-03-09 | 0.11016 | 0.0020675
Vector Lines | 2006 | 2006-03-10 | 0.057984 | 0.0013225
Vector Lines | 2006 | 2006-03-11 | 0.0013004 | 3.1178e-05
Vector Lines | 2006 | 2006-03-12
Vector Lines | 2006 | 2006-03-13 | 0.052322 | 0.00016997
Vector Lines | 2006 | 2006-03-14 | 0.0018201 | 5.6879e-06
Vector Lines | 2006 | 2006-03-15 | 0.11062 | 0.0028773
Vector Lines | 2006 | 2006-03-16 | 0.084887 | 0.00060813
Vector Lines | 2006 | 2006-03-17
Vector Lines | 2006 | 2006-03-18 | 0.094967 | 0.000991
Vector Lines | 2006 | 2006-03-19 | 0.0021182 | 4.3228e-05
Vector Lines | 2006 | 2006-03-20 | 0.17633 | 0.0030456
Vector Lines | 2006 | 2006-03-21 | 0.051561 | 0.00086332
Vector Lines | 2006 | 2006-03-22 | 0.36203 | 0.0041865
Vector Lines | 2006 | 2006-03-23 | 0.17467 | 0.0029345
Vector Lines | 2006 | 2006-03-24 | 0.60779 | 0.0081246
Vector Lines | 2006 | 2006-03-25 | 0.16102 | 0.0019544
Vector Lines | 2006 | 2006-03-26 | 2.0904 | 0.018186
Vector Lines | 2006 | 2006-03-27 | 0.93246 | 0.015677
Vector Lines | 2006 | 2006-03-28 | 0.63536 | 0.0059855
Vector Lines | 2006 | 2006-03-29 | 0.37936 | 0.010686
Vector Lines | 2006 | 2006-03-30 | 0.11108 | 0.0028902
Vector Lines | 2006 | 2006-03-31 | 0.36784 | 0.0055842
Vector Lines | 2007 | 2006-04-01
Vector Lines | 2007 | 2006-04-02 | 0.16979 | 0.0021046
Vector Lines | 2007 | 2006-04-03 | 0.20058 | 0.0043158
Vector Lines | 2007 | 2006-04-04 | 0.11256 | 0.0017348
Vector Lines | 2007 | 2006-04-05 | 0.17501 | 0.00057285
Vector Lines | 2007 | 2006-04-06 | 0.21954 | 0.0020353
Vector Lines | 2007 | 2006-04-07 | 0.15739 | 0.0027879
Vector Lines | 2007 | 2006-04-08 | 0.4772 | 0.0067288
Vector Lines | 2007 | 2006-04-09 | 0.46738 | 0.0064379
Vector Lines | 2007 | 2006-04-10 | 0.2005 | 0.0032797
Vector Lines | 2007 | 2006-04-11 | 0.27667 | 0.0051065
Vector Lines | 2007 | 2006-04-12 | 0.54129 | 0.0075114
Vector Lines | 2007 | 2006-04-13 | 0.0021602 | 2.1895e-05
Vector Lines | 2007 | 2006-04-14 | 0.21376 | 0.0014169
Vector Lines | 2007 | 2006-04-15 | 0.03869 | 0.00015601
Vector Lines | 2007 | 2006-04-16 | 0.052209 | 0.0014937
Vector Lines | 2007 | 2006-04-17 | 0.12895 | 0.0028516
Vector Lines | 2007 | 2006-04-18 | 0.63745 | 0.0050168
Vector Lines | 2007 | 2006-04-19 | 0.34383 | 0.0029373
Vector Lines | 2007 | 2006-04-20 | 0.024831 | 0.00014712
Vector Lines | 2007 | 2006-04-21
Vector Lines | 2007 | 2006-04-22 | 0.45337 | 0.0066732
Vector Lines | 2007 | 2006-04-23 | 0.0063204 | 5.3327e-05
Vector Lines | 2007 | 2006-04-24 | 0.070437 | 0.0012207
Vector Lines | 2007 | 2006-04-25 | 0.47491 | 0.0046495
Vector Lines | 2007 | 2006-04-26 | 0.5745 | 0.012245
Vector Lines | 2007 | 2006-04-27 | 0.34886 | 0.0058383
Vector Lines | 2007 | 2006-04-28 | 0.65962 | 0.0037101
Vector Lines | 2007 | 2006-04-29 | 0.37609 | 0.0037751
Vector Lines | 2007 | 2006-04-30 | 1.1416 | 0.0077215
Vector Lines | 2007 | 2006-05-01 | 0.010786 | 9.0839e-05
Vector Lines | 2007 | 2006-05-02 | 0.34565 | 0.0072846
Vector Lines | 2007 | 2006-05-03 | 0.89804 | 0.018189
Vector Lines | 2007 | 2006-05-04 | 0.084261 | 0.00096122
Vector Lines | 2007 | 2006-05-05 | 0.42192 | 0.0041239
Vector Lines | 2007 | 2006-05-06 | 2.8308 | 0.0309
Vector Lines | 2007 | 2006-05-07 | 0.43877 | 0.0044847
Vector Lines | 2007 | 2006-05-08 | 0.62956 | 0.013383
Vector Lines | 2007 | 2006-05-09 | 0.19858 | 0.0043177
Vector Lines | 2007 | 2006-05-10 | 0.012739 | 4.3775e-05
Vector Lines | 2007 | 2006-05-11 | 0.13576 | 0.00043396
Vector Lines | 2007 | 2006-05-12 | 0.15479 | 0.0014781
Vector Lines | 2007 | 2006-05-13 | 0.60696 | 0.009134
Vector Lines | 2007 | 2006-05-14 | 0.93318 | 0.0060139
Vector Lines | 2007 | 2006-05-15 | 1.1168 | 0.0085092
Vector Lines | 2007 | 2006-05-16 | 0.73424 | 0.01031
Vector Lines | 2007 | 2006-05-17 | 0.2047 | 0.0022787
Vector Lines | 2007 | 2006-05-18 | 0.042141 | 0.00054768
Vector Lines | 2007 | 2006-05-19 | 0.30087 | 0.0037942
Vector Lines | 2007 | 2006-05-20 | 0.50209 | 0.0062211
Vector Lines | 2007 | 2006-05-21 | 0.011321 | 4.1966e-05
Vector Lines | 2007 | 2006-05-22 | 0.14588 | 0.0014357
Vector Lines | 2007 | 2006-05-23 | 0.78828 | 0.0063407
Vector Lines | 2007 | 2006-05-24 | 0.0070401 | 7.7016e-05
Vector Lines | 2007 | 2006-05-25 | 0.11618 | 0.00043099
Vector Lines | 2007 | 2006-05-26 | 0.66951 | 0.0089441
Vector Lines | 2007 | 2006-05-27 | 0.10774 | 0.0024668
Vector Lines | 2007 | 2006-05-28 | 0.054355 | 0.0057969
Vector Lines | 2007 | 2006-05-29 | 0.00093802 | 5.9243e-06
Vector Lines | 2007 | 2006-05-30 | 0.42716 | 0.0048828
Vector Lines | 2007 | 2006-05-31 | 0.055492 | 0.00070654
Vector Lines | 2007 | 2006-06-01 | 0.48633 | 0.00376
Vector Lines | 2007 | 2006-06-02 | 0.0030806 | 7.7016e-05
Vector Lines | 2007 | 2006-06-03 | 0.21291 | 0.0032019
Vector Lines | 2007 | 2006-06-04 | 2.8911 | 0.013929
Vector Lines | 2007 | 2006-06-05 | 0.32134 | 0.002425
Vector Lines | 2007 | 2006-06-06 | 1.1523 | 0.010223
Vector Lines | 2007 | 2006-06-07 | 0.5667 | 0.0069948
Vector Lines | 2007 | 2006-06-08 | 0.060732 | 0.00063444
Vector Lines | 2007 | 2006-06-09 | 0.84399 | 0.0062307
Vector Lines | 2007 | 2006-06-10 | 0.22238 | 0.0034156
Vector Lines | 2007 | 2006-06-11 | 0.041319 | 0.0011438
Vector Lines | 2007 | 2006-06-12 | 3.3736 | 0.038927
Vector Lines | 2007 | 2006-06-13 | 0.97653 | 0.018589
Vector Lines | 2007 | 2006-06-14 | 0.23492 | 0.0063746
Vector Lines | 2007 | 2006-06-15 | 0.018371 | 0.001354
Vector Lines | 2007 | 2006-06-16 | 0.12803 | 0.0028822
Vector Lines | 2007 | 2006-06-17 | 0.1663 | 0.0021414
Vector Lines | 2007 | 2006-06-18 | 0.031092 | 0.0002429
Vector Lines | 2007 | 2006-06-19 | 0.88439 | 0.0088687
Vector Lines | 2007 | 2006-06-20 | 0.058147 | 0.00037718
Vector Lines | 2007 | 2006-06-21 | 0.050958 | 0.00026995
Vector Lines | 2007 | 2006-06-22 | 0.3242 | 0.0030896
Vector Lines | 2007 | 2006-06-23 | 0.52808 | 0.013551
Vector Lines | 2007 | 2006-06-24 | 0.0037684 | 1.531e-05
Vector Lines | 2007 | 2006-06-25 | 0.13709 | 0.0019174
Vector Lines | 2007 | 2006-06-26 | 0.029363 | 0.0025732
Vector Lines | 2007 | 2006-06-27 | 0.27579 | 0.0098078
Vector Lines | 2007 | 2006-06-28 | 0.31117 | 0.0051265
Vector Lines | 2007 | 2006-06-29 | 0.043177 | 0.00047493
Vector Lines | 2007 | 2006-06-30 | 0.48747 | 0.0055969
Vector Lines | 2007 | 2006-07-01 | 0.16082 | 0.0032149
Vector Lines | 2007 | 2006-07-02 | 0.25349 | 0.0014828
Vector Lines | 2007 | 2006-07-03 | 0.036427 | 0.00070302
Vector Lines | 2007 | 2006-07-04 | 0.03683 | 0.00044835
Vector Lines | 2007 | 2006-07-05 | 0.16978 | 0.0015661
Vector Lines | 2007 | 2006-07-06 | 0.63455 | 0.0055264
Vector Lines | 2007 | 2006-07-07 | 0.22921 | 0.0031583
Vector Lines | 2007 | 2006-07-08 | 1.1434 | 0.012107
Vector Lines | 2007 | 2006-07-09 | 0.019717 | 0.00026209
Vector Lines | 2007 | 2006-07-10 | 0.47981 | 0.0046794
Vector Lines | 2007 | 2006-07-11 | 0.023333 | 0.00018777
Vector Lines | 2007 | 2006-07-12 | 0.0105 | 3.6533e-05
Vector Lines | 2007 | 2006-07-13 | 0.7917 | 0.0072754
Vector Lines | 2007 | 2006-07-14 | 0.40702 | 0.003822
Vector Lines | 2007 | 2006-07-15 | 0.00078991 | 0.00035743
Vector Lines | 2007 | 2006-07-16 | 0.28053 | 0.0053302
Vector Lines | 2007 | 2006-07-17 | 0.010541 | 0.00014548
Vector Lines | 2007 | 2006-07-18 | 0.16258 | 0.0016718
Vector Lines | 2007 | 2006-07-19 | 0.9903 | 0.0113
Vector Lines | 2007 | 2006-07-20 | 0.098575 | 0.0031212
Vector Lines | 2007 | 2006-07-21 | 0.014479 | 6.501e-05
Vector Lines | 2007 | 2006-07-22 | 0.2424 | 0.001653
Vector Lines | 2007 | 2006-07-23 | 0.43911 | 0.0051732
Vector Lines | 2007 | 2006-07-24 | 0.47659 | 0.0058865
Vector Lines | 2007 | 2006-07-25 | 0.22109 | 0.0067488
Vector Lines | 2007 | 2006-07-26 | 0.22543 | 0.0051419
Vector Lines | 2007 | 2006-07-27 | 0.040991 | 0.00014218
Vector Lines | 2007 | 2006-07-28 | 0.026282 | 0.00019986
Vector Lines | 2007 | 2006-07-29 | 0.0045281 | 0.0001017
Vector Lines | 2007 | 2006-07-30 | 0.44641 | 0.0055861
Vector Lines | 2007 | 2006-07-31 | 0.12587 | 0.0014295
Vector Lines | 2007 | 2006-08-01 | 0.41888 | 0.0027099
Vector Lines | 2007 | 2006-08-02 | 0.057051 | 0.00046689
Vector Lines | 2007 | 2006-08-03 | 0.15049 | 0.0037649
Vector Lines | 2007 | 2006-08-04 | 0.00029967 | 4.6104e-06
Vector Lines | 2007 | 2006-08-05 | 0.65033 | 0.0051413
Vector Lines | 2007 | 2006-08-06 | 1.3927 | 0.01485
Vector Lines | 2007 | 2006-08-07
Vector Lines | 2007 | 2006-08-08 | 0.20313 | 0.001469
Vector Lines | 2007 | 2006-08-09 | 1.7843 | 0.027484
Vector Lines | 2007 | 2006-08-10 | 0.10271 | 0.0037505
Vector Lines | 2007 | 2006-08-11 | 0.0022404 | 1.6786e-05
Vector Lines | 2007 | 2006-08-12 | 0.36519 | 0.0073542
Vector Lines | 2007 | 2006-08-13 | 0.0025933 | 6.9156e-06
Vector Lines | 2007 | 2006-08-14 | 0.020158 | 8.689e-05
Vector Lines | 2007 | 2006-08-15 | 0.14108 | 0.0028835
Vector Lines | 2007 | 2006-08-16 | 0.27139 | 0.0045183
Vector Lines | 2007 | 2006-08-17 | 0.040129 | 0.0021189
Vector Lines | 2007 | 2006-08-18 | 0.44775 | 0.0038911
Vector Lines | 2007 | 2006-08-19 | 0.54999 | 0.0037567
Vector Lines | 2007 | 2006-08-20 | 0.30558 | 0.0038981
Vector Lines | 2007 | 2006-08-21 | 0.36867 | 0.0050681
Vector Lines | 2007 | 2006-08-22 | 0.016733 | 0.00026114
Vector Lines | 2007 | 2006-08-23 | 0.017963 | 0.00064674
Vector Lines | 2007 | 2006-08-24 | 0.26426 | 0.0025057
Vector Lines | 2007 | 2006-08-25 | 0.47691 | 0.0080059
Vector Lines | 2007 | 2006-08-26 | 0.33217 | 0.0044813
Vector Lines | 2007 | 2006-08-27 | 0.0042818 | 1.5475e-05
Vector Lines | 2007 | 2006-08-28 | 0.059043 | 0.00084711
Vector Lines | 2007 | 2006-08-29 | 0.78723 | 0.0070663
Vector Lines | 2007 | 2006-08-30 | 0.01332 | 5.9243e-05
Vector Lines | 2007 | 2006-08-31 | 0.18753 | 0.0017133
Vector Lines | 2007 | 2006-09-01 | 0.086422 | 0.00092646
Vector Lines | 2007 | 2006-09-02 | 0.013762 | 9.9726e-05
Vector Lines | 2007 | 2006-09-03 | 0.027609 | 6.685e-05
Vector Lines | 2007 | 2006-09-04 | 0.12875 | 0.0012224
Vector Lines | 2007 | 2006-09-05 | 0.34029 | 0.0038212
Vector Lines | 2007 | 2006-09-06 | 0.028655 | 0.00027664
Vector Lines | 2007 | 2006-09-07 | 0.40477 | 0.003217
Vector Lines | 2007 | 2006-09-08 | 0.070321 | 0.00026924
Vector Lines | 2007 | 2006-09-09 | 0.79032 | 0.0065585
Vector Lines | 2007 | 2006-09-10 | 0.079221 | 0.0018298
Vector Lines | 2007 | 2006-09-11 | 0.16831 | 0.004114
Vector Lines | 2007 | 2006-09-12 | 0.50888 | 0.0031746
Vector Lines | 2007 | 2006-09-13 | 0.10211 | 0.0016273
Vector Lines | 2007 | 2006-09-14 | 0.18772 | 0.0030036
Vector Lines | 2007 | 2006-09-15 | 0.0034914 | 6.7142e-05
Vector Lines | 2007 | 2006-09-16 | 0.40848 | 0.0082072
Vector Lines | 2007 | 2006-09-17 | 0.36427 | 0.0044903
Vector Lines | 2007 | 2006-09-18 | 0.26105 | 0.0051291
Vector Lines | 2007 | 2006-09-19 | 0.33976 | 0.0060525
Vector Lines | 2007 | 2006-09-20 | 0.027906 | 0.00028705
Vector Lines | 2007 | 2006-09-21 | 0.020251 | 6.418e-05
Vector Lines | 2007 | 2006-09-22 | 0.062521 | 0.0041118
Vector Lines | 2007 | 2006-09-23 | 0.47368 | 0.0020399
Vector Lines | 2007 | 2006-09-24 | 0.24789 | 0.0039679
Vector Lines | 2007 | 2006-09-25 | 0.073674 | 0.00096933
Vector Lines | 2007 | 2006-09-26 | 0.41482 | 0.0022564
Vector Lines | 2007 | 2006-09-27 | 0.013662 | 0.00025672
Vector Lines | 2007 | 2006-09-28 | 0.32254 | 0.0015098
Vector Lines | 2007 | 2006-09-29 | 0.37699 | 0.0080021
Vector Lines | 2007 | 2006-09-30 | 0.023187 | 0.00012458
Vector Lines | 2007 | 2006-10-01 | 0.30352 | 0.0088192
Vector Lines | 2007 | 2006-10-02 | 0.76745 | 0.0062456
Vector Lines | 2007 | 2006-10-03 | 0.12928 | 0.0012853
Vector Lines | 2007 | 2006-10-04 | 0.37086 | 0.0028595
Vector Lines | 2007 | 2006-10-05 | 0.12954 | 0.00047
Vector Lines | 2007 | 2006-10-06 | 0.4581 | 0.0051834
Vector Lines | 2007 | 2006-10-07 | 0.098729 | 0.0013001
Vector Lines | 2007 | 2006-10-08 | 0.040826 | 0.0008812
Vector Lines | 2007 | 2006-10-09 | 0.0017062 | 2.3697e-05
Vector Lines | 2007 | 2006-10-10 | 0.8315 | 0.010569
Vector Lines | 2007 | 2006-10-11 | 0.023017 | 0.00028058
Vector Lines | 2007 | 2006-10-12 | 0.07371 | 0.00022315
Vector Lines | 2007 | 2006-10-13 | 0.16849 | 0.0032821
Vector Lines | 2007 | 2006-10-14 | 0.099489 | 0.0037106
Vector Lines | 2007 | 2006-10-15 | 0.18628 | 0.0023255
Vector Lines | 2007 | 2006-10-16 | 0.53893 | 0.0083801
Vector Lines | 2007 | 2006-10-17 | 0.053414 | 0.0011612
Vector Lines | 2007 | 2006-10-18 | 0.2157 | 0.0035814
Vector Lines | 2007 | 2006-10-19 | 0.080908 | 0.0009774
Vector Lines | 2007 | 2006-10-20 | 0.097053 | 0.00088124
Vector Lines | 2007 | 2006-10-21 | 0.030629 | 0.00056281
Vector Lines | 2007 | 2006-10-22 | 0.029209 | 0.00017608
Vector Lines | 2007 | 2006-10-23 | 1.2816 | 0.011112
Vector Lines | 2007 | 2006-10-24 | 0.021529 | 9.0839e-05
Vector Lines | 2007 | 2006-10-25 | 0.092909 | 0.01248
Vector Lines | 2007 | 2006-10-26 | 0.43209 | 0.0060795
Vector Lines | 2007 | 2006-10-27 | 0.063898 | 0.0011345
Vector Lines | 2007 | 2006-10-28 | 0.0003051 | 9.8739e-07
Vector Lines | 2007 | 2006-10-29 | 0.64783 | 0.0057249
Vector Lines | 2007 | 2006-10-30 | 0.32634 | 0.0082183
Vector Lines | 2007 | 2006-10-31 | 0.21835 | 0.0023618
Vector Lines | 2007 | 2006-11-01 | 0.040475 | 0.00033176
Vector Lines | 2007 | 2006-11-02 | 0.37198 | 0.0043525
Vector Lines | 2007 | 2006-11-03 | 0.076107 | 0.0036678
Vector Lines | 2007 | 2006-11-04 | 0.25984 | 0.0036082
Vector Lines | 2007 | 2006-11-05 | 0.00054057 | 1.1526e-06
Vector Lines | 2007 | 2006-11-06 | 0.00062205 | 6.9117e-06
Vector Lines | 2007 | 2006-11-07 | 0.26271 | 0.0034509
Vector Lines | 2007 | 2006-11-08 | 0.24704 | 0.0040325
Vector Lines | 2007 | 2006-11-09 | 3.3736 | 0.038927
Vector Lines | 2007 | 2006-11-10 | 0.69253 | 0.011351
Vector Lines | 2007 | 2006-11-11 | 0.25792 | 0.00207
Vector Lines | 2007 | 2006-11-12 | 0.072672 | 0.0011849
Vector Lines | 2007 | 2006-11-13 | 1.3335 | 0.018493
Vector Lines | 2007 | 2006-11-14 | 0.02828 | 0.00038986
Vector Lines | 2007 | 2006-11-15 | 0.71688 | 0.0095364
Vector Lines | 2007 | 2006-11-16 | 0.27136 | 0.0065898
Vector Lines | 2007 | 2006-11-17 | 0.020664 | 0.00011059
Vector Lines | 2007 | 2006-11-18 | 0.51467 | 0.0072428
Vector Lines | 2007 | 2006-11-19 | 0.043088 | 0.00040285
Vector Lines | 2007 | 2006-11-20 | 0.042831 | 0.0004147
Vector Lines | 2007 | 2006-11-21 | 0.76308 | 0.007152
Vector Lines | 2007 | 2006-11-22 | 0.14942 | 0.0020253
Vector Lines | 2007 | 2006-11-23 | 0.021285 | 0.00033623
Vector Lines | 2007 | 2006-11-24 | 0.45029 | 0.0016435
Vector Lines | 2007 | 2006-11-25 | 0.026588 | 0.00040285
Vector Lines | 2007 | 2006-11-26 | 0.081314 | 0.0018934
Vector Lines | 2007 | 2006-11-27 | 0.30488 | 0.003837
Vector Lines | 2007 | 2006-11-28 | 0.47829 | 0.0068192
Vector Lines | 2007 | 2006-11-29 | 0.49208 | 0.0066237
Vector Lines | 2007 | 2006-11-30 | 0.70039 | 0.012324
Vector Lines | 2007 | 2006-12-01 | 0.34477 | 0.0032228
Vector Lines | 2007 | 2006-12-02 | 0.35717 | 0.0039443
Vector Lines | 2007 | 2006-12-03 | 0.019486 | 0.00018211
Vector Lines | 2007 | 2006-12-04 | 0.35644 | 0.005789
Vector Lines | 2007 | 2006-12-05 | 0.17914 | 0.0024047
Vector Lines | 2007 | 2006-12-06 | 0.36458 | 0.0048547
Vector Lines | 2007 | 2006-12-07 | 0.029236 | 0.00015996
Vector Lines | 2007 | 2006-12-08 | 0.084669 | 0.0032977
Vector Lines | 2007 | 2006-12-09 | 0.24387 | 0.0045307
Vector Lines | 2007 | 2006-12-10 | 0.53884 | 0.011831
Vector Lines | 2007 | 2006-12-11 | 0.12109 | 0.0028832
Vector Lines | 2007 | 2006-12-12 | 0.67653 | 0.016353
Vector Lines | 2007 | 2006-12-13 | 0.018148 | 0.00023697
Vector Lines | 2007 | 2006-12-14 | 0.33102 | 0.0043182
Vector Lines | 2007 | 2006-12-15 | 0.032695 | 0.0001411
Vector Lines | 2007 | 2006-12-16 | 0.14962 | 0.0028022
Vector Lines | 2007 | 2006-12-17 | 0.31763 | 0.010352
Vector Lines | 2007 | 2006-12-18 | 0.2907 | 0.0053379
Vector Lines | 2007 | 2006-12-19 | 0.59419 | 0.010566
Vector Lines | 2007 | 2006-12-20 | 0.064209 | 0.0026845
Vector Lines | 2007 | 2006-12-21 | 0.042367 | 0.00036336
Vector Lines | 2007 | 2006-12-22
Vector Lines | 2007 | 2006-12-23 | 0.011564 | 9.4789e-05
Vector Lines | 2007 | 2006-12-24
Vector Lines | 2007 | 2006-12-25 | 0.43604 | 0.012344
Vector Lines | 2007 | 2006-12-26 | 0.030411 | 0.00010861
Vector Lines | 2007 | 2006-12-27 | 0.0080724 | 0.00035417
Vector Lines | 2007 | 2006-12-28 | 0.0074528 | 6.7142e-05
Vector Lines | 2007 | 2006-12-29
Vector Lines | 2007 | 2006-12-30 | 0.14973 | 0.0018372
Vector Lines | 2007 | 2006-12-31
Vector Lines | 2007 | 2007-01-01 | 0.17904 | 0.0028731
Vector Lines | 2007 | 2007-01-02 | 0.00026625 | 3.4578e-06
Vector Lines | 2007 | 2007-01-03 | 0.1316 | 0.003787
Vector Lines | 2007 | 2007-01-04 | 0.0014771 | 7.8991e-06
Vector Lines | 2007 | 2007-01-05 | 0.0052252 | 0.00029029
Vector Lines | 2007 | 2007-01-06 | 0.083195 | 0.0019451
Vector Lines | 2007 | 2007-01-07 | 0.054067 | 0.00050746
Vector Lines | 2007 | 2007-01-08 | 0.0071683 | 1.4976e-05
Vector Lines | 2007 | 2007-01-09 | 0.49619 | 0.021425
Vector Lines | 2007 | 2007-01-10 | 0.089874 | 0.001953
Vector Lines | 2007 | 2007-01-11 | 0.22532 | 0.0019291
Vector Lines | 2007 | 2007-01-12 | 0.082909 | 0.0011078
Vector Lines | 2007 | 2007-01-13 | 0.41642 | 0.0057571
Vector Lines | 2007 | 2007-01-14 | 0.90065 | 0.01388
Vector Lines | 2007 | 2007-01-15 | 0.024278 | 0.00053352
Vector Lines | 2007 | 2007-01-16 | 0.099921 | 0.0033287
Vector Lines | 2007 | 2007-01-17 | 0.23533 | 0.0031328
Vector Lines | 2007 | 2007-01-18 | 0.029795 | 0.014898
Vector Lines | 2007 | 2007-01-19 | 0.0012079 | 9.2208e-06
Vector Lines | 2007 | 2007-01-20 | 0.0020977 | 4.1493e-05
Vector Lines | 2007 | 2007-01-21
Vector Lines | 2007 | 2007-01-22 | 0.043663 | 0.00071
Vector Lines | 2007 | 2007-01-23 | 0.11376 | 0.0010531
Vector Lines | 2007 | 2007-01-24 | 0.13929 | 0.0027474
Vector Lines | 2007 | 2007-01-25 | 0.078186 | 0.0024152
Vector Lines | 2007 | 2007-01-26 | 0.08076 | 0.0013547
Vector Lines | 2007 | 2007-01-27 | 0.20806 | 0.0036998
Vector Lines | 2007 | 2007-01-28 | 1.0759 | 0.013419
Vector Lines | 2007 | 2007-01-29 | 0.0014326 | 2.4028e-05
Vector Lines | 2007 | 2007-01-30 | 0.082691 | 0.00070504
Vector Lines | 2007 | 2007-01-31 | 0.50844 | 0.0041991
Vector Lines | 2007 | 2007-02-01
Vector Lines | 2007 | 2007-02-02 | 0.23389 | 0.0046232
Vector Lines | 2007 | 2007-02-03 | 0.13308 | 0.0026677
Vector Lines | 2007 | 2007-02-04 | 0.19945 | 0.003921
Vector Lines | 2007 | 2007-02-05 | 0.063437 | 0.0013995
Vector Lines | 2007 | 2007-02-06 | 0.30864 | 0.0052562
Vector Lines | 2007 | 2007-02-07 | 0.0054045 | 3.0774e-05
Vector Lines | 2007 | 2007-02-08 | 0.33165 | 0.0062701
Vector Lines | 2007 | 2007-02-09 | 0.13414 | 0.0017777
Vector Lines | 2007 | 2007-02-10 | 0.60071 | 0.010406
Vector Lines | 2007 | 2007-02-11 | 0.00039989 | 2.9622e-06
Vector Lines | 2007 | 2007-02-12 | 0.19243 | 0.0048263
Vector Lines | 2007 | 2007-02-13 | 0.0074478 | 5.9574e-05
Vector Lines | 2007 | 2007-02-14 | 0.13333 | 0.00072248
Vector Lines | 2007 | 2007-02-15 | 0.78577 | 0.013371
Vector Lines | 2007 | 2007-02-16 | 0.3376 | 0.0070308
Vector Lines | 2007 | 2007-02-17 | 0.0023993 | 5.3319e-05
Vector Lines | 2007 | 2007-02-18
Vector Lines | 2007 | 2007-02-19 | 0.13777 | 0.0022522
Vector Lines | 2007 | 2007-02-20 | 0.53308 | 0.0046798
Vector Lines | 2007 | 2007-02-21 | 0.00035546 | 5.9243e-06
Vector Lines | 2007 | 2007-02-22 | 1.2707 | 0.0099588
Vector Lines | 2007 | 2007-02-23 | 0.2435 | 0.0009056
Vector Lines | 2007 | 2007-02-24 | 0.03677 | 0.00075041
Vector Lines | 2007 | 2007-02-25 | 0.32209 | 0.0029878
Vector Lines | 2007 | 2007-02-26 | 0.067269 | 0.0016838
Vector Lines | 2007 | 2007-02-27 | 0.042776 | 0.00040894
Vector Lines | 2007 | 2007-02-28 | 0.86127 | 0.0059276
Vector Lines | 2007 | 2007-03-01 | 0.093473 | 0.0026077
Vector Lines | 2007 | 2007-03-02 | 0.12924 | 0.00099923
Vector Lines | 2007 | 2007-03-03 | 0.011187 | 0.00021784
Vector Lines | 2007 | 2007-03-04
Vector Lines | 2007 | 2007-03-05
Vector Lines | 2007 | 2007-03-06 | 0.011161 | 2.9622e-05
Vector Lines | 2007 | 2007-03-07 | 0.37473 | 0.0071002
Vector Lines | 2007 | 2007-03-08 | 0.12822 | 0.0011849
Vector Lines | 2007 | 2007-03-09 | 0.3627 | 0.0040822
Vector Lines | 2007 | 2007-03-10 | 0.23158 | 0.0071441
Vector Lines | 2007 | 2007-03-11 | 0.22864 | 0.0050296
Vector Lines | 2007 | 2007-03-12 | 0.84101 | 0.0084833
Vector Lines | 2007 | 2007-03-13 | 2.9233 | 0.026705
Vector Lines | 2007 | 2007-03-14 | 3.3736 | 0.038927
Vector Lines | 2007 | 2007-03-15 | 0.21837 | 0.0030609
Vector Lines | 2007 | 2007-03-16 | 0.34368 | 0.0058107
Vector Lines | 2007 | 2007-03-17 | 0.068149 | 0.00028634
Vector Lines | 2007 | 2007-03-18 | 0.13831 | 0.0023991
Vector Lines | 2007 | 2007-03-19 | 0.0081928 | 4.2461e-05
Vector Lines | 2007 | 2007-03-20 | 0.18195 | 0.0065241
Vector Lines | 2007 | 2007-03-21 | 0.025066 | 0.00027462
Vector Lines | 2007 | 2007-03-22 | 0.2266 | 0.0025399
Vector Lines | 2007 | 2007-03-23 | 0.030215 | 0.00047905
Vector Lines | 2007 | 2007-03-24 | 0.076441 | 0.0018306
Vector Lines | 2007 | 2007-03-25 | 0.032386 | 0.00090462
Vector Lines | 2007 | 2007-03-26 | 0.016795 | 5.5294e-05
Vector Lines | 2007 | 2007-03-27 | 0.026672 | 0.00026726
Vector Lines | 2007 | 2007-03-28 | 0.65137 | 0.0063039
Vector Lines | 2007 | 2007-03-29 | 2.4552 | 0.029959
Vector Lines | 2007 | 2007-03-30 | 0.8988 | 0.015864
Vector Lines | 2007 | 2007-03-31 | 0.0063311 | 7.5041e-05
Vector Lines | 2008 | 2007-04-01 | 0.35872 | 0.0053076
Vector Lines | 2008 | 2007-04-02 | 0.50507 | 0.011164
Vector Lines | 2008 | 2007-04-03 | 0.0042749 | 2.1394e-05
Vector Lines | 2008 | 2007-04-04 | 0.1191 | 0.0022775
Vector Lines | 2008 | 2007-04-05 | 0.17237 | 0.0034891
Vector Lines | 2008 | 2007-04-06 | 0.08524 | 0.0016959
Vector Lines | 2008 | 2007-04-07 | 0.48787 | 0.011389
Vector Lines | 2008 | 2007-04-08 | 0.58888 | 0.0058774
Vector Lines | 2008 | 2007-04-09
Vector Lines | 2008 | 2007-04-10 | 0.093043 | 0.00091215
Vector Lines | 2008 | 2007-04-11 | 0.0084165 | 9.2382e-05
Vector Lines | 2008 | 2007-04-12 | 0.26418 | 0.0045627
Vector Lines | 2008 | 2007-04-13 | 0.50789 | 0.010789
Vector Lines | 2008 | 2007-04-14 | 0.064428 | 0.00030535
Vector Lines | 2008 | 2007-04-15 | 0.091207 | 0.0016668
Vector Lines | 2008 | 2007-04-16 | 0.16574 | 0.0025974
Vector Lines | 2008 | 2007-04-17 | 0.21133 | 0.0020694
Vector Lines | 2008 | 2007-04-18 | 0.014979 | 0.0039753
Vector Lines | 2008 | 2007-04-19 | 0.080564 | 0.00043663
Vector Lines | 2008 | 2007-04-20 | 0.15473 | 0.0021802
Vector Lines | 2008 | 2007-04-21 | 1.5975 | 0.021965
Vector Lines | 2008 | 2007-04-22
Vector Lines | 2008 | 2007-04-23 | 0.11079 | 0.0030165
Vector Lines | 2008 | 2007-04-24 | 0.70812 | 0.0090233
Vector Lines | 2008 | 2007-04-25 | 0.036912 | 0.00037244
Vector Lines | 2008 | 2007-04-26 | 0.001307 | 4.8622e-06
Vector Lines | 2008 | 2007-04-27 | 0.33545 | 0.0052755
Vector Lines | 2008 | 2007-04-28 | 0.78112 | 0.013824
Vector Lines | 2008 | 2007-04-29
Vector Lines | 2008 | 2007-04-30 | 0.051337 | 0.0046113
Vector Lines | 2008 | 2007-05-01 | 0.13004 | 0.003387
Vector Lines | 2008 | 2007-05-02 | 0.21172 | 0.0039928
Vector Lines | 2008 | 2007-05-03 | 0.0062236 | 5.3484e-05
Vector Lines | 2008 | 2007-05-04
Vector Lines | 2008 | 2007-05-05 | 0.14861 | 0.0022463
Vector Lines | 2008 | 2007-05-06 | 1.2771 | 0.010156
Vector Lines | 2008 | 2007-05-07 | 0.063983 | 0.0017912
Vector Lines | 2008 | 2007-05-08 | 0.026805 | 0.0002081
Vector Lines | 2008 | 2007-05-09 | 0.21329 | 0.0021501
Vector Lines | 2008 | 2007-05-10 | 0.63687 | 0.0044178
Vector Lines | 2008 | 2007-05-11 | 0.024737 | 0.00010697
Vector Lines | 2008 | 2007-05-12
Vector Lines | 2008 | 2007-05-13 | 0.026634 | 0.0006739
Vector Lines | 2008 | 2007-05-14 | 0.0082823 | 0.00022463
Vector Lines | 2008 | 2007-05-15 | 0.11636 | 0.002188
Vector Lines | 2008 | 2007-05-16 | 0.30564 | 0.0036301
Vector Lines | 2008 | 2007-05-17 | 0.30314 | 0.0042321
Vector Lines | 2008 | 2007-05-18 | 0.025268 | 0.00022561
Vector Lines | 2008 | 2007-05-19 | 0.13388 | 0.0028424
Vector Lines | 2008 | 2007-05-20 | 0.0057131 | 4.9594e-05
Vector Lines | 2008 | 2007-05-21 | 0.35448 | 0.0053834
Vector Lines | 2008 | 2007-05-22 | 0.1466 | 0.0026596
Vector Lines | 2008 | 2007-05-23 | 0.57079 | 0.017601
Vector Lines | 2008 | 2007-05-24 | 1.1324 | 0.034177
Vector Lines | 2008 | 2007-05-25 | 0.23462 | 0.0030476
Vector Lines | 2008 | 2007-05-26 | 0.14915 | 0.003989
Vector Lines | 2008 | 2007-05-27 | 0.5595 | 0.010462
Vector Lines | 2008 | 2007-05-28 | 0.16488 | 0.0071688
Vector Lines | 2008 | 2007-05-29 | 0.0020694 | 1.7504e-05
Vector Lines | 2008 | 2007-05-30 | 0.032637 | 0.0013799
Vector Lines | 2008 | 2007-05-31 | 0.22782 | 0.0021326
Vector Lines | 2008 | 2007-06-01 | 0.23463 | 0.0036428
Vector Lines | 2008 | 2007-06-02 | 0.035498 | 0.00034813
Vector Lines | 2008 | 2007-06-03 | 0.30076 | 0.002857
Vector Lines | 2008 | 2007-06-04 | 0.073235 | 0.00052706
Vector Lines | 2008 | 2007-06-05 | 0.28124 | 0.0023533
Vector Lines | 2008 | 2007-06-06 | 0.010705 | 0.00024894
Vector Lines | 2008 | 2007-06-07 | 0.0018613 | 2.8201e-05
Vector Lines | 2008 | 2007-06-08 | 0.15136 | 0.0051967
Vector Lines | 2008 | 2007-06-09 | 0.097911 | 0.00084408
Vector Lines | 2008 | 2007-06-10
Vector Lines | 2008 | 2007-06-11 | 0.13758 | 0.001834
Vector Lines | 2008 | 2007-06-12 | 0.01378 | 0.00010016
Vector Lines | 2008 | 2007-06-13 | 0.033938 | 0.00057374
Vector Lines | 2008 | 2007-06-14 | 0.23045 | 0.0038898
Vector Lines | 2008 | 2007-06-15 | 0.024651 | 0.00059319
Vector Lines | 2008 | 2007-06-16 | 0.12585 | 0.0066029
Vector Lines | 2008 | 2007-06-17 | 0.78044 | 0.010112
Vector Lines | 2008 | 2007-06-18 | 0.15505 | 0.0022347
Vector Lines | 2008 | 2007-06-19 | 3.4022 | 0.039523
Vector Lines | 2008 | 2007-06-20 | 1.0948 | 0.017885
Vector Lines | 2008 | 2007-06-21 | 0.13217 | 0.0011854
Vector Lines | 2008 | 2007-06-22 | 0.020669 | 0.00057666
Vector Lines | 2008 | 2007-06-23 | 0.58509 | 0.0083241
Vector Lines | 2008 | 2007-06-24 | 0.044736 | 0.00084408
Vector Lines | 2008 | 2007-06-25 | 0.8342 | 0.010361
Vector Lines | 2008 | 2007-06-26 | 0.089889 | 0.0013857
Vector Lines | 2008 | 2007-06-27 | 0.16168 | 0.0032061
Vector Lines | 2008 | 2007-06-28 | 0.10504 | 0.0012622
Vector Lines | 2008 | 2007-06-29 | 0.54767 | 0.0035056
Vector Lines | 2008 | 2007-06-30 | 0.31971 | 0.0039637
Vector Lines | 2008 | 2007-07-01 | 0.099431 | 0.00030243
Vector Lines | 2008 | 2007-07-02 | 0.17302 | 0.00098994
Vector Lines | 2008 | 2007-07-03 | 0.18023 | 0.0031429
Vector Lines | 2008 | 2007-07-04 | 0.25906 | 0.0056596
Vector Lines | 2008 | 2007-07-05 | 0.15469 | 0.0029941
Vector Lines | 2008 | 2007-07-06 | 0.19831 | 0.0027413
Vector Lines | 2008 | 2007-07-07 | 0.23849 | 0.0013536
Vector Lines | 2008 | 2007-07-08 | 0.42506 | 0.0051131
Vector Lines | 2008 | 2007-07-09 | 0.60321 | 0.0052026
Vector Lines | 2008 | 2007-07-10 | 3.3736 | 0.038927
Vector Lines | 2008 | 2007-07-11 | 3.3736 | 0.034321
Vector Lines | 2008 | 2007-07-12 | 0.65928 | 0.0058094
Vector Lines | 2008 | 2007-07-13 | 0.57111 | 0.0060447
Vector Lines | 2008 | 2007-07-14 | 0.75935 | 0.019151
Vector Lines | 2008 | 2007-07-15 | 0.32168 | 0.0065095
Vector Lines | 2008 | 2007-07-16 | 0.31931 | 0.0062781
Vector Lines | 2008 | 2007-07-17 | 0.28454 | 0.0045345
Vector Lines | 2008 | 2007-07-18 | 0.10396 | 0.0024486
Vector Lines | 2008 | 2007-07-19 | 0.045698 | 0.0005611
Vector Lines | 2008 | 2007-07-20 | 0.07614 | 0.00031507
Vector Lines | 2008 | 2007-07-21 | 0.55465 | 0.0089309
Vector Lines | 2008 | 2007-07-22 | 0.62086 | 0.0097672
Vector Lines | 2008 | 2007-07-23 | 0.75964 | 0.0099899
Vector Lines | 2008 | 2007-07-24 | 0.073509 | 0.00085964
Vector Lines | 2008 | 2007-07-25 | 0.016227 | 8.8492e-05
Vector Lines | 2008 | 2007-07-26 | 0.16475 | 0.0019916
Vector Lines | 2008 | 2007-07-27 | 0.28321 | 0.0039627
Vector Lines | 2008 | 2007-07-28 | 0.013917 | 6.3209e-05
Vector Lines | 2008 | 2007-07-29 | 0.74584 | 0.030177
Vector Lines | 2008 | 2007-07-30 | 0.11376 | 0.0055993
Vector Lines | 2008 | 2007-07-31 | 0.094626 | 0.0013828
Vector Lines | 2008 | 2007-08-01 | 0.06991 | 0.00088006
Vector Lines | 2008 | 2007-08-02 | 0.0024408 | 9.7244e-06
Vector Lines | 2008 | 2007-08-03 | 0.073688 | 0.0012992
Vector Lines | 2008 | 2007-08-04 | 0.28927 | 0.012527
Vector Lines | 2008 | 2007-08-05 | 0.0025984 | 7.7795e-06
Vector Lines | 2008 | 2007-08-06 | 0.71143 | 0.0083737
Vector Lines | 2008 | 2007-08-07 | 1.997 | 0.026135
Vector Lines | 2008 | 2007-08-08 | 0.08559 | 0.0016259
Vector Lines | 2008 | 2007-08-09 | 0.0054671 | 2.4311e-05
Vector Lines | 2008 | 2007-08-10 | 0.026299 | 0.00024117
Vector Lines | 2008 | 2007-08-11 | 0.40099 | 0.0039938
Vector Lines | 2008 | 2007-08-12 | 0.57158 | 0.0046308
Vector Lines | 2008 | 2007-08-13 | 0.062932 | 0.0014139
Vector Lines | 2008 | 2007-08-14 | 0.30658 | 0.002682
Vector Lines | 2008 | 2007-08-15 | 0.46978 | 0.0082833
Vector Lines | 2008 | 2007-08-16 | 1.2089 | 0.014279
Vector Lines | 2008 | 2007-08-17 | 0.22699 | 0.0033997
Vector Lines | 2008 | 2007-08-18
Vector Lines | 2008 | 2007-08-19 | 0.05781 | 0.00019449
Vector Lines | 2008 | 2007-08-20 | 0.014436 | 8.8492e-05
Vector Lines | 2008 | 2007-08-21 | 0.053113 | 0.00039773
Vector Lines | 2008 | 2007-08-22 | 0.082748 | 0.00036856
Vector Lines | 2008 | 2007-08-23 | 0.11208 | 0.0028055
Vector Lines | 2008 | 2007-08-24 | 0.061622 | 0.00052706
Vector Lines | 2008 | 2007-08-25
Vector Lines | 2008 | 2007-08-26
Vector Lines | 2008 | 2007-08-27 | 0.29037 | 0.0017893
Vector Lines | 2008 | 2007-08-28 | 0.2799 | 0.0050421
Vector Lines | 2008 | 2007-08-29 | 0.40803 | 0.0066476
Vector Lines | 2008 | 2007-08-30 | 0.00067585 | 2.9173e-06
Vector Lines | 2008 | 2007-08-31 | 0.060324 | 0.00098994
Vector Lines | 2008 | 2007-09-01 | 0.016788 | 0.00010113
Vector Lines | 2008 | 2007-09-02 | 0.12171 | 0.00062625
Vector Lines | 2008 | 2007-09-03 | 0.44755 | 0.0064473
Vector Lines | 2008 | 2007-09-04 | 0.040688 | 0.00011961
Vector Lines | 2008 | 2007-09-05 | 0.17986 | 0.021153
Vector Lines | 2008 | 2007-09-06 | 0.17383 | 0.001023
Vector Lines | 2008 | 2007-09-07 | 0.012025 | 0.00018379
Vector Lines | 2008 | 2007-09-08 | 0.051757 | 0.00019838
Vector Lines | 2008 | 2007-09-09 | 0.15654 | 0.0027102
Vector Lines | 2008 | 2007-09-10 | 0.023776 | 0.00012836
Vector Lines | 2008 | 2007-09-11 | 0.00515 | 1.7504e-05
Vector Lines | 2008 | 2007-09-12 | 0.06208 | 0.0011679
Vector Lines | 2008 | 2007-09-13 | 0.7063 | 0.024722
Vector Lines | 2008 | 2007-09-14 | 0.29954 | 0.0035173
Vector Lines | 2008 | 2007-09-15 | 0.18372 | 0.0025984
Vector Lines | 2008 | 2007-09-16 | 0.28806 | 0.0032693
Vector Lines | 2008 | 2007-09-17 | 0.030502 | 0.00035883
Vector Lines | 2008 | 2007-09-18 | 0.14477 | 0.0019711
Vector Lines | 2008 | 2007-09-19 | 0.06049 | 0.001307
Vector Lines | 2008 | 2007-09-20 | 0.50001 | 0.0053319
Vector Lines | 2008 | 2007-09-21
Vector Lines | 2008 | 2007-09-22 | 0.43503 | 0.0043021
Vector Lines | 2008 | 2007-09-23 | 0.57128 | 0.0073944
Vector Lines | 2008 | 2007-09-24 | 0.60373 | 0.016598
Vector Lines | 2008 | 2007-09-25 | 0.067862 | 0.00034133
Vector Lines | 2008 | 2007-09-26 | 0.098211 | 0.0023436
Vector Lines | 2008 | 2007-09-27 | 0.13343 | 0.0015141
Vector Lines | 2008 | 2007-09-28 | 0.029047 | 9.6272e-05
Vector Lines | 2008 | 2007-09-29 | 0.12756 | 0.0020528
Vector Lines | 2008 | 2007-09-30 | 0.021499 | 0.00054262
Vector Lines | 2008 | 2007-10-01 | 3.2972 | 0.039094
Vector Lines | 2008 | 2007-10-02 | 1.2408 | 0.010732
Vector Lines | 2008 | 2007-10-03 | 0.64541 | 0.007905
Vector Lines | 2008 | 2007-10-04 | 0.0050353 | 1.2642e-05
Vector Lines | 2008 | 2007-10-05 | 0.22053 | 0.0027462
Vector Lines | 2008 | 2007-10-06 | 0.28086 | 0.0035358
Vector Lines | 2008 | 2007-10-07 | 0.030963 | 0.00029757
Vector Lines | 2008 | 2007-10-08 | 0.078326 | 0.00090437
Vector Lines | 2008 | 2007-10-09 | 0.080977 | 0.0014023
Vector Lines | 2008 | 2007-10-10 | 0.080242 | 0.0034269
Vector Lines | 2008 | 2007-10-11 | 0.03282 | 0.00014587
Vector Lines | 2008 | 2007-10-12 | 0.024957 | 0.00029562
Vector Lines | 2008 | 2007-10-13 | 0.25339 | 0.0034872
Vector Lines | 2008 | 2007-10-14 | 0.35401 | 0.0040522
Vector Lines | 2008 | 2007-10-15 | 0.30181 | 0.0036116
Vector Lines | 2008 | 2007-10-16 | 0.28276 | 0.0038907
Vector Lines | 2008 | 2007-10-17 | 0.12824 | 0.0021676
Vector Lines | 2008 | 2007-10-18 | 0.3885 | 0.0042612
Vector Lines | 2008 | 2007-10-19 | 0.35654 | 0.0033481
Vector Lines | 2008 | 2007-10-20 | 0.78095 | 0.0047552
Vector Lines | 2008 | 2007-10-21 | 0.35147 | 0.0065037
Vector Lines | 2008 | 2007-10-22 | 0.018554 | 0.00051539
Vector Lines | 2008 | 2007-10-23 | 0.014689 | 5.5429e-05
Vector Lines | 2008 | 2007-10-24 | 0.018613 | 0.0074635
Vector Lines | 2008 | 2007-10-25 | 0.18193 | 0.0018826
Vector Lines | 2008 | 2007-10-26 | 0.21584 | 0.0016784
Vector Lines | 2008 | 2007-10-27 | 0.20544 | 0.0025595
Vector Lines | 2008 | 2007-10-28 | 0.22361 | 0.0027909
Vector Lines | 2008 | 2007-10-29 | 0.128 | 0.0044577
Vector Lines | 2008 | 2007-10-30 | 0.31591 | 0.0012544
Vector Lines | 2008 | 2007-10-31 | 0.27285 | 0.0026091
Vector Lines | 2008 | 2007-11-01 | 0.40655 | 0.0032995
Vector Lines | 2008 | 2007-11-02 | 0.1357 | 0.00089367
Vector Lines | 2008 | 2007-11-03 | 0.28376 | 0.0021219
Vector Lines | 2008 | 2007-11-04 | 0.0016862 | 9.9189e-05
Vector Lines | 2008 | 2007-11-05 | 0.1755 | 0.0014159
Vector Lines | 2008 | 2007-11-06 | 0.027473 | 0.0020441
Vector Lines | 2008 | 2007-11-07 | 0.0090252 | 2.8201e-05
Vector Lines | 2008 | 2007-11-08 | 0.2024 | 0.0014188
Vector Lines | 2008 | 2007-11-09 | 0.36541 | 0.0024107
Vector Lines | 2008 | 2007-11-10 | 0.057388 | 0.00070988
Vector Lines | 2008 | 2007-11-11 | 0.24179 | 0.0050645
Vector Lines | 2008 | 2007-11-12
Vector Lines | 2008 | 2007-11-13 | 0.20574 | 0.0027909
Vector Lines | 2008 | 2007-11-14 | 0.88052 | 0.0063617
Vector Lines | 2008 | 2007-11-15 | 0.28013 | 0.0035971
Vector Lines | 2008 | 2007-11-16 | 0.0012369 | 5.8346e-06
Vector Lines | 2008 | 2007-11-17 | 0.21803 | 0.0016104
Vector Lines | 2008 | 2007-11-18
Vector Lines | 2008 | 2007-11-19 | 0.015681 | 0.00012544
Vector Lines | 2008 | 2007-11-20 | 0.036577 | 0.00045219
Vector Lines | 2008 | 2007-11-21 | 0.11389 | 0.00047747
Vector Lines | 2008 | 2007-11-22 | 0.0068421 | 0.00011669
Vector Lines | 2008 | 2007-11-23 | 0.38331 | 0.0061487
Vector Lines | 2008 | 2007-11-24 | 0.084696 | 0.00032869
Vector Lines | 2008 | 2007-11-25 | 0.54476 | 0.0067137
Vector Lines | 2008 | 2007-11-26 | 0.034599 | 0.00020227
Vector Lines | 2008 | 2007-11-27 | 0.082098 | 0.0013789
Vector Lines | 2008 | 2007-11-28 | 0.010248 | 7.2933e-05
Vector Lines | 2008 | 2007-11-29 | 0.60793 | 0.010133
Vector Lines | 2008 | 2007-11-30 | 0.14146 | 0.00093743
Vector Lines | 2008 | 2007-12-01 | 0.011193 | 3.0146e-05
Vector Lines | 2008 | 2007-12-02 | 0.011547 | 0.00016143
Vector Lines | 2008 | 2007-12-03 | 0.17717 | 0.0021715
Vector Lines | 2008 | 2007-12-04 | 0.079952 | 0.00052804
Vector Lines | 2008 | 2007-12-05 | 0.085421 | 0.00083144
Vector Lines | 2008 | 2007-12-06 | 0.38278 | 0.0056752
Vector Lines | 2008 | 2007-12-07 | 0.28603 | 0.0014937
Vector Lines | 2008 | 2007-12-08 | 0.039464 | 0.0021083
Vector Lines | 2008 | 2007-12-09 | 0.28153 | 0.0027792
Vector Lines | 2008 | 2007-12-10 | 0.35762 | 0.0076064
Vector Lines | 2008 | 2007-12-11 | 0.18162 | 0.0029494
Vector Lines | 2008 | 2007-12-12 | 0.10231 | 0.0008538
Vector Lines | 2008 | 2007-12-13 | 0.045619 | 0.00041718
Vector Lines | 2008 | 2007-12-14 | 0.0046288 | 7.7795e-05
Vector Lines | 2008 | 2007-12-15 | 0.064016 | 0.00044149
Vector Lines | 2008 | 2007-12-16 | 0.2824 | 0.003106
Vector Lines | 2008 | 2007-12-17 | 0.1161 | 0.0016687
Vector Lines | 2008 | 2007-12-18 | 1.3447 | 0.015999
Vector Lines | 2008 | 2007-12-19 | 0.51666 | 0.0057471
Vector Lines | 2008 | 2007-12-20 | 0.11436 | 0.0012146
Vector Lines | 2008 | 2007-12-21 | 0.1446 | 0.00080713
Vector Lines | 2008 | 2007-12-22
Vector Lines | 2008 | 2007-12-23 | 0.018087 | 6.0291e-05
Vector Lines | 2008 | 2007-12-24 | 0.005753 | 0.0019177
Vector Lines | 2008 | 2007-12-25
Vector Lines | 2008 | 2007-12-26 | 0.023978 | 0.0003598
Vector Lines | 2008 | 2007-12-27 | 0.16144 | 0.0056596
Vector Lines | 2008 | 2007-12-28 | 0.12856 | 0.0014509
Vector Lines | 2008 | 2007-12-29 | 0.15546 | 0.0021977
Vector Lines | 2008 | 2007-12-30
Vector Lines | 2008 | 2007-12-31 | 2.2664 | 0.024939
Vector Lines | 2008 | 2008-01-01 | 0.369 | 0.0083863
Vector Lines | 2008 | 2008-01-02 | 0.094313 | 0.018327
Vector Lines | 2008 | 2008-01-03 | 0.27977 | 0.003668
Vector Lines | 2008 | 2008-01-04 | 0.00013906 | 1.9449e-06
Vector Lines | 2008 | 2008-01-05 | 0.19511 | 0.0035494
Vector Lines | 2008 | 2008-01-06 | 0.04904 | 0.00011086
Vector Lines | 2008 | 2008-01-07 | 0.024128 | 0.00073906
Vector Lines | 2008 | 2008-01-08 | 0.32312 | 0.0060525
Vector Lines | 2008 | 2008-01-09 | 0.39651 | 0.005786
Vector Lines | 2008 | 2008-01-10 | 0.0012058 | 9.7244e-06
Vector Lines | 2008 | 2008-01-11 | 0.000635 | 5.8346e-06
Vector Lines | 2008 | 2008-01-12 | 0.059146 | 0.0019079
Vector Lines | 2008 | 2008-01-13 | 0.42956 | 0.0038246
Vector Lines | 2008 | 2008-01-14 | 0.23322 | 0.0036525
Vector Lines | 2008 | 2008-01-15 | 0.0013225 | 1.7504e-05
Vector Lines | 2008 | 2008-01-16 | 0.0015345 | 1.9449e-06
Vector Lines | 2008 | 2008-01-17 | 0.0038975 | 5.8346e-06
Vector Lines | 2008 | 2008-01-18 | 0.26619 | 0.0026431
Vector Lines | 2008 | 2008-01-19 | 0.17674 | 0.0032402
Vector Lines | 2008 | 2008-01-20 | 1.1825 | 0.014354
Vector Lines | 2008 | 2008-01-21 | 0.62878 | 0.006494
Vector Lines | 2008 | 2008-01-22 | 0.077865 | 0.0020178
Vector Lines | 2008 | 2008-01-23 | 0.34176 | 0.0017407
Vector Lines | 2008 | 2008-01-24 | 0.016917 | 0.00012058
Vector Lines | 2008 | 2008-01-25 | 0.0019031 | 1.0697e-05
Vector Lines | 2008 | 2008-01-26 | 0.046745 | 0.00086936
Vector Lines | 2008 | 2008-01-27 | 0.071355 | 0.00014878
Vector Lines | 2008 | 2008-01-28 | 0.056246 | 0.00080324
Vector Lines | 2008 | 2008-01-29 | 0.15597 | 0.0023757
Vector Lines | 2008 | 2008-01-30 | 0.19316 | 0.0024272
Vector Lines | 2008 | 2008-01-31 | 0.27962 | 0.0024496
Vector Lines | 2008 | 2008-02-01 | 0.06119 | 0.0011679
Vector Lines | 2008 | 2008-02-02 | 0.34223 | 0.0014412
Vector Lines | 2008 | 2008-02-03 | 0.13996 | 0.0016687
Vector Lines | 2008 | 2008-02-04 | 0.02718 | 0.00018574
Vector Lines | 2008 | 2008-02-05 | 0.01939 | 5.0567e-05
Vector Lines | 2008 | 2008-02-06 | 0.080117 | 0.00075461
Vector Lines | 2008 | 2008-02-07 | 0.009316 | 0.00011669
Vector Lines | 2008 | 2008-02-08 | 0.029815 | 0.00013614
Vector Lines | 2008 | 2008-02-09 | 0.0019293 | 3.8898e-06
Vector Lines | 2008 | 2008-02-10 | 2.5058 | 0.025645
Vector Lines | 2008 | 2008-02-11 | 0.56652 | 0.0029582
Vector Lines | 2008 | 2008-02-12 | 0.36504 | 0.025143
Vector Lines | 2008 | 2008-02-13 | 0.10939 | 0.0031215
Vector Lines | 2008 | 2008-02-14 | 0.032069 | 0.001376
Vector Lines | 2008 | 2008-02-15 | 0.016328 | 6.5154e-05
Vector Lines | 2008 | 2008-02-16 | 0.0046347 | 3.987e-05
Vector Lines | 2008 | 2008-02-17 | 0.82493 | 0.0076813
Vector Lines | 2008 | 2008-02-18 | 0.047526 | 0.00065154
Vector Lines | 2008 | 2008-02-19 | 0.014019 | 0.0001624
Vector Lines | 2008 | 2008-02-20 | 0.030754 | 0.0006457
Vector Lines | 2008 | 2008-02-21 | 0.24678 | 0.0041533
Vector Lines | 2008 | 2008-02-22 | 1.0897 | 0.027412
Vector Lines | 2008 | 2008-02-23 | 3.3741 | 0.03867
Vector Lines | 2008 | 2008-02-24 | 0.40215 | 0.010977
Vector Lines | 2008 | 2008-02-25 | 0.54171 | 0.0091234
Vector Lines | 2008 | 2008-02-26 | 0.031523 | 0.015128
Vector Lines | 2008 | 2008-02-27 | 0.81385 | 0.012014
Vector Lines | 2008 | 2008-02-28 | 0.31398 | 0.0037371
Vector Lines | 2008 | 2008-02-29 | 0.10025 | 0.00069238
Vector Lines | 2008 | 2008-03-01 | 1.1791 | 0.010726
Vector Lines | 2008 | 2008-03-02 | 0.29503 | 0.0016668
Vector Lines | 2008 | 2008-03-03 | 0.25043 | 0.003599
Vector Lines | 2008 | 2008-03-04 | 0.00067487 | 3.8898e-06
Vector Lines | 2008 | 2008-03-05 | 0.016461 | 0.00024894
Vector Lines | 2008 | 2008-03-06 | 0.25106 | 0.012926
Vector Lines | 2008 | 2008-03-07 | 0.036644 | 0.00022269
Vector Lines | 2008 | 2008-03-08 | 0.13944 | 0.0036661
Vector Lines | 2008 | 2008-03-09 | 0.019137 | 0.00013322
Vector Lines | 2008 | 2008-03-10 | 0.27918 | 0.017008
Vector Lines | 2008 | 2008-03-11 | 0.018 | 0.0054466
Vector Lines | 2008 | 2008-03-12 | 0.052212 | 0.0010833
Vector Lines | 2008 | 2008-03-13 | 0.44259 | 0.0051695
Vector Lines | 2008 | 2008-03-14 | 0.10583 | 0.0012875
Vector Lines | 2008 | 2008-03-15 | 0.0056275 | 3.7925e-05
Vector Lines | 2008 | 2008-03-16 | 0.012087 | 0.00025283
Vector Lines | 2008 | 2008-03-17 | 0.036634 | 0.00057374
Vector Lines | 2008 | 2008-03-18 | 0.019472 | 0.00064084
Vector Lines | 2008 | 2008-03-19 | 0.040218 | 0.00012836
Vector Lines | 2008 | 2008-03-20 | 0.19486 | 0.0013955
Vector Lines | 2008 | 2008-03-21
Vector Lines | 2008 | 2008-03-22 | 0.11559 | 0.0048136
Vector Lines | 2008 | 2008-03-23 | 0.25141 | 0.0029552
Vector Lines | 2008 | 2008-03-24
Vector Lines | 2008 | 2008-03-25 | 0.25019 | 0.0034162
Vector Lines | 2008 | 2008-03-26 | 0.013225 | 0.0020003
Vector Lines | 2008 | 2008-03-27 | 0.093554 | 0.0023212
Vector Lines | 2008 | 2008-03-28 | 0.12476 | 0.0018136
Vector Lines | 2008 | 2008-03-29 | 0.0018204 | 3.8898e-05
Vector Lines | 2008 | 2008-03-30 | 0.065459 | 0.0018029
Vector Lines | 2008 | 2008-03-31 | 0.0028726 | 1.3614e-05
Vector Lines | 2009 | 2008-04-01 | 0.64169 | 0.004034
Vector Lines | 2009 | 2008-04-02 | 0.0075447 | 0.00011256
Vector Lines | 2009 | 2008-04-03 | 0.032215 | 0.00023379
Vector Lines | 2009 | 2008-04-04 | 0.0059553 | 1.7318e-05
Vector Lines | 2009 | 2008-04-05 | 0.038108 | 0.00076582
Vector Lines | 2009 | 2008-04-06 | 0.27169 | 0.005658
Vector Lines | 2009 | 2008-04-07 | 0.12459 | 0.0021907
Vector Lines | 2009 | 2008-04-08 | 0.41958 | 0.0073773
Vector Lines | 2009 | 2008-04-09 | 0.13899 | 0.0012536
Vector Lines | 2009 | 2008-04-10 | 0.59162 | 0.0051375
Vector Lines | 2009 | 2008-04-11 | 0.036313 | 0.00015971
Vector Lines | 2009 | 2008-04-12 | 0.019196 | 0.0001116
Vector Lines | 2009 | 2008-04-13 | 0.27752 | 0.0050105
Vector Lines | 2009 | 2008-04-14 | 0.27874 | 0.0015778
Vector Lines | 2009 | 2008-04-15 | 1.5569 | 0.017094
Vector Lines | 2009 | 2008-04-16 | 0.051514 | 0.00030017
Vector Lines | 2009 | 2008-04-17 | 0.88414 | 0.0076909
Vector Lines | 2009 | 2008-04-18 | 0.07417 | 0.001675
Vector Lines | 2009 | 2008-04-19 | 0.061069 | 0.00079276
Vector Lines | 2009 | 2008-04-20
Vector Lines | 2009 | 2008-04-21 | 0.69746 | 0.038999
Vector Lines | 2009 | 2008-04-22 | 0.11508 | 0.0016009
Vector Lines | 2009 | 2008-04-23 | 0.10442 | 0.0015634
Vector Lines | 2009 | 2008-04-24 | 0.00078698 | 3.8483e-06
Vector Lines | 2009 | 2008-04-25
Vector Lines | 2009 | 2008-04-26 | 0.40296 | 0.0037319
Vector Lines | 2009 | 2008-04-27 | 0.016302 | 0.00018472
Vector Lines | 2009 | 2008-04-28 | 0.011322 | 4.5218e-05
Vector Lines | 2009 | 2008-04-29 | 0.81746 | 0.0069347
Vector Lines | 2009 | 2008-04-30 | 0.55359 | 0.0099672
Vector Lines | 2009 | 2008-05-01 | 0.19119 | 0.0084875
Vector Lines | 2009 | 2008-05-02 | 0.2313 | 0.0031633
Vector Lines | 2009 | 2008-05-03 | 0.087827 | 0.0015547
Vector Lines | 2009 | 2008-05-04 | 0.41169 | 0.0047719
Vector Lines | 2009 | 2008-05-05 | 1.4861 | 0.017937
Vector Lines | 2009 | 2008-05-06 | 0.034766 | 0.00017125
Vector Lines | 2009 | 2008-05-07 | 0.72626 | 0.0077255
Vector Lines | 2009 | 2008-05-08 | 0.14984 | 0.0032403
Vector Lines | 2009 | 2008-05-09 | 0.31472 | 0.0031229
Vector Lines | 2009 | 2008-05-10 | 0.016146 | 0.00026554
Vector Lines | 2009 | 2008-05-11 | 0.11249 | 0.00078121
Vector Lines | 2009 | 2008-05-12 | 0.013498 | 0.0026996
Vector Lines | 2009 | 2008-05-13 | 0.30551 | 0.0070809
Vector Lines | 2009 | 2008-05-14 | 0.065281 | 0.002054
Vector Lines | 2009 | 2008-05-15 | 0.49022 | 0.0052588
Vector Lines | 2009 | 2008-05-16 | 0.039272 | 0.00012315
Vector Lines | 2009 | 2008-05-17 | 0.00025495 | 9.6208e-07
Vector Lines | 2009 | 2008-05-18 | 0.1602 | 0.00039445
Vector Lines | 2009 | 2008-05-19 | 0.059624 | 0.0044044
Vector Lines | 2009 | 2008-05-20 | 0.030508 | 0.0036809
Vector Lines | 2009 | 2008-05-21 | 0.12217 | 0.00022801
Vector Lines | 2009 | 2008-05-22 | 0.23811 | 0.0048547
Vector Lines | 2009 | 2008-05-23 | 0.033028 | 0.00023667
Vector Lines | 2009 | 2008-05-24 | 0.041564 | 0.00046565
Vector Lines | 2009 | 2008-05-25 | 0.15874 | 0.0028314
Vector Lines | 2009 | 2008-05-26 | 0.25276 | 0.012474
Vector Lines | 2009 | 2008-05-27 | 0.072352 | 0.00023475
Vector Lines | 2009 | 2008-05-28 | 0.23741 | 0.0039157
Vector Lines | 2009 | 2008-05-29 | 0.015846 | 5.0028e-05
Vector Lines | 2009 | 2008-05-30 | 0.70742 | 0.0051635
Vector Lines | 2009 | 2008-05-31 | 0.23746 | 0.0010467
Vector Lines | 2009 | 2008-06-01 | 0.1975 | 0.0034116
Vector Lines | 2009 | 2008-06-02 | 0.0077005 | 9.4284e-05
Vector Lines | 2009 | 2008-06-03 | 0.15675 | 0.0011122
Vector Lines | 2009 | 2008-06-04 | 0.16104 | 0.00052818
Vector Lines | 2009 | 2008-06-05 | 0.4233 | 0.004237
Vector Lines | 2009 | 2008-06-06 | 0.1351 | 0.00083894
Vector Lines | 2009 | 2008-06-07 | 0.0025649 | 0.0025649
Vector Lines | 2009 | 2008-06-08 | 0.067368 | 0.00096882
Vector Lines | 2009 | 2008-06-09 | 0.0010525 | 0.00010487
Vector Lines | 2009 | 2008-06-10 | 0.0041629 | 6.1573e-05
Vector Lines | 2009 | 2008-06-11 | 0.20554 | 0.0021002
Vector Lines | 2009 | 2008-06-12 | 0.039759 | 0.00049259
Vector Lines | 2009 | 2008-06-13 | 0.067803 | 0.0015249
Vector Lines | 2009 | 2008-06-14 | 0.27117 | 0.0031066
Vector Lines | 2009 | 2008-06-15 | 0.081163 | 0.0021079
Vector Lines | 2009 | 2008-06-16 | 0.51221 | 0.0086703
Vector Lines | 2009 | 2008-06-17 | 0.18103 | 0.0021801
Vector Lines | 2009 | 2008-06-18 | 0.00033288 | 1.9242e-06
Vector Lines | 2009 | 2008-06-19 | 0.09623 | 0.0016336
Vector Lines | 2009 | 2008-06-20 | 0.013996 | 0.0032288
Vector Lines | 2009 | 2008-06-21 | 0.06637 | 0.00090147
Vector Lines | 2009 | 2008-06-22 | 0.46154 | 0.0085067
Vector Lines | 2009 | 2008-06-23 | 0.094625 | 0.0029632
Vector Lines | 2009 | 2008-06-24 | 1.2366 | 0.019434
Vector Lines | 2009 | 2008-06-25 | 1.2877 | 0.023537
Vector Lines | 2009 | 2008-06-26 | 0.71933 | 0.030629
Vector Lines | 2009 | 2008-06-27 | 3.3899 | 0.039005
Vector Lines | 2009 | 2008-06-28 | 1.4065 | 0.012605
Vector Lines | 2009 | 2008-06-29 | 0.012809 | 6.3498e-05
Vector Lines | 2009 | 2008-06-30 | 0.0088733 | 9.9095e-05
Vector Lines | 2009 | 2008-07-01 | 0.4724 | 0.005456
Vector Lines | 2009 | 2008-07-02 | 0.047794 | 0.00027612
Vector Lines | 2009 | 2008-07-03 | 0.24418 | 0.0067211
Vector Lines | 2009 | 2008-07-04 | 0.079147 | 0.0029777
Vector Lines | 2009 | 2008-07-05 | 1.1935 | 0.038749
Vector Lines | 2009 | 2008-07-06 | 0.039343 | 0.00025399
Vector Lines | 2009 | 2008-07-07 | 0.17736 | 0.0016971
Vector Lines | 2009 | 2008-07-08 | 0.036628 | 0.00052241
Vector Lines | 2009 | 2008-07-09 | 0.48075 | 0.0056147
Vector Lines | 2009 | 2008-07-10 | 0.10031 | 0.0012632
Vector Lines | 2009 | 2008-07-11 | 0.16412 | 0.0019607
Vector Lines | 2009 | 2008-07-12 | 0.4149 | 0.0040908
Vector Lines | 2009 | 2008-07-13 | 0.25911 | 0.0027891
Vector Lines | 2009 | 2008-07-14 | 0.055206 | 0.0018626
Vector Lines | 2009 | 2008-07-15 | 0.019774 | 0.0022157
Vector Lines | 2009 | 2008-07-16 | 0.0071137 | 1.828e-05
Vector Lines | 2009 | 2008-07-17 | 0.16356 | 0.0021012
Vector Lines | 2009 | 2008-07-18 | 0.006318 | 2.4052e-05
Vector Lines | 2009 | 2008-07-19 | 0.23742 | 0.0049846
Vector Lines | 2009 | 2008-07-20 | 0.3001 | 0.0028497
Vector Lines | 2009 | 2008-07-21 | 0.14393 | 0.0022301
Vector Lines | 2009 | 2008-07-22 | 0.0090397 | 0.00015393
Vector Lines | 2009 | 2008-07-23 | 0.15779 | 0.0033846
Vector Lines | 2009 | 2008-07-24 | 0.32626 | 0.0034818
Vector Lines | 2009 | 2008-07-25 | 0.003502 | 9.6208e-06
Vector Lines | 2009 | 2008-07-26 | 3.3736 | 0.038927
Vector Lines | 2009 | 2008-07-27 | 3.3736 | 0.011397
Vector Lines | 2009 | 2008-07-28 | 0.16561 | 0.0022878
Vector Lines | 2009 | 2008-07-29 | 0.11285 | 0.001497
Vector Lines | 2009 | 2008-07-30 | 3.3736 | 0.033598
Vector Lines | 2009 | 2008-07-31 | 0.84729 | 0.007206
Vector Lines | 2009 | 2008-08-01 | 0.87126 | 0.0048528
Vector Lines | 2009 | 2008-08-02 | 0.34293 | 0.0037502
Vector Lines | 2009 | 2008-08-03 | 0.7145 | 0.014301
Vector Lines | 2009 | 2008-08-04 | 0.037839 | 0.0029844
Vector Lines | 2009 | 2008-08-05 | 0.0051298 | 2.309e-05
Vector Lines | 2009 | 2008-08-06 | 0.42051 | 0.0070492
Vector Lines | 2009 | 2008-08-07
Vector Lines | 2009 | 2008-08-08 | 0.064953 | 0.00075908
Vector Lines | 2009 | 2008-08-09 | 0.11342 | 0.0032057
Vector Lines | 2009 | 2008-08-10 | 0.27638 | 0.0018126
Vector Lines | 2009 | 2008-08-11 | 0.2356 | 0.0042765
Vector Lines | 2009 | 2008-08-12 | 0.0017318 | 1.1545e-05
Vector Lines | 2009 | 2008-08-13 | 0.16862 | 0.0037473
Vector Lines | 2009 | 2008-08-14 | 0.47988 | 0.0078958
Vector Lines | 2009 | 2008-08-15 | 0.42713 | 0.0069751
Vector Lines | 2009 | 2008-08-16 | 0.046748 | 0.00089474
Vector Lines | 2009 | 2008-08-17 | 1.0733 | 0.015495
Vector Lines | 2009 | 2008-08-18 | 0.3381 | 0.0080931
Vector Lines | 2009 | 2008-08-19 | 0.054785 | 0.00057533
Vector Lines | 2009 | 2008-08-20 | 0.033631 | 0.00019338
Vector Lines | 2009 | 2008-08-21 | 0.10311 | 0.00033288
Vector Lines | 2009 | 2008-08-22 | 0.0057109 | 0.00010198
Vector Lines | 2009 | 2008-08-23 | 0.00047912 | 1.9242e-06
Vector Lines | 2009 | 2008-08-24 | 0.76509 | 0.010693
Vector Lines | 2009 | 2008-08-25 | 0.061183 | 0.0017394
Vector Lines | 2009 | 2008-08-26 | 0.41071 | 0.0042572
Vector Lines | 2009 | 2008-08-27 | 0.18632 | 0.0025159
Vector Lines | 2009 | 2008-08-28 | 0.055209 | 0.0004897
Vector Lines | 2009 | 2008-08-29 | 0.30522 | 0.0037964
Vector Lines | 2009 | 2008-08-30 | 0.0034019 | 0.0002588
Vector Lines | 2009 | 2008-08-31 | 0.31142 | 0.003958
Vector Lines | 2009 | 2008-09-01 | 0.15478 | 0.00033288
Vector Lines | 2009 | 2008-09-02 | 0.072306 | 0.0033211
Vector Lines | 2009 | 2008-09-03 | 0.0462 | 0.0018212
Vector Lines | 2009 | 2008-09-04 | 0.49798 | 0.005355
Vector Lines | 2009 | 2008-09-05 | 0.0002944 | 3.2711e-05
Vector Lines | 2009 | 2008-09-06 | 0.29893 | 0.0018443
Vector Lines | 2009 | 2008-09-07 | 0.36507 | 0.0032211
Vector Lines | 2009 | 2008-09-08 | 0.27813 | 0.0050615
Vector Lines | 2009 | 2008-09-09 | 0.060124 | 0.00092168
Vector Lines | 2009 | 2008-09-10 | 0.025535 | 0.00014816
Vector Lines | 2009 | 2008-09-11 | 0.24839 | 0.0038657
Vector Lines | 2009 | 2008-09-12 | 0.58219 | 0.0051
Vector Lines | 2009 | 2008-09-13 | 0.0019165 | 0.00020204
Vector Lines | 2009 | 2008-09-14 | 0.80815 | 0.021345
Vector Lines | 2009 | 2008-09-15 | 0.022565 | 0.00068693
Vector Lines | 2009 | 2008-09-16 | 0.075802 | 0.0017597
Vector Lines | 2009 | 2008-09-17 | 0.12118 | 0.0018222
Vector Lines | 2009 | 2008-09-18
Vector Lines | 2009 | 2008-09-19 | 0.0056426 | 2.2128e-05
Vector Lines | 2009 | 2008-09-20 | 0.014894 | 8.3701e-05
Vector Lines | 2009 | 2008-09-21 | 0.56253 | 0.0032345
Vector Lines | 2009 | 2008-09-22 | 0.20576 | 0.002917
Vector Lines | 2009 | 2008-09-23 | 0.063948 | 0.00073503
Vector Lines | 2009 | 2008-09-24 | 0.036034 | 0.00014431
Vector Lines | 2009 | 2008-09-25 | 0.0096699 | 3.5597e-05
Vector Lines | 2009 | 2008-09-26
Vector Lines | 2009 | 2008-09-27 | 0.00018953 | 9.6208e-07
Vector Lines | 2009 | 2008-09-28 | 0.20399 | 0.0039599
Vector Lines | 2009 | 2008-09-29 | 0.0052645 | 3.4635e-05
Vector Lines | 2009 | 2008-09-30 | 0.0084134 | 7.6967e-05
Vector Lines | 2009 | 2008-10-01 | 0.032064 | 0.00029632
Vector Lines | 2009 | 2008-10-02 | 0.76827 | 0.0070963
Vector Lines | 2009 | 2008-10-03 | 0.00033673 | 3.3673e-05
Vector Lines | 2009 | 2008-10-04 | 0.057794 | 0.00055608
Vector Lines | 2009 | 2008-10-05 | 0.10324 | 0.0022032
Vector Lines | 2009 | 2008-10-06 | 0.072527 | 0.00049836
Vector Lines | 2009 | 2008-10-07 | 1.2254 | 0.010795
Vector Lines | 2009 | 2008-10-08 | 0.043368 | 0.00036655
Vector Lines | 2009 | 2008-10-09 | 0.25569 | 0.0028151
Vector Lines | 2009 | 2008-10-10
Vector Lines | 2009 | 2008-10-11 | 0.45746 | 0.004822
Vector Lines | 2009 | 2008-10-12 | 0.011089 | 0.00064941
Vector Lines | 2009 | 2008-10-13 | 0.77713 | 0.012199
Vector Lines | 2009 | 2008-10-14 | 0.01495 | 9.7171e-05
Vector Lines | 2009 | 2008-10-15 | 0.10891 | 0.0014075
Vector Lines | 2009 | 2008-10-16 | 0.0012603 | 9.6208e-06
Vector Lines | 2009 | 2008-10-17 | 0.34238 | 0.0035366
Vector Lines | 2009 | 2008-10-18 | 0.38166 | 0.0040792
Vector Lines | 2009 | 2008-10-19
Vector Lines | 2009 | 2008-10-20 | 0.016631 | 0.00038676
Vector Lines | 2009 | 2008-10-21 | 0.14108 | 0.0022715
Vector Lines | 2009 | 2008-10-22 | 0.18413 | 0.0016683
Vector Lines | 2009 | 2008-10-23 | 0.86465 | 0.0076005
Vector Lines | 2009 | 2008-10-24 | 0.42822 | 0.0025476
Vector Lines | 2009 | 2008-10-25 | 0.14 | 0.0018992
Vector Lines | 2009 | 2008-10-26 | 0.28896 | 0.010702
Vector Lines | 2009 | 2008-10-27 | 0.25023 | 0.001853
Vector Lines | 2009 | 2008-10-28 | 0.11298 | 0.0038272
Vector Lines | 2009 | 2008-10-29 | 0.22819 | 0.0028064
Vector Lines | 2009 | 2008-10-30 | 0.037229 | 0.0004618
Vector Lines | 2009 | 2008-10-31 | 0.0023379 | 2.8863e-05
Vector Lines | 2009 | 2008-11-01 | 0.73102 | 0.0065172
Vector Lines | 2009 | 2008-11-02 | 0.26021 | 0.0029671
Vector Lines | 2009 | 2008-11-03 | 0.0069491 | 0.00010872
Vector Lines | 2009 | 2008-11-04 | 0.27184 | 0.0042216
Vector Lines | 2009 | 2008-11-05 | 0.25936 | 0.0030056
Vector Lines | 2009 | 2008-11-06 | 0.22413 | 0.0037492
Vector Lines | 2009 | 2008-11-07 | 0.0095266 | 0.00012122
Vector Lines | 2009 | 2008-11-08 | 0.06016 | 0.00090628
Vector Lines | 2009 | 2008-11-09 | 0.00088319 | 7.6005e-05
Vector Lines | 2009 | 2008-11-10 | 0.00047527 | 3.8483e-06
Vector Lines | 2009 | 2008-11-11 | 0.17191 | 0.003171
Vector Lines | 2009 | 2008-11-12 | 0.18329 | 0.0050634
Vector Lines | 2009 | 2008-11-13 | 0.16691 | 0.0028333
Vector Lines | 2009 | 2008-11-14 | 0.45417 | 0.0061371
Vector Lines | 2009 | 2008-11-15 | 0.19932 | 0.0032134
Vector Lines | 2009 | 2008-11-16 | 0.25614 | 0.004135
Vector Lines | 2009 | 2008-11-17 | 0.5444 | 0.0081642
Vector Lines | 2009 | 2008-11-18 | 0.080952 | 0.00047719
Vector Lines | 2009 | 2008-11-19 | 0.0050279 | 3.7521e-05
Vector Lines | 2009 | 2008-11-20 | 0.14254 | 0.0030729
Vector Lines | 2009 | 2008-11-21 | 0.044656 | 0.00097171
Vector Lines | 2009 | 2008-11-22 | 0.24481 | 0.0025505
Vector Lines | 2009 | 2008-11-23 | 0.041018 | 0.00032807
Vector Lines | 2009 | 2008-11-24 | 0.20094 | 0.021297
Vector Lines | 2009 | 2008-11-25 | 0.72281 | 0.0096016
Vector Lines | 2009 | 2008-11-26 | 0.13526 | 0.0018241
Vector Lines | 2009 | 2008-11-27 | 0.00026938 | 1.9242e-06
Vector Lines | 2009 | 2008-11-28 | 0.28169 | 0.0038214
Vector Lines | 2009 | 2008-11-29 | 0.049097 | 0.00023667
Vector Lines | 2009 | 2008-11-30 | 0.012694 | 5.099e-05
Vector Lines | 2009 | 2008-12-01 | 0.19439 | 0.0036405
Vector Lines | 2009 | 2008-12-02 | 0.016404 | 0.00022417
Vector Lines | 2009 | 2008-12-03 | 0.25383 | 0.0023071
Vector Lines | 2009 | 2008-12-04 | 0.11022 | 0.0026361
Vector Lines | 2009 | 2008-12-05 | 0.020029 | 0.014781
Vector Lines | 2009 | 2008-12-06
Vector Lines | 2009 | 2008-12-07 | 0.095423 | 0.00082739
Vector Lines | 2009 | 2008-12-08 | 0.22014 | 0.0013767
Vector Lines | 2009 | 2008-12-09 | 0.83965 | 0.0090994
Vector Lines | 2009 | 2008-12-10 | 0.11745 | 0.0053781
Vector Lines | 2009 | 2008-12-11 | 0.22534 | 0.0032461
Vector Lines | 2009 | 2008-12-12 | 0.09744 | 0.00050702
Vector Lines | 2009 | 2008-12-13 | 0.085762 | 0.0063151
Vector Lines | 2009 | 2008-12-14 | 0.4243 | 0.0051674
Vector Lines | 2009 | 2008-12-15 | 0.23991 | 0.007435
Vector Lines | 2009 | 2008-12-16 | 0.26827 | 0.02309
Vector Lines | 2009 | 2008-12-17 | 0.15816 | 0.0011891
Vector Lines | 2009 | 2008-12-18 | 0.2268 | 0.0032586
Vector Lines | 2009 | 2008-12-19 | 0.18631 | 0.0018607
Vector Lines | 2009 | 2008-12-20 | 0.28498 | 0.0035549
Vector Lines | 2009 | 2008-12-21 | 0.0059842 | 1.9242e-05
Vector Lines | 2009 | 2008-12-22 | 0.016538 | 0.0038916
Vector Lines | 2009 | 2008-12-23 | 0.029549 | 0.00047335
Vector Lines | 2009 | 2008-12-24 | 0.074743 | 0.00038964
Vector Lines | 2009 | 2008-12-25 | 0.24092 | 0.0019973
Vector Lines | 2009 | 2008-12-26 | 0.03826 | 0.00065037
Vector Lines | 2009 | 2008-12-27 | 0.44922 | 0.0058418
Vector Lines | 2009 | 2008-12-28 | 0.13735 | 0.0028439
Vector Lines | 2009 | 2008-12-29 | 0.045997 | 0.0010968
Vector Lines | 2009 | 2008-12-30 | 0.11557 | 0.0017779
Vector Lines | 2009 | 2008-12-31 | 0.078218 | 0.0022599
Vector Lines | 2009 | 2009-01-01 | 0.38999 | 0.0048778
Vector Lines | 2009 | 2009-01-02 | 0.18612 | 0.0021801
Vector Lines | 2009 | 2009-01-03 | 0.0065229 | 5.7725e-05
Vector Lines | 2009 | 2009-01-04 | 0.17132 | 0.0066499
Vector Lines | 2009 | 2009-01-05 | 0.10551 | 0.00096786
Vector Lines | 2009 | 2009-01-06 | 0.56631 | 0.0086665
Vector Lines | 2009 | 2009-01-07 | 0.012417 | 6.446e-05
Vector Lines | 2009 | 2009-01-08 | 0.12611 | 0.0017654
Vector Lines | 2009 | 2009-01-09 | 0.28909 | 0.0031306
Vector Lines | 2009 | 2009-01-10 | 0.41591 | 0.0046315
Vector Lines | 2009 | 2009-01-11 | 0.56657 | 0.0052732
Vector Lines | 2009 | 2009-01-12 | 0.027706 | 0.00035982
Vector Lines | 2009 | 2009-01-13 | 0.016055 | 0.0005734
Vector Lines | 2009 | 2009-01-14 | 0.17281 | 0.0042159
Vector Lines | 2009 | 2009-01-15 | 0.0037435 | 2.0204e-05
Vector Lines | 2009 | 2009-01-16
Vector Lines | 2009 | 2009-01-17 | 0.1327 | 0.0020896
Vector Lines | 2009 | 2009-01-18 | 0.11234 | 0.0013036
Vector Lines | 2009 | 2009-01-19 | 0.23585 | 0.0028786
Vector Lines | 2009 | 2009-01-20 | 0.099568 | 0.00047527
Vector Lines | 2009 | 2009-01-21 | 0.0070732 | 0.00075235
Vector Lines | 2009 | 2009-01-22 | 0.23689 | 0.0048585
Vector Lines | 2009 | 2009-01-23 | 0.27865 | 0.002513
Vector Lines | 2009 | 2009-01-24 | 0.35687 | 0.0044294
Vector Lines | 2009 | 2009-01-25 | 0.039174 | 0.00067731
Vector Lines | 2009 | 2009-01-26 | 0.038447 | 0.00072541
Vector Lines | 2009 | 2009-01-27
Vector Lines | 2009 | 2009-01-28 | 0.029829 | 0.00024726
Vector Lines | 2009 | 2009-01-29 | 0.010477 | 3.1749e-05
Vector Lines | 2009 | 2009-01-30 | 0.081065 | 0.0014855
Vector Lines | 2009 | 2009-01-31 | 0.62919 | 0.0014258
Vector Lines | 2009 | 2009-02-01 | 0.094432 | 0.0031527
Vector Lines | 2009 | 2009-02-02 | 0.00058014 | 3.8483e-06
Vector Lines | 2009 | 2009-02-03 | 0.057834 | 0.0017298
Vector Lines | 2009 | 2009-02-04 | 0.034198 | 0.00026457
Vector Lines | 2009 | 2009-02-05 | 0.029003 | 0.00051375
Vector Lines | 2009 | 2009-02-06 | 0.8909 | 0.019095
Vector Lines | 2009 | 2009-02-07 | 0.1147 | 0.0015201
Vector Lines | 2009 | 2009-02-08 | 0.020213 | 0.00010198
Vector Lines | 2009 | 2009-02-09 | 0.23134 | 0.0051606
Vector Lines | 2009 | 2009-02-10 | 0.051308 | 0.00035405
Vector Lines | 2009 | 2009-02-11 | 0.30701 | 0.0042553
Vector Lines | 2009 | 2009-02-12 | 0.12389 | 0.0029449
Vector Lines | 2009 | 2009-02-13 | 0.97424 | 0.01949
Vector Lines | 2009 | 2009-02-14 | 0.36804 | 0.0051125
Vector Lines | 2009 | 2009-02-15 | 0.0011545 | 3.8483e-05
Vector Lines | 2009 | 2009-02-16 | 0.18505 | 0.0034
Vector Lines | 2009 | 2009-02-17 | 0.013254 | 8.0815e-05
Vector Lines | 2009 | 2009-02-18 | 0.1866 | 0.0021214
Vector Lines | 2009 | 2009-02-19 | 0.3872 | 0.0055329
Vector Lines | 2009 | 2009-02-20 | 1.4267 | 0.015147
Vector Lines | 2009 | 2009-02-21 | 0.11224 | 0.0027785
Vector Lines | 2009 | 2009-02-22 | 0.3604 | 0.0055089
Vector Lines | 2009 | 2009-02-23 | 0.075148 | 0.0038772
Vector Lines | 2009 | 2009-02-24 | 0.15944 | 0.0025389
Vector Lines | 2009 | 2009-02-25 | 0.021261 | 6.446e-05
Vector Lines | 2009 | 2009-02-26 | 0.10615 | 0.0017635
Vector Lines | 2009 | 2009-02-27 | 0.15247 | 0.02132
Vector Lines | 2009 | 2009-02-28 | 2.7181 | 0.021749
Vector Lines | 2009 | 2009-03-01 | 0.012034 | 0.0001193
Vector Lines | 2009 | 2009-03-02 | 0.077019 | 0.0012199
Vector Lines | 2009 | 2009-03-03 | 0.65099 | 0.025234
Vector Lines | 2009 | 2009-03-04
Vector Lines | 2009 | 2009-03-05 | 1.8305 | 0.036267
Vector Lines | 2009 | 2009-03-06 | 1.338 | 0.016865
Vector Lines | 2009 | 2009-03-07 | 0.18934 | 0.0019954
Vector Lines | 2009 | 2009-03-08 | 0.23395 | 0.0057648
Vector Lines | 2009 | 2009-03-09 | 0.5564 | 0.0034972
Vector Lines | 2009 | 2009-03-10 | 0.090282 | 0.00035405
Vector Lines | 2009 | 2009-03-11 | 1.0652 | 0.038927
Vector Lines | 2009 | 2009-03-12 | 0.22618 | 0.0040812
Vector Lines | 2009 | 2009-03-13 | 0.26434 | 0.0042428
Vector Lines | 2009 | 2009-03-14 | 0.077949 | 0.0014537
Vector Lines | 2009 | 2009-03-15 | 0.78088 | 0.01022
Vector Lines | 2009 | 2009-03-16
Vector Lines | 2009 | 2009-03-17 | 0.078335 | 0.00077544
Vector Lines | 2009 | 2009-03-18 | 0.00077352 | 1.9242e-06
Vector Lines | 2009 | 2009-03-19 | 0.19181 | 0.0036117
Vector Lines | 2009 | 2009-03-20 | 0.39617 | 0.011822
Vector Lines | 2009 | 2009-03-21 | 0.17724 | 0.0032461
Vector Lines | 2009 | 2009-03-22 | 0.062853 | 0.00095439
Vector Lines | 2009 | 2009-03-23
Vector Lines | 2009 | 2009-03-24 | 0.047267 | 0.00076389
Vector Lines | 2009 | 2009-03-25 | 0.12906 | 0.001243
Vector Lines | 2009 | 2009-03-26
Vector Lines | 2009 | 2009-03-27 | 0.037169 | 0.00061766
Vector Lines | 2009 | 2009-03-28 | 0.00033096 | 3.8483e-06
Vector Lines | 2009 | 2009-03-29 | 0.0011834 | 3.8483e-06
Vector Lines | 2009 | 2009-03-30 | 0.0023032 | 5.7725e-06
Vector Lines | 2009 | 2009-03-31 | 0.0066672 | 0.0007408
Vector Lines | 2010 | 2009-04-01 | 0.10656 | 0.0020377
Vector Lines | 2010 | 2009-04-02 | 0.056528 | 0.0089112
Vector Lines | 2010 | 2009-04-03 | 0.08692 | 0.0020338
Vector Lines | 2010 | 2009-04-04
Vector Lines | 2010 | 2009-04-05 | 0.049941 | 0.00080058
Vector Lines | 2010 | 2009-04-06 | 0.14752 | 0.0069612
Vector Lines | 2010 | 2009-04-07 | 0.064277 | 0.005423
Vector Lines | 2010 | 2009-04-08 | 0.32215 | 0.0043708
Vector Lines | 2010 | 2009-04-09 | 0.030685 | 9.4354e-05
Vector Lines | 2010 | 2009-04-10 | 0.37825 | 0.0055335
Vector Lines | 2010 | 2009-04-11 | 0.020846 | 0.00018299
Vector Lines | 2010 | 2009-04-12 | 0.32986 | 0.0029526
Vector Lines | 2010 | 2009-04-13
Vector Lines | 2010 | 2009-04-14 | 0.25137 | 0.0031785
Vector Lines | 2010 | 2009-04-15 | 0.05332 | 0.0012619
Vector Lines | 2010 | 2009-04-16 | 0.26137 | 0.0043384
Vector Lines | 2010 | 2009-04-17 | 0.0010293 | 1.1437e-05
Vector Lines | 2010 | 2009-04-18 | 0.0031651 | 2.1921e-05
Vector Lines | 2010 | 2009-04-19 | 0.16597 | 0.0013305
Vector Lines | 2010 | 2009-04-20 | 1.6729 | 0.025959
Vector Lines | 2010 | 2009-04-21 | 0.11012 | 0.0052304
Vector Lines | 2010 | 2009-04-22 | 0.1727 | 0.001198
Vector Lines | 2010 | 2009-04-23 | 0.23668 | 0.0017117
Vector Lines | 2010 | 2009-04-24 | 0.12261 | 0.0063522
Vector Lines | 2010 | 2009-04-25 | 0.39909 | 0.0032061
Vector Lines | 2010 | 2009-04-26 | 0.33275 | 0.0042945
Vector Lines | 2010 | 2009-04-27 | 0.099945 | 0.0015221
Vector Lines | 2010 | 2009-04-28 | 0.20078 | 0.0012657
Vector Lines | 2010 | 2009-04-29 | 0.0064752 | 5.5278e-05
Vector Lines | 2010 | 2009-04-30 | 0.028736 | 0.00023922
Vector Lines | 2010 | 2009-05-01 | 0.037745 | 0.00040887
Vector Lines | 2010 | 2009-05-02 | 0.0062045 | 0.00017727
Vector Lines | 2010 | 2009-05-03 | 0.0023274 | 1.0484e-05
Vector Lines | 2010 | 2009-05-04 | 0.47344 | 0.0042164
Vector Lines | 2010 | 2009-05-05 | 0.043363 | 0.00030117
Vector Lines | 2010 | 2009-05-06 | 0.078659 | 0.00062426
Vector Lines | 2010 | 2009-05-07 | 0.17613 | 0.0030555
Vector Lines | 2010 | 2009-05-08 | 0.15651 | 0.0017784
Vector Lines | 2010 | 2009-05-09 | 0.13601 | 0.014668
Vector Lines | 2010 | 2009-05-10 | 0.017333 | 7.9105e-05
Vector Lines | 2010 | 2009-05-11 | 0.053017 | 0.0023846
Vector Lines | 2010 | 2009-05-12 | 0.16663 | 0.0014887
Vector Lines | 2010 | 2009-05-13 | 0.067169 | 0.0026105
Vector Lines | 2010 | 2009-05-14 | 0.12376 | 0.002458
Vector Lines | 2010 | 2009-05-15 | 0.081636 | 0.0013515
Vector Lines | 2010 | 2009-05-16 | 0.10004 | 0.0018089
Vector Lines | 2010 | 2009-05-17 | 0.01123 | 4.0029e-05
Vector Lines | 2010 | 2009-05-18 | 0.021982 | 0.0002011
Vector Lines | 2010 | 2009-05-19 | 0.21345 | 0.0048159
Vector Lines | 2010 | 2009-05-20 | 0.13265 | 0.0014677
Vector Lines | 2010 | 2009-05-21 | 0.10948 | 0.0041354
Vector Lines | 2010 | 2009-05-22 | 0.72891 | 0.0068735
Vector Lines | 2010 | 2009-05-23 | 0.11057 | 0.0019481
Vector Lines | 2010 | 2009-05-24 | 0.0004975 | 3.8123e-06
Vector Lines | 2010 | 2009-05-25 | 0.014529 | 0.00027639
Vector Lines | 2010 | 2009-05-26 | 0.0046929 | 0.002112
Vector Lines | 2010 | 2009-05-27 | 0.0017613 | 2.0968e-05
Vector Lines | 2010 | 2009-05-28 | 0.039993 | 0.00027067
Vector Lines | 2010 | 2009-05-29 | 0.0062826 | 0.0023865
Vector Lines | 2010 | 2009-05-30
Vector Lines | 2010 | 2009-05-31 | 0.32967 | 0.0031432
Vector Lines | 2010 | 2009-06-01 | 0.02514 | 0.0019195
Vector Lines | 2010 | 2009-06-02 | 0.057502 | 0.00097308
Vector Lines | 2010 | 2009-06-03 | 0.11918 | 0.0018785
Vector Lines | 2010 | 2009-06-04 | 0.348 | 0.0037227
Vector Lines | 2010 | 2009-06-05 | 0.17246 | 0.006518
Vector Lines | 2010 | 2009-06-06 | 0.016961 | 0.00054897
Vector Lines | 2010 | 2009-06-07 | 0.0002783 | 0.00013915
Vector Lines | 2010 | 2009-06-08 | 0.045277 | 0.00020586
Vector Lines | 2010 | 2009-06-09 | 0.11142 | 0.00076055
Vector Lines | 2010 | 2009-06-10 | 0.1011 | 0.0029822
Vector Lines | 2010 | 2009-06-11 | 0.023023 | 0.00019729
Vector Lines | 2010 | 2009-06-12 | 0.10916 | 0.00048702
Vector Lines | 2010 | 2009-06-13
Vector Lines | 2010 | 2009-06-14 | 0.032368 | 0.0001868
Vector Lines | 2010 | 2009-06-15 | 0.21406 | 0.0034501
Vector Lines | 2010 | 2009-06-16 | 0.3974 | 0.0043365
Vector Lines | 2010 | 2009-06-17 | 0.052482 | 0.00067287
Vector Lines | 2010 | 2009-06-18 | 0.03234 | 0.00064904
Vector Lines | 2010 | 2009-06-19 | 0.080796 | 0.00032309
Vector Lines | 2010 | 2009-06-20 | 0.011224 | 7.3386e-05
Vector Lines | 2010 | 2009-06-21 | 0.96789 | 0.0066105
Vector Lines | 2010 | 2009-06-22 | 0.0084833 | 0.00010579
Vector Lines | 2010 | 2009-06-23 | 0.035086 | 0.00020586
Vector Lines | 2010 | 2009-06-24 | 0.006458 | 9.9119e-05
Vector Lines | 2010 | 2009-06-25 | 0.16931 | 0.0015325
Vector Lines | 2010 | 2009-06-26 | 0.26825 | 0.0043851
Vector Lines | 2010 | 2009-06-27 | 0.067182 | 0.003635
Vector Lines | 2010 | 2009-06-28 | 0.0073272 | 7.6246e-06
Vector Lines | 2010 | 2009-06-29 | 0.23189 | 0.0028211
Vector Lines | 2010 | 2009-06-30 | 0.017004 | 5.909e-05
Vector Lines | 2010 | 2009-07-01 | 0.083634 | 0.0010417
Vector Lines | 2010 | 2009-07-02 | 0.10876 | 0.0015897
Vector Lines | 2010 | 2009-07-03 | 0.12507 | 0.0012323
Vector Lines | 2010 | 2009-07-04 | 0.22777 | 0.014883
Vector Lines | 2010 | 2009-07-05 | 0.0018632 | 2.0968e-05
Vector Lines | 2010 | 2009-07-06 | 0.092118 | 0.0011675
Vector Lines | 2010 | 2009-07-07 | 0.020728 | 0.00014582
Vector Lines | 2010 | 2009-07-08 | 0.35348 | 0.0056908
Vector Lines | 2010 | 2009-07-09 | 0.32638 | 0.003046
Vector Lines | 2010 | 2009-07-10 | 0.0035225 | 0.00010674
Vector Lines | 2010 | 2009-07-11 | 0.39462 | 0.0045642
Vector Lines | 2010 | 2009-07-12 | 0.81949 | 0.0087387
Vector Lines | 2010 | 2009-07-13 | 0.25093 | 0.0016555
Vector Lines | 2010 | 2009-07-14 | 0.80177 | 0.0057337
Vector Lines | 2010 | 2009-07-15 | 0.57964 | 0.0079257
Vector Lines | 2010 | 2009-07-16 | 0.14994 | 0.001666
Vector Lines | 2010 | 2009-07-17 | 0.0084042 | 3.431e-05
Vector Lines | 2010 | 2009-07-18 | 0.51777 | 0.0026095
Vector Lines | 2010 | 2009-07-19 | 0.021046 | 7.6246e-05
Vector Lines | 2010 | 2009-07-20 | 0.72477 | 0.011044
Vector Lines | 2010 | 2009-07-21 | 0.019847 | 9.7213e-05
Vector Lines | 2010 | 2009-07-22 | 0.018989 | 6.0996e-05
Vector Lines | 2010 | 2009-07-23 | 0.3698 | 0.0087835
Vector Lines | 2010 | 2009-07-24 | 0.19208 | 0.0017069
Vector Lines | 2010 | 2009-07-25 | 0.071153 | 0.00084918
Vector Lines | 2010 | 2009-07-26 | 0.072718 | 0.0020138
Vector Lines | 2010 | 2009-07-27 | 0.018871 | 0.00020586
Vector Lines | 2010 | 2009-07-28 | 0.015647 | 6.5762e-05
Vector Lines | 2010 | 2009-07-29 | 0.035454 | 0.00035454
Vector Lines | 2010 | 2009-07-30 | 0.093232 | 0.0033786
Vector Lines | 2010 | 2009-07-31 | 0.022165 | 6.8621e-05
Vector Lines | 2010 | 2009-08-01 | 0.0666 | 0.0012609
Vector Lines | 2010 | 2009-08-02 | 0.18396 | 0.0026724
Vector Lines | 2010 | 2009-08-03 | 0.08551 | 0.00097499
Vector Lines | 2010 | 2009-08-04 | 0.021366 | 7.0527e-05
Vector Lines | 2010 | 2009-08-05 | 0.027558 | 0.00013819
Vector Lines | 2010 | 2009-08-06 | 0.062329 | 0.0028258
Vector Lines | 2010 | 2009-08-07 | 0.16045 | 0.0018918
Vector Lines | 2010 | 2009-08-08 | 0.38977 | 0.0058509
Vector Lines | 2010 | 2009-08-09 | 0.20843 | 0.0036169
Vector Lines | 2010 | 2009-08-10 | 0.16603 | 0.0030203
Vector Lines | 2010 | 2009-08-11 | 0.69686 | 0.011499
Vector Lines | 2010 | 2009-08-12 | 0.072599 | 0.00068526
Vector Lines | 2010 | 2009-08-13 | 0.069574 | 0.0010217
Vector Lines | 2010 | 2009-08-14 | 0.086482 | 0.00095021
Vector Lines | 2010 | 2009-08-15 | 0.42665 | 0.012167
Vector Lines | 2010 | 2009-08-16 | 0.013689 | 7.8152e-05
Vector Lines | 2010 | 2009-08-17 | 0.6583 | 0.0090465
Vector Lines | 2010 | 2009-08-18 | 0.18 | 0.0032347
Vector Lines | 2010 | 2009-08-19 | 0.068407 | 0.00025923
Vector Lines | 2010 | 2009-08-20 | 0.19747 | 0.010481
Vector Lines | 2010 | 2009-08-21 | 0.1276 | 0.0015011
Vector Lines | 2010 | 2009-08-22 | 0.058974 | 0.00047558
Vector Lines | 2010 | 2009-08-23 | 0.086735 | 0.0014696
Vector Lines | 2010 | 2009-08-24 | 0.004975 | 6.0996e-05
Vector Lines | 2010 | 2009-08-25 | 0.0060873 | 3.5264e-05
Vector Lines | 2010 | 2009-08-26 | 0.11588 | 0.0012371
Vector Lines | 2010 | 2009-08-27 | 0.027566 | 7.9105e-05
Vector Lines | 2010 | 2009-08-28 | 0.11843 | 0.00059567
Vector Lines | 2010 | 2009-08-29 | 0.11919 | 0.0011237
Vector Lines | 2010 | 2009-08-30 | 0.39708 | 0.0021882
Vector Lines | 2010 | 2009-08-31 | 0.39562 | 0.0065095
Vector Lines | 2010 | 2009-09-01 | 0.11261 | 0.0018833
Vector Lines | 2010 | 2009-09-02 | 0.13999 | 0.00069765
Vector Lines | 2010 | 2009-09-03 | 0.1154 | 0.0015916
Vector Lines | 2010 | 2009-09-04 | 0.15063 | 0.002438
Vector Lines | 2010 | 2009-09-05 | 0.00057184 | 1.9061e-06
Vector Lines | 2010 | 2009-09-06 | 0.36478 | 0.0083527
Vector Lines | 2010 | 2009-09-07 | 0.022217 | 0.00011532
Vector Lines | 2010 | 2009-09-08 | 0.02122 | 0.0014039
Vector Lines | 2010 | 2009-09-09 | 0.131 | 0.0034206
Vector Lines | 2010 | 2009-09-10 | 0.079791 | 0.00022588
Vector Lines | 2010 | 2009-09-11 | 0.088759 | 0.018326
Vector Lines | 2010 | 2009-09-12 | 0.31045 | 0.0030193
Vector Lines | 2010 | 2009-09-13 | 0.19976 | 0.0020844
Vector Lines | 2010 | 2009-09-14 | 0.10072 | 0.0035321
Vector Lines | 2010 | 2009-09-15
Vector Lines | 2010 | 2009-09-16 | 0.077313 | 0.0011437
Vector Lines | 2010 | 2009-09-17 | 0.029916 | 0.00010293
Vector Lines | 2010 | 2009-09-18 | 0.0022569 | 2.0968e-05
Vector Lines | 2010 | 2009-09-19 | 0.042092 | 0.00034692
Vector Lines | 2010 | 2009-09-20 | 0.00045843 | 4.7653e-06
Vector Lines | 2010 | 2009-09-21 | 0.01598 | 0.00022016
Vector Lines | 2010 | 2009-09-22 | 0.15017 | 0.0020053
Vector Lines | 2010 | 2009-09-23 | 0.67074 | 0.0035473
Vector Lines | 2010 | 2009-09-24 | 0.045875 | 0.00042983
Vector Lines | 2010 | 2009-09-25 | 0.032057 | 0.0003717
Vector Lines | 2010 | 2009-09-26 | 0.086785 | 0.0003717
Vector Lines | 2010 | 2009-09-27 | 0.06389 | 0.0018175
Vector Lines | 2010 | 2009-09-28 | 0.30862 | 0.0060739
Vector Lines | 2010 | 2009-09-29 | 0.11026 | 0.0051218
Vector Lines | 2010 | 2009-09-30 | 0.2867 | 0.0069326
Vector Lines | 2010 | 2009-10-01 | 0.86416 | 0.0058156
Vector Lines | 2010 | 2009-10-02 | 0.09326 | 0.00035645
Vector Lines | 2010 | 2009-10-03 | 0.22203 | 0.0033739
Vector Lines | 2010 | 2009-10-04 | 0.062501 | 0.0012266
Vector Lines | 2010 | 2009-10-05
Vector Lines | 2010 | 2009-10-06 | 0.40072 | 0.0053658
Vector Lines | 2010 | 2009-10-07 | 0.047738 | 0.00056136
Vector Lines | 2010 | 2009-10-08 | 0.023556 | 0.00016679
Vector Lines | 2010 | 2009-10-09 | 0.36637 | 0.0059815
Vector Lines | 2010 | 2009-10-10 | 0.23831 | 0.0068087
Vector Lines | 2010 | 2009-10-11 | 0.19574 | 0.0025066
Vector Lines | 2010 | 2009-10-12 | 0.0072624 | 5.3372e-05
Vector Lines | 2010 | 2009-10-13 | 0.18661 | 0.0039085
Vector Lines | 2010 | 2009-10-14 | 0.14577 | 0.0021844
Vector Lines | 2010 | 2009-10-15 | 0.083664 | 0.00037742
Vector Lines | 2010 | 2009-10-16 | 0.013104 | 0.00013057
Vector Lines | 2010 | 2009-10-17 | 0.082218 | 0.00055945
Vector Lines | 2010 | 2009-10-18 | 0.10093 | 0.00022492
Vector Lines | 2010 | 2009-10-19 | 0.37558 | 0.0076293
Vector Lines | 2010 | 2009-10-20 | 0.054574 | 0.00046224
Vector Lines | 2010 | 2009-10-21 | 0.28636 | 0.0065161
Vector Lines | 2010 | 2009-10-22 | 0.017133 | 0.00053277
Vector Lines | 2010 | 2009-10-23 | 0.014748 | 0.000203
Vector Lines | 2010 | 2009-10-24 | 0.38637 | 0.0024303
Vector Lines | 2010 | 2009-10-25 | 0.017212 | 8.1964e-05
Vector Lines | 2010 | 2009-10-26 | 0.064549 | 0.002436
Vector Lines | 2010 | 2009-10-27 | 0.12867 | 0.0038656
Vector Lines | 2010 | 2009-10-28 | 0.014691 | 6.4809e-05
Vector Lines | 2010 | 2009-10-29 | 0.41486 | 0.0064075
Vector Lines | 2010 | 2009-10-30 | 0.12147 | 0.0019252
Vector Lines | 2010 | 2009-10-31 | 0.82453 | 0.0029335
Vector Lines | 2010 | 2009-11-01 | 0.011547 | 4.956e-05
Vector Lines | 2010 | 2009-11-02 | 0.018276 | 0.00017918
Vector Lines | 2010 | 2009-11-03 | 0.32221 | 0.0032633
Vector Lines | 2010 | 2009-11-04 | 0.051802 | 0.0087292
Vector Lines | 2010 | 2009-11-05 | 0.032885 | 0.00031547
Vector Lines | 2010 | 2009-11-06 | 0.03852 | 0.0001401
Vector Lines | 2010 | 2009-11-07 | 0.20238 | 0.0089379
Vector Lines | 2010 | 2009-11-08 | 0.0078571 | 4.8607e-05
Vector Lines | 2010 | 2009-11-09 | 0.028932 | 0.00057375
Vector Lines | 2010 | 2009-11-10 | 0.10695 | 0.0041954
Vector Lines | 2010 | 2009-11-11 | 0.045581 | 0.00092352
Vector Lines | 2010 | 2009-11-12 | 0.16817 | 0.0023646
Vector Lines | 2010 | 2009-11-13 | 0.013558 | 0.00014105
Vector Lines | 2010 | 2009-11-14
Vector Lines | 2010 | 2009-11-15 | 0.0070336 | 3.5264e-05
Vector Lines | 2010 | 2009-11-16 | 0.10122 | 0.0032566
Vector Lines | 2010 | 2009-11-17 | 0.034751 | 0.00038981
Vector Lines | 2010 | 2009-11-18 | 0.20066 | 0.0028116
Vector Lines | 2010 | 2009-11-19 | 0.013065 | 0.00072052
Vector Lines | 2010 | 2009-11-20 | 0.46523 | 0.0020767
Vector Lines | 2010 | 2009-11-21 | 0.12981 | 0.0018223
Vector Lines | 2010 | 2009-11-22 | 0.16542 | 0.0018118
Vector Lines | 2010 | 2009-11-23 | 0.12165 | 0.0018099
Vector Lines | 2010 | 2009-11-24 | 0.090789 | 0.00054897
Vector Lines | 2010 | 2009-11-25 | 0.015995 | 0.0002316
Vector Lines | 2010 | 2009-11-26 | 0.20064 | 0.0016021
Vector Lines | 2010 | 2009-11-27 | 0.00032404 | 1.9061e-06
Vector Lines | 2010 | 2009-11-28 | 0.022105 | 0.00064237
Vector Lines | 2010 | 2009-11-29 | 0.26209 | 0.0030136
Vector Lines | 2010 | 2009-11-30 | 0.19457 | 0.0024818
Vector Lines | 2010 | 2009-12-01 | 0.3414 | 0.0062893
Vector Lines | 2010 | 2009-12-02 | 0.5212 | 0.0072738
Vector Lines | 2010 | 2009-12-03 | 0.053942 | 0.00030117
Vector Lines | 2010 | 2009-12-04 | 0.33367 | 0.0061721
Vector Lines | 2010 | 2009-12-05 | 0.23671 | 0.0015764
Vector Lines | 2010 | 2009-12-06 | 0.2878 | 0.0028659
Vector Lines | 2010 | 2009-12-07 | 0.49999 | 0.0038933
Vector Lines | 2010 | 2009-12-08 | 0.33586 | 0.0034291
Vector Lines | 2010 | 2009-12-09 | 0.21756 | 0.0043365
Vector Lines | 2010 | 2009-12-10 | 0.085862 | 0.00054897
Vector Lines | 2010 | 2009-12-11 | 0.44848 | 0.0077599
Vector Lines | 2010 | 2009-12-12 | 0.98103 | 0.0058919
Vector Lines | 2010 | 2009-12-13
Vector Lines | 2010 | 2009-12-14 | 0.54063 | 0.0084938
Vector Lines | 2010 | 2009-12-15 | 0.17774 | 0.0029955
Vector Lines | 2010 | 2009-12-16 | 0.40614 | 0.0051313
Vector Lines | 2010 | 2009-12-17 | 0.05844 | 0.00065762
Vector Lines | 2010 | 2009-12-18 | 0.021022 | 9.626e-05
Vector Lines | 2010 | 2009-12-19 | 0.19775 | 0.0018737
Vector Lines | 2010 | 2009-12-20 | 0.019344 | 0.00020682
Vector Lines | 2010 | 2009-12-21 | 0.064588 | 0.00055183
Vector Lines | 2010 | 2009-12-22 | 0.13215 | 0.000325
Vector Lines | 2010 | 2009-12-23
Vector Lines | 2010 | 2009-12-24 | 0.2819 | 0.0051332
Vector Lines | 2010 | 2009-12-25
Vector Lines | 2010 | 2009-12-26 | 0.013192 | 0.00012771
Vector Lines | 2010 | 2009-12-27 | 0.062725 | 0.00091876
Vector Lines | 2010 | 2009-12-28 | 0.0035092 | 7.8152e-05
Vector Lines | 2010 | 2009-12-29 | 0.19122 | 0.0074549
Vector Lines | 2010 | 2009-12-30 | 0.2388 | 0.0050656
Vector Lines | 2010 | 2009-12-31 | 0.001056 | 6.0996e-05
Vector Lines | 2010 | 2010-01-01
Vector Lines | 2010 | 2010-01-02 | 0.12931 | 0.001807
Vector Lines | 2010 | 2010-01-03 | 0.074332 | 0.00138
Vector Lines | 2010 | 2010-01-04 | 0.71818 | 0.0081945
Vector Lines | 2010 | 2010-01-05 | 0.0066334 | 0.00022111
Vector Lines | 2010 | 2010-01-06 | 0.056762 | 0.00020586
Vector Lines | 2010 | 2010-01-07 | 0.040115 | 0.00012295
Vector Lines | 2010 | 2010-01-08 | 0.21291 | 0.0042726
Vector Lines | 2010 | 2010-01-09 | 0.011311 | 8.7682e-05
Vector Lines | 2010 | 2010-01-10 | 0.079191 | 0.0005442
Vector Lines | 2010 | 2010-01-11 | 0.34379 | 0.0028573
Vector Lines | 2010 | 2010-01-12 | 0.0064618 | 2.8592e-05
Vector Lines | 2010 | 2010-01-13 | 0.092875 | 0.000467
Vector Lines | 2010 | 2010-01-14 | 0.34389 | 0.0028449
Vector Lines | 2010 | 2010-01-15 | 0.081387 | 0.00059472
Vector Lines | 2010 | 2010-01-16 | 0.22414 | 0.0049541
Vector Lines | 2010 | 2010-01-17 | 0.00028592 | 1.9061e-06
Vector Lines | 2010 | 2010-01-18 | 0.032192 | 0.00013248
Vector Lines | 2010 | 2010-01-19 | 0.067546 | 0.00055469
Vector Lines | 2010 | 2010-01-20 | 0.015261 | 6.0996e-05
Vector Lines | 2010 | 2010-01-21 | 0.4234 | 0.0072042
Vector Lines | 2010 | 2010-01-22 | 0.37332 | 0.004223
Vector Lines | 2010 | 2010-01-23 | 0.031049 | 0.00026686
Vector Lines | 2010 | 2010-01-24 | 0.10314 | 0.00191
Vector Lines | 2010 | 2010-01-25 | 0.65944 | 0.0069279
Vector Lines | 2010 | 2010-01-26 | 0.0073291 | 0.0001239
Vector Lines | 2010 | 2010-01-27 | 0.73256 | 0.0082822
Vector Lines | 2010 | 2010-01-28 | 0.42292 | 0.0029202
Vector Lines | 2010 | 2010-01-29 | 0.026926 | 0.00030117
Vector Lines | 2010 | 2010-01-30 | 0.0028363 | 4.1935e-05
Vector Lines | 2010 | 2010-01-31 | 0.058877 | 0.0016736
Vector Lines | 2010 | 2010-02-01 | 1.2546 | 0.013745
Vector Lines | 2010 | 2010-02-02 | 0.15593 | 0.00020586
Vector Lines | 2010 | 2010-02-03 | 0.19934 | 0.0021053
Vector Lines | 2010 | 2010-02-04
Vector Lines | 2010 | 2010-02-05 | 0.077498 | 0.0016831
Vector Lines | 2010 | 2010-02-06 | 0.07026 | 0.00013534
Vector Lines | 2010 | 2010-02-07 | 0.20432 | 0.0013762
Vector Lines | 2010 | 2010-02-08 | 0.042944 | 0.00087873
Vector Lines | 2010 | 2010-02-09 | 0.46656 | 0.0089341
Vector Lines | 2010 | 2010-02-10 | 0.528 | 0.0052695
Vector Lines | 2010 | 2010-02-11 | 0.33092 | 0.0024494
Vector Lines | 2010 | 2010-02-12 | 0.04972 | 0.00053562
Vector Lines | 2010 | 2010-02-13 | 0.20614 | 0.003188
Vector Lines | 2010 | 2010-02-14 | 0.10477 | 0.003229
Vector Lines | 2010 | 2010-02-15 | 0.16188 | 0.0069917
Vector Lines | 2010 | 2010-02-16 | 0.073455 | 0.0016069
Vector Lines | 2010 | 2010-02-17 | 0.020968 | 5.2419e-05
Vector Lines | 2010 | 2010-02-18 | 0.38416 | 0.0090484
Vector Lines | 2010 | 2010-02-19 | 0.24029 | 0.0033014
Vector Lines | 2010 | 2010-02-20 | 0.075037 | 0.0013705
Vector Lines | 2010 | 2010-02-21 | 0.10292 | 0.0027248
Vector Lines | 2010 | 2010-02-22 | 0.0093896 | 6.5762e-05
Vector Lines | 2010 | 2010-02-23 | 0.22166 | 0.0025923
Vector Lines | 2010 | 2010-02-24 | 0.17668 | 0.0026
Vector Lines | 2010 | 2010-02-25 | 0.42862 | 0.017253
Vector Lines | 2010 | 2010-02-26 | 0.013236 | 5.3372e-05
Vector Lines | 2010 | 2010-02-27 | 0.00037551 | 2.8592e-06
Vector Lines | 2010 | 2010-02-28 | 0.26462 | 0.0056336
Vector Lines | 2010 | 2010-03-01 | 0.085643 | 0.00089207
Vector Lines | 2010 | 2010-03-02 | 0.088875 | 0.0011523
Vector Lines | 2010 | 2010-03-03 | 0.098849 | 0.0013791
Vector Lines | 2010 | 2010-03-04 | 0.91568 | 0.010055
Vector Lines | 2010 | 2010-03-05 | 0.2579 | 0.0035283
Vector Lines | 2010 | 2010-03-06 | 0.44947 | 0.004853
Vector Lines | 2010 | 2010-03-07 | 0.13418 | 0.00070813
Vector Lines | 2010 | 2010-03-08 | 0.0081926 | 0.00011627
Vector Lines | 2010 | 2010-03-09 | 0.07786 | 0.0014067
Vector Lines | 2010 | 2010-03-10 | 0.055622 | 0.00029545
Vector Lines | 2010 | 2010-03-11 | 0.11202 | 0.0018423
Vector Lines | 2010 | 2010-03-12 | 0.02441 | 0.00013057
Vector Lines | 2010 | 2010-03-13 | 0.02436 | 0.00010293
Vector Lines | 2010 | 2010-03-14 | 0.079314 | 0.0047043
Vector Lines | 2010 | 2010-03-15 | 0.00054134 | 0.00013534
Vector Lines | 2010 | 2010-03-16 | 0.05272 | 0.00020396
Vector Lines | 2010 | 2010-03-17 | 0.33066 | 0.004812
Vector Lines | 2010 | 2010-03-18 | 0.0061187 | 9.5307e-06
Vector Lines | 2010 | 2010-03-19 | 0.03619 | 0.00017536
Vector Lines | 2010 | 2010-03-20 | 0.00050513 | 1.9061e-06
Vector Lines | 2010 | 2010-03-21 | 0.091018 | 0.0014982
Vector Lines | 2010 | 2010-03-22 | 0.00085967 | 1.9061e-06
Vector Lines | 2010 | 2010-03-23 | 0.71013 | 0.039549
Vector Lines | 2010 | 2010-03-24 | 1.0001 | 0.023426
Vector Lines | 2010 | 2010-03-25 | 0.059292 | 0.0014144
Vector Lines | 2010 | 2010-03-26 | 0.058923 | 0.0013419
Vector Lines | 2010 | 2010-03-27 | 1.1111 | 0.016616
Vector Lines | 2010 | 2010-03-28 | 0.0072976 | 1.8108e-05
Vector Lines | 2010 | 2010-03-29 | 0.37794 | 0.013796
Vector Lines | 2010 | 2010-03-30 | 0.069019 | 0.0033872
Vector Lines | 2010 | 2010-03-31 | 0.22562 | 0.0007596
Vector Lines | 2011 | 2010-04-01 | 0.22513 | 0.0018464
Vector Lines | 2011 | 2010-04-02 | 0.11174 | 0.0012265
Vector Lines | 2011 | 2010-04-03 | 0.43123 | 0.0047171
Vector Lines | 2011 | 2010-04-04 | 0.24122 | 0.0053256
Vector Lines | 2011 | 2010-04-05 | 0.59682 | 0.0060211
Vector Lines | 2011 | 2010-04-06 | 0.11997 | 0.0010923
Vector Lines | 2011 | 2010-04-07 | 0.38602 | 0.0034764
Vector Lines | 2011 | 2010-04-08 | 0.0022111 | 1.1339e-05
Vector Lines | 2011 | 2010-04-09 | 0.23279 | 0.0067128
Vector Lines | 2011 | 2010-04-10 | 0.045543 | 0.00055278
Vector Lines | 2011 | 2010-04-11 | 0.36857 | 0.0027478
Vector Lines | 2011 | 2010-04-12 | 0.062137 | 0.0015346
Vector Lines | 2011 | 2010-04-13 | 0.30808 | 0.0039318
Vector Lines | 2011 | 2010-04-14 | 0.81139 | 0.007549
Vector Lines | 2011 | 2010-04-15 | 0.050464 | 0.00022867
Vector Lines | 2011 | 2010-04-16 | 0.19665 | 0.003225
Vector Lines | 2011 | 2010-04-17 | 0.00023245 | 5.6696e-06
Vector Lines | 2011 | 2010-04-18 | 0.021875 | 0.000875
Vector Lines | 2011 | 2010-04-19 | 0.39259 | 0.0056705
Vector Lines | 2011 | 2010-04-20 | 0.28625 | 0.0033413
Vector Lines | 2011 | 2010-04-21 | 0.052067 | 0.0031409
Vector Lines | 2011 | 2010-04-22 | 0.11845 | 0.001922
Vector Lines | 2011 | 2010-04-23 | 0.039169 | 0.00021733
Vector Lines | 2011 | 2010-04-24 | 0.022709 | 0.00027781
Vector Lines | 2011 | 2010-04-25 | 0.1246 | 0.00040065
Vector Lines | 2011 | 2010-04-26 | 0.017567 | 0.00016347
Vector Lines | 2011 | 2010-04-27 | 1.1012 | 0.013322
Vector Lines | 2011 | 2010-04-28 | 0.30495 | 0.0027667
Vector Lines | 2011 | 2010-04-29 | 0.076916 | 0.00022017
Vector Lines | 2011 | 2010-04-30 | 0.1605 | 0.0016461
Vector Lines | 2011 | 2010-05-01 | 0.37592 | 0.0048645
Vector Lines | 2011 | 2010-05-02 | 0.021643 | 0.00038931
Vector Lines | 2011 | 2010-05-03 | 0.16723 | 0.0020788
Vector Lines | 2011 | 2010-05-04 | 0.013924 | 0.00024568
Vector Lines | 2011 | 2010-05-05 | 0.030611 | 0.00012568
Vector Lines | 2011 | 2010-05-06
Vector Lines | 2011 | 2010-05-07
Vector Lines | 2011 | 2010-05-08 | 0.17942 | 0.0014826
Vector Lines | 2011 | 2010-05-09 | 0.18738 | 0.00070303
Vector Lines | 2011 | 2010-05-10 | 0.0028877 | 0.00018899
Vector Lines | 2011 | 2010-05-11 | 0.62403 | 0.0039044
Vector Lines | 2011 | 2010-05-12 | 1.6995 | 0.017095
Vector Lines | 2011 | 2010-05-13 | 0.16572 | 0.00084855
Vector Lines | 2011 | 2010-05-14 | 0.18487 | 0.0022329
Vector Lines | 2011 | 2010-05-15 | 0.32354 | 0.0030701
Vector Lines | 2011 | 2010-05-16 | 0.01088 | 0.00019088
Vector Lines | 2011 | 2010-05-17 | 0.099535 | 0.002334
Vector Lines | 2011 | 2010-05-18 | 0.10884 | 0.00029576
Vector Lines | 2011 | 2010-05-19 | 0.15396 | 0.0010763
Vector Lines | 2011 | 2010-05-20 | 0.033958 | 0.00011528
Vector Lines | 2011 | 2010-05-21 | 1.0265 | 0.021027
Vector Lines | 2011 | 2010-05-22 | 0.020152 | 0.0013456
Vector Lines | 2011 | 2010-05-23 | 0.6384 | 0.0042919
Vector Lines | 2011 | 2010-05-24 | 0.51302 | 0.0070813
Vector Lines | 2011 | 2010-05-25 | 0.41644 | 0.0056441
Vector Lines | 2011 | 2010-05-26 | 0.2797 | 0.0026619
Vector Lines | 2011 | 2010-05-27 | 0.10312 | 0.0007909
Vector Lines | 2011 | 2010-05-28 | 0.081485 | 0.00088823
Vector Lines | 2011 | 2010-05-29 | 0.31743 | 0.0042578
Vector Lines | 2011 | 2010-05-30 | 0.0042465 | 1.3229e-05
Vector Lines | 2011 | 2010-05-31 | 0.10116 | 0.0011812
Vector Lines | 2011 | 2010-06-01 | 0.21669 | 0.0029255
Vector Lines | 2011 | 2010-06-02 | 0.33719 | 0.0012955
Vector Lines | 2011 | 2010-06-03 | 0.13166 | 0.0020184
Vector Lines | 2011 | 2010-06-04 | 3.2574 | 0.026237
Vector Lines | 2011 | 2010-06-05 | 0.36594 | 0.0043958
Vector Lines | 2011 | 2010-06-06 | 0.010903 | 0.002077
Vector Lines | 2011 | 2010-06-07 | 0.47942 | 0.0026779
Vector Lines | 2011 | 2010-06-08 | 0.13404 | 0.0035397
Vector Lines | 2011 | 2010-06-09 | 0.043766 | 0.00014079
Vector Lines | 2011 | 2010-06-10 | 0.14996 | 0.0012653
Vector Lines | 2011 | 2010-06-11 | 0.18176 | 0.0016366
Vector Lines | 2011 | 2010-06-12 | 0.097987 | 0.002899
Vector Lines | 2011 | 2010-06-13 | 0.44422 | 0.0036739
Vector Lines | 2011 | 2010-06-14 | 0.18127 | 0.0060324
Vector Lines | 2011 | 2010-06-15 | 0.07822 | 0.000326
Vector Lines | 2011 | 2010-06-16 | 0.20699 | 0.0054541
Vector Lines | 2011 | 2010-06-17 | 0.26297 | 0.0036058
Vector Lines | 2011 | 2010-06-18 | 0.020515 | 0.00011717
Vector Lines | 2011 | 2010-06-19 | 0.0034263 | 1.3229e-05
Vector Lines | 2011 | 2010-06-20 | 0.029416 | 0.00027781
Vector Lines | 2011 | 2010-06-21 | 0.028162 | 0.0003912
Vector Lines | 2011 | 2010-06-22 | 0.094399 | 0.0013049
Vector Lines | 2011 | 2010-06-23 | 0.066713 | 0.0012227
Vector Lines | 2011 | 2010-06-24 | 0.19927 | 0.0028499
Vector Lines | 2011 | 2010-06-25 | 0.015365 | 5.2916e-05
Vector Lines | 2011 | 2010-06-26 | 0.070099 | 0.00015591
Vector Lines | 2011 | 2010-06-27 | 0.34691 | 0.004546
Vector Lines | 2011 | 2010-06-28 | 0.077189 | 0.00034868
Vector Lines | 2011 | 2010-06-29 | 0.25291 | 0.00052443
Vector Lines | 2011 | 2010-06-30 | 0.1188 | 0.0018445
Vector Lines | 2011 | 2010-07-01 | 0.25313 | 0.003242
Vector Lines | 2011 | 2010-07-02 | 0.077779 | 0.00028537
Vector Lines | 2011 | 2010-07-03 | 0.29886 | 0.0024653
Vector Lines | 2011 | 2010-07-04 | 1.7782 | 0.0097961
Vector Lines | 2011 | 2010-07-05 | 0.85865 | 0.0046377
Vector Lines | 2011 | 2010-07-06 | 0.13836 | 0.0064652
Vector Lines | 2011 | 2010-07-07 | 0.08241 | 0.0013305
Vector Lines | 2011 | 2010-07-08 | 0.25571 | 0.0043552
Vector Lines | 2011 | 2010-07-09 | 0.045443 | 0.00012662
Vector Lines | 2011 | 2010-07-10 | 0.13264 | 0.00096572
Vector Lines | 2011 | 2010-07-11 | 0.18123 | 0.0017727
Vector Lines | 2011 | 2010-07-12 | 0.085023 | 0.00032411
Vector Lines | 2011 | 2010-07-13 | 0.0394 | 0.00023151
Vector Lines | 2011 | 2010-07-14 | 0.09873 | 0.00082965
Vector Lines | 2011 | 2010-07-15 | 0.012135 | 3.3072e-05
Vector Lines | 2011 | 2010-07-16 | 0.13328 | 0.0013163
Vector Lines | 2011 | 2010-07-17 | 0.80557 | 0.0040481
Vector Lines | 2011 | 2010-07-18
Vector Lines | 2011 | 2010-07-19 | 0.029027 | 0.0018606
Vector Lines | 2011 | 2010-07-20 | 0.088778 | 0.00064822
Vector Lines | 2011 | 2010-07-21 | 0.11998 | 0.00092981
Vector Lines | 2011 | 2010-07-22 | 0.27835 | 0.0037523
Vector Lines | 2011 | 2010-07-23 | 0.13659 | 0.0019239
Vector Lines | 2011 | 2010-07-24 | 0.25667 | 0.0027478
Vector Lines | 2011 | 2010-07-25 | 0.013609 | 0.00024946
Vector Lines | 2011 | 2010-07-26 | 0.10425 | 0.0014448
Vector Lines | 2011 | 2010-07-27 | 0.25675 | 0.0039498
Vector Lines | 2011 | 2010-07-28 | 0.044449 | 0.0014335
Vector Lines | 2011 | 2010-07-29 | 0.28653 | 0.0020221
Vector Lines | 2011 | 2010-07-30 | 0.029606 | 0.00025986
Vector Lines | 2011 | 2010-07-31 | 0.12132 | 0.001836
Vector Lines | 2011 | 2010-08-01 | 0.39053 | 0.0036928
Vector Lines | 2011 | 2010-08-02 | 0.29304 | 0.0037854
Vector Lines | 2011 | 2010-08-03 | 0.17745 | 0.0005405
Vector Lines | 2011 | 2010-08-04 | 0.095708 | 0.0069112
Vector Lines | 2011 | 2010-08-05 | 0.10168 | 0.00050176
Vector Lines | 2011 | 2010-08-06 | 0.64044 | 0.0096298
Vector Lines | 2011 | 2010-08-07 | 0.15991 | 0.0015903
Vector Lines | 2011 | 2010-08-08 | 0.078915 | 0.0019976
Vector Lines | 2011 | 2010-08-09 | 0.26679 | 0.00068035
Vector Lines | 2011 | 2010-08-10 | 0.031731 | 0.00049231
Vector Lines | 2011 | 2010-08-11 | 0.49487 | 0.0064491
Vector Lines | 2011 | 2010-08-12 | 0.027657 | 8.5988e-05
Vector Lines | 2011 | 2010-08-13 | 0.051992 | 0.0010243
Vector Lines | 2011 | 2010-08-14 | 0.061348 | 0.00065389
Vector Lines | 2011 | 2010-08-15 | 0.0082473 | 4.1577e-05
Vector Lines | 2011 | 2010-08-16 | 0.12624 | 0.0023642
Vector Lines | 2011 | 2010-08-17 | 0.19436 | 0.0017689
Vector Lines | 2011 | 2010-08-18 | 0.37967 | 0.0064057
Vector Lines | 2011 | 2010-08-19 | 0.031083 | 0.0056611
Vector Lines | 2011 | 2010-08-20 | 0.053126 | 0.0065814
Vector Lines | 2011 | 2010-08-21 | 0.015324 | 4.8191e-05
Vector Lines | 2011 | 2010-08-22
Vector Lines | 2011 | 2010-08-23 | 0.079714 | 0.0012946
Vector Lines | 2011 | 2010-08-24 | 0.60963 | 0.0095324
Vector Lines | 2011 | 2010-08-25 | 0.087549 | 0.001425
Vector Lines | 2011 | 2010-08-26 | 0.051124 | 0.00033261
Vector Lines | 2011 | 2010-08-27 | 0.11208 | 0.0017604
Vector Lines | 2011 | 2010-08-28 | 0.23276 | 0.002523
Vector Lines | 2011 | 2010-08-29 | 0.14488 | 0.0002608
Vector Lines | 2011 | 2010-08-30 | 0.60938 | 0.0090174
Vector Lines | 2011 | 2010-08-31 | 0.05774 | 0.0010555
Vector Lines | 2011 | 2010-09-01 | 0.037869 | 0.00021828
Vector Lines | 2011 | 2010-09-02 | 1.2489 | 0.0043911
Vector Lines | 2011 | 2010-09-03 | 0.097976 | 0.00094871
Vector Lines | 2011 | 2010-09-04 | 0.49431 | 0.0045149
Vector Lines | 2011 | 2010-09-05 | 0.0054125 | 0.00020694
Vector Lines | 2011 | 2010-09-06 | 0.29745 | 0.0036673
Vector Lines | 2011 | 2010-09-07 | 0.01339 | 9.4493e-05
Vector Lines | 2011 | 2010-09-08 | 0.081516 | 0.0014675
Vector Lines | 2011 | 2010-09-09 | 0.80156 | 0.0049921
Vector Lines | 2011 | 2010-09-10 | 0.19956 | 0.0028301
Vector Lines | 2011 | 2010-09-11 | 0.0086357 | 4.0632e-05
Vector Lines | 2011 | 2010-09-12 | 0.40486 | 0.0028405
Vector Lines | 2011 | 2010-09-13 | 0.23078 | 0.0077049
Vector Lines | 2011 | 2010-09-14 | 0.054219 | 0.00035435
Vector Lines | 2011 | 2010-09-15 | 0.57803 | 0.010813
Vector Lines | 2011 | 2010-09-16 | 0.38317 | 0.0036871
Vector Lines | 2011 | 2010-09-17 | 3.3856 | 0.038989
Vector Lines | 2011 | 2010-09-18 | 1.7154 | 0.010955
Vector Lines | 2011 | 2010-09-19 | 0.60661 | 0.0058576
Vector Lines | 2011 | 2010-09-20 | 0.36471 | 0.016468
Vector Lines | 2011 | 2010-09-21 | 0.91571 | 0.010476
Vector Lines | 2011 | 2010-09-22 | 2.3332 | 0.02576
Vector Lines | 2011 | 2010-09-23 | 0.70963 | 0.0065729
Vector Lines | 2011 | 2010-09-24 | 0.22487 | 0.00098178
Vector Lines | 2011 | 2010-09-25 | 0.24162 | 0.0037098
Vector Lines | 2011 | 2010-09-26 | 0.098495 | 0.0018832
Vector Lines | 2011 | 2010-09-27 | 0.067894 | 0.00027119
Vector Lines | 2011 | 2010-09-28 | 0.36644 | 0.0072353
Vector Lines | 2011 | 2010-09-29 | 0.37329 | 0.0043608
Vector Lines | 2011 | 2010-09-30 | 0.27761 | 0.0008391
Vector Lines | 2011 | 2010-10-01 | 0.22799 | 0.0022886
Vector Lines | 2011 | 2010-10-02 | 0.36476 | 0.0085299
Vector Lines | 2011 | 2010-10-03 | 0.041908 | 0.0014703
Vector Lines | 2011 | 2010-10-04 | 0.12882 | 0.00097706
Vector Lines | 2011 | 2010-10-05 | 0.038106 | 0.00035057
Vector Lines | 2011 | 2010-10-06 | 0.085374 | 0.00043845
Vector Lines | 2011 | 2010-10-07 | 0.021137 | 0.00018048
Vector Lines | 2011 | 2010-10-08 | 0.36667 | 0.0034953
Vector Lines | 2011 | 2010-10-09 | 0.27914 | 0.0035331
Vector Lines | 2011 | 2010-10-10 | 0.086733 | 0.00027403
Vector Lines | 2011 | 2010-10-11 | 0.231 | 0.0056941
Vector Lines | 2011 | 2010-10-12 | 0.188 | 0.0037476
Vector Lines | 2011 | 2010-10-13 | 0.18482 | 0.0025749
Vector Lines | 2011 | 2010-10-14 | 0.14509 | 0.0015128
Vector Lines | 2011 | 2010-10-15 | 0.068349 | 0.0003997
Vector Lines | 2011 | 2010-10-16 | 0.27281 | 0.0033214
Vector Lines | 2011 | 2010-10-17 | 0.32947 | 0.0031145
Vector Lines | 2011 | 2010-10-18 | 0.090273 | 0.00061609
Vector Lines | 2011 | 2010-10-19 | 0.21365 | 0.0010319
Vector Lines | 2011 | 2010-10-20 | 0.055905 | 0.00033072
Vector Lines | 2011 | 2010-10-21 | 0.44823 | 0.0084628
Vector Lines | 2011 | 2010-10-22 | 0.25578 | 0.0010498
Vector Lines | 2011 | 2010-10-23 | 0.23021 | 0.0045791
Vector Lines | 2011 | 2010-10-24
Vector Lines | 2011 | 2010-10-25
Vector Lines | 2011 | 2010-10-26 | 0.014133 | 0.00035624
Vector Lines | 2011 | 2010-10-27 | 0.20541 | 0.0013021
Vector Lines | 2011 | 2010-10-28 | 0.12124 | 0.001081
Vector Lines | 2011 | 2010-10-29 | 0.14904 | 0.010628
Vector Lines | 2011 | 2010-10-30 | 0.074653 | 0.0010564
Vector Lines | 2011 | 2010-10-31 | 0.049635 | 0.00047435
Vector Lines | 2011 | 2010-11-01 | 0.12005 | 0.00071909
Vector Lines | 2011 | 2010-11-02 | 0.30165 | 0.0031986
Vector Lines | 2011 | 2010-11-03 | 0.50071 | 0.0064198
Vector Lines | 2011 | 2010-11-04 | 0.31445 | 0.0039243
Vector Lines | 2011 | 2010-11-05 | 0.28995 | 0.0038818
Vector Lines | 2011 | 2010-11-06 | 0.45701 | 0.0028858
Vector Lines | 2011 | 2010-11-07 | 0.051272 | 0.00020505
Vector Lines | 2011 | 2010-11-08 | 0.1573 | 0.0023907
Vector Lines | 2011 | 2010-11-09 | 0.27826 | 0.0018114
Vector Lines | 2011 | 2010-11-10 | 0.010442 | 3.1183e-05
Vector Lines | 2011 | 2010-11-11 | 0.3047 | 0.0044591
Vector Lines | 2011 | 2010-11-12 | 0.00094493 | 4.7246e-06
Vector Lines | 2011 | 2010-11-13 | 0.12624 | 0.0020817
Vector Lines | 2011 | 2010-11-14 | 0.20832 | 0.0019777
Vector Lines | 2011 | 2010-11-15 | 0.045636 | 0.00065578
Vector Lines | 2011 | 2010-11-16 | 0.042069 | 0.00036947
Vector Lines | 2011 | 2010-11-17 | 0.16723 | 0.0010914
Vector Lines | 2011 | 2010-11-18 | 0.070363 | 0.0002797
Vector Lines | 2011 | 2010-11-19 | 0.081028 | 0.00028159
Vector Lines | 2011 | 2010-11-20 | 0.0006898 | 7.5594e-06
Vector Lines | 2011 | 2010-11-21 | 0.84765 | 0.0057291
Vector Lines | 2011 | 2010-11-22
Vector Lines | 2011 | 2010-11-23 | 0.20816 | 0.0028149
Vector Lines | 2011 | 2010-11-24 | 0.082385 | 0.0003723
Vector Lines | 2011 | 2010-11-25 | 0.037472 | 0.0022518
Vector Lines | 2011 | 2010-11-26 | 0.026743 | 0.00020505
Vector Lines | 2011 | 2010-11-27 | 0.57144 | 0.0055354
Vector Lines | 2011 | 2010-11-28 | 0.58344 | 0.0099671
Vector Lines | 2011 | 2010-11-29 | 0.7347 | 0.0053162
Vector Lines | 2011 | 2010-11-30 | 0.42554 | 0.001888
Vector Lines | 2011 | 2010-12-01 | 0.017457 | 0.0015969
Vector Lines | 2011 | 2010-12-02 | 0.45048 | 0.0032893
Vector Lines | 2011 | 2010-12-03 | 0.0082417 | 3.5907e-05
Vector Lines | 2011 | 2010-12-04 | 0.054751 | 0.00095154
Vector Lines | 2011 | 2010-12-05 | 0.38467 | 0.0073033
Vector Lines | 2011 | 2010-12-06 | 0.37487 | 0.0041804
Vector Lines | 2011 | 2010-12-07 | 0.67649 | 0.0076624
Vector Lines | 2011 | 2010-12-08 | 0.030932 | 0.00025608
Vector Lines | 2011 | 2010-12-09 | 0.03674 | 0.00015402
Vector Lines | 2011 | 2010-12-10 | 0.051929 | 0.0013598
Vector Lines | 2011 | 2010-12-11 | 0.004186 | 3.9687e-05
Vector Lines | 2011 | 2010-12-12 | 0.3236 | 0.0041199
Vector Lines | 2011 | 2010-12-13 | 0.073939 | 0.0019815
Vector Lines | 2011 | 2010-12-14 | 0.99127 | 0.013248
Vector Lines | 2011 | 2010-12-15 | 0.27671 | 0.0038978
Vector Lines | 2011 | 2010-12-16 | 1.0595 | 0.011727
Vector Lines | 2011 | 2010-12-17 | 0.71819 | 0.007858
Vector Lines | 2011 | 2010-12-18 | 1.0188 | 0.024304
Vector Lines | 2011 | 2010-12-19 | 1.3556 | 0.0074744
Vector Lines | 2011 | 2010-12-20 | 0.058958 | 0.00038931
Vector Lines | 2011 | 2010-12-21 | 0.083945 | 0.00025324
Vector Lines | 2011 | 2010-12-22 | 0.17937 | 0.016097
Vector Lines | 2011 | 2010-12-23 | 0.010704 | 0.00010016
Vector Lines | 2011 | 2010-12-24 | 0.12845 | 0.0013475
Vector Lines | 2011 | 2010-12-25 | 0.052069 | 0.0010319
Vector Lines | 2011 | 2010-12-26 | 0.02872 | 0.0004838
Vector Lines | 2011 | 2010-12-27 | 0.2111 | 0.0039158
Vector Lines | 2011 | 2010-12-28 | 0.33469 | 0.0062819
Vector Lines | 2011 | 2010-12-29 | 0.023663 | 0.00016158
Vector Lines | 2011 | 2010-12-30
Vector Lines | 2011 | 2010-12-31 | 0.15372 | 0.0016489
Vector Lines | 2011 | 2011-01-01 | 0.1645 | 0.00057641
Vector Lines | 2011 | 2011-01-02 | 0.23665 | 0.0010224
Vector Lines | 2011 | 2011-01-03
Vector Lines | 2011 | 2011-01-04 | 0.0077786 | 0.00018521
Vector Lines | 2011 | 2011-01-05
Vector Lines | 2011 | 2011-01-06 | 0.057484 | 0.00094304
Vector Lines | 2011 | 2011-01-07 | 0.42561 | 0.0031939
Vector Lines | 2011 | 2011-01-08 | 0.2793 | 0.0035945
Vector Lines | 2011 | 2011-01-09 | 0.05205 | 0.00059341
Vector Lines | 2011 | 2011-01-10 | 0.039543 | 0.00016347
Vector Lines | 2011 | 2011-01-11 | 0.085194 | 0.00059152
Vector Lines | 2011 | 2011-01-12 | 0.1414 | 0.00072476
Vector Lines | 2011 | 2011-01-13 | 0.061322 | 0.00033639
Vector Lines | 2011 | 2011-01-14 | 0.44428 | 0.0050147
Vector Lines | 2011 | 2011-01-15 | 0.0034565 | 5.8586e-05
Vector Lines | 2011 | 2011-01-16 | 0.038772 | 0.00043372
Vector Lines | 2011 | 2011-01-17 | 0.7385 | 0.0019248
Vector Lines | 2011 | 2011-01-18 | 0.55075 | 0.0061798
Vector Lines | 2011 | 2011-01-19 | 0.27274 | 0.0021818
Vector Lines | 2011 | 2011-01-20 | 0.0014032 | 9.4493e-06
Vector Lines | 2011 | 2011-01-21 | 0.40061 | 0.003706
Vector Lines | 2011 | 2011-01-22 | 0.39138 | 0.0030606
Vector Lines | 2011 | 2011-01-23 | 3.3794 | 0.038259
Vector Lines | 2011 | 2011-01-24 | 1.7114 | 0.018985
Vector Lines | 2011 | 2011-01-25 | 0.19555 | 0.0072438
Vector Lines | 2011 | 2011-01-26 | 0.093977 | 0.00038742
Vector Lines | 2011 | 2011-01-27 | 0.088923 | 0.00025891
Vector Lines | 2011 | 2011-01-28 | 0.63202 | 0.0082927
Vector Lines | 2011 | 2011-01-29 | 1.8831 | 0.0087935
Vector Lines | 2011 | 2011-01-30 | 0.078859 | 0.0015922
Vector Lines | 2011 | 2011-01-31 | 0.47416 | 0.0053067
Vector Lines | 2011 | 2011-02-01 | 0.14867 | 0.0027526
Vector Lines | 2011 | 2011-02-02 | 0.62494 | 0.008047
Vector Lines | 2011 | 2011-02-03 | 0.07428 | 0.00044128
Vector Lines | 2011 | 2011-02-04 | 0.19601 | 0.0014939
Vector Lines | 2011 | 2011-02-05
Vector Lines | 2011 | 2011-02-06 | 0.09008 | 0.0013607
Vector Lines | 2011 | 2011-02-07 | 0.034732 | 0.00022206
Vector Lines | 2011 | 2011-02-08 | 0.28933 | 0.0021563
Vector Lines | 2011 | 2011-02-09 | 0.061903 | 0.00025513
Vector Lines | 2011 | 2011-02-10 | 0.36739 | 0.0044894
Vector Lines | 2011 | 2011-02-11 | 0.24998 | 0.00139
Vector Lines | 2011 | 2011-02-12 | 0.16361 | 0.0028405
Vector Lines | 2011 | 2011-02-13 | 0.0056724 | 2.7403e-05
Vector Lines | 2011 | 2011-02-14 | 0.25385 | 0.00223
Vector Lines | 2011 | 2011-02-15 | 0.023467 | 9.6383e-05
Vector Lines | 2011 | 2011-02-16 | 0.18134 | 0.0043712
Vector Lines | 2011 | 2011-02-17 | 0.18409 | 0.00061042
Vector Lines | 2011 | 2011-02-18 | 0.17303 | 0.0015109
Vector Lines | 2011 | 2011-02-19 | 0.13467 | 0.0013843
Vector Lines | 2011 | 2011-02-20 | 0.10463 | 0.0015903
Vector Lines | 2011 | 2011-02-21 | 0.023621 | 0.00079941
Vector Lines | 2011 | 2011-02-22 | 0.13396 | 0.0051206
Vector Lines | 2011 | 2011-02-23 | 1.0044 | 0.0084987
Vector Lines | 2011 | 2011-02-24 | 0.20857 | 0.0024578
Vector Lines | 2011 | 2011-02-25 | 0.14478 | 0.00087122
Vector Lines | 2011 | 2011-02-26 | 0.084565 | 0.0014363
Vector Lines | 2011 | 2011-02-27 | 0.10452 | 0.0023793
Vector Lines | 2011 | 2011-02-28 | 0.1483 | 0.0018407
Vector Lines | 2011 | 2011-03-01 | 0.20293 | 0.0046405
Vector Lines | 2011 | 2011-03-02 | 0.15762 | 0.0014741
Vector Lines | 2011 | 2011-03-03 | 0.33427 | 0.0026571
Vector Lines | 2011 | 2011-03-04 | 0.0010772 | 4.7246e-06
Vector Lines | 2011 | 2011-03-05 | 0.30583 | 0.0054796
Vector Lines | 2011 | 2011-03-06 | 0.54099 | 0.014142
Vector Lines | 2011 | 2011-03-07 | 0.050625 | 0.0015251
Vector Lines | 2011 | 2011-03-08 | 0.04709 | 0.00019938
Vector Lines | 2011 | 2011-03-09 | 0.34868 | 0.0020505
Vector Lines | 2011 | 2011-03-10 | 0.20752 | 0.0018625
Vector Lines | 2011 | 2011-03-11 | 0.20892 | 0.0011585
Vector Lines | 2011 | 2011-03-12 | 1.1997 | 0.0060041
Vector Lines | 2011 | 2011-03-13 | 0.00056696 | 1.4174e-05
Vector Lines | 2011 | 2011-03-14 | 0.18535 | 0.0015591
Vector Lines | 2011 | 2011-03-15 | 0.27198 | 0.002848
Vector Lines | 2011 | 2011-03-16 | 0.33083 | 0.0041227
Vector Lines | 2011 | 2011-03-17 | 0.064456 | 0.00041104
Vector Lines | 2011 | 2011-03-18 | 0.07266 | 0.00032695
Vector Lines | 2011 | 2011-03-19 | 0.71329 | 0.0060173
Vector Lines | 2011 | 2011-03-20 | 0.0080659 | 9.6383e-05
Vector Lines | 2011 | 2011-03-21 | 0.73393 | 0.015954
Vector Lines | 2011 | 2011-03-22 | 0.66465 | 0.0079799
Vector Lines | 2011 | 2011-03-23 | 0.11548 | 0.00043845
Vector Lines | 2011 | 2011-03-24 | 0.16738 | 0.0016281
Vector Lines | 2011 | 2011-03-25 | 0.25129 | 0.0026335
Vector Lines | 2011 | 2011-03-26 | 0.36308 | 0.0063348
Vector Lines | 2011 | 2011-03-27 | 0.1291 | 0.0028575
Vector Lines | 2011 | 2011-03-28 | 0.11135 | 0.0032373
Vector Lines | 2011 | 2011-03-29 | 0.19768 | 0.0018662
Vector Lines | 2011 | 2011-03-30 | 0.037233 | 0.00021828
Vector Lines | 2011 | 2011-03-31 | 0.30107 | 0.0026845
Vector Lines | 2012 | 2011-04-01 | 0.11297 | 0.0014476
Vector Lines | 2012 | 2011-04-02 | 0.0093677 | 0.00020077
Vector Lines | 2012 | 2011-04-03 | 0.11555 | 0.0018848
Vector Lines | 2012 | 2011-04-04 | 0.039377 | 0.00051694
Vector Lines | 2012 | 2011-04-05 | 0.23099 | 0.0017891
Vector Lines | 2012 | 2011-04-06 | 0.082624 | 0.00037058
Vector Lines | 2012 | 2011-04-07 | 0.089496 | 0.00064734
Vector Lines | 2012 | 2011-04-08 | 0.0088836 | 0.00016418
Vector Lines | 2012 | 2011-04-09 | 0.0081875 | 0.0018632
Vector Lines | 2012 | 2011-04-10 | 0.0011765 | 8.5374e-05
Vector Lines | 2012 | 2011-04-11 | 0.33864 | 0.0050174
Vector Lines | 2012 | 2011-04-12 | 0.13512 | 0.0013923
Vector Lines | 2012 | 2011-04-13 | 0.055965 | 0.0022291
Vector Lines | 2012 | 2011-04-14 | 0.040776 | 0.00019233
Vector Lines | 2012 | 2011-04-15 | 0.25475 | 0.0037677
Vector Lines | 2012 | 2011-04-16 | 0.94718 | 0.019937
Vector Lines | 2012 | 2011-04-17 | 0.5562 | 0.0056356
Vector Lines | 2012 | 2011-04-18 | 2.7236 | 0.018991
Vector Lines | 2012 | 2011-04-19 | 0.34127 | 0.003278
Vector Lines | 2012 | 2011-04-20 | 0.20802 | 0.0061845
Vector Lines | 2012 | 2011-04-21 | 0.086823 | 0.00096445
Vector Lines | 2012 | 2011-04-22 | 0.36167 | 0.0028877
Vector Lines | 2012 | 2011-04-23 | 0.041734 | 0.0002139
Vector Lines | 2012 | 2011-04-24 | 0.049541 | 0.0012637
Vector Lines | 2012 | 2011-04-25 | 0.73051 | 0.0047922
Vector Lines | 2012 | 2011-04-26 | 0.98381 | 0.018271
Vector Lines | 2012 | 2011-04-27 | 0.018941 | 8.8189e-05
Vector Lines | 2012 | 2011-04-28 | 0.035356 | 0.00068956
Vector Lines | 2012 | 2011-04-29 | 0.00019889 | 9.3818e-07
Vector Lines | 2012 | 2011-04-30 | 0.20618 | 0.0031354
Vector Lines | 2012 | 2011-05-01 | 1.1129 | 0.010949
Vector Lines | 2012 | 2011-05-02 | 0.77587 | 0.015592
Vector Lines | 2012 | 2011-05-03 | 1.2488 | 0.0075608
Vector Lines | 2012 | 2011-05-04 | 0.26377 | 0.0037837
Vector Lines | 2012 | 2011-05-05 | 0.26019 | 0.0019495
Vector Lines | 2012 | 2011-05-06 | 0.18371 | 0.0045445
Vector Lines | 2012 | 2011-05-07 | 0.14173 | 0.0015274
Vector Lines | 2012 | 2011-05-08 | 0.059679 | 0.00082559
Vector Lines | 2012 | 2011-05-09 | 0.13393 | 0.0022601
Vector Lines | 2012 | 2011-05-10 | 0.062251 | 0.00074022
Vector Lines | 2012 | 2011-05-11 | 0.79497 | 0.0076311
Vector Lines | 2012 | 2011-05-12 | 0.54845 | 0.010717
Vector Lines | 2012 | 2011-05-13 | 0.017508 | 0.0056431
Vector Lines | 2012 | 2011-05-14 | 0.18723 | 0.002049
Vector Lines | 2012 | 2011-05-15 | 0.029678 | 0.00045314
Vector Lines | 2012 | 2011-05-16 | 1.4638 | 0.020575
Vector Lines | 2012 | 2011-05-17 | 0.029264 | 0.00014542
Vector Lines | 2012 | 2011-05-18 | 0.17662 | 0.00095975
Vector Lines | 2012 | 2011-05-19 | 0.29659 | 0.0026081
Vector Lines | 2012 | 2011-05-20 | 1.0487 | 0.002201
Vector Lines | 2012 | 2011-05-21 | 0.059532 | 0.00059762
Vector Lines | 2012 | 2011-05-22 | 0.037033 | 0.0035904
Vector Lines | 2012 | 2011-05-23 | 0.023292 | 8.9127e-05
Vector Lines | 2012 | 2011-05-24 | 0.2622 | 0.0044179
Vector Lines | 2012 | 2011-05-25 | 0.16356 | 0.0013472
Vector Lines | 2012 | 2011-05-26 | 0.43354 | 0.0035951
Vector Lines | 2012 | 2011-05-27 | 0.11811 | 0.0012478
Vector Lines | 2012 | 2011-05-28
Vector Lines | 2012 | 2011-05-29 | 0.032605 | 0.00039591
Vector Lines | 2012 | 2011-05-30 | 0.10597 | 0.0016793
Vector Lines | 2012 | 2011-05-31 | 0.12155 | 0.0012178
Vector Lines | 2012 | 2011-06-01 | 0.29432 | 0.0025866
Vector Lines | 2012 | 2011-06-02 | 0.24575 | 0.0057951
Vector Lines | 2012 | 2011-06-03 | 0.23372 | 0.005797
Vector Lines | 2012 | 2011-06-04 | 0.86428 | 0.0082287
Vector Lines | 2012 | 2011-06-05 | 0.11194 | 0.0010864
Vector Lines | 2012 | 2011-06-06 | 0.035671 | 0.00029177
Vector Lines | 2012 | 2011-06-07 | 0.036336 | 0.00022704
Vector Lines | 2012 | 2011-06-08 | 0.045866 | 0.00018294
Vector Lines | 2012 | 2011-06-09 | 0.05186 | 0.00031147
Vector Lines | 2012 | 2011-06-10 | 0.23327 | 0.0042968
Vector Lines | 2012 | 2011-06-11 | 0.53261 | 0.0055315
Vector Lines | 2012 | 2011-06-12 | 0.0026729 | 7.5054e-06
Vector Lines | 2012 | 2011-06-13 | 0.056166 | 0.00044188
Vector Lines | 2012 | 2011-06-14 | 0.13177 | 0.0014044
Vector Lines | 2012 | 2011-06-15 | 0.084381 | 0.0020358
Vector Lines | 2012 | 2011-06-16 | 0.30002 | 0.0053983
Vector Lines | 2012 | 2011-06-17 | 0.11266 | 0.0012506
Vector Lines | 2012 | 2011-06-18 | 0.023969 | 0.00018294
Vector Lines | 2012 | 2011-06-19 | 0.0055671 | 0.00013041
Vector Lines | 2012 | 2011-06-20 | 0.27737 | 0.0040886
Vector Lines | 2012 | 2011-06-21 | 0.23025 | 0.0092448
Vector Lines | 2012 | 2011-06-22 | 0.020523 | 0.0024796
Vector Lines | 2012 | 2011-06-23 | 0.37231 | 0.0017713
Vector Lines | 2012 | 2011-06-24 | 0.099223 | 0.00062858
Vector Lines | 2012 | 2011-06-25 | 0.025229 | 0.00038747
Vector Lines | 2012 | 2011-06-26 | 0.060902 | 0.0004006
Vector Lines | 2012 | 2011-06-27 | 0.055208 | 0.00055821
Vector Lines | 2012 | 2011-06-28 | 0.62361 | 0.0084811
Vector Lines | 2012 | 2011-06-29 | 0.39076 | 0.0061526
Vector Lines | 2012 | 2011-06-30 | 0.19791 | 0.004294
Vector Lines | 2012 | 2011-07-01 | 0.035089 | 0.00099634
Vector Lines | 2012 | 2011-07-02 | 0.0024749 | 7.3178e-05
Vector Lines | 2012 | 2011-07-03 | 0.17987 | 0.0010864
Vector Lines | 2012 | 2011-07-04 | 0.2863 | 0.0039488
Vector Lines | 2012 | 2011-07-05 | 0.31508 | 0.0030078
Vector Lines | 2012 | 2011-07-06 | 1.0796 | 0.014185
Vector Lines | 2012 | 2011-07-07 | 0.2124 | 0.0032245
Vector Lines | 2012 | 2011-07-08 | 1.6218 | 0.02203
Vector Lines | 2012 | 2011-07-09 | 0.084425 | 0.002186
Vector Lines | 2012 | 2011-07-10 | 0.4773 | 0.0064978
Vector Lines | 2012 | 2011-07-11 | 0.090286 | 0.0014166
Vector Lines | 2012 | 2011-07-12 | 0.16649 | 0.0017216
Vector Lines | 2012 | 2011-07-13 | 0.31158 | 0.0060259
Vector Lines | 2012 | 2011-07-14 | 0.085185 | 0.0010339
Vector Lines | 2012 | 2011-07-15 | 0.46733 | 0.0039319
Vector Lines | 2012 | 2011-07-16 | 0.02259 | 0.00012478
Vector Lines | 2012 | 2011-07-17 | 0.069495 | 0.00077681
Vector Lines | 2012 | 2011-07-18 | 0.094098 | 0.00036964
Vector Lines | 2012 | 2011-07-19 | 0.51162 | 0.002124
Vector Lines | 2012 | 2011-07-20 | 0.35342 | 0.0085271
Vector Lines | 2012 | 2011-07-21 | 0.66113 | 0.0055249
Vector Lines | 2012 | 2011-07-22 | 0.11855 | 0.0086331
Vector Lines | 2012 | 2011-07-23 | 0.081517 | 0.00073272
Vector Lines | 2012 | 2011-07-24 | 0.088528 | 0.0010845
Vector Lines | 2012 | 2011-07-25 | 0.65591 | 0.0044723
Vector Lines | 2012 | 2011-07-26 | 0.053626 | 0.00033868
Vector Lines | 2012 | 2011-07-27 | 0.18361 | 0.002458
Vector Lines | 2012 | 2011-07-28 | 0.10438 | 0.00056666
Vector Lines | 2012 | 2011-07-29 | 0.068536 | 0.00031898
Vector Lines | 2012 | 2011-07-30 | 0.090572 | 0.0032527
Vector Lines | 2012 | 2011-07-31 | 0.021471 | 5.9105e-05
Vector Lines | 2012 | 2011-08-01 | 0.0611 | 0.00043531
Vector Lines | 2012 | 2011-08-02 | 0.31058 | 0.0017497
Vector Lines | 2012 | 2011-08-03 | 0.2737 | 0.0043259
Vector Lines | 2012 | 2011-08-04 | 0.11508 | 0.0021118
Vector Lines | 2012 | 2011-08-05 | 0.019305 | 0.00015761
Vector Lines | 2012 | 2011-08-06 | 0.01081 | 0.00012853
Vector Lines | 2012 | 2011-08-07 | 0.29705 | 0.0038878
Vector Lines | 2012 | 2011-08-08 | 0.088007 | 0.001623
Vector Lines | 2012 | 2011-08-09 | 0.26419 | 0.0042415
Vector Lines | 2012 | 2011-08-10 | 0.057074 | 0.00030397
Vector Lines | 2012 | 2011-08-11 | 0.22728 | 0.002974
Vector Lines | 2012 | 2011-08-12 | 0.27659 | 0.0021034
Vector Lines | 2012 | 2011-08-13 | 0.0002458 | 9.3818e-07
Vector Lines | 2012 | 2011-08-14 | 0.2077 | 0.002124
Vector Lines | 2012 | 2011-08-15 | 2.3038 | 0.019689
Vector Lines | 2012 | 2011-08-16 | 0.84215 | 0.0064556
Vector Lines | 2012 | 2011-08-17 | 0.10315 | 0.00048035
Vector Lines | 2012 | 2011-08-18 | 0.094617 | 0.00035182
Vector Lines | 2012 | 2011-08-19 | 0.039944 | 0.00028708
Vector Lines | 2012 | 2011-08-20 | 0.00018201 | 9.3818e-07
Vector Lines | 2012 | 2011-08-21 | 0.20026 | 0.0011934
Vector Lines | 2012 | 2011-08-22 | 0.027841 | 0.0001229
Vector Lines | 2012 | 2011-08-23 | 0.11548 | 0.0013716
Vector Lines | 2012 | 2011-08-24 | 0.055405 | 0.00034056
Vector Lines | 2012 | 2011-08-25 | 0.11507 | 0.00051881
Vector Lines | 2012 | 2011-08-26 | 0.010047 | 3.6589e-05
Vector Lines | 2012 | 2011-08-27 | 0.10531 | 0.0011042
Vector Lines | 2012 | 2011-08-28 | 0.01711 | 0.00044845
Vector Lines | 2012 | 2011-08-29 | 0.02374 | 0.00026081
Vector Lines | 2012 | 2011-08-30 | 0.28422 | 0.0025631
Vector Lines | 2012 | 2011-08-31 | 0.18772 | 0.001411
Vector Lines | 2012 | 2011-09-01 | 0.11125 | 0.00063796
Vector Lines | 2012 | 2011-09-02 | 0.0071264 | 6.4734e-05
Vector Lines | 2012 | 2011-09-03 | 0.17129 | 0.00071583
Vector Lines | 2012 | 2011-09-04 | 0.0068543 | 2.7207e-05
Vector Lines | 2012 | 2011-09-05 | 0.00056291 | 7.5054e-06
Vector Lines | 2012 | 2011-09-06 | 0.23203 | 0.0040135
Vector Lines | 2012 | 2011-09-07 | 0.025243 | 0.00012572
Vector Lines | 2012 | 2011-09-08 | 0.19763 | 0.0012797
Vector Lines | 2012 | 2011-09-09 | 0.0092983 | 0.00011633
Vector Lines | 2012 | 2011-09-10 | 0.00050099 | 1.8764e-06
Vector Lines | 2012 | 2011-09-11 | 0.42272 | 0.0095187
Vector Lines | 2012 | 2011-09-12 | 0.77546 | 0.010124
Vector Lines | 2012 | 2011-09-13 | 0.73181 | 0.013923
Vector Lines | 2012 | 2011-09-14 | 0.42497 | 0.0091885
Vector Lines | 2012 | 2011-09-15 | 0.075605 | 0.00031054
Vector Lines | 2012 | 2011-09-16 | 0.016475 | 6.3796e-05
Vector Lines | 2012 | 2011-09-17 | 0.021806 | 8.725e-05
Vector Lines | 2012 | 2011-09-18 | 0.015545 | 9.4756e-05
Vector Lines | 2012 | 2011-09-19 | 0.95926 | 0.0056244
Vector Lines | 2012 | 2011-09-20 | 1.2494 | 0.021473
Vector Lines | 2012 | 2011-09-21 | 0.0031185 | 2.2516e-05
Vector Lines | 2012 | 2011-09-22 | 0.053267 | 0.00023736
Vector Lines | 2012 | 2011-09-23 | 0.28927 | 0.00090534
Vector Lines | 2012 | 2011-09-24 | 0.23269 | 0.003095
Vector Lines | 2012 | 2011-09-25 | 0.011055 | 0.00025237
Vector Lines | 2012 | 2011-09-26 | 0.20608 | 0.0020546
Vector Lines | 2012 | 2011-09-27 | 0.5751 | 0.0073975
Vector Lines | 2012 | 2011-09-28 | 0.20293 | 0.00074585
Vector Lines | 2012 | 2011-09-29 | 0.077875 | 0.0017047
Vector Lines | 2012 | 2011-09-30 | 0.22249 | 0.00217
Vector Lines | 2012 | 2011-10-01 | 0.52426 | 0.0014185
Vector Lines | 2012 | 2011-10-02 | 0.48815 | 0.0035951
Vector Lines | 2012 | 2011-10-03 | 0.18469 | 0.0030613
Vector Lines | 2012 | 2011-10-04 | 0.51988 | 0.014114
Vector Lines | 2012 | 2011-10-05 | 0.07572 | 0.00065203
Vector Lines | 2012 | 2011-10-06 | 0.042856 | 0.0014514
Vector Lines | 2012 | 2011-10-07 | 0.02201 | 0.00015198
Vector Lines | 2012 | 2011-10-08 | 0.00025706 | 1.8764e-06
Vector Lines | 2012 | 2011-10-09 | 0.16121 | 0.0024796
Vector Lines | 2012 | 2011-10-10 | 0.55089 | 0.0024899
Vector Lines | 2012 | 2011-10-11 | 0.042181 | 0.00048316
Vector Lines | 2012 | 2011-10-12 | 0.083295 | 0.0012684
Vector Lines | 2012 | 2011-10-13 | 0.34764 | 0.0022779
Vector Lines | 2012 | 2011-10-14 | 0.088761 | 0.00033493
Vector Lines | 2012 | 2011-10-15 | 0.087423 | 0.0027573
Vector Lines | 2012 | 2011-10-16 | 0.024984 | 0.00012947
Vector Lines | 2012 | 2011-10-17 | 0.067864 | 0.0005751
Vector Lines | 2012 | 2011-10-18 | 0.095409 | 0.001366
Vector Lines | 2012 | 2011-10-19 | 0.13064 | 0.0019674
Vector Lines | 2012 | 2011-10-20 | 0.057696 | 0.00033681
Vector Lines | 2012 | 2011-10-21 | 0.22551 | 0.0031147
Vector Lines | 2012 | 2011-10-22 | 0.030629 | 0.0001426
Vector Lines | 2012 | 2011-10-23 | 0.0054846 | 5.0662e-05
Vector Lines | 2012 | 2011-10-24
Vector Lines | 2012 | 2011-10-25 | 0.065837 | 0.00028145
Vector Lines | 2012 | 2011-10-26 | 0.03759 | 0.0001942
Vector Lines | 2012 | 2011-10-27 | 0.15048 | 0.0044648
Vector Lines | 2012 | 2011-10-28 | 0.0429 | 0.00018201
Vector Lines | 2012 | 2011-10-29 | 0.0075007 | 7.5992e-05
Vector Lines | 2012 | 2011-10-30 | 0.24372 | 0.002837
Vector Lines | 2012 | 2011-10-31 | 0.037846 | 0.00043625
Vector Lines | 2012 | 2011-11-01 | 0.16215 | 0.00073178
Vector Lines | 2012 | 2011-11-02 | 0.046666 | 0.00020171
Vector Lines | 2012 | 2011-11-03 | 0.076383 | 0.00030866
Vector Lines | 2012 | 2011-11-04 | 0.039787 | 0.0020565
Vector Lines | 2012 | 2011-11-05 | 0.27027 | 0.013845
Vector Lines | 2012 | 2011-11-06 | 0.001092 | 3.7527e-06
Vector Lines | 2012 | 2011-11-07 | 0.067124 | 0.00043813
Vector Lines | 2012 | 2011-11-08 | 0.20158 | 0.002064
Vector Lines | 2012 | 2011-11-09 | 0.022649 | 0.00176
Vector Lines | 2012 | 2011-11-10 | 0.24384 | 0.0033071
Vector Lines | 2012 | 2011-11-11 | 0.019653 | 7.3178e-05
Vector Lines | 2012 | 2011-11-12 | 0.27668 | 0.0027179
Vector Lines | 2012 | 2011-11-13 | 0.13724 | 0.0020659
Vector Lines | 2012 | 2011-11-14 | 0.03128 | 0.00023736
Vector Lines | 2012 | 2011-11-15 | 0.040694 | 0.00015855
Vector Lines | 2012 | 2011-11-16 | 0.32921 | 0.0025284
Vector Lines | 2012 | 2011-11-17 | 0.012917 | 0.00039122
Vector Lines | 2012 | 2011-11-18 | 0.32748 | 0.00082935
Vector Lines | 2012 | 2011-11-19 | 0.001259 | 1.8764e-06
Vector Lines | 2012 | 2011-11-20 | 0.0039009 | 6.5672e-06
Vector Lines | 2012 | 2011-11-21 | 0.085536 | 0.00044657
Vector Lines | 2012 | 2011-11-22 | 0.15751 | 0.0032376
Vector Lines | 2012 | 2011-11-23 | 0.78513 | 0.0064124
Vector Lines | 2012 | 2011-11-24 | 1.4098 | 0.012775
Vector Lines | 2012 | 2011-11-25 | 0.003096 | 1.8764e-05
Vector Lines | 2012 | 2011-11-26 | 0.015195 | 3.6589e-05
Vector Lines | 2012 | 2011-11-27 | 0.022079 | 0.00032086
Vector Lines | 2012 | 2011-11-28 | 0.068459 | 0.001244
Vector Lines | 2012 | 2011-11-29 | 0.17411 | 0.0032564
Vector Lines | 2012 | 2011-11-30 | 0.27401 | 0.0077296
Vector Lines | 2012 | 2011-12-01 | 0.28751 | 0.0058795
Vector Lines | 2012 | 2011-12-02 | 0.27228 | 0.003657
Vector Lines | 2012 | 2011-12-03 | 0.0050868 | 1.8764e-05
Vector Lines | 2012 | 2011-12-04 | 0.079323 | 0.0012403
Vector Lines | 2012 | 2011-12-05 | 0.12347 | 0.0022554
Vector Lines | 2012 | 2011-12-06 | 0.46965 | 0.0033971
Vector Lines | 2012 | 2011-12-07 | 0.11845 | 0.0028783
Vector Lines | 2012 | 2011-12-08 | 0.24373 | 0.0016249
Vector Lines | 2012 | 2011-12-09 | 0.086991 | 0.00084811
Vector Lines | 2012 | 2011-12-10 | 0.087314 | 0.0091435
Vector Lines | 2012 | 2011-12-11
Vector Lines | 2012 | 2011-12-12 | 0.045859 | 0.0035942
Vector Lines | 2012 | 2011-12-13 | 0.056437 | 0.00024017
Vector Lines | 2012 | 2011-12-14 | 0.16557 | 0.0040726
Vector Lines | 2012 | 2011-12-15 | 1.131 | 0.0077887
Vector Lines | 2012 | 2011-12-16 | 0.099684 | 0.0020659
Vector Lines | 2012 | 2011-12-17 | 0.1972 | 0.0028802
Vector Lines | 2012 | 2011-12-18
Vector Lines | 2012 | 2011-12-19 | 0.46849 | 0.0024524
Vector Lines | 2012 | 2011-12-20 | 0.026221 | 0.00024955
Vector Lines | 2012 | 2011-12-21 | 0.40116 | 0.011413
Vector Lines | 2012 | 2011-12-22 | 0.33907 | 0.0032048
Vector Lines | 2012 | 2011-12-23
Vector Lines | 2012 | 2011-12-24 | 0.061657 | 0.0055015
Vector Lines | 2012 | 2011-12-25 | 0.10966 | 0.0017
Vector Lines | 2012 | 2011-12-26 | 0.003171 | 0.00063421
Vector Lines | 2012 | 2011-12-27
Vector Lines | 2012 | 2011-12-28 | 0.025233 | 0.00016324
Vector Lines | 2012 | 2011-12-29 | 0.19851 | 0.0045942
Vector Lines | 2012 | 2011-12-30 | 0.34114 | 0.0024693
Vector Lines | 2012 | 2011-12-31 | 0.26978 | 0.004567
Vector Lines | 2012 | 2012-01-01 | 0.36748 | 0.0028164
Vector Lines | 2012 | 2012-01-02 | 0.37663 | 0.0043475
Vector Lines | 2012 | 2012-01-03
Vector Lines | 2012 | 2012-01-04 | 0.040537 | 0.00066048
Vector Lines | 2012 | 2012-01-05 | 0.032475 | 0.00015105
Vector Lines | 2012 | 2012-01-06 | 0.29912 | 0.0039497
Vector Lines | 2012 | 2012-01-07 | 0.29192 | 0.0048091
Vector Lines | 2012 | 2012-01-08 | 0.26144 | 0.0030857
Vector Lines | 2012 | 2012-01-09 | 0.094594 | 0.0015846
Vector Lines | 2012 | 2012-01-10 | 0.09627 | 0.0010939
Vector Lines | 2012 | 2012-01-11 | 0.067594 | 0.0033915
Vector Lines | 2012 | 2012-01-12 | 0.2806 | 0.0015949
Vector Lines | 2012 | 2012-01-13 | 0.29082 | 0.0045361
Vector Lines | 2012 | 2012-01-14 | 0.00061075 | 4.6909e-06
Vector Lines | 2012 | 2012-01-15 | 0.013868 | 0.00013134
Vector Lines | 2012 | 2012-01-16 | 0.80526 | 0.0051572
Vector Lines | 2012 | 2012-01-17 | 0.039999 | 0.0002064
Vector Lines | 2012 | 2012-01-18 | 0.25126 | 0.0038728
Vector Lines | 2012 | 2012-01-19 | 0.29361 | 0.00099447
Vector Lines | 2012 | 2012-01-20 | 0.22445 | 0.003688
Vector Lines | 2012 | 2012-01-21 | 0.23786 | 0.0020086
Vector Lines | 2012 | 2012-01-22 | 0.073729 | 0.00039966
Vector Lines | 2012 | 2012-01-23 | 0.034195 | 0.00019796
Vector Lines | 2012 | 2012-01-24 | 0.089324 | 0.00032742
Vector Lines | 2012 | 2012-01-25 | 0.04683 | 0.0014804
Vector Lines | 2012 | 2012-01-26 | 0.012611 | 2.7207e-05
Vector Lines | 2012 | 2012-01-27 | 0.50751 | 0.0058242
Vector Lines | 2012 | 2012-01-28 | 0.3732 | 0.003369
Vector Lines | 2012 | 2012-01-29 | 0.06079 | 0.0011971
Vector Lines | 2012 | 2012-01-30 | 0.066723 | 0.002383
Vector Lines | 2012 | 2012-01-31 | 0.0016043 | 8.4436e-06
Vector Lines | 2012 | 2012-02-01 | 0.11279 | 0.00034713
Vector Lines | 2012 | 2012-02-02 | 0.28371 | 0.0028192
Vector Lines | 2012 | 2012-02-03 | 0.063482 | 0.00041092
Vector Lines | 2012 | 2012-02-04 | 0.070558 | 0.0015987
Vector Lines | 2012 | 2012-02-05 | 0.14014 | 0.0027263
Vector Lines | 2012 | 2012-02-06 | 0.022603 | 0.00020077
Vector Lines | 2012 | 2012-02-07 | 0.16287 | 0.0024533
Vector Lines | 2012 | 2012-02-08 | 0.034951 | 0.00014542
Vector Lines | 2012 | 2012-02-09 | 0.5309 | 0.0038962
Vector Lines | 2012 | 2012-02-10 | 0.16066 | 0.0024946
Vector Lines | 2012 | 2012-02-11 | 0.01891 | 4.5971e-05
Vector Lines | 2012 | 2012-02-12 | 0.18478 | 0.0029843
Vector Lines | 2012 | 2012-02-13 | 0.25441 | 0.0039225
Vector Lines | 2012 | 2012-02-14 | 0.02497 | 0.00014917
Vector Lines | 2012 | 2012-02-15 | 0.15293 | 0.0010114
Vector Lines | 2012 | 2012-02-16 | 0.030448 | 0.0002777
Vector Lines | 2012 | 2012-02-17 | 1.1037 | 0.023568
Vector Lines | 2012 | 2012-02-18 | 0.19801 | 0.0025481
Vector Lines | 2012 | 2012-02-19 | 0.12213 | 0.00094005
Vector Lines | 2012 | 2012-02-20 | 0.18402 | 0.0016981
Vector Lines | 2012 | 2012-02-21 | 0.44601 | 0.0026222
Vector Lines | 2012 | 2012-02-22 | 0.52771 | 0.0030153
Vector Lines | 2012 | 2012-02-23 | 0.12724 | 0.0019917
Vector Lines | 2012 | 2012-02-24 | 0.053575 | 0.0001745
Vector Lines | 2012 | 2012-02-25 | 0.40708 | 0.0031157
Vector Lines | 2012 | 2012-02-26 | 0.84743 | 0.0077906
Vector Lines | 2012 | 2012-02-27 | 0.045419 | 0.0066123
Vector Lines | 2012 | 2012-02-28 | 0.15283 | 0.00045877
Vector Lines | 2012 | 2012-02-29 | 0.37218 | 0.0067098
Vector Lines | 2012 | 2012-03-01 | 0.28421 | 0.0017056
Vector Lines | 2012 | 2012-03-02 | 0.63506 | 0.013043
Vector Lines | 2012 | 2012-03-03 | 1.5954 | 0.01878
Vector Lines | 2012 | 2012-03-04 | 0.0023004 | 1.1258e-05
Vector Lines | 2012 | 2012-03-05 | 0.060143 | 0.0028643
Vector Lines | 2012 | 2012-03-06 | 0.15448 | 0.0013078
Vector Lines | 2012 | 2012-03-07 | 0.41491 | 0.0066592
Vector Lines | 2012 | 2012-03-08 | 0.29147 | 0.0029571
Vector Lines | 2012 | 2012-03-09 | 0.63261 | 0.0016934
Vector Lines | 2012 | 2012-03-10 | 0.11143 | 0.0016277
Vector Lines | 2012 | 2012-03-11 | 0.29284 | 0.0020518
Vector Lines | 2012 | 2012-03-12 | 0.71938 | 0.010476
Vector Lines | 2012 | 2012-03-13 | 0.078223 | 0.0026691
Vector Lines | 2012 | 2012-03-14 | 0.16346 | 0.0026184
Vector Lines | 2012 | 2012-03-15 | 0.09299 | 0.00065672
Vector Lines | 2012 | 2012-03-16 | 0.050898 | 0.00058073
Vector Lines | 2012 | 2012-03-17 | 0.13269 | 0.0021672
Vector Lines | 2012 | 2012-03-18 | 0.075673 | 0.0012947
Vector Lines | 2012 | 2012-03-19 | 0.83417 | 0.010842
Vector Lines | 2012 | 2012-03-20 | 0.93921 | 0.0068768
Vector Lines | 2012 | 2012-03-21 | 0.59569 | 0.0050211
Vector Lines | 2012 | 2012-03-22 | 0.19606 | 0.0017234
Vector Lines | 2012 | 2012-03-23 | 0.36467 | 0.0054123
Vector Lines | 2012 | 2012-03-24 | 0.0060372 | 0.00012102
Vector Lines | 2012 | 2012-03-25 | 0.40315 | 0.0058129
Vector Lines | 2012 | 2012-03-26 | 0.090159 | 0.00029834
Vector Lines | 2012 | 2012-03-27 | 0.88841 | 0.011786
Vector Lines | 2012 | 2012-03-28 | 0.053708 | 0.00042406
Vector Lines | 2012 | 2012-03-29 | 0.73364 | 0.0073506
Vector Lines | 2012 | 2012-03-30 | 0.15979 | 0.00084717
Vector Lines | 2012 | 2012-03-31 | 0.11653 | 0.0014298
Vector Lines | 2013 | 2012-04-01 | 0.001888 | 1.8638e-05
Vector Lines | 2013 | 2012-04-02 | 0.045985 | 0.001628
Vector Lines | 2013 | 2012-04-03 | 0.089414 | 0.0015963
Vector Lines | 2013 | 2012-04-04 | 0.52804 | 0.0056602
Vector Lines | 2013 | 2012-04-05 | 0.41741 | 0.0034983
Vector Lines | 2013 | 2012-04-06 | 0.00077532 | 3.7275e-06
Vector Lines | 2013 | 2012-04-07 | 0.23217 | 0.0034945
Vector Lines | 2013 | 2012-04-08 | 0.16531 | 0.002271
Vector Lines | 2013 | 2012-04-09 | 0.05579 | 0.00083124
Vector Lines | 2013 | 2012-04-10 | 0.029093 | 0.00013046
Vector Lines | 2013 | 2012-04-11 | 0.040736 | 0.00060386
Vector Lines | 2013 | 2012-04-12 | 0.13382 | 0.0013522
Vector Lines | 2013 | 2012-04-13 | 0.027556 | 0.00015469
Vector Lines | 2013 | 2012-04-14 | 0.0032728 | 7.455e-06
Vector Lines | 2013 | 2012-04-15 | 0.0444 | 0.00059547
Vector Lines | 2013 | 2012-04-16 | 0.1631 | 0.0014193
Vector Lines | 2013 | 2012-04-17 | 0.037744 | 0.00087783
Vector Lines | 2013 | 2012-04-18 | 0.021302 | 7.6414e-05
Vector Lines | 2013 | 2012-04-19 | 0.10603 | 0.0035551
Vector Lines | 2013 | 2012-04-20 | 0.37707 | 0.0054906
Vector Lines | 2013 | 2012-04-21 | 0.03489 | 0.0013419
Vector Lines | 2013 | 2012-04-22 | 0.0004939 | 1.8638e-06
Vector Lines | 2013 | 2012-04-23 | 0.55234 | 0.0077952
Vector Lines | 2013 | 2012-04-24 | 0.035193 | 0.00011742
Vector Lines | 2013 | 2012-04-25 | 0.014403 | 0.00062622
Vector Lines | 2013 | 2012-04-26 | 0.034709 | 0.00048178
Vector Lines | 2013 | 2012-04-27 | 0.12545 | 0.0015842
Vector Lines | 2013 | 2012-04-28 | 0.012346 | 6.6163e-05
Vector Lines | 2013 | 2012-04-29 | 0.088558 | 0.00075296
Vector Lines | 2013 | 2012-04-30 | 0.060501 | 0.0014556
Vector Lines | 2013 | 2012-05-01 | 0.40382 | 0.0037927
Vector Lines | 2013 | 2012-05-02 | 0.077148 | 0.0011033
Vector Lines | 2013 | 2012-05-03 | 0.081655 | 0.0001901
Vector Lines | 2013 | 2012-05-04 | 0.18051 | 0.0011481
Vector Lines | 2013 | 2012-05-05 | 0.0063694 | 0.00035132
Vector Lines | 2013 | 2012-05-06 | 0.19616 | 0.002134
Vector Lines | 2013 | 2012-05-07 | 0.052913 | 0.0004091
Vector Lines | 2013 | 2012-05-08 | 0.42315 | 0.0017603
Vector Lines | 2013 | 2012-05-09 | 0.37658 | 0.0043687
Vector Lines | 2013 | 2012-05-10 | 0.090942 | 0.002545
Vector Lines | 2013 | 2012-05-11 | 0.15884 | 0.0028683
Vector Lines | 2013 | 2012-05-12 | 0.060973 | 0.006676
Vector Lines | 2013 | 2012-05-13 | 0.018746 | 0.0002777
Vector Lines | 2013 | 2012-05-14 | 0.15774 | 0.00264
Vector Lines | 2013 | 2012-05-15 | 0.14688 | 0.0021778
Vector Lines | 2013 | 2012-05-16 | 0.51516 | 0.0049548
Vector Lines | 2013 | 2012-05-17 | 0.29506 | 0.0029084
Vector Lines | 2013 | 2012-05-18 | 0.023109 | 0.0001724
Vector Lines | 2013 | 2012-05-19 | 0.69651 | 0.0065586
Vector Lines | 2013 | 2012-05-20 | 0.016225 | 0.0001053
Vector Lines | 2013 | 2012-05-21 | 0.17323 | 0.0026242
Vector Lines | 2013 | 2012-05-22 | 0.043833 | 0.00016122
Vector Lines | 2013 | 2012-05-23 | 0.16189 | 0.0024061
Vector Lines | 2013 | 2012-05-24 | 0.37837 | 0.0024592
Vector Lines | 2013 | 2012-05-25 | 0.29139 | 0.001395
Vector Lines | 2013 | 2012-05-26 | 0.4851 | 0.0034936
Vector Lines | 2013 | 2012-05-27 | 0.20027 | 0.0062324
Vector Lines | 2013 | 2012-05-28 | 0.1018 | 0.0007688
Vector Lines | 2013 | 2012-05-29 | 0.080315 | 0.0011238
Vector Lines | 2013 | 2012-05-30 | 0.34981 | 0.0026792
Vector Lines | 2013 | 2012-05-31 | 0.22309 | 0.0019337
Vector Lines | 2013 | 2012-06-01 | 0.33763 | 0.0034619
Vector Lines | 2013 | 2012-06-02 | 0.014907 | 0.0005526
Vector Lines | 2013 | 2012-06-03 | 0.0019569 | 1.1183e-05
Vector Lines | 2013 | 2012-06-04 | 0.00063741 | 3.7275e-06
Vector Lines | 2013 | 2012-06-05 | 0.23086 | 0.0026875
Vector Lines | 2013 | 2012-06-06 | 0.33674 | 0.0013512
Vector Lines | 2013 | 2012-06-07 | 0.10562 | 0.0009207
Vector Lines | 2013 | 2012-06-08 | 0.26403 | 0.0025459
Vector Lines | 2013 | 2012-06-09 | 0.016163 | 0.0010102
Vector Lines | 2013 | 2012-06-10 | 0.029192 | 0.0010279
Vector Lines | 2013 | 2012-06-11 | 0.2237 | 0.0026354
Vector Lines | 2013 | 2012-06-12 | 0.13804 | 0.0029317
Vector Lines | 2013 | 2012-06-13 | 0.0013084 | 3.6343e-05
Vector Lines | 2013 | 2012-06-14 | 0.30803 | 0.0028059
Vector Lines | 2013 | 2012-06-15
Vector Lines | 2013 | 2012-06-16 | 0.03467 | 0.00023111
Vector Lines | 2013 | 2012-06-17 | 0.0023148 | 1.6774e-05
Vector Lines | 2013 | 2012-06-18 | 0.18135 | 0.0025068
Vector Lines | 2013 | 2012-06-19 | 0.056594 | 0.00023297
Vector Lines | 2013 | 2012-06-20 | 0.072994 | 0.00040816
Vector Lines | 2013 | 2012-06-21 | 0.096011 | 0.00068586
Vector Lines | 2013 | 2012-06-22 | 0.30346 | 0.0034992
Vector Lines | 2013 | 2012-06-23 | 0.017053 | 9.3188e-05
Vector Lines | 2013 | 2012-06-24 | 0.010269 | 0.00027025
Vector Lines | 2013 | 2012-06-25 | 0.074556 | 0.0011071
Vector Lines | 2013 | 2012-06-26 | 0.045187 | 0.00025534
Vector Lines | 2013 | 2012-06-27 | 0.0091632 | 3.448e-05
Vector Lines | 2013 | 2012-06-28 | 0.10221 | 0.0010577
Vector Lines | 2013 | 2012-06-29 | 0.13241 | 0.0013643
Vector Lines | 2013 | 2012-06-30 | 0.091388 | 0.0018162
Vector Lines | 2013 | 2012-07-01 | 0.024827 | 0.00016774
Vector Lines | 2013 | 2012-07-02 | 0.71999 | 0.0042829
Vector Lines | 2013 | 2012-07-03 | 3.1239 | 0.024603
Vector Lines | 2013 | 2012-07-04 | 0.016313 | 0.00042214
Vector Lines | 2013 | 2012-07-05 | 0.087936 | 0.00064393
Vector Lines | 2013 | 2012-07-06 | 0.65573 | 0.0068102
Vector Lines | 2013 | 2012-07-07 | 0.29219 | 0.0012972
Vector Lines | 2013 | 2012-07-08 | 0.054467 | 0.00054142
Vector Lines | 2013 | 2012-07-09 | 0.102 | 0.00069705
Vector Lines | 2013 | 2012-07-10 | 0.11505 | 0.00023017
Vector Lines | 2013 | 2012-07-11 | 0.19443 | 0.0047274
Vector Lines | 2013 | 2012-07-12 | 0.003762 | 0.00015749
Vector Lines | 2013 | 2012-07-13 | 0.02204 | 0.00012021
Vector Lines | 2013 | 2012-07-14 | 0.098468 | 0.00064672
Vector Lines | 2013 | 2012-07-15 | 0.42413 | 0.0016103
Vector Lines | 2013 | 2012-07-16 | 0.44886 | 0.0046818
Vector Lines | 2013 | 2012-07-17 | 0.27141 | 0.0024294
Vector Lines | 2013 | 2012-07-18 | 0.10095 | 0.0003625
Vector Lines | 2013 | 2012-07-19 | 0.38814 | 0.022914
Vector Lines | 2013 | 2012-07-20 | 0.20219 | 0.0009002
Vector Lines | 2013 | 2012-07-21 | 0.1857 | 0.0019849
Vector Lines | 2013 | 2012-07-22 | 0.16944 | 0.0030007
Vector Lines | 2013 | 2012-07-23 | 0.10452 | 0.0046156
Vector Lines | 2013 | 2012-07-24 | 0.147 | 0.0012655
Vector Lines | 2013 | 2012-07-25 | 0.19595 | 0.0032644
Vector Lines | 2013 | 2012-07-26 | 0.12129 | 0.00080887
Vector Lines | 2013 | 2012-07-27 | 0.01079 | 8.2005e-05
Vector Lines | 2013 | 2012-07-28 | 0.054644 | 0.00084894
Vector Lines | 2013 | 2012-07-29 | 0.17944 | 0.0033343
Vector Lines | 2013 | 2012-07-30 | 1.447 | 0.011587
Vector Lines | 2013 | 2012-07-31 | 0.0068838 | 0.0010325
Vector Lines | 2013 | 2012-08-01 | 1.2527 | 0.0097736
Vector Lines | 2013 | 2012-08-02 | 0.047039 | 0.001422
Vector Lines | 2013 | 2012-08-03 | 0.037268 | 0.00045476
Vector Lines | 2013 | 2012-08-04 | 0.17742 | 0.0031432
Vector Lines | 2013 | 2012-08-05 | 0.016628 | 6.8959e-05
Vector Lines | 2013 | 2012-08-06 | 0.22765 | 0.0033138
Vector Lines | 2013 | 2012-08-07 | 0.22789 | 0.0011192
Vector Lines | 2013 | 2012-08-08 | 0.027722 | 0.00063554
Vector Lines | 2013 | 2012-08-09 | 0.045664 | 0.00015749
Vector Lines | 2013 | 2012-08-10 | 0.017006 | 9.5984e-05
Vector Lines | 2013 | 2012-08-11 | 0.18698 | 0.0033678
Vector Lines | 2013 | 2012-08-12 | 0.28976 | 0.0017184
Vector Lines | 2013 | 2012-08-13 | 0.1214 | 0.0010064
Vector Lines | 2013 | 2012-08-14 | 0.43589 | 0.012014
Vector Lines | 2013 | 2012-08-15 | 0.26148 | 0.0024956
Vector Lines | 2013 | 2012-08-16 | 0.029151 | 0.00013605
Vector Lines | 2013 | 2012-08-17 | 0.080403 | 0.00070543
Vector Lines | 2013 | 2012-08-18 | 0.80253 | 0.0089833
Vector Lines | 2013 | 2012-08-19 | 0.032367 | 0.00039139
Vector Lines | 2013 | 2012-08-20 | 0.19247 | 0.0017622
Vector Lines | 2013 | 2012-08-21 | 0.085662 | 0.0016494
Vector Lines | 2013 | 2012-08-22 | 0.21812 | 0.0048709
Vector Lines | 2013 | 2012-08-23 | 0.54118 | 0.0040695
Vector Lines | 2013 | 2012-08-24 | 0.0060237 | 0.00034573
Vector Lines | 2013 | 2012-08-25 | 0.024726 | 0.00018451
Vector Lines | 2013 | 2012-08-26 | 0.010205 | 3.2616e-05
Vector Lines | 2013 | 2012-08-27 | 0.0038636 | 1.6774e-05
Vector Lines | 2013 | 2012-08-28 | 0.1826 | 0.0012813
Vector Lines | 2013 | 2012-08-29 | 0.16697 | 0.0028823
Vector Lines | 2013 | 2012-08-30 | 0.025028 | 0.0058215
Vector Lines | 2013 | 2012-08-31
Vector Lines | 2013 | 2012-09-01 | 0.20231 | 0.0026288
Vector Lines | 2013 | 2012-09-02 | 0.20326 | 0.0021573
Vector Lines | 2013 | 2012-09-03 | 0.60741 | 0.006593
Vector Lines | 2013 | 2012-09-04 | 0.33902 | 0.0034349
Vector Lines | 2013 | 2012-09-05 | 0.10182 | 0.0016122
Vector Lines | 2013 | 2012-09-06 | 0.088225 | 0.00042773
Vector Lines | 2013 | 2012-09-07 | 0.42852 | 0.0047069
Vector Lines | 2013 | 2012-09-08 | 0.070363 | 0.0011714
Vector Lines | 2013 | 2012-09-09 | 0.78578 | 0.008578
Vector Lines | 2013 | 2012-09-10 | 0.0049772 | 5.4049e-05
Vector Lines | 2013 | 2012-09-11 | 0.21755 | 0.00097195
Vector Lines | 2013 | 2012-09-12 | 0.066467 | 0.00064393
Vector Lines | 2013 | 2012-09-13 | 0.1041 | 0.00055074
Vector Lines | 2013 | 2012-09-14 | 0.16815 | 0.0016737
Vector Lines | 2013 | 2012-09-15 | 0.11639 | 0.00077532
Vector Lines | 2013 | 2012-09-16 | 0.24292 | 0.0027826
Vector Lines | 2013 | 2012-09-17 | 0.070792 | 0.00059454
Vector Lines | 2013 | 2012-09-18 | 0.059536 | 0.00035411
Vector Lines | 2013 | 2012-09-19 | 0.16837 | 0.0017594
Vector Lines | 2013 | 2012-09-20 | 0.17576 | 0.0021927
Vector Lines | 2013 | 2012-09-21 | 0.049195 | 0.00025813
Vector Lines | 2013 | 2012-09-22
Vector Lines | 2013 | 2012-09-23 | 0.36298 | 0.0036567
Vector Lines | 2013 | 2012-09-24 | 0.15423 | 0.00071102
Vector Lines | 2013 | 2012-09-25 | 0.10992 | 0.0010698
Vector Lines | 2013 | 2012-09-26 | 0.17306 | 0.0027108
Vector Lines | 2013 | 2012-09-27 | 0.073523 | 0.00056658
Vector Lines | 2013 | 2012-09-28 | 0.10907 | 0.0018377
Vector Lines | 2013 | 2012-09-29 | 0.068072 | 0.00028329
Vector Lines | 2013 | 2012-09-30 | 0.16305 | 0.0025478
Vector Lines | 2013 | 2012-10-01 | 0.13342 | 0.0012021
Vector Lines | 2013 | 2012-10-02 | 0.48006 | 0.0057711
Vector Lines | 2013 | 2012-10-03 | 0.93731 | 0.0088603
Vector Lines | 2013 | 2012-10-04 | 0.05177 | 0.00055167
Vector Lines | 2013 | 2012-10-05 | 0.3275 | 0.0020585
Vector Lines | 2013 | 2012-10-06 | 0.17772 | 0.00079303
Vector Lines | 2013 | 2012-10-07 | 0.39728 | 0.0077104
Vector Lines | 2013 | 2012-10-08 | 0.43143 | 0.0048439
Vector Lines | 2013 | 2012-10-09 | 0.35915 | 0.0069434
Vector Lines | 2013 | 2012-10-10 | 0.042748 | 0.00044544
Vector Lines | 2013 | 2012-10-11 | 0.010392 | 6.8959e-05
Vector Lines | 2013 | 2012-10-12 | 0.30165 | 0.0043342
Vector Lines | 2013 | 2012-10-13 | 3.3776 | 0.03909
Vector Lines | 2013 | 2012-10-14 | 0.62453 | 0.0089759
Vector Lines | 2013 | 2012-10-15 | 0.49513 | 0.014763
Vector Lines | 2013 | 2012-10-16 | 0.081151 | 0.0005787
Vector Lines | 2013 | 2012-10-17 | 0.12245 | 0.00079862
Vector Lines | 2013 | 2012-10-18 | 0.58587 | 0.0048532
Vector Lines | 2013 | 2012-10-19 | 0.076087 | 0.00058615
Vector Lines | 2013 | 2012-10-20 | 0.084318 | 0.00036343
Vector Lines | 2013 | 2012-10-21 | 0.51644 | 0.0094809
Vector Lines | 2013 | 2012-10-22 | 0.062294 | 0.00065791
Vector Lines | 2013 | 2012-10-23 | 0.012344 | 0.00026465
Vector Lines | 2013 | 2012-10-24 | 0.26802 | 0.0034424
Vector Lines | 2013 | 2012-10-25 | 0.096778 | 0.00096077
Vector Lines | 2013 | 2012-10-26 | 0.034666 | 0.00037834
Vector Lines | 2013 | 2012-10-27 | 0.11616 | 0.00090486
Vector Lines | 2013 | 2012-10-28 | 0.48729 | 0.0055288
Vector Lines | 2013 | 2012-10-29 | 0.57054 | 0.0082369
Vector Lines | 2013 | 2012-10-30 | 0.016505 | 8.0142e-05
Vector Lines | 2013 | 2012-10-31 | 0.033953 | 0.00026465
Vector Lines | 2013 | 2012-11-01 | 0.22682 | 0.0021415
Vector Lines | 2013 | 2012-11-02 | 0.21663 | 0.0012944
Vector Lines | 2013 | 2012-11-03 | 0.012308 | 0.00043892
Vector Lines | 2013 | 2012-11-04 | 0.0007455 | 6.2436e-05
Vector Lines | 2013 | 2012-11-05 | 0.056224 | 0.0010307
Vector Lines | 2013 | 2012-11-06 | 0.003269 | 1.7706e-05
Vector Lines | 2013 | 2012-11-07 | 0.1266 | 0.004255
Vector Lines | 2013 | 2012-11-08 | 0.015636 | 0.00025534
Vector Lines | 2013 | 2012-11-09 | 0.16198 | 0.0027313
Vector Lines | 2013 | 2012-11-10 | 0.087125 | 0.00030845
Vector Lines | 2013 | 2012-11-11 | 0.30035 | 0.0027071
Vector Lines | 2013 | 2012-11-12 | 0.21954 | 0.0050797
Vector Lines | 2013 | 2012-11-13 | 0.096293 | 0.0013494
Vector Lines | 2013 | 2012-11-14 | 0.00054049 | 3.7275e-06
Vector Lines | 2013 | 2012-11-15 | 0.81407 | 0.014824
Vector Lines | 2013 | 2012-11-16 | 0.11864 | 0.0012142
Vector Lines | 2013 | 2012-11-17
Vector Lines | 2013 | 2012-11-18 | 0.36584 | 0.0031451
Vector Lines | 2013 | 2012-11-19 | 0.47421 | 0.0088939
Vector Lines | 2013 | 2012-11-20 | 0.085971 | 0.0032318
Vector Lines | 2013 | 2012-11-21 | 0.18358 | 0.0010931
Vector Lines | 2013 | 2012-11-22 | 0.083505 | 0.0018069
Vector Lines | 2013 | 2012-11-23 | 0.04343 | 0.00022086
Vector Lines | 2013 | 2012-11-24 | 0.0059137 | 7.2687e-05
Vector Lines | 2013 | 2012-11-25 | 0.090203 | 0.00073246
Vector Lines | 2013 | 2012-11-26 | 0.091676 | 0.0054086
Vector Lines | 2013 | 2012-11-27 | 0.076281 | 0.00035784
Vector Lines | 2013 | 2012-11-28 | 0.1592 | 0.00086572
Vector Lines | 2013 | 2012-11-29 | 0.26954 | 0.0023875
Vector Lines | 2013 | 2012-11-30 | 0.044485 | 0.0003187
Vector Lines | 2013 | 2012-12-01 | 0.010978 | 0.0054161
Vector Lines | 2013 | 2012-12-02 | 0.087515 | 0.0020837
Vector Lines | 2013 | 2012-12-03 | 0.33394 | 0.0028832
Vector Lines | 2013 | 2012-12-04 | 0.35367 | 0.0029811
Vector Lines | 2013 | 2012-12-05 | 0.16251 | 0.0022999
Vector Lines | 2013 | 2012-12-06 | 3.4316 | 0.010473
Vector Lines | 2013 | 2012-12-07 | 0.055615 | 2.982e-05
Vector Lines | 2013 | 2012-12-08 | 2.5161e-05 | 9.3188e-07
Vector Lines | 2013 | 2012-12-09 | 0.011337 | 0.00097568
Vector Lines | 2013 | 2012-12-10 | 0.06632 | 0.0016643
Vector Lines | 2013 | 2012-12-11 | 0.046713 | 0.00037182
Vector Lines | 2013 | 2012-12-12 | 0.1329 | 0.0014537
Vector Lines | 2013 | 2012-12-13 | 0.13612 | 0.00079303
Vector Lines | 2013 | 2012-12-14 | 0.13527 | 0.00086572
Vector Lines | 2013 | 2012-12-15 | 0.022121 | 0.00040257
Vector Lines | 2013 | 2012-12-16 | 0.17342 | 0.0022989
Vector Lines | 2013 | 2012-12-17 | 0.28257 | 0.0042009
Vector Lines | 2013 | 2012-12-18 | 0.1894 | 0.0022626
Vector Lines | 2013 | 2012-12-19 | 0.46658 | 0.0058205
Vector Lines | 2013 | 2012-12-20 | 0.30612 | 0.0052586
Vector Lines | 2013 | 2012-12-21 | 0.43875 | 0.0074131
Vector Lines | 2013 | 2012-12-22 | 0.096409 | 0.0017855
Vector Lines | 2013 | 2012-12-23
Vector Lines | 2013 | 2012-12-24 | 0.10006 | 0.00058149
Vector Lines | 2013 | 2012-12-25 | 0.018934 | 0.00051813
Vector Lines | 2013 | 2012-12-26 | 0.14466 | 0.0020893
Vector Lines | 2013 | 2012-12-27 | 0.14425 | 0.00091511
Vector Lines | 2013 | 2012-12-28 | 0.25408 | 0.0048085
Vector Lines | 2013 | 2012-12-29 | 0.18704 | 0.003392
Vector Lines | 2013 | 2012-12-30 | 0.54346 | 0.0070786
Vector Lines | 2013 | 2012-12-31
Vector Lines | 2013 | 2013-01-01 | 0.042512 | 0.00063181
Vector Lines | 2013 | 2013-01-02
Vector Lines | 2013 | 2013-01-03
Vector Lines | 2013 | 2013-01-04 | 0.12096 | 0.00084801
Vector Lines | 2013 | 2013-01-05 | 0.016028 | 0.00064113
Vector Lines | 2013 | 2013-01-06 | 0.014964 | 0.0018805
Vector Lines | 2013 | 2013-01-07 | 1.0216 | 0.0096161
Vector Lines | 2013 | 2013-01-08 | 0.59955 | 0.0042512
Vector Lines | 2013 | 2013-01-09 | 0.032127 | 0.00012767
Vector Lines | 2013 | 2013-01-10 | 0.18795 | 0.0011276
Vector Lines | 2013 | 2013-01-11 | 0.074035 | 0.00038207
Vector Lines | 2013 | 2013-01-12 | 0.21147 | 0.0021433
Vector Lines | 2013 | 2013-01-13 | 0.077465 | 0.00039139
Vector Lines | 2013 | 2013-01-14 | 0.0035821 | 2.7956e-05
Vector Lines | 2013 | 2013-01-15 | 1.5885 | 0.018308
Vector Lines | 2013 | 2013-01-16 | 0.097357 | 0.00032709
Vector Lines | 2013 | 2013-01-17 | 0.31785 | 0.0036893
Vector Lines | 2013 | 2013-01-18 | 0.52791 | 0.004405
Vector Lines | 2013 | 2013-01-19 | 0.00025068 | 9.3188e-07
Vector Lines | 2013 | 2013-01-20 | 0.74244 | 0.010865
Vector Lines | 2013 | 2013-01-21 | 0.0058429 | 3.5411e-05
Vector Lines | 2013 | 2013-01-22 | 0.22817 | 0.0036669
Vector Lines | 2013 | 2013-01-23 | 0.050015 | 0.0003625
Vector Lines | 2013 | 2013-01-24 | 0.29637 | 0.0027127
Vector Lines | 2013 | 2013-01-25 | 0.17298 | 0.00084987
Vector Lines | 2013 | 2013-01-26 | 0.14694 | 0.00047712
Vector Lines | 2013 | 2013-01-27 | 0.00053676 | 1.8638e-06
Vector Lines | 2013 | 2013-01-28 | 0.031594 | 0.00060572
Vector Lines | 2013 | 2013-01-29 | 0.10221 | 0.00074178
Vector Lines | 2013 | 2013-01-30 | 0.065844 | 0.00062063
Vector Lines | 2013 | 2013-01-31 | 0.043709 | 0.0053937
Vector Lines | 2013 | 2013-02-01 | 0.13134 | 0.0008564
Vector Lines | 2013 | 2013-02-02 | 0.86419 | 0.0099413
Vector Lines | 2013 | 2013-02-03 | 0.97519 | 0.0066797
Vector Lines | 2013 | 2013-02-04 | 2.0915 | 0.018639
Vector Lines | 2013 | 2013-02-05 | 0.36859 | 0.0053313
Vector Lines | 2013 | 2013-02-06 | 0.12688 | 0.0064244
Vector Lines | 2013 | 2013-02-07 | 0.16088 | 0.00076041
Vector Lines | 2013 | 2013-02-08 | 0.20802 | 0.00099152
Vector Lines | 2013 | 2013-02-09 | 0.005459 | 0.00012394
Vector Lines | 2013 | 2013-02-10 | 0.014821 | 0.00026931
Vector Lines | 2013 | 2013-02-11 | 0.39982 | 0.0029429
Vector Lines | 2013 | 2013-02-12 | 0.063924 | 0.00031032
Vector Lines | 2013 | 2013-02-13 | 0.044219 | 0.00016774
Vector Lines | 2013 | 2013-02-14 | 0.62986 | 0.0050443
Vector Lines | 2013 | 2013-02-15 | 0.020618 | 6.3368e-05
Vector Lines | 2013 | 2013-02-16 | 0.15106 | 0.0016625
Vector Lines | 2013 | 2013-02-17 | 0.11783 | 0.00096636
Vector Lines | 2013 | 2013-02-18 | 0.096092 | 0.0028916
Vector Lines | 2013 | 2013-02-19 | 0.035571 | 0.00019569
Vector Lines | 2013 | 2013-02-20 | 0.12892 | 0.0012962
Vector Lines | 2013 | 2013-02-21 | 0.46031 | 0.0020958
Vector Lines | 2013 | 2013-02-22 | 0.0019532 | 1.5842e-05
Vector Lines | 2013 | 2013-02-23 | 0.29915 | 0.0025534
Vector Lines | 2013 | 2013-02-24 | 0.28763 | 0.0068363
Vector Lines | 2013 | 2013-02-25 | 0.095456 | 0.00076041
Vector Lines | 2013 | 2013-02-26 | 0.1034 | 0.0020706
Vector Lines | 2013 | 2013-02-27 | 0.24986 | 0.0023269
Vector Lines | 2013 | 2013-02-28 | 0.5829 | 0.0057264
Vector Lines | 2013 | 2013-03-01 | 0.093567 | 0.0015376
Vector Lines | 2013 | 2013-03-02 | 0.0020473 | 1.2114e-05
Vector Lines | 2013 | 2013-03-03 | 0.74515 | 0.0065278
Vector Lines | 2013 | 2013-03-04 | 0.81515 | 0.0045066
Vector Lines | 2013 | 2013-03-05 | 0.29467 | 0.0010605
Vector Lines | 2013 | 2013-03-06 | 0.52061 | 0.010854
Vector Lines | 2013 | 2013-03-07 | 0.3 | 0.002504
Vector Lines | 2013 | 2013-03-08 | 0.28693 | 0.0045606
Vector Lines | 2013 | 2013-03-09 | 0.037637 | 0.0016429
Vector Lines | 2013 | 2013-03-10 | 0.16023 | 0.0019961
Vector Lines | 2013 | 2013-03-11 | 0.25192 | 0.0063591
Vector Lines | 2013 | 2013-03-12 | 0.042593 | 0.0002367
Vector Lines | 2013 | 2013-03-13 | 0.20324 | 0.0026382
Vector Lines | 2013 | 2013-03-14 | 0.0070012 | 0.00026465
Vector Lines | 2013 | 2013-03-15 | 0.061144 | 0.00050601
Vector Lines | 2013 | 2013-03-16 | 0.15351 | 0.00097847
Vector Lines | 2013 | 2013-03-17 | 0.47663 | 0.0079788
Vector Lines | 2013 | 2013-03-18 | 0.20142 | 0.0020576
Vector Lines | 2013 | 2013-03-19 | 0.27724 | 0.003995
Vector Lines | 2013 | 2013-03-20 | 0.26465 | 0.0026913
Vector Lines | 2013 | 2013-03-21 | 0.13853 | 0.0021778
Vector Lines | 2013 | 2013-03-22 | 0.2046 | 0.0013652
Vector Lines | 2013 | 2013-03-23 | 0.12976 | 0.0020166
Vector Lines | 2013 | 2013-03-24 | 0.39688 | 0.0037005
Vector Lines | 2013 | 2013-03-25 | 0.10076 | 0.0030034
Vector Lines | 2013 | 2013-03-26 | 0.18074 | 0.001915
Vector Lines | 2013 | 2013-03-27 | 0.053133 | 0.00025534
Vector Lines | 2013 | 2013-03-28 | 0.059096 | 0.00046035
Vector Lines | 2013 | 2013-03-29
Vector Lines | 2013 | 2013-03-30 | 0.052154 | 0.00010251
Vector Lines | 2013 | 2013-03-31 | 0.077288 | 0.0017575
Vector Lines | 2014 | 2013-04-01 | 0.000611 | 5.5545e-06
Vector Lines | 2014 | 2013-04-02 | 0.34838 | 0.0042011
Vector Lines | 2014 | 2013-04-03 | 0.4078 | 0.0042789
Vector Lines | 2014 | 2013-04-04 | 0.43221 | 0.0051148
Vector Lines | 2014 | 2013-04-05 | 0.17407 | 0.001272
Vector Lines | 2014 | 2013-04-06 | 0.2148 | 0.0022413
Vector Lines | 2014 | 2013-04-07 | 0.020839 | 0.00013238
Vector Lines | 2014 | 2013-04-08 | 0.025355 | 0.00012035
Vector Lines | 2014 | 2013-04-09 | 0.48498 | 0.0059535
Vector Lines | 2014 | 2013-04-10 | 0.035357 | 0.00013423
Vector Lines | 2014 | 2013-04-11 | 0.12939 | 0.00046195
Vector Lines | 2014 | 2013-04-12 | 0.044433 | 0.00075542
Vector Lines | 2014 | 2013-04-13 | 0.18168 | 0.0030643
Vector Lines | 2014 | 2013-04-14 | 0.15526 | 0.0030633
Vector Lines | 2014 | 2013-04-15 | 1.4462 | 0.017298
Vector Lines | 2014 | 2013-04-16 | 2.2302 | 0.028652
Vector Lines | 2014 | 2013-04-17 | 0.7461 | 0.015368
Vector Lines | 2014 | 2013-04-18 | 0.18792 | 0.011524
Vector Lines | 2014 | 2013-04-19 | 0.56388 | 0.006534
Vector Lines | 2014 | 2013-04-20 | 0.13585 | 0.00074801
Vector Lines | 2014 | 2013-04-21 | 0.3871 | 0.0051139
Vector Lines | 2014 | 2013-04-22 | 0.21009 | 0.0030272
Vector Lines | 2014 | 2013-04-23 | 0.18535 | 0.00217
Vector Lines | 2014 | 2013-04-24 | 0.073977 | 0.00027032
Vector Lines | 2014 | 2013-04-25 | 0.026708 | 0.00023144
Vector Lines | 2014 | 2013-04-26 | 0.18834 | 0.0024421
Vector Lines | 2014 | 2013-04-27 | 0.0044751 | 1.8515e-05
Vector Lines | 2014 | 2013-04-28 | 0.0053027 | 7.0358e-05
Vector Lines | 2014 | 2013-04-29 | 0.2765 | 0.0032605
Vector Lines | 2014 | 2013-04-30 | 0.6057 | 0.00601
Vector Lines | 2014 | 2013-05-01 | 0.061231 | 0.00032124
Vector Lines | 2014 | 2013-05-02 | 0.42931 | 0.0054092
Vector Lines | 2014 | 2013-05-03 | 0.19757 | 0.0025801
Vector Lines | 2014 | 2013-05-04 | 0.069285 | 0.0013072
Vector Lines | 2014 | 2013-05-05 | 2.266 | 0.013945
Vector Lines | 2014 | 2013-05-06 | 2.257 | 0.020215
Vector Lines | 2014 | 2013-05-07 | 0.4718 | 0.0059906
Vector Lines | 2014 | 2013-05-08 | 0.25533 | 0.0053805
Vector Lines | 2014 | 2013-05-09 | 1.2777 | 0.016911
Vector Lines | 2014 | 2013-05-10 | 0.32288 | 0.012195
Vector Lines | 2014 | 2013-05-11 | 0.34509 | 0.0038641
Vector Lines | 2014 | 2013-05-12 | 0.31626 | 0.0045584
Vector Lines | 2014 | 2013-05-13 | 0.2184 | 0.0037521
Vector Lines | 2014 | 2013-05-14 | 0.16724 | 0.0030485
Vector Lines | 2014 | 2013-05-15 | 0.14965 | 0.00044251
Vector Lines | 2014 | 2013-05-16 | 0.10004 | 0.00031753
Vector Lines | 2014 | 2013-05-17 | 0.76232 | 0.0082791
Vector Lines | 2014 | 2013-05-18 | 0.28045 | 0.0047232
Vector Lines | 2014 | 2013-05-19 | 0.090326 | 0.00027217
Vector Lines | 2014 | 2013-05-20 | 0.18143 | 0.0019404
Vector Lines | 2014 | 2013-05-21 | 0.39038 | 0.0054823
Vector Lines | 2014 | 2013-05-22 | 0.034852 | 0.00019626
Vector Lines | 2014 | 2013-05-23 | 0.39563 | 0.0039558
Vector Lines | 2014 | 2013-05-24 | 0.064679 | 0.00036938
Vector Lines | 2014 | 2013-05-25 | 0.0080856 | 0.00021663
Vector Lines | 2014 | 2013-05-26 | 0.15484 | 0.00067488
Vector Lines | 2014 | 2013-05-27 | 0.24476 | 0.0029476
Vector Lines | 2014 | 2013-05-28 | 3.2896 | 0.014244
Vector Lines | 2014 | 2013-05-29 | 0.18517 | 0.0026551
Vector Lines | 2014 | 2013-05-30 | 0.67684 | 0.0060008
Vector Lines | 2014 | 2013-05-31 | 0.17473 | 0.0018885
Vector Lines | 2014 | 2013-06-01 | 0.6241 | 0.0046825
Vector Lines | 2014 | 2013-06-02 | 0.024451 | 0.0002407
Vector Lines | 2014 | 2013-06-03 | 0.19482 | 0.0013349
Vector Lines | 2014 | 2013-06-04 | 0.60275 | 0.01131
Vector Lines | 2014 | 2013-06-05 | 0.27917 | 0.0036373
Vector Lines | 2014 | 2013-06-06 | 0.074037 | 0.00024718
Vector Lines | 2014 | 2013-06-07 | 0.027593 | 0.00019071
Vector Lines | 2014 | 2013-06-08 | 0.028415 | 0.00052768
Vector Lines | 2014 | 2013-06-09 | 0.10388 | 0.0016108
Vector Lines | 2014 | 2013-06-10 | 0.0028476 | 0.00014257
Vector Lines | 2014 | 2013-06-11 | 0.19034 | 0.001147
Vector Lines | 2014 | 2013-06-12 | 0.15342 | 0.0018043
Vector Lines | 2014 | 2013-06-13 | 0.018581 | 0.00022496
Vector Lines | 2014 | 2013-06-14 | 0.06554 | 0.0015386
Vector Lines | 2014 | 2013-06-15 | 0.042764 | 0.0024884
Vector Lines | 2014 | 2013-06-16 | 2.1126 | 0.029454
Vector Lines | 2014 | 2013-06-17 | 0.043856 | 0.00048787
Vector Lines | 2014 | 2013-06-18 | 0.02515 | 0.00016664
Vector Lines | 2014 | 2013-06-19 | 0.56433 | 0.0052305
Vector Lines | 2014 | 2013-06-20 | 1.069 | 0.0073588
Vector Lines | 2014 | 2013-06-21 | 0.74455 | 0.0059276
Vector Lines | 2014 | 2013-06-22 | 0.0071718 | 0.00033605
Vector Lines | 2014 | 2013-06-23 | 0.22251 | 0.0034503
Vector Lines | 2014 | 2013-06-24 | 0.031789 | 0.00033883
Vector Lines | 2014 | 2013-06-25 | 0.23087 | 0.00222
Vector Lines | 2014 | 2013-06-26 | 0.31057 | 0.0054712
Vector Lines | 2014 | 2013-06-27
Vector Lines | 2014 | 2013-06-28 | 0.20172 | 0.0025921
Vector Lines | 2014 | 2013-06-29 | 0.35214 | 0.0067488
Vector Lines | 2014 | 2013-06-30 | 0.00084799 | 0.000424
Vector Lines | 2014 | 2013-07-01 | 0.048649 | 0.00033512
Vector Lines | 2014 | 2013-07-02 | 0.25584 | 0.0039456
Vector Lines | 2014 | 2013-07-03 | 0.59287 | 0.008143
Vector Lines | 2014 | 2013-07-04 | 0.35087 | 0.0095909
Vector Lines | 2014 | 2013-07-05 | 0.31461 | 0.0035429
Vector Lines | 2014 | 2013-07-06 | 0.00078227 | 3.703e-06
Vector Lines | 2014 | 2013-07-07 | 0.13534 | 0.0056684
Vector Lines | 2014 | 2013-07-08 | 0.66734 | 0.011615
Vector Lines | 2014 | 2013-07-09 | 0.89712 | 0.013149
Vector Lines | 2014 | 2013-07-10 | 0.0035771 | 0.00024625
Vector Lines | 2014 | 2013-07-11 | 0.00187 | 0.00023422
Vector Lines | 2014 | 2013-07-12 | 0.006571 | 2.9624e-05
Vector Lines | 2014 | 2013-07-13 | 0.047661 | 0.00014442
Vector Lines | 2014 | 2013-07-14 | 0.0091187 | 0.00015738
Vector Lines | 2014 | 2013-07-15 | 0.70431 | 0.0071561
Vector Lines | 2014 | 2013-07-16 | 0.16165 | 0.0020098
Vector Lines | 2014 | 2013-07-17 | 0.27487 | 0.0023773
Vector Lines | 2014 | 2013-07-18 | 0.096907 | 0.00046473
Vector Lines | 2014 | 2013-07-19
Vector Lines | 2014 | 2013-07-20 | 0.39469 | 0.0040798
Vector Lines | 2014 | 2013-07-21 | 0.10511 | 0.0005536
Vector Lines | 2014 | 2013-07-22 | 0.089067 | 0.0016238
Vector Lines | 2014 | 2013-07-23 | 0.050111 | 0.00032124
Vector Lines | 2014 | 2013-07-24 | 0.46519 | 0.00091743
Vector Lines | 2014 | 2013-07-25 | 0.0078439 | 4.1659e-05
Vector Lines | 2014 | 2013-07-26 | 0.077473 | 0.0013368
Vector Lines | 2014 | 2013-07-27 | 0.011718 | 0.00014164
Vector Lines | 2014 | 2013-07-28 | 0.42149 | 0.0098473
Vector Lines | 2014 | 2013-07-29 | 0.018252 | 6.11e-05
Vector Lines | 2014 | 2013-07-30 | 0.25003 | 0.0032411
Vector Lines | 2014 | 2013-07-31 | 0.46355 | 0.0021811
Vector Lines | 2014 | 2013-08-01 | 0.034174 | 0.00017127
Vector Lines | 2014 | 2013-08-02 | 0.24717 | 0.0046297
Vector Lines | 2014 | 2013-08-03 | 0.11972 | 0.0013368
Vector Lines | 2014 | 2013-08-04 | 0.30857 | 0.0023274
Vector Lines | 2014 | 2013-08-05 | 0.075318 | 0.00086929
Vector Lines | 2014 | 2013-08-06 | 0.18584 | 0.0012924
Vector Lines | 2014 | 2013-08-07 | 0.037677 | 0.00049343
Vector Lines | 2014 | 2013-08-08 | 0.22866 | 0.0018802
Vector Lines | 2014 | 2013-08-09 | 0.44608 | 0.0058915
Vector Lines | 2014 | 2013-08-10 | 0.30922 | 0.0071839
Vector Lines | 2014 | 2013-08-11 | 0.56568 | 0.0051074
Vector Lines | 2014 | 2013-08-12 | 0.16067 | 0.001297
Vector Lines | 2014 | 2013-08-13 | 0.10201 | 0.0011442
Vector Lines | 2014 | 2013-08-14 | 0.50753 | 0.0070858
Vector Lines | 2014 | 2013-08-15 | 0.96251 | 0.0099389
Vector Lines | 2014 | 2013-08-16 | 0.20124 | 0.0049435
Vector Lines | 2014 | 2013-08-17 | 0.010757 | 2.2218e-05
Vector Lines | 2014 | 2013-08-18 | 0.09193 | 0.00059341
Vector Lines | 2014 | 2013-08-19 | 0.074223 | 0.0003916
Vector Lines | 2014 | 2013-08-20 | 0.12767 | 0.00090909
Vector Lines | 2014 | 2013-08-21 | 0.371 | 0.0018848
Vector Lines | 2014 | 2013-08-22 | 0.025872 | 0.00010276
Vector Lines | 2014 | 2013-08-23 | 0.097936 | 0.0024135
Vector Lines | 2014 | 2013-08-24 | 0.065451 | 0.00021848
Vector Lines | 2014 | 2013-08-25 | 0.14724 | 0.0026717
Vector Lines | 2014 | 2013-08-26 | 0.0091326 | 4.2585e-05
Vector Lines | 2014 | 2013-08-27 | 0.1569 | 0.001309
Vector Lines | 2014 | 2013-08-28 | 0.011549 | 0.00012127
Vector Lines | 2014 | 2013-08-29 | 0.021709 | 0.00012961
Vector Lines | 2014 | 2013-08-30 | 0.30747 | 0.0039808
Vector Lines | 2014 | 2013-08-31 | 0.24918 | 0.00087854
Vector Lines | 2014 | 2013-09-01 | 0.00026292 | 1.8515e-06
Vector Lines | 2014 | 2013-09-02 | 0.056631 | 0.0003092
Vector Lines | 2014 | 2013-09-03 | 0.021446 | 9.6279e-05
Vector Lines | 2014 | 2013-09-04 | 0.11077 | 0.0015025
Vector Lines | 2014 | 2013-09-05 | 0.70194 | 0.0075042
Vector Lines | 2014 | 2013-09-06 | 0.17862 | 0.0028791
Vector Lines | 2014 | 2013-09-07 | 0.011827 | 0.00016941
Vector Lines | 2014 | 2013-09-08
Vector Lines | 2014 | 2013-09-09 | 0.10257 | 0.0014803
Vector Lines | 2014 | 2013-09-10 | 0.031546 | 9.165e-05
Vector Lines | 2014 | 2013-09-11 | 0.37259 | 0.0013007
Vector Lines | 2014 | 2013-09-12 | 0.29964 | 0.0031531
Vector Lines | 2014 | 2013-09-13 | 0.25596 | 0.0028717
Vector Lines | 2014 | 2013-09-14 | 0.069308 | 0.00058878
Vector Lines | 2014 | 2013-09-15 | 0.011428 | 0.00012313
Vector Lines | 2014 | 2013-09-16 | 0.78362 | 0.0069256
Vector Lines | 2014 | 2013-09-17 | 0.16443 | 0.0014618
Vector Lines | 2014 | 2013-09-18 | 0.14441 | 0.0015812
Vector Lines | 2014 | 2013-09-19 | 0.25249 | 0.0020182
Vector Lines | 2014 | 2013-09-20 | 0.13369 | 0.0013238
Vector Lines | 2014 | 2013-09-21 | 0.24965 | 0.0022542
Vector Lines | 2014 | 2013-09-22 | 1.3367 | 0.015921
Vector Lines | 2014 | 2013-09-23 | 0.022094 | 0.00016016
Vector Lines | 2014 | 2013-09-24 | 3.4237 | 0.030255
Vector Lines | 2014 | 2013-09-25 | 1.7461 | 0.017667
Vector Lines | 2014 | 2013-09-26 | 0.36028 | 0.0042789
Vector Lines | 2014 | 2013-09-27 | 0.15745 | 0.0014905
Vector Lines | 2014 | 2013-09-28 | 0.42146 | 0.003566
Vector Lines | 2014 | 2013-09-29 | 0.18453 | 0.0037789
Vector Lines | 2014 | 2013-09-30 | 0.20119 | 0.0030772
Vector Lines | 2014 | 2013-10-01 | 0.13845 | 0.00057304
Vector Lines | 2014 | 2013-10-02 | 0.010285 | 0.00012775
Vector Lines | 2014 | 2013-10-03 | 0.10245 | 0.00022959
Vector Lines | 2014 | 2013-10-04 | 0.22914 | 0.003279
Vector Lines | 2014 | 2013-10-05 | 0.33425 | 0.0043085
Vector Lines | 2014 | 2013-10-06 | 0.15521 | 0.0015942
Vector Lines | 2014 | 2013-10-07 | 0.20568 | 0.0024616
Vector Lines | 2014 | 2013-10-08 | 0.75065 | 0.0045631
Vector Lines | 2014 | 2013-10-09 | 0.88251 | 0.0099556
Vector Lines | 2014 | 2013-10-10 | 0.26578 | 0.0017164
Vector Lines | 2014 | 2013-10-11 | 1.2571 | 0.010222
Vector Lines | 2014 | 2013-10-12 | 1.0342 | 0.011566
Vector Lines | 2014 | 2013-10-13 | 0.0108 | 8.7947e-05
Vector Lines | 2014 | 2013-10-14 | 0.069583 | 0.00106
Vector Lines | 2014 | 2013-10-15 | 2.8026 | 0.032142
Vector Lines | 2014 | 2013-10-16 | 0.72571 | 0.0061794
Vector Lines | 2014 | 2013-10-17 | 0.012054 | 4.8139e-05
Vector Lines | 2014 | 2013-10-18 | 0.0063942 | 2.3144e-05
Vector Lines | 2014 | 2013-10-19 | 0.50469 | 0.0026541
Vector Lines | 2014 | 2013-10-20 | 0.42678 | 0.0015775
Vector Lines | 2014 | 2013-10-21 | 0.011642 | 6.6655e-05
Vector Lines | 2014 | 2013-10-22 | 0.057177 | 0.0010267
Vector Lines | 2014 | 2013-10-23 | 0.18964 | 0.0021709
Vector Lines | 2014 | 2013-10-24 | 0.18269 | 0.0018025
Vector Lines | 2014 | 2013-10-25 | 0.37949 | 0.0064646
Vector Lines | 2014 | 2013-10-26 | 0.0099093 | 6.8506e-05
Vector Lines | 2014 | 2013-10-27 | 0.045249 | 0.00217
Vector Lines | 2014 | 2013-10-28 | 0.0010961 | 2.9624e-05
Vector Lines | 2014 | 2013-10-29 | 0.22279 | 0.0012627
Vector Lines | 2014 | 2013-10-30 | 0.13825 | 0.0035105
Vector Lines | 2014 | 2013-10-31 | 0.40647 | 0.003367
Vector Lines | 2014 | 2013-11-01 | 0.13278 | 0.0029476
Vector Lines | 2014 | 2013-11-02 | 0.45425 | 0.0054277
Vector Lines | 2014 | 2013-11-03 | 0.37548 | 0.0018423
Vector Lines | 2014 | 2013-11-04 | 0.37703 | 0.003691
Vector Lines | 2014 | 2013-11-05 | 0.12091 | 0.0018062
Vector Lines | 2014 | 2013-11-06 | 0.1739 | 0.001958
Vector Lines | 2014 | 2013-11-07 | 3.4037 | 0.039011
Vector Lines | 2014 | 2013-11-08 | 0.39069 | 0.0027541
Vector Lines | 2014 | 2013-11-09 | 0.35449 | 0.0023237
Vector Lines | 2014 | 2013-11-10 | 0.18069 | 0.0039919
Vector Lines | 2014 | 2013-11-11 | 0.24681 | 0.0036123
Vector Lines | 2014 | 2013-11-12 | 0.057063 | 0.00067858
Vector Lines | 2014 | 2013-11-13 | 0.15658 | 0.0012072
Vector Lines | 2014 | 2013-11-14 | 0.26242 | 0.0013461
Vector Lines | 2014 | 2013-11-15 | 0.0099899 | 7.8689e-05
Vector Lines | 2014 | 2013-11-16 | 0.10431 | 0.0017089
Vector Lines | 2014 | 2013-11-17 | 0.33889 | 0.0026745
Vector Lines | 2014 | 2013-11-18 | 0.085642 | 0.0004027
Vector Lines | 2014 | 2013-11-19 | 0.70642 | 0.0075921
Vector Lines | 2014 | 2013-11-20 | 0.1034 | 0.0016006
Vector Lines | 2014 | 2013-11-21 | 0.12249 | 0.00043418
Vector Lines | 2014 | 2013-11-22 | 0.024676 | 0.00016293
Vector Lines | 2014 | 2013-11-23 | 0.14483 | 0.0019811
Vector Lines | 2014 | 2013-11-24 | 0.36873 | 0.0051268
Vector Lines | 2014 | 2013-11-25 | 0.27511 | 0.0044853
Vector Lines | 2014 | 2013-11-26 | 0.071785 | 0.00040085
Vector Lines | 2014 | 2013-11-27 | 0.63094 | 0.0066608
Vector Lines | 2014 | 2013-11-28 | 0.89838 | 0.0028847
Vector Lines | 2014 | 2013-11-29 | 0.24473 | 0.0044751
Vector Lines | 2014 | 2013-11-30 | 1.5795 | 0.015044
Vector Lines | 2014 | 2013-12-01 | 0.059857 | 0.0017478
Vector Lines | 2014 | 2013-12-02 | 0.038327 | 0.00031013
Vector Lines | 2014 | 2013-12-03 | 0.53786 | 0.0047464
Vector Lines | 2014 | 2013-12-04 | 0.37421 | 0.0054509
Vector Lines | 2014 | 2013-12-05 | 0.40727 | 0.0039011
Vector Lines | 2014 | 2013-12-06 | 0.35693 | 0.0017414
Vector Lines | 2014 | 2013-12-07 | 0.24553 | 0.0010387
Vector Lines | 2014 | 2013-12-08 | 0.0033873 | 7.4061e-05
Vector Lines | 2014 | 2013-12-09 | 0.13608 | 0.0034827
Vector Lines | 2014 | 2013-12-10 | 0.41368 | 0.0023422
Vector Lines | 2014 | 2013-12-11 | 0.22006 | 0.0043992
Vector Lines | 2014 | 2013-12-12 | 0.29616 | 0.0022755
Vector Lines | 2014 | 2013-12-13 | 0.07657 | 0.00060359
Vector Lines | 2014 | 2013-12-14 | 0.60608 | 0.0074598
Vector Lines | 2014 | 2013-12-15 | 0.59015 | 0.020336
Vector Lines | 2014 | 2013-12-16 | 0.4507 | 0.0037863
Vector Lines | 2014 | 2013-12-17 | 0.10529 | 0.0004527
Vector Lines | 2014 | 2013-12-18 | 0.2761 | 0.0032068
Vector Lines | 2014 | 2013-12-19 | 0.72872 | 0.0049787
Vector Lines | 2014 | 2013-12-20 | 0.010996 | 0.00026014
Vector Lines | 2014 | 2013-12-21 | 0.19106 | 0.0029745
Vector Lines | 2014 | 2013-12-22 | 3.8882e-05 | 5.5545e-06
Vector Lines | 2014 | 2013-12-23 | 0.052468 | 0.00037586
Vector Lines | 2014 | 2013-12-24 | 0.091839 | 0.0026551
Vector Lines | 2014 | 2013-12-25 | 0.41099 | 0.005349
Vector Lines | 2014 | 2013-12-26
Vector Lines | 2014 | 2013-12-27 | 0.022492 | 0.00031476
Vector Lines | 2014 | 2013-12-28 | 0.0016238 | 6.4803e-06
Vector Lines | 2014 | 2013-12-29 | 0.42039 | 0.011403
Vector Lines | 2014 | 2013-12-30 | 0.25633 | 0.00121
Vector Lines | 2014 | 2013-12-31 | 0.012181 | 9.2576e-05
Vector Lines | 2014 | 2014-01-01 | 0.017058 | 0.00015368
Vector Lines | 2014 | 2014-01-02
Vector Lines | 2014 | 2014-01-03 | 0.023923 | 0.00043325
Vector Lines | 2014 | 2014-01-04 | 0.49717 | 0.0070885
Vector Lines | 2014 | 2014-01-05 | 0.41823 | 0.0092446
Vector Lines | 2014 | 2014-01-06 | 0.77028 | 0.014117
Vector Lines | 2014 | 2014-01-07 | 0.15263 | 0.0020163
Vector Lines | 2014 | 2014-01-08 | 0.0069358 | 2.6847e-05
Vector Lines | 2014 | 2014-01-09 | 0.51555 | 0.020028
Vector Lines | 2014 | 2014-01-10 | 0.022616 | 0.00010183
Vector Lines | 2014 | 2014-01-11 | 0.031471 | 0.00027495
Vector Lines | 2014 | 2014-01-12 | 0.20668 | 0.0026384
Vector Lines | 2014 | 2014-01-13 | 0.014906 | 5.8323e-05
Vector Lines | 2014 | 2014-01-14 | 0.075791 | 0.00029347
Vector Lines | 2014 | 2014-01-15 | 0.38184 | 0.0048519
Vector Lines | 2014 | 2014-01-16 | 0.12663 | 0.0015192
Vector Lines | 2014 | 2014-01-17 | 1.7977 | 0.0096334
Vector Lines | 2014 | 2014-01-18 | 0.11684 | 0.00029161
Vector Lines | 2014 | 2014-01-19 | 0.0058415 | 2.6847e-05
Vector Lines | 2014 | 2014-01-20 | 0.35048 | 0.0047501
Vector Lines | 2014 | 2014-01-21 | 2.7821 | 0.030262
Vector Lines | 2014 | 2014-01-22 | 0.074797 | 0.0004925
Vector Lines | 2014 | 2014-01-23 | 0.43708 | 0.0051194
Vector Lines | 2014 | 2014-01-24 | 0.027624 | 0.00091002
Vector Lines | 2014 | 2014-01-25 | 0.09173 | 0.0015766
Vector Lines | 2014 | 2014-01-26 | 0.35194 | 0.0053518
Vector Lines | 2014 | 2014-01-27 | 0.39139 | 0.0021977
Vector Lines | 2014 | 2014-01-28 | 0.50338 | 0.0047251
Vector Lines | 2014 | 2014-01-29 | 0.21691 | 0.00197
Vector Lines | 2014 | 2014-01-30 | 0.087825 | 0.00048787
Vector Lines | 2014 | 2014-01-31 | 0.777 | 0.010577
Vector Lines | 2014 | 2014-02-01 | 0.045506 | 0.00059619
Vector Lines | 2014 | 2014-02-02 | 0.098088 | 0.0050713
Vector Lines | 2014 | 2014-02-03 | 0.16744 | 0.001122
Vector Lines | 2014 | 2014-02-04 | 0.11023 | 0.0013053
Vector Lines | 2014 | 2014-02-05 | 0.18275 | 0.00094798
Vector Lines | 2014 | 2014-02-06 | 0.36608 | 0.0045927
Vector Lines | 2014 | 2014-02-07 | 0.7947 | 0.0092224
Vector Lines | 2014 | 2014-02-08 | 0.9888 | 0.0060091
Vector Lines | 2014 | 2014-02-09 | 0.033129 | 0.00025181
Vector Lines | 2014 | 2014-02-10 | 0.59076 | 0.0046714
Vector Lines | 2014 | 2014-02-11 | 0.20691 | 0.0034151
Vector Lines | 2014 | 2014-02-12 | 0.24656 | 0.0017747
Vector Lines | 2014 | 2014-02-13 | 0.13363 | 0.00066562
Vector Lines | 2014 | 2014-02-14 | 0.052485 | 0.00044066
Vector Lines | 2014 | 2014-02-15 | 0.010272 | 0.00017404
Vector Lines | 2014 | 2014-02-16 | 0.11696 | 0.0020746
Vector Lines | 2014 | 2014-02-17 | 0.061695 | 0.00023885
Vector Lines | 2014 | 2014-02-18 | 0.5399 | 0.0049824
Vector Lines | 2014 | 2014-02-19 | 0.33058 | 0.0036493
Vector Lines | 2014 | 2014-02-20 | 0.26926 | 0.0011192
Vector Lines | 2014 | 2014-02-21 | 0.016686 | 9.165e-05
Vector Lines | 2014 | 2014-02-22 | 0.30602 | 0.0044455
Vector Lines | 2014 | 2014-02-23 | 0.40549 | 0.0061767
Vector Lines | 2014 | 2014-02-24 | 0.11047 | 0.00074894
Vector Lines | 2014 | 2014-02-25 | 0.013071 | 8.2392e-05
Vector Lines | 2014 | 2014-02-26 | 0.095428 | 0.00070913
Vector Lines | 2014 | 2014-02-27 | 0.2339 | 0.0012988
Vector Lines | 2014 | 2014-02-28 | 0.13675 | 0.0010665
Vector Lines | 2014 | 2014-03-01 | 0.58908 | 0.0057897
Vector Lines | 2014 | 2014-03-02 | 0.053672 | 0.00080356
Vector Lines | 2014 | 2014-03-03 | 0.27864 | 0.0015118
Vector Lines | 2014 | 2014-03-04 | 0.19628 | 0.0046538
Vector Lines | 2014 | 2014-03-05 | 0.15812 | 0.0020422
Vector Lines | 2014 | 2014-03-06 | 0.21682 | 0.0010452
Vector Lines | 2014 | 2014-03-07 | 0.52244 | 0.0042344
Vector Lines | 2014 | 2014-03-08 | 0.14741 | 0.0011489
Vector Lines | 2014 | 2014-03-09 | 0.017595 | 0.00018515
Vector Lines | 2014 | 2014-03-10 | 0.050421 | 0.0015053
Vector Lines | 2014 | 2014-03-11 | 0.1442 | 0.00096371
Vector Lines | 2014 | 2014-03-12 | 0.26516 | 0.0032966
Vector Lines | 2014 | 2014-03-13 | 0.31142 | 0.0025301
Vector Lines | 2014 | 2014-03-14 | 0.22739 | 0.0024514
Vector Lines | 2014 | 2014-03-15 | 3.3736 | 0.038927
Vector Lines | 2014 | 2014-03-16 | 1.2574 | 0.0097853
Vector Lines | 2014 | 2014-03-17 | 0.024823 | 0.00017127
Vector Lines | 2014 | 2014-03-18 | 0.19388 | 0.0013886
Vector Lines | 2014 | 2014-03-19 | 0.088449 | 0.00073875
Vector Lines | 2014 | 2014-03-20 | 0.21023 | 0.0017765
Vector Lines | 2014 | 2014-03-21 | 0.43116 | 0.0036577
Vector Lines | 2014 | 2014-03-22 | 0.1256 | 0.0011331
Vector Lines | 2014 | 2014-03-23 | 0.08864 | 0.00044344
Vector Lines | 2014 | 2014-03-24 | 0.17102 | 0.0010378
Vector Lines | 2014 | 2014-03-25 | 0.39447 | 0.0036503
Vector Lines | 2014 | 2014-03-26 | 0.17504 | 0.0011239
Vector Lines | 2014 | 2014-03-27 | 0.12402 | 0.00077856
Vector Lines | 2014 | 2014-03-28 | 0.027625 | 7.4986e-05
Vector Lines | 2014 | 2014-03-29 | 0.0079337 | 3.5179e-05
Vector Lines | 2014 | 2014-03-30 | 0.018959 | 9.165e-05
Vector Lines | 2014 | 2014-03-31 | 0.07388 | 0.00045362
Wellington Electricity | 2005 | 2004-04-01
Wellington Electricity | 2005 | 2004-04-02 | 0.0025665 | 2.5411e-05
Wellington Electricity | 2005 | 2004-04-03 | 0.001963 | 1.9059e-05
Wellington Electricity | 2005 | 2004-04-04 | 0.069316 | 0.00051458
Wellington Electricity | 2005 | 2004-04-05
Wellington Electricity | 2005 | 2004-04-06
Wellington Electricity | 2005 | 2004-04-07
Wellington Electricity | 2005 | 2004-04-08
Wellington Electricity | 2005 | 2004-04-09
Wellington Electricity | 2005 | 2004-04-10
Wellington Electricity | 2005 | 2004-04-11 | 0.51761 | 0.0050632
Wellington Electricity | 2005 | 2004-04-12
Wellington Electricity | 2005 | 2004-04-13 | 0.026892 | 0.00032399
Wellington Electricity | 2005 | 2004-04-14
Wellington Electricity | 2005 | 2004-04-15
Wellington Electricity | 2005 | 2004-04-16 | 0.11293 | 0.0020075
Wellington Electricity | 2005 | 2004-04-17
Wellington Electricity | 2005 | 2004-04-18 | 0.039502 | 0.00070516
Wellington Electricity | 2005 | 2004-04-19
Wellington Electricity | 2005 | 2004-04-20
Wellington Electricity | 2005 | 2004-04-21
Wellington Electricity | 2005 | 2004-04-22 | 0.40991 | 0.0071914
Wellington Electricity | 2005 | 2004-04-23
Wellington Electricity | 2005 | 2004-04-24
Wellington Electricity | 2005 | 2004-04-25
Wellington Electricity | 2005 | 2004-04-26
Wellington Electricity | 2005 | 2004-04-27
Wellington Electricity | 2005 | 2004-04-28 | 0.32242 | 0.0031002
Wellington Electricity | 2005 | 2004-04-29
Wellington Electricity | 2005 | 2004-04-30
Wellington Electricity | 2005 | 2004-05-01
Wellington Electricity | 2005 | 2004-05-02
Wellington Electricity | 2005 | 2004-05-03
Wellington Electricity | 2005 | 2004-05-04
Wellington Electricity | 2005 | 2004-05-05 | 0.061476 | 0.00060352
Wellington Electricity | 2005 | 2004-05-06 | 0.099778 | 0.0015183
Wellington Electricity | 2005 | 2004-05-07
Wellington Electricity | 2005 | 2004-05-08 | 0.2808 | 0.003691
Wellington Electricity | 2005 | 2004-05-09
Wellington Electricity | 2005 | 2004-05-10
Wellington Electricity | 2005 | 2004-05-11
Wellington Electricity | 2005 | 2004-05-12 | 0.65612 | 0.0062321
Wellington Electricity | 2005 | 2004-05-13 | 0.86707 | 0.0087288
Wellington Electricity | 2005 | 2004-05-14
Wellington Electricity | 2005 | 2004-05-15 | 0.00050823 | 3.1764e-06
Wellington Electricity | 2005 | 2004-05-16
Wellington Electricity | 2005 | 2004-05-17 | 0.14706 | 0.0031319
Wellington Electricity | 2005 | 2004-05-18 | 0.0055143 | 1.2706e-05
Wellington Electricity | 2005 | 2004-05-19
Wellington Electricity | 2005 | 2004-05-20 | 0.018754 | 0.00026047
Wellington Electricity | 2005 | 2004-05-21
Wellington Electricity | 2005 | 2004-05-22 | 0.52055 | 0.0048091
Wellington Electricity | 2005 | 2004-05-23 | 0.077759 | 0.00064799
Wellington Electricity | 2005 | 2004-05-24
Wellington Electricity | 2005 | 2004-05-25 | 1.2597 | 0.015158
Wellington Electricity | 2005 | 2004-05-26
Wellington Electricity | 2005 | 2004-05-27
Wellington Electricity | 2005 | 2004-05-28
Wellington Electricity | 2005 | 2004-05-29 | 0.44265 | 0.0077949
Wellington Electricity | 2005 | 2004-05-30 | 0.050461 | 0.00025729
Wellington Electricity | 2005 | 2004-05-31
Wellington Electricity | 2005 | 2004-06-01
Wellington Electricity | 2005 | 2004-06-02
Wellington Electricity | 2005 | 2004-06-03
Wellington Electricity | 2005 | 2004-06-04
Wellington Electricity | 2005 | 2004-06-05
Wellington Electricity | 2005 | 2004-06-06
Wellington Electricity | 2005 | 2004-06-07
Wellington Electricity | 2005 | 2004-06-08
Wellington Electricity | 2005 | 2004-06-09
Wellington Electricity | 2005 | 2004-06-10 | 0.00040976 | 3.1764e-06
Wellington Electricity | 2005 | 2004-06-11
Wellington Electricity | 2005 | 2004-06-12 | 0.087479 | 0.00074646
Wellington Electricity | 2005 | 2004-06-13
Wellington Electricity | 2005 | 2004-06-14
Wellington Electricity | 2005 | 2004-06-15 | 0.34584 | 0.0046058
Wellington Electricity | 2005 | 2004-06-16
Wellington Electricity | 2005 | 2004-06-17
Wellington Electricity | 2005 | 2004-06-18 | 0.029617 | 0.00066705
Wellington Electricity | 2005 | 2004-06-19
Wellington Electricity | 2005 | 2004-06-20
Wellington Electricity | 2005 | 2004-06-21 | 0.10579 | 0.0026872
Wellington Electricity | 2005 | 2004-06-22 | 0.13748 | 0.0021155
Wellington Electricity | 2005 | 2004-06-23
Wellington Electricity | 2005 | 2004-06-24 | 0.11029 | 0.00078775
Wellington Electricity | 2005 | 2004-06-25 | 0.063751 | 0.00098469
Wellington Electricity | 2005 | 2004-06-26
Wellington Electricity | 2005 | 2004-06-27
Wellington Electricity | 2005 | 2004-06-28
Wellington Electricity | 2005 | 2004-06-29
Wellington Electricity | 2005 | 2004-06-30 | 0.80163 | 0.010574
Wellington Electricity | 2005 | 2004-07-01
Wellington Electricity | 2005 | 2004-07-02
Wellington Electricity | 2005 | 2004-07-03 | 0.091919 | 0.0034686
Wellington Electricity | 2005 | 2004-07-04
Wellington Electricity | 2005 | 2004-07-05 | 0.17864 | 0.0010101
Wellington Electricity | 2005 | 2004-07-06 | 0.009434 | 5.7176e-05
Wellington Electricity | 2005 | 2004-07-07
Wellington Electricity | 2005 | 2004-07-08
Wellington Electricity | 2005 | 2004-07-09
Wellington Electricity | 2005 | 2004-07-10
Wellington Electricity | 2005 | 2004-07-11
Wellington Electricity | 2005 | 2004-07-12 | 0.00043835 | 6.3528e-06
Wellington Electricity | 2005 | 2004-07-13 | 0.001639 | 1.9059e-05
Wellington Electricity | 2005 | 2004-07-14
Wellington Electricity | 2005 | 2004-07-15
Wellington Electricity | 2005 | 2004-07-16
Wellington Electricity | 2005 | 2004-07-17
Wellington Electricity | 2005 | 2004-07-18
Wellington Electricity | 2005 | 2004-07-19
Wellington Electricity | 2005 | 2004-07-20 | 0.17752 | 0.0047011
Wellington Electricity | 2005 | 2004-07-21
Wellington Electricity | 2005 | 2004-07-22
Wellington Electricity | 2005 | 2004-07-23
Wellington Electricity | 2005 | 2004-07-24
Wellington Electricity | 2005 | 2004-07-25 | 0.15112 | 0.0012992
Wellington Electricity | 2005 | 2004-07-26
Wellington Electricity | 2005 | 2004-07-27
Wellington Electricity | 2005 | 2004-07-28
Wellington Electricity | 2005 | 2004-07-29
Wellington Electricity | 2005 | 2004-07-30
Wellington Electricity | 2005 | 2004-07-31
Wellington Electricity | 2005 | 2004-08-01
Wellington Electricity | 2005 | 2004-08-02 | 0.0010609 | 6.3528e-06
Wellington Electricity | 2005 | 2004-08-03
Wellington Electricity | 2005 | 2004-08-04
Wellington Electricity | 2005 | 2004-08-05 | 0.0019059 | 6.3528e-06
Wellington Electricity | 2005 | 2004-08-06 | 0.045359 | 0.00032399
Wellington Electricity | 2005 | 2004-08-07
Wellington Electricity | 2005 | 2004-08-08 | 0.043123 | 0.00052093
Wellington Electricity | 2005 | 2004-08-09
Wellington Electricity | 2005 | 2004-08-10
Wellington Electricity | 2005 | 2004-08-11 | 0.26964 | 0.001747
Wellington Electricity | 2005 | 2004-08-12
Wellington Electricity | 2005 | 2004-08-13 | 0.041567 | 0.00062258
Wellington Electricity | 2005 | 2004-08-14
Wellington Electricity | 2005 | 2004-08-15 | 0.52271 | 0.0062766
Wellington Electricity | 2005 | 2004-08-16 | 0.006086 | 3.1764e-05
Wellington Electricity | 2005 | 2004-08-17 | 2.1026 | 0.031245
Wellington Electricity | 2005 | 2004-08-18 | 2.1026 | 0.031245
Wellington Electricity | 2005 | 2004-08-19 | 0.30032 | 0.0020837
Wellington Electricity | 2005 | 2004-08-20
Wellington Electricity | 2005 | 2004-08-21 | 0.0014929 | 3.1764e-05
Wellington Electricity | 2005 | 2004-08-22 | 0.00071152 | 2.5411e-05
Wellington Electricity | 2005 | 2004-08-23 | 0.045448 | 0.0045296
Wellington Electricity | 2005 | 2004-08-24 | 0.035925 | 0.0044406
Wellington Electricity | 2005 | 2004-08-25
Wellington Electricity | 2005 | 2004-08-26
Wellington Electricity | 2005 | 2004-08-27
Wellington Electricity | 2005 | 2004-08-28
Wellington Electricity | 2005 | 2004-08-29
Wellington Electricity | 2005 | 2004-08-30
Wellington Electricity | 2005 | 2004-08-31
Wellington Electricity | 2005 | 2004-09-01 | 0.82595 | 0.007922
Wellington Electricity | 2005 | 2004-09-02 | 0.0077632 | 0.00016517
Wellington Electricity | 2005 | 2004-09-03
Wellington Electricity | 2005 | 2004-09-04
Wellington Electricity | 2005 | 2004-09-05
Wellington Electricity | 2005 | 2004-09-06
Wellington Electricity | 2005 | 2004-09-07 | 0.11081 | 0.00045105
Wellington Electricity | 2005 | 2004-09-08 | 0.0027476 | 1.5882e-05
Wellington Electricity | 2005 | 2004-09-09 | 0.39417 | 0.0087669
Wellington Electricity | 2005 | 2004-09-10
Wellington Electricity | 2005 | 2004-09-11
Wellington Electricity | 2005 | 2004-09-12 | 0.30271 | 0.0031955
Wellington Electricity | 2005 | 2004-09-13
Wellington Electricity | 2005 | 2004-09-14 | 0.0011435 | 6.3528e-06
Wellington Electricity | 2005 | 2004-09-15
Wellington Electricity | 2005 | 2004-09-16
Wellington Electricity | 2005 | 2004-09-17 | 0.001045 | 3.1764e-06
Wellington Electricity | 2005 | 2004-09-18
Wellington Electricity | 2005 | 2004-09-19
Wellington Electricity | 2005 | 2004-09-20
Wellington Electricity | 2005 | 2004-09-21
Wellington Electricity | 2005 | 2004-09-22
Wellington Electricity | 2005 | 2004-09-23 | 0.15755 | 0.00078775
Wellington Electricity | 2005 | 2004-09-24 | 0.00057176 | 3.1764e-06
Wellington Electricity | 2005 | 2004-09-25 | 0.001261 | 3.1764e-06
Wellington Electricity | 2005 | 2004-09-26 | 0.0047519 | 0.00027952
Wellington Electricity | 2005 | 2004-09-27
Wellington Electricity | 2005 | 2004-09-28 | 0.13885 | 0.0031955
Wellington Electricity | 2005 | 2004-09-29
Wellington Electricity | 2005 | 2004-09-30
Wellington Electricity | 2005 | 2004-10-01
Wellington Electricity | 2005 | 2004-10-02
Wellington Electricity | 2005 | 2004-10-03
Wellington Electricity | 2005 | 2004-10-04
Wellington Electricity | 2005 | 2004-10-05 | 0.057824 | 0.00059717
Wellington Electricity | 2005 | 2004-10-06
Wellington Electricity | 2005 | 2004-10-07 | 0.0055905 | 0.00010165
Wellington Electricity | 2005 | 2004-10-08 | 0.015024 | 0.00027317
Wellington Electricity | 2005 | 2004-10-09
Wellington Electricity | 2005 | 2004-10-10
Wellington Electricity | 2005 | 2004-10-11
Wellington Electricity | 2005 | 2004-10-12
Wellington Electricity | 2005 | 2004-10-13
Wellington Electricity | 2005 | 2004-10-14 | 0.079626 | 0.00059717
Wellington Electricity | 2005 | 2004-10-15 | 0.0043263 | 8.894e-05
Wellington Electricity | 2005 | 2004-10-16
Wellington Electricity | 2005 | 2004-10-17
Wellington Electricity | 2005 | 2004-10-18
Wellington Electricity | 2005 | 2004-10-19
Wellington Electricity | 2005 | 2004-10-20
Wellington Electricity | 2005 | 2004-10-21
Wellington Electricity | 2005 | 2004-10-22
Wellington Electricity | 2005 | 2004-10-23
Wellington Electricity | 2005 | 2004-10-24 | 0.056604 | 0.00020964
Wellington Electricity | 2005 | 2004-10-25
Wellington Electricity | 2005 | 2004-10-26
Wellington Electricity | 2005 | 2004-10-27 | 0.15865 | 0.0016771
Wellington Electricity | 2005 | 2004-10-28
Wellington Electricity | 2005 | 2004-10-29
Wellington Electricity | 2005 | 2004-10-30
Wellington Electricity | 2005 | 2004-10-31
Wellington Electricity | 2005 | 2004-11-01
Wellington Electricity | 2005 | 2004-11-02
Wellington Electricity | 2005 | 2004-11-03 | 0.36761 | 0.0051776
Wellington Electricity | 2005 | 2004-11-04 | 0.066619 | 0.00045423
Wellington Electricity | 2005 | 2004-11-05 | 0.0017788 | 1.2706e-05
Wellington Electricity | 2005 | 2004-11-06
Wellington Electricity | 2005 | 2004-11-07
Wellington Electricity | 2005 | 2004-11-08 | 0.10428 | 0.00084493
Wellington Electricity | 2005 | 2004-11-09
Wellington Electricity | 2005 | 2004-11-10
Wellington Electricity | 2005 | 2004-11-11
Wellington Electricity | 2005 | 2004-11-12
Wellington Electricity | 2005 | 2004-11-13
Wellington Electricity | 2005 | 2004-11-14
Wellington Electricity | 2005 | 2004-11-15 | 0.13136 | 0.0020266
Wellington Electricity | 2005 | 2004-11-16
Wellington Electricity | 2005 | 2004-11-17 | 0.29244 | 0.005635
Wellington Electricity | 2005 | 2004-11-18 | 0.019694 | 0.00019694
Wellington Electricity | 2005 | 2004-11-19 | 0.031971 | 0.00052411
Wellington Electricity | 2005 | 2004-11-20
Wellington Electricity | 2005 | 2004-11-21
Wellington Electricity | 2005 | 2004-11-22 | 0.41459 | 0.0067277
Wellington Electricity | 2005 | 2004-11-23
Wellington Electricity | 2005 | 2004-11-24 | 0.0087669 | 1.2706e-05
Wellington Electricity | 2005 | 2004-11-25 | 0.086259 | 0.0011816
Wellington Electricity | 2005 | 2004-11-26 | 0.26331 | 0.0028207
Wellington Electricity | 2005 | 2004-11-27 | 0.98338 | 0.01052
Wellington Electricity | 2005 | 2004-11-28
Wellington Electricity | 2005 | 2004-11-29
Wellington Electricity | 2005 | 2004-11-30 | 0.0017534 | 6.3528e-06
Wellington Electricity | 2005 | 2004-12-01
Wellington Electricity | 2005 | 2004-12-02
Wellington Electricity | 2005 | 2004-12-03
Wellington Electricity | 2005 | 2004-12-04
Wellington Electricity | 2005 | 2004-12-05 | 1.3251 | 0.012394
Wellington Electricity | 2005 | 2004-12-06 | 0.56221 | 0.0037736
Wellington Electricity | 2005 | 2004-12-07 | 0.19728 | 0.0033416
Wellington Electricity | 2005 | 2004-12-08 | 0.013976 | 0.00012706
Wellington Electricity | 2005 | 2004-12-09
Wellington Electricity | 2005 | 2004-12-10 | 0.31901 | 0.0076552
Wellington Electricity | 2005 | 2004-12-11
Wellington Electricity | 2005 | 2004-12-12
Wellington Electricity | 2005 | 2004-12-13 | 0.3 | 0.0056604
Wellington Electricity | 2005 | 2004-12-14
Wellington Electricity | 2005 | 2004-12-15
Wellington Electricity | 2005 | 2004-12-16 | 0.12998 | 0.0010482
Wellington Electricity | 2005 | 2004-12-17
Wellington Electricity | 2005 | 2004-12-18
Wellington Electricity | 2005 | 2004-12-19 | 0.058446 | 0.00073058
Wellington Electricity | 2005 | 2004-12-20
Wellington Electricity | 2005 | 2004-12-21 | 0.066438 | 0.00040023
Wellington Electricity | 2005 | 2004-12-22 | 0.0013309 | 3.1764e-06
Wellington Electricity | 2005 | 2004-12-23
Wellington Electricity | 2005 | 2004-12-24 | 0.0027698 | 1.2706e-05
Wellington Electricity | 2005 | 2004-12-25
Wellington Electricity | 2005 | 2004-12-26
Wellington Electricity | 2005 | 2004-12-27
Wellington Electricity | 2005 | 2004-12-28
Wellington Electricity | 2005 | 2004-12-29
Wellington Electricity | 2005 | 2004-12-30
Wellington Electricity | 2005 | 2004-12-31 | 0.039032 | 0.00081316
Wellington Electricity | 2005 | 2005-01-01
Wellington Electricity | 2005 | 2005-01-02
Wellington Electricity | 2005 | 2005-01-03
Wellington Electricity | 2005 | 2005-01-04
Wellington Electricity | 2005 | 2005-01-05
Wellington Electricity | 2005 | 2005-01-06 | 0.21635 | 0.0033543
Wellington Electricity | 2005 | 2005-01-07
Wellington Electricity | 2005 | 2005-01-08
Wellington Electricity | 2005 | 2005-01-09 | 0.0078203 | 5.7176e-05
Wellington Electricity | 2005 | 2005-01-10 | 0.45723 | 0.0037164
Wellington Electricity | 2005 | 2005-01-11
Wellington Electricity | 2005 | 2005-01-12
Wellington Electricity | 2005 | 2005-01-13 | 0.01134 | 0.00013341
Wellington Electricity | 2005 | 2005-01-14 | 0.18866 | 0.0016962
Wellington Electricity | 2005 | 2005-01-15
Wellington Electricity | 2005 | 2005-01-16 | 0.021466 | 0.00019694
Wellington Electricity | 2005 | 2005-01-17 | 0.42109 | 0.0066578
Wellington Electricity | 2005 | 2005-01-18 | 0.0041929 | 1.2706e-05
Wellington Electricity | 2005 | 2005-01-19
Wellington Electricity | 2005 | 2005-01-20 | 0.0022616 | 6.3528e-06
Wellington Electricity | 2005 | 2005-01-21
Wellington Electricity | 2005 | 2005-01-22
Wellington Electricity | 2005 | 2005-01-23
Wellington Electricity | 2005 | 2005-01-24 | 0.0044724 | 2.5411e-05
Wellington Electricity | 2005 | 2005-01-25
Wellington Electricity | 2005 | 2005-01-26
Wellington Electricity | 2005 | 2005-01-27 | 0.022032 | 3.8117e-05
Wellington Electricity | 2005 | 2005-01-28
Wellington Electricity | 2005 | 2005-01-29 | 0.0036719 | 0.00015247
Wellington Electricity | 2005 | 2005-01-30
Wellington Electricity | 2005 | 2005-01-31
Wellington Electricity | 2005 | 2005-02-01
Wellington Electricity | 2005 | 2005-02-02
Wellington Electricity | 2005 | 2005-02-03
Wellington Electricity | 2005 | 2005-02-04 | 0.0038308 | 5.7176e-05
Wellington Electricity | 2005 | 2005-02-05
Wellington Electricity | 2005 | 2005-02-06
Wellington Electricity | 2005 | 2005-02-07
Wellington Electricity | 2005 | 2005-02-08
Wellington Electricity | 2005 | 2005-02-09
Wellington Electricity | 2005 | 2005-02-10
Wellington Electricity | 2005 | 2005-02-11
Wellington Electricity | 2005 | 2005-02-12
Wellington Electricity | 2005 | 2005-02-13
Wellington Electricity | 2005 | 2005-02-14 | 0.35029 | 0.0030494
Wellington Electricity | 2005 | 2005-02-15
Wellington Electricity | 2005 | 2005-02-16
Wellington Electricity | 2005 | 2005-02-17 | 0.021257 | 0.00017788
Wellington Electricity | 2005 | 2005-02-18 | 0.0020901 | 6.3528e-06
Wellington Electricity | 2005 | 2005-02-19
Wellington Electricity | 2005 | 2005-02-20
Wellington Electricity | 2005 | 2005-02-21
Wellington Electricity | 2005 | 2005-02-22
Wellington Electricity | 2005 | 2005-02-23
Wellington Electricity | 2005 | 2005-02-24
Wellington Electricity | 2005 | 2005-02-25
Wellington Electricity | 2005 | 2005-02-26
Wellington Electricity | 2005 | 2005-02-27 | 0.00073693 | 2.5411e-05
Wellington Electricity | 2005 | 2005-02-28
Wellington Electricity | 2005 | 2005-03-01 | 0.085039 | 0.0015819
Wellington Electricity | 2005 | 2005-03-02
Wellington Electricity | 2005 | 2005-03-03 | 0.039712 | 0.0056731
Wellington Electricity | 2005 | 2005-03-04
Wellington Electricity | 2005 | 2005-03-05
Wellington Electricity | 2005 | 2005-03-06
Wellington Electricity | 2005 | 2005-03-07 | 0.14484 | 0.00063528
Wellington Electricity | 2005 | 2005-03-08
Wellington Electricity | 2005 | 2005-03-09
Wellington Electricity | 2005 | 2005-03-10
Wellington Electricity | 2005 | 2005-03-11
Wellington Electricity | 2005 | 2005-03-12
Wellington Electricity | 2005 | 2005-03-13 | 0.062537 | 0.00058446
Wellington Electricity | 2005 | 2005-03-14
Wellington Electricity | 2005 | 2005-03-15
Wellington Electricity | 2005 | 2005-03-16 | 0.0026301 | 3.8117e-05
Wellington Electricity | 2005 | 2005-03-17
Wellington Electricity | 2005 | 2005-03-18
Wellington Electricity | 2005 | 2005-03-19
Wellington Electricity | 2005 | 2005-03-20
Wellington Electricity | 2005 | 2005-03-21 | 0.023823 | 1.9059e-05
Wellington Electricity | 2005 | 2005-03-22
Wellington Electricity | 2005 | 2005-03-23 | 0.080611 | 0.0013659
Wellington Electricity | 2005 | 2005-03-24 | 0.022127 | 0.00017153
Wellington Electricity | 2005 | 2005-03-25 | 0.068223 | 0.0021282
Wellington Electricity | 2005 | 2005-03-26
Wellington Electricity | 2005 | 2005-03-27
Wellington Electricity | 2005 | 2005-03-28
Wellington Electricity | 2005 | 2005-03-29
Wellington Electricity | 2005 | 2005-03-30 | 0.0076234 | 9.5293e-05
Wellington Electricity | 2005 | 2005-03-31 | 0.4017 | 0.0022807
Wellington Electricity | 2006 | 2005-04-01 | 0.0071521 | 0.00017029
Wellington Electricity | 2006 | 2005-04-02
Wellington Electricity | 2006 | 2005-04-03
Wellington Electricity | 2006 | 2005-04-04
Wellington Electricity | 2006 | 2005-04-05
Wellington Electricity | 2006 | 2005-04-06
Wellington Electricity | 2006 | 2005-04-07 | 0.00059285 | 6.307e-06
Wellington Electricity | 2006 | 2005-04-08
Wellington Electricity | 2006 | 2005-04-09 | 0.33745 | 0.009637
Wellington Electricity | 2006 | 2005-04-10 | 0.11295 | 0.0014947
Wellington Electricity | 2006 | 2005-04-11
Wellington Electricity | 2006 | 2005-04-12
Wellington Electricity | 2006 | 2005-04-13 | 0.536 | 0.010135
Wellington Electricity | 2006 | 2005-04-14 | 0.14978 | 0.0016713
Wellington Electricity | 2006 | 2005-04-15
Wellington Electricity | 2006 | 2005-04-16
Wellington Electricity | 2006 | 2005-04-17
Wellington Electricity | 2006 | 2005-04-18 | 0.11672 | 0.00059285
Wellington Electricity | 2006 | 2005-04-19
Wellington Electricity | 2006 | 2005-04-20
Wellington Electricity | 2006 | 2005-04-21
Wellington Electricity | 2006 | 2005-04-22
Wellington Electricity | 2006 | 2005-04-23
Wellington Electricity | 2006 | 2005-04-24 | 0.7 | 0.0086279
Wellington Electricity | 2006 | 2005-04-25
Wellington Electricity | 2006 | 2005-04-26
Wellington Electricity | 2006 | 2005-04-27
Wellington Electricity | 2006 | 2005-04-28
Wellington Electricity | 2006 | 2005-04-29
Wellington Electricity | 2006 | 2005-04-30 | 0.28299 | 0.0033427
Wellington Electricity | 2006 | 2005-05-01
Wellington Electricity | 2006 | 2005-05-02 | 2.1026 | 0.031245
Wellington Electricity | 2006 | 2005-05-03
Wellington Electricity | 2006 | 2005-05-04
Wellington Electricity | 2006 | 2005-05-05
Wellington Electricity | 2006 | 2005-05-06
Wellington Electricity | 2006 | 2005-05-07 | 0.026332 | 0.0010533
Wellington Electricity | 2006 | 2005-05-08 | 0.59118 | 0.004951
Wellington Electricity | 2006 | 2005-05-09 | 0.04874 | 0.00029012
Wellington Electricity | 2006 | 2005-05-10
Wellington Electricity | 2006 | 2005-05-11
Wellington Electricity | 2006 | 2005-05-12 | 0.010968 | 0.00023336
Wellington Electricity | 2006 | 2005-05-13 | 0.13006 | 0.0014065
Wellington Electricity | 2006 | 2005-05-14
Wellington Electricity | 2006 | 2005-05-15
Wellington Electricity | 2006 | 2005-05-16 | 0.059664 | 0.00027751
Wellington Electricity | 2006 | 2005-05-17 | 0.12031 | 0.00093974
Wellington Electricity | 2006 | 2005-05-18 | 0.17514 | 0.0059285
Wellington Electricity | 2006 | 2005-05-19 | 0.017357 | 0.0043392
Wellington Electricity | 2006 | 2005-05-20
Wellington Electricity | 2006 | 2005-05-21 | 0.077727 | 0.0014947
Wellington Electricity | 2006 | 2005-05-22
Wellington Electricity | 2006 | 2005-05-23
Wellington Electricity | 2006 | 2005-05-24
Wellington Electricity | 2006 | 2005-05-25 | 0.19668 | 0.0077071
Wellington Electricity | 2006 | 2005-05-26
Wellington Electricity | 2006 | 2005-05-27
Wellington Electricity | 2006 | 2005-05-28
Wellington Electricity | 2006 | 2005-05-29
Wellington Electricity | 2006 | 2005-05-30 | 0.4042 | 0.0066412
Wellington Electricity | 2006 | 2005-05-31 | 0.0081896 | 2.2074e-05
Wellington Electricity | 2006 | 2005-06-01
Wellington Electricity | 2006 | 2005-06-02
Wellington Electricity | 2006 | 2005-06-03
Wellington Electricity | 2006 | 2005-06-04
Wellington Electricity | 2006 | 2005-06-05
Wellington Electricity | 2006 | 2005-06-06 | 0.024124 | 0.0016083
Wellington Electricity | 2006 | 2005-06-07
Wellington Electricity | 2006 | 2005-06-08 | 0.061673 | 0.00038788
Wellington Electricity | 2006 | 2005-06-09 | 0.097033 | 0.0011416
Wellington Electricity | 2006 | 2005-06-10
Wellington Electricity | 2006 | 2005-06-11 | 0.63629 | 0.0077891
Wellington Electricity | 2006 | 2005-06-12 | 0.06773 | 0.0007253
Wellington Electricity | 2006 | 2005-06-13
Wellington Electricity | 2006 | 2005-06-14 | 0.80944 | 0.010211
Wellington Electricity | 2006 | 2005-06-15
Wellington Electricity | 2006 | 2005-06-16 | 0.014008 | 0.00051086
Wellington Electricity | 2006 | 2005-06-17 | 0.050531 | 0.00061178
Wellington Electricity | 2006 | 2005-06-18 | 0.074693 | 0.0010406
Wellington Electricity | 2006 | 2005-06-19
Wellington Electricity | 2006 | 2005-06-20
Wellington Electricity | 2006 | 2005-06-21 | 0.736 | 0.0094258
Wellington Electricity | 2006 | 2005-06-22 | 0.052316 | 0.00022074
Wellington Electricity | 2006 | 2005-06-23 | 0.66876 | 0.0092902
Wellington Electricity | 2006 | 2005-06-24 | 0.13815 | 0.0030841
Wellington Electricity | 2006 | 2005-06-25
Wellington Electricity | 2006 | 2005-06-26
Wellington Electricity | 2006 | 2005-06-27
Wellington Electricity | 2006 | 2005-06-28 | 0.023014 | 0.00012929
Wellington Electricity | 2006 | 2005-06-29 | 0.012545 | 8.199e-05
Wellington Electricity | 2006 | 2005-06-30 | 0.041229 | 0.00038472
Wellington Electricity | 2006 | 2005-07-01
Wellington Electricity | 2006 | 2005-07-02
Wellington Electricity | 2006 | 2005-07-03
Wellington Electricity | 2006 | 2005-07-04 | 0.00526 | 1.8921e-05
Wellington Electricity | 2006 | 2005-07-05
Wellington Electricity | 2006 | 2005-07-06 | 0.0013749 | 6.307e-06
Wellington Electricity | 2006 | 2005-07-07 | 0.2973 | 0.0018479
Wellington Electricity | 2006 | 2005-07-08
Wellington Electricity | 2006 | 2005-07-09
Wellington Electricity | 2006 | 2005-07-10 | 0.026401 | 0.00029012
Wellington Electricity | 2006 | 2005-07-11
Wellington Electricity | 2006 | 2005-07-12 | 0.049787 | 0.00059285
Wellington Electricity | 2006 | 2005-07-13
Wellington Electricity | 2006 | 2005-07-14 | 0.0013497 | 6.307e-06
Wellington Electricity | 2006 | 2005-07-15 | 0.24819 | 0.0036707
Wellington Electricity | 2006 | 2005-07-16 | 0.0049825 | 1.2614e-05
Wellington Electricity | 2006 | 2005-07-17
Wellington Electricity | 2006 | 2005-07-18
Wellington Electricity | 2006 | 2005-07-19
Wellington Electricity | 2006 | 2005-07-20 | 0.010091 | 5.0456e-05
Wellington Electricity | 2006 | 2005-07-21
Wellington Electricity | 2006 | 2005-07-22
Wellington Electricity | 2006 | 2005-07-23 | 0.05844 | 0.0014254
Wellington Electricity | 2006 | 2005-07-24
Wellington Electricity | 2006 | 2005-07-25
Wellington Electricity | 2006 | 2005-07-26
Wellington Electricity | 2006 | 2005-07-27
Wellington Electricity | 2006 | 2005-07-28
Wellington Electricity | 2006 | 2005-07-29 | 0.0055501 | 0.0027751
Wellington Electricity | 2006 | 2005-07-30 | 0.77171 | 0.014689
Wellington Electricity | 2006 | 2005-07-31
Wellington Electricity | 2006 | 2005-08-01
Wellington Electricity | 2006 | 2005-08-02
Wellington Electricity | 2006 | 2005-08-03 | 0.1395 | 0.001911
Wellington Electricity | 2006 | 2005-08-04 | 0.19547 | 0.015036
Wellington Electricity | 2006 | 2005-08-05
Wellington Electricity | 2006 | 2005-08-06
Wellington Electricity | 2006 | 2005-08-07 | 0.093242 | 0.00020182
Wellington Electricity | 2006 | 2005-08-08
Wellington Electricity | 2006 | 2005-08-09
Wellington Electricity | 2006 | 2005-08-10 | 0.0067989 | 0.00061808
Wellington Electricity | 2006 | 2005-08-11
Wellington Electricity | 2006 | 2005-08-12 | 0.65382 | 0.018498
Wellington Electricity | 2006 | 2005-08-13 | 0.23142 | 0.002794
Wellington Electricity | 2006 | 2005-08-14
Wellington Electricity | 2006 | 2005-08-15 | 0.79614 | 0.014714
Wellington Electricity | 2006 | 2005-08-16 | 0.095399 | 0.00059285
Wellington Electricity | 2006 | 2005-08-17
Wellington Electricity | 2006 | 2005-08-18 | 0.10395 | 0.0020371
Wellington Electricity | 2006 | 2005-08-19
Wellington Electricity | 2006 | 2005-08-20 | 0.060036 | 0.0010533
Wellington Electricity | 2006 | 2005-08-21 | 0.019362 | 0.0067421
Wellington Electricity | 2006 | 2005-08-22
Wellington Electricity | 2006 | 2005-08-23
Wellington Electricity | 2006 | 2005-08-24
Wellington Electricity | 2006 | 2005-08-25
Wellington Electricity | 2006 | 2005-08-26
Wellington Electricity | 2006 | 2005-08-27
Wellington Electricity | 2006 | 2005-08-28 | 0.40916 | 0.0055817
Wellington Electricity | 2006 | 2005-08-29
Wellington Electricity | 2006 | 2005-08-30
Wellington Electricity | 2006 | 2005-08-31 | 0.0018038 | 0.0009019
Wellington Electricity | 2006 | 2005-09-01 | 0.041443 | 0.004377
Wellington Electricity | 2006 | 2005-09-02
Wellington Electricity | 2006 | 2005-09-03
Wellington Electricity | 2006 | 2005-09-04 | 0.012399 | 7.253e-05
Wellington Electricity | 2006 | 2005-09-05 | 0.052663 | 0.0010533
Wellington Electricity | 2006 | 2005-09-06
Wellington Electricity | 2006 | 2005-09-07
Wellington Electricity | 2006 | 2005-09-08
Wellington Electricity | 2006 | 2005-09-09
Wellington Electricity | 2006 | 2005-09-10
Wellington Electricity | 2006 | 2005-09-11
Wellington Electricity | 2006 | 2005-09-12
Wellington Electricity | 2006 | 2005-09-13
Wellington Electricity | 2006 | 2005-09-14
Wellington Electricity | 2006 | 2005-09-15
Wellington Electricity | 2006 | 2005-09-16
Wellington Electricity | 2006 | 2005-09-17
Wellington Electricity | 2006 | 2005-09-18
Wellington Electricity | 2006 | 2005-09-19 | 0.083738 | 0.00044779
Wellington Electricity | 2006 | 2005-09-20
Wellington Electricity | 2006 | 2005-09-21 | 0.0017155 | 6.307e-06
Wellington Electricity | 2006 | 2005-09-22 | 0.61377 | 0.0087856
Wellington Electricity | 2006 | 2005-09-23
Wellington Electricity | 2006 | 2005-09-24 | 0.086872 | 0.0010533
Wellington Electricity | 2006 | 2005-09-25 | 0.017016 | 3.7842e-05
Wellington Electricity | 2006 | 2005-09-26 | 0.0019741 | 6.307e-06
Wellington Electricity | 2006 | 2005-09-27
Wellington Electricity | 2006 | 2005-09-28 | 0.017155 | 0.00025228
Wellington Electricity | 2006 | 2005-09-29
Wellington Electricity | 2006 | 2005-09-30 | 0.0033112 | 4.4149e-05
Wellington Electricity | 2006 | 2005-10-01
Wellington Electricity | 2006 | 2005-10-02
Wellington Electricity | 2006 | 2005-10-03
Wellington Electricity | 2006 | 2005-10-04 | 0.015894 | 0.00079468
Wellington Electricity | 2006 | 2005-10-05
Wellington Electricity | 2006 | 2005-10-06
Wellington Electricity | 2006 | 2005-10-07
Wellington Electricity | 2006 | 2005-10-08
Wellington Electricity | 2006 | 2005-10-09
Wellington Electricity | 2006 | 2005-10-10
Wellington Electricity | 2006 | 2005-10-11 | 0.18408 | 0.0065277
Wellington Electricity | 2006 | 2005-10-12 | 0.0094857 | 5.0456e-05
Wellington Electricity | 2006 | 2005-10-13 | 0.15804 | 0.014222
Wellington Electricity | 2006 | 2005-10-14
Wellington Electricity | 2006 | 2005-10-15 | 0.00039418 | 3.1535e-06
Wellington Electricity | 2006 | 2005-10-16 | 0.0017218 | 6.307e-06
Wellington Electricity | 2006 | 2005-10-17
Wellington Electricity | 2006 | 2005-10-18
Wellington Electricity | 2006 | 2005-10-19
Wellington Electricity | 2006 | 2005-10-20
Wellington Electricity | 2006 | 2005-10-21
Wellington Electricity | 2006 | 2005-10-22 | 0.1324 | 0.002939
Wellington Electricity | 2006 | 2005-10-23
Wellington Electricity | 2006 | 2005-10-24
Wellington Electricity | 2006 | 2005-10-25 | 0.018366 | 0.00035319
Wellington Electricity | 2006 | 2005-10-26
Wellington Electricity | 2006 | 2005-10-27
Wellington Electricity | 2006 | 2005-10-28
Wellington Electricity | 2006 | 2005-10-29 | 0.011037 | 4.4149e-05
Wellington Electricity | 2006 | 2005-10-30 | 0.27327 | 0.0042698
Wellington Electricity | 2006 | 2005-10-31
Wellington Electricity | 2006 | 2005-11-01
Wellington Electricity | 2006 | 2005-11-02
Wellington Electricity | 2006 | 2005-11-03
Wellington Electricity | 2006 | 2005-11-04
Wellington Electricity | 2006 | 2005-11-05
Wellington Electricity | 2006 | 2005-11-06
Wellington Electricity | 2006 | 2005-11-07
Wellington Electricity | 2006 | 2005-11-08
Wellington Electricity | 2006 | 2005-11-09
Wellington Electricity | 2006 | 2005-11-10
Wellington Electricity | 2006 | 2005-11-11
Wellington Electricity | 2006 | 2005-11-12
Wellington Electricity | 2006 | 2005-11-13
Wellington Electricity | 2006 | 2005-11-14
Wellington Electricity | 2006 | 2005-11-15
Wellington Electricity | 2006 | 2005-11-16
Wellington Electricity | 2006 | 2005-11-17
Wellington Electricity | 2006 | 2005-11-18
Wellington Electricity | 2006 | 2005-11-19
Wellington Electricity | 2006 | 2005-11-20 | 0.03361 | 0.00079152
Wellington Electricity | 2006 | 2005-11-21 | 0.59864 | 0.010728
Wellington Electricity | 2006 | 2005-11-22
Wellington Electricity | 2006 | 2005-11-23
Wellington Electricity | 2006 | 2005-11-24 | 0.1076 | 0.00058339
Wellington Electricity | 2006 | 2005-11-25
Wellington Electricity | 2006 | 2005-11-26
Wellington Electricity | 2006 | 2005-11-27
Wellington Electricity | 2006 | 2005-11-28
Wellington Electricity | 2006 | 2005-11-29
Wellington Electricity | 2006 | 2005-11-30 | 0.012803 | 0.0003658
Wellington Electricity | 2006 | 2005-12-01 | 0.02777 | 0.00034058
Wellington Electricity | 2006 | 2005-12-02
Wellington Electricity | 2006 | 2005-12-03
Wellington Electricity | 2006 | 2005-12-04
Wellington Electricity | 2006 | 2005-12-05 | 0.1326 | 0.0016777
Wellington Electricity | 2006 | 2005-12-06 | 0.28502 | 0.0043707
Wellington Electricity | 2006 | 2005-12-07 | 0.089836 | 0.0011857
Wellington Electricity | 2006 | 2005-12-08 | 0.00093658 | 2.8381e-05
Wellington Electricity | 2006 | 2005-12-09
Wellington Electricity | 2006 | 2005-12-10
Wellington Electricity | 2006 | 2005-12-11 | 0.0012393 | 6.307e-06
Wellington Electricity | 2006 | 2005-12-12
Wellington Electricity | 2006 | 2005-12-13 | 0.007253 | 0.00031535
Wellington Electricity | 2006 | 2005-12-14
Wellington Electricity | 2006 | 2005-12-15 | 0.026764 | 0.00038788
Wellington Electricity | 2006 | 2005-12-16 | 0.45956 | 0.0077891
Wellington Electricity | 2006 | 2005-12-17
Wellington Electricity | 2006 | 2005-12-18
Wellington Electricity | 2006 | 2005-12-19
Wellington Electricity | 2006 | 2005-12-20 | 0.49711 | 0.0089086
Wellington Electricity | 2006 | 2005-12-21
Wellington Electricity | 2006 | 2005-12-22
Wellington Electricity | 2006 | 2005-12-23
Wellington Electricity | 2006 | 2005-12-24
Wellington Electricity | 2006 | 2005-12-25
Wellington Electricity | 2006 | 2005-12-26 | 0.0017912 | 6.307e-06
Wellington Electricity | 2006 | 2005-12-27 | 0.015641 | 0.00019552
Wellington Electricity | 2006 | 2005-12-28 | 0.048614 | 0.00059285
Wellington Electricity | 2006 | 2005-12-29
Wellington Electricity | 2006 | 2005-12-30
Wellington Electricity | 2006 | 2005-12-31 | 0.77794 | 0.011271
Wellington Electricity | 2006 | 2006-01-01
Wellington Electricity | 2006 | 2006-01-02 | 1.9587 | 0.021734
Wellington Electricity | 2006 | 2006-01-03 | 0.19909 | 0.0012614
Wellington Electricity | 2006 | 2006-01-04 | 0.73706 | 0.014147
Wellington Electricity | 2006 | 2006-01-05
Wellington Electricity | 2006 | 2006-01-06
Wellington Electricity | 2006 | 2006-01-07
Wellington Electricity | 2006 | 2006-01-08 | 0.16398 | 0.0014254
Wellington Electricity | 2006 | 2006-01-09
Wellington Electricity | 2006 | 2006-01-10
Wellington Electricity | 2006 | 2006-01-11 | 0.0049383 | 0.00017029
Wellington Electricity | 2006 | 2006-01-12 | 0.49117 | 0.010444
Wellington Electricity | 2006 | 2006-01-13 | 0.82734 | 0.0099335
Wellington Electricity | 2006 | 2006-01-14
Wellington Electricity | 2006 | 2006-01-15
Wellington Electricity | 2006 | 2006-01-16
Wellington Electricity | 2006 | 2006-01-17 | 0.15921 | 0.0039387
Wellington Electricity | 2006 | 2006-01-18 | 0.40815 | 0.0043392
Wellington Electricity | 2006 | 2006-01-19 | 0.20889 | 0.0010533
Wellington Electricity | 2006 | 2006-01-20 | 0.013535 | 0.00023336
Wellington Electricity | 2006 | 2006-01-21
Wellington Electricity | 2006 | 2006-01-22
Wellington Electricity | 2006 | 2006-01-23
Wellington Electricity | 2006 | 2006-01-24 | 0.10973 | 0.0015263
Wellington Electricity | 2006 | 2006-01-25 | 0.32686 | 0.0015547
Wellington Electricity | 2006 | 2006-01-26 | 0.41395 | 0.0051055
Wellington Electricity | 2006 | 2006-01-27 | 0.027057 | 0.00040995
Wellington Electricity | 2006 | 2006-01-28 | 0.17704 | 0.0025291
Wellington Electricity | 2006 | 2006-01-29 | 0.14254 | 0.0018101
Wellington Electricity | 2006 | 2006-01-30 | 0.73991 | 0.0090505
Wellington Electricity | 2006 | 2006-01-31
Wellington Electricity | 2006 | 2006-02-01
Wellington Electricity | 2006 | 2006-02-02 | 0.0025859 | 6.307e-05
Wellington Electricity | 2006 | 2006-02-03 | 0.083252 | 0.00034688
Wellington Electricity | 2006 | 2006-02-04 | 0.14488 | 0.0021065
Wellington Electricity | 2006 | 2006-02-05 | 0.09029 | 0.0021759
Wellington Electricity | 2006 | 2006-02-06 | 0.041569 | 0.00014191
Wellington Electricity | 2006 | 2006-02-07
Wellington Electricity | 2006 | 2006-02-08
Wellington Electricity | 2006 | 2006-02-09
Wellington Electricity | 2006 | 2006-02-10 | 0.068639 | 0.0021696
Wellington Electricity | 2006 | 2006-02-11
Wellington Electricity | 2006 | 2006-02-12 | 0.00084513 | 6.307e-06
Wellington Electricity | 2006 | 2006-02-13
Wellington Electricity | 2006 | 2006-02-14
Wellington Electricity | 2006 | 2006-02-15
Wellington Electricity | 2006 | 2006-02-16
Wellington Electricity | 2006 | 2006-02-17
Wellington Electricity | 2006 | 2006-02-18 | 0.010104 | 0.00056132
Wellington Electricity | 2006 | 2006-02-19
Wellington Electricity | 2006 | 2006-02-20 | 0.016146 | 0.00020182
Wellington Electricity | 2006 | 2006-02-21
Wellington Electricity | 2006 | 2006-02-22
Wellington Electricity | 2006 | 2006-02-23 | 0.055974 | 0.00044779
Wellington Electricity | 2006 | 2006-02-24 | 0.31677 | 0.0090505
Wellington Electricity | 2006 | 2006-02-25 | 0.02876 | 0.00047933
Wellington Electricity | 2006 | 2006-02-26 | 0.0018669 | 1.2614e-05
Wellington Electricity | 2006 | 2006-02-27 | 0.00015137 | 6.307e-06
Wellington Electricity | 2006 | 2006-02-28 | 0.52535 | 0.012772
Wellington Electricity | 2006 | 2006-03-01 | 0.10273 | 0.0014884
Wellington Electricity | 2006 | 2006-03-02 | 0.0022705 | 1.8921e-05
Wellington Electricity | 2006 | 2006-03-03 | 0.49591 | 0.0021822
Wellington Electricity | 2006 | 2006-03-04 | 0.020453 | 0.00029643
Wellington Electricity | 2006 | 2006-03-05
Wellington Electricity | 2006 | 2006-03-06
Wellington Electricity | 2006 | 2006-03-07
Wellington Electricity | 2006 | 2006-03-08
Wellington Electricity | 2006 | 2006-03-09 | 0.0046545 | 3.7842e-05
Wellington Electricity | 2006 | 2006-03-10
Wellington Electricity | 2006 | 2006-03-11
Wellington Electricity | 2006 | 2006-03-12
Wellington Electricity | 2006 | 2006-03-13 | 0.55134 | 0.0062376
Wellington Electricity | 2006 | 2006-03-14 | 0.0052537 | 1.8921e-05
Wellington Electricity | 2006 | 2006-03-15
Wellington Electricity | 2006 | 2006-03-16
Wellington Electricity | 2006 | 2006-03-17
Wellington Electricity | 2006 | 2006-03-18
Wellington Electricity | 2006 | 2006-03-19
Wellington Electricity | 2006 | 2006-03-20 | 0.11267 | 0.0025606
Wellington Electricity | 2006 | 2006-03-21 | 0.41084 | 0.0057078
Wellington Electricity | 2006 | 2006-03-22
Wellington Electricity | 2006 | 2006-03-23 | 0.037337 | 0.00020182
Wellington Electricity | 2006 | 2006-03-24
Wellington Electricity | 2006 | 2006-03-25
Wellington Electricity | 2006 | 2006-03-26
Wellington Electricity | 2006 | 2006-03-27 | 0.056573 | 0.0017407
Wellington Electricity | 2006 | 2006-03-28
Wellington Electricity | 2006 | 2006-03-29
Wellington Electricity | 2006 | 2006-03-30
Wellington Electricity | 2006 | 2006-03-31
Wellington Electricity | 2007 | 2006-04-01 | 0.00069538 | 0.00069538
Wellington Electricity | 2007 | 2006-04-02 | 0.079236 | 0.0033015
Wellington Electricity | 2007 | 2006-04-03 | 0.58114 | 0.0098982
Wellington Electricity | 2007 | 2006-04-04 | 0.001278 | 6.2647e-06
Wellington Electricity | 2007 | 2006-04-05 | 0.15009 | 0.002556
Wellington Electricity | 2007 | 2006-04-06 | 0.018468 | 0.000426
Wellington Electricity | 2007 | 2006-04-07 | 0.1643 | 0.00265
Wellington Electricity | 2007 | 2006-04-08
Wellington Electricity | 2007 | 2006-04-09 | 0.11129 | 0.010117
Wellington Electricity | 2007 | 2006-04-10 | 0.60528 | 0.027471
Wellington Electricity | 2007 | 2006-04-11 | 0.0022553 | 0.00056382
Wellington Electricity | 2007 | 2006-04-12
Wellington Electricity | 2007 | 2006-04-13
Wellington Electricity | 2007 | 2006-04-14 | 0.082111 | 0.0010901
Wellington Electricity | 2007 | 2006-04-15
Wellington Electricity | 2007 | 2006-04-16
Wellington Electricity | 2007 | 2006-04-17 | 0.1219 | 0.0010775
Wellington Electricity | 2007 | 2006-04-18
Wellington Electricity | 2007 | 2006-04-19 | 0.028507 | 0.0015411
Wellington Electricity | 2007 | 2006-04-20
Wellington Electricity | 2007 | 2006-04-21
Wellington Electricity | 2007 | 2006-04-22 | 0.0014096 | 5.6382e-05
Wellington Electricity | 2007 | 2006-04-23 | 0.17305 | 0.0020987
Wellington Electricity | 2007 | 2006-04-24
Wellington Electricity | 2007 | 2006-04-25 | 0.074725 | 0.0010525
Wellington Electricity | 2007 | 2006-04-26 | 0.085977 | 0.0011778
Wellington Electricity | 2007 | 2006-04-27
Wellington Electricity | 2007 | 2006-04-28 | 0.032626 | 0.0010525
Wellington Electricity | 2007 | 2006-04-29 | 0.03631 | 0.00057635
Wellington Electricity | 2007 | 2006-04-30
Wellington Electricity | 2007 | 2006-05-01
Wellington Electricity | 2007 | 2006-05-02
Wellington Electricity | 2007 | 2006-05-03
Wellington Electricity | 2007 | 2006-05-04
Wellington Electricity | 2007 | 2006-05-05 | 0.10303 | 0.0012404
Wellington Electricity | 2007 | 2006-05-06
Wellington Electricity | 2007 | 2006-05-07 | 0.073529 | 0.00060767
Wellington Electricity | 2007 | 2006-05-08
Wellington Electricity | 2007 | 2006-05-09 | 0.11502 | 0.0022678
Wellington Electricity | 2007 | 2006-05-10 | 0.068724 | 0.001397
Wellington Electricity | 2007 | 2006-05-11
Wellington Electricity | 2007 | 2006-05-12 | 0.0021926 | 1.2529e-05
Wellington Electricity | 2007 | 2006-05-13
Wellington Electricity | 2007 | 2006-05-14
Wellington Electricity | 2007 | 2006-05-15 | 0.58118 | 0.0065591
Wellington Electricity | 2007 | 2006-05-16
Wellington Electricity | 2007 | 2006-05-17 | 0.093218 | 0.00060141
Wellington Electricity | 2007 | 2006-05-18 | 0.067433 | 0.00048865
Wellington Electricity | 2007 | 2006-05-19 | 0.54635 | 0.012937
Wellington Electricity | 2007 | 2006-05-20
Wellington Electricity | 2007 | 2006-05-21
Wellington Electricity | 2007 | 2006-05-22 | 0.0052999 | 1.8794e-05
Wellington Electricity | 2007 | 2006-05-23 | 0.01065 | 2.5059e-05
Wellington Electricity | 2007 | 2006-05-24
Wellington Electricity | 2007 | 2006-05-25
Wellington Electricity | 2007 | 2006-05-26
Wellington Electricity | 2007 | 2006-05-27
Wellington Electricity | 2007 | 2006-05-28 | 0.0075176 | 4.6985e-05
Wellington Electricity | 2007 | 2006-05-29
Wellington Electricity | 2007 | 2006-05-30
Wellington Electricity | 2007 | 2006-05-31 | 0.017854 | 4.6985e-05
Wellington Electricity | 2007 | 2006-06-01
Wellington Electricity | 2007 | 2006-06-02 | 0.36307 | 0.0059796
Wellington Electricity | 2007 | 2006-06-03
Wellington Electricity | 2007 | 2006-06-04
Wellington Electricity | 2007 | 2006-06-05 | 0.14694 | 0.00088332
Wellington Electricity | 2007 | 2006-06-06 | 0.16129 | 0.0021049
Wellington Electricity | 2007 | 2006-06-07
Wellington Electricity | 2007 | 2006-06-08
Wellington Electricity | 2007 | 2006-06-09 | 0.17376 | 0.0027972
Wellington Electricity | 2007 | 2006-06-10 | 0.021012 | 0.00016288
Wellington Electricity | 2007 | 2006-06-11 | 0.88576 | 0.017297
Wellington Electricity | 2007 | 2006-06-12 | 0.95388 | 0.0095975
Wellington Electricity | 2007 | 2006-06-13 | 0.0061143 | 0.00010023
Wellington Electricity | 2007 | 2006-06-14
Wellington Electricity | 2007 | 2006-06-15
Wellington Electricity | 2007 | 2006-06-16
Wellington Electricity | 2007 | 2006-06-17
Wellington Electricity | 2007 | 2006-06-18 | 0.19587 | 0.00062647
Wellington Electricity | 2007 | 2006-06-19 | 0.15506 | 0.0034894
Wellington Electricity | 2007 | 2006-06-20 | 0.085632 | 0.0018731
Wellington Electricity | 2007 | 2006-06-21
Wellington Electricity | 2007 | 2006-06-22 | 0.19756 | 0.0041159
Wellington Electricity | 2007 | 2006-06-23
Wellington Electricity | 2007 | 2006-06-24
Wellington Electricity | 2007 | 2006-06-25
Wellington Electricity | 2007 | 2006-06-26 | 0.12195 | 0.001397
Wellington Electricity | 2007 | 2006-06-27
Wellington Electricity | 2007 | 2006-06-28
Wellington Electricity | 2007 | 2006-06-29 | 0.035922 | 0.00076429
Wellington Electricity | 2007 | 2006-06-30
Wellington Electricity | 2007 | 2006-07-01 | 0.34169 | 0.0063649
Wellington Electricity | 2007 | 2006-07-02
Wellington Electricity | 2007 | 2006-07-03
Wellington Electricity | 2007 | 2006-07-04 | 0.031436 | 0.00026312
Wellington Electricity | 2007 | 2006-07-05 | 0.014077 | 0.00011276
Wellington Electricity | 2007 | 2006-07-06 | 0.42621 | 0.0057635
Wellington Electricity | 2007 | 2006-07-07 | 0.44197 | 0.0052623
Wellington Electricity | 2007 | 2006-07-08
Wellington Electricity | 2007 | 2006-07-09 | 0.035132 | 0.00045732
Wellington Electricity | 2007 | 2006-07-10 | 0.033222 | 0.000426
Wellington Electricity | 2007 | 2006-07-11 | 0.59139 | 0.011759
Wellington Electricity | 2007 | 2006-07-12 | 0.0015223 | 6.2647e-06
Wellington Electricity | 2007 | 2006-07-13
Wellington Electricity | 2007 | 2006-07-14
Wellington Electricity | 2007 | 2006-07-15 | 0.092818 | 0.00072044
Wellington Electricity | 2007 | 2006-07-16 | 0.013231 | 0.0016539
Wellington Electricity | 2007 | 2006-07-17
Wellington Electricity | 2007 | 2006-07-18
Wellington Electricity | 2007 | 2006-07-19
Wellington Electricity | 2007 | 2006-07-20 | 0.0091339 | 6.2647e-06
Wellington Electricity | 2007 | 2006-07-21 | 0.10106 | 0.00050117
Wellington Electricity | 2007 | 2006-07-22
Wellington Electricity | 2007 | 2006-07-23
Wellington Electricity | 2007 | 2006-07-24 | 0.35977 | 0.0062334
Wellington Electricity | 2007 | 2006-07-25
Wellington Electricity | 2007 | 2006-07-26 | 0.097287 | 0.00047925
Wellington Electricity | 2007 | 2006-07-27 | 0.27352 | 0.0040031
Wellington Electricity | 2007 | 2006-07-28 | 0.18787 | 0.031383
Wellington Electricity | 2007 | 2006-07-29
Wellington Electricity | 2007 | 2006-07-30 | 0.017334 | 0.00017541
Wellington Electricity | 2007 | 2006-07-31 | 0.32024 | 0.0046327
Wellington Electricity | 2007 | 2006-08-01 | 0.020392 | 0.0010525
Wellington Electricity | 2007 | 2006-08-02
Wellington Electricity | 2007 | 2006-08-03
Wellington Electricity | 2007 | 2006-08-04 | 0.026838 | 0.013419
Wellington Electricity | 2007 | 2006-08-05
Wellington Electricity | 2007 | 2006-08-06 | 0.026193 | 0.00023179
Wellington Electricity | 2007 | 2006-08-07 | 0.30823 | 0.0034518
Wellington Electricity | 2007 | 2006-08-08 | 1.8517 | 0.012749
Wellington Electricity | 2007 | 2006-08-09
Wellington Electricity | 2007 | 2006-08-10
Wellington Electricity | 2007 | 2006-08-11
Wellington Electricity | 2007 | 2006-08-12 | 0.9726 | 0.017792
Wellington Electricity | 2007 | 2006-08-13 | 0.00050744 | 6.2647e-06
Wellington Electricity | 2007 | 2006-08-14 | 0.9378 | 0.014653
Wellington Electricity | 2007 | 2006-08-15 | 0.096204 | 0.002083
Wellington Electricity | 2007 | 2006-08-16 | 0.18254 | 0.0020799
Wellington Electricity | 2007 | 2006-08-17
Wellington Electricity | 2007 | 2006-08-18
Wellington Electricity | 2007 | 2006-08-19 | 0.11285 | 0.0015787
Wellington Electricity | 2007 | 2006-08-20
Wellington Electricity | 2007 | 2006-08-21 | 0.19645 | 0.0023994
Wellington Electricity | 2007 | 2006-08-22
Wellington Electricity | 2007 | 2006-08-23 | 0.035145 | 0.0001065
Wellington Electricity | 2007 | 2006-08-24
Wellington Electricity | 2007 | 2006-08-25
Wellington Electricity | 2007 | 2006-08-26
Wellington Electricity | 2007 | 2006-08-27
Wellington Electricity | 2007 | 2006-08-28 | 0.016426 | 7.2044e-05
Wellington Electricity | 2007 | 2006-08-29 | 0.0049616 | 0.0016539
Wellington Electricity | 2007 | 2006-08-30 | 0.00058888 | 6.2647e-06
Wellington Electricity | 2007 | 2006-08-31
Wellington Electricity | 2007 | 2006-09-01
Wellington Electricity | 2007 | 2006-09-02
Wellington Electricity | 2007 | 2006-09-03
Wellington Electricity | 2007 | 2006-09-04
Wellington Electricity | 2007 | 2006-09-05 | 0.31463 | 0.005538
Wellington Electricity | 2007 | 2006-09-06 | 0.0074738 | 0.0005325
Wellington Electricity | 2007 | 2006-09-07
Wellington Electricity | 2007 | 2006-09-08
Wellington Electricity | 2007 | 2006-09-09
Wellington Electricity | 2007 | 2006-09-10 | 0.0021049 | 2.5059e-05
Wellington Electricity | 2007 | 2006-09-11
Wellington Electricity | 2007 | 2006-09-12
Wellington Electricity | 2007 | 2006-09-13 | 0.25447 | 0.012724
Wellington Electricity | 2007 | 2006-09-14
Wellington Electricity | 2007 | 2006-09-15 | 0.07906 | 0.0017604
Wellington Electricity | 2007 | 2006-09-16
Wellington Electricity | 2007 | 2006-09-17 | 0.14204 | 0.0032388
Wellington Electricity | 2007 | 2006-09-18
Wellington Electricity | 2007 | 2006-09-19 | 0.0091778 | 0.0015223
Wellington Electricity | 2007 | 2006-09-20
Wellington Electricity | 2007 | 2006-09-21
Wellington Electricity | 2007 | 2006-09-22
Wellington Electricity | 2007 | 2006-09-23
Wellington Electricity | 2007 | 2006-09-24
Wellington Electricity | 2007 | 2006-09-25
Wellington Electricity | 2007 | 2006-09-26
Wellington Electricity | 2007 | 2006-09-27
Wellington Electricity | 2007 | 2006-09-28
Wellington Electricity | 2007 | 2006-09-29
Wellington Electricity | 2007 | 2006-09-30
Wellington Electricity | 2007 | 2006-10-01
Wellington Electricity | 2007 | 2006-10-02
Wellington Electricity | 2007 | 2006-10-03 | 0.22888 | 0.0068473
Wellington Electricity | 2007 | 2006-10-04 | 1.0689 | 0.018174
Wellington Electricity | 2007 | 2006-10-05
Wellington Electricity | 2007 | 2006-10-06 | 0.072733 | 0.0040407
Wellington Electricity | 2007 | 2006-10-07
Wellington Electricity | 2007 | 2006-10-08 | 0.27653 | 0.0074738
Wellington Electricity | 2007 | 2006-10-09 | 0.019671 | 0.0014659
Wellington Electricity | 2007 | 2006-10-10
Wellington Electricity | 2007 | 2006-10-11 | 0.00072044 | 3.1323e-06
Wellington Electricity | 2007 | 2006-10-12
Wellington Electricity | 2007 | 2006-10-13 | 0.0041222 | 4.3853e-05
Wellington Electricity | 2007 | 2006-10-14
Wellington Electricity | 2007 | 2006-10-15 | 0.4715 | 0.0091527
Wellington Electricity | 2007 | 2006-10-16 | 0.038916 | 0.000426
Wellington Electricity | 2007 | 2006-10-17
Wellington Electricity | 2007 | 2006-10-18
Wellington Electricity | 2007 | 2006-10-19
Wellington Electricity | 2007 | 2006-10-20
Wellington Electricity | 2007 | 2006-10-21
Wellington Electricity | 2007 | 2006-10-22
Wellington Electricity | 2007 | 2006-10-23 | 2.1026 | 0.010462
Wellington Electricity | 2007 | 2006-10-24 | 0.49826 | 0.0090713
Wellington Electricity | 2007 | 2006-10-25 | 0.0015975 | 6.2647e-06
Wellington Electricity | 2007 | 2006-10-26
Wellington Electricity | 2007 | 2006-10-27 | 0.12574 | 0.0011903
Wellington Electricity | 2007 | 2006-10-28 | 0.0068786 | 0.00060767
Wellington Electricity | 2007 | 2006-10-29 | 0.0086954 | 2.5059e-05
Wellington Electricity | 2007 | 2006-10-30
Wellington Electricity | 2007 | 2006-10-31
Wellington Electricity | 2007 | 2006-11-01 | 0.16839 | 0.0052623
Wellington Electricity | 2007 | 2006-11-02
Wellington Electricity | 2007 | 2006-11-03
Wellington Electricity | 2007 | 2006-11-04
Wellington Electricity | 2007 | 2006-11-05
Wellington Electricity | 2007 | 2006-11-06
Wellington Electricity | 2007 | 2006-11-07
Wellington Electricity | 2007 | 2006-11-08
Wellington Electricity | 2007 | 2006-11-09 | 0.41599 | 0.004473
Wellington Electricity | 2007 | 2006-11-10 | 0.41195 | 0.005325
Wellington Electricity | 2007 | 2006-11-11
Wellington Electricity | 2007 | 2006-11-12 | 0.59317 | 0.010594
Wellington Electricity | 2007 | 2006-11-13 | 0.036348 | 0.001704
Wellington Electricity | 2007 | 2006-11-14 | 1.4277 | 0.021977
Wellington Electricity | 2007 | 2006-11-15 | 0.26223 | 0.0010775
Wellington Electricity | 2007 | 2006-11-16 | 0.46173 | 0.005563
Wellington Electricity | 2007 | 2006-11-17
Wellington Electricity | 2007 | 2006-11-18 | 0.076016 | 0.00012843
Wellington Electricity | 2007 | 2006-11-19
Wellington Electricity | 2007 | 2006-11-20
Wellington Electricity | 2007 | 2006-11-21
Wellington Electricity | 2007 | 2006-11-22
Wellington Electricity | 2007 | 2006-11-23
Wellington Electricity | 2007 | 2006-11-24 | 0.72432 | 0.0037525
Wellington Electricity | 2007 | 2006-11-25 | 0.058312 | 0.0011214
Wellington Electricity | 2007 | 2006-11-26 | 0.0019546 | 1.8794e-05
Wellington Electricity | 2007 | 2006-11-27
Wellington Electricity | 2007 | 2006-11-28
Wellington Electricity | 2007 | 2006-11-29
Wellington Electricity | 2007 | 2006-11-30 | 0.51366 | 0.0088708
Wellington Electricity | 2007 | 2006-12-01 | 0.41326 | 0.0088269
Wellington Electricity | 2007 | 2006-12-02
Wellington Electricity | 2007 | 2006-12-03
Wellington Electricity | 2007 | 2006-12-04
Wellington Electricity | 2007 | 2006-12-05
Wellington Electricity | 2007 | 2006-12-06
Wellington Electricity | 2007 | 2006-12-07 | 0.023987 | 0.00036335
Wellington Electricity | 2007 | 2006-12-08 | 0.041366 | 0.00067032
Wellington Electricity | 2007 | 2006-12-09
Wellington Electricity | 2007 | 2006-12-10
Wellington Electricity | 2007 | 2006-12-11
Wellington Electricity | 2007 | 2006-12-12
Wellington Electricity | 2007 | 2006-12-13 | 0.00080814 | 1.8794e-05
Wellington Electricity | 2007 | 2006-12-14 | 0.013344 | 0.00011276
Wellington Electricity | 2007 | 2006-12-15
Wellington Electricity | 2007 | 2006-12-16 | 0.0017353 | 6.2647e-06
Wellington Electricity | 2007 | 2006-12-17
Wellington Electricity | 2007 | 2006-12-18
Wellington Electricity | 2007 | 2006-12-19 | 0.005964 | 4.3853e-05
Wellington Electricity | 2007 | 2006-12-20
Wellington Electricity | 2007 | 2006-12-21
Wellington Electricity | 2007 | 2006-12-22 | 0.0010023 | 2.5059e-05
Wellington Electricity | 2007 | 2006-12-23 | 0.17275 | 0.0059452
Wellington Electricity | 2007 | 2006-12-24 | 0.40388 | 0.0049052
Wellington Electricity | 2007 | 2006-12-25 | 0.023593 | 0.00055442
Wellington Electricity | 2007 | 2006-12-26
Wellington Electricity | 2007 | 2006-12-27
Wellington Electricity | 2007 | 2006-12-28
Wellington Electricity | 2007 | 2006-12-29
Wellington Electricity | 2007 | 2006-12-30
Wellington Electricity | 2007 | 2006-12-31 | 0.54561 | 0.0048865
Wellington Electricity | 2007 | 2007-01-01 | 0.45276 | 0.0030133
Wellington Electricity | 2007 | 2007-01-02
Wellington Electricity | 2007 | 2007-01-03 | 0.35321 | 0.0034268
Wellington Electricity | 2007 | 2007-01-04
Wellington Electricity | 2007 | 2007-01-05 | 0.25499 | 0.0040407
Wellington Electricity | 2007 | 2007-01-06
Wellington Electricity | 2007 | 2007-01-07 | 0.11113 | 0.025466
Wellington Electricity | 2007 | 2007-01-08
Wellington Electricity | 2007 | 2007-01-09
Wellington Electricity | 2007 | 2007-01-10
Wellington Electricity | 2007 | 2007-01-11 | 0.46435 | 0.0076492
Wellington Electricity | 2007 | 2007-01-12
Wellington Electricity | 2007 | 2007-01-13
Wellington Electricity | 2007 | 2007-01-14
Wellington Electricity | 2007 | 2007-01-15 | 0.21442 | 0.0033422
Wellington Electricity | 2007 | 2007-01-16
Wellington Electricity | 2007 | 2007-01-17
Wellington Electricity | 2007 | 2007-01-18
Wellington Electricity | 2007 | 2007-01-19
Wellington Electricity | 2007 | 2007-01-20 | 0.48797 | 0.0064839
Wellington Electricity | 2007 | 2007-01-21 | 0.11477 | 0.0010525
Wellington Electricity | 2007 | 2007-01-22
Wellington Electricity | 2007 | 2007-01-23
Wellington Electricity | 2007 | 2007-01-24 | 0.13083 | 0.0038309
Wellington Electricity | 2007 | 2007-01-25
Wellington Electricity | 2007 | 2007-01-26 | 0.006628 | 3.7588e-05
Wellington Electricity | 2007 | 2007-01-27 | 0.00070791 | 6.2647e-06
Wellington Electricity | 2007 | 2007-01-28
Wellington Electricity | 2007 | 2007-01-29
Wellington Electricity | 2007 | 2007-01-30 | 0.021002 | 0.00044166
Wellington Electricity | 2007 | 2007-01-31 | 0.12065 | 0.0021175
Wellington Electricity | 2007 | 2007-02-01 | 0.00043226 | 1.8794e-05
Wellington Electricity | 2007 | 2007-02-02 | 0.00088332 | 3.1323e-06
Wellington Electricity | 2007 | 2007-02-03 | 0.0038716 | 3.7588e-05
Wellington Electricity | 2007 | 2007-02-04
Wellington Electricity | 2007 | 2007-02-05
Wellington Electricity | 2007 | 2007-02-06
Wellington Electricity | 2007 | 2007-02-07
Wellington Electricity | 2007 | 2007-02-08 | 0.1289 | 0.0011903
Wellington Electricity | 2007 | 2007-02-09
Wellington Electricity | 2007 | 2007-02-10 | 0.52761 | 0.0060955
Wellington Electricity | 2007 | 2007-02-11 | 0.051702 | 0.0057447
Wellington Electricity | 2007 | 2007-02-12 | 0.088357 | 0.0046233
Wellington Electricity | 2007 | 2007-02-13
Wellington Electricity | 2007 | 2007-02-14
Wellington Electricity | 2007 | 2007-02-15
Wellington Electricity | 2007 | 2007-02-16 | 0.36492 | 0.0093469
Wellington Electricity | 2007 | 2007-02-17
Wellington Electricity | 2007 | 2007-02-18 | 0.026462 | 0.0003007
Wellington Electricity | 2007 | 2007-02-19
Wellington Electricity | 2007 | 2007-02-20 | 0.00048551 | 3.1323e-06
Wellington Electricity | 2007 | 2007-02-21 | 0.35849 | 0.0038089
Wellington Electricity | 2007 | 2007-02-22 | 0.0027721 | 9.397e-06
Wellington Electricity | 2007 | 2007-02-23 | 0.079668 | 0.0027189
Wellington Electricity | 2007 | 2007-02-24
Wellington Electricity | 2007 | 2007-02-25
Wellington Electricity | 2007 | 2007-02-26 | 0.078265 | 0.0021112
Wellington Electricity | 2007 | 2007-02-27
Wellington Electricity | 2007 | 2007-02-28
Wellington Electricity | 2007 | 2007-03-01 | 0.017529 | 0.00020047
Wellington Electricity | 2007 | 2007-03-02 | 0.0015662 | 6.2647e-05
Wellington Electricity | 2007 | 2007-03-03 | 0.16462 | 0.0032952
Wellington Electricity | 2007 | 2007-03-04
Wellington Electricity | 2007 | 2007-03-05
Wellington Electricity | 2007 | 2007-03-06 | 0.0021926 | 6.2647e-06
Wellington Electricity | 2007 | 2007-03-07
Wellington Electricity | 2007 | 2007-03-08 | 0.0014973 | 2.1926e-05
Wellington Electricity | 2007 | 2007-03-09
Wellington Electricity | 2007 | 2007-03-10
Wellington Electricity | 2007 | 2007-03-11
Wellington Electricity | 2007 | 2007-03-12
Wellington Electricity | 2007 | 2007-03-13
Wellington Electricity | 2007 | 2007-03-14 | 0.20505 | 0.03127
Wellington Electricity | 2007 | 2007-03-15 | 0.30785 | 0.0029319
Wellington Electricity | 2007 | 2007-03-16
Wellington Electricity | 2007 | 2007-03-17 | 0.58263 | 0.0064025
Wellington Electricity | 2007 | 2007-03-18
Wellington Electricity | 2007 | 2007-03-19
Wellington Electricity | 2007 | 2007-03-20 | 0.039749 | 0.00028191
Wellington Electricity | 2007 | 2007-03-21
Wellington Electricity | 2007 | 2007-03-22
Wellington Electricity | 2007 | 2007-03-23 | 0.0073046 | 6.8912e-05
Wellington Electricity | 2007 | 2007-03-24
Wellington Electricity | 2007 | 2007-03-25 | 0.013469 | 6.2647e-05
Wellington Electricity | 2007 | 2007-03-26
Wellington Electricity | 2007 | 2007-03-27
Wellington Electricity | 2007 | 2007-03-28 | 0.0056664 | 5.9514e-05
Wellington Electricity | 2007 | 2007-03-29
Wellington Electricity | 2007 | 2007-03-30 | 0.0066875 | 2.1926e-05
Wellington Electricity | 2007 | 2007-03-31 | 0.23374 | 0.0033391
Wellington Electricity | 2008 | 2007-04-01
Wellington Electricity | 2008 | 2007-04-02
Wellington Electricity | 2008 | 2007-04-03
Wellington Electricity | 2008 | 2007-04-04 | 0.023781 | 0.00019817
Wellington Electricity | 2008 | 2007-04-05 | 0.33813 | 0.005202
Wellington Electricity | 2008 | 2007-04-06
Wellington Electricity | 2008 | 2007-04-07
Wellington Electricity | 2008 | 2007-04-08
Wellington Electricity | 2008 | 2007-04-09
Wellington Electricity | 2008 | 2007-04-10 | 0.10411 | 0.0016349
Wellington Electricity | 2008 | 2007-04-11 | 0.34718 | 0.0054993
Wellington Electricity | 2008 | 2007-04-12 | 0.076172 | 0.0012695
Wellington Electricity | 2008 | 2007-04-13
Wellington Electricity | 2008 | 2007-04-14
Wellington Electricity | 2008 | 2007-04-15
Wellington Electricity | 2008 | 2007-04-16 | 0.021403 | 0.00019817
Wellington Electricity | 2008 | 2007-04-17 | 0.29647 | 0.0033008
Wellington Electricity | 2008 | 2007-04-18 | 0.0042112 | 3.7157e-05
Wellington Electricity | 2008 | 2007-04-19
Wellington Electricity | 2008 | 2007-04-20
Wellington Electricity | 2008 | 2007-04-21 | 0.11422 | 0.0010776
Wellington Electricity | 2008 | 2007-04-22
Wellington Electricity | 2008 | 2007-04-23
Wellington Electricity | 2008 | 2007-04-24
Wellington Electricity | 2008 | 2007-04-25
Wellington Electricity | 2008 | 2007-04-26
Wellington Electricity | 2008 | 2007-04-27 | 0.082932 | 0.0011735
Wellington Electricity | 2008 | 2007-04-28
Wellington Electricity | 2008 | 2007-04-29
Wellington Electricity | 2008 | 2007-04-30
Wellington Electricity | 2008 | 2007-05-01 | 0.3754 | 0.0065025
Wellington Electricity | 2008 | 2007-05-02 | 0.29222 | 0.0011085
Wellington Electricity | 2008 | 2007-05-03 | 0.30557 | 0.0099024
Wellington Electricity | 2008 | 2007-05-04
Wellington Electricity | 2008 | 2007-05-05
Wellington Electricity | 2008 | 2007-05-06
Wellington Electricity | 2008 | 2007-05-07
Wellington Electricity | 2008 | 2007-05-08
Wellington Electricity | 2008 | 2007-05-09 | 0.50242 | 0.003499
Wellington Electricity | 2008 | 2007-05-10 | 0.887 | 0.0095989
Wellington Electricity | 2008 | 2007-05-11
Wellington Electricity | 2008 | 2007-05-12
Wellington Electricity | 2008 | 2007-05-13
Wellington Electricity | 2008 | 2007-05-14
Wellington Electricity | 2008 | 2007-05-15
Wellington Electricity | 2008 | 2007-05-16 | 0.013674 | 0.00019817
Wellington Electricity | 2008 | 2007-05-17
Wellington Electricity | 2008 | 2007-05-18
Wellington Electricity | 2008 | 2007-05-19
Wellington Electricity | 2008 | 2007-05-20
Wellington Electricity | 2008 | 2007-05-21 | 0.29046 | 0.0054559
Wellington Electricity | 2008 | 2007-05-22 | 0.31212 | 0.0019508
Wellington Electricity | 2008 | 2007-05-23
Wellington Electricity | 2008 | 2007-05-24 | 0.0022914 | 6.1929e-06
Wellington Electricity | 2008 | 2007-05-25
Wellington Electricity | 2008 | 2007-05-26
Wellington Electricity | 2008 | 2007-05-27 | 0.045703 | 0.0010156
Wellington Electricity | 2008 | 2007-05-28
Wellington Electricity | 2008 | 2007-05-29
Wellington Electricity | 2008 | 2007-05-30
Wellington Electricity | 2008 | 2007-05-31
Wellington Electricity | 2008 | 2007-06-01
Wellington Electricity | 2008 | 2007-06-02
Wellington Electricity | 2008 | 2007-06-03
Wellington Electricity | 2008 | 2007-06-04
Wellington Electricity | 2008 | 2007-06-05
Wellington Electricity | 2008 | 2007-06-06
Wellington Electricity | 2008 | 2007-06-07
Wellington Electricity | 2008 | 2007-06-08
Wellington Electricity | 2008 | 2007-06-09
Wellington Electricity | 2008 | 2007-06-10
Wellington Electricity | 2008 | 2007-06-11
Wellington Electricity | 2008 | 2007-06-12
Wellington Electricity | 2008 | 2007-06-13
Wellington Electricity | 2008 | 2007-06-14
Wellington Electricity | 2008 | 2007-06-15
Wellington Electricity | 2008 | 2007-06-16
Wellington Electricity | 2008 | 2007-06-17 | 0.010404 | 3.7157e-05
Wellington Electricity | 2008 | 2007-06-18
Wellington Electricity | 2008 | 2007-06-19
Wellington Electricity | 2008 | 2007-06-20 | 0.42061 | 0.0066419
Wellington Electricity | 2008 | 2007-06-21 | 0.50212 | 0.0031893
Wellington Electricity | 2008 | 2007-06-22
Wellington Electricity | 2008 | 2007-06-23
Wellington Electricity | 2008 | 2007-06-24
Wellington Electricity | 2008 | 2007-06-25
Wellington Electricity | 2008 | 2007-06-26
Wellington Electricity | 2008 | 2007-06-27 | 0.37615 | 0.0054373
Wellington Electricity | 2008 | 2007-06-28 | 0.00014863 | 6.1929e-06
Wellington Electricity | 2008 | 2007-06-29 | 0.14284 | 0.001381
Wellington Electricity | 2008 | 2007-06-30 | 0.56098 | 0.0053878
Wellington Electricity | 2008 | 2007-07-01
Wellington Electricity | 2008 | 2007-07-02
Wellington Electricity | 2008 | 2007-07-03
Wellington Electricity | 2008 | 2007-07-04
Wellington Electricity | 2008 | 2007-07-05 | 0.4896 | 0.005202
Wellington Electricity | 2008 | 2007-07-06 | 0.20241 | 0.005202
Wellington Electricity | 2008 | 2007-07-07
Wellington Electricity | 2008 | 2007-07-08
Wellington Electricity | 2008 | 2007-07-09 | 0.0027496 | 2.4771e-05
Wellington Electricity | 2008 | 2007-07-10
Wellington Electricity | 2008 | 2007-07-11
Wellington Electricity | 2008 | 2007-07-12
Wellington Electricity | 2008 | 2007-07-13
Wellington Electricity | 2008 | 2007-07-14
Wellington Electricity | 2008 | 2007-07-15 | 0.88109 | 0.01482
Wellington Electricity | 2008 | 2007-07-16
Wellington Electricity | 2008 | 2007-07-17
Wellington Electricity | 2008 | 2007-07-18
Wellington Electricity | 2008 | 2007-07-19
Wellington Electricity | 2008 | 2007-07-20 | 0.10315 | 0.0021489
Wellington Electricity | 2008 | 2007-07-21
Wellington Electricity | 2008 | 2007-07-22
Wellington Electricity | 2008 | 2007-07-23 | 0.0036228 | 6.1929e-06
Wellington Electricity | 2008 | 2007-07-24
Wellington Electricity | 2008 | 2007-07-25
Wellington Electricity | 2008 | 2007-07-26
Wellington Electricity | 2008 | 2007-07-27
Wellington Electricity | 2008 | 2007-07-28
Wellington Electricity | 2008 | 2007-07-29
Wellington Electricity | 2008 | 2007-07-30
Wellington Electricity | 2008 | 2007-07-31
Wellington Electricity | 2008 | 2007-08-01
Wellington Electricity | 2008 | 2007-08-02
Wellington Electricity | 2008 | 2007-08-03
Wellington Electricity | 2008 | 2007-08-04
Wellington Electricity | 2008 | 2007-08-05
Wellington Electricity | 2008 | 2007-08-06 | 0.1525 | 0.0010652
Wellington Electricity | 2008 | 2007-08-07 | 0.00093203 | 3.0964e-06
Wellington Electricity | 2008 | 2007-08-08
Wellington Electricity | 2008 | 2007-08-09 | 0.028952 | 0.001703
Wellington Electricity | 2008 | 2007-08-10 | 0.90898 | 0.0096237
Wellington Electricity | 2008 | 2007-08-11 | 0.062752 | 0.00135
Wellington Electricity | 2008 | 2007-08-12 | 0.87923 | 0.0063291
Wellington Electricity | 2008 | 2007-08-13
Wellington Electricity | 2008 | 2007-08-14
Wellington Electricity | 2008 | 2007-08-15 | 0.4764 | 0.0083418
Wellington Electricity | 2008 | 2007-08-16 | 0.0065025 | 6.1929e-05
Wellington Electricity | 2008 | 2007-08-17
Wellington Electricity | 2008 | 2007-08-18
Wellington Electricity | 2008 | 2007-08-19
Wellington Electricity | 2008 | 2007-08-20 | 0.00040254 | 6.1929e-06
Wellington Electricity | 2008 | 2007-08-21
Wellington Electricity | 2008 | 2007-08-22 | 0.10396 | 0.0017928
Wellington Electricity | 2008 | 2007-08-23 | 0.13246 | 0.0018145
Wellington Electricity | 2008 | 2007-08-24 | 0.024493 | 0.00021675
Wellington Electricity | 2008 | 2007-08-25
Wellington Electricity | 2008 | 2007-08-26
Wellington Electricity | 2008 | 2007-08-27
Wellington Electricity | 2008 | 2007-08-28
Wellington Electricity | 2008 | 2007-08-29 | 0.18115 | 0.0033194
Wellington Electricity | 2008 | 2007-08-30
Wellington Electricity | 2008 | 2007-08-31
Wellington Electricity | 2008 | 2007-09-01 | 0.1265 | 0.0016349
Wellington Electricity | 2008 | 2007-09-02
Wellington Electricity | 2008 | 2007-09-03
Wellington Electricity | 2008 | 2007-09-04
Wellington Electricity | 2008 | 2007-09-05
Wellington Electricity | 2008 | 2007-09-06
Wellington Electricity | 2008 | 2007-09-07 | 0.3897 | 0.0047685
Wellington Electricity | 2008 | 2007-09-08
Wellington Electricity | 2008 | 2007-09-09 | 0.0096671 | 6.1929e-06
Wellington Electricity | 2008 | 2007-09-10
Wellington Electricity | 2008 | 2007-09-11
Wellington Electricity | 2008 | 2007-09-12
Wellington Electricity | 2008 | 2007-09-13
Wellington Electricity | 2008 | 2007-09-14
Wellington Electricity | 2008 | 2007-09-15
Wellington Electricity | 2008 | 2007-09-16 | 0.044217 | 0.00042112
Wellington Electricity | 2008 | 2007-09-17
Wellington Electricity | 2008 | 2007-09-18
Wellington Electricity | 2008 | 2007-09-19
Wellington Electricity | 2008 | 2007-09-20 | 0.19348 | 0.0023595
Wellington Electricity | 2008 | 2007-09-21
Wellington Electricity | 2008 | 2007-09-22
Wellington Electricity | 2008 | 2007-09-23 | 0.0013377 | 3.0964e-06
Wellington Electricity | 2008 | 2007-09-24 | 0.65023 | 0.010943
Wellington Electricity | 2008 | 2007-09-25 | 0.71363 | 0.010472
Wellington Electricity | 2008 | 2007-09-26
Wellington Electricity | 2008 | 2007-09-27 | 0.002601 | 2.4771e-05
Wellington Electricity | 2008 | 2007-09-28
Wellington Electricity | 2008 | 2007-09-29
Wellington Electricity | 2008 | 2007-09-30 | 0.028419 | 8.0507e-05
Wellington Electricity | 2008 | 2007-10-01 | 0.2118 | 0.0069979
Wellington Electricity | 2008 | 2007-10-02
Wellington Electricity | 2008 | 2007-10-03 | 0.048026 | 0.00029106
Wellington Electricity | 2008 | 2007-10-04 | 0.6012 | 0.0084904
Wellington Electricity | 2008 | 2007-10-05 | 0.58861 | 0.0053321
Wellington Electricity | 2008 | 2007-10-06
Wellington Electricity | 2008 | 2007-10-07 | 0.71495 | 0.018034
Wellington Electricity | 2008 | 2007-10-08 | 0.0016968 | 6.1929e-06
Wellington Electricity | 2008 | 2007-10-09
Wellington Electricity | 2008 | 2007-10-10 | 0.77348 | 0.0031584
Wellington Electricity | 2008 | 2007-10-11
Wellington Electricity | 2008 | 2007-10-12 | 0.258 | 0.0046261
Wellington Electricity | 2008 | 2007-10-13 | 1.6767 | 0.013408
Wellington Electricity | 2008 | 2007-10-14 | 0.014863 | 4.9543e-05
Wellington Electricity | 2008 | 2007-10-15
Wellington Electricity | 2008 | 2007-10-16 | 0.49511 | 0.012163
Wellington Electricity | 2008 | 2007-10-17 | 0.12338 | 0.00867
Wellington Electricity | 2008 | 2007-10-18
Wellington Electricity | 2008 | 2007-10-19
Wellington Electricity | 2008 | 2007-10-20 | 0.00071218 | 6.1929e-06
Wellington Electricity | 2008 | 2007-10-21 | 0.014826 | 6.8122e-05
Wellington Electricity | 2008 | 2007-10-22 | 0.0053321 | 0.0053321
Wellington Electricity | 2008 | 2007-10-23
Wellington Electricity | 2008 | 2007-10-24 | 0.0011457 | 3.0964e-06
Wellington Electricity | 2008 | 2007-10-25 | 0.022579 | 0.00052639
Wellington Electricity | 2008 | 2007-10-26 | 0.054287 | 0.0016411
Wellington Electricity | 2008 | 2007-10-27
Wellington Electricity | 2008 | 2007-10-28
Wellington Electricity | 2008 | 2007-10-29
Wellington Electricity | 2008 | 2007-10-30 | 0.069812 | 0.0016349
Wellington Electricity | 2008 | 2007-10-31 | 0.0043474 | 1.2386e-05
Wellington Electricity | 2008 | 2007-11-01
Wellington Electricity | 2008 | 2007-11-02 | 0.033516 | 0.00085462
Wellington Electricity | 2008 | 2007-11-03
Wellington Electricity | 2008 | 2007-11-04
Wellington Electricity | 2008 | 2007-11-05 | 0.23327 | 0.0027868
Wellington Electricity | 2008 | 2007-11-06
Wellington Electricity | 2008 | 2007-11-07
Wellington Electricity | 2008 | 2007-11-08
Wellington Electricity | 2008 | 2007-11-09
Wellington Electricity | 2008 | 2007-11-10
Wellington Electricity | 2008 | 2007-11-11 | 0.10417 | 0.0049605
Wellington Electricity | 2008 | 2007-11-12
Wellington Electricity | 2008 | 2007-11-13 | 0.25506 | 0.0039356
Wellington Electricity | 2008 | 2007-11-14 | 0.88826 | 0.010769
Wellington Electricity | 2008 | 2007-11-15 | 0.022164 | 0.00084842
Wellington Electricity | 2008 | 2007-11-16
Wellington Electricity | 2008 | 2007-11-17 | 0.0027496 | 7.4314e-05
Wellington Electricity | 2008 | 2007-11-18 | 0.68649 | 0.0080569
Wellington Electricity | 2008 | 2007-11-19
Wellington Electricity | 2008 | 2007-11-20 | 0.012863 | 4.6447e-05
Wellington Electricity | 2008 | 2007-11-21
Wellington Electricity | 2008 | 2007-11-22 | 0.00032203 | 6.1929e-06
Wellington Electricity | 2008 | 2007-11-23
Wellington Electricity | 2008 | 2007-11-24 | 0.33809 | 0.016436
Wellington Electricity | 2008 | 2007-11-25
Wellington Electricity | 2008 | 2007-11-26
Wellington Electricity | 2008 | 2007-11-27
Wellington Electricity | 2008 | 2007-11-28 | 0.0063105 | 6.1929e-06
Wellington Electricity | 2008 | 2007-11-29
Wellington Electricity | 2008 | 2007-11-30
Wellington Electricity | 2008 | 2007-12-01
Wellington Electricity | 2008 | 2007-12-02
Wellington Electricity | 2008 | 2007-12-03
Wellington Electricity | 2008 | 2007-12-04
Wellington Electricity | 2008 | 2007-12-05 | 0.011581 | 0.00010528
Wellington Electricity | 2008 | 2007-12-06
Wellington Electricity | 2008 | 2007-12-07 | 0.00070599 | 1.2386e-05
Wellington Electricity | 2008 | 2007-12-08
Wellington Electricity | 2008 | 2007-12-09 | 0.26172 | 0.002601
Wellington Electricity | 2008 | 2007-12-10 | 0.58269 | 0.01638
Wellington Electricity | 2008 | 2007-12-11 | 1.1114 | 0.013686
Wellington Electricity | 2008 | 2007-12-12 | 0.057433 | 0.0020498
Wellington Electricity | 2008 | 2007-12-13 | 0.37692 | 0.0080445
Wellington Electricity | 2008 | 2007-12-14
Wellington Electricity | 2008 | 2007-12-15
Wellington Electricity | 2008 | 2007-12-16
Wellington Electricity | 2008 | 2007-12-17
Wellington Electricity | 2008 | 2007-12-18 | 0.070599 | 0.00061929
Wellington Electricity | 2008 | 2007-12-19 | 0.38633 | 0.004366
Wellington Electricity | 2008 | 2007-12-20 | 0.021056 | 6.1929e-05
Wellington Electricity | 2008 | 2007-12-21 | 0.045802 | 0.0006936
Wellington Electricity | 2008 | 2007-12-22
Wellington Electricity | 2008 | 2007-12-23
Wellington Electricity | 2008 | 2007-12-24 | 0.045926 | 0.00055736
Wellington Electricity | 2008 | 2007-12-25 | 0.21137 | 0.0015978
Wellington Electricity | 2008 | 2007-12-26
Wellington Electricity | 2008 | 2007-12-27 | 0.0031026 | 1.8579e-05
Wellington Electricity | 2008 | 2007-12-28
Wellington Electricity | 2008 | 2007-12-29
Wellington Electricity | 2008 | 2007-12-30
Wellington Electricity | 2008 | 2007-12-31 | 0.30989 | 0.0032451
Wellington Electricity | 2008 | 2008-01-01
Wellington Electricity | 2008 | 2008-01-02
Wellington Electricity | 2008 | 2008-01-03 | 0.035894 | 0.00022294
Wellington Electricity | 2008 | 2008-01-04
Wellington Electricity | 2008 | 2008-01-05
Wellington Electricity | 2008 | 2008-01-06
Wellington Electricity | 2008 | 2008-01-07 | 0.027695 | 0.00032203
Wellington Electricity | 2008 | 2008-01-08 | 0.007803 | 0.0002601
Wellington Electricity | 2008 | 2008-01-09
Wellington Electricity | 2008 | 2008-01-10 | 0.021681 | 0.00022294
Wellington Electricity | 2008 | 2008-01-11 | 0.0010652 | 2.4771e-05
Wellington Electricity | 2008 | 2008-01-12 | 0.01106 | 0.00023533
Wellington Electricity | 2008 | 2008-01-13 | 0.00061929 | 3.0964e-06
Wellington Electricity | 2008 | 2008-01-14 | 0.13238 | 0.010683
Wellington Electricity | 2008 | 2008-01-15 | 0.2592 | 0.0046632
Wellington Electricity | 2008 | 2008-01-16 | 0.0010899 | 6.1929e-06
Wellington Electricity | 2008 | 2008-01-17
Wellington Electricity | 2008 | 2008-01-18 | 0.064623 | 0.0010094
Wellington Electricity | 2008 | 2008-01-19
Wellington Electricity | 2008 | 2008-01-20 | 0.00055117 | 6.1929e-06
Wellington Electricity | 2008 | 2008-01-21 | 0.020003 | 0.00023533
Wellington Electricity | 2008 | 2008-01-22 | 0.063545 | 0.0015544
Wellington Electricity | 2008 | 2008-01-23 | 0.00048924 | 6.1929e-06
Wellington Electricity | 2008 | 2008-01-24
Wellington Electricity | 2008 | 2008-01-25 | 0.081003 | 0.0015668
Wellington Electricity | 2008 | 2008-01-26
Wellington Electricity | 2008 | 2008-01-27 | 0.0010156 | 1.2386e-05
Wellington Electricity | 2008 | 2008-01-28
Wellington Electricity | 2008 | 2008-01-29
Wellington Electricity | 2008 | 2008-01-30
Wellington Electricity | 2008 | 2008-01-31 | 0.0014553 | 0.0014553
Wellington Electricity | 2008 | 2008-02-01 | 0.20946 | 0.0017464
Wellington Electricity | 2008 | 2008-02-02
Wellington Electricity | 2008 | 2008-02-03 | 0.26958 | 0.0029354
Wellington Electricity | 2008 | 2008-02-04
Wellington Electricity | 2008 | 2008-02-05 | 0.0045765 | 1.2386e-05
Wellington Electricity | 2008 | 2008-02-06
Wellington Electricity | 2008 | 2008-02-07 | 0.022759 | 0.00021675
Wellington Electricity | 2008 | 2008-02-08 | 0.0021675 | 0.00015482
Wellington Electricity | 2008 | 2008-02-09
Wellington Electricity | 2008 | 2008-02-10
Wellington Electricity | 2008 | 2008-02-11 | 0.64035 | 0.0054373
Wellington Electricity | 2008 | 2008-02-12
Wellington Electricity | 2008 | 2008-02-13 | 0.0026815 | 6.1929e-06
Wellington Electricity | 2008 | 2008-02-14
Wellington Electricity | 2008 | 2008-02-15
Wellington Electricity | 2008 | 2008-02-16
Wellington Electricity | 2008 | 2008-02-17
Wellington Electricity | 2008 | 2008-02-18 | 0.38905 | 0.0090478
Wellington Electricity | 2008 | 2008-02-19
Wellington Electricity | 2008 | 2008-02-20
Wellington Electricity | 2008 | 2008-02-21 | 1.8957 | 0.031245
Wellington Electricity | 2008 | 2008-02-22 | 0.12827 | 0.0026815
Wellington Electricity | 2008 | 2008-02-23
Wellington Electricity | 2008 | 2008-02-24
Wellington Electricity | 2008 | 2008-02-25
Wellington Electricity | 2008 | 2008-02-26
Wellington Electricity | 2008 | 2008-02-27
Wellington Electricity | 2008 | 2008-02-28
Wellington Electricity | 2008 | 2008-02-29
Wellington Electricity | 2008 | 2008-03-01 | 0.52011 | 0.0075615
Wellington Electricity | 2008 | 2008-03-02 | 0.20618 | 0.001895
Wellington Electricity | 2008 | 2008-03-03
Wellington Electricity | 2008 | 2008-03-04
Wellington Electricity | 2008 | 2008-03-05
Wellington Electricity | 2008 | 2008-03-06 | 0.063923 | 0.00081127
Wellington Electricity | 2008 | 2008-03-07
Wellington Electricity | 2008 | 2008-03-08
Wellington Electricity | 2008 | 2008-03-09
Wellington Electricity | 2008 | 2008-03-10
Wellington Electricity | 2008 | 2008-03-11 | 0.075925 | 0.0019569
Wellington Electricity | 2008 | 2008-03-12 | 0.044477 | 0.0002601
Wellington Electricity | 2008 | 2008-03-13 | 0.012745 | 0.0002601
Wellington Electricity | 2008 | 2008-03-14 | 0.00053878 | 3.0964e-06
Wellington Electricity | 2008 | 2008-03-15 | 0.43559 | 0.031245
Wellington Electricity | 2008 | 2008-03-16 | 0.070351 | 0.00099086
Wellington Electricity | 2008 | 2008-03-17
Wellington Electricity | 2008 | 2008-03-18 | 0.050221 | 0.00030964
Wellington Electricity | 2008 | 2008-03-19 | 0.020214 | 0.010107
Wellington Electricity | 2008 | 2008-03-20 | 0.0047314 | 1.2386e-05
Wellington Electricity | 2008 | 2008-03-21
Wellington Electricity | 2008 | 2008-03-22 | 0.15581 | 0.0038953
Wellington Electricity | 2008 | 2008-03-23 | 0.30301 | 0.0024276
Wellington Electricity | 2008 | 2008-03-24
Wellington Electricity | 2008 | 2008-03-25 | 0.049246 | 0.00021985
Wellington Electricity | 2008 | 2008-03-26 | 0.011581 | 3.0964e-05
Wellington Electricity | 2008 | 2008-03-27 | 0.0024895 | 1.2386e-05
Wellington Electricity | 2008 | 2008-03-28
Wellington Electricity | 2008 | 2008-03-29
Wellington Electricity | 2008 | 2008-03-30 | 0.0021675 | 6.1929e-06
Wellington Electricity | 2008 | 2008-03-31
Wellington Electricity | 2009 | 2008-04-01 | 0.21265 | 0.006063
Wellington Electricity | 2009 | 2008-04-02 | 0.18624 | 0.0040492
Wellington Electricity | 2009 | 2008-04-03
Wellington Electricity | 2009 | 2008-04-04 | 0.014789 | 0.00039969
Wellington Electricity | 2009 | 2008-04-05
Wellington Electricity | 2009 | 2008-04-06
Wellington Electricity | 2009 | 2008-04-07
Wellington Electricity | 2009 | 2008-04-08
Wellington Electricity | 2009 | 2008-04-09
Wellington Electricity | 2009 | 2008-04-10
Wellington Electricity | 2009 | 2008-04-11
Wellington Electricity | 2009 | 2008-04-12
Wellington Electricity | 2009 | 2008-04-13
Wellington Electricity | 2009 | 2008-04-14 | 0.001814 | 6.1491e-06
Wellington Electricity | 2009 | 2008-04-15
Wellington Electricity | 2009 | 2008-04-16 | 0.053374 | 8.6088e-05
Wellington Electricity | 2009 | 2008-04-17 | 0.060138 | 9.2237e-05
Wellington Electricity | 2009 | 2008-04-18 | 0.0044274 | 1.8447e-05
Wellington Electricity | 2009 | 2008-04-19
Wellington Electricity | 2009 | 2008-04-20
Wellington Electricity | 2009 | 2008-04-21
Wellington Electricity | 2009 | 2008-04-22
Wellington Electricity | 2009 | 2008-04-23 | 0.00051038 | 3.0746e-06
Wellington Electricity | 2009 | 2008-04-24 | 0.0012667 | 3.0746e-06
Wellington Electricity | 2009 | 2008-04-25
Wellington Electricity | 2009 | 2008-04-26
Wellington Electricity | 2009 | 2008-04-27
Wellington Electricity | 2009 | 2008-04-28
Wellington Electricity | 2009 | 2008-04-29
Wellington Electricity | 2009 | 2008-04-30 | 0.00019677 | 6.1491e-06
Wellington Electricity | 2009 | 2008-05-01 | 0.00062106 | 2.1522e-05
Wellington Electricity | 2009 | 2008-05-02
Wellington Electricity | 2009 | 2008-05-03 | 0.041863 | 0.0001937
Wellington Electricity | 2009 | 2008-05-04
Wellington Electricity | 2009 | 2008-05-05 | 0.0016972 | 1.2298e-05
Wellington Electricity | 2009 | 2008-05-06 | 0.37305 | 0.030493
Wellington Electricity | 2009 | 2008-05-07 | 0.00078094 | 6.1491e-06
Wellington Electricity | 2009 | 2008-05-08
Wellington Electricity | 2009 | 2008-05-09 | 0.16341 | 0.0038002
Wellington Electricity | 2009 | 2008-05-10
Wellington Electricity | 2009 | 2008-05-11 | 0.10303 | 0.00098386
Wellington Electricity | 2009 | 2008-05-12
Wellington Electricity | 2009 | 2008-05-13 | 0.033543 | 0.00043966
Wellington Electricity | 2009 | 2008-05-14
Wellington Electricity | 2009 | 2008-05-15 | 0.018463 | 5.2267e-05
Wellington Electricity | 2009 | 2008-05-16
Wellington Electricity | 2009 | 2008-05-17
Wellington Electricity | 2009 | 2008-05-18
Wellington Electricity | 2009 | 2008-05-19
Wellington Electricity | 2009 | 2008-05-20
Wellington Electricity | 2009 | 2008-05-21
Wellington Electricity | 2009 | 2008-05-22 | 0.63489 | 0.013411
Wellington Electricity | 2009 | 2008-05-23 | 0.035776 | 0.00057802
Wellington Electricity | 2009 | 2008-05-24
Wellington Electricity | 2009 | 2008-05-25 | 0.032437 | 0.00038739
Wellington Electricity | 2009 | 2008-05-26
Wellington Electricity | 2009 | 2008-05-27 | 0.0091929 | 0.00014143
Wellington Electricity | 2009 | 2008-05-28
Wellington Electricity | 2009 | 2008-05-29 | 0.0045135 | 0.0022567
Wellington Electricity | 2009 | 2008-05-30
Wellington Electricity | 2009 | 2008-05-31
Wellington Electricity | 2009 | 2008-06-01 | 0.85831 | 0.0082767
Wellington Electricity | 2009 | 2008-06-02
Wellington Electricity | 2009 | 2008-06-03
Wellington Electricity | 2009 | 2008-06-04
Wellington Electricity | 2009 | 2008-06-05 | 0.54199 | 0.0090146
Wellington Electricity | 2009 | 2008-06-06
Wellington Electricity | 2009 | 2008-06-07 | 0.046727 | 0.0025088
Wellington Electricity | 2009 | 2008-06-08 | 0.010367 | 3.0746e-05
Wellington Electricity | 2009 | 2008-06-09 | 0.63851 | 0.019394
Wellington Electricity | 2009 | 2008-06-10 | 0.24649 | 0.0003259
Wellington Electricity | 2009 | 2008-06-11
Wellington Electricity | 2009 | 2008-06-12
Wellington Electricity | 2009 | 2008-06-13
Wellington Electricity | 2009 | 2008-06-14
Wellington Electricity | 2009 | 2008-06-15 | 0.0036649 | 2.4596e-05
Wellington Electricity | 2009 | 2008-06-16 | 0.0092421 | 2.7671e-05
Wellington Electricity | 2009 | 2008-06-17 | 0.12532 | 0.0021522
Wellington Electricity | 2009 | 2008-06-18
Wellington Electricity | 2009 | 2008-06-19
Wellington Electricity | 2009 | 2008-06-20
Wellington Electricity | 2009 | 2008-06-21
Wellington Electricity | 2009 | 2008-06-22
Wellington Electricity | 2009 | 2008-06-23
Wellington Electricity | 2009 | 2008-06-24 | 0.71819 | 0.0062168
Wellington Electricity | 2009 | 2008-06-25
Wellington Electricity | 2009 | 2008-06-26 | 0.017267 | 0.00011068
Wellington Electricity | 2009 | 2008-06-27 | 1.4026 | 0.0085534
Wellington Electricity | 2009 | 2008-06-28 | 0.020907 | 0.00041814
Wellington Electricity | 2009 | 2008-06-29 | 0.070444 | 0.0012052
Wellington Electricity | 2009 | 2008-06-30
Wellington Electricity | 2009 | 2008-07-01
Wellington Electricity | 2009 | 2008-07-02
Wellington Electricity | 2009 | 2008-07-03
Wellington Electricity | 2009 | 2008-07-04
Wellington Electricity | 2009 | 2008-07-05 | 0.61226 | 0.0052882
Wellington Electricity | 2009 | 2008-07-06 | 0.83881 | 0.0079078
Wellington Electricity | 2009 | 2008-07-07
Wellington Electricity | 2009 | 2008-07-08 | 0.023699 | 0.00028901
Wellington Electricity | 2009 | 2008-07-09
Wellington Electricity | 2009 | 2008-07-10
Wellington Electricity | 2009 | 2008-07-11
Wellington Electricity | 2009 | 2008-07-12
Wellington Electricity | 2009 | 2008-07-13 | 0.082644 | 0.00029516
Wellington Electricity | 2009 | 2008-07-14 | 0.010982 | 0.00028901
Wellington Electricity | 2009 | 2008-07-15
Wellington Electricity | 2009 | 2008-07-16
Wellington Electricity | 2009 | 2008-07-17 | 0.022263 | 9.5311e-05
Wellington Electricity | 2009 | 2008-07-18
Wellington Electricity | 2009 | 2008-07-19 | 0.029442 | 0.0003505
Wellington Electricity | 2009 | 2008-07-20
Wellington Electricity | 2009 | 2008-07-21 | 0.24229 | 0.0037387
Wellington Electricity | 2009 | 2008-07-22 | 0.00021522 | 6.1491e-06
Wellington Electricity | 2009 | 2008-07-23 | 0.30713 | 0.0024965
Wellington Electricity | 2009 | 2008-07-24 | 0.47487 | 0.0061184
Wellington Electricity | 2009 | 2008-07-25 | 0.78147 | 0.0073482
Wellington Electricity | 2009 | 2008-07-26
Wellington Electricity | 2009 | 2008-07-27
Wellington Electricity | 2009 | 2008-07-28
Wellington Electricity | 2009 | 2008-07-29
Wellington Electricity | 2009 | 2008-07-30 | 2.1026 | 0.024972
Wellington Electricity | 2009 | 2008-07-31 | 0.021983 | 0.00016603
Wellington Electricity | 2009 | 2008-08-01 | 0.0069731 | 0.00017218
Wellington Electricity | 2009 | 2008-08-02 | 0.30358 | 0.0048978
Wellington Electricity | 2009 | 2008-08-03 | 0.20039 | 0.0034312
Wellington Electricity | 2009 | 2008-08-04
Wellington Electricity | 2009 | 2008-08-05
Wellington Electricity | 2009 | 2008-08-06
Wellington Electricity | 2009 | 2008-08-07 | 0.0088732 | 1.8447e-05
Wellington Electricity | 2009 | 2008-08-08 | 0.93072 | 0.029073
Wellington Electricity | 2009 | 2008-08-09
Wellington Electricity | 2009 | 2008-08-10
Wellington Electricity | 2009 | 2008-08-11
Wellington Electricity | 2009 | 2008-08-12
Wellington Electricity | 2009 | 2008-08-13 | 0.74851 | 0.011087
Wellington Electricity | 2009 | 2008-08-14
Wellington Electricity | 2009 | 2008-08-15 | 0.95667 | 0.0065611
Wellington Electricity | 2009 | 2008-08-16 | 0.50683 | 0.0056879
Wellington Electricity | 2009 | 2008-08-17
Wellington Electricity | 2009 | 2008-08-18
Wellington Electricity | 2009 | 2008-08-19
Wellington Electricity | 2009 | 2008-08-20 | 0.0068747 | 0.00015988
Wellington Electricity | 2009 | 2008-08-21 | 0.0068686 | 0.0068686
Wellington Electricity | 2009 | 2008-08-22
Wellington Electricity | 2009 | 2008-08-23
Wellington Electricity | 2009 | 2008-08-24 | 0.42636 | 0.0073482
Wellington Electricity | 2009 | 2008-08-25
Wellington Electricity | 2009 | 2008-08-26
Wellington Electricity | 2009 | 2008-08-27 | 0.0090761 | 0.00011068
Wellington Electricity | 2009 | 2008-08-28 | 0.030143 | 0.00023367
Wellington Electricity | 2009 | 2008-08-29
Wellington Electricity | 2009 | 2008-08-30
Wellington Electricity | 2009 | 2008-08-31
Wellington Electricity | 2009 | 2008-09-01 | 0.0039231 | 0.00013528
Wellington Electricity | 2009 | 2008-09-02 | 0.051487 | 0.00099001
Wellington Electricity | 2009 | 2008-09-03
Wellington Electricity | 2009 | 2008-09-04
Wellington Electricity | 2009 | 2008-09-05
Wellington Electricity | 2009 | 2008-09-06
Wellington Electricity | 2009 | 2008-09-07
Wellington Electricity | 2009 | 2008-09-08
Wellington Electricity | 2009 | 2008-09-09 | 0.017906 | 0.00063951
Wellington Electricity | 2009 | 2008-09-10 | 0.03351 | 0.0010423
Wellington Electricity | 2009 | 2008-09-11
Wellington Electricity | 2009 | 2008-09-12
Wellington Electricity | 2009 | 2008-09-13
Wellington Electricity | 2009 | 2008-09-14 | 0.00027671 | 6.1491e-06
Wellington Electricity | 2009 | 2008-09-15
Wellington Electricity | 2009 | 2008-09-16 | 0.013171 | 3.6895e-05
Wellington Electricity | 2009 | 2008-09-17
Wellington Electricity | 2009 | 2008-09-18 | 0.28236 | 0.0051007
Wellington Electricity | 2009 | 2008-09-19
Wellington Electricity | 2009 | 2008-09-20
Wellington Electricity | 2009 | 2008-09-21
Wellington Electricity | 2009 | 2008-09-22 | 0.0035665 | 9.2237e-06
Wellington Electricity | 2009 | 2008-09-23 | 0.32769 | 0.0022444
Wellington Electricity | 2009 | 2008-09-24 | 0.0037018 | 1.2298e-05
Wellington Electricity | 2009 | 2008-09-25 | 0.99649 | 0.031347
Wellington Electricity | 2009 | 2008-09-26 | 0.0022444 | 6.1491e-06
Wellington Electricity | 2009 | 2008-09-27
Wellington Electricity | 2009 | 2008-09-28
Wellington Electricity | 2009 | 2008-09-29
Wellington Electricity | 2009 | 2008-09-30
Wellington Electricity | 2009 | 2008-10-01 | 0.010453 | 0.00012298
Wellington Electricity | 2009 | 2008-10-02
Wellington Electricity | 2009 | 2008-10-03
Wellington Electricity | 2009 | 2008-10-04 | 0.044766 | 0.0006887
Wellington Electricity | 2009 | 2008-10-05
Wellington Electricity | 2009 | 2008-10-06
Wellington Electricity | 2009 | 2008-10-07 | 0.60523 | 0.0090085
Wellington Electricity | 2009 | 2008-10-08 | 0.008947 | 7.3789e-05
Wellington Electricity | 2009 | 2008-10-09
Wellington Electricity | 2009 | 2008-10-10
Wellington Electricity | 2009 | 2008-10-11
Wellington Electricity | 2009 | 2008-10-12
Wellington Electricity | 2009 | 2008-10-13
Wellington Electricity | 2009 | 2008-10-14 | 0.030552 | 0.00012298
Wellington Electricity | 2009 | 2008-10-15 | 0.16323 | 0.0027794
Wellington Electricity | 2009 | 2008-10-16
Wellington Electricity | 2009 | 2008-10-17
Wellington Electricity | 2009 | 2008-10-18
Wellington Electricity | 2009 | 2008-10-19
Wellington Electricity | 2009 | 2008-10-20
Wellington Electricity | 2009 | 2008-10-21
Wellington Electricity | 2009 | 2008-10-22
Wellington Electricity | 2009 | 2008-10-23 | 0.005073 | 0.0010146
Wellington Electricity | 2009 | 2008-10-24 | 0.016787 | 0.00039969
Wellington Electricity | 2009 | 2008-10-25
Wellington Electricity | 2009 | 2008-10-26 | 0.38679 | 0.0073543
Wellington Electricity | 2009 | 2008-10-27 | 0.3385 | 0.0090822
Wellington Electricity | 2009 | 2008-10-28 | 0.021682 | 0.0011007
Wellington Electricity | 2009 | 2008-10-29
Wellington Electricity | 2009 | 2008-10-30 | 0.86645 | 0.012572
Wellington Electricity | 2009 | 2008-10-31 | 0.19587 | 0.0045411
Wellington Electricity | 2009 | 2008-11-01 | 2.1026 | 0.023834
Wellington Electricity | 2009 | 2008-11-02
Wellington Electricity | 2009 | 2008-11-03
Wellington Electricity | 2009 | 2008-11-04 | 0.031496 | 0.0073728
Wellington Electricity | 2009 | 2008-11-05
Wellington Electricity | 2009 | 2008-11-06 | 0.0060876 | 1.5373e-05
Wellington Electricity | 2009 | 2008-11-07 | 0.001937 | 6.1491e-06
Wellington Electricity | 2009 | 2008-11-08
Wellington Electricity | 2009 | 2008-11-09
Wellington Electricity | 2009 | 2008-11-10 | 0.00092544 | 3.0746e-06
Wellington Electricity | 2009 | 2008-11-11 | 0.0012145 | 3.0746e-06
Wellington Electricity | 2009 | 2008-11-12 | 0.069076 | 0.0014727
Wellington Electricity | 2009 | 2008-11-13
Wellington Electricity | 2009 | 2008-11-14
Wellington Electricity | 2009 | 2008-11-15
Wellington Electricity | 2009 | 2008-11-16
Wellington Electricity | 2009 | 2008-11-17
Wellington Electricity | 2009 | 2008-11-18 | 0.0047963 | 1.2298e-05
Wellington Electricity | 2009 | 2008-11-19
Wellington Electricity | 2009 | 2008-11-20
Wellington Electricity | 2009 | 2008-11-21
Wellington Electricity | 2009 | 2008-11-22 | 0.00073789 | 6.1491e-06
Wellington Electricity | 2009 | 2008-11-23
Wellington Electricity | 2009 | 2008-11-24
Wellington Electricity | 2009 | 2008-11-25 | 0.019474 | 0.0032283
Wellington Electricity | 2009 | 2008-11-26
Wellington Electricity | 2009 | 2008-11-27 | 0.0035911 | 2.1522e-05
Wellington Electricity | 2009 | 2008-11-28
Wellington Electricity | 2009 | 2008-11-29
Wellington Electricity | 2009 | 2008-11-30
Wellington Electricity | 2009 | 2008-12-01
Wellington Electricity | 2009 | 2008-12-02 | 0.19191 | 0.003917
Wellington Electricity | 2009 | 2008-12-03 | 0.054389 | 0.00059646
Wellington Electricity | 2009 | 2008-12-04
Wellington Electricity | 2009 | 2008-12-05 | 0.00082398 | 0.00041199
Wellington Electricity | 2009 | 2008-12-06
Wellington Electricity | 2009 | 2008-12-07 | 0.58153 | 0.0091376
Wellington Electricity | 2009 | 2008-12-08
Wellington Electricity | 2009 | 2008-12-09 | 0.24326 | 0.0010576
Wellington Electricity | 2009 | 2008-12-10 | 0.46245 | 0.0078463
Wellington Electricity | 2009 | 2008-12-11 | 1.3225 | 0.013393
Wellington Electricity | 2009 | 2008-12-12
Wellington Electricity | 2009 | 2008-12-13
Wellington Electricity | 2009 | 2008-12-14
Wellington Electricity | 2009 | 2008-12-15 | 0.0021399 | 0.0021399
Wellington Electricity | 2009 | 2008-12-16
Wellington Electricity | 2009 | 2008-12-17
Wellington Electricity | 2009 | 2008-12-18 | 0.0021276 | 6.1491e-06
Wellington Electricity | 2009 | 2008-12-19
Wellington Electricity | 2009 | 2008-12-20
Wellington Electricity | 2009 | 2008-12-21 | 0.32129 | 0.0010576
Wellington Electricity | 2009 | 2008-12-22
Wellington Electricity | 2009 | 2008-12-23
Wellington Electricity | 2009 | 2008-12-24
Wellington Electricity | 2009 | 2008-12-25
Wellington Electricity | 2009 | 2008-12-26
Wellington Electricity | 2009 | 2008-12-27
Wellington Electricity | 2009 | 2008-12-28
Wellington Electricity | 2009 | 2008-12-29
Wellington Electricity | 2009 | 2008-12-30
Wellington Electricity | 2009 | 2008-12-31 | 0.0076188 | 0.0003628
Wellington Electricity | 2009 | 2009-01-01
Wellington Electricity | 2009 | 2009-01-02
Wellington Electricity | 2009 | 2009-01-03
Wellington Electricity | 2009 | 2009-01-04 | 0.6751 | 0.0051653
Wellington Electricity | 2009 | 2009-01-05 | 0.059511 | 0.00094696
Wellington Electricity | 2009 | 2009-01-06 | 0.00041199 | 6.1491e-06
Wellington Electricity | 2009 | 2009-01-07 | 0.0047686 | 9.2237e-06
Wellington Electricity | 2009 | 2009-01-08 | 0.012175 | 2.4596e-05
Wellington Electricity | 2009 | 2009-01-09 | 0.0034927 | 2.4596e-05
Wellington Electricity | 2009 | 2009-01-10
Wellington Electricity | 2009 | 2009-01-11
Wellington Electricity | 2009 | 2009-01-12 | 0.63744 | 0.010263
Wellington Electricity | 2009 | 2009-01-13 | 0.0045135 | 1.2298e-05
Wellington Electricity | 2009 | 2009-01-14 | 0.51625 | 0.0058232
Wellington Electricity | 2009 | 2009-01-15
Wellington Electricity | 2009 | 2009-01-16
Wellington Electricity | 2009 | 2009-01-17 | 0.0006641 | 6.1491e-06
Wellington Electricity | 2009 | 2009-01-18
Wellington Electricity | 2009 | 2009-01-19
Wellington Electricity | 2009 | 2009-01-20 | 0.0027794 | 6.1491e-06
Wellington Electricity | 2009 | 2009-01-21
Wellington Electricity | 2009 | 2009-01-22 | 0.02424 | 0.00064258
Wellington Electricity | 2009 | 2009-01-23 | 0.0017709 | 1.2298e-05
Wellington Electricity | 2009 | 2009-01-24 | 0.0023367 | 0.00023367
Wellington Electricity | 2009 | 2009-01-25
Wellington Electricity | 2009 | 2009-01-26
Wellington Electricity | 2009 | 2009-01-27
Wellington Electricity | 2009 | 2009-01-28
Wellington Electricity | 2009 | 2009-01-29 | 0.45953 | 0.0045442
Wellington Electricity | 2009 | 2009-01-30
Wellington Electricity | 2009 | 2009-01-31
Wellington Electricity | 2009 | 2009-02-01 | 0.037436 | 0.000701
Wellington Electricity | 2009 | 2009-02-02
Wellington Electricity | 2009 | 2009-02-03
Wellington Electricity | 2009 | 2009-02-04 | 0.016098 | 6.1491e-05
Wellington Electricity | 2009 | 2009-02-05 | 0.00065181 | 6.1491e-06
Wellington Electricity | 2009 | 2009-02-06
Wellington Electricity | 2009 | 2009-02-07
Wellington Electricity | 2009 | 2009-02-08
Wellington Electricity | 2009 | 2009-02-09 | 6.1491e-06 | 6.1491e-06
Wellington Electricity | 2009 | 2009-02-10
Wellington Electricity | 2009 | 2009-02-11
Wellington Electricity | 2009 | 2009-02-12 | 0.26294 | 0.0018201
Wellington Electricity | 2009 | 2009-02-13
Wellington Electricity | 2009 | 2009-02-14
Wellington Electricity | 2009 | 2009-02-15
Wellington Electricity | 2009 | 2009-02-16
Wellington Electricity | 2009 | 2009-02-17 | 0.01913 | 0.00023367
Wellington Electricity | 2009 | 2009-02-18 | 0.017018 | 0.0015035
Wellington Electricity | 2009 | 2009-02-19 | 0.74326 | 0.0082767
Wellington Electricity | 2009 | 2009-02-20 | 0.12982 | 0.0024965
Wellington Electricity | 2009 | 2009-02-21 | 0.22786 | 0.0012729
Wellington Electricity | 2009 | 2009-02-22 | 0.029651 | 0.00028901
Wellington Electricity | 2009 | 2009-02-23 | 0.048086 | 0.00041814
Wellington Electricity | 2009 | 2009-02-24
Wellington Electricity | 2009 | 2009-02-25
Wellington Electricity | 2009 | 2009-02-26
Wellington Electricity | 2009 | 2009-02-27
Wellington Electricity | 2009 | 2009-02-28 | 0.26472 | 0.0032283
Wellington Electricity | 2009 | 2009-03-01
Wellington Electricity | 2009 | 2009-03-02
Wellington Electricity | 2009 | 2009-03-03 | 0.1633 | 0.0016141
Wellington Electricity | 2009 | 2009-03-04
Wellington Electricity | 2009 | 2009-03-05
Wellington Electricity | 2009 | 2009-03-06
Wellington Electricity | 2009 | 2009-03-07
Wellington Electricity | 2009 | 2009-03-08
Wellington Electricity | 2009 | 2009-03-09
Wellington Electricity | 2009 | 2009-03-10
Wellington Electricity | 2009 | 2009-03-11
Wellington Electricity | 2009 | 2009-03-12
Wellington Electricity | 2009 | 2009-03-13
Wellington Electricity | 2009 | 2009-03-14 | 0.03406 | 0.0011745
Wellington Electricity | 2009 | 2009-03-15 | 0.91151 | 0.016141
Wellington Electricity | 2009 | 2009-03-16
Wellington Electricity | 2009 | 2009-03-17
Wellington Electricity | 2009 | 2009-03-18
Wellington Electricity | 2009 | 2009-03-19
Wellington Electricity | 2009 | 2009-03-20
Wellington Electricity | 2009 | 2009-03-21 | 0.42613 | 0.004538
Wellington Electricity | 2009 | 2009-03-22
Wellington Electricity | 2009 | 2009-03-23
Wellington Electricity | 2009 | 2009-03-24 | 0.20673 | 0.0020292
Wellington Electricity | 2009 | 2009-03-25
Wellington Electricity | 2009 | 2009-03-26
Wellington Electricity | 2009 | 2009-03-27 | 1.6033 | 0.016357
Wellington Electricity | 2009 | 2009-03-28
Wellington Electricity | 2009 | 2009-03-29 | 0.11511 | 0.0088547
Wellington Electricity | 2009 | 2009-03-30
Wellington Electricity | 2009 | 2009-03-31
Wellington Electricity | 2010 | 2009-04-01
Wellington Electricity | 2010 | 2009-04-02
Wellington Electricity | 2010 | 2009-04-03
Wellington Electricity | 2010 | 2009-04-04 | 0.007097 | 5.5015e-05
Wellington Electricity | 2010 | 2009-04-05
Wellington Electricity | 2010 | 2009-04-06 | 0.0020478 | 1.5282e-05
Wellington Electricity | 2010 | 2009-04-07 | 0.47241 | 0.0050003
Wellington Electricity | 2010 | 2009-04-08
Wellington Electricity | 2010 | 2009-04-09
Wellington Electricity | 2010 | 2009-04-10 | 0.22737 | 0.00087719
Wellington Electricity | 2010 | 2009-04-11
Wellington Electricity | 2010 | 2009-04-12 | 0.0089247 | 6.1128e-05
Wellington Electricity | 2010 | 2009-04-13
Wellington Electricity | 2010 | 2009-04-14 | 0.00077021 | 6.1128e-06
Wellington Electricity | 2010 | 2009-04-15 | 0.0013387 | 6.1128e-06
Wellington Electricity | 2010 | 2009-04-16
Wellington Electricity | 2010 | 2009-04-17 | 0.0003087 | 3.0564e-06
Wellington Electricity | 2010 | 2009-04-18
Wellington Electricity | 2010 | 2009-04-19
Wellington Electricity | 2010 | 2009-04-20
Wellington Electricity | 2010 | 2009-04-21
Wellington Electricity | 2010 | 2009-04-22
Wellington Electricity | 2010 | 2009-04-23 | 0.058108 | 0.0010636
Wellington Electricity | 2010 | 2009-04-24 | 0.11296 | 0.0016138
Wellington Electricity | 2010 | 2009-04-25
Wellington Electricity | 2010 | 2009-04-26
Wellington Electricity | 2010 | 2009-04-27 | 0.0038633 | 4.279e-05
Wellington Electricity | 2010 | 2009-04-28
Wellington Electricity | 2010 | 2009-04-29
Wellington Electricity | 2010 | 2009-04-30
Wellington Electricity | 2010 | 2009-05-01
Wellington Electricity | 2010 | 2009-05-02
Wellington Electricity | 2010 | 2009-05-03
Wellington Electricity | 2010 | 2009-05-04
Wellington Electricity | 2010 | 2009-05-05 | 0.017862 | 0.0089308
Wellington Electricity | 2010 | 2009-05-06 | 0.032019 | 0.00031175
Wellington Electricity | 2010 | 2009-05-07 | 0.067485 | 0.00058683
Wellington Electricity | 2010 | 2009-05-08
Wellington Electricity | 2010 | 2009-05-09
Wellington Electricity | 2010 | 2009-05-10
Wellington Electricity | 2010 | 2009-05-11 | 0.0013509 | 3.0564e-06
Wellington Electricity | 2010 | 2009-05-12
Wellington Electricity | 2010 | 2009-05-13
Wellington Electricity | 2010 | 2009-05-14
Wellington Electricity | 2010 | 2009-05-15 | 0.90599 | 0.017318
Wellington Electricity | 2010 | 2009-05-16
Wellington Electricity | 2010 | 2009-05-17 | 1.3427 | 0.014762
Wellington Electricity | 2010 | 2009-05-18 | 0.0016199 | 3.0564e-06
Wellington Electricity | 2010 | 2009-05-19
Wellington Electricity | 2010 | 2009-05-20 | 0.018228 | 8.5579e-05
Wellington Electricity | 2010 | 2009-05-21 | 0.69543 | 0.0049819
Wellington Electricity | 2010 | 2009-05-22 | 0.056134 | 0.0013876
Wellington Electricity | 2010 | 2009-05-23 | 2.1026 | 0.031245
Wellington Electricity | 2010 | 2009-05-24
Wellington Electricity | 2010 | 2009-05-25
Wellington Electricity | 2010 | 2009-05-26
Wellington Electricity | 2010 | 2009-05-27 | 0.0015832 | 6.1128e-06
Wellington Electricity | 2010 | 2009-05-28
Wellington Electricity | 2010 | 2009-05-29 | 0.058903 | 0.00080689
Wellington Electricity | 2010 | 2009-05-30
Wellington Electricity | 2010 | 2009-05-31 | 0.053255 | 0.00040345
Wellington Electricity | 2010 | 2009-06-01 | 0.042172 | 0.00044012
Wellington Electricity | 2010 | 2009-06-02
Wellington Electricity | 2010 | 2009-06-03
Wellington Electricity | 2010 | 2009-06-04 | 0.12515 | 0.0021211
Wellington Electricity | 2010 | 2009-06-05
Wellington Electricity | 2010 | 2009-06-06
Wellington Electricity | 2010 | 2009-06-07
Wellington Electricity | 2010 | 2009-06-08
Wellington Electricity | 2010 | 2009-06-09
Wellington Electricity | 2010 | 2009-06-10 | 0.011431 | 0.0075799
Wellington Electricity | 2010 | 2009-06-11
Wellington Electricity | 2010 | 2009-06-12
Wellington Electricity | 2010 | 2009-06-13 | 0.00092915 | 0.00011614
Wellington Electricity | 2010 | 2009-06-14
Wellington Electricity | 2010 | 2009-06-15 | 0.80747 | 0.0090164
Wellington Electricity | 2010 | 2009-06-16
Wellington Electricity | 2010 | 2009-06-17
Wellington Electricity | 2010 | 2009-06-18
Wellington Electricity | 2010 | 2009-06-19 | 0.066752 | 7.9466e-05
Wellington Electricity | 2010 | 2009-06-20 | 0.80077 | 0.0017177
Wellington Electricity | 2010 | 2009-06-21 | 0.044911 | 0.00056849
Wellington Electricity | 2010 | 2009-06-22
Wellington Electricity | 2010 | 2009-06-23
Wellington Electricity | 2010 | 2009-06-24
Wellington Electricity | 2010 | 2009-06-25
Wellington Electricity | 2010 | 2009-06-26
Wellington Electricity | 2010 | 2009-06-27
Wellington Electricity | 2010 | 2009-06-28 | 0.0069686 | 6.1128e-05
Wellington Electricity | 2010 | 2009-06-29
Wellington Electricity | 2010 | 2009-06-30
Wellington Electricity | 2010 | 2009-07-01
Wellington Electricity | 2010 | 2009-07-02
Wellington Electricity | 2010 | 2009-07-03
Wellington Electricity | 2010 | 2009-07-04
Wellington Electricity | 2010 | 2009-07-05
Wellington Electricity | 2010 | 2009-07-06
Wellington Electricity | 2010 | 2009-07-07
Wellington Electricity | 2010 | 2009-07-08
Wellington Electricity | 2010 | 2009-07-09 | 0.0070297 | 0.0070297
Wellington Electricity | 2010 | 2009-07-10
Wellington Electricity | 2010 | 2009-07-11
Wellington Electricity | 2010 | 2009-07-12
Wellington Electricity | 2010 | 2009-07-13
Wellington Electricity | 2010 | 2009-07-14
Wellington Electricity | 2010 | 2009-07-15 | 0.016133 | 0.00017727
Wellington Electricity | 2010 | 2009-07-16
Wellington Electricity | 2010 | 2009-07-17
Wellington Electricity | 2010 | 2009-07-18
Wellington Electricity | 2010 | 2009-07-19
Wellington Electricity | 2010 | 2009-07-20
Wellington Electricity | 2010 | 2009-07-21
Wellington Electricity | 2010 | 2009-07-22 | 0.13697 | 0.00055015
Wellington Electricity | 2010 | 2009-07-23 | 0.37437 | 0.0014915
Wellington Electricity | 2010 | 2009-07-24
Wellington Electricity | 2010 | 2009-07-25
Wellington Electricity | 2010 | 2009-07-26 | 0.51996 | 0.031245
Wellington Electricity | 2010 | 2009-07-27
Wellington Electricity | 2010 | 2009-07-28
Wellington Electricity | 2010 | 2009-07-29
Wellington Electricity | 2010 | 2009-07-30
Wellington Electricity | 2010 | 2009-07-31
Wellington Electricity | 2010 | 2009-08-01
Wellington Electricity | 2010 | 2009-08-02 | 0.015148 | 0.00025674
Wellington Electricity | 2010 | 2009-08-03
Wellington Electricity | 2010 | 2009-08-04 | 0.055406 | 0.00062962
Wellington Electricity | 2010 | 2009-08-05 | 0.062662 | 0.003307
Wellington Electricity | 2010 | 2009-08-06
Wellington Electricity | 2010 | 2009-08-07
Wellington Electricity | 2010 | 2009-08-08
Wellington Electricity | 2010 | 2009-08-09
Wellington Electricity | 2010 | 2009-08-10
Wellington Electricity | 2010 | 2009-08-11
Wellington Electricity | 2010 | 2009-08-12 | 0.0016321 | 6.1128e-06
Wellington Electricity | 2010 | 2009-08-13
Wellington Electricity | 2010 | 2009-08-14
Wellington Electricity | 2010 | 2009-08-15 | 0.0023106 | 6.1128e-06
Wellington Electricity | 2010 | 2009-08-16
Wellington Electricity | 2010 | 2009-08-17 | 0.026499 | 9.1692e-05
Wellington Electricity | 2010 | 2009-08-18 | 0.00029953 | 2.1395e-05
Wellington Electricity | 2010 | 2009-08-19 | 0.00041873 | 0.00041873
Wellington Electricity | 2010 | 2009-08-20 | 0.066348 | 0.0012287
Wellington Electricity | 2010 | 2009-08-21
Wellington Electricity | 2010 | 2009-08-22
Wellington Electricity | 2010 | 2009-08-23 | 0.0093893 | 8.5579e-05
Wellington Electricity | 2010 | 2009-08-24 | 0.010652 | 5.1959e-05
Wellington Electricity | 2010 | 2009-08-25 | 0.16529 | 0.0012592
Wellington Electricity | 2010 | 2009-08-26 | 0.014121 | 0.0003362
Wellington Electricity | 2010 | 2009-08-27 | 0.0075279 | 0.0004554
Wellington Electricity | 2010 | 2009-08-28 | 0.0012898 | 9.1692e-06
Wellington Electricity | 2010 | 2009-08-29 | 0.00036066 | 6.1128e-06
Wellington Electricity | 2010 | 2009-08-30 | 0.76089 | 0.0063757
Wellington Electricity | 2010 | 2009-08-31 | 0.41614 | 0.0074698
Wellington Electricity | 2010 | 2009-09-01
Wellington Electricity | 2010 | 2009-09-02
Wellington Electricity | 2010 | 2009-09-03 | 0.041998 | 0.00022617
Wellington Electricity | 2010 | 2009-09-04
Wellington Electricity | 2010 | 2009-09-05
Wellington Electricity | 2010 | 2009-09-06 | 0.018259 | 0.00017727
Wellington Electricity | 2010 | 2009-09-07
Wellington Electricity | 2010 | 2009-09-08 | 0.064811 | 0.00027813
Wellington Electricity | 2010 | 2009-09-09
Wellington Electricity | 2010 | 2009-09-10 | 0.11849 | 0.00058683
Wellington Electricity | 2010 | 2009-09-11 | 0.014338 | 0.0007152
Wellington Electricity | 2010 | 2009-09-12 | 0.016969 | 0.0042423
Wellington Electricity | 2010 | 2009-09-13 | 0.0061434 | 9.1692e-05
Wellington Electricity | 2010 | 2009-09-14 | 0.00091692 | 9.1692e-06
Wellington Electricity | 2010 | 2009-09-15
Wellington Electricity | 2010 | 2009-09-16 | 0.29456 | 0.0073659
Wellington Electricity | 2010 | 2009-09-17 | 0.0042545 | 0.00014671
Wellington Electricity | 2010 | 2009-09-18 | 0.17576 | 0.0033498
Wellington Electricity | 2010 | 2009-09-19 | 0.32047 | 0.0035699
Wellington Electricity | 2010 | 2009-09-20 | 0.014472 | 0.00019255
Wellington Electricity | 2010 | 2009-09-21 | 0.0081025 | 0.00036982
Wellington Electricity | 2010 | 2009-09-22
Wellington Electricity | 2010 | 2009-09-23 | 0.0014304 | 7.9466e-05
Wellington Electricity | 2010 | 2009-09-24
Wellington Electricity | 2010 | 2009-09-25
Wellington Electricity | 2010 | 2009-09-26 | 0.20563 | 0.0047894
Wellington Electricity | 2010 | 2009-09-27 | 0.02914 | 0.00038816
Wellington Electricity | 2010 | 2009-09-28
Wellington Electricity | 2010 | 2009-09-29 | 0.024965 | 0.00055015
Wellington Electricity | 2010 | 2009-09-30 | 0.015019 | 7.9466e-05
Wellington Electricity | 2010 | 2009-10-01
Wellington Electricity | 2010 | 2009-10-02 | 0.00813 | 0.00028119
Wellington Electricity | 2010 | 2009-10-03
Wellington Electricity | 2010 | 2009-10-04
Wellington Electricity | 2010 | 2009-10-05 | 0.069613 | 0.00044623
Wellington Electricity | 2010 | 2009-10-06
Wellington Electricity | 2010 | 2009-10-07 | 0.009756 | 0.001626
Wellington Electricity | 2010 | 2009-10-08 | 0.039315 | 0.00027202
Wellington Electricity | 2010 | 2009-10-09 | 0.0022312 | 3.0564e-05
Wellington Electricity | 2010 | 2009-10-10 | 2.1026 | 0.012281
Wellington Electricity | 2010 | 2009-10-11 | 0.10096 | 0.0022312
Wellington Electricity | 2010 | 2009-10-12
Wellington Electricity | 2010 | 2009-10-13 | 0.44311 | 0.0059111
Wellington Electricity | 2010 | 2009-10-14
Wellington Electricity | 2010 | 2009-10-15
Wellington Electricity | 2010 | 2009-10-16 | 0.019365 | 0.00014671
Wellington Electricity | 2010 | 2009-10-17 | 0.074378 | 0.0012073
Wellington Electricity | 2010 | 2009-10-18
Wellington Electricity | 2010 | 2009-10-19 | 0.00081912 | 1.2226e-05
Wellington Electricity | 2010 | 2009-10-20
Wellington Electricity | 2010 | 2009-10-21 | 0.00092915 | 6.1128e-06
Wellington Electricity | 2010 | 2009-10-22
Wellington Electricity | 2010 | 2009-10-23 | 0.76249 | 0.011914
Wellington Electricity | 2010 | 2009-10-24
Wellington Electricity | 2010 | 2009-10-25
Wellington Electricity | 2010 | 2009-10-26 | 0.00022006 | 5.5015e-05
Wellington Electricity | 2010 | 2009-10-27 | 0.58436 | 0.0068769
Wellington Electricity | 2010 | 2009-10-28 | 0.043896 | 0.0012929
Wellington Electricity | 2010 | 2009-10-29
Wellington Electricity | 2010 | 2009-10-30
Wellington Electricity | 2010 | 2009-10-31
Wellington Electricity | 2010 | 2009-11-01
Wellington Electricity | 2010 | 2009-11-02 | 0.9108 | 0.0094748
Wellington Electricity | 2010 | 2009-11-03 | 0.050504 | 0.0002873
Wellington Electricity | 2010 | 2009-11-04 | 0.11927 | 0.0042484
Wellington Electricity | 2010 | 2009-11-05 | 0.028828 | 0.00033009
Wellington Electricity | 2010 | 2009-11-06 | 0.0075982 | 6.1128e-06
Wellington Electricity | 2010 | 2009-11-07
Wellington Electricity | 2010 | 2009-11-08
Wellington Electricity | 2010 | 2009-11-09 | 0.00062962 | 5.1959e-05
Wellington Electricity | 2010 | 2009-11-10 | 0.36358 | 0.0079039
Wellington Electricity | 2010 | 2009-11-11 | 0.0012287 | 1.8338e-05
Wellington Electricity | 2010 | 2009-11-12
Wellington Electricity | 2010 | 2009-11-13
Wellington Electricity | 2010 | 2009-11-14 | 0.012079 | 7.9466e-05
Wellington Electricity | 2010 | 2009-11-15 | 1.1238 | 0.018757
Wellington Electricity | 2010 | 2009-11-16 | 0.020209 | 0.0026285
Wellington Electricity | 2010 | 2009-11-17 | 0.0027508 | 0.00018338
Wellington Electricity | 2010 | 2009-11-18 | 0.1299 | 0.0018889
Wellington Electricity | 2010 | 2009-11-19
Wellington Electricity | 2010 | 2009-11-20
Wellington Electricity | 2010 | 2009-11-21 | 0.074014 | 0.004279
Wellington Electricity | 2010 | 2009-11-22
Wellington Electricity | 2010 | 2009-11-23 | 0.22135 | 0.0017513
Wellington Electricity | 2010 | 2009-11-24 | 0.70566 | 0.0072773
Wellington Electricity | 2010 | 2009-11-25
Wellington Electricity | 2010 | 2009-11-26 | 0.0049391 | 0.00059294
Wellington Electricity | 2010 | 2009-11-27
Wellington Electricity | 2010 | 2009-11-28
Wellington Electricity | 2010 | 2009-11-29 | 0.0082706 | 0.00010086
Wellington Electricity | 2010 | 2009-11-30
Wellington Electricity | 2010 | 2009-12-01 | 0.095341 | 0.00063573
Wellington Electricity | 2010 | 2009-12-02
Wellington Electricity | 2010 | 2009-12-03
Wellington Electricity | 2010 | 2009-12-04
Wellington Electricity | 2010 | 2009-12-05
Wellington Electricity | 2010 | 2009-12-06
Wellington Electricity | 2010 | 2009-12-07
Wellington Electricity | 2010 | 2009-12-08
Wellington Electricity | 2010 | 2009-12-09
Wellington Electricity | 2010 | 2009-12-10
Wellington Electricity | 2010 | 2009-12-11 | 0.1439 | 0.0030381
Wellington Electricity | 2010 | 2009-12-12 | 1.119 | 0.013198
Wellington Electricity | 2010 | 2009-12-13 | 0.80766 | 0.0095299
Wellington Electricity | 2010 | 2009-12-14 | 0.041017 | 0.00037288
Wellington Electricity | 2010 | 2009-12-15
Wellington Electricity | 2010 | 2009-12-16
Wellington Electricity | 2010 | 2009-12-17
Wellington Electricity | 2010 | 2009-12-18
Wellington Electricity | 2010 | 2009-12-19
Wellington Electricity | 2010 | 2009-12-20
Wellington Electricity | 2010 | 2009-12-21 | 0.52195 | 0.0092548
Wellington Electricity | 2010 | 2009-12-22
Wellington Electricity | 2010 | 2009-12-23
Wellington Electricity | 2010 | 2009-12-24
Wellington Electricity | 2010 | 2009-12-25
Wellington Electricity | 2010 | 2009-12-26
Wellington Electricity | 2010 | 2009-12-27
Wellington Electricity | 2010 | 2009-12-28
Wellington Electricity | 2010 | 2009-12-29
Wellington Electricity | 2010 | 2009-12-30
Wellington Electricity | 2010 | 2009-12-31
Wellington Electricity | 2010 | 2010-01-01 | 0.0016138 | 6.7241e-05
Wellington Electricity | 2010 | 2010-01-02
Wellington Electricity | 2010 | 2010-01-03 | 0.74485 | 0.0071336
Wellington Electricity | 2010 | 2010-01-04 | 0.024066 | 0.00053793
Wellington Electricity | 2010 | 2010-01-05
Wellington Electricity | 2010 | 2010-01-06 | 0.47605 | 0.005092
Wellington Electricity | 2010 | 2010-01-07 | 0.45366 | 0.0073109
Wellington Electricity | 2010 | 2010-01-08 | 0.0042545 | 2.4451e-05
Wellington Electricity | 2010 | 2010-01-09
Wellington Electricity | 2010 | 2010-01-10 | 0.027214 | 0.00035454
Wellington Electricity | 2010 | 2010-01-11
Wellington Electricity | 2010 | 2010-01-12
Wellington Electricity | 2010 | 2010-01-13 | 0.055737 | 0.00059294
Wellington Electricity | 2010 | 2010-01-14 | 0.068806 | 0.0016382
Wellington Electricity | 2010 | 2010-01-15
Wellington Electricity | 2010 | 2010-01-16 | 2.1026 | 0.0087902
Wellington Electricity | 2010 | 2010-01-17 | 0.14979 | 0.0020661
Wellington Electricity | 2010 | 2010-01-18 | 0.014463 | 7.9466e-05
Wellington Electricity | 2010 | 2010-01-19 | 0.0067669 | 0.0022556
Wellington Electricity | 2010 | 2010-01-20
Wellington Electricity | 2010 | 2010-01-21 | 0.12064 | 0.0036127
Wellington Electricity | 2010 | 2010-01-22 | 0.22348 | 0.0055871
Wellington Electricity | 2010 | 2010-01-23 | 0.10954 | 0.00078244
Wellington Electricity | 2010 | 2010-01-24
Wellington Electricity | 2010 | 2010-01-25 | 0.39813 | 0.004933
Wellington Electricity | 2010 | 2010-01-26
Wellington Electricity | 2010 | 2010-01-27
Wellington Electricity | 2010 | 2010-01-28 | 0.72704 | 0.0074943
Wellington Electricity | 2010 | 2010-01-29
Wellington Electricity | 2010 | 2010-01-30
Wellington Electricity | 2010 | 2010-01-31 | 0.44109 | 0.0082829
Wellington Electricity | 2010 | 2010-02-01
Wellington Electricity | 2010 | 2010-02-02
Wellington Electricity | 2010 | 2010-02-03
Wellington Electricity | 2010 | 2010-02-04
Wellington Electricity | 2010 | 2010-02-05
Wellington Electricity | 2010 | 2010-02-06 | 0.35509 | 0.0036249
Wellington Electricity | 2010 | 2010-02-07
Wellington Electricity | 2010 | 2010-02-08
Wellington Electricity | 2010 | 2010-02-09 | 0.04672 | 0.00070297
Wellington Electricity | 2010 | 2010-02-10 | 0.51513 | 0.009481
Wellington Electricity | 2010 | 2010-02-11 | 0.035283 | 0.00017116
Wellington Electricity | 2010 | 2010-02-12 | 1.1371 | 0.0054832
Wellington Electricity | 2010 | 2010-02-13 | 1.1403 | 0.014475
Wellington Electricity | 2010 | 2010-02-14
Wellington Electricity | 2010 | 2010-02-15 | 0.4294 | 0.007262
Wellington Electricity | 2010 | 2010-02-16
Wellington Electricity | 2010 | 2010-02-17
Wellington Electricity | 2010 | 2010-02-18 | 0.18968 | 0.0015649
Wellington Electricity | 2010 | 2010-02-19
Wellington Electricity | 2010 | 2010-02-20
Wellington Electricity | 2010 | 2010-02-21
Wellington Electricity | 2010 | 2010-02-22 | 0.2642 | 0.0024329
Wellington Electricity | 2010 | 2010-02-23
Wellington Electricity | 2010 | 2010-02-24 | 2.2395 | 0.0053212
Wellington Electricity | 2010 | 2010-02-25 | 0.42772 | 0.0094932
Wellington Electricity | 2010 | 2010-02-26 | 0.013534 | 0.00012531
Wellington Electricity | 2010 | 2010-02-27
Wellington Electricity | 2010 | 2010-02-28
Wellington Electricity | 2010 | 2010-03-01 | 0.00053181 | 9.1692e-06
Wellington Electricity | 2010 | 2010-03-02 | 0.061403 | 0.00053793
Wellington Electricity | 2010 | 2010-03-03
Wellington Electricity | 2010 | 2010-03-04
Wellington Electricity | 2010 | 2010-03-05 | 3.9733e-05 | 3.0564e-06
Wellington Electricity | 2010 | 2010-03-06
Wellington Electricity | 2010 | 2010-03-07 | 0.00029647 | 3.0564e-06
Wellington Electricity | 2010 | 2010-03-08 | 0.032395 | 0.00025368
Wellington Electricity | 2010 | 2010-03-09 | 0.1093 | 0.0073109
Wellington Electricity | 2010 | 2010-03-10 | 0.0078672 | 7.9466e-05
Wellington Electricity | 2010 | 2010-03-11 | 0.42875 | 0.0061739
Wellington Electricity | 2010 | 2010-03-12 | 2.1026 | 0.031245
Wellington Electricity | 2010 | 2010-03-13
Wellington Electricity | 2010 | 2010-03-14 | 0.019402 | 0.00022006
Wellington Electricity | 2010 | 2010-03-15 | 0.0028883 | 4.279e-05
Wellington Electricity | 2010 | 2010-03-16 | 0.0044012 | 0.00044012
Wellington Electricity | 2010 | 2010-03-17 | 0.028632 | 9.1692e-05
Wellington Electricity | 2010 | 2010-03-18 | 0.0032704 | 3.0564e-05
Wellington Electricity | 2010 | 2010-03-19
Wellington Electricity | 2010 | 2010-03-20
Wellington Electricity | 2010 | 2010-03-21 | 0.03925 | 0.00011003
Wellington Electricity | 2010 | 2010-03-22 | 0.079583 | 0.0013968
Wellington Electricity | 2010 | 2010-03-23 | 0.060089 | 0.00035454
Wellington Electricity | 2010 | 2010-03-24 | 0.43626 | 0.0076899
Wellington Electricity | 2010 | 2010-03-25 | 0.11131 | 0.00081912
Wellington Electricity | 2010 | 2010-03-26 | 0.011785 | 0.011785
Wellington Electricity | 2010 | 2010-03-27
Wellington Electricity | 2010 | 2010-03-28 | 0.00022006 | 6.1128e-06
Wellington Electricity | 2010 | 2010-03-29 | 0.075371 | 0.00070909
Wellington Electricity | 2010 | 2010-03-30 | 0.09315 | 0.00082829
Wellington Electricity | 2010 | 2010-03-31 | 0.36075 | 0.010199
Wellington Electricity | 2011 | 2010-04-01
Wellington Electricity | 2011 | 2010-04-02
Wellington Electricity | 2011 | 2010-04-03
Wellington Electricity | 2011 | 2010-04-04
Wellington Electricity | 2011 | 2010-04-05 | 0.011019 | 9.7513e-05
Wellington Electricity | 2011 | 2010-04-06
Wellington Electricity | 2011 | 2010-04-07 | 0.00017979 | 3.0473e-06
Wellington Electricity | 2011 | 2010-04-08 | 0.01119 | 7.3135e-05
Wellington Electricity | 2011 | 2010-04-09 | 0.35113 | 0.001158
Wellington Electricity | 2011 | 2010-04-10
Wellington Electricity | 2011 | 2010-04-11
Wellington Electricity | 2011 | 2010-04-12 | 0.001609 | 3.6567e-05
Wellington Electricity | 2011 | 2010-04-13 | 0.0047659 | 0.00010361
Wellington Electricity | 2011 | 2010-04-14 | 0.30818 | 0.0064816
Wellington Electricity | 2011 | 2010-04-15 | 0.014377 | 0.00026207
Wellington Electricity | 2011 | 2010-04-16 | 0.02706 | 0.0006765
Wellington Electricity | 2011 | 2010-04-17
Wellington Electricity | 2011 | 2010-04-18
Wellington Electricity | 2011 | 2010-04-19 | 0.014237 | 0.00012189
Wellington Electricity | 2011 | 2010-04-20
Wellington Electricity | 2011 | 2010-04-21
Wellington Electricity | 2011 | 2010-04-22
Wellington Electricity | 2011 | 2010-04-23 | 0.00030168 | 3.0473e-06
Wellington Electricity | 2011 | 2010-04-24
Wellington Electricity | 2011 | 2010-04-25
Wellington Electricity | 2011 | 2010-04-26
Wellington Electricity | 2011 | 2010-04-27
Wellington Electricity | 2011 | 2010-04-28
Wellington Electricity | 2011 | 2010-04-29 | 0.00021331 | 3.0473e-06
Wellington Electricity | 2011 | 2010-04-30 | 0.060324 | 0.00059727
Wellington Electricity | 2011 | 2010-05-01
Wellington Electricity | 2011 | 2010-05-02 | 0.027822 | 0.00050585
Wellington Electricity | 2011 | 2010-05-03 | 0.013438 | 0.00029863
Wellington Electricity | 2011 | 2010-05-04 | 0.00048756 | 6.0946e-06
Wellington Electricity | 2011 | 2010-05-05
Wellington Electricity | 2011 | 2010-05-06
Wellington Electricity | 2011 | 2010-05-07 | 0.08625 | 0.0017979
Wellington Electricity | 2011 | 2010-05-08 | 0.05028 | 0.00076182
Wellington Electricity | 2011 | 2010-05-09
Wellington Electricity | 2011 | 2010-05-10
Wellington Electricity | 2011 | 2010-05-11
Wellington Electricity | 2011 | 2010-05-12 | 0.082947 | 0.016589
Wellington Electricity | 2011 | 2010-05-13 | 0.029513 | 0.00028949
Wellington Electricity | 2011 | 2010-05-14 | 0.063926 | 0.0075451
Wellington Electricity | 2011 | 2010-05-15
Wellington Electricity | 2011 | 2010-05-16 | 0.014779 | 0.00013713
Wellington Electricity | 2011 | 2010-05-17 | 0.0049488 | 1.2189e-05
Wellington Electricity | 2011 | 2010-05-18 | 0.44732 | 0.0052901
Wellington Electricity | 2011 | 2010-05-19
Wellington Electricity | 2011 | 2010-05-20
Wellington Electricity | 2011 | 2010-05-21 | 0.012738 | 0.0001158
Wellington Electricity | 2011 | 2010-05-22
Wellington Electricity | 2011 | 2010-05-23
Wellington Electricity | 2011 | 2010-05-24 | 0.17552 | 0.0015846
Wellington Electricity | 2011 | 2010-05-25 | 0.027334 | 9.1418e-05
Wellington Electricity | 2011 | 2010-05-26
Wellington Electricity | 2011 | 2010-05-27
Wellington Electricity | 2011 | 2010-05-28
Wellington Electricity | 2011 | 2010-05-29
Wellington Electricity | 2011 | 2010-05-30 | 0.032325 | 0.00041443
Wellington Electricity | 2011 | 2010-05-31 | 0.0020051 | 6.0946e-06
Wellington Electricity | 2011 | 2010-06-01
Wellington Electricity | 2011 | 2010-06-02
Wellington Electricity | 2011 | 2010-06-03
Wellington Electricity | 2011 | 2010-06-04 | 0.02706 | 0.0017065
Wellington Electricity | 2011 | 2010-06-05
Wellington Electricity | 2011 | 2010-06-06
Wellington Electricity | 2011 | 2010-06-07 | 0.0074232 | 8.5324e-05
Wellington Electricity | 2011 | 2010-06-08
Wellington Electricity | 2011 | 2010-06-09 | 1.0908 | 0.010391
Wellington Electricity | 2011 | 2010-06-10 | 0.47331 | 0.010093
Wellington Electricity | 2011 | 2010-06-11
Wellington Electricity | 2011 | 2010-06-12
Wellington Electricity | 2011 | 2010-06-13
Wellington Electricity | 2011 | 2010-06-14 | 0.0021544 | 0.0001676
Wellington Electricity | 2011 | 2010-06-15
Wellington Electricity | 2011 | 2010-06-16
Wellington Electricity | 2011 | 2010-06-17 | 0.0016699 | 0.00021026
Wellington Electricity | 2011 | 2010-06-18 | 0.00063993 | 6.0946e-06
Wellington Electricity | 2011 | 2010-06-19
Wellington Electricity | 2011 | 2010-06-20 | 0.0062286 | 1.2189e-05
Wellington Electricity | 2011 | 2010-06-21
Wellington Electricity | 2011 | 2010-06-22 | 0.022696 | 0.00046319
Wellington Electricity | 2011 | 2010-06-23
Wellington Electricity | 2011 | 2010-06-24 | 0.44532 | 0.0029924
Wellington Electricity | 2011 | 2010-06-25
Wellington Electricity | 2011 | 2010-06-26
Wellington Electricity | 2011 | 2010-06-27
Wellington Electricity | 2011 | 2010-06-28
Wellington Electricity | 2011 | 2010-06-29 | 0.0038274 | 2.4378e-05
Wellington Electricity | 2011 | 2010-06-30
Wellington Electricity | 2011 | 2010-07-01 | 0.11095 | 0.002706
Wellington Electricity | 2011 | 2010-07-02 | 0.40045 | 0.0079168
Wellington Electricity | 2011 | 2010-07-03
Wellington Electricity | 2011 | 2010-07-04
Wellington Electricity | 2011 | 2010-07-05
Wellington Electricity | 2011 | 2010-07-06 | 0.00099951 | 6.0946e-06
Wellington Electricity | 2011 | 2010-07-07 | 0.0048513 | 2.4378e-05
Wellington Electricity | 2011 | 2010-07-08 | 0.46694 | 0.027429
Wellington Electricity | 2011 | 2010-07-09 | 0.057362 | 0.00055156
Wellington Electricity | 2011 | 2010-07-10
Wellington Electricity | 2011 | 2010-07-11
Wellington Electricity | 2011 | 2010-07-12
Wellington Electricity | 2011 | 2010-07-13 | 0.037027 | 0.0007283
Wellington Electricity | 2011 | 2010-07-14
Wellington Electricity | 2011 | 2010-07-15
Wellington Electricity | 2011 | 2010-07-16
Wellington Electricity | 2011 | 2010-07-17 | 0.010824 | 0.0002255
Wellington Electricity | 2011 | 2010-07-18 | 0.011665 | 6.704e-05
Wellington Electricity | 2011 | 2010-07-19
Wellington Electricity | 2011 | 2010-07-20 | 0.10692 | 0.0014139
Wellington Electricity | 2011 | 2010-07-21
Wellington Electricity | 2011 | 2010-07-22
Wellington Electricity | 2011 | 2010-07-23 | 0.29084 | 0.031245
Wellington Electricity | 2011 | 2010-07-24 | 0.35921 | 0.0049549
Wellington Electricity | 2011 | 2010-07-25
Wellington Electricity | 2011 | 2010-07-26 | 0.0013896 | 2.4378e-05
Wellington Electricity | 2011 | 2010-07-27
Wellington Electricity | 2011 | 2010-07-28 | 0.13715 | 0.00059117
Wellington Electricity | 2011 | 2010-07-29 | 0.54894 | 0.0095684
Wellington Electricity | 2011 | 2010-07-30
Wellington Electricity | 2011 | 2010-07-31
Wellington Electricity | 2011 | 2010-08-01 | 1.3182 | 0.0095319
Wellington Electricity | 2011 | 2010-08-02 | 0.54647 | 0.0087335
Wellington Electricity | 2011 | 2010-08-03
Wellington Electricity | 2011 | 2010-08-04 | 0.47988 | 0.0051743
Wellington Electricity | 2011 | 2010-08-05 | 0.25046 | 0.0028644
Wellington Electricity | 2011 | 2010-08-06
Wellington Electricity | 2011 | 2010-08-07
Wellington Electricity | 2011 | 2010-08-08
Wellington Electricity | 2011 | 2010-08-09 | 0.0245 | 0.00036567
Wellington Electricity | 2011 | 2010-08-10 | 0.035976 | 0.00039615
Wellington Electricity | 2011 | 2010-08-11
Wellington Electricity | 2011 | 2010-08-12
Wellington Electricity | 2011 | 2010-08-13
Wellington Electricity | 2011 | 2010-08-14
Wellington Electricity | 2011 | 2010-08-15 | 0.28519 | 0.0033947
Wellington Electricity | 2011 | 2010-08-16 | 0.043539 | 0.0011458
Wellington Electricity | 2011 | 2010-08-17
Wellington Electricity | 2011 | 2010-08-18 | 0.0021575 | 0.00035958
Wellington Electricity | 2011 | 2010-08-19
Wellington Electricity | 2011 | 2010-08-20 | 0.47294 | 0.011823
Wellington Electricity | 2011 | 2010-08-21
Wellington Electricity | 2011 | 2010-08-22
Wellington Electricity | 2011 | 2010-08-23 | 0.0064846 | 8.5324e-05
Wellington Electricity | 2011 | 2010-08-24
Wellington Electricity | 2011 | 2010-08-25 | 0.0074597 | 6.704e-05
Wellington Electricity | 2011 | 2010-08-26 | 0.014919 | 0.00014627
Wellington Electricity | 2011 | 2010-08-27
Wellington Electricity | 2011 | 2010-08-28 | 0.16516 | 0.0012677
Wellington Electricity | 2011 | 2010-08-29 | 0.039858 | 0.00018284
Wellington Electricity | 2011 | 2010-08-30 | 0.24393 | 0.0049579
Wellington Electricity | 2011 | 2010-08-31
Wellington Electricity | 2011 | 2010-09-01
Wellington Electricity | 2011 | 2010-09-02 | 0.0012433 | 6.0946e-06
Wellington Electricity | 2011 | 2010-09-03 | 0.016114 | 0.00041443
Wellington Electricity | 2011 | 2010-09-04
Wellington Electricity | 2011 | 2010-09-05
Wellington Electricity | 2011 | 2010-09-06 | 0.075743 | 0.00092637
Wellington Electricity | 2011 | 2010-09-07 | 0.054534 | 0.00030168
Wellington Electricity | 2011 | 2010-09-08
Wellington Electricity | 2011 | 2010-09-09
Wellington Electricity | 2011 | 2010-09-10
Wellington Electricity | 2011 | 2010-09-11
Wellington Electricity | 2011 | 2010-09-12
Wellington Electricity | 2011 | 2010-09-13 | 0.28694 | 0.0063444
Wellington Electricity | 2011 | 2010-09-14
Wellington Electricity | 2011 | 2010-09-15 | 0.16483 | 0.011756
Wellington Electricity | 2011 | 2010-09-16 | 0.0036445 | 0.00018893
Wellington Electricity | 2011 | 2010-09-17 | 1.4445 | 0.022471
Wellington Electricity | 2011 | 2010-09-18 | 0.52978 | 0.01442
Wellington Electricity | 2011 | 2010-09-19 | 0.40272 | 0.0076426
Wellington Electricity | 2011 | 2010-09-20 | 0.00054851 | 6.0946e-06
Wellington Electricity | 2011 | 2010-09-21
Wellington Electricity | 2011 | 2010-09-22 | 0.001292 | 3.0473e-06
Wellington Electricity | 2011 | 2010-09-23 | 0.32482 | 0.005546
Wellington Electricity | 2011 | 2010-09-24 | 0.058593 | 0.00077401
Wellington Electricity | 2011 | 2010-09-25
Wellington Electricity | 2011 | 2010-09-26
Wellington Electricity | 2011 | 2010-09-27
Wellington Electricity | 2011 | 2010-09-28 | 0.0056771 | 8.2276e-05
Wellington Electricity | 2011 | 2010-09-29 | 0.11062 | 0.0022123
Wellington Electricity | 2011 | 2010-09-30
Wellington Electricity | 2011 | 2010-10-01 | 0.11011 | 0.0018162
Wellington Electricity | 2011 | 2010-10-02
Wellington Electricity | 2011 | 2010-10-03
Wellington Electricity | 2011 | 2010-10-04
Wellington Electricity | 2011 | 2010-10-05 | 0.0016699 | 1.2189e-05
Wellington Electricity | 2011 | 2010-10-06
Wellington Electricity | 2011 | 2010-10-07
Wellington Electricity | 2011 | 2010-10-08
Wellington Electricity | 2011 | 2010-10-09 | 0.082136 | 0.00093856
Wellington Electricity | 2011 | 2010-10-10
Wellington Electricity | 2011 | 2010-10-11 | 0.16229 | 0.0021818
Wellington Electricity | 2011 | 2010-10-12
Wellington Electricity | 2011 | 2010-10-13
Wellington Electricity | 2011 | 2010-10-14
Wellington Electricity | 2011 | 2010-10-15
Wellington Electricity | 2011 | 2010-10-16 | 0.0083495 | 6.0946e-05
Wellington Electricity | 2011 | 2010-10-17
Wellington Electricity | 2011 | 2010-10-18
Wellington Electricity | 2011 | 2010-10-19 | 0.082465 | 0.000451
Wellington Electricity | 2011 | 2010-10-20
Wellington Electricity | 2011 | 2010-10-21 | 0.45579 | 0.0063018
Wellington Electricity | 2011 | 2010-10-22
Wellington Electricity | 2011 | 2010-10-23 | 0.0048635 | 0.00069478
Wellington Electricity | 2011 | 2010-10-24 | 0.0015114 | 1.2189e-05
Wellington Electricity | 2011 | 2010-10-25
Wellington Electricity | 2011 | 2010-10-26 | 0.086518 | 0.0066552
Wellington Electricity | 2011 | 2010-10-27 | 0.19734 | 0.0051926
Wellington Electricity | 2011 | 2010-10-28 | 0.20234 | 0.0071428
Wellington Electricity | 2011 | 2010-10-29
Wellington Electricity | 2011 | 2010-10-30 | 0.094344 | 0.00036567
Wellington Electricity | 2011 | 2010-10-31 | 0.0017735 | 3.0473e-06
Wellington Electricity | 2011 | 2010-11-01
Wellington Electricity | 2011 | 2010-11-02
Wellington Electricity | 2011 | 2010-11-03
Wellington Electricity | 2011 | 2010-11-04
Wellington Electricity | 2011 | 2010-11-05 | 0.22105 | 0.0034008
Wellington Electricity | 2011 | 2010-11-06 | 0.00058508 | 6.0946e-06
Wellington Electricity | 2011 | 2010-11-07 | 0.032581 | 0.00032911
Wellington Electricity | 2011 | 2010-11-08
Wellington Electricity | 2011 | 2010-11-09
Wellington Electricity | 2011 | 2010-11-10 | 0.013347 | 0.0008898
Wellington Electricity | 2011 | 2010-11-11
Wellington Electricity | 2011 | 2010-11-12 | 0.075426 | 0.00034129
Wellington Electricity | 2011 | 2010-11-13 | 2.1026 | 0.029284
Wellington Electricity | 2011 | 2010-11-14 | 0.021307 | 0.00046319
Wellington Electricity | 2011 | 2010-11-15
Wellington Electricity | 2011 | 2010-11-16 | 0.65391 | 0.01225
Wellington Electricity | 2011 | 2010-11-17 | 0.0024561 | 6.0946e-06
Wellington Electricity | 2011 | 2010-11-18 | 0.021121 | 8.8371e-05
Wellington Electricity | 2011 | 2010-11-19
Wellington Electricity | 2011 | 2010-11-20
Wellington Electricity | 2011 | 2010-11-21 | 0.56478 | 0.012079
Wellington Electricity | 2011 | 2010-11-22
Wellington Electricity | 2011 | 2010-11-23 | 0.089474 | 0.0013286
Wellington Electricity | 2011 | 2010-11-24
Wellington Electricity | 2011 | 2010-11-25
Wellington Electricity | 2011 | 2010-11-26 | 0.0024744 | 8.5324e-05
Wellington Electricity | 2011 | 2010-11-27 | 0.018704 | 0.00056679
Wellington Electricity | 2011 | 2010-11-28 | 0.3773 | 0.0092759
Wellington Electricity | 2011 | 2010-11-29
Wellington Electricity | 2011 | 2010-11-30
Wellington Electricity | 2011 | 2010-12-01
Wellington Electricity | 2011 | 2010-12-02
Wellington Electricity | 2011 | 2010-12-03
Wellington Electricity | 2011 | 2010-12-04 | 0.19011 | 0.00065821
Wellington Electricity | 2011 | 2010-12-05 | 0.025451 | 0.00019503
Wellington Electricity | 2011 | 2010-12-06 | 0.0018406 | 1.2189e-05
Wellington Electricity | 2011 | 2010-12-07 | 0.073555 | 0.00090809
Wellington Electricity | 2011 | 2010-12-08 | 0.15288 | 0.001999
Wellington Electricity | 2011 | 2010-12-09
Wellington Electricity | 2011 | 2010-12-10
Wellington Electricity | 2011 | 2010-12-11 | 0.0062957 | 0.00028644
Wellington Electricity | 2011 | 2010-12-12
Wellington Electricity | 2011 | 2010-12-13 | 0.071471 | 0.00069478
Wellington Electricity | 2011 | 2010-12-14
Wellington Electricity | 2011 | 2010-12-15
Wellington Electricity | 2011 | 2010-12-16
Wellington Electricity | 2011 | 2010-12-17 | 0.062859 | 0.00043881
Wellington Electricity | 2011 | 2010-12-18 | 0.10541 | 0.0022428
Wellington Electricity | 2011 | 2010-12-19
Wellington Electricity | 2011 | 2010-12-20
Wellington Electricity | 2011 | 2010-12-21 | 0.87167 | 0.010373
Wellington Electricity | 2011 | 2010-12-22
Wellington Electricity | 2011 | 2010-12-23
Wellington Electricity | 2011 | 2010-12-24 | 0.25242 | 0.0017065
Wellington Electricity | 2011 | 2010-12-25
Wellington Electricity | 2011 | 2010-12-26
Wellington Electricity | 2011 | 2010-12-27
Wellington Electricity | 2011 | 2010-12-28 | 2.1026 | 0.021697
Wellington Electricity | 2011 | 2010-12-29 | 0.0031082 | 6.0946e-05
Wellington Electricity | 2011 | 2010-12-30
Wellington Electricity | 2011 | 2010-12-31
Wellington Electricity | 2011 | 2011-01-01
Wellington Electricity | 2011 | 2011-01-02
Wellington Electricity | 2011 | 2011-01-03 | 0.0050463 | 7.3135e-05
Wellington Electricity | 2011 | 2011-01-04
Wellington Electricity | 2011 | 2011-01-05
Wellington Electricity | 2011 | 2011-01-06 | 0.50128 | 0.0053693
Wellington Electricity | 2011 | 2011-01-07 | 0.0019624 | 8.5324e-05
Wellington Electricity | 2011 | 2011-01-08
Wellington Electricity | 2011 | 2011-01-09 | 0.012853 | 0.00026816
Wellington Electricity | 2011 | 2011-01-10 | 0.0036263 | 6.0946e-06
Wellington Electricity | 2011 | 2011-01-11 | 0.0032911 | 5.4851e-05
Wellington Electricity | 2011 | 2011-01-12 | 0.0015602 | 3.0473e-06
Wellington Electricity | 2011 | 2011-01-13 | 0.00075268 | 3.0473e-06
Wellington Electricity | 2011 | 2011-01-14 | 0.18411 | 0.0044673
Wellington Electricity | 2011 | 2011-01-15
Wellington Electricity | 2011 | 2011-01-16
Wellington Electricity | 2011 | 2011-01-17 | 0.0091235 | 9.7513e-05
Wellington Electricity | 2011 | 2011-01-18
Wellington Electricity | 2011 | 2011-01-19 | 0.24993 | 0.0027852
Wellington Electricity | 2011 | 2011-01-20
Wellington Electricity | 2011 | 2011-01-21
Wellington Electricity | 2011 | 2011-01-22
Wellington Electricity | 2011 | 2011-01-23
Wellington Electricity | 2011 | 2011-01-24 | 0.0033215 | 3.0473e-05
Wellington Electricity | 2011 | 2011-01-25
Wellington Electricity | 2011 | 2011-01-26
Wellington Electricity | 2011 | 2011-01-27 | 0.053029 | 0.00048756
Wellington Electricity | 2011 | 2011-01-28 | 0.00083191 | 3.0473e-06
Wellington Electricity | 2011 | 2011-01-29 | 0.088956 | 0.00091418
Wellington Electricity | 2011 | 2011-01-30
Wellington Electricity | 2011 | 2011-01-31 | 0.30775 | 0.0042967
Wellington Electricity | 2011 | 2011-02-01 | 0.025256 | 0.00010056
Wellington Electricity | 2011 | 2011-02-02
Wellington Electricity | 2011 | 2011-02-03 | 0.13134 | 0.0018954
Wellington Electricity | 2011 | 2011-02-04 | 0.081685 | 0.0019624
Wellington Electricity | 2011 | 2011-02-05 | 0.070654 | 0.00090809
Wellington Electricity | 2011 | 2011-02-06
Wellington Electricity | 2011 | 2011-02-07 | 0.37795 | 0.010068
Wellington Electricity | 2011 | 2011-02-08 | 0.24197 | 0.00093551
Wellington Electricity | 2011 | 2011-02-09
Wellington Electricity | 2011 | 2011-02-10
Wellington Electricity | 2011 | 2011-02-11
Wellington Electricity | 2011 | 2011-02-12
Wellington Electricity | 2011 | 2011-02-13
Wellington Electricity | 2011 | 2011-02-14 | 0.029522 | 0.00070087
Wellington Electricity | 2011 | 2011-02-15
Wellington Electricity | 2011 | 2011-02-16 | 0.0028218 | 1.8284e-05
Wellington Electricity | 2011 | 2011-02-17 | 0.25536 | 0.0016943
Wellington Electricity | 2011 | 2011-02-18
Wellington Electricity | 2011 | 2011-02-19
Wellington Electricity | 2011 | 2011-02-20
Wellington Electricity | 2011 | 2011-02-21 | 0.14351 | 0.0049488
Wellington Electricity | 2011 | 2011-02-22 | 0.0037725 | 6.0946e-06
Wellington Electricity | 2011 | 2011-02-23 | 0.0061067 | 3.6567e-05
Wellington Electricity | 2011 | 2011-02-24
Wellington Electricity | 2011 | 2011-02-25
Wellington Electricity | 2011 | 2011-02-26
Wellington Electricity | 2011 | 2011-02-27
Wellington Electricity | 2011 | 2011-02-28 | 0.49482 | 0.004577
Wellington Electricity | 2011 | 2011-03-01
Wellington Electricity | 2011 | 2011-03-02 | 0.35903 | 0.0044399
Wellington Electricity | 2011 | 2011-03-03 | 0.4894 | 0.0097574
Wellington Electricity | 2011 | 2011-03-04 | 0.5179 | 0.010318
Wellington Electricity | 2011 | 2011-03-05
Wellington Electricity | 2011 | 2011-03-06 | 0.025079 | 6.0946e-06
Wellington Electricity | 2011 | 2011-03-07
Wellington Electricity | 2011 | 2011-03-08 | 0.4012 | 0.0069173
Wellington Electricity | 2011 | 2011-03-09
Wellington Electricity | 2011 | 2011-03-10
Wellington Electricity | 2011 | 2011-03-11
Wellington Electricity | 2011 | 2011-03-12
Wellington Electricity | 2011 | 2011-03-13 | 0.0042418 | 4.8756e-05
Wellington Electricity | 2011 | 2011-03-14
Wellington Electricity | 2011 | 2011-03-15
Wellington Electricity | 2011 | 2011-03-16 | 0.0083191 | 9.1418e-05
Wellington Electricity | 2011 | 2011-03-17 | 0.69118 | 0.0095867
Wellington Electricity | 2011 | 2011-03-18 | 0.0011305 | 3.0473e-06
Wellington Electricity | 2011 | 2011-03-19
Wellington Electricity | 2011 | 2011-03-20
Wellington Electricity | 2011 | 2011-03-21
Wellington Electricity | 2011 | 2011-03-22
Wellington Electricity | 2011 | 2011-03-23
Wellington Electricity | 2011 | 2011-03-24 | 0.30973 | 0.0044246
Wellington Electricity | 2011 | 2011-03-25
Wellington Electricity | 2011 | 2011-03-26
Wellington Electricity | 2011 | 2011-03-27
Wellington Electricity | 2011 | 2011-03-28 | 0.00013408 | 0.00013408
Wellington Electricity | 2011 | 2011-03-29
Wellington Electricity | 2011 | 2011-03-30
Wellington Electricity | 2011 | 2011-03-31 | 0.025902 | 6.0946e-05
Wellington Electricity | 2012 | 2011-04-01 | 0.13251 | 0.00099634
Wellington Electricity | 2012 | 2011-04-02 | 0.1838 | 0.0028766
Wellington Electricity | 2012 | 2011-04-03
Wellington Electricity | 2012 | 2011-04-04 | 0.089969 | 0.0011361
Wellington Electricity | 2012 | 2011-04-05
Wellington Electricity | 2012 | 2011-04-06
Wellington Electricity | 2012 | 2011-04-07
Wellington Electricity | 2012 | 2011-04-08 | 0.39626 | 0.0012272
Wellington Electricity | 2012 | 2011-04-09
Wellington Electricity | 2012 | 2011-04-10
Wellington Electricity | 2012 | 2011-04-11
Wellington Electricity | 2012 | 2011-04-12 | 0.00028554 | 6.0753e-06
Wellington Electricity | 2012 | 2011-04-13
Wellington Electricity | 2012 | 2011-04-14
Wellington Electricity | 2012 | 2011-04-15 | 0.24574 | 0.0022478
Wellington Electricity | 2012 | 2011-04-16 | 0.08879 | 0.0011239
Wellington Electricity | 2012 | 2011-04-17
Wellington Electricity | 2012 | 2011-04-18 | 0.052101 | 0.0014095
Wellington Electricity | 2012 | 2011-04-19 | 0.00042527 | 1.2151e-05
Wellington Electricity | 2012 | 2011-04-20
Wellington Electricity | 2012 | 2011-04-21
Wellington Electricity | 2012 | 2011-04-22
Wellington Electricity | 2012 | 2011-04-23
Wellington Electricity | 2012 | 2011-04-24
Wellington Electricity | 2012 | 2011-04-25
Wellington Electricity | 2012 | 2011-04-26 | 0.019009 | 1.8226e-05
Wellington Electricity | 2012 | 2011-04-27 | 0.81479 | 0.0092769
Wellington Electricity | 2012 | 2011-04-28 | 0.0043742 | 2.4301e-05
Wellington Electricity | 2012 | 2011-04-29
Wellington Electricity | 2012 | 2011-04-30 | 0.19561 | 0.0018287
Wellington Electricity | 2012 | 2011-05-01
Wellington Electricity | 2012 | 2011-05-02 | 0.23327 | 0.0051154
Wellington Electricity | 2012 | 2011-05-03 | 0.0064793 | 8.2016e-05
Wellington Electricity | 2012 | 2011-05-04 | 0.0048663 | 3.0376e-05
Wellington Electricity | 2012 | 2011-05-05
Wellington Electricity | 2012 | 2011-05-06 | 0.00074726 | 6.0753e-06
Wellington Electricity | 2012 | 2011-05-07
Wellington Electricity | 2012 | 2011-05-08
Wellington Electricity | 2012 | 2011-05-09
Wellington Electricity | 2012 | 2011-05-10 | 0.07006 | 0.00075333
Wellington Electricity | 2012 | 2011-05-11
Wellington Electricity | 2012 | 2011-05-12
Wellington Electricity | 2012 | 2011-05-13
Wellington Electricity | 2012 | 2011-05-14
Wellington Electricity | 2012 | 2011-05-15 | 0.19348 | 0.0017861
Wellington Electricity | 2012 | 2011-05-16
Wellington Electricity | 2012 | 2011-05-17 | 0.1557 | 0.0039884
Wellington Electricity | 2012 | 2011-05-18
Wellington Electricity | 2012 | 2011-05-19
Wellington Electricity | 2012 | 2011-05-20
Wellington Electricity | 2012 | 2011-05-21 | 0.0014216 | 1.2151e-05
Wellington Electricity | 2012 | 2011-05-22
Wellington Electricity | 2012 | 2011-05-23 | 0.14484 | 0.0053645
Wellington Electricity | 2012 | 2011-05-24
Wellington Electricity | 2012 | 2011-05-25 | 0.0040978 | 5.7715e-05
Wellington Electricity | 2012 | 2011-05-26 | 0.0072903 | 0.00014581
Wellington Electricity | 2012 | 2011-05-27 | 0.0094774 | 6.0753e-05
Wellington Electricity | 2012 | 2011-05-28 | 0.0010328 | 3.0376e-06
Wellington Electricity | 2012 | 2011-05-29
Wellington Electricity | 2012 | 2011-05-30
Wellington Electricity | 2012 | 2011-05-31
Wellington Electricity | 2012 | 2011-06-01 | 0.013098 | 0.00013366
Wellington Electricity | 2012 | 2011-06-02 | 0.040704 | 0.00081408
Wellington Electricity | 2012 | 2011-06-03 | 0.22998 | 0.0037575
Wellington Electricity | 2012 | 2011-06-04
Wellington Electricity | 2012 | 2011-06-05 | 0.054847 | 0.00022478
Wellington Electricity | 2012 | 2011-06-06 | 0.57921 | 0.007995
Wellington Electricity | 2012 | 2011-06-07 | 0.0099422 | 0.00010632
Wellington Electricity | 2012 | 2011-06-08 | 0.0036816 | 5.164e-05
Wellington Electricity | 2012 | 2011-06-09 | 0.012788 | 3.0376e-05
Wellington Electricity | 2012 | 2011-06-10 | 0.016099 | 0.00030376
Wellington Electricity | 2012 | 2011-06-11
Wellington Electricity | 2012 | 2011-06-12 | 0.032278 | 0.00023694
Wellington Electricity | 2012 | 2011-06-13
Wellington Electricity | 2012 | 2011-06-14
Wellington Electricity | 2012 | 2011-06-15
Wellington Electricity | 2012 | 2011-06-16
Wellington Electricity | 2012 | 2011-06-17
Wellington Electricity | 2012 | 2011-06-18 | 0.11548 | 0.016634
Wellington Electricity | 2012 | 2011-06-19 | 1.4168 | 0.031245
Wellington Electricity | 2012 | 2011-06-20
Wellington Electricity | 2012 | 2011-06-21 | 0.0012211 | 3.0376e-06
Wellington Electricity | 2012 | 2011-06-22 | 0.059477 | 0.00091129
Wellington Electricity | 2012 | 2011-06-23 | 0.0027339 | 0.00030376
Wellington Electricity | 2012 | 2011-06-24 | 0.00096597 | 6.0753e-06
Wellington Electricity | 2012 | 2011-06-25
Wellington Electricity | 2012 | 2011-06-26
Wellington Electricity | 2012 | 2011-06-27
Wellington Electricity | 2012 | 2011-06-28
Wellington Electricity | 2012 | 2011-06-29 | 0.35963 | 0.0032503
Wellington Electricity | 2012 | 2011-06-30 | 0.33678 | 0.0039914
Wellington Electricity | 2012 | 2011-07-01 | 0.00036452 | 3.0376e-06
Wellington Electricity | 2012 | 2011-07-02 | 0.032946 | 0.00017618
Wellington Electricity | 2012 | 2011-07-03
Wellington Electricity | 2012 | 2011-07-04 | 0.023785 | 0.00026427
Wellington Electricity | 2012 | 2011-07-05 | 0.060473 | 0.00054981
Wellington Electricity | 2012 | 2011-07-06 | 0.00046172 | 6.0753e-06
Wellington Electricity | 2012 | 2011-07-07 | 0.42602 | 0.0046233
Wellington Electricity | 2012 | 2011-07-08 | 0.014301 | 0.00012151
Wellington Electricity | 2012 | 2011-07-09 | 0.39839 | 0.0027764
Wellington Electricity | 2012 | 2011-07-10 | 0.018955 | 7.8978e-05
Wellington Electricity | 2012 | 2011-07-11 | 1.383 | 0.016573
Wellington Electricity | 2012 | 2011-07-12
Wellington Electricity | 2012 | 2011-07-13 | 0.043238 | 0.0005164
Wellington Electricity | 2012 | 2011-07-14
Wellington Electricity | 2012 | 2011-07-15 | 0.22868 | 0.0019532
Wellington Electricity | 2012 | 2011-07-16 | 0.063869 | 0.00014581
Wellington Electricity | 2012 | 2011-07-17
Wellington Electricity | 2012 | 2011-07-18 | 0.12582 | 0.012582
Wellington Electricity | 2012 | 2011-07-19
Wellington Electricity | 2012 | 2011-07-20
Wellington Electricity | 2012 | 2011-07-21 | 0.088626 | 0.0013274
Wellington Electricity | 2012 | 2011-07-22 | 0.021871 | 0.00021871
Wellington Electricity | 2012 | 2011-07-23
Wellington Electricity | 2012 | 2011-07-24 | 1.2102 | 0.021859
Wellington Electricity | 2012 | 2011-07-25 | 0.014471 | 3.6452e-05
Wellington Electricity | 2012 | 2011-07-26 | 0.46134 | 0.016677
Wellington Electricity | 2012 | 2011-07-27 | 0.0030073 | 9.1129e-06
Wellington Electricity | 2012 | 2011-07-28 | 0.083632 | 0.00047083
Wellington Electricity | 2012 | 2011-07-29 | 0.011163 | 7.5941e-05
Wellington Electricity | 2012 | 2011-07-30
Wellington Electricity | 2012 | 2011-07-31
Wellington Electricity | 2012 | 2011-08-01
Wellington Electricity | 2012 | 2011-08-02 | 0.00027946 | 1.8226e-05
Wellington Electricity | 2012 | 2011-08-03 | 0.0010267 | 6.0753e-06
Wellington Electricity | 2012 | 2011-08-04 | 0.0041464 | 2.1263e-05
Wellington Electricity | 2012 | 2011-08-05
Wellington Electricity | 2012 | 2011-08-06
Wellington Electricity | 2012 | 2011-08-07
Wellington Electricity | 2012 | 2011-08-08 | 0.00075333 | 3.0376e-06
Wellington Electricity | 2012 | 2011-08-09 | 1.0297 | 0.02435
Wellington Electricity | 2012 | 2011-08-10
Wellington Electricity | 2012 | 2011-08-11
Wellington Electricity | 2012 | 2011-08-12 | 3.9489e-05 | 3.0376e-06
Wellington Electricity | 2012 | 2011-08-13
Wellington Electricity | 2012 | 2011-08-14 | 2.1037 | 0.031254
Wellington Electricity | 2012 | 2011-08-15 | 2.1026 | 0.0074847
Wellington Electricity | 2012 | 2011-08-16 | 1.4742 | 0.0095625
Wellington Electricity | 2012 | 2011-08-17 | 0.077642 | 0.00098419
Wellington Electricity | 2012 | 2011-08-18
Wellington Electricity | 2012 | 2011-08-19 | 1.4064 | 0.0093255
Wellington Electricity | 2012 | 2011-08-20 | 0.26289 | 0.0059477
Wellington Electricity | 2012 | 2011-08-21 | 0.00057107 | 3.0376e-06
Wellington Electricity | 2012 | 2011-08-22 | 0.0031591 | 3.0376e-05
Wellington Electricity | 2012 | 2011-08-23 | 0.023912 | 9.7204e-05
Wellington Electricity | 2012 | 2011-08-24
Wellington Electricity | 2012 | 2011-08-25 | 0.0014581 | 1.2151e-05
Wellington Electricity | 2012 | 2011-08-26 | 0.0020413 | 6.0753e-06
Wellington Electricity | 2012 | 2011-08-27
Wellington Electricity | 2012 | 2011-08-28
Wellington Electricity | 2012 | 2011-08-29 | 0.0011847 | 0.00039489
Wellington Electricity | 2012 | 2011-08-30
Wellington Electricity | 2012 | 2011-08-31
Wellington Electricity | 2012 | 2011-09-01
Wellington Electricity | 2012 | 2011-09-02 | 0.0052551 | 0.00040097
Wellington Electricity | 2012 | 2011-09-03
Wellington Electricity | 2012 | 2011-09-04 | 0.49926 | 0.008882
Wellington Electricity | 2012 | 2011-09-05 | 0.00061968 | 3.0376e-06
Wellington Electricity | 2012 | 2011-09-06 | 0.0017922 | 2.4301e-05
Wellington Electricity | 2012 | 2011-09-07 | 0.13238 | 0.00082016
Wellington Electricity | 2012 | 2011-09-08
Wellington Electricity | 2012 | 2011-09-09 | 0.26803 | 0.002661
Wellington Electricity | 2012 | 2011-09-10
Wellington Electricity | 2012 | 2011-09-11
Wellington Electricity | 2012 | 2011-09-12
Wellington Electricity | 2012 | 2011-09-13 | 0.66753 | 0.011476
Wellington Electricity | 2012 | 2011-09-14 | 0.035297 | 0.0035297
Wellington Electricity | 2012 | 2011-09-15
Wellington Electricity | 2012 | 2011-09-16
Wellington Electricity | 2012 | 2011-09-17
Wellington Electricity | 2012 | 2011-09-18
Wellington Electricity | 2012 | 2011-09-19
Wellington Electricity | 2012 | 2011-09-20 | 0.051716 | 0.0011999
Wellington Electricity | 2012 | 2011-09-21
Wellington Electricity | 2012 | 2011-09-22 | 0.0050546 | 0.00063183
Wellington Electricity | 2012 | 2011-09-23
Wellington Electricity | 2012 | 2011-09-24 | 0.25031 | 0.003469
Wellington Electricity | 2012 | 2011-09-25
Wellington Electricity | 2012 | 2011-09-26
Wellington Electricity | 2012 | 2011-09-27
Wellington Electricity | 2012 | 2011-09-28
Wellington Electricity | 2012 | 2011-09-29
Wellington Electricity | 2012 | 2011-09-30 | 0.055892 | 0.00091736
Wellington Electricity | 2012 | 2011-10-01 | 0.15553 | 0.00077763
Wellington Electricity | 2012 | 2011-10-02
Wellington Electricity | 2012 | 2011-10-03 | 0.19835 | 0.0017618
Wellington Electricity | 2012 | 2011-10-04
Wellington Electricity | 2012 | 2011-10-05 | 0.015036 | 0.00060145
Wellington Electricity | 2012 | 2011-10-06
Wellington Electricity | 2012 | 2011-10-07
Wellington Electricity | 2012 | 2011-10-08
Wellington Electricity | 2012 | 2011-10-09 | 0.12863 | 0.0016525
Wellington Electricity | 2012 | 2011-10-10 | 0.22982 | 0.0063851
Wellington Electricity | 2012 | 2011-10-11
Wellington Electricity | 2012 | 2011-10-12 | 0.36798 | 0.0079586
Wellington Electricity | 2012 | 2011-10-13 | 0.0017861 | 1.2151e-05
Wellington Electricity | 2012 | 2011-10-14 | 0.010328 | 0.00015188
Wellington Electricity | 2012 | 2011-10-15
Wellington Electricity | 2012 | 2011-10-16
Wellington Electricity | 2012 | 2011-10-17 | 0.012822 | 0.00019137
Wellington Electricity | 2012 | 2011-10-18
Wellington Electricity | 2012 | 2011-10-19
Wellington Electricity | 2012 | 2011-10-20 | 0.027885 | 0.00082016
Wellington Electricity | 2012 | 2011-10-21
Wellington Electricity | 2012 | 2011-10-22
Wellington Electricity | 2012 | 2011-10-23
Wellington Electricity | 2012 | 2011-10-24
Wellington Electricity | 2012 | 2011-10-25
Wellington Electricity | 2012 | 2011-10-26 | 0.00068347 | 3.0376e-06
Wellington Electricity | 2012 | 2011-10-27 | 0.47343 | 0.0013244
Wellington Electricity | 2012 | 2011-10-28
Wellington Electricity | 2012 | 2011-10-29
Wellington Electricity | 2012 | 2011-10-30
Wellington Electricity | 2012 | 2011-10-31
Wellington Electricity | 2012 | 2011-11-01 | 0.093705 | 0.0045352
Wellington Electricity | 2012 | 2011-11-02 | 0.00020352 | 3.0376e-06
Wellington Electricity | 2012 | 2011-11-03 | 0.099513 | 0.00064398
Wellington Electricity | 2012 | 2011-11-04 | 0.00083839 | 1.8226e-05
Wellington Electricity | 2012 | 2011-11-05 | 0.00025212 | 3.0376e-06
Wellington Electricity | 2012 | 2011-11-06
Wellington Electricity | 2012 | 2011-11-07 | 0.25244 | 0.018839
Wellington Electricity | 2012 | 2011-11-08 | 0.0047964 | 0.00075029
Wellington Electricity | 2012 | 2011-11-09 | 0.058985 | 0.00099027
Wellington Electricity | 2012 | 2011-11-10 | 0.0045564 | 1.2151e-05
Wellington Electricity | 2012 | 2011-11-11 | 0.37776 | 0.005729
Wellington Electricity | 2012 | 2011-11-12
Wellington Electricity | 2012 | 2011-11-13
Wellington Electricity | 2012 | 2011-11-14 | 0.0056621 | 3.0376e-05
Wellington Electricity | 2012 | 2011-11-15 | 0.010352 | 0.00021567
Wellington Electricity | 2012 | 2011-11-16 | 0.45321 | 0.0080376
Wellington Electricity | 2012 | 2011-11-17
Wellington Electricity | 2012 | 2011-11-18
Wellington Electricity | 2012 | 2011-11-19 | 0.0068286 | 0.00012151
Wellington Electricity | 2012 | 2011-11-20
Wellington Electricity | 2012 | 2011-11-21 | 0.96372 | 0.022478
Wellington Electricity | 2012 | 2011-11-22
Wellington Electricity | 2012 | 2011-11-23 | 0.20288 | 0.006701
Wellington Electricity | 2012 | 2011-11-24
Wellington Electricity | 2012 | 2011-11-25 | 0.005492 | 0.00010935
Wellington Electricity | 2012 | 2011-11-26
Wellington Electricity | 2012 | 2011-11-27
Wellington Electricity | 2012 | 2011-11-28 | 0.51418 | 0.0032533
Wellington Electricity | 2012 | 2011-11-29 | 0.013621 | 0.00023086
Wellington Electricity | 2012 | 2011-11-30
Wellington Electricity | 2012 | 2011-12-01
Wellington Electricity | 2012 | 2011-12-02
Wellington Electricity | 2012 | 2011-12-03
Wellington Electricity | 2012 | 2011-12-04
Wellington Electricity | 2012 | 2011-12-05
Wellington Electricity | 2012 | 2011-12-06
Wellington Electricity | 2012 | 2011-12-07 | 0.00060753 | 1.2151e-05
Wellington Electricity | 2012 | 2011-12-08
Wellington Electricity | 2012 | 2011-12-09
Wellington Electricity | 2012 | 2011-12-10
Wellington Electricity | 2012 | 2011-12-11 | 0.00092344 | 0.00092344
Wellington Electricity | 2012 | 2011-12-12
Wellington Electricity | 2012 | 2011-12-13
Wellington Electricity | 2012 | 2011-12-14
Wellington Electricity | 2012 | 2011-12-15 | 0.0016342 | 6.0753e-06
Wellington Electricity | 2012 | 2011-12-16 | 0.003797 | 1.5188e-05
Wellington Electricity | 2012 | 2011-12-17 | 0.079282 | 0.00045564
Wellington Electricity | 2012 | 2011-12-18 | 0.018384 | 0.00020656
Wellington Electricity | 2012 | 2011-12-19 | 0.0012545 | 2.1263e-05
Wellington Electricity | 2012 | 2011-12-20 | 0.003147 | 3.0376e-05
Wellington Electricity | 2012 | 2011-12-21
Wellington Electricity | 2012 | 2011-12-22
Wellington Electricity | 2012 | 2011-12-23
Wellington Electricity | 2012 | 2011-12-24
Wellington Electricity | 2012 | 2011-12-25
Wellington Electricity | 2012 | 2011-12-26
Wellington Electricity | 2012 | 2011-12-27
Wellington Electricity | 2012 | 2011-12-28
Wellington Electricity | 2012 | 2011-12-29
Wellington Electricity | 2012 | 2011-12-30
Wellington Electricity | 2012 | 2011-12-31
Wellington Electricity | 2012 | 2012-01-01
Wellington Electricity | 2012 | 2012-01-02 | 0.36043 | 0.0045686
Wellington Electricity | 2012 | 2012-01-03
Wellington Electricity | 2012 | 2012-01-04
Wellington Electricity | 2012 | 2012-01-05
Wellington Electricity | 2012 | 2012-01-06
Wellington Electricity | 2012 | 2012-01-07
Wellington Electricity | 2012 | 2012-01-08 | 1.0079 | 0.0092648
Wellington Electricity | 2012 | 2012-01-09 | 0.004277 | 5.164e-05
Wellington Electricity | 2012 | 2012-01-10
Wellington Electricity | 2012 | 2012-01-11
Wellington Electricity | 2012 | 2012-01-12 | 0.23928 | 0.0059902
Wellington Electricity | 2012 | 2012-01-13 | 1.1408 | 0.022375
Wellington Electricity | 2012 | 2012-01-14 | 0.18705 | 0.0054738
Wellington Electricity | 2012 | 2012-01-15 | 0.0019107 | 3.0376e-06
Wellington Electricity | 2012 | 2012-01-16 | 0.12226 | 0.0034933
Wellington Electricity | 2012 | 2012-01-17 | 0.11959 | 0.00027339
Wellington Electricity | 2012 | 2012-01-18
Wellington Electricity | 2012 | 2012-01-19
Wellington Electricity | 2012 | 2012-01-20
Wellington Electricity | 2012 | 2012-01-21
Wellington Electricity | 2012 | 2012-01-22
Wellington Electricity | 2012 | 2012-01-23
Wellington Electricity | 2012 | 2012-01-24 | 0.21074 | 0.011482
Wellington Electricity | 2012 | 2012-01-25
Wellington Electricity | 2012 | 2012-01-26 | 0.00060145 | 6.0753e-06
Wellington Electricity | 2012 | 2012-01-27 | 0.577 | 0.0065431
Wellington Electricity | 2012 | 2012-01-28 | 0.001695 | 1.8226e-05
Wellington Electricity | 2012 | 2012-01-29
Wellington Electricity | 2012 | 2012-01-30 | 0.18104 | 0.0016707
Wellington Electricity | 2012 | 2012-01-31
Wellington Electricity | 2012 | 2012-02-01 | 7.2903e-05 | 7.2903e-05
Wellington Electricity | 2012 | 2012-02-02 | 0.04034 | 0.00025212
Wellington Electricity | 2012 | 2012-02-03 | 0.6009 | 0.0089428
Wellington Electricity | 2012 | 2012-02-04
Wellington Electricity | 2012 | 2012-02-05 | 0.33779 | 0.007187
Wellington Electricity | 2012 | 2012-02-06
Wellington Electricity | 2012 | 2012-02-07
Wellington Electricity | 2012 | 2012-02-08
Wellington Electricity | 2012 | 2012-02-09 | 0.0053766 | 9.4167e-05
Wellington Electricity | 2012 | 2012-02-10 | 0.063007 | 0.00091129
Wellington Electricity | 2012 | 2012-02-11 | 0.11508 | 0.00078978
Wellington Electricity | 2012 | 2012-02-12 | 0.052186 | 0.00072903
Wellington Electricity | 2012 | 2012-02-13 | 0.66073 | 0.0070291
Wellington Electricity | 2012 | 2012-02-14
Wellington Electricity | 2012 | 2012-02-15
Wellington Electricity | 2012 | 2012-02-16
Wellington Electricity | 2012 | 2012-02-17 | 0.00022782 | 3.0376e-06
Wellington Electricity | 2012 | 2012-02-18 | 0.0021324 | 1.8226e-05
Wellington Electricity | 2012 | 2012-02-19 | 0.057028 | 0.019009
Wellington Electricity | 2012 | 2012-02-20 | 0.68068 | 0.0096293
Wellington Electricity | 2012 | 2012-02-21 | 0.00113 | 3.0376e-06
Wellington Electricity | 2012 | 2012-02-22 | 0.43621 | 0.0063851
Wellington Electricity | 2012 | 2012-02-23 | 0.52714 | 0.0063365
Wellington Electricity | 2012 | 2012-02-24 | 0.16036 | 0.0011361
Wellington Electricity | 2012 | 2012-02-25 | 0.0040643 | 6.0753e-06
Wellington Electricity | 2012 | 2012-02-26 | 0.0014459 | 0.00020656
Wellington Electricity | 2012 | 2012-02-27 | 0.97917 | 0.020841
Wellington Electricity | 2012 | 2012-02-28 | 0.011264 | 0.001294
Wellington Electricity | 2012 | 2012-02-29 | 0.26572 | 0.0027096
Wellington Electricity | 2012 | 2012-03-01 | 0.00035237 | 0.00035237
Wellington Electricity | 2012 | 2012-03-02
Wellington Electricity | 2012 | 2012-03-03 | 2.1026 | 0.031245
Wellington Electricity | 2012 | 2012-03-04 | 0.030929 | 0.00046172
Wellington Electricity | 2012 | 2012-03-05
Wellington Electricity | 2012 | 2012-03-06 | 0.0061239 | 4.8602e-05
Wellington Electricity | 2012 | 2012-03-07
Wellington Electricity | 2012 | 2012-03-08 | 8.2016e-05 | 9.1129e-06
Wellington Electricity | 2012 | 2012-03-09
Wellington Electricity | 2012 | 2012-03-10
Wellington Electricity | 2012 | 2012-03-11 | 0.33492 | 0.0045564
Wellington Electricity | 2012 | 2012-03-12 | 0.054255 | 0.0021598
Wellington Electricity | 2012 | 2012-03-13
Wellington Electricity | 2012 | 2012-03-14 | 0.0006379 | 6.0753e-06
Wellington Electricity | 2012 | 2012-03-15 | 0.75469 | 0.012163
Wellington Electricity | 2012 | 2012-03-16
Wellington Electricity | 2012 | 2012-03-17 | 0.00064398 | 6.0753e-06
Wellington Electricity | 2012 | 2012-03-18
Wellington Electricity | 2012 | 2012-03-19
Wellington Electricity | 2012 | 2012-03-20 | 0.0077156 | 6.0753e-06
Wellington Electricity | 2012 | 2012-03-21
Wellington Electricity | 2012 | 2012-03-22 | 2.1026 | 0.012466
Wellington Electricity | 2012 | 2012-03-23 | 0.16008 | 0.0021992
Wellington Electricity | 2012 | 2012-03-24 | 0.01548 | 0.00017011
Wellington Electricity | 2012 | 2012-03-25 | 0.0024726 | 6.0753e-06
Wellington Electricity | 2012 | 2012-03-26
Wellington Electricity | 2012 | 2012-03-27 | 0.0062545 | 1.8226e-05
Wellington Electricity | 2012 | 2012-03-28
Wellington Electricity | 2012 | 2012-03-29
Wellington Electricity | 2012 | 2012-03-30
Wellington Electricity | 2012 | 2012-03-31 | 0.051366 | 0.0005407
Wellington Electricity | 2013 | 2012-04-01
Wellington Electricity | 2013 | 2012-04-02
Wellington Electricity | 2013 | 2012-04-03
Wellington Electricity | 2013 | 2012-04-04 | 0.00032786 | 3.0357e-06
Wellington Electricity | 2013 | 2012-04-05 | 0.042725 | 0.0013782
Wellington Electricity | 2013 | 2012-04-06
Wellington Electricity | 2013 | 2012-04-07
Wellington Electricity | 2013 | 2012-04-08 | 0.46361 | 0.0079081
Wellington Electricity | 2013 | 2012-04-09 | 1.7364 | 0.012392
Wellington Electricity | 2013 | 2012-04-10 | 0.056401 | 0.00037947
Wellington Electricity | 2013 | 2012-04-11 | 0.23287 | 0.0047418
Wellington Electricity | 2013 | 2012-04-12 | 0.086008 | 0.0016393
Wellington Electricity | 2013 | 2012-04-13 | 0.013521 | 0.00010321
Wellington Electricity | 2013 | 2012-04-14
Wellington Electricity | 2013 | 2012-04-15 | 0.0011779 | 1.2143e-05
Wellington Electricity | 2013 | 2012-04-16 | 0.0012507 | 6.0715e-06
Wellington Electricity | 2013 | 2012-04-17 | 0.0003783 | 3.0357e-06
Wellington Electricity | 2013 | 2012-04-18
Wellington Electricity | 2013 | 2012-04-19
Wellington Electricity | 2013 | 2012-04-20 | 0.043605 | 0.00023072
Wellington Electricity | 2013 | 2012-04-21
Wellington Electricity | 2013 | 2012-04-22
Wellington Electricity | 2013 | 2012-04-23
Wellington Electricity | 2013 | 2012-04-24
Wellington Electricity | 2013 | 2012-04-25
Wellington Electricity | 2013 | 2012-04-26 | 0.00081965 | 3.0357e-06
Wellington Electricity | 2013 | 2012-04-27 | 0.69262 | 0.006369
Wellington Electricity | 2013 | 2012-04-28
Wellington Electricity | 2013 | 2012-04-29 | 0.22815 | 0.0029173
Wellington Electricity | 2013 | 2012-04-30 | 0.0047175 | 0.0047175
Wellington Electricity | 2013 | 2012-05-01
Wellington Electricity | 2013 | 2012-05-02 | 0.053859 | 0.0016393
Wellington Electricity | 2013 | 2012-05-03
Wellington Electricity | 2013 | 2012-05-04
Wellington Electricity | 2013 | 2012-05-05 | 0.40497 | 0.0090161
Wellington Electricity | 2013 | 2012-05-06 | 0.0042409 | 3.3393e-05
Wellington Electricity | 2013 | 2012-05-07
Wellington Electricity | 2013 | 2012-05-08 | 0.3748 | 0.0062991
Wellington Electricity | 2013 | 2012-05-09 | 0.0020947 | 9.1072e-06
Wellington Electricity | 2013 | 2012-05-10 | 0.54844 | 0.0070611
Wellington Electricity | 2013 | 2012-05-11
Wellington Electricity | 2013 | 2012-05-12 | 0.031693 | 0.0017607
Wellington Electricity | 2013 | 2012-05-13
Wellington Electricity | 2013 | 2012-05-14
Wellington Electricity | 2013 | 2012-05-15 | 0.054473 | 0.00041286
Wellington Electricity | 2013 | 2012-05-16 | 0.40649 | 0.0047297
Wellington Electricity | 2013 | 2012-05-17
Wellington Electricity | 2013 | 2012-05-18
Wellington Electricity | 2013 | 2012-05-19
Wellington Electricity | 2013 | 2012-05-20 | 0.0033697 | 1.5179e-05
Wellington Electricity | 2013 | 2012-05-21
Wellington Electricity | 2013 | 2012-05-22
Wellington Electricity | 2013 | 2012-05-23
Wellington Electricity | 2013 | 2012-05-24 | 0.016733 | 0.00032179
Wellington Electricity | 2013 | 2012-05-25 | 0.0048511 | 0.00016697
Wellington Electricity | 2013 | 2012-05-26
Wellington Electricity | 2013 | 2012-05-27 | 0.096111 | 0.0011171
Wellington Electricity | 2013 | 2012-05-28
Wellington Electricity | 2013 | 2012-05-29
Wellington Electricity | 2013 | 2012-05-30
Wellington Electricity | 2013 | 2012-05-31
Wellington Electricity | 2013 | 2012-06-01 | 0.25058 | 0.011263
Wellington Electricity | 2013 | 2012-06-02 | 0.0083207 | 0.00010321
Wellington Electricity | 2013 | 2012-06-03
Wellington Electricity | 2013 | 2012-06-04
Wellington Electricity | 2013 | 2012-06-05
Wellington Electricity | 2013 | 2012-06-06 | 0.11078 | 0.0012204
Wellington Electricity | 2013 | 2012-06-07 | 0.28606 | 0.0012629
Wellington Electricity | 2013 | 2012-06-08 | 0.0067029 | 6.9822e-05
Wellington Electricity | 2013 | 2012-06-09
Wellington Electricity | 2013 | 2012-06-10 | 0.007744 | 4.25e-05
Wellington Electricity | 2013 | 2012-06-11 | 0.086974 | 0.00047965
Wellington Electricity | 2013 | 2012-06-12 | 1.328 | 0.024268
Wellington Electricity | 2013 | 2012-06-13
Wellington Electricity | 2013 | 2012-06-14
Wellington Electricity | 2013 | 2012-06-15
Wellington Electricity | 2013 | 2012-06-16
Wellington Electricity | 2013 | 2012-06-17 | 0.59271 | 0.0090343
Wellington Electricity | 2013 | 2012-06-18
Wellington Electricity | 2013 | 2012-06-19 | 0.0061534 | 2.125e-05
Wellington Electricity | 2013 | 2012-06-20 | 0.0014389 | 3.0357e-06
Wellington Electricity | 2013 | 2012-06-21 | 0.0033272 | 2.4286e-05
Wellington Electricity | 2013 | 2012-06-22 | 0.0016393 | 1.8214e-05
Wellington Electricity | 2013 | 2012-06-23 | 0.48115 | 0.0056161
Wellington Electricity | 2013 | 2012-06-24 | 0.21124 | 0.0038402
Wellington Electricity | 2013 | 2012-06-25 | 0.02271 | 0.00098358
Wellington Electricity | 2013 | 2012-06-26 | 0.13154 | 0.00095929
Wellington Electricity | 2013 | 2012-06-27 | 0.017397 | 0.00027929
Wellington Electricity | 2013 | 2012-06-28 | 0.0059925 | 2.125e-05
Wellington Electricity | 2013 | 2012-06-29 | 0.0035059 | 0.00010321
Wellington Electricity | 2013 | 2012-06-30
Wellington Electricity | 2013 | 2012-07-01 | 0.0096354 | 0.00041893
Wellington Electricity | 2013 | 2012-07-02
Wellington Electricity | 2013 | 2012-07-03
Wellington Electricity | 2013 | 2012-07-04 | 0.007814 | 7.8929e-05
Wellington Electricity | 2013 | 2012-07-05
Wellington Electricity | 2013 | 2012-07-06
Wellington Electricity | 2013 | 2012-07-07 | 7.2858e-05 | 3.6429e-05
Wellington Electricity | 2013 | 2012-07-08
Wellington Electricity | 2013 | 2012-07-09
Wellington Electricity | 2013 | 2012-07-10 | 0.0016514 | 1.2143e-05
Wellington Electricity | 2013 | 2012-07-11 | 0.64489 | 0.0079779
Wellington Electricity | 2013 | 2012-07-12
Wellington Electricity | 2013 | 2012-07-13
Wellington Electricity | 2013 | 2012-07-14
Wellington Electricity | 2013 | 2012-07-15 | 0.0544 | 0.0015543
Wellington Electricity | 2013 | 2012-07-16 | 0.013224 | 3.3393e-05
Wellington Electricity | 2013 | 2012-07-17
Wellington Electricity | 2013 | 2012-07-18
Wellington Electricity | 2013 | 2012-07-19 | 0.001102 | 3.0357e-06
Wellington Electricity | 2013 | 2012-07-20 | 0.2061 | 0.0044322
Wellington Electricity | 2013 | 2012-07-21 | 0.0044056 | 0.00010321
Wellington Electricity | 2013 | 2012-07-22
Wellington Electricity | 2013 | 2012-07-23
Wellington Electricity | 2013 | 2012-07-24 | 0.054742 | 0.0013054
Wellington Electricity | 2013 | 2012-07-25
Wellington Electricity | 2013 | 2012-07-26
Wellington Electricity | 2013 | 2012-07-27 | 0.072267 | 0.00091072
Wellington Electricity | 2013 | 2012-07-28
Wellington Electricity | 2013 | 2012-07-29
Wellington Electricity | 2013 | 2012-07-30 | 0.023023 | 0.00047965
Wellington Electricity | 2013 | 2012-07-31 | 0.35174 | 0.005179
Wellington Electricity | 2013 | 2012-08-01 | 0.18764 | 0.0039161
Wellington Electricity | 2013 | 2012-08-02
Wellington Electricity | 2013 | 2012-08-03 | 0.00374 | 2.4286e-05
Wellington Electricity | 2013 | 2012-08-04 | 0.0029991 | 0.002465
Wellington Electricity | 2013 | 2012-08-05 | 0.043381 | 0.00069215
Wellington Electricity | 2013 | 2012-08-06 | 0.0064722 | 0.00024893
Wellington Electricity | 2013 | 2012-08-07 | 0.0012932 | 1.8214e-05
Wellington Electricity | 2013 | 2012-08-08 | 0.00036429 | 6.0715e-06
Wellington Electricity | 2013 | 2012-08-09 | 0.0045415 | 0.00020643
Wellington Electricity | 2013 | 2012-08-10
Wellington Electricity | 2013 | 2012-08-11 | 0.78883 | 0.0077775
Wellington Electricity | 2013 | 2012-08-12 | 0.15139 | 0.001105
Wellington Electricity | 2013 | 2012-08-13
Wellington Electricity | 2013 | 2012-08-14
Wellington Electricity | 2013 | 2012-08-15
Wellington Electricity | 2013 | 2012-08-16
Wellington Electricity | 2013 | 2012-08-17 | 0.33508 | 0.0071279
Wellington Electricity | 2013 | 2012-08-18
Wellington Electricity | 2013 | 2012-08-19
Wellington Electricity | 2013 | 2012-08-20
Wellington Electricity | 2013 | 2012-08-21 | 0.10352 | 0.0033939
Wellington Electricity | 2013 | 2012-08-22
Wellington Electricity | 2013 | 2012-08-23 | 0.010054 | 0.00083786
Wellington Electricity | 2013 | 2012-08-24
Wellington Electricity | 2013 | 2012-08-25
Wellington Electricity | 2013 | 2012-08-26
Wellington Electricity | 2013 | 2012-08-27 | 0.051729 | 0.00036429
Wellington Electricity | 2013 | 2012-08-28
Wellington Electricity | 2013 | 2012-08-29 | 0.040557 | 0.0010139
Wellington Electricity | 2013 | 2012-08-30
Wellington Electricity | 2013 | 2012-08-31 | 0.0039586 | 6.375e-05
Wellington Electricity | 2013 | 2012-09-01
Wellington Electricity | 2013 | 2012-09-02
Wellington Electricity | 2013 | 2012-09-03 | 0.43303 | 0.0096536
Wellington Electricity | 2013 | 2012-09-04 | 0.0011991 | 1.2143e-05
Wellington Electricity | 2013 | 2012-09-05 | 0.0011991 | 3.0357e-06
Wellington Electricity | 2013 | 2012-09-06
Wellington Electricity | 2013 | 2012-09-07 | 0.84215 | 0.0062718
Wellington Electricity | 2013 | 2012-09-08 | 2.1026 | 0.031245
Wellington Electricity | 2013 | 2012-09-09 | 0.17292 | 0.00136
Wellington Electricity | 2013 | 2012-09-10 | 1.8192 | 0.031248
Wellington Electricity | 2013 | 2012-09-11 | 0.063742 | 0.00086822
Wellington Electricity | 2013 | 2012-09-12 | 0.065207 | 0.00034
Wellington Electricity | 2013 | 2012-09-13
Wellington Electricity | 2013 | 2012-09-14
Wellington Electricity | 2013 | 2012-09-15 | 0.070303 | 0.00066786
Wellington Electricity | 2013 | 2012-09-16
Wellington Electricity | 2013 | 2012-09-17 | 0.016187 | 4.8572e-05
Wellington Electricity | 2013 | 2012-09-18 | 0.015072 | 4.5536e-05
Wellington Electricity | 2013 | 2012-09-19
Wellington Electricity | 2013 | 2012-09-20 | 0.00028839 | 3.0357e-06
Wellington Electricity | 2013 | 2012-09-21 | 0.17781 | 0.0039768
Wellington Electricity | 2013 | 2012-09-22
Wellington Electricity | 2013 | 2012-09-23 | 0.0023557 | 2.4286e-05
Wellington Electricity | 2013 | 2012-09-24 | 0.0014936 | 1.2143e-05
Wellington Electricity | 2013 | 2012-09-25 | 0.33652 | 0.0019793
Wellington Electricity | 2013 | 2012-09-26 | 0.70774 | 0.0085
Wellington Electricity | 2013 | 2012-09-27 | 0.049725 | 0.00013661
Wellington Electricity | 2013 | 2012-09-28
Wellington Electricity | 2013 | 2012-09-29
Wellington Electricity | 2013 | 2012-09-30
Wellington Electricity | 2013 | 2012-10-01 | 0.00023375 | 3.0357e-06
Wellington Electricity | 2013 | 2012-10-02 | 0.00026714 | 3.0357e-06
Wellington Electricity | 2013 | 2012-10-03 | 0.0011414 | 6.0715e-06
Wellington Electricity | 2013 | 2012-10-04
Wellington Electricity | 2013 | 2012-10-05 | 0.53893 | 0.0015179
Wellington Electricity | 2013 | 2012-10-06
Wellington Electricity | 2013 | 2012-10-07 | 0.38373 | 0.006205
Wellington Electricity | 2013 | 2012-10-08 | 0.015973 | 0.00027929
Wellington Electricity | 2013 | 2012-10-09
Wellington Electricity | 2013 | 2012-10-10 | 0.22239 | 0.0078079
Wellington Electricity | 2013 | 2012-10-11 | 0.51378 | 0.0081236
Wellington Electricity | 2013 | 2012-10-12 | 0.00015786 | 6.0715e-06
Wellington Electricity | 2013 | 2012-10-13
Wellington Electricity | 2013 | 2012-10-14
Wellington Electricity | 2013 | 2012-10-15
Wellington Electricity | 2013 | 2012-10-16 | 0.46555 | 0.0061322
Wellington Electricity | 2013 | 2012-10-17
Wellington Electricity | 2013 | 2012-10-18 | 0.76828 | 0.018439
Wellington Electricity | 2013 | 2012-10-19
Wellington Electricity | 2013 | 2012-10-20
Wellington Electricity | 2013 | 2012-10-21 | 0.00091375 | 3.0357e-06
Wellington Electricity | 2013 | 2012-10-22
Wellington Electricity | 2013 | 2012-10-23 | 0.34821 | 0.0051668
Wellington Electricity | 2013 | 2012-10-24 | 0.0040072 | 3.3393e-05
Wellington Electricity | 2013 | 2012-10-25 | 0.26719 | 0.0039586
Wellington Electricity | 2013 | 2012-10-26
Wellington Electricity | 2013 | 2012-10-27 | 0.0041286 | 0.00010321
Wellington Electricity | 2013 | 2012-10-28 | 0.52666 | 0.0049118
Wellington Electricity | 2013 | 2012-10-29
Wellington Electricity | 2013 | 2012-10-30 | 0.00016393 | 3.0357e-06
Wellington Electricity | 2013 | 2012-10-31
Wellington Electricity | 2013 | 2012-11-01
Wellington Electricity | 2013 | 2012-11-02
Wellington Electricity | 2013 | 2012-11-03 | 0.775 | 0.0062779
Wellington Electricity | 2013 | 2012-11-04
Wellington Electricity | 2013 | 2012-11-05
Wellington Electricity | 2013 | 2012-11-06 | 0.00024286 | 1.2143e-05
Wellington Electricity | 2013 | 2012-11-07
Wellington Electricity | 2013 | 2012-11-08 | 0.003995 | 2.125e-05
Wellington Electricity | 2013 | 2012-11-09
Wellington Electricity | 2013 | 2012-11-10
Wellington Electricity | 2013 | 2012-11-11
Wellington Electricity | 2013 | 2012-11-12
Wellington Electricity | 2013 | 2012-11-13
Wellington Electricity | 2013 | 2012-11-14 | 0.023627 | 0.00013054
Wellington Electricity | 2013 | 2012-11-15 | 0.00026714 | 3.0357e-06
Wellington Electricity | 2013 | 2012-11-16 | 0.0037097 | 5.4643e-05
Wellington Electricity | 2013 | 2012-11-17 | 0.0013539 | 6.0715e-06
Wellington Electricity | 2013 | 2012-11-18
Wellington Electricity | 2013 | 2012-11-19
Wellington Electricity | 2013 | 2012-11-20
Wellington Electricity | 2013 | 2012-11-21
Wellington Electricity | 2013 | 2012-11-22
Wellington Electricity | 2013 | 2012-11-23
Wellington Electricity | 2013 | 2012-11-24
Wellington Electricity | 2013 | 2012-11-25 | 0.0020248 | 3.0357e-06
Wellington Electricity | 2013 | 2012-11-26
Wellington Electricity | 2013 | 2012-11-27
Wellington Electricity | 2013 | 2012-11-28
Wellington Electricity | 2013 | 2012-11-29
Wellington Electricity | 2013 | 2012-11-30 | 0.00022464 | 3.0357e-06
Wellington Electricity | 2013 | 2012-12-01 | 0.30454 | 0.0017941
Wellington Electricity | 2013 | 2012-12-02 | 0.00272 | 8.5e-05
Wellington Electricity | 2013 | 2012-12-03 | 0.006885 | 1.8214e-05
Wellington Electricity | 2013 | 2012-12-04 | 0.80977 | 0.0081783
Wellington Electricity | 2013 | 2012-12-05 | 0.48275 | 0.0059075
Wellington Electricity | 2013 | 2012-12-06
Wellington Electricity | 2013 | 2012-12-07
Wellington Electricity | 2013 | 2012-12-08
Wellington Electricity | 2013 | 2012-12-09
Wellington Electricity | 2013 | 2012-12-10
Wellington Electricity | 2013 | 2012-12-11
Wellington Electricity | 2013 | 2012-12-12
Wellington Electricity | 2013 | 2012-12-13 | 0.1869 | 0.0037977
Wellington Electricity | 2013 | 2012-12-14 | 0.47149 | 0.0080993
Wellington Electricity | 2013 | 2012-12-15 | 0.0031875 | 6.0715e-06
Wellington Electricity | 2013 | 2012-12-16 | 0.013715 | 0.00014268
Wellington Electricity | 2013 | 2012-12-17 | 0.1288 | 0.0020036
Wellington Electricity | 2013 | 2012-12-18 | 0.0032786 | 1.2143e-05
Wellington Electricity | 2013 | 2012-12-19 | 0.057975 | 0.00094715
Wellington Electricity | 2013 | 2012-12-20 | 0.39134 | 0.0056465
Wellington Electricity | 2013 | 2012-12-21
Wellington Electricity | 2013 | 2012-12-22
Wellington Electricity | 2013 | 2012-12-23
Wellington Electricity | 2013 | 2012-12-24
Wellington Electricity | 2013 | 2012-12-25 | 0.30243 | 0.005434
Wellington Electricity | 2013 | 2012-12-26 | 0.44914 | 0.0062597
Wellington Electricity | 2013 | 2012-12-27 | 1.6285 | 0.019769
Wellington Electricity | 2013 | 2012-12-28 | 0.00012143 | 2.4286e-05
Wellington Electricity | 2013 | 2012-12-29
Wellington Electricity | 2013 | 2012-12-30
Wellington Electricity | 2013 | 2012-12-31 | 0.0011839 | 6.0715e-06
Wellington Electricity | 2013 | 2013-01-01
Wellington Electricity | 2013 | 2013-01-02 | 0.83455 | 0.015889
Wellington Electricity | 2013 | 2013-01-03 | 0.04582 | 0.00049179
Wellington Electricity | 2013 | 2013-01-04
Wellington Electricity | 2013 | 2013-01-05
Wellington Electricity | 2013 | 2013-01-06
Wellington Electricity | 2013 | 2013-01-07
Wellington Electricity | 2013 | 2013-01-08
Wellington Electricity | 2013 | 2013-01-09
Wellington Electricity | 2013 | 2013-01-10 | 0.046428 | 0.00081965
Wellington Electricity | 2013 | 2013-01-11 | 0.34504 | 0.0086033
Wellington Electricity | 2013 | 2013-01-12 | 0.00076804 | 3.0357e-06
Wellington Electricity | 2013 | 2013-01-13 | 0.014693 | 0.0013357
Wellington Electricity | 2013 | 2013-01-14 | 0.0023739 | 1.2143e-05
Wellington Electricity | 2013 | 2013-01-15 | 0.35195 | 0.0071583
Wellington Electricity | 2013 | 2013-01-16 | 0.026296 | 0.00090161
Wellington Electricity | 2013 | 2013-01-17 | 0.81181 | 0.008409
Wellington Electricity | 2013 | 2013-01-18 | 0.00099572 | 6.0715e-06
Wellington Electricity | 2013 | 2013-01-19 | 9.1072e-05 | 6.0715e-06
Wellington Electricity | 2013 | 2013-01-20
Wellington Electricity | 2013 | 2013-01-21 | 0.26543 | 0.0055129
Wellington Electricity | 2013 | 2013-01-22 | 0.021457 | 0.00016089
Wellington Electricity | 2013 | 2013-01-23 | 0.014669 | 4.8572e-05
Wellington Electricity | 2013 | 2013-01-24
Wellington Electricity | 2013 | 2013-01-25 | 0.040098 | 0.000425
Wellington Electricity | 2013 | 2013-01-26
Wellington Electricity | 2013 | 2013-01-27 | 0.00083786 | 3.0357e-06
Wellington Electricity | 2013 | 2013-01-28
Wellington Electricity | 2013 | 2013-01-29 | 0.21426 | 0.0023709
Wellington Electricity | 2013 | 2013-01-30
Wellington Electricity | 2013 | 2013-01-31 | 0.23122 | 0.011117
Wellington Electricity | 2013 | 2013-02-01 | 0.022604 | 0.00027322
Wellington Electricity | 2013 | 2013-02-02
Wellington Electricity | 2013 | 2013-02-03
Wellington Electricity | 2013 | 2013-02-04 | 1.0871 | 0.007735
Wellington Electricity | 2013 | 2013-02-05 | 0.28858 | 0.0031632
Wellington Electricity | 2013 | 2013-02-06
Wellington Electricity | 2013 | 2013-02-07 | 0.022996 | 0.00030661
Wellington Electricity | 2013 | 2013-02-08 | 0.07656 | 0.00092286
Wellington Electricity | 2013 | 2013-02-09
Wellington Electricity | 2013 | 2013-02-10 | 0.00081358 | 6.0715e-06
Wellington Electricity | 2013 | 2013-02-11 | 0.025949 | 8.5e-05
Wellington Electricity | 2013 | 2013-02-12 | 0.24204 | 0.0086579
Wellington Electricity | 2013 | 2013-02-13
Wellington Electricity | 2013 | 2013-02-14
Wellington Electricity | 2013 | 2013-02-15 | 0.22461 | 0.0039161
Wellington Electricity | 2013 | 2013-02-16
Wellington Electricity | 2013 | 2013-02-17 | 0.00052822 | 6.0715e-06
Wellington Electricity | 2013 | 2013-02-18 | 0.036921 | 0.00097143
Wellington Electricity | 2013 | 2013-02-19 | 0.0039768 | 3.0357e-05
Wellington Electricity | 2013 | 2013-02-20
Wellington Electricity | 2013 | 2013-02-21
Wellington Electricity | 2013 | 2013-02-22
Wellington Electricity | 2013 | 2013-02-23 | 0.63612 | 0.010303
Wellington Electricity | 2013 | 2013-02-24
Wellington Electricity | 2013 | 2013-02-25 | 0.0026593 | 1.8214e-05
Wellington Electricity | 2013 | 2013-02-26
Wellington Electricity | 2013 | 2013-02-27 | 0.00033697 | 3.0357e-06
Wellington Electricity | 2013 | 2013-02-28 | 0.00023679 | 6.0715e-06
Wellington Electricity | 2013 | 2013-03-01
Wellington Electricity | 2013 | 2013-03-02
Wellington Electricity | 2013 | 2013-03-03 | 0.00068304 | 3.0357e-06
Wellington Electricity | 2013 | 2013-03-04 | 0.0028991 | 1.5179e-05
Wellington Electricity | 2013 | 2013-03-05 | 0.000765 | 3.0357e-06
Wellington Electricity | 2013 | 2013-03-06
Wellington Electricity | 2013 | 2013-03-07 | 0.00221 | 6.0715e-06
Wellington Electricity | 2013 | 2013-03-08 | 0.51792 | 0.006545
Wellington Electricity | 2013 | 2013-03-09
Wellington Electricity | 2013 | 2013-03-10 | 0.0024407 | 1.2143e-05
Wellington Electricity | 2013 | 2013-03-11
Wellington Electricity | 2013 | 2013-03-12 | 0.00034 | 3.0357e-06
Wellington Electricity | 2013 | 2013-03-13
Wellington Electricity | 2013 | 2013-03-14 | 0.54131 | 0.0078625
Wellington Electricity | 2013 | 2013-03-15
Wellington Electricity | 2013 | 2013-03-16
Wellington Electricity | 2013 | 2013-03-17 | 0.00023982 | 3.0357e-06
Wellington Electricity | 2013 | 2013-03-18 | 0.21108 | 0.005009
Wellington Electricity | 2013 | 2013-03-19 | 0.15361 | 0.00027929
Wellington Electricity | 2013 | 2013-03-20
Wellington Electricity | 2013 | 2013-03-21
Wellington Electricity | 2013 | 2013-03-22
Wellington Electricity | 2013 | 2013-03-23
Wellington Electricity | 2013 | 2013-03-24 | 0.0014784 | 3.0357e-06
Wellington Electricity | 2013 | 2013-03-25
Wellington Electricity | 2013 | 2013-03-26 | 0.00014268 | 3.0357e-06
Wellington Electricity | 2013 | 2013-03-27 | 0.0010352 | 3.0357e-06
Wellington Electricity | 2013 | 2013-03-28
Wellington Electricity | 2013 | 2013-03-29
Wellington Electricity | 2013 | 2013-03-30 | 0.12408 | 0.0036368
Wellington Electricity | 2013 | 2013-03-31
Wellington Electricity | 2014 | 2013-04-01 | 0.076458 | 0.00060681
Wellington Electricity | 2014 | 2013-04-02 | 0.0030583 | 5.4613e-05
Wellington Electricity | 2014 | 2013-04-03 | 0.030583 | 0.00019114
Wellington Electricity | 2014 | 2013-04-04
Wellington Electricity | 2014 | 2013-04-05 | 0.00083133 | 6.0681e-06
Wellington Electricity | 2014 | 2013-04-06 | 0.047938 | 0.00047938
Wellington Electricity | 2014 | 2013-04-07
Wellington Electricity | 2014 | 2013-04-08 | 0.0022664 | 0.00025182
Wellington Electricity | 2014 | 2013-04-09
Wellington Electricity | 2014 | 2013-04-10 | 8.4953e-05 | 6.0681e-06
Wellington Electricity | 2014 | 2013-04-11 | 0.21204 | 0.025911
Wellington Electricity | 2014 | 2013-04-12 | 0.1894 | 0.0016566
Wellington Electricity | 2014 | 2013-04-13 | 0.63627 | 0.0057647
Wellington Electricity | 2014 | 2013-04-14
Wellington Electricity | 2014 | 2013-04-15
Wellington Electricity | 2014 | 2013-04-16 | 0.00027913 | 3.034e-06
Wellington Electricity | 2014 | 2013-04-17 | 0.26769 | 0.0023119
Wellington Electricity | 2014 | 2013-04-18
Wellington Electricity | 2014 | 2013-04-19
Wellington Electricity | 2014 | 2013-04-20
Wellington Electricity | 2014 | 2013-04-21 | 0.0024181 | 9.1021e-06
Wellington Electricity | 2014 | 2013-04-22
Wellington Electricity | 2014 | 2013-04-23 | 0.18574 | 0.0041354
Wellington Electricity | 2014 | 2013-04-24 | 0.00267 | 2.4272e-05
Wellington Electricity | 2014 | 2013-04-25
Wellington Electricity | 2014 | 2013-04-26
Wellington Electricity | 2014 | 2013-04-27 | 0.00021845 | 1.2136e-05
Wellington Electricity | 2014 | 2013-04-28 | 0.065609 | 0.0008738
Wellington Electricity | 2014 | 2013-04-29
Wellington Electricity | 2014 | 2013-04-30
Wellington Electricity | 2014 | 2013-05-01 | 0.0023483 | 0.00026093
Wellington Electricity | 2014 | 2013-05-02 | 0.017208 | 0.015643
Wellington Electricity | 2014 | 2013-05-03 | 0.23618 | 0.0041324
Wellington Electricity | 2014 | 2013-05-04
Wellington Electricity | 2014 | 2013-05-05
Wellington Electricity | 2014 | 2013-05-06 | 1.2527 | 0.0068387
Wellington Electricity | 2014 | 2013-05-07 | 0.90153 | 0.011435
Wellington Electricity | 2014 | 2013-05-08 | 0.06241 | 0.00033374
Wellington Electricity | 2014 | 2013-05-09 | 0.00034588 | 3.034e-06
Wellington Electricity | 2014 | 2013-05-10 | 0.0030867 | 5.4613e-05
Wellington Electricity | 2014 | 2013-05-11
Wellington Electricity | 2014 | 2013-05-12
Wellington Electricity | 2014 | 2013-05-13 | 0.0032161 | 0.00032161
Wellington Electricity | 2014 | 2013-05-14
Wellington Electricity | 2014 | 2013-05-15
Wellington Electricity | 2014 | 2013-05-16 | 0.0015474 | 6.0681e-06
Wellington Electricity | 2014 | 2013-05-17 | 0.00044297 | 3.034e-06
Wellington Electricity | 2014 | 2013-05-18
Wellington Electricity | 2014 | 2013-05-19
Wellington Electricity | 2014 | 2013-05-20
Wellington Electricity | 2014 | 2013-05-21
Wellington Electricity | 2014 | 2013-05-22
Wellington Electricity | 2014 | 2013-05-23
Wellington Electricity | 2014 | 2013-05-24
Wellington Electricity | 2014 | 2013-05-25
Wellington Electricity | 2014 | 2013-05-26 | 0.35706 | 0.0051215
Wellington Electricity | 2014 | 2013-05-27 | 0.00097393 | 9.1021e-06
Wellington Electricity | 2014 | 2013-05-28 | 0.016226 | 8.4953e-05
Wellington Electricity | 2014 | 2013-05-29 | 0.29563 | 0.0062683
Wellington Electricity | 2014 | 2013-05-30
Wellington Electricity | 2014 | 2013-05-31 | 0.40445 | 0.0045784
Wellington Electricity | 2014 | 2013-06-01
Wellington Electricity | 2014 | 2013-06-02
Wellington Electricity | 2014 | 2013-06-03
Wellington Electricity | 2014 | 2013-06-04 | 1.95 | 0.018113
Wellington Electricity | 2014 | 2013-06-05
Wellington Electricity | 2014 | 2013-06-06 | 0.3703 | 0.0035377
Wellington Electricity | 2014 | 2013-06-07
Wellington Electricity | 2014 | 2013-06-08
Wellington Electricity | 2014 | 2013-06-09 | 0.015868 | 0.00022148
Wellington Electricity | 2014 | 2013-06-10
Wellington Electricity | 2014 | 2013-06-11
Wellington Electricity | 2014 | 2013-06-12 | 0.016432 | 0.00019721
Wellington Electricity | 2014 | 2013-06-13 | 0.82123 | 0.0099395
Wellington Electricity | 2014 | 2013-06-14 | 0.0013228 | 6.0681e-06
Wellington Electricity | 2014 | 2013-06-15 | 0.026791 | 0.0011135
Wellington Electricity | 2014 | 2013-06-16 | 0.0017719 | 3.034e-06
Wellington Electricity | 2014 | 2013-06-17
Wellington Electricity | 2014 | 2013-06-18 | 0.36054 | 0.006511
Wellington Electricity | 2014 | 2013-06-19 | 0.12554 | 0.0017506
Wellington Electricity | 2014 | 2013-06-20 | 2.1026 | 0.031245
Wellington Electricity | 2014 | 2013-06-21 | 2.1026 | 0.031245
Wellington Electricity | 2014 | 2013-06-22 | 2.1026 | 0.012567
Wellington Electricity | 2014 | 2013-06-23 | 1.039 | 0.013295
Wellington Electricity | 2014 | 2013-06-24 | 0.015486 | 9.1021e-05
Wellington Electricity | 2014 | 2013-06-25 | 0.081482 | 1.2136e-05
Wellington Electricity | 2014 | 2013-06-26 | 0.87514 | 0.01315
Wellington Electricity | 2014 | 2013-06-27 | 0.0079747 | 0.001244
Wellington Electricity | 2014 | 2013-06-28 | 0.15222 | 0.0022755
Wellington Electricity | 2014 | 2013-06-29
Wellington Electricity | 2014 | 2013-06-30 | 0.38564 | 0.0052125
Wellington Electricity | 2014 | 2013-07-01
Wellington Electricity | 2014 | 2013-07-02 | 0.057701 | 5.1579e-05
Wellington Electricity | 2014 | 2013-07-03 | 0.0031675 | 3.6408e-05
Wellington Electricity | 2014 | 2013-07-04 | 0.0028641 | 2.4272e-05
Wellington Electricity | 2014 | 2013-07-05 | 0.46585 | 0.0011833
Wellington Electricity | 2014 | 2013-07-06 | 0.087152 | 0.001608
Wellington Electricity | 2014 | 2013-07-07 | 0.0039928 | 8.4953e-05
Wellington Electricity | 2014 | 2013-07-08 | 0.45498 | 0.0027488
Wellington Electricity | 2014 | 2013-07-09 | 0.014011 | 0.00050365
Wellington Electricity | 2014 | 2013-07-10
Wellington Electricity | 2014 | 2013-07-11 | 0.019968 | 0.00066749
Wellington Electricity | 2014 | 2013-07-12 | 0.42969 | 0.0071543
Wellington Electricity | 2014 | 2013-07-13
Wellington Electricity | 2014 | 2013-07-14 | 1.7816 | 0.018926
Wellington Electricity | 2014 | 2013-07-15 | 0.076204 | 0.0010376
Wellington Electricity | 2014 | 2013-07-16 | 0.26546 | 0.0053338
Wellington Electricity | 2014 | 2013-07-17 | 0.0017021 | 9.1021e-06
Wellington Electricity | 2014 | 2013-07-18
Wellington Electricity | 2014 | 2013-07-19
Wellington Electricity | 2014 | 2013-07-20
Wellington Electricity | 2014 | 2013-07-21 | 1.8068 | 0.031245
Wellington Electricity | 2014 | 2013-07-22 | 0.13212 | 0.001074
Wellington Electricity | 2014 | 2013-07-23
Wellington Electricity | 2014 | 2013-07-24
Wellington Electricity | 2014 | 2013-07-25
Wellington Electricity | 2014 | 2013-07-26
Wellington Electricity | 2014 | 2013-07-27 | 0.00093125 | 1.2136e-05
Wellington Electricity | 2014 | 2013-07-28 | 0.077814 | 0.001875
Wellington Electricity | 2014 | 2013-07-29
Wellington Electricity | 2014 | 2013-07-30
Wellington Electricity | 2014 | 2013-07-31
Wellington Electricity | 2014 | 2013-08-01
Wellington Electricity | 2014 | 2013-08-02
Wellington Electricity | 2014 | 2013-08-03
Wellington Electricity | 2014 | 2013-08-04
Wellington Electricity | 2014 | 2013-08-05
Wellington Electricity | 2014 | 2013-08-06
Wellington Electricity | 2014 | 2013-08-07
Wellington Electricity | 2014 | 2013-08-08 | 0.054552 | 0.00087987
Wellington Electricity | 2014 | 2013-08-09
Wellington Electricity | 2014 | 2013-08-10
Wellington Electricity | 2014 | 2013-08-11 | 0.59761 | 0.0045268
Wellington Electricity | 2014 | 2013-08-12 | 0.023107 | 0.00010316
Wellington Electricity | 2014 | 2013-08-13 | 0.0076215 | 4.8545e-05
Wellington Electricity | 2014 | 2013-08-14 | 0.032039 | 0.00048545
Wellington Electricity | 2014 | 2013-08-15 | 0.0093509 | 3.9442e-05
Wellington Electricity | 2014 | 2013-08-16 | 1.0312 | 0.031245
Wellington Electricity | 2014 | 2013-08-17
Wellington Electricity | 2014 | 2013-08-18 | 0.0025698 | 6.0681e-06
Wellington Electricity | 2014 | 2013-08-19
Wellington Electricity | 2014 | 2013-08-20
Wellington Electricity | 2014 | 2013-08-21
Wellington Electricity | 2014 | 2013-08-22 | 0.00044904 | 3.034e-06
Wellington Electricity | 2014 | 2013-08-23
Wellington Electricity | 2014 | 2013-08-24 | 0.10073 | 0.0021663
Wellington Electricity | 2014 | 2013-08-25 | 1.2593 | 0.0079401
Wellington Electricity | 2014 | 2013-08-26 | 0.32022 | 0.00076761
Wellington Electricity | 2014 | 2013-08-27 | 0.032959 | 0.0011833
Wellington Electricity | 2014 | 2013-08-28 | 0.032675 | 0.00018811
Wellington Electricity | 2014 | 2013-08-29 | 0.07847 | 0.00032768
Wellington Electricity | 2014 | 2013-08-30
Wellington Electricity | 2014 | 2013-08-31 | 0.26547 | 0.0045025
Wellington Electricity | 2014 | 2013-09-01 | 0.0022088 | 6.0681e-06
Wellington Electricity | 2014 | 2013-09-02
Wellington Electricity | 2014 | 2013-09-03 | 0.0025288 | 2.4272e-05
Wellington Electricity | 2014 | 2013-09-04 | 0.034771 | 0.00033981
Wellington Electricity | 2014 | 2013-09-05 | 0.34514 | 0.0030158
Wellington Electricity | 2014 | 2013-09-06
Wellington Electricity | 2014 | 2013-09-07 | 0.00079795 | 6.0681e-06
Wellington Electricity | 2014 | 2013-09-08 | 1.1899 | 0.0078824
Wellington Electricity | 2014 | 2013-09-09 | 0.0002761 | 3.034e-06
Wellington Electricity | 2014 | 2013-09-10 | 0.01554 | 6.0681e-06
Wellington Electricity | 2014 | 2013-09-11 | 1.9033 | 0.017309
Wellington Electricity | 2014 | 2013-09-12 | 0.17844 | 0.0017597
Wellington Electricity | 2014 | 2013-09-13
Wellington Electricity | 2014 | 2013-09-14
Wellington Electricity | 2014 | 2013-09-15
Wellington Electricity | 2014 | 2013-09-16
Wellington Electricity | 2014 | 2013-09-17 | 0.1891 | 0.0059953
Wellington Electricity | 2014 | 2013-09-18 | 0.00097089 | 6.0681e-06
Wellington Electricity | 2014 | 2013-09-19
Wellington Electricity | 2014 | 2013-09-20 | 0.91837 | 0.010516
Wellington Electricity | 2014 | 2013-09-21 | 0.17449 | 0.00059467
Wellington Electricity | 2014 | 2013-09-22 | 0.0010619 | 3.034e-06
Wellington Electricity | 2014 | 2013-09-23 | 0.0035771 | 9.1021e-06
Wellington Electricity | 2014 | 2013-09-24 | 0.0043387 | 6.6749e-05
Wellington Electricity | 2014 | 2013-09-25
Wellington Electricity | 2014 | 2013-09-26
Wellington Electricity | 2014 | 2013-09-27 | 0.0085681 | 6.0681e-06
Wellington Electricity | 2014 | 2013-09-28 | 0.20393 | 0.0022027
Wellington Electricity | 2014 | 2013-09-29
Wellington Electricity | 2014 | 2013-09-30 | 0.0040868 | 3.6408e-05
Wellington Electricity | 2014 | 2013-10-01 | 0.012256 | 0.00023665
Wellington Electricity | 2014 | 2013-10-02
Wellington Electricity | 2014 | 2013-10-03
Wellington Electricity | 2014 | 2013-10-04 | 0.00038836 | 3.034e-06
Wellington Electricity | 2014 | 2013-10-05 | 0.0014988 | 6.0681e-06
Wellington Electricity | 2014 | 2013-10-06 | 0.00061894 | 3.034e-06
Wellington Electricity | 2014 | 2013-10-07
Wellington Electricity | 2014 | 2013-10-08
Wellington Electricity | 2014 | 2013-10-09
Wellington Electricity | 2014 | 2013-10-10 | 0.0015534 | 9.1021e-06
Wellington Electricity | 2014 | 2013-10-11
Wellington Electricity | 2014 | 2013-10-12
Wellington Electricity | 2014 | 2013-10-13
Wellington Electricity | 2014 | 2013-10-14 | 2.1026 | 0.031245
Wellington Electricity | 2014 | 2013-10-15 | 0.94476 | 0.0049637
Wellington Electricity | 2014 | 2013-10-16 | 0.0073424 | 4.2477e-05
Wellington Electricity | 2014 | 2013-10-17 | 0.0010924 | 9.1021e-06
Wellington Electricity | 2014 | 2013-10-18 | 0.49505 | 0.011457
Wellington Electricity | 2014 | 2013-10-19
Wellington Electricity | 2014 | 2013-10-20
Wellington Electricity | 2014 | 2013-10-21
Wellington Electricity | 2014 | 2013-10-22 | 0.0011529 | 6.0681e-06
Wellington Electricity | 2014 | 2013-10-23
Wellington Electricity | 2014 | 2013-10-24 | 0.10044 | 0.0011954
Wellington Electricity | 2014 | 2013-10-25 | 0.028611 | 3.034e-05
Wellington Electricity | 2014 | 2013-10-26 | 1.0127 | 0.010012
Wellington Electricity | 2014 | 2013-10-27 | 0.25365 | 0.0040231
Wellington Electricity | 2014 | 2013-10-28
Wellington Electricity | 2014 | 2013-10-29 | 0.00038532 | 3.034e-06
Wellington Electricity | 2014 | 2013-10-30 | 0.00063998 | 3.9442e-05
Wellington Electricity | 2014 | 2013-10-31 | 0.051275 | 0.00084953
Wellington Electricity | 2014 | 2013-11-01 | 0.0030644 | 3.034e-05
Wellington Electricity | 2014 | 2013-11-02 | 0.0042325 | 1.517e-05
Wellington Electricity | 2014 | 2013-11-03 | 0.00062501 | 3.034e-06
Wellington Electricity | 2014 | 2013-11-04 | 0.019165 | 0.0025456
Wellington Electricity | 2014 | 2013-11-05 | 0.00028823 | 3.034e-06
Wellington Electricity | 2014 | 2013-11-06
Wellington Electricity | 2014 | 2013-11-07
Wellington Electricity | 2014 | 2013-11-08
Wellington Electricity | 2014 | 2013-11-09
Wellington Electricity | 2014 | 2013-11-10 | 0.0010498 | 6.0681e-06
Wellington Electricity | 2014 | 2013-11-11 | 0.0022209 | 6.0681e-06
Wellington Electricity | 2014 | 2013-11-12
Wellington Electricity | 2014 | 2013-11-13
Wellington Electricity | 2014 | 2013-11-14 | 0.0024394 | 1.2136e-05
Wellington Electricity | 2014 | 2013-11-15 | 0.0015292 | 5.4613e-05
Wellington Electricity | 2014 | 2013-11-16
Wellington Electricity | 2014 | 2013-11-17 | 0.0020935 | 6.0681e-06
Wellington Electricity | 2014 | 2013-11-18 | 0.11692 | 0.0034042
Wellington Electricity | 2014 | 2013-11-19
Wellington Electricity | 2014 | 2013-11-20 | 0.34672 | 0.0078885
Wellington Electricity | 2014 | 2013-11-21 | 0.7701 | 0.0078399
Wellington Electricity | 2014 | 2013-11-22
Wellington Electricity | 2014 | 2013-11-23 | 0.038305 | 0.00085256
Wellington Electricity | 2014 | 2013-11-24 | 1.3087 | 0.0072453
Wellington Electricity | 2014 | 2013-11-25 | 0.70945 | 0.0066567
Wellington Electricity | 2014 | 2013-11-26 | 0.23029 | 0.0012622
Wellington Electricity | 2014 | 2013-11-27 | 0.001162 | 9.1021e-06
Wellington Electricity | 2014 | 2013-11-28
Wellington Electricity | 2014 | 2013-11-29 | 0.94185 | 0.01375
Wellington Electricity | 2014 | 2013-11-30 | 0.94402 | 0.016584
Wellington Electricity | 2014 | 2013-12-01 | 0.001787 | 3.034e-06
Wellington Electricity | 2014 | 2013-12-02
Wellington Electricity | 2014 | 2013-12-03 | 0.0019357 | 1.8204e-05
Wellington Electricity | 2014 | 2013-12-04 | 0.2964 | 0.014054
Wellington Electricity | 2014 | 2013-12-05 | 0.0004369 | 1.2136e-05
Wellington Electricity | 2014 | 2013-12-06 | 0.031772 | 0.00029734
Wellington Electricity | 2014 | 2013-12-07
Wellington Electricity | 2014 | 2013-12-08
Wellington Electricity | 2014 | 2013-12-09 | 0.0096846 | 7.2817e-05
Wellington Electricity | 2014 | 2013-12-10 | 0.001068 | 6.6749e-05
Wellington Electricity | 2014 | 2013-12-11
Wellington Electricity | 2014 | 2013-12-12
Wellington Electricity | 2014 | 2013-12-13 | 0.0014199 | 5.4613e-05
Wellington Electricity | 2014 | 2013-12-14 | 0.076787 | 0.00092235
Wellington Electricity | 2014 | 2013-12-15 | 0.00090718 | 6.0681e-06
Wellington Electricity | 2014 | 2013-12-16 | 0.00014867 | 3.034e-06
Wellington Electricity | 2014 | 2013-12-17
Wellington Electricity | 2014 | 2013-12-18
Wellington Electricity | 2014 | 2013-12-19 | 0.14636 | 0.0016444
Wellington Electricity | 2014 | 2013-12-20
Wellington Electricity | 2014 | 2013-12-21 | 0.58578 | 0.0063593
Wellington Electricity | 2014 | 2013-12-22 | 0.24671 | 0.0034527
Wellington Electricity | 2014 | 2013-12-23 | 0.00033071 | 6.0681e-06
Wellington Electricity | 2014 | 2013-12-24 | 0.4967 | 0.0065171
Wellington Electricity | 2014 | 2013-12-25
Wellington Electricity | 2014 | 2013-12-26 | 0.0086035 | 6.0681e-05
Wellington Electricity | 2014 | 2013-12-27 | 0.49265 | 0.0081403
Wellington Electricity | 2014 | 2013-12-28 | 0.033896 | 0.00069176
Wellington Electricity | 2014 | 2013-12-29 | 0.015292 | 0.00016991
Wellington Electricity | 2014 | 2013-12-30
Wellington Electricity | 2014 | 2013-12-31 | 0.13349 | 0.0034527
Wellington Electricity | 2014 | 2014-01-01
Wellington Electricity | 2014 | 2014-01-02 | 0.35024 | 0.0076276
Wellington Electricity | 2014 | 2014-01-03 | 0.33308 | 0.0046603
Wellington Electricity | 2014 | 2014-01-04 | 0.0040959 | 0.0001517
Wellington Electricity | 2014 | 2014-01-05
Wellington Electricity | 2014 | 2014-01-06 | 0.010492 | 7.8885e-05
Wellington Electricity | 2014 | 2014-01-07
Wellington Electricity | 2014 | 2014-01-08 | 0.00048545 | 3.034e-06
Wellington Electricity | 2014 | 2014-01-09 | 0.12154 | 0.00092841
Wellington Electricity | 2014 | 2014-01-10 | 0.0014897 | 3.034e-06
Wellington Electricity | 2014 | 2014-01-11 | 0.00069783 | 6.0681e-06
Wellington Electricity | 2014 | 2014-01-12 | 0.028289 | 0.00032768
Wellington Electricity | 2014 | 2014-01-13
Wellington Electricity | 2014 | 2014-01-14
Wellington Electricity | 2014 | 2014-01-15
Wellington Electricity | 2014 | 2014-01-16
Wellington Electricity | 2014 | 2014-01-17 | 0.00050972 | 2.4272e-05
Wellington Electricity | 2014 | 2014-01-18
Wellington Electricity | 2014 | 2014-01-19 | 0.011863 | 0.00033374
Wellington Electricity | 2014 | 2014-01-20
Wellington Electricity | 2014 | 2014-01-21
Wellington Electricity | 2014 | 2014-01-22 | 0.020352 | 0.00026093
Wellington Electricity | 2014 | 2014-01-23 | 0.19384 | 0.0029127
Wellington Electricity | 2014 | 2014-01-24 | 0.0010012 | 3.034e-06
Wellington Electricity | 2014 | 2014-01-25
Wellington Electricity | 2014 | 2014-01-26 | 0.094073 | 0.00037015
Wellington Electricity | 2014 | 2014-01-27 | 0.21934 | 0.0044236
Wellington Electricity | 2014 | 2014-01-28
Wellington Electricity | 2014 | 2014-01-29 | 0.0245 | 0.0024303
Wellington Electricity | 2014 | 2014-01-30
Wellington Electricity | 2014 | 2014-01-31 | 0.06028 | 0.0012834
Wellington Electricity | 2014 | 2014-02-01 | 0.0012925 | 3.034e-06
Wellington Electricity | 2014 | 2014-02-02 | 0.0008829 | 3.034e-06
Wellington Electricity | 2014 | 2014-02-03 | 0.08079 | 0.00047634
Wellington Electricity | 2014 | 2014-02-04
Wellington Electricity | 2014 | 2014-02-05
Wellington Electricity | 2014 | 2014-02-06
Wellington Electricity | 2014 | 2014-02-07 | 0.23686 | 0.0040838
Wellington Electricity | 2014 | 2014-02-08
Wellington Electricity | 2014 | 2014-02-09 | 0.49676 | 0.0078824
Wellington Electricity | 2014 | 2014-02-10
Wellington Electricity | 2014 | 2014-02-11 | 0.0010285 | 9.1021e-06
Wellington Electricity | 2014 | 2014-02-12 | 0.52829 | 0.011645
Wellington Electricity | 2014 | 2014-02-13
Wellington Electricity | 2014 | 2014-02-14 | 0.0051336 | 5.4613e-05
Wellington Electricity | 2014 | 2014-02-15 | 0.0011312 | 3.034e-06
Wellington Electricity | 2014 | 2014-02-16 | 0.0038229 | 9.1021e-06
Wellington Electricity | 2014 | 2014-02-17 | 0.00014563 | 3.034e-06
Wellington Electricity | 2014 | 2014-02-18 | 0.075004 | 0.00045207
Wellington Electricity | 2014 | 2014-02-19 | 0.039685 | 0.00012136
Wellington Electricity | 2014 | 2014-02-20
Wellington Electricity | 2014 | 2014-02-21 | 0.045733 | 0.00071603
Wellington Electricity | 2014 | 2014-02-22 | 0.14758 | 0.0036408
Wellington Electricity | 2014 | 2014-02-23
Wellington Electricity | 2014 | 2014-02-24
Wellington Electricity | 2014 | 2014-02-25
Wellington Electricity | 2014 | 2014-02-26 | 0.0063836 | 2.4272e-05
Wellington Electricity | 2014 | 2014-02-27
Wellington Electricity | 2014 | 2014-02-28 | 0.056709 | 0.00072817
Wellington Electricity | 2014 | 2014-03-01
Wellington Electricity | 2014 | 2014-03-02 | 0.0019843 | 6.0681e-06
Wellington Electricity | 2014 | 2014-03-03 | 2.1026 | 0.031245
Wellington Electricity | 2014 | 2014-03-04 | 0.426 | 0.0083527
Wellington Electricity | 2014 | 2014-03-05 | 0.072926 | 0.00037622
Wellington Electricity | 2014 | 2014-03-06 | 0.01602 | 1.2136e-05
Wellington Electricity | 2014 | 2014-03-07
Wellington Electricity | 2014 | 2014-03-08 | 0.19721 | 0.0034527
Wellington Electricity | 2014 | 2014-03-09
Wellington Electricity | 2014 | 2014-03-10 | 0.020407 | 0.00034588
Wellington Electricity | 2014 | 2014-03-11 | 0.36579 | 0.0091415
Wellington Electricity | 2014 | 2014-03-12
Wellington Electricity | 2014 | 2014-03-13 | 0.070439 | 0.0061712
Wellington Electricity | 2014 | 2014-03-14 | 0.0024758 | 9.1021e-06
Wellington Electricity | 2014 | 2014-03-15 | 0.017193 | 0.00033374
Wellington Electricity | 2014 | 2014-03-16 | 0.21796 | 0.0010498
Wellington Electricity | 2014 | 2014-03-17 | 9.1021e-05 | 6.0681e-06
Wellington Electricity | 2014 | 2014-03-18 | 0.013319 | 3.034e-05
Wellington Electricity | 2014 | 2014-03-19 | 0.012937 | 3.034e-05
Wellington Electricity | 2014 | 2014-03-20
Wellington Electricity | 2014 | 2014-03-21 | 0.0049819 | 6.0681e-06
Wellington Electricity | 2014 | 2014-03-22
Wellington Electricity | 2014 | 2014-03-23
Wellington Electricity | 2014 | 2014-03-24 | 0.41863 | 0.0078278
Wellington Electricity | 2014 | 2014-03-25 | 0.016111 | 0.0003034
Wellington Electricity | 2014 | 2014-03-26 | 0.28568 | 0.013307
Wellington Electricity | 2014 | 2014-03-27 | 0.38556 | 0.0039018
Wellington Electricity | 2014 | 2014-03-28
Wellington Electricity | 2014 | 2014-03-29
Wellington Electricity | 2014 | 2014-03-30
Wellington Electricity | 2014 | 2014-03-31

## cc_annual (hidden)
edb | disc_yr | saidi_Nannual | saifi_Nannual
Alpine Energy | 2005 | 63.5657 | 0.94507
Alpine Energy | 2006 | 53.8413 | 0.9708
Alpine Energy | 2007 | 169.7223 | 1.3437
Alpine Energy | 2008 | 115.1195 | 1.4835
Alpine Energy | 2009 | 149.7997 | 1.3505
Alpine Energy | 2010 | 136.41 | 1.4038
Alpine Energy | 2011 | 169.9498 | 1.4928
Alpine Energy | 2012 | 126.4871 | 1.1268
Alpine Energy | 2013 | 129.0601 | 1.1676
Alpine Energy | 2014 | 214.1326 | 1.688
Aurora Energy | 2005 | 72.4537 | 1.3919
Aurora Energy | 2006 | 76.2429 | 1.4141
Aurora Energy | 2007 | 79.8032 | 1.5371
Aurora Energy | 2008 | 71.3461 | 1.3539
Aurora Energy | 2009 | 63.5571 | 1.187
Aurora Energy | 2010 | 62.4113 | 1.2627
Aurora Energy | 2011 | 91.1486 | 1.3964
Aurora Energy | 2012 | 83.2476 | 1.3947
Aurora Energy | 2013 | 63.5537 | 0.88722
Aurora Energy | 2014 | 80.8687 | 1.1219
Centralines | 2005 | 115.5608 | 3.7145
Centralines | 2006 | 117.4853 | 2.931
Centralines | 2007 | 143.3314 | 4.8422
Centralines | 2008 | 129.3031 | 3.8224
Centralines | 2009 | 157.8061 | 5.1321
Centralines | 2010 | 98.8685 | 2.1401
Centralines | 2011 | 145.7715 | 4.2785
Centralines | 2012 | 94.9005 | 3.2347
Centralines | 2013 | 82.3768 | 2.1398
Centralines | 2014 | 105.3144 | 2.9784
Eastland Network | 2005 | 214.7303 | 2.6729
Eastland Network | 2006 | 249.6385 | 3.3226
Eastland Network | 2007 | 223.367 | 3.4556
Eastland Network | 2008 | 188.743 | 3.0756
Eastland Network | 2009 | 205.8536 | 3.1856
Eastland Network | 2010 | 275.459 | 3.112
Eastland Network | 2011 | 283.8635 | 3.3219
Eastland Network | 2012 | 314.1808 | 3.0706
Eastland Network | 2013 | 237.3562 | 3.1786
Eastland Network | 2014 | 228.3018 | 2.459
Electricity Ashburton | 2005 | 93.245 | 1.0315
Electricity Ashburton | 2006 | 95.3549 | 0.92298
Electricity Ashburton | 2007 | 182.4163 | 1.8639
Electricity Ashburton | 2008 | 141.956 | 1.2949
Electricity Ashburton | 2009 | 148.589 | 1.6056
Electricity Ashburton | 2010 | 136.0916 | 1.2885
Electricity Ashburton | 2011 | 128.584 | 1.4018
Electricity Ashburton | 2012 | 130.25 | 1.3715
Electricity Ashburton | 2013 | 113.3644 | 1.3811
Electricity Ashburton | 2014 | 158.6151 | 1.7086
Electricity Invercargill | 2005 | 12.9797 | 0.25983
Electricity Invercargill | 2006 | 15.7105 | 0.49331
Electricity Invercargill | 2007 | 28.7925 | 0.70677
Electricity Invercargill | 2008 | 33.0593 | 0.7784
Electricity Invercargill | 2009 | 26.1334 | 0.71307
Electricity Invercargill | 2010 | 28.1694 | 0.77623
Electricity Invercargill | 2011 | 32.467 | 0.71948
Electricity Invercargill | 2012 | 28.2891 | 0.71255
Electricity Invercargill | 2013 | 14.9074 | 0.26889
Electricity Invercargill | 2014 | 20.2506 | 0.50649
Horizon Energy | 2005 | 211.8201 | 2.2695
Horizon Energy | 2006 | 137.5739 | 1.7428
Horizon Energy | 2007 | 145.9094 | 1.7697
Horizon Energy | 2008 | 132.2869 | 1.5575
Horizon Energy | 2009 | 121.1528 | 1.9984
Horizon Energy | 2010 | 127.4636 | 2.0065
Horizon Energy | 2011 | 148.7419 | 1.9595
Horizon Energy | 2012 | 150.9785 | 2.0207
Horizon Energy | 2013 | 175.4428 | 2.2048
Horizon Energy | 2014 | 149.8698 | 1.6982
The Lines Company | 2005 | 224.729 | 3.541
The Lines Company | 2006 | 202.1014 | 3.3611
The Lines Company | 2007 | 196.817 | 2.6491
The Lines Company | 2008 | 198.9824 | 2.5984
The Lines Company | 2009 | 232.2952 | 4.3161
The Lines Company | 2010 | 198.7894 | 2.3652
The Lines Company | 2011 | 222.5621 | 3.2374
The Lines Company | 2012 | 237.9617 | 3.3783
The Lines Company | 2013 | 151.449 | 2.0468
The Lines Company | 2014 | 222.0602 | 3.214
Nelson Electricity | 2005 | 17.1302 | 0.2515
Nelson Electricity | 2006 | 11.6586 | 0.11344
Nelson Electricity | 2007 | 13.4642 | 0.14672
Nelson Electricity | 2008 | 9.4526 | 0.11398
Nelson Electricity | 2009 | 29.1514 | 0.28276
Nelson Electricity | 2010 | 37.7584 | 0.27139
Nelson Electricity | 2011 | 8.5804 | 0.065462
Nelson Electricity | 2012 | 7.6384 | 0.10986
Nelson Electricity | 2013 | 17.9026 | 0.18028
Nelson Electricity | 2014 | 9.3191 | 0.21565
Network Tasman | 2005 | 121.9852 | 1.4655
Network Tasman | 2006 | 102.011 | 0.99343
Network Tasman | 2007 | 93.6389 | 1.3811
Network Tasman | 2008 | 120.373 | 1.2121
Network Tasman | 2009 | 101.4944 | 1.1938
Network Tasman | 2010 | 113.2022 | 1.1578
Network Tasman | 2011 | 137.7762 | 1.4356
Network Tasman | 2012 | 129.6497 | 1.2201
Network Tasman | 2013 | 105.0013 | 1.1355
Network Tasman | 2014 | 99.6487 | 1.1033
OtagoNet | 2005 | 143.6081 | 1.7372
OtagoNet | 2006 | 214.5247 | 2.5809
OtagoNet | 2007 | 307.8538 | 3.3403
OtagoNet | 2008 | 295.1192 | 2.6054
OtagoNet | 2009 | 192.5641 | 2.6023
OtagoNet | 2010 | 246.8018 | 3.2404
OtagoNet | 2011 | 188.7397 | 2.0142
OtagoNet | 2012 | 218.6451 | 2.3099
OtagoNet | 2013 | 186.5079 | 2.0982
OtagoNet | 2014 | 251.4094 | 2.7097
Powerco | 2005 | 185.0938 | 2.7219
Powerco | 2006 | 176.4544 | 2.4701
Powerco | 2007 | 164.2368 | 2.283
Powerco | 2008 | 196.4514 | 2.3885
Powerco | 2009 | 202.5157 | 2.4019
Powerco | 2010 | 186.3243 | 2.3388
Powerco | 2011 | 225.9742 | 1.8729
Powerco | 2012 | 206.4878 | 1.7602
Powerco | 2013 | 145.7771 | 1.335
Powerco | 2014 | 199.3129 | 1.4953
Top Energy | 2005 | 324.2629 | 3.6061
Top Energy | 2006 | 430.7418 | 5.0387
Top Energy | 2007 | 375.603 | 5.404
Top Energy | 2008 | 435.0954 | 5.5385
Top Energy | 2009 | 566.6052 | 8.5606
Top Energy | 2010 | 358.7234 | 4.0162
Top Energy | 2011 | 429.5248 | 4.895
Top Energy | 2012 | 408.5169 | 6.3225
Top Energy | 2013 | 323.1095 | 4.3429
Top Energy | 2014 | 401.9081 | 5.0683
Unison Networks | 2005 | 120.6126 | 2.7655
Unison Networks | 2006 | 118.8868 | 2.6728
Unison Networks | 2007 | 110.4857 | 2.0118
Unison Networks | 2008 | 98.2455 | 1.8783
Unison Networks | 2009 | 100.5391 | 1.9224
Unison Networks | 2010 | 79.0176 | 1.49
Unison Networks | 2011 | 92.9336 | 1.5908
Unison Networks | 2012 | 108.7603 | 2.1775
Unison Networks | 2013 | 71.6304 | 1.3672
Unison Networks | 2014 | 90.2598 | 1.5397
Vector Lines | 2005 | 93.8189 | 1.3708
Vector Lines | 2006 | 109.4185 | 1.6036
Vector Lines | 2007 | 112.6097 | 1.4951
Vector Lines | 2008 | 100.2208 | 1.5016
Vector Lines | 2009 | 97.14 | 1.4774
Vector Lines | 2010 | 61.9657 | 0.98453
Vector Lines | 2011 | 99.6814 | 1.1585
Vector Lines | 2012 | 86.5243 | 1.0736
Vector Lines | 2013 | 80.6139 | 0.93066
Vector Lines | 2014 | 118.3704 | 1.3184
Wellington Electricity | 2005 | 24.5988 | 0.32305
Wellington Electricity | 2006 | 29.1647 | 0.48151
Wellington Electricity | 2007 | 34.2944 | 0.63389
Wellington Electricity | 2008 | 31.3356 | 0.5059
Wellington Electricity | 2009 | 33.9158 | 0.52185
Wellington Electricity | 2010 | 39.9929 | 0.54859
Wellington Electricity | 2011 | 29.6553 | 0.51834
Wellington Electricity | 2012 | 41.1137 | 0.64138
Wellington Electricity | 2013 | 36.8478 | 0.54359
Wellington Electricity | 2014 | 53.4392 | 0.74681

## Reference dataset
Reference dataset
disc_yr | date | class | customers affected | saidi_indiv | saifi_indiv
2008 | 2007-04-03 | C | 77 | 0.034669 | 0.00024764
2008 | 2007-04-01 | C | 130 | 0.015469 | 0.00041809
2008 | 2007-04-01 | C | 97 | 0.012166 | 0.00031196
2008 | 2007-04-01 | C | 419 | 0.067968 | 0.0013475
2008 | 2007-04-01 | C | 11 | 0.0081366 | 3.5376e-05
2008 | 2007-04-02 | B | 166 | 0.10464 | 0.00053386
2008 | 2007-04-02 | B | 41 | 0.032964 | 0.00013186
2008 | 2007-04-02 | B | 11 | 0.0031485 | 3.5376e-05
2008 | 2007-04-02 | C | 71 | 0.03838 | 0.00022834
2008 | 2007-04-02 | C | 15 | 0.0032804 | 4.8241e-05
2008 | 2007-04-02 | B | 68 | 0.014215 | 0.00021869
2008 | 2007-04-02 | B | 87 | 0.016228 | 0.0002798
2008 | 2007-04-02 | B | 82 | 0.012658 | 0.00026372
2008 | 2007-04-03 | B | 20 | 0.0044381 | 6.4321e-05
2008 | 2007-04-03 | B | 43 | 0.01134 | 0.00013829
2008 | 2007-04-03 | B | 2 | 0.00072683 | 6.4321e-06
2008 | 2007-04-03 | B | 50 | 0.011256 | 0.0001608
2008 | 2007-04-03 | B | 48 | 0.046311 | 0.00015437
2008 | 2007-04-03 | C | 1584 | 0.29683 | 0.0050942
2008 | 2007-04-03 | B | 154 | 0.020801 | 0.00049527
2008 | 2007-04-02 | B | 10 | 0.0067537 | 3.216e-05
2008 | 2007-04-03 | C | 799 | 0.13208 | 0.0025696
2008 | 2007-04-04 | C | 142 | 0.080581 | 0.00045668
2008 | 2007-04-04 | C | 61 | 0.0070624 | 0.00019618
2008 | 2007-04-04 | B | 7 | 0.0058532 | 2.2512e-05
2008 | 2007-04-04 | C | 168 | 0.042908 | 0.0005403
2008 | 2007-04-05 | B | 5 | 0.0051778 | 1.608e-05
2008 | 2007-04-04 | B | 6 | 0.0058854 | 1.9296e-05
2008 | 2007-04-05 | B | 45 | 0.048482 | 0.00014472
2008 | 2007-04-05 | C | 42 | 0.0076992 | 0.00013507
2008 | 2007-04-06 | C | 11 | 0.0069692 | 3.5376e-05
2008 | 2007-04-06 | C | 14 | 0.0029266 | 4.5025e-05
2008 | 2007-04-06 | C | 540 | 0.19899 | 0.0017367
2008 | 2007-04-07 | C | 780 | 0.082163 | 0.0025085
2008 | 2007-04-03 | C | 166 | 0.036386 | 0.00053386
2008 | 2007-04-08 | C | 882 | 0.1787 | 0.0028366
2008 | 2007-04-04 | C | 6 | 0.00084904 | 1.9296e-05
2008 | 2007-04-05 | C | 49 | 0.0083681 | 0.00015759
2008 | 2007-04-07 | C | 5494 | 13.4465 | 0.017669
2008 | 2007-04-08 | C | 37 | 0.026179 | 0.00011899
2008 | 2007-04-08 | C | 468 | 0.048163 | 0.0015051
2008 | 2007-04-09 | C | 563 | 0.054358 | 0.0018106
2008 | 2007-04-09 | C | 616 | 0.083196 | 0.0019811
2008 | 2007-04-10 | C | 111 | 0.062829 | 0.00035698
2008 | 2007-04-10 | C | 46 | 0.030623 | 0.00014794
2008 | 2007-04-10 | C | 166 | 0.019219 | 0.00053386
2008 | 2007-04-10 | C | 22 | 0.0029716 | 7.0753e-05
2008 | 2007-04-11 | C | 89 | 0.017746 | 0.00028623
2008 | 2007-04-07 | C | 81 | 0.028121 | 0.0002605
2008 | 2007-04-11 | B | 4 | 0.0022255 | 1.2864e-05
2008 | 2007-04-11 | B | 4 | 0.0015694 | 1.2864e-05
2008 | 2007-04-11 | B | 1 | 0.00062391 | 0
2008 | 2007-04-11 | B | 46 | 0.028256 | 0.00014794
2008 | 2007-04-11 | B | 18 | 0.015804 | 5.7889e-05
2008 | 2007-04-11 | B | 32 | 0.033344 | 0.00010291
2008 | 2007-04-11 | C | 99 | 0.046803 | 0.00031839
2008 | 2007-04-12 | B | 20 | 0.0078471 | 6.4321e-05
2008 | 2007-04-12 | B | 66 | 0.058371 | 0.00021226
2008 | 2007-04-12 | C | 474 | 0.082421 | 0.0015244
2008 | 2007-04-12 | B | 45 | 0.03401 | 0.00014472
2008 | 2007-04-12 | B | 42 | 0.038091 | 0.00013507
2008 | 2007-04-12 | C | 477 | 0.094375 | 0.0015341
2008 | 2007-04-12 | C | 21 | 0.013372 | 6.7537e-05
2008 | 2007-04-04 | B | 18 | 0.017598 | 5.7889e-05
2008 | 2007-04-12 | C | 34 | 0.0053579 | 0.00010935
2008 | 2007-04-12 | C | 219 | 0.094095 | 0.00070431
2008 | 2007-04-12 | C | 113 | 0.0447 | 0.00036341
2008 | 2007-04-12 | C | 431 | 0.015247 | 0.0013861
2008 | 2007-04-12 | C | 364 | 0.098025 | 0.0011706
2008 | 2007-04-12 | C | 93 | 0.016151 | 0.00029909
2008 | 2007-04-13 | C | 5 | 0.0017688 | 1.608e-05
2008 | 2007-04-13 | C | 4 | 0.00059175 | 1.2864e-05
2008 | 2007-04-13 | C | 4 | 0.00081044 | 1.2864e-05
2008 | 2007-04-13 | C | 50 | 0.01106 | 0.0001608
2008 | 2007-04-13 | B | 283 | 0.0054608 | 0.00091014
2008 | 2007-04-13 | C | 597 | 0.28542 | 0.00192
2008 | 2007-04-13 | C | 239 | 0.091165 | 0.00076863
2008 | 2007-04-13 | C | 1471 | 0.62284 | 0.0047308
2008 | 2007-04-13 | C | 292 | 0.03719 | 0.00093908
2008 | 2007-04-13 | C | 561 | 0.075252 | 0.0018042
2008 | 2007-04-13 | C | 29 | 0.0032643 | 9.3265e-05
2008 | 2007-04-13 | C | 66 | 0.0072168 | 0.00021226
2008 | 2007-04-14 | C | 597 | 0.12508 | 0.00192
2008 | 2007-04-14 | C | 163 | 0.007339 | 0.00052422
2008 | 2007-04-14 | C | 429 | 0.089853 | 0.0013797
2008 | 2007-04-13 | C | 784 | 0.45269 | 0.0025214
2008 | 2007-04-14 | C | 21 | 0.0038496 | 6.7537e-05
2008 | 2007-04-09 | C | 2855 | 0.18892 | 0.0091818
2008 | 2007-04-09 | C | 5851 | 0.075268 | 0.018817
2008 | 2007-04-14 | C | 186 | 0.011964 | 0.00059818
2008 | 2007-04-15 | C | 10 | 0.00041809 | 3.216e-05
2008 | 2007-04-15 | C | 207 | 0.038612 | 0.00066572
2008 | 2007-04-15 | C | 223 | 0.16208 | 0.00071718
2008 | 2007-04-15 | C | 49 | 0.0017431 | 0.00015759
2008 | 2007-04-16 | B | 10 | 0.0056924 | 3.216e-05
2008 | 2007-04-13 | B | 16 | 0.013739 | 5.1457e-05
2008 | 2007-04-16 | B | 10 | 0.0067859 | 3.216e-05
2008 | 2007-04-16 | C | 1 | 0.00012221 | 0
2008 | 2007-04-16 | C | 21 | 0.0058757 | 6.7537e-05
2008 | 2007-04-16 | C | 1750 | 0.022512 | 0.0056281
2008 | 2007-04-16 | C | 576 | 0.15005 | 0.0018524
2008 | 2007-04-17 | C | 64 | 0.01379 | 0.00020583
2008 | 2007-04-17 | C | 222 | 0.035505 | 0.00071396
2008 | 2007-04-17 | B | 3 | 0.00090692 | 9.6481e-06
2008 | 2007-04-17 | B | 2 | 0.0016981 | 6.4321e-06
2008 | 2007-04-17 | B | 2 | 0.00079115 | 6.4321e-06
2008 | 2007-04-17 | B | 21 | 0.026137 | 6.7537e-05
2008 | 2007-04-17 | B | 32 | 0.031492 | 0.00010291
2008 | 2007-04-18 | B | 35 | 0.025551 | 0.00011256
2008 | 2007-04-18 | C | 1735 | 0.15624 | 0.0055798
2008 | 2007-04-18 | C | 110 | 0.022641 | 0.00035376
2008 | 2007-04-18 | C | 407 | 0.22764 | 0.0013089
2008 | 2007-04-19 | C | 22 | 0.005165 | 7.0753e-05
2008 | 2007-04-18 | C | 1019 | 0.52669 | 0.0032771
2008 | 2007-04-19 | B | 8 | 0.0014665 | 2.5728e-05
2008 | 2007-04-17 | B | 8 | 0.0025214 | 2.5728e-05
2008 | 2007-04-19 | B | 4 | 0.0045925 | 1.2864e-05
2008 | 2007-04-20 | B | 25 | 0.012462 | 8.0401e-05
2008 | 2007-04-20 | B | 25 | 0.012462 | 8.0401e-05
2008 | 2007-04-20 | B | 1 | 0.00081366 | 0
2008 | 2007-04-20 | B | 1 | 0.00071718 | 0
2008 | 2007-04-20 | B | 1 | 0.00039557 | 0
2008 | 2007-04-20 | B | 38 | 0.027864 | 0.00012221
2008 | 2007-04-21 | B | 1 | 0.00050492 | 0
2008 | 2007-04-21 | C | 711 | 0.099974 | 0.0022866
2008 | 2007-04-22 | C | 1134 | 1.2125 | 0.003647
2008 | 2007-04-23 | C | 301 | 0.05202 | 0.00096803
2008 | 2007-04-23 | B | 108 | 0.049669 | 0.00034733
2008 | 2007-04-23 | B | 13 | 0.0061459 | 4.1809e-05
2008 | 2007-04-23 | B | 46 | 0.036837 | 0.00014794
2008 | 2007-04-23 | B | 7 | 0.0014183 | 2.2512e-05
2008 | 2007-04-23 | B | 17 | 0.019518 | 5.4673e-05
2008 | 2007-04-23 | B | 5 | 0.0031356 | 1.608e-05
2008 | 2007-04-23 | B | 7 | 0.0049977 | 2.2512e-05
2008 | 2007-04-23 | C | 94 | 0.019444 | 0.00030231
2008 | 2007-04-23 | C | 74 | 0.018563 | 0.00023799
2008 | 2007-04-23 | C | 26 | 0.0026757 | 8.3617e-05
2008 | 2007-04-23 | B | 1 | 6.7537e-05 | 0
2008 | 2007-04-23 | B | 2 | 9.0049e-05 | 6.4321e-06
2008 | 2007-04-23 | B | 31 | 0.0018943 | 9.9697e-05
2008 | 2007-04-24 | B | 37 | 0.0028558 | 0.00011899
2008 | 2007-04-24 | B | 14 | 0.0025664 | 4.5025e-05
2008 | 2007-04-23 | B | 16 | 0.0088506 | 5.1457e-05
2008 | 2007-04-24 | C | 17 | 0.0021869 | 5.4673e-05
2008 | 2007-04-24 | C | 877 | 0.014102 | 0.0028205
2008 | 2007-04-24 | B | 81 | 0.059394 | 0.0002605
2008 | 2007-04-24 | B | 29 | 0.027607 | 9.3265e-05
2008 | 2007-04-25 | C | 455 | 0.046874 | 0.0014633
2008 | 2007-04-25 | C | 22 | 0.0084196 | 7.0753e-05
2008 | 2007-04-25 | C | 81 | 0.015109 | 0.0002605
2008 | 2007-04-26 | B | 1 | 0.0011481 | 0
2008 | 2007-04-26 | B | 31 | 0.035592 | 9.9697e-05
2008 | 2007-04-26 | B | 1 | 0.00082652 | 0
2008 | 2007-04-26 | B | 4 | 0.002277 | 1.2864e-05
2008 | 2007-04-26 | B | 17 | 0.014598 | 5.4673e-05
2008 | 2007-04-26 | C | 174 | 0.033576 | 0.00055959
2008 | 2007-04-26 | C | 50 | 0.0051457 | 0.0001608
2008 | 2007-04-27 | C | 29 | 0.012684 | 9.3265e-05
2008 | 2007-04-27 | B | 16 | 0.017032 | 5.1457e-05
2008 | 2007-04-27 | B | 28 | 0.031157 | 9.0049e-05
2008 | 2007-04-18 | B | 71 | 0.057541 | 0.00022834
2008 | 2007-04-24 | B | 29 | 0.025928 | 9.3265e-05
2008 | 2007-04-28 | C | 20 | 0.0044381 | 6.4321e-05
2008 | 2007-04-28 | C | 42 | 0.0099955 | 0.00013507
2008 | 2007-04-28 | C | 21 | 0.0027015 | 6.7537e-05
2008 | 2007-04-28 | C | 99 | 0.0064932 | 0.00031839
2008 | 2007-04-27 | C | 3 | 0.0010324 | 9.6481e-06
2008 | 2007-04-27 | C | 5 | 0.0023156 | 1.608e-05
2008 | 2007-04-28 | C | 127 | 0.17726 | 0.00040844
2008 | 2007-04-28 | C | 329 | 0.24859 | 0.0010581
2008 | 2007-04-27 | C | 315 | 0.047353 | 0.0010131
2008 | 2007-04-27 | C | 1331 | 0.21642 | 0.0042806
2008 | 2007-04-28 | C | 83 | 0.035476 | 0.00026693
2008 | 2007-04-29 | C | 71 | 0.017582 | 0.00022834
2008 | 2007-04-28 | C | 1 | 0.00085868 | 0
2008 | 2007-04-30 | C | 483 | 0.020194 | 0.0015533
2008 | 2007-04-30 | C | 207 | 0.0053258 | 0.00066572
2008 | 2007-04-30 | B | 30 | 0.017077 | 9.6481e-05
2008 | 2007-04-30 | B | 5 | 0.0019618 | 1.608e-05
2008 | 2007-04-30 | B | 10 | 0.0095517 | 3.216e-05
2008 | 2007-04-30 | B | 13 | 0.013546 | 4.1809e-05
2008 | 2007-05-01 | B | 41 | 0.030195 | 0.00013186
2008 | 2007-05-01 | B | 71 | 0.017582 | 0.00022834
2008 | 2007-05-01 | B | 144 | 0.10744 | 0.00046311
2008 | 2007-05-01 | B | 31 | 0.028912 | 9.9697e-05
2008 | 2007-05-01 | C | 18 | 0.0079887 | 5.7889e-05
2008 | 2007-04-23 | B | 20 | 0.010098 | 6.4321e-05
2008 | 2007-05-02 | C | 10 | 0.00086833 | 3.216e-05
2008 | 2007-05-02 | C | 474 | 0.028964 | 0.0015244
2008 | 2007-05-03 | C | 319 | 0.10855 | 0.0010259
2008 | 2007-05-02 | B | 1 | 0.0012928 | 0
2008 | 2007-05-01 | B | 1 | 0.0010613 | 0
2008 | 2007-05-03 | C | 807 | 0.28465 | 0.0025953
2008 | 2007-05-03 | C | 40 | 0.014537 | 0.00012864
2008 | 2007-05-03 | C | 1067 | 0.075493 | 0.0034315
2008 | 2007-05-02 | B | 5 | 0.0047276 | 1.608e-05
2008 | 2007-05-03 | B | 16 | 0.0011835 | 5.1457e-05
2008 | 2007-05-03 | B | 31 | 0.030408 | 9.9697e-05
2008 | 2007-05-04 | C | 164 | 0.0084389 | 0.00052743
2008 | 2007-05-04 | C | 329 | 0.010925 | 0.0010581
2008 | 2007-05-04 | C | 542 | 0.041834 | 0.0017431
2008 | 2007-05-04 | B | 12 | 0.004361 | 3.8593e-05
2008 | 2007-05-03 | B | 102 | 0.067247 | 0.00032804
2008 | 2007-05-04 | B | 3 | 0.0022866 | 9.6481e-06
2008 | 2007-05-04 | B | 39 | 0.03838 | 0.00012543
2008 | 2007-05-04 | B | 1 | 0.00063678 | 0
2008 | 2007-05-04 | B | 3 | 0.0040233 | 9.6481e-06
2008 | 2007-05-04 | C | 51 | 0.019518 | 0.00016402
2008 | 2007-05-04 | C | 1384 | 0.11128 | 0.004451
2008 | 2007-05-05 | C | 475 | 0.0091657 | 0.0015276
2008 | 2007-05-05 | B | 1 | 0.00085868 | 0
2008 | 2007-05-05 | C | 780 | 0.39306 | 0.0025085
2008 | 2007-05-06 | B | 2 | 0.0013314 | 6.4321e-06
2008 | 2007-05-06 | B | 7 | 0.0028366 | 2.2512e-05
2008 | 2007-05-06 | C | 40 | 0.010549 | 0.00012864
2008 | 2007-05-06 | C | 8 | 0.0023156 | 2.5728e-05
2008 | 2007-05-06 | C | 1 | 0.00054673 | 0
2008 | 2007-05-07 | C | 1694 | 0.3869 | 0.005448
2008 | 2007-05-07 | C | 11 | 0.00329 | 3.5376e-05
2008 | 2007-05-07 | C | 2 | 0.00079115 | 6.4321e-06
2008 | 2007-05-07 | B | 25 | 0.0012864 | 8.0401e-05
2008 | 2007-05-07 | B | 49 | 0.046173 | 0.00015759
2008 | 2007-05-07 | B | 1 | 0.00029588 | 0
2008 | 2007-05-07 | B | 6 | 0.0033383 | 1.9296e-05
2008 | 2007-05-07 | C | 1 | 0.00056924 | 0
2008 | 2007-05-07 | C | 376 | 0.033859 | 0.0012092
2008 | 2007-05-07 | C | 395 | 0.07622 | 0.0012703
2008 | 2007-05-07 | B | 668 | 0.096674 | 0.0021483
2008 | 2007-05-08 | B | 527 | 0.047456 | 0.0016949
2008 | 2007-05-08 | B | 668 | 0.06445 | 0.0021483
2008 | 2007-05-08 | B | 911 | 0.12305 | 0.0029298
2008 | 2007-05-07 | B | 8 | 0.0082845 | 2.5728e-05
2008 | 2007-05-08 | C | 16 | 0.0016466 | 5.1457e-05
2008 | 2007-05-08 | B | 47 | 0.016476 | 0.00015115
2008 | 2007-05-08 | B | 5 | 0.0055798 | 1.608e-05
2008 | 2007-05-08 | B | 31 | 0.026121 | 9.9697e-05
2008 | 2007-05-08 | B | 3 | 0.0022094 | 9.6481e-06
2008 | 2007-05-08 | B | 15 | 0.0099858 | 4.8241e-05
2008 | 2007-05-08 | B | 1 | 6.7537e-05 | 0
2008 | 2007-05-09 | C | 311 | 0.017003 | 0.0010002
2008 | 2007-05-09 | C | 190 | 0.010999 | 0.00061105
2008 | 2007-05-09 | B | 55 | 0.019634 | 0.00017688
2008 | 2007-05-09 | B | 41 | 0.022284 | 0.00013186
2008 | 2007-05-10 | C | 47 | 0.0083135 | 0.00015115
2008 | 2007-05-10 | B | 63 | 0.030999 | 0.00020261
2008 | 2007-05-10 | B | 31 | 0.0329 | 9.9697e-05
2008 | 2007-05-10 | B | 1 | 0.00020583 | 0
2008 | 2007-05-10 | B | 4 | 0.0038207 | 1.2864e-05
2008 | 2007-05-10 | B | 6 | 0.0034926 | 1.9296e-05
2008 | 2007-05-10 | C | 192 | 0.030257 | 0.00061748
2008 | 2007-05-10 | C | 984 | 0.16219 | 0.0031646
2008 | 2007-05-11 | C | 893 | 0.0086158 | 0.0028719
2008 | 2007-05-11 | C | 160 | 0.0015437 | 0.00051457
2008 | 2007-05-11 | B | 13 | 0.012083 | 4.1809e-05
2008 | 2007-05-12 | C | 179 | 0.026548 | 0.00057567
2008 | 2007-05-11 | B | 23 | 0.03913 | 7.3969e-05
2008 | 2007-05-12 | C | 2559 | 0.02469 | 0.0082299
2008 | 2007-05-12 | C | 177 | 0.020309 | 0.00056924
2008 | 2007-05-12 | B | 6 | 0.0070045 | 1.9296e-05
2008 | 2007-05-13 | C | 865 | 0.033383 | 0.0027819
2008 | 2007-05-14 | B | 12 | 0.0086061 | 3.8593e-05
2008 | 2007-05-14 | C | 451 | 0.15767 | 0.0014504
2008 | 2007-05-14 | C | 2 | 0.00016723 | 6.4321e-06
2008 | 2007-05-14 | B | 24 | 0.02524 | 7.7185e-05
2008 | 2007-05-14 | B | 10 | 0.013411 | 3.216e-05
2008 | 2007-05-15 | C | 272 | 0.097536 | 0.00087476
2008 | 2007-05-15 | C | 542 | 0.052293 | 0.0017431
2008 | 2007-05-15 | C | 3467 | 0.046945 | 0.01115
2008 | 2007-05-15 | B | 17 | 0.0096771 | 5.4673e-05
2008 | 2007-05-15 | B | 6 | 0.005731 | 1.9296e-05
2008 | 2007-05-15 | B | 25 | 0.019377 | 8.0401e-05
2008 | 2007-05-15 | B | 48 | 0.048009 | 0.00015437
2008 | 2007-05-15 | C | 739 | 0.13642 | 0.0023767
2008 | 2007-05-16 | B | 39 | 0.0222 | 0.00012543
2008 | 2007-05-16 | B | 29 | 0.033296 | 9.3265e-05
2008 | 2007-05-16 | B | 24 | 0.02524 | 7.7185e-05
2008 | 2007-05-16 | B | 5 | 0.0057406 | 1.608e-05
2008 | 2007-05-16 | B | 23 | 0.026407 | 7.3969e-05
2008 | 2007-05-16 | B | 148 | 0.066833 | 0.00047597
2008 | 2007-05-16 | B | 13 | 0.00079436 | 4.1809e-05
2008 | 2007-05-17 | B | 18 | 0.010999 | 5.7889e-05
2008 | 2007-05-17 | B | 3 | 0.0031067 | 9.6481e-06
2008 | 2007-05-17 | C | 5 | 0.0011417 | 1.608e-05
2008 | 2007-05-17 | B | 62 | 0.059021 | 0.00019939
2008 | 2007-05-17 | B | 30 | 0.025182 | 9.6481e-05
2008 | 2007-05-17 | B | 21 | 0.023368 | 6.7537e-05
2008 | 2007-05-17 | C | 619 | 0.022155 | 0.0019907
2008 | 2007-05-17 | C | 622 | 0.060185 | 0.0020004
2008 | 2007-05-17 | B | 2 | 0.00047597 | 6.4321e-06
2008 | 2007-05-17 | C | 1127 | 0.2877 | 0.0036245
2008 | 2007-05-18 | B | 9 | 0.0068598 | 2.8944e-05
2008 | 2007-05-18 | B | 5 | 0.0031035 | 1.608e-05
2008 | 2007-05-18 | B | 1 | 0.00012221 | 0
2008 | 2007-05-18 | B | 63 | 0.028163 | 0.00020261
2008 | 2007-05-18 | C | 88 | 0.031131 | 0.00028301
2008 | 2007-05-18 | C | 447 | 0.18401 | 0.0014376
2008 | 2007-05-18 | C | 1 | 0.0022223 | 0
2008 | 2007-05-18 | C | 10 | 0.00096481 | 3.216e-05
2008 | 2007-05-19 | C | 1752 | 0.095787 | 0.0056345
2008 | 2007-05-19 | C | 64 | 0.012967 | 0.00020583
2008 | 2007-05-19 | C | 3554 | 0.057149 | 0.01143
2008 | 2007-05-20 | B | 85 | 0.025149 | 0.00027336
2008 | 2007-05-20 | B | 31 | 0.013459 | 9.9697e-05
2008 | 2007-05-20 | C | 172 | 0.030356 | 0.00055316
2008 | 2007-05-21 | C | 94 | 0.027086 | 0.00030231
2008 | 2007-05-21 | C | 42 | 0.0041873 | 0.00013507
2008 | 2007-05-21 | C | 138 | 0.031765 | 0.00044381
2008 | 2007-05-21 | B | 5 | 0.0047597 | 1.608e-05
2008 | 2007-05-21 | C | 7 | 0.0013733 | 2.2512e-05
2008 | 2007-05-21 | B | 7 | 0.0085772 | 2.2512e-05
2008 | 2007-05-21 | C | 226 | 0.033405 | 0.00072683
2008 | 2007-05-22 | C | 25 | 0.0030552 | 8.0401e-05
2008 | 2007-05-21 | C | 5 | 0.00033768 | 1.608e-05
2008 | 2007-05-22 | B | 40 | 0.025857 | 0.00012864
2008 | 2007-05-22 | C | 30 | 0.002412 | 9.6481e-05
2008 | 2007-05-22 | B | 10 | 0.0049205 | 3.216e-05
2008 | 2007-05-22 | B | 55 | 0.056072 | 0.00017688
2008 | 2007-05-22 | B | 1 | 0.0011288 | 0
2008 | 2007-05-22 | C | 585 | 0.079317 | 0.0018814
2008 | 2007-05-22 | C | 585 | 0.038544 | 0.0018814
2008 | 2007-05-22 | C | 585 | 0.035746 | 0.0018814
2008 | 2007-05-22 | B | 2 | 0.0011385 | 6.4321e-06
2008 | 2007-05-22 | C | 389 | 0.06005 | 0.001251
2008 | 2007-05-23 | B | 51 | 0.016402 | 0.00016402
2008 | 2007-05-23 | C | 50 | 0.0078793 | 0.0001608
2008 | 2007-05-23 | C | 139 | 0.068971 | 0.00044703
2008 | 2007-05-23 | C | 3554 | 0.02286 | 0.01143
2008 | 2007-05-23 | B | 20 | 0.014279 | 6.4321e-05
2008 | 2007-05-23 | C | 352 | 0.050119 | 0.001132
2008 | 2007-05-23 | C | 633 | 0.12622 | 0.0020358
2008 | 2007-05-23 | B | 87 | 0.042809 | 0.0002798
2008 | 2007-05-24 | B | 17 | 0.017113 | 5.4673e-05
2008 | 2007-05-24 | B | 8 | 0.0086447 | 2.5728e-05
2008 | 2007-05-24 | B | 228 | 0.2955 | 0.00073326
2008 | 2007-05-24 | C | 9 | 0.00060783 | 2.8944e-05
2008 | 2007-05-24 | C | 7 | 0.00074291 | 2.2512e-05
2008 | 2007-05-25 | B | 155 | 0.013459 | 0.00049849
2008 | 2007-05-25 | C | 207 | 0.021303 | 0.00066572
2008 | 2007-05-25 | B | 3 | 0.0011095 | 9.6481e-06
2008 | 2007-05-25 | C | 1275 | 0.036904 | 0.0041005
2008 | 2007-05-25 | C | 972 | 0.028134 | 0.003126
2008 | 2007-05-25 | C | 915 | 0.11279 | 0.0029427
2008 | 2007-05-26 | B | 93 | 0.059519 | 0.00029909
2008 | 2007-05-26 | C | 85 | 0.018042 | 0.00027336
2008 | 2007-05-27 | C | 10 | 0.00083617 | 3.216e-05
2008 | 2007-05-27 | C | 109 | 0.044272 | 0.00035055
2008 | 2007-05-27 | C | 23 | 0.01398 | 7.3969e-05
2008 | 2007-05-27 | C | 65 | 0.0073165 | 0.00020904
2008 | 2007-05-27 | C | 90 | 0.036084 | 0.00028944
2008 | 2007-05-28 | B | 8 | 0.0090564 | 2.5728e-05
2008 | 2007-05-28 | C | 228 | 0.037396 | 0.00073326
2008 | 2007-05-29 | B | 53 | 0.034772 | 0.00017045
2008 | 2007-05-28 | C | 88 | 0.095285 | 0.00028301
2008 | 2007-05-29 | C | 1 | 0.00044381 | 0
2008 | 2007-05-28 | C | 1 | 0.0036824 | 0
2008 | 2007-05-29 | B | 56 | 0.042683 | 0.0001801
2008 | 2007-05-29 | B | 36 | 0.043995 | 0.00011578
2008 | 2007-05-29 | B | 24 | 0.0090307 | 7.7185e-05
2008 | 2007-05-29 | C | 39 | 0.0038882 | 0.00012543
2008 | 2007-05-29 | B | 5 | 0.0036663 | 1.608e-05
2008 | 2007-05-30 | B | 53 | 0.030852 | 0.00017045
2008 | 2007-05-29 | C | 87 | 0.0075545 | 0.0002798
2008 | 2007-05-30 | B | 5 | 0.0045185 | 1.608e-05
2008 | 2007-05-30 | B | 88 | 0.093677 | 0.00028301
2008 | 2007-05-30 | B | 51 | 0.009349 | 0.00016402
2008 | 2007-05-30 | B | 2 | 0.00078471 | 6.4321e-06
2008 | 2007-05-30 | B | 100 | 0.092944 | 0.0003216
2008 | 2007-05-30 | B | 1 | 0.00060783 | 0
2008 | 2007-05-30 | B | 31 | 0.024127 | 9.9697e-05
2008 | 2007-05-30 | C | 18 | 0.0089728 | 5.7889e-05
2008 | 2007-05-31 | B | 5 | 0.0043738 | 1.608e-05
2008 | 2007-05-31 | B | 33 | 0.00042452 | 0.00010613
2008 | 2007-05-31 | B | 21 | 0.016884 | 6.7537e-05
2008 | 2007-05-31 | B | 15 | 0.0074773 | 4.8241e-05
2008 | 2007-05-31 | B | 28 | 0.014948 | 9.0049e-05
2008 | 2007-05-31 | B | 26 | 0.028597 | 8.3617e-05
2008 | 2007-05-31 | C | 103 | 0.010269 | 0.00033125
2008 | 2007-05-31 | C | 58 | 0.0067151 | 0.00018653
2008 | 2007-06-01 | B | 21 | 0.012697 | 6.7537e-05
2008 | 2007-06-01 | B | 3 | 0.0021515 | 9.6481e-06
2008 | 2007-06-01 | B | 5 | 0.0034894 | 1.608e-05
2008 | 2007-06-01 | C | 120 | 0.038232 | 0.00038593
2008 | 2007-06-01 | B | 35 | 0.043561 | 0.00011256
2008 | 2007-06-01 | C | 123 | 0.015427 | 0.00039557
2008 | 2007-06-01 | C | 74 | 0.012375 | 0.00023799
2008 | 2007-06-02 | C | 761 | 0.082028 | 0.0024474
2008 | 2007-06-02 | C | 3 | 0.00094552 | 9.6481e-06
2008 | 2007-06-03 | C | 38 | 0.0091657 | 0.00012221
2008 | 2007-06-03 | C | 195 | 0.0066411 | 0.00062713
2008 | 2007-06-03 | C | 90 | 0.11607 | 0.00028944
2008 | 2007-06-02 | C | 159 | 0.055557 | 0.00051135
2008 | 2007-06-03 | C | 45 | 0.0057889 | 0.00014472
2008 | 2007-06-03 | C | 5 | 0.0017527 | 1.608e-05
2008 | 2007-06-03 | C | 1329 | 0.25927 | 0.0042741
2008 | 2007-06-02 | C | 103 | 0.18517 | 0.00033125
2008 | 2007-06-03 | C | 590 | 0.25202 | 0.0018975
2008 | 2007-06-04 | C | 225 | 0.089647 | 0.00072361
2008 | 2007-06-04 | C | 24 | 0.0040908 | 7.7185e-05
2008 | 2007-06-04 | C | 219 | 0.021998 | 0.00070431
2008 | 2007-06-04 | C | 61 | 0.011073 | 0.00019618
2008 | 2007-06-05 | C | 142 | 0.050347 | 0.00045668
2008 | 2007-06-05 | B | 32 | 0.0077185 | 0.00010291
2008 | 2007-06-05 | B | 34 | 0.036303 | 0.00010935
2008 | 2007-06-05 | B | 4 | 0.0026243 | 1.2864e-05
2008 | 2007-06-05 | B | 25 | 0.026211 | 8.0401e-05
2008 | 2007-06-05 | C | 89 | 0.031311 | 0.00028623
2008 | 2007-06-05 | C | 72 | 0.016209 | 0.00023156
2008 | 2007-06-06 | B | 14 | 0.0079694 | 4.5025e-05
2008 | 2007-06-05 | C | 14 | 0.038136 | 4.5025e-05
2008 | 2007-06-06 | B | 12 | 0.0091464 | 3.8593e-05
2008 | 2007-06-07 | C | 8 | 0.00041165 | 2.5728e-05
2008 | 2007-06-07 | C | 18 | 0.0050363 | 5.7889e-05
2008 | 2007-06-07 | C | 741 | 0.15022 | 0.0023831
2008 | 2007-06-07 | B | 80 | 0.051714 | 0.00025728
2008 | 2007-06-06 | C | 72 | 0.14727 | 0.00023156
2008 | 2007-06-07 | C | 87 | 0.047565 | 0.0002798
2008 | 2007-06-07 | B | 3 | 0.0019296 | 9.6481e-06
2008 | 2007-06-07 | B | 40 | 0.042194 | 0.00012864
2008 | 2007-06-07 | B | 11 | 0.013691 | 3.5376e-05
2008 | 2007-06-07 | C | 15 | 0.0034251 | 4.8241e-05
2008 | 2007-06-07 | C | 54 | 0.0013893 | 0.00017367
2008 | 2007-06-07 | C | 82 | 0.088338 | 0.00026372
2008 | 2007-06-07 | B | 2 | 0.0014729 | 6.4321e-06
2008 | 2007-06-07 | C | 16 | 0.0013379 | 5.1457e-05
2008 | 2007-06-08 | C | 112 | 0.13075 | 0.0003602
2008 | 2007-06-08 | C | 1091 | 0.16163 | 0.0035087
2008 | 2007-06-08 | C | 1 | 0.00010291 | 0
2008 | 2007-06-08 | C | 18 | 0.0024892 | 5.7889e-05
2008 | 2007-06-08 | C | 113 | 0.036341 | 0.00036341
2008 | 2007-06-08 | B | 23 | 0.027812 | 7.3969e-05
2008 | 2007-06-08 | C | 16 | 0.001801 | 5.1457e-05
2008 | 2007-06-08 | C | 283 | 0.079285 | 0.00091014
2008 | 2007-06-08 | C | 541 | 0.10687 | 0.0017399
2008 | 2007-06-09 | C | 34 | 0.025915 | 0.00010935
2008 | 2007-06-09 | C | 335 | 0.08116 | 0.0010774
2008 | 2007-06-09 | C | 333 | 0.13042 | 0.0010709
2008 | 2007-06-09 | C | 126 | 0.067453 | 0.00040522
2008 | 2007-06-10 | C | 276 | 0.042387 | 0.00088763
2008 | 2007-06-10 | C | 1 | 0.0006818 | 0
2008 | 2007-06-10 | B | 58 | 0.063793 | 0.00018653
2008 | 2007-06-10 | C | 37 | 0.014874 | 0.00011899
2008 | 2007-06-10 | C | 155 | 0.15652 | 0.00049849
2008 | 2007-06-10 | C | 13 | 0.00091979 | 4.1809e-05
2008 | 2007-06-09 | C | 156 | 0.1367 | 0.0005017
2008 | 2007-06-10 | C | 279 | 0.12656 | 0.00089728
2008 | 2007-06-11 | C | 21 | 0.0041198 | 6.7537e-05
2008 | 2007-06-11 | C | 222 | 0.039988 | 0.00071396
2008 | 2007-06-11 | C | 480 | 0.17598 | 0.0015437
2008 | 2007-06-11 | B | 16 | 0.01837 | 5.1457e-05
2008 | 2007-06-11 | C | 89 | 0.020737 | 0.00028623
2008 | 2007-06-11 | C | 38 | 0.02102 | 0.00012221
2008 | 2007-06-11 | C | 28 | 0.012877 | 9.0049e-05
2008 | 2007-06-12 | B | 15 | 0.011433 | 4.8241e-05
2008 | 2007-06-12 | B | 2 | 0.001846 | 6.4321e-06
2008 | 2007-06-12 | B | 17 | 0.015144 | 5.4673e-05
2008 | 2007-06-12 | B | 1 | 0.0007622 | 0
2008 | 2007-06-12 | B | 26 | 0.024834 | 8.3617e-05
2008 | 2007-06-13 | B | 205 | 0.12395 | 0.00065929
2008 | 2007-06-13 | B | 5 | 0.0026693 | 1.608e-05
2008 | 2007-06-13 | B | 26 | 0.0056023 | 8.3617e-05
2008 | 2007-06-13 | B | 26 | 0.021573 | 8.3617e-05
2008 | 2007-06-13 | C | 43 | 0.0040104 | 0.00013829
2008 | 2007-06-14 | C | 805 | 0.018122 | 0.0025889
2008 | 2007-06-14 | C | 8926 | 0.92992 | 0.028706
2008 | 2007-06-14 | C | 447 | 0.078147 | 0.0014376
2008 | 2007-06-14 | B | 183 | 0.087103 | 0.00058854
2008 | 2007-06-14 | C | 28 | 0.0021612 | 9.0049e-05
2008 | 2007-06-14 | B | 15 | 0.010179 | 4.8241e-05
2008 | 2007-06-14 | C | 742 | 0.059188 | 0.0023863
2008 | 2007-06-14 | B | 5201 | 0.10036 | 0.016727
2008 | 2007-06-14 | B | 19 | 0.0043384 | 6.1105e-05
2008 | 2007-06-15 | B | 19 | 0.0037885 | 6.1105e-05
2008 | 2007-06-15 | C | 24 | 0.004168 | 7.7185e-05
2008 | 2007-06-15 | C | 510 | 0.044446 | 0.0016402
2008 | 2007-06-15 | B | 8 | 0.0076413 | 2.5728e-05
2008 | 2007-06-15 | B | 60 | 0.077571 | 0.00019296
2008 | 2007-06-15 | B | 10 | 0.010163 | 3.216e-05
2008 | 2007-06-16 | C | 129 | 0.059153 | 0.00041487
2008 | 2007-06-16 | C | 1085 | 0.069788 | 0.0034894
2008 | 2007-06-16 | C | 152 | 0.008098 | 0.00048884
2008 | 2007-06-16 | C | 6 | 0.003126 | 1.9296e-05
2008 | 2007-06-16 | C | 1 | 0.00055959 | 0
2008 | 2007-06-16 | C | 70 | 0.017955 | 0.00022512
2008 | 2007-06-16 | C | 451 | 0.085753 | 0.0014504
2008 | 2007-06-17 | C | 5 | 0.00059497 | 1.608e-05
2008 | 2007-06-16 | B | 1 | 0.0043513 | 0
2008 | 2007-06-17 | C | 199 | 0.029176 | 0.00063999
2008 | 2007-06-17 | C | 166 | 0.10731 | 0.00053386
2008 | 2007-06-18 | B | 20 | 0.0052743 | 6.4321e-05
2008 | 2007-06-18 | C | 26 | 0.0058532 | 8.3617e-05
2008 | 2007-06-18 | B | 6 | 0.006445 | 1.9296e-05
2008 | 2007-06-18 | B | 14 | 0.015398 | 4.5025e-05
2008 | 2007-06-18 | B | 8 | 0.009468 | 2.5728e-05
2008 | 2007-06-18 | B | 6 | 0.0022577 | 1.9296e-05
2008 | 2007-06-18 | C | 1079 | 0.067013 | 0.0034701
2008 | 2007-06-18 | B | 78 | 0.16054 | 0.00025085
2008 | 2007-06-18 | C | 825 | 0.38963 | 0.0026532
2008 | 2007-06-19 | B | 68 | 0.076323 | 0.00021869
2008 | 2007-06-19 | C | 75 | 0.0016884 | 0.0002412
2008 | 2007-06-20 | B | 639 | 0.25483 | 0.0020551
2008 | 2007-06-19 | C | 388 | 0.10815 | 0.0012478
2008 | 2007-06-19 | B | 31 | 0.033598 | 9.9697e-05
2008 | 2007-06-19 | B | 2 | 0.0016723 | 6.4321e-06
2008 | 2007-06-19 | B | 3 | 0.0029234 | 9.6481e-06
2008 | 2007-06-19 | B | 49 | 0.023673 | 0.00015759
2008 | 2007-06-20 | B | 19 | 0.012954 | 6.1105e-05
2008 | 2007-06-20 | C | 29 | 0.010819 | 9.3265e-05
2008 | 2007-06-20 | B | 41 | 0.013713 | 0.00013186
2008 | 2007-06-20 | B | 1 | 0.00068502 | 0
2008 | 2007-06-20 | B | 21 | 0.011616 | 6.7537e-05
2008 | 2007-06-20 | B | 123 | 0.11511 | 0.00039557
2008 | 2007-06-20 | C | 154 | 0.12966 | 0.00049527
2008 | 2007-06-20 | C | 51 | 0.026899 | 0.00016402
2008 | 2007-06-20 | C | 682 | 0.10206 | 0.0021933
2008 | 2007-06-21 | B | 3 | 0.00030874 | 9.6481e-06
2008 | 2007-06-21 | B | 15 | 0.0079597 | 4.8241e-05
2008 | 2007-06-21 | B | 22 | 0.017051 | 7.0753e-05
2008 | 2007-06-21 | B | 10 | 0.0095517 | 3.216e-05
2008 | 2007-06-21 | C | 43 | 0.0035955 | 0.00013829
2008 | 2007-06-21 | B | 18 | 0.020666 | 5.7889e-05
2008 | 2007-06-21 | C | 1142 | 0.084125 | 0.0036727
2008 | 2007-06-21 | C | 584 | 0.030051 | 0.0018782
2008 | 2007-06-22 | B | 295 | 0.13093 | 0.00094873
2008 | 2007-06-22 | C | 283 | 0.050058 | 0.00091014
2008 | 2007-06-21 | C | 63 | 0.022792 | 0.00020261
2008 | 2007-06-22 | C | 995 | 0.36748 | 0.0032
2008 | 2007-06-22 | C | 432 | 0.095619 | 0.0013893
2008 | 2007-06-21 | C | 207 | 0.066341 | 0.00066572
2008 | 2007-06-22 | C | 216 | 0.046543 | 0.00069467
2008 | 2007-06-22 | C | 86 | 0.013276 | 0.00027658
2008 | 2007-06-21 | C | 204 | 0.057445 | 0.00065607
2008 | 2007-06-21 | C | 130 | 0.050383 | 0.00041809
2008 | 2007-06-22 | C | 19 | 0.0053161 | 6.1105e-05
2008 | 2007-06-22 | C | 111 | 0.014984 | 0.00035698
2008 | 2007-06-22 | B | 47 | 0.014813 | 0.00015115
2008 | 2007-06-22 | C | 1 | 0.00010935 | 0
2008 | 2007-06-22 | B | 19 | 0.0034219 | 6.1105e-05
2008 | 2007-06-22 | B | 43 | 0.017563 | 0.00013829
2008 | 2007-06-22 | C | 2 | 0.0021162 | 6.4321e-06
2008 | 2007-06-22 | C | 48 | 0.0040136 | 0.00015437
2008 | 2007-06-22 | C | 1085 | 0.087235 | 0.0034894
2008 | 2007-06-22 | C | 895 | 0.14245 | 0.0028784
2008 | 2007-06-21 | C | 4 | 0.011989 | 1.2864e-05
2008 | 2007-06-22 | C | 939 | 0.13589 | 0.0030199
2008 | 2007-06-22 | C | 1990 | 0.3584 | 0.0063999
2008 | 2007-06-22 | C | 225 | 0.16029 | 0.00072361
2008 | 2007-06-23 | C | 3945 | 0.050749 | 0.012687
2008 | 2007-06-23 | C | 827 | 0.034576 | 0.0026597
2008 | 2007-06-23 | C | 173 | 0.10565 | 0.00055638
2008 | 2007-06-23 | C | 85 | 0.0019135 | 0.00027336
2008 | 2007-06-23 | C | 36 | 0.00521 | 0.00011578
2008 | 2007-06-23 | C | 10 | 0.0018653 | 3.216e-05
2008 | 2007-06-23 | C | 12 | 0.0020454 | 3.8593e-05
2008 | 2007-06-23 | C | 212 | 0.054544 | 0.0006818
2008 | 2007-06-24 | C | 811 | 0.091287 | 0.0026082
2008 | 2007-06-23 | C | 62 | 0.078761 | 0.00019939
2008 | 2007-06-24 | C | 668 | 0.33557 | 0.0021483
2008 | 2007-06-23 | C | 433 | 0.038104 | 0.0013925
2008 | 2007-06-24 | C | 365 | 0.067588 | 0.0011739
2008 | 2007-06-23 | C | 74 | 0.052833 | 0.00023799
2008 | 2007-06-23 | C | 618 | 0.31018 | 0.0019875
2008 | 2007-06-23 | C | 12 | 0.03867 | 3.8593e-05
2008 | 2007-06-23 | C | 939 | 0.13287 | 0.0030199
2008 | 2007-06-23 | C | 96 | 0.087373 | 0.00030874
2008 | 2007-06-24 | C | 86 | 0.0060848 | 0.00027658
2008 | 2007-06-22 | C | 236 | 0.042069 | 0.00075899
2008 | 2007-06-23 | C | 325 | 0.036583 | 0.0010452
2008 | 2007-06-23 | C | 4 | 0.0033061 | 1.2864e-05
2008 | 2007-06-23 | C | 1635 | 1.1155 | 0.0052582
2008 | 2007-06-24 | C | 20 | 0.0055316 | 6.4321e-05
2008 | 2007-06-23 | C | 43 | 0.036923 | 0.00013829
2008 | 2007-06-22 | C | 3 | 0.023744 | 9.6481e-06
2008 | 2007-06-22 | C | 129 | 0.11207 | 0.00041487
2008 | 2007-06-22 | C | 848 | 0.22853 | 0.0027272
2008 | 2007-06-24 | C | 40 | 0.0047597 | 0.00012864
2008 | 2007-06-24 | C | 644 | 0.10389 | 0.0020711
2008 | 2007-06-23 | C | 555 | 0.12838 | 0.0017849
2008 | 2007-06-25 | C | 7 | 0.00060783 | 2.2512e-05
2008 | 2007-06-25 | C | 36 | 0.0096095 | 0.00011578
2008 | 2007-05-30 | B | 1 | 0.00042452 | 0
2008 | 2007-05-25 | B | 24 | 0.024776 | 7.7185e-05
2008 | 2007-06-25 | C | 137 | 0.14848 | 0.0004406
2008 | 2007-05-08 | B | 47 | 0.017987 | 0.00015115
2008 | 2007-05-03 | B | 26 | 0.013128 | 8.3617e-05
2008 | 2007-06-25 | C | 621 | 0.073895 | 0.0019972
2008 | 2007-06-25 | C | 430 | 0.046337 | 0.0013829
2008 | 2007-06-25 | C | 136 | 0.075162 | 0.00043738
2008 | 2007-06-25 | B | 38 | 0.050228 | 0.00012221
2008 | 2007-06-25 | C | 111 | 0.028558 | 0.00035698
2008 | 2007-06-25 | B | 17 | 0.024821 | 5.4673e-05
2008 | 2007-06-25 | C | 112 | 0.024239 | 0.0003602
2008 | 2007-06-25 | C | 494 | 0.093654 | 0.0015887
2008 | 2007-06-05 | B | 35 | 0.023188 | 0.00011256
2008 | 2007-06-14 | B | 10 | 0.0070753 | 3.216e-05
2008 | 2007-06-14 | B | 3 | 0.0035505 | 9.6481e-06
2008 | 2007-06-14 | B | 56 | 0.03746 | 0.0001801
2008 | 2007-06-05 | B | 155 | 0.11216 | 0.00049849
2008 | 2007-06-26 | B | 142 | 0.026031 | 0.00045668
2008 | 2007-06-26 | C | 18 | 0.00040522 | 5.7889e-05
2008 | 2007-06-26 | B | 142 | 0.026031 | 0.00045668
2008 | 2007-06-26 | B | 114 | 0.064893 | 0.00036663
2008 | 2007-06-26 | C | 25 | 0.0049045 | 8.0401e-05
2008 | 2007-06-26 | C | 44 | 0.0094809 | 0.00014151
2008 | 2007-06-26 | B | 10 | 0.010034 | 3.216e-05
2008 | 2007-06-26 | C | 239 | 0.10205 | 0.00076863
2008 | 2007-06-26 | B | 51 | 0.055438 | 0.00016402
2008 | 2007-06-26 | B | 135 | 0.024747 | 0.00043417
2008 | 2007-06-26 | B | 34 | 0.00098411 | 0.00010935
2008 | 2007-06-26 | C | 512 | 0.13961 | 0.0016466
2008 | 2007-06-26 | C | 238 | 0.0819 | 0.00076542
2008 | 2007-06-27 | C | 649 | 0.077044 | 0.0020872
2008 | 2007-06-27 | B | 9 | 0.0085965 | 2.8944e-05
2008 | 2007-06-27 | C | 22 | 0.0058017 | 7.0753e-05
2008 | 2007-06-27 | C | 27 | 0.0051232 | 8.6833e-05
2008 | 2007-06-27 | B | 8 | 0.0027529 | 2.5728e-05
2008 | 2007-06-27 | B | 7 | 0.0093876 | 2.2512e-05
2008 | 2007-06-27 | B | 18 | 0.018582 | 5.7889e-05
2008 | 2007-06-27 | C | 43 | 0.045221 | 0.00013829
2008 | 2007-06-28 | C | 16 | 0.0063292 | 5.1457e-05
2008 | 2007-06-27 | C | 161 | 0.0010356 | 0.00051778
2008 | 2007-06-28 | C | 64 | 0.0030874 | 0.00020583
2008 | 2007-06-28 | C | 898 | 0.19082 | 0.002888
2008 | 2007-06-28 | C | 5 | 0.00027336 | 1.608e-05
2008 | 2007-06-28 | B | 19 | 0.012649 | 6.1105e-05
2008 | 2007-06-28 | B | 43 | 0.059188 | 0.00013829
2008 | 2007-06-25 | B | 43 | 0.059188 | 0.00013829
2008 | 2007-06-27 | B | 72 | 0.027902 | 0.00023156
2008 | 2007-06-28 | B | 45 | 0.04689 | 0.00014472
2008 | 2007-06-28 | C | 1493 | 0.081626 | 0.0048016
2008 | 2007-06-28 | C | 77 | 0.0024764 | 0.00024764
2008 | 2007-06-28 | B | 22 | 0.021014 | 7.0753e-05
2008 | 2007-06-29 | C | 27 | 0.0071203 | 8.6833e-05
2008 | 2007-06-29 | B | 32 | 0.0106 | 0.00010291
2008 | 2007-06-24 | B | 18 | 0.023445 | 5.7889e-05
2008 | 2007-06-23 | B | 10 | 0.0070753 | 3.216e-05
2008 | 2007-07-03 | B | 22 | 0.016768 | 7.0753e-05
2008 | 2007-06-21 | B | 3 | 0.00040522 | 9.6481e-06
2008 | 2007-06-26 | B | 142 | 0.026031 | 0.00045668
2008 | 2007-06-29 | B | 50 | 0.031035 | 0.0001608
2008 | 2007-06-29 | C | 548 | 0.1444 | 0.0017624
2008 | 2007-06-29 | C | 301 | 0.24173 | 0.00096803
2008 | 2007-06-29 | C | 611 | 0.021615 | 0.001965
2008 | 2007-06-30 | C | 33 | 0.0070045 | 0.00010613
2008 | 2007-06-29 | C | 277 | 0.023162 | 0.00089084
2008 | 2007-06-30 | C | 106 | 0.0027272 | 0.0003409
2008 | 2007-06-30 | C | 506 | 0.08025 | 0.0016273
2008 | 2007-06-30 | B | 12 | 0.011462 | 3.8593e-05
2008 | 2007-06-29 | C | 279 | 0.03682 | 0.00089728
2008 | 2007-06-30 | C | 518 | 0.079411 | 0.0016659
2008 | 2007-06-30 | C | 10 | 0.007011 | 3.216e-05
2008 | 2007-06-30 | C | 4 | 0.00034733 | 1.2864e-05
2008 | 2007-06-30 | C | 805 | 0.093706 | 0.0025889
2008 | 2007-06-30 | C | 28 | 0.001891 | 9.0049e-05
2008 | 2007-07-01 | C | 131 | 0.02313 | 0.0004213
2008 | 2007-06-29 | C | 187 | 0.075326 | 0.0006014
2008 | 2007-06-30 | C | 281 | 0.056901 | 0.00090371
2008 | 2007-07-01 | C | 48 | 0.005403 | 0.00015437
2008 | 2007-07-01 | C | 460 | 0.060967 | 0.0014794
2008 | 2007-07-01 | C | 463 | 0.0088956 | 0.001489
2008 | 2007-06-27 | B | 31 | 0.047257 | 9.9697e-05
2008 | 2007-07-02 | C | 326 | 0.13672 | 0.0010484
2008 | 2007-07-02 | C | 800 | 0.079327 | 0.0025728
2008 | 2007-07-02 | C | 212 | 0.03409 | 0.0006818
2008 | 2007-07-02 | B | 42 | 0.050247 | 0.00013507
2008 | 2007-07-02 | C | 314 | 0.074889 | 0.0010098
2008 | 2007-07-02 | C | 79 | 0.03255 | 0.00025407
2008 | 2007-07-03 | C | 8 | 0.0026757 | 2.5728e-05
2008 | 2007-07-03 | B | 102 | 0.048221 | 0.00032804
2008 | 2007-07-03 | C | 80 | 0.026095 | 0.00025728
2008 | 2007-07-03 | C | 182 | 0.011706 | 0.00058532
2008 | 2007-07-03 | C | 342 | 0.025297 | 0.0010999
2008 | 2007-07-03 | C | 449 | 0.14873 | 0.001444
2008 | 2007-07-03 | C | 534 | 0.094455 | 0.0017174
2008 | 2007-07-03 | B | 54 | 0.056789 | 0.00017367
2008 | 2007-07-03 | B | 15 | 0.0050653 | 4.8241e-05
2008 | 2007-07-03 | B | 50 | 0.054834 | 0.0001608
2008 | 2007-07-02 | C | 1 | 0.0040265 | 0
2008 | 2007-07-04 | C | 808 | 0.014508 | 0.0025986
2008 | 2007-07-04 | B | 3 | 0.0034444 | 9.6481e-06
2008 | 2007-07-04 | B | 14 | 0.013372 | 4.5025e-05
2008 | 2007-07-04 | C | 82 | 0.010285 | 0.00026372
2008 | 2007-07-04 | B | 35 | 0.037708 | 0.00011256
2008 | 2007-07-04 | B | 23 | 0.029292 | 7.3969e-05
2008 | 2007-07-04 | C | 211 | 0.0020358 | 0.00067859
2008 | 2007-07-04 | C | 208 | 0.0066894 | 0.00066894
2008 | 2007-07-04 | C | 188 | 0.22371 | 0.00060462
2008 | 2007-07-04 | C | 15 | 0.0070914 | 4.8241e-05
2008 | 2007-07-04 | C | 2 | 0.00066894 | 6.4321e-06
2008 | 2007-07-05 | C | 104 | 0.026327 | 0.00033447
2008 | 2007-07-04 | B | 103 | 0.089438 | 0.00033125
2008 | 2007-07-04 | C | 158 | 0.18801 | 0.00050813
2008 | 2007-07-04 | C | 3 | 0.0038014 | 9.6481e-06
2008 | 2007-07-05 | B | 11 | 0.0072876 | 3.5376e-05
2008 | 2007-07-05 | C | 21 | 0.0024989 | 6.7537e-05
2008 | 2007-07-05 | B | 3 | 0.0031549 | 9.6481e-06
2008 | 2007-07-05 | B | 25 | 0.01801 | 8.0401e-05
2008 | 2007-07-05 | C | 167 | 0.0042966 | 0.00053708
2008 | 2007-07-05 | C | 336 | 0.052341 | 0.0010806
2008 | 2007-07-05 | C | 57 | 0.06471 | 0.00018331
2008 | 2007-07-05 | C | 880 | 0.74149 | 0.0028301
2008 | 2007-07-05 | C | 670 | 0.028012 | 0.0021547
2008 | 2007-07-05 | C | 33 | 0.0078536 | 0.00010613
2008 | 2007-07-05 | C | 185 | 0.082701 | 0.00059497
2008 | 2007-07-05 | B | 16 | 0.0046311 | 5.1457e-05
2008 | 2007-07-05 | C | 26 | 0.0025085 | 8.3617e-05
2008 | 2007-07-05 | B | 22 | 0.018396 | 7.0753e-05
2008 | 2007-07-05 | C | 241 | 0.17594 | 0.00077507
2008 | 2007-07-05 | C | 229 | 0.12888 | 0.00073647
2008 | 2007-07-05 | C | 25 | 0.059256 | 8.0401e-05
2008 | 2007-07-05 | C | 138 | 0.45713 | 0.00044381
2008 | 2007-07-06 | B | 8 | 0.0037306 | 2.5728e-05
2008 | 2007-07-05 | C | 177 | 0.44504 | 0.00056924
2008 | 2007-07-05 | C | 181 | 0.24578 | 0.0005821
2008 | 2007-07-05 | C | 18 | 0.061999 | 5.7889e-05
2008 | 2007-07-05 | C | 315 | 0.87528 | 0.0010131
2008 | 2007-07-06 | C | 27 | 0.05731 | 8.6833e-05
2008 | 2007-07-05 | C | 8 | 0.017881 | 2.5728e-05
2008 | 2007-07-05 | C | 302 | 1.0259 | 0.00097125
2008 | 2007-07-06 | C | 57 | 0.095661 | 0.00018331
2008 | 2007-07-05 | C | 55 | 0.16521 | 0.00017688
2008 | 2007-07-05 | C | 44 | 0.18283 | 0.00014151
2008 | 2007-07-05 | C | 24 | 0.097793 | 7.7185e-05
2008 | 2007-07-06 | C | 8 | 0.0010291 | 2.5728e-05
2008 | 2007-07-06 | C | 1032 | 0.19159 | 0.003319
2008 | 2007-07-05 | C | 9 | 0.031492 | 2.8944e-05
2008 | 2007-07-05 | C | 209 | 0.78562 | 0.00067215
2008 | 2007-07-05 | C | 1590 | 3.3401 | 0.0051135
2008 | 2007-07-06 | C | 120 | 0.053393 | 0.00038593
2008 | 2007-07-05 | C | 202 | 0.97259 | 0.00064964
2008 | 2007-07-07 | C | 33 | 0.0039268 | 0.00010613
2008 | 2007-07-05 | C | 23 | 0.098083 | 7.3969e-05
2008 | 2007-07-06 | C | 188 | 0.14269 | 0.00060462
2008 | 2007-07-06 | C | 2 | 0.0072104 | 6.4321e-06
2008 | 2007-07-07 | C | 17 | 0.0072168 | 5.4673e-05
2008 | 2007-07-06 | C | 3 | 0.00056924 | 9.6481e-06
2008 | 2007-07-06 | C | 1201 | 1.1163 | 0.0038625
2008 | 2007-07-06 | C | 9 | 0.0025182 | 2.8944e-05
2008 | 2007-07-07 | C | 9 | 0.0011578 | 2.8944e-05
2008 | 2007-07-07 | C | 24 | 0.0036277 | 7.7185e-05
2008 | 2007-07-06 | C | 22 | 0.028796 | 7.0753e-05
2008 | 2007-07-06 | C | 113 | 0.10503 | 0.00036341
2008 | 2007-07-05 | C | 1277 | 0.20575 | 0.0041069
2008 | 2007-07-07 | C | 31 | 0.011465 | 9.9697e-05
2008 | 2007-07-07 | C | 7 | 0.0027915 | 2.2512e-05
2008 | 2007-07-07 | C | 19 | 0.0025664 | 6.1105e-05
2008 | 2007-07-05 | C | 35 | 0.33453 | 0.00011256
2008 | 2007-07-05 | C | 41 | 0.38608 | 0.00013186
2008 | 2007-07-05 | C | 28 | 0.27672 | 9.0049e-05
2008 | 2007-07-05 | C | 18 | 0.1497 | 5.7889e-05
2008 | 2007-07-07 | C | 87 | 0.13782 | 0.0002798
2008 | 2007-07-07 | C | 6 | 0.002277 | 1.9296e-05
2008 | 2007-07-06 | C | 10 | 0.05924 | 3.216e-05
2008 | 2007-07-07 | C | 85 | 0.033897 | 0.00027336
2008 | 2007-07-05 | C | 798 | 0.084691 | 0.0025664
2008 | 2007-07-07 | C | 1152 | 0.22305 | 0.0037049
2008 | 2007-07-08 | C | 17 | 0.0036084 | 5.4673e-05
2008 | 2007-07-08 | C | 57 | 0.0091657 | 0.00018331
2008 | 2007-07-08 | C | 28 | 0.0012607 | 9.0049e-05
2008 | 2007-07-05 | C | 145 | 0.18201 | 0.00046633
2008 | 2007-07-05 | C | 98 | 0.17491 | 0.00031517
2008 | 2007-07-08 | C | 2 | 0.004406 | 6.4321e-06
2008 | 2007-07-08 | C | 2 | 0.00013507 | 6.4321e-06
2008 | 2007-07-09 | C | 411 | 0.16353 | 0.0013218
2008 | 2007-07-09 | C | 172 | 0.028211 | 0.00055316
2008 | 2007-07-09 | C | 28 | 0.0032418 | 9.0049e-05
2008 | 2007-07-09 | C | 8 | 0.0012864 | 2.5728e-05
2008 | 2007-07-09 | C | 30 | 0.0059818 | 9.6481e-05
2008 | 2007-07-09 | C | 30 | 0.0033768 | 9.6481e-05
2008 | 2007-07-09 | C | 221 | 0.012469 | 0.00071075
2008 | 2007-07-10 | C | 299 | 0.028848 | 0.0009616
2008 | 2007-07-10 | C | 184 | 0.01006 | 0.00059175
2008 | 2007-07-10 | B | 20 | 0.0075255 | 6.4321e-05
2008 | 2007-07-10 | B | 4 | 0.0012478 | 1.2864e-05
2008 | 2007-07-10 | C | 466 | 0.10491 | 0.0014987
2008 | 2007-07-10 | C | 75 | 0.042934 | 0.0002412
2008 | 2007-07-10 | C | 14 | 0.0021162 | 4.5025e-05
2008 | 2007-07-10 | C | 106 | 0.073097 | 0.0003409
2008 | 2007-07-10 | C | 263 | 0.07823 | 0.00084582
2008 | 2007-07-10 | C | 48 | 0.0018524 | 0.00015437
2008 | 2007-07-10 | C | 706 | 0.17172 | 0.0022705
2008 | 2007-07-10 | C | 307 | 0.74444 | 0.00098733
2008 | 2007-07-11 | C | 57 | 0.10779 | 0.00018331
2008 | 2007-07-10 | C | 398 | 0.1798 | 0.00128
2008 | 2007-07-11 | C | 36 | 0.0077571 | 0.00011578
2008 | 2007-07-10 | C | 421 | 0.41255 | 0.001354
2008 | 2007-07-11 | C | 17 | 0.0044832 | 5.4673e-05
2008 | 2007-07-10 | C | 335 | 0.078803 | 0.0010774
2008 | 2007-07-10 | C | 4690 | 16.8932 | 0.015083
2008 | 2007-07-10 | C | 454 | 1.1184 | 0.0014601
2008 | 2007-07-11 | C | 164 | 0.051688 | 0.00052743
2008 | 2007-07-10 | C | 219 | 0.076066 | 0.00070431
2008 | 2007-07-10 | C | 133 | 0.043118 | 0.00042773
2008 | 2007-07-11 | C | 155 | 0.024924 | 0.00049849
2008 | 2007-07-10 | C | 27 | 0.10403 | 8.6833e-05
2008 | 2007-07-11 | C | 248 | 0.038149 | 0.00079758
2008 | 2007-07-11 | C | 1399 | 0.27895 | 0.0044992
2008 | 2007-07-11 | C | 142 | 0.048858 | 0.00045668
2008 | 2007-07-11 | C | 319 | 0.12419 | 0.0010259
2008 | 2007-07-11 | C | 6 | 0.0024506 | 1.9296e-05
2008 | 2007-07-11 | C | 3 | 0.00045346 | 9.6481e-06
2008 | 2007-07-12 | C | 2258 | 0.76992 | 0.0072618
2008 | 2007-07-12 | C | 204 | 0.067836 | 0.00065607
2008 | 2007-07-11 | C | 951 | 0.50165 | 0.0030585
2008 | 2007-07-10 | C | 562 | 2.3026 | 0.0018074
2008 | 2007-07-10 | C | 803 | 1.6352 | 0.0025825
2008 | 2007-07-10 | C | 9795 | 52.1822 | 0.031501
2008 | 2007-07-10 | C | 3936 | 18.5445 | 0.012658
2008 | 2007-07-10 | C | 2908 | 13.6543 | 0.0093523
2008 | 2007-07-11 | C | 82 | 0.068566 | 0.00026372
2008 | 2007-07-10 | C | 371 | 1.2874 | 0.0011932
2008 | 2007-07-10 | C | 305 | 1.3291 | 0.00098089
2008 | 2007-07-11 | C | 496 | 1.0799 | 0.0015952
2008 | 2007-07-11 | C | 478 | 0.057368 | 0.0015373
2008 | 2007-07-12 | C | 1168 | 0.1446 | 0.0037563
2008 | 2007-07-12 | C | 8 | 0.0014922 | 2.5728e-05
2008 | 2007-07-12 | C | 3 | 0.00035698 | 9.6481e-06
2008 | 2007-07-11 | C | 231 | 0.32369 | 0.00074291
2008 | 2007-07-12 | B | 55 | 0.016096 | 0.00017688
2008 | 2007-07-12 | C | 2 | 0.00025728 | 6.4321e-06
2008 | 2007-07-12 | B | 66 | 0.07896 | 0.00021226
2008 | 2007-07-12 | C | 1 | 0.00054994 | 0
2008 | 2007-07-12 | B | 8 | 0.0038593 | 2.5728e-05
2008 | 2007-07-12 | C | 48 | 0.094011 | 0.00015437
2008 | 2007-07-12 | C | 30 | 0.0060783 | 9.6481e-05
2008 | 2007-07-12 | C | 513 | 0.18478 | 0.0016498
2008 | 2007-07-11 | C | 80 | 0.44201 | 0.00025728
2008 | 2007-07-12 | C | 134 | 0.019824 | 0.00043095
2008 | 2007-07-10 | C | 301 | 1.5346 | 0.00096803
2008 | 2007-07-11 | C | 707 | 0.20353 | 0.0022737
2008 | 2007-07-10 | C | 585 | 1.6891 | 0.0018814
2008 | 2007-07-10 | C | 232 | 1.039 | 0.00074612
2008 | 2007-07-11 | C | 517 | 1.8921 | 0.0016627
2008 | 2007-07-10 | C | 493 | 4.2733 | 0.0015855
2008 | 2007-07-13 | C | 10 | 0.0029266 | 3.216e-05
2008 | 2007-07-13 | B | 89 | 0.059342 | 0.00028623
2008 | 2007-07-14 | C | 77 | 0.084196 | 0.00024764
2008 | 2007-07-14 | C | 7 | 0.00045025 | 2.2512e-05
2008 | 2007-07-08 | B | 23 | 0.01975 | 7.3969e-05
2008 | 2007-07-08 | B | 5 | 0.0046793 | 1.608e-05
2008 | 2007-07-15 | C | 87 | 0.015842 | 0.0002798
2008 | 2007-07-13 | B | 11 | 0.0076413 | 3.5376e-05
2008 | 2007-07-13 | B | 66 | 0.062192 | 0.00021226
2008 | 2007-07-14 | B | 1 | 0.0010131 | 0
2008 | 2007-07-13 | C | 305 | 0.019618 | 0.00098089
2008 | 2007-07-13 | C | 41 | 0.0019779 | 0.00013186
2008 | 2007-07-13 | C | 9 | 0.0098411 | 2.8944e-05
2008 | 2007-07-13 | C | 876 | 0.064797 | 0.0028173
2008 | 2007-07-13 | C | 34 | 0.0022963 | 0.00010935
2008 | 2007-07-14 | C | 77 | 0.0024764 | 0.00024764
2008 | 2007-07-14 | C | 138 | 0.036837 | 0.00044381
2008 | 2007-07-13 | C | 218 | 0.11007 | 0.0007011
2008 | 2007-07-14 | C | 17 | 0.0010935 | 5.4673e-05
2008 | 2007-07-14 | C | 6 | 0.001891 | 1.9296e-05
2008 | 2007-07-14 | C | 74 | 0.0076156 | 0.00023799
2008 | 2007-07-13 | C | 134 | 0.0073261 | 0.00043095
2008 | 2007-07-13 | C | 14 | 0.0013057 | 4.5025e-05
2008 | 2007-07-14 | C | 2 | 0.002605 | 6.4321e-06
2008 | 2007-07-13 | C | 14 | 0.0070238 | 4.5025e-05
2008 | 2007-07-14 | C | 3 | 0.0002798 | 9.6481e-06
2008 | 2007-07-12 | C | 167 | 0.79286 | 0.00053708
2008 | 2007-07-15 | C | 2908 | 2.0294 | 0.0093523
2008 | 2007-07-14 | C | 229 | 0.031668 | 0.00073647
2008 | 2007-07-11 | C | 876 | 1.3378 | 0.0028173
2008 | 2007-07-10 | C | 273 | 2.4801 | 0.00087798
2008 | 2007-07-14 | C | 120 | 0.074484 | 0.00038593
2008 | 2007-07-09 | B | 30 | 0.031067 | 9.6481e-05
2008 | 2007-07-12 | B | 4 | 0.0039364 | 1.2864e-05
2008 | 2007-07-16 | C | 146 | 0.013147 | 0.00046954
2008 | 2007-07-16 | B | 2 | 0.0016402 | 6.4321e-06
2008 | 2007-07-16 | B | 340 | 0.0065607 | 0.0010935
2008 | 2007-07-16 | C | 30 | 0.0053065 | 9.6481e-05
2008 | 2007-07-15 | C | 151 | 0.01554 | 0.00048562
2008 | 2007-07-16 | C | 507 | 0.11514 | 0.0016305
2008 | 2007-07-16 | C | 214 | 0.008947 | 0.00068823
2008 | 2007-07-16 | C | 625 | 0.02412 | 0.00201
2008 | 2007-07-16 | C | 1 | 0.0002412 | 0
2008 | 2007-07-16 | C | 525 | 0.094201 | 0.0016884
2008 | 2007-07-17 | B | 291 | 0.07487 | 0.00093587
2008 | 2007-07-17 | C | 51 | 0.0021322 | 0.00016402
2008 | 2007-07-16 | C | 498 | 0.033633 | 0.0016016
2008 | 2007-07-17 | B | 390 | 0.05895 | 0.0012543
2008 | 2007-07-17 | B | 63 | 0.029784 | 0.00020261
2008 | 2007-07-17 | B | 20 | 0.0097125 | 6.4321e-05
2008 | 2007-07-17 | B | 292 | 0.030051 | 0.00093908
2008 | 2007-07-17 | C | 1461 | 0.3279 | 0.0046986
2008 | 2007-07-17 | C | 194 | 0.004123 | 0.00062391
2008 | 2007-07-15 | C | 182 | 0.099279 | 0.00058532
2008 | 2007-07-15 | C | 21 | 0.01425 | 6.7537e-05
2008 | 2007-07-16 | C | 1053 | 0.1651 | 0.0033865
2008 | 2007-07-18 | C | 793 | 0.1282 | 0.0025503
2008 | 2007-07-16 | B | 66 | 0.089361 | 0.00021226
2008 | 2007-07-18 | C | 129 | 0.0307 | 0.00041487
2008 | 2007-07-18 | B | 32 | 0.013687 | 0.00010291
2008 | 2007-07-18 | B | 152 | 0.044973 | 0.00048884
2008 | 2007-07-18 | B | 1 | 0.00024764 | 0
2008 | 2007-07-18 | B | 309 | 0.067576 | 0.00099376
2008 | 2007-07-14 | B | 2 | 0.0012414 | 6.4321e-06
2008 | 2007-07-18 | C | 178 | 0.10018 | 0.00057246
2008 | 2007-07-18 | B | 5 | 0.0043095 | 1.608e-05
2008 | 2007-07-19 | C | 93 | 0.02303 | 0.00029909
2008 | 2007-07-19 | B | 3 | 0.0013121 | 9.6481e-06
2008 | 2007-07-19 | B | 9 | 0.0051232 | 2.8944e-05
2008 | 2007-07-11 | C | 4 | 0.14237 | 1.2864e-05
2008 | 2007-07-19 | B | 204 | 0.030835 | 0.00065607
2008 | 2007-07-19 | C | 381 | 0.11886 | 0.0012253
2008 | 2007-07-10 | C | 2 | 0.083238 | 6.4321e-06
2008 | 2007-07-11 | B | 160 | 0.027272 | 0.00051457
2008 | 2007-07-19 | C | 516 | 0.036509 | 0.0016595
2008 | 2007-07-19 | B | 18 | 0.02414 | 5.7889e-05
2008 | 2007-07-20 | C | 3571 | 0.12633 | 0.011484
2008 | 2007-07-20 | C | 73 | 0.027703 | 0.00023477
2008 | 2007-07-20 | C | 368 | 0.021303 | 0.0011835
2008 | 2007-07-20 | C | 486 | 0.010587 | 0.001563
2008 | 2007-07-20 | B | 3 | 0.0019296 | 9.6481e-06
2008 | 2007-07-20 | C | 1219 | 1.1266 | 0.0039204
2008 | 2007-07-20 | C | 52 | 0.0055187 | 0.00016723
2008 | 2007-07-20 | C | 5 | 0.0044542 | 1.608e-05
2008 | 2007-07-20 | C | 24 | 0.0063292 | 7.7185e-05
2008 | 2007-07-21 | C | 1 | 0.00015759 | 0
2008 | 2007-07-21 | C | 25 | 0.0035376 | 8.0401e-05
2008 | 2007-07-21 | C | 375 | 0.13024 | 0.001206
2008 | 2007-07-21 | C | 200 | 0.026507 | 0.00064321
2008 | 2007-07-21 | C | 19 | 0.0014054 | 6.1105e-05
2008 | 2007-07-21 | C | 275 | 0.089239 | 0.00088441
2008 | 2007-07-22 | C | 20 | 0.0022512 | 6.4321e-05
2008 | 2007-07-22 | B | 30 | 0.0054994 | 9.6481e-05
2008 | 2007-07-22 | C | 1221 | 0.036653 | 0.0039268
2008 | 2007-07-22 | C | 49 | 0.016074 | 0.00015759
2008 | 2007-07-22 | C | 307 | 0.11573 | 0.00098733
2008 | 2007-07-22 | C | 19 | 0.0025664 | 6.1105e-05
2008 | 2007-07-22 | C | 208 | 0.10122 | 0.00066894
2008 | 2007-07-22 | C | 1879 | 0.27731 | 0.0060429
2008 | 2007-07-23 | B | 21 | 0.017627 | 6.7537e-05
2008 | 2007-07-23 | C | 577 | 0.12787 | 0.0018557
2008 | 2007-07-23 | C | 525 | 0.12649 | 0.0016884
2008 | 2007-07-23 | C | 130 | 0.030102 | 0.00041809
2008 | 2007-07-23 | C | 5 | 0.001399 | 1.608e-05
2008 | 2007-07-23 | B | 7 | 0.005538 | 2.2512e-05
2008 | 2007-07-23 | B | 5 | 0.0033286 | 1.608e-05
2008 | 2007-07-24 | C | 18 | 0.0037049 | 5.7889e-05
2008 | 2007-07-24 | B | 82 | 0.083862 | 0.00026372
2008 | 2007-07-24 | B | 18 | 0.016788 | 5.7889e-05
2008 | 2007-07-24 | B | 31 | 0.035592 | 9.9697e-05
2008 | 2007-07-24 | C | 175 | 0.082627 | 0.00056281
2008 | 2007-07-25 | C | 185 | 0.0071396 | 0.00059497
2008 | 2007-07-25 | C | 31 | 0.014855 | 9.9697e-05
2008 | 2007-07-25 | B | 11 | 0.016804 | 3.5376e-05
2008 | 2007-07-25 | B | 50 | 0.050331 | 0.0001608
2008 | 2007-07-26 | C | 7 | 0.00087798 | 2.2512e-05
2008 | 2007-07-26 | C | 577 | 0.12636 | 0.0018557
2008 | 2007-07-27 | B | 153 | 0.037888 | 0.00049205
2008 | 2007-07-26 | B | 136 | 0.027118 | 0.00043738
2008 | 2007-07-27 | B | 4 | 0.0022255 | 1.2864e-05
2008 | 2007-07-27 | B | 3 | 0.0020358 | 9.6481e-06
2008 | 2007-07-27 | C | 721 | 0.078838 | 0.0023188
2008 | 2007-07-27 | C | 22 | 0.00091979 | 7.0753e-05
2008 | 2007-07-28 | C | 32 | 0.018216 | 0.00010291
2008 | 2007-07-27 | C | 96 | 0.14356 | 0.00030874
2008 | 2007-07-29 | C | 718 | 0.21643 | 0.0023091
2008 | 2007-07-29 | C | 185 | 0.035988 | 0.00059497
2008 | 2007-07-30 | C | 897 | 0.24135 | 0.0028848
2008 | 2007-07-30 | C | 2486 | 0.82349 | 0.0079951
2008 | 2007-07-30 | C | 972 | 0.4982 | 0.003126
2008 | 2007-07-29 | C | 218 | 0.058252 | 0.0007011
2008 | 2007-07-27 | B | 20 | 0.015759 | 6.4321e-05
2008 | 2007-07-19 | B | 2 | 0.0019168 | 6.4321e-06
2008 | 2007-07-25 | B | 11 | 0.015919 | 3.5376e-05
2008 | 2007-07-29 | C | 123 | 0.36709 | 0.00039557
2008 | 2007-07-30 | C | 26 | 0.0035955 | 8.3617e-05
2008 | 2007-07-31 | C | 123 | 0.002769 | 0.00039557
2008 | 2007-07-31 | C | 1707 | 0.01098 | 0.0054898
2008 | 2007-07-31 | C | 289 | 0.038448 | 0.00092944
2008 | 2007-07-31 | C | 10 | 0.0042452 | 3.216e-05
2008 | 2007-07-31 | B | 27 | 0.014241 | 8.6833e-05
2008 | 2007-07-31 | B | 55 | 0.053949 | 0.00017688
2008 | 2007-07-31 | C | 52 | 0.0055187 | 0.00016723
2008 | 2007-07-31 | C | 311 | 0.088251 | 0.0010002
2008 | 2007-08-01 | C | 15 | 0.0019296 | 4.8241e-05
2008 | 2007-08-01 | C | 1878 | 0.2187 | 0.0060397
2008 | 2007-08-01 | C | 10 | 0.0053708 | 3.216e-05
2008 | 2007-08-02 | C | 1140 | 0.072705 | 0.0036663
2008 | 2007-08-02 | C | 1375 | 0.030954 | 0.0044221
2008 | 2007-08-02 | B | 10 | 0.0010935 | 3.216e-05
2008 | 2007-08-02 | B | 3 | 0.000521 | 9.6481e-06
2008 | 2007-08-02 | B | 9 | 0.0032418 | 2.8944e-05
2008 | 2007-08-02 | B | 29 | 0.0071814 | 9.3265e-05
2008 | 2007-08-02 | B | 12 | 0.01069 | 3.8593e-05
2008 | 2007-08-02 | B | 12 | 0.015939 | 3.8593e-05
2008 | 2007-08-02 | C | 9 | 0.0027787 | 2.8944e-05
2008 | 2007-08-03 | B | 4 | 0.0019296 | 1.2864e-05
2008 | 2007-07-31 | B | 25 | 0.013186 | 8.0401e-05
2008 | 2007-08-03 | B | 6 | 0.003647 | 1.9296e-05
2008 | 2007-08-03 | B | 33 | 0.024198 | 0.00010613
2008 | 2007-08-03 | B | 7 | 0.0023188 | 2.2512e-05
2008 | 2007-08-04 | C | 276 | 0.0044381 | 0.00088763
2008 | 2007-08-04 | C | 16 | 0.002933 | 5.1457e-05
2008 | 2007-08-04 | B | 2 | 0.0018138 | 6.4321e-06
2008 | 2007-08-05 | C | 989 | 0.15646 | 0.0031807
2008 | 2007-08-04 | B | 108 | 0.15338 | 0.00034733
2008 | 2007-08-05 | B | 4 | 0.00045025 | 1.2864e-05
2008 | 2007-08-06 | C | 21 | 0.0029041 | 6.7537e-05
2008 | 2007-08-06 | C | 798 | 0.025664 | 0.0025664
2008 | 2007-08-06 | C | 95 | 0.0048884 | 0.00030552
2008 | 2007-08-01 | B | 16 | 0.013533 | 5.1457e-05
2008 | 2007-08-06 | C | 99 | 0.027677 | 0.00031839
2008 | 2007-08-06 | C | 14 | 0.0010356 | 4.5025e-05
2008 | 2007-08-06 | C | 93 | 0.15273 | 0.00029909
2008 | 2007-08-06 | C | 8 | 0.003885 | 2.5728e-05
2008 | 2007-08-06 | C | 43 | 0.011755 | 0.00013829
2008 | 2007-08-07 | C | 366 | 0.069267 | 0.0011771
2008 | 2007-08-07 | C | 31 | 0.004287 | 9.9697e-05
2008 | 2007-08-08 | C | 2511 | 0.056528 | 0.0080755
2008 | 2007-08-08 | C | 90 | 0.011867 | 0.00028944
2008 | 2007-08-08 | B | 3 | 0.0021515 | 9.6481e-06
2008 | 2007-08-08 | B | 9 | 0.0059915 | 2.8944e-05
2008 | 2007-08-08 | B | 63 | 0.02249 | 0.00020261
2008 | 2007-08-08 | C | 26 | 0.0086126 | 8.3617e-05
2008 | 2007-08-08 | B | 2 | 0.00095838 | 6.4321e-06
2008 | 2007-08-08 | B | 87 | 0.070788 | 0.0002798
2008 | 2007-08-09 | B | 32 | 0.012761 | 0.00010291
2008 | 2007-08-09 | B | 40 | 0.017495 | 0.00012864
2008 | 2007-08-09 | B | 18 | 0.012272 | 5.7889e-05
2008 | 2007-08-09 | B | 25 | 0.028703 | 8.0401e-05
2008 | 2007-07-18 | B | 9 | 0.010044 | 2.8944e-05
2008 | 2007-08-09 | B | 3 | 0.0022866 | 9.6481e-06
2008 | 2007-08-09 | B | 17 | 0.021158 | 5.4673e-05
2008 | 2007-08-10 | C | 62 | 0.007577 | 0.00019939
2008 | 2007-08-10 | C | 45 | 0.0028944 | 0.00014472
2008 | 2007-08-11 | C | 93 | 0.018544 | 0.00029909
2008 | 2007-08-10 | B | 5 | 0.0045507 | 1.608e-05
2008 | 2007-08-10 | B | 3 | 0.0027015 | 9.6481e-06
2008 | 2007-08-10 | C | 535 | 0.15814 | 0.0017206
2008 | 2007-08-10 | C | 86 | 0.036213 | 0.00027658
2008 | 2007-08-10 | C | 89 | 0.042648 | 0.00028623
2008 | 2007-08-10 | C | 119 | 0.058468 | 0.00038271
2008 | 2007-08-11 | C | 545 | 0.19094 | 0.0017527
2008 | 2007-08-11 | C | 26 | 0.0086126 | 8.3617e-05
2008 | 2007-08-11 | C | 282 | 0.046253 | 0.00090692
2008 | 2007-08-11 | C | 56 | 0.034965 | 0.0001801
2008 | 2007-08-11 | C | 719 | 0.027748 | 0.0023123
2008 | 2007-08-11 | C | 6 | 0.0020261 | 1.9296e-05
2008 | 2007-08-11 | C | 37 | 0.0038078 | 0.00011899
2008 | 2007-08-11 | C | 130 | 0.20517 | 0.00041809
2008 | 2007-08-12 | C | 328 | 0.098559 | 0.0010549
2008 | 2007-08-12 | C | 2161 | 0.1251 | 0.0069499
2008 | 2007-08-11 | C | 6 | 0.017463 | 1.9296e-05
2008 | 2007-08-11 | C | 80 | 0.04734 | 0.00025728
2008 | 2007-08-12 | C | 37 | 0.040577 | 0.00011899
2008 | 2007-08-12 | C | 105 | 0.062928 | 0.00033768
2008 | 2007-08-12 | C | 6 | 0.0017753 | 1.9296e-05
2008 | 2007-08-12 | C | 1 | 0.00011899 | 0
2008 | 2007-08-11 | C | 16 | 0.04523 | 5.1457e-05
2008 | 2007-08-12 | C | 338 | 0.063755 | 0.001087
2008 | 2007-08-12 | C | 196 | 0.10722 | 0.00063034
2008 | 2007-08-12 | C | 9 | 0.00049205 | 2.8944e-05
2008 | 2007-08-11 | C | 39 | 0.14098 | 0.00012543
2008 | 2007-08-12 | C | 250 | 0.034598 | 0.00080401
2008 | 2007-08-12 | C | 4 | 0.0015051 | 1.2864e-05
2008 | 2007-08-12 | B | 23 | 0.031511 | 7.3969e-05
2008 | 2007-08-12 | C | 10 | 0.0045346 | 3.216e-05
2008 | 2007-08-12 | C | 18 | 0.00075255 | 5.7889e-05
2008 | 2007-08-11 | C | 140 | 0.68437 | 0.00045025
2008 | 2007-08-13 | C | 25 | 0.0045829 | 8.0401e-05
2008 | 2007-08-13 | C | 63 | 0.0054705 | 0.00020261
2008 | 2007-08-13 | B | 1 | 0.00057889 | 0
2008 | 2007-08-13 | C | 1 | 0.00058532 | 0
2008 | 2007-08-11 | C | 1 | 0.0082556 | 0
2008 | 2007-08-13 | C | 13 | 0.0011706 | 4.1809e-05
2008 | 2007-08-13 | C | 8 | 0.0078471 | 2.5728e-05
2008 | 2007-08-13 | C | 2 | 0.0011385 | 6.4321e-06
2008 | 2007-08-13 | C | 8 | 0.00074612 | 2.5728e-05
2008 | 2007-08-14 | C | 682 | 0.030707 | 0.0021933
2008 | 2007-08-14 | C | 5512 | 0.21272 | 0.017727
2008 | 2007-08-14 | C | 2485 | 0.095902 | 0.0079919
2008 | 2007-08-11 | C | 6 | 0.018216 | 1.9296e-05
2008 | 2007-08-14 | C | 6 | 0.0012543 | 1.9296e-05
2008 | 2007-08-14 | C | 18 | 0.0037628 | 5.7889e-05
2008 | 2007-08-13 | C | 3 | 0.013575 | 9.6481e-06
2008 | 2007-08-15 | C | 264 | 0.076182 | 0.00084904
2008 | 2007-08-15 | C | 53 | 0.0088634 | 0.00017045
2008 | 2007-08-14 | B | 16 | 0.0084904 | 5.1457e-05
2008 | 2007-08-15 | B | 25 | 0.020904 | 8.0401e-05
2008 | 2007-08-15 | B | 5 | 0.0050492 | 1.608e-05
2008 | 2007-08-15 | C | 66 | 0.022712 | 0.00021226
2008 | 2007-08-16 | C | 515 | 0.066251 | 0.0016563
2008 | 2007-08-16 | B | 83 | 0.067267 | 0.00026693
2008 | 2007-08-16 | C | 252 | 0.007294 | 0.00081044
2008 | 2007-08-16 | C | 299 | 0.082546 | 0.0009616
2008 | 2007-08-16 | B | 4 | 0.00099054 | 1.2864e-05
2008 | 2007-08-16 | C | 82 | 0.012922 | 0.00026372
2008 | 2007-08-16 | B | 9 | 0.010912 | 2.8944e-05
2008 | 2007-08-16 | C | 414 | 0.030623 | 0.0013314
2008 | 2007-08-16 | C | 285 | 0.014665 | 0.00091657
2008 | 2007-08-16 | C | 206 | 0.106 | 0.00066251
2008 | 2007-08-16 | C | 190 | 0.024989 | 0.00061105
2008 | 2007-08-16 | C | 221 | 0.059349 | 0.00071075
2008 | 2007-08-16 | C | 171 | 0.079279 | 0.00054994
2008 | 2007-08-16 | C | 590 | 0.09413 | 0.0018975
2008 | 2007-08-16 | C | 131 | 0.086422 | 0.0004213
2008 | 2007-08-16 | C | 92 | 0.010356 | 0.00029588
2008 | 2007-08-16 | C | 239 | 0.082244 | 0.00076863
2008 | 2007-08-17 | C | 175 | 0.085026 | 0.00056281
2008 | 2007-08-16 | C | 111 | 0.10924 | 0.00035698
2008 | 2007-08-16 | C | 1 | 0.00066572 | 0
2008 | 2007-08-16 | C | 8 | 0.013121 | 2.5728e-05
2008 | 2007-08-16 | C | 451 | 0.29009 | 0.0014504
2008 | 2007-08-17 | C | 515 | 0.22158 | 0.0016563
2008 | 2007-08-17 | C | 265 | 0.087534 | 0.00085225
2008 | 2007-08-17 | C | 41 | 0.0044832 | 0.00013186
2008 | 2007-08-17 | C | 85 | 0.02843 | 0.00027336
2008 | 2007-08-17 | C | 11 | 0.0077475 | 3.5376e-05
2008 | 2007-08-17 | C | 97 | 0.074792 | 0.00031196
2008 | 2007-08-08 | B | 1 | 0.00070753 | 0
2008 | 2007-08-17 | C | 77 | 0.014327 | 0.00024764
2008 | 2007-08-18 | B | 2 | 0.0010034 | 6.4321e-06
2008 | 2007-08-18 | C | 12 | 0.0037435 | 3.8593e-05
2008 | 2007-08-18 | C | 256 | 0.14449 | 0.00082331
2008 | 2007-08-18 | C | 35 | 0.039171 | 0.00011256
2008 | 2007-08-18 | C | 151 | 0.003885 | 0.00048562
2008 | 2007-08-19 | B | 33 | 0.024198 | 0.00010613
2008 | 2007-08-19 | C | 704 | 0.14014 | 0.0022641
2008 | 2007-08-17 | B | 178 | 0.078999 | 0.00057246
2008 | 2007-08-16 | B | 28 | 0.033588 | 9.0049e-05
2008 | 2007-08-21 | C | 93 | 0.0071782 | 0.00029909
2008 | 2007-08-21 | B | 3 | 0.0018717 | 9.6481e-06
2008 | 2007-08-21 | B | 253 | 0.067534 | 0.00081366
2008 | 2007-08-21 | B | 17 | 0.014652 | 5.4673e-05
2008 | 2007-08-20 | B | 103 | 0.11561 | 0.00033125
2008 | 2007-08-21 | C | 43 | 0.01452 | 0.00013829
2008 | 2007-08-21 | B | 19 | 0.022853 | 6.1105e-05
2008 | 2007-08-21 | B | 41 | 0.01134 | 0.00013186
2008 | 2007-08-21 | B | 3 | 0.0016402 | 9.6481e-06
2008 | 2007-08-22 | C | 93 | 0.00059818 | 0.00029909
2008 | 2007-08-21 | B | 29 | 0.037772 | 9.3265e-05
2008 | 2007-08-22 | B | 17 | 0.013449 | 5.4673e-05
2008 | 2007-08-22 | B | 83 | 0.016817 | 0.00026693
2008 | 2007-08-22 | B | 9 | 0.010333 | 2.8944e-05
2008 | 2007-08-23 | B | 49 | 0.022377 | 0.00015759
2008 | 2007-08-23 | C | 8 | 0.0014151 | 2.5728e-05
2008 | 2007-08-23 | B | 56 | 0.028095 | 0.0001801
2008 | 2007-08-23 | B | 44 | 0.025375 | 0.00014151
2008 | 2007-08-23 | B | 3 | 0.0028173 | 9.6481e-06
2008 | 2007-08-23 | B | 4 | 0.0032289 | 1.2864e-05
2008 | 2007-08-23 | B | 17 | 0.012629 | 5.4673e-05
2008 | 2007-08-24 | B | 8 | 0.0082588 | 2.5728e-05
2008 | 2007-08-24 | B | 2 | 0.0014344 | 6.4321e-06
2008 | 2007-08-24 | C | 897 | 0.0057696 | 0.0028848
2008 | 2007-08-24 | C | 363 | 0.07239 | 0.0011674
2008 | 2007-08-25 | B | 197 | 0.051952 | 0.00063356
2008 | 2007-08-25 | B | 51 | 0.036248 | 0.00016402
2008 | 2007-08-25 | C | 19 | 0.0013443 | 6.1105e-05
2008 | 2007-08-27 | B | 1 | 4.5025e-05 | 0
2008 | 2007-08-27 | C | 406 | 0.10234 | 0.0013057
2008 | 2007-08-27 | C | 66 | 0.0061555 | 0.00021226
2008 | 2007-08-27 | C | 421 | 0.023017 | 0.001354
2008 | 2007-08-27 | C | 29 | 0.094944 | 9.3265e-05
2008 | 2007-08-28 | C | 206 | 0.017225 | 0.00066251
2008 | 2007-08-28 | B | 29 | 0.0097929 | 9.3265e-05
2008 | 2007-08-28 | B | 9 | 0.0028076 | 2.8944e-05
2008 | 2007-08-28 | B | 23 | 0.016051 | 7.3969e-05
2008 | 2007-08-28 | B | 31 | 0.025722 | 9.9697e-05
2008 | 2007-08-28 | C | 227 | 0.058783 | 0.00073004
2008 | 2007-08-28 | C | 15 | 0.0002412 | 4.8241e-05
2008 | 2007-08-29 | C | 52 | 0.013713 | 0.00016723
2008 | 2007-08-29 | C | 110 | 0.0067215 | 0.00035376
2008 | 2007-08-28 | B | 22 | 0.027169 | 7.0753e-05
2008 | 2007-08-28 | B | 5 | 0.0023638 | 1.608e-05
2008 | 2007-08-29 | B | 6 | 0.0015823 | 1.9296e-05
2008 | 2007-08-29 | B | 10 | 0.0084582 | 3.216e-05
2008 | 2007-08-28 | B | 55 | 0.052003 | 0.00017688
2008 | 2007-08-29 | B | 13 | 0.015051 | 4.1809e-05
2008 | 2007-08-30 | C | 97 | 0.021451 | 0.00031196
2008 | 2007-08-29 | B | 95 | 0.045536 | 0.00030552
2008 | 2007-08-30 | C | 7 | 0.0011256 | 2.2512e-05
2008 | 2007-08-30 | C | 13 | 0.0010034 | 4.1809e-05
2008 | 2007-08-30 | B | 4 | 0.0040265 | 1.2864e-05
2008 | 2007-08-30 | C | 1474 | 0.16002 | 0.0047404
2008 | 2007-08-30 | B | 121 | 0.065495 | 0.00038914
2008 | 2007-08-30 | C | 50 | 0.0036985 | 0.0001608
2008 | 2007-08-30 | C | 206 | 0.037763 | 0.00066251
2008 | 2007-08-31 | C | 964 | 0.083707 | 0.0031003
2008 | 2007-08-31 | C | 11 | 0.001132 | 3.5376e-05
2008 | 2007-08-31 | C | 1055 | 0.66278 | 0.0033929
2008 | 2007-08-30 | C | 80 | 0.030585 | 0.00025728
2008 | 2007-08-30 | B | 18 | 0.025703 | 5.7889e-05
2008 | 2007-08-30 | B | 2 | 0.0011642 | 6.4321e-06
2008 | 2007-08-30 | B | 103 | 0.013913 | 0.00033125
2008 | 2007-08-30 | B | 11 | 0.014398 | 3.5376e-05
2008 | 2007-08-31 | B | 8 | 0.0016981 | 2.5728e-05
2008 | 2007-08-31 | C | 16 | 0.0026757 | 5.1457e-05
2008 | 2007-08-31 | C | 10 | 0.0020261 | 3.216e-05
2008 | 2007-08-31 | C | 670 | 0.36727 | 0.0021547
2008 | 2007-08-31 | C | 744 | 0.0023927 | 0
2008 | 2007-08-31 | C | 1 | 2.5728e-05 | 0
2008 | 2007-08-31 | C | 26 | 0.011456 | 8.3617e-05
2008 | 2007-09-01 | C | 7 | 0.00090049 | 2.2512e-05
2008 | 2007-09-01 | C | 14 | 0.00067537 | 4.5025e-05
2008 | 2007-08-26 | B | 2 | 0.00065607 | 6.4321e-06
2008 | 2007-09-02 | B | 61 | 0.056499 | 0.00019618
2008 | 2007-08-26 | B | 2 | 0.00032804 | 6.4321e-06
2008 | 2007-09-02 | C | 68 | 0.017006 | 0.00021869
2008 | 2007-09-02 | C | 562 | 0.050608 | 0.0018074
2008 | 2007-09-02 | C | 589 | 0.054933 | 0.0018943
2008 | 2007-09-02 | C | 787 | 0.56071 | 0.002531
2008 | 2007-09-03 | C | 40 | 0.0095195 | 0.00012864
2008 | 2007-08-31 | B | 18 | 0.017309 | 5.7889e-05
2008 | 2007-09-03 | C | 1444 | 0.20898 | 0.004644
2008 | 2007-09-03 | C | 242 | 0.071345 | 0.00077828
2008 | 2007-09-04 | C | 208 | 0.11706 | 0.00066894
2008 | 2007-09-03 | C | 27 | 0.026224 | 8.6833e-05
2008 | 2007-09-04 | C | 120 | 0.027787 | 0.00038593
2008 | 2007-09-04 | B | 18 | 0.011809 | 5.7889e-05
2008 | 2007-09-04 | B | 34 | 0.025915 | 0.00010935
2008 | 2007-09-04 | C | 298 | 0.062391 | 0.00095838
2008 | 2007-09-04 | B | 53 | 0.060851 | 0.00017045
2008 | 2007-09-04 | C | 261 | 0.031057 | 0.00083939
2008 | 2007-09-04 | C | 206 | 0.021863 | 0.00066251
2008 | 2007-09-04 | C | 204 | 0.090532 | 0.00065607
2008 | 2007-09-04 | C | 312 | 0.4486 | 0.0010034
2008 | 2007-09-05 | B | 13 | 0.0043063 | 4.1809e-05
2008 | 2007-09-05 | B | 108 | 0.079539 | 0.00034733
2008 | 2007-09-05 | C | 144 | 0.056036 | 0.00046311
2008 | 2007-09-05 | C | 2 | 0.00030231 | 6.4321e-06
2008 | 2007-09-05 | B | 51 | 0.050354 | 0.00016402
2008 | 2007-09-05 | B | 26 | 0.00786 | 8.3617e-05
2008 | 2007-09-05 | C | 168 | 0.082234 | 0.0005403
2008 | 2007-09-05 | C | 90 | 0.016209 | 0.00028944
2008 | 2007-09-05 | C | 538 | 0.24358 | 0.0017302
2008 | 2007-09-06 | B | 5 | 0.0025889 | 1.608e-05
2008 | 2007-09-06 | C | 2248 | 0.25724 | 0.0072297
2008 | 2007-09-05 | B | 12 | 0.011269 | 3.8593e-05
2008 | 2007-09-06 | C | 2 | 0.00066894 | 6.4321e-06
2008 | 2007-09-06 | B | 59 | 0.055596 | 0.00018975
2008 | 2007-09-07 | C | 368 | 0.13952 | 0.0011835
2008 | 2007-09-07 | B | 51 | 0.0392 | 0.00016402
2008 | 2007-09-07 | C | 554 | 0.099659 | 0.0017817
2008 | 2007-09-03 | B | 4 | 0.0054544 | 1.2864e-05
2008 | 2007-09-10 | B | 28 | 0.0067537 | 9.0049e-05
2008 | 2007-09-10 | B | 20 | 0.025342 | 6.4321e-05
2008 | 2007-09-10 | B | 96 | 0.050942 | 0.00030874
2008 | 2007-09-07 | B | 88 | 0.033961 | 0.00028301
2008 | 2007-09-06 | B | 4 | 0.0016723 | 1.2864e-05
2008 | 2007-09-10 | C | 1328 | 0.22612 | 0.0042709
2008 | 2007-09-11 | C | 595 | 0.12102 | 0.0019135
2008 | 2007-09-11 | C | 199 | 0.00063999 | 0
2008 | 2007-09-11 | C | 15 | 0.0015437 | 4.8241e-05
2008 | 2007-09-11 | C | 28 | 0.010086 | 9.0049e-05
2008 | 2007-09-11 | B | 28 | 0.032148 | 9.0049e-05
2008 | 2007-09-11 | B | 2 | 0.0022963 | 6.4321e-06
2008 | 2007-09-12 | C | 90 | 0.013314 | 0.00028944
2008 | 2007-09-12 | C | 903 | 0.18586 | 0.0029041
2008 | 2007-09-12 | B | 142 | 0.026031 | 0.00045668
2008 | 2007-09-12 | B | 17 | 0.0086383 | 5.4673e-05
2008 | 2007-09-12 | C | 8 | 0.0033961 | 2.5728e-05
2008 | 2007-09-12 | B | 2 | 0.0015244 | 6.4321e-06
2008 | 2007-09-12 | B | 6 | 0.010941 | 1.9296e-05
2008 | 2007-09-12 | B | 2 | 0.0022963 | 6.4321e-06
2008 | 2007-09-12 | B | 55 | 0.029539 | 0.00017688
2008 | 2007-09-13 | B | 3 | 0.00028944 | 9.6481e-06
2008 | 2007-09-13 | B | 109 | 0.041014 | 0.00035055
2008 | 2007-09-13 | B | 18 | 0.011867 | 5.7889e-05
2008 | 2007-09-13 | B | 71 | 0.066218 | 0.00022834
2008 | 2007-09-13 | B | 11 | 0.013797 | 3.5376e-05
2008 | 2007-09-13 | B | 2 | 0.0015244 | 6.4321e-06
2008 | 2007-09-13 | C | 1170 | 0.53507 | 0.0037628
2008 | 2007-09-13 | C | 232 | 0.15072 | 0.00074612
2008 | 2007-09-13 | C | 22 | 0.0053772 | 7.0753e-05
2008 | 2007-09-13 | C | 10 | 0.0026372 | 3.216e-05
2008 | 2007-09-04 | B | 24 | 0.019837 | 7.7185e-05
2008 | 2007-09-12 | B | 103 | 0.12819 | 0.00033125
2008 | 2007-09-14 | C | 26 | 0.0018396 | 8.3617e-05
2008 | 2007-09-11 | B | 19 | 0.0066604 | 6.1105e-05
2008 | 2007-09-04 | B | 22 | 0.019245 | 7.0753e-05
2008 | 2007-09-13 | B | 24 | 0.007101 | 7.7185e-05
2008 | 2007-09-14 | C | 283 | 0.06799 | 0.00091014
2008 | 2007-09-14 | C | 50 | 0.019618 | 0.0001608
2008 | 2007-09-14 | B | 2 | 0.0011385 | 6.4321e-06
2008 | 2007-09-14 | B | 7 | 0.0061008 | 2.2512e-05
2008 | 2007-09-14 | B | 64 | 0.04734 | 0.00020583
2008 | 2007-09-14 | B | 10 | 0.0053065 | 3.216e-05
2008 | 2007-09-14 | C | 86 | 0.013176 | 0.00027658
2008 | 2007-09-14 | C | 12 | 0.0041294 | 3.8593e-05
2008 | 2007-09-15 | B | 284 | 0.049321 | 0.00091336
2008 | 2007-09-14 | C | 129 | 0.33356 | 0.00041487
2008 | 2007-09-11 | B | 4 | 0.0027787 | 1.2864e-05
2008 | 2007-09-11 | B | 114 | 0.087624 | 0.00036663
2008 | 2007-09-17 | C | 3 | 0.00057889 | 9.6481e-06
2008 | 2007-09-17 | C | 2 | 0.00015437 | 6.4321e-06
2008 | 2007-09-17 | B | 54 | 0.045501 | 0.00017367
2008 | 2007-09-17 | B | 1 | 0.0010291 | 0
2008 | 2007-09-17 | B | 7 | 0.0079243 | 2.2512e-05
2008 | 2007-09-17 | B | 2 | 0.0013314 | 6.4321e-06
2008 | 2007-09-18 | C | 258 | 0.033624 | 0.00082974
2008 | 2007-09-18 | B | 76 | 0.017598 | 0.00024442
2008 | 2007-09-18 | B | 59 | 0.02277 | 0.00018975
2008 | 2007-09-18 | B | 244 | 0.11128 | 0.00078471
2008 | 2007-09-18 | C | 43 | 0.0069145 | 0.00013829
2008 | 2007-09-19 | B | 62 | 0.031504 | 0.00019939
2008 | 2007-09-19 | C | 698 | 0.32159 | 0.0022448
2008 | 2007-09-20 | C | 139 | 0.018634 | 0.00044703
2008 | 2007-09-20 | B | 8 | 0.0034733 | 2.5728e-05
2008 | 2007-09-20 | B | 51 | 0.017878 | 0.00016402
2008 | 2007-09-20 | B | 34 | 0.029195 | 0.00010935
2008 | 2007-09-20 | B | 36 | 0.025625 | 0.00011578
2008 | 2007-09-20 | C | 148 | 0.020943 | 0.00047597
2008 | 2007-09-20 | C | 553 | 0.093777 | 0.0017785
2008 | 2007-09-21 | C | 185 | 0.026179 | 0.00059497
2008 | 2007-09-21 | B | 34 | 0.036303 | 0.00010935
2008 | 2007-09-21 | B | 23 | 0.021155 | 7.3969e-05
2008 | 2007-09-21 | B | 36 | 0.029871 | 0.00011578
2008 | 2007-09-21 | B | 125 | 0.14794 | 0.00040201
2008 | 2007-09-21 | B | 6 | 0.0063485 | 1.9296e-05
2008 | 2007-09-21 | C | 829 | 0.082649 | 0.0026661
2008 | 2007-09-22 | C | 12 | 0.0011964 | 3.8593e-05
2008 | 2007-09-22 | C | 2383 | 0.46749 | 0.0076638
2008 | 2007-09-23 | C | 294 | 0.075165 | 0.00094552
2008 | 2007-09-23 | C | 323 | 0.081118 | 0.0010388
2008 | 2007-09-23 | C | 240 | 0.096295 | 0.00077185
2008 | 2007-09-23 | C | 2485 | 1.2947 | 0.0079919
2008 | 2007-09-24 | C | 423 | 0.17467 | 0.0013604
2008 | 2007-09-19 | B | 95 | 0.12282 | 0.00030552
2008 | 2007-09-19 | B | 134 | 0.038355 | 0.00043095
2008 | 2007-09-24 | B | 29 | 0.00018653 | 9.3265e-05
2008 | 2007-09-24 | C | 542 | 0.0017431 | 0
2008 | 2007-09-24 | C | 2996 | 0.0096353 | 0
2008 | 2007-09-24 | C | 578 | 0.0018589 | 0
2008 | 2007-09-24 | C | 5 | 0.00099697 | 1.608e-05
2008 | 2007-09-24 | C | 2135 | 0.45768 | 0.0068663
2008 | 2007-09-24 | B | 46 | 0.046009 | 0.00014794
2008 | 2007-09-24 | C | 275 | 0.0017688 | 0.00088441
2008 | 2007-09-24 | C | 4 | 0.00064321 | 1.2864e-05
2008 | 2007-09-24 | C | 21 | 0.0014183 | 6.7537e-05
2008 | 2007-09-25 | B | 2 | 0.0016466 | 6.4321e-06
2008 | 2007-09-25 | B | 115 | 0.030697 | 0.00036985
2008 | 2007-09-25 | B | 12 | 0.014241 | 3.8593e-05
2008 | 2007-09-25 | B | 8 | 0.0032932 | 2.5728e-05
2008 | 2007-09-25 | B | 32 | 0.016569 | 0.00010291
2008 | 2007-09-25 | B | 50 | 0.044542 | 0.0001608
2008 | 2007-09-25 | C | 80 | 0.0059175 | 0.00025728
2008 | 2007-09-25 | C | 45 | 0.0060783 | 0.00014472
2008 | 2007-09-25 | B | 3 | 0.0014183 | 9.6481e-06
2008 | 2007-09-24 | B | 171 | 0.025297 | 0.00054994
2008 | 2007-09-25 | C | 1 | 0.0012832 | 0
2008 | 2007-09-26 | B | 7 | 0.0031742 | 2.2512e-05
2008 | 2007-09-26 | B | 23 | 0.0088023 | 7.3969e-05
2008 | 2007-09-26 | C | 1999 | 0.11084 | 0.0064289
2008 | 2007-09-26 | B | 1 | 0.0008619 | 0
2008 | 2007-09-26 | B | 13 | 0.010828 | 4.1809e-05
2008 | 2007-09-26 | C | 241 | 0.0038753 | 0.00077507
2008 | 2007-09-26 | B | 17 | 0.02094 | 5.4673e-05
2008 | 2007-09-24 | B | 34 | 0.038599 | 0.00010935
2008 | 2007-09-26 | C | 121 | 0.0019457 | 0.00038914
2008 | 2007-09-26 | C | 713 | 0.013758 | 0.002293
2008 | 2007-09-26 | B | 61 | 0.065916 | 0.00019618
2008 | 2007-09-27 | C | 9 | 0.0033286 | 2.8944e-05
2008 | 2007-09-27 | B | 35 | 0.023075 | 0.00011256
2008 | 2007-09-27 | B | 25 | 0.018251 | 8.0401e-05
2008 | 2007-09-27 | B | 50 | 0.049688 | 0.0001608
2008 | 2007-09-27 | B | 17 | 0.017714 | 5.4673e-05
2008 | 2007-09-28 | C | 12 | 0.005017 | 3.8593e-05
2008 | 2007-09-28 | B | 73 | 0.053528 | 0.00023477
2008 | 2007-09-28 | B | 10 | 0.008008 | 3.216e-05
2008 | 2007-09-27 | B | 70 | 0.070013 | 0.00022512
2008 | 2007-09-28 | C | 1211 | 0.15968 | 0.0038946
2008 | 2007-09-28 | C | 1412 | 0.33247 | 0.0045411
2008 | 2007-09-30 | C | 212 | 0.045681 | 0.0006818
2008 | 2007-09-29 | B | 1 | 0.00090371 | 0
2008 | 2007-09-30 | C | 43 | 0.026275 | 0.00013829
2008 | 2007-09-30 | C | 7 | 0.00049527 | 2.2512e-05
2008 | 2007-09-30 | C | 19 | 0.0092879 | 6.1105e-05
2008 | 2007-09-30 | C | 22 | 0.0022641 | 7.0753e-05
2008 | 2007-10-01 | B | 54 | 0.03126 | 0.00017367
2008 | 2007-10-01 | B | 37 | 0.034865 | 0.00011899
2008 | 2007-10-01 | C | 54 | 0.0097253 | 0.00017367
2008 | 2007-10-01 | B | 28 | 0.0181 | 9.0049e-05
2008 | 2007-10-01 | C | 880 | 0.35943 | 0.0028301
2008 | 2007-10-01 | B | 5 | 0.003811 | 1.608e-05
2008 | 2007-09-30 | C | 46 | 0.091278 | 0.00014794
2008 | 2007-10-01 | C | 145 | 0.088136 | 0.00046633
2008 | 2007-10-01 | C | 437 | 0.16384 | 0.0014054
2008 | 2007-10-01 | C | 25 | 0.0028944 | 8.0401e-05
2008 | 2007-10-01 | C | 294 | 0.08298 | 0.00094552
2008 | 2007-10-01 | C | 525 | 0.3897 | 0.0016884
2008 | 2007-10-02 | B | 59 | 0.0085386 | 0.00018975
2008 | 2007-10-02 | B | 10 | 0.0087476 | 3.216e-05
2008 | 2007-10-02 | C | 8 | 0.0051457 | 2.5728e-05
2008 | 2007-10-02 | C | 304 | 0.033768 | 0.00097768
2008 | 2007-10-03 | C | 304 | 0.040348 | 0.00097768
2008 | 2007-10-03 | C | 383 | 0.18237 | 0.0012317
2008 | 2007-10-03 | C | 182 | 0.029748 | 0.00058532
2008 | 2007-10-03 | C | 557 | 0.017913 | 0.0017913
2008 | 2007-10-03 | C | 134 | 0.011205 | 0.00043095
2008 | 2007-10-03 | C | 224 | 0.010806 | 0.00072039
2008 | 2007-10-03 | C | 95 | 0.023348 | 0.00030552
2008 | 2007-10-03 | C | 236 | 0.0053129 | 0.00075899
2008 | 2007-10-03 | C | 112 | 0.01909 | 0.0003602
2008 | 2007-10-03 | C | 273 | 0.052569 | 0.00087798
2008 | 2007-10-03 | C | 26 | 0.0057696 | 8.3617e-05
2008 | 2007-10-03 | C | 327 | 0.08044 | 0.0010516
2008 | 2007-10-02 | C | 51 | 0.0032804 | 0.00016402
2008 | 2007-10-02 | C | 81 | 0.011983 | 0.0002605
2008 | 2007-10-03 | C | 27 | 0.0050363 | 8.6833e-05
2008 | 2007-10-04 | C | 82 | 0.015559 | 0.00026372
2008 | 2007-10-04 | B | 100 | 0.040522 | 0.0003216
2008 | 2007-10-04 | B | 50 | 0.049688 | 0.0001608
2008 | 2007-10-02 | B | 60 | 0.05731 | 0.00019296
2008 | 2007-10-04 | B | 13 | 0.012417 | 4.1809e-05
2008 | 2007-10-04 | C | 85 | 0.015035 | 0.00027336
2008 | 2007-10-04 | B | 199 | 0.15432 | 0.00063999
2008 | 2007-10-04 | C | 126 | 0.0052679 | 0.00040522
2008 | 2007-10-05 | C | 92 | 0.030771 | 0.00029588
2008 | 2007-10-05 | C | 76 | 0.019065 | 0.00024442
2008 | 2007-10-02 | B | 27 | 0.025027 | 8.6833e-05
2008 | 2007-10-04 | C | 6 | 0.015205 | 1.9296e-05
2008 | 2007-10-05 | C | 14 | 0.0029266 | 4.5025e-05
2008 | 2007-10-05 | C | 133 | 0.066299 | 0.00042773
2008 | 2007-10-05 | B | 2 | 0.00019296 | 6.4321e-06
2008 | 2007-10-05 | C | 6 | 0.0012157 | 1.9296e-05
2008 | 2007-10-05 | C | 17 | 0.042863 | 5.4673e-05
2008 | 2007-10-05 | B | 1 | 4.5025e-05 | 0
2008 | 2007-10-04 | C | 541 | 0.10887 | 0.0017399
2008 | 2007-10-04 | C | 126 | 0.11775 | 0.00040522
2008 | 2007-10-05 | C | 231 | 0.24516 | 0.00074291
2008 | 2007-10-05 | C | 289 | 0.033212 | 0.00092944
2008 | 2007-10-05 | C | 282 | 0.026301 | 0.00090692
2008 | 2007-10-05 | C | 24 | 0.0036277 | 7.7185e-05
2008 | 2007-10-05 | C | 541 | 0.12179 | 0.0017399
2008 | 2007-10-06 | C | 152 | 0.0087991 | 0.00048884
2008 | 2007-10-06 | C | 6 | 0.0032321 | 1.9296e-05
2008 | 2007-10-06 | C | 30 | 0.0055959 | 9.6481e-05
2008 | 2007-10-06 | C | 217 | 0.10796 | 0.00069788
2008 | 2007-10-06 | C | 282 | 0.038091 | 0.00090692
2008 | 2007-10-06 | C | 842 | 0.18488 | 0.0027079
2008 | 2007-10-06 | C | 23 | 0.0029588 | 7.3969e-05
2008 | 2007-10-05 | C | 448 | 0.01873 | 0.0014408
2008 | 2007-10-05 | C | 578 | 1.6116 | 0.0018589
2008 | 2007-10-06 | C | 6 | 0.00137 | 1.9296e-05
2008 | 2007-10-06 | C | 56 | 0.035872 | 0.0001801
2008 | 2007-10-06 | C | 54 | 0.013199 | 0.00017367
2008 | 2007-10-06 | C | 93 | 0.0070528 | 0.00029909
2008 | 2007-10-05 | C | 108 | 0.21586 | 0.00034733
2008 | 2007-10-06 | C | 99 | 0.011144 | 0.00031839
2008 | 2007-10-06 | C | 54 | 0.038194 | 0.00017367
2008 | 2007-10-06 | C | 21 | 0.0085097 | 6.7537e-05
2008 | 2007-10-06 | C | 1268 | 0.32216 | 0.0040779
2008 | 2007-10-07 | C | 153 | 0.060947 | 0.00049205
2008 | 2007-10-07 | C | 90 | 0.041632 | 0.00028944
2008 | 2007-10-07 | C | 324 | 0.10958 | 0.001042
2008 | 2007-10-07 | C | 187 | 0.092088 | 0.0006014
2008 | 2007-10-05 | C | 85 | 0.32448 | 0.00027336
2008 | 2007-10-08 | C | 704 | 0.12905 | 0.0022641
2008 | 2007-10-08 | C | 58 | 0.018467 | 0.00018653
2008 | 2007-10-08 | C | 227 | 0.051103 | 0.00073004
2008 | 2007-10-08 | C | 70 | 0.013958 | 0.00022512
2008 | 2007-10-08 | C | 123 | 0.024921 | 0.00039557
2008 | 2007-10-08 | C | 217 | 0.031086 | 0.00069788
2008 | 2007-10-08 | C | 13 | 0.019525 | 4.1809e-05
2008 | 2007-10-08 | C | 1323 | 0.017019 | 0.0042548
2008 | 2007-10-08 | C | 239 | 0.15828 | 0.00076863
2008 | 2007-10-08 | C | 45 | 0.010873 | 0.00014472
2008 | 2007-10-08 | C | 1078 | 0.062404 | 0.0034669
2008 | 2007-10-08 | C | 14 | 0.0034669 | 4.5025e-05
2008 | 2007-10-08 | C | 719 | 0.067151 | 0.0023123
2008 | 2007-10-08 | C | 35 | 0.0068663 | 0.00011256
2008 | 2007-10-08 | C | 779 | 0.10611 | 0.0025053
2008 | 2007-10-08 | C | 1677 | 0.091686 | 0.0053933
2008 | 2007-10-08 | C | 1676 | 0.06982 | 0.0053901
2008 | 2007-10-08 | C | 617 | 0.059841 | 0.0019843
2008 | 2007-10-08 | C | 56 | 0.020351 | 0.0001801
2008 | 2007-10-08 | B | 176 | 0.0084904 | 0.00056602
2008 | 2007-10-08 | C | 227 | 0.043838 | 0.00073004
2008 | 2007-10-08 | C | 27 | 0.0049495 | 8.6833e-05
2008 | 2007-10-08 | C | 272 | 0.048112 | 0.00087476
2008 | 2007-10-08 | C | 6 | 0.0036277 | 1.9296e-05
2008 | 2007-10-08 | C | 300 | 0.17694 | 0.00096481
2008 | 2007-10-08 | C | 335 | 0.067415 | 0.0010774
2008 | 2007-10-09 | C | 35 | 0.0057406 | 0.00011256
2008 | 2007-10-09 | C | 1 | 0.00031196 | 0
2008 | 2007-10-09 | C | 1 | 0.00015115 | 0
2008 | 2007-10-09 | C | 10 | 0.0027658 | 3.216e-05
2008 | 2007-10-09 | C | 1 | 0.00014472 | 0
2008 | 2007-10-09 | B | 13 | 0.014089 | 4.1809e-05
2008 | 2007-10-09 | B | 102 | 0.069872 | 0.00032804
2008 | 2007-10-09 | B | 50 | 0.061266 | 0.0001608
2008 | 2007-10-09 | C | 214 | 0.030514 | 0.00068823
2008 | 2007-10-09 | C | 495 | 0.07285 | 0.0015919
2008 | 2007-10-09 | C | 245 | 0.028581 | 0.00078793
2008 | 2007-10-09 | C | 46 | 0.012588 | 0.00014794
2008 | 2007-10-10 | B | 14 | 0.0085997 | 4.5025e-05
2008 | 2007-10-10 | B | 8 | 0.0054801 | 2.5728e-05
2008 | 2007-10-10 | C | 115 | 0.03703 | 0.00036985
2008 | 2007-10-10 | C | 8 | 0.0014408 | 2.5728e-05
2008 | 2007-10-10 | B | 58 | 0.0554 | 0.00018653
2008 | 2007-10-10 | C | 190 | 0.0097768 | 0.00061105
2008 | 2007-10-10 | C | 208 | 0.071001 | 0.00066894
2008 | 2007-10-11 | C | 214 | 0.042558 | 0.00068823
2008 | 2007-10-11 | C | 201 | 0.047488 | 0.00064642
2008 | 2007-10-09 | B | 126 | 0.040464 | 0.00040522
2008 | 2007-10-11 | C | 1 | 0.00023799 | 0
2008 | 2007-10-08 | B | 8 | 0.0072554 | 2.5728e-05
2008 | 2007-10-09 | B | 115 | 0.0018492 | 0.00036985
2008 | 2007-10-11 | C | 189 | 0.029681 | 0.00060783
2008 | 2007-10-11 | C | 22 | 0.0053065 | 7.0753e-05
2008 | 2007-10-11 | C | 45 | 0.0031839 | 0.00014472
2008 | 2007-10-11 | B | 32 | 0.031903 | 0.00010291
2008 | 2007-10-11 | B | 50 | 0.049045 | 0.0001608
2008 | 2007-10-11 | B | 261 | 0.074705 | 0.00083939
2008 | 2007-10-11 | B | 27 | 0.019885 | 8.6833e-05
2008 | 2007-10-12 | B | 10 | 0.0028623 | 3.216e-05
2008 | 2007-10-12 | B | 32 | 0.0049398 | 0.00010291
2008 | 2007-10-12 | C | 19 | 0.0040329 | 6.1105e-05
2008 | 2007-10-12 | C | 54 | 0.0051328 | 0.00017367
2008 | 2007-10-13 | C | 29 | 0.021638 | 9.3265e-05
2008 | 2007-10-14 | C | 434 | 0.12912 | 0.0013958
2008 | 2007-10-14 | C | 86 | 0.035955 | 0.00027658
2008 | 2007-10-14 | C | 259 | 0.16587 | 0.00083296
2008 | 2007-10-14 | C | 35 | 0.0043899 | 0.00011256
2008 | 2007-10-14 | C | 402 | 0.022049 | 0.0012928
2008 | 2007-10-14 | C | 32 | 0.0063806 | 0.00010291
2008 | 2007-10-14 | C | 550 | 0.11758 | 0.0017688
2008 | 2007-10-14 | C | 35 | 0.012607 | 0.00011256
2008 | 2007-10-14 | C | 46 | 0.0068051 | 0.00014794
2008 | 2007-10-14 | C | 190 | 0.026172 | 0.00061105
2008 | 2007-10-14 | C | 194 | 0.141 | 0.00062391
2008 | 2007-10-14 | C | 312 | 0.17058 | 0.0010034
2008 | 2007-10-14 | C | 188 | 0.090136 | 0.00060462
2008 | 2007-10-14 | B | 26 | 0.029851 | 8.3617e-05
2008 | 2007-10-14 | C | 65 | 0.049543 | 0.00020904
2008 | 2007-10-14 | C | 174 | 0.058374 | 0.00055959
2008 | 2007-10-14 | C | 537 | 0.089219 | 0.001727
2008 | 2007-10-15 | C | 139 | 0.024059 | 0.00044703
2008 | 2007-10-15 | C | 24 | 0.0047083 | 7.7185e-05
2008 | 2007-10-14 | C | 52 | 0.055174 | 0.00016723
2008 | 2007-10-14 | C | 275 | 0.13859 | 0.00088441
2008 | 2007-10-15 | C | 23 | 0.0031067 | 7.3969e-05
2008 | 2007-10-15 | C | 29 | 0.015669 | 9.3265e-05
2008 | 2007-10-15 | C | 13 | 0.0079018 | 4.1809e-05
2008 | 2007-10-15 | C | 114 | 0.016132 | 0.00036663
2008 | 2007-10-15 | C | 829 | 0.36566 | 0.0026661
2008 | 2007-10-15 | C | 9 | 0.0044864 | 2.8944e-05
2008 | 2007-10-15 | C | 219 | 0.02906 | 0.00070431
2008 | 2007-10-15 | C | 33 | 0.0081913 | 0.00010613
2008 | 2007-10-16 | C | 706 | 0.28225 | 0.0022705
2008 | 2007-10-16 | B | 16 | 0.00777 | 5.1457e-05
2008 | 2007-10-16 | B | 6 | 0.0032997 | 1.9296e-05
2008 | 2007-10-16 | B | 2 | 0.00096481 | 6.4321e-06
2008 | 2007-10-16 | C | 13 | 0.0012961 | 4.1809e-05
2008 | 2007-10-16 | B | 24 | 0.019759 | 7.7185e-05
2008 | 2007-10-16 | B | 8 | 0.0080015 | 2.5728e-05
2008 | 2007-10-16 | C | 34 | 0.0047019 | 0.00010935
2008 | 2007-10-16 | B | 61 | 0.065524 | 0.00019618
2008 | 2007-10-16 | B | 3 | 0.0023734 | 9.6481e-06
2008 | 2007-10-16 | C | 105 | 0.044574 | 0.00033768
2008 | 2007-10-16 | C | 5 | 0.00046633 | 1.608e-05
2008 | 2007-10-16 | C | 186 | 0.094822 | 0.00059818
2008 | 2007-10-16 | C | 133 | 0.020103 | 0.00042773
2008 | 2007-10-16 | B | 8 | 0.011063 | 2.5728e-05
2008 | 2007-10-16 | C | 281 | 0.0244 | 0.00090371
2008 | 2007-10-16 | B | 22 | 0.013443 | 7.0753e-05
2008 | 2007-10-16 | C | 126 | 0.091831 | 0.00040522
2008 | 2007-10-17 | C | 448 | 0.028816 | 0.0014408
2008 | 2007-10-17 | C | 134 | 0.0025857 | 0.00043095
2008 | 2007-10-17 | C | 12 | 0.0025857 | 3.8593e-05
2008 | 2007-10-17 | C | 126 | 0.00081044 | 0.00040522
2008 | 2007-10-17 | C | 197 | 0.00063356 | 0
2008 | 2007-10-17 | C | 245 | 0.0031517 | 0.00078793
2008 | 2007-10-17 | C | 37 | 0.00023799 | 0.00011899
2008 | 2007-10-17 | C | 41 | 0.046282 | 0.00013186
2008 | 2007-10-17 | B | 74 | 0.053309 | 0.00023799
2008 | 2007-10-17 | C | 126 | 0.24736 | 0.00040522
2008 | 2007-10-17 | C | 46 | 0.0053258 | 0.00014794
2008 | 2007-10-17 | C | 3 | 0.00054994 | 9.6481e-06
2008 | 2007-10-16 | C | 578 | 1.3105 | 0.0018589
2008 | 2007-10-17 | C | 23 | 0.0028848 | 7.3969e-05
2008 | 2007-10-17 | C | 2 | 0.00079758 | 6.4321e-06
2008 | 2007-10-16 | C | 542 | 0.58917 | 0.0017431
2008 | 2007-10-17 | C | 169 | 0.025002 | 0.00054351
2008 | 2007-10-17 | C | 31 | 0.011565 | 9.9697e-05
2008 | 2007-10-17 | C | 63 | 0.053489 | 0.00020261
2008 | 2007-10-17 | C | 3 | 0.00043417 | 9.6481e-06
2008 | 2007-10-17 | C | 1 | 0.0002798 | 0
2008 | 2007-10-17 | C | 70 | 0.0087798 | 0.00022512
2008 | 2007-10-17 | C | 42 | 0.0025664 | 0.00013507
2008 | 2007-10-17 | C | 15 | 0.024268 | 4.8241e-05
2008 | 2007-10-17 | C | 268 | 0.061873 | 0.0008619
2008 | 2007-10-17 | C | 3 | 0.0010709 | 9.6481e-06
2008 | 2007-10-18 | C | 1 | 0.00055638 | 0
2008 | 2007-10-18 | B | 61 | 0.070036 | 0.00019618
2008 | 2007-10-18 | B | 50 | 0.042934 | 0.0001608
2008 | 2007-10-18 | C | 5 | 0.0020261 | 1.608e-05
2008 | 2007-10-18 | B | 78 | 0.044401 | 0.00025085
2008 | 2007-10-19 | C | 5 | 0.0039236 | 1.608e-05
2008 | 2007-10-19 | C | 100 | 0.0096481 | 0.0003216
2008 | 2007-10-20 | C | 897 | 0.39754 | 0.0028848
2008 | 2007-10-20 | C | 11 | 0.0023702 | 3.5376e-05
2008 | 2007-10-20 | C | 83 | 0.007741 | 0.00026693
2008 | 2007-10-20 | C | 104 | 0.058812 | 0.00033447
2008 | 2007-10-20 | C | 272 | 0.12425 | 0.00087476
2008 | 2007-10-21 | C | 690 | 0.30305 | 0.0022191
2008 | 2007-10-21 | C | 90 | 0.041178 | 0.00028944
2008 | 2007-10-21 | C | 724 | 0.20352 | 0.0023284
2008 | 2007-10-21 | C | 77 | 0.013125 | 0.00024764
2008 | 2007-10-21 | C | 248 | 0.07258 | 0.00079758
2008 | 2007-10-21 | C | 164 | 0.021625 | 0.00052743
2008 | 2007-10-21 | C | 3 | 0.00055959 | 9.6481e-06
2008 | 2007-10-21 | C | 310 | 0.061613 | 0.00099697
2008 | 2007-10-21 | C | 45 | 0.0034733 | 0.00014472
2008 | 2007-10-22 | C | 611 | 0.065569 | 0.001965
2008 | 2007-10-22 | C | 236 | 0.087943 | 0.00075899
2008 | 2007-10-22 | C | 48 | 0.015746 | 0.00015437
2008 | 2007-10-22 | C | 48 | 0.0087991 | 0.00015437
2008 | 2007-10-22 | C | 53 | 0.033328 | 0.00017045
2008 | 2007-10-22 | C | 2592 | 0.016672 | 0.008336
2008 | 2007-10-22 | C | 136 | 0.0078729 | 0.00043738
2008 | 2007-10-22 | C | 382 | 0.18574 | 0.0012285
2008 | 2007-10-22 | C | 889 | 0.16914 | 0.0028591
2008 | 2007-10-23 | C | 281 | 0.034341 | 0.00090371
2008 | 2007-10-23 | B | 25 | 0.029668 | 8.0401e-05
2008 | 2007-10-23 | C | 1 | 0.00018653 | 0
2008 | 2007-10-23 | C | 23 | 0.0032546 | 7.3969e-05
2008 | 2007-10-23 | C | 3 | 0.00075255 | 9.6481e-06
2008 | 2007-10-23 | C | 6 | 0.0026243 | 1.9296e-05
2008 | 2007-10-23 | C | 7 | 0.0012382 | 2.2512e-05
2008 | 2007-10-23 | B | 45 | 0.026195 | 0.00014472
2008 | 2007-10-23 | C | 119 | 0.02742 | 0.00038271
2008 | 2007-10-23 | C | 24 | 0.0024699 | 7.7185e-05
2008 | 2007-10-23 | C | 61 | 0.06818 | 0.00019618
2008 | 2007-10-23 | B | 29 | 0.0053161 | 9.3265e-05
2008 | 2007-10-23 | C | 5566 | 0.98453 | 0.017901
2008 | 2007-10-23 | C | 281 | 0.11206 | 0.00090371
2008 | 2007-10-23 | C | 182 | 0.099086 | 0.00058532
2008 | 2007-10-23 | C | 202 | 0.081205 | 0.00064964
2008 | 2007-10-23 | C | 113 | 0.13851 | 0.00036341
2008 | 2007-10-24 | C | 367 | 0.075407 | 0.0011803
2008 | 2007-10-23 | C | 261 | 0.075545 | 0.00083939
2008 | 2007-10-24 | B | 81 | 0.054965 | 0.0002605
2008 | 2007-10-24 | C | 281 | 0.033437 | 0.00090371
2008 | 2007-10-24 | B | 8 | 0.0049141 | 2.5728e-05
2008 | 2007-10-24 | C | 2 | 0.00080401 | 6.4321e-06
2008 | 2007-10-24 | C | 36 | 0.0021998 | 0.00011578
2008 | 2007-10-24 | C | 226 | 0.17448 | 0.00072683
2008 | 2007-10-24 | C | 37 | 0.0033318 | 0.00011899
2008 | 2007-10-24 | C | 1376 | 0.25224 | 0.0044253
2008 | 2007-10-24 | C | 36 | 0.0034733 | 0.00011578
2008 | 2007-10-24 | C | 102 | 0.022635 | 0.00032804
2008 | 2007-10-24 | B | 73 | 0.042024 | 0.00023477
2008 | 2007-10-25 | C | 51 | 0.0013121 | 0.00016402
2008 | 2007-10-24 | C | 77 | 0.045967 | 0.00024764
2008 | 2007-10-25 | C | 1425 | 0.26581 | 0.0045829
2008 | 2007-10-25 | C | 36 | 0.0025471 | 0.00011578
2008 | 2007-10-25 | B | 19 | 0.012099 | 6.1105e-05
2008 | 2007-10-25 | B | 32 | 0.019965 | 0.00010291
2008 | 2007-10-25 | C | 65 | 0.036373 | 0.00020904
2008 | 2007-10-25 | C | 70 | 0.034894 | 0.00022512
2008 | 2007-10-25 | C | 61 | 0.031585 | 0.00019618
2008 | 2007-10-25 | C | 82 | 0.066234 | 0.00026372
2008 | 2007-10-25 | C | 25 | 0.0016884 | 8.0401e-05
2008 | 2007-10-25 | B | 16 | 0.0091078 | 5.1457e-05
2008 | 2007-10-25 | C | 883 | 0.096552 | 0.0028398
2008 | 2007-10-26 | C | 686 | 0.21194 | 0.0022062
2008 | 2007-10-26 | C | 475 | 0.015276 | 0.0015276
2008 | 2007-10-23 | B | 67 | 0.01573 | 0.00021547
2008 | 2007-10-26 | B | 114 | 0.06416 | 0.00036663
2008 | 2007-10-26 | C | 149 | 0.0071879 | 0.00047919
2008 | 2007-10-26 | C | 113 | 0.057419 | 0.00036341
2008 | 2007-10-26 | C | 21 | 0.0095902 | 6.7537e-05
2008 | 2007-10-26 | C | 477 | 0.10459 | 0.0015341
2008 | 2007-10-27 | C | 770 | 0.3982 | 0.0024764
2008 | 2007-10-27 | C | 159 | 0.056249 | 0.00051135
2008 | 2007-10-27 | C | 93 | 0.029311 | 0.00029909
2008 | 2007-10-27 | C | 86 | 0.034643 | 0.00027658
2008 | 2007-10-28 | C | 525 | 0.11288 | 0.0016884
2008 | 2007-10-27 | C | 89 | 0.040156 | 0.00028623
2008 | 2007-10-28 | C | 1040 | 0.040136 | 0.0033447
2008 | 2007-10-28 | B | 9810 | 11.6417 | 0.031549
2008 | 2007-10-28 | C | 123 | 0.14715 | 0.00039557
2008 | 2007-10-29 | B | 96 | 0.015437 | 0.00030874
2008 | 2007-10-29 | C | 9 | 0.0039364 | 2.8944e-05
2008 | 2007-10-29 | C | 17 | 0.0048112 | 5.4673e-05
2008 | 2007-10-29 | C | 545 | 0.4016 | 0.0017527
2008 | 2007-10-30 | C | 182 | 0.068482 | 0.00058532
2008 | 2007-10-30 | B | 89 | 0.040358 | 0.00028623
2008 | 2007-10-30 | B | 81 | 0.05236 | 0.0002605
2008 | 2007-10-30 | B | 102 | 0.12433 | 0.00032804
2008 | 2007-10-30 | C | 1 | 0.00037949 | 0
2008 | 2007-10-30 | B | 1 | 0.0012832 | 0
2008 | 2007-10-30 | C | 259 | 0.042108 | 0.00083296
2008 | 2007-10-30 | C | 9 | 0.00017367 | 2.8944e-05
2008 | 2007-10-30 | C | 46 | 0.0016273 | 0.00014794
2008 | 2007-10-30 | B | 1 | 0.0002412 | 0
2008 | 2007-10-26 | B | 4 | 0.002084 | 1.2864e-05
2008 | 2007-10-31 | B | 95 | 0.042773 | 0.00030552
2008 | 2007-10-31 | B | 6 | 0.0031453 | 1.9296e-05
2008 | 2007-10-31 | C | 109 | 0.0028044 | 0.00035055
2008 | 2007-10-31 | B | 85 | 0.074628 | 0.00027336
2008 | 2007-10-31 | B | 58 | 0.055213 | 0.00018653
2008 | 2007-11-01 | C | 3 | 0.00021226 | 9.6481e-06
2008 | 2007-11-01 | C | 145 | 0.047099 | 0.00046633
2008 | 2007-11-01 | C | 326 | 0.024114 | 0.0010484
2008 | 2007-11-01 | B | 3 | 0.0040233 | 9.6481e-06
2008 | 2007-11-01 | C | 248 | 0.043069 | 0.00079758
2008 | 2007-11-01 | C | 87 | 0.0053161 | 0.0002798
2008 | 2007-11-01 | B | 22 | 0.013655 | 7.0753e-05
2008 | 2007-11-01 | B | 4 | 0.0019296 | 1.2864e-05
2008 | 2007-11-02 | C | 86 | 0.051489 | 0.00027658
2008 | 2007-11-02 | C | 18 | 0.0019682 | 5.7889e-05
2008 | 2007-11-02 | B | 8 | 0.0044253 | 2.5728e-05
2008 | 2007-11-02 | B | 16 | 0.011475 | 5.1457e-05
2008 | 2007-11-01 | B | 59 | 0.076278 | 0.00018975
2008 | 2007-11-03 | C | 99 | 0.042027 | 0.00031839
2008 | 2007-11-03 | C | 467 | 0.32208 | 0.0015019
2008 | 2007-11-03 | C | 3758 | 1.5377 | 0.012086
2008 | 2007-11-04 | C | 67 | 0.10907 | 0.00021547
2008 | 2007-11-04 | C | 3583 | 0.057615 | 0.011523
2008 | 2007-11-04 | C | 135 | 0.0073808 | 0.00043417
2008 | 2007-11-04 | C | 135 | 0.012864 | 0.00043417
2008 | 2007-11-04 | C | 5990 | 0.23117 | 0.019264
2008 | 2007-11-04 | C | 96 | 0.10343 | 0.00030874
2008 | 2007-11-04 | C | 6377 | 1.0459 | 0.020509
2008 | 2007-11-04 | C | 1136 | 0.25173 | 0.0036534
2008 | 2007-11-04 | C | 31 | 0.0049849 | 9.9697e-05
2008 | 2007-11-04 | C | 264 | 0.14051 | 0.00084904
2008 | 2007-11-04 | C | 3483 | 0.33604 | 0.011201
2008 | 2007-11-05 | C | 1470 | 0.27891 | 0.0047276
2008 | 2007-11-04 | C | 822 | 0.28915 | 0.0026436
2008 | 2007-11-05 | C | 610 | 0.26166 | 0.0019618
2008 | 2007-11-05 | C | 357 | 0.06774 | 0.0011481
2008 | 2007-11-05 | C | 96 | 0.074715 | 0.00030874
2008 | 2007-11-05 | C | 234 | 0.14134 | 0.00075255
2008 | 2007-11-05 | C | 1199 | 0.29702 | 0.003856
2008 | 2007-11-05 | C | 43 | 0.0020743 | 0.00013829
2008 | 2007-11-05 | C | 56 | 0.01891 | 0.0001801
2008 | 2007-11-06 | C | 1772 | 0.48523 | 0.0056988
2008 | 2007-11-06 | B | 134 | 0.011636 | 0.00043095
2008 | 2007-11-06 | C | 91 | 0.037168 | 0.00029266
2008 | 2007-11-06 | B | 4 | 0.0031131 | 1.2864e-05
2008 | 2007-11-06 | C | 796 | 0.00256 | 0
2008 | 2007-11-06 | C | 74 | 0.063305 | 0.00023799
2008 | 2007-11-06 | B | 58 | 0.027607 | 0.00018653
2008 | 2007-11-07 | B | 5 | 0.0041326 | 1.608e-05
2008 | 2007-11-07 | B | 2 | 0.0025278 | 6.4321e-06
2008 | 2007-11-07 | B | 26 | 0.020403 | 8.3617e-05
2008 | 2007-11-07 | B | 11 | 0.010365 | 3.5376e-05
2008 | 2007-11-07 | C | 709 | 0.12323 | 0.0022802
2008 | 2007-11-08 | C | 345 | 0.014424 | 0.0011095
2008 | 2007-11-08 | B | 184 | 0.069235 | 0.00059175
2008 | 2007-11-08 | B | 1 | 0.00079436 | 0
2008 | 2007-11-08 | C | 28 | 0.0060333 | 9.0049e-05
2008 | 2007-11-08 | B | 11 | 0.0083842 | 3.5376e-05
2008 | 2007-11-08 | B | 407 | 0.08062 | 0.0013089
2008 | 2007-11-08 | B | 43 | 0.011616 | 0.00013829
2008 | 2007-11-09 | C | 2 | 0.00038593 | 6.4321e-06
2008 | 2007-11-09 | C | 40 | 0.0038593 | 0.00012864
2008 | 2007-11-09 | C | 3222 | 0.39376 | 0.010362
2008 | 2007-11-09 | C | 292 | 0.12222 | 0.00093908
2008 | 2007-11-09 | B | 7 | 0.0066411 | 2.2512e-05
2008 | 2007-11-09 | C | 86 | 0.01134 | 0.00027658
2008 | 2007-11-10 | C | 242 | 0.051978 | 0.00077828
2008 | 2007-11-10 | C | 5 | 0.0043417 | 1.608e-05
2008 | 2007-11-10 | C | 303 | 0.025336 | 0.00097446
2008 | 2007-11-10 | C | 237 | 0.05183 | 0.0007622
2008 | 2007-11-11 | C | 21 | 0.0058757 | 6.7537e-05
2008 | 2007-11-11 | C | 72 | 0.0011578 | 0.00023156
2008 | 2007-11-11 | C | 344 | 0.086705 | 0.0011063
2008 | 2007-11-11 | C | 766 | 0.1941 | 0.0024635
2008 | 2007-11-12 | B | 1 | 0.00030231 | 0
2008 | 2007-11-12 | C | 2542 | 0.052952 | 0.0081752
2008 | 2007-11-12 | C | 3 | 0.0016402 | 9.6481e-06
2008 | 2007-11-12 | C | 116 | 0.037306 | 0.00037306
2008 | 2007-11-12 | B | 5 | 0.0041326 | 1.608e-05
2008 | 2007-11-12 | B | 37 | 0.03427 | 0.00011899
2008 | 2007-11-12 | C | 39 | 0.017058 | 0.00012543
2008 | 2007-11-12 | C | 677 | 0.24434 | 0.0021773
2008 | 2007-11-13 | B | 9 | 0.0018524 | 2.8944e-05
2008 | 2007-11-08 | B | 3 | 0.0060558 | 9.6481e-06
2008 | 2007-11-13 | B | 3 | 0.0014569 | 9.6481e-06
2008 | 2007-11-13 | B | 24 | 0.018061 | 7.7185e-05
2008 | 2007-11-13 | B | 91 | 0.0096578 | 0.00029266
2008 | 2007-11-13 | C | 281 | 0.036148 | 0.00090371
2008 | 2007-11-13 | B | 80 | 0.017238 | 0.00025728
2008 | 2007-11-13 | B | 1 | 0.00029909 | 0
2008 | 2007-11-13 | B | 16 | 0.0096224 | 5.1457e-05
2008 | 2007-11-13 | B | 41 | 0.053402 | 0.00013186
2008 | 2007-11-13 | C | 196 | 0.044754 | 0.00063034
2008 | 2007-11-13 | C | 59 | 0.015006 | 0.00018975
2008 | 2007-11-14 | C | 208 | 0.041066 | 0.00066894
2008 | 2007-11-13 | B | 51 | 0.03182 | 0.00016402
2008 | 2007-11-14 | C | 51 | 0.049698 | 0.00016402
2008 | 2007-11-14 | C | 185 | 0.032154 | 0.00059497
2008 | 2007-11-14 | C | 3 | 0.00022191 | 9.6481e-06
2008 | 2007-11-14 | C | 15 | 0.0020261 | 4.8241e-05
2008 | 2007-11-14 | C | 4 | 0.0011449 | 1.2864e-05
2008 | 2007-11-14 | C | 218 | 0.055461 | 0.0007011
2008 | 2007-11-14 | C | 336 | 0.29392 | 0.0010806
2008 | 2007-11-14 | C | 125 | 0.12009 | 0.00040201
2008 | 2007-11-14 | C | 285 | 0.061346 | 0.00091657
2008 | 2007-11-14 | C | 205 | 0.07331 | 0.00065929
2008 | 2007-11-15 | B | 12 | 0.0036277 | 3.8593e-05
2008 | 2007-11-15 | B | 18 | 0.00086833 | 5.7889e-05
2008 | 2007-11-14 | C | 14 | 0.0026565 | 4.5025e-05
2008 | 2007-11-15 | B | 15 | 0.0023156 | 4.8241e-05
2008 | 2007-11-14 | C | 1113 | 0.12756 | 0.0035795
2008 | 2007-11-15 | B | 62 | 0.033299 | 0.00019939
2008 | 2007-11-14 | C | 69 | 0.03912 | 0.00022191
2008 | 2007-11-15 | C | 12 | 0.00065607 | 3.8593e-05
2008 | 2007-11-15 | B | 7 | 0.0075191 | 2.2512e-05
2008 | 2007-11-14 | B | 3 | 0.0035023 | 9.6481e-06
2008 | 2007-11-14 | B | 6 | 0.0068502 | 1.9296e-05
2008 | 2007-11-14 | B | 40 | 0.036534 | 0.00012864
2008 | 2007-11-15 | B | 23 | 0.020637 | 7.3969e-05
2008 | 2007-11-15 | B | 6 | 0.0030681 | 1.9296e-05
2008 | 2007-11-15 | B | 23 | 0.022191 | 7.3969e-05
2008 | 2007-11-15 | B | 131 | 0.011375 | 0.0004213
2008 | 2007-11-15 | B | 2 | 0.00053386 | 6.4321e-06
2008 | 2007-11-15 | B | 188 | 0.00786 | 0.00060462
2008 | 2007-11-15 | B | 96 | 0.007101 | 0.00030874
2008 | 2007-11-15 | C | 329 | 0.038802 | 0.0010581
2008 | 2007-11-15 | C | 9 | 0.0077571 | 2.8944e-05
2008 | 2007-11-15 | B | 55 | 0.076413 | 0.00017688
2008 | 2007-11-16 | B | 5 | 0.0038432 | 1.608e-05
2008 | 2007-11-16 | B | 3 | 0.0015533 | 9.6481e-06
2008 | 2007-11-16 | C | 35 | 0.00022512 | 0.00011256
2008 | 2007-11-16 | B | 26 | 0.022075 | 8.3617e-05
2008 | 2007-11-16 | C | 23 | 0.0045121 | 7.3969e-05
2008 | 2007-11-16 | B | 26 | 0.03236 | 8.3617e-05
2008 | 2007-11-16 | C | 95 | 0.03208 | 0.00030552
2008 | 2007-11-16 | C | 1 | 0.0013572 | 0
2008 | 2007-11-17 | B | 1 | 0.00047276 | 0
2008 | 2007-11-17 | B | 2 | 0.00090692 | 6.4321e-06
2008 | 2007-11-17 | C | 14 | 0.0016659 | 4.5025e-05
2008 | 2007-11-16 | C | 1385 | 0.82404 | 0.0044542
2008 | 2007-11-18 | B | 1 | 0.00053386 | 0
2008 | 2007-11-18 | C | 406 | 0.094027 | 0.0013057
2008 | 2007-11-18 | C | 826 | 0.077712 | 0.0026565
2008 | 2007-11-19 | C | 979 | 0.012594 | 0.0031485
2008 | 2007-11-19 | B | 1 | 0.00063034 | 0
2008 | 2007-11-19 | C | 6 | 0.0010227 | 1.9296e-05
2008 | 2007-11-17 | B | 16 | 0.0080787 | 5.1457e-05
2008 | 2007-11-20 | B | 24 | 0.0064835 | 7.7185e-05
2008 | 2007-11-20 | B | 1 | 0.00042773 | 0
2008 | 2007-11-20 | B | 15 | 0.007815 | 4.8241e-05
2008 | 2007-11-20 | B | 6 | 0.0038978 | 1.9296e-05
2008 | 2007-11-13 | B | 1 | 0.0010613 | 0
2008 | 2007-11-20 | B | 57 | 0.0043995 | 0.00018331
2008 | 2007-11-20 | B | 40 | 0.042323 | 0.00012864
2008 | 2007-11-20 | B | 11 | 0.011568 | 3.5376e-05
2008 | 2007-11-20 | B | 19 | 0.023525 | 6.1105e-05
2008 | 2007-11-20 | B | 3 | 0.00329 | 9.6481e-06
2008 | 2007-11-20 | C | 128 | 0.021419 | 0.00041165
2008 | 2007-11-21 | B | 52 | 0.0073583 | 0.00016723
2008 | 2007-11-21 | B | 7 | 0.0010356 | 2.2512e-05
2008 | 2007-11-21 | B | 16 | 0.0069981 | 5.1457e-05
2008 | 2007-11-21 | B | 5 | 0.0021708 | 1.608e-05
2008 | 2007-11-21 | B | 37 | 0.015707 | 0.00011899
2008 | 2007-11-21 | B | 95 | 0.044912 | 0.00030552
2008 | 2007-11-21 | B | 23 | 0.010873 | 7.3969e-05
2008 | 2007-11-21 | C | 53 | 0.0049431 | 0.00017045
2008 | 2007-11-21 | B | 6 | 0.0058854 | 1.9296e-05
2008 | 2007-11-21 | B | 130 | 0.082395 | 0.00041809
2008 | 2007-11-21 | C | 29 | 0.0067151 | 9.3265e-05
2008 | 2007-11-22 | C | 281 | 0.019882 | 0.00090371
2008 | 2007-11-22 | B | 11 | 0.011674 | 3.5376e-05
2008 | 2007-11-22 | B | 13 | 0.015344 | 4.1809e-05
2008 | 2007-11-22 | B | 60 | 0.063678 | 0.00019296
2008 | 2007-11-22 | B | 130 | 0.098668 | 0.00041809
2008 | 2007-11-22 | C | 28 | 0.0017109 | 9.0049e-05
2008 | 2007-11-22 | C | 501 | 0.051264 | 0.0016112
2008 | 2007-11-22 | C | 471 | 0.041021 | 0.0015148
2008 | 2007-11-23 | B | 1 | 0.00016723 | 0
2008 | 2007-11-23 | B | 14 | 0.0020261 | 4.5025e-05
2008 | 2007-11-23 | C | 7706 | 0.38949 | 0.024783
2008 | 2007-11-23 | B | 60 | 0.065607 | 0.00019296
2008 | 2007-11-23 | C | 2164 | 0.094532 | 0.0069595
2008 | 2007-11-24 | B | 10 | 0.0059497 | 3.216e-05
2008 | 2007-11-24 | C | 308 | 0.10309 | 0.00099054
2008 | 2007-11-25 | B | 2 | 0.00054673 | 6.4321e-06
2008 | 2007-11-25 | B | 1 | 0.00056924 | 0
2008 | 2007-11-25 | C | 294 | 0.21936 | 0.00094552
2008 | 2007-11-26 | C | 76 | 0.033241 | 0.00024442
2008 | 2007-11-27 | C | 1766 | 0.27731 | 0.0056795
2008 | 2007-11-27 | B | 83 | 0.041908 | 0.00026693
2008 | 2007-11-27 | B | 5 | 0.005017 | 1.608e-05
2008 | 2007-11-27 | B | 60 | 0.067923 | 0.00019296
2008 | 2007-11-27 | B | 30 | 0.031549 | 9.6481e-05
2008 | 2007-11-27 | C | 1629 | 1.5947 | 0.0052389
2008 | 2007-11-28 | C | 461 | 0.053338 | 0.0014826
2008 | 2007-11-28 | B | 2 | 0.00039236 | 6.4321e-06
2008 | 2007-11-28 | C | 102 | 0.039474 | 0.00032804
2008 | 2007-11-28 | B | 7 | 0.0056056 | 2.2512e-05
2008 | 2007-11-28 | B | 1 | 0.00057889 | 0
2008 | 2007-11-23 | B | 4 | 0.0045925 | 1.2864e-05
2008 | 2007-11-28 | B | 4 | 0.0040136 | 1.2864e-05
2008 | 2007-11-28 | B | 2 | 0.0024378 | 6.4321e-06
2008 | 2007-11-28 | C | 236 | 0.045674 | 0.00075899
2008 | 2007-11-28 | C | 241 | 0.023461 | 0.00077507
2008 | 2007-11-28 | C | 785 | 0.1185 | 0.0025246
2008 | 2007-11-29 | C | 101 | 0.0022737 | 0.00032482
2008 | 2007-11-29 | C | 78 | 0.020049 | 0.00025085
2008 | 2007-11-29 | C | 2 | 0.0011385 | 6.4321e-06
2008 | 2007-11-29 | B | 113 | 0.004361 | 0.00036341
2008 | 2007-11-29 | C | 25 | 0.017367 | 8.0401e-05
2008 | 2007-11-29 | B | 60 | 0.047855 | 0.00019296
2008 | 2007-11-29 | C | 21 | 0.0010806 | 6.7537e-05
2008 | 2007-11-29 | C | 22 | 0.0033961 | 7.0753e-05
2008 | 2007-11-29 | B | 136 | 0.020341 | 0.00043738
2008 | 2007-11-30 | C | 129 | 0.027796 | 0.00041487
2008 | 2007-11-30 | C | 293 | 0.013192 | 0.0009423
2008 | 2007-11-30 | C | 39 | 0.013044 | 0.00012543
2008 | 2007-11-30 | C | 462 | 0.010401 | 0.0014858
2008 | 2007-12-01 | B | 1 | 7.3969e-05 | 0
2008 | 2007-12-01 | C | 17 | 0.0045378 | 5.4673e-05
2008 | 2007-12-01 | C | 228 | 0.052145 | 0.00073326
2008 | 2007-12-01 | C | 211 | 0.05046 | 0.00067859
2008 | 2007-12-02 | B | 82 | 0.0023734 | 0.00026372
2008 | 2007-12-02 | C | 418 | 0.10313 | 0.0013443
2008 | 2007-12-02 | C | 178 | 0.080658 | 0.00057246
2008 | 2007-12-03 | B | 46 | 0.052814 | 0.00014794
2008 | 2007-12-03 | C | 30 | 0.013797 | 9.6481e-05
2008 | 2007-12-04 | C | 17 | 0.01416 | 5.4673e-05
2008 | 2007-11-30 | B | 113 | 0.039975 | 0.00036341
2008 | 2007-11-30 | B | 8 | 0.0040651 | 2.5728e-05
2008 | 2007-11-29 | B | 2 | 0.0017431 | 6.4321e-06
2008 | 2007-12-04 | C | 2725 | 0.019698 | 0.0087637
2008 | 2007-12-04 | B | 47 | 0.019197 | 0.00015115
2008 | 2007-12-04 | B | 8 | 0.0037563 | 2.5728e-05
2008 | 2007-12-04 | B | 1 | 0.00054351 | 0
2008 | 2007-12-04 | B | 12 | 0.007487 | 3.8593e-05
2008 | 2007-12-04 | B | 1 | 0.0010131 | 0
2008 | 2007-12-04 | B | 5 | 0.0022995 | 1.608e-05
2008 | 2007-12-04 | B | 33 | 0.035341 | 0.00010613
2008 | 2007-12-04 | C | 98 | 0.024931 | 0.00031517
2008 | 2007-12-04 | C | 121 | 0.026893 | 0.00038914
2008 | 2007-12-05 | B | 83 | 0.012012 | 0.00026693
2008 | 2007-12-05 | B | 1 | 0.00087476 | 0
2008 | 2007-12-05 | C | 28 | 0.022963 | 9.0049e-05
2008 | 2007-12-05 | B | 65 | 0.0056442 | 0.00020904
2008 | 2007-12-05 | B | 5 | 0.005805 | 1.608e-05
2008 | 2007-12-06 | C | 318 | 0.18856 | 0.0010227
2008 | 2007-12-06 | C | 372 | 0.098263 | 0.0011964
2008 | 2007-12-06 | C | 4 | 0.00074612 | 1.2864e-05
2008 | 2007-12-06 | C | 375 | 0.045732 | 0.001206
2008 | 2007-12-06 | C | 736 | 0.15966 | 0.002367
2008 | 2007-12-06 | C | 129 | 0.04114 | 0.00041487
2008 | 2007-12-06 | C | 783 | 0.18807 | 0.0025182
2008 | 2007-12-07 | C | 459 | 0.010333 | 0.0014762
2008 | 2007-12-07 | C | 58 | 0.038239 | 0.00018653
2008 | 2007-12-06 | C | 72 | 0.042259 | 0.00023156
2008 | 2007-12-06 | C | 268 | 0.10329 | 0.0008619
2008 | 2007-12-06 | B | 1 | 0.00021226 | 0
2008 | 2007-12-07 | B | 8 | 0.0017238 | 2.5728e-05
2008 | 2007-12-07 | B | 29 | 0.010912 | 9.3265e-05
2008 | 2007-12-07 | C | 14 | 0.00090049 | 4.5025e-05
2008 | 2007-12-07 | B | 34 | 0.012793 | 0.00010935
2008 | 2007-12-07 | B | 12 | 0.0072168 | 3.8593e-05
2008 | 2007-12-07 | B | 5 | 0.003811 | 1.608e-05
2008 | 2007-12-07 | B | 1 | 0.0011481 | 0
2008 | 2007-12-07 | C | 50 | 0.018975 | 0.0001608
2008 | 2007-12-08 | C | 9 | 0.0039943 | 2.8944e-05
2008 | 2007-12-09 | B | 109 | 0.095349 | 0.00035055
2008 | 2007-12-09 | C | 454 | 0.049714 | 0.0014601
2008 | 2007-12-09 | C | 374 | 0.048385 | 0.0012028
2008 | 2007-12-09 | C | 418 | 0.31188 | 0.0013443
2008 | 2007-12-09 | C | 575 | 0.098909 | 0.0018492
2008 | 2007-12-09 | C | 66 | 0.058944 | 0.00021226
2008 | 2007-12-09 | C | 1134 | 0.043764 | 0.003647
2008 | 2007-12-09 | C | 1111 | 0.063758 | 0.003573
2008 | 2007-12-09 | C | 303 | 0.039921 | 0.00097446
2008 | 2007-12-09 | C | 313 | 0.0030199 | 0.0010066
2008 | 2007-12-10 | C | 742 | 0.19832 | 0.0023863
2008 | 2007-12-10 | B | 33 | 0.033112 | 0.00010613
2008 | 2007-12-10 | C | 77 | 0.020213 | 0.00024764
2008 | 2007-12-10 | B | 44 | 0.02349 | 0.00014151
2008 | 2007-12-10 | C | 20 | 0.0046311 | 6.4321e-05
2008 | 2007-12-10 | C | 898 | 0.040432 | 0.002888
2008 | 2007-12-11 | B | 2 | 0.0019425 | 6.4321e-06
2008 | 2007-12-11 | C | 603 | 0.021332 | 0.0019393
2008 | 2007-12-11 | B | 17 | 0.012793 | 5.4673e-05
2008 | 2007-12-11 | C | 1240 | 0.22731 | 0.0039879
2008 | 2007-12-11 | B | 5 | 0.0029266 | 1.608e-05
2008 | 2007-12-11 | C | 3 | 0.00042452 | 9.6481e-06
2008 | 2007-12-11 | C | 2 | 0.00077185 | 6.4321e-06
2008 | 2007-12-11 | C | 394 | 0.067952 | 0.0012671
2008 | 2007-12-11 | C | 73 | 0.017756 | 0.00023477
2008 | 2007-12-12 | C | 272 | 0.12189 | 0.00087476
2008 | 2007-12-12 | B | 19 | 0.0080658 | 6.1105e-05
2008 | 2007-12-12 | B | 1 | 0.00033768 | 0
2008 | 2007-12-12 | C | 331 | 0.10103 | 0.0010645
2008 | 2007-12-12 | B | 75 | 0.024844 | 0.0002412
2008 | 2007-12-12 | B | 2 | 0.0021162 | 6.4321e-06
2008 | 2007-12-12 | C | 20 | 0.00090049 | 6.4321e-05
2008 | 2007-12-12 | C | 114 | 0.087155 | 0.00036663
2008 | 2007-12-12 | C | 133 | 0.0055605 | 0.00042773
2008 | 2007-12-13 | C | 368 | 0.0082845 | 0.0011835
2008 | 2007-12-13 | C | 709 | 0.15361 | 0.0022802
2008 | 2007-12-05 | B | 1 | 0.00015115 | 0
2008 | 2007-12-13 | C | 27 | 0.013199 | 8.6833e-05
2008 | 2007-12-13 | B | 7 | 0.0052904 | 2.2512e-05
2008 | 2007-12-13 | C | 174 | 0.09708 | 0.00055959
2008 | 2007-12-13 | B | 2 | 0.0020454 | 6.4321e-06
2008 | 2007-12-13 | C | 25 | 0.0029748 | 8.0401e-05
2008 | 2007-12-13 | C | 715 | 0.2846 | 0.0022995
2008 | 2007-12-13 | C | 998 | 0.24261 | 0.0032096
2008 | 2007-12-13 | B | 9 | 0.0058178 | 2.8944e-05
2008 | 2007-12-13 | B | 52 | 0.065427 | 0.00016723
2008 | 2007-12-14 | C | 34 | 0.0066701 | 0.00010935
2008 | 2007-12-14 | B | 5 | 0.0043738 | 1.608e-05
2008 | 2007-12-14 | C | 4 | 0.0016338 | 1.2864e-05
2008 | 2007-12-14 | B | 14 | 0.010401 | 4.5025e-05
2008 | 2007-12-14 | C | 10 | 0.0027015 | 3.216e-05
2008 | 2007-12-14 | B | 50 | 0.020743 | 0.0001608
2008 | 2007-12-14 | C | 1 | 0.00041809 | 0
2008 | 2007-12-15 | C | 390 | 0.10946 | 0.0012543
2008 | 2007-12-15 | C | 3759 | 0.45939 | 0.012089
2008 | 2007-12-15 | C | 26 | 0.0097832 | 8.3617e-05
2008 | 2007-12-16 | C | 187 | 0.10344 | 0.0006014
2008 | 2007-12-17 | C | 304 | 0.13864 | 0.00097768
2008 | 2007-12-13 | B | 111 | 0.0060687 | 0.00035698
2008 | 2007-12-17 | B | 71 | 0.031739 | 0.00022834
2008 | 2007-12-17 | B | 82 | 0.053798 | 0.00026372
2008 | 2007-12-17 | B | 62 | 0.012961 | 0.00019939
2008 | 2007-12-17 | B | 23 | 0.02478 | 7.3969e-05
2008 | 2007-12-17 | C | 10 | 0.0034412 | 3.216e-05
2008 | 2007-12-17 | C | 92 | 0.12302 | 0.00029588
2008 | 2007-12-17 | C | 467 | 0.052566 | 0.0015019
2008 | 2007-12-17 | C | 736 | 0.18226 | 0.002367
2008 | 2007-12-17 | B | 105 | 0.039509 | 0.00033768
2008 | 2007-12-18 | C | 783 | 0.032736 | 0.0025182
2008 | 2007-12-18 | C | 59 | 0.0068309 | 0.00018975
2008 | 2007-12-17 | B | 67 | 0.021763 | 0.00021547
2008 | 2007-12-18 | C | 15 | 0.0011095 | 4.8241e-05
2008 | 2007-12-18 | C | 276 | 0.12563 | 0.00088763
2008 | 2007-12-18 | C | 783 | 0.022663 | 0.0025182
2008 | 2007-12-18 | B | 100 | 0.039236 | 0.0003216
2008 | 2007-12-18 | C | 25 | 0.0057889 | 8.0401e-05
2008 | 2007-12-18 | C | 649 | 0.012523 | 0.0020872
2008 | 2007-12-18 | C | 28 | 0.0020711 | 9.0049e-05
2008 | 2007-12-18 | C | 743 | 0.20706 | 0.0023895
2008 | 2007-12-18 | C | 865 | 0.058419 | 0.0027819
2008 | 2007-12-18 | C | 865 | 0.013909 | 0.0027819
2008 | 2007-12-18 | C | 595 | 0.041159 | 0.0019135
2008 | 2007-12-18 | C | 610 | 0.14843 | 0.0019618
2008 | 2007-12-19 | C | 408 | 0.088097 | 0.0013121
2008 | 2007-12-18 | C | 41 | 0.051029 | 0.00013186
2008 | 2007-12-19 | C | 246 | 0.045848 | 0.00079115
2008 | 2007-12-17 | B | 13 | 0.0075674 | 4.1809e-05
2008 | 2007-12-18 | B | 72 | 0.047469 | 0.00023156
2008 | 2007-12-18 | B | 8 | 0.0078729 | 2.5728e-05
2008 | 2007-12-19 | C | 783 | 0.012591 | 0.0025182
2008 | 2007-12-17 | B | 37 | 0.042957 | 0.00011899
2008 | 2007-12-19 | C | 198 | 0.093606 | 0.00063678
2008 | 2007-12-19 | B | 11 | 0.0055895 | 3.5376e-05
2008 | 2007-12-19 | B | 45 | 0.038641 | 0.00014472
2008 | 2007-12-19 | B | 26 | 0.020068 | 8.3617e-05
2008 | 2007-12-19 | C | 5 | 0.0027176 | 1.608e-05
2008 | 2007-12-19 | C | 53 | 0.0025568 | 0.00017045
2008 | 2007-12-19 | C | 510 | 0.069685 | 0.0016402
2008 | 2007-12-19 | B | 2 | 0.00093908 | 6.4321e-06
2008 | 2007-12-19 | B | 88 | 0.02349 | 0.00028301
2008 | 2007-12-20 | B | 15 | 0.0053065 | 4.8241e-05
2008 | 2007-12-19 | B | 28 | 0.025484 | 9.0049e-05
2008 | 2007-12-20 | C | 9880 | 0.3247 | 0.031775
2008 | 2007-12-20 | C | 43 | 0.0091271 | 0.00013829
2008 | 2007-12-20 | C | 1333 | 0.1676 | 0.004287
2008 | 2007-12-21 | C | 484 | 0.23672 | 0.0015566
2008 | 2007-12-21 | C | 14 | 0.0014858 | 4.5025e-05
2008 | 2007-12-22 | C | 361 | 0.11674 | 0.001161
2008 | 2007-12-22 | C | 723 | 0.17045 | 0.0023252
2008 | 2007-12-23 | C | 480 | 0.094803 | 0.0015437
2008 | 2007-12-23 | C | 1617 | 0.19327 | 0.0052003
2008 | 2007-12-24 | C | 18 | 0.0018524 | 5.7889e-05
2008 | 2007-12-25 | C | 1368 | 0.21504 | 0.0043995
2008 | 2007-12-25 | C | 447 | 0.064331 | 0.0014376
2008 | 2007-12-25 | C | 2005 | 0.38486 | 0.0064482
2008 | 2007-12-25 | C | 551 | 0.051389 | 0.001772
2008 | 2007-12-25 | C | 983 | 0.12914 | 0.0031614
2008 | 2007-12-25 | C | 51 | 0.0062327 | 0.00016402
2008 | 2007-12-26 | C | 563 | 0.021728 | 0.0018106
2008 | 2007-12-26 | C | 563 | 0.12493 | 0.0018106
2008 | 2007-12-26 | C | 374 | 0.0084325 | 0.0012028
2008 | 2007-12-26 | C | 295 | 0.021821 | 0.00094873
2008 | 2007-12-26 | C | 574 | 0.069428 | 0.001846
2008 | 2007-12-26 | C | 82 | 0.0063292 | 0.00026372
2008 | 2007-12-26 | C | 3 | 0.00057889 | 9.6481e-06
2008 | 2007-12-26 | C | 298 | 0.05758 | 0.00095838
2008 | 2007-12-26 | C | 1368 | 0.22866 | 0.0043995
2008 | 2007-12-26 | C | 523 | 0.027947 | 0.001682
2008 | 2007-12-26 | C | 17 | 0.011864 | 5.4673e-05
2008 | 2007-12-27 | C | 2164 | 0.86298 | 0.0069595
2008 | 2007-12-27 | C | 7721 | 0.12416 | 0.024831
2008 | 2007-12-27 | C | 207 | 0.045587 | 0.00066572
2008 | 2007-12-27 | C | 1211 | 0.093471 | 0.0038946
2008 | 2007-12-27 | C | 1016 | 0.01307 | 0.0032675
2008 | 2007-12-27 | C | 1204 | 0.046465 | 0.0038721
2008 | 2007-12-27 | B | 77 | 0.014115 | 0.00024764
2008 | 2007-12-28 | C | 25 | 0.0041005 | 8.0401e-05
2008 | 2007-12-28 | C | 2 | 0.00052743 | 6.4321e-06
2008 | 2007-12-28 | C | 3601 | 0.036537 | 0.011581
2008 | 2007-12-28 | C | 272 | 0.26068 | 0.00087476
2008 | 2007-12-29 | C | 10 | 0.0012864 | 3.216e-05
2008 | 2007-12-29 | B | 2 | 0.0011706 | 6.4321e-06
2008 | 2007-12-29 | C | 304 | 0.063514 | 0.00097768
2008 | 2007-12-30 | B | 1 | 9.6481e-05 | 0
2008 | 2007-12-31 | C | 211 | 0.020229 | 0.00067859
2008 | 2007-12-31 | C | 395 | 0.085113 | 0.0012703
2008 | 2008-01-01 | C | 27 | 0.013285 | 8.6833e-05
2008 | 2008-01-01 | C | 118 | 0.22374 | 0.00037949
2008 | 2008-01-02 | C | 210 | 0.040619 | 0.00067537
2008 | 2008-01-02 | C | 50 | 0.029909 | 0.0001608
2008 | 2008-01-01 | C | 321 | 0.15431 | 0.0010324
2008 | 2008-01-02 | C | 91 | 0.0079018 | 0.00029266
2008 | 2008-01-02 | C | 8 | 0.00061748 | 2.5728e-05
2008 | 2008-01-03 | C | 165 | 0.087557 | 0.00053065
2008 | 2008-01-04 | C | 41 | 0.0015823 | 0.00013186
2008 | 2008-01-04 | C | 17 | 0.003007 | 5.4673e-05
2008 | 2008-01-04 | C | 17 | 0.0013668 | 5.4673e-05
2008 | 2008-01-05 | C | 105 | 0.044488 | 0.00033768
2008 | 2008-01-06 | C | 812 | 0.031337 | 0.0026114
2008 | 2007-12-02 | B | 144 | 0.0032418 | 0.00046311
2008 | 2008-01-07 | C | 97 | 0.0039815 | 0.00031196
2008 | 2008-01-07 | B | 5 | 0.0017206 | 1.608e-05
2008 | 2008-01-07 | C | 48 | 0.0092622 | 0.00015437
2008 | 2008-01-07 | C | 842 | 0.1589 | 0.0027079
2008 | 2008-01-07 | C | 502 | 0.053759 | 0.0016145
2008 | 2008-01-07 | C | 59 | 0.0036052 | 0.00018975
2008 | 2008-01-08 | B | 6 | 0.0015823 | 1.9296e-05
2008 | 2008-01-08 | C | 67 | 0.030382 | 0.00021547
2008 | 2008-01-08 | B | 30 | 0.024796 | 9.6481e-05
2008 | 2008-01-08 | C | 223 | 0.046153 | 0.00071718
2008 | 2008-01-08 | C | 89 | 0.015743 | 0.00028623
2008 | 2008-01-09 | C | 298 | 0.10802 | 0.00095838
2008 | 2008-01-09 | B | 12 | 0.0019682 | 3.8593e-05
2008 | 2008-01-09 | B | 5 | 0.0025085 | 1.608e-05
2008 | 2008-01-08 | B | 22 | 0.012806 | 7.0753e-05
2008 | 2008-01-08 | B | 17 | 0.014051 | 5.4673e-05
2008 | 2008-01-09 | B | 6 | 0.004689 | 1.9296e-05
2008 | 2008-01-09 | C | 2 | 0.00062391 | 6.4321e-06
2008 | 2008-01-10 | B | 48 | 0.022538 | 0.00015437
2008 | 2008-01-10 | C | 1231 | 0.050399 | 0.003959
2008 | 2008-01-10 | C | 211 | 0.022358 | 0.00067859
2008 | 2008-01-10 | C | 6 | 0.0025085 | 1.9296e-05
2008 | 2008-01-10 | B | 30 | 0.033479 | 9.6481e-05
2008 | 2008-01-10 | C | 19 | 0.013932 | 6.1105e-05
2008 | 2008-01-10 | C | 269 | 0.0069209 | 0.00086512
2008 | 2008-01-11 | C | 685 | 0.14741 | 0.002203
2008 | 2008-01-11 | B | 28 | 0.007294 | 9.0049e-05
2008 | 2008-01-11 | C | 24 | 0.0024699 | 7.7185e-05
2008 | 2008-01-11 | B | 1 | 0.00040844 | 0
2008 | 2008-01-11 | C | 1 | 0.00033768 | 0
2008 | 2008-01-12 | C | 53 | 0.0090339 | 0.00017045
2008 | 2008-01-12 | C | 284 | 0.031054 | 0.00091336
2008 | 2008-01-13 | C | 2819 | 0.011671 | 0.009066
2008 | 2008-01-13 | C | 320 | 0.03602 | 0.0010291
2008 | 2008-01-14 | B | 4 | 0.0040394 | 1.2864e-05
2008 | 2008-01-14 | B | 65 | 0.033727 | 0.00020904
2008 | 2008-01-14 | C | 739 | 0.12828 | 0.0023767
2008 | 2008-01-14 | C | 9 | 0.0068598 | 2.8944e-05
2008 | 2008-01-15 | C | 1 | 0.00050492 | 0
2008 | 2008-01-15 | B | 2 | 0.0011771 | 6.4321e-06
2008 | 2008-01-15 | B | 75 | 0.070431 | 0.0002412
2008 | 2008-01-15 | C | 61 | 0.012163 | 0.00019618
2008 | 2008-01-15 | B | 55 | 0.046343 | 0.00017688
2008 | 2008-01-15 | B | 39 | 0.041014 | 0.00012543
2008 | 2008-01-15 | C | 1 | 0.0022705 | 0
2008 | 2008-01-16 | C | 812 | 0.03656 | 0.0026114
2008 | 2008-01-16 | B | 74 | 0.070724 | 0.00023799
2008 | 2008-01-16 | B | 3 | 0.0014183 | 9.6481e-06
2008 | 2008-01-16 | C | 45 | 0.031839 | 0.00014472
2008 | 2008-01-17 | C | 464 | 0.022384 | 0.0014922
2008 | 2008-01-17 | C | 251 | 0.0096867 | 0.00080723
2008 | 2008-01-16 | B | 74 | 0.065209 | 0.00023799
2008 | 2008-01-16 | C | 1298 | 0.29033 | 0.0041744
2008 | 2008-01-17 | C | 73 | 0.046028 | 0.00023477
2008 | 2008-01-17 | B | 4 | 0.0048241 | 1.2864e-05
2008 | 2008-01-17 | B | 1 | 0.00068823 | 0
2008 | 2008-01-17 | B | 17 | 0.014543 | 5.4673e-05
2008 | 2008-01-17 | B | 27 | 0.0049495 | 8.6833e-05
2008 | 2008-01-18 | B | 265 | 0.048578 | 0.00085225
2008 | 2008-01-18 | C | 812 | 0.031337 | 0.0026114
2008 | 2008-01-18 | B | 348 | 0.0078343 | 0.0011192
2008 | 2008-01-18 | B | 279 | 0.077166 | 0.00089728
2008 | 2008-01-18 | C | 173 | 0.040882 | 0.00055638
2008 | 2008-01-19 | C | 2172 | 0.020956 | 0.0069852
2008 | 2008-01-19 | C | 7748 | 0.19934 | 0.024918
2008 | 2008-01-19 | C | 109 | 0.036808 | 0.00035055
2008 | 2008-01-19 | C | 99 | 0.022589 | 0.00031839
2008 | 2008-01-19 | C | 238 | 0.042693 | 0.00076542
2008 | 2008-01-19 | C | 273 | 0.046015 | 0.00087798
2008 | 2008-01-19 | C | 5546 | 0.57984 | 0.017836
2008 | 2008-01-20 | C | 26 | 0.0068566 | 8.3617e-05
2008 | 2008-01-20 | C | 645 | 0.058082 | 0.0020743
2008 | 2008-01-20 | C | 733 | 0.14147 | 0.0023574
2008 | 2008-01-20 | C | 2 | 0.00095838 | 6.4321e-06
2008 | 2008-01-20 | C | 1066 | 0.1787 | 0.0034283
2008 | 2008-01-20 | C | 43 | 0.0051167 | 0.00013829
2008 | 2008-01-21 | C | 772 | 0.10179 | 0.0024828
2008 | 2008-01-21 | C | 571 | 0.26939 | 0.0018364
2008 | 2008-01-18 | B | 1 | 0.0010452 | 0
2008 | 2008-01-15 | B | 45 | 0.023156 | 0.00014472
2008 | 2008-01-21 | C | 310 | 0.048993 | 0.00099697
2008 | 2008-01-20 | C | 15 | 0.027545 | 4.8241e-05
2008 | 2008-01-21 | B | 10 | 0.0090692 | 3.216e-05
2008 | 2008-01-21 | C | 540 | 0.32123 | 0.0017367
2008 | 2008-01-21 | C | 450 | 0.057278 | 0.0014472
2008 | 2008-01-21 | B | 2 | 0.0014858 | 6.4321e-06
2008 | 2008-01-22 | C | 82 | 0.010549 | 0.00026372
2008 | 2008-01-21 | C | 8 | 0.0037563 | 2.5728e-05
2008 | 2008-01-21 | C | 64 | 0.040754 | 0.00020583
2008 | 2008-01-22 | C | 1049 | 0.023615 | 0.0033736
2008 | 2008-01-21 | C | 955 | 0.018428 | 0.0030713
2008 | 2008-01-21 | C | 163 | 0.027783 | 0.00052422
2008 | 2008-01-21 | C | 1699 | 0.38625 | 0.0054641
2008 | 2008-01-21 | C | 785 | 0.070689 | 0.0025246
2008 | 2008-01-21 | C | 286 | 0.084621 | 0.00091979
2008 | 2008-01-21 | C | 1639 | 0.91724 | 0.0052711
2008 | 2008-01-21 | C | 136 | 0.023181 | 0.00043738
2008 | 2008-01-21 | C | 1049 | 0.49407 | 0.0033736
2008 | 2008-01-22 | B | 45 | 0.0063678 | 0.00014472
2008 | 2008-01-22 | B | 100 | 0.015115 | 0.0003216
2008 | 2008-01-22 | B | 38 | 0.016621 | 0.00012221
2008 | 2008-01-21 | C | 851 | 0.51316 | 0.0027369
2008 | 2008-01-22 | B | 3 | 0.0011095 | 9.6481e-06
2008 | 2008-01-22 | C | 51 | 0.0036084 | 0.00016402
2008 | 2008-01-22 | C | 4 | 0.002084 | 1.2864e-05
2008 | 2008-01-22 | C | 269 | 0.014707 | 0.00086512
2008 | 2008-01-22 | C | 252 | 0.14831 | 0.00081044
2008 | 2008-01-22 | C | 17 | 0.0072715 | 5.4673e-05
2008 | 2008-01-22 | C | 386 | 0.31283 | 0.0012414
2008 | 2008-01-22 | C | 159 | 0.074506 | 0.00051135
2008 | 2008-01-22 | C | 218 | 0.13531 | 0.0007011
2008 | 2008-01-22 | C | 288 | 0.033344 | 0.00092622
2008 | 2008-01-22 | C | 184 | 0.097047 | 0.00059175
2008 | 2008-01-22 | C | 252 | 0.016209 | 0.00081044
2008 | 2008-01-22 | C | 285 | 0.081025 | 0.00091657
2008 | 2008-01-22 | C | 10 | 0.0026372 | 3.216e-05
2008 | 2008-01-22 | C | 1604 | 0.72198 | 0.0051585
2008 | 2008-01-22 | C | 704 | 0.83545 | 0.0022641
2008 | 2008-01-22 | C | 426 | 0.030141 | 0.00137
2008 | 2008-01-22 | C | 782 | 0.30431 | 0.0025149
2008 | 2008-01-22 | C | 87 | 0.035444 | 0.0002798
2008 | 2008-01-22 | C | 320 | 0.077069 | 0.0010291
2008 | 2008-01-22 | C | 169 | 0.070113 | 0.00054351
2008 | 2008-01-22 | C | 54 | 0.040117 | 0.00017367
2008 | 2008-01-22 | C | 9 | 0.00098411 | 2.8944e-05
2008 | 2008-01-22 | C | 117 | 0.053962 | 0.00037628
2008 | 2008-01-22 | C | 1301 | 0.1835 | 0.0041841
2008 | 2008-01-22 | C | 4 | 0.003126 | 1.2864e-05
2008 | 2008-01-22 | C | 17 | 0.0044285 | 5.4673e-05
2008 | 2008-01-22 | C | 211 | 0.063925 | 0.00067859
2008 | 2008-01-23 | C | 281 | 0.018074 | 0.00090371
2008 | 2008-01-23 | C | 126 | 0.06362 | 0.00040522
2008 | 2008-01-23 | C | 446 | 0.086061 | 0.0014344
2008 | 2008-01-23 | C | 347 | 0.01674 | 0.001116
2008 | 2008-01-22 | C | 4 | 0.00083617 | 1.2864e-05
2008 | 2008-01-22 | C | 2 | 0.00072039 | 6.4321e-06
2008 | 2008-01-23 | C | 546 | 0.012292 | 0.001756
2008 | 2008-01-22 | C | 683 | 0.066003 | 0.0021966
2008 | 2008-01-22 | C | 27 | 0.0092912 | 8.6833e-05
2008 | 2008-01-22 | C | 3177 | 0.037023 | 0.010217
2008 | 2008-01-22 | C | 59 | 0.012713 | 0.00018975
2008 | 2008-01-22 | C | 39 | 0.005895 | 0.00012543
2008 | 2008-01-22 | C | 61 | 0.035901 | 0.00019618
2008 | 2008-01-22 | C | 200 | 0.037306 | 0.00064321
2008 | 2008-01-23 | C | 29 | 0.0046633 | 9.3265e-05
2008 | 2008-01-23 | C | 5 | 0.0012382 | 1.608e-05
2008 | 2008-01-22 | C | 156 | 0.051646 | 0.0005017
2008 | 2008-01-23 | C | 7 | 0.0030166 | 2.2512e-05
2008 | 2008-01-22 | C | 2 | 0.0049977 | 6.4321e-06
2008 | 2008-01-22 | C | 205 | 0.054637 | 0.00065929
2008 | 2008-01-22 | C | 54 | 0.0039943 | 0.00017367
2008 | 2008-01-22 | C | 189 | 0.20642 | 0.00060783
2008 | 2008-01-22 | C | 1069 | 0.13724 | 0.003438
2008 | 2008-01-22 | C | 524 | 0.11496 | 0.0016852
2008 | 2008-01-23 | C | 50 | 0.026159 | 0.0001608
2008 | 2008-01-23 | C | 2 | 0.0020904 | 6.4321e-06
2008 | 2008-01-22 | B | 83 | 0.071271 | 0.00026693
2008 | 2008-01-23 | C | 27 | 0.0054705 | 8.6833e-05
2008 | 2008-01-22 | C | 325 | 0.25528 | 0.0010452
2008 | 2008-01-23 | C | 797 | 0.14354 | 0.0025632
2008 | 2008-01-22 | C | 99 | 0.039249 | 0.00031839
2008 | 2008-01-23 | C | 24 | 0.0017753 | 7.7185e-05
2008 | 2008-01-23 | C | 21 | 0.01891 | 6.7537e-05
2008 | 2008-01-22 | C | 8 | 0.027607 | 2.5728e-05
2008 | 2008-01-23 | C | 66 | 0.00084904 | 0.00021226
2008 | 2008-01-23 | C | 5 | 0.0010774 | 1.608e-05
2008 | 2008-01-23 | C | 24 | 0.0010034 | 7.7185e-05
2008 | 2008-01-23 | C | 92 | 0.13314 | 0.00029588
2008 | 2008-01-23 | C | 8 | 0.00010291 | 2.5728e-05
2008 | 2008-01-22 | C | 2651 | 0.53712 | 0.0085257
2008 | 2008-01-22 | C | 614 | 0.18957 | 0.0019747
2008 | 2008-01-22 | C | 169 | 0.079398 | 0.00054351
2008 | 2008-01-24 | C | 21 | 0.0019586 | 6.7537e-05
2008 | 2008-01-22 | C | 1195 | 0.026902 | 0.0038432
2008 | 2008-01-24 | B | 20 | 0.0043095 | 6.4321e-05
2008 | 2008-01-24 | B | 18 | 0.00521 | 5.7889e-05
2008 | 2008-01-24 | C | 94 | 0.03537 | 0.00030231
2008 | 2008-01-24 | B | 48 | 0.049398 | 0.00015437
2008 | 2008-01-22 | B | 103 | 0.071882 | 0.00033125
2008 | 2008-01-24 | B | 135 | 0.1292 | 0.00043417
2008 | 2008-01-24 | B | 26 | 0.023162 | 8.3617e-05
2008 | 2008-01-24 | B | 4 | 0.0024699 | 1.2864e-05
2008 | 2008-01-24 | C | 3 | 0.0008008 | 9.6481e-06
2008 | 2008-01-25 | B | 9 | 0.0096385 | 2.8944e-05
2008 | 2008-01-24 | C | 74 | 0.045719 | 0.00023799
2008 | 2008-01-25 | C | 22 | 0.0021933 | 7.0753e-05
2008 | 2008-01-26 | C | 3 | 0.0010324 | 9.6481e-06
2008 | 2008-01-26 | C | 111 | 0.01892 | 0.00035698
2008 | 2008-01-25 | C | 245 | 0.063887 | 0.00078793
2008 | 2008-01-25 | C | 165 | 0.057368 | 0.00053065
2008 | 2008-01-25 | C | 342 | 0.12831 | 0.0010999
2008 | 2008-01-25 | B | 29 | 0.013897 | 9.3265e-05
2008 | 2008-01-25 | B | 50 | 0.025728 | 0.0001608
2008 | 2008-01-25 | B | 9 | 0.0073808 | 2.8944e-05
2008 | 2008-01-25 | B | 16 | 0.0070496 | 5.1457e-05
2008 | 2008-01-27 | C | 841 | 0.20847 | 0.0027047
2008 | 2008-01-27 | C | 253 | 0.042584 | 0.00081366
2008 | 2008-01-27 | C | 8 | 0.0030102 | 2.5728e-05
2008 | 2008-01-28 | C | 5 | 0.001399 | 1.608e-05
2008 | 2008-01-28 | B | 11 | 0.008738 | 3.5376e-05
2008 | 2008-01-29 | C | 27 | 0.0039943 | 8.6833e-05
2008 | 2008-01-25 | B | 35 | 0.011369 | 0.00011256
2008 | 2008-01-29 | C | 29 | 0.018653 | 9.3265e-05
2008 | 2008-01-29 | C | 191 | 0.19964 | 0.00061426
2008 | 2008-01-29 | C | 1 | 0.00058532 | 0
2008 | 2008-01-29 | B | 48 | 0.045539 | 0.00015437
2008 | 2008-01-29 | B | 15 | 0.018187 | 4.8241e-05
2008 | 2008-01-29 | C | 356 | 0.063665 | 0.0011449
2008 | 2008-01-29 | B | 48 | 0.045539 | 0.00015437
2008 | 2008-01-29 | C | 1 | 0.0002798 | 0
2008 | 2008-01-30 | B | 99 | 0.021332 | 0.00031839
2008 | 2008-01-30 | C | 650 | 0.14198 | 0.0020904
2008 | 2008-01-30 | C | 2 | 0.00097125 | 6.4321e-06
2008 | 2008-01-30 | B | 4 | 0.0054673 | 1.2864e-05
2008 | 2008-01-30 | B | 55 | 0.063678 | 0.00017688
2008 | 2008-01-30 | B | 5 | 0.0040683 | 1.608e-05
2008 | 2008-01-30 | C | 12 | 0.0010806 | 3.8593e-05
2008 | 2008-01-30 | C | 20 | 0.01042 | 6.4321e-05
2008 | 2008-01-31 | C | 75 | 0.00096481 | 0.0002412
2008 | 2008-01-08 | B | 2 | 0.00096481 | 6.4321e-06
2008 | 2008-01-17 | B | 8 | 0.016363 | 2.5728e-05
2008 | 2008-01-31 | B | 31 | 0.023728 | 9.9697e-05
2008 | 2008-02-01 | B | 4 | 0.0053772 | 1.2864e-05
2008 | 2008-01-31 | C | 1205 | 0.054255 | 0.0038753
2008 | 2008-01-31 | B | 9 | 0.0059625 | 2.8944e-05
2008 | 2008-01-31 | B | 2 | 0.0021226 | 6.4321e-06
2008 | 2008-01-31 | C | 373 | 0.0035988 | 0.0011996
2008 | 2008-01-31 | B | 72 | 0.10767 | 0.00023156
2008 | 2008-01-31 | C | 608 | 0.11208 | 0.0019554
2008 | 2008-02-01 | C | 203 | 0.0457 | 0.00065286
2008 | 2008-02-01 | B | 20 | 0.0080401 | 6.4321e-05
2008 | 2008-02-01 | B | 2 | 0.001042 | 6.4321e-06
2008 | 2008-02-01 | C | 1 | 0.001116 | 0
2008 | 2008-02-01 | B | 204 | 0.18961 | 0.00065607
2008 | 2008-02-01 | C | 1116 | 0.40607 | 0.0035891
2008 | 2008-02-01 | B | 2 | 0.0019811 | 6.4321e-06
2008 | 2008-02-01 | B | 142 | 0.054345 | 0.00045668
2008 | 2008-02-01 | C | 405 | 0.083103 | 0.0013025
2008 | 2008-02-01 | C | 4 | 0.00084904 | 1.2864e-05
2008 | 2008-02-01 | C | 19 | 0.0043384 | 6.1105e-05
2008 | 2008-02-02 | B | 2 | 0.00095838 | 6.4321e-06
2008 | 2008-02-02 | C | 25 | 0.00096481 | 8.0401e-05
2008 | 2008-02-02 | C | 39 | 0.027513 | 0.00012543
2008 | 2008-02-02 | B | 5 | 0.00086833 | 1.608e-05
2008 | 2008-02-02 | C | 744 | 0.10977 | 0.0023927
2008 | 2008-02-03 | C | 1793 | 0.86383 | 0.0057664
2008 | 2008-02-04 | C | 19 | 0.0044607 | 6.1105e-05
2008 | 2008-02-04 | B | 9 | 0.0095227 | 2.8944e-05
2008 | 2008-02-04 | B | 13 | 0.011456 | 4.1809e-05
2008 | 2008-02-04 | B | 43 | 0.03319 | 0.00013829
2008 | 2008-02-04 | B | 3 | 0.0032514 | 9.6481e-06
2008 | 2008-02-04 | C | 6 | 0.004882 | 1.9296e-05
2008 | 2008-02-04 | C | 436 | 0.014022 | 0.0014022
2008 | 2008-02-04 | C | 1 | 0.00051778 | 0
2008 | 2008-02-05 | C | 2919 | 0.39428 | 0.0093876
2008 | 2008-02-04 | C | 10 | 0.0013186 | 3.216e-05
2008 | 2008-02-05 | C | 2 | 0.00024442 | 6.4321e-06
2008 | 2008-02-05 | C | 24 | 0.0074098 | 7.7185e-05
2008 | 2008-02-05 | C | 20 | 0.0014151 | 6.4321e-05
2008 | 2008-02-05 | C | 633 | 0.24263 | 0.0020358
2008 | 2008-02-05 | C | 370 | 0.032128 | 0.0011899
2008 | 2008-02-05 | C | 27 | 0.00043417 | 8.6833e-05
2008 | 2008-02-05 | C | 609 | 0.12339 | 0.0019586
2008 | 2008-02-05 | C | 22 | 0.0013443 | 7.0753e-05
2008 | 2008-02-05 | B | 57 | 0.024381 | 0.00018331
2008 | 2008-02-05 | B | 28 | 0.015849 | 9.0049e-05
2008 | 2008-02-05 | B | 4 | 0.0031775 | 1.2864e-05
2008 | 2008-02-05 | B | 20 | 0.0099697 | 6.4321e-05
2008 | 2008-02-05 | C | 1337 | 0.081167 | 0.0042999
2008 | 2008-02-05 | C | 755 | 0.10969 | 0.0024281
2008 | 2008-02-05 | C | 464 | 0.11341 | 0.0014922
2008 | 2008-02-05 | C | 209 | 0.16871 | 0.00067215
2008 | 2008-02-05 | C | 19 | 0.008188 | 6.1105e-05
2008 | 2008-02-05 | B | 6 | 0.0031453 | 1.9296e-05
2008 | 2008-02-04 | C | 225 | 0.043429 | 0.00072361
2008 | 2008-02-05 | C | 8 | 0.0068695 | 2.5728e-05
2008 | 2008-02-05 | C | 362 | 0.092461 | 0.0011642
2008 | 2008-02-05 | C | 10 | 0.010195 | 3.216e-05
2008 | 2008-02-06 | C | 332 | 0.065131 | 0.0010677
2008 | 2008-02-06 | C | 1108 | 0.25482 | 0.0035634
2008 | 2008-02-07 | C | 2288 | 0.044089 | 0.0073583
2008 | 2008-02-07 | B | 8 | 0.0056602 | 2.5728e-05
2008 | 2008-02-07 | B | 169 | 0.12881 | 0.00054351
2008 | 2008-02-07 | B | 12 | 0.013778 | 3.8593e-05
2008 | 2008-02-07 | B | 29 | 0.0277 | 9.3265e-05
2008 | 2008-02-07 | C | 118 | 0.093355 | 0.00037949
2008 | 2008-02-03 | B | 51 | 0.059375 | 0.00016402
2008 | 2008-02-05 | B | 22 | 0.017405 | 7.0753e-05
2008 | 2008-02-07 | B | 2 | 0.0011063 | 6.4321e-06
2008 | 2008-02-08 | C | 28 | 0.0022512 | 9.0049e-05
2008 | 2008-02-08 | C | 91 | 0.0070238 | 0.00029266
2008 | 2008-02-08 | B | 7 | 0.0033093 | 2.2512e-05
2008 | 2008-02-08 | C | 62 | 0.0033897 | 0.00019939
2008 | 2008-02-08 | C | 100 | 0.0064321 | 0.0003216
2008 | 2008-02-08 | B | 4 | 0.0042452 | 1.2864e-05
2008 | 2008-02-08 | C | 1 | 0.0011063 | 0
2008 | 2008-02-08 | C | 401 | 0.010533 | 0.0012896
2008 | 2008-02-09 | B | 10 | 0.0055638 | 3.216e-05
2008 | 2008-02-09 | C | 869 | 0.016768 | 0.0027947
2008 | 2008-02-10 | C | 302 | 0.051476 | 0.00097125
2008 | 2008-02-10 | C | 816 | 0.15522 | 0.0026243
2008 | 2008-02-09 | C | 47 | 0.018743 | 0.00015115
2008 | 2008-02-09 | C | 158 | 0.032013 | 0.00050813
2008 | 2008-02-10 | C | 549 | 0.10758 | 0.0017656
2008 | 2008-02-10 | C | 234 | 0.077555 | 0.00075255
2008 | 2008-02-10 | C | 60 | 0.0090692 | 0.00019296
2008 | 2008-02-11 | C | 568 | 0.11143 | 0.0018267
2008 | 2008-02-08 | B | 12 | 0.0066379 | 3.8593e-05
2008 | 2008-02-11 | B | 62 | 0.060018 | 0.00019939
2008 | 2008-02-11 | B | 1 | 0.00010291 | 0
2008 | 2008-02-11 | C | 159 | 0.081305 | 0.00051135
2008 | 2008-02-11 | C | 287 | 0.14218 | 0.000923
2008 | 2008-02-11 | C | 4 | 0.0022384 | 1.2864e-05
2008 | 2008-02-11 | C | 198 | 0.028655 | 0.00063678
2008 | 2008-02-11 | C | 807 | 0.028549 | 0.0025953
2008 | 2008-02-11 | B | 217 | 0.069788 | 0.00069788
2008 | 2008-02-12 | B | 125 | 0.042211 | 0.00040201
2008 | 2008-02-12 | B | 46 | 0.0059175 | 0.00014794
2008 | 2008-02-12 | C | 3 | 0.00068502 | 9.6481e-06
2008 | 2008-02-11 | C | 221 | 0.045636 | 0.00071075
2008 | 2008-02-11 | C | 120 | 0.019296 | 0.00038593
2008 | 2008-02-12 | C | 280 | 0.010806 | 0.00090049
2008 | 2008-02-12 | C | 808 | 0.075384 | 0.0025986
2008 | 2008-02-12 | C | 312 | 0.045333 | 0.0010034
2008 | 2008-02-12 | C | 286 | 0.023915 | 0.00091979
2008 | 2008-02-12 | C | 568 | 0.069415 | 0.0018267
2008 | 2008-02-12 | B | 8 | 0.0059175 | 2.5728e-05
2008 | 2008-02-12 | C | 429 | 0.08645 | 0.0013797
2008 | 2008-02-12 | B | 54 | 0.038207 | 0.00017367
2008 | 2008-02-12 | C | 347 | 0.085199 | 0.001116
2008 | 2008-02-12 | B | 1 | 0.00026372 | 0
2008 | 2008-02-12 | C | 29 | 0.011005 | 9.3265e-05
2008 | 2008-02-12 | B | 247 | 0.35031 | 0.00079436
2008 | 2008-02-12 | C | 537 | 0.18652 | 0.001727
2008 | 2008-02-12 | B | 130 | 0.038046 | 0.00041809
2008 | 2008-02-11 | C | 3 | 0.014395 | 9.6481e-06
2008 | 2008-02-12 | B | 205 | 0.030327 | 0.00065929
2008 | 2008-02-12 | B | 93 | 0.010169 | 0.00029909
2008 | 2008-02-12 | C | 5 | 0.0010131 | 1.608e-05
2008 | 2008-02-13 | B | 29 | 0.0037306 | 9.3265e-05
2008 | 2008-02-13 | B | 98 | 0.01891 | 0.00031517
2008 | 2008-02-13 | C | 1 | 0.00013507 | 0
2008 | 2008-02-13 | B | 30 | 0.0083939 | 9.6481e-05
2008 | 2008-02-13 | B | 22 | 0.015212 | 7.0753e-05
2008 | 2008-02-13 | B | 1 | 0.00019939 | 0
2008 | 2008-02-13 | B | 16 | 0.011835 | 5.1457e-05
2008 | 2008-02-13 | B | 88 | 0.068489 | 0.00028301
2008 | 2008-02-12 | B | 24 | 0.022924 | 7.7185e-05
2008 | 2008-02-13 | C | 11 | 0.0042806 | 3.5376e-05
2008 | 2008-02-13 | B | 10 | 0.011481 | 3.216e-05
2008 | 2008-02-14 | B | 1 | 0.00011899 | 0
2008 | 2008-02-14 | B | 1 | 0.00021226 | 0
2008 | 2008-02-13 | B | 1 | 0.00010613 | 0
2008 | 2008-02-13 | B | 32 | 0.0053515 | 0.00010291
2008 | 2008-02-14 | C | 315 | 0.0088795 | 0.0010131
2008 | 2008-02-14 | C | 68 | 0.0087476 | 0.00021869
2008 | 2008-02-14 | C | 60 | 0.0073326 | 0.00019296
2008 | 2008-02-14 | B | 186 | 0.11007 | 0.00059818
2008 | 2008-02-14 | B | 62 | 0.036489 | 0.00019939
2008 | 2008-02-14 | B | 57 | 0.040879 | 0.00018331
2008 | 2008-02-14 | B | 70 | 0.065286 | 0.00022512
2008 | 2008-02-15 | C | 334 | 0.016112 | 0.0010742
2008 | 2008-02-15 | C | 42 | 0.0075641 | 0.00013507
2008 | 2008-02-15 | C | 85 | 0.018042 | 0.00027336
2008 | 2008-02-15 | C | 877 | 0.019743 | 0.0028205
2008 | 2008-02-15 | C | 462 | 0.0014858 | 0
2008 | 2008-02-15 | B | 58 | 0.0052229 | 0.00018653
2008 | 2008-02-15 | C | 14 | 0.0026565 | 4.5025e-05
2008 | 2008-02-15 | C | 816 | 0.17311 | 0.0026243
2008 | 2008-02-15 | C | 1485 | 0.1459 | 0.0047758
2008 | 2008-02-15 | C | 4 | 0.001235 | 1.2864e-05
2008 | 2008-02-15 | C | 24 | 0.026011 | 7.7185e-05
2008 | 2008-02-15 | C | 1 | 0.0030134 | 0
2008 | 2008-02-16 | C | 43 | 0.054522 | 0.00013829
2008 | 2008-02-16 | C | 5 | 0.0018814 | 1.608e-05
2008 | 2008-02-16 | C | 358 | 0.07678 | 0.0011513
2008 | 2008-02-16 | C | 25 | 0.0075095 | 8.0401e-05
2008 | 2008-02-16 | C | 284 | 0.072181 | 0.00091336
2008 | 2008-02-17 | C | 53 | 0.039715 | 0.00017045
2008 | 2008-02-17 | C | 33 | 0.0039268 | 0.00010613
2008 | 2008-02-16 | C | 55 | 0.0024764 | 0.00017688
2008 | 2008-02-17 | C | 77 | 0.014115 | 0.00024764
2008 | 2008-02-18 | B | 1 | 0.00022512 | 0
2008 | 2008-02-18 | B | 92 | 0.058583 | 0.00029588
2008 | 2008-02-18 | C | 73 | 0.0028173 | 0.00023477
2008 | 2008-02-18 | C | 53 | 0.0040908 | 0.00017045
2008 | 2008-02-18 | C | 28 | 0.0049527 | 9.0049e-05
2008 | 2008-02-18 | B | 49 | 0.010716 | 0.00015759
2008 | 2008-02-19 | B | 49 | 0.0083521 | 0.00015759
2008 | 2008-02-19 | B | 17 | 0.0016949 | 5.4673e-05
2008 | 2008-02-19 | B | 25 | 0.010854 | 8.0401e-05
2008 | 2008-02-19 | B | 4 | 0.0024442 | 1.2864e-05
2008 | 2008-02-19 | B | 1 | 0.00029588 | 0
2008 | 2008-02-19 | B | 13 | 0.0074001 | 4.1809e-05
2008 | 2008-02-19 | B | 30 | 0.027208 | 9.6481e-05
2008 | 2008-02-19 | C | 493 | 0.060249 | 0.0015855
2008 | 2008-02-19 | C | 158 | 0.039454 | 0.00050813
2008 | 2008-02-19 | B | 20 | 0.019875 | 6.4321e-05
2008 | 2008-02-18 | B | 1 | 0.0010581 | 0
2008 | 2008-02-20 | B | 499 | 0.044935 | 0.0016048
2008 | 2008-02-20 | B | 20 | 0.014279 | 6.4321e-05
2008 | 2008-02-20 | B | 2 | 0.0017302 | 6.4321e-06
2008 | 2008-02-20 | B | 92 | 0.1003 | 0.00029588
2008 | 2008-02-20 | C | 6 | 0.0012543 | 1.9296e-05
2008 | 2008-02-20 | B | 37 | 0.041886 | 0.00011899
2008 | 2008-02-20 | C | 898 | 0.08664 | 0.002888
2008 | 2008-02-21 | C | 21 | 0.0011481 | 6.7537e-05
2008 | 2008-02-21 | C | 1215 | 0.1563 | 0.0039075
2008 | 2008-02-21 | C | 486 | 0.089303 | 0.001563
2008 | 2008-02-21 | C | 2 | 0.00080401 | 6.4321e-06
2008 | 2008-02-21 | B | 12 | 0.0089535 | 3.8593e-05
2008 | 2008-02-21 | C | 4 | 0.00078471 | 1.2864e-05
2008 | 2008-02-21 | C | 15 | 0.0011578 | 4.8241e-05
2008 | 2008-02-21 | B | 30 | 0.033865 | 9.6481e-05
2008 | 2008-02-21 | C | 632 | 0.014228 | 0.0020325
2008 | 2008-02-22 | B | 19 | 0.047478 | 6.1105e-05
2008 | 2008-02-22 | B | 15 | 0.0097446 | 4.8241e-05
2008 | 2008-02-22 | C | 2493 | 0.33674 | 0.0080176
2008 | 2008-02-22 | C | 206 | 0.031421 | 0.00066251
2008 | 2008-02-22 | C | 695 | 0.35531 | 0.0022352
2008 | 2008-02-22 | C | 85 | 0.031729 | 0.00027336
2008 | 2008-02-23 | C | 171 | 0.0809 | 0.00054994
2008 | 2008-02-22 | B | 15 | 0.018669 | 4.8241e-05
2008 | 2008-02-22 | B | 1 | 0.00021869 | 0
2008 | 2008-02-23 | C | 4 | 0.00097768 | 1.2864e-05
2008 | 2008-02-22 | C | 541 | 0.012179 | 0.0017399
2008 | 2008-02-22 | C | 1117 | 0.50036 | 0.0035923
2008 | 2008-02-22 | C | 1759 | 0.51314 | 0.005657
2008 | 2008-02-23 | C | 59 | 0.012713 | 0.00018975
2008 | 2008-02-23 | C | 6 | 0.00081044 | 1.9296e-05
2008 | 2008-02-23 | C | 5 | 0.0021065 | 1.608e-05
2008 | 2008-02-23 | C | 33 | 0.0083842 | 0.00010613
2008 | 2008-02-23 | C | 2 | 0.0024249 | 6.4321e-06
2008 | 2008-02-23 | C | 985 | 0.20009 | 0.0031678
2008 | 2008-02-23 | C | 222 | 0.067556 | 0.00071396
2008 | 2008-02-23 | C | 1021 | 0.36262 | 0.0032836
2008 | 2008-02-24 | C | 47 | 0.0080112 | 0.00015115
2008 | 2008-02-24 | C | 251 | 0.2003 | 0.00080723
2008 | 2008-02-24 | C | 1066 | 0.70064 | 0.0034283
2008 | 2008-02-24 | C | 190 | 0.012221 | 0.00061105
2008 | 2008-02-24 | C | 1287 | 0.56012 | 0.004139
2008 | 2008-02-23 | C | 444 | 0.1328 | 0.0014279
2008 | 2008-02-25 | C | 139 | 0.025995 | 0.00044703
2008 | 2008-02-17 | B | 5 | 0.0039879 | 1.608e-05
2008 | 2008-02-25 | C | 33 | 0.0029716 | 0.00010613
2008 | 2008-02-25 | B | 2 | 0.0019747 | 6.4321e-06
2008 | 2008-02-24 | C | 1 | 0.0030842 | 0
2008 | 2008-02-25 | C | 115 | 0.0059175 | 0.00036985
2008 | 2008-02-25 | C | 41 | 0.0039557 | 0.00013186
2008 | 2008-02-25 | C | 1213 | 0.019505 | 0.0039011
2008 | 2008-02-25 | C | 8 | 0.00090049 | 2.5728e-05
2008 | 2008-02-25 | C | 222 | 0.10613 | 0.00071396
2008 | 2008-02-25 | C | 441 | 0.21274 | 0.0014183
2008 | 2008-02-25 | C | 10 | 0.002798 | 3.216e-05
2008 | 2008-02-25 | C | 1273 | 0.38723 | 0.004094
2008 | 2008-02-26 | C | 20 | 0.00090049 | 6.4321e-05
2008 | 2008-02-26 | C | 417 | 0.23367 | 0.0013411
2008 | 2008-02-26 | C | 34 | 0.0024056 | 0.00010935
2008 | 2008-02-26 | C | 2 | 0.00027015 | 6.4321e-06
2008 | 2008-02-26 | C | 756 | 0.047832 | 0.0024313
2008 | 2008-02-26 | B | 7 | 0.0058307 | 2.2512e-05
2008 | 2008-02-26 | C | 16 | 0.0022126 | 5.1457e-05
2008 | 2008-02-26 | B | 9 | 0.0028108 | 2.8944e-05
2008 | 2008-02-25 | B | 58 | 0.030218 | 0.00018653
2008 | 2008-02-26 | C | 7 | 0.00072039 | 2.2512e-05
2008 | 2008-02-26 | B | 18 | 0.02165 | 5.7889e-05
2008 | 2008-02-26 | C | 2002 | 0.51223 | 0.0064385
2008 | 2008-02-26 | C | 233 | 0.054522 | 0.00074934
2008 | 2008-02-27 | C | 16 | 0.00072039 | 5.1457e-05
2008 | 2008-02-27 | B | 238 | 0.11634 | 0.00076542
2008 | 2008-02-27 | C | 101 | 0.035364 | 0.00032482
2008 | 2008-02-27 | B | 10 | 0.01042 | 3.216e-05
2008 | 2008-02-27 | B | 118 | 0.021107 | 0.00037949
2008 | 2008-02-27 | C | 62 | 0.015353 | 0.00019939
2008 | 2008-02-27 | B | 30 | 0.038496 | 9.6481e-05
2008 | 2008-02-28 | C | 7889 | 1.3499 | 0.025371
2008 | 2008-02-28 | C | 163 | 0.020444 | 0.00052422
2008 | 2008-02-28 | C | 5581 | 1.8846 | 0.017949
2008 | 2008-02-27 | B | 144 | 0.072245 | 0.00046311
2008 | 2008-02-28 | C | 671 | 0.15753 | 0.002158
2008 | 2008-02-28 | B | 105 | 0.077667 | 0.00033768
2008 | 2008-02-28 | B | 27 | 0.025529 | 8.6833e-05
2008 | 2008-02-28 | B | 225 | 0.26556 | 0.00072361
2008 | 2008-02-28 | B | 20 | 0.011256 | 6.4321e-05
2008 | 2008-02-28 | C | 1 | 0.002724 | 0
2008 | 2008-02-28 | C | 119 | 0.015768 | 0.00038271
2008 | 2008-02-28 | C | 111 | 0.042124 | 0.00035698
2008 | 2008-02-29 | B | 8 | 0.0041937 | 2.5728e-05
2008 | 2008-02-29 | C | 43 | 0.003319 | 0.00013829
2008 | 2008-02-29 | B | 2 | 0.0015501 | 6.4321e-06
2008 | 2008-02-29 | B | 7 | 0.0046375 | 2.2512e-05
2008 | 2008-02-29 | C | 461 | 0.077095 | 0.0014826
2008 | 2008-03-01 | C | 65 | 0.0041809 | 0.00020904
2008 | 2008-03-01 | C | 369 | 0.066543 | 0.0011867
2008 | 2008-03-01 | B | 2 | 0.0016338 | 6.4321e-06
2008 | 2008-03-01 | C | 568 | 0.0018267 | 0
2008 | 2008-03-01 | C | 595 | 0.0019135 | 0
2008 | 2008-03-01 | C | 70 | 0.0058532 | 0.00022512
2008 | 2008-03-01 | C | 1306 | 0.27076 | 0.0042002
2008 | 2008-03-01 | C | 615 | 0.037579 | 0.0019779
2008 | 2008-03-01 | C | 495 | 0.097108 | 0.0015919
2008 | 2008-03-01 | C | 195 | 0.092912 | 0.00062713
2008 | 2008-03-01 | C | 156 | 0.075802 | 0.0005017
2008 | 2008-03-01 | C | 70 | 0.015083 | 0.00022512
2008 | 2008-03-01 | C | 163 | 0.015726 | 0.00052422
2008 | 2008-03-02 | C | 151 | 0.034235 | 0.00048562
2008 | 2008-03-02 | C | 6 | 0.0016209 | 1.9296e-05
2008 | 2008-03-02 | C | 21 | 0.0047951 | 6.7537e-05
2008 | 2008-03-02 | C | 20 | 0.013121 | 6.4321e-05
2008 | 2008-03-02 | C | 1 | 0.00054673 | 0
2008 | 2008-03-01 | C | 131 | 0.35328 | 0.0004213
2008 | 2008-03-02 | C | 6 | 0.00069467 | 1.9296e-05
2008 | 2008-03-02 | C | 5 | 0.0049366 | 1.608e-05
2008 | 2008-03-02 | C | 38 | 0.013076 | 0.00012221
2008 | 2008-03-02 | C | 257 | 0.019837 | 0.00082652
2008 | 2008-03-03 | C | 817 | 0.25696 | 0.0026275
2008 | 2008-03-03 | C | 692 | 0.17212 | 0.0022255
2008 | 2008-03-03 | C | 139 | 0.028301 | 0.00044703
2008 | 2008-03-03 | C | 166 | 0.062462 | 0.00053386
2008 | 2008-03-03 | B | 7 | 0.0032193 | 2.2512e-05
2008 | 2008-03-01 | C | 1 | 0.0069016 | 0
2008 | 2008-03-01 | C | 200 | 0.0038593 | 0.00064321
2008 | 2008-03-03 | C | 43 | 0.0044253 | 0.00013829
2008 | 2008-03-03 | C | 362 | 0.20374 | 0.0011642
2008 | 2008-03-03 | B | 2 | 0.0017817 | 6.4321e-06
2008 | 2008-03-03 | C | 10 | 0.0031196 | 3.216e-05
2008 | 2008-03-03 | C | 105 | 0.06105 | 0.00033768
2008 | 2008-03-03 | C | 17 | 0.010224 | 5.4673e-05
2008 | 2008-03-03 | C | 5 | 0.00036985 | 1.608e-05
2008 | 2008-03-03 | B | 30 | 0.031742 | 9.6481e-05
2008 | 2008-03-04 | C | 12 | 0.0013186 | 3.8593e-05
2008 | 2008-03-04 | B | 37 | 0.033437 | 0.00011899
2008 | 2008-03-04 | C | 40 | 0.0075899 | 0.00012864
2008 | 2008-03-04 | C | 59 | 0.00075899 | 0.00018975
2008 | 2008-03-04 | B | 23 | 0.014572 | 7.3969e-05
2008 | 2008-03-04 | B | 1 | 0.00054673 | 0
2008 | 2008-03-04 | B | 1 | 0.00050492 | 0
2008 | 2008-03-04 | C | 16 | 0.0015437 | 5.1457e-05
2008 | 2008-03-04 | C | 27 | 0.004168 | 8.6833e-05
2008 | 2008-03-04 | C | 39 | 0.0051425 | 0.00012543
2008 | 2008-03-04 | B | 29 | 0.012498 | 9.3265e-05
2008 | 2008-03-04 | C | 1170 | 0.75877 | 0.0037628
2008 | 2008-03-04 | C | 997 | 0.081128 | 0.0032064
2008 | 2008-03-05 | C | 259 | 0.090792 | 0.00083296
2008 | 2008-03-05 | C | 103 | 0.0089438 | 0.00033125
2008 | 2008-03-05 | C | 4 | 0.00066894 | 1.2864e-05
2008 | 2008-03-05 | C | 1054 | 0.010169 | 0.0033897
2008 | 2008-03-05 | C | 40 | 0.0037306 | 0.00012864
2008 | 2008-03-05 | B | 8 | 0.0068695 | 2.5728e-05
2008 | 2008-03-05 | B | 20 | 0.020776 | 6.4321e-05
2008 | 2008-03-05 | C | 11 | 0.00049527 | 3.5376e-05
2008 | 2008-03-05 | C | 1 | 0.00031196 | 0
2008 | 2008-03-05 | B | 287 | 0.067379 | 0.000923
2008 | 2008-03-05 | C | 156 | 0.038129 | 0.0005017
2008 | 2008-03-06 | B | 7 | 0.0029491 | 2.2512e-05
2008 | 2008-03-06 | B | 27 | 0.0050363 | 8.6833e-05
2008 | 2008-03-06 | B | 1 | 0.00030552 | 0
2008 | 2008-03-06 | B | 56 | 0.033678 | 0.0001801
2008 | 2008-03-06 | B | 76 | 0.076503 | 0.00024442
2008 | 2008-03-06 | B | 19 | 0.0012832 | 6.1105e-05
2008 | 2008-03-06 | C | 172 | 0.065826 | 0.00055316
2008 | 2008-03-07 | B | 21 | 0.0086447 | 6.7537e-05
2008 | 2008-03-07 | B | 263 | 0.042291 | 0.00084582
2008 | 2008-03-07 | C | 259 | 0.072338 | 0.00083296
2008 | 2008-03-07 | B | 8 | 0.0055059 | 2.5728e-05
2008 | 2008-03-07 | C | 861 | 0.17214 | 0.002769
2008 | 2008-03-08 | C | 1570 | 0.30614 | 0.0050492
2008 | 2008-03-08 | B | 2 | 0.00039879 | 6.4321e-06
2008 | 2008-03-08 | B | 16 | 0.0080787 | 5.1457e-05
2008 | 2008-03-08 | C | 49 | 0.029469 | 0.00015759
2008 | 2008-03-08 | C | 34 | 0.0045925 | 0.00010935
2008 | 2008-03-08 | C | 33 | 0.0084904 | 0.00010613
2008 | 2008-03-08 | C | 278 | 0.026719 | 0.00089406
2008 | 2008-03-09 | C | 2 | 0.00012864 | 6.4321e-06
2008 | 2008-03-09 | C | 288 | 0.031492 | 0.00092622
2008 | 2008-03-09 | C | 154 | 0.016839 | 0.00049527
2008 | 2008-03-09 | C | 325 | 0.030311 | 0.0010452
2008 | 2008-03-09 | C | 135 | 0.032855 | 0.00043417
2008 | 2008-03-09 | B | 80 | 0.031389 | 0.00025728
2008 | 2008-03-10 | C | 464 | 0.010446 | 0.0014922
2008 | 2008-03-10 | C | 86 | 0.003319 | 0.00027658
2008 | 2008-03-10 | B | 22 | 0.013868 | 7.0753e-05
2008 | 2008-03-08 | C | 1367 | 0.69055 | 0.0043963
2008 | 2008-03-10 | B | 36 | 0.0012736 | 0.00011578
2008 | 2008-03-11 | C | 897 | 0.034617 | 0.0028848
2008 | 2008-03-11 | B | 12 | 0.0047469 | 3.8593e-05
2008 | 2008-03-11 | B | 37 | 0.038316 | 0.00011899
2008 | 2008-03-11 | C | 4 | 0.00095195 | 1.2864e-05
2008 | 2008-03-11 | C | 1 | 0.0011224 | 0
2008 | 2008-03-11 | C | 1021 | 0.28145 | 0.0032836
2008 | 2008-03-11 | C | 6 | 0.0021612 | 1.9296e-05
2008 | 2008-03-11 | B | 116 | 0.032456 | 0.00037306
2008 | 2008-03-11 | B | 75 | 0.013749 | 0.0002412
2008 | 2008-03-12 | B | 182 | 0.021657 | 0.00058532
2008 | 2008-03-12 | C | 1730 | 0.33553 | 0.0055638
2008 | 2008-03-11 | C | 1718 | 0.12155 | 0.0055252
2008 | 2008-03-11 | B | 80 | 0.082588 | 0.00025728
2008 | 2008-03-11 | B | 19 | 0.02047 | 6.1105e-05
2008 | 2008-03-11 | B | 33 | 0.026426 | 0.00010613
2008 | 2008-03-12 | B | 8 | 0.0010291 | 2.5728e-05
2008 | 2008-03-12 | B | 8 | 0.0026243 | 2.5728e-05
2008 | 2008-03-12 | B | 12 | 0.008143 | 3.8593e-05
2008 | 2008-03-12 | B | 37 | 0.022371 | 0.00011899
2008 | 2008-03-12 | B | 41 | 0.0075159 | 0.00013186
2008 | 2008-03-12 | B | 1 | 0.00040522 | 0
2008 | 2008-03-12 | C | 1718 | 0.12118 | 0.0055252
2008 | 2008-03-12 | B | 2 | 0.001042 | 6.4321e-06
2008 | 2008-03-12 | C | 205 | 0.058413 | 0.00065929
2008 | 2008-03-12 | B | 103 | 0.019544 | 0.00033125
2008 | 2008-03-12 | B | 214 | 0.031659 | 0.00068823
2008 | 2008-03-13 | B | 176 | 0.03849 | 0.00056602
2008 | 2008-03-12 | C | 120 | 0.11806 | 0.00038593
2008 | 2008-03-12 | B | 80 | 0.0265 | 0.00025728
2008 | 2008-03-10 | B | 1 | 3.8593e-05 | 0
2008 | 2008-03-10 | B | 20 | 0.022448 | 6.4321e-05
2008 | 2008-03-13 | B | 1 | 0.00053708 | 0
2008 | 2008-03-13 | C | 11 | 0.00091979 | 3.5376e-05
2008 | 2008-03-13 | B | 21 | 0.0015533 | 6.7537e-05
2008 | 2008-03-13 | B | 2 | 0.00030231 | 6.4321e-06
2008 | 2008-03-13 | B | 1 | 0.00053708 | 0
2008 | 2008-03-13 | B | 61 | 0.0616 | 0.00019618
2008 | 2008-03-13 | B | 41 | 0.034019 | 0.00013186
2008 | 2008-03-13 | B | 9 | 0.0081623 | 2.8944e-05
2008 | 2008-03-13 | B | 344 | 0.0011063 | 0
2008 | 2008-03-13 | C | 17 | 0.0032257 | 5.4673e-05
2008 | 2008-03-13 | C | 291 | 0.15711 | 0.00093587
2008 | 2008-03-13 | B | 19 | 0.028475 | 6.1105e-05
2008 | 2008-03-13 | B | 89 | 0.016315 | 0.00028623
2008 | 2008-03-13 | B | 15 | 0.0019779 | 4.8241e-05
2008 | 2008-03-14 | B | 125 | 0.014874 | 0.00040201
2008 | 2008-03-13 | B | 25 | 0.011739 | 8.0401e-05
2008 | 2008-03-14 | B | 26 | 0.0022577 | 8.3617e-05
2008 | 2008-03-14 | C | 158 | 0.082559 | 0.00050813
2008 | 2008-03-13 | C | 3 | 0.011597 | 9.6481e-06
2008 | 2008-03-14 | B | 1 | 0.0006014 | 0
2008 | 2008-03-14 | B | 13 | 0.0042227 | 4.1809e-05
2008 | 2008-03-14 | B | 3 | 0.0022287 | 9.6481e-06
2008 | 2008-03-14 | B | 3 | 0.0022094 | 9.6481e-06
2008 | 2008-03-14 | C | 66 | 0.027169 | 0.00021226
2008 | 2008-03-14 | C | 13 | 0.0042227 | 4.1809e-05
2008 | 2008-03-14 | C | 4 | 0.0016209 | 1.2864e-05
2008 | 2008-03-14 | C | 52 | 0.043343 | 0.00016723
2008 | 2008-03-15 | B | 280 | 0.097253 | 0.00090049
2008 | 2008-03-15 | B | 35 | 0.034782 | 0.00011256
2008 | 2008-03-15 | B | 1 | 0.00083296 | 0
2008 | 2008-03-15 | C | 12 | 0.0023541 | 3.8593e-05
2008 | 2008-03-15 | C | 138 | 0.023207 | 0.00044381
2008 | 2008-03-15 | C | 40 | 0.032675 | 0.00012864
2008 | 2008-03-16 | B | 2 | 0.00036663 | 6.4321e-06
2008 | 2008-03-16 | B | 1 | 0.00037628 | 0
2008 | 2008-03-16 | B | 1 | 0.00018331 | 0
2008 | 2008-03-16 | C | 405 | 0.19537 | 0.0013025
2008 | 2008-03-16 | C | 1327 | 0.19396 | 0.0042677
2008 | 2008-03-16 | C | 359 | 0.065582 | 0.0011546
2008 | 2008-03-16 | C | 245 | 0.40873 | 0.00078793
2008 | 2008-03-16 | C | 168 | 0.12373 | 0.0005403
2008 | 2008-03-16 | C | 56 | 0.027015 | 0.0001801
2008 | 2008-03-17 | B | 8 | 0.0012092 | 2.5728e-05
2008 | 2008-03-17 | C | 190 | 0.075841 | 0.00061105
2008 | 2008-03-17 | B | 118 | 0.054647 | 0.00037949
2008 | 2008-03-17 | B | 11 | 0.012629 | 3.5376e-05
2008 | 2008-03-17 | B | 32 | 0.033859 | 0.00010291
2008 | 2008-03-17 | C | 2 | 0.0017495 | 6.4321e-06
2008 | 2008-03-17 | B | 2 | 0.00010291 | 6.4321e-06
2008 | 2008-03-17 | B | 144 | 0.036586 | 0.00046311
2008 | 2008-03-18 | B | 67 | 0.0060333 | 0.00021547
2008 | 2008-03-18 | C | 47 | 0.012395 | 0.00015115
2008 | 2008-03-18 | C | 418 | 0.10846 | 0.0013443
2008 | 2008-03-18 | B | 41 | 0.03125 | 0.00013186
2008 | 2008-03-18 | B | 26 | 0.0034283 | 8.3617e-05
2008 | 2008-03-18 | B | 73 | 0.028877 | 0.00023477
2008 | 2008-03-18 | B | 16 | 0.013893 | 5.1457e-05
2008 | 2008-03-18 | B | 13 | 0.014717 | 4.1809e-05
2008 | 2008-03-18 | B | 41 | 0.044964 | 0.00013186
2008 | 2008-03-18 | B | 381 | 0.48645 | 0.0012253
2008 | 2008-03-18 | B | 26 | 0.033614 | 8.3617e-05
2008 | 2008-03-18 | B | 247 | 0.30265 | 0.00079436
2008 | 2008-03-18 | B | 773 | 0.1489 | 0.002486
2008 | 2008-03-19 | C | 3974 | 0.051122 | 0.012781
2008 | 2008-03-18 | C | 1641 | 0.19772 | 0.0052775
2008 | 2008-03-19 | C | 87 | 0.0075545 | 0.0002798
2008 | 2008-03-19 | B | 43 | 0.035679 | 0.00013829
2008 | 2008-03-19 | B | 53 | 0.054203 | 0.00017045
2008 | 2008-03-19 | B | 15 | 0.015051 | 4.8241e-05
2008 | 2008-03-19 | B | 5 | 0.0028462 | 1.608e-05
2008 | 2008-03-19 | B | 27 | 0.013372 | 8.6833e-05
2008 | 2008-03-19 | B | 12 | 0.0025857 | 3.8593e-05
2008 | 2008-03-19 | B | 1 | 0.00031517 | 0
2008 | 2008-03-19 | C | 1590 | 0.082794 | 0.0051135
2008 | 2008-03-19 | B | 1 | 0.0014215 | 0
2008 | 2008-03-19 | C | 29 | 0.0039171 | 9.3265e-05
2008 | 2008-03-19 | C | 192 | 0.097527 | 0.00061748
2008 | 2008-03-19 | C | 1047 | 0.0033672 | 0
2008 | 2008-03-20 | C | 77 | 0.0096578 | 0.00024764
2008 | 2008-03-20 | B | 1 | 0.00071075 | 0
2008 | 2008-03-20 | C | 2 | 0.00037949 | 6.4321e-06
2008 | 2008-03-20 | B | 33 | 0.032794 | 0.00010613
2008 | 2008-03-20 | B | 7 | 0.0063935 | 2.2512e-05
2008 | 2008-03-20 | B | 13 | 0.012041 | 4.1809e-05
2008 | 2008-03-22 | C | 34 | 0.0094037 | 0.00010935
2008 | 2008-03-23 | C | 464 | 0.010446 | 0.0014922
2008 | 2008-03-24 | C | 495 | 0.065122 | 0.0015919
2008 | 2008-03-25 | B | 17 | 0.019518 | 5.4673e-05
2008 | 2008-03-25 | B | 12 | 0.0099955 | 3.8593e-05
2008 | 2008-03-25 | C | 2 | 0.0011256 | 6.4321e-06
2008 | 2008-03-26 | C | 925 | 0.08627 | 0.0029748
2008 | 2008-03-26 | C | 2988 | 0.2979 | 0.0096095
2008 | 2008-03-26 | B | 42 | 0.025394 | 0.00013507
2008 | 2008-03-26 | B | 8 | 0.007384 | 2.5728e-05
2008 | 2008-03-20 | B | 41 | 0.034547 | 0.00013186
2008 | 2008-03-26 | B | 5 | 0.0025889 | 1.608e-05
2008 | 2008-03-27 | B | 19 | 0.0087991 | 6.1105e-05
2008 | 2008-03-27 | B | 3 | 0.00087798 | 9.6481e-06
2008 | 2008-03-27 | C | 384 | 0.0024699 | 0.001235
2008 | 2008-03-27 | B | 9 | 0.0084228 | 2.8944e-05
2008 | 2008-03-27 | B | 74 | 0.076632 | 0.00023799
2008 | 2008-03-27 | B | 37 | 0.042481 | 0.00011899
2008 | 2008-03-27 | B | 19 | 0.013871 | 6.1105e-05
2008 | 2008-03-27 | B | 91 | 0.06819 | 0.00029266
2008 | 2008-03-27 | B | 19 | 0.0097157 | 6.1105e-05
2008 | 2008-03-27 | B | 10 | 0.0090692 | 3.216e-05
2008 | 2008-03-27 | C | 37 | 0.0084196 | 0.00011899
2008 | 2008-03-28 | C | 779 | 0.037579 | 0.0025053
2008 | 2008-03-28 | B | 9 | 0.0087702 | 2.8944e-05
2008 | 2008-03-28 | C | 127 | 0.081768 | 0.00040844
2008 | 2008-03-29 | C | 99 | 0.010507 | 0.00031839
2008 | 2008-03-29 | C | 92 | 0.029408 | 0.00029588
2008 | 2008-03-28 | B | 65 | 0.066894 | 0.00020904
2008 | 2008-03-28 | B | 1 | 0.00037628 | 0
2008 | 2008-03-28 | C | 2 | 0.0026307 | 6.4321e-06
2008 | 2008-03-29 | C | 11 | 0.0022287 | 3.5376e-05
2008 | 2008-03-30 | C | 54 | 0.0092043 | 0.00017367
2008 | 2008-03-30 | C | 2 | 0.0014022 | 6.4321e-06
2008 | 2008-03-30 | C | 99 | 0.05027 | 0.00031839
2008 | 2008-03-30 | C | 107 | 0.067247 | 0.00034412
2008 | 2008-03-31 | C | 1442 | 0.66762 | 0.0046375
2008 | 2008-03-31 | C | 453 | 0.049534 | 0.0014569
2008 | 2008-03-31 | B | 14 | 0.0070689 | 4.5025e-05
2008 | 2008-03-31 | C | 278 | 0.03254 | 0.00089406
2008 | 2008-03-31 | C | 4 | 0.00029588 | 1.2864e-05
2008 | 2008-03-10 | B | 3 | 0.0022963 | 9.6481e-06
2008 | 2008-03-31 | C | 6 | 0.0015437 | 1.9296e-05
2008 | 2008-03-31 | C | 925 | 0.023799 | 0.0029748
2008 | 2008-03-31 | C | 699 | 0.015736 | 0.002248
2008 | 2008-03-31 | C | 2988 | 0.75828 | 0.0096095
2008 | 2008-03-31 | C | 387 | 0.06472 | 0.0012446
2009 | 2008-04-01 | B | 56 | 0.055543 | 0.00017802
2009 | 2008-04-01 | B | 9 | 0.011931 | 2.8611e-05
2009 | 2008-04-02 | C | 272 | 0.032858 | 0.00086469
2009 | 2008-04-02 | B | 2 | 0.0010364 | 6.358e-06
2009 | 2008-04-02 | B | 2 | 0.0017866 | 6.358e-06
2009 | 2008-04-02 | C | 41 | 0.0029978 | 0.00013034
2009 | 2008-04-02 | B | 5 | 0.005452 | 1.5895e-05
2009 | 2008-04-02 | B | 26 | 0.02397 | 8.2654e-05
2009 | 2008-04-02 | B | 23 | 0.021716 | 7.3117e-05
2009 | 2008-04-01 | C | 2 | 0.0020346 | 6.358e-06
2009 | 2008-04-03 | C | 2 | 0.0012907 | 6.358e-06
2009 | 2008-04-02 | B | 12 | 0.0088885 | 3.8148e-05
2009 | 2008-04-03 | B | 7 | 0.0057858 | 2.2253e-05
2009 | 2008-04-03 | B | 48 | 0.033875 | 0.00015259
2009 | 2008-04-03 | C | 260 | 0.051245 | 0.00082654
2009 | 2008-04-01 | B | 88 | 0.020981 | 0.00027975
2009 | 2008-04-03 | B | 2 | 0.0013097 | 6.358e-06
2009 | 2008-04-04 | B | 57 | 0.031167 | 0.0001812
2009 | 2008-04-04 | B | 49 | 0.019471 | 0.00015577
2009 | 2008-04-04 | B | 12 | 0.015984 | 3.8148e-05
2009 | 2008-04-04 | C | 7 | 0.0064311 | 2.2253e-05
2009 | 2008-04-05 | C | 159 | 0.030515 | 0.00050546
2009 | 2008-04-05 | C | 35 | 0.0060083 | 0.00011126
2009 | 2008-04-06 | C | 160 | 0.083843 | 0.00050864
2009 | 2008-04-07 | C | 26 | 0.004298 | 8.2654e-05
2009 | 2008-04-07 | C | 41 | 0.040535 | 0.00013034
2009 | 2008-04-07 | B | 1 | 0.0010205 | 3.179e-06
2009 | 2008-04-08 | C | 2024 | 0.21499 | 0.0064343
2009 | 2008-04-08 | C | 902 | 0.11757 | 0.0028675
2009 | 2008-04-08 | B | 8 | 0.00094098 | 2.5432e-05
2009 | 2008-04-08 | B | 18 | 0.015107 | 5.7222e-05
2009 | 2008-04-08 | B | 15 | 0.017024 | 4.7685e-05
2009 | 2008-04-08 | B | 78 | 0.078852 | 0.00024796
2009 | 2008-04-08 | B | 65 | 0.0059924 | 0.00020663
2009 | 2008-04-08 | C | 597 | 0.013285 | 0.0018979
2009 | 2008-04-09 | B | 37 | 0.031876 | 0.00011762
2009 | 2008-04-08 | B | 27 | 0.040084 | 8.5833e-05
2009 | 2008-04-09 | C | 3603 | 0.034362 | 0.011454
2009 | 2008-04-09 | C | 1018 | 0.11092 | 0.0032362
2009 | 2008-04-09 | C | 98 | 0.015577 | 0.00031154
2009 | 2008-04-09 | C | 12 | 0.0054933 | 3.8148e-05
2009 | 2008-04-09 | C | 212 | 0.054161 | 0.00067395
2009 | 2008-04-10 | B | 28 | 0.024122 | 8.9012e-05
2009 | 2008-04-10 | B | 2 | 0.00041327 | 6.358e-06
2009 | 2008-04-10 | B | 9 | 0.0040055 | 2.8611e-05
2009 | 2008-04-10 | C | 14 | 0.0023143 | 4.4506e-05
2009 | 2008-04-10 | B | 16 | 0.016785 | 5.0864e-05
2009 | 2008-04-10 | B | 147 | 0.023833 | 0.00046731
2009 | 2008-04-10 | B | 65 | 0.0041327 | 0.00020663
2009 | 2008-04-11 | C | 931 | 0.020717 | 0.0029596
2009 | 2008-04-11 | B | 8 | 0.0026449 | 2.5432e-05
2009 | 2008-04-11 | B | 11 | 0.0084974 | 3.4969e-05
2009 | 2008-04-11 | B | 18 | 0.017624 | 5.7222e-05
2009 | 2008-04-11 | B | 6 | 0.0058366 | 1.9074e-05
2009 | 2008-04-11 | B | 49 | 0.0366 | 0.00015577
2009 | 2008-04-11 | C | 21 | 0.0010014 | 6.6759e-05
2009 | 2008-04-12 | B | 5 | 0.0042916 | 1.5895e-05
2009 | 2008-04-12 | B | 1 | 0.00059447 | 3.179e-06
2009 | 2008-04-12 | C | 2274 | 0.36306 | 0.007229
2009 | 2008-04-13 | B | 16 | 0.002238 | 5.0864e-05
2009 | 2008-04-12 | C | 737 | 0.44554 | 0.0023429
2009 | 2008-04-13 | B | 4 | 0.0012334 | 1.2716e-05
2009 | 2008-04-13 | B | 31 | 0.0038434 | 9.8549e-05
2009 | 2008-04-13 | B | 18 | 0.012989 | 5.7222e-05
2009 | 2008-04-13 | B | 337 | 0.40924 | 0.0010713
2009 | 2008-04-14 | C | 88 | 0.087282 | 0.00027975
2009 | 2008-04-13 | B | 97 | 0.073699 | 0.00030836
2009 | 2008-04-14 | B | 19 | 0.0048321 | 6.0401e-05
2009 | 2008-04-14 | C | 156 | 0.069944 | 0.00049592
2009 | 2008-04-14 | C | 1287 | 0.020457 | 0.0040914
2009 | 2008-04-14 | C | 365 | 0.057222 | 0.0011603
2009 | 2008-04-14 | B | 6 | 0.0022317 | 1.9074e-05
2009 | 2008-04-14 | C | 190 | 0.025302 | 0.00060401
2009 | 2008-04-14 | C | 80 | 0.0061037 | 0.00025432
2009 | 2008-04-15 | C | 404 | 0.044951 | 0.0012843
2009 | 2008-04-15 | C | 249 | 0.089177 | 0.00079157
2009 | 2008-04-14 | C | 1 | 0.00016531 | 3.179e-06
2009 | 2008-04-14 | C | 311 | 0.16109 | 0.00098867
2009 | 2008-04-14 | C | 286 | 0.13261 | 0.00090919
2009 | 2008-04-15 | C | 209 | 0.046912 | 0.00066441
2009 | 2008-04-15 | C | 1375 | 0.19231 | 0.0043711
2009 | 2008-04-15 | C | 29 | 0.0017516 | 9.2191e-05
2009 | 2008-04-15 | B | 37 | 0.025524 | 0.00011762
2009 | 2008-04-15 | B | 4 | 0.002912 | 1.2716e-05
2009 | 2008-04-15 | C | 313 | 0.10494 | 0.00099502
2009 | 2008-04-15 | C | 233 | 0.091107 | 0.00074071
2009 | 2008-04-15 | C | 34 | 0.027562 | 0.00010809
2009 | 2008-04-15 | C | 126 | 0.0060083 | 0.00040055
2009 | 2008-04-15 | C | 279 | 0.11499 | 0.00088694
2009 | 2008-04-15 | B | 20 | 0.010618 | 6.358e-05
2009 | 2008-04-15 | C | 31 | 0.00098549 | 9.8549e-05
2009 | 2008-04-16 | B | 461 | 0.051293 | 0.0014655
2009 | 2008-04-15 | C | 36 | 0.0022889 | 0.00011444
2009 | 2008-04-15 | C | 25 | 0.070335 | 7.9475e-05
2009 | 2008-04-16 | C | 100 | 0.024481 | 0.0003179
2009 | 2008-04-16 | B | 14 | 0.0027149 | 4.4506e-05
2009 | 2008-04-16 | B | 52 | 0.0076042 | 0.00016531
2009 | 2008-04-16 | B | 2 | 0.0012334 | 6.358e-06
2009 | 2008-04-16 | C | 5227 | 0.66441 | 0.016617
2009 | 2008-04-16 | C | 634 | 0.038294 | 0.0020155
2009 | 2008-04-16 | B | 7 | 0.0028929 | 2.2253e-05
2009 | 2008-04-15 | B | 6 | 0.0058176 | 1.9074e-05
2009 | 2008-04-16 | C | 890 | 0.033952 | 0.0028293
2009 | 2008-04-16 | B | 4 | 0.0017421 | 1.2716e-05
2009 | 2008-04-17 | C | 1 | 6.6759e-05 | 3.179e-06
2009 | 2008-04-17 | C | 374 | 0.21158 | 0.0011889
2009 | 2008-04-17 | B | 12 | 0.0028229 | 3.8148e-05
2009 | 2008-04-17 | B | 47 | 0.01539 | 0.00014941
2009 | 2008-04-17 | B | 37 | 0.0097627 | 0.00011762
2009 | 2008-04-17 | B | 6 | 0.0040055 | 1.9074e-05
2009 | 2008-04-17 | B | 4 | 0.004031 | 1.2716e-05
2009 | 2008-04-17 | B | 20 | 0.016785 | 6.358e-05
2009 | 2008-04-17 | B | 35 | 0.041057 | 0.00011126
2009 | 2008-04-17 | C | 204 | 0.03048 | 0.00064851
2009 | 2008-04-17 | C | 94 | 0.010157 | 0.00029883
2009 | 2008-04-17 | C | 369 | 0.054904 | 0.001173
2009 | 2008-04-17 | C | 222 | 0.03811 | 0.00070574
2009 | 2008-04-17 | C | 10 | 0.00085833 | 3.179e-05
2009 | 2008-04-18 | C | 57 | 0.022832 | 0.0001812
2009 | 2008-04-18 | C | 814 | 0.025877 | 0.0025877
2009 | 2008-04-18 | B | 34 | 0.0045396 | 0.00010809
2009 | 2008-04-18 | C | 3607 | 0.78884 | 0.011467
2009 | 2008-04-18 | C | 905 | 0.11085 | 0.002877
2009 | 2008-04-18 | B | 28 | 0.031688 | 8.9012e-05
2009 | 2008-04-18 | B | 18 | 0.020428 | 5.7222e-05
2009 | 2008-04-18 | C | 37 | 0.0027053 | 0.00011762
2009 | 2008-04-18 | C | 4 | 0.0015895 | 1.2716e-05
2009 | 2008-04-18 | C | 218 | 0.024256 | 0.00069302
2009 | 2008-04-18 | C | 4 | 0.00069938 | 1.2716e-05
2009 | 2008-04-18 | C | 24 | 0.027085 | 7.6296e-05
2009 | 2008-04-19 | C | 85 | 0.0024319 | 0.00027021
2009 | 2008-04-19 | C | 1065 | 0.46292 | 0.0033856
2009 | 2008-04-19 | C | 21 | 0.0020028 | 6.6759e-05
2009 | 2008-04-19 | C | 187 | 0.060232 | 0.00059447
2009 | 2008-04-20 | C | 14 | 0.023232 | 4.4506e-05
2009 | 2008-04-20 | B | 31 | 0.020203 | 9.8549e-05
2009 | 2008-04-20 | C | 508 | 0.044302 | 0.0016149
2009 | 2008-04-20 | C | 50 | 0.06056 | 0.00015895
2009 | 2008-04-20 | C | 418 | 0.40795 | 0.0013288
2009 | 2008-04-20 | C | 873 | 0.22967 | 0.0027753
2009 | 2008-04-21 | B | 47 | 0.038997 | 0.00014941
2009 | 2008-04-21 | C | 1 | 0.00022571 | 3.179e-06
2009 | 2008-04-21 | C | 289 | 0.053531 | 0.00091873
2009 | 2008-04-21 | C | 4 | 0.0017548 | 1.2716e-05
2009 | 2008-04-21 | B | 159 | 0.013647 | 0.00050546
2009 | 2008-04-22 | B | 159 | 0.024262 | 0.00050546
2009 | 2009-02-12 | C | 339 | 0.0086214 | 0.0010777
2009 | 2008-04-22 | B | 23 | 0.025664 | 7.3117e-05
2009 | 2008-04-22 | C | 1246 | 0.13071 | 0.003961
2009 | 2008-04-21 | C | 1 | 0.0030932 | 3.179e-06
2009 | 2008-04-22 | B | 63 | 0.069496 | 0.00020028
2009 | 2008-04-22 | B | 16 | 0.0071209 | 5.0864e-05
2009 | 2008-04-22 | B | 52 | 0.058023 | 0.00016531
2009 | 2008-04-22 | B | 18 | 0.02203 | 5.7222e-05
2009 | 2008-04-22 | B | 69 | 0.086424 | 0.00021935
2009 | 2008-04-22 | B | 6 | 0.0058366 | 1.9074e-05
2009 | 2009-02-12 | C | 48 | 0.0045778 | 0.00015259
2009 | 2008-04-23 | C | 1 | 8.2654e-05 | 3.179e-06
2009 | 2008-04-23 | B | 202 | 0.064858 | 0.00064216
2009 | 2008-04-22 | C | 38 | 0.11319 | 0.0001208
2009 | 2008-04-23 | B | 18 | 0.017567 | 5.7222e-05
2009 | 2008-04-23 | B | 36 | 0.040856 | 0.00011444
2009 | 2008-04-23 | C | 305 | 0.026179 | 0.00096959
2009 | 2008-04-23 | B | 18 | 0.020142 | 5.7222e-05
2009 | 2008-04-23 | B | 129 | 0.017634 | 0.00041009
2009 | 2008-04-23 | C | 294 | 0.037703 | 0.00093462
2009 | 2008-04-23 | C | 201 | 0.033866 | 0.00063898
2009 | 2008-04-24 | C | 205 | 0.044213 | 0.00065169
2009 | 2008-04-24 | B | 52 | 0.051411 | 0.00016531
2009 | 2008-04-24 | C | 2 | 0.0013797 | 6.358e-06
2009 | 2008-04-24 | B | 33 | 0.02801 | 0.00010491
2009 | 2008-04-24 | B | 28 | 0.027772 | 8.9012e-05
2009 | 2008-04-24 | B | 28 | 0.010414 | 8.9012e-05
2009 | 2008-04-24 | C | 2 | 0.00022889 | 6.358e-06
2009 | 2008-04-24 | C | 253 | 0.32259 | 0.00080429
2009 | 2008-04-25 | C | 106 | 0.010783 | 0.00033697
2009 | 2008-04-25 | C | 1060 | 0.26036 | 0.0033697
2009 | 2008-04-25 | C | 1337 | 0.20384 | 0.0042503
2009 | 2008-04-26 | C | 181 | 0.0092064 | 0.0005754
2009 | 2008-04-26 | C | 398 | 0.054405 | 0.0012652
2009 | 2008-04-27 | C | 428 | 0.089047 | 0.0013606
2009 | 2008-04-26 | C | 4 | 0.0003179 | 1.2716e-05
2009 | 2008-04-27 | C | 215 | 0.0095688 | 0.00068348
2009 | 2008-04-27 | C | 5 | 0.00081064 | 1.5895e-05
2009 | 2008-04-27 | C | 14 | 0.010977 | 4.4506e-05
2009 | 2008-04-27 | C | 1259 | 0.25408 | 0.0040024
2009 | 2008-04-28 | B | 10 | 0.0017802 | 3.179e-05
2009 | 2008-04-28 | C | 215 | 0.026802 | 0.00068348
2009 | 2008-04-28 | B | 12 | 0.0048448 | 3.8148e-05
2009 | 2008-04-28 | B | 18 | 0.0050927 | 5.7222e-05
2009 | 2008-04-28 | B | 19 | 0.014677 | 6.0401e-05
2009 | 2008-04-28 | C | 1340 | 0.14562 | 0.0042599
2009 | 2008-04-28 | B | 16 | 0.013326 | 5.0864e-05
2009 | 2008-04-28 | C | 1145 | 0.017697 | 0.0036399
2009 | 2008-04-24 | B | 27 | 0.0048925 | 8.5833e-05
2009 | 2008-04-29 | C | 31 | 0.0022666 | 9.8549e-05
2009 | 2008-04-29 | C | 134 | 0.014058 | 0.00042599
2009 | 2008-04-29 | B | 20 | 0.0085197 | 6.358e-05
2009 | 2008-04-29 | C | 1 | 0.00023842 | 3.179e-06
2009 | 2008-04-29 | C | 193 | 0.014112 | 0.00061355
2009 | 2008-04-29 | B | 23 | 0.023397 | 7.3117e-05
2009 | 2008-04-29 | B | 64 | 0.065513 | 0.00020346
2009 | 2008-04-30 | C | 773 | 0.017202 | 0.0024574
2009 | 2008-04-30 | C | 636 | 0.15185 | 0.0020218
2009 | 2008-04-29 | C | 232 | 0.0059002 | 0.00073753
2009 | 2008-04-29 | C | 1163 | 0.51407 | 0.0036972
2009 | 2008-04-30 | C | 3611 | 0.3903 | 0.011479
2009 | 2008-04-29 | C | 135 | 0.084974 | 0.00042916
2009 | 2008-04-30 | C | 393 | 0.093669 | 0.0012493
2009 | 2008-04-29 | C | 31 | 0.0040405 | 9.8549e-05
2009 | 2008-04-30 | C | 90 | 0.011158 | 0.00028611
2009 | 2008-04-30 | C | 4775 | 0.27323 | 0.01518
2009 | 2008-04-30 | B | 23 | 0.016671 | 7.3117e-05
2009 | 2008-04-30 | B | 56 | 0.027416 | 0.00017802
2009 | 2008-04-30 | C | 5 | 0.0056745 | 1.5895e-05
2009 | 2008-04-30 | B | 5 | 0.003481 | 1.5895e-05
2009 | 2008-04-30 | B | 14 | 0.003872 | 4.4506e-05
2009 | 2008-04-30 | C | 45 | 0.0042916 | 0.00014305
2009 | 2008-04-30 | C | 1924 | 0.37404 | 0.0061164
2009 | 2008-04-30 | C | 199 | 0.099289 | 0.00063262
2009 | 2008-05-01 | B | 8 | 0.01119 | 2.5432e-05
2009 | 2008-05-01 | C | 499 | 0.13468 | 0.0015863
2009 | 2008-05-01 | B | 67 | 0.0095847 | 0.00021299
2009 | 2008-05-02 | C | 100 | 0.003179 | 0.0003179
2009 | 2008-05-02 | B | 33 | 0.0054552 | 0.00010491
2009 | 2008-05-02 | B | 6 | 0.0023461 | 1.9074e-05
2009 | 2008-05-02 | C | 2 | 0.00020346 | 6.358e-06
2009 | 2008-05-02 | B | 47 | 0.026446 | 0.00014941
2009 | 2008-05-02 | B | 1 | 0.00087422 | 3.179e-06
2009 | 2008-05-01 | B | 2 | 0.0016149 | 6.358e-06
2009 | 2008-05-02 | C | 50 | 0.0071527 | 0.00015895
2009 | 2008-05-01 | C | 2 | 0.0050673 | 6.358e-06
2009 | 2008-05-02 | B | 7 | 0.0079443 | 2.2253e-05
2009 | 2008-05-02 | B | 15 | 0.017024 | 4.7685e-05
2009 | 2008-05-02 | C | 423 | 0.086259 | 0.0013447
2009 | 2008-05-03 | C | 29 | 0.0061768 | 9.2191e-05
2009 | 2008-05-02 | C | 8 | 0.016989 | 2.5432e-05
2009 | 2008-05-04 | C | 756 | 0.14752 | 0.0024033
2009 | 2008-05-04 | B | 3 | 7.6296e-05 | 9.537e-06
2009 | 2008-05-04 | C | 99 | 0.045634 | 0.00031472
2009 | 2008-05-04 | C | 337 | 0.037474 | 0.0010713
2009 | 2008-05-04 | C | 350 | 0.05897 | 0.0011126
2009 | 2008-05-05 | C | 40 | 0.0094098 | 0.00012716
2009 | 2008-05-05 | C | 3 | 0.00099185 | 9.537e-06
2009 | 2008-05-05 | B | 5 | 0.004085 | 1.5895e-05
2009 | 2008-05-05 | B | 5 | 0.0014464 | 1.5895e-05
2009 | 2008-05-05 | C | 7 | 0.0013129 | 2.2253e-05
2009 | 2008-05-05 | C | 1006 | 0.11591 | 0.0031981
2009 | 2008-05-05 | C | 48 | 0.010834 | 0.00015259
2009 | 2008-05-06 | B | 63 | 0.03605 | 0.00020028
2009 | 2008-05-06 | B | 127 | 0.067423 | 0.00040373
2009 | 2008-05-06 | B | 80 | 0.07655 | 0.00025432
2009 | 2008-05-06 | B | 21 | 0.0064756 | 6.6759e-05
2009 | 2008-05-06 | B | 123 | 0.113 | 0.00039102
2009 | 2008-05-06 | B | 2 | 0.0019265 | 6.358e-06
2009 | 2008-05-06 | B | 129 | 0.047981 | 0.00041009
2009 | 2008-05-07 | B | 4 | 0.0022762 | 1.2716e-05
2009 | 2008-05-07 | B | 59 | 0.040138 | 0.00018756
2009 | 2008-05-07 | B | 50 | 0.035548 | 0.00015895
2009 | 2008-05-08 | C | 896 | 0.068361 | 0.0028484
2009 | 2008-05-08 | C | 923 | 0.16617 | 0.0029342
2009 | 2008-05-08 | B | 1 | 0.00054043 | 3.179e-06
2009 | 2008-05-08 | B | 18 | 0.020428 | 5.7222e-05
2009 | 2008-05-08 | B | 52 | 0.065627 | 0.00016531
2009 | 2008-05-08 | B | 1 | 0.00056268 | 3.179e-06
2009 | 2008-05-08 | C | 29 | 0.004333 | 9.2191e-05
2009 | 2008-05-08 | B | 2 | 0.00060401 | 6.358e-06
2009 | 2008-05-08 | C | 459 | 0.070532 | 0.0014592
2009 | 2008-05-09 | C | 1 | 0.00038466 | 3.179e-06
2009 | 2008-05-09 | C | 67 | 0.014696 | 0.00021299
2009 | 2008-05-09 | B | 7 | 0.0079443 | 2.2253e-05
2009 | 2008-05-09 | C | 332 | 0.014776 | 0.0010554
2009 | 2008-05-09 | C | 634 | 0.024186 | 0.0020155
2009 | 2008-05-09 | C | 51 | 0.0019455 | 0.00016213
2009 | 2008-05-10 | C | 1153 | 0.1906 | 0.0036654
2009 | 2008-05-10 | C | 448 | 0.19462 | 0.0014242
2009 | 2008-05-10 | C | 27 | 0.0042058 | 8.5833e-05
2009 | 2008-05-10 | C | 10 | 0.0016531 | 3.179e-05
2009 | 2008-05-10 | B | 60 | 0.028229 | 0.00019074
2009 | 2008-05-10 | C | 12 | 0.013237 | 3.8148e-05
2009 | 2008-05-11 | C | 1923 | 0.648 | 0.0061132
2009 | 2008-05-11 | C | 322 | 0.047087 | 0.0010236
2009 | 2008-05-11 | C | 163 | 0.0036272 | 0.00051818
2009 | 2008-05-09 | B | 6 | 0.00041963 | 1.9074e-05
2009 | 2008-05-10 | B | 22 | 0.01084 | 6.9938e-05
2009 | 2008-05-11 | B | 6 | 0.0033761 | 1.9074e-05
2009 | 2008-05-12 | C | 240 | 0.021363 | 0.00076296
2009 | 2009-01-18 | C | 238 | 0.045396 | 0.0007566
2009 | 2008-05-12 | B | 2 | 0.0023079 | 6.358e-06
2009 | 2008-05-09 | B | 70 | 0.060083 | 0.00022253
2009 | 2009-01-18 | C | 238 | 0.007566 | 0.0007566
2009 | 2008-05-11 | C | 10 | 0.0009537 | 3.179e-05
2009 | 2008-05-13 | B | 400 | 0.097913 | 0.0012716
2009 | 2008-05-13 | B | 21 | 0.010615 | 6.6759e-05
2009 | 2008-05-13 | C | 56 | 0.031154 | 0.00017802
2009 | 2008-05-12 | C | 1 | 0.0044061 | 3.179e-06
2009 | 2008-05-13 | B | 6 | 0.0049592 | 1.9074e-05
2009 | 2008-05-13 | B | 109 | 0.10636 | 0.00034651
2009 | 2008-05-14 | C | 632 | 0.028128 | 0.0020091
2009 | 2008-05-13 | C | 904 | 0.26624 | 0.0028738
2009 | 2008-05-14 | B | 2 | 0.00045778 | 6.358e-06
2009 | 2008-05-14 | B | 37 | 0.034581 | 0.00011762
2009 | 2008-05-13 | B | 14 | 0.015889 | 4.4506e-05
2009 | 2008-05-14 | B | 163 | 0.055445 | 0.00051818
2009 | 2008-05-15 | C | 137 | 0.054879 | 0.00043552
2009 | 2008-05-15 | C | 6 | 0.0016785 | 1.9074e-05
2009 | 2008-05-15 | B | 5 | 0.0012557 | 1.5895e-05
2009 | 2008-05-15 | B | 5 | 0.0067236 | 1.5895e-05
2009 | 2008-05-15 | B | 81 | 0.090639 | 0.0002575
2009 | 2008-05-15 | B | 53 | 0.062677 | 0.00016849
2009 | 2008-05-15 | B | 18 | 0.018139 | 5.7222e-05
2009 | 2008-05-15 | C | 1549 | 0.43694 | 0.0049243
2009 | 2008-05-15 | B | 57 | 0.032073 | 0.0001812
2009 | 2008-05-15 | C | 549 | 0.0017453 | 0.0017453
2009 | 2008-05-16 | B | 2 | 0.0011572 | 6.358e-06
2009 | 2008-05-16 | C | 1031 | 0.40303 | 0.0032775
2009 | 2008-05-17 | C | 445 | 0.011317 | 0.0014147
2009 | 2008-05-17 | C | 2 | 7.6296e-05 | 6.358e-06
2009 | 2008-05-17 | C | 699 | 0.12096 | 0.0022221
2009 | 2008-05-18 | B | 103 | 0.13654 | 0.00032744
2009 | 2008-05-18 | B | 1 | 0.00089012 | 3.179e-06
2009 | 2008-05-18 | B | 120 | 0.044633 | 0.00038148
2009 | 2008-05-18 | C | 134 | 0.0038339 | 0.00042599
2009 | 2008-05-19 | B | 1 | 0.00025432 | 3.179e-06
2009 | 2008-05-19 | C | 119 | 0.023076 | 0.0003783
2009 | 2008-05-19 | C | 61 | 0.025985 | 0.00019392
2009 | 2008-05-20 | B | 2 | 0.00069302 | 6.358e-06
2009 | 2008-05-20 | B | 13 | 0.0059511 | 4.1327e-05
2009 | 2008-05-20 | C | 127 | 0.03329 | 0.00040373
2009 | 2008-05-20 | B | 123 | 0.088761 | 0.00039102
2009 | 2008-05-20 | B | 17 | 0.01778 | 5.4043e-05
2009 | 2008-05-20 | B | 20 | 0.021363 | 6.358e-05
2009 | 2008-05-20 | B | 132 | 0.17415 | 0.00041963
2009 | 2008-05-20 | B | 17 | 0.016645 | 5.4043e-05
2009 | 2008-05-20 | B | 8 | 0.0015768 | 2.5432e-05
2009 | 2008-05-21 | B | 17 | 0.016429 | 5.4043e-05
2009 | 2008-05-21 | B | 79 | 0.064292 | 0.00025114
2009 | 2008-05-21 | B | 30 | 0.029374 | 9.537e-05
2009 | 2008-05-22 | C | 1 | 6.0401e-05 | 3.179e-06
2009 | 2008-05-22 | C | 390 | 0.099115 | 0.0012398
2009 | 2008-05-22 | B | 17 | 0.014321 | 5.4043e-05
2009 | 2008-05-22 | B | 23 | 0.022154 | 7.3117e-05
2009 | 2008-05-22 | B | 3 | 0.0027371 | 9.537e-06
2009 | 2008-05-22 | C | 5 | 0.0010968 | 1.5895e-05
2009 | 2008-05-22 | B | 28 | 0.014776 | 8.9012e-05
2009 | 2008-05-22 | B | 12 | 0.0079348 | 3.8148e-05
2009 | 2008-05-23 | C | 774 | 0.036908 | 0.0024605
2009 | 2008-05-22 | B | 1 | 0.00050864 | 3.179e-06
2009 | 2008-05-22 | B | 36 | 0.017052 | 0.00011444
2009 | 2008-05-23 | C | 26 | 0.0086787 | 8.2654e-05
2009 | 2008-05-23 | C | 10 | 0.00015895 | 3.179e-05
2009 | 2008-05-23 | B | 58 | 0.050152 | 0.00018438
2009 | 2008-05-22 | B | 1 | 0.0013543 | 3.179e-06
2009 | 2008-05-21 | B | 1 | 0.001812 | 3.179e-06
2009 | 2008-05-24 | B | 14 | 0.0084116 | 4.4506e-05
2009 | 2008-05-24 | C | 584 | 0.12987 | 0.0018565
2009 | 2008-05-25 | C | 191 | 0.068612 | 0.00060719
2009 | 2008-05-25 | B | 87 | 0.024062 | 0.00027657
2009 | 2008-05-25 | B | 1 | 0.0010395 | 3.179e-06
2009 | 2008-05-25 | C | 199 | 0.057718 | 0.00063262
2009 | 2008-05-26 | B | 2 | 0.0018883 | 6.358e-06
2009 | 2008-05-26 | C | 95 | 0.020234 | 0.000302
2009 | 2008-05-26 | C | 34 | 0.0020536 | 0.00010809
2009 | 2008-05-26 | C | 547 | 0.11645 | 0.0017389
2009 | 2008-05-27 | B | 17 | 0.010322 | 5.4043e-05
2009 | 2008-05-27 | B | 31 | 0.018232 | 9.8549e-05
2009 | 2008-05-27 | B | 1 | 0.00091555 | 3.179e-06
2009 | 2008-05-27 | B | 12 | 0.011559 | 3.8148e-05
2009 | 2008-05-27 | B | 26 | 0.030913 | 8.2654e-05
2009 | 2008-05-27 | B | 1 | 0.00089966 | 3.179e-06
2009 | 2008-05-27 | B | 22 | 0.01126 | 6.9938e-05
2009 | 2008-05-27 | B | 1 | 0.00086469 | 3.179e-06
2009 | 2008-05-27 | B | 11 | 0.010176 | 3.4969e-05
2009 | 2008-05-27 | C | 7 | 0.0095465 | 2.2253e-05
2009 | 2008-05-28 | C | 19 | 0.015221 | 6.0401e-05
2009 | 2008-05-28 | B | 4 | 0.0032299 | 1.2716e-05
2009 | 2008-05-28 | B | 66 | 0.059377 | 0.00020981
2009 | 2008-05-27 | B | 17 | 0.015348 | 5.4043e-05
2009 | 2008-05-29 | C | 59 | 0.0086278 | 0.00018756
2009 | 2008-05-29 | B | 1 | 0.00097277 | 3.179e-06
2009 | 2008-05-29 | C | 49 | 0.0057635 | 0.00015577
2009 | 2008-05-29 | B | 18 | 0.0099566 | 5.7222e-05
2009 | 2008-05-28 | B | 153 | 0.014592 | 0.00048639
2009 | 2008-05-28 | B | 73 | 0.093987 | 0.00023207
2009 | 2008-05-28 | B | 153 | 0.0107 | 0.00048639
2009 | 2008-05-28 | B | 16 | 0.0098167 | 5.0864e-05
2009 | 2008-05-29 | C | 630 | 0.0040055 | 0.0020028
2009 | 2008-05-28 | B | 1 | 0.00072163 | 3.179e-06
2009 | 2008-05-29 | C | 6884 | 0.57234 | 0.021884
2009 | 2008-05-29 | C | 227 | 0.041855 | 0.00072163
2009 | 2008-05-29 | B | 45 | 0.012446 | 0.00014305
2009 | 2008-05-30 | B | 50 | 0.0089012 | 0.00015895
2009 | 2008-05-30 | C | 207 | 0.039146 | 0.00065805
2009 | 2008-05-29 | C | 883 | 0.16123 | 0.0028071
2009 | 2008-05-30 | B | 18 | 0.011902 | 5.7222e-05
2009 | 2008-05-30 | C | 914 | 0.30201 | 0.0029056
2009 | 2008-05-30 | C | 19 | 0.0010872 | 6.0401e-05
2009 | 2008-05-30 | C | 276 | 0.053522 | 0.0008774
2009 | 2008-05-30 | C | 380 | 0.094225 | 0.001208
2009 | 2008-05-30 | C | 5586 | 0.14206 | 0.017758
2009 | 2008-05-30 | C | 1 | 0.00067077 | 3.179e-06
2009 | 2008-05-31 | C | 882 | 0.17104 | 0.0028039
2009 | 2008-05-31 | C | 13 | 0.026656 | 4.1327e-05
2009 | 2008-05-31 | C | 288 | 0.062935 | 0.00091555
2009 | 2008-05-31 | C | 72 | 0.038911 | 0.00022889
2009 | 2008-05-31 | B | 34 | 0.035344 | 0.00010809
2009 | 2008-05-30 | B | 2 | 0.0024288 | 6.358e-06
2009 | 2008-06-01 | C | 283 | 0.0062976 | 0.00089966
2009 | 2008-06-01 | C | 632 | 0.016073 | 0.0020091
2009 | 2008-06-01 | C | 1002 | 0.41025 | 0.0031854
2009 | 2008-06-01 | C | 55 | 0.044061 | 0.00017484
2009 | 2008-06-01 | C | 596 | 0.31481 | 0.0018947
2009 | 2008-06-01 | B | 3 | 0.0043489 | 9.537e-06
2009 | 2008-06-01 | C | 5 | 0.0019233 | 1.5895e-05
2009 | 2008-06-02 | C | 168 | 0.0053407 | 0.00053407
2009 | 2008-06-02 | C | 648 | 0.047272 | 0.00206
2009 | 2008-06-02 | C | 2181 | 0.0069334 | 0.0069334
2009 | 2008-06-03 | C | 141 | 0.025998 | 0.00044824
2009 | 2008-06-03 | B | 73 | 0.040612 | 0.00023207
2009 | 2008-06-03 | B | 4 | 0.0032934 | 1.2716e-05
2009 | 2008-06-03 | B | 23 | 0.021496 | 7.3117e-05
2009 | 2008-06-03 | C | 68 | 0.010592 | 0.00021617
2009 | 2008-06-03 | B | 22 | 0.02266 | 6.9938e-05
2009 | 2008-06-03 | B | 12 | 0.0096133 | 3.8148e-05
2009 | 2008-06-03 | B | 2 | 0.00052771 | 6.358e-06
2009 | 2008-06-03 | C | 13 | 0.0033888 | 4.1327e-05
2009 | 2008-06-03 | C | 1066 | 0.094887 | 0.0033888
2009 | 2008-06-04 | B | 24 | 0.0045015 | 7.6296e-05
2009 | 2008-06-04 | C | 69 | 0.010748 | 0.00021935
2009 | 2008-06-04 | B | 51 | 0.037776 | 0.00016213
2009 | 2008-06-04 | B | 68 | 0.045396 | 0.00021617
2009 | 2008-06-04 | B | 11 | 0.012973 | 3.4969e-05
2009 | 2008-06-04 | C | 1920 | 0.67577 | 0.0061037
2009 | 2008-06-05 | B | 11 | 0.012659 | 3.4969e-05
2009 | 2008-06-05 | B | 21 | 0.022164 | 6.6759e-05
2009 | 2008-06-05 | B | 1 | 0.0011095 | 3.179e-06
2009 | 2008-06-05 | B | 49 | 0.044239 | 0.00015577
2009 | 2008-06-05 | B | 39 | 0.056535 | 0.00012398
2009 | 2008-06-05 | B | 8 | 0.0057476 | 2.5432e-05
2009 | 2008-06-05 | B | 27 | 0.023089 | 8.5833e-05
2009 | 2008-06-05 | B | 40 | 0.026322 | 0.00012716
2009 | 2008-06-05 | B | 13 | 0.011282 | 4.1327e-05
2009 | 2008-06-05 | C | 2 | 0.00015895 | 6.358e-06
2009 | 2008-06-05 | C | 86 | 0.0084752 | 0.00027339
2009 | 2008-06-05 | C | 50 | 0.0038148 | 0.00015895
2009 | 2008-06-06 | C | 271 | 0.0060306 | 0.00086151
2009 | 2008-06-06 | C | 177 | 0.0039388 | 0.00056268
2009 | 2008-06-06 | B | 64 | 0.061444 | 0.00020346
2009 | 2008-06-06 | B | 99 | 0.050041 | 0.00031472
2009 | 2008-06-06 | C | 100 | 0.035519 | 0.0003179
2009 | 2008-06-06 | C | 133 | 0.0038053 | 0.00042281
2009 | 2008-06-06 | C | 715 | 0.16411 | 0.002273
2009 | 2008-06-06 | C | 2 | 0.00062944 | 6.358e-06
2009 | 2008-06-06 | C | 633 | 0.020123 | 0.0020123
2009 | 2008-06-06 | C | 86 | 0.093129 | 0.00027339
2009 | 2008-06-07 | C | 1 | 4.4506e-05 | 3.179e-06
2009 | 2008-06-07 | C | 10 | 0.00079475 | 3.179e-05
2009 | 2008-06-07 | B | 29 | 0.019821 | 9.2191e-05
2009 | 2008-06-07 | C | 561 | 0.2586 | 0.0017834
2009 | 2008-06-07 | C | 100 | 0.019138 | 0.0003179
2009 | 2008-06-07 | C | 236 | 0.067325 | 0.00075024
2009 | 2008-06-08 | C | 64 | 0.053916 | 0.00020346
2009 | 2008-06-08 | C | 224 | 0.015771 | 0.00071209
2009 | 2008-06-08 | C | 235 | 0.12476 | 0.00074706
2009 | 2008-06-08 | C | 3 | 0.00044824 | 9.537e-06
2009 | 2008-06-08 | C | 56 | 0.007477 | 0.00017802
2009 | 2008-06-08 | B | 2 | 0.0012207 | 6.358e-06
2009 | 2008-06-08 | B | 41 | 0.062563 | 0.00013034
2009 | 2008-06-07 | C | 558 | 0.22784 | 0.0017739
2009 | 2008-06-08 | C | 15 | 0.0011444 | 4.7685e-05
2009 | 2008-06-09 | C | 16 | 0.013225 | 5.0864e-05
2009 | 2008-06-09 | C | 2 | 8.2654e-05 | 6.358e-06
2009 | 2008-06-09 | C | 24 | 0.0019074 | 7.6296e-05
2009 | 2008-06-09 | C | 44 | 0.018743 | 0.00013988
2009 | 2008-06-09 | B | 5 | 0.00076296 | 1.5895e-05
2009 | 2008-06-09 | C | 644 | 0.2111 | 0.0020473
2009 | 2008-06-09 | C | 64 | 0.014649 | 0.00020346
2009 | 2008-06-09 | C | 100 | 0.0022253 | 0.0003179
2009 | 2008-06-09 | C | 20 | 0.0030518 | 6.358e-05
2009 | 2008-06-09 | C | 22 | 0.0046858 | 6.9938e-05
2009 | 2008-06-06 | B | 64 | 0.038657 | 0.00020346
2009 | 2008-06-10 | B | 55 | 0.012414 | 0.00017484
2009 | 2008-06-10 | B | 11 | 0.0076932 | 3.4969e-05
2009 | 2008-06-10 | C | 20 | 0.0027975 | 6.358e-05
2009 | 2008-06-10 | B | 63 | 0.05047 | 0.00020028
2009 | 2008-06-10 | C | 1002 | 0.066892 | 0.0031854
2009 | 2008-06-10 | B | 1 | 0.00034651 | 3.179e-06
2009 | 2008-06-10 | B | 14 | 0.015266 | 4.4506e-05
2009 | 2008-06-10 | B | 138 | 0.1689 | 0.0004387
2009 | 2008-06-10 | C | 1145 | 0.21353 | 0.0036399
2009 | 2008-06-10 | C | 4000 | 0.15259 | 0.012716
2009 | 2008-06-10 | C | 3016 | 0.18217 | 0.0095878
2009 | 2008-06-10 | C | 544 | 0.025941 | 0.0017294
2009 | 2008-06-10 | C | 579 | 0.02761 | 0.0018406
2009 | 2008-06-11 | C | 67 | 0.0036209 | 0.00021299
2009 | 2008-06-11 | B | 23 | 0.012942 | 7.3117e-05
2009 | 2008-06-11 | B | 3 | 0.001688 | 9.537e-06
2009 | 2008-06-11 | B | 1 | 0.0014941 | 3.179e-06
2009 | 2008-06-11 | B | 10 | 0.007725 | 3.179e-05
2009 | 2008-06-11 | B | 163 | 0.20053 | 0.00051818
2009 | 2008-06-11 | B | 66 | 0.015736 | 0.00020981
2009 | 2008-06-11 | B | 37 | 0.039404 | 0.00011762
2009 | 2008-06-12 | C | 13 | 0.00090919 | 4.1327e-05
2009 | 2008-06-12 | B | 1 | 0.00033379 | 3.179e-06
2009 | 2008-06-12 | B | 166 | 0.1504 | 0.00052771
2009 | 2008-06-12 | B | 163 | 0.20053 | 0.00051818
2009 | 2008-06-13 | C | 66 | 0.021401 | 0.00020981
2009 | 2008-06-12 | B | 4 | 0.0031917 | 1.2716e-05
2009 | 2008-06-12 | C | 1 | 0.0010395 | 3.179e-06
2009 | 2008-06-12 | C | 2177 | 0.20942 | 0.0069207
2009 | 2008-06-13 | C | 1545 | 1.3387 | 0.0049115
2009 | 2008-06-13 | B | 1 | 0.00056268 | 3.179e-06
2009 | 2008-06-13 | B | 416 | 0.42054 | 0.0013225
2009 | 2008-06-13 | B | 3 | 0.0025082 | 9.537e-06
2009 | 2008-06-14 | C | 465 | 0.019217 | 0.0014782
2009 | 2008-06-14 | C | 8 | 0.0044252 | 2.5432e-05
2009 | 2008-06-14 | C | 116 | 0.04017 | 0.00036876
2009 | 2008-06-14 | C | 483 | 0.51898 | 0.0015355
2009 | 2008-06-15 | C | 440 | 0.11166 | 0.0013988
2009 | 2008-06-15 | B | 89 | 0.054888 | 0.00028293
2009 | 2008-06-13 | C | 530 | 0.052231 | 0.0016849
2009 | 2008-06-15 | B | 61 | 0.065068 | 0.00019392
2009 | 2008-06-15 | C | 621 | 0.2104 | 0.0019742
2009 | 2008-06-16 | C | 74 | 0.066339 | 0.00023525
2009 | 2008-06-16 | C | 41 | 0.0093844 | 0.00013034
2009 | 2008-06-16 | C | 4826 | 0.35286 | 0.015342
2009 | 2008-06-16 | B | 6 | 0.0035668 | 1.9074e-05
2009 | 2008-06-16 | B | 166 | 0.047596 | 0.00052771
2009 | 2008-06-16 | B | 14 | 0.016601 | 4.4506e-05
2009 | 2008-06-16 | C | 780 | 0.15069 | 0.0024796
2009 | 2008-06-16 | C | 17 | 0.0078362 | 5.4043e-05
2009 | 2008-06-16 | C | 312 | 0.10811 | 0.00099185
2009 | 2008-06-16 | C | 141 | 0.055133 | 0.00044824
2009 | 2008-06-17 | B | 133 | 0.10316 | 0.00042281
2009 | 2008-06-17 | B | 44 | 0.023779 | 0.00013988
2009 | 2008-06-17 | C | 26 | 0.0012398 | 8.2654e-05
2009 | 2008-06-17 | C | 8 | 0.0015259 | 2.5432e-05
2009 | 2008-06-17 | B | 105 | 0.034381 | 0.00033379
2009 | 2008-06-17 | C | 20 | 0.00038148 | 6.358e-05
2009 | 2008-06-17 | C | 245 | 0.028039 | 0.00077885
2009 | 2008-06-17 | C | 47 | 0.0044824 | 0.00014941
2009 | 2008-06-17 | C | 47 | 0.011057 | 0.00014941
2009 | 2008-06-17 | C | 875 | 0.14285 | 0.0027816
2009 | 2008-06-17 | C | 321 | 0.12203 | 0.0010205
2009 | 2008-06-18 | C | 631 | 0.0080238 | 0.0020059
2009 | 2008-06-17 | C | 235 | 0.07957 | 0.00074706
2009 | 2008-06-17 | C | 2281 | 0.26348 | 0.0072513
2009 | 2008-06-18 | C | 195 | 0.014878 | 0.0006199
2009 | 2008-06-18 | B | 6 | 0.0027085 | 1.9074e-05
2009 | 2008-06-18 | B | 10 | 0.0038148 | 3.179e-05
2009 | 2008-06-18 | C | 40 | 0.0035605 | 0.00012716
2009 | 2008-06-18 | B | 80 | 0.07833 | 0.00025432
2009 | 2008-06-18 | C | 8 | 0.0031281 | 2.5432e-05
2009 | 2008-06-18 | C | 8 | 0.004476 | 2.5432e-05
2009 | 2008-06-18 | C | 15 | 0.0031949 | 4.7685e-05
2009 | 2008-06-19 | C | 1919 | 0.14641 | 0.0061005
2009 | 2008-06-19 | B | 20 | 0.0038784 | 6.358e-05
2009 | 2008-06-18 | C | 2 | 0.0062944 | 6.358e-06
2009 | 2008-06-19 | C | 446 | 0.16592 | 0.0014178
2009 | 2008-06-19 | B | 1 | 0.00032426 | 3.179e-06
2009 | 2008-06-20 | B | 372 | 0.1904 | 0.0011826
2009 | 2008-06-20 | B | 1 | 0.00013352 | 3.179e-06
2009 | 2008-06-20 | B | 7 | 0.0084784 | 2.2253e-05
2009 | 2008-06-20 | B | 26 | 0.0018184 | 8.2654e-05
2009 | 2008-06-21 | C | 882 | 0.21029 | 0.0028039
2009 | 2008-06-21 | C | 23 | 0.0026322 | 7.3117e-05
2009 | 2008-06-22 | C | 1184 | 0.090334 | 0.0037639
2009 | 2008-06-22 | C | 327 | 0.13576 | 0.0010395
2009 | 2008-06-22 | C | 28 | 0.0085451 | 8.9012e-05
2009 | 2008-06-22 | C | 27 | 0.0042058 | 8.5833e-05
2009 | 2008-06-22 | C | 480 | 0.014344 | 0.0015259
2009 | 2008-06-22 | C | 951 | 0.052596 | 0.0030232
2009 | 2008-06-22 | C | 776 | 0.11907 | 0.0024669
2009 | 2008-06-22 | C | 135 | 0.027492 | 0.00042916
2009 | 2008-06-23 | C | 204 | 0.036164 | 0.00064851
2009 | 2008-06-22 | B | 107 | 0.061908 | 0.00034015
2009 | 2008-06-23 | C | 36 | 0.0046922 | 0.00011444
2009 | 2008-06-23 | C | 134 | 0.044687 | 0.00042599
2009 | 2008-06-23 | C | 40 | 0.0053407 | 0.00012716
2009 | 2008-06-23 | C | 1 | 0.00028293 | 3.179e-06
2009 | 2008-06-23 | C | 326 | 0.096215 | 0.0010364
2009 | 2008-06-23 | C | 465 | 0.1638 | 0.0014782
2009 | 2008-06-24 | C | 330 | 0.071457 | 0.0010491
2009 | 2008-06-24 | C | 34 | 0.0054043 | 0.00010809
2009 | 2008-06-24 | B | 409 | 0.27174 | 0.0013002
2009 | 2008-06-24 | C | 11 | 0.001084 | 3.4969e-05
2009 | 2008-06-24 | C | 426 | 0.028439 | 0.0013543
2009 | 2008-06-24 | C | 14 | 0.0014687 | 4.4506e-05
2009 | 2008-06-24 | B | 2 | 0.001119 | 6.358e-06
2009 | 2008-06-24 | B | 290 | 0.092922 | 0.00092191
2009 | 2008-06-24 | B | 42 | 0.033513 | 0.00013352
2009 | 2008-06-24 | C | 426 | 0.017605 | 0.0013543
2009 | 2008-06-24 | C | 95 | 0.022952 | 0.000302
2009 | 2008-06-24 | C | 11 | 0.0014337 | 3.4969e-05
2009 | 2008-06-24 | C | 40 | 0.008774 | 0.00012716
2009 | 2008-06-25 | C | 69 | 0.045599 | 0.00021935
2009 | 2008-06-24 | C | 95 | 0.0099661 | 0.000302
2009 | 2008-06-20 | B | 1 | 0.0010395 | 3.179e-06
2009 | 2008-06-25 | B | 8 | 0.0014496 | 2.5432e-05
2009 | 2008-06-25 | C | 796 | 0.015183 | 0.0025305
2009 | 2008-06-25 | C | 226 | 0.067535 | 0.00071845
2009 | 2008-06-25 | B | 96 | 0.032655 | 0.00030518
2009 | 2008-06-24 | B | 20 | 0.012207 | 6.358e-05
2009 | 2008-06-25 | B | 19 | 0.0011476 | 6.0401e-05
2009 | 2008-06-25 | C | 10 | 0.0094098 | 3.179e-05
2009 | 2008-06-25 | C | 151 | 0.073479 | 0.00048003
2009 | 2008-06-25 | C | 182 | 0.046906 | 0.00057858
2009 | 2008-06-25 | C | 61 | 0.011635 | 0.00019392
2009 | 2008-06-25 | C | 75 | 0.04635 | 0.00023842
2009 | 2008-06-25 | C | 2614 | 0.63485 | 0.0083099
2009 | 2008-06-25 | C | 874 | 0.15541 | 0.0027784
2009 | 2008-06-25 | C | 182 | 0.023143 | 0.00057858
2009 | 2008-06-25 | C | 239 | 0.041683 | 0.00075978
2009 | 2008-06-25 | C | 138 | 0.027199 | 0.0004387
2009 | 2008-06-25 | C | 1700 | 0.21617 | 0.0054043
2009 | 2008-06-25 | C | 2618 | 0.29129 | 0.0083226
2009 | 2008-06-25 | C | 1333 | 0.50691 | 0.0042376
2009 | 2008-06-26 | C | 219 | 0.0048734 | 0.0006962
2009 | 2008-06-26 | C | 632 | 0.014064 | 0.0020091
2009 | 2008-06-26 | C | 8 | 0.001119 | 2.5432e-05
2009 | 2008-06-26 | C | 2 | 0.00068666 | 6.358e-06
2009 | 2008-06-26 | C | 32 | 0.0029501 | 0.00010173
2009 | 2008-06-25 | C | 47 | 0.10309 | 0.00014941
2009 | 2008-06-26 | B | 6 | 0.0028802 | 1.9074e-05
2009 | 2008-06-26 | C | 173 | 0.0010999 | 0.00054997
2009 | 2008-06-26 | C | 15 | 0.00081064 | 4.7685e-05
2009 | 2008-06-26 | C | 3 | 0.0035478 | 9.537e-06
2009 | 2008-06-26 | B | 19 | 0.02253 | 6.0401e-05
2009 | 2008-06-26 | C | 30 | 0.0054361 | 9.537e-05
2009 | 2008-06-26 | C | 266 | 0.025368 | 0.00084561
2009 | 2008-06-26 | C | 393 | 0.033732 | 0.0012493
2009 | 2008-06-26 | C | 5734 | 6.0336 | 0.018228
2009 | 2008-06-26 | C | 1270 | 0.20273 | 0.0040373
2009 | 2008-06-26 | C | 3610 | 0.17214 | 0.011476
2009 | 2008-06-26 | C | 919 | 0.0029215 | 0.0029215
2009 | 2008-08-24 | C | 103 | 0.018079 | 0.00032744
2009 | 2008-06-26 | C | 882 | 0.29535 | 0.0028039
2009 | 2008-06-27 | B | 5 | 0.0012557 | 1.5895e-05
2009 | 2008-06-27 | C | 673 | 0.13844 | 0.0021395
2009 | 2008-06-27 | C | 93 | 0.004139 | 0.00029565
2009 | 2008-06-27 | C | 393 | 0.016241 | 0.0012493
2009 | 2008-08-24 | C | 96 | 0.091291 | 0.00030518
2009 | 2008-06-27 | B | 4 | 0.0023397 | 1.2716e-05
2009 | 2008-06-27 | C | 647 | 0.053477 | 0.0020568
2009 | 2008-06-27 | B | 1 | 0.0010427 | 3.179e-06
2009 | 2008-06-27 | C | 26 | 0.0058684 | 8.2654e-05
2009 | 2008-06-27 | C | 1 | 7.9475e-05 | 3.179e-06
2009 | 2008-06-27 | C | 8 | 0.0040691 | 2.5432e-05
2009 | 2008-06-28 | C | 573 | 0.098364 | 0.0018216
2009 | 2008-06-28 | C | 177 | 0.030385 | 0.00056268
2009 | 2008-06-27 | C | 202 | 0.0096323 | 0.00064216
2009 | 2008-06-27 | C | 86 | 0.0095688 | 0.00027339
2009 | 2008-06-27 | C | 86 | 0.019411 | 0.00027339
2009 | 2008-06-27 | C | 126 | 0.0084116 | 0.00040055
2009 | 2008-06-26 | C | 2 | 0.0058684 | 6.358e-06
2009 | 2008-06-27 | C | 393 | 0.053722 | 0.0012493
2009 | 2008-06-28 | C | 11 | 0.0019932 | 3.4969e-05
2009 | 2008-06-27 | C | 498 | 0.26164 | 0.0015831
2009 | 2008-06-28 | C | 1 | 0.00034333 | 3.179e-06
2009 | 2008-06-28 | C | 5 | 0.00058811 | 1.5895e-05
2009 | 2008-06-28 | C | 209 | 0.20663 | 0.00066441
2009 | 2008-06-28 | C | 134 | 0.0085197 | 0.00042599
2009 | 2008-06-28 | C | 6 | 0.0019455 | 1.9074e-05
2009 | 2008-06-28 | C | 1 | 0.00011762 | 3.179e-06
2009 | 2008-06-28 | C | 713 | 0.033999 | 0.0022666
2009 | 2008-06-28 | C | 504 | 0.18703 | 0.0016022
2009 | 2008-06-27 | C | 479 | 0.26256 | 0.0015227
2009 | 2008-06-28 | C | 868 | 0.15856 | 0.0027594
2009 | 2008-06-29 | C | 69 | 0.014477 | 0.00021935
2009 | 2008-06-29 | C | 131 | 0.037318 | 0.00041645
2009 | 2008-06-29 | C | 672 | 0.068828 | 0.0021363
2009 | 2008-09-29 | C | 22 | 0.0047558 | 6.9938e-05
2009 | 2008-06-29 | C | 217 | 0.027908 | 0.00068984
2009 | 2008-09-29 | C | 706 | 0.11991 | 0.0022444
2009 | 2008-06-29 | B | 269 | 0.27536 | 0.00085515
2009 | 2008-06-29 | C | 413 | 0.11725 | 0.0013129
2009 | 2008-06-29 | C | 31 | 0.0026608 | 9.8549e-05
2009 | 2008-06-29 | C | 747 | 0.057374 | 0.0023747
2009 | 2008-06-29 | C | 95 | 0.013288 | 0.000302
2009 | 2008-06-29 | C | 125 | 0.010332 | 0.00039737
2009 | 2008-09-11 | C | 78 | 0.08439 | 0.00024796
2009 | 2008-06-30 | C | 135 | 0.37037 | 0.00042916
2009 | 2008-06-30 | C | 27 | 0.0038625 | 8.5833e-05
2009 | 2008-06-30 | C | 20 | 0.0094098 | 6.358e-05
2009 | 2008-06-30 | C | 294 | 0.017758 | 0.00093462
2009 | 2008-06-30 | B | 8 | 0.0045269 | 2.5432e-05
2009 | 2008-06-30 | B | 28 | 0.028484 | 8.9012e-05
2009 | 2008-06-30 | B | 1 | 0.0011826 | 3.179e-06
2009 | 2008-06-30 | B | 28 | 0.021452 | 8.9012e-05
2009 | 2008-06-30 | C | 11 | 0.00090919 | 3.4969e-05
2009 | 2008-06-30 | C | 60 | 0.025693 | 0.00019074
2009 | 2008-09-11 | C | 66 | 0.02287 | 0.00020981
2009 | 2008-06-30 | C | 23 | 0.0024129 | 7.3117e-05
2009 | 2008-07-01 | C | 404 | 0.053827 | 0.0012843
2009 | 2008-07-01 | C | 176 | 0.059867 | 0.0005595
2009 | 2008-07-01 | B | 1 | 0.00078203 | 3.179e-06
2009 | 2008-07-01 | B | 51 | 0.018645 | 0.00016213
2009 | 2008-07-01 | B | 1 | 0.00068348 | 3.179e-06
2009 | 2008-07-01 | B | 19 | 0.014315 | 6.0401e-05
2009 | 2008-07-01 | B | 388 | 0.13075 | 0.0012334
2009 | 2008-07-01 | B | 1 | 0.00039737 | 3.179e-06
2009 | 2008-07-01 | C | 95 | 0.029294 | 0.000302
2009 | 2008-07-02 | C | 1220 | 0.054297 | 0.0038784
2009 | 2008-07-02 | C | 198 | 0.045736 | 0.00062944
2009 | 2008-07-02 | B | 12 | 0.0045396 | 3.8148e-05
2009 | 2008-07-02 | B | 1 | 0.00089012 | 3.179e-06
2009 | 2008-07-01 | C | 3 | 0.013609 | 9.537e-06
2009 | 2008-07-02 | B | 30 | 0.0054361 | 9.537e-05
2009 | 2008-07-02 | B | 96 | 0.081484 | 0.00030518
2009 | 2008-07-02 | C | 247 | 0.082934 | 0.00078521
2009 | 2008-07-02 | C | 1081 | 0.15464 | 0.0034365
2009 | 2008-07-02 | C | 132 | 0.059015 | 0.00041963
2009 | 2008-07-02 | C | 4 | 0.00021617 | 1.2716e-05
2009 | 2008-07-02 | C | 146 | 0.087257 | 0.00046413
2009 | 2008-07-02 | C | 16 | 0.0076804 | 5.0864e-05
2009 | 2008-07-02 | C | 897 | 0.27276 | 0.0028516
2009 | 2008-07-02 | C | 797 | 0.18242 | 0.0025337
2009 | 2008-07-02 | C | 188 | 0.16854 | 0.00059765
2009 | 2008-07-02 | C | 284 | 0.014064 | 0.00090283
2009 | 2008-07-03 | B | 3 | 0.00054361 | 9.537e-06
2009 | 2008-07-03 | B | 6 | 0.0035096 | 1.9074e-05
2009 | 2008-07-03 | B | 3 | 0.002184 | 9.537e-06
2009 | 2008-07-03 | B | 42 | 0.017949 | 0.00013352
2009 | 2008-07-03 | C | 177 | 0.010128 | 0.00056268
2009 | 2008-07-03 | C | 274 | 0.088872 | 0.00087104
2009 | 2008-07-03 | B | 30 | 0.0084879 | 9.537e-05
2009 | 2008-07-03 | C | 857 | 0.2998 | 0.0027244
2009 | 2008-07-03 | B | 67 | 0.044089 | 0.00021299
2009 | 2008-07-03 | B | 94 | 0.061259 | 0.00029883
2009 | 2008-07-03 | C | 205 | 0.091186 | 0.00065169
2009 | 2008-07-03 | C | 394 | 0.31304 | 0.0012525
2009 | 2008-07-03 | C | 880 | 0.054087 | 0.0027975
2009 | 2008-07-04 | C | 311 | 0.04141 | 0.00098867
2009 | 2008-07-04 | C | 78 | 0.040291 | 0.00024796
2009 | 2008-07-04 | B | 29 | 0.014013 | 9.2191e-05
2009 | 2008-07-04 | C | 215 | 0.037108 | 0.00068348
2009 | 2008-07-03 | B | 2 | 0.0019646 | 6.358e-06
2009 | 2008-07-04 | B | 42 | 0.049669 | 0.00013352
2009 | 2008-07-04 | B | 111 | 0.095885 | 0.00035287
2009 | 2008-07-04 | C | 40 | 0.013345 | 0.00012716
2009 | 2008-07-04 | C | 14 | 0.0027594 | 4.4506e-05
2009 | 2008-07-04 | C | 713 | 0.078028 | 0.0022666
2009 | 2008-07-04 | C | 263 | 0.081776 | 0.00083608
2009 | 2008-07-04 | C | 863 | 0.13498 | 0.0027435
2009 | 2008-07-04 | C | 57 | 0.037026 | 0.0001812
2009 | 2008-07-05 | C | 45 | 0.012303 | 0.00014305
2009 | 2008-07-05 | C | 1007 | 0.65024 | 0.0032012
2009 | 2008-07-05 | C | 35 | 0.016022 | 0.00011126
2009 | 2008-07-05 | C | 31 | 0.0046318 | 9.8549e-05
2009 | 2008-07-05 | C | 720 | 0.12131 | 0.0022889
2009 | 2008-07-05 | C | 343 | 0.11811 | 0.0010904
2009 | 2008-07-05 | B | 3 | 0.0018311 | 9.537e-06
2009 | 2008-07-05 | C | 1253 | 0.84047 | 0.0039833
2009 | 2008-07-04 | C | 197 | 0.11214 | 0.00062626
2009 | 2008-07-05 | C | 1253 | 0.027883 | 0.0039833
2009 | 2008-07-05 | C | 1251 | 0.1415 | 0.0039769
2009 | 2008-07-05 | C | 69 | 0.024679 | 0.00021935
2009 | 2008-07-05 | C | 100 | 0.022075 | 0.0003179
2009 | 2008-07-05 | C | 1198 | 0.27802 | 0.0038084
2009 | 2008-07-05 | C | 558 | 0.062086 | 0.0017739
2009 | 2008-07-05 | C | 580 | 0.064534 | 0.0018438
2009 | 2008-07-05 | C | 543 | 0.060417 | 0.0017262
2009 | 2008-07-05 | C | 415 | 0.039578 | 0.0013193
2009 | 2008-07-06 | C | 720 | 0.13733 | 0.0022889
2009 | 2008-07-06 | C | 392 | 0.078508 | 0.0012462
2009 | 2008-07-05 | C | 378 | 0.095739 | 0.0012017
2009 | 2008-09-21 | C | 546 | 0.10516 | 0.0017357
2009 | 2008-07-05 | C | 152 | 0.027543 | 0.00048321
2009 | 2008-07-06 | C | 19 | 0.014738 | 6.0401e-05
2009 | 2008-07-06 | C | 76 | 0.01353 | 0.0002416
2009 | 2008-07-06 | C | 138 | 0.075895 | 0.0004387
2009 | 2008-07-06 | C | 16 | 0.0024415 | 5.0864e-05
2009 | 2008-07-06 | C | 33 | 0.0097563 | 0.00010491
2009 | 2008-07-06 | C | 15 | 0.0077726 | 4.7685e-05
2009 | 2008-07-05 | C | 1 | 0.0033443 | 3.179e-06
2009 | 2008-09-21 | C | 27 | 0.0097849 | 8.5833e-05
2009 | 2008-07-06 | C | 4 | 0.0005595 | 1.2716e-05
2009 | 2008-07-06 | C | 3 | 0.0010872 | 9.537e-06
2009 | 2008-07-07 | C | 347 | 0.044042 | 0.0011031
2009 | 2008-07-07 | B | 2 | 0.0016594 | 6.358e-06
2009 | 2008-07-07 | B | 28 | 0.017446 | 8.9012e-05
2009 | 2008-07-07 | C | 7 | 0.0037162 | 2.2253e-05
2009 | 2008-07-07 | C | 135 | 0.053646 | 0.00042916
2009 | 2008-07-08 | C | 230 | 0.039795 | 0.00073117
2009 | 2008-07-08 | C | 1030 | 0.17965 | 0.0032744
2009 | 2008-07-08 | B | 17 | 0.0065932 | 5.4043e-05
2009 | 2008-07-08 | C | 3 | 0.00033379 | 9.537e-06
2009 | 2008-07-08 | B | 1 | 0.00088694 | 3.179e-06
2009 | 2008-07-08 | B | 12 | 0.012284 | 3.8148e-05
2009 | 2008-07-08 | B | 146 | 0.05059 | 0.00046413
2009 | 2008-07-08 | B | 11 | 0.0017135 | 3.4969e-05
2009 | 2008-07-08 | B | 10 | 0.012239 | 3.179e-05
2009 | 2008-07-08 | C | 1269 | 0.22584 | 0.0040341
2009 | 2008-07-08 | C | 714 | 0.046235 | 0.0022698
2009 | 2008-07-08 | C | 6 | 0.0025559 | 1.9074e-05
2009 | 2008-07-09 | B | 70 | 0.054297 | 0.00022253
2009 | 2008-07-09 | B | 23 | 0.023836 | 7.3117e-05
2009 | 2008-07-09 | B | 23 | 0.017694 | 7.3117e-05
2009 | 2008-07-09 | C | 67 | 0.015548 | 0.00021299
2009 | 2008-07-10 | B | 13 | 0.0075215 | 4.1327e-05
2009 | 2008-07-10 | B | 24 | 0.013504 | 7.6296e-05
2009 | 2008-07-10 | B | 1 | 8.5833e-05 | 3.179e-06
2009 | 2008-07-10 | B | 21 | 0.022498 | 6.6759e-05
2009 | 2008-07-10 | B | 4 | 0.0014751 | 1.2716e-05
2009 | 2008-07-10 | B | 33 | 0.037452 | 0.00010491
2009 | 2008-07-11 | B | 17 | 0.0043775 | 5.4043e-05
2009 | 2008-07-11 | C | 2 | 0.0011635 | 6.358e-06
2009 | 2008-07-11 | B | 28 | 0.007744 | 8.9012e-05
2009 | 2008-07-11 | C | 966 | 0.14433 | 0.0030709
2009 | 2008-07-11 | C | 67 | 0.23512 | 0.00021299
2009 | 2008-07-11 | C | 10 | 0.0022253 | 3.179e-05
2009 | 2008-07-12 | C | 10 | 0.00079475 | 3.179e-05
2009 | 2008-07-12 | C | 816 | 0.031129 | 0.0025941
2009 | 2008-07-12 | C | 816 | 0.45655 | 0.0025941
2009 | 2008-07-12 | C | 148 | 0.088961 | 0.00047049
2009 | 2008-07-12 | C | 134 | 0.027263 | 0.00042599
2009 | 2008-07-12 | C | 15 | 0.013686 | 4.7685e-05
2009 | 2008-07-13 | C | 49 | 0.03941 | 0.00015577
2009 | 2008-07-13 | C | 2267 | 0.54328 | 0.0072068
2009 | 2008-07-13 | B | 393 | 0.26087 | 0.0012493
2009 | 2008-07-12 | C | 200 | 0.31408 | 0.0006358
2009 | 2008-07-11 | C | 7850 | 0.27451 | 0.024955
2009 | 2008-07-11 | C | 2183 | 0.055518 | 0.0069397
2009 | 2008-07-14 | B | 12 | 0.0014496 | 3.8148e-05
2009 | 2008-07-14 | C | 32 | 0.0045778 | 0.00010173
2009 | 2008-07-14 | C | 86 | 0.028586 | 0.00027339
2009 | 2008-07-14 | B | 13 | 0.0082527 | 4.1327e-05
2009 | 2008-07-14 | C | 5203 | 0.13401 | 0.01654
2009 | 2008-07-15 | C | 1 | 0.00062308 | 3.179e-06
2009 | 2008-07-14 | C | 379 | 0.0060242 | 0.0012048
2009 | 2008-07-15 | B | 37 | 0.040227 | 0.00011762
2009 | 2008-07-15 | B | 130 | 0.12522 | 0.00041327
2009 | 2008-07-15 | C | 237 | 0.075848 | 0.00075342
2009 | 2008-07-14 | C | 906 | 0.054723 | 0.0028802
2009 | 2008-07-15 | B | 9 | 0.009413 | 2.8611e-05
2009 | 2008-08-16 | C | 297 | 0.054761 | 0.00094416
2009 | 2008-07-15 | C | 665 | 0.03171 | 0.002114
2009 | 2008-07-16 | B | 1 | 0.00060719 | 3.179e-06
2009 | 2008-07-16 | B | 7 | 0.0079443 | 2.2253e-05
2009 | 2008-08-16 | C | 48 | 0.0039674 | 0.00015259
2009 | 2008-07-16 | B | 226 | 0.038053 | 0.00071845
2009 | 2008-07-16 | B | 2 | 0.0013797 | 6.358e-06
2009 | 2008-07-17 | B | 1 | 0.00062626 | 3.179e-06
2009 | 2008-07-17 | C | 681 | 0.357 | 0.0021649
2009 | 2008-07-18 | B | 78 | 0.062486 | 0.00024796
2009 | 2008-07-18 | B | 32 | 0.0084434 | 0.00010173
2009 | 2008-07-18 | C | 40 | 0.011699 | 0.00012716
2009 | 2008-07-19 | C | 5738 | 4.615 | 0.018241
2009 | 2008-07-19 | C | 3492 | 0.88808 | 0.011101
2009 | 2008-07-19 | C | 2648 | 0.5135 | 0.008418
2009 | 2008-07-19 | C | 493 | 0.26025 | 0.0015672
2009 | 2008-07-19 | C | 832 | 0.18476 | 0.0026449
2009 | 2008-07-19 | C | 1548 | 0.13529 | 0.0049211
2009 | 2008-07-19 | C | 913 | 0.13641 | 0.0029024
2009 | 2008-07-19 | C | 218 | 0.13722 | 0.00069302
2009 | 2008-07-19 | C | 165 | 0.12618 | 0.00052453
2009 | 2008-07-19 | C | 209 | 0.10525 | 0.00066441
2009 | 2008-07-19 | C | 398 | 0.05651 | 0.0012652
2009 | 2008-07-19 | C | 1377 | 0.039397 | 0.0043775
2009 | 2008-07-19 | C | 208 | 0.031828 | 0.00066123
2009 | 2008-07-19 | C | 35 | 0.024256 | 0.00011126
2009 | 2008-07-19 | C | 70 | 0.0082336 | 0.00022253
2009 | 2008-07-19 | C | 10 | 0.0072481 | 3.179e-05
2009 | 2008-07-19 | C | 324 | 0.00412 | 0.00103
2009 | 2008-07-19 | C | 29 | 0.0029501 | 9.2191e-05
2009 | 2008-07-19 | C | 1 | 0.00072481 | 3.179e-06
2009 | 2008-10-08 | C | 166 | 0.23726 | 0.00052771
2009 | 2008-07-20 | C | 989 | 0.0918 | 0.003144
2009 | 2008-07-20 | C | 40 | 0.0053407 | 0.00012716
2009 | 2008-07-20 | C | 39 | 0.0092986 | 0.00012398
2009 | 2008-07-20 | C | 1033 | 0.1215 | 0.0032839
2009 | 2008-10-08 | C | 166 | 0.09907 | 0.00052771
2009 | 2008-07-20 | B | 5 | 0.00027021 | 1.5895e-05
2009 | 2008-07-20 | B | 40 | 0.037131 | 0.00012716
2009 | 2008-07-20 | C | 26 | 0.0075215 | 8.2654e-05
2009 | 2008-07-20 | C | 76 | 0.0086977 | 0.0002416
2009 | 2008-07-20 | C | 126 | 0.0068094 | 0.00040055
2009 | 2008-07-20 | B | 8 | 0.0090792 | 2.5432e-05
2009 | 2008-07-20 | B | 141 | 0.19947 | 0.00044824
2009 | 2008-07-20 | C | 51 | 0.0025941 | 0.00016213
2009 | 2008-07-20 | C | 442 | 0.11188 | 0.0014051
2009 | 2008-07-20 | C | 2281 | 0.58527 | 0.0072513
2009 | 2008-07-20 | C | 90 | 0.19818 | 0.00028611
2009 | 2008-07-21 | C | 1219 | 0.038752 | 0.0038752
2009 | 2008-07-21 | C | 9 | 0.06489 | 2.8611e-05
2009 | 2008-07-21 | C | 218 | 0.041149 | 0.00069302
2009 | 2008-07-21 | C | 19 | 0.0041677 | 6.0401e-05
2009 | 2008-07-21 | C | 247 | 0.05418 | 0.00078521
2009 | 2008-07-21 | C | 7 | 0.0014242 | 2.2253e-05
2009 | 2008-07-21 | C | 377 | 1.0089 | 0.0011985
2009 | 2008-07-22 | B | 149 | 0.14589 | 0.00047367
2009 | 2008-07-22 | C | 96 | 0.0073244 | 0.00030518
2009 | 2008-07-22 | C | 717 | 0.015955 | 0.0022793
2009 | 2008-07-22 | C | 1353 | 0.22257 | 0.0043012
2009 | 2008-07-23 | B | 298 | 0.098523 | 0.00094734
2009 | 2008-07-23 | C | 23 | 0.0039483 | 7.3117e-05
2009 | 2008-07-22 | B | 2 | 0.0010364 | 6.358e-06
2009 | 2008-07-23 | B | 1 | 0.00035605 | 3.179e-06
2009 | 2008-07-23 | C | 218 | 0.036037 | 0.00069302
2009 | 2008-07-23 | C | 86 | 0.019907 | 0.00027339
2009 | 2008-07-23 | B | 43 | 0.032124 | 0.0001367
2009 | 2008-07-23 | B | 49 | 0.052495 | 0.00015577
2009 | 2008-07-23 | C | 28 | 0.0023143 | 8.9012e-05
2009 | 2008-07-23 | C | 15 | 0.0078203 | 4.7685e-05
2009 | 2008-07-23 | C | 1 | 0.00012398 | 3.179e-06
2009 | 2008-07-23 | C | 20 | 0.0056586 | 6.358e-05
2009 | 2008-07-23 | C | 772 | 0.22243 | 0.0024542
2009 | 2008-07-24 | C | 22 | 0.0016785 | 6.9938e-05
2009 | 2008-07-23 | B | 59 | 0.059832 | 0.00018756
2009 | 2008-07-24 | B | 146 | 0.06405 | 0.00046413
2009 | 2008-07-24 | B | 130 | 0.050832 | 0.00041327
2009 | 2008-07-24 | B | 2 | 0.0027467 | 6.358e-06
2009 | 2008-07-24 | C | 340 | 0.090665 | 0.0010809
2009 | 2008-07-24 | C | 75 | 0.0090601 | 0.00023842
2009 | 2008-07-24 | C | 19 | 0.0032012 | 6.0401e-05
2009 | 2008-07-25 | B | 298 | 0.070103 | 0.00094734
2009 | 2008-07-25 | C | 29 | 0.0079284 | 9.2191e-05
2009 | 2008-07-25 | C | 56 | 0.022787 | 0.00017802
2009 | 2008-07-25 | B | 1 | 0.00033062 | 3.179e-06
2009 | 2008-07-25 | B | 5 | 0.002114 | 1.5895e-05
2009 | 2008-07-25 | C | 3 | 0.0019074 | 9.537e-06
2009 | 2008-07-25 | C | 104 | 0.038021 | 0.00033062
2009 | 2008-07-25 | C | 32 | 0.0014242 | 0.00010173
2009 | 2008-07-25 | C | 13 | 0.0011158 | 4.1327e-05
2009 | 2008-07-25 | C | 37 | 0.0015291 | 0.00011762
2009 | 2008-07-26 | C | 4 | 0.0027085 | 1.2716e-05
2009 | 2008-07-26 | C | 49 | 0.0048289 | 0.00015577
2009 | 2008-07-26 | B | 1 | 0.00057858 | 3.179e-06
2009 | 2008-07-26 | C | 304 | 0.0077313 | 0.00096641
2009 | 2008-07-26 | C | 37 | 0.00094098 | 0.00011762
2009 | 2008-07-26 | C | 2185 | 0.048623 | 0.0069461
2009 | 2008-07-26 | C | 7869 | 0.37523 | 0.025015
2009 | 2008-07-26 | C | 1711 | 0.043514 | 0.0054393
2009 | 2008-07-26 | C | 324 | 0.062931 | 0.00103
2009 | 2008-07-26 | C | 2 | 0.0012398 | 6.358e-06
2009 | 2008-07-26 | C | 52 | 0.0057858 | 0.00016531
2009 | 2008-07-26 | C | 97 | 0.016343 | 0.00030836
2009 | 2008-07-26 | C | 84 | 0.021096 | 0.00026704
2009 | 2008-07-27 | C | 20 | 0.0017167 | 6.358e-05
2009 | 2008-07-26 | C | 661 | 0.22004 | 0.0021013
2009 | 2008-07-26 | C | 29 | 0.0015672 | 9.2191e-05
2009 | 2008-07-26 | C | 2320 | 0.66492 | 0.0073753
2009 | 2008-07-26 | C | 2936 | 13.8043 | 0.0093335
2009 | 2008-07-27 | C | 7868 | 15.3826 | 0.025012
2009 | 2008-07-26 | C | 6 | 0.018063 | 1.9074e-05
2009 | 2008-07-27 | C | 10 | 0.018375 | 3.179e-05
2009 | 2008-07-26 | C | 51 | 0.0082686 | 0.00016213
2009 | 2008-07-27 | C | 3 | 0.0023366 | 9.537e-06
2009 | 2008-07-27 | C | 44 | 0.0051118 | 0.00013988
2009 | 2008-07-27 | C | 36 | 0.0043489 | 0.00011444
2009 | 2008-07-26 | C | 52 | 0.024961 | 0.00016531
2009 | 2008-07-26 | C | 240 | 0.47993 | 0.00076296
2009 | 2008-07-27 | C | 16 | 0.00096641 | 5.0864e-05
2009 | 2008-07-26 | C | 212 | 0.089918 | 0.00067395
2009 | 2008-07-26 | C | 359 | 0.19757 | 0.0011413
2009 | 2008-07-27 | C | 108 | 0.043177 | 0.00034333
2009 | 2008-07-26 | C | 74 | 0.11972 | 0.00023525
2009 | 2008-07-26 | C | 138 | 0.14648 | 0.0004387
2009 | 2008-07-27 | C | 2 | 0.00010809 | 6.358e-06
2009 | 2008-07-27 | C | 13 | 0.0055378 | 4.1327e-05
2009 | 2008-07-27 | C | 4 | 0.0003942 | 1.2716e-05
2009 | 2008-07-27 | C | 565 | 0.10832 | 0.0017961
2009 | 2008-07-26 | C | 816 | 3.5435 | 0.0025941
2009 | 2008-07-27 | C | 4 | 0.0015513 | 1.2716e-05
2009 | 2008-07-26 | C | 138 | 0.47467 | 0.0004387
2009 | 2008-07-26 | C | 394 | 0.18913 | 0.0012525
2009 | 2008-07-26 | C | 537 | 0.29352 | 0.0017071
2009 | 2008-07-26 | C | 38 | 0.02416 | 0.0001208
2009 | 2008-07-26 | C | 296 | 0.14766 | 0.00094098
2009 | 2008-07-26 | C | 5738 | 5.7824 | 0.018241
2009 | 2008-07-26 | C | 2997 | 2.4771 | 0.0095274
2009 | 2008-07-27 | C | 37 | 0.00070574 | 0.00011762
2009 | 2008-07-27 | C | 105 | 0.056745 | 0.00033379
2009 | 2008-07-26 | C | 212 | 0.68186 | 0.00067395
2009 | 2008-07-26 | C | 363 | 0.59403 | 0.001154
2009 | 2008-07-26 | C | 198 | 1.1091 | 0.00062944
2009 | 2008-07-27 | C | 74 | 0.046579 | 0.00023525
2009 | 2008-07-26 | C | 747 | 2.7452 | 0.0023747
2009 | 2008-07-27 | C | 57 | 0.0241 | 0.0001812
2009 | 2008-07-27 | C | 255 | 0.0056745 | 0.00081064
2009 | 2008-07-26 | C | 178 | 0.075101 | 0.00056586
2009 | 2008-07-26 | C | 1578 | 0.50624 | 0.0050165
2009 | 2008-07-26 | C | 324 | 0.85886 | 0.00103
2009 | 2008-07-26 | C | 15 | 0.0032903 | 4.7685e-05
2009 | 2008-07-26 | C | 430 | 0.62106 | 0.001367
2009 | 2008-07-26 | C | 163 | 0.0357 | 0.00051818
2009 | 2008-07-28 | C | 36 | 0.013275 | 0.00011444
2009 | 2008-07-27 | C | 28 | 0.0084561 | 8.9012e-05
2009 | 2008-07-28 | C | 3 | 0.0012207 | 9.537e-06
2009 | 2008-07-27 | C | 25 | 0.032346 | 7.9475e-05
2009 | 2008-07-28 | C | 28 | 0.0033824 | 8.9012e-05
2009 | 2008-07-27 | C | 9 | 0.0024605 | 2.8611e-05
2009 | 2008-07-26 | C | 1028 | 2.3559 | 0.003268
2009 | 2008-07-27 | C | 11 | 0.0026576 | 3.4969e-05
2009 | 2008-07-28 | C | 37 | 0.0037639 | 0.00011762
2009 | 2008-07-27 | C | 140 | 0.029374 | 0.00044506
2009 | 2008-07-27 | C | 117 | 0.018969 | 0.00037194
2009 | 2008-07-27 | C | 182 | 0.20398 | 0.00057858
2009 | 2008-07-28 | C | 70 | 0.0095688 | 0.00022253
2009 | 2008-07-27 | C | 208 | 0.24747 | 0.00066123
2009 | 2008-07-26 | C | 259 | 0.66912 | 0.00082336
2009 | 2008-07-28 | C | 93 | 0.42632 | 0.00029565
2009 | 2008-07-27 | C | 3 | 0.00065805 | 9.537e-06
2009 | 2008-07-27 | C | 44 | 0.01175 | 0.00013988
2009 | 2008-07-28 | C | 31 | 0.0073912 | 9.8549e-05
2009 | 2008-07-28 | C | 20 | 0.0058493 | 6.358e-05
2009 | 2008-07-27 | C | 241 | 0.01257 | 0.00076614
2009 | 2008-07-27 | C | 8 | 0.00094098 | 2.5432e-05
2009 | 2008-07-27 | C | 21 | 0.011883 | 6.6759e-05
2009 | 2008-07-26 | C | 46 | 0.34116 | 0.00014623
2009 | 2008-07-28 | C | 4 | 0.0028611 | 1.2716e-05
2009 | 2008-07-28 | C | 8 | 0.0029247 | 2.5432e-05
2009 | 2008-07-28 | C | 57 | 0.010147 | 0.0001812
2009 | 2008-07-27 | C | 254 | 0.48616 | 0.00080746
2009 | 2008-07-28 | C | 11 | 0.00083925 | 3.4969e-05
2009 | 2008-07-27 | C | 97 | 0.075549 | 0.00030836
2009 | 2008-07-27 | C | 501 | 0.26188 | 0.0015927
2009 | 2008-07-26 | C | 216 | 1.2274 | 0.00068666
2009 | 2008-07-26 | C | 191 | 0.37224 | 0.00060719
2009 | 2008-07-26 | C | 286 | 0.81282 | 0.00090919
2009 | 2008-07-28 | C | 27 | 0.016025 | 8.5833e-05
2009 | 2008-07-28 | C | 627 | 0.2028 | 0.0019932
2009 | 2008-07-26 | C | 7868 | 0.6003 | 0.025012
2009 | 2008-07-26 | C | 583 | 0.58411 | 0.0018534
2009 | 2008-07-26 | C | 312 | 1.5681 | 0.00099185
2009 | 2008-07-26 | C | 261 | 1.4538 | 0.00082972
2009 | 2008-07-29 | C | 62 | 0.012417 | 0.0001971
2009 | 2008-07-29 | C | 11 | 0.0004546 | 3.4969e-05
2009 | 2008-07-29 | C | 300 | 0.039102 | 0.0009537
2009 | 2008-07-29 | C | 45 | 0.0044347 | 0.00014305
2009 | 2008-07-29 | C | 5 | 0.00057222 | 1.5895e-05
2009 | 2008-07-29 | C | 82 | 0.0041708 | 0.00026068
2009 | 2008-07-29 | C | 2935 | 0.99835 | 0.0093303
2009 | 2008-07-30 | C | 862 | 5.167 | 0.0027403
2009 | 2008-07-30 | C | 1147 | 1.3955 | 0.0036463
2009 | 2008-07-29 | C | 24 | 0.0083162 | 7.6296e-05
2009 | 2008-07-30 | C | 1940 | 0.86209 | 0.0061672
2009 | 2008-07-30 | C | 171 | 0.77899 | 0.00054361
2009 | 2008-07-30 | C | 825 | 0.73937 | 0.0026227
2009 | 2008-07-30 | C | 968 | 0.61072 | 0.0030773
2009 | 2008-07-30 | C | 1381 | 0.49609 | 0.0043902
2009 | 2008-07-30 | C | 459 | 0.46751 | 0.0014592
2009 | 2008-07-30 | C | 532 | 0.44987 | 0.0016912
2009 | 2008-07-30 | C | 99 | 0.40567 | 0.00031472
2009 | 2008-07-30 | C | 794 | 0.38783 | 0.0025241
2009 | 2008-07-30 | C | 379 | 0.37153 | 0.0012048
2009 | 2008-07-30 | C | 809 | 0.3681 | 0.0025718
2009 | 2008-07-30 | C | 418 | 0.36621 | 0.0013288
2009 | 2008-07-30 | C | 5736 | 0.36469 | 0.018235
2009 | 2008-07-30 | C | 145 | 0.33586 | 0.00046095
2009 | 2008-07-30 | C | 400 | 0.27103 | 0.0012716
2009 | 2008-07-30 | C | 203 | 0.26978 | 0.00064534
2009 | 2008-07-30 | C | 254 | 0.25464 | 0.00080746
2009 | 2008-07-30 | C | 666 | 0.24161 | 0.0021172
2009 | 2008-07-30 | C | 247 | 0.23652 | 0.00078521
2009 | 2008-07-30 | C | 192 | 0.23411 | 0.00061037
2009 | 2008-07-30 | C | 391 | 0.23345 | 0.001243
2009 | 2008-07-30 | C | 41 | 0.23318 | 0.00013034
2009 | 2008-08-03 | C | 706 | 0.23196 | 0.0022444
2009 | 2008-07-30 | C | 63 | 0.22093 | 0.00020028
2009 | 2008-07-31 | C | 503 | 0.20628 | 0.001599
2009 | 2008-07-30 | C | 69 | 0.20202 | 0.00021935
2009 | 2008-08-02 | C | 1247 | 0.19028 | 0.0039642
2009 | 2008-07-30 | C | 95 | 0.1812 | 0.000302
2009 | 2008-07-30 | C | 302 | 0.1749 | 0.00096006
2009 | 2008-07-31 | C | 808 | 0.17209 | 0.0025686
2009 | 2008-07-30 | C | 421 | 0.1606 | 0.0013384
2009 | 2008-07-30 | C | 3606 | 0.16049 | 0.011463
2009 | 2008-08-03 | C | 1296 | 0.15931 | 0.00412
2009 | 2008-07-30 | C | 358 | 0.15244 | 0.0011381
2009 | 2008-07-30 | C | 547 | 0.14876 | 0.0017389
2009 | 2008-07-31 | C | 85 | 0.14809 | 0.00027021
2009 | 2008-07-30 | C | 301 | 0.14736 | 0.00095688
2009 | 2008-07-30 | C | 1130 | 0.1401 | 0.0035923
2009 | 2008-07-30 | C | 262 | 0.13829 | 0.0008329
2009 | 2008-07-31 | C | 877 | 0.13661 | 0.002788
2009 | 2008-07-30 | C | 203 | 0.13455 | 0.00064534
2009 | 2008-07-30 | C | 22 | 0.13246 | 6.9938e-05
2009 | 2008-07-30 | C | 465 | 0.13199 | 0.0014782
2009 | 2008-07-30 | C | 113 | 0.12965 | 0.00035923
2009 | 2008-07-30 | C | 96 | 0.12769 | 0.00030518
2009 | 2008-07-30 | C | 114 | 0.12757 | 0.00036241
2009 | 2008-07-30 | C | 61 | 0.12385 | 0.00019392
2009 | 2008-07-31 | C | 799 | 0.11938 | 0.00254
2009 | 2008-07-30 | C | 387 | 0.11817 | 0.0012303
2009 | 2008-08-02 | C | 972 | 0.11601 | 0.00309
2009 | 2008-07-31 | C | 1367 | 0.11299 | 0.0043457
2009 | 2008-08-01 | C | 285 | 0.11212 | 0.00090601
2009 | 2008-07-30 | C | 443 | 0.11126 | 0.0014083
2009 | 2008-07-30 | C | 31 | 0.10022 | 9.8549e-05
2009 | 2008-07-30 | C | 656 | 0.10013 | 0.0020854
2009 | 2008-07-30 | C | 322 | 0.092604 | 0.0010236
2009 | 2008-07-30 | C | 352 | 0.090639 | 0.001119
2009 | 2008-07-31 | C | 186 | 0.088103 | 0.00059129
2009 | 2008-07-30 | C | 109 | 0.087667 | 0.00034651
2009 | 2008-08-03 | C | 395 | 0.086408 | 0.0012557
2009 | 2008-07-30 | C | 121 | 0.080448 | 0.00038466
2009 | 2008-08-01 | C | 16 | 0.079297 | 5.0864e-05
2009 | 2008-08-02 | C | 15 | 0.073292 | 4.7685e-05
2009 | 2008-07-30 | C | 22 | 0.073225 | 6.9938e-05
2009 | 2008-07-31 | C | 286 | 0.069105 | 0.00090919
2009 | 2008-07-29 | C | 1165 | 0.56812 | 0.0037035
2009 | 2008-07-30 | C | 44 | 0.068819 | 0.00013988
2009 | 2008-07-31 | C | 152 | 0.06763 | 0.00048321
2009 | 2008-07-31 | C | 86 | 0.063154 | 0.00027339
2009 | 2008-08-02 | C | 195 | 0.06199 | 0.0006199
2009 | 2008-07-30 | C | 41 | 0.060086 | 0.00013034
2009 | 2008-07-30 | C | 28 | 0.05946 | 8.9012e-05
2009 | 2008-07-30 | C | 330 | 0.057699 | 0.0010491
2009 | 2008-07-30 | C | 87 | 0.056697 | 0.00027657
2009 | 2008-07-30 | C | 54 | 0.053512 | 0.00017167
2009 | 2008-07-31 | C | 671 | 0.052943 | 0.0021331
2009 | 2008-08-02 | C | 252 | 0.05198 | 0.00080111
2009 | 2008-08-01 | C | 47 | 0.051099 | 0.00014941
2009 | 2008-07-31 | C | 282 | 0.049465 | 0.00089648
2009 | 2008-08-01 | C | 12 | 0.047418 | 3.8148e-05
2009 | 2008-08-01 | C | 1192 | 0.045472 | 0.0037894
2009 | 2008-07-30 | C | 281 | 0.043794 | 0.0008933
2009 | 2008-07-30 | C | 904 | 0.043107 | 0.0028738
2009 | 2008-07-30 | C | 56 | 0.040767 | 0.00017802
2009 | 2008-07-30 | C | 1241 | 0.039451 | 0.0039451
2009 | 2008-07-31 | C | 95 | 0.035637 | 0.000302
2009 | 2008-07-30 | C | 443 | 0.033799 | 0.0014083
2009 | 2008-07-30 | C | 9 | 0.031873 | 2.8611e-05
2009 | 2008-07-30 | C | 291 | 0.030528 | 0.00092509
2009 | 2008-07-30 | C | 518 | 0.029641 | 0.0016467
2009 | 2008-08-03 | C | 310 | 0.029565 | 0.00098549
2009 | 2008-07-26 | C | 126 | 0.75845 | 0.00040055
2009 | 2008-08-03 | C | 38 | 0.028872 | 0.0001208
2009 | 2008-07-30 | C | 99 | 0.028325 | 0.00031472
2009 | 2008-08-01 | C | 45 | 0.023032 | 0.00014305
2009 | 2008-07-30 | C | 91 | 0.022898 | 0.00028929
2009 | 2008-07-31 | C | 87 | 0.022402 | 0.00027657
2009 | 2008-07-30 | C | 215 | 0.019138 | 0.00068348
2009 | 2008-07-31 | C | 50 | 0.01812 | 0.00015895
2009 | 2008-07-31 | C | 245 | 0.017135 | 0.00077885
2009 | 2008-07-30 | C | 69 | 0.016451 | 0.00021935
2009 | 2008-07-30 | C | 65 | 0.015911 | 0.00020663
2009 | 2008-07-30 | C | 48 | 0.014038 | 0.00015259
2009 | 2008-08-02 | C | 196 | 0.012646 | 0.00062308
2009 | 2008-08-03 | C | 100 | 0.012398 | 0.0003179
2009 | 2008-07-30 | C | 40 | 0.011317 | 0.00012716
2009 | 2008-07-30 | C | 72 | 0.010758 | 0.00022889
2009 | 2008-07-31 | C | 28 | 0.010503 | 8.9012e-05
2009 | 2008-08-02 | C | 272 | 0.010376 | 0.00086469
2009 | 2008-07-31 | C | 47 | 0.01016 | 0.00014941
2009 | 2008-07-26 | C | 331 | 0.16836 | 0.0010522
2009 | 2008-08-01 | C | 1 | 0.0099916 | 3.179e-06
2009 | 2008-07-30 | C | 92 | 0.0099439 | 0.00029247
2009 | 2008-07-31 | C | 141 | 0.009413 | 0.00044824
2009 | 2008-07-30 | C | 328 | 0.0093844 | 0.0010427
2009 | 2008-08-02 | C | 230 | 0.008774 | 0.00073117
2009 | 2008-07-31 | C | 89 | 0.0087708 | 0.00028293
2009 | 2008-07-30 | C | 16 | 0.00824 | 5.0864e-05
2009 | 2008-07-31 | C | 26 | 0.0079348 | 8.2654e-05
2009 | 2008-08-03 | C | 230 | 0.0073117 | 0.00073117
2009 | 2008-07-31 | C | 19 | 0.0073085 | 6.0401e-05
2009 | 2008-07-31 | C | 55 | 0.0069938 | 0.00017484
2009 | 2008-08-01 | C | 543 | 0.0069048 | 0.0017262
2009 | 2008-07-30 | C | 22 | 0.0058048 | 6.9938e-05
2009 | 2008-07-31 | C | 152 | 0.0057985 | 0.00048321
2009 | 2008-08-01 | C | 17 | 0.0056205 | 5.4043e-05
2009 | 2008-07-30 | C | 37 | 0.0054106 | 0.00011762
2009 | 2008-07-31 | C | 40 | 0.0052135 | 0.00012716
2009 | 2008-07-30 | C | 87 | 0.0044252 | 0.00027657
2009 | 2008-07-30 | C | 121 | 0.0042312 | 0.00038466
2009 | 2008-07-30 | C | 104 | 0.0039674 | 0.00033062
2009 | 2008-08-03 | C | 37 | 0.0037639 | 0.00011762
2009 | 2008-08-03 | C | 38 | 0.0037449 | 0.0001208
2009 | 2008-07-31 | C | 10 | 0.0033697 | 3.179e-05
2009 | 2008-08-03 | C | 16 | 0.0027975 | 5.0864e-05
2009 | 2008-07-30 | C | 29 | 0.0027657 | 9.2191e-05
2009 | 2008-08-03 | C | 8 | 0.0026195 | 2.5432e-05
2009 | 2008-07-26 | C | 466 | 1.7615 | 0.0014814
2009 | 2008-07-30 | C | 5 | 0.002575 | 1.5895e-05
2009 | 2008-07-31 | C | 30 | 0.002575 | 9.537e-05
2009 | 2008-08-01 | B | 1 | 0.0019837 | 3.179e-06
2009 | 2008-07-31 | C | 66 | 0.0018883 | 0.00020981
2009 | 2008-07-31 | C | 7 | 0.0012239 | 2.2253e-05
2009 | 2008-07-31 | C | 3 | 0.001173 | 9.537e-06
2009 | 2008-08-03 | C | 18 | 0.0010872 | 5.7222e-05
2009 | 2008-07-31 | C | 1 | 0.00065805 | 3.179e-06
2009 | 2008-07-31 | C | 1 | 0.00061355 | 3.179e-06
2009 | 2008-07-31 | C | 56 | 0.00053407 | 0.00017802
2009 | 2008-07-30 | C | 3 | 0.00050546 | 9.537e-06
2009 | 2008-07-31 | C | 3 | 0.00041009 | 9.537e-06
2009 | 2008-07-31 | C | 3 | 0.00029565 | 9.537e-06
2009 | 2008-08-03 | C | 1 | 0.00016531 | 3.179e-06
2009 | 2008-07-30 | C | 2 | 0.00013988 | 6.358e-06
2009 | 2008-08-02 | C | 1 | 0.00011762 | 3.179e-06
2009 | 2008-08-03 | C | 2 | 0.00011444 | 6.358e-06
2009 | 2008-07-23 | B | 26 | 0.029507 | 8.2654e-05
2009 | 2008-08-04 | C | 46 | 0.0035096 | 0.00014623
2009 | 2008-08-05 | C | 16 | 0.0016276 | 5.0864e-05
2009 | 2008-08-04 | C | 6 | 0.016327 | 1.9074e-05
2009 | 2008-08-05 | C | 26 | 0.0025623 | 8.2654e-05
2009 | 2008-08-05 | C | 4 | 0.0038784 | 1.2716e-05
2009 | 2008-08-05 | C | 346 | 0.013199 | 0.0010999
2009 | 2008-08-05 | C | 315 | 0.055076 | 0.0010014
2009 | 2008-08-05 | C | 4805 | 0.50408 | 0.015275
2009 | 2008-08-05 | B | 132 | 0.09022 | 0.00041963
2009 | 2008-08-05 | B | 34 | 0.034912 | 0.00010809
2009 | 2008-08-05 | B | 22 | 0.027066 | 6.9938e-05
2009 | 2008-08-05 | C | 266 | 0.020295 | 0.00084561
2009 | 2008-08-05 | C | 144 | 0.021058 | 0.00045778
2009 | 2008-08-04 | C | 1 | 0.003233 | 3.179e-06
2009 | 2008-08-05 | C | 50 | 0.009537 | 0.00015895
2009 | 2008-08-05 | C | 3 | 0.001297 | 9.537e-06
2009 | 2008-08-05 | C | 31 | 0.0071941 | 9.8549e-05
2009 | 2008-08-05 | C | 315 | 0.072322 | 0.0010014
2009 | 2008-08-05 | C | 673 | 0.22183 | 0.0021395
2009 | 2008-08-05 | C | 235 | 0.041553 | 0.00074706
2009 | 2008-08-05 | C | 131 | 0.038199 | 0.00041645
2009 | 2008-08-06 | B | 1 | 0.00089966 | 3.179e-06
2009 | 2008-07-27 | C | 2181 | 4.2224 | 0.0069334
2009 | 2008-08-06 | B | 11 | 0.01133 | 3.4969e-05
2009 | 2008-08-06 | C | 64 | 0.004476 | 0.00020346
2009 | 2008-08-06 | C | 435 | 0.549 | 0.0013829
2009 | 2008-08-05 | C | 458 | 0.056351 | 0.001456
2009 | 2008-08-05 | C | 1090 | 0.25988 | 0.0034651
2009 | 2008-08-07 | B | 34 | 0.036533 | 0.00010809
2009 | 2008-08-07 | C | 365 | 0.19633 | 0.0011603
2009 | 2008-08-07 | C | 156 | 0.013886 | 0.00049592
2009 | 2008-08-07 | C | 89 | 0.0022634 | 0.00028293
2009 | 2008-08-07 | C | 8 | 0.0018565 | 2.5432e-05
2009 | 2008-08-07 | C | 3 | 0.00031472 | 9.537e-06
2009 | 2008-08-07 | C | 170 | 0.090792 | 0.00054043
2009 | 2008-08-07 | C | 59 | 0.0088153 | 0.00018756
2009 | 2008-08-08 | C | 54 | 0.011502 | 0.00017167
2009 | 2008-08-07 | C | 69 | 0.024348 | 0.00021935
2009 | 2008-08-07 | C | 289 | 0.086361 | 0.00091873
2009 | 2008-08-08 | C | 118 | 0.01538 | 0.00037512
2009 | 2008-08-08 | C | 125 | 0.10432 | 0.00039737
2009 | 2008-08-08 | B | 6 | 0.0029374 | 1.9074e-05
2009 | 2008-08-08 | B | 2 | 0.00066123 | 6.358e-06
2009 | 2008-08-08 | B | 4 | 0.0032426 | 1.2716e-05
2009 | 2008-08-08 | C | 5 | 0.00069938 | 1.5895e-05
2009 | 2008-08-09 | C | 272 | 0.074191 | 0.00086469
2009 | 2008-08-09 | B | 3 | 0.0020695 | 9.537e-06
2009 | 2008-08-09 | C | 7 | 0.001669 | 2.2253e-05
2009 | 2008-08-09 | C | 8 | 0.0032553 | 2.5432e-05
2009 | 2008-08-09 | B | 1 | 0.0010872 | 3.179e-06
2009 | 2008-08-09 | B | 1 | 0.0015672 | 3.179e-06
2009 | 2008-08-09 | C | 594 | 0.11708 | 0.0018883
2009 | 2008-08-10 | B | 46 | 0.02252 | 0.00014623
2009 | 2008-08-10 | C | 19 | 0.003322 | 6.0401e-05
2009 | 2008-08-11 | C | 3 | 0.00049592 | 9.537e-06
2009 | 2008-08-11 | C | 32 | 0.0039674 | 0.00010173
2009 | 2008-08-11 | C | 16 | 0.0025432 | 5.0864e-05
2009 | 2008-08-11 | C | 154 | 0.15225 | 0.00048956
2009 | 2008-08-11 | C | 132 | 0.014687 | 0.00041963
2009 | 2008-10-09 | C | 106 | 0.082069 | 0.00033697
2009 | 2008-08-12 | C | 460 | 0.063707 | 0.0014623
2009 | 2008-08-12 | C | 17 | 0.0046477 | 5.4043e-05
2009 | 2008-08-12 | C | 864 | 0.25963 | 0.0027467
2009 | 2008-08-12 | B | 340 | 0.16969 | 0.0010809
2009 | 2008-04-22 | C | 508 | 0.014534 | 0.0016149
2009 | 2008-08-12 | B | 30 | 0.017453 | 9.537e-05
2009 | 2008-08-12 | C | 41 | 0.037016 | 0.00013034
2009 | 2008-08-12 | B | 55 | 0.064168 | 0.00017484
2009 | 2008-08-12 | C | 27 | 0.001545 | 8.5833e-05
2009 | 2008-08-13 | C | 32 | 0.029196 | 0.00010173
2009 | 2008-08-13 | B | 45 | 0.0030041 | 0.00014305
2009 | 2008-08-13 | B | 52 | 0.01901 | 0.00016531
2009 | 2008-08-13 | B | 32 | 0.041505 | 0.00010173
2009 | 2008-08-13 | B | 25 | 0.030121 | 7.9475e-05
2009 | 2008-08-13 | B | 54 | 0.07313 | 0.00017167
2009 | 2008-08-13 | C | 30 | 0.0032426 | 9.537e-05
2009 | 2008-08-13 | B | 1 | 0.00096641 | 3.179e-06
2009 | 2008-08-13 | C | 1467 | 0.13668 | 0.0046636
2009 | 2008-08-13 | C | 10 | 0.00089012 | 3.179e-05
2009 | 2008-08-13 | C | 2 | 0.00026068 | 6.358e-06
2009 | 2008-08-14 | B | 25 | 0.01057 | 7.9475e-05
2009 | 2008-08-14 | B | 60 | 0.063135 | 0.00019074
2009 | 2008-08-14 | C | 46 | 0.011406 | 0.00014623
2009 | 2008-08-14 | B | 161 | 0.19756 | 0.00051182
2009 | 2008-08-14 | C | 314 | 0.048413 | 0.0009982
2009 | 2008-08-14 | B | 32 | 0.046591 | 0.00010173
2009 | 2008-08-14 | C | 2 | 0.00040055 | 6.358e-06
2009 | 2008-08-14 | C | 206 | 0.088001 | 0.00065487
2009 | 2008-08-15 | C | 3973 | 0.088411 | 0.01263
2009 | 2008-08-15 | C | 206 | 0.0045841 | 0.00065487
2009 | 2008-08-15 | B | 1 | 0.00021935 | 3.179e-06
2009 | 2008-08-15 | C | 139 | 0.020326 | 0.00044188
2009 | 2008-08-15 | C | 768 | 0.15137 | 0.0024415
2009 | 2008-08-16 | C | 58 | 0.0036876 | 0.00018438
2009 | 2008-04-22 | C | 10 | 0.0022889 | 3.179e-05
2009 | 2008-08-16 | C | 35 | 0.00077885 | 0.00011126
2009 | 2008-07-15 | C | 100 | 0.0038148 | 0.0003179
2009 | 2008-08-16 | C | 22 | 0.0041263 | 6.9938e-05
2009 | 2008-08-16 | C | 134 | 0.057508 | 0.00042599
2009 | 2008-08-16 | C | 52 | 0.0011572 | 0.00016531
2009 | 2008-08-17 | C | 386 | 0.24531 | 0.0012271
2009 | 2008-08-15 | C | 36 | 0.0052644 | 0.00011444
2009 | 2008-08-15 | B | 4 | 0.00083925 | 1.2716e-05
2009 | 2008-08-17 | C | 210 | 0.0086787 | 0.00066759
2009 | 2008-08-17 | B | 45 | 0.042773 | 0.00014305
2009 | 2008-08-17 | B | 1 | 0.0017421 | 3.179e-06
2009 | 2008-08-16 | C | 693 | 0.14801 | 0.002203
2009 | 2008-08-17 | C | 37 | 0.0051849 | 0.00011762
2009 | 2008-08-17 | C | 142 | 0.028023 | 0.00045142
2009 | 2008-08-18 | B | 44 | 0.0060147 | 0.00013988
2009 | 2008-08-18 | B | 6 | 0.002327 | 1.9074e-05
2009 | 2008-08-18 | B | 1 | 0.00047049 | 3.179e-06
2009 | 2008-08-18 | B | 44 | 0.0060147 | 0.00013988
2009 | 2008-08-18 | B | 34 | 0.022158 | 0.00010809
2009 | 2008-08-18 | B | 19 | 0.02114 | 6.0401e-05
2009 | 2008-08-18 | C | 30 | 0.0052453 | 9.537e-05
2009 | 2008-08-18 | B | 6 | 0.0059892 | 1.9074e-05
2009 | 2008-08-18 | C | 125 | 0.083957 | 0.00039737
2009 | 2008-08-18 | C | 125 | 0.0027816 | 0.00039737
2009 | 2008-08-18 | C | 125 | 0.0027816 | 0.00039737
2009 | 2008-08-19 | B | 5 | 0.00090601 | 1.5895e-05
2009 | 2008-08-19 | C | 59 | 0.018944 | 0.00018756
2009 | 2008-08-19 | B | 3 | 0.0017643 | 9.537e-06
2009 | 2008-08-19 | B | 9 | 0.0065805 | 2.8611e-05
2009 | 2008-08-19 | B | 161 | 0.15713 | 0.00051182
2009 | 2008-08-19 | C | 52 | 0.0033062 | 0.00016531
2009 | 2008-08-19 | B | 32 | 0.039572 | 0.00010173
2009 | 2008-08-20 | C | 28 | 0.0052517 | 8.9012e-05
2009 | 2008-08-20 | B | 28 | 0.012106 | 8.9012e-05
2009 | 2008-08-20 | B | 10 | 0.011349 | 3.179e-05
2009 | 2008-08-20 | B | 1 | 0.0011349 | 3.179e-06
2009 | 2008-08-20 | B | 114 | 0.13844 | 0.00036241
2009 | 2008-08-20 | B | 32 | 0.027772 | 0.00010173
2009 | 2008-08-20 | C | 114 | 0.027358 | 0.00036241
2009 | 2008-08-20 | C | 73 | 0.060569 | 0.00023207
2009 | 2008-08-20 | C | 88 | 0.026576 | 0.00027975
2009 | 2008-08-20 | C | 21 | 0.0028039 | 6.6759e-05
2009 | 2008-08-21 | C | 5356 | 1.277 | 0.017027
2009 | 2008-08-21 | B | 5 | 0.0048003 | 1.5895e-05
2009 | 2008-08-21 | B | 9 | 0.0057508 | 2.8611e-05
2009 | 2008-08-20 | B | 26 | 0.0020663 | 8.2654e-05
2009 | 2008-08-21 | B | 4 | 0.0070828 | 1.2716e-05
2009 | 2008-08-21 | C | 376 | 0.048826 | 0.0011953
2009 | 2008-08-21 | C | 49 | 0.047354 | 0.00015577
2009 | 2008-08-22 | C | 196 | 0.42743 | 0.00062308
2009 | 2008-08-22 | B | 16 | 0.0036622 | 5.0864e-05
2009 | 2008-08-22 | B | 1 | 0.00089012 | 3.179e-06
2009 | 2008-08-22 | B | 85 | 0.024049 | 0.00027021
2009 | 2008-08-22 | B | 28 | 0.027683 | 8.9012e-05
2009 | 2008-08-22 | C | 38 | 0.0021744 | 0.0001208
2009 | 2008-08-22 | C | 84 | 0.010147 | 0.00026704
2009 | 2008-08-22 | C | 14 | 0.0029374 | 4.4506e-05
2009 | 2008-08-22 | C | 84 | 0.023385 | 0.00026704
2009 | 2008-08-22 | C | 23 | 0.0038021 | 7.3117e-05
2009 | 2008-08-23 | C | 1155 | 0.2348 | 0.0036717
2009 | 2008-08-23 | C | 18 | 0.0029755 | 5.7222e-05
2009 | 2008-08-22 | C | 895 | 0.24598 | 0.0028452
2009 | 2008-08-23 | C | 145 | 0.068695 | 0.00046095
2009 | 2008-08-24 | C | 357 | 0.048801 | 0.0011349
2009 | 2008-08-24 | C | 644 | 0.29892 | 0.0020473
2009 | 2008-08-23 | C | 3 | 0.0066187 | 9.537e-06
2009 | 2008-08-24 | C | 185 | 0.021172 | 0.00058811
2009 | 2008-08-24 | C | 8 | 0.00061037 | 2.5432e-05
2009 | 2008-07-16 | C | 1 | 0.0011413 | 3.179e-06
2009 | 2008-06-29 | C | 74 | 0.017879 | 0.00023525
2009 | 2008-08-22 | B | 47 | 0.041387 | 0.00014941
2009 | 2008-08-22 | B | 48 | 0.018311 | 0.00015259
2009 | 2008-08-25 | C | 15 | 0.0015736 | 4.7685e-05
2009 | 2008-08-25 | C | 85 | 0.013511 | 0.00027021
2009 | 2008-08-12 | B | 25 | 0.0023842 | 7.9475e-05
2009 | 2008-08-25 | B | 186 | 0.066225 | 0.00059129
2009 | 2008-08-25 | C | 6 | 0.00022889 | 1.9074e-05
2009 | 2008-08-25 | B | 70 | 0.084116 | 0.00022253
2009 | 2008-08-22 | B | 1 | 0.0010332 | 3.179e-06
2009 | 2008-08-25 | B | 2 | 0.0020155 | 6.358e-06
2009 | 2008-08-25 | C | 3 | 0.0055219 | 9.537e-06
2009 | 2008-08-25 | C | 103 | 0.017421 | 0.00032744
2009 | 2008-08-26 | C | 1 | 0.00026704 | 3.179e-06
2009 | 2008-08-26 | B | 87 | 0.033742 | 0.00027657
2009 | 2008-08-26 | B | 22 | 0.014337 | 6.9938e-05
2009 | 2008-08-26 | B | 6 | 0.0046922 | 1.9074e-05
2009 | 2008-08-26 | B | 9 | 0.0033475 | 2.8611e-05
2009 | 2008-08-26 | C | 101 | 0.035929 | 0.00032108
2009 | 2008-08-26 | B | 84 | 0.14126 | 0.00026704
2009 | 2008-08-26 | C | 414 | 0.088281 | 0.0013161
2009 | 2008-08-26 | C | 11 | 0.00097913 | 3.4969e-05
2009 | 2008-08-26 | C | 25 | 0.0022253 | 7.9475e-05
2009 | 2008-08-25 | C | 286 | 0.10295 | 0.00090919
2009 | 2008-08-26 | C | 7 | 0.012106 | 2.2253e-05
2009 | 2008-08-27 | C | 204 | 0.054475 | 0.00064851
2009 | 2008-08-27 | B | 2 | 0.0012398 | 6.358e-06
2009 | 2008-08-27 | B | 15 | 0.010348 | 4.7685e-05
2009 | 2008-08-27 | C | 147 | 0.16169 | 0.00046731
2009 | 2008-08-27 | B | 12 | 0.0077822 | 3.8148e-05
2009 | 2008-08-27 | B | 46 | 0.053522 | 0.00014623
2009 | 2008-08-27 | B | 9 | 0.0031186 | 2.8611e-05
2009 | 2008-08-27 | B | 41 | 0.038711 | 0.00013034
2009 | 2008-08-27 | C | 1 | 0.00048956 | 3.179e-06
2009 | 2008-08-27 | B | 135 | 0.16609 | 0.00042916
2009 | 2008-08-27 | C | 76 | 0.0084561 | 0.0002416
2009 | 2008-08-27 | B | 68 | 0.10376 | 0.00021617
2009 | 2008-08-27 | B | 38 | 0.058106 | 0.0001208
2009 | 2008-08-27 | C | 131 | 0.058277 | 0.00041645
2009 | 2008-08-27 | C | 282 | 0.075304 | 0.00089648
2009 | 2008-08-28 | B | 5 | 0.0014941 | 1.5895e-05
2009 | 2008-08-28 | B | 69 | 0.055496 | 0.00021935
2009 | 2008-08-28 | B | 20 | 0.0062944 | 6.358e-05
2009 | 2008-08-28 | B | 73 | 0.04711 | 0.00023207
2009 | 2008-08-28 | B | 47 | 0.0064247 | 0.00014941
2009 | 2008-08-28 | B | 68 | 0.073931 | 0.00021617
2009 | 2008-08-28 | B | 85 | 0.086198 | 0.00027021
2009 | 2008-08-28 | C | 74 | 0.0089393 | 0.00023525
2009 | 2008-08-28 | C | 744 | 0.20691 | 0.0023652
2009 | 2008-08-28 | C | 271 | 0.01098 | 0.00086151
2009 | 2008-08-28 | B | 45 | 0.10157 | 0.00014305
2009 | 2008-08-29 | C | 2420 | 0.33081 | 0.0076932
2009 | 2008-08-29 | B | 298 | 0.2662 | 0.00094734
2009 | 2008-08-29 | B | 18 | 0.0037194 | 5.7222e-05
2009 | 2008-08-29 | C | 3 | 0.00020981 | 9.537e-06
2009 | 2008-08-29 | B | 38 | 0.011597 | 0.0001208
2009 | 2008-08-29 | B | 4 | 0.0024288 | 1.2716e-05
2009 | 2008-08-29 | C | 1253 | 0.55262 | 0.0039833
2009 | 2008-08-30 | C | 1026 | 0.26883 | 0.0032616
2009 | 2008-08-29 | B | 18 | 0.013047 | 5.7222e-05
2009 | 2008-08-29 | B | 8 | 0.00091555 | 2.5432e-05
2009 | 2008-08-30 | B | 54 | 0.024033 | 0.00017167
2009 | 2008-08-30 | C | 637 | 0.0243 | 0.002025
2009 | 2008-08-30 | B | 7 | 0.010392 | 2.2253e-05
2009 | 2008-08-30 | C | 51 | 0.0066473 | 0.00016213
2009 | 2008-08-31 | C | 58 | 0.0042408 | 0.00018438
2009 | 2008-08-31 | C | 34 | 0.043667 | 0.00010809
2009 | 2008-09-01 | B | 1 | 0.00032744 | 3.179e-06
2009 | 2008-09-01 | C | 346 | 0.036082 | 0.0010999
2009 | 2008-09-01 | B | 57 | 0.03008 | 0.0001812
2009 | 2008-09-01 | B | 4 | 0.0033952 | 1.2716e-05
2009 | 2008-09-01 | C | 17 | 0.0017834 | 5.4043e-05
2009 | 2008-09-01 | B | 44 | 0.039305 | 0.00013988
2009 | 2008-09-01 | C | 32 | 0.0010173 | 0.00010173
2009 | 2008-09-01 | C | 26 | 0.0032235 | 8.2654e-05
2009 | 2008-09-01 | C | 881 | 0.19318 | 0.0028007
2009 | 2008-09-02 | C | 2278 | 1.6566 | 0.0072417
2009 | 2008-09-02 | B | 100 | 0.065805 | 0.0003179
2009 | 2008-09-02 | C | 136 | 0.031059 | 0.00043234
2009 | 2008-09-02 | B | 74 | 0.061634 | 0.00023525
2009 | 2008-09-02 | B | 32 | 0.022278 | 0.00010173
2009 | 2008-09-02 | B | 82 | 0.085242 | 0.00026068
2009 | 2008-09-02 | C | 208 | 0.031739 | 0.00066123
2009 | 2008-09-02 | B | 23 | 0.023544 | 7.3117e-05
2009 | 2008-09-02 | B | 1 | 0.0011349 | 3.179e-06
2009 | 2008-09-02 | B | 99 | 0.029898 | 0.00031472
2009 | 2008-09-02 | C | 90 | 0.068666 | 0.00028611
2009 | 2008-09-01 | B | 47 | 0.0046318 | 0.00014941
2009 | 2008-09-03 | B | 3 | 0.0014019 | 9.537e-06
2009 | 2008-09-03 | B | 135 | 0.12746 | 0.00042916
2009 | 2008-09-03 | B | 71 | 0.073807 | 0.00022571
2009 | 2008-09-03 | B | 9 | 0.0084974 | 2.8611e-05
2009 | 2008-09-03 | B | 6 | 0.0071527 | 1.9074e-05
2009 | 2008-09-03 | B | 264 | 0.29379 | 0.00083925
2009 | 2008-09-03 | B | 98 | 0.03645 | 0.00031154
2009 | 2008-09-03 | C | 366 | 0.078899 | 0.0011635
2009 | 2008-09-03 | C | 341 | 0.1157 | 0.001084
2009 | 2008-09-02 | B | 13 | 0.011943 | 4.1327e-05
2009 | 2008-09-04 | C | 22 | 0.0037067 | 6.9938e-05
2009 | 2008-09-04 | B | 85 | 0.053232 | 0.00027021
2009 | 2008-09-04 | B | 30 | 0.023461 | 9.537e-05
2009 | 2008-09-04 | C | 5 | 0.0018915 | 1.5895e-05
2009 | 2008-09-04 | B | 16 | 0.017039 | 5.0864e-05
2009 | 2008-09-04 | C | 921 | 0.28295 | 0.0029279
2009 | 2008-09-04 | C | 152 | 0.023477 | 0.00048321
2009 | 2008-09-04 | B | 42 | 0.031377 | 0.00013352
2009 | 2008-09-04 | B | 129 | 0.050851 | 0.00041009
2009 | 2008-09-05 | B | 8 | 0.0056205 | 2.5432e-05
2009 | 2008-09-05 | B | 26 | 0.02149 | 8.2654e-05
2009 | 2008-09-05 | C | 417 | 0.053026 | 0.0013256
2009 | 2008-09-05 | C | 388 | 0.077621 | 0.0012334
2009 | 2008-09-05 | C | 36 | 0.10094 | 0.00011444
2009 | 2008-09-05 | C | 14 | 0.053318 | 4.4506e-05
2009 | 2008-09-06 | B | 1 | 0.00053407 | 3.179e-06
2009 | 2008-09-06 | C | 368 | 0.5709 | 0.0011699
2009 | 2008-09-06 | C | 1068 | 0.17655 | 0.0033952
2009 | 2008-09-06 | C | 25 | 0.073403 | 7.9475e-05
2009 | 2008-09-07 | C | 8 | 0.0047812 | 2.5432e-05
2009 | 2008-09-05 | B | 58 | 0.0027657 | 0.00018438
2009 | 2008-09-07 | C | 521 | 0.049688 | 0.0016563
2009 | 2008-09-08 | C | 278 | 0.02121 | 0.00088376
2009 | 2008-09-08 | C | 1227 | 0.3165 | 0.0039006
2009 | 2008-09-08 | C | 389 | 0.13612 | 0.0012366
2009 | 2008-09-08 | C | 583 | 0.066721 | 0.0018534
2009 | 2008-09-08 | C | 41 | 0.020333 | 0.00013034
2009 | 2008-09-09 | C | 87 | 0.016594 | 0.00027657
2009 | 2008-09-09 | B | 14 | 0.0043171 | 4.4506e-05
2009 | 2008-09-09 | C | 32 | 0.014038 | 0.00010173
2009 | 2008-09-09 | B | 10 | 0.0028611 | 3.179e-05
2009 | 2008-09-09 | B | 34 | 0.041181 | 0.00010809
2009 | 2008-09-09 | B | 24 | 0.014038 | 7.6296e-05
2009 | 2008-09-09 | B | 11 | 0.0014337 | 3.4969e-05
2009 | 2008-09-09 | C | 344 | 0.078658 | 0.0010936
2009 | 2008-09-09 | C | 2 | 0.003427 | 6.358e-06
2009 | 2008-09-09 | B | 1 | 0.00020346 | 3.179e-06
2009 | 2008-09-10 | B | 4 | 0.0022507 | 1.2716e-05
2009 | 2008-09-10 | C | 206 | 0.048461 | 0.00065487
2009 | 2008-09-10 | C | 308 | 0.038186 | 0.00097913
2009 | 2008-09-10 | B | 28 | 0.029107 | 8.9012e-05
2009 | 2008-09-10 | B | 15 | 0.019885 | 4.7685e-05
2009 | 2008-09-10 | C | 1228 | 0.12492 | 0.0039038
2009 | 2008-06-30 | C | 74 | 0.070809 | 0.00023525
2009 | 2008-09-09 | C | 14 | 0.0054297 | 4.4506e-05
2009 | 2008-09-09 | C | 71 | 0.006997 | 0.00022571
2009 | 2008-09-09 | C | 77 | 0.014503 | 0.00024478
2009 | 2008-09-10 | C | 64 | 0.025432 | 0.00020346
2009 | 2008-09-11 | C | 24 | 0.0038148 | 7.6296e-05
2009 | 2008-09-11 | C | 24 | 0.0025178 | 7.6296e-05
2009 | 2008-09-11 | C | 14 | 0.0011572 | 4.4506e-05
2009 | 2008-10-18 | C | 17 | 0.0070256 | 5.4043e-05
2009 | 2008-09-11 | B | 1 | 0.00058811 | 3.179e-06
2009 | 2008-09-11 | C | 1 | 0.00027021 | 3.179e-06
2009 | 2008-09-11 | B | 7 | 0.0052739 | 2.2253e-05
2009 | 2008-09-12 | B | 1 | 0.00055632 | 3.179e-06
2009 | 2008-09-12 | B | 50 | 0.03322 | 0.00015895
2009 | 2008-09-12 | B | 24 | 0.021058 | 7.6296e-05
2009 | 2008-09-12 | B | 34 | 0.036749 | 0.00010809
2009 | 2008-09-12 | C | 141 | 0.10265 | 0.00044824
2009 | 2008-09-14 | C | 134 | 0.030245 | 0.00042599
2009 | 2008-09-14 | C | 330 | 0.052937 | 0.0010491
2009 | 2008-09-15 | C | 14 | 0.0040945 | 4.4506e-05
2009 | 2008-09-15 | B | 24 | 0.0041963 | 7.6296e-05
2009 | 2008-09-15 | B | 22 | 0.010211 | 6.9938e-05
2009 | 2008-09-15 | C | 80 | 0.0066123 | 0.00025432
2009 | 2008-09-15 | B | 3 | 0.0024033 | 9.537e-06
2009 | 2008-09-15 | C | 2 | 0.00049592 | 6.358e-06
2009 | 2008-09-15 | B | 21 | 0.017891 | 6.6759e-05
2009 | 2008-09-16 | B | 48 | 0.0086977 | 0.00015259
2009 | 2008-09-16 | B | 240 | 0.056459 | 0.00076296
2009 | 2008-09-16 | B | 87 | 0.091545 | 0.00027657
2009 | 2008-09-16 | B | 8 | 0.0060782 | 2.5432e-05
2009 | 2008-09-16 | B | 25 | 0.02273 | 7.9475e-05
2009 | 2008-09-16 | B | 1 | 0.00076296 | 3.179e-06
2009 | 2008-09-16 | B | 20 | 0.015005 | 6.358e-05
2009 | 2008-09-16 | B | 2 | 0.00094734 | 6.358e-06
2009 | 2008-09-16 | B | 37 | 0.034934 | 0.00011762
2009 | 2008-09-16 | C | 1 | 0.0020886 | 3.179e-06
2009 | 2008-09-16 | C | 2 | 0.00050864 | 6.358e-06
2009 | 2008-09-17 | B | 85 | 0.017024 | 0.00027021
2009 | 2008-09-17 | B | 85 | 0.020266 | 0.00027021
2009 | 2008-09-17 | C | 103 | 0.02423 | 0.00032744
2009 | 2008-09-17 | C | 49 | 0.0026481 | 0.00015577
2009 | 2008-09-17 | B | 3 | 0.00089648 | 9.537e-06
2009 | 2008-09-17 | C | 32 | 0.015463 | 0.00010173
2009 | 2008-09-17 | C | 9 | 0.00068666 | 2.8611e-05
2009 | 2008-09-17 | C | 647 | 0.20177 | 0.0020568
2009 | 2008-09-17 | B | 9 | 0.0060083 | 2.8611e-05
2009 | 2008-09-18 | C | 91 | 0.11224 | 0.00028929
2009 | 2008-09-18 | B | 9 | 0.0076105 | 2.8611e-05
2009 | 2008-09-18 | B | 33 | 0.04511 | 0.00010491
2009 | 2008-09-18 | B | 1 | 0.00040373 | 3.179e-06
2009 | 2008-09-18 | B | 60 | 0.045778 | 0.00019074
2009 | 2008-09-19 | C | 44 | 0.035668 | 0.00013988
2009 | 2008-09-19 | C | 32 | 0.011597 | 0.00010173
2009 | 2008-09-19 | B | 14 | 0.015889 | 4.4506e-05
2009 | 2008-09-19 | B | 11 | 0.010386 | 3.4969e-05
2009 | 2008-09-18 | B | 34 | 0.038587 | 0.00010809
2009 | 2008-09-19 | C | 26 | 0.021325 | 8.2654e-05
2009 | 2008-09-20 | C | 361 | 0.0045905 | 0.0011476
2009 | 2008-09-20 | C | 3 | 0.0015068 | 9.537e-06
2009 | 2008-09-20 | B | 32 | 0.039877 | 0.00010173
2009 | 2008-09-20 | B | 74 | 0.048696 | 0.00023525
2009 | 2008-09-20 | C | 149 | 0.052104 | 0.00047367
2009 | 2008-09-20 | C | 102 | 0.026265 | 0.00032426
2009 | 2008-10-19 | C | 17 | 0.006323 | 5.4043e-05
2009 | 2008-09-21 | C | 86 | 0.017866 | 0.00027339
2009 | 2008-09-22 | C | 136 | 0.07004 | 0.00043234
2009 | 2008-10-07 | C | 360 | 0.057266 | 0.0011444
2009 | 2008-09-22 | B | 172 | 0.14162 | 0.00054679
2009 | 2008-09-22 | B | 30 | 0.01688 | 9.537e-05
2009 | 2008-09-22 | B | 6 | 0.00047685 | 1.9074e-05
2009 | 2008-09-22 | C | 546 | 0.03645 | 0.0017357
2009 | 2008-09-22 | B | 26 | 0.025953 | 8.2654e-05
2009 | 2008-09-22 | C | 435 | 0.049278 | 0.0013829
2009 | 2008-09-23 | C | 215 | 0.13397 | 0.00068348
2009 | 2008-09-23 | B | 12 | 0.0022126 | 3.8148e-05
2009 | 2008-09-23 | B | 13 | 0.014382 | 4.1327e-05
2009 | 2008-09-23 | B | 19 | 0.016731 | 6.0401e-05
2009 | 2008-09-23 | B | 17 | 0.012268 | 5.4043e-05
2009 | 2008-09-23 | B | 17 | 0.010755 | 5.4043e-05
2009 | 2008-09-23 | B | 33 | 0.034619 | 0.00010491
2009 | 2008-09-23 | C | 23 | 0.0013161 | 7.3117e-05
2009 | 2008-09-23 | C | 5 | 0.002114 | 1.5895e-05
2009 | 2008-09-23 | C | 458 | 0.02912 | 0.001456
2009 | 2008-09-23 | C | 50 | 0.01065 | 0.00015895
2009 | 2008-09-23 | C | 91 | 0.22275 | 0.00028929
2009 | 2008-09-23 | C | 25 | 0.0014305 | 7.9475e-05
2009 | 2008-09-24 | C | 167 | 0.23837 | 0.00053089
2009 | 2008-09-24 | C | 38 | 0.015583 | 0.0001208
2009 | 2008-09-24 | B | 53 | 0.035045 | 0.00016849
2009 | 2008-09-24 | C | 21 | 0.0026036 | 6.6759e-05
2009 | 2008-09-24 | B | 8 | 0.0032299 | 2.5432e-05
2009 | 2008-09-24 | B | 7 | 0.0082558 | 2.2253e-05
2009 | 2008-09-24 | B | 34 | 0.033723 | 0.00010809
2009 | 2008-09-24 | C | 44 | 0.047278 | 0.00013988
2009 | 2008-09-24 | B | 6 | 0.005169 | 1.9074e-05
2009 | 2008-09-24 | B | 1 | 0.00089966 | 3.179e-06
2009 | 2008-09-24 | C | 3 | 0.002184 | 9.537e-06
2009 | 2008-09-24 | C | 329 | 0.0073212 | 0.0010459
2009 | 2008-09-24 | B | 20 | 0.02238 | 6.358e-05
2009 | 2008-09-24 | C | 6 | 0.0136 | 1.9074e-05
2009 | 2008-09-25 | B | 82 | 0.023461 | 0.00026068
2009 | 2008-09-25 | B | 33 | 0.027486 | 0.00010491
2009 | 2008-09-25 | B | 29 | 0.019268 | 9.2191e-05
2009 | 2008-09-25 | B | 97 | 0.036078 | 0.00030836
2009 | 2008-09-26 | C | 563 | 0.059686 | 0.0017898
2009 | 2008-09-26 | C | 697 | 0.15732 | 0.0022158
2009 | 2008-09-26 | B | 8 | 0.0023143 | 2.5432e-05
2009 | 2008-09-26 | B | 74 | 0.044226 | 0.00023525
2009 | 2008-09-26 | B | 17 | 0.0095656 | 5.4043e-05
2009 | 2008-09-26 | B | 22 | 0.021121 | 6.9938e-05
2009 | 2008-09-26 | B | 22 | 0.024968 | 6.9938e-05
2009 | 2008-09-26 | B | 256 | 0.071616 | 0.00081382
2009 | 2008-09-26 | C | 21 | 0.0075438 | 6.6759e-05
2009 | 2008-09-27 | C | 6 | 0.00080111 | 1.9074e-05
2009 | 2008-09-27 | C | 268 | 0.17689 | 0.00085197
2009 | 2008-09-27 | C | 40 | 0.0044506 | 0.00012716
2009 | 2008-09-27 | C | 51 | 0.024968 | 0.00016213
2009 | 2008-09-27 | C | 94 | 0.074706 | 0.00029883
2009 | 2008-09-27 | C | 354 | 0.42409 | 0.0011254
2009 | 2008-09-27 | C | 365 | 0.10477 | 0.0011603
2009 | 2008-09-27 | C | 40 | 0.0057222 | 0.00012716
2009 | 2008-10-08 | C | 36 | 0.0067522 | 0.00011444
2009 | 2008-09-28 | B | 26 | 0.0054552 | 8.2654e-05
2009 | 2008-09-27 | C | 30 | 0.011546 | 9.537e-05
2009 | 2008-09-28 | C | 7032 | 1.699 | 0.022355
2009 | 2008-09-28 | C | 2668 | 0.6446 | 0.0084816
2009 | 2008-09-28 | C | 1237 | 0.29886 | 0.0039324
2009 | 2008-09-28 | C | 206 | 0.015825 | 0.00065487
2009 | 2008-09-28 | B | 5733 | 9.4953 | 0.018225
2009 | 2008-09-28 | B | 58 | 0.094588 | 0.00018438
2009 | 2008-09-29 | B | 3 | 0.0031854 | 9.537e-06
2009 | 2008-09-29 | B | 22 | 0.013638 | 6.9938e-05
2009 | 2008-09-29 | C | 132 | 0.039865 | 0.00041963
2009 | 2008-07-20 | C | 1109 | 0.024679 | 0.0035255
2009 | 2008-07-20 | C | 28 | 0.0092572 | 8.9012e-05
2009 | 2008-09-30 | B | 18 | 0.019284 | 5.7222e-05
2009 | 2008-09-30 | C | 2 | 0.00061672 | 6.358e-06
2009 | 2008-09-30 | B | 349 | 0.42936 | 0.0011095
2009 | 2008-09-30 | B | 10 | 0.010205 | 3.179e-05
2009 | 2008-09-30 | C | 40 | 0.015281 | 0.00012716
2009 | 2008-09-30 | C | 37 | 0.013584 | 0.00011762
2009 | 2008-09-30 | B | 45 | 0.039626 | 0.00014305
2009 | 2008-10-01 | C | 3 | 0.0015927 | 9.537e-06
2009 | 2008-10-01 | C | 17 | 0.002486 | 5.4043e-05
2009 | 2008-10-01 | B | 47 | 0.064546 | 0.00014941
2009 | 2008-10-01 | B | 33 | 0.038606 | 0.00010491
2009 | 2008-10-01 | B | 42 | 0.04099 | 0.00013352
2009 | 2008-10-01 | B | 2 | 0.0020155 | 6.358e-06
2009 | 2008-10-01 | B | 54 | 0.0053216 | 0.00017167
2009 | 2008-10-01 | C | 133 | 0.012261 | 0.00042281
2009 | 2008-10-01 | C | 600 | 0.055082 | 0.0019074
2009 | 2008-10-01 | C | 44 | 0.014515 | 0.00013988
2009 | 2008-10-02 | B | 65 | 0.018804 | 0.00020663
2009 | 2008-10-02 | B | 2 | 0.0018502 | 6.358e-06
2009 | 2008-10-02 | B | 130 | 0.12687 | 0.00041327
2009 | 2008-10-02 | B | 34 | 0.039992 | 0.00010809
2009 | 2008-10-02 | B | 86 | 0.063974 | 0.00027339
2009 | 2008-10-02 | B | 1 | 0.00073753 | 3.179e-06
2009 | 2008-10-03 | C | 146 | 0.044032 | 0.00046413
2009 | 2008-10-03 | B | 35 | 0.018915 | 0.00011126
2009 | 2008-10-03 | B | 2 | 0.00054043 | 6.358e-06
2009 | 2008-10-03 | B | 37 | 0.025413 | 0.00011762
2009 | 2008-10-03 | B | 6 | 0.00080111 | 1.9074e-05
2009 | 2008-10-03 | B | 28 | 0.013886 | 8.9012e-05
2009 | 2008-10-03 | C | 98 | 0.014331 | 0.00031154
2009 | 2008-10-04 | C | 17 | 0.0034047 | 5.4043e-05
2009 | 2008-10-04 | C | 4 | 0.00091555 | 1.2716e-05
2009 | 2008-10-04 | C | 92 | 0.069785 | 0.00029247
2009 | 2008-10-04 | C | 13 | 0.0015291 | 4.1327e-05
2009 | 2008-10-04 | C | 258 | 0.15337 | 0.00082018
2009 | 2008-10-04 | B | 3 | 0.00086787 | 9.537e-06
2009 | 2008-10-04 | C | 288 | 0.17578 | 0.00091555
2009 | 2008-10-04 | C | 5 | 0.00042916 | 1.5895e-05
2009 | 2008-10-04 | C | 256 | 0.12916 | 0.00081382
2009 | 2008-10-04 | C | 8 | 0.00045778 | 2.5432e-05
2009 | 2008-10-04 | B | 33 | 0.011015 | 0.00010491
2009 | 2008-10-04 | C | 54 | 0.016308 | 0.00017167
2009 | 2008-10-04 | C | 54 | 0.026265 | 0.00017167
2009 | 2008-10-04 | C | 86 | 0.075565 | 0.00027339
2009 | 2008-10-04 | C | 20 | 0.0026704 | 6.358e-05
2009 | 2008-10-03 | C | 258 | 0.14305 | 0.00082018
2009 | 2008-10-03 | C | 2292 | 0.094721 | 0.0072863
2009 | 2008-10-03 | C | 138 | 0.0052644 | 0.0004387
2009 | 2008-10-03 | C | 316 | 0.12359 | 0.0010046
2009 | 2008-10-04 | C | 330 | 0.12292 | 0.0010491
2009 | 2008-10-05 | B | 166 | 0.045383 | 0.00052771
2009 | 2008-10-05 | C | 5593 | 0.19558 | 0.01778
2009 | 2008-10-05 | B | 1 | 0.00026386 | 3.179e-06
2009 | 2008-10-04 | C | 41 | 0.18534 | 0.00013034
2009 | 2008-10-05 | C | 54 | 0.042325 | 0.00017167
2009 | 2008-10-05 | C | 397 | 0.16508 | 0.0012621
2009 | 2008-10-05 | C | 340 | 0.15169 | 0.0010809
2009 | 2008-10-05 | C | 10 | 0.0068984 | 3.179e-05
2009 | 2008-10-06 | C | 107 | 0.0020409 | 0.00034015
2009 | 2008-10-06 | C | 33 | 0.010071 | 0.00010491
2009 | 2008-10-06 | C | 31 | 0.0032521 | 9.8549e-05
2009 | 2008-10-06 | C | 222 | 0.059282 | 0.00070574
2009 | 2008-10-06 | C | 2 | 0.00070574 | 6.358e-06
2009 | 2008-10-06 | B | 6 | 0.0057413 | 1.9074e-05
2009 | 2008-10-06 | B | 1 | 0.0011126 | 3.179e-06
2009 | 2008-10-06 | B | 138 | 0.069315 | 0.0004387
2009 | 2008-10-06 | C | 1 | 0.0010077 | 3.179e-06
2009 | 2008-10-07 | C | 147 | 0.01215 | 0.00046731
2009 | 2008-10-07 | C | 72 | 0.012131 | 0.00022889
2009 | 2008-10-07 | C | 209 | 0.038536 | 0.00066441
2009 | 2008-10-07 | C | 544 | 0.33204 | 0.0017294
2009 | 2008-10-07 | C | 57 | 0.02718 | 0.0001812
2009 | 2008-10-07 | C | 241 | 0.050997 | 0.00076614
2009 | 2008-10-07 | C | 60 | 0.014687 | 0.00019074
2009 | 2008-10-07 | C | 100 | 0.032426 | 0.0003179
2009 | 2008-10-07 | C | 165 | 0.056077 | 0.00052453
2009 | 2008-10-07 | C | 40 | 0.0038148 | 0.00012716
2009 | 2008-10-07 | B | 89 | 0.068469 | 0.00028293
2009 | 2008-10-07 | B | 163 | 0.054968 | 0.00051818
2009 | 2009-02-28 | C | 122 | 0.052908 | 0.00038784
2009 | 2008-10-07 | C | 96 | 0.043692 | 0.00030518
2009 | 2008-10-07 | C | 203 | 0.083925 | 0.00064534
2009 | 2008-10-07 | C | 12 | 0.00030518 | 3.8148e-05
2009 | 2008-10-07 | C | 14 | 0.0021808 | 4.4506e-05
2009 | 2008-10-07 | C | 13 | 0.0031408 | 4.1327e-05
2009 | 2008-10-07 | C | 53 | 0.108 | 0.00016849
2009 | 2008-10-07 | C | 85 | 0.06496 | 0.00027021
2009 | 2008-10-07 | C | 181 | 0.010357 | 0.0005754
2009 | 2008-10-07 | C | 193 | 0.041034 | 0.00061355
2009 | 2008-10-07 | C | 284 | 0.083964 | 0.00090283
2009 | 2008-10-07 | C | 594 | 0.11708 | 0.0018883
2009 | 2009-02-28 | C | 45 | 0.0084402 | 0.00014305
2009 | 2008-10-07 | C | 51 | 0.070278 | 0.00016213
2009 | 2008-10-07 | C | 450 | 0.29236 | 0.0014305
2009 | 2008-10-07 | C | 29 | 0.0020282 | 9.2191e-05
2009 | 2008-10-07 | C | 250 | 0.003179 | 0.00079475
2009 | 2008-10-07 | C | 13 | 0.012026 | 4.1327e-05
2009 | 2008-10-07 | C | 53 | 0.076197 | 0.00016849
2009 | 2008-10-07 | C | 736 | 0.46395 | 0.0023397
2009 | 2008-10-07 | C | 177 | 0.17032 | 0.00056268
2009 | 2008-10-07 | C | 312 | 0.076363 | 0.00099185
2009 | 2008-10-07 | C | 562 | 0.10898 | 0.0017866
2009 | 2008-10-07 | C | 92 | 0.072532 | 0.00029247
2009 | 2008-10-07 | C | 1506 | 0.13405 | 0.0047876
2009 | 2008-10-07 | C | 4 | 0.00053407 | 1.2716e-05
2009 | 2008-10-08 | C | 68 | 0.017942 | 0.00021617
2009 | 2009-02-28 | C | 402 | 0.025559 | 0.001278
2009 | 2008-10-07 | C | 57 | 0.080947 | 0.0001812
2009 | 2008-10-08 | C | 13 | 0.0098771 | 4.1327e-05
2009 | 2008-10-08 | C | 2 | 0.00050864 | 6.358e-06
2009 | 2008-10-08 | B | 99 | 0.099452 | 0.00031472
2009 | 2008-10-08 | C | 256 | 0.043946 | 0.00081382
2009 | 2008-07-06 | C | 653 | 0.31969 | 0.0020759
2009 | 2008-10-08 | C | 4 | 0.0008774 | 1.2716e-05
2009 | 2008-10-08 | C | 177 | 0.021945 | 0.00056268
2009 | 2008-10-07 | C | 36 | 0.14367 | 0.00011444
2009 | 2008-10-08 | C | 7 | 0.0013129 | 2.2253e-05
2009 | 2008-10-07 | C | 238 | 1.0956 | 0.0007566
2009 | 2008-10-08 | C | 15 | 0.0056268 | 4.7685e-05
2009 | 2008-10-08 | C | 5 | 0.0014623 | 1.5895e-05
2009 | 2008-10-07 | C | 70 | 0.084113 | 0.00022253
2009 | 2008-10-07 | C | 49 | 0.095554 | 0.00015577
2009 | 2008-10-08 | C | 17 | 0.0032966 | 5.4043e-05
2009 | 2008-10-08 | C | 12 | 0.0014115 | 3.8148e-05
2009 | 2008-07-06 | C | 87 | 0.0049783 | 0.00027657
2009 | 2008-10-08 | C | 101 | 0.027292 | 0.00032108
2009 | 2008-06-29 | C | 405 | 0.18926 | 0.0012875
2009 | 2008-10-08 | B | 9 | 0.0059797 | 2.8611e-05
2009 | 2008-10-08 | C | 11 | 0.00080429 | 3.4969e-05
2009 | 2008-10-08 | C | 367 | 0.039667 | 0.0011667
2009 | 2008-10-08 | C | 6 | 0.0014496 | 1.9074e-05
2009 | 2008-10-08 | C | 27 | 0.0070383 | 8.5833e-05
2009 | 2008-10-08 | C | 64 | 0.011788 | 0.00020346
2009 | 2008-10-08 | C | 151 | 0.010751 | 0.00048003
2009 | 2008-10-09 | C | 64 | 0.0056968 | 0.00020346
2009 | 2008-10-09 | B | 6 | 0.0016976 | 1.9074e-05
2009 | 2008-10-09 | C | 28 | 0.0040945 | 8.9012e-05
2009 | 2008-10-09 | C | 237 | 0.013562 | 0.00075342
2009 | 2008-10-09 | C | 96 | 0.026945 | 0.00030518
2009 | 2008-06-29 | C | 405 | 0.058023 | 0.0012875
2009 | 2008-10-09 | B | 49 | 0.018225 | 0.00015577
2009 | 2008-10-10 | B | 2 | 0.00060401 | 6.358e-06
2009 | 2008-10-07 | C | 73 | 0.098905 | 0.00023207
2009 | 2008-10-10 | B | 26 | 0.0038847 | 8.2654e-05
2009 | 2008-10-10 | B | 8 | 0.0086977 | 2.5432e-05
2009 | 2008-10-10 | C | 35 | 0.0035605 | 0.00011126
2009 | 2008-10-10 | B | 49 | 0.041279 | 0.00015577
2009 | 2008-10-10 | C | 14 | 0.00071209 | 4.4506e-05
2009 | 2008-10-10 | C | 71 | 0.052358 | 0.00022571
2009 | 2008-10-10 | C | 134 | 0.020838 | 0.00042599
2009 | 2008-10-10 | C | 402 | 0.1195 | 0.001278
2009 | 2008-10-10 | C | 4 | 0.004031 | 1.2716e-05
2009 | 2008-10-11 | C | 3 | 0.0016594 | 9.537e-06
2009 | 2008-10-12 | C | 777 | 0.063491 | 0.0024701
2009 | 2008-10-12 | C | 39 | 0.018508 | 0.00012398
2009 | 2008-10-12 | C | 200 | 0.0025432 | 0.0006358
2009 | 2008-10-10 | B | 3 | 0.00034333 | 9.537e-06
2009 | 2008-10-08 | B | 20 | 0.011063 | 6.358e-05
2009 | 2008-10-13 | C | 72 | 0.0084688 | 0.00022889
2009 | 2008-10-13 | B | 2 | 0.0018057 | 6.358e-06
2009 | 2008-10-13 | C | 214 | 0.0061227 | 0.0006803
2009 | 2008-10-13 | C | 95 | 0.003322 | 0.000302
2009 | 2008-10-13 | B | 356 | 0.12223 | 0.0011317
2009 | 2008-10-14 | B | 26 | 0.022564 | 8.2654e-05
2009 | 2008-10-14 | B | 60 | 0.070955 | 0.00019074
2009 | 2008-10-14 | B | 1 | 0.0003179 | 3.179e-06
2009 | 2008-10-14 | B | 47 | 0.037204 | 0.00014941
2009 | 2008-10-14 | B | 10 | 0.014115 | 3.179e-05
2009 | 2008-10-14 | C | 3 | 0.002327 | 9.537e-06
2009 | 2008-10-15 | C | 19 | 0.0035637 | 6.0401e-05
2009 | 2008-10-15 | B | 67 | 0.013206 | 0.00021299
2009 | 2008-10-15 | B | 41 | 0.054351 | 0.00013034
2009 | 2008-10-17 | B | 95 | 0.044395 | 0.000302
2009 | 2008-10-15 | B | 60 | 0.033761 | 0.00019074
2009 | 2008-10-15 | B | 34 | 0.040748 | 0.00010809
2009 | 2008-10-15 | C | 626 | 0.17627 | 0.00199
2009 | 2008-10-15 | B | 14 | 0.015177 | 4.4506e-05
2009 | 2008-10-15 | B | 58 | 0.043698 | 0.00018438
2009 | 2008-10-15 | B | 2 | 0.0030518 | 6.358e-06
2009 | 2008-10-15 | B | 2 | 0.0017739 | 6.358e-06
2009 | 2008-10-16 | B | 20 | 0.022698 | 6.358e-05
2009 | 2008-10-16 | B | 3 | 0.0034047 | 9.537e-06
2009 | 2008-10-16 | B | 9 | 0.0084974 | 2.8611e-05
2009 | 2008-10-16 | B | 6 | 0.0026704 | 1.9074e-05
2009 | 2008-10-16 | B | 148 | 0.17126 | 0.00047049
2009 | 2008-10-16 | B | 20 | 0.022698 | 6.358e-05
2009 | 2008-10-16 | C | 734 | 0.19543 | 0.0023334
2009 | 2008-10-16 | C | 39 | 0.020209 | 0.00012398
2009 | 2008-10-17 | C | 458 | 0.073034 | 0.001456
2009 | 2008-10-17 | C | 200 | 0.015259 | 0.0006358
2009 | 2008-10-17 | C | 38 | 0.0096641 | 0.0001208
2009 | 2008-10-17 | C | 47 | 0.010011 | 0.00014941
2009 | 2008-10-17 | C | 45 | 0.0095847 | 0.00014305
2009 | 2008-10-17 | C | 142 | 0.054377 | 0.00045142
2009 | 2008-10-17 | C | 410 | 0.11991 | 0.0013034
2009 | 2008-10-17 | C | 16 | 0.0024923 | 5.0864e-05
2009 | 2008-10-17 | B | 208 | 0.047609 | 0.00066123
2009 | 2008-10-17 | B | 14 | 0.0085006 | 4.4506e-05
2009 | 2008-10-17 | B | 15 | 0.010681 | 4.7685e-05
2009 | 2008-10-18 | C | 43 | 0.009022 | 0.0001367
2009 | 2008-10-18 | C | 42 | 0.0056077 | 0.00013352
2009 | 2008-10-18 | B | 45 | 0.038053 | 0.00014305
2009 | 2008-10-18 | B | 34 | 0.034263 | 0.00010809
2009 | 2008-10-18 | B | 27 | 0.023947 | 8.5833e-05
2009 | 2008-10-18 | C | 38 | 0.0085388 | 0.0001208
2009 | 2008-10-18 | C | 4668 | 0.11872 | 0.01484
2009 | 2008-10-18 | C | 99 | 0.014067 | 0.00031472
2009 | 2008-10-07 | C | 85 | 0.017834 | 0.00027021
2009 | 2008-10-18 | C | 20 | 0.006803 | 6.358e-05
2009 | 2008-10-19 | C | 848 | 0.056612 | 0.0026958
2009 | 2008-10-19 | B | 8 | 0.010096 | 2.5432e-05
2009 | 2008-10-07 | C | 87 | 0.034737 | 0.00027657
2009 | 2008-10-19 | C | 237 | 0.0060274 | 0.00075342
2009 | 2008-10-19 | C | 104 | 0.011085 | 0.00033062
2009 | 2008-10-18 | C | 574 | 0.40219 | 0.0018247
2009 | 2008-10-19 | C | 7 | 0.010437 | 2.2253e-05
2009 | 2008-10-20 | B | 3 | 0.00035287 | 9.537e-06
2009 | 2008-10-20 | B | 1 | 0.00059129 | 3.179e-06
2009 | 2008-10-20 | B | 9 | 0.0064375 | 2.8611e-05
2009 | 2008-10-20 | B | 29 | 0.029501 | 9.2191e-05
2009 | 2008-10-20 | C | 338 | 0.036034 | 0.0010745
2009 | 2008-10-20 | C | 13 | 0.0018184 | 4.1327e-05
2009 | 2009-03-08 | C | 67 | 0.0014909 | 0.00021299
2009 | 2008-10-20 | C | 6 | 0.0014687 | 1.9074e-05
2009 | 2008-10-20 | C | 846 | 0.033522 | 0.0026894
2009 | 2008-10-20 | C | 217 | 0.11045 | 0.00068984
2009 | 2008-10-21 | C | 46 | 0.02486 | 0.00014623
2009 | 2008-10-21 | B | 28 | 0.0095243 | 8.9012e-05
2009 | 2009-03-09 | C | 16 | 0.002238 | 5.0864e-05
2009 | 2008-10-21 | B | 23 | 0.02486 | 7.3117e-05
2009 | 2008-10-21 | B | 7 | 0.0003783 | 2.2253e-05
2009 | 2008-10-21 | C | 487 | 0.029415 | 0.0015482
2009 | 2008-10-21 | C | 200 | 0.006358 | 0.0006358
2009 | 2008-10-21 | C | 63 | 0.0038053 | 0.00020028
2009 | 2008-10-21 | C | 200 | 0.0076296 | 0.0006358
2009 | 2008-10-22 | C | 246 | 0.075488 | 0.00078203
2009 | 2008-10-22 | C | 846 | 0.11565 | 0.0026894
2009 | 2008-10-22 | B | 7 | 0.0074102 | 2.2253e-05
2009 | 2008-10-22 | B | 9 | 0.0092699 | 2.8611e-05
2009 | 2008-10-22 | C | 459 | 0.011673 | 0.0014592
2009 | 2008-10-22 | C | 255 | 0.041343 | 0.00081064
2009 | 2008-10-22 | C | 11 | 0.0015386 | 3.4969e-05
2009 | 2008-10-21 | B | 36 | 0.033418 | 0.00011444
2009 | 2008-10-22 | C | 219 | 0.035506 | 0.0006962
2009 | 2008-10-23 | B | 1 | 0.00060401 | 3.179e-06
2009 | 2008-10-23 | B | 6 | 0.0022889 | 1.9074e-05
2009 | 2008-10-23 | C | 50 | 0.0058811 | 0.00015895
2009 | 2008-08-12 | C | 232 | 0.0088503 | 0.00073753
2009 | 2008-10-23 | C | 10 | 0.0010173 | 3.179e-05
2009 | 2008-10-23 | C | 82 | 0.026615 | 0.00026068
2009 | 2008-10-23 | B | 47 | 0.02759 | 0.00014941
2009 | 2008-10-23 | B | 14 | 0.013975 | 4.4506e-05
2009 | 2008-10-23 | B | 1 | 0.00094416 | 3.179e-06
2009 | 2008-10-23 | C | 43 | 0.0071082 | 0.0001367
2009 | 2008-10-23 | C | 773 | 0.13997 | 0.0024574
2009 | 2008-08-12 | C | 463 | 0.062661 | 0.0014719
2009 | 2008-10-24 | B | 69 | 0.0039483 | 0.00021935
2009 | 2008-10-23 | B | 69 | 0.0061418 | 0.00021935
2009 | 2008-10-24 | B | 48 | 0.037843 | 0.00015259
2009 | 2008-10-24 | B | 8 | 0.0075533 | 2.5432e-05
2009 | 2008-10-24 | C | 374 | 0.038192 | 0.0011889
2009 | 2008-10-24 | C | 146 | 0.0041772 | 0.00046413
2009 | 2008-10-24 | B | 27 | 0.031758 | 8.5833e-05
2009 | 2008-10-24 | C | 883 | 0.31985 | 0.0028071
2009 | 2008-10-24 | C | 1 | 0.00011126 | 3.179e-06
2009 | 2008-10-24 | C | 82 | 0.0018247 | 0.00026068
2009 | 2008-10-24 | C | 329 | 0.0073212 | 0.0010459
2009 | 2008-10-24 | C | 1393 | 0.78702 | 0.0044283
2009 | 2008-10-25 | C | 82 | 0.029991 | 0.00026068
2009 | 2008-10-25 | C | 835 | 0.15927 | 0.0026545
2009 | 2008-10-25 | C | 1 | 6.9938e-05 | 3.179e-06
2009 | 2008-10-23 | B | 11 | 0.0026926 | 3.4969e-05
2009 | 2008-10-25 | C | 10 | 0.0068666 | 3.179e-05
2009 | 2008-10-26 | C | 43 | 0.021735 | 0.0001367
2009 | 2008-10-26 | C | 71 | 0.0018057 | 0.00022571
2009 | 2008-10-26 | C | 124 | 0.014585 | 0.0003942
2009 | 2008-10-26 | C | 42 | 0.0084116 | 0.00013352
2009 | 2008-10-25 | C | 1540 | 0.13799 | 0.0048956
2009 | 2008-10-27 | C | 37 | 0.0055156 | 0.00011762
2009 | 2008-10-27 | C | 14 | 0.0013797 | 4.4506e-05
2009 | 2008-10-26 | C | 6 | 0.022126 | 1.9074e-05
2009 | 2008-10-26 | C | 158 | 0.026157 | 0.00050228
2009 | 2008-10-27 | C | 292 | 0.069213 | 0.00092827
2009 | 2008-10-28 | C | 15 | 0.00081064 | 4.7685e-05
2009 | 2008-10-28 | B | 16 | 0.013326 | 5.0864e-05
2009 | 2008-10-28 | B | 92 | 0.078966 | 0.00029247
2009 | 2008-10-28 | C | 2 | 0.00045142 | 6.358e-06
2009 | 2008-10-29 | C | 160 | 0.048321 | 0.00050864
2009 | 2008-10-28 | C | 2 | 0.00034333 | 6.358e-06
2009 | 2008-10-29 | C | 194 | 0.052282 | 0.00061672
2009 | 2008-10-28 | C | 100 | 0.045571 | 0.0003179
2009 | 2008-10-28 | C | 1640 | 0.28003 | 0.0052135
2009 | 2008-10-28 | C | 55 | 0.0047208 | 0.00017484
2009 | 2008-10-28 | C | 621 | 0.13511 | 0.0019742
2009 | 2008-10-29 | B | 30 | 0.032903 | 9.537e-05
2009 | 2008-10-29 | C | 5 | 0.0044029 | 1.5895e-05
2009 | 2008-10-29 | B | 94 | 0.054386 | 0.00029883
2009 | 2008-10-29 | C | 81 | 0.082142 | 0.0002575
2009 | 2008-10-29 | C | 104 | 0.10644 | 0.00033062
2009 | 2008-10-30 | B | 7 | 0.0051404 | 2.2253e-05
2009 | 2008-10-30 | B | 5 | 0.0023842 | 1.5895e-05
2009 | 2008-10-30 | B | 20 | 0.0042599 | 6.358e-05
2009 | 2008-10-30 | B | 60 | 0.068666 | 0.00019074
2009 | 2008-10-30 | C | 3 | 0.00046731 | 9.537e-06
2009 | 2008-10-30 | C | 335 | 0.060045 | 0.001065
2009 | 2008-10-30 | B | 3 | 0.0011349 | 9.537e-06
2009 | 2008-10-30 | B | 99 | 0.075533 | 0.00031472
2009 | 2008-10-30 | C | 92 | 0.041019 | 0.00029247
2009 | 2008-10-31 | C | 187 | 0.060636 | 0.00059447
2009 | 2008-10-31 | C | 1238 | 0.16136 | 0.0039356
2009 | 2008-10-31 | B | 77 | 0.084695 | 0.00024478
2009 | 2008-10-31 | B | 2 | 0.0021363 | 6.358e-06
2009 | 2008-10-31 | B | 19 | 0.0070669 | 6.0401e-05
2009 | 2008-11-01 | C | 85 | 0.003783 | 0.00027021
2009 | 2008-11-01 | C | 146 | 0.14749 | 0.00046413
2009 | 2008-11-01 | C | 15 | 0.0015259 | 4.7685e-05
2009 | 2008-11-01 | C | 105 | 0.0023366 | 0.00033379
2009 | 2008-11-01 | C | 20 | 0.0036876 | 6.358e-05
2009 | 2008-11-01 | B | 32 | 0.017802 | 0.00010173
2009 | 2008-11-01 | C | 616 | 0.28591 | 0.0019583
2009 | 2008-11-01 | C | 594 | 0.018883 | 0.0018883
2009 | 2008-11-01 | C | 13 | 0.04765 | 4.1327e-05
2009 | 2008-11-01 | C | 97 | 0.060299 | 0.00030836
2009 | 2008-11-02 | C | 197 | 0.070141 | 0.00062626
2009 | 2008-11-02 | B | 88 | 0.053992 | 0.00027975
2009 | 2008-10-30 | B | 43 | 0.034584 | 0.0001367
2009 | 2008-10-24 | B | 31 | 0.035379 | 9.8549e-05
2009 | 2008-10-29 | B | 1 | 0.00034015 | 3.179e-06
2009 | 2008-11-03 | B | 5 | 0.0028293 | 1.5895e-05
2009 | 2008-11-03 | B | 5 | 0.0034651 | 1.5895e-05
2009 | 2008-11-04 | B | 6 | 0.00013352 | 1.9074e-05
2009 | 2008-11-04 | B | 71 | 0.051462 | 0.00022571
2009 | 2008-11-04 | C | 6 | 0.0039102 | 1.9074e-05
2009 | 2008-11-04 | B | 2 | 0.002397 | 6.358e-06
2009 | 2008-11-04 | C | 547 | 0.10781 | 0.0017389
2009 | 2008-11-04 | C | 219 | 0.041842 | 0.0006962
2009 | 2008-11-05 | C | 90 | 0.041381 | 0.00028611
2009 | 2008-11-05 | B | 11 | 0.005665 | 3.4969e-05
2009 | 2008-11-05 | B | 2 | 0.0012207 | 6.358e-06
2009 | 2008-11-05 | B | 15 | 0.017262 | 4.7685e-05
2009 | 2008-11-05 | B | 54 | 0.036393 | 0.00017167
2009 | 2008-11-05 | C | 11 | 0.0072386 | 3.4969e-05
2009 | 2008-11-05 | C | 85 | 0.0045936 | 0.00027021
2009 | 2008-11-05 | C | 37 | 0.0047049 | 0.00011762
2009 | 2008-11-05 | B | 364 | 0.027263 | 0.0011572
2009 | 2008-11-05 | C | 41 | 0.024243 | 0.00013034
2009 | 2008-11-05 | C | 93 | 0.04346 | 0.00029565
2009 | 2008-11-05 | C | 531 | 0.082097 | 0.001688
2009 | 2008-11-05 | C | 29 | 0.0068221 | 9.2191e-05
2009 | 2008-11-05 | C | 54 | 0.011845 | 0.00017167
2009 | 2008-11-05 | C | 4 | 0.00078839 | 1.2716e-05
2009 | 2008-11-05 | C | 95 | 0.024024 | 0.000302
2009 | 2008-11-05 | C | 5 | 0.00046095 | 1.5895e-05
2009 | 2008-11-06 | B | 56 | 0.019939 | 0.00017802
2009 | 2008-11-05 | B | 79 | 0.034155 | 0.00025114
2009 | 2008-11-06 | B | 4 | 0.0034587 | 1.2716e-05
2009 | 2008-11-06 | B | 2 | 0.0016086 | 6.358e-06
2009 | 2008-11-06 | B | 9 | 0.011072 | 2.8611e-05
2009 | 2008-11-06 | B | 191 | 0.14208 | 0.00060719
2009 | 2008-11-06 | B | 308 | 0.095103 | 0.00097913
2009 | 2008-11-06 | B | 51 | 0.018483 | 0.00016213
2009 | 2008-11-06 | C | 2313 | 0.3208 | 0.007353
2009 | 2008-11-07 | C | 584 | 0.012996 | 0.0018565
2009 | 2008-11-07 | B | 9 | 0.0079538 | 2.8611e-05
2009 | 2008-11-07 | B | 38 | 0.010631 | 0.0001208
2009 | 2008-11-07 | C | 68 | 0.011673 | 0.00021617
2009 | 2008-11-07 | C | 76 | 0.0079729 | 0.0002416
2009 | 2008-11-07 | C | 149 | 0.012789 | 0.00047367
2009 | 2008-11-08 | B | 51 | 0.017348 | 0.00016213
2009 | 2008-11-08 | B | 1 | 0.00062308 | 3.179e-06
2009 | 2008-11-08 | C | 50 | 0.0081064 | 0.00015895
2009 | 2008-11-08 | C | 163 | 0.080899 | 0.00051818
2009 | 2008-11-08 | C | 223 | 0.13446 | 0.00070892
2009 | 2008-11-07 | C | 30 | 0.0019074 | 9.537e-05
2009 | 2008-11-09 | C | 1154 | 0.32946 | 0.0036686
2009 | 2008-11-07 | B | 3 | 0.00022889 | 9.537e-06
2009 | 2008-11-08 | B | 1 | 0.0007566 | 3.179e-06
2009 | 2008-11-10 | B | 2 | 0.0015259 | 6.358e-06
2009 | 2008-11-10 | B | 4 | 0.0028611 | 1.2716e-05
2009 | 2008-11-10 | B | 28 | 0.028929 | 8.9012e-05
2009 | 2008-11-11 | C | 362 | 0.063294 | 0.0011508
2009 | 2008-11-11 | C | 6 | 0.00022889 | 1.9074e-05
2009 | 2008-11-11 | B | 12 | 0.010185 | 3.8148e-05
2009 | 2008-11-11 | B | 49 | 0.035204 | 0.00015577
2009 | 2008-11-11 | B | 4 | 0.0028484 | 1.2716e-05
2009 | 2008-11-11 | C | 25 | 0.014703 | 7.9475e-05
2009 | 2008-11-11 | B | 23 | 0.028077 | 7.3117e-05
2009 | 2008-11-11 | B | 2 | 0.0013543 | 6.358e-06
2009 | 2008-11-11 | C | 4 | 0.00035605 | 1.2716e-05
2009 | 2008-10-23 | C | 242 | 0.0053852 | 0.00076932
2009 | 2008-11-12 | B | 25 | 0.015974 | 7.9475e-05
2009 | 2008-11-12 | B | 90 | 0.07353 | 0.00028611
2009 | 2008-11-12 | B | 7 | 0.001847 | 2.2253e-05
2009 | 2008-11-12 | B | 2 | 0.001882 | 6.358e-06
2009 | 2008-11-12 | B | 46 | 0.064343 | 0.00014623
2009 | 2008-10-24 | C | 202 | 0.089536 | 0.00064216
2009 | 2008-11-12 | C | 748 | 0.023779 | 0.0023779
2009 | 2008-11-12 | C | 318 | 0.25912 | 0.0010109
2009 | 2008-11-13 | C | 39 | 0.010538 | 0.00012398
2009 | 2008-11-13 | C | 390 | 0.051214 | 0.0012398
2009 | 2008-11-13 | B | 31 | 0.032225 | 9.8549e-05
2009 | 2008-11-13 | B | 7 | 0.0071432 | 2.2253e-05
2009 | 2008-11-13 | B | 22 | 0.026227 | 6.9938e-05
2009 | 2008-11-13 | B | 182 | 0.19324 | 0.00057858
2009 | 2008-11-13 | C | 34 | 0.0028102 | 0.00010809
2009 | 2008-11-13 | C | 15 | 0.0015736 | 4.7685e-05
2009 | 2008-11-13 | C | 395 | 0.056071 | 0.0012557
2009 | 2008-11-14 | C | 108 | 0.036393 | 0.00034333
2009 | 2008-11-14 | C | 70 | 0.048543 | 0.00022253
2009 | 2008-11-14 | B | 1 | 0.00034015 | 3.179e-06
2009 | 2008-11-14 | B | 7 | 0.003694 | 2.2253e-05
2009 | 2008-11-14 | B | 3 | 0.0014019 | 9.537e-06
2009 | 2008-11-14 | C | 364 | 0.091933 | 0.0011572
2009 | 2008-11-15 | C | 4 | 0.0019964 | 1.2716e-05
2009 | 2008-11-15 | C | 97 | 0.029911 | 0.00030836
2009 | 2008-11-15 | C | 3 | 0.0098612 | 9.537e-06
2009 | 2008-11-16 | C | 169 | 0.037585 | 0.00053725
2009 | 2008-11-17 | C | 287 | 0.047478 | 0.00091237
2009 | 2008-11-14 | B | 74 | 0.029641 | 0.00023525
2009 | 2008-11-17 | C | 150 | 0.087718 | 0.00047685
2009 | 2008-11-17 | C | 1019 | 0.14012 | 0.0032394
2009 | 2008-11-17 | C | 3 | 0.0001812 | 9.537e-06
2009 | 2008-11-17 | B | 2 | 0.00046413 | 6.358e-06
2009 | 2008-11-17 | C | 84 | 0.0018692 | 0.00026704
2009 | 2008-11-17 | B | 23 | 0.016378 | 7.3117e-05
2009 | 2008-11-17 | B | 50 | 0.0034969 | 0.00015895
2009 | 2008-11-17 | B | 151 | 0.015841 | 0.00048003
2009 | 2008-11-17 | C | 51 | 0.0016213 | 0.00016213
2009 | 2008-11-17 | B | 50 | 0.01367 | 0.00015895
2009 | 2008-11-17 | C | 252 | 0.085718 | 0.00080111
2009 | 2008-11-17 | C | 481 | 0.10092 | 0.0015291
2009 | 2008-11-17 | C | 1564 | 0.24784 | 0.0049719
2009 | 2008-11-17 | C | 335 | 0.060143 | 0.001065
2009 | 2008-11-18 | C | 25 | 0.0045301 | 7.9475e-05
2009 | 2008-11-18 | B | 1 | 0.00027975 | 3.179e-06
2009 | 2008-11-18 | C | 365 | 0.019726 | 0.0011603
2009 | 2008-11-18 | B | 56 | 0.00035605 | 0.00017802
2009 | 2008-11-18 | B | 14 | 0.013708 | 4.4506e-05
2009 | 2008-11-18 | B | 93 | 0.09372 | 0.00029565
2009 | 2008-11-18 | B | 1 | 0.00046095 | 3.179e-06
2009 | 2008-11-18 | B | 47 | 0.049007 | 0.00014941
2009 | 2008-11-18 | C | 69 | 0.012722 | 0.00021935
2009 | 2008-11-19 | B | 3 | 0.0013066 | 9.537e-06
2009 | 2008-11-19 | B | 132 | 0.012169 | 0.00041963
2009 | 2008-11-19 | B | 5 | 0.0033538 | 1.5895e-05
2009 | 2008-11-19 | C | 317 | 0.056227 | 0.0010077
2009 | 2008-11-19 | B | 78 | 0.016861 | 0.00024796
2009 | 2008-11-19 | B | 2 | 0.0016976 | 6.358e-06
2009 | 2008-11-19 | B | 41 | 0.034149 | 0.00013034
2009 | 2008-11-19 | B | 33 | 0.036508 | 0.00010491
2009 | 2008-11-19 | B | 25 | 0.025829 | 7.9475e-05
2009 | 2008-11-19 | B | 38 | 0.041435 | 0.0001208
2009 | 2008-11-19 | C | 71 | 0.038145 | 0.00022571
2009 | 2008-11-20 | B | 23 | 0.016598 | 7.3117e-05
2009 | 2008-11-20 | B | 2 | 0.00069302 | 6.358e-06
2009 | 2008-11-20 | B | 7 | 0.0059415 | 2.2253e-05
2009 | 2008-11-20 | B | 10 | 0.00817 | 3.179e-05
2009 | 2008-11-20 | B | 38 | 0.035878 | 0.0001208
2009 | 2008-11-20 | B | 79 | 0.033007 | 0.00025114
2009 | 2008-11-20 | B | 14 | 0.017491 | 4.4506e-05
2009 | 2008-11-20 | C | 55 | 0.030073 | 0.00017484
2009 | 2008-11-20 | C | 411 | 0.18292 | 0.0013066
2009 | 2008-11-20 | C | 70 | 0.016467 | 0.00022253
2009 | 2008-11-21 | C | 58 | 0.0092191 | 0.00018438
2009 | 2008-11-20 | C | 1733 | 0.16528 | 0.0055092
2009 | 2008-11-21 | B | 139 | 0.011489 | 0.00044188
2009 | 2008-11-21 | B | 1 | 0.00040691 | 3.179e-06
2009 | 2008-11-21 | C | 26 | 0.0046286 | 8.2654e-05
2009 | 2008-11-21 | B | 11 | 0.0082177 | 3.4969e-05
2009 | 2008-11-21 | B | 4 | 0.0025559 | 1.2716e-05
2009 | 2008-11-21 | B | 101 | 0.014449 | 0.00032108
2009 | 2008-11-21 | B | 37 | 0.01682 | 0.00011762
2009 | 2008-11-21 | C | 446 | 0.029774 | 0.0014178
2009 | 2008-11-22 | C | 97 | 0.011409 | 0.00030836
2009 | 2008-11-22 | C | 60 | 0.028611 | 0.00019074
2009 | 2008-11-22 | C | 132 | 0.025724 | 0.00041963
2009 | 2008-11-23 | C | 9176 | 1.8377 | 0.02917
2009 | 2008-11-23 | C | 5272 | 1.0559 | 0.01676
2009 | 2008-11-22 | B | 135 | 0.039152 | 0.00042916
2009 | 2008-11-24 | C | 15 | 0.0020981 | 4.7685e-05
2009 | 2008-11-24 | B | 1 | 0.00044506 | 3.179e-06
2009 | 2008-11-24 | B | 8 | 0.0015768 | 2.5432e-05
2009 | 2008-11-24 | B | 13 | 0.015663 | 4.1327e-05
2009 | 2008-11-24 | C | 128 | 0.047087 | 0.00040691
2009 | 2008-11-24 | C | 54 | 0.043921 | 0.00017167
2009 | 2008-11-24 | C | 131 | 0.03885 | 0.00041645
2009 | 2008-11-24 | C | 132 | 0.0050355 | 0.00041963
2009 | 2008-11-25 | C | 347 | 0.071028 | 0.0011031
2009 | 2008-11-25 | C | 132 | 0.0025178 | 0.00041963
2009 | 2008-11-25 | C | 160 | 0.062639 | 0.00050864
2009 | 2008-11-25 | B | 7 | 0.0030487 | 2.2253e-05
2009 | 2008-11-25 | C | 101 | 0.015733 | 0.00032108
2009 | 2008-11-25 | C | 25 | 0.0083449 | 7.9475e-05
2009 | 2008-11-25 | B | 32 | 0.030315 | 0.00010173
2009 | 2008-11-25 | B | 54 | 0.01291 | 0.00017167
2009 | 2008-11-25 | C | 67 | 0.017465 | 0.00021299
2009 | 2008-11-25 | C | 58 | 0.023191 | 0.00018438
2009 | 2008-11-25 | B | 46 | 0.042001 | 0.00014623
2009 | 2008-11-26 | B | 2 | 0.0012716 | 6.358e-06
2009 | 2008-11-26 | B | 7 | 0.0028929 | 2.2253e-05
2009 | 2008-11-26 | C | 42 | 0.0066759 | 0.00013352
2009 | 2008-11-26 | B | 57 | 0.015698 | 0.0001812
2009 | 2008-11-26 | C | 17 | 0.0014051 | 5.4043e-05
2009 | 2008-11-26 | C | 76 | 0.035274 | 0.0002416
2009 | 2008-11-26 | C | 149 | 0.025403 | 0.00047367
2009 | 2008-11-26 | B | 10 | 0.01119 | 3.179e-05
2009 | 2008-11-26 | C | 11 | 0.0018883 | 3.4969e-05
2009 | 2008-11-26 | C | 380 | 0.016912 | 0.001208
2009 | 2008-11-26 | C | 1 | 0.00082972 | 3.179e-06
2009 | 2008-11-27 | B | 18 | 0.015107 | 5.7222e-05
2009 | 2008-11-27 | B | 1 | 2.8611e-05 | 3.179e-06
2009 | 2008-11-27 | B | 13 | 0.013431 | 4.1327e-05
2009 | 2008-11-27 | B | 33 | 0.033675 | 0.00010491
2009 | 2008-11-27 | B | 53 | 0.017186 | 0.00016849
2009 | 2008-11-27 | B | 47 | 0.057076 | 0.00014941
2009 | 2008-11-27 | C | 37 | 0.031993 | 0.00011762
2009 | 2008-11-27 | C | 832 | 0.13225 | 0.0026449
2009 | 2008-11-25 | C | 149 | 0.15178 | 0.00047367
2009 | 2008-11-27 | C | 857 | 0.33962 | 0.0027244
2009 | 2008-11-27 | C | 23 | 0.0046795 | 7.3117e-05
2009 | 2008-11-27 | C | 456 | 0.13194 | 0.0014496
2009 | 2008-11-27 | C | 401 | 0.40155 | 0.0012748
2009 | 2008-11-28 | B | 10 | 0.0056268 | 3.179e-05
2009 | 2008-11-28 | B | 24 | 0.011215 | 7.6296e-05
2009 | 2008-11-28 | C | 8 | 0.0016785 | 2.5432e-05
2009 | 2008-11-28 | C | 754 | 0.10023 | 0.002397
2009 | 2008-11-29 | C | 6 | 0.0049211 | 1.9074e-05
2009 | 2008-11-29 | C | 85 | 0.011349 | 0.00027021
2009 | 2008-11-29 | C | 47 | 0.013447 | 0.00014941
2009 | 2008-11-29 | C | 69 | 0.026103 | 0.00021935
2009 | 2008-11-30 | C | 488 | 0.0015513 | 0.0015513
2009 | 2008-11-30 | C | 102 | 0.099547 | 0.00032426
2009 | 2008-11-30 | C | 1041 | 0.045835 | 0.0033093
2009 | 2008-11-30 | B | 36 | 0.020257 | 0.00011444
2009 | 2008-11-30 | B | 74 | 0.05293 | 0.00023525
2009 | 2008-11-30 | B | 21 | 0.028105 | 6.6759e-05
2009 | 2008-11-30 | C | 149 | 0.048372 | 0.00047367
2009 | 2008-11-30 | C | 2860 | 0.027276 | 0.0090919
2009 | 2008-12-01 | C | 579 | 0.15461 | 0.0018406
2009 | 2008-12-01 | B | 1 | 0.00060719 | 3.179e-06
2009 | 2008-12-01 | B | 17 | 0.012862 | 5.4043e-05
2009 | 2008-12-01 | C | 9 | 0.00080111 | 2.8611e-05
2009 | 2008-12-01 | C | 52 | 0.0095878 | 0.00016531
2009 | 2008-12-01 | B | 4 | 0.0011826 | 1.2716e-05
2009 | 2008-12-01 | C | 330 | 0.12348 | 0.0010491
2009 | 2008-12-01 | C | 142 | 0.014897 | 0.00045142
2009 | 2008-12-02 | C | 274 | 0.020133 | 0.00087104
2009 | 2008-12-02 | B | 14 | 0.0064089 | 4.4506e-05
2009 | 2008-12-02 | C | 23 | 0.0048988 | 7.3117e-05
2009 | 2008-12-02 | C | 217 | 0.16004 | 0.00068984
2009 | 2008-12-02 | B | 10 | 0.0097277 | 3.179e-05
2009 | 2008-12-02 | B | 33 | 0.049516 | 0.00010491
2009 | 2008-12-02 | C | 52 | 0.0206 | 0.00016531
2009 | 2008-12-02 | C | 69 | 0.0098708 | 0.00021935
2009 | 2008-12-02 | B | 53 | 0.024768 | 0.00016849
2009 | 2008-12-03 | B | 193 | 0.033131 | 0.00061355
2009 | 2008-12-02 | B | 4 | 0.003001 | 1.2716e-05
2009 | 2008-12-01 | B | 7 | 0.0064979 | 2.2253e-05
2009 | 2008-12-03 | B | 33 | 0.0041963 | 0.00010491
2009 | 2008-12-03 | B | 4 | 0.00025432 | 1.2716e-05
2009 | 2008-12-03 | B | 29 | 0.0020282 | 9.2191e-05
2009 | 2008-12-03 | B | 11 | 0.0088122 | 3.4969e-05
2009 | 2008-12-03 | B | 8 | 0.0066123 | 2.5432e-05
2009 | 2008-12-03 | B | 136 | 0.17337 | 0.00043234
2009 | 2008-12-03 | C | 48 | 0.0019837 | 0.00015259
2009 | 2008-12-03 | C | 105 | 0.0090124 | 0.00033379
2009 | 2008-12-03 | B | 10 | 0.018979 | 3.179e-05
2009 | 2008-12-04 | B | 23 | 0.0045332 | 7.3117e-05
2009 | 2008-12-04 | B | 1 | 0.00054997 | 3.179e-06
2009 | 2008-12-03 | B | 1 | 0.00048003 | 3.179e-06
2009 | 2008-12-04 | B | 15 | 0.011683 | 4.7685e-05
2009 | 2008-12-04 | B | 14 | 0.0048956 | 4.4506e-05
2009 | 2008-12-04 | B | 4 | 0.0041836 | 1.2716e-05
2009 | 2008-12-04 | C | 100 | 0.0036304 | 0.0003179
2009 | 2008-12-04 | B | 22 | 0.020422 | 6.9938e-05
2009 | 2008-12-04 | B | 21 | 0.023499 | 6.6759e-05
2009 | 2008-12-04 | C | 32 | 0.0043743 | 0.00010173
2009 | 2008-12-05 | B | 199 | 0.059466 | 0.00063262
2009 | 2008-12-04 | B | 46 | 0.0045332 | 0.00014623
2009 | 2008-12-05 | B | 3 | 0.0021554 | 9.537e-06
2009 | 2008-12-05 | B | 22 | 0.017624 | 6.9938e-05
2009 | 2008-12-05 | C | 814 | 0.028465 | 0.0025877
2009 | 2008-12-05 | C | 661 | 0.1107 | 0.0021013
2009 | 2008-12-06 | C | 25 | 0.0023842 | 7.9475e-05
2009 | 2008-12-07 | B | 5 | 0.0046095 | 1.5895e-05
2009 | 2008-12-07 | C | 157 | 0.0826 | 0.0004991
2009 | 2008-12-07 | C | 286 | 0.12456 | 0.00090919
2009 | 2008-12-05 | B | 29 | 0.010786 | 9.2191e-05
2009 | 2008-12-08 | C | 1383 | 0.29457 | 0.0043965
2009 | 2008-12-08 | C | 784 | 0.030461 | 0.0024923
2009 | 2008-12-05 | B | 8 | 0.0017294 | 2.5432e-05
2009 | 2008-12-08 | B | 11 | 0.0079379 | 3.4969e-05
2009 | 2008-12-08 | B | 2 | 0.0015068 | 6.358e-06
2009 | 2008-12-08 | C | 2 | 0.0011826 | 6.358e-06
2009 | 2008-12-08 | C | 22 | 0.0011889 | 6.9938e-05
2009 | 2008-12-08 | C | 23 | 0.0048257 | 7.3117e-05
2009 | 2008-12-08 | B | 6 | 0.0030137 | 1.9074e-05
2009 | 2008-12-08 | B | 4 | 0.0036876 | 1.2716e-05
2009 | 2008-05-12 | C | 322 | 0.0071655 | 0.0010236
2009 | 2008-12-09 | B | 206 | 0.092992 | 0.00065487
2009 | 2008-12-09 | B | 8 | 0.0020854 | 2.5432e-05
2009 | 2008-12-09 | C | 10 | 0.00089012 | 3.179e-05
2009 | 2008-12-09 | B | 208 | 0.19639 | 0.00066123
2009 | 2008-12-09 | C | 150 | 0.037786 | 0.00047685
2009 | 2008-12-09 | C | 535 | 0.38802 | 0.0017008
2009 | 2008-12-09 | C | 24 | 0.00206 | 7.6296e-05
2009 | 2008-05-12 | C | 150 | 0.206 | 0.00047685
2009 | 2008-10-20 | C | 3 | 0.0033888 | 9.537e-06
2009 | 2008-12-09 | C | 94 | 0.044589 | 0.00029883
2009 | 2008-10-20 | C | 1 | 0.0031917 | 3.179e-06
2009 | 2008-12-10 | C | 87 | 0.036123 | 0.00027657
2009 | 2008-12-10 | B | 59 | 0.036949 | 0.00018756
2009 | 2008-12-10 | C | 47 | 0.013298 | 0.00014941
2009 | 2008-12-10 | B | 1 | 0.001084 | 3.179e-06
2009 | 2008-12-10 | B | 2 | 0.0014051 | 6.358e-06
2009 | 2008-12-10 | B | 123 | 0.034909 | 0.00039102
2009 | 2008-12-10 | B | 322 | 0.21253 | 0.0010236
2009 | 2008-12-10 | B | 123 | 0.051614 | 0.00039102
2009 | 2008-12-10 | B | 5 | 0.0034174 | 1.5895e-05
2009 | 2008-12-10 | C | 84 | 0.023521 | 0.00026704
2009 | 2008-12-10 | C | 598 | 0.13721 | 0.001901
2009 | 2008-12-11 | B | 18 | 0.0047494 | 5.7222e-05
2009 | 2008-12-11 | B | 36 | 0.036965 | 0.00011444
2009 | 2008-12-11 | C | 418 | 0.083417 | 0.0013288
2009 | 2008-12-11 | B | 22 | 0.029933 | 6.9938e-05
2009 | 2008-12-11 | C | 126 | 0.01482 | 0.00040055
2009 | 2008-12-11 | B | 30 | 0.036717 | 9.537e-05
2009 | 2008-12-11 | B | 200 | 0.17612 | 0.0006358
2009 | 2008-12-12 | B | 1 | 0.0003783 | 3.179e-06
2009 | 2008-12-12 | B | 84 | 0.026971 | 0.00026704
2009 | 2008-12-12 | B | 80 | 0.049338 | 0.00025432
2009 | 2008-12-12 | C | 46 | 0.0090665 | 0.00014623
2009 | 2008-12-12 | C | 407 | 0.12629 | 0.0012939
2009 | 2008-12-12 | B | 2 | 0.00041963 | 6.358e-06
2009 | 2008-12-13 | B | 30 | 0.021649 | 9.537e-05
2009 | 2008-12-13 | B | 3 | 0.0021935 | 9.537e-06
2009 | 2008-12-13 | C | 54 | 0.028563 | 0.00017167
2009 | 2008-12-14 | C | 39 | 0.0057031 | 0.00012398
2009 | 2008-12-14 | B | 1 | 0.00075342 | 3.179e-06
2009 | 2008-12-15 | C | 185 | 0.02176 | 0.00058811
2009 | 2008-12-12 | B | 2 | 0.002149 | 6.358e-06
2009 | 2008-12-15 | B | 55 | 0.028675 | 0.00017484
2009 | 2008-12-15 | B | 87 | 0.026551 | 0.00027657
2009 | 2008-12-15 | C | 32 | 0.0020346 | 0.00010173
2009 | 2008-12-15 | B | 22 | 0.02273 | 6.9938e-05
2009 | 2008-12-15 | B | 1 | 0.00064851 | 3.179e-06
2009 | 2008-12-15 | C | 242 | 0.02238 | 0.00076932
2009 | 2008-12-15 | C | 7 | 0.00060083 | 2.2253e-05
2009 | 2008-12-16 | C | 1179 | 0.47798 | 0.003748
2009 | 2008-12-16 | B | 285 | 0.041677 | 0.00090601
2009 | 2008-12-16 | B | 81 | 0.050727 | 0.0002575
2009 | 2008-12-16 | B | 1 | 0.00064534 | 3.179e-06
2009 | 2008-12-16 | B | 47 | 0.04064 | 0.00014941
2009 | 2008-12-16 | B | 7 | 0.0083894 | 2.2253e-05
2009 | 2008-12-16 | B | 46 | 0.05279 | 0.00014623
2009 | 2008-12-16 | C | 5 | 0.0047462 | 1.5895e-05
2009 | 2008-12-16 | B | 5 | 0.0052135 | 1.5895e-05
2009 | 2008-12-16 | B | 269 | 0.1339 | 0.00085515
2009 | 2008-12-16 | B | 28 | 0.032311 | 8.9012e-05
2009 | 2008-12-16 | C | 1200 | 0.22468 | 0.0038148
2009 | 2008-12-16 | C | 1 | 6.358e-05 | 3.179e-06
2009 | 2008-12-17 | C | 221 | 0.08782 | 0.00070256
2009 | 2008-12-16 | C | 1 | 8.9012e-05 | 3.179e-06
2009 | 2008-12-16 | B | 79 | 0.04194 | 0.00025114
2009 | 2008-12-17 | C | 128 | 0.047609 | 0.00040691
2009 | 2008-12-17 | C | 5 | 0.0019233 | 1.5895e-05
2009 | 2008-12-17 | C | 321 | 0.013266 | 0.0010205
2009 | 2008-12-16 | B | 367 | 0.022396 | 0.0011667
2009 | 2008-12-17 | B | 63 | 0.078508 | 0.00020028
2009 | 2008-12-16 | B | 367 | 0.08054 | 0.0011667
2009 | 2008-12-17 | C | 192 | 0.043336 | 0.00061037
2009 | 2008-12-17 | C | 159 | 0.037251 | 0.00050546
2009 | 2008-12-17 | C | 491 | 0.093132 | 0.0015609
2009 | 2008-12-17 | C | 5 | 0.00055632 | 1.5895e-05
2009 | 2008-12-17 | C | 178 | 0.17851 | 0.00056586
2009 | 2008-12-17 | C | 797 | 0.0025337 | 0.0025337
2009 | 2008-12-18 | B | 10 | 0.0018756 | 3.179e-05
2009 | 2008-12-18 | B | 132 | 0.09022 | 0.00041963
2009 | 2008-12-18 | B | 40 | 0.015132 | 0.00012716
2009 | 2008-12-18 | B | 82 | 0.075857 | 0.00026068
2009 | 2008-12-18 | B | 178 | 0.084434 | 0.00056586
2009 | 2008-12-18 | B | 83 | 0.0219 | 0.00026386
2009 | 2008-12-17 | B | 3 | 0.0017739 | 9.537e-06
2009 | 2008-12-18 | B | 7 | 0.0074325 | 2.2253e-05
2009 | 2008-12-18 | B | 322 | 0.19347 | 0.0010236
2009 | 2008-12-18 | C | 711 | 0.10849 | 0.0022603
2009 | 2008-12-18 | C | 4 | 0.0039292 | 1.2716e-05
2009 | 2008-12-18 | B | 219 | 0.0076582 | 0.0006962
2009 | 2008-12-19 | B | 7 | 0.0016022 | 2.2253e-05
2009 | 2008-12-19 | B | 1 | 0.00020028 | 3.179e-06
2009 | 2008-12-19 | B | 4 | 0.0028865 | 1.2716e-05
2009 | 2008-12-19 | C | 537 | 0.0056268 | 0.0017071
2009 | 2008-12-19 | B | 133 | 0.11331 | 0.00042281
2009 | 2008-12-19 | B | 42 | 0.01442 | 0.00013352
2009 | 2008-12-19 | B | 9 | 0.0050355 | 2.8611e-05
2009 | 2008-12-19 | C | 11 | 0.0027625 | 3.4969e-05
2009 | 2008-12-19 | C | 7 | 0.0020918 | 2.2253e-05
2009 | 2008-12-19 | C | 1341 | 0.25203 | 0.004263
2009 | 2008-12-19 | C | 167 | 0.041305 | 0.00053089
2009 | 2008-12-20 | C | 39 | 0.0034715 | 0.00012398
2009 | 2008-12-20 | C | 5 | 0.0013511 | 1.5895e-05
2009 | 2008-12-20 | C | 203 | 0.11745 | 0.00064534
2009 | 2008-12-20 | C | 163 | 0.0062181 | 0.00051818
2009 | 2008-12-20 | C | 157 | 0.039575 | 0.0004991
2009 | 2008-12-20 | C | 60 | 0.0047685 | 0.00019074
2009 | 2008-12-20 | C | 1270 | 0.43467 | 0.0040373
2009 | 2008-12-20 | C | 203 | 0.037162 | 0.00064534
2009 | 2008-12-21 | C | 264 | 0.20939 | 0.00083925
2009 | 2008-12-21 | C | 42 | 0.0057413 | 0.00013352
2009 | 2008-12-21 | C | 54 | 0.010472 | 0.00017167
2009 | 2008-12-21 | C | 14 | 0.0025368 | 4.4506e-05
2009 | 2008-12-21 | C | 4 | 0.00094098 | 1.2716e-05
2009 | 2008-12-21 | C | 556 | 0.0088376 | 0.0017675
2009 | 2008-12-21 | C | 99 | 0.24591 | 0.00031472
2009 | 2008-12-22 | B | 6 | 0.00085833 | 1.9074e-05
2009 | 2008-12-22 | B | 1 | 0.00075978 | 3.179e-06
2009 | 2008-12-22 | C | 9 | 0.0018883 | 2.8611e-05
2009 | 2008-12-22 | B | 1 | 0.0013034 | 3.179e-06
2009 | 2008-12-22 | B | 166 | 0.0094988 | 0.00052771
2009 | 2008-12-22 | B | 105 | 0.050069 | 0.00033379
2009 | 2008-12-22 | C | 126 | 0.028039 | 0.00040055
2009 | 2008-12-22 | C | 43 | 0.019684 | 0.0001367
2009 | 2008-12-23 | B | 38 | 0.0002416 | 0.0001208
2009 | 2008-12-23 | C | 1 | 0.00049274 | 3.179e-06
2009 | 2008-12-23 | C | 4 | 0.00020346 | 1.2716e-05
2009 | 2008-12-23 | B | 17 | 0.0045396 | 5.4043e-05
2009 | 2008-12-23 | C | 10 | 0.0020028 | 3.179e-05
2009 | 2008-12-23 | C | 7 | 0.0024478 | 2.2253e-05
2009 | 2008-12-23 | B | 65 | 0.050625 | 0.00020663
2009 | 2008-12-23 | B | 56 | 0.026169 | 0.00017802
2009 | 2008-12-23 | C | 354 | 0.079042 | 0.0011254
2009 | 2008-12-23 | C | 79 | 0.027826 | 0.00025114
2009 | 2008-12-24 | C | 1765 | 0.084164 | 0.0056109
2009 | 2008-12-24 | C | 1670 | 0.28315 | 0.0053089
2009 | 2008-12-24 | C | 1384 | 0.41417 | 0.0043997
2009 | 2008-12-24 | C | 150 | 0.049195 | 0.00047685
2009 | 2008-12-25 | C | 6 | 0.002575 | 1.9074e-05
2009 | 2008-12-25 | C | 340 | 0.03858 | 0.0010809
2009 | 2008-12-25 | C | 269 | 0.083191 | 0.00085515
2009 | 2008-12-25 | C | 282 | 0.061609 | 0.00089648
2009 | 2008-12-26 | C | 103 | 0.01496 | 0.00032744
2009 | 2008-12-26 | C | 35 | 0.0064534 | 0.00011126
2009 | 2008-12-26 | C | 2 | 0.0061291 | 6.358e-06
2009 | 2008-12-26 | C | 329 | 0.056917 | 0.0010459
2009 | 2008-12-26 | C | 93 | 0.016852 | 0.00029565
2009 | 2008-12-26 | C | 2187 | 0.55104 | 0.0069525
2009 | 2008-12-27 | C | 946 | 0.027066 | 0.0030073
2009 | 2008-12-27 | C | 314 | 0.0069874 | 0.0009982
2009 | 2008-12-27 | C | 93 | 0.02306 | 0.00029565
2009 | 2008-12-26 | C | 79 | 0.0060274 | 0.00025114
2009 | 2008-12-27 | C | 229 | 0.24242 | 0.00072799
2009 | 2008-12-27 | C | 6 | 0.00013352 | 1.9074e-05
2009 | 2008-12-27 | C | 1 | 0.00094416 | 3.179e-06
2009 | 2008-12-28 | C | 260 | 0.10724 | 0.00082654
2009 | 2008-12-28 | C | 70 | 0.013797 | 0.00022253
2009 | 2008-12-28 | C | 31 | 0.013501 | 9.8549e-05
2009 | 2008-12-29 | C | 233 | 0.042961 | 0.00074071
2009 | 2008-12-29 | C | 1036 | 0.1648 | 0.0032934
2009 | 2008-12-29 | C | 250 | 0.050069 | 0.00079475
2009 | 2008-12-29 | C | 14 | 0.0011572 | 4.4506e-05
2009 | 2008-12-30 | C | 1 | 0.00056268 | 3.179e-06
2009 | 2008-12-30 | C | 647 | 0.10989 | 0.0020568
2009 | 2008-12-30 | C | 51 | 0.0012557 | 0.00016213
2009 | 2008-12-31 | B | 11 | 0.0010141 | 3.4969e-05
2009 | 2009-01-01 | C | 33 | 0.0017834 | 0.00010491
2009 | 2009-01-01 | C | 11 | 0.0037417 | 3.4969e-05
2009 | 2009-01-01 | C | 3 | 0.00020981 | 9.537e-06
2009 | 2009-01-01 | C | 127 | 0.02087 | 0.00040373
2009 | 2009-01-02 | C | 17 | 0.0049688 | 5.4043e-05
2009 | 2009-01-02 | C | 36 | 0.0019455 | 0.00011444
2009 | 2009-01-03 | C | 470 | 0.044341 | 0.0014941
2009 | 2009-01-03 | C | 1043 | 0.27749 | 0.0033157
2009 | 2009-01-03 | C | 26 | 0.024218 | 8.2654e-05
2009 | 2009-01-03 | C | 30 | 0.0031472 | 9.537e-05
2009 | 2009-01-03 | C | 309 | 0.078051 | 0.00098231
2009 | 2009-01-04 | C | 474 | 0.28646 | 0.0015068
2009 | 2009-01-04 | C | 8 | 0.0011444 | 2.5432e-05
2009 | 2009-01-04 | C | 310 | 0.065246 | 0.00098549
2009 | 2009-01-04 | C | 1951 | 0.32573 | 0.0062022
2009 | 2009-01-04 | B | 145 | 0.10141 | 0.00046095
2009 | 2009-01-05 | C | 18 | 0.0066377 | 5.7222e-05
2009 | 2009-01-06 | C | 111 | 0.005293 | 0.00035287
2009 | 2009-01-06 | C | 12 | 0.0035096 | 3.8148e-05
2009 | 2009-01-06 | B | 95 | 0.053455 | 0.000302
2009 | 2009-01-06 | C | 1202 | 0.25984 | 0.0038211
2009 | 2009-01-06 | B | 55 | 0.036193 | 0.00017484
2009 | 2009-01-06 | B | 41 | 0.03089 | 0.00013034
2009 | 2009-01-06 | B | 1 | 0.0011603 | 3.179e-06
2009 | 2009-01-06 | C | 276 | 0.14992 | 0.0008774
2009 | 2009-01-07 | B | 10 | 0.00085833 | 3.179e-05
2009 | 2009-01-07 | B | 13 | 0.012109 | 4.1327e-05
2009 | 2009-01-07 | B | 35 | 0.0097913 | 0.00011126
2009 | 2009-01-07 | B | 37 | 0.0083512 | 0.00011762
2009 | 2009-01-08 | B | 13 | 0.0073149 | 4.1327e-05
2009 | 2009-01-08 | B | 79 | 0.048219 | 0.00025114
2009 | 2009-01-08 | B | 34 | 0.037073 | 0.00010809
2009 | 2009-01-08 | B | 11 | 0.011819 | 3.4969e-05
2009 | 2009-01-08 | B | 19 | 0.0090601 | 6.0401e-05
2009 | 2009-01-08 | C | 32 | 0.0075279 | 0.00010173
2009 | 2009-01-08 | C | 50 | 0.043104 | 0.00015895
2009 | 2009-01-08 | B | 72 | 0.028611 | 0.00022889
2009 | 2009-01-09 | C | 282 | 0.097191 | 0.00089648
2009 | 2009-01-09 | C | 50 | 0.0034969 | 0.00015895
2009 | 2009-01-09 | B | 11 | 0.007833 | 3.4969e-05
2009 | 2009-01-09 | B | 13 | 0.0071082 | 4.1327e-05
2009 | 2009-01-10 | C | 710 | 0.031599 | 0.0022571
2009 | 2009-01-11 | B | 1 | 0.00019074 | 3.179e-06
2009 | 2009-01-11 | C | 78 | 0.02327 | 0.00024796
2009 | 2009-01-11 | C | 798 | 0.13384 | 0.0025368
2009 | 2009-01-11 | C | 9 | 0.0068952 | 2.8611e-05
2009 | 2009-01-11 | C | 5 | 0.01168 | 1.5895e-05
2009 | 2009-01-11 | C | 151 | 0.0057603 | 0.00048003
2009 | 2009-01-11 | C | 158 | 0.013059 | 0.00050228
2009 | 2009-01-09 | B | 1 | 0.00026704 | 3.179e-06
2009 | 2009-01-07 | B | 1 | 0.00037194 | 3.179e-06
2009 | 2009-01-12 | B | 132 | 0.028954 | 0.00041963
2009 | 2009-01-12 | B | 77 | 0.037207 | 0.00024478
2009 | 2009-01-12 | B | 32 | 0.0097659 | 0.00010173
2009 | 2009-01-12 | C | 158 | 0.025832 | 0.00050228
2009 | 2009-01-12 | B | 28 | 0.013085 | 8.9012e-05
2009 | 2009-01-13 | C | 95 | 0.0042281 | 0.000302
2009 | 2009-01-13 | B | 28 | 0.019316 | 8.9012e-05
2009 | 2009-01-13 | C | 339 | 0.054962 | 0.0010777
2009 | 2009-01-13 | C | 229 | 0.026936 | 0.00072799
2009 | 2009-01-13 | C | 460 | 0.017548 | 0.0014623
2009 | 2009-01-13 | C | 1610 | 0.37302 | 0.0051182
2009 | 2009-01-13 | C | 73 | 0.0088185 | 0.00023207
2009 | 2009-01-13 | C | 7 | 0.0081668 | 2.2253e-05
2009 | 2008-12-13 | B | 1 | 0.00021617 | 3.179e-06
2009 | 2009-01-13 | C | 163 | 0.050524 | 0.00051818
2009 | 2009-01-13 | C | 3 | 0.0029565 | 9.537e-06
2009 | 2009-01-13 | C | 1321 | 1.3799 | 0.0041995
2009 | 2009-01-13 | C | 130 | 0.0082654 | 0.00041327
2009 | 2009-01-14 | C | 91 | 0.0162 | 0.00028929
2009 | 2009-01-14 | C | 143 | 0.023184 | 0.0004546
2009 | 2009-01-14 | B | 3 | 0.00065805 | 9.537e-06
2009 | 2009-01-14 | B | 23 | 0.0020473 | 7.3117e-05
2009 | 2009-01-14 | C | 16 | 0.0013733 | 5.0864e-05
2009 | 2009-01-14 | B | 81 | 0.094502 | 0.0002575
2009 | 2009-01-14 | B | 49 | 0.05561 | 0.00015577
2009 | 2009-01-14 | B | 44 | 0.046718 | 0.00013988
2009 | 2009-01-02 | C | 12 | 0.00038148 | 3.8148e-05
2009 | 2009-01-14 | C | 291 | 0.0055505 | 0.00092509
2009 | 2009-01-14 | C | 143 | 0.027397 | 0.0004546
2009 | 2009-01-14 | C | 528 | 0.086291 | 0.0016785
2009 | 2009-01-15 | B | 350 | 0.19694 | 0.0011126
2009 | 2009-01-15 | C | 780 | 0.032235 | 0.0024796
2009 | 2009-01-15 | B | 67 | 0.066028 | 0.00021299
2009 | 2009-01-15 | B | 11 | 0.0069938 | 3.4969e-05
2009 | 2009-01-15 | B | 34 | 0.038587 | 0.00010809
2009 | 2009-01-15 | B | 4 | 0.0018692 | 1.2716e-05
2009 | 2009-01-15 | C | 110 | 0.13043 | 0.00034969
2009 | 2009-01-15 | C | 2 | 0.00026704 | 6.358e-06
2009 | 2009-01-15 | C | 50 | 0.0047685 | 0.00015895
2009 | 2009-01-15 | C | 1 | 0.00035605 | 3.179e-06
2009 | 2009-01-15 | C | 37 | 0.0067045 | 0.00011762
2009 | 2009-01-15 | C | 10 | 0.0010809 | 3.179e-05
2009 | 2009-01-14 | C | 162 | 0.077889 | 0.000515
2009 | 2009-01-15 | C | 16 | 0.0043743 | 5.0864e-05
2009 | 2009-01-15 | C | 411 | 0.016985 | 0.0013066
2009 | 2009-01-16 | B | 1 | 0.0010395 | 3.179e-06
2009 | 2009-01-16 | B | 15 | 0.019885 | 4.7685e-05
2009 | 2009-01-16 | B | 14 | 0.0078775 | 4.4506e-05
2009 | 2009-01-16 | C | 54 | 0.031294 | 0.00017167
2009 | 2009-01-17 | C | 4882 | 0.1898 | 0.01552
2009 | 2008-11-11 | C | 86 | 0.01963 | 0.00027339
2009 | 2009-01-18 | C | 595 | 0.17719 | 0.0018915
2009 | 2008-11-12 | C | 85 | 0.015943 | 0.00027021
2009 | 2009-01-18 | C | 70 | 0.0068984 | 0.00022253
2009 | 2009-01-18 | C | 7 | 0.0029819 | 2.2253e-05
2009 | 2009-01-18 | C | 765 | 0.068094 | 0.0024319
2009 | 2009-01-18 | C | 655 | 0.080905 | 0.0020822
2009 | 2009-01-18 | C | 463 | 0.10702 | 0.0014719
2009 | 2009-01-19 | C | 11 | 0.0014337 | 3.4969e-05
2009 | 2009-01-19 | B | 26 | 0.0061164 | 8.2654e-05
2009 | 2009-01-19 | B | 14 | 0.010548 | 4.4506e-05
2009 | 2009-01-19 | C | 21 | 0.010681 | 6.6759e-05
2009 | 2009-01-19 | C | 73 | 0.027848 | 0.00023207
2009 | 2009-01-19 | C | 347 | 0.078601 | 0.0011031
2009 | 2009-01-20 | C | 93 | 0.076572 | 0.00029565
2009 | 2009-01-20 | B | 161 | 0.20063 | 0.00051182
2009 | 2009-01-20 | B | 12 | 0.0075151 | 3.8148e-05
2009 | 2009-01-20 | B | 210 | 0.21163 | 0.00066759
2009 | 2009-01-20 | B | 123 | 0.15132 | 0.00039102
2009 | 2009-01-20 | B | 10 | 0.0094416 | 3.179e-05
2009 | 2009-01-20 | C | 1 | 0.00041963 | 3.179e-06
2009 | 2009-01-20 | C | 109 | 0.0090093 | 0.00034651
2009 | 2009-01-20 | C | 31 | 0.0015768 | 9.8549e-05
2009 | 2009-01-21 | C | 360 | 0.07477 | 0.0011444
2009 | 2009-01-21 | B | 24 | 0.025712 | 7.6296e-05
2009 | 2009-01-21 | B | 4 | 0.0026449 | 1.2716e-05
2009 | 2009-01-21 | B | 3 | 0.0030137 | 9.537e-06
2009 | 2009-01-21 | B | 41 | 0.046531 | 0.00013034
2009 | 2009-01-21 | C | 5766 | 0.31161 | 0.01833
2009 | 2009-01-21 | B | 19 | 0.0080333 | 6.0401e-05
2009 | 2009-01-21 | C | 60 | 0.012017 | 0.00019074
2009 | 2009-01-22 | B | 3 | 0.0013161 | 9.537e-06
2009 | 2009-01-22 | B | 19 | 0.018422 | 6.0401e-05
2009 | 2009-01-22 | B | 33 | 0.037452 | 0.00010491
2009 | 2009-01-22 | B | 72 | 0.085833 | 0.00022889
2009 | 2009-01-22 | B | 79 | 0.082123 | 0.00025114
2009 | 2009-01-22 | C | 53 | 0.0028643 | 0.00016849
2009 | 2009-01-22 | C | 60 | 0.0089648 | 0.00019074
2009 | 2009-01-22 | C | 379 | 0.027819 | 0.0012048
2009 | 2009-01-22 | C | 54 | 0.00206 | 0.00017167
2009 | 2009-01-23 | B | 119 | 0.066959 | 0.0003783
2009 | 2009-01-22 | B | 192 | 0.059206 | 0.00061037
2009 | 2009-01-22 | B | 1 | 0.00068984 | 3.179e-06
2009 | 2009-01-22 | C | 2206 | 0.40675 | 0.0070129
2009 | 2009-01-23 | B | 1 | 0.00056268 | 3.179e-06
2009 | 2009-01-23 | B | 8 | 0.0079348 | 2.5432e-05
2009 | 2009-01-23 | B | 32 | 0.037843 | 0.00010173
2009 | 2009-01-23 | B | 1 | 0.00059129 | 3.179e-06
2009 | 2009-01-23 | C | 49 | 0.0026481 | 0.00015577
2009 | 2009-01-24 | C | 462 | 0.02203 | 0.0014687
2009 | 2009-01-25 | C | 2772 | 0.025162 | 0.0088122
2009 | 2009-01-25 | B | 2 | 0.0006358 | 6.358e-06
2009 | 2009-01-25 | C | 462 | 0.013218 | 0.0014687
2009 | 2009-01-25 | C | 351 | 0.079933 | 0.0011158
2009 | 2009-01-26 | B | 1 | 0.0006358 | 3.179e-06
2009 | 2009-01-26 | C | 2 | 0.0010681 | 6.358e-06
2009 | 2009-01-26 | C | 1031 | 0.70095 | 0.0032775
2009 | 2009-01-27 | C | 1 | 0.00034015 | 3.179e-06
2009 | 2009-01-27 | B | 14 | 0.0053852 | 4.4506e-05
2009 | 2009-01-27 | B | 10 | 0.0067713 | 3.179e-05
2009 | 2009-01-27 | B | 81 | 0.053817 | 0.0002575
2009 | 2009-01-27 | C | 123 | 0.0074293 | 0.00039102
2009 | 2009-01-27 | B | 51 | 0.014916 | 0.00016213
2009 | 2009-01-27 | B | 35 | 0.01847 | 0.00011126
2009 | 2009-01-27 | B | 10 | 0.011349 | 3.179e-05
2009 | 2009-01-27 | B | 53 | 0.057285 | 0.00016849
2009 | 2009-01-27 | C | 117 | 0.018225 | 0.00037194
2009 | 2009-01-27 | C | 470 | 0.010459 | 0.0014941
2009 | 2009-01-27 | C | 10 | 0.00302 | 3.179e-05
2009 | 2009-01-28 | C | 285 | 0.001812 | 0.00090601
2009 | 2009-01-28 | C | 1061 | 0.12142 | 0.0033729
2009 | 2009-01-28 | B | 1 | 0.00048003 | 3.179e-06
2009 | 2009-01-28 | C | 123 | 0.0093844 | 0.00039102
2009 | 2009-01-28 | B | 62 | 0.068393 | 0.0001971
2009 | 2009-01-28 | B | 145 | 0.10694 | 0.00046095
2009 | 2009-01-28 | B | 33 | 0.03934 | 0.00010491
2009 | 2009-01-28 | B | 24 | 0.01709 | 7.6296e-05
2009 | 2009-01-28 | B | 322 | 0.38489 | 0.0010236
2009 | 2009-01-28 | C | 444 | 0.075269 | 0.0014115
2009 | 2009-01-29 | B | 46 | 0.0084816 | 0.00014623
2009 | 2009-01-29 | B | 58 | 0.028198 | 0.00018438
2009 | 2009-01-29 | B | 34 | 0.040532 | 0.00010809
2009 | 2009-01-29 | B | 220 | 0.23989 | 0.00069938
2009 | 2009-01-29 | B | 6 | 0.0046922 | 1.9074e-05
2009 | 2009-01-29 | C | 724 | 0.043975 | 0.0023016
2009 | 2009-01-29 | B | 3 | 0.00065805 | 9.537e-06
2009 | 2009-01-28 | C | 353 | 0.013466 | 0.0011222
2009 | 2009-01-20 | B | 2 | 0.00045778 | 6.358e-06
2009 | 2009-01-30 | B | 11 | 0.011435 | 3.4969e-05
2009 | 2009-01-30 | B | 3 | 0.0030041 | 9.537e-06
2009 | 2009-01-30 | B | 12 | 0.014611 | 3.8148e-05
2009 | 2009-01-29 | B | 78 | 0.095713 | 0.00024796
2009 | 2009-01-29 | B | 208 | 0.3035 | 0.00066123
2009 | 2009-01-30 | C | 285 | 0.049258 | 0.00090601
2009 | 2009-01-31 | C | 5259 | 1.531 | 0.016718
2009 | 2009-01-31 | C | 328 | 0.0075374 | 0.0010427
2009 | 2009-02-01 | C | 250 | 0.012716 | 0.00079475
2009 | 2009-02-01 | C | 238 | 0.054911 | 0.0007566
2009 | 2009-01-31 | C | 1 | 0.0030645 | 3.179e-06
2009 | 2009-02-01 | C | 166 | 0.022692 | 0.00052771
2009 | 2009-02-01 | C | 271 | 0.068921 | 0.00086151
2009 | 2009-02-02 | C | 72 | 0.018082 | 0.00022889
2009 | 2009-02-01 | C | 44 | 0.12227 | 0.00013988
2009 | 2009-01-31 | C | 657 | 0.25588 | 0.0020886
2009 | 2009-02-02 | B | 2 | 0.0019773 | 6.358e-06
2009 | 2009-02-02 | B | 93 | 0.020059 | 0.00029565
2009 | 2009-02-02 | B | 73 | 0.016013 | 0.00023207
2009 | 2009-02-02 | B | 7 | 0.0079443 | 2.2253e-05
2009 | 2009-02-03 | B | 4 | 0.0020854 | 1.2716e-05
2009 | 2009-02-03 | B | 40 | 0.036495 | 0.00012716
2009 | 2009-02-03 | B | 224 | 0.23642 | 0.00071209
2009 | 2009-02-03 | B | 10 | 0.011921 | 3.179e-05
2009 | 2009-02-03 | B | 148 | 0.1308 | 0.00047049
2009 | 2009-02-03 | B | 8 | 0.0080111 | 2.5432e-05
2009 | 2009-02-03 | B | 2 | 0.0020473 | 6.358e-06
2009 | 2009-02-03 | C | 16 | 0.0036113 | 5.0864e-05
2009 | 2009-02-03 | C | 208 | 0.050247 | 0.00066123
2009 | 2009-02-02 | C | 1192 | 0.4625 | 0.0037894
2009 | 2009-02-04 | C | 33 | 0.0063993 | 0.00010491
2009 | 2009-02-04 | B | 8 | 0.0075533 | 2.5432e-05
2009 | 2009-02-04 | C | 565 | 0.15241 | 0.0017961
2009 | 2009-02-04 | B | 10 | 0.010395 | 3.179e-05
2009 | 2009-02-04 | B | 54 | 0.034161 | 0.00017167
2009 | 2009-02-03 | C | 1 | 0.00013352 | 3.179e-06
2009 | 2009-02-03 | C | 251 | 0.061167 | 0.00079793
2009 | 2009-02-04 | B | 2 | 0.0025305 | 6.358e-06
2009 | 2009-02-04 | C | 55 | 0.0027975 | 0.00017484
2009 | 2009-02-05 | B | 395 | 0.39806 | 0.0012557
2009 | 2009-02-05 | B | 3 | 0.00088694 | 9.537e-06
2009 | 2009-02-05 | C | 114 | 0.010147 | 0.00036241
2009 | 2009-02-05 | B | 4 | 0.0047939 | 1.2716e-05
2009 | 2009-02-05 | B | 56 | 0.055187 | 0.00017802
2009 | 2009-02-05 | B | 3 | 0.0031186 | 9.537e-06
2009 | 2009-02-06 | C | 151 | 0.0067204 | 0.00048003
2009 | 2009-02-06 | C | 19 | 0.0041677 | 6.0401e-05
2009 | 2009-02-07 | C | 5 | 0.0021458 | 1.5895e-05
2009 | 2009-02-07 | B | 10 | 0.00047685 | 3.179e-05
2009 | 2009-02-07 | C | 1 | 0.00032426 | 3.179e-06
2009 | 2009-02-07 | C | 1 | 0.000302 | 3.179e-06
2009 | 2009-02-06 | C | 375 | 0.01669 | 0.0011921
2009 | 2009-02-06 | C | 1028 | 0.3011 | 0.003268
2009 | 2009-02-08 | C | 259 | 0.0057635 | 0.00082336
2009 | 2009-02-09 | B | 39 | 0.025416 | 0.00012398
2009 | 2009-02-09 | C | 52 | 0.0072735 | 0.00016531
2009 | 2009-02-09 | B | 5 | 0.0032108 | 1.5895e-05
2009 | 2009-02-09 | C | 1 | 5.0864e-05 | 3.179e-06
2009 | 2009-02-09 | C | 816 | 0.16861 | 0.0025941
2009 | 2009-02-09 | C | 183 | 0.0040723 | 0.00058176
2009 | 2009-02-10 | C | 85 | 0.028643 | 0.00027021
2009 | 2009-02-09 | C | 202 | 0.057149 | 0.00064216
2009 | 2009-02-10 | C | 104 | 0.040996 | 0.00033062
2009 | 2009-02-10 | B | 47 | 0.026446 | 0.00014941
2009 | 2009-02-10 | B | 16 | 0.0118 | 5.0864e-05
2009 | 2009-02-10 | B | 55 | 0.034969 | 0.00017484
2009 | 2009-02-10 | C | 1 | 0.00055314 | 3.179e-06
2009 | 2009-02-10 | B | 31 | 0.032127 | 9.8549e-05
2009 | 2009-02-10 | B | 94 | 0.065742 | 0.00029883
2009 | 2009-02-10 | B | 16 | 0.010834 | 5.0864e-05
2009 | 2009-02-09 | C | 14 | 0.043972 | 4.4506e-05
2009 | 2009-02-10 | C | 29 | 0.0066377 | 9.2191e-05
2009 | 2009-02-10 | C | 9 | 0.0019455 | 2.8611e-05
2009 | 2009-02-10 | C | 99 | 0.025168 | 0.00031472
2009 | 2009-02-10 | C | 491 | 0.086701 | 0.0015609
2009 | 2009-02-10 | C | 287 | 0.074853 | 0.00091237
2009 | 2009-02-10 | C | 103 | 0.035036 | 0.00032744
2009 | 2009-02-10 | C | 6 | 0.00099185 | 1.9074e-05
2009 | 2009-02-10 | C | 437 | 0.024685 | 0.0013892
2009 | 2009-02-11 | C | 132 | 0.021821 | 0.00041963
2009 | 2009-02-10 | C | 112 | 0.0056968 | 0.00035605
2009 | 2009-02-11 | B | 157 | 0.033939 | 0.0004991
2009 | 2009-02-11 | B | 1 | 0.00067077 | 3.179e-06
2009 | 2009-02-11 | B | 59 | 0.059082 | 0.00018756
2009 | 2009-02-11 | B | 97 | 0.12149 | 0.00030836
2009 | 2009-02-11 | B | 25 | 0.018677 | 7.9475e-05
2009 | 2009-02-11 | B | 24 | 0.015946 | 7.6296e-05
2009 | 2009-02-11 | B | 39 | 0.041038 | 0.00012398
2009 | 2009-02-12 | C | 698 | 0.017751 | 0.0022189
2009 | 2008-09-27 | C | 1340 | 0.20618 | 0.0042599
2009 | 2009-02-12 | B | 30 | 0.014115 | 9.537e-05
2009 | 2009-02-16 | B | 2 | 0.0013352 | 6.358e-06
2009 | 2008-12-09 | C | 120 | 0.0045778 | 0.00038148
2009 | 2009-02-12 | C | 267 | 0.07071 | 0.00084879
2009 | 2009-02-12 | C | 184 | 0.030585 | 0.00058493
2009 | 2009-02-12 | C | 163 | 0.026535 | 0.00051818
2009 | 2009-02-12 | C | 5 | 0.00038148 | 1.5895e-05
2009 | 2009-02-12 | B | 1 | 0.00020346 | 3.179e-06
2009 | 2009-02-12 | C | 709 | 0.17873 | 0.0022539
2009 | 2009-02-13 | B | 1 | 0.00020981 | 3.179e-06
2009 | 2009-02-12 | C | 283 | 0.042726 | 0.00089966
2009 | 2009-02-13 | C | 459 | 0.030378 | 0.0014592
2009 | 2009-02-12 | B | 108 | 0.066416 | 0.00034333
2009 | 2009-02-12 | C | 677 | 0.25256 | 0.0021522
2009 | 2009-02-13 | C | 158 | 0.094429 | 0.00050228
2009 | 2009-02-13 | B | 7 | 0.0039388 | 2.2253e-05
2009 | 2009-02-13 | B | 8 | 0.0060782 | 2.5432e-05
2009 | 2009-02-13 | C | 19 | 0.00036241 | 6.0401e-05
2009 | 2009-02-13 | B | 1 | 0.00026386 | 3.179e-06
2009 | 2009-02-13 | B | 56 | 0.056968 | 0.00017802
2009 | 2009-02-13 | C | 120 | 0.0015259 | 0.00038148
2009 | 2009-02-13 | B | 1 | 0.00091237 | 3.179e-06
2009 | 2009-02-13 | B | 78 | 0.061494 | 0.00024796
2009 | 2009-02-13 | C | 158 | 0.12005 | 0.00050228
2009 | 2009-02-13 | C | 12 | 0.0033189 | 3.8148e-05
2009 | 2009-02-13 | C | 15 | 0.0035287 | 4.7685e-05
2009 | 2009-02-14 | C | 602 | 0.12822 | 0.0019138
2009 | 2009-02-14 | C | 31 | 0.0072926 | 9.8549e-05
2009 | 2009-02-14 | C | 25 | 0.0071972 | 7.9475e-05
2009 | 2009-02-15 | C | 79 | 0.065799 | 0.00025114
2009 | 2009-02-16 | B | 7 | 0.0081891 | 2.2253e-05
2009 | 2009-02-16 | C | 37 | 0.0031758 | 0.00011762
2009 | 2009-02-16 | B | 3 | 0.0029088 | 9.537e-06
2009 | 2009-02-16 | C | 2 | 0.00040691 | 6.358e-06
2009 | 2009-02-16 | B | 1 | 0.00029247 | 3.179e-06
2009 | 2009-02-17 | C | 13 | 0.008472 | 4.1327e-05
2009 | 2009-02-17 | C | 20 | 0.004387 | 6.358e-05
2009 | 2009-02-17 | C | 13 | 0.0019424 | 4.1327e-05
2009 | 2009-02-17 | C | 208 | 0.037827 | 0.00066123
2009 | 2009-02-17 | B | 8 | 0.0051373 | 2.5432e-05
2009 | 2009-02-17 | B | 20 | 0.022126 | 6.358e-05
2009 | 2009-02-17 | B | 8 | 0.0068666 | 2.5432e-05
2009 | 2009-02-17 | B | 322 | 0.27741 | 0.0010236
2009 | 2009-02-17 | C | 10 | 0.011031 | 3.179e-05
2009 | 2009-02-17 | C | 290 | 0.054297 | 0.00092191
2009 | 2009-02-18 | C | 6 | 0.00064851 | 1.9074e-05
2009 | 2009-02-18 | B | 9 | 0.0014305 | 2.8611e-05
2009 | 2009-02-18 | B | 32 | 0.034282 | 0.00010173
2009 | 2009-02-18 | B | 11 | 0.01161 | 3.4969e-05
2009 | 2009-02-18 | B | 274 | 0.18493 | 0.00087104
2009 | 2009-02-18 | B | 41 | 0.049659 | 0.00013034
2009 | 2009-02-18 | B | 1 | 0.0012811 | 3.179e-06
2009 | 2009-02-18 | B | 2 | 0.0017039 | 6.358e-06
2009 | 2009-02-18 | B | 58 | 0.036139 | 0.00018438
2009 | 2009-02-18 | B | 211 | 0.0065583 | 0.00067077
2009 | 2009-02-18 | B | 21 | 0.02884 | 6.6759e-05
2009 | 2009-02-18 | C | 85 | 0.0029724 | 0.00027021
2009 | 2009-02-19 | C | 458 | 0.046016 | 0.001456
2009 | 2009-02-19 | B | 2 | 0.0010681 | 6.358e-06
2009 | 2009-02-19 | B | 100 | 0.056268 | 0.0003179
2009 | 2009-02-19 | B | 48 | 0.039826 | 0.00015259
2009 | 2009-02-19 | C | 43 | 0.018864 | 0.0001367
2009 | 2009-02-19 | B | 24 | 0.024415 | 7.6296e-05
2009 | 2009-02-19 | B | 4 | 0.0032553 | 1.2716e-05
2009 | 2009-02-19 | B | 21 | 0.016957 | 6.6759e-05
2009 | 2009-02-19 | B | 43 | 0.021051 | 0.0001367
2009 | 2009-02-19 | B | 211 | 0.039575 | 0.00067077
2009 | 2009-02-19 | C | 21 | 0.0018025 | 6.6759e-05
2009 | 2009-02-19 | B | 59 | 0.024758 | 0.00018756
2009 | 2009-02-20 | B | 280 | 0.21096 | 0.00089012
2009 | 2009-02-20 | C | 600 | 0.032426 | 0.0019074
2009 | 2009-02-20 | C | 991 | 0.11465 | 0.0031504
2009 | 2009-02-20 | C | 17 | 0.0023238 | 5.4043e-05
2009 | 2009-02-20 | B | 1 | 0.000515 | 3.179e-06
2009 | 2009-02-20 | C | 853 | 0.22755 | 0.0027117
2009 | 2009-02-20 | C | 35 | 0.0055632 | 0.00011126
2009 | 2009-02-20 | C | 51 | 0.0064851 | 0.00016213
2009 | 2009-02-20 | C | 345 | 0.35864 | 0.0010968
2009 | 2009-02-20 | C | 72 | 0.0016022 | 0.00022889
2009 | 2009-02-20 | C | 248 | 0.26758 | 0.00078839
2009 | 2009-02-20 | C | 211 | 0.0646 | 0.00067077
2009 | 2009-02-20 | C | 41 | 0.010297 | 0.00013034
2009 | 2009-02-20 | C | 463 | 0.60012 | 0.0014719
2009 | 2009-02-20 | C | 346 | 0.34089 | 0.0010999
2009 | 2009-02-20 | C | 3704 | 0.07065 | 0.011775
2009 | 2009-02-20 | C | 72 | 0.0043489 | 0.00022889
2009 | 2009-02-20 | C | 24 | 0.00083925 | 7.6296e-05
2009 | 2009-02-20 | C | 120 | 0.050355 | 0.00038148
2009 | 2009-02-20 | C | 57 | 0.0043489 | 0.0001812
2009 | 2009-02-20 | C | 19 | 0.002416 | 6.0401e-05
2009 | 2009-02-20 | C | 1029 | 0.44815 | 0.0032712
2009 | 2009-02-20 | C | 498 | 0.096082 | 0.0015831
2009 | 2009-02-20 | C | 449 | 0.079631 | 0.0014274
2009 | 2009-02-21 | C | 2841 | 0.15685 | 0.0090315
2009 | 2009-02-21 | C | 454 | 0.13069 | 0.0014433
2009 | 2009-02-22 | C | 436 | 0.020791 | 0.001386
2009 | 2009-02-20 | C | 461 | 0.16744 | 0.0014655
2009 | 2009-02-20 | C | 1773 | 0.95254 | 0.0056364
2009 | 2009-02-20 | C | 952 | 0.6918 | 0.0030264
2009 | 2009-02-21 | C | 22 | 0.021261 | 6.9938e-05
2009 | 2009-02-21 | C | 2 | 0.00022253 | 6.358e-06
2009 | 2009-02-22 | C | 4 | 0.0011063 | 1.2716e-05
2009 | 2009-02-22 | C | 1 | 7.6296e-05 | 3.179e-06
2009 | 2009-02-22 | C | 285 | 0.039162 | 0.00090601
2009 | 2009-02-23 | B | 2 | 0.0024351 | 6.358e-06
2009 | 2009-02-23 | B | 1 | 0.00059765 | 3.179e-06
2009 | 2009-02-23 | B | 35 | 0.019694 | 0.00011126
2009 | 2009-02-23 | C | 21 | 0.0028706 | 6.6759e-05
2009 | 2009-02-23 | C | 71 | 0.024981 | 0.00022571
2009 | 2009-02-23 | C | 2286 | 0.10901 | 0.0072672
2009 | 2009-02-23 | B | 1 | 0.00091237 | 3.179e-06
2009 | 2009-02-23 | B | 1 | 0.0011444 | 3.179e-06
2009 | 2009-02-23 | C | 1 | 0.00039737 | 3.179e-06
2009 | 2009-02-22 | C | 3704 | 0.02355 | 0.011775
2009 | 2009-02-24 | B | 45 | 0.012446 | 0.00014305
2009 | 2009-02-24 | B | 38 | 0.027301 | 0.0001208
2009 | 2009-02-24 | B | 173 | 0.17434 | 0.00054997
2009 | 2009-02-24 | B | 2 | 0.0010618 | 6.358e-06
2009 | 2009-02-24 | C | 58 | 0.016207 | 0.00018438
2009 | 2009-02-24 | B | 135 | 0.078108 | 0.00042916
2009 | 2009-02-24 | B | 32 | 0.020651 | 0.00010173
2009 | 2009-02-24 | B | 8 | 0.0065869 | 2.5432e-05
2009 | 2009-02-24 | C | 2 | 0.00075024 | 6.358e-06
2009 | 2009-02-24 | B | 1786 | 0.12144 | 0.0056777
2009 | 2009-02-24 | C | 141 | 0.021067 | 0.00044824
2009 | 2009-02-24 | C | 444 | 0.1252 | 0.0014115
2009 | 2009-02-25 | B | 2 | 0.0016976 | 6.358e-06
2009 | 2009-02-25 | B | 13 | 0.010208 | 4.1327e-05
2009 | 2009-02-25 | B | 47 | 0.027641 | 0.00014941
2009 | 2009-02-25 | B | 20 | 0.024033 | 6.358e-05
2009 | 2009-02-25 | C | 410 | 0.057349 | 0.0013034
2009 | 2009-02-25 | C | 360 | 0.018311 | 0.0011444
2009 | 2009-02-26 | B | 1 | 0.00074706 | 3.179e-06
2009 | 2009-02-26 | C | 3 | 0.00033379 | 9.537e-06
2009 | 2009-02-26 | B | 8 | 0.010096 | 2.5432e-05
2009 | 2009-02-26 | B | 146 | 0.043164 | 0.00046413
2009 | 2009-02-26 | B | 99 | 0.034305 | 0.00031472
2009 | 2009-02-26 | B | 5 | 0.0048162 | 1.5895e-05
2009 | 2009-02-26 | C | 57 | 0.0079729 | 0.0001812
2009 | 2009-02-26 | B | 201 | 0.14507 | 0.00063898
2009 | 2009-02-26 | B | 16 | 0.0030518 | 5.0864e-05
2009 | 2009-02-27 | C | 1 | 2.2253e-05 | 3.179e-06
2009 | 2009-02-27 | B | 2 | 0.0014496 | 6.358e-06
2009 | 2009-02-27 | C | 3 | 0.00017167 | 9.537e-06
2009 | 2009-02-27 | B | 4 | 0.0027594 | 1.2716e-05
2009 | 2009-02-28 | C | 72 | 0.00206 | 0.00022889
2009 | 2009-02-28 | C | 33 | 0.0023079 | 0.00010491
2009 | 2009-02-28 | C | 301 | 0.097601 | 0.00095688
2009 | 2009-02-28 | C | 111 | 0.0067045 | 0.00035287
2009 | 2009-02-28 | C | 111 | 0.008116 | 0.00035287
2009 | 2009-02-28 | C | 143 | 0.0063643 | 0.0004546
2009 | 2009-02-28 | C | 29 | 0.0013829 | 9.2191e-05
2009 | 2009-02-28 | C | 248 | 0.039264 | 0.00078839
2009 | 2008-12-09 | C | 120 | 0.078585 | 0.00038148
2009 | 2009-02-28 | C | 1030 | 0.23248 | 0.0032744
2009 | 2009-02-28 | C | 247 | 0.31111 | 0.00078521
2009 | 2009-02-28 | C | 325 | 0.12088 | 0.0010332
2009 | 2009-02-28 | C | 262 | 0.032483 | 0.0008329
2009 | 2009-02-28 | C | 777 | 0.27712 | 0.0024701
2009 | 2008-06-27 | C | 72 | 0.016709 | 0.00022889
2009 | 2009-02-28 | C | 951 | 0.16144 | 0.0030232
2009 | 2009-02-28 | C | 37 | 0.0037639 | 0.00011762
2009 | 2009-02-28 | C | 64 | 0.008507 | 0.00020346
2009 | 2009-02-28 | C | 369 | 0.037538 | 0.001173
2009 | 2009-02-28 | C | 419 | 0.19505 | 0.001332
2009 | 2009-02-28 | C | 351 | 0.10296 | 0.0011158
2009 | 2009-02-28 | C | 11 | 0.00080429 | 3.4969e-05
2009 | 2009-02-28 | C | 855 | 0.25735 | 0.002718
2009 | 2009-02-28 | C | 159 | 0.064391 | 0.00050546
2009 | 2009-02-28 | C | 747 | 0.064982 | 0.0023747
2009 | 2009-02-28 | C | 402 | 0.057788 | 0.001278
2009 | 2008-06-27 | C | 76 | 0.070993 | 0.0002416
2009 | 2009-02-28 | C | 21 | 0.0082781 | 6.6759e-05
2009 | 2009-02-28 | C | 69 | 0.0048257 | 0.00021935
2009 | 2009-02-28 | C | 1306 | 0.17114 | 0.0041518
2009 | 2009-02-28 | C | 98 | 0.21247 | 0.00031154
2009 | 2009-02-28 | C | 27 | 0.0070383 | 8.5833e-05
2009 | 2009-02-28 | C | 157 | 0.12637 | 0.0004991
2009 | 2009-02-28 | C | 1282 | 0.4788 | 0.0040755
2009 | 2009-02-28 | C | 266 | 0.14375 | 0.00084561
2009 | 2009-02-28 | C | 259 | 0.22725 | 0.00082336
2009 | 2009-02-28 | C | 334 | 0.15954 | 0.0010618
2009 | 2009-02-28 | C | 240 | 0.069773 | 0.00076296
2009 | 2009-02-28 | C | 175 | 0.032903 | 0.00055632
2009 | 2009-02-28 | C | 485 | 0.074007 | 0.0015418
2009 | 2009-02-28 | C | 56 | 0.12907 | 0.00017802
2009 | 2009-02-28 | C | 14 | 0.003872 | 4.4506e-05
2009 | 2009-02-28 | C | 185 | 0.063669 | 0.00058811
2009 | 2009-02-28 | C | 210 | 0.079262 | 0.00066759
2009 | 2009-03-01 | C | 11 | 0.0023429 | 3.4969e-05
2009 | 2009-03-01 | C | 2 | 1.9074e-05 | 6.358e-06
2009 | 2009-03-01 | C | 83 | 0.009235 | 0.00026386
2009 | 2009-02-28 | C | 2 | 0.0042217 | 6.358e-06
2009 | 2009-03-01 | C | 1 | 0.00035605 | 3.179e-06
2009 | 2009-03-01 | C | 522 | 0.13815 | 0.0016594
2009 | 2009-03-01 | B | 2 | 0.00031154 | 6.358e-06
2009 | 2009-03-01 | C | 1 | 0.00046731 | 3.179e-06
2009 | 2009-03-02 | B | 7 | 0.0014464 | 2.2253e-05
2009 | 2009-03-02 | C | 566 | 0.02519 | 0.0017993
2009 | 2009-03-01 | B | 1 | 0.0001812 | 3.179e-06
2009 | 2009-03-02 | B | 26 | 0.017109 | 8.2654e-05
2009 | 2009-03-02 | C | 146 | 0.0043171 | 0.00046413
2009 | 2009-03-02 | B | 7 | 0.0011794 | 2.2253e-05
2009 | 2009-03-02 | B | 7 | 0.0011572 | 2.2253e-05
2009 | 2009-03-02 | C | 433 | 0.046569 | 0.0013765
2009 | 2009-03-03 | C | 153 | 0.053321 | 0.00048639
2009 | 2009-03-02 | C | 399 | 0.034247 | 0.0012684
2009 | 2009-03-02 | B | 78 | 0.053064 | 0.00024796
2009 | 2009-03-03 | B | 33 | 0.029584 | 0.00010491
2009 | 2009-03-03 | B | 172 | 0.15255 | 0.00054679
2009 | 2009-03-03 | B | 6 | 0.0052835 | 1.9074e-05
2009 | 2009-03-03 | B | 47 | 0.052593 | 0.00014941
2009 | 2009-03-03 | B | 1 | 0.00094098 | 3.179e-06
2009 | 2009-03-03 | B | 9 | 0.0081255 | 2.8611e-05
2009 | 2009-03-03 | B | 2 | 0.00031154 | 6.358e-06
2009 | 2009-03-03 | B | 71 | 0.032502 | 0.00022571
2009 | 2009-03-03 | B | 69 | 0.030051 | 0.00021935
2009 | 2009-03-03 | B | 62 | 0.060903 | 0.0001971
2009 | 2009-03-02 | B | 123 | 0.035287 | 0.00039102
2009 | 2009-03-04 | C | 86 | 0.032957 | 0.00027339
2009 | 2009-03-02 | B | 27 | 0.0090983 | 8.5833e-05
2009 | 2009-03-03 | B | 18 | 0.020199 | 5.7222e-05
2009 | 2009-03-04 | B | 63 | 0.028239 | 0.00020028
2009 | 2009-03-04 | B | 1 | 0.00056904 | 3.179e-06
2009 | 2009-03-04 | B | 13 | 0.010952 | 4.1327e-05
2009 | 2009-03-04 | B | 60 | 0.070001 | 0.00019074
2009 | 2009-03-04 | C | 80 | 0.032604 | 0.00025432
2009 | 2009-03-04 | B | 1 | 0.00097913 | 3.179e-06
2009 | 2009-03-04 | B | 2 | 0.002238 | 6.358e-06
2009 | 2009-03-04 | B | 8 | 0.01353 | 2.5432e-05
2009 | 2009-03-04 | C | 163 | 0.077262 | 0.00051818
2009 | 2009-03-05 | B | 10 | 0.0095688 | 3.179e-05
2009 | 2009-03-05 | C | 45 | 0.0022889 | 0.00014305
2009 | 2009-03-05 | C | 19 | 0.0022348 | 6.0401e-05
2009 | 2009-03-05 | C | 14 | 0.0068539 | 4.4506e-05
2009 | 2009-03-05 | B | 30 | 0.026036 | 9.537e-05
2009 | 2009-03-05 | B | 12 | 0.016175 | 3.8148e-05
2009 | 2009-03-05 | B | 7 | 0.0076105 | 2.2253e-05
2009 | 2009-03-05 | C | 1030 | 0.37983 | 0.0032744
2009 | 2009-03-05 | C | 98 | 0.026316 | 0.00031154
2009 | 2009-03-06 | B | 62 | 0.035872 | 0.0001971
2009 | 2009-03-06 | C | 414 | 0.11744 | 0.0013161
2009 | 2009-03-06 | C | 133 | 0.031717 | 0.00042281
2009 | 2009-03-06 | C | 3 | 0.00085833 | 9.537e-06
2009 | 2009-03-06 | C | 36 | 0.00309 | 0.00011444
2009 | 2009-03-06 | B | 28 | 0.019049 | 8.9012e-05
2009 | 2009-03-06 | C | 1251 | 0.41255 | 0.0039769
2009 | 2009-03-06 | C | 1096 | 0.10104 | 0.0034842
2009 | 2009-03-07 | C | 650 | 0.24993 | 0.0020663
2009 | 2009-03-07 | C | 199 | 0.0056936 | 0.00063262
2009 | 2009-03-08 | C | 201 | 0.053986 | 0.00063898
2009 | 2009-03-08 | C | 859 | 0.16931 | 0.0027308
2009 | 2009-03-08 | C | 164 | 0.020546 | 0.00052135
2009 | 2009-03-07 | C | 232 | 0.1239 | 0.00073753
2009 | 2009-03-14 | C | 488 | 0.044989 | 0.0015513
2009 | 2009-03-09 | C | 743 | 0.085613 | 0.002362
2009 | 2009-03-09 | B | 2 | 0.00017802 | 6.358e-06
2009 | 2009-03-09 | B | 184 | 0.056182 | 0.00058493
2009 | 2009-03-09 | B | 68 | 0.037042 | 0.00021617
2009 | 2009-03-06 | B | 11 | 0.011505 | 3.4969e-05
2009 | 2009-03-09 | B | 9 | 0.004635 | 2.8611e-05
2009 | 2009-03-09 | B | 120 | 0.067522 | 0.00038148
2009 | 2009-03-09 | C | 29 | 0.0029501 | 9.2191e-05
2009 | 2009-03-14 | C | 471 | 0.11863 | 0.0014973
2009 | 2009-03-09 | C | 2420 | 0.015386 | 0.0076932
2009 | 2009-03-09 | C | 7 | 0.0035986 | 2.2253e-05
2009 | 2009-03-09 | C | 39 | 0.0054552 | 0.00012398
2009 | 2009-03-10 | B | 319 | 0.0020282 | 0.0010141
2009 | 2009-03-10 | B | 44 | 0.049936 | 0.00013988
2009 | 2009-03-10 | B | 224 | 0.29694 | 0.00071209
2009 | 2009-03-10 | B | 18 | 0.020257 | 5.7222e-05
2009 | 2009-03-10 | B | 175 | 0.10793 | 0.00055632
2009 | 2009-03-10 | B | 1 | 0.00041009 | 3.179e-06
2009 | 2009-03-10 | B | 37 | 0.0039992 | 0.00011762
2009 | 2009-03-10 | C | 132 | 0.029374 | 0.00041963
2009 | 2009-03-10 | C | 109 | 0.018712 | 0.00034651
2009 | 2009-03-10 | C | 864 | 0.10987 | 0.0027467
2009 | 2009-03-10 | C | 624 | 0.065554 | 0.0019837
2009 | 2009-03-10 | C | 45 | 0.14549 | 0.00014305
2009 | 2009-03-10 | C | 807 | 0.15385 | 0.0025654
2009 | 2009-03-10 | C | 720 | 0.20265 | 0.0022889
2009 | 2009-03-10 | C | 155 | 0.067617 | 0.00049274
2009 | 2009-03-10 | C | 213 | 0.15733 | 0.00067713
2009 | 2009-03-10 | C | 132 | 0.027174 | 0.00041963
2009 | 2009-03-11 | B | 1 | 0.0010268 | 3.179e-06
2009 | 2009-03-11 | C | 1307 | 0.054014 | 0.0041549
2009 | 2009-03-11 | C | 13 | 0.012481 | 4.1327e-05
2009 | 2009-03-11 | C | 55 | 0.0064693 | 0.00017484
2009 | 2009-03-11 | C | 25 | 0.0078839 | 7.9475e-05
2009 | 2009-03-11 | C | 3706 | 0.25919 | 0.011781
2009 | 2009-03-11 | C | 2210 | 0.11241 | 0.0070256
2009 | 2009-03-11 | B | 144 | 0.075991 | 0.00045778
2009 | 2009-03-11 | B | 1 | 0.0007566 | 3.179e-06
2009 | 2009-03-11 | B | 31 | 0.0069525 | 9.8549e-05
2009 | 2009-03-11 | C | 488 | 0.021719 | 0.0015513
2009 | 2009-03-11 | C | 1470 | 0.1968 | 0.0046731
2009 | 2009-03-12 | B | 319 | 0.0091269 | 0.0010141
2009 | 2009-03-11 | C | 24 | 0.0015259 | 7.6296e-05
2009 | 2009-03-11 | C | 216 | 0.11024 | 0.00068666
2009 | 2009-03-11 | C | 7992 | 0.30488 | 0.025407
2009 | 2009-03-11 | C | 1549 | 0.24567 | 0.0049243
2009 | 2009-03-12 | C | 15 | 0.0012875 | 4.7685e-05
2009 | 2009-03-12 | B | 1 | 0.00075342 | 3.179e-06
2009 | 2009-03-12 | B | 10 | 0.0065805 | 3.179e-05
2009 | 2009-03-12 | B | 13 | 0.0060751 | 4.1327e-05
2009 | 2009-03-12 | B | 24 | 0.022278 | 7.6296e-05
2009 | 2009-03-12 | B | 16 | 0.018158 | 5.0864e-05
2009 | 2009-03-12 | B | 93 | 0.091059 | 0.00029565
2009 | 2009-03-12 | C | 10 | 0.0023525 | 3.179e-05
2009 | 2009-03-12 | B | 33 | 0.034829 | 0.00010491
2009 | 2009-03-12 | C | 11 | 0.00041963 | 3.4969e-05
2009 | 2009-03-12 | C | 1254 | 0.23925 | 0.0039865
2009 | 2009-03-12 | C | 93 | 0.032817 | 0.00029565
2009 | 2009-03-12 | C | 215 | 0.044204 | 0.00068348
2009 | 2009-03-11 | C | 163 | 0.047771 | 0.00051818
2009 | 2009-03-11 | C | 260 | 0.078063 | 0.00082654
2009 | 2009-03-13 | C | 45 | 0.0044347 | 0.00014305
2009 | 2009-03-13 | B | 27 | 0.032359 | 8.5833e-05
2009 | 2009-03-13 | B | 484 | 0.11232 | 0.0015386
2009 | 2009-03-13 | C | 309 | 0.18084 | 0.00098231
2009 | 2009-03-13 | C | 845 | 0.11959 | 0.0026862
2009 | 2009-03-13 | B | 135 | 0.052596 | 0.00042916
2009 | 2008-12-09 | C | 1711 | 0.28652 | 0.0054393
2009 | 2008-12-09 | C | 1843 | 0.22264 | 0.0058589
2009 | 2009-03-14 | C | 1 | 0.00014941 | 3.179e-06
2009 | 2009-03-14 | B | 37 | 0.041991 | 0.00011762
2009 | 2009-03-14 | C | 4 | 0.0020473 | 1.2716e-05
2009 | 2009-03-14 | C | 146 | 0.023426 | 0.00046413
2009 | 2009-03-15 | C | 491 | 0.049948 | 0.0015609
2009 | 2009-03-14 | C | 892 | 0.77366 | 0.0028357
2009 | 2009-03-14 | C | 61 | 0.12159 | 0.00019392
2009 | 2009-03-15 | B | 146 | 0.026456 | 0.00046413
2009 | 2009-03-15 | C | 1230 | 0.18306 | 0.0039102
2009 | 2009-03-15 | C | 54 | 0.0090983 | 0.00017167
2009 | 2009-03-15 | C | 532 | 0.071031 | 0.0016912
2009 | 2009-03-15 | B | 155 | 0.051245 | 0.00049274
2009 | 2009-03-16 | C | 51 | 0.02286 | 0.00016213
2009 | 2009-03-14 | B | 6 | 0.0047876 | 1.9074e-05
2009 | 2009-03-15 | B | 29 | 0.0050705 | 9.2191e-05
2009 | 2009-03-16 | C | 38 | 0.014979 | 0.0001208
2009 | 2009-03-16 | B | 23 | 0.020619 | 7.3117e-05
2009 | 2009-03-16 | B | 3 | 0.00071527 | 9.537e-06
2009 | 2009-03-16 | C | 125 | 0.039022 | 0.00039737
2009 | 2009-03-16 | B | 346 | 0.11721 | 0.0010999
2009 | 2009-03-16 | C | 32 | 0.0054965 | 0.00010173
2009 | 2009-03-16 | C | 132 | 0.013892 | 0.00041963
2009 | 2009-03-17 | B | 305 | 0.033936 | 0.00096959
2009 | 2009-03-17 | C | 4 | 0.0035096 | 1.2716e-05
2009 | 2009-03-17 | B | 258 | 0.16029 | 0.00082018
2009 | 2009-03-17 | B | 6 | 0.0079348 | 1.9074e-05
2009 | 2009-03-17 | C | 287 | 0.050025 | 0.00091237
2009 | 2009-03-17 | B | 44 | 0.0449 | 0.00013988
2009 | 2009-03-17 | B | 224 | 0.28769 | 0.00071209
2009 | 2009-03-17 | C | 1 | 0.00098231 | 3.179e-06
2009 | 2009-03-17 | B | 21 | 0.014954 | 6.6759e-05
2009 | 2009-03-17 | B | 159 | 0.059139 | 0.00050546
2009 | 2009-03-17 | C | 24 | 0.0019074 | 7.6296e-05
2009 | 2009-03-17 | B | 1 | 0.00024478 | 3.179e-06
2009 | 2009-03-18 | B | 1 | 0.000302 | 3.179e-06
2009 | 2009-03-18 | B | 322 | 0.18118 | 0.0010236
2009 | 2009-03-18 | B | 2 | 0.0014305 | 6.358e-06
2009 | 2009-03-18 | B | 119 | 0.10857 | 0.0003783
2009 | 2009-03-18 | B | 144 | 0.11032 | 0.00045778
2009 | 2009-03-18 | B | 50 | 0.039102 | 0.00015895
2009 | 2009-03-18 | B | 1 | 0.00065805 | 3.179e-06
2009 | 2009-03-18 | C | 328 | 0.063876 | 0.0010427
2009 | 2009-03-18 | B | 23 | 0.026103 | 7.3117e-05
2009 | 2009-03-18 | B | 34 | 0.0086469 | 0.00010809
2009 | 2009-03-19 | B | 307 | 0.0097595 | 0.00097595
2009 | 2009-03-18 | C | 92 | 0.0091428 | 0.00029247
2009 | 2009-03-18 | C | 142 | 0.030693 | 0.00045142
2009 | 2009-03-19 | C | 214 | 0.008844 | 0.0006803
2009 | 2009-03-19 | C | 597 | 0.10083 | 0.0018979
2009 | 2009-03-19 | C | 302 | 0.043539 | 0.00096006
2009 | 2009-03-19 | C | 303 | 0.31441 | 0.00096323
2009 | 2009-03-19 | C | 248 | 0.04888 | 0.00078839
2009 | 2009-03-19 | B | 88 | 0.10798 | 0.00027975
2009 | 2009-03-19 | B | 28 | 0.026169 | 8.9012e-05
2009 | 2009-03-13 | B | 11 | 0.0096864 | 3.4969e-05
2009 | 2009-03-19 | B | 76 | 0.032057 | 0.0002416
2009 | 2009-03-19 | C | 54 | 0.0044633 | 0.00017167
2009 | 2009-03-18 | B | 37 | 0.019789 | 0.00011762
2009 | 2009-03-19 | B | 56 | 0.020396 | 0.00017802
2009 | 2009-03-19 | C | 2 | 0.00061672 | 6.358e-06
2009 | 2009-03-19 | C | 285 | 0.042583 | 0.00090601
2009 | 2009-03-20 | B | 73 | 0.018565 | 0.00023207
2009 | 2009-03-19 | B | 46 | 0.01126 | 0.00014623
2009 | 2009-03-19 | C | 304 | 0.12314 | 0.00096641
2009 | 2009-03-20 | B | 10 | 0.0050546 | 3.179e-05
2009 | 2009-03-20 | C | 62 | 0.001971 | 0.0001971
2009 | 2009-03-20 | C | 107 | 0.054348 | 0.00034015
2009 | 2009-03-20 | B | 21 | 0.012951 | 6.6759e-05
2009 | 2009-03-20 | B | 13 | 0.01558 | 4.1327e-05
2009 | 2009-03-20 | B | 1 | 0.00064851 | 3.179e-06
2009 | 2009-03-20 | B | 37 | 0.021728 | 0.00011762
2009 | 2009-03-20 | B | 1 | 0.0011826 | 3.179e-06
2009 | 2009-03-20 | C | 153 | 0.099223 | 0.00048639
2009 | 2009-03-21 | C | 80 | 0.016365 | 0.00025432
2009 | 2009-03-21 | C | 469 | 0.12295 | 0.0014909
2009 | 2009-03-21 | C | 56 | 0.030264 | 0.00017802
2009 | 2009-03-21 | C | 213 | 0.25189 | 0.00067713
2009 | 2009-03-22 | C | 286 | 0.040211 | 0.00090919
2009 | 2009-03-21 | C | 308 | 0.12095 | 0.00097913
2009 | 2009-03-22 | C | 234 | 0.26286 | 0.00074388
2009 | 2009-03-22 | C | 313 | 0.0029851 | 0.00099502
2009 | 2009-03-22 | C | 1542 | 0.6096 | 0.004902
2009 | 2009-03-22 | C | 306 | 0.098237 | 0.00097277
2009 | 2009-03-22 | C | 325 | 0.010332 | 0.0010332
2009 | 2009-03-23 | C | 540 | 0.12014 | 0.0017167
2009 | 2009-03-22 | C | 781 | 0.15145 | 0.0024828
2009 | 2009-03-23 | C | 3 | 0.00076296 | 9.537e-06
2009 | 2009-03-23 | C | 56 | 0.010147 | 0.00017802
2009 | 2009-03-23 | B | 10 | 0.0094734 | 3.179e-05
2009 | 2009-03-23 | C | 154 | 0.018114 | 0.00048956
2009 | 2009-03-12 | B | 23 | 0.025006 | 7.3117e-05
2009 | 2009-03-23 | C | 215 | 0.0088853 | 0.00068348
2009 | 2009-03-23 | B | 50 | 0.0084243 | 0.00015895
2009 | 2009-03-24 | B | 364 | 0.019672 | 0.0011572
2009 | 2009-03-21 | B | 49 | 0.0093462 | 0.00015577
2009 | 2009-03-21 | B | 3 | 0.0011826 | 9.537e-06
2009 | 2009-03-24 | B | 163 | 0.05389 | 0.00051818
2009 | 2009-03-24 | C | 397 | 0.0037862 | 0.0012621
2009 | 2009-03-24 | B | 200 | 0.19583 | 0.0006358
2009 | 2009-03-24 | C | 119 | 0.026103 | 0.0003783
2009 | 2009-03-24 | B | 6 | 0.0059511 | 1.9074e-05
2009 | 2009-03-24 | B | 67 | 0.076038 | 0.00021299
2009 | 2009-03-24 | C | 230 | 0.025785 | 0.00073117
2009 | 2009-03-24 | C | 191 | 0.016394 | 0.00060719
2009 | 2009-03-24 | C | 4 | 0.0020854 | 1.2716e-05
2009 | 2009-03-24 | B | 260 | 0.1496 | 0.00082654
2009 | 2009-03-25 | C | 368 | 0.22345 | 0.0011699
2009 | 2009-03-25 | C | 413 | 0.057292 | 0.0013129
2009 | 2009-03-25 | B | 39 | 0.013886 | 0.00012398
2009 | 2009-03-25 | B | 90 | 0.035191 | 0.00028611
2009 | 2009-03-25 | B | 5 | 0.0020187 | 1.5895e-05
2009 | 2009-03-25 | B | 187 | 0.052908 | 0.00059447
2009 | 2009-03-24 | B | 2 | 0.0012525 | 6.358e-06
2009 | 2009-03-25 | B | 421 | 0.23957 | 0.0013384
2009 | 2009-03-25 | C | 73 | 0.055928 | 0.00023207
2009 | 2009-03-25 | B | 3 | 0.0038816 | 9.537e-06
2009 | 2009-03-25 | B | 1 | 0.00034651 | 3.179e-06
2009 | 2009-03-25 | C | 19 | 0.010268 | 6.0401e-05
2009 | 2009-03-25 | C | 116 | 0.007744 | 0.00036876
2009 | 2009-03-26 | B | 21 | 0.010815 | 6.6759e-05
2009 | 2009-03-26 | B | 30 | 0.038053 | 9.537e-05
2009 | 2009-03-26 | B | 6 | 0.0059511 | 1.9074e-05
2009 | 2009-03-26 | B | 51 | 0.059015 | 0.00016213
2009 | 2009-03-26 | B | 1 | 0.00021935 | 3.179e-06
2009 | 2009-03-27 | B | 57 | 0.015765 | 0.0001812
2009 | 2009-03-26 | C | 164 | 0.0082145 | 0.00052135
2009 | 2009-03-26 | B | 436 | 0.25763 | 0.001386
2009 | 2009-03-27 | B | 3 | 0.0022412 | 9.537e-06
2009 | 2009-03-27 | B | 5 | 0.0043075 | 1.5895e-05
2009 | 2009-03-27 | C | 3 | 0.0018025 | 9.537e-06
2009 | 2009-03-27 | B | 3 | 0.0034905 | 9.537e-06
2009 | 2009-03-27 | B | 1 | 0.00053089 | 3.179e-06
2009 | 2009-03-28 | C | 1361 | 0.21478 | 0.0043266
2009 | 2009-03-28 | C | 367 | 0.0081668 | 0.0011667
2009 | 2009-03-28 | C | 204 | 0.022049 | 0.00064851
2009 | 2009-03-27 | C | 96 | 0.041896 | 0.00030518
2009 | 2009-03-27 | C | 110 | 0.050625 | 0.00034969
2009 | 2009-03-27 | C | 1521 | 0.16683 | 0.0048352
2009 | 2009-03-29 | C | 35 | 0.017106 | 0.00011126
2009 | 2009-03-30 | C | 74 | 0.013409 | 0.00023525
2009 | 2009-03-30 | B | 1 | 0.00103 | 3.179e-06
2009 | 2009-03-30 | C | 181 | 0.042684 | 0.0005754
2009 | 2009-03-31 | B | 17 | 0.011403 | 5.4043e-05
2009 | 2009-03-31 | B | 62 | 0.06386 | 0.0001971
2009 | 2009-03-31 | B | 50 | 0.053725 | 0.00015895
2009 | 2009-03-31 | B | 10 | 0.011349 | 3.179e-05
2009 | 2009-03-31 | B | 15 | 0.019408 | 4.7685e-05
2009 | 2009-03-31 | C | 4599 | 0.11653 | 0.01462
2009 | 2009-03-31 | C | 1121 | 0.26464 | 0.0035637
2009 | 2009-03-27 | B | 1 | 0.0011349 | 3.179e-06
2009 | 2009-03-31 | C | 101 | 0.0061005 | 0.00032108
2009 | 2008-09-26 | B | 19 | 0.018845 | 6.0401e-05
2010 | 2009-04-01 | B | 32 | 0.0065729 | 0.00010112
2010 | 2009-04-01 | C | 19 | 0.0012609 | 6.004e-05
2010 | 2009-04-01 | B | 1 | 0.00084373 | 3.16e-06
2010 | 2009-04-01 | B | 7 | 0.0053752 | 2.212e-05
2010 | 2009-04-01 | C | 306 | 0.099705 | 0.00096697
2010 | 2009-04-01 | B | 10 | 0.011376 | 3.16e-05
2010 | 2009-04-01 | B | 21 | 0.0096223 | 6.6361e-05
2010 | 2009-04-01 | C | 4 | 0.00034128 | 1.264e-05
2010 | 2009-04-01 | C | 36 | 0.016382 | 0.00011376
2010 | 2009-04-02 | B | 7 | 0.0026765 | 2.212e-05
2010 | 2009-04-02 | B | 173 | 0.066089 | 0.00054668
2010 | 2009-04-02 | B | 8 | 0.0075588 | 2.528e-05
2010 | 2009-04-02 | B | 1 | 0.0010144 | 3.16e-06
2010 | 2009-04-02 | B | 30 | 0.026734 | 9.4801e-05
2010 | 2009-04-02 | C | 129 | 0.11743 | 0.00040764
2010 | 2009-04-02 | C | 1 | 0.00014852 | 3.16e-06
2010 | 2009-04-03 | C | 171 | 0.027012 | 0.00054036
2010 | 2009-04-03 | C | 12 | 0.0005688 | 3.792e-05
2010 | 2009-04-03 | B | 36 | 0.020477 | 0.00011376
2010 | 2009-04-03 | C | 4 | 0.00075841 | 1.264e-05
2010 | 2009-04-03 | C | 169 | 0.0080107 | 0.00053404
2010 | 2009-04-05 | B | 1 | 0.0016906 | 3.16e-06
2010 | 2009-04-06 | B | 89 | 0.015424 | 0.00028124
2010 | 2009-04-06 | B | 1 | 0.0005372 | 3.16e-06
2010 | 2009-04-06 | B | 9 | 0.0068257 | 2.844e-05
2010 | 2009-04-06 | B | 1 | 0.000474 | 3.16e-06
2010 | 2009-04-06 | B | 5 | 0.002844 | 1.58e-05
2010 | 2009-04-06 | C | 40 | 0.012387 | 0.0001264
2010 | 2009-04-06 | C | 127 | 0.0064212 | 0.00040132
2010 | 2009-04-06 | C | 41 | 0.040293 | 0.00012956
2010 | 2009-04-07 | C | 67 | 0.0021172 | 0.00021172
2010 | 2009-04-07 | B | 68 | 0.045817 | 0.00021488
2010 | 2009-04-07 | B | 6 | 0.0049107 | 1.896e-05
2010 | 2009-04-07 | B | 118 | 0.14915 | 0.00037288
2010 | 2009-04-07 | C | 130 | 0.0073945 | 0.0004108
2010 | 2009-04-07 | C | 163 | 0.042117 | 0.00051508
2010 | 2009-04-07 | C | 322 | 0.088759 | 0.0010175
2010 | 2009-04-08 | B | 3 | 0.0021046 | 9.4801e-06
2010 | 2009-04-08 | B | 135 | 0.055885 | 0.0004266
2010 | 2009-04-08 | B | 13 | 0.01027 | 4.108e-05
2010 | 2009-04-08 | C | 363 | 0.30015 | 0.0011471
2010 | 2009-04-08 | B | 15 | 0.017064 | 4.74e-05
2010 | 2009-04-08 | B | 25 | 0.010191 | 7.9001e-05
2010 | 2009-04-08 | B | 70 | 0.031189 | 0.0002212
2010 | 2009-04-08 | B | 2 | 0.0017064 | 6.3201e-06
2010 | 2009-04-08 | C | 16 | 0.0062189 | 5.056e-05
2010 | 2009-04-08 | C | 284 | 0.050747 | 0.00089745
2010 | 2009-04-09 | C | 1591 | 0.6101 | 0.0050276
2010 | 2009-04-09 | C | 70 | 0.056337 | 0.0002212
2010 | 2009-04-08 | C | 1 | 0.0027271 | 3.16e-06
2010 | 2009-04-08 | C | 68 | 0.10121 | 0.00021488
2010 | 2009-04-08 | C | 326 | 0.071518 | 0.0010302
2010 | 2009-04-09 | C | 26 | 0.017254 | 8.2161e-05
2010 | 2009-04-09 | B | 18 | 0.018088 | 5.688e-05
2010 | 2009-04-09 | B | 36 | 0.029578 | 0.00011376
2010 | 2009-04-08 | C | 446 | 0.22426 | 0.0014094
2010 | 2009-04-09 | C | 652 | 0.074172 | 0.0020603
2010 | 2009-04-09 | C | 74 | 0.037181 | 0.00023384
2010 | 2009-04-09 | C | 899 | 0.10922 | 0.0028409
2010 | 2009-04-10 | C | 1144 | 1.3918 | 0.0036151
2010 | 2009-04-10 | C | 1361 | 1.2515 | 0.0043008
2010 | 2009-04-10 | C | 1 | 5.056e-05 | 3.16e-06
2010 | 2009-04-11 | C | 427 | 0.046866 | 0.0013493
2010 | 2009-04-12 | C | 286 | 0.084768 | 0.00090377
2010 | 2009-04-12 | C | 33 | 0.0047969 | 0.00010428
2010 | 2009-04-13 | C | 270 | 0.14147 | 0.00085321
2010 | 2009-04-13 | C | 1329 | 0.076646 | 0.0041997
2010 | 2009-04-14 | C | 948 | 0.14178 | 0.0029957
2010 | 2009-04-14 | B | 10 | 0.0029704 | 3.16e-05
2010 | 2009-04-14 | C | 4 | 0.0019971 | 1.264e-05
2010 | 2009-04-14 | B | 84 | 0.095559 | 0.00026544
2010 | 2009-04-14 | B | 2 | 0.001896 | 6.3201e-06
2010 | 2009-04-14 | C | 47 | 0.0074261 | 0.00014852
2010 | 2009-04-14 | B | 41 | 0.022414 | 0.00012956
2010 | 2009-04-14 | B | 61 | 0.05513 | 0.00019276
2010 | 2009-04-14 | B | 39 | 0.043504 | 0.00012324
2010 | 2009-04-14 | C | 748 | 0.095079 | 0.0023637
2010 | 2009-04-14 | C | 128 | 0.016179 | 0.00040448
2010 | 2009-04-14 | B | 119 | 0.046253 | 0.00037604
2010 | 2009-04-14 | B | 105 | 0.080296 | 0.0003318
2010 | 2009-04-15 | C | 114 | 0.12967 | 0.00036024
2010 | 2009-04-14 | C | 74 | 0.0098214 | 0.00023384
2010 | 2009-04-15 | B | 48 | 0.028213 | 0.00015168
2010 | 2009-04-15 | B | 178 | 0.20587 | 0.00056248
2010 | 2009-04-15 | B | 20 | 0.021615 | 6.3201e-05
2010 | 2009-04-15 | B | 1 | 0.00071417 | 3.16e-06
2010 | 2009-04-15 | C | 25 | 0.0063991 | 7.9001e-05
2010 | 2009-04-15 | B | 3 | 0.0035929 | 9.4801e-06
2010 | 2009-04-15 | B | 77 | 0.086379 | 0.00024332
2010 | 2009-04-15 | C | 51 | 0.0035455 | 0.00016116
2010 | 2009-04-15 | C | 7990 | 0.25249 | 0.025249
2010 | 2009-04-15 | C | 2209 | 0.069805 | 0.0069805
2010 | 2009-04-15 | C | 1233 | 0.015585 | 0.0038963
2010 | 2009-04-16 | B | 13 | 0.0073945 | 4.108e-05
2010 | 2009-04-16 | C | 559 | 0.21132 | 0.0017665
2010 | 2009-04-16 | C | 4967 | 0.16917 | 0.015696
2010 | 2009-04-16 | B | 33 | 0.03702 | 0.00010428
2010 | 2009-04-16 | B | 6 | 0.0068257 | 1.896e-05
2010 | 2009-04-16 | B | 35 | 0.039816 | 0.0001106
2010 | 2009-04-16 | C | 146 | 0.057244 | 0.00046136
2010 | 2009-04-17 | C | 405 | 0.091786 | 0.0012798
2010 | 2009-04-17 | B | 6 | 0.002389 | 1.896e-05
2010 | 2009-04-17 | B | 6 | 0.0062569 | 1.896e-05
2010 | 2009-04-17 | B | 35 | 0.019908 | 0.0001106
2010 | 2009-04-17 | C | 22 | 0.001738 | 6.9521e-05
2010 | 2009-04-17 | C | 2 | 0.0016432 | 6.3201e-06
2010 | 2009-04-17 | C | 23 | 0.0098846 | 7.2681e-05
2010 | 2009-04-17 | C | 83 | 0.00078685 | 0.00026228
2010 | 2009-04-18 | B | 3 | 0.0012988 | 9.4801e-06
2010 | 2009-04-18 | C | 94 | 0.040695 | 0.00029704
2010 | 2009-04-18 | C | 127 | 0.0096318 | 0.00040132
2010 | 2009-04-18 | C | 163 | 0.017513 | 0.00051508
2010 | 2009-04-18 | C | 724 | 0.011439 | 0.0022879
2010 | 2009-04-19 | B | 66 | 0.02607 | 0.00020856
2010 | 2009-04-19 | C | 590 | 0.13903 | 0.0018644
2010 | 2009-04-19 | B | 4 | 0.0063833 | 1.264e-05
2010 | 2009-04-19 | C | 227 | 0.047347 | 0.00071733
2010 | 2009-04-19 | C | 812 | 0.43497 | 0.0025659
2010 | 2009-04-20 | C | 26 | 0.0016432 | 8.2161e-05
2010 | 2009-04-20 | C | 127 | 0.026475 | 0.00040132
2010 | 2009-04-20 | B | 117 | 0.029948 | 0.00036972
2010 | 2009-04-20 | C | 37 | 0.0017538 | 0.00011692
2010 | 2009-04-20 | C | 38 | 0.026137 | 0.00012008
2010 | 2009-04-20 | B | 58 | 0.014144 | 0.00018328
2010 | 2009-04-20 | C | 260 | 0.063905 | 0.00082161
2010 | 2009-04-20 | C | 36 | 0.015016 | 0.00011376
2010 | 2009-04-20 | C | 135 | 0.064215 | 0.0004266
2010 | 2009-04-20 | C | 116 | 0.030943 | 0.00036656
2010 | 2009-04-21 | C | 2305 | 0.41053 | 0.0072839
2010 | 2009-04-21 | B | 1 | 0.00016116 | 3.16e-06
2010 | 2009-04-21 | B | 1 | 6.3201e-05 | 3.16e-06
2010 | 2009-04-21 | C | 15 | 0.0015642 | 4.74e-05
2010 | 2009-04-21 | C | 11 | 0.0019466 | 3.476e-05
2010 | 2009-04-21 | B | 6 | 0.0061052 | 1.896e-05
2010 | 2009-04-21 | B | 84 | 0.095559 | 0.00026544
2010 | 2009-04-21 | B | 4 | 0.0041712 | 1.264e-05
2010 | 2009-04-20 | C | 1 | 0.0027935 | 3.16e-06
2010 | 2009-04-21 | B | 11 | 0.013626 | 3.476e-05
2010 | 2009-04-20 | C | 2 | 0.0056248 | 6.3201e-06
2010 | 2009-04-21 | C | 3 | 0.00072997 | 9.4801e-06
2010 | 2009-04-21 | C | 50 | 0.01027 | 0.000158
2010 | 2009-04-21 | C | 29 | 0.04857 | 9.1641e-05
2010 | 2009-04-21 | C | 290 | 0.066898 | 0.00091641
2010 | 2009-04-20 | C | 75 | 0.14588 | 0.000237
2010 | 2009-04-22 | C | 515 | 0.14874 | 0.0016274
2010 | 2009-04-17 | B | 33 | 0.035768 | 0.00010428
2010 | 2009-04-22 | B | 32 | 0.018606 | 0.00010112
2010 | 2009-04-22 | C | 3709 | 0.046882 | 0.011721
2010 | 2009-04-22 | B | 130 | 0.14789 | 0.0004108
2010 | 2009-04-22 | B | 35 | 0.038821 | 0.0001106
2010 | 2009-04-21 | B | 111 | 0.12522 | 0.00035076
2010 | 2009-04-22 | C | 29 | 0.01732 | 9.1641e-05
2010 | 2009-04-22 | B | 17 | 0.023261 | 5.372e-05
2010 | 2009-04-23 | C | 205 | 0.091938 | 0.00064781
2010 | 2009-04-23 | B | 5 | 0.0012008 | 1.58e-05
2010 | 2009-04-23 | B | 45 | 0.019482 | 0.0001422
2010 | 2009-04-23 | B | 197 | 0.20979 | 0.00062252
2010 | 2009-04-23 | B | 111 | 0.12627 | 0.00035076
2010 | 2009-04-23 | B | 84 | 0.09609 | 0.00026544
2010 | 2009-04-23 | B | 34 | 0.025786 | 0.00010744
2010 | 2009-04-23 | B | 6 | 0.0058776 | 1.896e-05
2010 | 2009-04-23 | C | 4 | 0.00073313 | 1.264e-05
2010 | 2009-04-23 | B | 11 | 0.015434 | 3.476e-05
2010 | 2009-04-23 | C | 385 | 0.15733 | 0.0012166
2010 | 2009-04-23 | C | 313 | 0.077215 | 0.00098909
2010 | 2009-04-24 | B | 6 | 0.0011376 | 1.896e-05
2010 | 2009-04-24 | B | 5 | 0.002844 | 1.58e-05
2010 | 2009-04-24 | B | 31 | 0.026449 | 9.7961e-05
2010 | 2009-04-24 | B | 1 | 0.00049296 | 3.16e-06
2010 | 2009-04-23 | B | 9 | 0.0031 | 2.844e-05
2010 | 2009-04-24 | C | 3 | 0.0024459 | 9.4801e-06
2010 | 2009-04-24 | C | 3 | 0.00075841 | 9.4801e-06
2010 | 2009-04-24 | B | 1 | 0.00068573 | 3.16e-06
2010 | 2009-04-24 | B | 11 | 0.013557 | 3.476e-05
2010 | 2009-04-25 | C | 9 | 0.00051192 | 2.844e-05
2010 | 2009-04-24 | C | 463 | 0.21928 | 0.0014631
2010 | 2009-04-26 | C | 56 | 0.004778 | 0.00017696
2010 | 2009-04-26 | C | 292 | 0.060277 | 0.00092273
2010 | 2009-04-26 | C | 387 | 0.05014 | 0.0012229
2010 | 2009-04-26 | C | 280 | 0.0214 | 0.00088481
2010 | 2009-04-27 | C | 264 | 0.015339 | 0.00083425
2010 | 2009-04-27 | B | 252 | 0.066891 | 0.00079633
2010 | 2009-04-27 | C | 13 | 0.0052994 | 4.108e-05
2010 | 2009-04-27 | B | 85 | 0.034381 | 0.0002686
2010 | 2009-04-27 | C | 6 | 0.00062569 | 1.896e-05
2010 | 2009-04-27 | C | 63 | 0.010153 | 0.00019908
2010 | 2009-04-27 | B | 4 | 0.0031347 | 1.264e-05
2010 | 2009-04-27 | B | 82 | 0.030058 | 0.00025912
2010 | 2009-04-27 | B | 20 | 0.0095433 | 6.3201e-05
2010 | 2009-04-27 | B | 34 | 0.037389 | 0.00010744
2010 | 2009-04-27 | B | 13 | 0.012694 | 4.108e-05
2010 | 2009-04-27 | B | 1 | 8.8481e-05 | 3.16e-06
2010 | 2009-04-28 | B | 60 | 0.040196 | 0.0001896
2010 | 2009-04-28 | C | 15 | 0.002133 | 4.74e-05
2010 | 2009-04-28 | B | 10 | 0.0086585 | 3.16e-05
2010 | 2009-04-28 | C | 55 | 0.006102 | 0.0001738
2010 | 2009-04-28 | B | 6 | 0.005688 | 1.896e-05
2010 | 2009-04-28 | C | 37 | 0.022345 | 0.00011692
2010 | 2009-04-28 | C | 13 | 0.0093663 | 4.108e-05
2010 | 2009-04-28 | B | 109 | 0.10264 | 0.00034444
2010 | 2009-04-28 | B | 6 | 0.0065413 | 1.896e-05
2010 | 2009-04-28 | C | 9 | 0.0021899 | 2.844e-05
2010 | 2009-04-29 | C | 2311 | 0.42422 | 0.0073028
2010 | 2009-04-28 | C | 764 | 0.37811 | 0.0024143
2010 | 2009-04-29 | C | 2 | 0.000474 | 6.3201e-06
2010 | 2009-04-29 | B | 109 | 0.087833 | 0.00034444
2010 | 2009-04-29 | C | 87 | 0.0093474 | 0.00027492
2010 | 2009-04-29 | C | 277 | 0.031989 | 0.00087533
2010 | 2009-04-29 | B | 34 | 0.037819 | 0.00010744
2010 | 2009-04-29 | C | 25 | 0.003871 | 7.9001e-05
2010 | 2009-04-29 | B | 195 | 0.15836 | 0.0006162
2010 | 2009-04-29 | C | 51 | 0.02224 | 0.00016116
2010 | 2009-04-29 | C | 216 | 0.036956 | 0.00068257
2010 | 2009-04-30 | C | 683 | 0.26997 | 0.0021583
2010 | 2009-04-29 | B | 82 | 0.10909 | 0.00025912
2010 | 2009-04-30 | B | 44 | 0.017797 | 0.00013904
2010 | 2009-04-30 | C | 4 | 0.0013778 | 1.264e-05
2010 | 2009-04-30 | C | 853 | 0.1789 | 0.0026955
2010 | 2009-04-30 | B | 8 | 0.0066993 | 2.528e-05
2010 | 2009-04-30 | B | 169 | 0.095679 | 0.00053404
2010 | 2009-04-30 | B | 272 | 0.22777 | 0.00085953
2010 | 2009-04-30 | B | 501 | 0.18365 | 0.0015832
2010 | 2009-04-30 | B | 5 | 0.005609 | 1.58e-05
2010 | 2009-04-30 | B | 191 | 0.17139 | 0.00060356
2010 | 2009-04-30 | C | 8 | 0.0080897 | 2.528e-05
2010 | 2009-04-30 | B | 1 | 0.00017696 | 3.16e-06
2010 | 2009-05-01 | B | 131 | 0.010763 | 0.00041396
2010 | 2009-05-01 | C | 1 | 0.00043292 | 3.16e-06
2010 | 2009-05-01 | C | 413 | 0.063949 | 0.0013051
2010 | 2009-05-01 | B | 4 | 0.0040575 | 1.264e-05
2010 | 2009-05-01 | B | 92 | 0.069483 | 0.00029072
2010 | 2009-05-01 | B | 23 | 0.017734 | 7.2681e-05
2010 | 2009-05-01 | B | 31 | 0.014694 | 9.7961e-05
2010 | 2009-05-01 | C | 1 | 4.74e-05 | 3.16e-06
2010 | 2009-05-02 | C | 301 | 0.076571 | 0.00095117
2010 | 2009-05-02 | C | 294 | 0.10963 | 0.00092905
2010 | 2009-05-02 | C | 133 | 0.018492 | 0.00042028
2010 | 2009-05-02 | C | 63 | 0.004977 | 0.00019908
2010 | 2009-05-02 | B | 3 | 0.0019813 | 9.4801e-06
2010 | 2009-05-02 | B | 4 | 0.0026797 | 1.264e-05
2010 | 2009-05-02 | C | 131 | 0.022354 | 0.00041396
2010 | 2009-05-02 | C | 71 | 0.0040385 | 0.00022436
2010 | 2009-05-02 | C | 39 | 0.015987 | 0.00012324
2010 | 2009-05-03 | C | 20 | 0.002528 | 6.3201e-05
2010 | 2009-05-03 | C | 411 | 0.29179 | 0.0012988
2010 | 2009-05-03 | B | 318 | 0.27433 | 0.0010049
2010 | 2009-05-03 | C | 566 | 0.046503 | 0.0017886
2010 | 2009-05-04 | B | 1 | 0.0006004 | 3.16e-06
2010 | 2009-05-04 | B | 131 | 0.066234 | 0.00041396
2010 | 2009-05-04 | B | 25 | 0.01817 | 7.9001e-05
2010 | 2009-05-04 | C | 14 | 0.0022563 | 4.424e-05
2010 | 2009-05-04 | B | 35 | 0.011281 | 0.0001106
2010 | 2009-05-04 | B | 6 | 0.0031663 | 1.896e-05
2010 | 2009-04-28 | B | 9 | 0.0046926 | 2.844e-05
2010 | 2009-05-04 | B | 112 | 0.023713 | 0.00035392
2010 | 2009-05-04 | C | 595 | 0.20024 | 0.0018802
2010 | 2009-05-04 | C | 1149 | 0.018154 | 0.0036309
2010 | 2009-05-04 | C | 1 | 0.00023068 | 3.16e-06
2010 | 2009-05-04 | C | 206 | 0.0019529 | 0.00065097
2010 | 2009-05-04 | B | 612 | 0.28816 | 0.0019339
2010 | 2009-05-04 | C | 219 | 0.031749 | 0.00069205
2010 | 2009-05-04 | B | 23 | 0.025438 | 7.2681e-05
2010 | 2009-05-04 | C | 545 | 0.017222 | 0.0017222
2010 | 2009-05-05 | C | 118 | 0.013051 | 0.00037288
2010 | 2009-05-05 | C | 118 | 0.010441 | 0.00037288
2010 | 2009-05-05 | C | 12 | 0.017898 | 3.792e-05
2010 | 2009-05-05 | B | 4 | 0.002212 | 1.264e-05
2010 | 2009-05-05 | C | 79 | 0.0054921 | 0.00024964
2010 | 2009-05-05 | B | 64 | 0.048336 | 0.00020224
2010 | 2009-05-05 | B | 58 | 0.010997 | 0.00018328
2010 | 2009-05-05 | B | 151 | 0.19564 | 0.00047716
2010 | 2009-05-05 | C | 7 | 0.0026102 | 2.212e-05
2010 | 2009-05-06 | C | 104 | 0.050851 | 0.00032864
2010 | 2009-05-06 | B | 6 | 0.0018012 | 1.896e-05
2010 | 2009-05-06 | B | 151 | 0.12836 | 0.00047716
2010 | 2009-05-06 | B | 20 | 0.020856 | 6.3201e-05
2010 | 2009-05-07 | B | 64 | 0.048538 | 0.00020224
2010 | 2009-05-07 | B | 83 | 0.049202 | 0.00026228
2010 | 2009-05-07 | B | 77 | 0.087596 | 0.00024332
2010 | 2009-05-07 | B | 11 | 0.011436 | 3.476e-05
2010 | 2009-05-07 | C | 16 | 0.0015168 | 5.056e-05
2010 | 2009-05-07 | C | 238 | 0.067688 | 0.00075209
2010 | 2009-05-08 | C | 367 | 0.018556 | 0.0011597
2010 | 2009-05-07 | B | 1 | 0.00074893 | 3.16e-06
2010 | 2009-05-08 | C | 356 | 0.039222 | 0.001125
2010 | 2009-05-08 | C | 521 | 0.044452 | 0.0016464
2010 | 2009-05-08 | C | 155 | 0.015007 | 0.0004898
2010 | 2009-05-08 | B | 5 | 0.0028914 | 1.58e-05
2010 | 2009-05-07 | C | 2 | 0.0082097 | 6.3201e-06
2010 | 2009-05-08 | C | 137 | 0.037664 | 0.00043292
2010 | 2009-05-08 | B | 33 | 0.023463 | 0.00010428
2010 | 2009-05-08 | C | 282 | 0.038318 | 0.00089113
2010 | 2009-05-09 | C | 730 | 0.1056 | 0.0023068
2010 | 2009-05-09 | C | 1262 | 0.17132 | 0.003988
2010 | 2009-05-09 | B | 1 | 0.001027 | 3.16e-06
2010 | 2009-05-02 | B | 1 | 0.00019908 | 3.16e-06
2010 | 2009-05-09 | C | 6 | 0.00075841 | 1.896e-05
2010 | 2009-05-10 | C | 227 | 0.041526 | 0.00071733
2010 | 2009-05-10 | C | 18 | 0.0019908 | 5.688e-05
2010 | 2009-05-09 | C | 12 | 0.02461 | 3.792e-05
2010 | 2009-05-10 | C | 731 | 0.087779 | 0.00231
2010 | 2009-05-10 | C | 731 | 0.01155 | 0.00231
2010 | 2009-05-10 | C | 107 | 0.036034 | 0.00033812
2010 | 2009-05-10 | C | 679 | 0.096694 | 0.0021457
2010 | 2009-05-07 | B | 18 | 0.0026165 | 5.688e-05
2010 | 2009-05-11 | B | 32 | 0.00040448 | 0.00010112
2010 | 2009-05-11 | B | 57 | 0.038906 | 0.00018012
2010 | 2009-05-11 | C | 176 | 0.025584 | 0.00055616
2010 | 2009-05-11 | C | 451 | 0.36347 | 0.0014252
2010 | 2009-05-11 | C | 71 | 0.0011218 | 0.00022436
2010 | 2009-05-11 | C | 104 | 0.065198 | 0.00032864
2010 | 2009-05-11 | B | 27 | 0.030971 | 8.5321e-05
2010 | 2009-05-12 | B | 1 | 0.00014536 | 3.16e-06
2010 | 2009-05-12 | B | 41 | 0.021378 | 0.00012956
2010 | 2009-05-12 | B | 70 | 0.028756 | 0.0002212
2010 | 2009-05-12 | B | 226 | 0.15997 | 0.00071417
2010 | 2009-05-12 | B | 151 | 0.14792 | 0.00047716
2010 | 2009-05-12 | B | 61 | 0.05166 | 0.00019276
2010 | 2009-05-12 | B | 34 | 0.033414 | 0.00010744
2010 | 2009-05-12 | B | 3 | 0.0029388 | 9.4801e-06
2010 | 2009-05-12 | B | 9 | 0.0044936 | 2.844e-05
2010 | 2009-05-12 | B | 100 | 0.11408 | 0.000316
2010 | 2009-05-12 | B | 74 | 0.10055 | 0.00023384
2010 | 2009-05-12 | B | 1 | 0.0013588 | 3.16e-06
2010 | 2009-05-12 | C | 14 | 0.0023447 | 4.424e-05
2010 | 2009-05-12 | B | 161 | 0.030526 | 0.00050876
2010 | 2009-05-13 | C | 297 | 0.071268 | 0.00093853
2010 | 2009-05-13 | B | 14 | 0.0078305 | 4.424e-05
2010 | 2009-05-13 | B | 27 | 0.02662 | 8.5321e-05
2010 | 2009-05-13 | B | 89 | 0.073967 | 0.00028124
2010 | 2009-05-13 | B | 38 | 0.0056628 | 0.00012008
2010 | 2009-05-13 | B | 40 | 0.044872 | 0.0001264
2010 | 2009-05-13 | B | 25 | 0.01106 | 7.9001e-05
2010 | 2009-05-13 | B | 70 | 0.00066361 | 0.0002212
2010 | 2009-05-13 | B | 37 | 0.046301 | 0.00011692
2010 | 2009-05-13 | C | 21 | 0.0072997 | 6.6361e-05
2010 | 2009-05-13 | C | 871 | 0.11453 | 0.0027524
2010 | 2009-05-12 | B | 59 | 0.058916 | 0.00018644
2010 | 2009-05-13 | B | 1 | 0.00021804 | 3.16e-06
2010 | 2009-05-14 | C | 578 | 0.091132 | 0.0018265
2010 | 2009-05-14 | C | 643 | 0.14223 | 0.0020319
2010 | 2009-05-14 | B | 77 | 0.06448 | 0.00024332
2010 | 2009-05-14 | C | 30 | 0.0055774 | 9.4801e-05
2010 | 2009-05-14 | B | 1 | 0.001757 | 3.16e-06
2010 | 2009-05-14 | B | 20 | 0.033496 | 6.3201e-05
2010 | 2009-05-14 | B | 77 | 0.058397 | 0.00024332
2010 | 2009-05-14 | B | 22 | 0.024958 | 6.9521e-05
2010 | 2009-05-14 | C | 1 | 0.00021804 | 3.16e-06
2010 | 2009-05-14 | B | 68 | 0.086382 | 0.00021488
2010 | 2009-05-14 | B | 40 | 0.044872 | 0.0001264
2010 | 2009-05-14 | C | 390 | 0.063577 | 0.0012324
2010 | 2009-05-14 | B | 62 | 0.063283 | 0.00019592
2010 | 2009-05-14 | B | 17 | 0.011013 | 5.372e-05
2010 | 2009-05-14 | C | 39 | 0.0052994 | 0.00012324
2010 | 2009-05-15 | C | 140 | 0.038246 | 0.0004424
2010 | 2009-05-15 | C | 24 | 0.0062189 | 7.5841e-05
2010 | 2009-05-15 | B | 8 | 0.0087217 | 2.528e-05
2010 | 2009-05-15 | B | 32 | 0.032055 | 0.00010112
2010 | 2009-05-15 | C | 79 | 0.01423 | 0.00024964
2010 | 2009-05-15 | B | 6 | 0.0016116 | 1.896e-05
2010 | 2009-05-15 | B | 9 | 0.0046926 | 2.844e-05
2010 | 2009-05-15 | B | 1 | 0.0010712 | 3.16e-06
2010 | 2009-05-15 | C | 1046 | 0.066108 | 0.0033054
2010 | 2009-05-15 | C | 122 | 0.070228 | 0.00038552
2010 | 2009-05-16 | C | 210 | 0.2097 | 0.00066361
2010 | 2009-05-16 | C | 22 | 0.0040322 | 6.9521e-05
2010 | 2009-05-16 | C | 85 | 0.032232 | 0.0002686
2010 | 2009-05-16 | C | 343 | 0.035481 | 0.0010839
2010 | 2009-05-16 | C | 12 | 0.0018581 | 3.792e-05
2010 | 2009-05-16 | C | 6 | 0.016116 | 1.896e-05
2010 | 2009-05-16 | C | 191 | 0.018711 | 0.00060356
2010 | 2009-05-15 | C | 40 | 0.0085953 | 0.0001264
2010 | 2009-05-15 | C | 82 | 0.0178 | 0.00025912
2010 | 2009-05-15 | C | 853 | 0.25786 | 0.0026955
2010 | 2009-05-15 | C | 9 | 0.0005688 | 2.844e-05
2010 | 2009-05-15 | C | 13 | 0.0063264 | 4.108e-05
2010 | 2009-05-15 | C | 55 | 0.020856 | 0.0001738
2010 | 2009-05-15 | C | 17 | 0.01094 | 5.372e-05
2010 | 2009-05-16 | C | 9 | 0.00036972 | 2.844e-05
2010 | 2009-05-17 | C | 1346 | 0.56133 | 0.0042534
2010 | 2009-05-17 | C | 14 | 0.0028756 | 4.424e-05
2010 | 2009-05-17 | C | 134 | 0.036726 | 0.00042344
2010 | 2009-05-17 | C | 607 | 0.068696 | 0.0019181
2010 | 2009-05-17 | B | 30 | 0.016021 | 9.4801e-05
2010 | 2009-05-17 | C | 98 | 0.056053 | 0.00030968
2010 | 2009-05-17 | C | 67 | 0.0080454 | 0.00021172
2010 | 2009-05-17 | C | 201 | 0.073091 | 0.00063517
2010 | 2009-05-17 | C | 18 | 0.013765 | 5.688e-05
2010 | 2009-05-17 | C | 1049 | 0.18191 | 0.0033149
2010 | 2009-05-17 | C | 73 | 0.029123 | 0.00023068
2010 | 2009-05-17 | C | 304 | 0.17126 | 0.00096065
2010 | 2009-05-18 | C | 8286 | 0.31421 | 0.026184
2010 | 2009-05-18 | B | 15 | 0.010902 | 4.74e-05
2010 | 2009-05-18 | C | 6 | 0.0047211 | 1.896e-05
2010 | 2009-05-18 | C | 2 | 0.00014536 | 6.3201e-06
2010 | 2009-05-18 | B | 1 | 0.00066361 | 3.16e-06
2010 | 2009-05-18 | C | 472 | 0.026848 | 0.0014915
2010 | 2009-05-18 | B | 223 | 0.084562 | 0.00070469
2010 | 2009-05-18 | B | 14 | 0.015927 | 4.424e-05
2010 | 2009-05-18 | C | 186 | 0.01058 | 0.00058776
2010 | 2009-05-18 | B | 77 | 0.10949 | 0.00024332
2010 | 2009-05-18 | C | 7 | 0.001836 | 2.212e-05
2010 | 2009-05-18 | C | 231 | 0.040948 | 0.00072997
2010 | 2009-05-18 | C | 2 | 6.9521e-05 | 6.3201e-06
2010 | 2009-05-18 | C | 700 | 0.071505 | 0.002212
2010 | 2009-05-18 | B | 1 | 0.0004108 | 3.16e-06
2010 | 2009-05-18 | C | 632 | 0.073894 | 0.0019971
2010 | 2009-05-18 | C | 85 | 0.11594 | 0.0002686
2010 | 2009-05-19 | B | 7 | 0.0072333 | 2.212e-05
2010 | 2009-05-19 | B | 2 | 0.00051824 | 6.3201e-06
2010 | 2009-05-19 | B | 8 | 0.0052077 | 2.528e-05
2010 | 2009-05-19 | B | 2 | 0.0013335 | 6.3201e-06
2010 | 2009-05-19 | B | 135 | 0.12102 | 0.0004266
2010 | 2009-05-19 | B | 91 | 0.10554 | 0.00028756
2010 | 2009-05-19 | C | 24 | 0.00857 | 7.5841e-05
2010 | 2009-05-20 | C | 902 | 0.028503 | 0.0028503
2010 | 2009-05-20 | C | 590 | 0.059661 | 0.0018644
2010 | 2009-05-20 | C | 4 | 0.0005688 | 1.264e-05
2010 | 2009-05-20 | B | 38 | 0.027138 | 0.00012008
2010 | 2009-05-19 | C | 3 | 0.013917 | 9.4801e-06
2010 | 2009-05-20 | C | 11 | 0.00059092 | 3.476e-05
2010 | 2009-05-20 | C | 14 | 0.0074766 | 4.424e-05
2010 | 2009-05-21 | C | 305 | 0.013493 | 0.00096381
2010 | 2009-05-20 | C | 44 | 0.0025027 | 0.00013904
2010 | 2009-05-21 | C | 684 | 0.057051 | 0.0021615
2010 | 2009-05-21 | B | 15 | 0.0086743 | 4.74e-05
2010 | 2009-05-21 | C | 7 | 0.001659 | 2.212e-05
2010 | 2009-05-21 | B | 1 | 0.0010902 | 3.16e-06
2010 | 2009-05-21 | C | 26 | 0.0013146 | 8.2161e-05
2010 | 2009-05-21 | C | 30 | 0.11815 | 9.4801e-05
2010 | 2009-05-21 | B | 4 | 0.003792 | 1.264e-05
2010 | 2009-05-21 | B | 32 | 0.022954 | 0.00010112
2010 | 2009-05-21 | B | 162 | 0.032251 | 0.00051192
2010 | 2009-05-21 | B | 19 | 0.0094264 | 6.004e-05
2010 | 2009-05-22 | C | 4 | 0.00059408 | 1.264e-05
2010 | 2009-05-22 | B | 4 | 0.00066993 | 1.264e-05
2010 | 2009-05-22 | B | 762 | 0.33711 | 0.0024079
2010 | 2009-05-22 | C | 483 | 0.024421 | 0.0015263
2010 | 2009-05-22 | C | 138 | 0.0082856 | 0.00043608
2010 | 2009-05-22 | C | 144 | 0.0063706 | 0.00045504
2010 | 2009-05-22 | C | 29 | 0.092924 | 9.1641e-05
2010 | 2009-05-23 | C | 90 | 0.013936 | 0.0002844
2010 | 2009-05-23 | C | 49 | 0.025874 | 0.00015484
2010 | 2009-05-23 | C | 83 | 0.047144 | 0.00026228
2010 | 2009-05-23 | C | 2 | 0.0022563 | 6.3201e-06
2010 | 2009-05-23 | C | 13 | 0.00073945 | 4.108e-05
2010 | 2009-05-23 | C | 11 | 0.0051888 | 3.476e-05
2010 | 2009-05-23 | C | 749 | 0.023669 | 0.0023669
2010 | 2009-05-23 | C | 187 | 0.06685 | 0.00059092
2010 | 2009-05-23 | C | 273 | 0.04722 | 0.00086269
2010 | 2009-05-24 | B | 76 | 0.0069647 | 0.00024016
2010 | 2009-05-24 | C | 560 | 0.028314 | 0.0017696
2010 | 2009-05-24 | C | 77 | 0.11168 | 0.00024332
2010 | 2009-05-24 | C | 31 | 0.011755 | 9.7961e-05
2010 | 2009-05-24 | C | 360 | 0.063735 | 0.0011376
2010 | 2009-05-24 | C | 228 | 0.061469 | 0.00072049
2010 | 2009-05-24 | C | 60 | 0.0062569 | 0.0001896
2010 | 2009-05-24 | C | 61 | 0.011566 | 0.00019276
2010 | 2009-05-24 | C | 2 | 0.001915 | 6.3201e-06
2010 | 2009-05-24 | C | 3 | 0.000237 | 9.4801e-06
2010 | 2009-05-24 | C | 309 | 0.010741 | 0.00097645
2010 | 2009-05-24 | C | 85 | 0.034966 | 0.0002686
2010 | 2009-05-24 | C | 258 | 0.08212 | 0.00081529
2010 | 2009-05-24 | C | 7 | 0.0032295 | 2.212e-05
2010 | 2009-05-24 | C | 348 | 0.015945 | 0.0010997
2010 | 2009-05-24 | C | 3 | 0.0028725 | 9.4801e-06
2010 | 2009-05-24 | C | 5 | 0.0002054 | 1.58e-05
2010 | 2009-05-24 | C | 187 | 0.08175 | 0.00059092
2010 | 2009-05-22 | C | 160 | 0.062379 | 0.0005056
2010 | 2009-05-24 | C | 41 | 0.0077737 | 0.00012956
2010 | 2009-05-24 | C | 31 | 0.0032327 | 9.7961e-05
2010 | 2009-05-24 | C | 219 | 0.10056 | 0.00069205
2010 | 2009-05-24 | C | 71 | 0.10545 | 0.00022436
2010 | 2009-05-24 | C | 248 | 0.22438 | 0.00078369
2010 | 2009-05-25 | C | 143 | 0.0045188 | 0.00045188
2010 | 2009-05-25 | B | 1 | 0.0010523 | 3.16e-06
2010 | 2009-05-25 | B | 61 | 0.034312 | 0.00019276
2010 | 2009-05-25 | C | 12 | 0.005688 | 3.792e-05
2010 | 2009-05-25 | C | 18 | 0.0057449 | 5.688e-05
2010 | 2009-05-25 | C | 435 | 0.023368 | 0.0013746
2010 | 2009-05-25 | C | 89 | 0.020531 | 0.00028124
2010 | 2009-05-25 | C | 29 | 0.02181 | 9.1641e-05
2010 | 2009-05-25 | C | 145 | 0.10484 | 0.0004582
2010 | 2009-05-25 | C | 209 | 0.06327 | 0.00066045
2010 | 2009-05-25 | B | 163 | 0.14268 | 0.00051508
2010 | 2009-05-25 | B | 74 | 0.068282 | 0.00023384
2010 | 2009-05-25 | C | 249 | 0.024392 | 0.00078685
2010 | 2009-05-26 | B | 22 | 0.022455 | 6.9521e-05
2010 | 2009-05-26 | C | 7293 | 0.2545 | 0.023046
2010 | 2009-05-26 | C | 6 | 0.001422 | 1.896e-05
2010 | 2009-05-27 | C | 963 | 0.091293 | 0.0030431
2010 | 2009-05-27 | B | 46 | 0.015118 | 0.00014536
2010 | 2009-05-27 | B | 187 | 0.050229 | 0.00059092
2010 | 2009-05-27 | B | 15 | 0.0089587 | 4.74e-05
2010 | 2009-05-27 | B | 46 | 0.049132 | 0.00014536
2010 | 2009-05-27 | B | 519 | 0.59042 | 0.0016401
2010 | 2009-05-27 | B | 379 | 0.20275 | 0.0011976
2010 | 2009-05-27 | B | 105 | 0.033986 | 0.0003318
2010 | 2009-05-27 | C | 25 | 0.017775 | 7.9001e-05
2010 | 2009-05-28 | C | 824 | 0.25562 | 0.0026039
2010 | 2009-05-27 | C | 279 | 0.074498 | 0.00088165
2010 | 2009-05-28 | C | 1812 | 0.26339 | 0.005726
2010 | 2009-05-28 | B | 11 | 0.0048317 | 3.476e-05
2010 | 2009-05-28 | B | 397 | 0.19445 | 0.0012545
2010 | 2009-05-28 | B | 3 | 0.00046452 | 9.4801e-06
2010 | 2009-05-28 | B | 6 | 0.0070342 | 1.896e-05
2010 | 2009-05-28 | B | 1 | 0.00055616 | 3.16e-06
2010 | 2009-05-29 | B | 257 | 0.01137 | 0.00081213
2010 | 2009-05-29 | B | 478 | 0.17371 | 0.0015105
2010 | 2009-05-28 | B | 257 | 0.01137 | 0.00081213
2010 | 2009-05-29 | B | 636 | 0.18088 | 0.0020098
2010 | 2009-05-29 | B | 2 | 0.0013399 | 6.3201e-06
2010 | 2009-05-29 | B | 54 | 0.043855 | 0.00017064
2010 | 2009-05-29 | B | 2 | 0.00084057 | 6.3201e-06
2010 | 2009-05-29 | B | 27 | 0.031313 | 8.5321e-05
2010 | 2009-05-29 | B | 5 | 0.004819 | 1.58e-05
2010 | 2009-05-29 | C | 813 | 0.025691 | 0.0025691
2010 | 2009-05-29 | C | 32 | 0.0070785 | 0.00010112
2010 | 2009-05-29 | C | 88 | 0.037263 | 0.00027808
2010 | 2009-05-29 | C | 888 | 0.056122 | 0.0028061
2010 | 2009-05-30 | C | 353 | 0.04462 | 0.0011155
2010 | 2009-05-30 | C | 169 | 0.0053404 | 0.00053404
2010 | 2009-05-30 | C | 256 | 0.013086 | 0.00080897
2010 | 2009-05-31 | B | 55 | 0.019987 | 0.0001738
2010 | 2009-05-30 | C | 369 | 0.091094 | 0.001166
2010 | 2009-05-30 | C | 162 | 0.062259 | 0.00051192
2010 | 2009-05-31 | C | 15 | 0.003081 | 4.74e-05
2010 | 2009-05-31 | C | 60 | 0.0043608 | 0.0001896
2010 | 2009-05-31 | C | 1325 | 0.072658 | 0.004187
2010 | 2009-05-31 | C | 267 | 0.042193 | 0.00084373
2010 | 2009-05-31 | C | 31 | 0.0052899 | 9.7961e-05
2010 | 2009-05-31 | C | 54 | 0.004778 | 0.00017064
2010 | 2009-06-01 | C | 187 | 0.0088639 | 0.00059092
2010 | 2009-05-31 | B | 45 | 0.015927 | 0.0001422
2010 | 2009-05-31 | C | 1 | 0.0042818 | 3.16e-06
2010 | 2009-05-31 | C | 54 | 0.015358 | 0.00017064
2010 | 2009-05-31 | C | 370 | 0.053553 | 0.0011692
2010 | 2009-06-01 | C | 230 | 0.044695 | 0.00072681
2010 | 2009-05-29 | B | 92 | 0.059598 | 0.00029072
2010 | 2009-05-29 | C | 112 | 0.019466 | 0.00035392
2010 | 2009-06-02 | B | 7 | 0.0021457 | 2.212e-05
2010 | 2009-05-26 | B | 5 | 0.003792 | 1.58e-05
2010 | 2009-05-26 | B | 361 | 0.29533 | 0.0011408
2010 | 2009-05-26 | B | 5 | 0.003792 | 1.58e-05
2010 | 2009-06-02 | B | 112 | 0.036454 | 0.00035392
2010 | 2009-06-02 | C | 4 | 0.00042976 | 1.264e-05
2010 | 2009-06-02 | C | 466 | 0.014726 | 0.0014726
2010 | 2009-06-02 | B | 42 | 0.032118 | 0.00013272
2010 | 2009-06-02 | B | 6 | 0.0029767 | 1.896e-05
2010 | 2009-06-02 | C | 279 | 0.045362 | 0.00088165
2010 | 2009-06-02 | C | 286 | 0.10299 | 0.00090377
2010 | 2009-06-02 | B | 8 | 0.0012893 | 2.528e-05
2010 | 2009-06-03 | C | 688 | 0.021741 | 0.0021741
2010 | 2009-06-03 | B | 52 | 0.023169 | 0.00016432
2010 | 2009-06-02 | B | 65 | 0.038616 | 0.0002054
2010 | 2009-06-03 | B | 32 | 0.042673 | 0.00010112
2010 | 2009-06-03 | B | 5 | 0.001422 | 1.58e-05
2010 | 2009-06-03 | B | 13 | 0.0066139 | 4.108e-05
2010 | 2009-06-03 | B | 98 | 0.10093 | 0.00030968
2010 | 2009-06-03 | B | 15 | 0.0032706 | 4.74e-05
2010 | 2009-06-04 | C | 362 | 0.028598 | 0.0011439
2010 | 2009-06-04 | C | 424 | 0.0053594 | 0.0013399
2010 | 2009-06-04 | B | 14 | 0.0035392 | 4.424e-05
2010 | 2009-06-04 | B | 10 | 0.001896 | 3.16e-05
2010 | 2009-06-04 | B | 29 | 0.016954 | 9.1641e-05
2010 | 2009-06-04 | B | 14 | 0.0097329 | 4.424e-05
2010 | 2009-06-04 | B | 1 | 0.0003792 | 3.16e-06
2010 | 2009-06-04 | B | 147 | 0.11288 | 0.00046452
2010 | 2009-06-04 | C | 261 | 0.11105 | 0.00082477
2010 | 2009-06-04 | B | 30 | 0.032706 | 9.4801e-05
2010 | 2009-06-04 | B | 25 | 0.0094801 | 7.9001e-05
2010 | 2009-06-04 | B | 27 | 0.032934 | 8.5321e-05
2010 | 2009-06-04 | B | 1 | 0.00097013 | 3.16e-06
2010 | 2009-06-04 | B | 15 | 0.014268 | 4.74e-05
2010 | 2009-06-04 | C | 272 | 0.023207 | 0.00085953
2010 | 2009-06-04 | C | 105 | 0.10172 | 0.0003318
2010 | 2009-06-04 | B | 16 | 0.0057639 | 5.056e-05
2010 | 2009-06-05 | C | 29 | 0.0010997 | 9.1641e-05
2010 | 2009-06-05 | B | 45 | 0.046926 | 0.0001422
2010 | 2009-06-05 | B | 10 | 0.0065413 | 3.16e-05
2010 | 2009-06-05 | B | 4 | 0.0018581 | 1.264e-05
2010 | 2009-06-05 | B | 3 | 0.0012324 | 9.4801e-06
2010 | 2009-06-06 | C | 696 | 0.14324 | 0.0021994
2010 | 2009-06-06 | C | 171 | 0.00054036 | 0.00054036
2010 | 2009-06-06 | B | 166 | 0.099667 | 0.00052456
2010 | 2009-06-06 | B | 5 | 0.0071891 | 1.58e-05
2010 | 2009-06-06 | C | 875 | 0.11957 | 0.002765
2010 | 2009-06-05 | C | 279 | 0.43433 | 0.00088165
2010 | 2009-06-07 | C | 67 | 0.012492 | 0.00021172
2010 | 2009-06-08 | C | 520 | 0.11145 | 0.0016432
2010 | 2009-06-08 | C | 127 | 0.065014 | 0.00040132
2010 | 2009-06-08 | C | 25 | 0.003081 | 7.9001e-05
2010 | 2009-06-08 | B | 16 | 0.006674 | 5.056e-05
2010 | 2009-06-08 | B | 106 | 0.082066 | 0.00033496
2010 | 2009-06-08 | B | 5 | 0.0032074 | 1.58e-05
2010 | 2009-06-08 | B | 3 | 0.0034602 | 9.4801e-06
2010 | 2009-06-08 | C | 58 | 0.021994 | 0.00018328
2010 | 2009-06-08 | C | 3235 | 0.87915 | 0.010223
2010 | 2009-06-08 | C | 125 | 0.027255 | 0.000395
2010 | 2009-06-08 | C | 282 | 0.086597 | 0.00089113
2010 | 2009-06-09 | C | 1 | 0.00016116 | 3.16e-06
2010 | 2009-06-09 | C | 1 | 0.0001264 | 3.16e-06
2010 | 2009-06-09 | C | 17 | 0.0017191 | 5.372e-05
2010 | 2009-06-09 | C | 15 | 0.001422 | 4.74e-05
2010 | 2009-06-09 | B | 31 | 0.035168 | 9.7961e-05
2010 | 2009-06-09 | C | 24 | 0.0072807 | 7.5841e-05
2010 | 2009-06-09 | C | 11 | 0.00086901 | 3.476e-05
2010 | 2009-06-10 | C | 471 | 0.038862 | 0.0014884
2010 | 2009-06-10 | B | 58 | 0.015029 | 0.00018328
2010 | 2009-06-10 | C | 727 | 0.052839 | 0.0022973
2010 | 2009-06-10 | B | 258 | 0.19569 | 0.00081529
2010 | 2009-06-10 | C | 10 | 0.0013588 | 3.16e-05
2010 | 2009-06-10 | C | 10 | 0.00066361 | 3.16e-05
2010 | 2009-06-10 | C | 289 | 0.059374 | 0.00091325
2010 | 2009-06-10 | C | 553 | 0.29183 | 0.0017475
2010 | 2009-06-11 | C | 237 | 0.051894 | 0.00074893
2010 | 2009-06-10 | C | 1302 | 0.37104 | 0.0041144
2010 | 2009-06-11 | B | 7 | 0.0069236 | 2.212e-05
2010 | 2009-06-11 | B | 3 | 0.0031284 | 9.4801e-06
2010 | 2009-06-11 | B | 2 | 0.0001896 | 6.3201e-06
2010 | 2009-06-11 | B | 3 | 0.0016875 | 9.4801e-06
2010 | 2009-06-11 | B | 10 | 0.010807 | 3.16e-05
2010 | 2009-06-11 | B | 18 | 0.019624 | 5.688e-05
2010 | 2009-06-11 | B | 12 | 0.0094801 | 3.792e-05
2010 | 2009-06-11 | C | 39 | 0.03081 | 0.00012324
2010 | 2009-06-11 | C | 715 | 0.12971 | 0.0022594
2010 | 2009-06-11 | C | 822 | 0.067147 | 0.0025975
2010 | 2009-06-12 | B | 277 | 0.08175 | 0.00087533
2010 | 2009-06-13 | C | 391 | 0.071663 | 0.0012356
2010 | 2009-06-13 | C | 36 | 0.00091009 | 0.00011376
2010 | 2009-06-13 | C | 1027 | 0.63136 | 0.0032453
2010 | 2009-06-13 | C | 412 | 0.17926 | 0.0013019
2010 | 2009-06-13 | C | 1116 | 0.0070532 | 0.0035266
2010 | 2009-06-13 | B | 20 | 0.026544 | 6.3201e-05
2010 | 2009-06-14 | B | 8 | 0.0064717 | 2.528e-05
2010 | 2009-06-15 | B | 88 | 0.083147 | 0.00027808
2010 | 2009-06-15 | C | 36 | 0.0043229 | 0.00011376
2010 | 2009-06-14 | C | 254 | 0.068901 | 0.00080265
2010 | 2009-06-15 | C | 749 | 0.03787 | 0.0023669
2010 | 2009-06-16 | B | 7 | 0.0048222 | 2.212e-05
2010 | 2009-06-16 | B | 46 | 0.035759 | 0.00014536
2010 | 2009-06-16 | B | 32 | 0.035999 | 0.00010112
2010 | 2009-06-16 | C | 76 | 0.020174 | 0.00024016
2010 | 2009-06-15 | C | 161 | 0.028598 | 0.00050876
2010 | 2009-06-16 | C | 120 | 0.15654 | 0.0003792
2010 | 2009-06-17 | C | 32 | 0.010112 | 0.00010112
2010 | 2009-06-17 | C | 114 | 0.024863 | 0.00036024
2010 | 2009-06-17 | C | 214 | 0.066136 | 0.00067625
2010 | 2009-06-19 | B | 24 | 0.020477 | 7.5841e-05
2010 | 2009-06-17 | B | 109 | 0.064066 | 0.00034444
2010 | 2009-06-17 | B | 45 | 0.033702 | 0.0001422
2010 | 2009-06-17 | C | 788 | 1.7059 | 0.0024901
2010 | 2009-06-17 | C | 732 | 0.13471 | 0.0023131
2010 | 2009-06-17 | C | 5 | 0.000474 | 1.58e-05
2010 | 2009-06-16 | B | 5 | 0.0038868 | 1.58e-05
2010 | 2009-06-17 | C | 47 | 0.022575 | 0.00014852
2010 | 2009-06-18 | C | 221 | 0.0069837 | 0.00069837
2010 | 2009-06-18 | C | 94 | 0.020793 | 0.00029704
2010 | 2009-06-18 | C | 188 | 0.0059408 | 0.00059408
2010 | 2009-06-18 | B | 1 | 0.00064149 | 3.16e-06
2010 | 2009-06-18 | B | 41 | 0.045865 | 0.00012956
2010 | 2009-06-18 | B | 37 | 0.023384 | 0.00011692
2010 | 2009-06-18 | B | 117 | 0.084297 | 0.00036972
2010 | 2009-06-18 | B | 4 | 0.0010238 | 1.264e-05
2010 | 2009-06-18 | B | 72 | 0.086686 | 0.00022752
2010 | 2009-06-18 | B | 2 | 0.0022752 | 6.3201e-06
2010 | 2009-06-18 | B | 100 | 0.08995 | 0.000316
2010 | 2009-06-18 | B | 89 | 0.075414 | 0.00028124
2010 | 2009-06-18 | C | 66 | 0.026487 | 0.00020856
2010 | 2009-06-19 | C | 96 | 0.046389 | 0.00030336
2010 | 2009-06-19 | B | 24 | 0.016912 | 7.5841e-05
2010 | 2009-06-19 | B | 13 | 0.01331 | 4.108e-05
2010 | 2009-06-19 | C | 334 | 0.084278 | 0.0010554
2010 | 2009-06-19 | C | 18 | 0.0020477 | 5.688e-05
2010 | 2009-06-20 | B | 30 | 0.031284 | 9.4801e-05
2010 | 2009-06-20 | C | 579 | 0.092898 | 0.0018297
2010 | 2009-06-20 | C | 2165 | 0.43264 | 0.0068415
2010 | 2009-06-21 | B | 10 | 0.0063517 | 3.16e-05
2010 | 2009-06-21 | B | 114 | 0.067536 | 0.00036024
2010 | 2009-06-21 | B | 1 | 0.00047716 | 3.16e-06
2010 | 2009-06-21 | C | 14 | 0.0015484 | 4.424e-05
2010 | 2009-06-17 | B | 165 | 0.039105 | 0.0005214
2010 | 2009-06-22 | B | 9 | 0.0099256 | 2.844e-05
2010 | 2009-06-23 | B | 267 | 0.16168 | 0.00084373
2010 | 2009-06-23 | B | 2 | 0.00023384 | 6.3201e-06
2010 | 2009-06-23 | C | 2553 | 0.16942 | 0.0080675
2010 | 2009-06-23 | B | 57 | 0.0021615 | 0.00018012
2010 | 2009-06-23 | B | 43 | 0.038862 | 0.00013588
2010 | 2009-06-23 | B | 653 | 0.6273 | 0.0020635
2010 | 2009-06-23 | B | 20 | 0.026165 | 6.3201e-05
2010 | 2009-06-23 | C | 406 | 0.017962 | 0.001283
2010 | 2009-06-23 | B | 79 | 0.036448 | 0.00024964
2010 | 2009-06-23 | B | 22 | 0.018075 | 6.9521e-05
2010 | 2009-06-23 | C | 121 | 0.00076473 | 0.00038236
2010 | 2009-06-23 | B | 3 | 0.0011376 | 9.4801e-06
2010 | 2009-06-24 | C | 25 | 0.00158 | 7.9001e-05
2010 | 2009-06-24 | B | 83 | 0.073439 | 0.00026228
2010 | 2009-06-24 | C | 5 | 0.0012956 | 1.58e-05
2010 | 2009-06-24 | B | 180 | 0.068257 | 0.0005688
2010 | 2009-06-24 | B | 2 | 0.00079633 | 6.3201e-06
2010 | 2009-06-24 | B | 88 | 0.10623 | 0.00027808
2010 | 2009-06-24 | C | 739 | 0.14997 | 0.0023353
2010 | 2009-06-25 | C | 369 | 0.1452 | 0.001166
2010 | 2009-06-24 | B | 164 | 0.21196 | 0.00051824
2010 | 2009-06-25 | C | 1061 | 0.044484 | 0.0033528
2010 | 2009-06-25 | B | 35 | 0.035945 | 0.0001106
2010 | 2009-06-25 | B | 12 | 0.014865 | 3.792e-05
2010 | 2009-06-25 | B | 7 | 0.0087596 | 2.212e-05
2010 | 2009-06-25 | B | 408 | 0.5055 | 0.0012893
2010 | 2009-06-25 | C | 23 | 0.00705 | 7.2681e-05
2010 | 2009-06-26 | C | 933 | 0.27764 | 0.0029483
2010 | 2009-06-26 | C | 31 | 0.0051919 | 9.7961e-05
2010 | 2009-06-26 | B | 52 | 0.026784 | 0.00016432
2010 | 2009-06-26 | B | 1 | 0.00066045 | 3.16e-06
2010 | 2009-06-26 | B | 11 | 0.0072301 | 3.476e-05
2010 | 2009-06-26 | C | 136 | 0.034877 | 0.00042976
2010 | 2009-06-26 | C | 749 | 0.030769 | 0.0023669
2010 | 2009-06-26 | C | 12 | 0.0013651 | 3.792e-05
2010 | 2009-06-26 | C | 63 | 0.0079633 | 0.00019908
2010 | 2009-06-27 | B | 41 | 0.062319 | 0.00012956
2010 | 2009-06-28 | C | 726 | 0.13635 | 0.0022942
2010 | 2009-06-28 | C | 199 | 0.045233 | 0.00062885
2010 | 2009-06-26 | B | 289 | 0.042923 | 0.00091325
2010 | 2009-06-29 | B | 2 | 0.00082161 | 6.3201e-06
2010 | 2009-06-29 | B | 31 | 0.011755 | 9.7961e-05
2010 | 2009-06-29 | C | 826 | 0.34265 | 0.0026102
2010 | 2009-06-28 | C | 38 | 0.078173 | 0.00012008
2010 | 2009-06-29 | C | 40 | 0.016179 | 0.0001264
2010 | 2009-06-29 | C | 232 | 0.26893 | 0.00073313
2010 | 2009-06-29 | C | 2258 | 0.47093 | 0.0071353
2010 | 2009-06-29 | C | 25 | 0.037525 | 7.9001e-05
2010 | 2009-06-26 | B | 200 | 0.036024 | 0.00063201
2010 | 2009-06-29 | C | 5 | 0.0034128 | 1.58e-05
2010 | 2009-06-29 | C | 11 | 0.0011123 | 3.476e-05
2010 | 2009-06-29 | C | 630 | 0.15927 | 0.0019908
2010 | 2009-06-29 | C | 28 | 0.0029199 | 8.8481e-05
2010 | 2009-06-29 | C | 32 | 0.0022247 | 0.00010112
2010 | 2009-06-29 | C | 38 | 0.022575 | 0.00012008
2010 | 2009-06-28 | C | 26 | 0.0023005 | 8.2161e-05
2010 | 2009-06-29 | C | 112 | 0.096975 | 0.00035392
2010 | 2009-06-28 | C | 1905 | 0.46165 | 0.0060198
2010 | 2009-06-29 | C | 277 | 0.08746 | 0.00087533
2010 | 2009-06-29 | C | 203 | 0.15162 | 0.00064149
2010 | 2009-06-29 | C | 404 | 0.19923 | 0.0012767
2010 | 2009-06-28 | C | 190 | 0.13539 | 0.0006004
2010 | 2009-06-29 | C | 732 | 0.6425 | 0.0023131
2010 | 2009-06-29 | C | 14 | 0.0015927 | 4.424e-05
2010 | 2009-06-29 | C | 19 | 0.011948 | 6.004e-05
2010 | 2009-06-29 | C | 371 | 0.026964 | 0.0011724
2010 | 2009-06-28 | C | 323 | 0.28555 | 0.0010207
2010 | 2009-06-28 | C | 339 | 0.18089 | 0.0010712
2010 | 2009-06-29 | C | 348 | 0.030791 | 0.0010997
2010 | 2009-06-30 | B | 2 | 0.00065729 | 6.3201e-06
2010 | 2009-06-30 | B | 48 | 0.028819 | 0.00015168
2010 | 2009-06-30 | C | 29 | 0.0004582 | 9.1641e-05
2010 | 2009-06-30 | C | 21 | 0.0037162 | 6.6361e-05
2010 | 2009-06-30 | C | 18 | 0.0044367 | 5.688e-05
2010 | 2009-06-29 | B | 27 | 0.027644 | 8.5321e-05
2010 | 2009-06-30 | C | 364 | 0.08795 | 0.0011502
2010 | 2009-07-01 | C | 13 | 0.0019308 | 4.108e-05
2010 | 2009-06-30 | C | 53 | 0.10669 | 0.00016748
2010 | 2009-07-01 | C | 1 | 9.7961e-05 | 3.16e-06
2010 | 2009-07-01 | C | 149 | 0.0070627 | 0.00047084
2010 | 2009-07-01 | B | 79 | 0.082344 | 0.00024964
2010 | 2009-07-01 | B | 39 | 0.041902 | 0.00012324
2010 | 2009-07-02 | B | 1 | 0.00043292 | 3.16e-06
2010 | 2009-07-02 | B | 52 | 0.023991 | 0.00016432
2010 | 2009-07-02 | B | 13 | 0.0050118 | 4.108e-05
2010 | 2009-07-03 | C | 16 | 0.010567 | 5.056e-05
2010 | 2009-07-03 | C | 29 | 0.0028409 | 9.1641e-05
2010 | 2009-07-03 | B | 27 | 0.024743 | 8.5321e-05
2010 | 2009-07-03 | B | 8 | 0.0083425 | 2.528e-05
2010 | 2009-07-03 | B | 18 | 0.0085889 | 5.688e-05
2010 | 2009-07-03 | B | 1 | 0.0011376 | 3.16e-06
2010 | 2009-07-03 | B | 1 | 0.0003318 | 3.16e-06
2010 | 2009-07-03 | B | 5 | 0.003792 | 1.58e-05
2010 | 2009-07-04 | B | 18 | 0.013708 | 5.688e-05
2010 | 2009-07-05 | C | 284 | 0.21987 | 0.00089745
2010 | 2009-07-05 | C | 1639 | 0.66173 | 0.0051793
2010 | 2009-07-05 | C | 248 | 0.20663 | 0.00078369
2010 | 2009-07-03 | B | 149 | 0.062764 | 0.00047084
2010 | 2009-07-06 | B | 78 | 0.063346 | 0.00024648
2010 | 2009-07-06 | C | 736 | 0.28523 | 0.0023258
2010 | 2009-07-06 | B | 33 | 0.015746 | 0.00010428
2010 | 2009-07-06 | C | 83 | 0.016261 | 0.00026228
2010 | 2009-07-06 | B | 3 | 0.0021425 | 9.4801e-06
2010 | 2009-07-07 | B | 1 | 0.00043292 | 3.16e-06
2010 | 2009-07-07 | C | 83 | 0.0055079 | 0.00026228
2010 | 2009-07-07 | C | 605 | 0.075161 | 0.0019118
2010 | 2009-07-07 | B | 33 | 0.032327 | 0.00010428
2010 | 2009-07-07 | B | 19 | 0.021494 | 6.004e-05
2010 | 2009-07-07 | C | 36 | 0.012855 | 0.00011376
2010 | 2009-07-07 | B | 8 | 0.0056628 | 2.528e-05
2010 | 2009-07-07 | B | 36 | 0.041181 | 0.00011376
2010 | 2009-07-07 | C | 10 | 0.017728 | 3.16e-05
2010 | 2009-07-07 | C | 28 | 0.024244 | 8.8481e-05
2010 | 2009-07-08 | B | 24 | 0.020325 | 7.5841e-05
2010 | 2009-07-08 | B | 44 | 0.04491 | 0.00013904
2010 | 2009-07-08 | C | 48 | 0.017747 | 0.00015168
2010 | 2009-07-08 | C | 51 | 0.021596 | 0.00016116
2010 | 2009-07-08 | B | 19 | 0.0090661 | 6.004e-05
2010 | 2009-07-09 | C | 14 | 0.0040701 | 4.424e-05
2010 | 2009-07-09 | B | 6 | 0.0044936 | 1.896e-05
2010 | 2009-07-09 | B | 14 | 0.013007 | 4.424e-05
2010 | 2009-07-09 | B | 19 | 0.018553 | 6.004e-05
2010 | 2009-07-09 | C | 7 | 0.00084057 | 2.212e-05
2010 | 2009-07-09 | B | 60 | 0.013272 | 0.0001896
2010 | 2009-07-10 | C | 470 | 0.037304 | 0.0014852
2010 | 2009-07-09 | B | 10 | 0.014915 | 3.16e-05
2010 | 2009-07-10 | B | 2 | 0.00095433 | 6.3201e-06
2010 | 2009-07-10 | C | 21 | 0.00046452 | 6.6361e-05
2010 | 2009-07-10 | C | 54 | 0.025426 | 0.00017064
2010 | 2009-07-11 | C | 10 | 0.0046452 | 3.16e-05
2010 | 2009-07-11 | C | 265 | 0.1044 | 0.00083741
2010 | 2009-07-11 | C | 8292 | 21.3554 | 0.026203
2010 | 2009-07-12 | C | 1703 | 1.4162 | 0.0053815
2010 | 2009-07-11 | C | 2289 | 5.9819 | 0.0072333
2010 | 2009-07-12 | C | 66 | 0.012097 | 0.00020856
2010 | 2009-07-12 | C | 1123 | 0.28458 | 0.0035487
2010 | 2009-07-12 | C | 12 | 0.00094801 | 3.792e-05
2010 | 2009-07-12 | C | 295 | 0.20967 | 0.00093221
2010 | 2009-07-12 | C | 69 | 0.10292 | 0.00021804
2010 | 2009-07-12 | C | 158 | 0.063422 | 0.00049928
2010 | 2009-07-12 | C | 3 | 0.00084373 | 9.4801e-06
2010 | 2009-07-12 | C | 213 | 0.065962 | 0.00067309
2010 | 2009-07-12 | C | 31 | 0.0038205 | 9.7961e-05
2010 | 2009-07-12 | C | 605 | 0.32473 | 0.0019118
2010 | 2009-07-12 | C | 569 | 0.13596 | 0.0017981
2010 | 2009-07-12 | C | 472 | 0.43858 | 0.0014915
2010 | 2009-07-12 | C | 53 | 0.029979 | 0.00016748
2010 | 2009-07-12 | B | 1 | 0.00030652 | 3.16e-06
2010 | 2009-07-12 | C | 1 | 0.0042787 | 3.16e-06
2010 | 2009-07-13 | C | 3 | 0.00048348 | 9.4801e-06
2010 | 2009-07-13 | C | 5 | 0.0010428 | 1.58e-05
2010 | 2009-07-12 | C | 3 | 0.015746 | 9.4801e-06
2010 | 2009-07-13 | B | 78 | 0.014675 | 0.00024648
2010 | 2009-07-13 | B | 15 | 0.010618 | 4.74e-05
2010 | 2009-07-12 | B | 25 | 0.041485 | 7.9001e-05
2010 | 2009-07-13 | C | 158 | 0.081766 | 0.00049928
2010 | 2009-07-13 | C | 270 | 0.057083 | 0.00085321
2010 | 2009-07-12 | C | 610 | 0.028851 | 0.0019276
2010 | 2009-07-14 | C | 20 | 0.0021488 | 6.3201e-05
2010 | 2009-07-14 | C | 156 | 0.047325 | 0.00049296
2010 | 2009-07-13 | B | 1 | 0.00081213 | 3.16e-06
2010 | 2009-07-14 | B | 7 | 0.0064149 | 2.212e-05
2010 | 2009-07-14 | B | 408 | 0.33522 | 0.0012893
2010 | 2009-07-14 | B | 33 | 0.036185 | 0.00010428
2010 | 2009-07-14 | B | 5 | 0.005846 | 1.58e-05
2010 | 2009-07-14 | B | 30 | 0.031853 | 9.4801e-05
2010 | 2009-07-14 | B | 98 | 0.067201 | 0.00030968
2010 | 2009-07-14 | B | 32 | 0.024269 | 0.00010112
2010 | 2009-07-14 | B | 263 | 0.40308 | 0.00083109
2010 | 2009-07-14 | C | 3 | 0.0034697 | 9.4801e-06
2010 | 2009-07-14 | C | 549 | 0.18187 | 0.0017349
2010 | 2009-07-14 | C | 22 | 0.0018771 | 6.9521e-05
2010 | 2009-07-14 | C | 240 | 0.0857 | 0.00075841
2010 | 2009-07-14 | B | 161 | 0.0091578 | 0.00050876
2010 | 2009-07-14 | B | 239 | 0.012839 | 0.00075525
2010 | 2009-07-14 | C | 502 | 0.44763 | 0.0015863
2010 | 2009-07-15 | C | 713 | 0.15054 | 0.0022531
2010 | 2009-07-15 | B | 61 | 0.047805 | 0.00019276
2010 | 2009-07-15 | B | 26 | 0.029578 | 8.2161e-05
2010 | 2009-07-15 | B | 30 | 0.038489 | 9.4801e-05
2010 | 2009-07-15 | B | 19 | 0.016031 | 6.004e-05
2010 | 2009-07-15 | C | 1 | 0.00017696 | 3.16e-06
2010 | 2009-07-15 | C | 749 | 0.023669 | 0.0023669
2010 | 2009-07-16 | B | 179 | 0.0090503 | 0.00056564
2010 | 2009-07-16 | B | 181 | 0.011439 | 0.00057196
2010 | 2009-07-15 | B | 57 | 0.0025217 | 0.00018012
2010 | 2009-07-15 | B | 57 | 0.0019813 | 0.00018012
2010 | 2009-07-15 | B | 102 | 0.0035455 | 0.00032232
2010 | 2009-07-16 | C | 75 | 0.022041 | 0.000237
2010 | 2009-07-16 | C | 34 | 0.012893 | 0.00010744
2010 | 2009-07-16 | B | 31 | 0.036833 | 9.7961e-05
2010 | 2009-07-16 | B | 3 | 0.0014125 | 9.4801e-06
2010 | 2009-07-16 | B | 66 | 0.037958 | 0.00020856
2010 | 2009-07-16 | B | 19 | 0.01537 | 6.004e-05
2010 | 2009-07-15 | B | 32 | 0.028718 | 0.00010112
2010 | 2009-07-16 | B | 19 | 0.020114 | 6.004e-05
2010 | 2009-07-16 | C | 734 | 0.16108 | 0.0023195
2010 | 2009-07-16 | B | 26 | 0.002547 | 8.2161e-05
2010 | 2009-07-17 | B | 61 | 0.039131 | 0.00019276
2010 | 2009-07-17 | B | 4 | 0.0039311 | 1.264e-05
2010 | 2009-07-17 | B | 1 | 0.0012198 | 3.16e-06
2010 | 2009-07-17 | B | 223 | 0.20577 | 0.00070469
2010 | 2009-07-17 | B | 39 | 0.01331 | 0.00012324
2010 | 2009-07-17 | B | 1 | 0.00011692 | 3.16e-06
2010 | 2009-07-17 | B | 39 | 0.015405 | 0.00012324
2010 | 2009-07-17 | C | 9 | 0.0011945 | 2.844e-05
2010 | 2009-07-17 | B | 18 | 0.0062569 | 5.688e-05
2010 | 2009-07-18 | C | 187 | 0.10518 | 0.00059092
2010 | 2009-07-18 | C | 29 | 0.002291 | 9.1641e-05
2010 | 2009-07-18 | C | 116 | 0.087975 | 0.00036656
2010 | 2009-07-18 | C | 23 | 0.0059598 | 7.2681e-05
2010 | 2009-07-18 | C | 14 | 0.0015927 | 4.424e-05
2010 | 2009-07-18 | C | 22 | 0.0020856 | 6.9521e-05
2010 | 2009-07-18 | C | 740 | 0.10717 | 0.0023384
2010 | 2009-07-19 | C | 678 | 0.16615 | 0.0021425
2010 | 2009-07-19 | C | 19 | 0.0066045 | 6.004e-05
2010 | 2009-07-19 | C | 45 | 0.019197 | 0.0001422
2010 | 2009-07-19 | C | 83 | 0.0062948 | 0.00026228
2010 | 2009-07-19 | C | 8 | 0.0013399 | 2.528e-05
2010 | 2009-07-19 | C | 485 | 0.085741 | 0.0015326
2010 | 2009-07-19 | C | 514 | 0.071467 | 0.0016243
2010 | 2009-07-19 | C | 7 | 0.0017475 | 2.212e-05
2010 | 2009-07-19 | C | 41 | 0.0063485 | 0.00012956
2010 | 2009-07-19 | C | 99 | 0.056975 | 0.00031284
2010 | 2009-07-20 | C | 26 | 0.0058334 | 8.2161e-05
2010 | 2009-07-20 | B | 15 | 0.01422 | 4.74e-05
2010 | 2009-07-20 | C | 132 | 0.033787 | 0.00041712
2010 | 2009-07-21 | B | 144 | 0.14334 | 0.00045504
2010 | 2009-07-21 | B | 183 | 0.13416 | 0.00057828
2010 | 2009-07-21 | B | 106 | 0.08776 | 0.00033496
2010 | 2009-07-21 | B | 80 | 0.053088 | 0.0002528
2010 | 2009-07-21 | C | 323 | 0.053076 | 0.0010207
2010 | 2009-07-21 | C | 127 | 0.031705 | 0.00040132
2010 | 2009-07-21 | B | 99 | 0.0037541 | 0.00031284
2010 | 2009-07-21 | B | 37 | 0.031452 | 0.00011692
2010 | 2009-07-21 | B | 34 | 0.036422 | 0.00010744
2010 | 2009-07-21 | C | 323 | 0.17688 | 0.0010207
2010 | 2009-07-21 | C | 19 | 0.010567 | 6.004e-05
2010 | 2009-07-21 | C | 289 | 0.23927 | 0.00091325
2010 | 2009-07-21 | C | 315 | 0.29265 | 0.00099541
2010 | 2009-07-21 | C | 203 | 0.18218 | 0.00064149
2010 | 2009-07-21 | C | 331 | 0.28345 | 0.001046
2010 | 2009-07-21 | C | 636 | 0.098252 | 0.0020098
2010 | 2009-07-21 | C | 331 | 0.21349 | 0.001046
2010 | 2009-07-21 | C | 298 | 0.10641 | 0.00094169
2010 | 2009-07-22 | B | 11 | 0.0076125 | 3.476e-05
2010 | 2009-07-22 | C | 822 | 0.27214 | 0.0025975
2010 | 2009-07-22 | C | 717 | 0.17507 | 0.0022657
2010 | 2009-07-22 | C | 3 | 0.00038868 | 9.4801e-06
2010 | 2009-07-22 | C | 430 | 0.072017 | 0.0013588
2010 | 2009-07-22 | C | 1388 | 0.017544 | 0.0043861
2010 | 2009-07-22 | C | 8 | 0.0087217 | 2.528e-05
2010 | 2009-07-22 | B | 5 | 0.0064307 | 1.58e-05
2010 | 2009-07-21 | C | 293 | 0.60783 | 0.00092589
2010 | 2009-07-22 | C | 2 | 0.00049296 | 6.3201e-06
2010 | 2009-07-23 | B | 10 | 0.010934 | 3.16e-05
2010 | 2009-07-23 | C | 15 | 0.0015168 | 4.74e-05
2010 | 2009-07-23 | C | 17 | 0.0045662 | 5.372e-05
2010 | 2009-07-23 | C | 291 | 0.07057 | 0.00091957
2010 | 2009-07-23 | C | 1 | 0.00029072 | 3.16e-06
2010 | 2009-07-23 | C | 50 | 0.00094801 | 0.000158
2010 | 2009-07-24 | C | 356 | 0.0942 | 0.001125
2010 | 2009-07-23 | B | 70 | 0.066803 | 0.0002212
2010 | 2009-07-23 | B | 8 | 0.0062695 | 2.528e-05
2010 | 2009-07-23 | C | 23 | 0.0045062 | 7.2681e-05
2010 | 2009-07-23 | C | 7 | 0.0013936 | 2.212e-05
2010 | 2009-07-23 | C | 640 | 0.14469 | 0.0020224
2010 | 2009-07-23 | C | 145 | 0.10114 | 0.0004582
2010 | 2009-07-23 | C | 69 | 0.064976 | 0.00021804
2010 | 2009-07-23 | C | 155 | 0.06273 | 0.0004898
2010 | 2009-07-23 | C | 280 | 0.08399 | 0.00088481
2010 | 2009-07-23 | C | 154 | 0.040878 | 0.00048664
2010 | 2009-07-23 | C | 61 | 0.008867 | 0.00019276
2010 | 2009-07-24 | C | 219 | 0.078422 | 0.00069205
2010 | 2009-07-23 | C | 141 | 0.082075 | 0.00044556
2010 | 2009-07-24 | C | 75 | 0.018249 | 0.000237
2010 | 2009-07-24 | C | 5 | 0.002528 | 1.58e-05
2010 | 2009-07-23 | C | 4 | 0.015851 | 1.264e-05
2010 | 2009-07-23 | C | 81 | 0.099547 | 0.00025596
2010 | 2009-07-24 | C | 628 | 0.20837 | 0.0019845
2010 | 2009-07-23 | C | 37 | 0.025489 | 0.00011692
2010 | 2009-07-24 | B | 50 | 0.0158 | 0.000158
2010 | 2009-07-24 | B | 5 | 0.0044556 | 1.58e-05
2010 | 2009-07-24 | C | 9 | 0.00036972 | 2.844e-05
2010 | 2009-07-24 | C | 725 | 0.34533 | 0.002291
2010 | 2009-07-23 | C | 620 | 0.068573 | 0.0019592
2010 | 2009-07-23 | C | 576 | 0.063706 | 0.0018202
2010 | 2009-07-23 | C | 55 | 0.071417 | 0.0001738
2010 | 2009-07-24 | C | 23 | 0.00094485 | 7.2681e-05
2010 | 2009-07-24 | C | 12 | 0.0074324 | 3.792e-05
2010 | 2009-07-24 | C | 12 | 0.010656 | 3.792e-05
2010 | 2009-07-24 | C | 356 | 0.0033749 | 0.001125
2010 | 2009-07-23 | C | 152 | 0.74882 | 0.00048032
2010 | 2009-07-25 | B | 2 | 0.0012008 | 6.3201e-06
2010 | 2009-07-25 | C | 14 | 0.00048664 | 4.424e-05
2010 | 2009-07-26 | C | 134 | 0.0271 | 0.00042344
2010 | 2009-07-25 | C | 361 | 0.01301 | 0.0011408
2010 | 2009-07-26 | C | 59 | 0.0091356 | 0.00018644
2010 | 2009-07-26 | B | 277 | 0.20308 | 0.00087533
2010 | 2009-07-26 | C | 470 | 0.096457 | 0.0014852
2010 | 2009-07-26 | C | 1 | 9.7961e-05 | 3.16e-06
2010 | 2009-07-27 | C | 3 | 0.00055932 | 9.4801e-06
2010 | 2009-07-27 | B | 302 | 0.31684 | 0.00095433
2010 | 2009-07-27 | B | 73 | 0.072665 | 0.00023068
2010 | 2009-07-27 | B | 82 | 0.062189 | 0.00025912
2010 | 2009-07-27 | C | 2 | 0.00012008 | 6.3201e-06
2010 | 2009-07-27 | C | 4 | 0.00040448 | 1.264e-05
2010 | 2009-07-28 | B | 41 | 0.029022 | 0.00012956
2010 | 2009-07-28 | B | 62 | 0.064654 | 0.00019592
2010 | 2009-07-28 | B | 24 | 0.027303 | 7.5841e-05
2010 | 2009-07-28 | B | 4 | 0.00092273 | 1.264e-05
2010 | 2009-07-28 | C | 553 | 0.15203 | 0.0017475
2010 | 2009-07-29 | C | 196 | 0.0386 | 0.00061936
2010 | 2009-07-29 | C | 10 | 0.0030336 | 3.16e-05
2010 | 2009-07-29 | B | 106 | 0.12327 | 0.00033496
2010 | 2009-07-29 | C | 40 | 0.0066993 | 0.0001264
2010 | 2009-07-29 | B | 1 | 0.00043924 | 3.16e-06
2010 | 2009-07-30 | C | 6 | 0.0040385 | 1.896e-05
2010 | 2009-07-29 | C | 1012 | 0.63959 | 0.0031979
2010 | 2009-07-29 | C | 1098 | 0.21635 | 0.0034697
2010 | 2009-07-30 | C | 5 | 0.0017222 | 1.58e-05
2010 | 2009-07-30 | B | 66 | 0.053183 | 0.00020856
2010 | 2009-07-30 | B | 62 | 0.063087 | 0.00019592
2010 | 2009-07-30 | B | 118 | 0.12156 | 0.00037288
2010 | 2009-07-30 | B | 16 | 0.018202 | 5.056e-05
2010 | 2009-07-30 | B | 13 | 0.00069837 | 4.108e-05
2010 | 2009-07-30 | B | 413 | 0.32366 | 0.0013051
2010 | 2009-07-30 | B | 41 | 0.033038 | 0.00012956
2010 | 2009-07-30 | C | 207 | 0.028782 | 0.00065413
2010 | 2009-07-30 | C | 121 | 0.039017 | 0.00038236
2010 | 2009-07-31 | C | 1170 | 0.20704 | 0.0036972
2010 | 2009-07-31 | C | 36 | 0.0081908 | 0.00011376
2010 | 2009-07-31 | C | 42 | 0.0088544 | 0.00013272
2010 | 2009-07-31 | B | 15 | 0.01678 | 4.74e-05
2010 | 2009-07-31 | C | 194 | 0.039848 | 0.00061304
2010 | 2009-07-31 | C | 817 | 0.17296 | 0.0025817
2010 | 2009-07-31 | C | 1613 | 0.12743 | 0.0050971
2010 | 2009-07-31 | C | 207 | 0.013737 | 0.00065413
2010 | 2009-07-31 | C | 121 | 0.014533 | 0.00038236
2010 | 2009-07-31 | C | 1 | 0.00012324 | 3.16e-06
2010 | 2009-07-31 | C | 6 | 0.0018581 | 1.896e-05
2010 | 2009-08-01 | C | 637 | 0.17915 | 0.0020129
2010 | 2009-08-01 | C | 57 | 0.035664 | 0.00018012
2010 | 2009-08-01 | C | 216 | 0.053992 | 0.00068257
2010 | 2009-08-01 | C | 666 | 0.065242 | 0.0021046
2010 | 2009-08-02 | C | 56 | 0.024421 | 0.00017696
2010 | 2009-08-02 | C | 44 | 0.021551 | 0.00013904
2010 | 2009-08-02 | C | 123 | 0.033038 | 0.00038868
2010 | 2009-08-02 | C | 207 | 0.005233 | 0.00065413
2010 | 2009-08-02 | C | 207 | 0.0045789 | 0.00065413
2010 | 2009-08-01 | C | 44 | 0.0040322 | 0.00013904
2010 | 2009-08-01 | C | 47 | 0.0093979 | 0.00014852
2010 | 2009-08-01 | C | 420 | 0.013272 | 0.0013272
2010 | 2009-08-01 | C | 12 | 0.0023511 | 3.792e-05
2010 | 2009-08-01 | C | 3 | 0.0036593 | 9.4801e-06
2010 | 2009-08-02 | C | 123 | 0.077348 | 0.00038868
2010 | 2009-07-31 | B | 2 | 0.0026291 | 6.3201e-06
2010 | 2009-08-03 | B | 1 | 0.0002844 | 3.16e-06
2010 | 2009-08-03 | B | 25 | 0.025043 | 7.9001e-05
2010 | 2009-08-02 | C | 34 | 0.11023 | 0.00010744
2010 | 2009-08-03 | C | 296 | 0.20934 | 0.00093537
2010 | 2009-08-04 | B | 477 | 0.040698 | 0.0015073
2010 | 2009-08-04 | B | 58 | 0.032441 | 0.00018328
2010 | 2009-08-03 | B | 4 | 0.0015168 | 1.264e-05
2010 | 2009-08-04 | C | 204 | 0.057373 | 0.00064465
2010 | 2009-08-04 | C | 83 | 0.068598 | 0.00026228
2010 | 2009-08-04 | C | 98 | 0.02504 | 0.00030968
2010 | 2009-08-04 | C | 1354 | 0.48297 | 0.0042787
2010 | 2009-08-04 | B | 157 | 0.010419 | 0.00049612
2010 | 2009-08-04 | C | 123 | 0.018268 | 0.00038868
2010 | 2009-08-04 | C | 24 | 0.031708 | 7.5841e-05
2010 | 2009-08-04 | B | 106 | 0.11389 | 0.00033496
2010 | 2009-08-04 | B | 51 | 0.058018 | 0.00016116
2010 | 2009-07-04 | B | 53 | 0.055269 | 0.00016748
2010 | 2009-08-04 | C | 11 | 0.0013904 | 3.476e-05
2010 | 2009-08-03 | C | 1 | 0.0093632 | 3.16e-06
2010 | 2009-08-05 | B | 57 | 0.013149 | 0.00018012
2010 | 2009-08-05 | B | 236 | 0.16481 | 0.00074577
2010 | 2009-08-05 | B | 49 | 0.0077421 | 0.00015484
2010 | 2009-08-05 | C | 76 | 0.077332 | 0.00024016
2010 | 2009-08-05 | C | 2570 | 0.024364 | 0.0081213
2010 | 2009-08-05 | C | 1730 | 0.016401 | 0.0054668
2010 | 2009-08-06 | B | 53 | 0.055269 | 0.00016748
2010 | 2009-08-04 | B | 16 | 0.019314 | 5.056e-05
2010 | 2009-08-06 | C | 269 | 0.053152 | 0.00085005
2010 | 2009-08-06 | C | 640 | 0.10472 | 0.0020224
2010 | 2009-08-06 | B | 183 | 0.1544 | 0.00057828
2010 | 2009-08-06 | B | 181 | 0.17502 | 0.00057196
2010 | 2009-08-06 | C | 515 | 0.0016274 | 0.0016274
2010 | 2009-08-06 | C | 6 | 0.0013272 | 1.896e-05
2010 | 2009-08-07 | C | 575 | 0.19939 | 0.001817
2010 | 2009-08-07 | B | 171 | 0.036204 | 0.00054036
2010 | 2009-08-07 | C | 1 | 9.1641e-05 | 3.16e-06
2010 | 2009-08-07 | B | 44 | 0.017936 | 0.00013904
2010 | 2009-08-07 | C | 30 | 0.006162 | 9.4801e-05
2010 | 2009-08-07 | C | 34 | 0.0074134 | 0.00010744
2010 | 2009-08-07 | C | 1404 | 0.15163 | 0.0044367
2010 | 2009-08-07 | C | 168 | 0.15449 | 0.00053088
2010 | 2009-08-08 | C | 166 | 0.011016 | 0.00052456
2010 | 2009-08-08 | C | 2871 | 0.51264 | 0.0090724
2010 | 2009-08-09 | B | 3 | 0.0022373 | 9.4801e-06
2010 | 2009-08-09 | C | 173 | 0.044932 | 0.00054668
2010 | 2009-08-10 | B | 21 | 0.011812 | 6.6361e-05
2010 | 2009-08-10 | B | 2 | 0.0019276 | 6.3201e-06
2010 | 2009-08-10 | C | 486 | 0.050699 | 0.0015358
2010 | 2009-08-10 | C | 120 | 0.018202 | 0.0003792
2010 | 2009-08-10 | C | 31 | 0.0070532 | 9.7961e-05
2010 | 2009-08-11 | C | 5 | 0.0005372 | 1.58e-05
2010 | 2009-08-11 | B | 34 | 0.0361 | 0.00010744
2010 | 2009-08-11 | C | 3 | 0.00063517 | 9.4801e-06
2010 | 2009-08-11 | B | 12 | 0.0060293 | 3.792e-05
2010 | 2009-08-11 | B | 6 | 0.0024079 | 1.896e-05
2010 | 2009-08-11 | B | 103 | 0.11945 | 0.00032548
2010 | 2009-08-12 | B | 263 | 0.13713 | 0.00083109
2010 | 2009-08-12 | B | 31 | 0.019494 | 9.7961e-05
2010 | 2009-08-12 | C | 18 | 0.0068257 | 5.688e-05
2010 | 2009-08-12 | B | 69 | 0.066503 | 0.00021804
2010 | 2009-08-12 | B | 10 | 0.0050876 | 3.16e-05
2010 | 2009-08-12 | C | 3091 | 0.0097676 | 0.0097676
2010 | 2009-08-13 | B | 134 | 0.15498 | 0.00042344
2010 | 2009-08-13 | B | 33 | 0.035247 | 0.00010428
2010 | 2009-08-13 | C | 217 | 0.035452 | 0.00068573
2010 | 2009-08-13 | C | 92 | 0.0034887 | 0.00029072
2010 | 2009-08-13 | B | 14 | 0.017962 | 4.424e-05
2010 | 2009-08-13 | B | 4 | 0.0028567 | 1.264e-05
2010 | 2009-08-14 | C | 131 | 0.062508 | 0.00041396
2010 | 2009-08-14 | C | 58 | 0.001283 | 0.00018328
2010 | 2009-08-14 | B | 15 | 0.0068731 | 4.74e-05
2010 | 2009-08-14 | B | 2 | 0.001896 | 6.3201e-06
2010 | 2009-08-13 | B | 34 | 0.030298 | 0.00010744
2010 | 2009-08-14 | C | 2 | 0.0013651 | 6.3201e-06
2010 | 2009-08-14 | C | 599 | 0.06861 | 0.0018929
2010 | 2009-08-14 | C | 131 | 0.11674 | 0.00041396
2010 | 2009-08-14 | C | 279 | 0.11697 | 0.00088165
2010 | 2009-08-14 | C | 328 | 0.072706 | 0.0010365
2010 | 2009-08-14 | C | 25 | 0.015484 | 7.9001e-05
2010 | 2009-08-15 | C | 18 | 0.0059156 | 5.688e-05
2010 | 2009-08-15 | C | 266 | 0.11581 | 0.00084057
2010 | 2009-08-15 | C | 16 | 0.0049549 | 5.056e-05
2010 | 2009-08-15 | C | 64 | 0.033977 | 0.00020224
2010 | 2009-08-16 | C | 142 | 0.04577 | 0.00044872
2010 | 2009-08-16 | B | 1 | 0.00024332 | 3.16e-06
2010 | 2009-08-16 | C | 265 | 0.12558 | 0.00083741
2010 | 2009-08-16 | C | 587 | 0.13001 | 0.0018549
2010 | 2009-08-17 | C | 461 | 0.082451 | 0.0014568
2010 | 2009-08-16 | C | 655 | 0.18248 | 0.0020698
2010 | 2009-08-17 | C | 30 | 0.0063517 | 9.4801e-05
2010 | 2009-08-17 | C | 63 | 0.0063706 | 0.00019908
2010 | 2009-08-17 | C | 9 | 0.0077263 | 2.844e-05
2010 | 2009-08-18 | B | 219 | 0.092734 | 0.00069205
2010 | 2009-08-18 | B | 53 | 0.020098 | 0.00016748
2010 | 2009-08-18 | B | 77 | 0.043798 | 0.00024332
2010 | 2009-08-18 | B | 8 | 0.0090503 | 2.528e-05
2010 | 2009-08-18 | B | 40 | 0.030336 | 0.0001264
2010 | 2009-08-18 | B | 4 | 0.0022626 | 1.264e-05
2010 | 2009-08-18 | B | 1 | 0.00078369 | 3.16e-06
2010 | 2009-08-18 | B | 2 | 0.0012198 | 6.3201e-06
2010 | 2009-08-18 | B | 16 | 0.0068762 | 5.056e-05
2010 | 2009-08-18 | B | 7 | 0.0067688 | 2.212e-05
2010 | 2009-08-18 | B | 1 | 0.00061936 | 3.16e-06
2010 | 2009-08-18 | C | 62 | 0.0058776 | 0.00019592
2010 | 2009-08-18 | C | 151 | 0.059617 | 0.00047716
2010 | 2009-08-25 | B | 7 | 0.0038047 | 2.212e-05
2010 | 2009-08-19 | B | 3 | 0.0027303 | 9.4801e-06
2010 | 2009-08-19 | C | 1 | 0.00013272 | 3.16e-06
2010 | 2009-08-19 | C | 213 | 0.033578 | 0.00067309
2010 | 2009-08-19 | C | 164 | 0.079718 | 0.00051824
2010 | 2009-08-19 | C | 10 | 0.0072681 | 3.16e-05
2010 | 2009-08-19 | C | 99 | 0.019491 | 0.00031284
2010 | 2009-08-19 | B | 70 | 0.036277 | 0.0002212
2010 | 2009-08-20 | B | 22 | 0.016337 | 6.9521e-05
2010 | 2009-08-20 | B | 4 | 0.0044367 | 1.264e-05
2010 | 2009-08-20 | B | 38 | 0.034583 | 0.00012008
2010 | 2009-08-20 | B | 41 | 0.037832 | 0.00012956
2010 | 2009-08-20 | C | 51 | 0.014021 | 0.00016116
2010 | 2009-08-21 | C | 424 | 0.37644 | 0.0013399
2010 | 2009-08-21 | B | 1 | 0.00098277 | 3.16e-06
2010 | 2009-08-21 | B | 18 | 0.0065413 | 5.688e-05
2010 | 2009-08-21 | B | 6 | 0.0060293 | 1.896e-05
2010 | 2009-08-20 | B | 29 | 0.032991 | 9.1641e-05
2010 | 2009-08-21 | B | 89 | 0.084373 | 0.00028124
2010 | 2009-08-21 | C | 287 | 0.057136 | 0.00090693
2010 | 2009-08-21 | C | 71 | 0.019968 | 0.00022436
2010 | 2009-08-22 | B | 1 | 0.000237 | 3.16e-06
2010 | 2009-08-22 | B | 14 | 0.011945 | 4.424e-05
2010 | 2009-08-23 | C | 304 | 0.049954 | 0.00096065
2010 | 2009-08-24 | C | 1617 | 0.17373 | 0.0051098
2010 | 2009-08-24 | B | 62 | 0.079152 | 0.00019592
2010 | 2009-08-24 | C | 123 | 0.024487 | 0.00038868
2010 | 2009-08-24 | C | 31 | 0.0068573 | 9.7961e-05
2010 | 2009-08-24 | B | 57 | 0.0090061 | 0.00018012
2010 | 2009-08-24 | C | 91 | 0.0097771 | 0.00028756
2010 | 2009-08-25 | C | 789 | 0.22235 | 0.0024933
2010 | 2009-08-25 | B | 29 | 0.0082477 | 9.1641e-05
2010 | 2009-08-25 | B | 7 | 0.0079633 | 2.212e-05
2010 | 2009-08-25 | B | 260 | 0.24641 | 0.00082161
2010 | 2009-08-25 | C | 31 | 0.0062695 | 9.7961e-05
2010 | 2009-08-25 | B | 70 | 0.071669 | 0.0002212
2010 | 2009-08-25 | B | 66 | 0.016685 | 0.00020856
2010 | 2009-08-25 | B | 34 | 0.024174 | 0.00010744
2010 | 2009-08-25 | B | 7 | 0.0072997 | 2.212e-05
2010 | 2009-08-25 | C | 64 | 0.036606 | 0.00020224
2010 | 2009-08-25 | C | 92 | 0.0049423 | 0.00029072
2010 | 2009-08-25 | C | 314 | 0.019845 | 0.00099225
2010 | 2009-08-25 | C | 281 | 0.040846 | 0.00088797
2010 | 2009-08-25 | C | 2 | 0.00020856 | 6.3201e-06
2010 | 2009-08-26 | C | 749 | 0.047337 | 0.0023669
2010 | 2009-08-26 | C | 1022 | 0.051673 | 0.0032295
2010 | 2009-08-26 | C | 204 | 0.021273 | 0.00064465
2010 | 2009-08-26 | C | 314 | 0.013891 | 0.00099225
2010 | 2009-08-26 | C | 204 | 0.022563 | 0.00064465
2010 | 2009-08-26 | C | 788 | 0.072213 | 0.0024901
2010 | 2009-08-26 | C | 897 | 0.090705 | 0.0028345
2010 | 2009-08-25 | C | 314 | 0.014884 | 0.00099225
2010 | 2009-08-26 | C | 204 | 0.021273 | 0.00064465
2010 | 2009-08-26 | C | 204 | 0.014182 | 0.00064465
2010 | 2009-08-24 | B | 27 | 0.011803 | 8.5321e-05
2010 | 2009-08-26 | C | 897 | 0.053856 | 0.0028345
2010 | 2009-08-26 | C | 1373 | 0.22995 | 0.0043387
2010 | 2009-08-26 | C | 2272 | 0.39488 | 0.0071796
2010 | 2009-08-26 | C | 1190 | 0.45877 | 0.0037604
2010 | 2009-08-26 | C | 240 | 0.070636 | 0.00075841
2010 | 2009-08-26 | B | 136 | 0.11604 | 0.00042976
2010 | 2009-08-26 | C | 143 | 0.021239 | 0.00045188
2010 | 2009-08-26 | C | 9 | 0.010466 | 2.844e-05
2010 | 2009-08-26 | C | 14 | 0.0019023 | 4.424e-05
2010 | 2009-08-26 | C | 49 | 0.056362 | 0.00015484
2010 | 2009-08-25 | C | 139 | 0.11514 | 0.00043924
2010 | 2009-08-25 | C | 919 | 0.10455 | 0.0029041
2010 | 2009-08-25 | C | 199 | 0.046035 | 0.00062885
2010 | 2009-08-27 | C | 755 | 0.042945 | 0.0023858
2010 | 2009-08-26 | C | 3832 | 0.56913 | 0.012109
2010 | 2009-08-27 | C | 95 | 0.0048032 | 0.0003002
2010 | 2009-08-26 | C | 6 | 0.0053088 | 1.896e-05
2010 | 2009-08-26 | C | 2 | 0.00044872 | 6.3201e-06
2010 | 2009-08-27 | C | 314 | 0.18555 | 0.00099225
2010 | 2009-08-26 | C | 1 | 0.00010744 | 3.16e-06
2010 | 2009-08-26 | C | 10 | 0.0049296 | 3.16e-05
2010 | 2009-08-26 | C | 4 | 0.0019087 | 1.264e-05
2010 | 2009-08-26 | C | 7 | 0.0077199 | 2.212e-05
2010 | 2009-08-27 | B | 4 | 0.001896 | 1.264e-05
2010 | 2009-08-26 | C | 19 | 0.0018012 | 6.004e-05
2010 | 2009-08-26 | C | 9 | 0.0022752 | 2.844e-05
2010 | 2009-08-26 | C | 30 | 0.0068257 | 9.4801e-05
2010 | 2009-08-26 | C | 224 | 0.0809 | 0.00070785
2010 | 2009-08-27 | C | 4 | 0.0002528 | 1.264e-05
2010 | 2009-08-26 | C | 223 | 0.20833 | 0.00070469
2010 | 2009-08-26 | B | 85 | 0.042171 | 0.0002686
2010 | 2009-08-26 | C | 77 | 0.1511 | 0.00024332
2010 | 2009-08-26 | C | 287 | 0.17199 | 0.00090693
2010 | 2009-08-27 | B | 227 | 0.23313 | 0.00071733
2010 | 2009-08-26 | C | 227 | 0.091533 | 0.00071733
2010 | 2009-08-27 | B | 30 | 0.032517 | 9.4801e-05
2010 | 2009-08-27 | B | 71 | 0.074488 | 0.00022436
2010 | 2009-08-27 | C | 1360 | 0.28364 | 0.0042976
2010 | 2009-08-27 | C | 1179 | 0.089416 | 0.0037257
2010 | 2009-08-27 | C | 61 | 0.0019434 | 0.00019276
2010 | 2009-08-27 | C | 1052 | 0.37433 | 0.0033243
2010 | 2009-08-27 | C | 17 | 0.0055996 | 5.372e-05
2010 | 2009-08-27 | C | 215 | 0.054128 | 0.00067941
2010 | 2009-08-27 | C | 92 | 0.025309 | 0.00029072
2010 | 2009-08-27 | C | 9 | 0.0016495 | 2.844e-05
2010 | 2009-08-27 | C | 181 | 0.050194 | 0.00057196
2010 | 2009-08-26 | C | 114 | 0.46599 | 0.00036024
2010 | 2009-08-27 | C | 420 | 0.015927 | 0.0013272
2010 | 2009-08-27 | C | 23 | 0.013955 | 7.2681e-05
2010 | 2009-08-27 | C | 87 | 0.044556 | 0.00027492
2010 | 2009-08-27 | C | 2284 | 1.2152 | 0.0072175
2010 | 2009-08-27 | C | 24 | 0.0075082 | 7.5841e-05
2010 | 2009-08-27 | C | 74 | 0.044196 | 0.00023384
2010 | 2009-08-28 | C | 33 | 0.014495 | 0.00010428
2010 | 2009-08-27 | C | 902 | 0.36484 | 0.0028503
2010 | 2009-08-27 | C | 19 | 0.0025817 | 6.004e-05
2010 | 2009-08-27 | C | 77 | 0.015573 | 0.00024332
2010 | 2009-08-27 | C | 236 | 0.026848 | 0.00074577
2010 | 2009-08-27 | C | 62 | 0.03447 | 0.00019592
2010 | 2009-08-26 | C | 51 | 0.00048348 | 0.00016116
2010 | 2009-08-27 | C | 40 | 0.0075841 | 0.0001264
2010 | 2009-08-28 | B | 43 | 0.029214 | 0.00013588
2010 | 2009-08-27 | C | 498 | 0.026753 | 0.0015737
2010 | 2009-08-27 | B | 7 | 0.0051982 | 2.212e-05
2010 | 2009-08-27 | B | 14 | 0.01022 | 4.424e-05
2010 | 2009-08-27 | C | 923 | 0.20125 | 0.0029167
2010 | 2009-08-27 | C | 234 | 0.057569 | 0.00073945
2010 | 2009-08-27 | C | 923 | 0.046667 | 0.0029167
2010 | 2009-08-27 | C | 432 | 0.096014 | 0.0013651
2010 | 2009-08-27 | C | 708 | 0.26741 | 0.0022373
2010 | 2009-08-27 | C | 1310 | 0.59331 | 0.0041396
2010 | 2009-08-27 | C | 26 | 0.0033686 | 8.2161e-05
2010 | 2009-08-28 | C | 5 | 0.00158 | 1.58e-05
2010 | 2009-08-28 | B | 7 | 0.0032074 | 2.212e-05
2010 | 2009-08-28 | B | 5 | 0.0012166 | 1.58e-05
2010 | 2009-08-28 | C | 472 | 0.09695 | 0.0014915
2010 | 2009-08-28 | C | 8 | 0.00075841 | 2.528e-05
2010 | 2009-08-28 | C | 406 | 0.16794 | 0.001283
2010 | 2009-08-28 | C | 897 | 0.017007 | 0.0028345
2010 | 2009-08-28 | C | 50 | 0.001896 | 0.000158
2010 | 2009-08-28 | C | 13 | 0.0052583 | 4.108e-05
2010 | 2009-08-28 | C | 209 | 0.087605 | 0.00066045
2010 | 2009-08-28 | C | 1164 | 0.33828 | 0.0036783
2010 | 2009-08-28 | C | 896 | 0.04778 | 0.0028314
2010 | 2009-08-29 | B | 68 | 0.015901 | 0.00021488
2010 | 2009-08-28 | C | 9 | 0.0014505 | 2.844e-05
2010 | 2009-08-29 | B | 77 | 0.021412 | 0.00024332
2010 | 2009-08-29 | C | 17 | 0.0024174 | 5.372e-05
2010 | 2009-08-29 | B | 14 | 0.013847 | 4.424e-05
2010 | 2009-08-27 | C | 139 | 0.11038 | 0.00043924
2010 | 2009-08-29 | C | 105 | 0.020904 | 0.0003318
2010 | 2009-08-30 | C | 140 | 0.0079633 | 0.0004424
2010 | 2009-08-30 | C | 420 | 0.021235 | 0.0013272
2010 | 2009-08-30 | C | 433 | 0.058536 | 0.0013683
2010 | 2009-08-30 | C | 146 | 0.0064591 | 0.00046136
2010 | 2009-08-30 | C | 228 | 0.085586 | 0.00072049
2010 | 2009-08-30 | C | 28 | 0.011149 | 8.8481e-05
2010 | 2009-08-30 | B | 4 | 0.00075841 | 1.264e-05
2010 | 2009-08-31 | C | 184 | 0.068029 | 0.00058144
2010 | 2009-08-31 | C | 485 | 0.016859 | 0.0015326
2010 | 2009-08-31 | C | 138 | 0.086749 | 0.00043608
2010 | 2009-08-30 | C | 243 | 0.035323 | 0.00076789
2010 | 2009-08-30 | C | 920 | 0.25771 | 0.0029072
2010 | 2009-08-31 | C | 1974 | 1.0521 | 0.0062379
2010 | 2009-08-31 | C | 151 | 0.014315 | 0.00047716
2010 | 2009-08-31 | C | 130 | 0.010681 | 0.0004108
2010 | 2009-08-31 | C | 233 | 0.079266 | 0.00073629
2010 | 2009-08-31 | C | 92 | 0.033724 | 0.00029072
2010 | 2009-08-28 | B | 64 | 0.0014157 | 0.00020224
2010 | 2009-08-31 | C | 158 | 0.05957 | 0.00049928
2010 | 2009-08-31 | B | 1 | 0.00066361 | 3.16e-06
2010 | 2009-08-31 | C | 47 | 0.027113 | 0.00014852
2010 | 2009-08-31 | B | 217 | 0.061715 | 0.00068573
2010 | 2009-08-31 | C | 286 | 0.035247 | 0.00090377
2010 | 2009-08-31 | C | 76 | 0.03026 | 0.00024016
2010 | 2009-08-31 | C | 11 | 0.0011818 | 3.476e-05
2010 | 2009-08-31 | C | 304 | 0.027859 | 0.00096065
2010 | 2009-08-31 | C | 190 | 0.097844 | 0.0006004
2010 | 2009-08-31 | C | 111 | 0.0063137 | 0.00035076
2010 | 2009-08-31 | C | 34 | 0.065539 | 0.00010744
2010 | 2009-08-31 | C | 129 | 0.10069 | 0.00040764
2010 | 2009-08-31 | C | 1833 | 0.65619 | 0.0057923
2010 | 2009-08-31 | B | 21 | 0.0038489 | 6.6361e-05
2010 | 2009-08-31 | C | 233 | 0.19517 | 0.00073629
2010 | 2009-08-31 | C | 8 | 0.0043229 | 2.528e-05
2010 | 2009-08-31 | C | 627 | 0.23242 | 0.0019813
2010 | 2009-08-31 | C | 48 | 0.003337 | 0.00015168
2010 | 2009-08-31 | C | 182 | 0.090228 | 0.00057512
2010 | 2009-08-31 | C | 299 | 0.093976 | 0.00094485
2010 | 2009-08-30 | C | 99 | 0.22556 | 0.00031284
2010 | 2009-08-31 | C | 1 | 0.00035392 | 3.16e-06
2010 | 2009-08-31 | C | 105 | 0.047448 | 0.0003318
2010 | 2009-08-31 | C | 215 | 0.22277 | 0.00067941
2010 | 2009-08-31 | C | 53 | 0.022442 | 0.00016748
2010 | 2009-08-31 | C | 46 | 0.022822 | 0.00014536
2010 | 2009-08-31 | C | 299 | 0.32597 | 0.00094485
2010 | 2009-08-31 | C | 109 | 0.066819 | 0.00034444
2010 | 2009-08-31 | C | 271 | 0.036982 | 0.00085637
2010 | 2009-09-01 | C | 114 | 0.055225 | 0.00036024
2010 | 2009-09-01 | C | 51 | 0.0078969 | 0.00016116
2010 | 2009-08-31 | C | 1 | 0.0012166 | 3.16e-06
2010 | 2009-09-01 | C | 367 | 0.020875 | 0.0011597
2010 | 2009-08-31 | C | 51 | 0.0062853 | 0.00016116
2010 | 2009-09-01 | C | 545 | 0.14282 | 0.0017222
2010 | 2009-09-01 | C | 10 | 0.0039816 | 3.16e-05
2010 | 2009-09-01 | C | 6 | 0.0044746 | 1.896e-05
2010 | 2009-08-31 | C | 8306 | 0.23622 | 0.026247
2010 | 2009-09-01 | C | 2296 | 1.6542 | 0.0072554
2010 | 2009-08-31 | C | 2296 | 0.065299 | 0.0072554
2010 | 2009-09-01 | B | 67 | 0.071985 | 0.00021172
2010 | 2009-09-01 | B | 4 | 0.0060672 | 1.264e-05
2010 | 2009-09-01 | C | 63 | 0.022695 | 0.00019908
2010 | 2009-09-01 | C | 40 | 0.0054352 | 0.0001264
2010 | 2009-09-01 | C | 341 | 0.047198 | 0.0010776
2010 | 2009-09-01 | C | 6 | 0.0025217 | 1.896e-05
2010 | 2009-09-01 | C | 8307 | 0.52501 | 0.02625
2010 | 2009-09-01 | C | 8307 | 0.99751 | 0.02625
2010 | 2009-09-01 | C | 8307 | 0.99751 | 0.02625
2010 | 2009-09-02 | C | 9 | 0.0013083 | 2.844e-05
2010 | 2009-09-02 | B | 22 | 0.025027 | 6.9521e-05
2010 | 2009-09-02 | B | 14 | 0.01429 | 4.424e-05
2010 | 2009-09-02 | B | 135 | 0.078068 | 0.0004266
2010 | 2009-09-02 | B | 1 | 0.00097329 | 3.16e-06
2010 | 2009-09-02 | B | 5 | 0.00474 | 1.58e-05
2010 | 2009-09-02 | B | 2 | 0.0003476 | 6.3201e-06
2010 | 2009-09-02 | B | 1 | 0.00021488 | 3.16e-06
2010 | 2009-09-02 | B | 43 | 0.027992 | 0.00013588
2010 | 2009-09-02 | B | 26 | 0.027359 | 8.2161e-05
2010 | 2009-09-03 | B | 278 | 0.030747 | 0.00087849
2010 | 2009-09-03 | C | 2612 | 0.70645 | 0.008254
2010 | 2009-09-03 | C | 46 | 0.023549 | 0.00014536
2010 | 2009-09-03 | B | 2 | 0.001896 | 6.3201e-06
2010 | 2009-09-03 | B | 14 | 0.013272 | 4.424e-05
2010 | 2009-09-03 | B | 89 | 0.10659 | 0.00028124
2010 | 2009-09-03 | B | 78 | 0.05245 | 0.00024648
2010 | 2009-09-02 | C | 3 | 0.015598 | 9.4801e-06
2010 | 2009-09-04 | B | 98 | 0.04831 | 0.00030968
2010 | 2009-09-04 | C | 27 | 0.0058018 | 8.5321e-05
2010 | 2009-09-04 | C | 11 | 0.00097329 | 3.476e-05
2010 | 2009-09-04 | B | 7 | 0.0057734 | 2.212e-05
2010 | 2009-09-04 | B | 4 | 0.0036024 | 1.264e-05
2010 | 2009-09-04 | B | 10 | 0.0097961 | 3.16e-05
2010 | 2009-09-04 | B | 5 | 0.0017696 | 1.58e-05
2010 | 2009-09-04 | B | 11 | 0.0038932 | 3.476e-05
2010 | 2009-09-04 | B | 25 | 0.01501 | 7.9001e-05
2010 | 2009-09-04 | C | 162 | 0.061687 | 0.00051192
2010 | 2009-09-05 | C | 157 | 0.02918 | 0.00049612
2010 | 2009-09-05 | C | 6 | 0.0022373 | 1.896e-05
2010 | 2009-09-05 | C | 612 | 0.23619 | 0.0019339
2010 | 2009-09-06 | C | 31 | 0.0067593 | 9.7961e-05
2010 | 2009-09-07 | C | 439 | 0.099901 | 0.0013873
2010 | 2009-09-07 | B | 1 | 0.00064149 | 3.16e-06
2010 | 2009-09-07 | B | 107 | 0.081149 | 0.00033812
2010 | 2009-09-07 | C | 28 | 0.0035392 | 8.8481e-05
2010 | 2009-09-07 | C | 4 | 0.0010238 | 1.264e-05
2010 | 2009-09-07 | B | 67 | 0.049966 | 0.00021172
2010 | 2009-09-07 | B | 57 | 0.0046832 | 0.00018012
2010 | 2009-08-07 | B | 57 | 0.036204 | 0.00018012
2010 | 2009-09-08 | B | 17 | 0.0089713 | 5.372e-05
2010 | 2009-09-08 | B | 12 | 0.010428 | 3.792e-05
2010 | 2009-09-08 | B | 5 | 0.0030178 | 1.58e-05
2010 | 2009-09-08 | C | 200 | 0.039443 | 0.00063201
2010 | 2009-09-08 | C | 477 | 0.049742 | 0.0015073
2010 | 2009-09-08 | C | 223 | 0.024664 | 0.00070469
2010 | 2009-09-08 | B | 9 | 0.0089871 | 2.844e-05
2010 | 2009-09-08 | C | 15 | 0.0021804 | 4.74e-05
2010 | 2009-09-09 | B | 1 | 0.0012672 | 3.16e-06
2010 | 2009-09-09 | B | 9 | 0.0092431 | 2.844e-05
2010 | 2009-09-09 | B | 5 | 0.0054668 | 1.58e-05
2010 | 2009-09-09 | B | 11 | 0.0086553 | 3.476e-05
2010 | 2009-09-09 | B | 35 | 0.028646 | 0.0001106
2010 | 2009-09-02 | B | 43 | 0.029758 | 0.00013588
2010 | 2009-09-09 | C | 6 | 0.00070153 | 1.896e-05
2010 | 2009-09-09 | C | 368 | 0.11422 | 0.0011629
2010 | 2009-09-09 | C | 102 | 0.013784 | 0.00032232
2010 | 2009-09-09 | C | 788 | 0.079683 | 0.0024901
2010 | 2009-09-09 | B | 2 | 0.00077105 | 6.3201e-06
2010 | 2009-09-10 | B | 88 | 0.028364 | 0.00027808
2010 | 2009-09-10 | B | 5 | 0.005609 | 1.58e-05
2010 | 2009-09-10 | B | 85 | 0.089445 | 0.0002686
2010 | 2009-09-10 | B | 57 | 0.055658 | 0.00018012
2010 | 2009-09-10 | C | 574 | 0.0072554 | 0.0018139
2010 | 2009-09-10 | C | 15 | 0.0024648 | 4.74e-05
2010 | 2009-09-10 | C | 1 | 0.00067309 | 3.16e-06
2010 | 2009-09-11 | C | 711 | 0.20022 | 0.0022468
2010 | 2009-09-10 | B | 57 | 0.037105 | 0.00018012
2010 | 2009-09-11 | C | 34 | 0.0061241 | 0.00010744
2010 | 2009-09-11 | C | 189 | 0.030915 | 0.00059724
2010 | 2009-09-11 | C | 882 | 0.1367 | 0.0027871
2010 | 2009-09-12 | C | 16 | 0.0018202 | 5.056e-05
2010 | 2009-09-12 | C | 933 | 0.22716 | 0.0029483
2010 | 2009-09-12 | B | 22 | 0.025027 | 6.9521e-05
2010 | 2009-09-12 | C | 186 | 0.062205 | 0.00058776
2010 | 2009-09-13 | C | 47 | 0.0028219 | 0.00014852
2010 | 2009-09-13 | C | 261 | 0.0065981 | 0.00082477
2010 | 2009-09-13 | C | 3 | 0.00071101 | 9.4801e-06
2010 | 2009-09-13 | C | 40 | 0.0065729 | 0.0001264
2010 | 2009-09-13 | C | 987 | 0.062379 | 0.0031189
2010 | 2009-09-13 | C | 22 | 0.018075 | 6.9521e-05
2010 | 2009-09-13 | C | 314 | 0.11538 | 0.00099225
2010 | 2009-09-14 | C | 100 | 0.016552 | 0.000316
2010 | 2009-09-13 | C | 493 | 0.35208 | 0.0015579
2010 | 2009-09-14 | B | 2 | 0.0020603 | 6.3201e-06
2010 | 2009-09-14 | C | 189 | 0.019112 | 0.00059724
2010 | 2009-09-14 | C | 485 | 0.089302 | 0.0015326
2010 | 2009-09-14 | C | 7 | 0.0010618 | 2.212e-05
2010 | 2009-09-14 | C | 539 | 0.12263 | 0.0017033
2010 | 2009-09-14 | C | 166 | 0.056438 | 0.00052456
2010 | 2009-09-15 | B | 5 | 0.0070153 | 1.58e-05
2010 | 2009-09-15 | B | 10 | 0.010902 | 3.16e-05
2010 | 2009-09-15 | C | 7 | 0.0035835 | 2.212e-05
2010 | 2009-09-15 | B | 58 | 0.021975 | 0.00018328
2010 | 2009-09-15 | C | 317 | 0.030624 | 0.0010017
2010 | 2009-09-15 | C | 313 | 0.026705 | 0.00098909
2010 | 2009-09-15 | C | 793 | 0.069767 | 0.0025059
2010 | 2009-09-16 | B | 1 | 0.00085321 | 3.16e-06
2010 | 2009-09-16 | B | 115 | 0.11665 | 0.0003634
2010 | 2009-09-16 | B | 30 | 0.02133 | 9.4801e-05
2010 | 2009-09-16 | B | 259 | 0.25536 | 0.00081845
2010 | 2009-09-16 | C | 31 | 0.01107 | 9.7961e-05
2010 | 2009-09-16 | B | 88 | 0.031145 | 0.00027808
2010 | 2009-09-16 | C | 1777 | 0.08423 | 0.0056154
2010 | 2009-09-16 | C | 1777 | 0.043036 | 0.0056154
2010 | 2009-09-17 | C | 72 | 0.010238 | 0.00022752
2010 | 2009-09-15 | B | 10 | 0.012577 | 3.16e-05
2010 | 2009-09-17 | C | 2806 | 0.053202 | 0.008867
2010 | 2009-09-17 | B | 48 | 0.036403 | 0.00015168
2010 | 2009-09-17 | C | 248 | 0.0070532 | 0.00078369
2010 | 2009-09-18 | B | 8 | 0.002073 | 2.528e-05
2010 | 2009-09-17 | B | 80 | 0.019971 | 0.0002528
2010 | 2009-09-17 | B | 7 | 0.0083393 | 2.212e-05
2010 | 2009-09-17 | B | 3 | 0.0027587 | 9.4801e-06
2010 | 2009-09-18 | B | 15 | 0.0071575 | 4.74e-05
2010 | 2009-09-18 | C | 15 | 0.00099541 | 4.74e-05
2010 | 2009-09-18 | B | 4 | 0.0016559 | 1.264e-05
2010 | 2009-09-18 | B | 10 | 0.00237 | 3.16e-05
2010 | 2009-09-18 | B | 22 | 0.015086 | 6.9521e-05
2010 | 2009-09-18 | B | 28 | 0.0069015 | 8.8481e-05
2010 | 2009-09-19 | B | 26 | 0.016596 | 8.2161e-05
2010 | 2009-09-19 | C | 28 | 0.0040701 | 8.8481e-05
2010 | 2009-09-19 | B | 20 | 0.0021488 | 6.3201e-05
2010 | 2009-09-19 | C | 33 | 0.0071954 | 0.00010428
2010 | 2009-09-19 | C | 68 | 0.022348 | 0.00021488
2010 | 2009-09-19 | B | 1 | 0.0017064 | 3.16e-06
2010 | 2009-09-19 | C | 1131 | 0.21795 | 0.003574
2010 | 2009-09-20 | B | 499 | 0.18922 | 0.0015769
2010 | 2009-09-20 | C | 940 | 0.042161 | 0.0029704
2010 | 2009-09-20 | C | 14 | 0.0080075 | 4.424e-05
2010 | 2009-09-20 | C | 710 | 0.16559 | 0.0022436
2010 | 2009-09-20 | B | 4 | 0.0028819 | 1.264e-05
2010 | 2009-09-21 | C | 62 | 0.023315 | 0.00019592
2010 | 2009-09-19 | C | 971 | 0.13808 | 0.0030684
2010 | 2009-09-21 | B | 20 | 0.015168 | 6.3201e-05
2010 | 2009-09-21 | C | 1274 | 0.14857 | 0.0040259
2010 | 2009-09-21 | B | 71 | 0.017276 | 0.00022436
2010 | 2009-09-22 | C | 269 | 0.083267 | 0.00085005
2010 | 2009-09-22 | C | 98 | 0.033812 | 0.00030968
2010 | 2009-09-22 | B | 32 | 0.038021 | 0.00010112
2010 | 2009-09-22 | B | 28 | 0.025571 | 8.8481e-05
2010 | 2009-09-22 | B | 195 | 0.20889 | 0.0006162
2010 | 2009-09-22 | C | 79 | 0.01398 | 0.00024964
2010 | 2009-09-22 | C | 551 | 0.064386 | 0.0017412
2010 | 2009-09-22 | C | 64 | 0.027505 | 0.00020224
2010 | 2009-09-22 | B | 1 | 0.00050876 | 3.16e-06
2010 | 2009-09-23 | C | 4691 | 0.09742 | 0.014824
2010 | 2009-09-23 | B | 1 | 0.0010839 | 3.16e-06
2010 | 2009-09-23 | B | 49 | 0.032672 | 0.00015484
2010 | 2009-09-23 | C | 5 | 0.001343 | 1.58e-05
2010 | 2009-09-23 | C | 280 | 0.0017696 | 0.00088481
2010 | 2009-09-23 | B | 182 | 0.10792 | 0.00057512
2010 | 2009-09-23 | B | 47 | 0.049012 | 0.00014852
2010 | 2009-09-23 | B | 3 | 0.0034128 | 9.4801e-06
2010 | 2009-09-23 | C | 348 | 0.023093 | 0.0010997
2010 | 2009-09-23 | C | 615 | 0.21438 | 0.0019434
2010 | 2009-09-24 | B | 8 | 0.0055616 | 2.528e-05
2010 | 2009-09-24 | C | 3128 | 0.34149 | 0.0098846
2010 | 2009-09-24 | B | 102 | 0.095085 | 0.00032232
2010 | 2009-09-24 | C | 1666 | 0.40011 | 0.0052646
2010 | 2009-09-24 | C | 3 | 0.0003792 | 9.4801e-06
2010 | 2009-09-24 | C | 13 | 0.0029167 | 4.108e-05
2010 | 2009-09-24 | C | 814 | 0.19546 | 0.0025723
2010 | 2009-09-24 | C | 215 | 0.12179 | 0.00067941
2010 | 2009-09-25 | C | 22 | 0.005075 | 6.9521e-05
2010 | 2009-09-25 | C | 1191 | 0.060217 | 0.0037636
2010 | 2009-09-25 | C | 2278 | 0.12238 | 0.0071985
2010 | 2009-09-25 | C | 3833 | 0.23014 | 0.012112
2010 | 2009-09-25 | C | 1375 | 0.099936 | 0.004345
2010 | 2009-09-25 | B | 78 | 0.096128 | 0.00024648
2010 | 2009-09-25 | C | 171 | 0.02918 | 0.00054036
2010 | 2009-09-25 | C | 300 | 0.066724 | 0.00094801
2010 | 2009-09-25 | C | 314 | 0.092279 | 0.00099225
2010 | 2009-09-26 | B | 2 | 0.0010428 | 6.3201e-06
2010 | 2009-09-26 | C | 37 | 0.0053784 | 0.00011692
2010 | 2009-09-26 | B | 28 | 0.020793 | 8.8481e-05
2010 | 2009-09-25 | C | 621 | 0.071985 | 0.0019624
2010 | 2009-09-26 | C | 161 | 0.077841 | 0.00050876
2010 | 2009-09-27 | C | 88 | 0.0044493 | 0.00027808
2010 | 2009-09-26 | B | 67 | 0.021172 | 0.00021172
2010 | 2009-09-26 | C | 297 | 0.036204 | 0.00093853
2010 | 2009-09-27 | C | 1170 | 0.54462 | 0.0036972
2010 | 2009-09-27 | C | 1274 | 0.17464 | 0.0040259
2010 | 2009-09-27 | C | 19 | 0.0023416 | 6.004e-05
2010 | 2009-09-28 | C | 10 | 0.0036972 | 3.16e-05
2010 | 2009-09-28 | B | 28 | 0.0012387 | 8.8481e-05
2010 | 2009-09-28 | B | 2 | 0.00076473 | 6.3201e-06
2010 | 2009-09-28 | C | 259 | 0.027827 | 0.00081845
2010 | 2009-09-26 | C | 1 | 0.0023289 | 3.16e-06
2010 | 2009-09-28 | B | 33 | 0.026174 | 0.00010428
2010 | 2009-09-28 | C | 136 | 0.10112 | 0.00042976
2010 | 2009-09-28 | B | 6 | 0.0020477 | 1.896e-05
2010 | 2009-09-29 | C | 48 | 0.010163 | 0.00015168
2010 | 2009-09-29 | C | 432 | 0.0013651 | 0.0013651
2010 | 2009-09-29 | C | 101 | 0.0047874 | 0.00031916
2010 | 2009-09-29 | B | 51 | 0.037067 | 0.00016116
2010 | 2009-09-29 | B | 172 | 0.1511 | 0.00054352
2010 | 2009-09-29 | B | 103 | 0.026039 | 0.00032548
2010 | 2009-09-29 | B | 8 | 0.0068509 | 2.528e-05
2010 | 2009-09-29 | C | 11 | 0.0052836 | 3.476e-05
2010 | 2009-09-29 | B | 2 | 0.0026607 | 6.3201e-06
2010 | 2009-09-29 | C | 6 | 0.019245 | 1.896e-05
2010 | 2009-09-30 | B | 31 | 0.027919 | 9.7961e-05
2010 | 2009-09-30 | B | 18 | 0.013715 | 5.688e-05
2010 | 2009-09-30 | B | 1 | 0.0012925 | 3.16e-06
2010 | 2009-09-30 | B | 38 | 0.0054036 | 0.00012008
2010 | 2009-09-30 | C | 284 | 0.55547 | 0.00089745
2010 | 2009-10-01 | B | 19 | 0.0036024 | 6.004e-05
2010 | 2009-09-30 | C | 3 | 0.001422 | 9.4801e-06
2010 | 2009-09-30 | C | 8 | 0.0045504 | 2.528e-05
2010 | 2009-09-30 | C | 14 | 0.00048664 | 4.424e-05
2010 | 2009-10-01 | C | 10 | 0.0015484 | 3.16e-05
2010 | 2009-10-01 | B | 4 | 0.0048917 | 1.264e-05
2010 | 2009-10-01 | C | 35 | 0.0057512 | 0.0001106
2010 | 2009-10-01 | B | 26 | 0.0042724 | 8.2161e-05
2010 | 2009-10-01 | C | 160 | 0.051572 | 0.0005056
2010 | 2009-10-02 | B | 183 | 0.088478 | 0.00057828
2010 | 2009-10-02 | B | 1 | 0.0003792 | 3.16e-06
2010 | 2009-10-02 | B | 30 | 0.014884 | 9.4801e-05
2010 | 2009-10-02 | B | 73 | 0.034833 | 0.00023068
2010 | 2009-10-02 | C | 90 | 0.013651 | 0.0002844
2010 | 2009-10-02 | B | 9 | 0.0083899 | 2.844e-05
2010 | 2009-10-02 | B | 29 | 0.030883 | 9.1641e-05
2010 | 2009-10-02 | B | 6 | 0.0083425 | 1.896e-05
2010 | 2009-10-02 | C | 428 | 0.12285 | 0.0013525
2010 | 2009-10-02 | C | 16 | 0.0026291 | 5.056e-05
2010 | 2009-10-02 | C | 119 | 0.02122 | 0.00037604
2010 | 2009-10-02 | C | 67 | 0.0061399 | 0.00021172
2010 | 2009-10-03 | C | 132 | 0.088013 | 0.00041712
2010 | 2009-10-03 | C | 22 | 0.00090377 | 6.9521e-05
2010 | 2009-10-03 | B | 154 | 0.053531 | 0.00048664
2010 | 2009-10-04 | B | 33 | 0.0060483 | 0.00010428
2010 | 2009-10-04 | C | 12 | 0.00041712 | 3.792e-05
2010 | 2009-10-04 | B | 359 | 0.074874 | 0.0011344
2010 | 2009-10-04 | C | 32 | 0.0037415 | 0.00010112
2010 | 2009-10-04 | C | 1241 | 0.035294 | 0.0039216
2010 | 2009-10-04 | C | 222 | 0.080979 | 0.00070153
2010 | 2009-10-04 | C | 237 | 0.041191 | 0.00074893
2010 | 2009-10-04 | C | 320 | 0.023258 | 0.0010112
2010 | 2009-10-05 | C | 352 | 0.23135 | 0.0011123
2010 | 2009-10-05 | C | 353 | 0.11254 | 0.0011155
2010 | 2009-10-05 | B | 33 | 0.011888 | 0.00010428
2010 | 2009-10-03 | B | 81 | 0.024572 | 0.00025596
2010 | 2009-10-05 | C | 25 | 0.002212 | 7.9001e-05
2010 | 2009-10-05 | C | 10 | 0.0026228 | 3.16e-05
2010 | 2009-10-05 | C | 13 | 0.0037383 | 4.108e-05
2010 | 2009-10-05 | C | 4 | 0.0021867 | 1.264e-05
2010 | 2009-10-05 | C | 4 | 0.00040448 | 1.264e-05
2010 | 2009-10-04 | C | 112 | 0.16647 | 0.00035392
2010 | 2009-10-04 | C | 133 | 0.36838 | 0.00042028
2010 | 2009-10-05 | C | 260 | 0.054062 | 0.00082161
2010 | 2009-10-04 | C | 20 | 0.10649 | 6.3201e-05
2010 | 2009-10-05 | C | 81 | 0.059639 | 0.00025596
2010 | 2009-10-04 | C | 162 | 0.55339 | 0.00051192
2010 | 2009-10-05 | C | 45 | 0.025312 | 0.0001422
2010 | 2009-10-05 | C | 653 | 0.22036 | 0.0020635
2010 | 2009-10-06 | C | 291 | 0.06345 | 0.00091957
2010 | 2009-10-05 | C | 610 | 0.56653 | 0.0019276
2010 | 2009-10-06 | C | 418 | 0.16115 | 0.0013209
2010 | 2009-10-06 | C | 967 | 0.16054 | 0.0030557
2010 | 2009-10-04 | C | 60 | 0.5233 | 0.0001896
2010 | 2009-10-05 | C | 327 | 0.33101 | 0.0010333
2010 | 2009-10-04 | C | 51 | 0.5087 | 0.00016116
2010 | 2009-10-06 | B | 78 | 0.063346 | 0.00024648
2010 | 2009-10-06 | C | 49 | 0.0030968 | 0.00015484
2010 | 2009-10-06 | B | 60 | 0.043608 | 0.0001896
2010 | 2009-10-06 | C | 20 | 0.0084689 | 6.3201e-05
2010 | 2009-10-06 | C | 5 | 0.00097961 | 1.58e-05
2010 | 2009-10-05 | C | 233 | 0.27533 | 0.00073629
2010 | 2009-10-05 | C | 146 | 0.068547 | 0.00046136
2010 | 2009-10-06 | C | 233 | 0.015974 | 0.00073629
2010 | 2009-10-06 | B | 262 | 0.3011 | 0.00082793
2010 | 2009-10-07 | C | 614 | 0.085713 | 0.0019403
2010 | 2009-10-06 | C | 139 | 0.12343 | 0.00043924
2010 | 2009-10-06 | B | 1 | 0.0021172 | 3.16e-06
2010 | 2009-10-07 | C | 1923 | 0.35843 | 0.0060767
2010 | 2009-10-07 | C | 111 | 0.016486 | 0.00035076
2010 | 2009-10-07 | B | 71 | 0.015705 | 0.00022436
2010 | 2009-10-07 | B | 81 | 0.061431 | 0.00025596
2010 | 2009-10-07 | B | 34 | 0.044373 | 0.00010744
2010 | 2009-10-07 | B | 113 | 0.021425 | 0.00035708
2010 | 2009-10-07 | C | 1257 | 0.091359 | 0.0039722
2010 | 2009-10-08 | C | 666 | 0.13469 | 0.0021046
2010 | 2009-10-08 | B | 3 | 0.0003318 | 9.4801e-06
2010 | 2009-10-08 | B | 14 | 0.0086269 | 4.424e-05
2010 | 2009-10-08 | B | 69 | 0.065413 | 0.00021804
2010 | 2009-10-08 | B | 6 | 0.0049296 | 1.896e-05
2010 | 2009-10-08 | B | 27 | 0.033275 | 8.5321e-05
2010 | 2009-10-08 | B | 10 | 0.011313 | 3.16e-05
2010 | 2009-10-08 | B | 43 | 0.048102 | 0.00013588
2010 | 2009-10-08 | B | 171 | 0.1459 | 0.00054036
2010 | 2009-10-08 | C | 330 | 0.087596 | 0.0010428
2010 | 2009-10-08 | C | 577 | 0.030997 | 0.0018233
2010 | 2009-10-09 | C | 748 | 0.13473 | 0.0023637
2010 | 2009-10-08 | B | 82 | 0.04917 | 0.00025912
2010 | 2009-10-09 | C | 316 | 0.023855 | 0.00099857
2010 | 2009-10-09 | B | 18 | 0.009499 | 5.688e-05
2010 | 2009-10-09 | C | 887 | 0.15069 | 0.0028029
2010 | 2009-10-09 | C | 1052 | 0.089757 | 0.0033243
2010 | 2009-10-10 | C | 62 | 0.010384 | 0.00019592
2010 | 2009-10-09 | C | 4 | 0.008886 | 1.264e-05
2010 | 2009-10-10 | C | 218 | 0.11022 | 0.00068889
2010 | 2009-10-10 | C | 36 | 0.0034128 | 0.00011376
2010 | 2009-10-10 | B | 1 | 0.00036972 | 3.16e-06
2010 | 2009-10-09 | C | 61 | 0.004048 | 0.00019276
2010 | 2009-10-10 | C | 336 | 0.25685 | 0.0010618
2010 | 2009-10-10 | C | 18 | 0.0051192 | 5.688e-05
2010 | 2009-10-09 | C | 17 | 0.0026323 | 5.372e-05
2010 | 2009-10-10 | C | 810 | 0.17658 | 0.0025596
2010 | 2009-10-10 | C | 28 | 0.0092905 | 8.8481e-05
2010 | 2009-10-10 | C | 22 | 0.0035455 | 6.9521e-05
2010 | 2009-10-10 | C | 26 | 0.019226 | 8.2161e-05
2010 | 2009-10-09 | C | 46 | 0.0050876 | 0.00014536
2010 | 2009-10-10 | C | 9 | 0.012514 | 2.844e-05
2010 | 2009-10-10 | C | 39 | 0.00073945 | 0.00012324
2010 | 2009-10-09 | C | 1467 | 0.29669 | 0.0046358
2010 | 2009-10-09 | C | 5788 | 0.69503 | 0.01829
2010 | 2009-10-09 | C | 211 | 0.10624 | 0.00066677
2010 | 2009-10-10 | C | 10 | 0.0091641 | 3.16e-05
2010 | 2009-10-10 | C | 1967 | 0.018647 | 0.0062158
2010 | 2009-10-10 | C | 199 | 0.0031442 | 0.00062885
2010 | 2009-10-10 | C | 53 | 0.008709 | 0.00016748
2010 | 2009-10-10 | C | 11 | 0.0010776 | 3.476e-05
2010 | 2009-10-10 | C | 2 | 0.00060672 | 6.3201e-06
2010 | 2009-10-10 | C | 1630 | 0.13051 | 0.0051508
2010 | 2009-10-11 | C | 29 | 0.0028409 | 9.1641e-05
2010 | 2009-10-10 | C | 170 | 0.40639 | 0.0005372
2010 | 2009-10-11 | C | 16 | 0.006674 | 5.056e-05
2010 | 2009-10-11 | C | 21 | 0.016856 | 6.6361e-05
2010 | 2009-10-11 | C | 198 | 0.04455 | 0.00062569
2010 | 2009-10-11 | C | 116 | 0.012097 | 0.00036656
2010 | 2009-10-12 | B | 1 | 0.00048348 | 3.16e-06
2010 | 2009-10-12 | B | 92 | 0.038679 | 0.00029072
2010 | 2009-10-12 | C | 11 | 0.00093853 | 3.476e-05
2010 | 2009-10-12 | C | 81 | 0.012798 | 0.00025596
2010 | 2009-10-12 | C | 8 | 0.0036656 | 2.528e-05
2010 | 2009-10-10 | C | 374 | 0.017728 | 0.0011818
2010 | 2009-10-12 | C | 37 | 0.0056122 | 0.00011692
2010 | 2009-10-13 | B | 20 | 0.0025912 | 6.3201e-05
2010 | 2009-10-13 | B | 6 | 0.002844 | 1.896e-05
2010 | 2009-10-13 | B | 96 | 0.03792 | 0.00030336
2010 | 2009-10-13 | B | 3 | 0.001896 | 9.4801e-06
2010 | 2009-10-13 | B | 2 | 0.0012008 | 6.3201e-06
2010 | 2009-10-13 | C | 21 | 0.0076978 | 6.6361e-05
2010 | 2009-10-13 | B | 136 | 0.093534 | 0.00042976
2010 | 2009-10-13 | C | 47 | 0.0026734 | 0.00014852
2010 | 2009-10-14 | C | 1 | 0.00016432 | 3.16e-06
2010 | 2009-10-14 | C | 280 | 0.023005 | 0.00088481
2010 | 2009-10-14 | B | 8 | 0.0066993 | 2.528e-05
2010 | 2009-10-14 | C | 96 | 0.11094 | 0.00030336
2010 | 2009-10-14 | C | 2 | 0.0002528 | 6.3201e-06
2010 | 2009-10-14 | C | 1709 | 0.091808 | 0.0054005
2010 | 2009-10-14 | C | 186 | 0.024999 | 0.00058776
2010 | 2009-10-15 | C | 106 | 0.041636 | 0.00033496
2010 | 2009-10-15 | C | 440 | 0.13585 | 0.0013904
2010 | 2009-10-15 | B | 8 | 0.0043735 | 2.528e-05
2010 | 2009-10-15 | B | 61 | 0.054359 | 0.00019276
2010 | 2009-10-15 | B | 6 | 0.00051192 | 1.896e-05
2010 | 2009-10-15 | B | 6 | 0.0025596 | 1.896e-05
2010 | 2009-10-15 | B | 105 | 0.077642 | 0.0003318
2010 | 2009-10-15 | B | 43 | 0.029486 | 0.00013588
2010 | 2009-10-15 | C | 101 | 0.053938 | 0.00031916
2010 | 2009-10-15 | C | 1092 | 0.18041 | 0.0034507
2010 | 2009-10-15 | C | 424 | 0.14471 | 0.0013399
2010 | 2009-10-15 | C | 52 | 0.054719 | 0.00016432
2010 | 2009-10-16 | C | 393 | 0.34276 | 0.0012419
2010 | 2009-10-16 | B | 61 | 0.056094 | 0.00019276
2010 | 2009-10-16 | B | 11 | 0.010845 | 3.476e-05
2010 | 2009-10-16 | B | 5 | 0.00395 | 1.58e-05
2010 | 2009-10-16 | C | 8 | 0.0034887 | 2.528e-05
2010 | 2009-10-17 | B | 424 | 0.16748 | 0.0013399
2010 | 2009-10-17 | C | 476 | 0.13918 | 0.0015042
2010 | 2009-10-17 | C | 421 | 0.0079822 | 0.0013304
2010 | 2009-10-17 | C | 23 | 0.0018897 | 7.2681e-05
2010 | 2009-10-17 | C | 121 | 0.042025 | 0.00038236
2010 | 2009-10-17 | C | 85 | 0.0085953 | 0.0002686
2010 | 2009-10-17 | C | 193 | 0.074807 | 0.00060988
2010 | 2009-10-18 | C | 597 | 0.12311 | 0.0018865
2010 | 2009-10-18 | C | 107 | 0.1011 | 0.00033812
2010 | 2009-10-17 | C | 395 | 0.09888 | 0.0012482
2010 | 2009-10-18 | C | 199 | 0.00062885 | 0.00062885
2010 | 2009-10-18 | C | 232 | 0.13426 | 0.00073313
2010 | 2009-10-17 | C | 103 | 0.019854 | 0.00032548
2010 | 2009-10-19 | C | 7 | 0.00030968 | 2.212e-05
2010 | 2009-10-20 | B | 282 | 0.026734 | 0.00089113
2010 | 2009-10-20 | C | 2 | 0.0004108 | 6.3201e-06
2010 | 2009-10-20 | C | 28 | 0.0071669 | 8.8481e-05
2010 | 2009-10-20 | B | 6 | 0.0044177 | 1.896e-05
2010 | 2009-10-20 | B | 17 | 0.0048886 | 5.372e-05
2010 | 2009-10-09 | B | 18 | 0.0079633 | 5.688e-05
2010 | 2009-10-20 | C | 6 | 0.0036403 | 1.896e-05
2010 | 2009-10-20 | C | 391 | 0.060543 | 0.0012356
2010 | 2009-10-20 | B | 38 | 0.011237 | 0.00012008
2010 | 2009-10-20 | B | 465 | 0.56132 | 0.0014694
2010 | 2009-10-21 | C | 87 | 0.033752 | 0.00027492
2010 | 2009-10-21 | B | 5 | 0.003792 | 1.58e-05
2010 | 2009-10-21 | B | 461 | 0.2779 | 0.0014568
2010 | 2009-10-21 | C | 4 | 0.00022752 | 1.264e-05
2010 | 2009-10-21 | C | 10 | 0.012134 | 3.16e-05
2010 | 2009-10-21 | B | 11 | 0.012479 | 3.476e-05
2010 | 2009-10-21 | B | 63 | 0.065896 | 0.00019908
2010 | 2009-10-21 | C | 11 | 0.0062569 | 3.476e-05
2010 | 2009-10-21 | B | 41 | 0.0090693 | 0.00012956
2010 | 2009-10-22 | B | 21 | 0.01951 | 6.6361e-05
2010 | 2009-10-22 | B | 138 | 0.11687 | 0.00043608
2010 | 2009-10-22 | B | 1 | 0.0001264 | 3.16e-06
2010 | 2009-10-22 | C | 1 | 0.0002686 | 3.16e-06
2010 | 2009-10-22 | C | 67 | 0.0097392 | 0.00021172
2010 | 2009-10-22 | B | 1 | 0.0010523 | 3.16e-06
2010 | 2009-10-22 | C | 51 | 0.064787 | 0.00016116
2010 | 2009-10-22 | B | 63 | 0.022098 | 0.00019908
2010 | 2009-10-22 | C | 110 | 0.050402 | 0.0003476
2010 | 2009-10-22 | C | 246 | 0.052406 | 0.00077737
2010 | 2009-10-22 | C | 195 | 0.078653 | 0.0006162
2010 | 2009-10-23 | C | 303 | 0.036385 | 0.00095749
2010 | 2009-10-23 | B | 3 | 0.00088165 | 9.4801e-06
2010 | 2009-10-23 | B | 16 | 0.011831 | 5.056e-05
2010 | 2009-10-23 | B | 148 | 0.20578 | 0.00046768
2010 | 2009-10-23 | B | 449 | 0.10075 | 0.0014189
2010 | 2009-10-24 | C | 2919 | 0.39688 | 0.0092241
2010 | 2009-10-24 | B | 1 | 0.00050876 | 3.16e-06
2010 | 2009-10-24 | C | 149 | 0.0065918 | 0.00047084
2010 | 2009-10-24 | C | 1378 | 0.206 | 0.0043545
2010 | 2009-10-24 | C | 274 | 0.049173 | 0.00086585
2010 | 2009-10-25 | C | 112 | 0.013133 | 0.00035392
2010 | 2009-10-25 | C | 188 | 0.12333 | 0.00059408
2010 | 2009-10-25 | C | 65 | 0.0024648 | 0.0002054
2010 | 2009-10-26 | C | 445 | 0.065011 | 0.0014062
2010 | 2009-10-26 | C | 2778 | 0.017557 | 0.0087786
2010 | 2009-10-26 | C | 151 | 0.0023858 | 0.00047716
2010 | 2009-10-23 | B | 45 | 0.039959 | 0.0001422
2010 | 2009-10-27 | B | 16 | 0.01628 | 5.056e-05
2010 | 2009-10-27 | C | 21 | 0.011945 | 6.6361e-05
2010 | 2009-10-27 | B | 11 | 0.0018075 | 3.476e-05
2010 | 2009-10-27 | C | 526 | 0.07646 | 0.0016622
2010 | 2009-10-28 | B | 14 | 0.0097329 | 4.424e-05
2010 | 2009-10-28 | C | 140 | 0.021276 | 0.0004424
2010 | 2009-10-28 | B | 41 | 0.038868 | 0.00012956
2010 | 2009-10-28 | B | 8 | 0.0064465 | 2.528e-05
2010 | 2009-10-28 | B | 5 | 0.001185 | 1.58e-05
2010 | 2009-10-28 | B | 2 | 0.0015737 | 6.3201e-06
2010 | 2009-10-28 | B | 35 | 0.033401 | 0.0001106
2010 | 2009-10-28 | B | 21 | 0.023027 | 6.6361e-05
2010 | 2009-10-16 | B | 11 | 0.010984 | 3.476e-05
2010 | 2009-10-28 | C | 1814 | 1.5382 | 0.0057323
2010 | 2009-10-28 | C | 1052 | 0.21941 | 0.0033243
2010 | 2009-10-28 | B | 344 | 0.088051 | 0.001087
2010 | 2009-10-28 | C | 20 | 0.0044872 | 6.3201e-05
2010 | 2009-10-28 | C | 933 | 0.27788 | 0.0029483
2010 | 2009-10-29 | C | 467 | 0.16651 | 0.0014757
2010 | 2009-10-29 | C | 310 | 0.054858 | 0.00097961
2010 | 2009-10-29 | C | 249 | 0.014277 | 0.00078685
2010 | 2009-10-29 | B | 63 | 0.02389 | 0.00019908
2010 | 2009-10-29 | C | 36 | 0.0063706 | 0.00011376
2010 | 2009-10-29 | C | 2 | 0.00075841 | 6.3201e-06
2010 | 2009-10-29 | B | 174 | 0.11634 | 0.00054984
2010 | 2009-10-29 | B | 13 | 0.0071891 | 4.108e-05
2010 | 2009-10-29 | B | 1 | 6.6361e-05 | 3.16e-06
2010 | 2009-10-29 | B | 6 | 0.0075082 | 1.896e-05
2010 | 2009-10-29 | B | 1 | 0.0001422 | 3.16e-06
2010 | 2009-10-28 | B | 29 | 0.028958 | 9.1641e-05
2010 | 2009-10-29 | C | 119 | 0.0063927 | 0.00037604
2010 | 2009-10-29 | C | 220 | 0.064796 | 0.00069521
2010 | 2009-10-30 | C | 422 | 0.049682 | 0.0013335
2010 | 2009-10-29 | C | 56 | 0.092551 | 0.00017696
2010 | 2009-10-29 | C | 5028 | 0.38038 | 0.015889
2010 | 2009-10-29 | C | 373 | 0.089723 | 0.0011787
2010 | 2009-10-30 | B | 1 | 0.00059408 | 3.16e-06
2010 | 2009-10-30 | B | 1 | 0.0002844 | 3.16e-06
2010 | 2009-10-30 | B | 13 | 0.0053404 | 4.108e-05
2010 | 2009-10-30 | B | 3 | 0.00065413 | 9.4801e-06
2010 | 2009-10-30 | C | 1 | 0.00016432 | 3.16e-06
2010 | 2009-10-30 | B | 7 | 0.0059724 | 2.212e-05
2010 | 2009-10-30 | C | 15 | 0.001896 | 4.74e-05
2010 | 2009-10-30 | B | 29 | 0.022727 | 9.1641e-05
2010 | 2009-10-30 | C | 1177 | 0.014877 | 0.0037193
2010 | 2009-10-30 | C | 1 | 0.00061304 | 3.16e-06
2010 | 2009-10-31 | C | 53 | 0.0036846 | 0.00016748
2010 | 2009-10-31 | C | 59 | 0.019576 | 0.00018644
2010 | 2009-10-31 | B | 86 | 0.016577 | 0.00027176
2010 | 2009-10-31 | C | 930 | 0.21747 | 0.0029388
2010 | 2009-10-31 | C | 353 | 0.015532 | 0.0011155
2010 | 2009-10-31 | C | 930 | 0.15652 | 0.0029388
2010 | 2009-11-01 | C | 19 | 0.0037225 | 6.004e-05
2010 | 2009-11-01 | C | 265 | 0.0016748 | 0.00083741
2010 | 2009-10-29 | C | 12 | 0.067334 | 3.792e-05
2010 | 2009-11-01 | C | 638 | 0.0060483 | 0.0020161
2010 | 2009-11-02 | B | 46 | 0.017153 | 0.00014536
2010 | 2009-11-02 | B | 43 | 0.042038 | 0.00013588
2010 | 2009-11-02 | C | 86 | 0.049597 | 0.00027176
2010 | 2009-11-02 | C | 2 | 0.0004424 | 6.3201e-06
2010 | 2009-11-02 | B | 95 | 0.071748 | 0.0003002
2010 | 2009-11-02 | C | 34 | 0.0050497 | 0.00010744
2010 | 2009-11-03 | B | 271 | 0.059946 | 0.00085637
2010 | 2009-11-03 | C | 324 | 0.015358 | 0.0010238
2010 | 2009-11-03 | B | 74 | 0.052147 | 0.00023384
2010 | 2009-11-03 | B | 158 | 0.040442 | 0.00049928
2010 | 2009-11-03 | B | 43 | 0.01617 | 0.00013588
2010 | 2009-11-03 | B | 6 | 0.0072617 | 1.896e-05
2010 | 2009-11-03 | B | 3 | 0.0024079 | 9.4801e-06
2010 | 2009-11-03 | C | 88 | 0.013904 | 0.00027808
2010 | 2009-11-03 | B | 19 | 0.0057038 | 6.004e-05
2010 | 2009-11-04 | B | 99 | 0.043798 | 0.00031284
2010 | 2009-11-04 | B | 45 | 0.045078 | 0.0001422
2010 | 2009-11-04 | B | 8 | 0.0062442 | 2.528e-05
2010 | 2009-11-04 | C | 64 | 0.017191 | 0.00020224
2010 | 2009-11-04 | B | 62 | 0.01587 | 0.00019592
2010 | 2009-11-04 | C | 49 | 0.029967 | 0.00015484
2010 | 2009-11-04 | B | 22 | 0.016407 | 6.9521e-05
2010 | 2009-11-04 | C | 55 | 0.0078211 | 0.0001738
2010 | 2009-11-04 | B | 69 | 0.041428 | 0.00021804
2010 | 2009-11-04 | C | 69 | 0.034688 | 0.00021804
2010 | 2009-11-04 | B | 94 | 0.0023763 | 0.00029704
2010 | 2009-11-04 | C | 349 | 0.12825 | 0.0011028
2010 | 2009-11-05 | C | 228 | 0.046111 | 0.00072049
2010 | 2009-11-04 | B | 8 | 0.0051572 | 2.528e-05
2010 | 2009-11-05 | B | 384 | 0.095863 | 0.0012134
2010 | 2009-11-05 | C | 518 | 0.4634 | 0.0016369
2010 | 2009-11-05 | B | 45 | 0.035977 | 0.0001422
2010 | 2009-11-05 | B | 10 | 0.0010428 | 3.16e-05
2010 | 2009-11-05 | C | 182 | 0.055212 | 0.00057512
2010 | 2009-11-05 | C | 6 | 0.0017064 | 1.896e-05
2010 | 2009-11-05 | C | 59 | 0.03428 | 0.00018644
2010 | 2009-11-05 | C | 940 | 0.0059408 | 0.0029704
2010 | 2009-11-05 | C | 20 | 0.0001264 | 6.3201e-05
2010 | 2009-11-06 | B | 367 | 0.056827 | 0.0011597
2010 | 2009-11-06 | C | 31 | 0.0084246 | 9.7961e-05
2010 | 2009-11-06 | B | 3 | 0.0021615 | 9.4801e-06
2010 | 2009-11-06 | B | 1 | 0.000237 | 3.16e-06
2010 | 2009-11-06 | B | 2 | 0.000474 | 6.3201e-06
2010 | 2009-11-06 | B | 10 | 0.002054 | 3.16e-05
2010 | 2009-11-06 | C | 12 | 0.02954 | 3.792e-05
2010 | 2009-10-10 | B | 344 | 0.12936 | 0.001087
2010 | 2009-11-07 | B | 1 | 0.00017064 | 3.16e-06
2010 | 2009-11-06 | C | 525 | 0.051429 | 0.001659
2010 | 2009-11-06 | C | 87 | 0.0046737 | 0.00027492
2010 | 2009-11-07 | C | 6 | 0.0012514 | 1.896e-05
2010 | 2009-11-07 | C | 438 | 0.13997 | 0.0013841
2010 | 2009-11-07 | B | 1 | 0.00046136 | 3.16e-06
2010 | 2009-11-08 | B | 433 | 0.16283 | 0.0013683
2010 | 2009-11-08 | C | 361 | 0.048513 | 0.0011408
2010 | 2009-11-08 | B | 59 | 0.025729 | 0.00018644
2010 | 2009-11-08 | C | 238 | 0.037952 | 0.00075209
2010 | 2009-11-08 | B | 113 | 0.081772 | 0.00035708
2010 | 2009-11-08 | B | 2 | 0.0019845 | 6.3201e-06
2010 | 2009-11-08 | C | 134 | 0.047966 | 0.00042344
2010 | 2009-11-09 | C | 1101 | 0.020875 | 0.0034792
2010 | 2009-11-09 | C | 15 | 0.0069205 | 4.74e-05
2010 | 2009-11-09 | C | 15 | 0.001659 | 4.74e-05
2010 | 2009-11-10 | C | 5 | 0.001817 | 1.58e-05
2010 | 2009-11-10 | B | 14 | 0.0073881 | 4.424e-05
2010 | 2009-11-09 | B | 3 | 0.0014125 | 9.4801e-06
2010 | 2009-11-10 | C | 21 | 0.004977 | 6.6361e-05
2010 | 2009-11-10 | C | 279 | 0.10606 | 0.00088165
2010 | 2009-11-10 | B | 25 | 0.023305 | 7.9001e-05
2010 | 2009-11-10 | B | 59 | 0.044746 | 0.00018644
2010 | 2009-11-10 | B | 8 | 0.009202 | 2.528e-05
2010 | 2009-11-10 | C | 54 | 0.024478 | 0.00017064
2010 | 2009-11-10 | C | 271 | 0.045387 | 0.00085637
2010 | 2009-11-10 | B | 7 | 0.0019687 | 2.212e-05
2010 | 2009-11-11 | B | 1 | 0.00040448 | 3.16e-06
2010 | 2009-11-11 | C | 176 | 0.023915 | 0.00055616
2010 | 2009-11-11 | C | 1311 | 0.2259 | 0.0041428
2010 | 2009-11-11 | B | 2 | 0.0024648 | 6.3201e-06
2010 | 2009-11-11 | B | 35 | 0.010286 | 0.0001106
2010 | 2009-11-11 | C | 271 | 0.036824 | 0.00085637
2010 | 2009-11-11 | C | 1 | 8.8481e-05 | 3.16e-06
2010 | 2009-11-11 | B | 20 | 0.012071 | 6.3201e-05
2010 | 2009-11-12 | C | 271 | 0.080666 | 0.00085637
2010 | 2009-11-12 | B | 3 | 0.0034128 | 9.4801e-06
2010 | 2009-11-12 | B | 34 | 0.013215 | 0.00010744
2010 | 2009-11-12 | B | 21 | 0.02316 | 6.6361e-05
2010 | 2009-11-12 | B | 32 | 0.03337 | 0.00010112
2010 | 2009-11-12 | B | 11 | 0.0038584 | 3.476e-05
2010 | 2009-11-13 | C | 4 | 0.00021488 | 1.264e-05
2010 | 2009-11-13 | C | 766 | 0.17145 | 0.0024206
2010 | 2009-11-13 | B | 7 | 0.0053088 | 2.212e-05
2010 | 2009-11-13 | C | 145 | 0.038031 | 0.0004582
2010 | 2009-11-13 | B | 45 | 0.023274 | 0.0001422
2010 | 2009-11-13 | C | 46 | 0.0037794 | 0.00014536
2010 | 2009-11-13 | C | 4 | 0.0036656 | 1.264e-05
2010 | 2009-11-13 | C | 424 | 0.020098 | 0.0013399
2010 | 2009-11-14 | C | 83 | 0.10091 | 0.00026228
2010 | 2009-11-14 | C | 162 | 0.022525 | 0.00051192
2010 | 2009-11-14 | C | 954 | 0.20661 | 0.0030147
2010 | 2009-11-15 | C | 21 | 0.0045789 | 6.6361e-05
2010 | 2009-11-15 | C | 340 | 0.074501 | 0.0010744
2010 | 2009-11-15 | C | 364 | 0.12599 | 0.0011502
2010 | 2009-11-16 | C | 302 | 0.045808 | 0.00095433
2010 | 2009-11-16 | C | 121 | 0.029802 | 0.00038236
2010 | 2009-11-16 | C | 8 | 0.0022752 | 2.528e-05
2010 | 2009-11-16 | C | 20 | 0.00316 | 6.3201e-05
2010 | 2009-11-16 | B | 45 | 0.024459 | 0.0001422
2010 | 2009-11-14 | C | 302 | 0.084935 | 0.00095433
2010 | 2009-11-16 | B | 10 | 0.0010112 | 3.16e-05
2010 | 2009-11-16 | C | 11 | 0.0018423 | 3.476e-05
2010 | 2009-11-16 | C | 155 | 0.018887 | 0.0004898
2010 | 2009-11-16 | C | 226 | 0.034504 | 0.00071417
2010 | 2009-11-16 | C | 5 | 0.0012008 | 1.58e-05
2010 | 2009-11-16 | B | 28 | 0.0046895 | 8.8481e-05
2010 | 2009-11-16 | C | 5 | 0.010649 | 1.58e-05
2010 | 2009-11-17 | C | 10 | 0.0029072 | 3.16e-05
2010 | 2009-11-17 | B | 17 | 0.017996 | 5.372e-05
2010 | 2009-11-17 | B | 22 | 0.0089682 | 6.9521e-05
2010 | 2009-11-17 | B | 61 | 0.062262 | 0.00019276
2010 | 2009-11-17 | B | 223 | 0.070469 | 0.00070469
2010 | 2009-11-17 | B | 5 | 0.000474 | 1.58e-05
2010 | 2009-11-17 | B | 67 | 0.049119 | 0.00021172
2010 | 2009-11-18 | C | 64 | 0.013146 | 0.00020224
2010 | 2009-11-18 | C | 262 | 0.16393 | 0.00082793
2010 | 2009-11-17 | C | 96 | 0.036707 | 0.00030336
2010 | 2009-11-18 | B | 23 | 0.0010175 | 7.2681e-05
2010 | 2009-11-18 | C | 3 | 0.0010807 | 9.4801e-06
2010 | 2009-11-18 | C | 320 | 0.055323 | 0.0010112
2010 | 2009-11-18 | C | 143 | 0.032017 | 0.00045188
2010 | 2009-11-18 | C | 9 | 0.0017917 | 2.844e-05
2010 | 2009-11-18 | C | 40 | 0.0077105 | 0.0001264
2010 | 2009-11-18 | C | 7 | 0.0023226 | 2.212e-05
2010 | 2009-11-18 | C | 44 | 0.0090377 | 0.00013904
2010 | 2009-11-18 | C | 197 | 0.019175 | 0.00062252
2010 | 2009-11-18 | C | 744 | 0.53509 | 0.0023511
2010 | 2009-11-18 | C | 10 | 0.00063201 | 3.16e-05
2010 | 2009-11-19 | B | 171 | 0.14806 | 0.00054036
2010 | 2009-11-19 | C | 26 | 0.0065729 | 8.2161e-05
2010 | 2009-11-19 | B | 4 | 0.0016938 | 1.264e-05
2010 | 2009-11-19 | B | 54 | 0.056312 | 0.00017064
2010 | 2009-11-19 | B | 15 | 0.01422 | 4.74e-05
2010 | 2009-11-17 | B | 2 | 0.00059724 | 6.3201e-06
2010 | 2009-11-19 | B | 117 | 0.036603 | 0.00036972
2010 | 2009-11-19 | B | 234 | 0.2625 | 0.00073945
2010 | 2009-11-19 | B | 4 | 0.0012008 | 1.264e-05
2010 | 2009-11-19 | B | 1296 | 0.14104 | 0.0040954
2010 | 2009-11-19 | C | 19 | 0.00036024 | 6.004e-05
2010 | 2009-11-19 | C | 177 | 0.001678 | 0.00055932
2010 | 2009-11-19 | C | 39 | 0.011954 | 0.00012324
2010 | 2009-11-20 | C | 70 | 0.0035392 | 0.0002212
2010 | 2009-11-20 | C | 894 | 0.12173 | 0.0028251
2010 | 2009-11-20 | B | 44 | 0.027391 | 0.00013904
2010 | 2009-11-20 | B | 45 | 0.028014 | 0.0001422
2010 | 2009-11-20 | C | 476 | 0.1733 | 0.0015042
2010 | 2009-11-21 | C | 27 | 0.0040828 | 8.5321e-05
2010 | 2009-11-21 | C | 29 | 0.027034 | 9.1641e-05
2010 | 2009-11-21 | C | 564 | 0.17497 | 0.0017823
2010 | 2009-11-21 | C | 254 | 0.092023 | 0.00080265
2010 | 2009-11-21 | C | 10 | 0.02686 | 3.16e-05
2010 | 2009-11-22 | C | 246 | 0.032261 | 0.00077737
2010 | 2009-11-22 | C | 173 | 0.16265 | 0.00054668
2010 | 2009-11-23 | C | 1 | 2.212e-05 | 3.16e-06
2010 | 2009-11-22 | C | 950 | 0.063043 | 0.003002
2010 | 2009-11-23 | C | 159 | 0.023615 | 0.00050244
2010 | 2009-11-21 | C | 821 | 0.11415 | 0.0025944
2010 | 2009-11-23 | C | 32 | 0.0057639 | 0.00010112
2010 | 2009-11-23 | C | 2 | 0.00017064 | 6.3201e-06
2010 | 2009-11-23 | B | 12 | 0.012514 | 3.792e-05
2010 | 2009-11-23 | B | 12 | 0.0045504 | 3.792e-05
2010 | 2009-11-23 | B | 12 | 0.0018202 | 3.792e-05
2010 | 2009-11-23 | C | 96 | 0.10295 | 0.00030336
2010 | 2009-11-23 | C | 7 | 0.001659 | 2.212e-05
2010 | 2009-11-23 | C | 15 | 0.0027492 | 4.74e-05
2010 | 2009-11-23 | C | 749 | 0.19408 | 0.0023669
2010 | 2009-11-23 | C | 119 | 0.098147 | 0.00037604
2010 | 2009-11-23 | C | 947 | 0.25953 | 0.0029925
2010 | 2009-11-24 | C | 9 | 0.00099541 | 2.844e-05
2010 | 2009-11-24 | B | 108 | 0.040954 | 0.00034128
2010 | 2009-11-24 | B | 32 | 0.03337 | 0.00010112
2010 | 2009-11-24 | B | 47 | 0.062379 | 0.00014852
2010 | 2009-11-24 | B | 27 | 0.016808 | 8.5321e-05
2010 | 2009-11-24 | B | 171 | 0.11402 | 0.00054036
2010 | 2009-11-24 | B | 73 | 0.055136 | 0.00023068
2010 | 2009-11-24 | B | 1 | 0.00099541 | 3.16e-06
2010 | 2009-11-24 | B | 29 | 0.020528 | 9.1641e-05
2010 | 2009-11-24 | B | 97 | 0.080922 | 0.00030652
2010 | 2009-11-24 | B | 2 | 0.0020414 | 6.3201e-06
2010 | 2009-11-24 | C | 11 | 0.013904 | 3.476e-05
2010 | 2009-11-25 | B | 225 | 0.12798 | 0.00071101
2010 | 2009-11-24 | C | 2 | 0.00042344 | 6.3201e-06
2010 | 2009-11-24 | C | 4 | 0.00060672 | 1.264e-05
2010 | 2009-11-24 | C | 23 | 0.097828 | 7.2681e-05
2010 | 2009-11-25 | C | 88 | 0.0055616 | 0.00027808
2010 | 2009-11-25 | C | 178 | 0.0095622 | 0.00056248
2010 | 2009-11-25 | C | 882 | 0.026652 | 0.0027871
2010 | 2009-11-25 | B | 24 | 0.024193 | 7.5841e-05
2010 | 2009-11-25 | B | 1 | 0.00072049 | 3.16e-06
2010 | 2009-11-25 | B | 1 | 0.0010049 | 3.16e-06
2010 | 2009-11-25 | B | 6 | 0.0071859 | 1.896e-05
2010 | 2009-11-26 | C | 341 | 0.048491 | 0.0010776
2010 | 2009-11-26 | B | 49 | 0.043046 | 0.00015484
2010 | 2009-11-26 | B | 32 | 0.03337 | 0.00010112
2010 | 2009-11-26 | C | 146 | 0.033218 | 0.00046136
2010 | 2009-11-26 | B | 32 | 0.042471 | 0.00010112
2010 | 2009-11-26 | C | 3 | 0.0013936 | 9.4801e-06
2010 | 2009-11-26 | B | 55 | 0.030241 | 0.0001738
2010 | 2009-11-26 | C | 2 | 0.00069521 | 6.3201e-06
2010 | 2009-11-26 | C | 61 | 0.015999 | 0.00019276
2010 | 2009-11-26 | C | 124 | 0.11291 | 0.00039184
2010 | 2009-11-26 | C | 451 | 0.038555 | 0.0014252
2010 | 2009-11-27 | B | 4 | 0.0022752 | 1.264e-05
2010 | 2009-11-27 | B | 115 | 0.065413 | 0.0003634
2010 | 2009-11-27 | C | 1 | 0.0001106 | 3.16e-06
2010 | 2009-11-27 | C | 28 | 0.0030083 | 8.8481e-05
2010 | 2009-11-27 | B | 69 | 0.0028345 | 0.00021804
2010 | 2009-11-27 | C | 69 | 0.0013746 | 0.00021804
2010 | 2009-11-28 | C | 91 | 0.012653 | 0.00028756
2010 | 2009-11-28 | C | 230 | 0.048822 | 0.00072681
2010 | 2009-11-27 | B | 44 | 0.040357 | 0.00013904
2010 | 2009-11-28 | C | 253 | 0.082363 | 0.00079949
2010 | 2009-11-29 | C | 171 | 0.083662 | 0.00054036
2010 | 2009-11-28 | C | 1625 | 0.44367 | 0.005135
2010 | 2009-11-29 | C | 53 | 0.011891 | 0.00016748
2010 | 2009-11-29 | C | 78 | 0.045846 | 0.00024648
2010 | 2009-11-29 | C | 88 | 0.030867 | 0.00027808
2010 | 2009-11-27 | B | 2 | 0.00096065 | 6.3201e-06
2010 | 2009-11-30 | B | 30 | 0.027018 | 9.4801e-05
2010 | 2009-11-30 | C | 21 | 0.0039153 | 6.6361e-05
2010 | 2009-11-30 | B | 96 | 0.050055 | 0.00030336
2010 | 2009-11-30 | C | 580 | 0.17676 | 0.0018328
2010 | 2009-12-01 | C | 333 | 0.028412 | 0.0010523
2010 | 2009-12-01 | B | 32 | 0.024471 | 0.00010112
2010 | 2009-12-02 | C | 246 | 0.045062 | 0.00077737
2010 | 2009-12-01 | C | 2962 | 0.82028 | 0.00936
2010 | 2009-12-02 | C | 471 | 0.086834 | 0.0014884
2010 | 2009-12-02 | C | 113 | 0.021782 | 0.00035708
2010 | 2009-12-02 | C | 928 | 0.07038 | 0.0029325
2010 | 2009-12-02 | C | 106 | 0.044215 | 0.00033496
2010 | 2009-12-02 | C | 167 | 0.065662 | 0.00052772
2010 | 2009-12-02 | C | 196 | 0.03902 | 0.00061936
2010 | 2009-12-02 | B | 1 | 0.0011376 | 3.16e-06
2010 | 2009-12-02 | C | 32 | 0.016483 | 0.00010112
2010 | 2009-12-02 | C | 1188 | 0.018771 | 0.0037541
2010 | 2009-12-02 | B | 178 | 0.067498 | 0.00056248
2010 | 2009-12-02 | B | 177 | 0.055996 | 0.00055932
2010 | 2009-12-02 | C | 82 | 0.016843 | 0.00025912
2010 | 2009-12-02 | C | 196 | 0.022917 | 0.00061936
2010 | 2009-12-02 | C | 294 | 0.028744 | 0.00092905
2010 | 2009-12-02 | C | 737 | 0.21304 | 0.0023289
2010 | 2009-12-02 | C | 915 | 0.16249 | 0.0028914
2010 | 2009-12-02 | C | 150 | 0.057828 | 0.000474
2010 | 2009-12-03 | C | 241 | 0.015993 | 0.00076157
2010 | 2009-12-03 | C | 1862 | 0.23408 | 0.005884
2010 | 2009-12-03 | C | 21 | 0.0036498 | 6.6361e-05
2010 | 2009-12-03 | C | 271 | 0.054254 | 0.00085637
2010 | 2009-12-03 | B | 58 | 0.076978 | 0.00018328
2010 | 2009-12-03 | B | 5 | 0.005688 | 1.58e-05
2010 | 2009-12-03 | B | 17 | 0.020897 | 5.372e-05
2010 | 2009-12-03 | B | 43 | 0.0066582 | 0.00013588
2010 | 2009-12-03 | C | 130 | 0.027963 | 0.0004108
2010 | 2009-12-03 | C | 637 | 0.17221 | 0.0020129
2010 | 2009-12-03 | B | 57 | 0.035304 | 0.00018012
2010 | 2009-12-03 | B | 3 | 0.0023416 | 9.4801e-06
2010 | 2009-12-03 | B | 142 | 0.02303 | 0.00044872
2010 | 2009-12-03 | B | 4 | 0.0016432 | 1.264e-05
2010 | 2009-12-03 | B | 76 | 0.012122 | 0.00024016
2010 | 2009-12-03 | C | 1821 | 0.10933 | 0.0057544
2010 | 2009-12-02 | B | 38 | 0.032422 | 0.00012008
2010 | 2009-12-02 | C | 239 | 0.066231 | 0.00075525
2010 | 2009-12-02 | C | 250 | 0.08241 | 0.00079001
2010 | 2009-12-02 | C | 1124 | 0.053278 | 0.0035519
2010 | 2009-12-02 | C | 1001 | 0.36827 | 0.0031632
2010 | 2009-12-02 | C | 226 | 0.21605 | 0.00071417
2010 | 2009-12-04 | C | 246 | 0.017879 | 0.00077737
2010 | 2009-12-03 | B | 17 | 0.020897 | 5.372e-05
2010 | 2009-12-03 | B | 1 | 0.0011376 | 3.16e-06
2010 | 2009-12-03 | C | 335 | 0.09943 | 0.0010586
2010 | 2009-12-04 | B | 2 | 0.00094801 | 6.3201e-06
2010 | 2009-12-03 | C | 339 | 0.16055 | 0.0010712
2010 | 2009-12-03 | C | 370 | 0.079174 | 0.0011692
2010 | 2009-12-04 | C | 505 | 0.073407 | 0.0015958
2010 | 2009-12-04 | C | 819 | 0.15011 | 0.0025881
2010 | 2009-12-03 | C | 1055 | 0.19956 | 0.0033338
2010 | 2009-12-04 | B | 1 | 0.0010428 | 3.16e-06
2010 | 2009-12-03 | C | 6 | 0.022632 | 1.896e-05
2010 | 2009-12-03 | C | 662 | 0.060666 | 0.0020919
2010 | 2009-12-04 | C | 130 | 0.025653 | 0.0004108
2010 | 2009-12-03 | C | 200 | 0.14242 | 0.00063201
2010 | 2009-12-04 | C | 5 | 0.001106 | 1.58e-05
2010 | 2009-12-05 | C | 286 | 0.013557 | 0.00090377
2010 | 2009-12-05 | C | 332 | 0.09221 | 0.0010491
2010 | 2009-12-05 | C | 114 | 0.095818 | 0.00036024
2010 | 2009-12-05 | C | 1355 | 0.24835 | 0.0042818
2010 | 2009-12-05 | C | 5 | 0.0010049 | 1.58e-05
2010 | 2009-12-05 | B | 3 | 0.0012893 | 9.4801e-06
2010 | 2009-12-05 | C | 265 | 0.012561 | 0.00083741
2010 | 2009-12-06 | C | 67 | 0.020114 | 0.00021172
2010 | 2009-12-06 | C | 2521 | 0.23672 | 0.0079664
2010 | 2009-12-06 | C | 114 | 0.016571 | 0.00036024
2010 | 2009-12-06 | C | 10 | 0.001106 | 3.16e-05
2010 | 2009-12-07 | C | 201 | 0.0095275 | 0.00063517
2010 | 2009-12-04 | C | 547 | 0.13828 | 0.0017285
2010 | 2009-12-03 | C | 79 | 0.027211 | 0.00024964
2010 | 2009-12-07 | B | 13 | 0.0069837 | 4.108e-05
2010 | 2009-12-03 | C | 418 | 0.22587 | 0.0013209
2010 | 2009-12-07 | B | 64 | 0.067549 | 0.00020224
2010 | 2009-12-05 | C | 3 | 0.026317 | 9.4801e-06
2010 | 2009-12-07 | B | 4 | 0.004285 | 1.264e-05
2010 | 2009-12-07 | C | 15 | 0.010807 | 4.74e-05
2010 | 2009-12-07 | C | 1744 | 0.027555 | 0.0055111
2010 | 2009-12-08 | B | 54 | 0.04266 | 0.00017064
2010 | 2009-12-08 | B | 64 | 0.075841 | 0.00020224
2010 | 2009-12-08 | B | 125 | 0.071502 | 0.000395
2010 | 2009-12-08 | B | 945 | 0.054994 | 0.0029862
2010 | 2009-12-08 | B | 62 | 0.075234 | 0.00019592
2010 | 2009-12-09 | C | 62 | 0.00039184 | 0.00019592
2010 | 2009-12-09 | B | 6 | 0.0067877 | 1.896e-05
2010 | 2009-12-09 | B | 102 | 0.10185 | 0.00032232
2010 | 2009-12-09 | C | 1 | 0.00030968 | 3.16e-06
2010 | 2009-12-09 | C | 2928 | 0.04035 | 0.0092526
2010 | 2009-12-09 | C | 97 | 0.027919 | 0.00030652
2010 | 2009-12-10 | C | 12 | 0.00068257 | 3.792e-05
2010 | 2009-12-10 | C | 124 | 0.053834 | 0.00039184
2010 | 2009-12-10 | C | 894 | 0.24005 | 0.0028251
2010 | 2009-12-10 | B | 16 | 0.018202 | 5.056e-05
2010 | 2009-12-10 | B | 113 | 0.01964 | 0.00035708
2010 | 2009-12-10 | C | 421 | 0.0053215 | 0.0013304
2010 | 2009-12-10 | C | 4358 | 0.74366 | 0.013771
2010 | 2009-12-11 | C | 29 | 0.0062316 | 9.1641e-05
2010 | 2009-12-11 | B | 6 | 0.0010049 | 1.896e-05
2010 | 2009-12-11 | B | 6 | 0.0010049 | 1.896e-05
2010 | 2009-12-11 | B | 185 | 0.030399 | 0.0005846
2010 | 2009-12-11 | B | 12 | 0.0045884 | 3.792e-05
2010 | 2009-12-11 | B | 1 | 0.00073313 | 3.16e-06
2010 | 2009-12-11 | B | 10 | 0.0079949 | 3.16e-05
2010 | 2009-12-11 | C | 229 | 0.032792 | 0.00072365
2010 | 2009-12-11 | C | 87 | 0.01897 | 0.00027492
2010 | 2009-12-12 | C | 286 | 0.013557 | 0.00090377
2010 | 2009-12-11 | C | 580 | 0.075177 | 0.0018328
2010 | 2009-12-12 | C | 18 | 0.0032422 | 5.688e-05
2010 | 2009-12-12 | C | 97 | 0.042082 | 0.00030652
2010 | 2009-12-12 | C | 1 | 0.0001106 | 3.16e-06
2010 | 2009-12-12 | C | 207 | 0.083621 | 0.00065413
2010 | 2009-12-12 | C | 107 | 0.0541 | 0.00033812
2010 | 2009-12-12 | C | 1125 | 0.10665 | 0.003555
2010 | 2009-12-12 | C | 21 | 0.0017917 | 6.6361e-05
2010 | 2009-12-13 | C | 61 | 0.0073249 | 0.00019276
2010 | 2009-12-13 | C | 236 | 0.042796 | 0.00074577
2010 | 2009-12-13 | C | 16 | 0.0024269 | 5.056e-05
2010 | 2009-12-13 | C | 127 | 0.0064465 | 0.00040132
2010 | 2009-12-14 | C | 414 | 0.024857 | 0.0013083
2010 | 2009-12-14 | B | 38 | 0.018012 | 0.00012008
2010 | 2009-12-14 | B | 5 | 0.002844 | 1.58e-05
2010 | 2009-12-14 | C | 239 | 0.018126 | 0.00075525
2010 | 2009-12-14 | C | 2 | 0.0005056 | 6.3201e-06
2010 | 2009-12-14 | B | 53 | 0.02261 | 0.00016748
2010 | 2009-12-14 | B | 5 | 0.00237 | 1.58e-05
2010 | 2009-12-14 | C | 34 | 0.012785 | 0.00010744
2010 | 2009-12-14 | C | 278 | 0.063807 | 0.00087849
2010 | 2009-12-15 | B | 54 | 0.022183 | 0.00017064
2010 | 2009-12-15 | C | 2 | 0.0013462 | 6.3201e-06
2010 | 2009-12-15 | B | 106 | 0.10216 | 0.00033496
2010 | 2009-12-15 | C | 1305 | 0.33912 | 0.0041238
2010 | 2009-12-15 | B | 4 | 0.0019466 | 1.264e-05
2010 | 2009-12-15 | B | 42 | 0.041807 | 0.00013272
2010 | 2009-12-15 | C | 7 | 0.00050876 | 2.212e-05
2010 | 2009-12-15 | B | 254 | 0.14207 | 0.00080265
2010 | 2009-12-15 | B | 27 | 0.018088 | 8.5321e-05
2010 | 2009-12-15 | B | 4 | 0.0034381 | 1.264e-05
2010 | 2009-12-15 | B | 96 | 0.094042 | 0.00030336
2010 | 2009-12-15 | B | 255 | 0.1249 | 0.00080581
2010 | 2009-12-15 | C | 52 | 0.004108 | 0.00016432
2010 | 2009-12-16 | B | 20 | 0.003792 | 6.3201e-05
2010 | 2009-12-16 | B | 20 | 0.022436 | 6.3201e-05
2010 | 2009-12-16 | B | 16 | 0.0052077 | 5.056e-05
2010 | 2009-12-16 | B | 1 | 0.0003318 | 3.16e-06
2010 | 2009-12-16 | B | 102 | 0.093796 | 0.00032232
2010 | 2009-12-16 | B | 29 | 0.037023 | 9.1641e-05
2010 | 2009-12-16 | B | 114 | 0.0092178 | 0.00036024
2010 | 2009-12-17 | B | 24 | 0.011452 | 7.5841e-05
2010 | 2009-12-17 | B | 109 | 0.0124 | 0.00034444
2010 | 2009-12-16 | B | 147 | 0.10591 | 0.00046452
2010 | 2009-12-17 | C | 178 | 0.019706 | 0.00056248
2010 | 2009-12-17 | B | 126 | 0.13538 | 0.00039816
2010 | 2009-12-17 | C | 241 | 0.05123 | 0.00076157
2010 | 2009-12-17 | B | 116 | 0.099541 | 0.00036656
2010 | 2009-12-17 | B | 23 | 0.0093031 | 7.2681e-05
2010 | 2009-12-17 | B | 80 | 0.024016 | 0.0002528
2010 | 2009-12-18 | C | 232 | 0.079623 | 0.00073313
2010 | 2009-12-17 | C | 3 | 0.0012609 | 9.4801e-06
2010 | 2009-12-18 | C | 30 | 0.0057828 | 9.4801e-05
2010 | 2009-12-18 | C | 16 | 0.002528 | 5.056e-05
2010 | 2009-12-18 | B | 21 | 0.023558 | 6.6361e-05
2010 | 2009-12-18 | B | 3 | 0.00080581 | 9.4801e-06
2010 | 2009-12-18 | C | 239 | 0.064196 | 0.00075525
2010 | 2009-12-18 | C | 231 | 0.084837 | 0.00072997
2010 | 2009-12-18 | C | 79 | 0.09062 | 0.00024964
2010 | 2009-12-18 | B | 60 | 0.044746 | 0.0001896
2010 | 2009-12-17 | B | 9 | 0.0069963 | 2.844e-05
2010 | 2009-12-18 | C | 21 | 0.0043798 | 6.6361e-05
2010 | 2009-12-20 | C | 688 | 0.041308 | 0.0021741
2010 | 2009-12-20 | C | 61 | 0.01253 | 0.00019276
2010 | 2009-12-20 | C | 177 | 0.16053 | 0.00055932
2010 | 2009-12-20 | C | 964 | 0.83812 | 0.0030463
2010 | 2009-09-18 | B | 6 | 0.0020667 | 1.896e-05
2010 | 2009-12-20 | C | 240 | 0.01441 | 0.00075841
2010 | 2009-12-20 | C | 184 | 0.067448 | 0.00058144
2010 | 2009-12-21 | C | 1146 | 0.20397 | 0.0036214
2010 | 2009-12-21 | C | 99 | 0.029827 | 0.00031284
2010 | 2009-12-21 | B | 4 | 0.0022752 | 1.264e-05
2010 | 2009-12-21 | C | 553 | 0.25688 | 0.0017475
2010 | 2009-12-21 | C | 330 | 0.047628 | 0.0010428
2010 | 2009-12-21 | B | 83 | 0.067406 | 0.00026228
2010 | 2009-12-21 | C | 25 | 0.069995 | 7.9001e-05
2010 | 2009-12-21 | C | 488 | 0.10803 | 0.0015421
2010 | 2009-12-22 | B | 1 | 0.00016748 | 3.16e-06
2010 | 2009-12-22 | B | 11 | 0.0066045 | 3.476e-05
2010 | 2009-12-22 | C | 33 | 0.0042755 | 0.00010428
2010 | 2009-12-22 | B | 5 | 0.0057038 | 1.58e-05
2010 | 2009-12-21 | B | 114 | 0.19597 | 0.00036024
2010 | 2009-12-23 | C | 354 | 0.062085 | 0.0011186
2010 | 2009-12-23 | B | 10 | 0.012008 | 3.16e-05
2010 | 2009-12-23 | B | 9 | 0.0013367 | 2.844e-05
2010 | 2009-12-24 | C | 260 | 0.073423 | 0.00082161
2010 | 2009-12-26 | B | 4 | 0.00058144 | 1.264e-05
2010 | 2009-12-26 | C | 9 | 0.0013367 | 2.844e-05
2010 | 2009-12-26 | C | 1971 | 0.193 | 0.0062284
2010 | 2009-12-27 | C | 47 | 0.0029704 | 0.00014852
2010 | 2009-12-27 | C | 343 | 0.070247 | 0.0010839
2010 | 2009-12-27 | C | 1344 | 0.32614 | 0.0042471
2010 | 2009-12-28 | C | 33 | 0.028469 | 0.00010428
2010 | 2009-12-29 | C | 362 | 0.063855 | 0.0011439
2010 | 2009-12-29 | C | 41 | 0.028892 | 0.00012956
2010 | 2009-12-29 | C | 564 | 0.10285 | 0.0017823
2010 | 2009-12-29 | C | 540 | 0.027303 | 0.0017064
2010 | 2009-12-29 | C | 1328 | 0.17747 | 0.0041965
2010 | 2009-12-29 | C | 77 | 0.1129 | 0.00024332
2010 | 2009-12-29 | C | 41 | 0.011531 | 0.00012956
2010 | 2009-12-30 | B | 5 | 0.00079001 | 1.58e-05
2010 | 2009-12-30 | C | 38 | 0.0018012 | 0.00012008
2010 | 2009-12-30 | C | 20 | 0.0014536 | 6.3201e-05
2010 | 2009-12-30 | C | 114 | 0.024206 | 0.00036024
2010 | 2009-12-30 | C | 949 | 0.12898 | 0.0029989
2010 | 2009-12-30 | C | 53 | 0.004522 | 0.00016748
2010 | 2009-12-30 | C | 188 | 0.0095054 | 0.00059408
2010 | 2009-12-30 | C | 63 | 0.021302 | 0.00019908
2010 | 2009-12-30 | C | 242 | 0.16136 | 0.00076473
2010 | 2009-12-30 | C | 499 | 0.031537 | 0.0015769
2010 | 2009-12-30 | C | 263 | 0.043431 | 0.00083109
2010 | 2009-12-30 | C | 525 | 0.04977 | 0.001659
2010 | 2009-12-30 | C | 233 | 0.012517 | 0.00073629
2010 | 2009-12-30 | C | 343 | 0.1012 | 0.0010839
2010 | 2009-12-30 | C | 756 | 0.16796 | 0.002389
2010 | 2009-12-30 | C | 18 | 0.0046642 | 5.688e-05
2010 | 2009-12-30 | C | 1147 | 0.27846 | 0.0036245
2010 | 2009-12-31 | C | 52 | 0.018739 | 0.00016432
2010 | 2009-12-31 | B | 1 | 0.00074261 | 3.16e-06
2010 | 2009-12-31 | C | 18 | 0.002844 | 5.688e-05
2010 | 2009-12-30 | C | 6 | 0.025615 | 1.896e-05
2010 | 2009-12-30 | C | 176 | 0.1821 | 0.00055616
2010 | 2009-12-31 | C | 628 | 0.12546 | 0.0019845
2010 | 2009-12-31 | C | 726 | 0.263 | 0.0022942
2010 | 2010-01-01 | C | 3 | 0.00021804 | 9.4801e-06
2010 | 2010-01-01 | C | 40 | 0.013651 | 0.0001264
2010 | 2010-01-01 | C | 11 | 0.0037541 | 3.476e-05
2010 | 2010-01-01 | C | 240 | 0.12376 | 0.00075841
2010 | 2010-01-02 | C | 811 | 0.12558 | 0.0025628
2010 | 2010-01-02 | C | 75 | 0.025587 | 0.000237
2010 | 2010-01-02 | C | 6 | 0.00064465 | 1.896e-05
2010 | 2010-01-02 | C | 269 | 0.12581 | 0.00085005
2010 | 2010-01-03 | C | 5 | 0.0003002 | 1.58e-05
2010 | 2010-01-03 | C | 2 | 0.00055616 | 6.3201e-06
2010 | 2010-01-03 | C | 27 | 0.0067403 | 8.5321e-05
2010 | 2010-01-03 | C | 3879 | 0.39225 | 0.012258
2010 | 2010-01-03 | C | 262 | 0.088342 | 0.00082793
2010 | 2010-01-04 | C | 1527 | 0.22968 | 0.0048254
2010 | 2010-01-04 | C | 921 | 0.29433 | 0.0029104
2010 | 2010-01-04 | C | 217 | 0.062708 | 0.00068573
2010 | 2010-01-04 | C | 244 | 0.056084 | 0.00077105
2010 | 2010-01-04 | C | 613 | 0.10785 | 0.0019371
2010 | 2010-01-04 | C | 174 | 0.013196 | 0.00054984
2010 | 2010-01-04 | C | 320 | 0.016179 | 0.0010112
2010 | 2010-01-04 | C | 1246 | 0.25036 | 0.0039374
2010 | 2010-01-04 | C | 34 | 0.0018265 | 0.00010744
2010 | 2010-01-04 | C | 1180 | 0.19112 | 0.0037288
2010 | 2010-01-04 | C | 83 | 0.031474 | 0.00026228
2010 | 2010-01-04 | C | 3 | 0.0015168 | 9.4801e-06
2010 | 2009-12-23 | B | 4 | 0.0016559 | 1.264e-05
2010 | 2010-01-04 | C | 2 | 0.0089998 | 6.3201e-06
2010 | 2010-01-05 | C | 2 | 0.00048664 | 6.3201e-06
2010 | 2010-01-05 | C | 5 | 0.0004424 | 1.58e-05
2010 | 2010-01-06 | C | 18 | 0.011035 | 5.688e-05
2010 | 2010-01-06 | C | 244 | 0.071707 | 0.00077105
2010 | 2010-01-07 | C | 3098 | 0.039159 | 0.0097898
2010 | 2010-01-07 | C | 273 | 0.029331 | 0.00086269
2010 | 2010-01-08 | C | 756 | 0.21196 | 0.002389
2010 | 2010-01-08 | C | 1264 | 0.15178 | 0.0039943
2010 | 2010-01-08 | C | 38 | 0.0085257 | 0.00012008
2010 | 2010-01-08 | C | 14 | 0.00061936 | 4.424e-05
2010 | 2010-01-08 | C | 33 | 0.0018771 | 0.00010428
2010 | 2010-01-08 | C | 14 | 0.0010618 | 4.424e-05
2010 | 2010-01-08 | C | 6633 | 1.614 | 0.02096
2010 | 2010-01-08 | C | 4358 | 1.0879 | 0.013771
2010 | 2010-01-10 | C | 242 | 0.045884 | 0.00076473
2010 | 2010-01-10 | C | 271 | 0.29444 | 0.00085637
2010 | 2010-01-10 | C | 89 | 0.0087185 | 0.00028124
2010 | 2010-01-11 | C | 44 | 0.0065349 | 0.00013904
2010 | 2010-01-11 | C | 399 | 0.076081 | 0.0012609
2010 | 2010-01-11 | C | 326 | 0.095806 | 0.0010302
2010 | 2010-01-11 | C | 35 | 0.003318 | 0.0001106
2010 | 2010-01-11 | C | 24 | 0.00091009 | 7.5841e-05
2010 | 2010-01-11 | C | 2 | 0.00069521 | 6.3201e-06
2010 | 2010-01-11 | C | 77 | 0.015573 | 0.00024332
2010 | 2010-01-11 | C | 110 | 0.027461 | 0.0003476
2010 | 2010-01-11 | C | 27 | 0.010238 | 8.5321e-05
2010 | 2010-01-11 | C | 2986 | 0.28698 | 0.0094358
2010 | 2010-01-11 | C | 1505 | 1.0273 | 0.0047558
2010 | 2010-01-11 | C | 556 | 0.35826 | 0.001757
2010 | 2010-01-12 | C | 124 | 0.061519 | 0.00039184
2010 | 2010-01-12 | B | 1 | 0.00019908 | 3.16e-06
2010 | 2010-01-12 | C | 352 | 0.040044 | 0.0011123
2010 | 2010-01-12 | C | 21 | 0.00099541 | 6.6361e-05
2010 | 2010-01-12 | B | 70 | 0.012229 | 0.0002212
2010 | 2010-01-12 | B | 1 | 0.00063517 | 3.16e-06
2010 | 2010-01-12 | B | 2 | 0.0010491 | 6.3201e-06
2010 | 2010-01-12 | C | 190 | 0.024617 | 0.0006004
2010 | 2010-01-12 | B | 9 | 0.004067 | 2.844e-05
2010 | 2010-01-12 | C | 145 | 0.016037 | 0.0004582
2010 | 2010-01-13 | B | 2 | 0.0017317 | 6.3201e-06
2010 | 2010-01-13 | C | 18 | 0.0021615 | 5.688e-05
2010 | 2010-01-13 | B | 48 | 0.02973 | 0.00015168
2010 | 2010-01-13 | B | 24 | 0.033901 | 7.5841e-05
2010 | 2010-01-14 | C | 348 | 0.021994 | 0.0010997
2010 | 2010-01-12 | B | 9 | 0.0094706 | 2.844e-05
2010 | 2010-01-14 | B | 3 | 0.0025975 | 9.4801e-06
2010 | 2010-01-14 | B | 124 | 0.11755 | 0.00039184
2010 | 2010-01-14 | B | 1 | 0.00042028 | 3.16e-06
2010 | 2010-01-15 | B | 99 | 0.0078211 | 0.00031284
2010 | 2010-01-15 | B | 71 | 0.093783 | 0.00022436
2010 | 2010-01-15 | C | 255 | 0.076552 | 0.00080581
2010 | 2010-01-15 | C | 550 | 0.15161 | 0.001738
2010 | 2010-01-15 | C | 65 | 0.052377 | 0.0002054
2010 | 2010-01-16 | C | 349 | 0.1147 | 0.0011028
2010 | 2010-01-16 | C | 11 | 0.0057354 | 3.476e-05
2010 | 2010-01-16 | C | 22 | 0.003476 | 6.9521e-05
2010 | 2010-01-16 | C | 1033 | 0.36708 | 0.0032643
2010 | 2010-01-17 | C | 417 | 0.14212 | 0.0013177
2010 | 2010-01-17 | C | 80 | 0.020123 | 0.0002528
2010 | 2010-01-16 | C | 75 | 0.03081 | 0.000237
2010 | 2010-01-16 | C | 734 | 0.14613 | 0.0023195
2010 | 2010-01-16 | C | 583 | 0.092115 | 0.0018423
2010 | 2010-01-18 | C | 25 | 0.028731 | 7.9001e-05
2010 | 2010-01-18 | C | 8 | 0.0015421 | 2.528e-05
2010 | 2010-01-18 | C | 232 | 0.0043988 | 0.00073313
2010 | 2010-01-18 | C | 336 | 0.071284 | 0.0010618
2010 | 2010-01-19 | C | 1123 | 0.1171 | 0.0035487
2010 | 2010-01-19 | C | 11 | 0.001599 | 3.476e-05
2010 | 2010-01-18 | C | 18 | 0.02175 | 5.688e-05
2010 | 2010-01-19 | B | 3 | 0.0020098 | 9.4801e-06
2010 | 2010-01-19 | B | 1 | 0.00093221 | 3.16e-06
2010 | 2010-01-20 | C | 240 | 0.011376 | 0.00075841
2010 | 2010-01-20 | B | 100 | 0.027492 | 0.000316
2010 | 2010-01-19 | B | 6 | 0.0059914 | 1.896e-05
2010 | 2010-01-20 | C | 200 | 0.063226 | 0.00063201
2010 | 2010-01-20 | B | 71 | 0.082565 | 0.00022436
2010 | 2010-01-20 | C | 288 | 0.032763 | 0.00091009
2010 | 2010-01-20 | B | 28 | 0.027429 | 8.8481e-05
2010 | 2010-01-20 | C | 15 | 0.00085321 | 4.74e-05
2010 | 2010-01-20 | C | 38 | 0.010807 | 0.00012008
2010 | 2010-01-20 | B | 9 | 0.0081339 | 2.844e-05
2010 | 2010-01-20 | B | 25 | 0.023463 | 7.9001e-05
2010 | 2010-01-21 | B | 23 | 0.0041428 | 7.2681e-05
2010 | 2010-01-21 | C | 331 | 0.01569 | 0.001046
2010 | 2010-01-21 | C | 93 | 0.011168 | 0.00029388
2010 | 2010-01-29 | B | 8 | 0.0066487 | 2.528e-05
2010 | 2010-01-21 | B | 1 | 0.00094801 | 3.16e-06
2010 | 2010-01-21 | C | 82 | 0.054416 | 0.00025912
2010 | 2010-01-21 | B | 55 | 0.044351 | 0.0001738
2010 | 2010-01-21 | B | 22 | 0.01891 | 6.9521e-05
2010 | 2010-01-21 | B | 25 | 0.0237 | 7.9001e-05
2010 | 2010-01-19 | B | 32 | 0.035392 | 0.00010112
2010 | 2010-01-21 | C | 204 | 0.012248 | 0.00064465
2010 | 2010-01-22 | B | 74 | 0.011692 | 0.00023384
2010 | 2010-01-22 | C | 294 | 0.023226 | 0.00092905
2010 | 2010-01-22 | C | 437 | 0.16122 | 0.0013809
2010 | 2010-01-21 | B | 23 | 0.022894 | 7.2681e-05
2010 | 2010-01-22 | C | 837 | 0.076703 | 0.0026449
2010 | 2010-01-22 | C | 207 | 0.04121 | 0.00065413
2010 | 2010-01-23 | C | 109 | 0.0041333 | 0.00034444
2010 | 2010-01-23 | C | 6 | 0.0018012 | 1.896e-05
2010 | 2010-01-23 | C | 24 | 0.022601 | 7.5841e-05
2010 | 2010-01-23 | C | 11 | 0.0010776 | 3.476e-05
2010 | 2010-01-24 | C | 188 | 0.059257 | 0.00059408
2010 | 2010-01-25 | C | 97 | 0.0045978 | 0.00030652
2010 | 2010-01-24 | C | 588 | 0.16939 | 0.0018581
2010 | 2010-01-22 | B | 19 | 0.0095464 | 6.004e-05
2010 | 2010-01-25 | C | 139 | 0.042607 | 0.00043924
2010 | 2010-01-25 | C | 1 | 0.00019276 | 3.16e-06
2010 | 2010-01-25 | C | 52 | 0.013146 | 0.00016432
2010 | 2010-01-26 | B | 9 | 0.0018486 | 2.844e-05
2010 | 2010-01-26 | C | 1369 | 0.24673 | 0.0043261
2010 | 2010-01-26 | C | 9 | 0.0022183 | 2.844e-05
2010 | 2010-01-26 | C | 15 | 0.0042186 | 4.74e-05
2010 | 2010-01-26 | C | 4 | 0.00020224 | 1.264e-05
2010 | 2010-01-26 | C | 23 | 0.017371 | 7.2681e-05
2010 | 2010-01-26 | C | 9 | 0.0071385 | 2.844e-05
2010 | 2010-01-26 | C | 49 | 0.0072775 | 0.00015484
2010 | 2010-01-26 | C | 1 | 0.00041712 | 3.16e-06
2010 | 2010-01-26 | C | 117 | 0.0059156 | 0.00036972
2010 | 2010-01-26 | C | 22 | 0.0072997 | 6.9521e-05
2010 | 2010-01-26 | C | 159 | 0.028639 | 0.00050244
2010 | 2010-01-26 | C | 36 | 0 | 0.00011376
2010 | 2010-01-22 | B | 10 | 0.0067625 | 3.16e-05
2010 | 2010-01-26 | C | 414 | 0.0039248 | 0.0013083
2010 | 2010-01-26 | C | 20 | 0.00088481 | 6.3201e-05
2010 | 2010-01-26 | C | 16 | 0.0095559 | 5.056e-05
2010 | 2010-01-26 | C | 74 | 0.010757 | 0.00023384
2010 | 2010-01-26 | C | 232 | 0.087495 | 0.00073313
2010 | 2010-01-26 | C | 964 | 0.14622 | 0.0030463
2010 | 2010-01-26 | C | 176 | 0.065071 | 0.00055616
2010 | 2010-01-27 | C | 701 | 0.022152 | 0.0022152
2010 | 2010-01-27 | C | 812 | 0.1775 | 0.0025659
2010 | 2010-01-26 | B | 5 | 0.005688 | 1.58e-05
2010 | 2010-01-27 | C | 43 | 0.0082887 | 0.00013588
2010 | 2010-01-27 | C | 2 | 0.00099225 | 6.3201e-06
2010 | 2010-01-27 | C | 321 | 0.098447 | 0.0010144
2010 | 2010-01-27 | B | 33 | 0.040878 | 0.00010428
2010 | 2010-01-26 | B | 8 | 0.0092273 | 2.528e-05
2010 | 2010-01-26 | B | 45 | 0.019055 | 0.0001422
2010 | 2010-01-27 | C | 310 | 0.24248 | 0.00097961
2010 | 2010-01-27 | B | 25 | 0.0237 | 7.9001e-05
2010 | 2010-01-28 | C | 1 | 0.00050244 | 3.16e-06
2010 | 2010-02-05 | B | 5 | 0.0032706 | 1.58e-05
2010 | 2010-01-28 | B | 1 | 0.00022436 | 3.16e-06
2010 | 2010-01-28 | C | 107 | 0.0060862 | 0.00033812
2010 | 2010-01-29 | C | 265 | 0.012561 | 0.00083741
2010 | 2010-01-28 | B | 23 | 0.0032706 | 7.2681e-05
2010 | 2010-01-28 | C | 1129 | 0.29922 | 0.0035677
2010 | 2010-01-28 | B | 5 | 0.0057828 | 1.58e-05
2010 | 2010-01-29 | B | 8 | 0.0031095 | 2.528e-05
2010 | 2010-01-29 | B | 40 | 0.012261 | 0.0001264
2010 | 2010-01-29 | B | 152 | 0.06004 | 0.00048032
2010 | 2010-01-29 | B | 7 | 0.0029862 | 2.212e-05
2010 | 2010-01-29 | B | 63 | 0.025881 | 0.00019908
2010 | 2010-01-28 | B | 3 | 0.0051382 | 9.4801e-06
2010 | 2010-01-29 | C | 69 | 0.026165 | 0.00021804
2010 | 2010-01-29 | B | 8 | 0.0098087 | 2.528e-05
2010 | 2010-01-28 | B | 16 | 0.0063706 | 5.056e-05
2010 | 2010-01-29 | C | 333 | 0.15176 | 0.0010523
2010 | 2010-01-29 | C | 385 | 0.015816 | 0.0012166
2010 | 2010-01-30 | C | 984 | 0.046642 | 0.0031095
2010 | 2010-01-29 | C | 460 | 0.08412 | 0.0014536
2010 | 2010-01-30 | C | 1264 | 0.10638 | 0.0039943
2010 | 2010-01-30 | B | 1 | 0.00037604 | 3.16e-06
2010 | 2010-01-30 | C | 304 | 0.05956 | 0.00096065
2010 | 2010-01-30 | C | 637 | 0.085488 | 0.0020129
2010 | 2010-01-30 | C | 901 | 0.059791 | 0.0028472
2010 | 2010-01-31 | C | 309 | 0.094854 | 0.00097645
2010 | 2010-01-31 | C | 587 | 0.15396 | 0.0018549
2010 | 2010-01-31 | C | 289 | 0.013699 | 0.00091325
2010 | 2010-01-31 | C | 984 | 0.077737 | 0.0031095
2010 | 2010-01-31 | C | 3852 | 0.1339 | 0.012172
2010 | 2010-01-31 | C | 8712 | 0.46576 | 0.02753
2010 | 2010-01-31 | C | 587 | 0.14015 | 0.0018549
2010 | 2010-01-31 | C | 897 | 0.18252 | 0.0028345
2010 | 2010-01-31 | C | 277 | 0.036764 | 0.00087533
2010 | 2010-01-31 | C | 243 | 0.011518 | 0.00076789
2010 | 2010-01-31 | C | 29 | 0.015396 | 9.1641e-05
2010 | 2010-01-31 | C | 200 | 0.01896 | 0.00063201
2010 | 2010-01-31 | C | 364 | 0.11092 | 0.0011502
2010 | 2010-01-31 | C | 45 | 0.048491 | 0.0001422
2010 | 2010-02-01 | C | 266 | 0.10478 | 0.00084057
2010 | 2010-02-01 | C | 1 | 0.00017064 | 3.16e-06
2010 | 2010-02-01 | C | 61 | 0.004819 | 0.00019276
2010 | 2010-01-29 | C | 1264 | 0.067903 | 0.0039943
2010 | 2010-02-01 | C | 748 | 0.042547 | 0.0023637
2010 | 2010-02-01 | C | 39 | 0.029208 | 0.00012324
2010 | 2010-02-01 | C | 245 | 0.041248 | 0.00077421
2010 | 2010-02-01 | B | 53 | 0.011724 | 0.00016748
2010 | 2010-02-02 | C | 344 | 0.13588 | 0.001087
2010 | 2010-02-02 | C | 84 | 0.035835 | 0.00026544
2010 | 2010-02-02 | C | 1 | 0.0013651 | 3.16e-06
2010 | 2010-02-02 | B | 14 | 0.015705 | 4.424e-05
2010 | 2010-02-02 | B | 57 | 0.052055 | 0.00018012
2010 | 2010-02-02 | C | 1458 | 0.34974 | 0.0046073
2010 | 2010-02-03 | B | 5 | 0.0057512 | 1.58e-05
2010 | 2010-02-03 | B | 13 | 0.014789 | 4.108e-05
2010 | 2010-02-03 | C | 10 | 0.000474 | 3.16e-05
2010 | 2010-02-03 | C | 58 | 0.013013 | 0.00018328
2010 | 2010-02-03 | C | 701 | 0.21157 | 0.0022152
2010 | 2010-02-04 | B | 17 | 0.01386 | 5.372e-05
2010 | 2010-02-04 | B | 54 | 0.068768 | 0.00017064
2010 | 2010-02-04 | B | 5 | 0.005925 | 1.58e-05
2010 | 2010-02-04 | B | 15 | 0.019008 | 4.74e-05
2010 | 2010-02-04 | C | 5 | 0.0006162 | 1.58e-05
2010 | 2010-02-04 | B | 69 | 0.063668 | 0.00021804
2010 | 2010-02-04 | C | 672 | 0.13591 | 0.0021235
2010 | 2010-02-05 | C | 618 | 0.10041 | 0.0019529
2010 | 2010-02-05 | B | 34 | 0.029116 | 0.00010744
2010 | 2010-02-05 | B | 27 | 0.027985 | 8.5321e-05
2010 | 2010-02-05 | B | 57 | 0.055838 | 0.00018012
2010 | 2010-02-05 | C | 270 | 0.065988 | 0.00085321
2010 | 2010-02-06 | C | 67 | 0.003811 | 0.00021172
2010 | 2010-02-05 | B | 27 | 0.0020477 | 8.5321e-05
2010 | 2010-02-05 | B | 2 | 0.0015358 | 6.3201e-06
2010 | 2010-02-05 | B | 27 | 0.010068 | 8.5321e-05
2010 | 2010-02-06 | C | 37 | 0.038818 | 0.00011692
2010 | 2010-02-07 | C | 1299 | 0.065678 | 0.0041049
2010 | 2010-02-06 | C | 27 | 0.0076789 | 8.5321e-05
2010 | 2010-02-07 | C | 1 | 0.00082793 | 3.16e-06
2010 | 2010-02-06 | C | 1 | 0.0014947 | 3.16e-06
2010 | 2010-02-07 | C | 2 | 0.0016559 | 6.3201e-06
2010 | 2010-02-07 | C | 572 | 0.11018 | 0.0018075
2010 | 2010-02-07 | C | 367 | 0.38387 | 0.0011597
2010 | 2010-02-08 | C | 754 | 0.045271 | 0.0023827
2010 | 2010-02-05 | C | 2977 | 0.1317 | 0.0094074
2010 | 2010-02-08 | C | 848 | 0.016078 | 0.0026797
2010 | 2010-02-08 | C | 666 | 0.29121 | 0.0021046
2010 | 2010-02-09 | B | 57 | 0.049353 | 0.00018012
2010 | 2010-02-09 | B | 1 | 0.00099541 | 3.16e-06
2010 | 2010-02-09 | B | 14 | 0.010839 | 4.424e-05
2010 | 2010-02-09 | B | 11 | 0.011818 | 3.476e-05
2010 | 2010-02-09 | B | 2 | 0.00025912 | 6.3201e-06
2010 | 2010-02-09 | B | 18 | 0.013367 | 5.688e-05
2010 | 2010-02-09 | C | 29 | 0.0047653 | 9.1641e-05
2010 | 2010-02-09 | C | 195 | 0.027113 | 0.0006162
2010 | 2010-02-09 | C | 224 | 0.031423 | 0.00070785
2010 | 2010-02-10 | B | 3 | 0.0023511 | 9.4801e-06
2010 | 2010-02-10 | B | 1 | 0.00066045 | 3.16e-06
2010 | 2010-02-10 | C | 19 | 0.0085858 | 6.004e-05
2010 | 2010-02-10 | C | 269 | 0.06279 | 0.00085005
2010 | 2010-02-10 | C | 586 | 0.32462 | 0.0018518
2010 | 2010-02-10 | B | 2 | 0.0013904 | 6.3201e-06
2010 | 2010-02-10 | C | 316 | 0.037984 | 0.00099857
2010 | 2010-02-10 | C | 1 | 0.0001106 | 3.16e-06
2010 | 2010-02-10 | C | 66 | 0.018353 | 0.00020856
2010 | 2010-02-10 | C | 201 | 0.074738 | 0.00063517
2010 | 2010-02-10 | C | 31 | 0.0060736 | 9.7961e-05
2010 | 2010-02-11 | C | 672 | 0.044594 | 0.0021235
2010 | 2010-02-11 | C | 1412 | 0.30009 | 0.004462
2010 | 2010-02-11 | B | 24 | 0.015244 | 7.5841e-05
2010 | 2010-02-11 | B | 5 | 0.0039342 | 1.58e-05
2010 | 2010-02-11 | B | 176 | 0.20022 | 0.00055616
2010 | 2010-02-11 | C | 99 | 0.013983 | 0.00031284
2010 | 2010-02-12 | B | 36 | 0.0098972 | 0.00011376
2010 | 2010-02-11 | B | 78 | 0.014296 | 0.00024648
2010 | 2010-01-26 | C | 1 | 0.00023384 | 3.16e-06
2010 | 2010-02-11 | B | 34 | 0.019339 | 0.00010744
2010 | 2010-02-11 | B | 1 | 0.0011376 | 3.16e-06
2010 | 2010-02-12 | B | 32 | 0.0091009 | 0.00010112
2010 | 2010-02-12 | B | 226 | 0.11641 | 0.00071417
2010 | 2010-02-12 | C | 69 | 0.014609 | 0.00021804
2010 | 2010-02-12 | C | 124 | 0.036833 | 0.00039184
2010 | 2010-02-12 | C | 123 | 0.019045 | 0.00038868
2010 | 2010-02-13 | C | 839 | 0.13574 | 0.0026513
2010 | 2010-02-13 | C | 473 | 0.0014947 | 0.0014947
2010 | 2010-02-13 | C | 140 | 0.039993 | 0.0004424
2010 | 2010-02-13 | C | 892 | 0.12528 | 0.0028187
2010 | 2010-02-13 | C | 176 | 0.02614 | 0.00055616
2010 | 2010-02-13 | C | 226 | 0.013569 | 0.00071417
2010 | 2010-02-13 | B | 2 | 0.0017127 | 6.3201e-06
2010 | 2010-02-13 | C | 214 | 0.026374 | 0.00067625
2010 | 2010-02-13 | C | 901 | 0.17045 | 0.0028472
2010 | 2010-02-13 | C | 330 | 0.10325 | 0.0010428
2010 | 2010-02-14 | B | 5 | 0.0053404 | 1.58e-05
2010 | 2010-02-12 | C | 35 | 0.01422 | 0.0001106
2010 | 2010-02-12 | C | 78 | 0.024376 | 0.00024648
2010 | 2010-02-13 | C | 100 | 0.053088 | 0.000316
2010 | 2010-02-14 | C | 75 | 0.019671 | 0.000237
2010 | 2010-02-14 | C | 71 | 0.012564 | 0.00022436
2010 | 2010-02-13 | C | 964 | 0.17059 | 0.0030463
2010 | 2010-02-15 | C | 572 | 0.25134 | 0.0018075
2010 | 2010-02-15 | C | 76 | 0.025217 | 0.00024016
2010 | 2010-02-15 | C | 53 | 0.038353 | 0.00016748
2010 | 2010-02-15 | C | 2 | 0.00030968 | 6.3201e-06
2010 | 2010-02-15 | C | 2268 | 0.17917 | 0.0071669
2010 | 2010-02-15 | C | 3 | 0.00051192 | 9.4801e-06
2010 | 2010-02-15 | B | 6 | 0.0053657 | 1.896e-05
2010 | 2010-02-16 | B | 2 | 0.00036656 | 6.3201e-06
2010 | 2010-02-16 | B | 41 | 0.036148 | 0.00012956
2010 | 2010-02-16 | B | 40 | 0.027555 | 0.0001264
2010 | 2010-02-16 | B | 5 | 0.004503 | 1.58e-05
2010 | 2010-02-16 | C | 411 | 0.058464 | 0.0012988
2010 | 2010-02-16 | B | 77 | 0.06667 | 0.00024332
2010 | 2010-02-16 | B | 5 | 0.0015958 | 1.58e-05
2010 | 2010-02-16 | B | 20 | 0.012261 | 6.3201e-05
2010 | 2010-02-17 | C | 1168 | 0.14675 | 0.0036909
2010 | 2010-02-17 | C | 257 | 0.012182 | 0.00081213
2010 | 2010-02-17 | C | 59 | 0.015661 | 0.00018644
2010 | 2010-02-17 | B | 2 | 0.0012956 | 6.3201e-06
2010 | 2010-02-17 | B | 1 | 0.00015484 | 3.16e-06
2010 | 2010-02-18 | C | 239 | 0.11617 | 0.00075525
2010 | 2010-02-17 | C | 557 | 0.026402 | 0.0017601
2010 | 2010-02-18 | B | 31 | 0.028507 | 9.7961e-05
2010 | 2010-02-18 | B | 1 | 0.00054668 | 3.16e-06
2010 | 2010-02-19 | C | 1396 | 0.24159 | 0.0044114
2010 | 2010-02-19 | B | 1 | 6.3201e-05 | 3.16e-06
2010 | 2010-02-19 | C | 8 | 0.0023005 | 2.528e-05
2010 | 2010-02-19 | B | 54 | 0.020477 | 0.00017064
2010 | 2010-02-19 | B | 67 | 0.020749 | 0.00021172
2010 | 2010-02-19 | B | 11 | 0.013174 | 3.476e-05
2010 | 2010-02-19 | B | 1 | 0.00066677 | 3.16e-06
2010 | 2010-02-19 | B | 3 | 0.0004266 | 9.4801e-06
2010 | 2010-02-19 | B | 33 | 0.013139 | 0.00010428
2010 | 2010-02-19 | B | 1 | 0.0013272 | 3.16e-06
2010 | 2010-02-19 | C | 2 | 0.00073945 | 6.3201e-06
2010 | 2010-02-20 | B | 1 | 0.00059092 | 3.16e-06
2010 | 2010-02-20 | B | 1 | 0.0003634 | 3.16e-06
2010 | 2010-02-20 | B | 1 | 0.00063201 | 3.16e-06
2010 | 2010-02-19 | C | 52 | 0.0031221 | 0.00016432
2010 | 2010-02-21 | C | 184 | 0.063656 | 0.00058144
2010 | 2010-02-21 | B | 2 | 0.0022057 | 6.3201e-06
2010 | 2010-02-21 | B | 54 | 0.050169 | 0.00017064
2010 | 2010-02-21 | C | 139 | 0.11213 | 0.00043924
2010 | 2010-02-22 | B | 1 | 0.00036972 | 3.16e-06
2010 | 2010-02-22 | B | 4 | 0.0034255 | 1.264e-05
2010 | 2010-02-22 | B | 1 | 0.0012577 | 3.16e-06
2010 | 2010-02-22 | B | 3 | 0.0042092 | 9.4801e-06
2010 | 2010-02-22 | C | 230 | 0.044335 | 0.00072681
2010 | 2010-02-22 | C | 26 | 0.018075 | 8.2161e-05
2010 | 2010-02-23 | C | 2779 | 0.031686 | 0.0087817
2010 | 2010-02-23 | C | 151 | 0.0047716 | 0.00047716
2010 | 2010-02-23 | B | 52 | 0.015446 | 0.00016432
2010 | 2010-02-23 | B | 62 | 0.039968 | 0.00019592
2010 | 2010-02-23 | B | 55 | 0.049707 | 0.0001738
2010 | 2010-02-23 | B | 29 | 0.038489 | 9.1641e-05
2010 | 2010-02-23 | B | 57 | 0.065024 | 0.00018012
2010 | 2010-02-23 | B | 1 | 0.0011376 | 3.16e-06
2010 | 2010-02-24 | C | 327 | 0.077345 | 0.0010333
2010 | 2010-02-23 | B | 43 | 0.016985 | 0.00013588
2010 | 2010-02-23 | B | 26 | 0.006655 | 8.2161e-05
2010 | 2010-02-23 | B | 1 | 0.000316 | 3.16e-06
2010 | 2010-02-24 | C | 67 | 0.021807 | 0.00021172
2010 | 2010-02-18 | B | 10 | 0.0040764 | 3.16e-05
2010 | 2010-02-23 | B | 98 | 0.096058 | 0.00030968
2010 | 2010-02-23 | B | 1 | 0.00063517 | 3.16e-06
2010 | 2010-02-24 | C | 642 | 0.0040575 | 0.0020287
2010 | 2010-02-24 | C | 750 | 0.00237 | 0.00237
2010 | 2010-02-24 | B | 42 | 0.03902 | 0.00013272
2010 | 2010-02-25 | C | 1116 | 0.17505 | 0.0035266
2010 | 2010-02-25 | C | 20 | 0.0083425 | 6.3201e-05
2010 | 2010-02-25 | C | 140 | 0.035392 | 0.0004424
2010 | 2010-02-25 | C | 76 | 0.025937 | 0.00024016
2010 | 2010-02-25 | B | 7 | 0.0084499 | 2.212e-05
2010 | 2010-02-25 | B | 32 | 0.013146 | 0.00010112
2010 | 2010-02-25 | C | 173 | 0.047258 | 0.00054668
2010 | 2010-02-25 | B | 138 | 0.14042 | 0.00043608
2010 | 2010-02-25 | B | 268 | 0.10847 | 0.00084689
2010 | 2010-02-25 | C | 694 | 0.14693 | 0.0021931
2010 | 2010-02-25 | C | 97 | 0.0052109 | 0.00030652
2010 | 2010-02-25 | C | 305 | 0.051082 | 0.00096381
2010 | 2010-02-25 | C | 1002 | 0.098157 | 0.0031663
2010 | 2010-02-25 | C | 9 | 0.00019908 | 2.844e-05
2010 | 2010-02-25 | C | 470 | 0.017823 | 0.0014852
2010 | 2010-02-26 | B | 210 | 0.0099541 | 0.00066361
2010 | 2010-02-26 | C | 159 | 0.033161 | 0.00050244
2010 | 2010-02-26 | B | 8 | 0.006042 | 2.528e-05
2010 | 2010-02-26 | B | 3 | 0.002844 | 9.4801e-06
2010 | 2010-02-26 | C | 1 | 0.0002686 | 3.16e-06
2010 | 2010-02-25 | B | 38 | 0.04431 | 0.00012008
2010 | 2010-02-26 | C | 218 | 0.030311 | 0.00068889
2010 | 2010-02-27 | C | 31 | 0.0053878 | 9.7961e-05
2010 | 2010-02-27 | C | 46 | 0.01817 | 0.00014536
2010 | 2010-02-27 | B | 1 | 0.0013177 | 3.16e-06
2010 | 2010-02-28 | C | 1 | 0.000237 | 3.16e-06
2010 | 2010-02-28 | B | 30 | 0.029388 | 9.4801e-05
2010 | 2010-02-21 | B | 1 | 0.0004266 | 3.16e-06
2010 | 2010-02-28 | C | 3887 | 0.51589 | 0.012283
2010 | 2010-02-26 | B | 74 | 0.079506 | 0.00023384
2010 | 2010-03-01 | B | 7 | 0.0071227 | 2.212e-05
2010 | 2010-03-01 | C | 1 | 0.0011566 | 3.16e-06
2010 | 2010-03-01 | B | 14 | 0.01429 | 4.424e-05
2010 | 2010-02-01 | B | 46 | 0.060325 | 0.00014536
2010 | 2010-03-01 | C | 233 | 0.061213 | 0.00073629
2010 | 2010-03-01 | C | 857 | 0.078536 | 0.0027081
2010 | 2010-03-02 | C | 104 | 0.0059156 | 0.00032864
2010 | 2010-03-01 | B | 26 | 0.036151 | 8.2161e-05
2010 | 2010-03-01 | B | 3 | 0.0045504 | 9.4801e-06
2010 | 2010-03-02 | C | 7 | 0.00053088 | 2.212e-05
2010 | 2010-03-02 | B | 15 | 0.0071101 | 4.74e-05
2010 | 2010-03-02 | B | 29 | 0.025659 | 9.1641e-05
2010 | 2010-03-02 | B | 16 | 0.015927 | 5.056e-05
2010 | 2010-03-02 | B | 40 | 0.039184 | 0.0001264
2010 | 2010-03-02 | C | 228 | 0.1468 | 0.00072049
2010 | 2010-03-02 | B | 2 | 0.0010302 | 6.3201e-06
2010 | 2010-03-03 | C | 15 | 0.0021804 | 4.74e-05
2010 | 2010-03-03 | C | 278 | 0.0035139 | 0.00087849
2010 | 2010-03-03 | C | 686 | 0.0065033 | 0.0021678
2010 | 2010-03-03 | B | 3 | 0.0044936 | 9.4801e-06
2010 | 2010-03-03 | B | 2 | 0.0013967 | 6.3201e-06
2010 | 2010-03-03 | C | 13 | 0.00078053 | 4.108e-05
2010 | 2010-03-04 | B | 112 | 0.037516 | 0.00035392
2010 | 2010-03-04 | C | 2 | 0.00011376 | 6.3201e-06
2010 | 2010-03-04 | B | 45 | 0.036261 | 0.0001422
2010 | 2010-03-04 | B | 4 | 0.0014031 | 1.264e-05
2010 | 2010-03-04 | B | 2 | 0.00061936 | 6.3201e-06
2010 | 2010-03-04 | B | 3 | 0.0030052 | 9.4801e-06
2010 | 2010-03-03 | C | 63 | 0.04559 | 0.00019908
2010 | 2010-03-04 | C | 113 | 0.047849 | 0.00035708
2010 | 2010-03-04 | C | 112 | 0.022651 | 0.00035392
2010 | 2010-03-05 | C | 44 | 0.0037541 | 0.00013904
2010 | 2010-03-04 | B | 74 | 0.064774 | 0.00023384
2010 | 2010-03-05 | B | 1 | 0.0011471 | 3.16e-06
2010 | 2010-03-05 | B | 43 | 0.033834 | 0.00013588
2010 | 2010-03-05 | C | 17 | 0.0051034 | 5.372e-05
2010 | 2010-03-05 | C | 51 | 0.032555 | 0.00016116
2010 | 2010-03-06 | C | 123 | 0.042755 | 0.00038868
2010 | 2010-03-06 | C | 527 | 0.080072 | 0.0016653
2010 | 2010-03-06 | C | 630 | 0.11946 | 0.0019908
2010 | 2010-03-06 | B | 54 | 0.018771 | 0.00017064
2010 | 2010-03-06 | C | 8372 | 0.68785 | 0.026456
2010 | 2010-03-04 | B | 3 | 0.0051666 | 9.4801e-06
2010 | 2010-03-08 | C | 6 | 0.0011566 | 1.896e-05
2010 | 2010-03-08 | C | 107 | 0.09675 | 0.00033812
2010 | 2010-03-08 | C | 187 | 0.048456 | 0.00059092
2010 | 2010-03-08 | B | 470 | 0.19456 | 0.0014852
2010 | 2010-03-08 | B | 15 | 0.020098 | 4.74e-05
2010 | 2010-03-08 | B | 2 | 0.0010175 | 6.3201e-06
2010 | 2010-03-08 | B | 54 | 0.027473 | 0.00017064
2010 | 2010-03-08 | C | 170 | 0.066613 | 0.0005372
2010 | 2010-03-08 | C | 76 | 0.073249 | 0.00024016
2010 | 2010-03-08 | C | 32 | 0.033774 | 0.00010112
2010 | 2010-03-09 | C | 220 | 0.039627 | 0.00069521
2010 | 2010-03-05 | B | 3 | 0.0038868 | 9.4801e-06
2010 | 2010-03-09 | B | 21 | 0.025881 | 6.6361e-05
2010 | 2010-03-09 | B | 21 | 0.0084278 | 6.6361e-05
2010 | 2010-03-09 | B | 2 | 0.0018202 | 6.3201e-06
2010 | 2010-03-09 | C | 1 | 0.0010428 | 3.16e-06
2010 | 2010-03-09 | C | 70 | 0.0077421 | 0.0002212
2010 | 2010-03-10 | C | 35 | 0.0039816 | 0.0001106
2010 | 2010-03-10 | B | 36 | 0.020477 | 0.00011376
2010 | 2010-03-10 | B | 60 | 0.020856 | 0.0001896
2010 | 2010-03-08 | B | 11 | 0.013626 | 3.476e-05
2010 | 2010-03-10 | C | 53 | 0.016442 | 0.00016748
2010 | 2010-03-11 | B | 21 | 0.012011 | 6.6361e-05
2010 | 2010-03-11 | B | 83 | 0.019409 | 0.00026228
2010 | 2010-03-11 | B | 74 | 0.011926 | 0.00023384
2010 | 2010-03-11 | B | 11 | 0.012583 | 3.476e-05
2010 | 2010-03-11 | B | 64 | 0.08393 | 0.00020224
2010 | 2010-03-11 | B | 21 | 0.025217 | 6.6361e-05
2010 | 2010-03-11 | B | 33 | 0.018979 | 0.00010428
2010 | 2010-03-11 | B | 2 | 0.0015168 | 6.3201e-06
2010 | 2010-03-11 | B | 18 | 0.0072807 | 5.688e-05
2010 | 2010-03-12 | C | 432 | 0.086003 | 0.0013651
2010 | 2010-03-12 | C | 1174 | 0.055648 | 0.0037099
2010 | 2010-03-11 | C | 776 | 0.1493 | 0.0024522
2010 | 2010-03-11 | C | 416 | 0.030235 | 0.0013146
2010 | 2010-03-11 | C | 103 | 0.12422 | 0.00032548
2010 | 2010-03-12 | C | 370 | 0.14836 | 0.0011692
2010 | 2010-03-12 | C | 1694 | 0.86663 | 0.0053531
2010 | 2010-03-12 | B | 11 | 0.0041712 | 3.476e-05
2010 | 2010-03-12 | B | 25 | 0.014457 | 7.9001e-05
2010 | 2010-03-12 | C | 416 | 0.070987 | 0.0013146
2010 | 2010-03-12 | C | 1 | 0.00033496 | 3.16e-06
2010 | 2010-03-12 | C | 355 | 0.068781 | 0.0011218
2010 | 2010-03-12 | C | 136 | 0.012893 | 0.00042976
2010 | 2010-03-12 | C | 299 | 0.050115 | 0.00094485
2010 | 2010-03-12 | C | 18 | 0.0034128 | 5.688e-05
2010 | 2010-03-12 | C | 256 | 0.0072807 | 0.00080897
2010 | 2010-03-12 | C | 69 | 0.0032706 | 0.00021804
2010 | 2010-03-12 | C | 136 | 0.033092 | 0.00042976
2010 | 2010-03-12 | C | 23 | 0.024711 | 7.2681e-05
2010 | 2010-03-13 | C | 35 | 0.010886 | 0.0001106
2010 | 2010-03-13 | C | 54 | 0.0030715 | 0.00017064
2010 | 2010-03-13 | C | 43 | 0.0048917 | 0.00013588
2010 | 2010-03-13 | C | 110 | 0.033452 | 0.0003476
2010 | 2010-03-13 | C | 416 | 0.022348 | 0.0013146
2010 | 2010-03-13 | C | 75 | 0.003792 | 0.000237
2010 | 2010-03-13 | C | 26 | 0.0082161 | 8.2161e-05
2010 | 2010-03-13 | C | 28 | 0.0017696 | 8.8481e-05
2010 | 2010-03-14 | C | 278 | 0.013177 | 0.00087849
2010 | 2010-03-14 | C | 22 | 0.0031284 | 6.9521e-05
2010 | 2010-03-14 | C | 5 | 0.0013588 | 1.58e-05
2010 | 2010-03-14 | C | 811 | 0.19643 | 0.0025628
2010 | 2010-03-14 | C | 12 | 0.00087217 | 3.792e-05
2010 | 2010-03-14 | C | 139 | 0.066458 | 0.00043924
2010 | 2010-03-12 | B | 43 | 0.015355 | 0.00013588
2010 | 2010-03-15 | B | 70 | 0.077863 | 0.0002212
2010 | 2010-03-15 | C | 106 | 0.00066993 | 0.00033496
2010 | 2010-03-15 | B | 83 | 0.039959 | 0.00026228
2010 | 2010-03-15 | C | 53 | 0.027969 | 0.00016748
2010 | 2010-03-15 | B | 6 | 0.0072617 | 1.896e-05
2010 | 2010-03-15 | C | 416 | 0.067043 | 0.0013146
2010 | 2010-03-15 | C | 59 | 0.0078305 | 0.00018644
2010 | 2010-03-15 | C | 190 | 0.11562 | 0.0006004
2010 | 2010-03-15 | C | 572 | 0.17659 | 0.0018075
2010 | 2010-03-16 | B | 1 | 0.0001896 | 3.16e-06
2010 | 2010-03-16 | B | 23 | 0.021077 | 7.2681e-05
2010 | 2010-03-16 | B | 3 | 0.0033085 | 9.4801e-06
2010 | 2010-03-16 | B | 33 | 0.04067 | 0.00010428
2010 | 2010-03-16 | C | 485 | 0.026054 | 0.0015326
2010 | 2010-03-17 | B | 11 | 0.013 | 3.476e-05
2010 | 2010-03-17 | C | 1332 | 0.19444 | 0.0042092
2010 | 2010-03-17 | C | 29 | 0.009439 | 9.1641e-05
2010 | 2010-03-17 | C | 5 | 0.0002686 | 1.58e-05
2010 | 2010-03-17 | C | 90 | 0.014789 | 0.0002844
2010 | 2010-03-17 | C | 121 | 0.025236 | 0.00038236
2010 | 2010-03-17 | C | 70 | 0.040259 | 0.0002212
2010 | 2010-03-17 | C | 572 | 0.22413 | 0.0018075
2010 | 2010-03-17 | B | 67 | 0.032871 | 0.00021172
2010 | 2010-03-17 | C | 4134 | 3.71 | 0.013064
2010 | 2010-03-17 | B | 188 | 0.04515 | 0.00059408
2010 | 2010-02-17 | B | 245 | 0.091356 | 0.00077421
2010 | 2010-03-17 | C | 8374 | 7.5417 | 0.026462
2010 | 2010-03-18 | B | 12 | 0.0054605 | 3.792e-05
2010 | 2010-03-17 | C | 2309 | 2.0868 | 0.0072965
2010 | 2010-03-18 | B | 1 | 0.00053404 | 3.16e-06
2010 | 2010-03-18 | B | 8 | 0.0061178 | 2.528e-05
2010 | 2010-03-18 | B | 21 | 0.014268 | 6.6361e-05
2010 | 2010-03-18 | B | 57 | 0.032422 | 0.00018012
2010 | 2010-03-18 | B | 198 | 0.22963 | 0.00062569
2010 | 2010-03-18 | C | 221 | 0.055784 | 0.00069837
2010 | 2010-03-18 | B | 33 | 0.053288 | 0.00010428
2010 | 2010-03-18 | C | 205 | 0.25783 | 0.00064781
2010 | 2010-03-18 | C | 101 | 0.014362 | 0.00031916
2010 | 2010-03-18 | C | 497 | 0.10505 | 0.0015705
2010 | 2010-03-18 | C | 43 | 0.027448 | 0.00013588
2010 | 2010-03-18 | C | 25 | 0.031442 | 7.9001e-05
2010 | 2010-03-19 | C | 1125 | 0.34484 | 0.003555
2010 | 2010-03-19 | C | 297 | 0.06723 | 0.00093853
2010 | 2010-03-19 | C | 481 | 0.18211 | 0.00152
2010 | 2010-03-19 | C | 31 | 0.0073471 | 9.7961e-05
2010 | 2010-03-19 | C | 20 | 0.013525 | 6.3201e-05
2010 | 2010-03-19 | C | 334 | 0.091824 | 0.0010554
2010 | 2010-03-19 | C | 51 | 0.0083804 | 0.00016116
2010 | 2010-03-19 | C | 15 | 0.017017 | 4.74e-05
2010 | 2010-03-19 | C | 1460 | 0.30911 | 0.0046136
2010 | 2010-03-19 | C | 63 | 0.013045 | 0.00019908
2010 | 2010-03-20 | C | 173 | 0.073777 | 0.00054668
2010 | 2010-03-20 | C | 30 | 0.0032232 | 9.4801e-05
2010 | 2010-03-20 | C | 259 | 0.062328 | 0.00081845
2010 | 2010-03-21 | C | 35 | 0.0064149 | 0.0001106
2010 | 2010-03-21 | C | 30 | 0.0040764 | 9.4801e-05
2010 | 2010-03-22 | C | 38 | 0.013089 | 0.00012008
2010 | 2010-03-22 | B | 80 | 0.060672 | 0.0002528
2010 | 2010-03-22 | B | 105 | 0.039485 | 0.0003318
2010 | 2010-03-22 | C | 1057 | 0.18173 | 0.0033401
2010 | 2010-03-22 | C | 128 | 0.036808 | 0.00040448
2010 | 2010-03-22 | C | 165 | 0.046405 | 0.0005214
2010 | 2010-03-23 | C | 6 | 0.0011566 | 1.896e-05
2010 | 2010-03-23 | B | 10 | 0.0085005 | 3.16e-05
2010 | 2010-03-23 | B | 20 | 0.024711 | 6.3201e-05
2010 | 2010-03-23 | C | 1256 | 0.23176 | 0.003969
2010 | 2010-03-23 | C | 14 | 0.0059282 | 4.424e-05
2010 | 2010-03-23 | B | 11 | 0.01081 | 3.476e-05
2010 | 2010-03-23 | C | 60 | 0.015547 | 0.0001896
2010 | 2010-03-23 | C | 237 | 0.052046 | 0.00074893
2010 | 2010-03-23 | C | 365 | 0.020761 | 0.0011534
2010 | 2010-03-23 | C | 1156 | 0.16729 | 0.003653
2010 | 2010-03-23 | C | 176 | 0.042268 | 0.00055616
2010 | 2010-03-23 | C | 126 | 0.0051761 | 0.00039816
2010 | 2010-03-24 | B | 233 | 0.1259 | 0.00073629
2010 | 2010-03-24 | C | 68 | 0.013108 | 0.00021488
2010 | 2010-03-24 | C | 38 | 0.0028819 | 0.00012008
2010 | 2010-03-23 | B | 33 | 0.031284 | 0.00010428
2010 | 2010-03-24 | B | 6 | 0.0052899 | 1.896e-05
2010 | 2010-03-24 | B | 18 | 0.02116 | 5.688e-05
2010 | 2010-03-24 | B | 11 | 0.012722 | 3.476e-05
2010 | 2010-03-24 | C | 164 | 0.084028 | 0.00051824
2010 | 2010-03-24 | B | 1 | 0.0010175 | 3.16e-06
2010 | 2010-03-24 | C | 3 | 0.00044556 | 9.4801e-06
2010 | 2010-03-24 | C | 286 | 0.08022 | 0.00090377
2010 | 2010-03-24 | B | 182 | 0.23753 | 0.00057512
2010 | 2010-03-24 | C | 64 | 0.0091009 | 0.00020224
2010 | 2010-03-24 | C | 636 | 0.15297 | 0.0020098
2010 | 2010-03-24 | C | 255 | 0.022563 | 0.00080581
2010 | 2010-03-24 | C | 267 | 0.10522 | 0.00084373
2010 | 2010-03-24 | C | 262 | 0.038085 | 0.00082793
2010 | 2010-03-25 | C | 127 | 0.0068225 | 0.00040132
2010 | 2010-03-25 | C | 144 | 0.0077357 | 0.00045504
2010 | 2010-03-25 | C | 24 | 0.0053088 | 7.5841e-05
2010 | 2010-03-25 | B | 19 | 0.010567 | 6.004e-05
2010 | 2010-02-26 | B | 20 | 0.019592 | 6.3201e-05
2010 | 2010-03-25 | C | 436 | 0.58861 | 0.0013778
2010 | 2010-03-25 | C | 207 | 0.037342 | 0.00065413
2010 | 2010-03-25 | B | 6 | 0.0031853 | 1.896e-05
2010 | 2010-03-25 | B | 11 | 0.011992 | 3.476e-05
2010 | 2010-03-25 | C | 169 | 0.03428 | 0.00053404
2010 | 2010-03-26 | B | 32 | 0.021033 | 0.00010112
2010 | 2010-03-26 | C | 6 | 0.0013083 | 1.896e-05
2010 | 2010-03-26 | B | 25 | 0.014773 | 7.9001e-05
2010 | 2010-03-26 | C | 26 | 0.0024648 | 8.2161e-05
2010 | 2010-03-26 | B | 15 | 0.012182 | 4.74e-05
2010 | 2010-03-26 | C | 900 | 0.078002 | 0.002844
2010 | 2010-03-26 | B | 21 | 0.018676 | 6.6361e-05
2010 | 2010-03-27 | B | 1306 | 0.52826 | 0.004127
2010 | 2010-03-27 | C | 81 | 0.01459 | 0.00025596
2010 | 2010-03-27 | C | 50 | 0.012315 | 0.000158
2010 | 2010-03-27 | C | 64 | 0.0052583 | 0.00020224
2010 | 2010-03-27 | B | 33 | 0.016893 | 0.00010428
2010 | 2010-03-28 | C | 133 | 0.060521 | 0.00042028
2010 | 2010-03-28 | C | 16 | 0.0019213 | 5.056e-05
2010 | 2010-03-28 | C | 14 | 0.0023005 | 4.424e-05
2010 | 2010-03-28 | C | 216 | 0.11793 | 0.00068257
2010 | 2010-03-29 | C | 61 | 0.016192 | 0.00019276
2010 | 2010-03-29 | C | 63 | 0.0059724 | 0.00019908
2010 | 2010-03-29 | C | 518 | 0.12277 | 0.0016369
2010 | 2010-03-29 | C | 50 | 0.003002 | 0.000158
2010 | 2010-03-29 | C | 64 | 0.017595 | 0.00020224
2010 | 2010-03-29 | C | 1 | 0.0002212 | 3.16e-06
2010 | 2010-03-29 | B | 360 | 0.24686 | 0.0011376
2010 | 2010-03-29 | C | 201 | 0.04419 | 0.00063517
2010 | 2010-03-27 | B | 7 | 0.0070785 | 2.212e-05
2010 | 2010-03-22 | B | 85 | 0.048886 | 0.0002686
2010 | 2010-03-22 | B | 98 | 0.064724 | 0.00030968
2010 | 2010-03-29 | B | 1 | 7.9001e-05 | 3.16e-06
2010 | 2010-03-30 | B | 43 | 0.056255 | 0.00013588
2010 | 2010-03-30 | B | 1 | 0.00048032 | 3.16e-06
2010 | 2010-03-30 | C | 76 | 0.012729 | 0.00024016
2010 | 2010-03-30 | B | 89 | 0.049499 | 0.00028124
2010 | 2010-03-30 | B | 53 | 0.027467 | 0.00016748
2010 | 2010-03-30 | C | 576 | 0.092829 | 0.0018202
2010 | 2010-03-31 | C | 201 | 0.0578 | 0.00063517
2010 | 2010-03-30 | B | 113 | 0.26424 | 0.00035708
2010 | 2010-03-30 | C | 210 | 0.067868 | 0.00066361
2010 | 2010-03-31 | C | 514 | 0.17299 | 0.0016243
2010 | 2010-03-31 | C | 878 | 0.011098 | 0.0027745
2010 | 2010-03-31 | C | 10 | 0.0096697 | 3.16e-05
2010 | 2010-03-31 | B | 4 | 0.00069521 | 1.264e-05
2010 | 2010-03-31 | B | 41 | 0.02358 | 0.00012956
2010 | 2010-03-31 | B | 7 | 0.0020793 | 2.212e-05
2010 | 2010-03-31 | B | 182 | 0.22602 | 0.00057512
2010 | 2010-03-31 | B | 7 | 0.0070563 | 2.212e-05
2010 | 2010-03-31 | B | 5 | 0.0072365 | 1.58e-05
2010 | 2010-03-31 | C | 10 | 0.0079633 | 3.16e-05
2010 | 2010-03-31 | B | 438 | 0.14533 | 0.0013841
2010 | 2010-03-31 | C | 1815 | 0.086032 | 0.0057354
2010 | 2010-03-31 | C | 218 | 0.069577 | 0.00068889
2010 | 2010-03-30 | B | 46 | 0.049423 | 0.00014536
2010 | 2010-03-30 | B | 42 | 0.044196 | 0.00013272
2010 | 2010-03-30 | B | 267 | 0.1004 | 0.00084373
2010 | 2010-03-29 | B | 1 | 0.00072997 | 3.16e-06
2011 | 2010-04-01 | C | 41 | 0.011976 | 0.00012877
2011 | 2010-04-01 | C | 2 | 0.0020541 | 6.2816e-06
2011 | 2010-04-01 | C | 36.0625 | 0.0032847 | 0.00011935
2011 | 2010-04-02 | C | 42 | 0.015434 | 0.00013191
2011 | 2010-04-03 | C | 269.1304 | 0.094673 | 0.0021892
2011 | 2010-04-02 | C | 10.4077 | 0.013533 | 0.00011307
2011 | 2010-04-03 | C | 245.2778 | 0.10862 | 0.001828
2011 | 2010-04-03 | C | 59.0526 | 0.03116 | 0.00021672
2011 | 2010-04-04 | C | 90.3071 | 0.071193 | 0.0022488
2011 | 2010-04-05 | C | 1083 | 0.04422 | 0.0034015
2011 | 2010-04-06 | C | 355 | 0.15387 | 0.001115
2011 | 2010-04-06 | B | 2 | 0.0010176 | 6.2816e-06
2011 | 2010-04-06 | B | 6 | 0.0055969 | 1.8845e-05
2011 | 2010-04-06 | B | 4 | 0.0033544 | 1.2563e-05
2011 | 2010-04-06 | B | 1 | 0.0008386 | 3.1408e-06
2011 | 2010-04-06 | B | 110 | 0.13094 | 0.00034549
2011 | 2010-04-06 | C | 149 | 0.049138 | 0.00046798
2011 | 2010-04-06 | C | 210 | 0.033638 | 0.00065957
2011 | 2010-04-06 | C | 33.8531 | 0.12132 | 0.00097994
2011 | 2010-04-06 | C | 321.6595 | 0.18387 | 0.0022143
2011 | 2010-04-07 | B | 4 | 0.0029775 | 1.2563e-05
2011 | 2010-04-07 | B | 83 | 0.067779 | 0.00026069
2011 | 2010-04-07 | C | 28 | 0.01794 | 8.7943e-05
2011 | 2010-04-07 | B | 162 | 0.19488 | 0.00050881
2011 | 2010-04-07 | C | 1 | 0.0010176 | 3.1408e-06
2011 | 2010-04-08 | B | 104 | 0.077742 | 0.00032665
2011 | 2010-04-08 | B | 100 | 0.14197 | 0.00031408
2011 | 2010-04-08 | B | 148 | 0.21197 | 0.00046484
2011 | 2010-04-08 | C | 185.1531 | 0.11224 | 0.0035743
2011 | 2010-04-08 | B | 1 | 0.0014448 | 3.1408e-06
2011 | 2010-04-08 | B | 182 | 0.21436 | 0.00057163
2011 | 2010-04-08 | B | 33 | 0.03638 | 0.00010365
2011 | 2010-04-08 | B | 17 | 0.0090236 | 5.3394e-05
2011 | 2010-04-08 | B | 234 | 0.19256 | 0.00073495
2011 | 2010-04-08 | C | 11 | 0.0017966 | 3.4549e-05
2011 | 2010-04-09 | C | 147 | 0.0087723 | 0.0004617
2011 | 2010-04-09 | C | 127.1556 | 0.088661 | 0.0014636
2011 | 2010-04-09 | B | 20 | 0.0223 | 6.2816e-05
2011 | 2010-04-09 | B | 148 | 0.19895 | 0.00046484
2011 | 2010-04-09 | C | 14 | 0.0014511 | 4.3972e-05
2011 | 2010-04-11 | C | 258 | 0.013776 | 0.00081033
2011 | 2010-04-11 | C | 688 | 0.034574 | 0.0021609
2011 | 2010-04-11 | B | 210 | 0.13455 | 0.00065957
2011 | 2010-04-11 | B | 1 | 0.00071611 | 3.1408e-06
2011 | 2010-04-11 | C | 217 | 0.036804 | 0.00068156
2011 | 2010-04-12 | C | 5 | 0.0042715 | 1.5704e-05
2011 | 2010-04-12 | C | 76.7851 | 0.028458 | 0.00034863
2011 | 2010-04-12 | B | 5 | 0.0050567 | 1.5704e-05
2011 | 2010-04-13 | B | 61 | 0.016094 | 0.00019159
2011 | 2010-04-13 | B | 14 | 0.0097617 | 4.3972e-05
2011 | 2010-04-13 | B | 2 | 0.00223 | 6.2816e-06
2011 | 2010-04-13 | B | 15 | 0.013521 | 4.7112e-05
2011 | 2010-04-13 | B | 1 | 0.00074437 | 3.1408e-06
2011 | 2010-04-13 | B | 145 | 0.14756 | 0.00045542
2011 | 2010-04-13 | C | 2 | 0.00081033 | 6.2816e-06
2011 | 2010-04-13 | C | 901.6593 | 0.24921 | 0.0034706
2011 | 2010-04-13 | C | 11 | 0.0016238 | 3.4549e-05
2011 | 2010-04-14 | C | 102.2314 | 0.22797 | 0.0010459
2011 | 2010-04-14 | C | 335 | 0.012626 | 0.0010522
2011 | 2010-04-14 | B | 15 | 0.012108 | 4.7112e-05
2011 | 2010-04-14 | B | 8 | 0.0075128 | 2.5127e-05
2011 | 2010-04-14 | B | 182 | 0.22065 | 0.00057163
2011 | 2010-04-14 | C | 50.715 | 0.091749 | 0.00079463
2011 | 2010-04-14 | C | 252 | 0.0094978 | 0.00079149
2011 | 2010-04-14 | C | 37 | 0.0077861 | 0.00011621
2011 | 2010-04-14 | C | 253 | 0.016687 | 0.00079463
2011 | 2010-04-14 | C | 235 | 0.03469 | 0.00073809
2011 | 2010-04-15 | C | 1047 | 0.06248 | 0.0032884
2011 | 2010-04-15 | C | 660 | 0.041459 | 0.0020729
2011 | 2010-04-15 | C | 46 | 0.010402 | 0.00014448
2011 | 2010-04-15 | C | 201 | 0.047979 | 0.00063131
2011 | 2010-04-15 | B | 5 | 0.00095795 | 1.5704e-05
2011 | 2010-04-15 | B | 483 | 0.64777 | 0.001517
2011 | 2010-04-15 | C | 267.2426 | 0.13933 | 0.001963
2011 | 2010-04-15 | B | 118 | 0.13231 | 0.00037062
2011 | 2010-04-15 | B | 47 | 0.0527 | 0.00014762
2011 | 2010-04-15 | B | 16 | 0.016433 | 5.0253e-05
2011 | 2010-04-15 | C | 3 | 0.0011213 | 9.4225e-06
2011 | 2010-04-16 | C | 964 | 0.21194 | 0.0030278
2011 | 2010-04-16 | B | 20 | 0.0081661 | 6.2816e-05
2011 | 2010-04-16 | B | 2 | 0.0010553 | 6.2816e-06
2011 | 2010-04-16 | B | 25 | 0.028817 | 7.8521e-05
2011 | 2010-04-16 | B | 6 | 0.0041647 | 1.8845e-05
2011 | 2010-04-16 | B | 10 | 0.010553 | 3.1408e-05
2011 | 2010-04-16 | B | 110 | 0.088791 | 0.00034549
2011 | 2010-04-16 | B | 153 | 0.13696 | 0.00048055
2011 | 2010-04-16 | B | 74 | 0.062056 | 0.00023242
2011 | 2010-04-16 | B | 19 | 0.0078772 | 5.9676e-05
2011 | 2010-04-16 | C | 275 | 0.055278 | 0.00086373
2011 | 2010-04-16 | C | 185 | 0.0023242 | 0.00058105
2011 | 2010-04-16 | C | 14 | 0.0038695 | 4.3972e-05
2011 | 2010-04-16 | C | 2784 | 0.034976 | 0.008744
2011 | 2010-04-17 | C | 454.6389 | 0.098528 | 0.0025566
2011 | 2010-04-17 | C | 106 | 0.0096549 | 0.00033293
2011 | 2010-04-17 | B | 2 | 0.0010553 | 6.2816e-06
2011 | 2010-04-16 | B | 1 | 0.00056535 | 3.1408e-06
2011 | 2010-04-17 | C | 504.5965 | 0.085582 | 0.0023493
2011 | 2010-04-18 | C | 36 | 0.003279 | 0.00011307
2011 | 2010-04-18 | C | 19 | 0.0072207 | 5.9676e-05
2011 | 2010-04-16 | C | 1 | 0.00015076 | 3.1408e-06
2011 | 2010-04-16 | C | 194.8178 | 0.14257 | 0.0022394
2011 | 2010-04-16 | C | 365.3516 | 0.14344 | 0.001382
2011 | 2010-04-18 | C | 283 | 0.076441 | 0.00088885
2011 | 2010-04-18 | C | 1390.2308 | 0.15719 | 0.0056095
2011 | 2010-04-18 | C | 30 | 0.0065957 | 9.4225e-05
2011 | 2010-04-18 | C | 575 | 0.025284 | 0.001806
2011 | 2010-04-19 | C | 575 | 0.023478 | 0.001806
2011 | 2010-04-16 | C | 151 | 0.0042684 | 0.00047426
2011 | 2010-04-19 | B | 1 | 0.00043657 | 3.1408e-06
2011 | 2010-04-19 | B | 1 | 0.00054022 | 3.1408e-06
2011 | 2010-04-19 | B | 13 | 0.012943 | 4.0831e-05
2011 | 2010-04-19 | C | 45 | 0.015123 | 0.00014134
2011 | 2010-04-19 | B | 49 | 0.057097 | 0.0001539
2011 | 2010-04-19 | B | 2 | 0.0026571 | 6.2816e-06
2011 | 2010-04-19 | B | 1 | 0.0011621 | 3.1408e-06
2011 | 2010-04-19 | B | 10 | 0.011841 | 3.1408e-05
2011 | 2010-04-19 | C | 106 | 0.013317 | 0.00033293
2011 | 2010-04-20 | B | 12 | 0.0034675 | 3.769e-05
2011 | 2010-04-20 | B | 162 | 0.046302 | 0.00050881
2011 | 2010-04-20 | C | 4 | 0.0011558 | 1.2563e-05
2011 | 2010-04-20 | C | 55 | 0.057179 | 0.00017275
2011 | 2010-04-20 | C | 1053 | 0.53247 | 0.0033073
2011 | 2010-04-20 | C | 2479.9452 | 2.6794 | 0.0082227
2011 | 2010-04-20 | C | 1739.1224 | 0.51892 | 0.0071705
2011 | 2010-04-20 | B | 176.3373 | 0.27581 | 0.00094539
2011 | 2010-04-20 | B | 165 | 0.085509 | 0.00051824
2011 | 2010-04-20 | B | 3 | 0.0030152 | 9.4225e-06
2011 | 2010-04-20 | B | 12 | 0.0011307 | 3.769e-05
2011 | 2010-04-20 | B | 2 | 0.0013694 | 6.2816e-06
2011 | 2010-04-21 | B | 182 | 0.20807 | 0.00057163
2011 | 2010-04-21 | B | 39 | 0.027806 | 0.00012249
2011 | 2010-04-21 | C | 8 | 0.0020353 | 2.5127e-05
2011 | 2010-04-21 | C | 12 | 0.010402 | 3.769e-05
2011 | 2010-04-21 | B | 299 | 0.39536 | 0.00093911
2011 | 2010-04-21 | B | 5 | 0.0026697 | 1.5704e-05
2011 | 2010-04-21 | B | 248.0896 | 0.15428 | 0.00087315
2011 | 2010-04-21 | C | 745 | 0.021059 | 0.0023399
2011 | 2010-04-01 | B | 9 | 0.0054839 | 2.8267e-05
2011 | 2010-04-09 | B | 162 | 0.18673 | 0.00050881
2011 | 2010-04-16 | B | 11 | 0.0086027 | 3.4549e-05
2011 | 2010-04-09 | B | 20 | 0.0223 | 6.2816e-05
2011 | 2010-04-20 | B | 1 | 8.1661e-05 | 3.1408e-06
2011 | 2010-04-06 | B | 1 | 0.0010522 | 3.1408e-06
2011 | 2010-04-07 | B | 29 | 0.015484 | 9.1084e-05
2011 | 2010-04-07 | B | 49 | 0.050787 | 0.0001539
2011 | 2010-04-07 | B | 34 | 0.011533 | 0.00010679
2011 | 2010-04-07 | B | 119 | 0.057932 | 0.00037376
2011 | 2010-04-22 | B | 39 | 0.04373 | 0.00012249
2011 | 2010-04-06 | B | 53 | 0.028632 | 0.00016646
2011 | 2010-04-22 | B | 35 | 0.024844 | 0.00010993
2011 | 2010-04-22 | C | 141 | 0.0066428 | 0.00044286
2011 | 2010-04-22 | B | 68 | 0.056598 | 0.00021358
2011 | 2010-04-22 | B | 3 | 0.0011024 | 9.4225e-06
2011 | 2010-04-22 | B | 1 | 0.0011213 | 3.1408e-06
2011 | 2010-04-22 | B | 18 | 0.007293 | 5.6535e-05
2011 | 2010-04-22 | B | 7 | 0.009212 | 2.1986e-05
2011 | 2010-04-22 | B | 110 | 0.13025 | 0.00034549
2011 | 2010-04-22 | B | 1 | 0.0013474 | 3.1408e-06
2011 | 2010-04-22 | B | 1 | 0.00062188 | 3.1408e-06
2011 | 2010-04-22 | C | 19 | 0.0011338 | 5.9676e-05
2011 | 2010-04-22 | C | 181.3885 | 0.25637 | 0.0022928
2011 | 2010-04-23 | C | 147 | 0.039706 | 0.0004617
2011 | 2010-04-23 | B | 122 | 0.085832 | 0.00038318
2011 | 2010-04-23 | B | 1 | 0.00021986 | 3.1408e-06
2011 | 2010-04-23 | B | 49 | 0.048017 | 0.0001539
2011 | 2010-04-23 | C | 6 | 0.00069726 | 1.8845e-05
2011 | 2010-04-23 | C | 1072.962 | 0.25612 | 0.0035397
2011 | 2010-04-23 | C | 713.8571 | 0.60537 | 0.0036622
2011 | 2010-04-24 | C | 474.0534 | 0.19058 | 0.0017212
2011 | 2010-04-24 | C | 863 | 0.0027105 | 0.0027105
2011 | 2010-04-24 | C | 478.5833 | 0.067642 | 0.0015264
2011 | 2010-04-24 | C | 232.3471 | 0.24593 | 0.0011652
2011 | 2010-04-24 | C | 949 | 0.062593 | 0.0029806
2011 | 2010-04-25 | C | 244.3617 | 0.21413 | 0.0025409
2011 | 2010-04-25 | C | 7 | 0.00037376 | 2.1986e-05
2011 | 2010-04-25 | C | 126.0448 | 0.025337 | 0.0011401
2011 | 2010-04-26 | C | 26 | 0.029398 | 8.1661e-05
2011 | 2010-04-26 | B | 49 | 0.052634 | 0.0001539
2011 | 2010-04-27 | B | 98 | 0.052018 | 0.0003078
2011 | 2010-04-27 | B | 86 | 0.034844 | 0.00027011
2011 | 2010-04-27 | B | 35 | 0.020996 | 0.00010993
2011 | 2010-04-27 | C | 13 | 0.0014699 | 4.0831e-05
2011 | 2010-04-27 | B | 24 | 0.026006 | 7.538e-05
2011 | 2010-04-27 | C | 6 | 0.001828 | 1.8845e-05
2011 | 2010-04-27 | C | 161 | 0.010619 | 0.00050567
2011 | 2010-04-27 | B | 11 | 0.012887 | 3.4549e-05
2011 | 2010-04-27 | B | 10.0526 | 0.011903 | 0.00016646
2011 | 2010-04-27 | C | 1147.5214 | 0.91546 | 0.0072804
2011 | 2010-04-27 | C | 29 | 0.0030058 | 9.1084e-05
2011 | 2010-04-28 | C | 4 | 0.00054022 | 1.2563e-05
2011 | 2010-04-28 | C | 106 | 0.014982 | 0.00033293
2011 | 2010-04-28 | B | 182 | 0.2075 | 0.00057163
2011 | 2010-04-28 | B | 27 | 0.015858 | 8.4802e-05
2011 | 2010-04-28 | B | 14.2632 | 0.016889 | 7.8521e-05
2011 | 2010-04-28 | C | 37 | 0.0046484 | 0.00011621
2011 | 2010-04-28 | B | 37 | 0.031028 | 0.00011621
2011 | 2010-04-28 | B | 162 | 0.10532 | 0.00050881
2011 | 2010-04-28 | B | 106 | 0.1062 | 0.00033293
2011 | 2010-04-28 | C | 76 | 0.0076385 | 0.0002387
2011 | 2010-04-28 | C | 4 | 0.00074123 | 1.2563e-05
2011 | 2010-04-28 | C | 448.3333 | 0.021122 | 0.0014793
2011 | 2010-04-28 | C | 117.7792 | 0.027374 | 0.0004617
2011 | 2010-04-29 | C | 370.5359 | 0.27233 | 0.0022363
2011 | 2010-04-29 | C | 86 | 0.018908 | 0.00027011
2011 | 2010-04-29 | B | 47 | 0.054324 | 0.00014762
2011 | 2010-04-29 | B | 20 | 0.017526 | 6.2816e-05
2011 | 2010-04-29 | B | 1 | 0.00087943 | 3.1408e-06
2011 | 2010-04-29 | B | 93 | 0.099313 | 0.0002921
2011 | 2010-04-29 | B | 1 | 0.0013882 | 3.1408e-06
2011 | 2010-04-29 | B | 15 | 0.0155 | 4.7112e-05
2011 | 2010-04-30 | C | 303 | 0.037115 | 0.00095167
2011 | 2010-04-29 | C | 794 | 0.014963 | 0.0024938
2011 | 2010-04-30 | B | 2 | 0.00055278 | 6.2816e-06
2011 | 2010-04-30 | B | 60 | 0.031283 | 0.00018845
2011 | 2010-04-30 | B | 29 | 0.0071045 | 9.1084e-05
2011 | 2010-04-30 | B | 11 | 0.0050442 | 3.4549e-05
2011 | 2010-04-30 | B | 14 | 0.013147 | 4.3972e-05
2011 | 2010-04-30 | B | 60 | 0.031283 | 0.00018845
2011 | 2010-04-29 | C | 1 | 0.0050253 | 3.1408e-06
2011 | 2010-04-30 | C | 320.5644 | 0.40374 | 0.0041051
2011 | 2010-04-30 | B | 21 | 0.023547 | 6.5957e-05
2011 | 2010-04-30 | C | 210.0294 | 0.042878 | 0.00070354
2011 | 2010-04-30 | C | 5 | 0.0010051 | 1.5704e-05
2011 | 2010-04-30 | B | 167 | 0.046158 | 0.00052452
2011 | 2010-05-01 | C | 21 | 0.0049468 | 6.5957e-05
2011 | 2010-05-01 | C | 145.1279 | 0.11623 | 0.00052452
2011 | 2010-05-01 | B | 4 | 0.0032288 | 1.2563e-05
2011 | 2010-05-01 | C | 160.6008 | 0.12358 | 0.001338
2011 | 2010-05-02 | C | 299.574 | 0.15619 | 0.0022991
2011 | 2010-05-02 | B | 55 | 0.008119 | 0.00017275
2011 | 2010-04-28 | B | 142.223 | 0.060751 | 0.00077892
2011 | 2010-05-02 | C | 14 | 0.0036057 | 4.3972e-05
2011 | 2010-05-03 | C | 15 | 0.0042401 | 4.7112e-05
2011 | 2010-05-03 | B | 19 | 0.0048934 | 5.9676e-05
2011 | 2010-05-03 | B | 8 | 0.0022614 | 2.5127e-05
2011 | 2010-05-03 | C | 210.4416 | 0.048911 | 0.00096737
2011 | 2010-05-03 | C | 43 | 0.024445 | 0.00013506
2011 | 2010-05-03 | B | 1 | 0.00052766 | 3.1408e-06
2011 | 2010-05-03 | C | 92 | 0.0075128 | 0.00028896
2011 | 2010-05-04 | C | 309 | 0.0029115 | 0.00097051
2011 | 2010-05-04 | B | 206 | 0.13264 | 0.00064701
2011 | 2010-05-04 | B | 35 | 0.028472 | 0.00010993
2011 | 2010-05-04 | C | 59 | 0.016122 | 0.00018531
2011 | 2010-05-04 | B | 13 | 0.014454 | 4.0831e-05
2011 | 2010-05-04 | B | 1 | 0.0011684 | 3.1408e-06
2011 | 2010-05-04 | B | 328 | 0.12877 | 0.0010302
2011 | 2010-05-04 | B | 116 | 0.13371 | 0.00036434
2011 | 2010-05-04 | B | 122 | 0.18508 | 0.00038318
2011 | 2010-05-04 | B | 1 | 0.00136 | 3.1408e-06
2011 | 2010-05-04 | B | 34 | 0.0073684 | 0.00010679
2011 | 2010-05-05 | C | 14.2275 | 0.010278 | 0.00012249
2011 | 2010-05-05 | B | 38 | 0.0062063 | 0.00011935
2011 | 2010-05-05 | C | 545.8571 | 0.10287 | 0.0018625
2011 | 2010-05-05 | B | 88 | 0.059701 | 0.00027639
2011 | 2010-05-05 | B | 260 | 0.19517 | 0.00081661
2011 | 2010-05-05 | B | 11 | 0.013889 | 3.4549e-05
2011 | 2010-05-05 | C | 416.8718 | 0.098199 | 0.0021829
2011 | 2010-05-05 | B | 1 | 0.0012752 | 3.1408e-06
2011 | 2010-05-05 | B | 93 | 0.1221 | 0.0002921
2011 | 2010-05-05 | C | 208.8853 | 0.14106 | 0.0012469
2011 | 2010-05-05 | C | 201.3875 | 0.16952 | 0.0020761
2011 | 2010-05-05 | C | 233.9699 | 0.095532 | 0.00094539
2011 | 2010-05-06 | C | 429 | 0.039075 | 0.0013474
2011 | 2010-05-06 | B | 25 | 0.024812 | 7.8521e-05
2011 | 2010-05-06 | C | 36 | 0.0035052 | 0.00011307
2011 | 2010-05-06 | C | 38 | 0.0053708 | 0.00011935
2011 | 2010-05-06 | C | 62 | 0.07575 | 0.00019473
2011 | 2010-05-07 | B | 72 | 0.035956 | 0.00022614
2011 | 2010-05-07 | C | 88 | 0.010227 | 0.00027639
2011 | 2010-05-07 | C | 201 | 0.01452 | 0.00063131
2011 | 2010-05-08 | C | 8 | 0.0027388 | 2.5127e-05
2011 | 2010-05-10 | B | 178 | 0.025717 | 0.00055907
2011 | 2010-05-10 | B | 114 | 0.068388 | 0.00035805
2011 | 2010-05-10 | B | 33 | 0.029021 | 0.00010365
2011 | 2010-05-10 | B | 15 | 0.014039 | 4.7112e-05
2011 | 2010-05-10 | B | 14 | 0.01561 | 4.3972e-05
2011 | 2010-05-10 | B | 77 | 0.08658 | 0.00024184
2011 | 2010-05-10 | B | 49 | 0.015852 | 0.0001539
2011 | 2010-05-10 | C | 260.4958 | 0.094908 | 0.0011715
2011 | 2010-05-11 | C | 232 | 0.044449 | 0.00072867
2011 | 2010-05-11 | C | 429.3544 | 0.20902 | 0.0027231
2011 | 2010-05-09 | B | 45 | 0.037737 | 0.00014134
2011 | 2010-05-05 | B | 3 | 0.0045887 | 9.4225e-06
2011 | 2010-05-11 | B | 81 | 0.052917 | 0.00025441
2011 | 2010-05-11 | B | 6 | 0.0048055 | 1.8845e-05
2011 | 2010-05-11 | B | 41 | 0.044169 | 0.00012877
2011 | 2010-05-11 | C | 55 | 0.012783 | 0.00017275
2011 | 2010-05-11 | C | 9 | 0.0027137 | 2.8267e-05
2011 | 2010-05-11 | C | 3.6062 | 0.033991 | 0.0006156
2011 | 2010-05-11 | B | 37 | 0.029634 | 0.00011621
2011 | 2010-05-12 | C | 148.0706 | 0.077666 | 0.0009234
2011 | 2010-05-12 | C | 63 | 0.010091 | 0.00019787
2011 | 2010-05-12 | C | 26.2527 | 0.0072561 | 0.00019787
2011 | 2010-05-12 | C | 4 | 0.00059047 | 1.2563e-05
2011 | 2010-05-12 | C | 18 | 0.0030529 | 5.6535e-05
2011 | 2010-05-12 | C | 400.6733 | 0.25043 | 0.001382
2011 | 2010-05-12 | C | 325.2843 | 0.10114 | 0.0035397
2011 | 2010-05-13 | C | 197.1818 | 0.10033 | 0.00064073
2011 | 2010-05-12 | C | 206.0606 | 0.062131 | 0.00093911
2011 | 2010-05-13 | C | 8 | 0.0011558 | 2.5127e-05
2011 | 2010-05-12 | B | 211 | 0.077537 | 0.00066271
2011 | 2010-05-13 | C | 92 | 0.0052012 | 0.00028896
2011 | 2010-05-13 | B | 3 | 0.0017526 | 9.4225e-06
2011 | 2010-05-13 | C | 135 | 0.082682 | 0.00042401
2011 | 2010-05-12 | C | 24.9958 | 0.074503 | 0.00036748
2011 | 2010-05-13 | B | 30 | 0.033167 | 9.4225e-05
2011 | 2010-05-13 | C | 9 | 0.00053708 | 2.8267e-05
2011 | 2010-05-13 | B | 3 | 0.0046547 | 9.4225e-06
2011 | 2010-05-12 | B | 125.7484 | 0.18879 | 0.00084488
2011 | 2010-05-13 | C | 19 | 0.0037596 | 5.9676e-05
2011 | 2010-05-13 | B | 1 | 0.00031094 | 3.1408e-06
2011 | 2010-05-14 | C | 3 | 0.0011967 | 9.4225e-06
2011 | 2010-05-14 | B | 44 | 0.0093973 | 0.0001382
2011 | 2010-05-14 | C | 68 | 0.0059801 | 0.00021358
2011 | 2010-05-14 | B | 11 | 0.0047678 | 3.4549e-05
2011 | 2010-05-14 | B | 31 | 0.024147 | 9.7365e-05
2011 | 2010-05-14 | B | 32 | 0.037288 | 0.00010051
2011 | 2010-05-14 | B | 27 | 0.036974 | 8.4802e-05
2011 | 2010-05-14 | B | 1 | 0.0019505 | 3.1408e-06
2011 | 2010-05-14 | B | 14.8533 | 0.0068578 | 8.1661e-05
2011 | 2010-05-14 | C | 680.1593 | 0.62379 | 0.0043595
2011 | 2010-05-14 | C | 6 | 0.003034 | 1.8845e-05
2011 | 2010-05-15 | C | 262 | 0.010698 | 0.0008229
2011 | 2010-05-15 | C | 220 | 0.022111 | 0.00069098
2011 | 2010-05-14 | C | 330.8855 | 0.13302 | 0.0016521
2011 | 2010-05-15 | C | 59.8985 | 0.12548 | 0.00086373
2011 | 2010-05-15 | C | 142.0746 | 0.088354 | 0.00080091
2011 | 2010-05-15 | B | 131 | 0.073649 | 0.00041145
2011 | 2010-05-14 | C | 25 | 0.084567 | 7.8521e-05
2011 | 2010-05-15 | C | 51 | 0.019702 | 0.00016018
2011 | 2010-05-15 | C | 200.8407 | 0.1842 | 0.0011338
2011 | 2010-05-16 | C | 242.9831 | 0.042737 | 0.0010804
2011 | 2010-05-16 | B | 445 | 0.36339 | 0.0013977
2011 | 2010-05-16 | C | 36 | 0.00079149 | 0.00011307
2011 | 2010-05-16 | C | 1 | 0.00073495 | 3.1408e-06
2011 | 2010-05-17 | B | 1 | 0.00059362 | 3.1408e-06
2011 | 2010-05-17 | B | 93 | 0.037096 | 0.0002921
2011 | 2010-05-17 | C | 3 | 0.00031094 | 9.4225e-06
2011 | 2010-05-17 | B | 79 | 0.024564 | 0.00024812
2011 | 2010-05-17 | B | 37 | 0.027774 | 0.00011621
2011 | 2010-05-17 | C | 175 | 0.075851 | 0.00054964
2011 | 2010-05-17 | B | 60 | 0.0033921 | 0.00018845
2011 | 2010-05-14 | B | 62 | 0.017915 | 0.00019473
2011 | 2010-05-14 | B | 20 | 0.0087943 | 6.2816e-05
2011 | 2010-05-13 | B | 30 | 0.011401 | 9.4225e-05
2011 | 2010-05-13 | B | 40 | 0.014071 | 0.00012563
2011 | 2010-05-18 | B | 32 | 0.033368 | 0.00010051
2011 | 2010-05-18 | B | 17 | 0.021411 | 5.3394e-05
2011 | 2010-05-18 | B | 172 | 0.18962 | 0.00054022
2011 | 2010-05-18 | B | 2 | 0.0012249 | 6.2816e-06
2011 | 2010-05-18 | C | 156.498 | 0.1219 | 0.0011652
2011 | 2010-05-18 | B | 130 | 0.022865 | 0.00040831
2011 | 2010-05-19 | B | 1 | 0.00043029 | 3.1408e-06
2011 | 2010-05-19 | B | 1 | 0.00052766 | 3.1408e-06
2011 | 2010-05-19 | B | 9 | 0.0054273 | 2.8267e-05
2011 | 2010-05-19 | B | 4 | 0.0024875 | 1.2563e-05
2011 | 2010-05-19 | C | 17 | 0.015324 | 5.3394e-05
2011 | 2010-05-19 | B | 238 | 0.076994 | 0.00074752
2011 | 2010-05-19 | B | 165.5662 | 0.22621 | 0.00095167
2011 | 2010-05-19 | B | 493 | 0.43666 | 0.0015484
2011 | 2010-05-19 | C | 9 | 0.0070951 | 2.8267e-05
2011 | 2010-05-19 | C | 18 | 0.0049185 | 5.6535e-05
2011 | 2010-05-19 | B | 202.6731 | 0.064293 | 0.00073495
2011 | 2010-05-20 | C | 630.3134 | 0.1267 | 0.0023054
2011 | 2010-05-20 | C | 46 | 0.0031785 | 0.00014448
2011 | 2010-05-20 | B | 18 | 0.0087064 | 5.6535e-05
2011 | 2010-05-20 | C | 10 | 0.0046484 | 3.1408e-05
2011 | 2010-05-20 | B | 108 | 0.023405 | 0.00033921
2011 | 2010-05-20 | B | 430 | 0.22554 | 0.0013506
2011 | 2010-05-20 | B | 73 | 0.034392 | 0.00022928
2011 | 2010-05-20 | B | 108 | 0.097692 | 0.00033921
2011 | 2010-05-20 | B | 14 | 0.009322 | 4.3972e-05
2011 | 2010-05-20 | B | 2 | 0.0019599 | 6.2816e-06
2011 | 2010-05-20 | B | 7 | 0.0075631 | 2.1986e-05
2011 | 2010-05-20 | B | 67 | 0.0726 | 0.00021044
2011 | 2010-05-20 | B | 61 | 0.074337 | 0.00019159
2011 | 2010-05-20 | C | 196.9683 | 0.037119 | 0.0013348
2011 | 2010-05-20 | C | 245.586 | 0.11879 | 0.001473
2011 | 2010-05-20 | C | 142 | 0.0071359 | 0.000446
2011 | 2010-05-21 | C | 616 | 0.23217 | 0.0019347
2011 | 2010-05-21 | B | 13.15 | 0.016397 | 7.8521e-05
2011 | 2010-05-21 | B | 4 | 0.0021986 | 1.2563e-05
2011 | 2010-05-21 | C | 470.7045 | 0.12566 | 0.0029241
2011 | 2010-05-22 | C | 163 | 0.03942 | 0.00051195
2011 | 2010-05-21 | C | 11 | 0.00082918 | 3.4549e-05
2011 | 2010-05-22 | B | 24 | 0.0038444 | 7.538e-05
2011 | 2010-05-22 | B | 53 | 0.014482 | 0.00016646
2011 | 2010-05-23 | B | 77 | 0.063363 | 0.00024184
2011 | 2010-05-24 | C | 288 | 0.027137 | 0.00090456
2011 | 2010-05-22 | C | 470.2903 | 0.13294 | 0.0023493
2011 | 2010-05-24 | C | 8 | 0.0018594 | 2.5127e-05
2011 | 2010-05-24 | C | 167.6647 | 0.086363 | 0.00061246
2011 | 2010-05-24 | B | 37 | 0.02638 | 0.00011621
2011 | 2010-05-24 | B | 6 | 0.0012438 | 1.8845e-05
2011 | 2010-05-24 | B | 73 | 0.089878 | 0.00022928
2011 | 2010-05-24 | C | 166 | 0.030761 | 0.00052138
2011 | 2010-05-24 | B | 108 | 0.13467 | 0.00033921
2011 | 2010-05-24 | C | 89 | 0.031028 | 0.00027953
2011 | 2010-05-24 | C | 40 | 0.032036 | 0.00012563
2011 | 2010-05-24 | C | 27 | 0.0057665 | 8.4802e-05
2011 | 2010-05-24 | C | 58 | 0.011294 | 0.00018217
2011 | 2010-05-25 | C | 218 | 0.0082164 | 0.0006847
2011 | 2010-05-25 | C | 630 | 0.067276 | 0.0019787
2011 | 2010-05-25 | B | 18 | 0.016678 | 5.6535e-05
2011 | 2010-05-25 | C | 1436 | 0.090204 | 0.0045102
2011 | 2010-05-25 | B | 352 | 0.20232 | 0.0011056
2011 | 2010-05-25 | B | 5 | 0.0050567 | 1.5704e-05
2011 | 2010-05-25 | B | 53.1818 | 0.05462 | 0.00050253
2011 | 2010-05-25 | B | 244 | 0.24677 | 0.00076636
2011 | 2010-05-25 | B | 275 | 0.1071 | 0.00086373
2011 | 2010-05-25 | B | 46 | 0.050567 | 0.00014448
2011 | 2010-05-25 | C | 3 | 0.0013097 | 9.4225e-06
2011 | 2010-05-25 | C | 68 | 0.029687 | 0.00021358
2011 | 2010-05-25 | C | 250.494 | 0.062941 | 0.0013914
2011 | 2010-05-25 | B | 68 | 0.064073 | 0.00021358
2011 | 2010-05-25 | C | 156 | 0.0063696 | 0.00048997
2011 | 2010-05-26 | C | 24 | 0.0047489 | 7.538e-05
2011 | 2010-05-26 | C | 336.0503 | 0.18576 | 0.0027419
2011 | 2010-05-26 | B | 41 | 0.043912 | 0.00012877
2011 | 2010-05-26 | B | 21 | 0.023019 | 6.5957e-05
2011 | 2010-05-26 | B | 15 | 0.005889 | 4.7112e-05
2011 | 2010-05-26 | B | 72 | 0.057892 | 0.00022614
2011 | 2010-05-26 | B | 46 | 0.050856 | 0.00014448
2011 | 2010-05-25 | B | 39 | 0.015801 | 0.00012249
2011 | 2010-05-26 | C | 684 | 0.036521 | 0.0021483
2011 | 2010-05-26 | C | 55 | 0.042323 | 0.00017275
2011 | 2010-05-27 | C | 60 | 0.0045228 | 0.00018845
2011 | 2010-05-22 | B | 7 | 0.0025723 | 2.1986e-05
2011 | 2010-05-27 | B | 172 | 0.093999 | 0.00054022
2011 | 2010-05-27 | B | 4 | 0.0036559 | 1.2563e-05
2011 | 2010-05-21 | B | 3 | 0.0024687 | 9.4225e-06
2011 | 2010-05-27 | B | 99 | 0.095459 | 0.00031094
2011 | 2010-05-25 | B | 9 | 0.0026289 | 2.8267e-05
2011 | 2010-05-20 | B | 461 | 0.017375 | 0.0014479
2011 | 2010-05-27 | B | 2 | 0.0016144 | 6.2816e-06
2011 | 2010-05-27 | B | 84 | 0.01926 | 0.00026383
2011 | 2010-05-27 | C | 37.9667 | 0.028261 | 0.00026069
2011 | 2010-05-27 | C | 117.9691 | 0.034829 | 0.0005999
2011 | 2010-05-27 | C | 87 | 0.0046453 | 0.00027325
2011 | 2010-05-27 | B | 30 | 0.032036 | 9.4225e-05
2011 | 2010-05-27 | B | 37 | 0.038466 | 0.00011621
2011 | 2010-05-27 | B | 30 | 0.036088 | 9.4225e-05
2011 | 2010-05-27 | B | 49 | 0.050941 | 0.0001539
2011 | 2010-05-27 | C | 712 | 0.026835 | 0.0022363
2011 | 2010-05-28 | C | 254.5895 | 0.073565 | 0.00096109
2011 | 2010-05-28 | B | 87 | 0.010657 | 0.00027325
2011 | 2010-05-27 | B | 214 | 0.07864 | 0.00067214
2011 | 2010-05-27 | C | 184 | 0.0069349 | 0.00057791
2011 | 2010-05-27 | C | 712 | 0.022363 | 0
2011 | 2010-05-27 | C | 123.8065 | 0.010888 | 0
2011 | 2010-05-28 | B | 2 | 0.00086059 | 6.2816e-06
2011 | 2010-05-28 | C | 22 | 0.0035931 | 6.9098e-05
2011 | 2010-05-28 | C | 93 | 0.0040894 | 0.0002921
2011 | 2010-05-28 | B | 76 | 0.066121 | 0.0002387
2011 | 2010-05-28 | B | 21 | 0.021766 | 6.5957e-05
2011 | 2010-05-29 | B | 418 | 0.04595 | 0.0013129
2011 | 2010-05-27 | B | 77 | 0.0089482 | 0.00024184
2011 | 2010-05-29 | B | 316 | 0.28782 | 0.0009925
2011 | 2010-05-29 | B | 224 | 0.23076 | 0.00070354
2011 | 2010-05-30 | C | 75 | 0.0030623 | 0.00023556
2011 | 2010-05-29 | C | 1 | 0.00035805 | 3.1408e-06
2011 | 2010-05-29 | C | 103.2948 | 0.055153 | 0.00047112
2011 | 2010-05-29 | C | 341 | 0.04177 | 0.001071
2011 | 2010-05-29 | C | 149 | 0.0032759 | 0.00046798
2011 | 2010-05-29 | C | 59.8468 | 0.022744 | 0.0004617
2011 | 2010-05-30 | C | 32 | 0.037187 | 0.00010051
2011 | 2010-05-30 | C | 83 | 0.020334 | 0.00026069
2011 | 2010-05-31 | C | 20 | 0.005465 | 6.2816e-05
2011 | 2010-05-31 | C | 473 | 0.13965 | 0.0014856
2011 | 2010-05-31 | B | 18 | 0.0049185 | 5.6535e-05
2011 | 2010-05-31 | B | 22 | 0.010019 | 6.9098e-05
2011 | 2010-05-31 | C | 33 | 0.025808 | 0.00010365
2011 | 2010-05-31 | B | 31 | 0.028139 | 9.7365e-05
2011 | 2010-05-31 | B | 4 | 0.0043343 | 1.2563e-05
2011 | 2010-05-31 | B | 6 | 0.0059927 | 1.8845e-05
2011 | 2010-05-31 | B | 35 | 0.041993 | 0.00010993
2011 | 2010-05-31 | B | 34 | 0.030328 | 0.00010679
2011 | 2010-06-01 | C | 397 | 0.039901 | 0.0012469
2011 | 2010-06-01 | B | 92 | 0.055768 | 0.00028896
2011 | 2010-06-01 | C | 149 | 0.11793 | 0.00046798
2011 | 2010-06-01 | C | 226.2927 | 0.056149 | 0.0015484
2011 | 2010-06-01 | B | 7 | 0.0078489 | 2.1986e-05
2011 | 2010-06-01 | B | 32 | 0.0018091 | 0.00010051
2011 | 2010-06-01 | C | 5 | 0.0007538 | 1.5704e-05
2011 | 2010-06-01 | C | 9 | 0.0018939 | 2.8267e-05
2011 | 2010-06-01 | C | 285 | 0.048337 | 0.00089513
2011 | 2010-06-01 | C | 548 | 0.027539 | 0.0017212
2011 | 2010-06-02 | C | 8210 | 0.077358 | 0.025786
2011 | 2010-06-02 | B | 84 | 0.092076 | 0.00026383
2011 | 2010-06-02 | B | 15 | 0.014652 | 4.7112e-05
2011 | 2010-06-02 | B | 40 | 0.059424 | 0.00012563
2011 | 2010-06-02 | C | 3 | 0.00039574 | 9.4225e-06
2011 | 2010-06-03 | C | 507 | 0.18313 | 0.0015924
2011 | 2010-06-03 | C | 317 | 0.020908 | 0.00099564
2011 | 2010-06-03 | C | 85.4259 | 0.028172 | 0.00062502
2011 | 2010-06-03 | B | 10.5695 | 0.0099259 | 0.00011307
2011 | 2010-06-03 | B | 142 | 0.14183 | 0.000446
2011 | 2010-06-03 | B | 52 | 0.059939 | 0.00016332
2011 | 2010-06-03 | B | 30 | 0.036371 | 9.4225e-05
2011 | 2010-06-03 | B | 147 | 0.14128 | 0.0004617
2011 | 2010-06-03 | C | 21 | 0.0020447 | 6.5957e-05
2011 | 2010-06-03 | B | 382 | 0.49432 | 0.0011998
2011 | 2010-06-03 | C | 3 | 0.0008386 | 9.4225e-06
2011 | 2010-06-03 | C | 77 | 0.0094319 | 0.00024184
2011 | 2010-06-03 | C | 601.3636 | 0.43064 | 0.0052923
2011 | 2010-06-04 | B | 21 | 0.007717 | 6.5957e-05
2011 | 2010-06-04 | B | 15 | 0.015406 | 4.7112e-05
2011 | 2010-06-04 | B | 4 | 0.0024498 | 1.2563e-05
2011 | 2010-06-04 | B | 45 | 0.047348 | 0.00014134
2011 | 2010-06-04 | B | 9 | 0.0057665 | 2.8267e-05
2011 | 2010-06-04 | B | 55 | 0.04025 | 0.00017275
2011 | 2010-06-04 | C | 120.4423 | 0.057878 | 0.00069412
2011 | 2010-06-05 | B | 222 | 0.20011 | 0.00069726
2011 | 2010-06-06 | C | 11 | 0.0025221 | 3.4549e-05
2011 | 2010-06-04 | C | 786.6385 | 0.31378 | 0.002877
2011 | 2010-06-06 | C | 839.8947 | 0.29281 | 0.0050661
2011 | 2010-06-06 | C | 747.1084 | 0.18772 | 0.0025441
2011 | 2010-06-06 | C | 812 | 0.033155 | 0.0025503
2011 | 2010-06-06 | C | 430.5623 | 0.39758 | 0
2011 | 2010-06-06 | C | 54 | 0.019335 | 0.0001696
2011 | 2010-06-07 | C | 1116 | 0.045567 | 0.0035052
2011 | 2010-06-07 | C | 5.9292 | 0.0020485 | 1.8845e-05
2011 | 2010-06-06 | C | 26.5083 | 0.064608 | 0.00047112
2011 | 2010-06-06 | C | 37 | 0.0053457 | 0.00011621
2011 | 2010-06-07 | C | 8315 | 0.20893 | 0.026116
2011 | 2010-06-07 | C | 131 | 0.022218 | 0.00041145
2011 | 2010-06-07 | C | 15 | 0.0064073 | 4.7112e-05
2011 | 2010-06-07 | C | 96 | 0.040404 | 0.00030152
2011 | 2010-06-07 | C | 75.1983 | 0.054086 | 0.00043343
2011 | 2010-06-07 | C | 310.6019 | 0.097555 | 0.0012155
2011 | 2010-06-07 | C | 278.4528 | 0.13643 | 0.00223
2011 | 2010-06-07 | C | 76.4706 | 0.089107 | 0.0011558
2011 | 2010-06-07 | C | 54.8864 | 0.037408 | 0.00055593
2011 | 2010-06-07 | C | 987 | 0.0434 | 0.0031
2011 | 2010-06-08 | C | 33 | 0.0019693 | 0.00010365
2011 | 2010-06-08 | C | 338.515 | 0.17437 | 0.0029681
2011 | 2010-06-08 | C | 118 | 0.0040768 | 0.00037062
2011 | 2010-06-08 | C | 123 | 0.041723 | 0.00038632
2011 | 2010-06-08 | B | 24 | 0.016734 | 7.538e-05
2011 | 2010-06-08 | B | 24 | 0.01892 | 7.538e-05
2011 | 2010-06-07 | C | 15 | 0.040469 | 4.7112e-05
2011 | 2010-06-08 | B | 57 | 0.063913 | 0.00017903
2011 | 2010-06-08 | C | 40 | 0.013191 | 0.00012563
2011 | 2010-06-08 | C | 45 | 0.045652 | 0.00014134
2011 | 2010-06-08 | C | 81 | 0.011957 | 0.00025441
2011 | 2010-06-08 | B | 30 | 0.033638 | 9.4225e-05
2011 | 2010-06-08 | C | 18 | 0.0083106 | 5.6535e-05
2011 | 2010-06-09 | B | 40 | 0.0095481 | 0.00012563
2011 | 2010-06-09 | B | 56 | 0.060857 | 0.00017589
2011 | 2010-06-09 | B | 87 | 0.082249 | 0.00027325
2011 | 2010-06-09 | B | 3 | 0.0026854 | 9.4225e-06
2011 | 2010-06-09 | B | 69 | 0.033374 | 0.00021672
2011 | 2010-06-09 | B | 7 | 0.0027042 | 2.1986e-05
2011 | 2010-06-09 | C | 91.4871 | 0.16609 | 0.00058419
2011 | 2010-06-09 | C | 367.6271 | 0.26903 | 0.0042809
2011 | 2010-06-09 | B | 7 | 0.0075191 | 2.1986e-05
2011 | 2010-06-09 | B | 17 | 0.016712 | 5.3394e-05
2011 | 2010-06-09 | B | 5 | 0.0020101 | 1.5704e-05
2011 | 2010-06-10 | C | 54 | 0.016112 | 0.0001696
2011 | 2010-06-10 | C | 96.878 | 0.073939 | 0.0004774
2011 | 2010-06-10 | B | 63 | 0.030472 | 0.00019787
2011 | 2010-06-10 | B | 39 | 0.030011 | 0.00012249
2011 | 2010-06-10 | B | 108 | 0.12313 | 0.00033921
2011 | 2010-06-10 | C | 106.5564 | 0.085007 | 0.0010082
2011 | 2010-06-10 | B | 127 | 0.16953 | 0.00039888
2011 | 2010-06-10 | B | 44 | 0.060806 | 0.0001382
2011 | 2010-06-10 | B | 20.8238 | 0.026162 | 0.00036748
2011 | 2010-06-10 | C | 113.7959 | 0.016441 | 0.00059362
2011 | 2010-06-10 | C | 340.9725 | 0.26988 | 0.0019724
2011 | 2010-06-10 | C | 37.6116 | 0.099112 | 0.00078835
2011 | 2010-06-11 | C | 45 | 0.010883 | 0.00014134
2011 | 2010-06-11 | B | 3 | 0.003034 | 9.4225e-06
2011 | 2010-06-11 | C | 6 | 0.0013568 | 1.8845e-05
2011 | 2010-06-11 | C | 186.9252 | 0.061058 | 0.001071
2011 | 2010-06-11 | C | 23.913 | 0.025686 | 0.00028896
2011 | 2010-06-11 | C | 28 | 0.0051886 | 8.7943e-05
2011 | 2010-06-11 | C | 26 | 0.022457 | 8.1661e-05
2011 | 2010-06-12 | B | 1 | 0.00032979 | 3.1408e-06
2011 | 2010-06-12 | C | 292.7339 | 0.11125 | 0.0024561
2011 | 2010-06-12 | C | 76 | 0.0093094 | 0.0002387
2011 | 2010-06-12 | C | 55.8235 | 0.02928 | 0.00025127
2011 | 2010-06-12 | C | 86 | 0.059424 | 0.00027011
2011 | 2010-06-12 | B | 32 | 0.040303 | 0.00010051
2011 | 2010-06-13 | C | 115.2044 | 0.048486 | 0.00063131
2011 | 2010-06-13 | B | 7 | 0.010465 | 2.1986e-05
2011 | 2010-06-11 | C | 520.2587 | 0.65198 | 0.0038978
2011 | 2010-06-14 | C | 533.1293 | 0.18921 | 0.0028393
2011 | 2010-06-14 | B | 108 | 0.11499 | 0.00033921
2011 | 2010-06-14 | B | 12 | 0.0090456 | 3.769e-05
2011 | 2010-06-14 | C | 142.098 | 0.044184 | 0.0014605
2011 | 2010-06-14 | B | 18 | 0.013399 | 5.6535e-05
2011 | 2010-06-14 | B | 8 | 0.0059299 | 2.5127e-05
2011 | 2010-06-14 | C | 93.2941 | 0.029009 | 0.00035177
2011 | 2010-06-15 | C | 56 | 0.0068596 | 0.00017589
2011 | 2010-06-14 | C | 383.212 | 0.21785 | 0.0041113
2011 | 2010-06-15 | B | 41 | 0.017384 | 0.00012877
2011 | 2010-06-15 | B | 196 | 0.014159 | 0.0006156
2011 | 2010-06-15 | C | 2 | 0.0026509 | 6.2816e-06
2011 | 2010-06-15 | B | 66 | 0.052031 | 0.00020729
2011 | 2010-06-15 | C | 22 | 0.0029021 | 6.9098e-05
2011 | 2010-06-15 | B | 23 | 0.03034 | 7.2239e-05
2011 | 2010-06-15 | C | 56.6667 | 0.040045 | 0.00031722
2011 | 2010-06-16 | C | 184 | 0.026006 | 0.00057791
2011 | 2010-06-16 | C | 19 | 0.0014322 | 5.9676e-05
2011 | 2010-06-16 | B | 77 | 0.035551 | 0.00024184
2011 | 2010-06-16 | B | 13 | 0.0062879 | 4.0831e-05
2011 | 2010-06-16 | B | 59 | 0.043918 | 0.00018531
2011 | 2010-06-16 | B | 2 | 0.0015893 | 6.2816e-06
2011 | 2010-06-16 | C | 16 | 0.0016081 | 5.0253e-05
2011 | 2010-06-16 | C | 74 | 0.015107 | 0.00023242
2011 | 2010-06-16 | B | 30 | 0.025252 | 9.4225e-05
2011 | 2010-06-16 | B | 128.8213 | 0.1052 | 0.00062816
2011 | 2010-06-13 | B | 115 | 0.030702 | 0.00036119
2011 | 2010-06-16 | C | 139.1447 | 0.068176 | 0.00079463
2011 | 2010-06-16 | B | 4 | 0.0061811 | 1.2563e-05
2011 | 2010-06-16 | B | 167.0983 | 0.2388 | 0.0010867
2011 | 2010-06-16 | B | 41 | 0.0023179 | 0.00012877
2011 | 2010-06-16 | B | 9 | 0.0098088 | 2.8267e-05
2011 | 2010-06-16 | C | 5 | 0.0034863 | 1.5704e-05
2011 | 2010-06-02 | B | 156.95 | 0.028098 | 0.00067214
2011 | 2010-06-17 | C | 6 | 0.00022614 | 1.8845e-05
2011 | 2010-06-17 | C | 782 | 0.12035 | 0.0024561
2011 | 2010-06-17 | B | 15 | 0.015359 | 4.7112e-05
2011 | 2010-06-17 | B | 3 | 0.0036182 | 9.4225e-06
2011 | 2010-06-17 | B | 44 | 0.050856 | 0.0001382
2011 | 2010-06-17 | B | 53 | 0.013484 | 0.00016646
2011 | 2010-06-17 | B | 21 | 0.0087064 | 6.5957e-05
2011 | 2010-06-17 | B | 3 | 0.0028079 | 9.4225e-06
2011 | 2010-06-17 | B | 26 | 0.017884 | 8.1661e-05
2011 | 2010-06-16 | C | 249 | 0.013295 | 0.00078206
2011 | 2010-06-17 | C | 3 | 0.00030152 | 9.4225e-06
2011 | 2010-06-17 | C | 1 | 0.0001696 | 3.1408e-06
2011 | 2010-06-17 | C | 752 | 0.044876 | 0.0023619
2011 | 2010-06-18 | B | 29 | 0.0099281 | 9.1084e-05
2011 | 2010-06-18 | C | 61.3653 | 0.061676 | 0.00038632
2011 | 2010-06-17 | C | 175.1469 | 0.11442 | 0.00082918
2011 | 2010-06-18 | B | 1 | 0.00071611 | 3.1408e-06
2011 | 2010-06-18 | B | 6 | 0.0074626 | 1.8845e-05
2011 | 2010-06-18 | C | 12 | 0.0098747 | 3.769e-05
2011 | 2010-06-18 | B | 24 | 0.0064073 | 7.538e-05
2011 | 2010-06-18 | B | 196 | 0.30903 | 0.0006156
2011 | 2010-06-18 | C | 178.5875 | 0.088063 | 0.0010522
2011 | 2010-06-19 | C | 667 | 0.15083 | 0.0020949
2011 | 2010-06-19 | C | 378.2253 | 0.29698 | 0.00261
2011 | 2010-06-19 | C | 1816 | 0.43919 | 0.0057037
2011 | 2010-06-19 | B | 4 | 0.0024247 | 1.2563e-05
2011 | 2010-06-19 | B | 32 | 0.028242 | 0.00010051
2011 | 2010-06-20 | C | 77.4177 | 0.10115 | 0.00079463
2011 | 2010-06-20 | C | 155 | 0.05988 | 0.00048683
2011 | 2010-06-21 | C | 43.3287 | 0.048447 | 0.00054964
2011 | 2010-06-21 | B | 2 | 0.0022425 | 6.2816e-06
2011 | 2010-06-21 | C | 10 | 0.0015704 | 3.1408e-05
2011 | 2010-06-21 | B | 305.3282 | 0.24838 | 0.0011998
2011 | 2010-06-21 | B | 1 | 0.0011433 | 3.1408e-06
2011 | 2010-06-21 | B | 26 | 0.026867 | 8.1661e-05
2011 | 2010-06-13 | B | 2 | 0.00071611 | 6.2816e-06
2011 | 2010-06-22 | B | 14 | 0.0051447 | 4.3972e-05
2011 | 2010-06-22 | B | 59 | 0.015195 | 0.00018531
2011 | 2010-06-22 | B | 251.3495 | 0.078944 | 0.00085116
2011 | 2010-06-22 | C | 1 | 0.00030466 | 3.1408e-06
2011 | 2010-06-22 | B | 45 | 0.045369 | 0.00014134
2011 | 2010-06-22 | B | 94 | 0.10333 | 0.00029524
2011 | 2010-06-22 | B | 105.2549 | 0.13389 | 0.00055907
2011 | 2010-06-22 | C | 413 | 0.073938 | 0.0012972
2011 | 2010-06-22 | B | 43 | 0.062396 | 0.00013506
2011 | 2010-06-23 | B | 11 | 0.0053551 | 3.4549e-05
2011 | 2010-06-23 | B | 65.2583 | 0.048577 | 0.001049
2011 | 2010-06-23 | B | 75 | 0.073495 | 0.00023556
2011 | 2010-06-23 | C | 411 | 0.26076 | 0.0012909
2011 | 2010-06-23 | B | 15 | 0.018374 | 4.7112e-05
2011 | 2010-06-23 | B | 24 | 0.026157 | 7.538e-05
2011 | 2010-06-23 | C | 573.9333 | 0.12979 | 0.0047678
2011 | 2010-06-24 | B | 216 | 0.062414 | 0.00067842
2011 | 2010-06-24 | C | 8 | 0.0003769 | 2.5127e-05
2011 | 2010-06-24 | B | 34 | 0.016232 | 0.00010679
2011 | 2010-06-24 | B | 1 | 0.00049311 | 3.1408e-06
2011 | 2010-06-24 | B | 14 | 0.009322 | 4.3972e-05
2011 | 2010-06-24 | B | 145 | 0.043265 | 0.00045542
2011 | 2010-06-24 | B | 52 | 0.060756 | 0.00016332
2011 | 2010-06-24 | C | 163 | 0.02099 | 0.00051195
2011 | 2010-06-24 | C | 110.0632 | 0.064644 | 0.00056221
2011 | 2010-06-25 | B | 15 | 0.016819 | 4.7112e-05
2011 | 2010-06-25 | B | 52 | 0.010453 | 0.00016332
2011 | 2010-06-24 | C | 1546.8007 | 1.302 | 0.0087535
2011 | 2010-06-25 | C | 1 | 0.00053708 | 3.1408e-06
2011 | 2010-06-25 | C | 10 | 0.005465 | 3.1408e-05
2011 | 2010-06-25 | B | 94 | 0.057571 | 0.00029524
2011 | 2010-06-24 | C | 193 | 0.006668 | 0.00060618
2011 | 2010-06-25 | B | 36 | 0.0036182 | 0.00011307
2011 | 2010-06-25 | C | 63 | 0.010883 | 0.00019787
2011 | 2010-06-26 | C | 357.0462 | 0.21531 | 0.002051
2011 | 2010-06-25 | C | 1344 | 0.17729 | 0.0042213
2011 | 2010-06-26 | B | 68 | 0.010252 | 0.00021358
2011 | 2010-06-26 | C | 4 | 0.00059047 | 1.2563e-05
2011 | 2010-06-26 | C | 986 | 0.27872 | 0.0030969
2011 | 2010-06-26 | C | 23 | 0.0024561 | 7.2239e-05
2011 | 2010-06-27 | C | 15.1218 | 0.01819 | 0.00015704
2011 | 2010-06-27 | C | 2 | 0.0012438 | 6.2816e-06
2011 | 2010-06-27 | B | 22 | 0.0067716 | 6.9098e-05
2011 | 2010-06-26 | B | 2 | 0.0030089 | 6.2816e-06
2011 | 2010-06-28 | C | 753 | 0.089871 | 0.002365
2011 | 2010-06-25 | C | 1160 | 0.15302 | 0.0036434
2011 | 2010-06-28 | B | 3 | 0.0033638 | 9.4225e-06
2011 | 2010-06-28 | B | 2 | 0.002431 | 6.2816e-06
2011 | 2010-06-28 | C | 921 | 0.13306 | 0.0028927
2011 | 2010-06-28 | C | 171 | 0.042429 | 0.00053708
2011 | 2010-06-28 | B | 66 | 0.069444 | 0.00020729
2011 | 2010-06-28 | B | 7 | 0.0049688 | 2.1986e-05
2011 | 2010-06-28 | B | 58.389 | 0.072989 | 0.00047112
2011 | 2010-06-28 | C | 162 | 0.020861 | 0.00050881
2011 | 2010-06-28 | C | 8.7462 | 0.023625 | 0.00063445
2011 | 2010-06-28 | C | 53 | 0.0069915 | 0.00016646
2011 | 2010-06-22 | B | 63 | 0.066683 | 0.00019787
2011 | 2010-06-28 | B | 4 | 0.0014448 | 1.2563e-05
2011 | 2010-06-29 | B | 16 | 0.0088948 | 5.0253e-05
2011 | 2010-06-29 | B | 28.8484 | 0.033797 | 0.0003078
2011 | 2010-06-29 | C | 4 | 0.003568 | 1.2563e-05
2011 | 2010-06-29 | C | 8 | 0.0021106 | 2.5127e-05
2011 | 2010-06-29 | C | 94 | 0.020371 | 0.00029524
2011 | 2010-06-30 | B | 16 | 0.023569 | 5.0253e-05
2011 | 2010-06-30 | C | 106 | 0.0039951 | 0.00033293
2011 | 2010-06-30 | B | 37 | 0.013829 | 0.00011621
2011 | 2010-06-30 | B | 34 | 0.038337 | 0.00010679
2011 | 2010-06-29 | B | 127 | 0.14838 | 0.00039888
2011 | 2010-06-28 | B | 233 | 0.13099 | 0.00073181
2011 | 2010-06-30 | B | 51.3435 | 0.073212 | 0.00041459
2011 | 2010-07-01 | C | 63 | 0.01484 | 0.00019787
2011 | 2010-07-01 | B | 176 | 0.11553 | 0.00055278
2011 | 2010-07-01 | C | 116 | 0.027689 | 0.00036434
2011 | 2010-07-01 | C | 62 | 0.010126 | 0.00019473
2011 | 2010-07-01 | C | 556 | 0.029687 | 0.0017463
2011 | 2010-07-01 | B | 24 | 0.020503 | 7.538e-05
2011 | 2010-07-02 | B | 93 | 0.051409 | 0.0002921
2011 | 2010-07-02 | B | 66 | 0.038349 | 0.00020729
2011 | 2010-07-02 | B | 39 | 0.014822 | 0.00012249
2011 | 2010-07-02 | B | 49 | 0.041399 | 0.0001539
2011 | 2010-07-02 | B | 5 | 0.0030466 | 1.5704e-05
2011 | 2010-07-02 | C | 3 | 0.00070668 | 9.4225e-06
2011 | 2010-07-03 | C | 87.3784 | 0.060102 | 0.0012909
2011 | 2010-07-03 | C | 369.625 | 0.098679 | 0.0013945
2011 | 2010-07-03 | B | 31 | 0.0073024 | 9.7365e-05
2011 | 2010-07-04 | C | 188.6623 | 0.089476 | 0.0014636
2011 | 2010-07-04 | C | 208 | 0.024172 | 0.00065329
2011 | 2010-07-04 | C | 191.4615 | 0.037283 | 0.00060618
2011 | 2010-07-04 | B | 4 | 0.0047992 | 1.2563e-05
2011 | 2010-07-04 | C | 625 | 0.068705 | 0.001963
2011 | 2010-07-05 | C | 178.5246 | 0.032521 | 0.00056535
2011 | 2010-07-05 | C | 228.4732 | 0.078218 | 0.0010836
2011 | 2010-07-05 | C | 135 | 0.027985 | 0.00042401
2011 | 2010-07-05 | C | 25 | 0.0010208 | 7.8521e-05
2011 | 2010-07-05 | C | 239 | 0.097585 | 0.00075066
2011 | 2010-07-05 | B | 53 | 0.032294 | 0.00016646
2011 | 2010-07-05 | C | 1 | 0.00016332 | 3.1408e-06
2011 | 2010-07-05 | C | 326.6166 | 0.31801 | 0.0020447
2011 | 2010-07-05 | C | 26 | 0.02703 | 8.1661e-05
2011 | 2010-07-05 | C | 110.9818 | 0.075641 | 0.0019536
2011 | 2010-07-05 | C | 13 | 0.0021232 | 4.0831e-05
2011 | 2010-07-05 | C | 4 | 0.002475 | 1.2563e-05
2011 | 2010-07-05 | C | 208 | 0.021559 | 0.00065329
2011 | 2010-07-05 | C | 89.9703 | 0.28456 | 0.0027953
2011 | 2010-07-06 | B | 109 | 0.11058 | 0.00034235
2011 | 2010-07-06 | B | 5 | 0.0048997 | 1.5704e-05
2011 | 2010-07-06 | C | 36 | 0.011533 | 0.00011307
2011 | 2010-07-06 | C | 42 | 0.0063319 | 0.00013191
2011 | 2010-07-06 | C | 17 | 0.0077421 | 5.3394e-05
2011 | 2010-07-07 | B | 11 | 0.0062534 | 3.4549e-05
2011 | 2010-07-07 | B | 5 | 0.0065486 | 1.5704e-05
2011 | 2010-07-07 | C | 543 | 0.028993 | 0.0017055
2011 | 2010-07-08 | C | 117.5385 | 0.046884 | 0.0011213
2011 | 2010-07-08 | B | 79 | 0.063272 | 0.00024812
2011 | 2010-07-08 | C | 244.6296 | 0.01844 | 0.0007695
2011 | 2010-07-08 | C | 1 | 0.00015076 | 3.1408e-06
2011 | 2010-07-08 | C | 12 | 0.001696 | 3.769e-05
2011 | 2010-07-08 | B | 29.8351 | 0.036077 | 0.00031408
2011 | 2010-07-08 | C | 11 | 0.0058388 | 3.4549e-05
2011 | 2010-07-09 | C | 10 | 0.0011307 | 3.1408e-05
2011 | 2010-07-09 | B | 99 | 0.058457 | 0.00031094
2011 | 2010-07-09 | B | 73 | 0.042646 | 0.00022928
2011 | 2010-07-09 | B | 292 | 0.34392 | 0.00091712
2011 | 2010-07-09 | C | 116.2174 | 0.040882 | 0.00059362
2011 | 2010-07-09 | C | 32.142 | 0.017465 | 0.00059676
2011 | 2010-07-09 | B | 10 | 0.014668 | 3.1408e-05
2011 | 2010-07-10 | C | 680.5 | 0.32274 | 0.0031722
2011 | 2010-07-10 | C | 77 | 0.070135 | 0.00024184
2011 | 2010-07-10 | C | 5.3867 | 0.0012181 | 1.8845e-05
2011 | 2010-07-11 | C | 5.5215 | 0.0027747 | 1.8845e-05
2011 | 2010-07-12 | B | 29 | 0.01512 | 9.1084e-05
2011 | 2010-07-12 | B | 7 | 0.0025723 | 2.1986e-05
2011 | 2010-07-12 | C | 192.5 | 0.012697 | 0.00063759
2011 | 2010-07-12 | C | 311.4752 | 0.39229 | 0.0041647
2011 | 2010-07-12 | C | 4.9059 | 0.0043761 | 1.8845e-05
2011 | 2010-07-13 | B | 292 | 0.34851 | 0.00091712
2011 | 2010-07-13 | B | 3 | 0.0027608 | 9.4225e-06
2011 | 2010-07-13 | B | 139 | 0.086442 | 0.00043657
2011 | 2010-07-13 | C | 6 | 0.0011119 | 1.8845e-05
2011 | 2010-07-13 | C | 80 | 0.025629 | 0.00025127
2011 | 2010-07-13 | C | 6 | 0.00043343 | 1.8845e-05
2011 | 2010-07-13 | C | 5173.3415 | 0.61744 | 0.018
2011 | 2010-07-13 | B | 36 | 0.0031659 | 0.00011307
2011 | 2010-07-14 | B | 21 | 0.019062 | 0
2011 | 2010-07-14 | B | 19 | 0.021006 | 5.9676e-05
2011 | 2010-07-14 | B | 1 | 0.00079149 | 3.1408e-06
2011 | 2010-07-14 | B | 6 | 0.005107 | 1.8845e-05
2011 | 2010-07-14 | C | 161.0211 | 0.16588 | 0.0019787
2011 | 2010-07-15 | C | 155 | 0.090063 | 0.00048683
2011 | 2010-07-14 | C | 256.9063 | 0.26466 | 0.0021232
2011 | 2010-07-15 | C | 410 | 0.273 | 0.0012877
2011 | 2010-07-15 | B | 63 | 0.037991 | 0.00019787
2011 | 2010-07-15 | B | 11 | 0.0086718 | 3.4549e-05
2011 | 2010-07-15 | B | 86 | 0.077522 | 0.00027011
2011 | 2010-07-15 | B | 6 | 0.00571 | 1.8845e-05
2011 | 2010-07-15 | C | 281 | 0.036185 | 0.00088257
2011 | 2010-07-15 | C | 215.7184 | 0.067753 | 0.00075694
2011 | 2010-07-15 | C | 76 | 0.023393 | 0.0002387
2011 | 2010-07-15 | B | 56 | 0.11257 | 0.00017589
2011 | 2010-07-15 | C | 30 | 0.0061246 | 9.4225e-05
2011 | 2010-07-16 | C | 57.4788 | 0.063186 | 0.00024498
2011 | 2010-07-16 | B | 36 | 0.008141 | 0.00011307
2011 | 2010-07-16 | B | 22 | 0.015754 | 6.9098e-05
2011 | 2010-07-14 | B | 21 | 0.0021106 | 6.5957e-05
2011 | 2010-07-09 | B | 5 | 0.0032508 | 1.5704e-05
2011 | 2010-07-09 | B | 1 | 0.00027325 | 3.1408e-06
2011 | 2010-07-16 | B | 2 | 0.0018656 | 6.2816e-06
2011 | 2010-07-16 | B | 7 | 0.0058702 | 2.1986e-05
2011 | 2010-07-16 | C | 13 | 0.0023273 | 4.0831e-05
2011 | 2010-07-16 | C | 311 | 0.25885 | 0.0009768
2011 | 2010-07-16 | C | 12 | 0.00045228 | 3.769e-05
2011 | 2010-07-16 | C | 162 | 0.022388 | 0.00050881
2011 | 2010-07-16 | C | 212.7333 | 0.088197 | 0.00084802
2011 | 2010-07-17 | C | 1 | 0.00016018 | 3.1408e-06
2011 | 2010-07-17 | C | 16 | 0.003568 | 5.0253e-05
2011 | 2010-07-18 | C | 73 | 0.070389 | 0.00022928
2011 | 2010-07-19 | B | 8 | 0.0035177 | 2.5127e-05
2011 | 2010-07-20 | C | 111 | 0.013597 | 0.00034863
2011 | 2010-07-19 | B | 8 | 0.0004774 | 2.5127e-05
2011 | 2010-07-19 | B | 5 | 0.0024027 | 1.5704e-05
2011 | 2010-07-20 | B | 25 | 0.029524 | 7.8521e-05
2011 | 2010-07-20 | B | 65 | 0.021436 | 0.00020415
2011 | 2010-07-20 | B | 61 | 0.055561 | 0.00019159
2011 | 2010-07-20 | B | 19 | 0.010384 | 5.9676e-05
2011 | 2010-07-20 | C | 135 | 0.019929 | 0.00042401
2011 | 2010-07-20 | C | 189.3846 | 0.06781 | 0.00063131
2011 | 2010-07-20 | C | 201 | 0.0025252 | 0.00063131
2011 | 2010-07-20 | B | 19 | 0.017724 | 5.9676e-05
2011 | 2010-07-21 | B | 42 | 0.056855 | 0.00013191
2011 | 2010-07-21 | B | 58 | 0.061026 | 0.00018217
2011 | 2010-07-21 | B | 1 | 0.00035177 | 3.1408e-06
2011 | 2010-07-21 | C | 16 | 0.0027137 | 5.0253e-05
2011 | 2010-07-21 | C | 6 | 0.0013003 | 1.8845e-05
2011 | 2010-07-21 | C | 117.0851 | 0.033465 | 0.00040203
2011 | 2010-07-21 | C | 7 | 0.015896 | 2.1986e-05
2011 | 2010-07-22 | B | 145 | 0.037344 | 0.00045542
2011 | 2010-07-22 | C | 8 | 0.0013317 | 2.5127e-05
2011 | 2010-07-22 | C | 330 | 0.26015 | 0.0010365
2011 | 2010-07-22 | C | 165 | 0.0015547 | 0.00051824
2011 | 2010-07-22 | B | 4 | 0.0017212 | 1.2563e-05
2011 | 2010-07-22 | C | 447.6652 | 0.30652 | 0.0039951
2011 | 2010-07-23 | B | 242 | 0.018242 | 0.00076008
2011 | 2010-07-23 | C | 287 | 0.0045071 | 0.00090142
2011 | 2010-07-22 | B | 18 | 0.0050881 | 5.6535e-05
2011 | 2010-07-23 | B | 242 | 0.018242 | 0.00076008
2011 | 2010-07-23 | C | 156 | 0.021069 | 0.00048997
2011 | 2010-07-23 | C | 172 | 0.1021 | 0.00054022
2011 | 2010-07-23 | C | 6 | 0.0044851 | 1.8845e-05
2011 | 2010-07-23 | C | 172 | 0.021609 | 0.00054022
2011 | 2010-07-23 | C | 38 | 0.0025064 | 0.00011935
2011 | 2010-07-23 | C | 31 | 0.00019473 | 9.7365e-05
2011 | 2010-07-23 | C | 142.4471 | 0.036687 | 0.0007538
2011 | 2010-07-23 | C | 6 | 0.012456 | 1.8845e-05
2011 | 2010-07-24 | C | 18.7172 | 0.0056436 | 5.9676e-05
2011 | 2010-07-24 | C | 9 | 0.002855 | 2.8267e-05
2011 | 2010-07-24 | B | 1 | 0.00028581 | 3.1408e-06
2011 | 2010-07-24 | B | 12 | 0.0015076 | 3.769e-05
2011 | 2010-07-23 | C | 140 | 0.022865 | 0.00043972
2011 | 2010-07-23 | C | 47.8908 | 0.14696 | 0.00044286
2011 | 2010-07-24 | C | 170 | 0.030969 | 0.00053394
2011 | 2010-07-24 | B | 179 | 0.031484 | 0.00056221
2011 | 2010-07-25 | C | 279.3704 | 0.11582 | 0.0018123
2011 | 2010-07-25 | C | 73.8571 | 0.046394 | 0.00025441
2011 | 2010-07-25 | C | 215.4167 | 0.095399 | 0.0008229
2011 | 2010-07-25 | C | 12 | 0.0044097 | 3.769e-05
2011 | 2010-07-26 | B | 12 | 0.0024875 | 3.769e-05
2011 | 2010-07-26 | B | 100 | 0.039574 | 0.00031408
2011 | 2010-07-26 | B | 26 | 0.017312 | 8.1661e-05
2011 | 2010-07-26 | B | 49 | 0.051095 | 0.0001539
2011 | 2010-07-26 | B | 79 | 0.020842 | 0.00024812
2011 | 2010-07-26 | B | 5 | 0.0051038 | 1.5704e-05
2011 | 2010-07-26 | C | 15 | 0.012438 | 4.7112e-05
2011 | 2010-07-26 | C | 83 | 0.00078206 | 0.00026069
2011 | 2010-07-27 | B | 33 | 0.0071517 | 0.00010365
2011 | 2010-07-26 | B | 339 | 0.15652 | 0.0010647
2011 | 2010-07-27 | C | 3 | 0.0002921 | 9.4225e-06
2011 | 2010-07-27 | B | 526 | 0.13051 | 0.0016521
2011 | 2010-07-27 | C | 123 | 0.00038632 | 0.00038632
2011 | 2010-07-27 | B | 1 | 0.00042401 | 3.1408e-06
2011 | 2010-07-27 | B | 3 | 0.0016301 | 9.4225e-06
2011 | 2010-07-27 | B | 99 | 0.076492 | 0.00031094
2011 | 2010-07-27 | B | 17 | 0.0057665 | 5.3394e-05
2011 | 2010-07-27 | C | 163.9237 | 0.26824 | 0.0005308
2011 | 2010-07-27 | C | 421 | 0.052891 | 0.0013223
2011 | 2010-07-27 | C | 108.301 | 0.06565 | 0.00048683
2011 | 2010-07-27 | C | 179.0126 | 0.13213 | 0.002274
2011 | 2010-07-27 | C | 190.9565 | 0.053379 | 0.00077892
2011 | 2010-07-27 | C | 56 | 0.0051007 | 0.00017589
2011 | 2010-07-27 | B | 362 | 0.096643 | 0.001137
2011 | 2010-07-27 | C | 717 | 0.0045039 | 0.002252
2011 | 2010-07-28 | C | 8 | 0.0015578 | 2.5127e-05
2011 | 2010-07-28 | C | 6 | 0.0022237 | 1.8845e-05
2011 | 2010-07-28 | B | 42 | 0.052502 | 0.00013191
2011 | 2010-07-28 | B | 52 | 0.0094727 | 0.00016332
2011 | 2010-07-29 | C | 260.1 | 0.062903 | 0.00096423
2011 | 2010-07-29 | B | 46 | 0.010258 | 0.00014448
2011 | 2010-07-29 | B | 23 | 0.03193 | 7.2239e-05
2011 | 2010-07-29 | B | 24 | 0.027287 | 7.538e-05
2011 | 2010-07-29 | B | 3 | 0.001027 | 9.4225e-06
2011 | 2010-07-29 | B | 95.6593 | 0.094341 | 0.0008543
2011 | 2010-07-29 | C | 843.4906 | 0.13246 | 0.0026917
2011 | 2010-07-29 | B | 7 | 0.0019567 | 2.1986e-05
2011 | 2010-07-30 | C | 189 | 0.11516 | 0.00059362
2011 | 2010-07-30 | B | 6 | 0.0077076 | 1.8845e-05
2011 | 2010-07-30 | B | 1 | 0.0010019 | 3.1408e-06
2011 | 2010-07-30 | B | 227 | 0.027093 | 0.00071297
2011 | 2010-07-30 | C | 98 | 0.034166 | 0.0003078
2011 | 2010-07-30 | C | 970 | 0.060932 | 0.0030466
2011 | 2010-07-30 | C | 123.9879 | 0.095409 | 0
2011 | 2010-07-31 | C | 651.2703 | 0.14523 | 0.0023964
2011 | 2010-07-31 | C | 90.75 | 0.077813 | 0.0004617
2011 | 2010-07-31 | B | 3 | 0.00074437 | 9.4225e-06
2011 | 2010-07-31 | C | 13 | 0.0011024 | 4.0831e-05
2011 | 2010-07-31 | C | 152 | 0.045831 | 0.0004774
2011 | 2010-08-01 | B | 31 | 0.0017526 | 9.7365e-05
2011 | 2010-08-01 | C | 30 | 0.0038632 | 9.4225e-05
2011 | 2010-08-01 | C | 90.7925 | 0.044485 | 0.00056535
2011 | 2010-08-01 | C | 337.2414 | 0.24256 | 0.0023368
2011 | 2010-08-01 | C | 1097 | 0.093028 | 0.0034455
2011 | 2010-08-01 | C | 236 | 0.028908 | 0.00074123
2011 | 2010-08-01 | C | 50 | 0.010993 | 0.00015704
2011 | 2010-08-01 | B | 11 | 0.0024875 | 3.4549e-05
2011 | 2010-08-01 | C | 161.9355 | 0.045775 | 0.00058105
2011 | 2010-08-01 | C | 29 | 0.053557 | 9.1084e-05
2011 | 2010-08-02 | C | 3 | 0.00045228 | 9.4225e-06
2011 | 2010-08-02 | C | 12 | 0.012362 | 3.769e-05
2011 | 2010-08-02 | C | 14 | 0.0019787 | 4.3972e-05
2011 | 2010-08-02 | C | 84 | 0.014511 | 0.00026383
2011 | 2010-08-02 | C | 12 | 0.0044851 | 3.769e-05
2011 | 2010-08-02 | C | 5 | 0.00045542 | 1.5704e-05
2011 | 2010-08-02 | C | 67 | 0.017045 | 0.00021044
2011 | 2010-08-02 | C | 149.2208 | 0.034682 | 0
2011 | 2010-08-02 | B | 132.488 | 0.17269 | 0.00064701
2011 | 2010-08-03 | C | 24 | 0.0016584 | 7.538e-05
2011 | 2010-08-03 | C | 6 | 0.00079149 | 1.8845e-05
2011 | 2010-08-03 | B | 205 | 0.13264 | 0.00064387
2011 | 2010-08-04 | B | 62.5221 | 0.043791 | 0.00038004
2011 | 2010-08-04 | C | 110.3415 | 0.027378 | 0.00035805
2011 | 2010-08-04 | B | 23 | 0.028173 | 7.2239e-05
2011 | 2010-08-04 | C | 617 | 0.052323 | 0.0024655
2011 | 2010-08-04 | C | 18 | 0.0019787 | 5.6535e-05
2011 | 2010-08-04 | C | 17.437 | 0.026781 | 0.00048683
2011 | 2010-08-03 | C | 1058 | 0.1595 | 0.003323
2011 | 2010-08-03 | C | 241.1634 | 0.15073 | 0.0012563
2011 | 2010-08-03 | C | 10.7189 | 0.0072046 | 6.2816e-05
2011 | 2010-08-03 | C | 1497.0165 | 2.5484 | 0.0082384
2011 | 2010-08-04 | C | 16 | 0.003367 | 5.0253e-05
2011 | 2010-08-04 | C | 23 | 0.0072239 | 7.2239e-05
2011 | 2010-08-04 | B | 7 | 0.0042213 | 2.1986e-05
2011 | 2010-08-04 | B | 4 | 0.0014699 | 1.2563e-05
2011 | 2010-08-05 | B | 118 | 0.038915 | 0.00037062
2011 | 2010-08-05 | C | 75 | 0.035334 | 0.00023556
2011 | 2010-08-05 | B | 94 | 0.11012 | 0.00029524
2011 | 2010-08-05 | B | 182.5094 | 0.059043 | 0.0005999
2011 | 2010-08-05 | B | 99 | 0.083021 | 0.00031094
2011 | 2010-08-06 | C | 342.3568 | 0.1957 | 0.001583
2011 | 2010-08-06 | B | 16 | 0.0020101 | 5.0253e-05
2011 | 2010-08-06 | C | 64 | 0.01588 | 0.00020101
2011 | 2010-08-06 | C | 73 | 0.0094005 | 0.00022928
2011 | 2010-08-06 | C | 312 | 0.11563 | 0.00097994
2011 | 2010-08-06 | B | 8 | 0.0034423 | 2.5127e-05
2011 | 2010-08-06 | B | 5 | 0.0020572 | 1.5704e-05
2011 | 2010-08-06 | B | 9 | 0.0031942 | 2.8267e-05
2011 | 2010-08-06 | B | 35 | 0.039354 | 0.00010993
2011 | 2010-08-07 | C | 448.5446 | 0.15356 | 0.0014165
2011 | 2010-08-07 | C | 273 | 0.011147 | 0.00085744
2011 | 2010-08-07 | C | 187.7339 | 0.071346 | 0.001382
2011 | 2010-08-07 | C | 128.7788 | 0.086557 | 0
2011 | 2010-08-07 | C | 197.48 | 0.060164 | 0.00080719
2011 | 2010-08-06 | C | 99.5934 | 0.094467 | 0.00080091
2011 | 2010-08-07 | B | 53 | 0.0049939 | 0.00016646
2011 | 2010-08-07 | C | 228 | 0.021483 | 0.00071611
2011 | 2010-08-06 | C | 274.8095 | 0.16054 | 0.00092968
2011 | 2010-08-08 | C | 242.7778 | 0.011438 | 0.00077264
2011 | 2010-08-07 | C | 55.3759 | 0.13966 | 0.0010459
2011 | 2010-08-07 | C | 101 | 0.063762 | 0.00031722
2011 | 2010-08-07 | C | 259 | 0.012202 | 0.00081347
2011 | 2010-08-08 | C | 4954 | 0.031119 | 0.01556
2011 | 2010-08-08 | C | 93.8844 | 0.050129 | 0.00075066
2011 | 2010-08-08 | C | 20 | 0.0033293 | 6.2816e-05
2011 | 2010-08-08 | C | 288.7033 | 0.24483 | 0.0028173
2011 | 2010-08-08 | C | 240 | 0.012815 | 0.0007538
2011 | 2010-08-08 | C | 236 | 0.0088948 | 0.00074123
2011 | 2010-08-07 | C | 102 | 0.015057 | 0.00032036
2011 | 2010-08-08 | C | 1 | 0.0033513 | 3.1408e-06
2011 | 2010-08-09 | B | 205 | 0.10817 | 0.00064387
2011 | 2010-08-09 | C | 380 | 0.051321 | 0.0011935
2011 | 2010-08-09 | C | 81.6593 | 0.30033 | 0.0042307
2011 | 2010-08-10 | C | 282 | 0.015057 | 0.00088571
2011 | 2010-08-10 | C | 128 | 0.0068344 | 0.00040203
2011 | 2010-08-10 | B | 6 | 0.0016772 | 1.8845e-05
2011 | 2010-08-10 | B | 107 | 0.071246 | 0.00033607
2011 | 2010-08-10 | B | 76.5526 | 0.090645 | 0.00041773
2011 | 2010-08-11 | C | 3238.3636 | 0.081369 | 0.012714
2011 | 2010-08-11 | B | 113 | 0.14977 | 0.00035491
2011 | 2010-08-11 | C | 212.4527 | 0.096755 | 0.0028142
2011 | 2010-08-11 | B | 141 | 0.036314 | 0.00044286
2011 | 2010-08-11 | C | 64 | 0.0054273 | 0.00020101
2011 | 2010-08-12 | C | 19 | 0.0082949 | 5.9676e-05
2011 | 2010-08-12 | B | 39 | 0.022049 | 0.00012249
2011 | 2010-08-12 | B | 7 | 0.0058042 | 2.1986e-05
2011 | 2010-08-12 | B | 6 | 0.00069726 | 1.8845e-05
2011 | 2010-08-12 | B | 105 | 0.11773 | 0.00032979
2011 | 2010-08-13 | B | 3 | 0.0003769 | 9.4225e-06
2011 | 2010-08-13 | C | 137 | 0.007315 | 0.00043029
2011 | 2010-08-13 | C | 26 | 0.011678 | 8.1661e-05
2011 | 2010-08-13 | C | 66 | 0.021973 | 0.00020729
2011 | 2010-08-13 | C | 201.7668 | 0.17744 | 0.0021044
2011 | 2010-08-13 | C | 144.063 | 0.11357 | 0.00068784
2011 | 2010-08-13 | C | 727.0707 | 0.21923 | 0.0030089
2011 | 2010-08-13 | C | 105 | 0.0465 | 0.00098936
2011 | 2010-08-13 | C | 73 | 0.0084834 | 0.00022928
2011 | 2010-08-14 | C | 220.2727 | 0.028365 | 0.00074437
2011 | 2010-08-13 | C | 371 | 0.020974 | 0.0011652
2011 | 2010-08-13 | C | 92.0971 | 0.079547 | 0.00041459
2011 | 2010-08-14 | C | 80.9119 | 0.065565 | 0.00045856
2011 | 2010-08-14 | C | 86 | 0.17611 | 0.00027011
2011 | 2010-08-13 | C | 10 | 0.0019159 | 3.1408e-05
2011 | 2010-08-13 | C | 121.12 | 0.055921 | 0.00060304
2011 | 2010-08-13 | C | 128.4865 | 0.058515 | 0.0010899
2011 | 2010-08-14 | C | 230 | 0.014448 | 0.00072239
2011 | 2010-08-13 | C | 201.4773 | 0.65432 | 0.00074123
2011 | 2010-08-14 | C | 56.6809 | 0.032935 | 0.00033293
2011 | 2010-08-14 | C | 104.9848 | 0.10782 | 0.0004617
2011 | 2010-08-14 | C | 230 | 0.0050567 | 0.00072239
2011 | 2010-08-15 | C | 216 | 0.14722 | 0.00067842
2011 | 2010-08-16 | C | 44 | 0.0045605 | 0.0001382
2011 | 2010-08-16 | B | 23 | 0.023839 | 7.2239e-05
2011 | 2010-08-16 | B | 12 | 0.004372 | 3.769e-05
2011 | 2010-08-16 | C | 34 | 0.0049122 | 0.00010679
2011 | 2010-08-17 | B | 25 | 0.010443 | 7.8521e-05
2011 | 2010-08-11 | B | 31 | 0.02697 | 9.7365e-05
2011 | 2010-08-17 | B | 25 | 0.015626 | 7.8521e-05
2011 | 2010-08-17 | B | 59 | 0.0391 | 0.00018531
2011 | 2010-08-17 | B | 94 | 0.11573 | 0.00029524
2011 | 2010-08-17 | B | 45 | 0.046783 | 0.00014134
2011 | 2010-08-17 | C | 9 | 0.00065015 | 2.8267e-05
2011 | 2010-08-17 | B | 118.5619 | 0.14337 | 0.00069412
2011 | 2010-08-17 | B | 21 | 0.021172 | 6.5957e-05
2011 | 2010-08-17 | C | 8 | 0.0029398 | 2.5127e-05
2011 | 2010-08-17 | C | 13 | 0.018251 | 4.0831e-05
2011 | 2010-08-18 | C | 62.092 | 0.067282 | 0.00051195
2011 | 2010-08-17 | C | 101 | 0.0050756 | 0.00031722
2011 | 2010-08-18 | C | 38 | 0.0015516 | 0.00011935
2011 | 2010-08-18 | B | 32 | 0.013568 | 0.00010051
2011 | 2010-08-18 | B | 6 | 0.0073307 | 1.8845e-05
2011 | 2010-08-18 | B | 359 | 0.16688 | 0.0011276
2011 | 2010-08-18 | B | 382 | 0.31195 | 0.0011998
2011 | 2010-08-18 | B | 14 | 0.0080468 | 4.3972e-05
2011 | 2010-08-17 | B | 23 | 0.022539 | 7.2239e-05
2011 | 2010-08-17 | B | 102 | 0.11629 | 0.00032036
2011 | 2010-08-19 | B | 173 | 0.033688 | 0.00054336
2011 | 2010-08-19 | B | 38 | 0.015635 | 0.00011935
2011 | 2010-08-19 | C | 1 | 9.7365e-05 | 3.1408e-06
2011 | 2010-08-20 | C | 156.7607 | 0.3092 | 0.0023462
2011 | 2010-08-20 | C | 16 | 0.012111 | 5.0253e-05
2011 | 2010-08-20 | C | 122.2743 | 0.066055 | 0.0011087
2011 | 2010-08-20 | C | 20 | 0.0050253 | 6.2816e-05
2011 | 2010-08-20 | C | 278.9769 | 0.11128 | 0.0013129
2011 | 2010-08-21 | B | 1 | 0.00019159 | 3.1408e-06
2011 | 2010-08-21 | C | 814.7214 | 0.91097 | 0.0030623
2011 | 2010-08-22 | C | 224.2609 | 0.25709 | 0.0017871
2011 | 2010-08-22 | C | 556.4528 | 0.087386 | 0.0017966
2011 | 2010-08-23 | B | 8 | 0.0041961 | 2.5127e-05
2011 | 2010-08-23 | B | 22 | 0.0096737 | 6.9098e-05
2011 | 2010-08-23 | B | 3 | 0.00096109 | 9.4225e-06
2011 | 2010-08-23 | B | 14 | 0.015478 | 4.3972e-05
2011 | 2010-08-24 | C | 70.6667 | 0.11519 | 0.00035177
2011 | 2010-08-23 | B | 9 | 0.0024593 | 2.8267e-05
2011 | 2010-08-24 | B | 76 | 0.030077 | 0.0002387
2011 | 2010-08-24 | C | 95 | 0.062361 | 0.00048683
2011 | 2010-08-24 | C | 2601 | 0.38396 | 0.0081693
2011 | 2010-08-24 | C | 80 | 0.014573 | 0.00025127
2011 | 2010-08-24 | C | 40 | 0.007538 | 0.00012563
2011 | 2010-08-24 | B | 99 | 0.11132 | 0.00031094
2011 | 2010-08-24 | B | 185 | 0.21557 | 0.00058105
2011 | 2010-08-24 | B | 58 | 0.053922 | 0.00018217
2011 | 2010-08-24 | B | 53.9372 | 0.064205 | 0.00032036
2011 | 2010-08-24 | B | 82 | 0.091429 | 0.00025755
2011 | 2010-08-24 | B | 4 | 0.0037815 | 1.2563e-05
2011 | 2010-08-24 | C | 5.2795 | 0.017394 | 4.3972e-05
2011 | 2010-08-24 | C | 21 | 0.0037596 | 6.5957e-05
2011 | 2010-08-25 | C | 15 | 0.00094225 | 4.7112e-05
2011 | 2010-08-25 | B | 5 | 0.001382 | 1.5704e-05
2011 | 2010-08-25 | B | 26 | 0.023845 | 8.1661e-05
2011 | 2010-08-25 | B | 89 | 0.0086655 | 0.00027953
2011 | 2010-08-25 | C | 198.3423 | 0.090952 | 0.00083232
2011 | 2010-08-26 | C | 24 | 0.0045228 | 7.538e-05
2011 | 2010-08-26 | C | 557 | 0.10147 | 0.0017494
2011 | 2010-08-26 | C | 226.9805 | 0.10765 | 0.0011181
2011 | 2010-08-26 | B | 32 | 0.033971 | 0.00010051
2011 | 2010-08-26 | B | 2 | 0.00174 | 6.2816e-06
2011 | 2010-08-26 | B | 2 | 0.001985 | 6.2816e-06
2011 | 2010-08-26 | B | 4 | 0.0043972 | 1.2563e-05
2011 | 2010-08-26 | B | 115.871 | 0.14848 | 0.0007004
2011 | 2010-08-27 | B | 9 | 0.0057948 | 2.8267e-05
2011 | 2010-08-27 | B | 1 | 0.00025755 | 3.1408e-06
2011 | 2010-08-28 | C | 136.5588 | 0.11538 | 0.0009077
2011 | 2010-08-28 | C | 66 | 0.010987 | 0.00020729
2011 | 2010-08-28 | B | 52 | 0.055693 | 0.00016332
2011 | 2010-08-29 | C | 99.6233 | 0.20839 | 0.00060932
2011 | 2010-08-29 | C | 264 | 0.010779 | 0.00082918
2011 | 2010-08-29 | C | 28 | 0.0070354 | 8.7943e-05
2011 | 2010-08-29 | C | 16.9741 | 0.010129 | 7.538e-05
2011 | 2010-08-29 | C | 219.9101 | 0.36676 | 0.0035491
2011 | 2010-08-30 | C | 1 | 0.00011621 | 3.1408e-06
2011 | 2010-08-30 | B | 43 | 0.029982 | 0.00013506
2011 | 2010-08-30 | C | 201.0839 | 0.095998 | 0.00084802
2011 | 2010-08-31 | C | 180 | 0.0073495 | 0.00056535
2011 | 2010-08-31 | C | 32 | 0.039499 | 0.00010051
2011 | 2010-08-31 | B | 45 | 0.049327 | 0.00014134
2011 | 2010-08-31 | B | 33 | 0.0098465 | 0.00010365
2011 | 2010-08-31 | B | 23 | 0.01806 | 7.2239e-05
2011 | 2010-08-31 | C | 364.3878 | 0.10873 | 0.0014165
2011 | 2010-08-31 | C | 56.8204 | 0.057108 | 0.00035805
2011 | 2010-08-31 | C | 257 | 0.039552 | 0.00080719
2011 | 2010-09-01 | B | 32 | 0.026333 | 0.00010051
2011 | 2010-09-01 | B | 82 | 0.059493 | 0.00025755
2011 | 2010-09-01 | B | 4 | 0.0043972 | 1.2563e-05
2011 | 2010-09-01 | B | 2 | 0.00079777 | 6.2816e-06
2011 | 2010-09-02 | C | 79 | 0.0024812 | 0.00024812
2011 | 2010-09-02 | B | 18 | 0.0091021 | 5.6535e-05
2011 | 2010-09-02 | B | 7 | 0.0017589 | 2.1986e-05
2011 | 2010-09-02 | C | 99.52 | 0.045948 | 0.00053708
2011 | 2010-09-02 | B | 29 | 0.042809 | 9.1084e-05
2011 | 2010-09-02 | C | 332.8235 | 0.014635 | 0.0010836
2011 | 2010-09-02 | C | 94.9657 | 0.068602 | 0.00089199
2011 | 2010-09-02 | C | 75 | 0.010836 | 0.00023556
2011 | 2010-09-02 | C | 42 | 0.041817 | 0.00017903
2011 | 2010-09-02 | C | 97 | 0.041738 | 0.00030466
2011 | 2010-09-02 | C | 172.6239 | 0.061809 | 0.001338
2011 | 2010-09-02 | B | 709 | 0.14252 | 0.0022268
2011 | 2010-09-03 | B | 7 | 0.0038255 | 2.1986e-05
2011 | 2010-09-03 | B | 11 | 0.0069789 | 3.4549e-05
2011 | 2010-09-03 | C | 21 | 0.00079149 | 6.5957e-05
2011 | 2010-09-03 | C | 34.6414 | 0.01545 | 0.0004774
2011 | 2010-09-03 | C | 96 | 0.011156 | 0.00030152
2011 | 2010-09-03 | C | 74 | 0.0083671 | 0.00023242
2011 | 2010-09-03 | C | 7 | 0.0016489 | 2.1986e-05
2011 | 2010-09-03 | C | 282.782 | 0.18474 | 0.0027828
2011 | 2010-09-03 | C | 67.2759 | 0.036133 | 0.0012281
2011 | 2010-09-04 | B | 203 | 0.030604 | 0.00063759
2011 | 2010-09-04 | B | 203 | 0.036342 | 0.00063759
2011 | 2010-09-03 | C | 80.1351 | 0.20412 | 0.000446
2011 | 2010-09-04 | C | 516 | 0.33548 | 0.0016207
2011 | 2010-09-04 | C | 56 | 0.030956 | 0.00017589
2011 | 2010-09-04 | C | 83.0643 | 0.080354 | 0.00095167
2011 | 2010-09-04 | C | 103.2203 | 0.07262 | 0.00049939
2011 | 2010-09-04 | C | 3 | 0.030171 | 9.4225e-06
2011 | 2010-09-04 | C | 38.2222 | 0.10012 | 0.0003769
2011 | 2010-09-05 | C | 610.2316 | 0.17633 | 0.0025661
2011 | 2010-09-05 | C | 43 | 0.017152 | 0.00013506
2011 | 2010-09-05 | C | 106 | 0.06825 | 0.00033293
2011 | 2010-09-05 | C | 26 | 0.11163 | 8.1661e-05
2011 | 2010-09-05 | C | 303 | 0.0076134 | 0.00095167
2011 | 2010-09-05 | C | 34.7826 | 0.12782 | 0.0003926
2011 | 2010-09-05 | C | 373 | 0.04569 | 0.0011715
2011 | 2010-09-05 | C | 984 | 0.012362 | 0.0030906
2011 | 2010-09-05 | C | 77.1313 | 0.062017 | 0.00042401
2011 | 2010-09-06 | B | 68 | 0.07347 | 0.00021358
2011 | 2010-09-06 | C | 161 | 0.13957 | 0.00050567
2011 | 2010-09-06 | C | 5781 | 0.036314 | 0.018157
2011 | 2010-09-06 | B | 135 | 0.069114 | 0.00042401
2011 | 2010-09-06 | C | 3 | 0.0015924 | 9.4225e-06
2011 | 2010-09-06 | C | 56.3591 | 0.063548 | 0.00019159
2011 | 2010-09-06 | C | 56 | 0.010201 | 0.00017589
2011 | 2010-09-06 | C | 29.842 | 0.075639 | 0.00076636
2011 | 2010-09-06 | C | 164 | 0.0077264 | 0.00051509
2011 | 2010-09-06 | C | 1855.2152 | 0.44284 | 0.0070794
2011 | 2010-09-06 | B | 23 | 0.0034675 | 7.2239e-05
2011 | 2010-09-07 | B | 23 | 0.0044066 | 7.2239e-05
2011 | 2010-09-07 | C | 39 | 0.0013474 | 0.00012249
2011 | 2010-09-06 | C | 107 | 0.03159 | 0.00033607
2011 | 2010-09-07 | C | 425.2243 | 0.34724 | 0.0017149
2011 | 2010-09-07 | C | 21 | 0.0075191 | 6.5957e-05
2011 | 2010-09-05 | C | 115.8755 | 0.33519 | 0.00040831
2011 | 2010-09-06 | C | 93.7947 | 0.088083 | 0.00078835
2011 | 2010-09-05 | C | 153 | 0.44931 | 0.00048055
2011 | 2010-09-05 | C | 136.9991 | 0.50043 | 0.00050567
2011 | 2010-09-07 | C | 265 | 0.11236 | 0.00083232
2011 | 2010-09-07 | C | 1 | 5.9676e-05 | 3.1408e-06
2011 | 2010-09-07 | B | 177 | 0.072826 | 0.00055593
2011 | 2010-09-07 | B | 67 | 0.044823 | 0.00021044
2011 | 2010-09-07 | C | 28 | 0.0071234 | 8.7943e-05
2011 | 2010-09-07 | B | 66 | 0.010572 | 0.00020729
2011 | 2010-09-07 | C | 73.6458 | 0.15475 | 0.0019505
2011 | 2010-09-08 | B | 40 | 0.0041459 | 0.00012563
2011 | 2010-09-08 | B | 52 | 0.048507 | 0.00016332
2011 | 2010-09-08 | B | 132 | 0.038142 | 0.00041459
2011 | 2010-09-08 | C | 15 | 0.0019787 | 4.7112e-05
2011 | 2010-09-08 | B | 58 | 0.03443 | 0.00018217
2011 | 2010-09-08 | B | 4 | 0.0026132 | 1.2563e-05
2011 | 2010-09-08 | C | 357.6154 | 0.08424 | 0.0011747
2011 | 2010-09-08 | C | 58 | 0.0078332 | 0.00018217
2011 | 2010-09-08 | C | 6.2773 | 0.002287 | 0.00013191
2011 | 2010-09-08 | B | 34 | 0.042074 | 0.00010679
2011 | 2010-09-08 | C | 14.7935 | 0.016959 | 0.00010993
2011 | 2010-09-08 | C | 124.9138 | 0.044334 | 0.00093596
2011 | 2010-09-09 | B | 129 | 0.022689 | 0.00040517
2011 | 2010-09-09 | B | 373 | 0.066777 | 0.0011715
2011 | 2010-09-09 | B | 54 | 0.0057665 | 0.0001696
2011 | 2010-09-09 | C | 1130 | 0.22714 | 0.0035491
2011 | 2010-09-09 | C | 332 | 0.01877 | 0.0010428
2011 | 2010-09-09 | C | 177 | 0.049477 | 0.00055593
2011 | 2010-09-09 | B | 14 | 0.014774 | 4.3972e-05
2011 | 2010-09-09 | B | 8 | 0.0091209 | 2.5127e-05
2011 | 2010-09-09 | B | 34 | 0.02093 | 0.00010679
2011 | 2010-09-09 | B | 39 | 0.03099 | 0.00012249
2011 | 2010-09-09 | C | 615 | 0.036701 | 0.0019316
2011 | 2010-09-10 | C | 23 | 0.055841 | 7.2239e-05
2011 | 2010-09-10 | C | 5 | 0.00080091 | 1.5704e-05
2011 | 2010-09-10 | B | 5 | 0.0014291 | 1.5704e-05
2011 | 2010-09-10 | B | 16 | 0.011056 | 5.0253e-05
2011 | 2010-09-10 | B | 8 | 0.0053771 | 2.5127e-05
2011 | 2010-09-10 | C | 57 | 0.010205 | 0.00017903
2011 | 2010-09-10 | C | 183.9176 | 0.047368 | 0.00072867
2011 | 2010-09-11 | C | 49.5941 | 0.030997 | 0.00074437
2011 | 2010-09-11 | C | 75.1176 | 0.059455 | 0.0002387
2011 | 2010-09-11 | C | 24 | 0.015001 | 7.538e-05
2011 | 2010-09-11 | C | 163.1066 | 0.060962 | 0.0008543
2011 | 2010-09-12 | B | 81 | 0.012212 | 0.00025441
2011 | 2010-09-12 | C | 118.0731 | 0.12572 | 0.00070983
2011 | 2010-09-12 | C | 54.7388 | 0.04556 | 0.00034549
2011 | 2010-09-12 | B | 1 | 0.00043029 | 3.1408e-06
2011 | 2010-09-12 | C | 508 | 0.020742 | 0.0015955
2011 | 2010-09-11 | C | 99.6348 | 0.071036 | 0.0015736
2011 | 2010-09-11 | B | 211 | 0.15375 | 0.00066271
2011 | 2010-09-13 | B | 51 | 0.011213 | 0.00016018
2011 | 2010-09-13 | B | 41 | 0.037473 | 0.00012877
2011 | 2010-09-13 | C | 580.9683 | 0.10948 | 0.00223
2011 | 2010-09-13 | B | 465 | 0.045275 | 0.0014605
2011 | 2010-09-13 | C | 301.4098 | 0.2859 | 0.0034989
2011 | 2010-09-14 | B | 153 | 0.072562 | 0.00048055
2011 | 2010-09-14 | B | 284 | 0.1784 | 0.00089199
2011 | 2010-09-14 | C | 103 | 0.0061466 | 0.0003235
2011 | 2010-09-14 | C | 7 | 0.0006156 | 2.1986e-05
2011 | 2010-09-14 | B | 255 | 0.057665 | 0.00080091
2011 | 2010-09-14 | C | 244 | 0.065907 | 0.00076636
2011 | 2010-09-14 | C | 567.8169 | 0.12127 | 0.0018374
2011 | 2010-09-14 | C | 201.1573 | 0.1668 | 0.0018248
2011 | 2010-09-14 | C | 186.8833 | 0.068675 | 0.0028048
2011 | 2010-09-14 | C | 1 | 5.0253e-05 | 3.1408e-06
2011 | 2010-09-15 | B | 90.226 | 0.090683 | 0.00040203
2011 | 2010-09-15 | B | 103 | 0.052408 | 0.0003235
2011 | 2010-09-15 | B | 19 | 0.021304 | 5.9676e-05
2011 | 2010-09-15 | B | 99 | 0.10043 | 0.00031094
2011 | 2010-09-15 | C | 7 | 0.001605 | 2.1986e-05
2011 | 2010-09-15 | C | 157.5942 | 0.066822 | 0.0011401
2011 | 2010-09-15 | B | 20 | 0.0074752 | 6.2816e-05
2011 | 2010-09-16 | B | 1 | 0.00012563 | 3.1408e-06
2011 | 2010-09-16 | B | 27 | 0.017639 | 8.4802e-05
2011 | 2010-09-16 | C | 78 | 0.0093094 | 0.00024498
2011 | 2010-09-16 | C | 353.7647 | 0.12889 | 0.0017086
2011 | 2010-09-16 | B | 54 | 0.020183 | 0.0001696
2011 | 2010-09-16 | C | 608.3333 | 0.05732 | 0.0028362
2011 | 2010-09-16 | C | 1 | 4.7112e-05 | 3.1408e-06
2011 | 2010-09-16 | C | 290.7564 | 0.21095 | 0.0028424
2011 | 2010-09-16 | C | 98.8754 | 0.096271 | 0.0010804
2011 | 2010-09-16 | C | 68.2211 | 0.040069 | 0.00034549
2011 | 2010-09-16 | C | 305 | 0.028739 | 0.00095795
2011 | 2010-09-14 | B | 14 | 0.015038 | 4.3972e-05
2011 | 2010-09-14 | B | 12 | 0.009724 | 3.769e-05
2011 | 2010-09-14 | B | 374 | 0.10572 | 0.0011747
2011 | 2010-09-16 | B | 185 | 0.03893 | 0.00058105
2011 | 2010-09-17 | C | 162 | 0.036635 | 0.0011495
2011 | 2010-09-17 | C | 41 | 0.0033481 | 0.00012877
2011 | 2010-09-17 | B | 1 | 0.0014982 | 3.1408e-06
2011 | 2010-09-17 | C | 112 | 0.0056284 | 0.00035177
2011 | 2010-09-17 | B | 1 | 0.0010113 | 3.1408e-06
2011 | 2010-09-17 | C | 860 | 0.035114 | 0.0027011
2011 | 2010-09-17 | B | 1 | 0.0014197 | 3.1408e-06
2011 | 2010-09-17 | C | 160 | 0.043218 | 0.00050253
2011 | 2010-09-17 | C | 475 | 0.23721 | 0.0014919
2011 | 2010-09-17 | C | 114 | 0.0057289 | 0.00035805
2011 | 2010-09-17 | C | 17 | 0.0049122 | 5.3394e-05
2011 | 2010-09-17 | C | 131 | 0.016869 | 0.00041145
2011 | 2010-09-17 | C | 19 | 0.0082352 | 5.9676e-05
2011 | 2010-09-18 | C | 9 | 0.0035617 | 2.8267e-05
2011 | 2010-09-18 | C | 674 | 0.27308 | 0.0021169
2011 | 2010-09-17 | C | 705 | 0.80157 | 0.0022143
2011 | 2010-09-17 | C | 473.9839 | 0.18013 | 0.0028864
2011 | 2010-09-17 | C | 143.5 | 0.045522 | 0.00073495
2011 | 2010-09-18 | C | 162.208 | 0.24098 | 0.00084802
2011 | 2010-09-18 | C | 728 | 1.4291 | 0.0022865
2011 | 2010-09-18 | C | 36 | 0.0039574 | 0.00011307
2011 | 2010-09-17 | C | 142.7204 | 0.3353 | 0.00096423
2011 | 2010-09-17 | C | 361.4458 | 0.94906 | 0.0018814
2011 | 2010-09-18 | C | 198 | 0.12002 | 0.00062188
2011 | 2010-09-18 | C | 274.8921 | 0.11742 | 0.001382
2011 | 2010-09-18 | C | 478 | 0.0090079 | 0.0015013
2011 | 2010-09-18 | C | 367.6617 | 0.22864 | 0.0017526
2011 | 2010-09-18 | C | 17 | 0.015484 | 5.3394e-05
2011 | 2010-09-17 | C | 38.0026 | 0.135 | 0.00063131
2011 | 2010-09-18 | C | 258.8874 | 0.18539 | 0.0013537
2011 | 2010-09-17 | C | 104 | 0.018292 | 0.00032665
2011 | 2010-09-17 | C | 129.1826 | 0.53436 | 0.0042433
2011 | 2010-09-17 | C | 198.845 | 0.7357 | 0.0015045
2011 | 2010-09-18 | C | 3 | 0.0011024 | 9.4225e-06
2011 | 2010-09-18 | C | 104.5882 | 0.1107 | 0.00043657
2011 | 2010-09-18 | C | 1 | 0.0003926 | 3.1408e-06
2011 | 2010-09-18 | C | 18 | 0.0013003 | 5.6535e-05
2011 | 2010-09-18 | C | 402.1388 | 0.75151 | 0.0014479
2011 | 2010-09-18 | C | 211 | 0.028497 | 0.00066271
2011 | 2010-09-18 | C | 283.3333 | 0.14416 | 0.0010302
2011 | 2010-09-17 | C | 45.9872 | 0.13505 | 0.00032036
2011 | 2010-09-18 | C | 162.4844 | 0.11329 | 0.00074437
2011 | 2010-09-18 | C | 418 | 0.015754 | 0.0013129
2011 | 2010-09-18 | C | 84.2772 | 0.07941 | 0.00028896
2011 | 2010-09-17 | C | 245 | 0.41399 | 0.0007695
2011 | 2010-09-17 | C | 577 | 1.1363 | 0.0018123
2011 | 2010-09-18 | C | 112.2768 | 0.038438 | 0.001382
2011 | 2010-09-18 | C | 57 | 0.0010742 | 0.00017903
2011 | 2010-09-18 | C | 65.746 | 0.050592 | 0.00043972
2011 | 2010-09-18 | C | 32 | 0.011357 | 0.00010051
2011 | 2010-09-17 | C | 512 | 0.5564 | 0.0016081
2011 | 2010-09-18 | C | 119.7914 | 0.13959 | 0.0023462
2011 | 2010-09-18 | C | 30.4718 | 0.02852 | 0.00016018
2011 | 2010-09-17 | C | 344.7609 | 0.14618 | 0.0015861
2011 | 2010-09-17 | C | 122.3786 | 0.10647 | 0.00069098
2011 | 2010-09-18 | C | 176.1264 | 0.094594 | 0.00093911
2011 | 2010-09-17 | C | 1248 | 1.1563 | 0.0039197
2011 | 2010-09-17 | C | 900 | 1.4953 | 0.0028267
2011 | 2010-09-18 | C | 399.9187 | 0.45972 | 0.0030152
2011 | 2010-09-18 | C | 119 | 0.024294 | 0.00062816
2011 | 2010-09-18 | C | 12 | 0.0013945 | 3.769e-05
2011 | 2010-09-18 | C | 4 | 0.00062816 | 1.2563e-05
2011 | 2010-09-18 | C | 28 | 0.0049248 | 8.7943e-05
2011 | 2010-09-18 | C | 670 | 0.42929 | 0.0021044
2011 | 2010-09-18 | C | 185 | 0.11563 | 0.00058105
2011 | 2010-09-17 | C | 3144 | 3.3969 | 0.0098747
2011 | 2010-09-17 | C | 76 | 0.025064 | 0.0002387
2011 | 2010-09-19 | C | 3 | 0.00059362 | 9.4225e-06
2011 | 2010-09-19 | C | 20 | 0.015327 | 6.2816e-05
2011 | 2010-09-19 | C | 108.4718 | 0.083469 | 0.00050881
2011 | 2010-09-19 | C | 81 | 0.017554 | 0.00025441
2011 | 2010-09-18 | C | 20.0861 | 0.15728 | 7.8521e-05
2011 | 2010-09-19 | C | 1 | 0.00034235 | 3.1408e-06
2011 | 2010-09-19 | C | 10 | 0.005999 | 3.1408e-05
2011 | 2010-09-17 | C | 116.0708 | 0.82281 | 0.00043972
2011 | 2010-09-19 | C | 105.3192 | 0.069466 | 0.00045228
2011 | 2010-09-19 | C | 23 | 0.0052734 | 7.2239e-05
2011 | 2010-09-18 | C | 5 | 0.0023242 | 1.5704e-05
2011 | 2010-09-19 | C | 2 | 0.00064701 | 6.2816e-06
2011 | 2010-09-19 | C | 42 | 0.012268 | 0.00013191
2011 | 2010-09-18 | C | 88 | 0.39718 | 0.00027639
2011 | 2010-09-17 | C | 56 | 0.42828 | 0.00017589
2011 | 2010-09-18 | C | 672.816 | 0.44166 | 0.0023399
2011 | 2010-09-18 | C | 15 | 0.078301 | 4.7112e-05
2011 | 2010-09-18 | C | 9 | 0.026741 | 2.8267e-05
2011 | 2010-09-18 | C | 935 | 0.1439 | 0.0029367
2011 | 2010-09-19 | C | 4 | 0.0018594 | 1.2563e-05
2011 | 2010-09-19 | C | 49 | 0.0063099 | 0.0001539
2011 | 2010-09-18 | C | 347.401 | 0.20622 | 0.0031911
2011 | 2010-09-18 | C | 116 | 0.030604 | 0.00036434
2011 | 2010-09-18 | C | 525.6364 | 0.32193 | 0.0023085
2011 | 2010-09-19 | C | 8 | 0.0021609 | 2.5127e-05
2011 | 2010-09-18 | C | 205 | 0.069538 | 0.00064387
2011 | 2010-09-18 | C | 45 | 0.0052295 | 0.00014134
2011 | 2010-09-20 | C | 268.7608 | 0.6044 | 0.00086059
2011 | 2010-09-18 | C | 741 | 0.30488 | 0.0023273
2011 | 2010-09-18 | C | 932 | 0.1932 | 0.0029272
2011 | 2010-09-18 | C | 36 | 0.018883 | 0.00011307
2011 | 2010-09-20 | C | 16 | 0.0021609 | 5.0253e-05
2011 | 2010-09-20 | C | 85 | 0.0098779 | 0.00026697
2011 | 2010-09-17 | C | 1 | 0.0032727 | 3.1408e-06
2011 | 2010-09-17 | C | 273 | 0.99292 | 0.00085744
2011 | 2010-09-18 | C | 116.8933 | 0.081505 | 0.00061874
2011 | 2010-09-19 | C | 321.7597 | 0.12733 | 0.0015076
2011 | 2010-09-18 | C | 149 | 0.082833 | 0.00046798
2011 | 2010-09-18 | C | 196.6933 | 0.04448 | 0.0010176
2011 | 2010-09-20 | C | 20 | 0.0003769 | 6.2816e-05
2011 | 2010-09-18 | C | 2 | 0.00086059 | 6.2816e-06
2011 | 2010-09-18 | C | 437.168 | 0.34739 | 0.0015736
2011 | 2010-09-17 | C | 144 | 0.39981 | 0.00045228
2011 | 2010-09-20 | C | 127 | 0.0047866 | 0.00039888
2011 | 2010-09-17 | C | 320.6296 | 0.078549 | 0.0013851
2011 | 2010-09-19 | C | 44 | 0.020315 | 0.0001382
2011 | 2010-09-18 | C | 115.7997 | 0.65067 | 0.00069726
2011 | 2010-09-17 | C | 905 | 0.17055 | 0.0028424
2011 | 2010-09-19 | C | 2 | 0.00039574 | 6.2816e-06
2011 | 2010-09-18 | C | 68.9655 | 0.17524 | 0.00056221
2011 | 2010-09-19 | C | 84.2242 | 0.042854 | 0.00064701
2011 | 2010-09-17 | C | 324 | 0.087516 | 0.0010176
2011 | 2010-09-18 | C | 214.9027 | 0.59465 | 0.00087943
2011 | 2010-09-18 | C | 969 | 0.28304 | 0.0030435
2011 | 2010-09-19 | C | 6 | 0.019448 | 0
2011 | 2010-09-20 | C | 90 | 0.0098936 | 0.00028267
2011 | 2010-09-17 | C | 36.6239 | 0.13424 | 0.00093596
2011 | 2010-09-20 | C | 8 | 0.0071611 | 2.5127e-05
2011 | 2010-09-21 | C | 201 | 0.11174 | 0.00063131
2011 | 2010-09-20 | C | 367.7864 | 0.11552 | 0.0020855
2011 | 2010-09-20 | C | 99 | 0.0080845 | 0.00031094
2011 | 2010-09-19 | C | 49 | 0.012466 | 0.0001539
2011 | 2010-09-20 | C | 150.7458 | 0.026514 | 0.00069098
2011 | 2010-09-21 | C | 57 | 0.0048337 | 0.00017903
2011 | 2010-09-21 | C | 1099.8125 | 0.26598 | 0.004014
2011 | 2010-09-21 | C | 734 | 0.20748 | 0.0023054
2011 | 2010-09-18 | C | 261.1818 | 0.069728 | 0.001115
2011 | 2010-09-21 | C | 18 | 0.0066146 | 5.6535e-05
2011 | 2010-09-21 | C | 47 | 0.0035428 | 0.00014762
2011 | 2010-09-18 | C | 596.9045 | 1.1924 | 0.0022017
2011 | 2010-09-17 | C | 65.2044 | 0.48332 | 0.00072239
2011 | 2010-09-21 | C | 273 | 0.011147 | 0.00085744
2011 | 2010-09-18 | C | 141.0237 | 0.61656 | 0.0018719
2011 | 2010-09-21 | C | 1375.1957 | 0.18573 | 0.0057571
2011 | 2010-09-21 | C | 16 | 0.0008543 | 5.0253e-05
2011 | 2010-09-20 | C | 3912 | 0.71264 | 0.012287
2011 | 2010-09-21 | C | 15 | 0.001272 | 4.7112e-05
2011 | 2010-09-20 | C | 125 | 0.021201 | 0.0003926
2011 | 2010-09-20 | C | 968 | 0.018242 | 0.0030403
2011 | 2010-09-20 | C | 47.4635 | 0.14848 | 0.00040203
2011 | 2010-09-20 | C | 109 | 0.0065046 | 0.00034235
2011 | 2010-09-20 | C | 2 | 0.00058419 | 6.2816e-06
2011 | 2010-09-19 | C | 41 | 0.10134 | 0.00012877
2011 | 2010-09-21 | C | 515.4427 | 0.20722 | 0.0017557
2011 | 2010-09-19 | C | 1352 | 0.067942 | 0.0042464
2011 | 2010-09-19 | C | 1302 | 0.32306 | 0.0040894
2011 | 2010-09-19 | C | 1248 | 0.23518 | 0.0039197
2011 | 2010-09-20 | C | 87.1982 | 0.061348 | 0.001049
2011 | 2010-09-19 | C | 1356 | 0.055366 | 0.004259
2011 | 2010-09-20 | C | 824 | 0.054349 | 0.002588
2011 | 2010-09-20 | C | 87.5061 | 0.29188 | 0.00074123
2011 | 2010-09-21 | C | 1077.6 | 1.0052 | 0.0054116
2011 | 2010-09-21 | C | 1194 | 0.14251 | 0.0037501
2011 | 2010-09-21 | C | 1052.6863 | 0.1587 | 0.0033073
2011 | 2010-09-21 | C | 218 | 0.032181 | 0.0006847
2011 | 2010-09-21 | C | 1195 | 0.0075066 | 0.0037533
2011 | 2010-09-21 | C | 16 | 0.018895 | 5.0253e-05
2011 | 2010-09-21 | C | 223.8655 | 0.19125 | 0.0021515
2011 | 2010-09-22 | C | 417 | 0.10347 | 0.0013097
2011 | 2010-09-18 | C | 187.8635 | 0.28794 | 0.00065015
2011 | 2010-09-21 | C | 227 | 0.017111 | 0.00071297
2011 | 2010-09-21 | C | 65 | 0.01572 | 0.00020415
2011 | 2010-09-18 | C | 189.1291 | 0.19603 | 0.0010679
2011 | 2010-09-21 | C | 148.2373 | 0.053542 | 0.00055278
2011 | 2010-09-20 | C | 82.6885 | 0.15011 | 0.00044914
2011 | 2010-09-21 | C | 39 | 0.0011024 | 0.00012249
2011 | 2010-09-21 | C | 11 | 0.0026257 | 3.4549e-05
2011 | 2010-09-18 | C | 2 | 0.0012186 | 6.2816e-06
2011 | 2010-09-21 | C | 5990 | 4.6281 | 0.018814
2011 | 2010-09-20 | C | 824 | 0.064701 | 0.002588
2011 | 2010-09-18 | C | 92 | 0.0043343 | 0.00028896
2011 | 2010-09-21 | C | 135.1164 | 0.060686 | 0.00073809
2011 | 2010-09-21 | C | 1303 | 0.085942 | 0.0040925
2011 | 2010-09-18 | C | 67.4948 | 0.22259 | 0.00048997
2011 | 2010-09-21 | C | 617.3442 | 0.76589 | 0.002387
2011 | 2010-09-17 | C | 387.3223 | 1.3929 | 0.001605
2011 | 2010-09-18 | C | 85.7719 | 0.31573 | 0.00050881
2011 | 2010-09-17 | C | 110.75 | 0.2828 | 0.00055278
2011 | 2010-09-21 | C | 734 | 0.73541 | 0.0023054
2011 | 2010-09-19 | C | 54.6207 | 0.10396 | 0.00069726
2011 | 2010-09-18 | C | 28 | 0.053118 | 8.7943e-05
2011 | 2010-09-21 | C | 1205 | 0.29899 | 0.0037847
2011 | 2010-09-20 | C | 351.0742 | 0.33852 | 0.0017777
2011 | 2010-09-20 | C | 24.1927 | 0.13229 | 0.00011307
2011 | 2010-09-19 | C | 117 | 0.014332 | 0.00036748
2011 | 2010-09-18 | C | 2 | 0.0075505 | 6.2816e-06
2011 | 2010-09-21 | C | 1301 | 0.012259 | 0.0040862
2011 | 2010-09-21 | C | 1248 | 0.047037 | 0.0039197
2011 | 2010-09-21 | C | 22.6614 | 0.063275 | 0.00014762
2011 | 2010-09-21 | C | 601.06 | 0.18312 | 0.0026289
2011 | 2010-09-20 | C | 70.0588 | 0.018043 | 0.00023556
2011 | 2010-09-18 | C | 1719.05 | 1.9275 | 0.0071485
2011 | 2010-09-22 | C | 63 | 0.0059362 | 0.00019787
2011 | 2010-09-22 | C | 1 | 0.00079463 | 3.1408e-06
2011 | 2010-09-21 | C | 2 | 0.00050881 | 6.2816e-06
2011 | 2010-09-18 | C | 503 | 0.23698 | 0.0015798
2011 | 2010-09-20 | C | 23 | 0.0012281 | 7.2239e-05
2011 | 2010-09-19 | C | 633.089 | 1.1553 | 0.0021044
2011 | 2010-09-20 | C | 90.199 | 0.05326 | 0.00034549
2011 | 2010-09-21 | C | 90.0148 | 0.11365 | 0.00033293
2011 | 2010-09-18 | C | 80 | 0.033921 | 0.00025127
2011 | 2010-09-18 | C | 492.1637 | 0.25969 | 0.0028707
2011 | 2010-09-18 | C | 613.0283 | 1.627 | 0.0049028
2011 | 2010-09-22 | C | 247 | 0.16757 | 0.00077578
2011 | 2010-09-20 | C | 413.867 | 0.24048 | 0.0022708
2011 | 2010-09-21 | B | 31 | 0.015773 | 9.7365e-05
2011 | 2010-09-22 | C | 32 | 0.0022111 | 0.00010051
2011 | 2010-09-20 | C | 95.8799 | 0.32764 | 0.0015704
2011 | 2010-09-22 | C | 80.6916 | 0.026358 | 0.00039574
2011 | 2010-09-23 | C | 237 | 0.0096769 | 0.00074437
2011 | 2010-09-22 | C | 90.3805 | 0.031226 | 0.00028581
2011 | 2010-09-18 | C | 90.4347 | 0.29711 | 0.00038946
2011 | 2010-09-19 | C | 41 | 0.0025755 | 0.00012877
2011 | 2010-09-23 | C | 237 | 0.0074437 | 0.00074437
2011 | 2010-09-22 | C | 28.6667 | 0.010534 | 0.00022928
2011 | 2010-09-22 | C | 361 | 0.29026 | 0.0011338
2011 | 2010-09-22 | C | 40 | 0.014071 | 0.00012563
2011 | 2010-09-19 | C | 571 | 0.037662 | 0.0017934
2011 | 2010-09-22 | C | 311 | 0.1094 | 0.0009768
2011 | 2010-09-19 | C | 70 | 0.010333 | 0.00021986
2011 | 2010-09-23 | C | 145.2 | 0.044237 | 0.00080091
2011 | 2010-09-18 | C | 149.7049 | 0.76971 | 0.00051195
2011 | 2010-09-22 | C | 940.7347 | 0.85981 | 0.0043814
2011 | 2010-09-19 | C | 168 | 0.021106 | 0.00052766
2011 | 2010-09-22 | C | 310.0092 | 0.20837 | 0.0021201
2011 | 2010-09-22 | C | 74.5684 | 0.088296 | 0.00028896
2011 | 2010-09-22 | C | 107.6923 | 0.042957 | 0.00043972
2011 | 2010-09-22 | C | 60.9444 | 0.020099 | 0.00031408
2011 | 2010-09-23 | C | 211 | 0.28894 | 0.00066271
2011 | 2010-09-19 | C | 69 | 0.0047678 | 0.00021672
2011 | 2010-09-22 | C | 3 | 0.0013097 | 9.4225e-06
2011 | 2010-09-17 | C | 18.194 | 0.21069 | 0.00019473
2011 | 2010-09-21 | C | 1 | 0.00079149 | 3.1408e-06
2011 | 2010-09-23 | C | 96.6676 | 0.10232 | 0.00082918
2011 | 2010-09-20 | C | 138.7262 | 0.57471 | 0.00059362
2011 | 2010-09-18 | C | 2 | 0.0016081 | 6.2816e-06
2011 | 2010-09-22 | C | 2 | 0.00043972 | 6.2816e-06
2011 | 2010-09-18 | C | 115 | 0.26981 | 0.00036119
2011 | 2010-09-18 | C | 245.0069 | 0.66333 | 0.0013694
2011 | 2010-09-19 | C | 6 | 0.020484 | 1.8845e-05
2011 | 2010-09-22 | C | 3 | 0.00067842 | 9.4225e-06
2011 | 2010-09-19 | C | 8.2406 | 0.029402 | 3.1408e-05
2011 | 2010-09-22 | C | 14 | 0.0041333 | 4.3972e-05
2011 | 2010-09-20 | C | 5 | 0.0018845 | 1.5704e-05
2011 | 2010-09-23 | C | 73 | 0.0084834 | 0.00022928
2011 | 2010-09-22 | C | 245.6009 | 0.5176 | 0.00082604
2011 | 2010-09-20 | C | 165 | 0.032131 | 0.00051824
2011 | 2010-09-20 | C | 219.9592 | 0.13333 | 0.0015139
2011 | 2010-09-23 | C | 75 | 0.019552 | 0.00023556
2011 | 2010-09-19 | C | 43 | 0.010399 | 0.00013506
2011 | 2010-09-23 | C | 5989 | 1.6929 | 0.01881
2011 | 2010-09-23 | C | 423 | 0.010629 | 0.0013286
2011 | 2010-09-24 | C | 147 | 0.0036936 | 0.0004617
2011 | 2010-09-24 | B | 139 | 0.040601 | 0.00043657
2011 | 2010-09-23 | C | 36 | 0.0045228 | 0.00011307
2011 | 2010-09-23 | C | 75 | 0.0044757 | 0.00023556
2011 | 2010-09-23 | C | 1 | 0.00032979 | 3.1408e-06
2011 | 2010-09-23 | C | 94.4985 | 0.099726 | 0.00035491
2011 | 2010-09-23 | C | 38 | 0.010145 | 0.00011935
2011 | 2010-09-23 | C | 65 | 0.051038 | 0.00020415
2011 | 2010-09-23 | C | 2 | 0.00042715 | 6.2816e-06
2011 | 2010-09-23 | C | 503.1489 | 0.069533 | 0.0020918
2011 | 2010-09-23 | C | 61.7778 | 0.058792 | 0.00062502
2011 | 2010-09-23 | C | 187.5581 | 0.3128 | 0.00087943
2011 | 2010-09-23 | C | 63 | 0.017413 | 0.00019787
2011 | 2010-09-24 | C | 65 | 0.005308 | 0.00020415
2011 | 2010-09-23 | C | 224.977 | 0.15122 | 0.00083232
2011 | 2010-09-23 | C | 50 | 0.014919 | 0.00015704
2011 | 2010-09-23 | C | 4 | 0.0010176 | 1.2563e-05
2011 | 2010-09-23 | C | 125 | 0.0051038 | 0.0003926
2011 | 2010-09-24 | B | 63 | 0.041949 | 0.00019787
2011 | 2010-09-24 | C | 6 | 0.00050881 | 1.8845e-05
2011 | 2010-09-23 | C | 57 | 0.02202 | 0.00017903
2011 | 2010-09-23 | C | 75 | 0.0056535 | 0.00023556
2011 | 2010-09-23 | C | 97.9497 | 0.060298 | 0.00031408
2011 | 2010-09-22 | C | 4 | 0.0026132 | 1.2563e-05
2011 | 2010-09-19 | C | 47 | 0.020519 | 0.00014762
2011 | 2010-09-23 | C | 8 | 0.0019599 | 2.5127e-05
2011 | 2010-09-18 | C | 234.273 | 0.42898 | 0.0016929
2011 | 2010-09-23 | C | 71.0099 | 0.11241 | 0.0002387
2011 | 2010-09-23 | C | 108 | 0.0030529 | 0.00033921
2011 | 2010-09-20 | C | 1 | 0.00022928 | 3.1408e-06
2011 | 2010-09-23 | C | 3 | 0.00065957 | 9.4225e-06
2011 | 2010-09-19 | C | 34.3229 | 0.11988 | 0.00014448
2011 | 2010-09-23 | C | 53 | 0.0058262 | 0.00016646
2011 | 2010-09-18 | C | 58.125 | 0.24919 | 0.0013945
2011 | 2010-09-23 | C | 33 | 0.020522 | 0.00010365
2011 | 2010-09-20 | C | 2 | 0.00027639 | 6.2816e-06
2011 | 2010-09-19 | C | 5 | 0.022535 | 1.5704e-05
2011 | 2010-09-23 | C | 5 | 0.0043186 | 1.5704e-05
2011 | 2010-09-20 | C | 1 | 0.0011747 | 3.1408e-06
2011 | 2010-09-23 | C | 476.0938 | 0.56972 | 0.0041145
2011 | 2010-09-23 | C | 10 | 0.0041145 | 3.1408e-05
2011 | 2010-09-22 | C | 8 | 0.00080405 | 2.5127e-05
2011 | 2010-09-23 | C | 136.2335 | 0.095846 | 0.00082604
2011 | 2010-09-21 | C | 4220 | 0.079526 | 0.013254
2011 | 2010-09-17 | C | 8 | 0.065505 | 2.5127e-05
2011 | 2010-09-19 | C | 2 | 0.00035805 | 6.2816e-06
2011 | 2010-09-18 | C | 73.4171 | 0.27463 | 0.00043972
2011 | 2010-09-19 | C | 44 | 0.0017966 | 0.0001382
2011 | 2010-09-24 | B | 29 | 0.020767 | 9.1084e-05
2011 | 2010-09-24 | C | 5 | 0.0026226 | 1.5704e-05
2011 | 2010-09-24 | C | 2 | 0.00035805 | 6.2816e-06
2011 | 2010-09-24 | C | 11 | 0.0034204 | 3.4549e-05
2011 | 2010-09-24 | C | 85.2809 | 0.023035 | 0.00037062
2011 | 2010-09-25 | C | 70.5185 | 0.029236 | 0.00028896
2011 | 2010-09-24 | C | 93.2871 | 0.060358 | 0.0003235
2011 | 2010-09-25 | C | 116 | 0.014209 | 0.00036434
2011 | 2010-09-24 | C | 125 | 0.020808 | 0.0003926
2011 | 2010-09-19 | C | 41.5 | 0.10258 | 0.00031408
2011 | 2010-09-23 | C | 9 | 0.035532 | 2.8267e-05
2011 | 2010-09-24 | C | 24 | 0.0040705 | 7.538e-05
2011 | 2010-09-25 | C | 53.1554 | 0.075796 | 0.00174
2011 | 2010-09-24 | C | 148 | 0.012551 | 0.00046484
2011 | 2010-09-25 | C | 7 | 0.0056943 | 2.1986e-05
2011 | 2010-09-22 | C | 1490.4386 | 0.25278 | 0.0050818
2011 | 2010-09-25 | C | 329 | 0.038233 | 0.0010333
2011 | 2010-09-18 | C | 25.1112 | 0.09906 | 9.1084e-05
2011 | 2010-09-25 | C | 11 | 0.0014856 | 3.4549e-05
2011 | 2010-09-24 | C | 140 | 0.043532 | 0.00043972
2011 | 2010-09-22 | C | 127.2032 | 0.099082 | 0.0010302
2011 | 2010-09-24 | C | 6.8602 | 0.015966 | 6.9098e-05
2011 | 2010-09-23 | C | 175.2195 | 0.15629 | 0.00082918
2011 | 2010-09-21 | C | 559 | 0.070229 | 0.0017557
2011 | 2010-09-25 | C | 20 | 0.0019473 | 6.2816e-05
2011 | 2010-09-25 | C | 18 | 0.0013003 | 5.6535e-05
2011 | 2010-09-25 | C | 688.9804 | 0.21423 | 0.0042118
2011 | 2010-09-22 | C | 3 | 0.0028267 | 9.4225e-06
2011 | 2010-09-25 | C | 12 | 0.0038821 | 3.769e-05
2011 | 2010-09-22 | C | 1 | 0.00035491 | 3.1408e-06
2011 | 2010-09-22 | C | 48 | 0.0052766 | 0.00015076
2011 | 2010-09-25 | C | 12 | 0.0030152 | 3.769e-05
2011 | 2010-09-20 | C | 10 | 0.0010993 | 3.1408e-05
2011 | 2010-09-25 | C | 580.3621 | 0.20598 | 0.0030089
2011 | 2010-09-20 | C | 651 | 0.24945 | 0.0020447
2011 | 2010-09-20 | C | 16 | 0.0084425 | 5.0253e-05
2011 | 2010-09-20 | C | 38 | 0.0085933 | 0.00011935
2011 | 2010-09-20 | C | 28 | 0.0075631 | 8.7943e-05
2011 | 2010-09-25 | C | 49 | 0.012466 | 0.0001539
2011 | 2010-09-24 | C | 36 | 0.0055404 | 0.00011307
2011 | 2010-09-26 | B | 115 | 0.026006 | 0.00036119
2011 | 2010-09-25 | C | 202.7785 | 0.56747 | 0.00064073
2011 | 2010-09-20 | C | 137.2771 | 0.10607 | 0.00047112
2011 | 2010-09-26 | C | 72.1136 | 0.019252 | 0.00039888
2011 | 2010-09-26 | C | 42.4844 | 0.016679 | 0.00031408
2011 | 2010-09-20 | C | 2 | 0.00091712 | 6.2816e-06
2011 | 2010-09-20 | C | 1 | 0.00097051 | 3.1408e-06
2011 | 2010-09-18 | C | 1298 | 1.1333 | 0.0040768
2011 | 2010-09-19 | C | 32 | 0.0044223 | 0.00010051
2011 | 2010-09-18 | C | 10 | 0.0063759 | 3.1408e-05
2011 | 2010-09-20 | C | 33 | 0.029747 | 0.00010365
2011 | 2010-09-26 | C | 37 | 0.0015107 | 0.00011621
2011 | 2010-09-26 | C | 94 | 0.005019 | 0.00029524
2011 | 2010-09-26 | C | 897.6154 | 0.35804 | 0.0054462
2011 | 2010-09-26 | C | 798.8478 | 0.10789 | 0.0040705
2011 | 2010-09-26 | C | 86 | 0.0027011 | 0.00027011
2011 | 2010-09-27 | C | 993.4444 | 0.13105 | 0.0042118
2011 | 2010-09-27 | C | 12 | 0.0018468 | 3.769e-05
2011 | 2010-09-21 | B | 113.5918 | 0.086339 | 0.00038946
2011 | 2010-09-22 | C | 310 | 0.14021 | 0.00097365
2011 | 2010-09-22 | C | 502 | 0.10564 | 0.0015767
2011 | 2010-09-26 | C | 91.1326 | 0.050949 | 0.00051195
2011 | 2010-09-17 | C | 107 | 0.024533 | 0.00033607
2011 | 2010-09-26 | C | 64 | 0.046635 | 0.00020101
2011 | 2010-09-17 | C | 1196 | 0.96916 | 0.0037564
2011 | 2010-09-19 | C | 23 | 0.097667 | 7.2239e-05
2011 | 2010-09-24 | C | 957 | 0.060115 | 0.0030058
2011 | 2010-09-27 | B | 8 | 0.0033167 | 2.5127e-05
2011 | 2010-09-27 | B | 21 | 0.012994 | 6.5957e-05
2011 | 2010-09-27 | B | 64 | 0.044826 | 0.00020101
2011 | 2010-09-27 | C | 648 | 0.21574 | 0.0020353
2011 | 2010-09-27 | C | 67 | 0.10922 | 0.00021044
2011 | 2010-09-17 | C | 296.4308 | 1.2616 | 0.0009925
2011 | 2010-09-27 | B | 5 | 0.0037376 | 1.5704e-05
2011 | 2010-09-27 | C | 12 | 0.00090456 | 3.769e-05
2011 | 2010-09-26 | C | 35.7838 | 0.016297 | 0.00023556
2011 | 2010-09-28 | C | 26 | 0.0080028 | 8.1661e-05
2011 | 2010-09-28 | B | 45 | 0.045935 | 0.00014134
2011 | 2010-09-28 | B | 13 | 0.0020415 | 4.0831e-05
2011 | 2010-09-28 | B | 13 | 0.0053897 | 4.0831e-05
2011 | 2010-09-29 | C | 343.8824 | 0.088566 | 0.0017463
2011 | 2010-09-29 | C | 46.1471 | 0.034061 | 0.000223
2011 | 2010-09-22 | C | 1119 | 0.21439 | 0.0035146
2011 | 2010-09-22 | C | 941.81 | 1.2986 | 0.0045385
2011 | 2010-09-29 | C | 345.9175 | 0.10213 | 0.0011056
2011 | 2010-09-29 | C | 338.4424 | 0.1722 | 0.0014039
2011 | 2010-09-29 | C | 10.6312 | 0.0086816 | 3.769e-05
2011 | 2010-09-23 | B | 168 | 0.09234 | 0.00052766
2011 | 2010-09-29 | C | 75 | 0.025205 | 0.00023556
2011 | 2010-09-29 | C | 221.5 | 0.11062 | 0.0021452
2011 | 2010-09-29 | C | 45 | 0.02431 | 0.00014134
2011 | 2010-09-29 | C | 29 | 0.0082886 | 9.1084e-05
2011 | 2010-09-29 | C | 117.8193 | 0.029604 | 0.00083232
2011 | 2010-09-29 | C | 176 | 0.20619 | 0.00055278
2011 | 2010-09-29 | C | 158.6 | 0.073226 | 0.0017746
2011 | 2010-09-29 | B | 25 | 0.010208 | 7.8521e-05
2011 | 2010-09-29 | B | 73 | 0.050671 | 0.00022928
2011 | 2010-09-30 | C | 35.2363 | 0.074149 | 0.0006847
2011 | 2010-09-19 | C | 62 | 0.031936 | 0.00019473
2011 | 2010-09-30 | B | 37 | 0.024056 | 0.00011621
2011 | 2010-09-30 | B | 12 | 0.012249 | 3.769e-05
2011 | 2010-09-30 | B | 34 | 0.029901 | 0.00010679
2011 | 2010-09-30 | B | 16 | 0.01794 | 5.0253e-05
2011 | 2010-09-30 | C | 6 | 0.0003769 | 1.8845e-05
2011 | 2010-10-01 | C | 105.7672 | 0.10032 | 0.0015861
2011 | 2010-10-01 | C | 460.0186 | 0.38433 | 0.001718
2011 | 2010-10-01 | B | 37 | 0.0024404 | 0.00011621
2011 | 2010-10-01 | B | 30 | 0.020918 | 9.4225e-05
2011 | 2010-10-01 | C | 1 | 0.00023242 | 3.1408e-06
2011 | 2010-10-01 | C | 82 | 0.0087566 | 0.00025755
2011 | 2010-10-01 | C | 50 | 0.0091084 | 0.00015704
2011 | 2010-10-01 | C | 2 | 0.001539 | 6.2816e-06
2011 | 2010-10-01 | B | 57 | 0.047263 | 0.00017903
2011 | 2010-10-01 | C | 59 | 0.015937 | 0.00018531
2011 | 2010-10-01 | C | 94 | 0.085914 | 0.00029524
2011 | 2010-10-01 | C | 25 | 0.033057 | 7.8521e-05
2011 | 2010-10-01 | C | 33.7474 | 0.041232 | 0.00033607
2011 | 2010-10-01 | C | 26 | 0.0031848 | 8.1661e-05
2011 | 2010-10-01 | B | 9 | 0.0084802 | 2.8267e-05
2011 | 2010-10-01 | C | 40 | 0.030026 | 0.00012563
2011 | 2010-10-02 | C | 498.6912 | 0.10181 | 0.0019096
2011 | 2010-10-02 | C | 483 | 0.1244 | 0.001517
2011 | 2010-10-02 | C | 380 | 0.099062 | 0.0011935
2011 | 2010-10-02 | B | 124 | 0.073608 | 0.00038946
2011 | 2010-10-02 | B | 42 | 0.013719 | 0.00013191
2011 | 2010-10-02 | C | 182 | 0.0074312 | 0.00057163
2011 | 2010-10-03 | C | 52.5611 | 0.02922 | 0.00031722
2011 | 2010-10-03 | B | 117 | 0.031235 | 0.00036748
2011 | 2010-10-03 | B | 27 | 0.00059362 | 8.4802e-05
2011 | 2010-10-04 | C | 577 | 0.027184 | 0.0018123
2011 | 2010-10-04 | B | 28 | 0.007651 | 8.7943e-05
2011 | 2010-10-04 | B | 13 | 0.015965 | 4.0831e-05
2011 | 2010-10-04 | B | 40 | 0.017714 | 0.00012563
2011 | 2010-10-04 | B | 100 | 0.089513 | 0.00031408
2011 | 2010-10-04 | C | 3 | 0.0014699 | 9.4225e-06
2011 | 2010-10-04 | B | 83 | 0.008342 | 0.00026069
2011 | 2010-10-05 | C | 5 | 0.00073809 | 1.5704e-05
2011 | 2010-10-05 | B | 57 | 0.054245 | 0.00017903
2011 | 2010-10-05 | B | 76 | 0.052992 | 0.0002387
2011 | 2010-10-05 | C | 29 | 0.0042809 | 9.1084e-05
2011 | 2010-10-05 | B | 57 | 0.051202 | 0.00017903
2011 | 2010-10-05 | B | 7 | 0.0078269 | 2.1986e-05
2011 | 2010-10-05 | B | 8 | 0.0027388 | 2.5127e-05
2011 | 2010-10-05 | C | 266 | 0.00083546 | 0.00083546
2011 | 2010-10-06 | B | 23 | 0.020155 | 7.2239e-05
2011 | 2010-10-06 | B | 19 | 0.010861 | 5.9676e-05
2011 | 2010-10-06 | B | 79 | 0.074189 | 0.00024812
2011 | 2010-10-06 | B | 50 | 0.037376 | 0.00015704
2011 | 2010-10-06 | B | 17 | 0.0099847 | 5.3394e-05
2011 | 2010-10-06 | C | 29 | 0.0073778 | 9.1084e-05
2011 | 2010-10-06 | C | 284 | 0.043708 | 0.00089199
2011 | 2010-10-06 | C | 51 | 0.056865 | 0.00016018
2011 | 2010-10-06 | C | 554 | 0.085261 | 0.00174
2011 | 2010-10-06 | C | 946 | 0.035655 | 0.0029712
2011 | 2010-10-06 | C | 117 | 0.0044097 | 0.00036748
2011 | 2010-10-07 | B | 36 | 0.018656 | 0.00011307
2011 | 2010-10-07 | C | 1015 | 0.095638 | 0.0031879
2011 | 2010-10-07 | C | 78.6261 | 0.086433 | 0.00069412
2011 | 2010-10-07 | B | 177 | 0.028352 | 0.00055593
2011 | 2010-10-07 | C | 139 | 0.02925 | 0.00043657
2011 | 2010-10-07 | C | 81 | 0.025949 | 0.00025441
2011 | 2010-10-07 | C | 175.3981 | 0.055089 | 0.00090142
2011 | 2010-10-07 | C | 13 | 0.015597 | 4.0831e-05
2011 | 2010-10-07 | B | 801 | 0.31196 | 0.0025158
2011 | 2010-10-07 | C | 577 | 0.021747 | 0.0018123
2011 | 2010-10-04 | B | 2 | 0.0012061 | 6.2816e-06
2011 | 2010-10-08 | B | 77 | 0.091659 | 0.00024184
2011 | 2010-10-08 | C | 160.2203 | 0.057871 | 0.0010176
2011 | 2010-10-09 | C | 71 | 0.027429 | 0.000223
2011 | 2010-10-09 | C | 20 | 0.0012563 | 6.2816e-05
2011 | 2010-10-09 | C | 946 | 0.15153 | 0.0029712
2011 | 2010-10-09 | C | 62 | 0.02142 | 0.00019473
2011 | 2010-10-08 | C | 65.731 | 0.14059 | 0.00073495
2011 | 2010-10-09 | C | 2 | 0.00053394 | 6.2816e-06
2011 | 2010-10-09 | C | 6 | 0.0026571 | 1.8845e-05
2011 | 2010-10-09 | C | 51 | 0.0075286 | 0.00016018
2011 | 2010-10-09 | C | 4 | 0.00045228 | 1.2563e-05
2011 | 2010-10-09 | C | 130.3857 | 0.11344 | 0.00070983
2011 | 2010-10-09 | C | 91 | 0.013719 | 0.00028581
2011 | 2010-10-10 | C | 17 | 0.0025629 | 5.3394e-05
2011 | 2010-10-11 | C | 174 | 0.069406 | 0.0005465
2011 | 2010-10-11 | C | 161.1209 | 0.044533 | 0.00054022
2011 | 2010-09-17 | C | 8342 | 4.6375 | 0.026201
2011 | 2010-10-11 | C | 36.2388 | 0.075918 | 0.00052138
2011 | 2010-09-17 | C | 2319 | 1.2892 | 0.0072836
2011 | 2010-10-10 | B | 136 | 0.13797 | 0.00042715
2011 | 2010-10-11 | C | 2 | 0.00077892 | 6.2816e-06
2011 | 2010-10-11 | C | 6 | 0.0016584 | 1.8845e-05
2011 | 2010-10-11 | B | 161 | 0.019721 | 0.00050567
2011 | 2010-10-11 | C | 150.361 | 0.1124 | 0.00083232
2011 | 2010-10-11 | C | 4 | 0.0022363 | 1.2563e-05
2011 | 2010-10-11 | C | 1 | 0.00030152 | 3.1408e-06
2011 | 2010-10-11 | C | 283.4773 | 0.27156 | 0.0017966
2011 | 2010-10-11 | C | 26 | 0.0054713 | 8.1661e-05
2011 | 2010-10-11 | C | 89 | 0.015933 | 0.00027953
2011 | 2010-10-11 | C | 14 | 0.0032979 | 4.3972e-05
2011 | 2010-10-11 | C | 66 | 0.051409 | 0.00020729
2011 | 2010-10-11 | C | 61 | 0.0021075 | 0.00019159
2011 | 2010-10-11 | C | 473.5 | 0.046103 | 0.0014919
2011 | 2010-10-11 | C | 269 | 0.029571 | 0.00084488
2011 | 2010-10-11 | C | 475 | 0.041773 | 0.0014919
2011 | 2010-10-11 | C | 1343 | 0.11811 | 0.0042181
2011 | 2010-10-11 | C | 124.24 | 0.067117 | 0.00091084
2011 | 2010-10-11 | C | 20 | 0.0035177 | 6.2816e-05
2011 | 2010-10-11 | C | 622 | 0.63101 | 0.0019536
2011 | 2010-10-11 | C | 15.9098 | 0.074655 | 0.00045542
2011 | 2010-10-11 | B | 83 | 0.012252 | 0.00026069
2011 | 2010-10-12 | C | 324.8288 | 0.14589 | 0.0011872
2011 | 2010-10-12 | C | 239.3704 | 0.09924 | 0.0015484
2011 | 2010-10-12 | B | 57 | 0.047979 | 0.00017903
2011 | 2010-10-11 | B | 13 | 0.015148 | 4.0831e-05
2011 | 2010-10-12 | C | 30.3798 | 0.096944 | 0.00091084
2011 | 2010-10-12 | C | 527.0486 | 0.23341 | 0.0016866
2011 | 2010-10-12 | B | 8 | 0.0055027 | 2.5127e-05
2011 | 2010-10-11 | B | 10 | 0.0035491 | 3.1408e-05
2011 | 2010-10-12 | C | 202.1404 | 0.11111 | 0.00088257
2011 | 2010-10-13 | B | 7 | 0.0028581 | 2.1986e-05
2011 | 2010-10-13 | B | 94 | 0.058752 | 0.00029524
2011 | 2010-10-13 | C | 237.931 | 0.041101 | 0.0035428
2011 | 2010-10-11 | C | 89 | 0.38156 | 0.00027953
2011 | 2010-10-13 | B | 149 | 0.13618 | 0.00046798
2011 | 2010-10-13 | C | 26 | 0.0012249 | 8.1661e-05
2011 | 2010-10-13 | C | 31 | 0.0047709 | 9.7365e-05
2011 | 2010-10-14 | C | 218.6933 | 0.1099 | 0.0013977
2011 | 2010-10-14 | C | 190.8983 | 0.068951 | 0.0010899
2011 | 2010-10-12 | C | 103 | 0.016175 | 0.0003235
2011 | 2010-10-12 | C | 1 | 0.00015704 | 3.1408e-06
2011 | 2010-10-11 | C | 66 | 0.22927 | 0.00020729
2011 | 2010-10-11 | C | 31.6667 | 0.0041773 | 0.00019159
2011 | 2010-10-11 | C | 1 | 0.00052452 | 3.1408e-06
2011 | 2010-10-11 | C | 1 | 0.00055278 | 3.1408e-06
2011 | 2010-10-12 | C | 209 | 0.074833 | 0.00065643
2011 | 2010-10-11 | C | 578 | 0.58637 | 0.0018154
2011 | 2010-10-14 | C | 65.2049 | 0.075365 | 0.00049939
2011 | 2010-10-14 | B | 57 | 0.050486 | 0.00017903
2011 | 2010-10-14 | B | 13 | 0.013147 | 4.0831e-05
2011 | 2010-10-15 | B | 521 | 0.093273 | 0.0016364
2011 | 2010-10-14 | C | 5 | 0.0011621 | 1.5704e-05
2011 | 2010-10-14 | C | 163 | 0.021502 | 0.00051195
2011 | 2010-10-15 | B | 7 | 0.0032319 | 2.1986e-05
2011 | 2010-10-15 | C | 984 | 0.18234 | 0.0030906
2011 | 2010-10-15 | C | 19 | 0.0030435 | 5.9676e-05
2011 | 2010-10-15 | C | 115 | 0.019143 | 0.00036119
2011 | 2010-10-15 | C | 26.0364 | 0.00875 | 0.00015076
2011 | 2010-10-15 | B | 20.526 | 0.022113 | 0.00011621
2011 | 2010-10-15 | B | 33 | 0.020729 | 0.00010365
2011 | 2010-10-15 | B | 31 | 0.01626 | 9.7365e-05
2011 | 2010-10-15 | C | 38 | 0.03306 | 0.00011935
2011 | 2010-10-15 | C | 127.381 | 0.032407 | 0.00055593
2011 | 2010-10-16 | B | 1 | 0.00063131 | 3.1408e-06
2011 | 2010-10-16 | C | 37 | 0.0046484 | 0.00011621
2011 | 2010-10-16 | B | 10 | 0.0095481 | 3.1408e-05
2011 | 2010-10-16 | C | 67.875 | 0.028353 | 0.00055278
2011 | 2010-10-17 | C | 422 | 0.0066271 | 0.0013254
2011 | 2010-10-17 | B | 133 | 0.052216 | 0.00041773
2011 | 2010-10-17 | C | 375.3429 | 0.24403 | 0.0030592
2011 | 2010-10-17 | C | 2157 | 0.54198 | 0.0067748
2011 | 2010-10-17 | C | 152 | 0.035805 | 0.0004774
2011 | 2010-10-17 | C | 22 | 0.0050442 | 6.9098e-05
2011 | 2010-10-17 | C | 108.4103 | 0.038817 | 0.00058419
2011 | 2010-10-17 | C | 47.1486 | 0.021472 | 0.000223
2011 | 2010-10-17 | C | 311 | 0.049817 | 0.0009768
2011 | 2010-10-17 | C | 30 | 0.002921 | 9.4225e-05
2011 | 2010-10-17 | C | 571 | 0.095051 | 0.0017934
2011 | 2010-10-17 | C | 58 | 0.0074689 | 0.00018217
2011 | 2010-10-17 | C | 705 | 0.028786 | 0.0022143
2011 | 2010-10-17 | C | 19 | 0.0013129 | 5.9676e-05
2011 | 2010-10-17 | C | 578 | 0.029046 | 0.0018154
2011 | 2010-10-17 | C | 488.622 | 0.1903 | 0.0017243
2011 | 2010-10-17 | C | 240 | 0.22915 | 0.0007538
2011 | 2010-10-17 | C | 134.7292 | 0.079977 | 0.00077264
2011 | 2010-10-18 | C | 123 | 0.0015453 | 0.00038632
2011 | 2010-10-18 | C | 140 | 0.03122 | 0.00043972
2011 | 2010-10-17 | C | 229.2 | 0.062629 | 0.00092968
2011 | 2010-10-18 | C | 18 | 0.0027702 | 5.6535e-05
2011 | 2010-10-18 | B | 6 | 0.0067465 | 1.8845e-05
2011 | 2010-10-18 | B | 56 | 0.054349 | 0.00017589
2011 | 2010-10-18 | C | 57.3529 | 0.0055842 | 0.00031722
2011 | 2010-10-18 | C | 2443 | 0.14579 | 0.007673
2011 | 2010-10-18 | B | 5 | 0.0051195 | 1.5704e-05
2011 | 2010-10-18 | B | 94 | 0.055209 | 0.00029524
2011 | 2010-10-18 | B | 8 | 0.0027639 | 2.5127e-05
2011 | 2010-10-18 | C | 4 | 0.00052766 | 1.2563e-05
2011 | 2010-10-18 | C | 31 | 0.0069129 | 9.7365e-05
2011 | 2010-10-18 | B | 2 | 0.00031408 | 6.2816e-06
2011 | 2010-10-18 | C | 7 | 0.00087943 | 2.1986e-05
2011 | 2010-10-18 | C | 25 | 0.0048683 | 7.8521e-05
2011 | 2010-10-18 | C | 4 | 0.0025629 | 1.2563e-05
2011 | 2010-10-18 | C | 273.013 | 0.12948 | 0.0012877
2011 | 2010-10-19 | C | 22 | 0.0011056 | 6.9098e-05
2011 | 2010-10-19 | B | 6 | 0.0033544 | 1.8845e-05
2011 | 2010-10-19 | C | 20 | 0.012626 | 6.2816e-05
2011 | 2010-10-18 | C | 131.5685 | 0.059092 | 0.00053708
2011 | 2010-10-18 | C | 55.1818 | 0.11387 | 0.00021986
2011 | 2010-10-19 | B | 90 | 0.059644 | 0.00028267
2011 | 2010-10-19 | B | 87 | 0.0235 | 0.00027325
2011 | 2010-10-19 | B | 5 | 0.0055278 | 1.5704e-05
2011 | 2010-10-19 | B | 27 | 0.010346 | 8.4802e-05
2011 | 2010-10-19 | C | 27 | 0.0024593 | 8.4802e-05
2011 | 2010-10-18 | C | 15 | 0.0024498 | 4.7112e-05
2011 | 2010-10-19 | C | 15 | 0.0020729 | 4.7112e-05
2011 | 2010-10-18 | C | 45 | 0.0083389 | 0.00014134
2011 | 2010-10-18 | C | 3 | 0.00070668 | 9.4225e-06
2011 | 2010-10-18 | C | 4 | 0.0016081 | 1.2563e-05
2011 | 2010-10-19 | C | 31 | 0.002921 | 9.7365e-05
2011 | 2010-10-19 | C | 57 | 0.0062659 | 0.00017903
2011 | 2010-10-19 | B | 32 | 0.0041208 | 0.00010051
2011 | 2010-10-19 | C | 171.6667 | 0.053378 | 0.00070983
2011 | 2010-10-20 | C | 97.9176 | 0.025218 | 0.00071925
2011 | 2010-10-20 | B | 23 | 0.012425 | 7.2239e-05
2011 | 2010-10-20 | B | 65 | 0.067779 | 0.00020415
2011 | 2010-10-20 | B | 3 | 0.0031565 | 9.4225e-06
2011 | 2010-10-20 | B | 45 | 0.050881 | 0.00014134
2011 | 2010-10-20 | B | 2 | 8.1661e-05 | 6.2816e-06
2011 | 2010-10-21 | C | 77.0514 | 0.041625 | 0.00076008
2011 | 2010-10-21 | C | 232.8621 | 0.019016 | 0.00089828
2011 | 2010-10-21 | B | 2 | 0.0015955 | 6.2816e-06
2011 | 2010-10-21 | B | 1 | 0.00088571 | 3.1408e-06
2011 | 2010-10-21 | C | 25 | 0.005889 | 7.8521e-05
2011 | 2010-10-21 | C | 38 | 0.025302 | 0.00011935
2011 | 2010-10-21 | C | 114 | 0.061585 | 0.00035805
2011 | 2010-10-21 | C | 186 | 0.069519 | 0.00058419
2011 | 2010-10-21 | C | 35 | 0.026493 | 0.00010993
2011 | 2010-10-21 | C | 25 | 0.011621 | 7.8521e-05
2011 | 2010-10-22 | C | 135 | 0.055121 | 0.00042401
2011 | 2010-10-22 | C | 113.6075 | 0.037109 | 0.0012815
2011 | 2010-10-21 | C | 38.4443 | 0.15782 | 0.00020101
2011 | 2010-10-22 | B | 1 | 9.7365e-05 | 3.1408e-06
2011 | 2010-10-22 | B | 25 | 0.028346 | 7.8521e-05
2011 | 2010-10-22 | C | 670 | 0.11995 | 0.0021044
2011 | 2010-10-22 | C | 2 | 0.00077264 | 6.2816e-06
2011 | 2010-10-23 | C | 697.844 | 0.23233 | 0.0025158
2011 | 2010-10-23 | C | 75 | 0.020965 | 0.00023556
2011 | 2010-10-23 | C | 16 | 0.0031659 | 5.0253e-05
2011 | 2010-10-24 | C | 304.1413 | 0.1729 | 0.0014793
2011 | 2010-10-24 | C | 3 | 0.0071045 | 9.4225e-06
2011 | 2010-10-26 | B | 3 | 0.00041459 | 9.4225e-06
2011 | 2010-10-26 | B | 5 | 0.0012563 | 1.5704e-05
2011 | 2010-10-26 | B | 12 | 0.0079149 | 3.769e-05
2011 | 2010-10-26 | B | 10 | 0.0013191 | 3.1408e-05
2011 | 2010-10-26 | B | 126 | 0.065693 | 0.00039574
2011 | 2010-10-26 | B | 7 | 0.0028142 | 2.1986e-05
2011 | 2010-10-26 | B | 2 | 0.0022363 | 6.2816e-06
2011 | 2010-10-26 | B | 169 | 0.089705 | 0.0005308
2011 | 2010-10-26 | C | 287.194 | 0.1786 | 0.0021923
2011 | 2010-10-26 | C | 20.589 | 0.023409 | 0.0001696
2011 | 2010-10-26 | B | 2 | 0.0027828 | 6.2816e-06
2011 | 2010-10-26 | B | 53 | 0.013484 | 0.00016646
2011 | 2010-10-27 | B | 96 | 0.017187 | 0.00030152
2011 | 2010-10-27 | B | 82 | 0.01468 | 0.00025755
2011 | 2010-10-27 | C | 2 | 0.00045228 | 6.2816e-06
2011 | 2010-10-27 | C | 340 | 0.14096 | 0.0010679
2011 | 2010-10-27 | C | 13 | 0.0020415 | 4.0831e-05
2011 | 2010-10-27 | C | 18 | 0.0023745 | 5.6535e-05
2011 | 2010-10-27 | B | 20 | 0.011621 | 6.2816e-05
2011 | 2010-10-27 | C | 287 | 0.01262 | 0.00090142
2011 | 2010-10-27 | C | 6 | 0.00045228 | 1.8845e-05
2011 | 2010-10-27 | B | 282 | 0.19486 | 0.00088571
2011 | 2010-10-27 | B | 2 | 0.0024373 | 6.2816e-06
2011 | 2010-10-27 | B | 178 | 0.21412 | 0.00055907
2011 | 2010-10-27 | B | 2 | 0.0026194 | 6.2816e-06
2011 | 2010-10-27 | C | 93.5581 | 0.037025 | 0.00050567
2011 | 2010-10-27 | C | 204.6163 | 0.053341 | 0.0021954
2011 | 2010-10-27 | C | 166 | 0.0078206 | 0.00052138
2011 | 2010-10-27 | C | 163 | 0.0097271 | 0.00051195
2011 | 2010-10-27 | B | 65 | 0.013882 | 0.00020415
2011 | 2010-10-28 | B | 68 | 0.0098245 | 0.00021358
2011 | 2010-10-28 | C | 113 | 0.004259 | 0.00035491
2011 | 2010-10-28 | B | 12 | 0.0047866 | 3.769e-05
2011 | 2010-10-28 | C | 3434 | 0.28043 | 0.010786
2011 | 2010-10-28 | B | 90 | 0.070951 | 0.00028267
2011 | 2010-10-28 | B | 62 | 0.056277 | 0.00019473
2011 | 2010-10-28 | B | 2 | 0.0026823 | 6.2816e-06
2011 | 2010-10-12 | B | 76 | 0.037954 | 0.0002387
2011 | 2010-10-28 | C | 128.2857 | 0.021355 | 0.00045542
2011 | 2010-10-29 | B | 56 | 0.012312 | 0.00017589
2011 | 2010-10-29 | C | 733 | 0.16116 | 0.0023022
2011 | 2010-10-29 | B | 5 | 0.0013663 | 1.5704e-05
2011 | 2010-10-29 | B | 2 | 0.0025629 | 6.2816e-06
2011 | 2010-10-29 | C | 367.0278 | 0.20404 | 0.0016489
2011 | 2010-10-29 | B | 101 | 0.022206 | 0.00031722
2011 | 2010-10-14 | B | 1 | 0.00038946 | 3.1408e-06
2011 | 2010-10-30 | B | 1 | 0.0011213 | 3.1408e-06
2011 | 2010-10-29 | C | 171.2898 | 0.093072 | 0.00070668
2011 | 2010-10-30 | C | 38 | 0.019454 | 0.00011935
2011 | 2010-10-30 | C | 744 | 0.2033 | 0.0023368
2011 | 2010-10-13 | B | 1 | 0.0004774 | 3.1408e-06
2011 | 2010-10-28 | C | 61 | 0.011687 | 0.00019159
2011 | 2010-10-05 | B | 58 | 0.075964 | 0.00018217
2011 | 2010-10-30 | C | 119.5422 | 0.0612 | 0.00063759
2011 | 2010-10-30 | C | 100.5221 | 0.041991 | 0.00042401
2011 | 2010-10-30 | C | 49.2451 | 0.038667 | 0.00026069
2011 | 2010-10-30 | C | 4 | 0.0031157 | 1.2563e-05
2011 | 2010-10-30 | B | 384 | 0.11096 | 0.0012061
2011 | 2010-10-30 | C | 87.581 | 0.048413 | 0.00044914
2011 | 2010-10-31 | C | 207.8223 | 0.156 | 0.002142
2011 | 2010-10-31 | B | 1 | 0.00028896 | 3.1408e-06
2011 | 2010-10-30 | C | 82 | 0.086536 | 0.00025755
2011 | 2010-10-31 | B | 3 | 0.0050033 | 9.4225e-06
2011 | 2010-10-30 | C | 100 | 0.060932 | 0.00031408
2011 | 2010-11-01 | C | 177 | 0.0016678 | 0.00055593
2011 | 2010-11-01 | C | 963 | 0.0090738 | 0.0030246
2011 | 2010-11-01 | C | 16 | 0.0047238 | 5.0253e-05
2011 | 2010-11-01 | B | 75 | 0.026147 | 0.00023556
2011 | 2010-11-01 | B | 117 | 0.031603 | 0.00036748
2011 | 2010-11-01 | B | 5 | 0.0027168 | 1.5704e-05
2011 | 2010-11-01 | B | 7 | 0.0007695 | 2.1986e-05
2011 | 2010-10-07 | B | 79 | 0.058806 | 0.00024812
2011 | 2010-11-01 | C | 99.8308 | 0.01944 | 0.0003769
2011 | 2010-11-02 | C | 3 | 0.002431 | 9.4225e-06
2011 | 2010-11-02 | B | 57 | 0.028107 | 0.00017903
2011 | 2010-11-02 | B | 59 | 0.035023 | 0.00018531
2011 | 2010-11-02 | C | 288 | 0.010855 | 0.00090456
2011 | 2010-11-02 | C | 229.354 | 0.07924 | 0.00091084
2011 | 2010-11-03 | C | 1357 | 0.21737 | 0.0042621
2011 | 2010-11-03 | B | 43 | 0.0036465 | 0.00013506
2011 | 2010-11-03 | C | 219 | 0.016508 | 0.00068784
2011 | 2010-11-03 | B | 2 | 0.0012124 | 6.2816e-06
2011 | 2010-11-03 | B | 91 | 0.023437 | 0.00028581
2011 | 2010-11-03 | C | 1284 | 0.22987 | 0.0040328
2011 | 2010-11-03 | C | 416.9457 | 0.11655 | 0.0013537
2011 | 2010-11-03 | B | 21 | 0.0052766 | 6.5957e-05
2011 | 2010-11-03 | C | 31.2958 | 0.027621 | 0.00013506
2011 | 2010-11-04 | B | 80 | 0.014322 | 0.00025127
2011 | 2010-11-03 | C | 43 | 0.0025661 | 0.00013506
2011 | 2010-11-02 | C | 56.0717 | 0.046141 | 0.00061874
2011 | 2010-11-03 | B | 56 | 0.019875 | 0.00017589
2011 | 2010-11-04 | B | 14 | 0.0016269 | 4.3972e-05
2011 | 2010-11-04 | C | 3 | 0.002431 | 9.4225e-06
2011 | 2010-11-04 | B | 641 | 0.44091 | 0.0020133
2011 | 2010-11-04 | B | 65 | 0.057775 | 0.00020415
2011 | 2010-11-04 | C | 173.1128 | 0.143 | 0.0019662
2011 | 2010-11-04 | C | 283.3032 | 0.16461 | 0.0024875
2011 | 2010-11-04 | C | 28 | 0.032451 | 8.7943e-05
2011 | 2010-11-05 | C | 100 | 0.11935 | 0.00031408
2011 | 2010-11-04 | C | 191 | 0.062389 | 0.0005999
2011 | 2010-11-05 | C | 147 | 0.064176 | 0.00087629
2011 | 2010-11-05 | C | 55.2101 | 0.08861 | 0.00071925
2011 | 2010-11-05 | C | 267.7671 | 0.12026 | 0.0010742
2011 | 2010-11-05 | C | 186 | 0.1443 | 0.00058419
2011 | 2010-11-05 | B | 47 | 0.047386 | 0.00014762
2011 | 2010-11-05 | C | 773 | 0.014567 | 0.0024279
2011 | 2010-11-05 | C | 363.1512 | 0.29085 | 0.0017275
2011 | 2010-11-06 | C | 298.4602 | 0.10312 | 0.0010804
2011 | 2010-11-06 | C | 386.1484 | 0.18435 | 0.0042778
2011 | 2010-11-06 | C | 862 | 0.17327 | 0.0027074
2011 | 2010-11-06 | C | 27 | 0.012551 | 8.4802e-05
2011 | 2010-11-06 | B | 3 | 0.0017808 | 9.4225e-06
2011 | 2010-11-06 | C | 100 | 0.041773 | 0.00031408
2011 | 2010-11-07 | C | 658.0959 | 0.14469 | 0.0024498
2011 | 2010-11-06 | C | 21 | 0.0033638 | 6.5957e-05
2011 | 2010-11-06 | C | 79.2451 | 0.050028 | 0.00090456
2011 | 2010-11-07 | C | 15 | 0.0026383 | 4.7112e-05
2011 | 2010-11-07 | C | 486 | 0.09006 | 0.0015264
2011 | 2010-11-08 | C | 3 | 0.0014699 | 9.4225e-06
2011 | 2010-11-08 | B | 2 | 0.00027011 | 6.2816e-06
2011 | 2010-11-08 | C | 13 | 0.0022049 | 4.0831e-05
2011 | 2010-11-08 | B | 1 | 5.6535e-05 | 3.1408e-06
2011 | 2010-11-08 | B | 4 | 0.0011056 | 1.2563e-05
2011 | 2010-11-08 | B | 1 | 0.00042401 | 3.1408e-06
2011 | 2010-11-09 | B | 85 | 0.017086 | 0.00026697
2011 | 2010-11-09 | C | 112 | 0.034474 | 0.00035177
2011 | 2010-11-09 | B | 7 | 0.0018688 | 2.1986e-05
2011 | 2010-11-09 | B | 6 | 0.0029398 | 1.8845e-05
2011 | 2010-11-09 | B | 77 | 0.060945 | 0.00024184
2011 | 2010-11-09 | B | 8 | 0.0087189 | 2.5127e-05
2011 | 2010-11-09 | B | 1 | 0.00040203 | 3.1408e-06
2011 | 2010-11-09 | B | 154 | 0.038211 | 0.00048369
2011 | 2010-11-09 | B | 19 | 0.021304 | 5.9676e-05
2011 | 2010-11-09 | B | 27 | 0.024253 | 8.4802e-05
2011 | 2010-11-09 | C | 15 | 0.026524 | 4.7112e-05
2011 | 2010-11-09 | C | 9 | 0.0034769 | 2.8267e-05
2011 | 2010-11-09 | C | 36 | 0.058118 | 0.00011307
2011 | 2010-11-09 | C | 3 | 0.0028079 | 9.4225e-06
2011 | 2010-11-09 | C | 929.2727 | 0.18388 | 0.0029272
2011 | 2010-11-10 | C | 167.7295 | 0.06269 | 0.0013348
2011 | 2010-11-10 | C | 963 | 0.036295 | 0.0030246
2011 | 2010-11-10 | C | 28 | 0.0065078 | 8.7943e-05
2011 | 2010-11-10 | C | 45 | 0.012579 | 0.00014134
2011 | 2010-11-10 | C | 2 | 0.00032036 | 6.2816e-06
2011 | 2010-11-10 | B | 10 | 0.010867 | 3.1408e-05
2011 | 2010-11-10 | B | 2 | 0.0022425 | 6.2816e-06
2011 | 2010-11-11 | B | 45 | 0.026571 | 0.00014134
2011 | 2010-11-11 | B | 120 | 0.057665 | 0.0003769
2011 | 2010-11-11 | C | 126 | 0.082315 | 0.00039574
2011 | 2010-11-11 | C | 267.5658 | 0.061347 | 0.00085116
2011 | 2010-11-11 | C | 2853 | 0.17922 | 0.0089608
2011 | 2010-11-11 | C | 3324.3636 | 0.08353 | 0.011772
2011 | 2010-11-11 | B | 63 | 0.025921 | 0.00019787
2011 | 2010-11-11 | C | 2824.5357 | 0.47018 | 0.0089608
2011 | 2010-11-11 | B | 34 | 0.025843 | 0.00010679
2011 | 2010-11-11 | C | 37 | 0.032539 | 0.00011621
2011 | 2010-11-11 | B | 200 | 0.058419 | 0.00062816
2011 | 2010-11-11 | C | 2726.6667 | 0.025692 | 0.012965
2011 | 2010-11-12 | B | 5 | 0.0030152 | 1.5704e-05
2011 | 2010-11-12 | B | 8 | 0.0059801 | 2.5127e-05
2011 | 2010-11-12 | C | 39 | 0.0094319 | 0.00012249
2011 | 2010-11-12 | C | 33.8596 | 0.017866 | 0.00015704
2011 | 2010-11-13 | C | 272.9686 | 0.16118 | 0.0025346
2011 | 2010-11-12 | C | 22 | 0.0013129 | 6.9098e-05
2011 | 2010-11-12 | C | 149.2171 | 0.15185 | 0.0011464
2011 | 2010-11-12 | C | 5 | 0.0011935 | 1.5704e-05
2011 | 2010-11-12 | C | 58 | 0.005465 | 0.00018217
2011 | 2010-11-14 | C | 34.3704 | 0.017164 | 0.00051195
2011 | 2010-11-14 | C | 65 | 0.049813 | 0.00020415
2011 | 2010-11-14 | C | 10 | 0.0029838 | 3.1408e-05
2011 | 2010-11-14 | C | 54 | 0.022388 | 0.0001696
2011 | 2010-11-14 | C | 36 | 0.0041836 | 0.00011307
2011 | 2010-11-14 | C | 100.1961 | 0.079304 | 0.00063445
2011 | 2010-11-14 | C | 160 | 0.035177 | 0.00050253
2011 | 2010-11-14 | C | 150.4841 | 0.058135 | 0.00086059
2011 | 2010-11-14 | C | 104 | 0.016659 | 0.00032665
2011 | 2010-11-15 | C | 193.3415 | 0.07287 | 0.00070668
2011 | 2010-11-15 | C | 466.3939 | 0.092286 | 0.0016929
2011 | 2010-10-28 | B | 14 | 0.006112 | 4.3972e-05
2011 | 2010-10-28 | B | 6 | 0.0026571 | 1.8845e-05
2011 | 2010-11-12 | B | 63 | 0.057185 | 0.00019787
2011 | 2010-11-15 | C | 14 | 0.0033858 | 4.3972e-05
2011 | 2010-11-15 | C | 62 | 0.012073 | 0.00019473
2011 | 2010-11-15 | C | 204.0264 | 0.19224 | 0.0011935
2011 | 2010-11-15 | C | 410.0938 | 0.07857 | 0.0017871
2011 | 2010-11-15 | B | 92 | 0.025139 | 0.00028896
2011 | 2010-11-16 | B | 92 | 0.025717 | 0.00028896
2011 | 2010-11-15 | B | 33 | 0.019693 | 0.00010365
2011 | 2010-11-15 | B | 34 | 0.020076 | 0.00010679
2011 | 2010-11-16 | B | 4 | 0.003078 | 1.2563e-05
2011 | 2010-11-16 | B | 50 | 0.031722 | 0.00015704
2011 | 2010-11-16 | C | 67.4273 | 0.18721 | 0.00093911
2011 | 2010-11-16 | B | 1 | 0.0010522 | 3.1408e-06
2011 | 2010-11-16 | B | 26 | 0.034053 | 8.1661e-05
2011 | 2010-11-16 | B | 18 | 0.023123 | 5.6535e-05
2011 | 2010-11-16 | C | 70.8087 | 0.11676 | 0.00026069
2011 | 2010-11-16 | C | 58.8261 | 0.033442 | 0.00020101
2011 | 2010-11-17 | B | 60 | 0.037313 | 0.00018845
2011 | 2010-11-16 | C | 37 | 0.0039512 | 0.00011621
2011 | 2010-11-16 | B | 7 | 0.0052106 | 2.1986e-05
2011 | 2010-11-17 | B | 2 | 0.0022425 | 6.2816e-06
2011 | 2010-11-17 | B | 112 | 0.12312 | 0.00035177
2011 | 2010-11-17 | B | 13 | 0.011065 | 4.0831e-05
2011 | 2010-11-17 | B | 6 | 0.0029587 | 1.8845e-05
2011 | 2010-11-17 | B | 7 | 0.0067057 | 2.1986e-05
2011 | 2010-11-17 | C | 2522.6154 | 0.18223 | 0.013125
2011 | 2010-11-17 | B | 299 | 0.056346 | 0.00093911
2011 | 2010-11-17 | C | 146 | 0.04769 | 0.00045856
2011 | 2010-11-17 | C | 50 | 0.0036119 | 0.00015704
2011 | 2010-11-17 | C | 21 | 0.0021106 | 6.5957e-05
2011 | 2010-11-17 | C | 7 | 0.0031659 | 2.1986e-05
2011 | 2010-11-17 | B | 53 | 0.017812 | 0.00016646
2011 | 2010-11-18 | C | 248 | 0.011684 | 0.00077892
2011 | 2010-11-18 | B | 178 | 0.13865 | 0.00055907
2011 | 2010-11-18 | B | 6 | 0.0047489 | 1.8845e-05
2011 | 2010-11-18 | B | 26 | 0.029153 | 8.1661e-05
2011 | 2010-11-18 | B | 25 | 0.014134 | 7.8521e-05
2011 | 2010-11-18 | C | 17 | 0.0023493 | 5.3394e-05
2011 | 2010-11-18 | C | 81.14 | 0.062947 | 0.00038632
2011 | 2010-11-18 | B | 299 | 0.081702 | 0.00093911
2011 | 2010-11-19 | C | 1018 | 0.038368 | 0.0031974
2011 | 2010-11-19 | B | 111 | 0.033469 | 0.00034863
2011 | 2010-11-19 | B | 19 | 0.0046547 | 5.9676e-05
2011 | 2010-11-19 | B | 111 | 0.050552 | 0.00034863
2011 | 2010-11-19 | B | 24 | 0.029247 | 7.538e-05
2011 | 2010-11-20 | C | 272 | 0.01196 | 0.0008543
2011 | 2010-11-20 | C | 518.25 | 0.13185 | 0.0019724
2011 | 2010-11-20 | C | 61.4432 | 0.035123 | 0.00048997
2011 | 2010-11-19 | C | 6 | 0.018958 | 1.8845e-05
2011 | 2010-11-20 | C | 271 | 0.057028 | 0.00085116
2011 | 2010-11-20 | C | 392.8899 | 0.1308 | 0.0018751
2011 | 2010-11-20 | C | 6 | 0.001941 | 1.8845e-05
2011 | 2010-11-20 | C | 11 | 0.00065643 | 3.4549e-05
2011 | 2010-11-21 | C | 53 | 0.004661 | 0.00016646
2011 | 2010-11-20 | C | 108 | 0.070895 | 0.00033921
2011 | 2010-11-21 | C | 262.9412 | 0.10984 | 0.00090456
2011 | 2010-11-21 | C | 265 | 0.049107 | 0.00083232
2011 | 2010-11-21 | C | 116 | 0.12132 | 0.00036434
2011 | 2010-11-21 | C | 563 | 0.077804 | 0.0017683
2011 | 2010-11-21 | C | 87.686 | 0.070229 | 0.00033293
2011 | 2010-11-20 | C | 1126.9123 | 0.19113 | 0.0035648
2011 | 2010-11-21 | C | 1 | 0.00028581 | 3.1408e-06
2011 | 2010-11-21 | C | 1108.6094 | 1.3266 | 0.0053645
2011 | 2010-11-21 | C | 349.8667 | 0.079119 | 0.0012877
2011 | 2010-11-21 | C | 32.2756 | 0.01257 | 0.00016332
2011 | 2010-11-22 | C | 962 | 0.051365 | 0.0030215
2011 | 2010-11-22 | B | 18 | 0.015321 | 5.6535e-05
2011 | 2010-11-22 | B | 2 | 0.0015767 | 6.2816e-06
2011 | 2010-11-22 | C | 32 | 0.022915 | 0.00010051
2011 | 2010-11-22 | C | 47.2837 | 0.031484 | 0.00025127
2011 | 2010-11-22 | B | 135 | 0.06869 | 0.00042401
2011 | 2010-11-23 | C | 93 | 0.0043814 | 0.0002921
2011 | 2010-11-23 | C | 1287.1781 | 0.57812 | 0.012274
2011 | 2010-11-23 | C | 233 | 0.030736 | 0.00073181
2011 | 2010-11-23 | B | 85 | 0.029367 | 0.00026697
2011 | 2010-11-23 | C | 178 | 0.0016772 | 0.00055907
2011 | 2010-11-23 | B | 5 | 0.0047426 | 1.5704e-05
2011 | 2010-11-23 | B | 58 | 0.022771 | 0.00018217
2011 | 2010-11-23 | C | 142 | 0.0084739 | 0.000446
2011 | 2010-11-23 | C | 93 | 0.0084708 | 0.0002921
2011 | 2010-11-23 | B | 4 | 0.0044851 | 1.2563e-05
2011 | 2010-11-19 | B | 125 | 0.045149 | 0.0003926
2011 | 2010-11-23 | C | 55.6935 | 0.032011 | 0.0002921
2011 | 2010-11-24 | C | 974.2843 | 0.30295 | 0.0060995
2011 | 2010-11-24 | B | 120 | 0.12626 | 0.0003769
2011 | 2010-11-24 | B | 117 | 0.054019 | 0.00036748
2011 | 2010-11-24 | B | 24 | 0.029398 | 7.538e-05
2011 | 2010-11-24 | B | 77 | 0.09311 | 0.00024184
2011 | 2010-11-24 | B | 32 | 0.02985 | 0.00010051
2011 | 2010-11-24 | B | 112 | 0.12558 | 0.00035177
2011 | 2010-11-23 | B | 26 | 0.029153 | 8.1661e-05
2011 | 2010-11-24 | C | 60 | 0.018468 | 0.00018845
2011 | 2010-11-25 | C | 106.2207 | 0.047374 | 0.00065957
2011 | 2010-11-25 | B | 3 | 0.0025441 | 9.4225e-06
2011 | 2010-11-25 | B | 103 | 0.048849 | 0.0003235
2011 | 2010-11-25 | C | 148.1433 | 0.13493 | 0.0010804
2011 | 2010-11-25 | B | 8 | 0.0076887 | 2.5127e-05
2011 | 2010-11-25 | B | 90 | 0.11222 | 0.00028267
2011 | 2010-11-25 | C | 17 | 0.010999 | 5.3394e-05
2011 | 2010-11-25 | B | 18 | 0.02284 | 5.6535e-05
2011 | 2010-11-25 | B | 7 | 0.0019128 | 2.1986e-05
2011 | 2010-11-25 | B | 33 | 0.044154 | 0.00010365
2011 | 2010-11-25 | B | 18 | 0.014416 | 5.6535e-05
2011 | 2010-11-25 | C | 387.6579 | 0.088882 | 0.0013348
2011 | 2010-11-23 | B | 40 | 0.044851 | 0.00012563
2011 | 2010-11-23 | B | 8 | 0.0082164 | 2.5127e-05
2011 | 2010-11-26 | C | 142.2532 | 0.033956 | 0.00072553
2011 | 2010-11-26 | B | 3 | 0.0014699 | 9.4225e-06
2011 | 2010-11-26 | B | 7 | 0.0029241 | 2.1986e-05
2011 | 2010-11-26 | B | 59 | 0.062449 | 0.00018531
2011 | 2010-11-26 | B | 3 | 0.0042118 | 9.4225e-06
2011 | 2010-11-27 | B | 280 | 0.13543 | 0.00087943
2011 | 2010-11-27 | B | 5 | 0.0018845 | 1.5704e-05
2011 | 2010-11-25 | C | 98.5284 | 0.053537 | 0.0012375
2011 | 2010-11-28 | B | 13 | 0.0075945 | 4.0831e-05
2011 | 2010-11-28 | C | 18 | 0.015943 | 5.6535e-05
2011 | 2010-11-29 | C | 530.8571 | 0.13505 | 0.0023273
2011 | 2010-11-29 | C | 13 | 0.010493 | 4.0831e-05
2011 | 2010-11-29 | C | 10 | 0.0021044 | 3.1408e-05
2011 | 2010-11-29 | B | 354 | 0.16789 | 0.0011119
2011 | 2010-11-29 | B | 2 | 0.0019976 | 6.2816e-06
2011 | 2010-11-29 | B | 318 | 0.15681 | 0.00099878
2011 | 2010-11-29 | C | 105 | 0.012532 | 0.00032979
2011 | 2010-11-29 | B | 163 | 0.057339 | 0.00051195
2011 | 2010-11-29 | C | 2 | 0.0070292 | 6.2816e-06
2011 | 2010-11-30 | C | 55 | 0.0055278 | 0.00017275
2011 | 2010-11-30 | B | 25 | 0.017117 | 7.8521e-05
2011 | 2010-11-30 | B | 30 | 0.020447 | 9.4225e-05
2011 | 2010-11-30 | B | 25 | 0.0056535 | 7.8521e-05
2011 | 2010-11-29 | B | 1 | 0.00042087 | 3.1408e-06
2011 | 2010-11-30 | B | 9 | 0.0084237 | 2.8267e-05
2011 | 2010-11-30 | B | 44 | 0.047539 | 0.0001382
2011 | 2010-11-30 | B | 1 | 0.0011527 | 3.1408e-06
2011 | 2010-11-30 | B | 12 | 0.005352 | 3.769e-05
2011 | 2010-11-30 | B | 57 | 0.015933 | 0.00017903
2011 | 2010-11-30 | B | 24 | 0.026911 | 7.538e-05
2011 | 2010-11-30 | B | 34 | 0.010892 | 0.00010679
2011 | 2010-11-09 | B | 22 | 0.023355 | 6.9098e-05
2011 | 2010-12-01 | B | 1 | 0.00074437 | 3.1408e-06
2011 | 2010-12-01 | B | 37 | 0.041487 | 0.00011621
2011 | 2010-12-01 | B | 112 | 0.13614 | 0.00035177
2011 | 2010-12-01 | B | 436 | 0.22869 | 0.0013694
2011 | 2010-12-01 | B | 55 | 0.053897 | 0.00017275
2011 | 2010-11-30 | C | 59 | 0.017048 | 0.00018531
2011 | 2010-12-02 | C | 3 | 0.00028267 | 9.4225e-06
2011 | 2010-12-02 | B | 169 | 0.15234 | 0.0005308
2011 | 2010-12-02 | B | 112 | 0.13262 | 0.00035177
2011 | 2010-12-02 | C | 102 | 0.007048 | 0.00032036
2011 | 2010-12-02 | C | 47 | 0.0010333 | 0.00014762
2011 | 2010-12-01 | C | 295.52 | 0.25246 | 0.0020981
2011 | 2010-12-03 | C | 131 | 0.071592 | 0.00041145
2011 | 2010-12-01 | C | 48 | 0.013116 | 0.00015076
2011 | 2010-12-03 | C | 116 | 0.080882 | 0.00036434
2011 | 2010-12-03 | B | 16 | 0.0096486 | 5.0253e-05
2011 | 2010-12-03 | B | 3 | 0.003034 | 9.4225e-06
2011 | 2010-12-03 | B | 41 | 0.011203 | 0.00012877
2011 | 2010-12-03 | B | 9 | 0.006558 | 2.8267e-05
2011 | 2010-12-03 | B | 95 | 0.0080562 | 0.00029838
2011 | 2010-12-03 | C | 317 | 0.10554 | 0.0013694
2011 | 2010-12-03 | C | 211.9139 | 0.35342 | 0.0012406
2011 | 2010-12-04 | C | 824.252 | 0.32101 | 0.0051101
2011 | 2010-12-04 | C | 2 | 0.00082918 | 6.2816e-06
2011 | 2010-12-04 | C | 315 | 0.01484 | 0.00098936
2011 | 2010-12-04 | B | 1 | 0.00048369 | 3.1408e-06
2011 | 2010-12-04 | C | 87 | 0.01011 | 0.00027325
2011 | 2010-12-04 | C | 807.5253 | 0.24348 | 0.0025912
2011 | 2010-12-03 | C | 228 | 0.097391 | 0.00071611
2011 | 2010-12-05 | B | 13 | 0.004818 | 4.0831e-05
2011 | 2010-12-04 | C | 10 | 0.03948 | 3.1408e-05
2011 | 2010-12-06 | C | 1 | 0.00013191 | 3.1408e-06
2011 | 2010-12-06 | C | 89 | 0.0030749 | 0.00027953
2011 | 2010-12-06 | B | 26 | 0.028908 | 8.1661e-05
2011 | 2010-12-06 | B | 6 | 0.0075568 | 1.8845e-05
2011 | 2010-12-06 | C | 191.6158 | 0.25036 | 0.0019505
2011 | 2010-12-07 | C | 96.5401 | 0.16525 | 0.0008543
2011 | 2010-12-06 | B | 13 | 0.012413 | 4.0831e-05
2011 | 2010-12-06 | B | 70 | 0.010333 | 0.00021986
2011 | 2010-12-06 | B | 6 | 0.0093848 | 1.8845e-05
2011 | 2010-12-07 | B | 28 | 0.034913 | 8.7943e-05
2011 | 2010-12-07 | B | 24 | 0.035052 | 7.538e-05
2011 | 2010-12-07 | B | 90 | 0.092434 | 0.00028267
2011 | 2010-12-07 | B | 75 | 0.07114 | 0.00023556
2011 | 2010-12-07 | B | 23 | 0.02131 | 7.2239e-05
2011 | 2010-12-07 | B | 27 | 0.0073778 | 8.4802e-05
2011 | 2010-12-07 | C | 274.0179 | 0.18934 | 0.0014008
2011 | 2010-12-07 | B | 1 | 0.00028267 | 3.1408e-06
2011 | 2010-12-07 | B | 3 | 0.003279 | 9.4225e-06
2011 | 2010-11-22 | B | 2 | 0.0020541 | 6.2816e-06
2011 | 2010-12-07 | B | 2 | 0.0017023 | 6.2816e-06
2011 | 2010-12-07 | B | 27 | 0.0061906 | 8.4802e-05
2011 | 2010-12-08 | B | 14 | 0.0020667 | 4.3972e-05
2011 | 2010-12-08 | C | 380 | 0.013129 | 0.0011935
2011 | 2010-12-08 | B | 2 | 0.0013945 | 6.2816e-06
2011 | 2010-12-08 | C | 15 | 0.001272 | 4.7112e-05
2011 | 2010-12-08 | B | 112 | 0.10377 | 0.00035177
2011 | 2010-12-08 | B | 94 | 0.034543 | 0.00029524
2011 | 2010-12-08 | B | 51 | 0.025629 | 0.00016018
2011 | 2010-12-08 | B | 55.1667 | 0.061857 | 0.00035177
2011 | 2010-12-08 | B | 31 | 0.030767 | 9.7365e-05
2011 | 2010-12-08 | B | 1 | 0.00054964 | 3.1408e-06
2011 | 2010-12-09 | C | 134.1302 | 0.15082 | 0.0012406
2011 | 2010-12-09 | B | 6 | 0.0050128 | 1.8845e-05
2011 | 2010-12-09 | B | 45 | 0.025017 | 0.00014134
2011 | 2010-12-09 | C | 10 | 0.0027953 | 3.1408e-05
2011 | 2010-12-08 | B | 4 | 0.022388 | 1.2563e-05
2011 | 2010-12-09 | B | 65 | 0.072883 | 0.00020415
2011 | 2010-12-08 | B | 8 | 0.0089702 | 2.5127e-05
2011 | 2010-12-09 | B | 69.985 | 0.087265 | 0.00073809
2011 | 2010-12-09 | C | 687 | 0.0021577 | 0.0021577
2011 | 2010-12-09 | C | 171 | 0.00053708 | 0.00053708
2011 | 2010-12-09 | B | 21 | 0.007717 | 6.5957e-05
2011 | 2010-12-10 | B | 215.1538 | 0.14732 | 0.00074752
2011 | 2010-12-10 | B | 13 | 0.0011024 | 4.0831e-05
2011 | 2010-12-10 | B | 209 | 0.11619 | 0.00065643
2011 | 2010-12-10 | B | 26 | 0.029153 | 8.1661e-05
2011 | 2010-12-10 | B | 2 | 0.0001696 | 6.2816e-06
2011 | 2010-12-10 | B | 15 | 0.01616 | 4.7112e-05
2011 | 2010-12-10 | B | 3 | 0.0030811 | 9.4225e-06
2011 | 2010-12-10 | B | 1 | 0.00034863 | 3.1408e-06
2011 | 2010-12-10 | C | 37.0586 | 0.063202 | 0.00027011
2011 | 2010-12-10 | C | 73 | 0.015362 | 0.00022928
2011 | 2010-12-10 | C | 327 | 0.012325 | 0.001027
2011 | 2010-12-10 | C | 80 | 0.031911 | 0.00025127
2011 | 2010-12-10 | B | 45 | 0.026571 | 0.00014134
2011 | 2010-12-11 | C | 178 | 0.0089451 | 0.00055907
2011 | 2010-12-11 | C | 263 | 0.0099124 | 0.00082604
2011 | 2010-12-11 | B | 1 | 0.00045228 | 3.1408e-06
2011 | 2010-12-11 | B | 1 | 7.2239e-05 | 3.1408e-06
2011 | 2010-12-11 | C | 44.2627 | 0.015987 | 0.00020729
2011 | 2010-12-11 | C | 24 | 0.0020353 | 7.538e-05
2011 | 2010-12-11 | C | 18 | 0.0016395 | 5.6535e-05
2011 | 2010-12-11 | C | 28 | 0.0025503 | 8.7943e-05
2011 | 2010-12-11 | B | 102 | 0.0044851 | 0.00032036
2011 | 2010-12-11 | C | 183.9252 | 0.060078 | 0.00095795
2011 | 2010-12-11 | C | 118.7249 | 0.12902 | 0.0028236
2011 | 2010-12-12 | C | 275 | 0.0017275 | 0.00086373
2011 | 2010-12-12 | C | 167 | 0.0073432 | 0.00052452
2011 | 2010-12-12 | B | 34 | 0.013669 | 0.00010679
2011 | 2010-12-12 | B | 2 | 0.0008229 | 6.2816e-06
2011 | 2010-12-12 | C | 141.4818 | 0.059545 | 0.00080091
2011 | 2010-12-13 | C | 56 | 0.0021106 | 0.00017589
2011 | 2010-12-11 | B | 1 | 0.0010899 | 3.1408e-06
2011 | 2010-12-13 | B | 1 | 0.0011119 | 3.1408e-06
2011 | 2010-12-13 | B | 8 | 0.0084928 | 2.5127e-05
2011 | 2010-12-13 | B | 55 | 0.059943 | 0.00017275
2011 | 2010-12-13 | C | 99.1132 | 0.048562 | 0.00071297
2011 | 2010-12-13 | C | 235.0652 | 0.065709 | 0.001137
2011 | 2010-12-13 | C | 69.5153 | 0.056549 | 0.00097994
2011 | 2010-12-14 | C | 128 | 0.0048243 | 0.00040203
2011 | 2010-12-14 | C | 113.8632 | 0.074743 | 0.00092026
2011 | 2010-12-13 | B | 10 | 0.011244 | 3.1408e-05
2011 | 2010-12-14 | C | 105.5068 | 0.095768 | 0.00048369
2011 | 2010-12-14 | B | 31 | 0.024828 | 9.7365e-05
2011 | 2010-12-14 | B | 34 | 0.03524 | 0.00010679
2011 | 2010-12-14 | B | 26 | 0.032256 | 8.1661e-05
2011 | 2010-12-14 | B | 18 | 0.011929 | 5.6535e-05
2011 | 2010-12-14 | B | 20 | 0.021169 | 6.2816e-05
2011 | 2010-12-14 | C | 28.069 | 0.0048488 | 0.00099564
2011 | 2010-12-14 | C | 77.1041 | 0.052793 | 0.00051824
2011 | 2010-12-14 | C | 241 | 0.036333 | 0.00075694
2011 | 2010-12-14 | C | 107.8683 | 0.068437 | 0.00077578
2011 | 2010-12-14 | C | 5 | 0.0029367 | 1.5704e-05
2011 | 2010-12-14 | B | 6 | 0.0022991 | 1.8845e-05
2011 | 2010-12-14 | B | 164 | 0.062842 | 0.00051509
2011 | 2010-12-15 | C | 638 | 0.0060115 | 0.0020038
2011 | 2010-12-15 | C | 23 | 0.0033952 | 7.2239e-05
2011 | 2010-12-15 | B | 1 | 0.00090456 | 3.1408e-06
2011 | 2010-12-15 | C | 101.2249 | 0.090928 | 0.00096423
2011 | 2010-12-15 | B | 1 | 0.00036748 | 3.1408e-06
2011 | 2010-12-15 | B | 62 | 0.075361 | 0.00019473
2011 | 2010-12-15 | B | 75 | 0.077029 | 0.00023556
2011 | 2010-12-15 | B | 373 | 0.089036 | 0.0011715
2011 | 2010-12-15 | B | 272.122 | 0.06752 | 0.0011684
2011 | 2010-12-16 | B | 11 | 0.0069444 | 3.4549e-05
2011 | 2010-12-16 | B | 50 | 0.067371 | 0.00015704
2011 | 2010-12-16 | C | 15 | 0.0096109 | 4.7112e-05
2011 | 2010-12-16 | B | 17 | 0.019062 | 5.3394e-05
2011 | 2010-12-16 | C | 44 | 0.014372 | 0.0001382
2011 | 2010-12-16 | C | 53 | 0.012984 | 0.00016646
2011 | 2010-12-16 | C | 131 | 0.049374 | 0.00041145
2011 | 2010-12-16 | C | 443.2636 | 0.17542 | 0.0028487
2011 | 2010-12-16 | C | 1970 | 0.037125 | 0.0061874
2011 | 2010-12-16 | C | 160.2581 | 0.029697 | 0.00084488
2011 | 2010-12-16 | C | 43 | 0.0016207 | 0.00013506
2011 | 2010-12-16 | C | 124.0741 | 0.05144 | 0.00070983
2011 | 2010-12-16 | C | 555 | 0.3312 | 0.0017432
2011 | 2010-12-16 | C | 136.9809 | 0.066256 | 0.001382
2011 | 2010-12-16 | C | 138.6757 | 0.095387 | 0.00056535
2011 | 2010-12-16 | B | 457 | 0.11913 | 0.0014354
2011 | 2010-12-16 | C | 250 | 0.059676 | 0.00078521
2011 | 2010-12-16 | C | 223.0059 | 0.11627 | 0.0011056
2011 | 2010-12-17 | C | 46.0341 | 0.029206 | 0.00016646
2011 | 2010-12-17 | C | 186 | 0.038557 | 0.00058419
2011 | 2010-12-08 | B | 3 | 0.001159 | 9.4225e-06
2011 | 2010-12-17 | C | 40.345 | 0.028638 | 0.00016646
2011 | 2010-12-17 | C | 65 | 0.043076 | 0.00020415
2011 | 2010-12-17 | B | 8 | 0.0071611 | 2.5127e-05
2011 | 2010-12-17 | B | 71 | 0.011596 | 0.000223
2011 | 2010-12-15 | C | 23.2116 | 0.10936 | 0.00058419
2011 | 2010-12-17 | B | 46 | 0.055479 | 0.00014448
2011 | 2010-12-17 | C | 225 | 0.0084802 | 0.00070668
2011 | 2010-12-17 | C | 140 | 0.014071 | 0.00043972
2011 | 2010-12-16 | C | 274.8913 | 0.037126 | 0.0011087
2011 | 2010-12-18 | C | 3 | 0.0013097 | 9.4225e-06
2011 | 2010-12-18 | C | 216 | 0.014925 | 0.00067842
2011 | 2010-12-18 | C | 353 | 0.10311 | 0.0011087
2011 | 2010-12-18 | C | 486 | 0.065637 | 0.0015264
2011 | 2010-12-18 | C | 7 | 0.0038695 | 2.1986e-05
2011 | 2010-12-18 | C | 1018 | 0.04796 | 0.0031974
2011 | 2010-12-18 | C | 373 | 0.10895 | 0.0011715
2011 | 2010-12-18 | C | 3 | 0.0018374 | 9.4225e-06
2011 | 2010-12-18 | C | 12 | 0.00086687 | 3.769e-05
2011 | 2010-12-18 | C | 2 | 0.00087315 | 6.2816e-06
2011 | 2010-12-18 | C | 53 | 0.0063256 | 0.00016646
2011 | 2010-12-18 | C | 206.9116 | 0.2554 | 0.0012218
2011 | 2010-12-19 | B | 1 | 0.00016018 | 3.1408e-06
2011 | 2010-12-19 | C | 179.1857 | 0.15589 | 0.0023682
2011 | 2010-12-19 | B | 112 | 0.03377 | 0.00035177
2011 | 2010-12-19 | C | 159.3548 | 0.060561 | 0.00066585
2011 | 2010-12-19 | C | 129 | 0.015396 | 0.00040517
2011 | 2010-12-19 | C | 169 | 0.015924 | 0.0005308
2011 | 2010-12-19 | B | 55 | 0.035413 | 0.00017275
2011 | 2010-12-19 | C | 142.732 | 0.04214 | 0.00067528
2011 | 2010-12-19 | C | 250 | 0.018845 | 0.00078521
2011 | 2010-12-18 | C | 77 | 0.092384 | 0.00024184
2011 | 2010-12-19 | C | 216.5168 | 0.099286 | 0.0014291
2011 | 2010-12-19 | C | 5 | 0.00072239 | 1.5704e-05
2011 | 2010-12-18 | C | 178.7288 | 0.031436 | 0.0007004
2011 | 2010-12-18 | C | 573.3656 | 0.16208 | 0.0018719
2011 | 2010-12-19 | C | 65 | 0.018374 | 0.00020415
2011 | 2010-12-19 | B | 33 | 0.0054933 | 0.00010365
2011 | 2010-12-20 | B | 60 | 0.010742 | 0.00018845
2011 | 2010-12-20 | C | 262.642 | 0.19798 | 0.0014636
2011 | 2010-12-18 | C | 1958.1912 | 1.5253 | 0.0076448
2011 | 2010-12-20 | B | 9 | 0.0091869 | 2.8267e-05
2011 | 2010-12-20 | B | 95 | 0.042966 | 0.00029838
2011 | 2010-12-20 | B | 13 | 0.0028173 | 4.0831e-05
2011 | 2010-12-21 | B | 83 | 0.015381 | 0.00026069
2011 | 2010-12-21 | C | 67 | 0.012626 | 0.00021044
2011 | 2010-12-21 | C | 11 | 0.0063916 | 3.4549e-05
2011 | 2010-12-21 | C | 147 | 0.0050787 | 0.0004617
2011 | 2010-12-20 | B | 1 | 0.0049782 | 3.1408e-06
2011 | 2010-12-20 | B | 105 | 0.074202 | 0.00032979
2011 | 2010-12-21 | B | 231 | 0.19154 | 0.00072553
2011 | 2010-12-20 | B | 12 | 0.0088948 | 3.769e-05
2011 | 2010-12-21 | B | 17 | 0.01431 | 5.3394e-05
2011 | 2010-12-21 | C | 82 | 0.012877 | 0.00025755
2011 | 2010-09-21 | B | 8 | 0.0089199 | 2.5127e-05
2011 | 2010-12-21 | C | 9 | 0.00036748 | 2.8267e-05
2011 | 2010-12-21 | B | 14 | 0.016313 | 4.3972e-05
2011 | 2010-12-21 | C | 341 | 0.11353 | 0.001071
2011 | 2010-12-21 | B | 2.409 | 0.0028449 | 1.2563e-05
2011 | 2010-12-21 | C | 15 | 0.0040988 | 4.7112e-05
2011 | 2010-12-21 | B | 14 | 0.014511 | 4.3972e-05
2011 | 2010-12-21 | C | 33 | 0.015236 | 0.00010365
2011 | 2010-12-22 | B | 119 | 0.019435 | 0.00037376
2011 | 2010-12-21 | B | 14 | 0.0029021 | 4.3972e-05
2011 | 2010-12-21 | C | 37 | 0.0079023 | 0.00011621
2011 | 2010-12-21 | C | 509 | 0.17745 | 0.0015987
2011 | 2010-12-21 | C | 820 | 0.3992 | 0.0025755
2011 | 2010-12-21 | C | 35 | 0.0037376 | 0.00010993
2011 | 2010-12-21 | C | 192.0426 | 0.11159 | 0.00094853
2011 | 2010-12-21 | C | 6 | 0.00045228 | 1.8845e-05
2011 | 2010-12-21 | C | 118.5 | 0.056945 | 0.00056849
2011 | 2010-12-21 | C | 38.6856 | 0.035965 | 0.00014134
2011 | 2010-12-21 | C | 486 | 0.059531 | 0.0015264
2011 | 2010-12-21 | C | 2 | 0.0079903 | 6.2816e-06
2011 | 2010-12-21 | C | 85.8051 | 0.083545 | 0.00073809
2011 | 2010-12-21 | C | 4.2325 | 0.01328 | 0.00078521
2011 | 2010-12-22 | B | 68 | 0.054889 | 0.00021358
2011 | 2010-12-22 | B | 17 | 0.021625 | 5.3394e-05
2011 | 2010-12-22 | B | 21 | 0.0088383 | 6.5957e-05
2011 | 2010-12-22 | C | 34 | 0.017727 | 0.00010679
2011 | 2010-12-22 | C | 163 | 0.072697 | 0.00051195
2011 | 2010-12-22 | C | 16 | 0.0038695 | 5.0253e-05
2011 | 2010-12-22 | C | 663 | 0.13327 | 0.0020824
2011 | 2010-12-22 | C | 65 | 0.0034706 | 0.00020415
2011 | 2010-12-22 | C | 198.8052 | 0.094286 | 0.00095481
2011 | 2010-12-23 | C | 34 | 0.005019 | 0.00010679
2011 | 2010-12-21 | C | 34 | 0.0029901 | 0.00010679
2011 | 2010-12-22 | B | 27 | 0.011703 | 8.4802e-05
2011 | 2010-12-22 | C | 350.5128 | 0.1255 | 0.0021672
2011 | 2010-12-21 | C | 155 | 0.29258 | 0.00048683
2011 | 2010-12-23 | C | 60 | 0.0043343 | 0.00018845
2011 | 2010-12-23 | C | 18 | 0.0030529 | 5.6535e-05
2011 | 2010-12-22 | C | 34.7419 | 0.080857 | 0.00068784
2011 | 2010-12-23 | C | 151.5909 | 0.082369 | 0.0008386
2011 | 2010-12-24 | C | 137 | 0.016781 | 0.00043029
2011 | 2010-12-24 | C | 178 | 0.10455 | 0.00055907
2011 | 2010-12-24 | B | 28 | 0.010289 | 8.7943e-05
2011 | 2010-12-24 | C | 125 | 0.0066742 | 0.0003926
2011 | 2010-12-24 | C | 461 | 0.23167 | 0.0014479
2011 | 2010-12-24 | C | 220.1712 | 0.15144 | 0.00098936
2011 | 2010-12-24 | C | 140.4286 | 0.041901 | 0.00049311
2011 | 2010-12-24 | C | 46 | 0.013003 | 0.00014448
2011 | 2010-12-24 | C | 174 | 0.27052 | 0.0005465
2011 | 2010-12-24 | C | 5 | 0.0019944 | 1.5704e-05
2011 | 2010-12-24 | C | 64 | 0.018694 | 0.00020101
2011 | 2010-12-24 | C | 205 | 0.013521 | 0.00064387
2011 | 2010-12-24 | C | 18 | 0.0028267 | 5.6535e-05
2011 | 2010-12-24 | C | 80 | 0.021609 | 0.00025127
2011 | 2010-12-24 | C | 10 | 0.0043657 | 3.1408e-05
2011 | 2010-12-25 | C | 1 | 0.00037062 | 3.1408e-06
2011 | 2010-12-25 | C | 27 | 0.0010176 | 8.4802e-05
2011 | 2010-12-25 | C | 10 | 0.0035177 | 3.1408e-05
2011 | 2010-12-25 | C | 60 | 0.021483 | 0.00018845
2011 | 2010-12-26 | C | 827 | 0.070131 | 0.0025975
2011 | 2010-12-27 | C | 112 | 0.015126 | 0.00035177
2011 | 2010-12-28 | C | 142 | 0.1338 | 0.000446
2011 | 2010-12-28 | C | 101 | 0.0063445 | 0.00031722
2011 | 2010-12-28 | C | 173.3175 | 0.066956 | 0.00054964
2011 | 2010-12-28 | C | 44 | 0.0082918 | 0.0001382
2011 | 2010-12-28 | C | 656 | 0.1195 | 0.0020604
2011 | 2010-12-28 | C | 64 | 0.043821 | 0.00020101
2011 | 2010-12-28 | C | 109 | 0.06847 | 0.00034235
2011 | 2010-12-28 | C | 529 | 0.03323 | 0.0016615
2011 | 2010-12-28 | C | 1109 | 0.059214 | 0.0034832
2011 | 2010-12-28 | C | 1109 | 0.3518 | 0.0034832
2011 | 2010-12-28 | C | 128.6475 | 0.054952 | 0.00064073
2011 | 2010-12-28 | C | 457 | 0.01866 | 0.0014354
2011 | 2010-12-28 | C | 125.5733 | 0.057977 | 0.00053708
2011 | 2010-12-28 | C | 463 | 0.018905 | 0.0014542
2011 | 2010-12-28 | C | 186 | 0.010515 | 0.00058419
2011 | 2010-12-28 | C | 324.3738 | 0.10596 | 0.0016741
2011 | 2010-12-28 | C | 27 | 0.0069538 | 8.4802e-05
2011 | 2010-12-28 | C | 37.442 | 0.020933 | 0.00016646
2011 | 2010-12-28 | C | 112.0809 | 0.10772 | 0.00068156
2011 | 2010-12-28 | C | 675 | 0.0042401 | 0.0021201
2011 | 2010-12-28 | C | 65 | 0.01572 | 0.00020415
2011 | 2010-12-28 | C | 37 | 0.039395 | 0.00011621
2011 | 2010-12-28 | C | 5 | 0.00095795 | 1.5704e-05
2011 | 2010-12-28 | C | 5 | 0.0013348 | 1.5704e-05
2011 | 2010-12-28 | C | 572.3167 | 0.21031 | 0.0020384
2011 | 2010-12-28 | C | 41.7833 | 0.062599 | 0.00021358
2011 | 2010-12-28 | C | 266.1379 | 0.045974 | 0.0011464
2011 | 2010-12-28 | C | 238 | 0.040366 | 0.00074752
2011 | 2010-12-28 | C | 744 | 0.11684 | 0.0023368
2011 | 2010-12-28 | C | 178 | 0.12747 | 0.00055907
2011 | 2010-12-28 | C | 314 | 0.14793 | 0.00098622
2011 | 2010-12-28 | C | 54 | 0.061736 | 0.0001696
2011 | 2010-12-28 | C | 20 | 0.0035805 | 6.2816e-05
2011 | 2010-12-28 | C | 162 | 0.10024 | 0.00050881
2011 | 2010-12-28 | C | 55.677 | 0.038996 | 0.00026383
2011 | 2010-12-27 | C | 176.7033 | 0.048839 | 0.00067214
2011 | 2010-12-28 | C | 122 | 0.073187 | 0.00038318
2011 | 2010-12-28 | C | 476.5676 | 0.49395 | 0.0026351
2011 | 2010-12-28 | C | 185 | 0.0069726 | 0.00058105
2011 | 2010-12-29 | C | 42 | 0.0083106 | 0.00013191
2011 | 2010-12-28 | C | 106 | 0.052935 | 0.00033293
2011 | 2010-12-28 | C | 27.4485 | 0.13354 | 0.00074437
2011 | 2010-12-28 | C | 597 | 0.022501 | 0.0018751
2011 | 2010-12-28 | C | 37 | 0.016153 | 0.00011621
2011 | 2010-12-28 | C | 13 | 0.0029398 | 4.0831e-05
2011 | 2010-12-29 | C | 6 | 0.0037125 | 1.8845e-05
2011 | 2010-12-28 | C | 20.559 | 0.084137 | 9.4225e-05
2011 | 2010-12-28 | C | 4 | 0.018506 | 1.2563e-05
2011 | 2010-12-29 | C | 27 | 0.013399 | 8.4802e-05
2011 | 2010-12-28 | C | 61.6477 | 0.24455 | 0.000446
2011 | 2010-12-29 | C | 49 | 0.0023085 | 0.0001539
2011 | 2010-12-29 | C | 341 | 0.0074971 | 0.001071
2011 | 2010-12-29 | C | 17 | 0.028459 | 5.3394e-05
2011 | 2010-12-29 | C | 695 | 0.10259 | 0.0021829
2011 | 2010-12-28 | C | 668 | 0.067138 | 0.0020981
2011 | 2010-12-28 | C | 268.5778 | 0.22523 | 0.0011998
2011 | 2010-12-28 | C | 130.3006 | 0.1989 | 0.00065015
2011 | 2010-12-28 | C | 44 | 0.24267 | 0.0001382
2011 | 2010-12-28 | C | 174.1613 | 0.049231 | 0.0011715
2011 | 2010-12-28 | C | 46.9407 | 0.30312 | 0.0013474
2011 | 2010-12-28 | C | 130.3519 | 0.042988 | 0.00082604
2011 | 2010-12-28 | C | 59.9695 | 0.024109 | 0.00026069
2011 | 2010-12-28 | C | 174 | 0.12132 | 0.00060618
2011 | 2010-12-28 | C | 210.1308 | 0.068638 | 0.00085116
2011 | 2010-12-28 | C | 1114.5189 | 0.63709 | 0.0036936
2011 | 2010-12-28 | C | 240.0116 | 0.25781 | 0.00079149
2011 | 2010-12-28 | C | 32.5607 | 0.030885 | 0.00051509
2011 | 2010-12-28 | C | 310 | 0.43036 | 0.00097365
2011 | 2010-12-30 | C | 5 | 0.0011464 | 1.5704e-05
2011 | 2010-12-28 | C | 15 | 0.0036748 | 4.7112e-05
2011 | 2010-12-30 | C | 50 | 0.0058105 | 0.00015704
2011 | 2010-12-28 | C | 65 | 0.081049 | 0.00020415
2011 | 2010-12-28 | C | 913 | 0.38999 | 0.0028676
2011 | 2010-12-28 | C | 502.5625 | 0.62665 | 0.0021766
2011 | 2010-12-28 | C | 102.902 | 0.17711 | 0.00036119
2011 | 2010-12-28 | C | 172.459 | 0.13054 | 0.00058105
2011 | 2010-12-28 | C | 10 | 0.088194 | 3.1408e-05
2011 | 2010-12-28 | C | 1121 | 0.045771 | 0.0035209
2011 | 2010-12-28 | C | 29.0689 | 0.29663 | 0.00025127
2011 | 2010-12-30 | C | 9 | 0.00093282 | 2.8267e-05
2011 | 2010-12-28 | C | 224 | 0.14141 | 0.00070354
2011 | 2010-12-29 | C | 8.0219 | 0.048299 | 3.769e-05
2011 | 2010-12-30 | B | 102 | 0.028833 | 0.00032036
2011 | 2010-12-31 | B | 93 | 0.023368 | 0.0002921
2011 | 2010-12-28 | C | 819.2841 | 0.21872 | 0.0034549
2011 | 2010-12-28 | C | 1121 | 0.10915 | 0.0035209
2011 | 2010-12-28 | C | 1121 | 0.088022 | 0.0035209
2011 | 2010-12-28 | C | 717.6417 | 0.71677 | 0.0033638
2011 | 2010-12-31 | C | 4 | 0.00052766 | 1.2563e-05
2011 | 2011-01-01 | C | 1 | 0.021496 | 3.1408e-06
2011 | 2011-01-01 | C | 1013.0725 | 0.21 | 0.0035083
2011 | 2011-01-01 | C | 11 | 0.0033167 | 3.4549e-05
2011 | 2011-01-02 | C | 70.5862 | 0.018623 | 0.00029838
2011 | 2011-01-02 | C | 43 | 0.067123 | 0.00013506
2011 | 2011-01-03 | C | 162 | 0.075304 | 0.00050881
2011 | 2011-01-03 | C | 70 | 0.0054964 | 0.00021986
2011 | 2011-01-04 | C | 4061 | 0.66325 | 0.012755
2011 | 2011-01-04 | C | 13 | 0.0011024 | 4.0831e-05
2011 | 2011-01-04 | C | 34 | 0.003524 | 0.00010679
2011 | 2011-01-04 | C | 56 | 0.011608 | 0.00017589
2011 | 2011-01-05 | C | 169.0758 | 0.068504 | 0.00070354
2011 | 2011-01-05 | B | 2 | 0.00035805 | 6.2816e-06
2011 | 2011-01-05 | B | 32 | 0.0041208 | 0.00010051
2011 | 2010-12-19 | B | 79 | 0.019602 | 0.00024812
2011 | 2011-01-05 | C | 28 | 0.0068596 | 8.7943e-05
2011 | 2011-01-05 | C | 93.1852 | 0.06234 | 0.00054022
2011 | 2010-12-29 | C | 12 | 0.002186 | 3.769e-05
2011 | 2010-12-28 | C | 2 | 0.081391 | 6.2816e-06
2011 | 2011-01-06 | B | 5 | 0.0031722 | 1.5704e-05
2011 | 2011-01-06 | C | 2 | 0.00050881 | 6.2816e-06
2011 | 2011-01-06 | C | 292.3299 | 0.086307 | 0.001696
2011 | 2011-01-06 | C | 192 | 0.0072365 | 0.00060304
2011 | 2011-01-07 | C | 691 | 0.028214 | 0.0021703
2011 | 2011-01-07 | C | 691 | 0.023873 | 0.0021703
2011 | 2011-01-07 | C | 7 | 0.0003078 | 2.1986e-05
2011 | 2011-01-07 | C | 288.1186 | 0.17284 | 0.0025818
2011 | 2011-01-07 | C | 259.55 | 0.12799 | 0.0030906
2011 | 2011-01-07 | C | 699.7436 | 0.07912 | 0.0030592
2011 | 2011-01-07 | C | 1 | 0.00023242 | 3.1408e-06
2011 | 2011-01-08 | C | 260 | 0.013066 | 0.00081661
2011 | 2011-01-08 | C | 162 | 0.0050881 | 0.00050881
2011 | 2011-01-08 | C | 6 | 0.0019599 | 1.8845e-05
2011 | 2011-01-08 | B | 1 | 0.0011684 | 3.1408e-06
2011 | 2011-01-08 | B | 1 | 0.00046798 | 3.1408e-06
2011 | 2011-01-08 | C | 4 | 0.00052766 | 1.2563e-05
2011 | 2011-01-09 | C | 5 | 0.0011935 | 1.5704e-05
2011 | 2011-01-09 | C | 27 | 0.0030529 | 8.4802e-05
2011 | 2011-01-10 | C | 4 | 0.0011558 | 1.2563e-05
2011 | 2011-01-10 | B | 78.3032 | 0.091734 | 0.00031722
2011 | 2011-01-10 | B | 71 | 0.052405 | 0.000223
2011 | 2011-01-10 | C | 513 | 0.0080562 | 0.0016112
2011 | 2011-01-10 | C | 82 | 0.037602 | 0.00025755
2011 | 2011-01-11 | B | 13 | 0.010004 | 4.0831e-05
2011 | 2011-01-11 | C | 114 | 0.039744 | 0.00035805
2011 | 2011-01-11 | C | 15 | 0.0069255 | 4.7112e-05
2011 | 2011-01-11 | B | 38 | 0.017425 | 0.00011935
2011 | 2011-01-12 | C | 116 | 0.005465 | 0.00036434
2011 | 2011-01-12 | C | 3 | 0.00084802 | 9.4225e-06
2011 | 2011-01-12 | B | 13 | 0.0049405 | 4.0831e-05
2011 | 2011-01-12 | B | 40 | 0.044851 | 0.00012563
2011 | 2011-01-12 | B | 7 | 0.0060461 | 2.1986e-05
2011 | 2011-01-12 | B | 5 | 0.0051981 | 1.5704e-05
2011 | 2011-01-12 | B | 93 | 0.086753 | 0.0002921
2011 | 2011-01-12 | B | 28 | 0.0095858 | 8.7943e-05
2011 | 2011-01-12 | C | 92.2281 | 0.075315 | 0.00074437
2011 | 2011-01-13 | C | 6 | 0.0062377 | 1.8845e-05
2011 | 2011-01-13 | B | 30 | 0.034957 | 9.4225e-05
2011 | 2011-01-13 | B | 17 | 0.0048055 | 5.3394e-05
2011 | 2011-01-13 | C | 81.7534 | 0.055463 | 0.00098622
2011 | 2011-01-13 | B | 8 | 0.0025378 | 2.5127e-05
2011 | 2011-01-14 | C | 149.0179 | 0.024806 | 0.00064387
2011 | 2011-01-13 | C | 37.4398 | 0.041627 | 0.00027953
2011 | 2011-01-13 | C | 151 | 0.033198 | 0.00047426
2011 | 2011-01-13 | B | 4 | 0.0014825 | 1.2563e-05
2011 | 2011-01-14 | B | 5 | 0.0043657 | 1.5704e-05
2011 | 2011-01-14 | B | 57 | 0.01289 | 0.00017903
2011 | 2011-01-13 | C | 3 | 0.015547 | 9.4225e-06
2011 | 2011-01-14 | B | 2 | 0.00033293 | 6.2816e-06
2011 | 2011-01-14 | B | 3 | 0.0012061 | 9.4225e-06
2011 | 2011-01-14 | B | 62 | 0.080813 | 0.00019473
2011 | 2011-01-14 | B | 47 | 0.049747 | 0.00014762
2011 | 2011-01-14 | C | 986 | 0.26943 | 0.0030969
2011 | 2011-01-15 | C | 522 | 0.024593 | 0.0016395
2011 | 2011-01-15 | B | 5 | 0.0032193 | 1.5704e-05
2011 | 2011-01-15 | C | 120 | 0.070857 | 0.0003769
2011 | 2011-01-15 | C | 86.443 | 0.042083 | 0.00075694
2011 | 2011-01-15 | C | 34.0411 | 0.015289 | 0.00014134
2011 | 2011-01-16 | C | 106.7692 | 0.03387 | 0.00039888
2011 | 2011-01-16 | C | 4 | 0.001495 | 1.2563e-05
2011 | 2011-01-16 | C | 160.2174 | 0.033212 | 0.00058105
2011 | 2011-01-15 | B | 17 | 0.018101 | 5.3394e-05
2011 | 2011-01-16 | C | 95.9349 | 0.063879 | 0.002252
2011 | 2011-01-16 | C | 40 | 0.011056 | 0.00012563
2011 | 2011-01-16 | C | 5 | 0.0091241 | 1.5704e-05
2011 | 2011-01-14 | C | 668 | 0.0041961 | 0.0020981
2011 | 2011-01-17 | B | 14 | 0.011565 | 4.3972e-05
2011 | 2011-01-17 | C | 1 | 0.00033607 | 3.1408e-06
2011 | 2011-01-17 | C | 78.9647 | 0.041418 | 0.00087943
2011 | 2011-01-18 | C | 67 | 0.0079965 | 0.00021044
2011 | 2011-01-18 | C | 29 | 0.0092906 | 9.1084e-05
2011 | 2011-01-18 | C | 699.5556 | 0.32958 | 0.005509
2011 | 2011-01-18 | C | 148.8297 | 0.14678 | 0.0011841
2011 | 2011-01-18 | C | 619 | 0.40633 | 0.0019442
2011 | 2011-01-18 | C | 12 | 0.0061058 | 3.769e-05
2011 | 2011-01-18 | C | 50 | 0.0040831 | 0.00015704
2011 | 2011-01-18 | C | 32 | 0.047238 | 0.00010051
2011 | 2011-01-18 | C | 62 | 0.019084 | 0.00019473
2011 | 2011-01-18 | B | 43 | 0.048485 | 0.00013506
2011 | 2011-01-18 | B | 4 | 0.0042338 | 1.2563e-05
2011 | 2011-01-18 | B | 15 | 0.015688 | 4.7112e-05
2011 | 2011-01-18 | B | 6 | 0.0040328 | 1.8845e-05
2011 | 2011-01-18 | C | 317.2804 | 0.3737 | 0.0015893
2011 | 2011-01-18 | C | 34 | 0.038123 | 0.00010679
2011 | 2011-01-18 | C | 563 | 0.070731 | 0.0017683
2011 | 2011-01-18 | B | 64 | 0.017287 | 0.00020101
2011 | 2011-01-18 | C | 9 | 0.0010176 | 2.8267e-05
2011 | 2011-01-18 | C | 71 | 0.002899 | 0.000223
2011 | 2011-01-18 | C | 65 | 0.0042872 | 0.00020415
2011 | 2011-01-19 | C | 178 | 0.0095041 | 0.00055907
2011 | 2011-01-19 | C | 225 | 0.021907 | 0.00070668
2011 | 2011-01-18 | C | 633.2517 | 0.27845 | 0.0022049
2011 | 2011-01-18 | C | 173.5909 | 0.094323 | 0.00077578
2011 | 2011-01-18 | C | 65.9249 | 0.20623 | 0.00035491
2011 | 2011-01-18 | C | 45.5748 | 0.054108 | 0.00028896
2011 | 2011-01-19 | C | 736 | 0.11327 | 0.0023116
2011 | 2011-01-19 | B | 12 | 0.0041459 | 3.769e-05
2011 | 2011-01-18 | C | 1121 | 0.27463 | 0.0035209
2011 | 2011-01-18 | C | 1121 | 0.34152 | 0.0035209
2011 | 2011-01-19 | B | 38 | 0.010622 | 0.00011935
2011 | 2011-01-19 | C | 53 | 0.010154 | 0.00016646
2011 | 2011-01-19 | C | 164.0678 | 0.29476 | 0.00059362
2011 | 2011-01-19 | B | 34 | 0.043356 | 0.00010679
2011 | 2011-01-19 | B | 4 | 0.0047364 | 1.2563e-05
2011 | 2011-01-19 | B | 128 | 0.18694 | 0.00040203
2011 | 2011-01-19 | B | 6 | 0.0078018 | 1.8845e-05
2011 | 2011-01-19 | C | 41 | 0.0070826 | 0.00012877
2011 | 2011-01-19 | C | 25 | 0.0021201 | 7.8521e-05
2011 | 2011-01-19 | C | 26.4912 | 0.004493 | 0.00013191
2011 | 2011-01-19 | C | 123 | 0.04829 | 0.00038632
2011 | 2011-01-19 | C | 162.1811 | 0.12225 | 0.00057163
2011 | 2011-01-19 | B | 158 | 0.12307 | 0.00049625
2011 | 2011-01-19 | C | 37 | 0.02452 | 0.00011621
2011 | 2011-01-19 | C | 5 | 0.00089513 | 1.5704e-05
2011 | 2011-01-19 | C | 744 | 0.42529 | 0.0023368
2011 | 2011-01-19 | C | 34 | 0.0042715 | 0.00010679
2011 | 2011-01-19 | B | 16 | 0.0056284 | 5.0253e-05
2011 | 2011-01-19 | C | 9 | 0.0026854 | 2.8267e-05
2011 | 2011-01-18 | C | 91.3979 | 0.27472 | 0.00035491
2011 | 2011-01-20 | B | 42 | 0.035881 | 0.00013191
2011 | 2011-01-20 | B | 17 | 0.015858 | 5.3394e-05
2011 | 2011-01-20 | B | 1 | 0.00090456 | 3.1408e-06
2011 | 2011-01-20 | C | 739.5 | 0.090583 | 0.0023713
2011 | 2011-01-20 | B | 48 | 0.058344 | 0.00015076
2011 | 2011-01-20 | B | 7 | 0.0042213 | 2.1986e-05
2011 | 2011-01-20 | B | 17 | 0.0068878 | 5.3394e-05
2011 | 2011-01-20 | C | 201 | 0.010732 | 0.00063131
2011 | 2011-01-20 | C | 35 | 0.0043972 | 0.00010993
2011 | 2011-01-20 | C | 6 | 0.0013003 | 1.8845e-05
2011 | 2011-01-20 | C | 12 | 0.00086687 | 3.769e-05
2011 | 2011-01-21 | C | 11 | 0.0026948 | 3.4549e-05
2011 | 2011-01-21 | C | 13 | 0.0037564 | 4.0831e-05
2011 | 2011-01-21 | B | 10 | 0.0023242 | 3.1408e-05
2011 | 2011-01-21 | B | 12 | 0.012664 | 3.769e-05
2011 | 2011-01-21 | C | 141.5507 | 0.060019 | 0.00060618
2011 | 2011-01-21 | B | 55.8194 | 0.079069 | 0.00049311
2011 | 2011-01-21 | B | 2 | 0.0016646 | 6.2816e-06
2011 | 2011-01-21 | C | 161.6729 | 0.05281 | 0.00054336
2011 | 2011-01-21 | C | 36 | 0.0062188 | 0.00011307
2011 | 2011-01-21 | C | 170.5487 | 0.058923 | 0.00056221
2011 | 2011-01-22 | C | 183.24 | 0.055826 | 0.00095481
2011 | 2011-01-21 | C | 307 | 0.020249 | 0.00096423
2011 | 2011-01-22 | C | 6 | 0.0010742 | 1.8845e-05
2011 | 2011-01-22 | C | 15 | 0.0039103 | 4.7112e-05
2011 | 2011-01-22 | C | 17 | 0.0076887 | 5.3394e-05
2011 | 2011-01-22 | C | 9 | 0.0021201 | 2.8267e-05
2011 | 2011-01-23 | C | 432 | 0.016282 | 0.0013568
2011 | 2011-01-22 | C | 49.2406 | 0.032323 | 0.00030466
2011 | 2011-01-23 | C | 82 | 0.032966 | 0.00025755
2011 | 2011-01-23 | C | 169.9444 | 0.075261 | 0.00072239
2011 | 2011-01-23 | C | 282.4333 | 0.26346 | 0.0013694
2011 | 2011-01-23 | C | 39 | 0.019354 | 0.00012249
2011 | 2011-01-23 | C | 432 | 0.020353 | 0.0013568
2011 | 2011-01-23 | C | 1683 | 0.042288 | 0.005286
2011 | 2011-01-23 | C | 205 | 0.021248 | 0.00064387
2011 | 2011-01-23 | C | 18 | 0.0035052 | 5.6535e-05
2011 | 2011-01-23 | C | 312.3298 | 0.27663 | 0.0037878
2011 | 2011-01-23 | C | 104.3102 | 0.098286 | 0.00079149
2011 | 2011-01-22 | B | 17 | 0.091838 | 5.3394e-05
2011 | 2011-01-23 | C | 955.1636 | 0.321 | 0.0037847
2011 | 2011-01-23 | B | 17 | 0.01495 | 5.3394e-05
2011 | 2011-01-23 | C | 395 | 0.024812 | 0.0012406
2011 | 2011-01-23 | C | 19 | 0.0081159 | 5.9676e-05
2011 | 2011-01-23 | C | 469.6957 | 0.36881 | 0.0035209
2011 | 2011-01-23 | C | 1061 | 0.41322 | 0.0033324
2011 | 2011-01-23 | C | 139 | 0.11089 | 0.00043657
2011 | 2011-01-23 | C | 53 | 0.0054933 | 0.00016646
2011 | 2011-01-23 | C | 280.4013 | 0.39895 | 0.0022802
2011 | 2011-01-23 | C | 707.8727 | 0.23789 | 0.0038538
2011 | 2011-01-23 | C | 1255 | 0.27198 | 0.0039417
2011 | 2011-01-22 | C | 149.1277 | 0.064637 | 0.00054964
2011 | 2011-01-23 | C | 5 | 0.00084802 | 1.5704e-05
2011 | 2011-01-23 | C | 414 | 0.072817 | 0.0013003
2011 | 2011-01-23 | C | 85.9676 | 0.049142 | 0.00050881
2011 | 2011-01-23 | C | 691.6314 | 0.67124 | 0.0062691
2011 | 2011-01-23 | C | 19 | 0.032225 | 5.9676e-05
2011 | 2011-01-21 | C | 144.3259 | 0.32547 | 0.00056221
2011 | 2011-01-21 | B | 1 | 0.0009234 | 3.1408e-06
2011 | 2011-01-23 | C | 154.8667 | 0.12257 | 0.0016018
2011 | 2011-01-23 | C | 135.3036 | 0.093917 | 0.0006156
2011 | 2011-01-24 | C | 6 | 0.0021672 | 1.8845e-05
2011 | 2011-01-24 | C | 795 | 0.92637 | 0.002497
2011 | 2011-01-24 | C | 73 | 0.016967 | 0.00022928
2011 | 2011-01-24 | C | 69.2 | 0.12106 | 0.00052452
2011 | 2011-01-23 | C | 164.7264 | 0.10244 | 0.00092026
2011 | 2011-01-24 | C | 68 | 0.089488 | 0.00021358
2011 | 2011-01-24 | C | 3 | 0.0010176 | 9.4225e-06
2011 | 2011-01-24 | C | 80 | 0.04573 | 0.00025127
2011 | 2011-01-24 | C | 2 | 0.00064701 | 6.2816e-06
2011 | 2011-01-24 | C | 356.318 | 0.31336 | 0.0011747
2011 | 2011-01-23 | C | 105.3333 | 0.04764 | 0.00048369
2011 | 2011-01-24 | C | 268.0742 | 0.3831 | 0.0018091
2011 | 2011-01-24 | C | 32 | 0.0039197 | 0.00010051
2011 | 2011-01-24 | C | 27 | 0.0020353 | 8.4802e-05
2011 | 2011-01-24 | C | 94.3567 | 0.045639 | 0.00093911
2011 | 2011-01-24 | C | 4 | 0.00092968 | 1.2563e-05
2011 | 2011-01-24 | C | 66.1373 | 0.090153 | 0.00067214
2011 | 2011-01-24 | C | 328 | 0.19574 | 0.002387
2011 | 2011-01-25 | C | 319.3289 | 0.073216 | 0.0026069
2011 | 2011-01-25 | C | 52 | 0.0093094 | 0.00016332
2011 | 2011-01-24 | C | 5556.9 | 0.12217 | 0.018525
2011 | 2011-01-24 | C | 595.1568 | 1.1982 | 0.0023713
2011 | 2011-01-24 | C | 270.1921 | 0.342 | 0.0022237
2011 | 2011-01-23 | C | 10 | 0.0021044 | 3.1408e-05
2011 | 2011-01-24 | C | 315.1102 | 0.11382 | 0.0012186
2011 | 2011-01-23 | C | 143.0906 | 0.14741 | 0.0010239
2011 | 2011-01-23 | C | 121.211 | 0.081851 | 0.0017903
2011 | 2011-01-24 | C | 8 | 0.0056535 | 2.5127e-05
2011 | 2011-01-24 | C | 30 | 0.01338 | 9.4225e-05
2011 | 2011-01-25 | C | 24 | 0.018016 | 7.538e-05
2011 | 2011-01-24 | C | 91.3947 | 0.097312 | 0.00080719
2011 | 2011-01-25 | C | 7 | 0.0027262 | 2.1986e-05
2011 | 2011-01-24 | C | 43.8907 | 0.068926 | 0.00047426
2011 | 2011-01-24 | C | 46.0299 | 0.096285 | 0.00099564
2011 | 2011-01-24 | C | 56.516 | 0.19384 | 0.00018531
2011 | 2011-01-24 | C | 39 | 0.0020824 | 0.00012249
2011 | 2011-01-25 | B | 4 | 0.0050756 | 1.2563e-05
2011 | 2011-01-25 | B | 21 | 0.022557 | 6.5957e-05
2011 | 2011-01-25 | B | 190 | 0.054902 | 0.00059676
2011 | 2011-01-25 | C | 3 | 0.00030152 | 9.4225e-06
2011 | 2011-01-25 | C | 25 | 0.0038475 | 7.8521e-05
2011 | 2011-01-25 | C | 6 | 0.00028267 | 1.8845e-05
2011 | 2011-01-25 | C | 141 | 0.0066428 | 0.00044286
2011 | 2011-01-25 | C | 329.6809 | 0.094228 | 0.0015233
2011 | 2011-01-25 | C | 50 | 0.0080091 | 0.00015704
2011 | 2011-01-25 | C | 2.4708 | 0.0088935 | 8.4802e-05
2011 | 2011-01-26 | C | 897 | 0.19439 | 0.0028173
2011 | 2011-01-25 | C | 953.0943 | 0.14967 | 0.0036999
2011 | 2011-01-26 | B | 5 | 0.0036276 | 1.5704e-05
2011 | 2011-01-26 | C | 183 | 0.035061 | 0.00057477
2011 | 2011-01-26 | B | 48 | 0.059248 | 0.00015076
2011 | 2011-01-26 | C | 80 | 0.019347 | 0.00025127
2011 | 2011-01-26 | B | 35 | 0.043092 | 0.00010993
2011 | 2011-01-26 | B | 9 | 0.011194 | 2.8267e-05
2011 | 2011-01-26 | B | 412 | 0.23034 | 0.001294
2011 | 2011-01-24 | C | 25 | 0.071611 | 7.8521e-05
2011 | 2011-01-26 | C | 56 | 0.0038695 | 0.00017589
2011 | 2011-01-26 | B | 4 | 0.0022237 | 1.2563e-05
2011 | 2011-01-25 | C | 34.6071 | 0.014891 | 0.00016646
2011 | 2011-01-27 | C | 18 | 0.014756 | 5.6535e-05
2011 | 2011-01-27 | B | 1 | 0.00074437 | 3.1408e-06
2011 | 2011-01-27 | B | 18 | 0.0066146 | 5.6535e-05
2011 | 2011-01-27 | B | 19 | 0.019574 | 5.9676e-05
2011 | 2011-01-27 | B | 10 | 0.0085744 | 3.1408e-05
2011 | 2011-01-27 | B | 16 | 0.017438 | 5.0253e-05
2011 | 2011-01-27 | B | 110 | 0.12161 | 0.00034549
2011 | 2011-01-27 | B | 20 | 0.022802 | 6.2816e-05
2011 | 2011-01-27 | C | 98 | 0.050479 | 0.0003078
2011 | 2011-01-27 | B | 1 | 0.00060618 | 3.1408e-06
2011 | 2011-01-27 | C | 14.2428 | 0.060481 | 0.0005465
2011 | 2011-01-27 | C | 1 | 0.00019159 | 3.1408e-06
2011 | 2011-01-28 | C | 1 | 0.00012249 | 3.1408e-06
2011 | 2011-01-28 | C | 395 | 0.066994 | 0.0012406
2011 | 2011-01-28 | C | 187 | 0.031716 | 0.00058733
2011 | 2011-01-28 | C | 7 | 0.0020886 | 2.1986e-05
2011 | 2011-01-28 | C | 4 | 0.0023493 | 1.2563e-05
2011 | 2011-01-28 | B | 35 | 0.033748 | 0.00010993
2011 | 2011-01-28 | C | 244 | 0.085832 | 0.00076636
2011 | 2011-01-28 | C | 22 | 0.0032476 | 6.9098e-05
2011 | 2011-01-28 | B | 43 | 0.044163 | 0.00013506
2011 | 2011-01-28 | C | 62 | 0.034078 | 0.00019473
2011 | 2011-01-28 | C | 147 | 0.035089 | 0.0004617
2011 | 2011-01-28 | C | 5 | 0.00048683 | 1.5704e-05
2011 | 2011-01-28 | C | 3 | 0.00097994 | 9.4225e-06
2011 | 2011-01-28 | C | 412.95 | 0.15175 | 0.0027671
2011 | 2011-01-29 | C | 281.7778 | 0.045136 | 0.00089199
2011 | 2011-01-29 | C | 96.272 | 0.07136 | 0.0022394
2011 | 2011-01-29 | B | 3 | 0.00038632 | 9.4225e-06
2011 | 2011-01-29 | C | 479 | 0.049647 | 0.0015045
2011 | 2011-01-29 | C | 310.1325 | 0.3721 | 0.0019096
2011 | 2011-01-29 | C | 1 | 0.00024184 | 3.1408e-06
2011 | 2011-01-29 | C | 92 | 0.012714 | 0.00028896
2011 | 2011-01-29 | C | 86.3333 | 0.038233 | 0.00035491
2011 | 2011-01-29 | C | 479 | 0.021062 | 0.0015045
2011 | 2011-01-29 | C | 48 | 0.0040705 | 0.00015076
2011 | 2011-01-30 | C | 272 | 0.013669 | 0.0008543
2011 | 2011-01-29 | C | 48 | 0.10463 | 0.00015076
2011 | 2011-01-29 | C | 31 | 0.0033104 | 9.7365e-05
2011 | 2011-01-29 | C | 213.6265 | 0.053677 | 0.0010993
2011 | 2011-01-30 | C | 18 | 0.0049185 | 5.6535e-05
2011 | 2011-01-29 | C | 736 | 0.039298 | 0.0023116
2011 | 2011-01-29 | C | 760 | 0.042966 | 0.002387
2011 | 2011-01-29 | C | 146 | 0.016967 | 0.00045856
2011 | 2011-01-29 | C | 134 | 0.12037 | 0.00042087
2011 | 2011-01-31 | C | 20 | 0.0021358 | 6.2816e-05
2011 | 2011-01-31 | C | 187 | 0.0076353 | 0.00058733
2011 | 2011-01-28 | B | 11.4302 | 0.10461 | 0.00094539
2011 | 2011-01-31 | C | 286 | 0.25152 | 0.00089828
2011 | 2011-01-29 | C | 61 | 0.0013411 | 0.00019159
2011 | 2011-01-29 | C | 196.3596 | 0.21771 | 0.0012218
2011 | 2011-01-31 | C | 125 | 0.001963 | 0.0003926
2011 | 2011-01-29 | C | 190.0297 | 0.3599 | 0.0014982
2011 | 2011-01-29 | C | 191.6506 | 0.098116 | 0.00099878
2011 | 2011-01-29 | C | 110 | 0.0048369 | 0.00034549
2011 | 2011-01-29 | C | 140.7313 | 0.92823 | 0.0012155
2011 | 2011-01-29 | C | 262 | 0.026333 | 0.0008229
2011 | 2011-01-29 | C | 62 | 0.013826 | 0.00019473
2011 | 2011-01-29 | C | 319.6667 | 0.087349 | 0.0016238
2011 | 2011-01-30 | C | 14 | 0.0053645 | 4.3972e-05
2011 | 2011-01-30 | C | 2 | 0.0015893 | 6.2816e-06
2011 | 2011-01-30 | C | 422.1488 | 0.21877 | 0.001718
2011 | 2011-01-31 | C | 17 | 0.0016018 | 5.3394e-05
2011 | 2011-01-29 | C | 773.9048 | 0.29898 | 0.0032319
2011 | 2011-01-31 | C | 125 | 0.019238 | 0.0003926
2011 | 2011-01-30 | C | 5 | 0.0015547 | 1.5704e-05
2011 | 2011-01-31 | C | 56 | 0.0033418 | 0.00017589
2011 | 2011-01-30 | C | 280 | 0.18556 | 0.0035774
2011 | 2011-01-31 | C | 253 | 0.081052 | 0.00079463
2011 | 2011-01-24 | C | 307.0083 | 0.23046 | 0.0015202
2011 | 2011-01-31 | C | 769.6935 | 0.29251 | 0.002811
2011 | 2011-01-31 | C | 12 | 0.0036936 | 3.769e-05
2011 | 2011-01-31 | C | 53 | 0.0029963 | 0.00016646
2011 | 2011-01-29 | C | 97.5122 | 0.19999 | 0.0003235
2011 | 2011-01-31 | C | 9 | 0.0015547 | 2.8267e-05
2011 | 2011-01-31 | C | 131.3885 | 0.12091 | 0.0013286
2011 | 2011-01-31 | C | 46 | 0.024272 | 0.00014448
2011 | 2011-01-31 | C | 135.902 | 0.22964 | 0.00223
2011 | 2011-01-31 | C | 517 | 0.016238 | 0.0016238
2011 | 2011-01-31 | C | 223.957 | 0.12872 | 0.00084488
2011 | 2011-02-01 | C | 578 | 0.14886 | 0.0018154
2011 | 2011-01-29 | C | 39 | 0.076803 | 0.00012249
2011 | 2011-01-31 | C | 107.5306 | 0.081732 | 0.00034235
2011 | 2011-01-31 | C | 65 | 0.011637 | 0.00020415
2011 | 2011-01-31 | C | 303 | 0.050438 | 0.00095167
2011 | 2011-01-31 | C | 569.4 | 0.012519 | 0.0026885
2011 | 2011-01-31 | C | 28 | 0.0059801 | 8.7943e-05
2011 | 2011-01-31 | C | 116 | 0.12497 | 0.00036434
2011 | 2011-01-31 | C | 15 | 0.012014 | 4.7112e-05
2011 | 2011-01-31 | C | 26 | 0.018619 | 8.1661e-05
2011 | 2011-01-29 | C | 379.9749 | 0.37713 | 0.0024122
2011 | 2011-02-01 | C | 336.9719 | 0.29846 | 0.0023525
2011 | 2011-02-01 | B | 80 | 0.09724 | 0.00025127
2011 | 2011-01-31 | C | 20.1304 | 0.046345 | 6.5957e-05
2011 | 2011-02-01 | C | 3 | 0.0033167 | 9.4225e-06
2011 | 2011-02-01 | B | 55 | 0.087409 | 0.00017275
2011 | 2011-02-01 | C | 5 | 0.001806 | 1.5704e-05
2011 | 2011-02-01 | C | 6 | 0.0016018 | 1.8845e-05
2011 | 2011-02-01 | B | 9 | 0.010035 | 2.8267e-05
2011 | 2011-02-01 | B | 7 | 0.0050128 | 2.1986e-05
2011 | 2011-02-01 | C | 3 | 0.00019787 | 9.4225e-06
2011 | 2011-01-31 | C | 66 | 0.031923 | 0.00020729
2011 | 2011-02-02 | B | 17 | 0.0050724 | 5.3394e-05
2011 | 2011-02-02 | B | 130 | 0.13474 | 0.00040831
2011 | 2011-02-02 | B | 62 | 0.011489 | 0.00019473
2011 | 2011-02-02 | B | 77 | 0.042806 | 0.00024184
2011 | 2011-02-02 | B | 127 | 0.046669 | 0.00039888
2011 | 2011-02-02 | C | 429 | 0.044465 | 0.0013474
2011 | 2011-02-02 | C | 81.9276 | 0.056096 | 0.00038004
2011 | 2011-02-02 | C | 29 | 0.011385 | 9.1084e-05
2011 | 2011-02-02 | C | 136 | 0.0068344 | 0.00042715
2011 | 2011-02-02 | B | 5 | 0.0060775 | 1.5704e-05
2011 | 2011-02-02 | C | 179 | 0.051723 | 0.00056221
2011 | 2011-02-02 | C | 78.5802 | 0.039242 | 0.00036119
2011 | 2011-02-02 | C | 270.6788 | 0.278 | 0.0012343
2011 | 2011-02-02 | C | 106 | 0.017978 | 0.00033293
2011 | 2011-02-02 | C | 37 | 0.0061592 | 0.00011621
2011 | 2011-02-03 | C | 8 | 0.0031408 | 2.5127e-05
2011 | 2011-02-03 | C | 17 | 0.0024561 | 5.3394e-05
2011 | 2011-02-03 | C | 76 | 0.0031031 | 0.0002387
2011 | 2011-01-30 | C | 68 | 0.014737 | 0.00021358
2011 | 2011-02-03 | B | 50 | 0.01806 | 0.00015704
2011 | 2011-02-03 | B | 3 | 0.0017149 | 9.4225e-06
2011 | 2011-02-03 | B | 29 | 0.022498 | 9.1084e-05
2011 | 2011-02-03 | B | 57 | 0.050665 | 0.00017903
2011 | 2011-02-03 | B | 49 | 0.05171 | 0.0001539
2011 | 2011-02-03 | B | 40 | 0.044223 | 0.00012563
2011 | 2011-02-03 | B | 11 | 0.013301 | 3.4549e-05
2011 | 2011-02-02 | C | 183 | 0.056327 | 0.00057477
2011 | 2011-02-02 | C | 123 | 0.0042495 | 0.00038632
2011 | 2011-02-02 | C | 2 | 0.00043972 | 6.2816e-06
2011 | 2011-02-02 | C | 6 | 0.012815 | 1.8845e-05
2011 | 2011-02-03 | C | 365 | 0.025221 | 0.0011464
2011 | 2011-02-03 | C | 99.8862 | 0.10102 | 0.00055278
2011 | 2011-02-03 | C | 34 | 0.018901 | 0.00010679
2011 | 2011-02-04 | C | 52 | 0.0080028 | 0.00016332
2011 | 2011-02-04 | C | 82 | 0.012877 | 0.00025755
2011 | 2011-02-04 | C | 777.297 | 0.23925 | 0.0029869
2011 | 2011-02-04 | C | 546.8895 | 0.32121 | 0.002387
2011 | 2011-02-04 | C | 935.7753 | 0.25276 | 0.0036936
2011 | 2011-02-04 | C | 72.8991 | 0.02427 | 0.00027325
2011 | 2011-02-04 | C | 82 | 0.0046359 | 0.00025755
2011 | 2011-02-04 | C | 6 | 0.0017714 | 1.8845e-05
2011 | 2011-02-04 | C | 58.1922 | 0.046058 | 0.00081347
2011 | 2011-02-04 | C | 4 | 0.00095481 | 1.2563e-05
2011 | 2011-02-04 | C | 951 | 0.23895 | 0.0029869
2011 | 2011-02-04 | C | 22 | 0.014718 | 6.9098e-05
2011 | 2011-02-04 | C | 82 | 0.0036057 | 0.00025755
2011 | 2011-02-04 | B | 1 | 0.00096423 | 3.1408e-06
2011 | 2011-02-04 | B | 1 | 0.0010302 | 3.1408e-06
2011 | 2011-02-04 | C | 98.4541 | 0.063082 | 0.00074752
2011 | 2011-02-04 | C | 1193 | 0.1836 | 0.003747
2011 | 2011-02-04 | C | 499.7941 | 0.048663 | 0.0029869
2011 | 2011-02-04 | C | 124 | 0.061924 | 0.00038946
2011 | 2011-02-04 | C | 62 | 0.023368 | 0.00019473
2011 | 2011-02-04 | C | 82.4749 | 0.11812 | 0.00040203
2011 | 2011-02-05 | C | 1 | 0.0015861 | 3.1408e-06
2011 | 2011-02-05 | C | 114.1608 | 0.10147 | 0.0010867
2011 | 2011-02-06 | C | 423 | 0.079714 | 0.0013286
2011 | 2011-02-06 | C | 27 | 0.019505 | 8.4802e-05
2011 | 2011-02-06 | C | 139 | 0.018773 | 0.00043657
2011 | 2011-02-07 | C | 226 | 0.022714 | 0.00070983
2011 | 2011-02-07 | C | 110 | 0.025566 | 0.00034549
2011 | 2011-02-07 | C | 2907.0408 | 0.42 | 0.0098339
2011 | 2011-02-07 | B | 60 | 0.063319 | 0.00018845
2011 | 2011-02-07 | B | 9 | 0.011618 | 2.8267e-05
2011 | 2011-02-07 | B | 3 | 0.0025252 | 9.4225e-06
2011 | 2011-02-07 | B | 33 | 0.031301 | 0.00010365
2011 | 2011-02-07 | C | 187.7742 | 0.071362 | 0.0005999
2011 | 2011-02-07 | C | 213.6111 | 0.070446 | 0.00073809
2011 | 2011-02-07 | C | 375 | 0.023556 | 0.0011778
2011 | 2011-02-07 | C | 56 | 0.0026383 | 0.00017589
2011 | 2011-02-08 | C | 151.4425 | 0.052322 | 0.00085744
2011 | 2011-02-08 | C | 375 | 0.024734 | 0.0011778
2011 | 2011-02-08 | C | 401.3557 | 0.24077 | 0.0015736
2011 | 2011-02-08 | C | 19 | 0.0030435 | 5.9676e-05
2011 | 2011-02-08 | B | 52 | 0.012739 | 0.00016332
2011 | 2011-02-08 | B | 81 | 0.0491 | 0.00025441
2011 | 2011-02-08 | B | 91 | 0.049732 | 0.00028581
2011 | 2011-02-08 | B | 30 | 0.02252 | 9.4225e-05
2011 | 2011-02-08 | C | 90 | 0.04127 | 0.00028267
2011 | 2011-02-08 | B | 21 | 0.022162 | 6.5957e-05
2011 | 2011-02-08 | C | 11 | 0.0026603 | 3.4549e-05
2011 | 2011-02-08 | B | 43 | 0.032683 | 0.00013506
2011 | 2011-02-08 | B | 19 | 0.021304 | 5.9676e-05
2011 | 2011-02-08 | C | 38 | 0.00083546 | 0.00011935
2011 | 2011-02-08 | C | 10 | 0.00084802 | 3.1408e-05
2011 | 2011-02-08 | C | 16 | 0.0029147 | 5.0253e-05
2011 | 2011-02-08 | C | 277.0625 | 0.1227 | 0.0021389
2011 | 2011-02-09 | B | 120 | 0.033921 | 0.0003769
2011 | 2011-02-09 | B | 1 | 0.00034549 | 3.1408e-06
2011 | 2011-02-09 | B | 3 | 0.0025818 | 9.4225e-06
2011 | 2011-02-09 | B | 7 | 0.0078489 | 2.1986e-05
2011 | 2011-02-09 | B | 19 | 0.021304 | 5.9676e-05
2011 | 2011-02-09 | B | 11 | 0.012334 | 3.4549e-05
2011 | 2011-02-09 | C | 171.1566 | 0.043006 | 0.000669
2011 | 2011-02-09 | C | 8 | 0.0017086 | 2.5127e-05
2011 | 2011-02-09 | B | 1 | 0.0004617 | 3.1408e-06
2011 | 2011-02-10 | B | 7 | 0.0034957 | 2.1986e-05
2011 | 2011-02-10 | C | 26 | 0.0035114 | 8.1661e-05
2011 | 2011-02-10 | B | 108 | 0.12449 | 0.00033921
2011 | 2011-02-10 | B | 80 | 0.098747 | 0.00025127
2011 | 2011-02-10 | B | 3 | 0.0013568 | 9.4225e-06
2011 | 2011-02-10 | C | 8 | 0.0024624 | 2.5127e-05
2011 | 2011-03-11 | B | 8 | 0.0080656 | 2.5127e-05
2011 | 2011-02-10 | B | 50 | 0.032822 | 0.00015704
2011 | 2011-02-10 | B | 2 | 0.0023054 | 6.2816e-06
2011 | 2011-02-10 | B | 60 | 0.061434 | 0.00018845
2011 | 2011-02-10 | B | 5 | 0.0062031 | 1.5704e-05
2011 | 2011-02-10 | C | 91 | 0.0037156 | 0.00028581
2011 | 2011-02-10 | C | 24 | 0.011458 | 7.538e-05
2011 | 2011-02-10 | C | 2 | 0.0034612 | 6.2816e-06
2011 | 2011-02-11 | C | 3144 | 0.049374 | 0.0098747
2011 | 2011-02-10 | B | 62 | 0.056667 | 0.00019473
2011 | 2011-02-11 | B | 3 | 0.0020918 | 9.4225e-06
2011 | 2011-02-11 | B | 20 | 0.0050253 | 6.2816e-05
2011 | 2011-02-11 | B | 1 | 0.001027 | 3.1408e-06
2011 | 2011-02-11 | C | 5725 | 0.64732 | 0.017981
2011 | 2011-02-11 | C | 1019.5946 | 0.22737 | 0.0040234
2011 | 2011-02-11 | C | 198.0704 | 0.12193 | 0.0030089
2011 | 2011-02-11 | B | 4 | 0.0040454 | 1.2563e-05
2011 | 2011-02-11 | C | 3 | 0.0003769 | 9.4225e-06
2011 | 2011-02-11 | B | 33 | 0.0029021 | 0.00010365
2011 | 2011-02-11 | C | 279.9459 | 0.062427 | 0.0011401
2011 | 2011-02-09 | C | 185.023 | 0.048814 | 0.00081033
2011 | 2011-02-11 | C | 247.375 | 0.072257 | 0.00081347
2011 | 2011-02-09 | C | 200 | 0.032665 | 0.00062816
2011 | 2011-02-11 | C | 111.7161 | 0.081755 | 0.0011244
2011 | 2011-02-11 | C | 92.0546 | 0.099749 | 0.001473
2011 | 2011-02-12 | C | 221 | 0.012494 | 0.00069412
2011 | 2011-02-12 | C | 46 | 0.020227 | 0.00014448
2011 | 2011-02-12 | B | 1 | 0.00011621 | 3.1408e-06
2011 | 2011-02-12 | B | 3 | 0.0031565 | 9.4225e-06
2011 | 2011-02-13 | B | 23 | 0.0050567 | 7.2239e-05
2011 | 2011-02-13 | C | 94.3474 | 0.055413 | 0.00080091
2011 | 2011-02-13 | C | 675 | 0.042401 | 0.0021201
2011 | 2011-02-11 | B | 7 | 0.0069035 | 2.1986e-05
2011 | 2011-02-14 | C | 566.4607 | 0.31135 | 0.0041427
2011 | 2011-02-14 | B | 4 | 0.0042841 | 1.2563e-05
2011 | 2011-02-14 | C | 11 | 0.011989 | 3.4549e-05
2011 | 2011-02-14 | B | 19 | 0.013666 | 5.9676e-05
2011 | 2011-02-14 | B | 28 | 0.027878 | 8.7943e-05
2011 | 2011-02-14 | C | 96.1074 | 0.044071 | 0.00070354
2011 | 2011-02-14 | C | 237 | 0.01191 | 0.00074437
2011 | 2011-02-14 | B | 342 | 0.058005 | 0.0010742
2011 | 2011-02-14 | B | 102 | 0.034279 | 0.00032036
2011 | 2011-02-15 | B | 94 | 0.016238 | 0.00029524
2011 | 2011-02-15 | C | 8224 | 0.23247 | 0.02583
2011 | 2011-02-15 | B | 20 | 0.0084174 | 6.2816e-05
2011 | 2011-02-15 | B | 2 | 0.0016458 | 6.2816e-06
2011 | 2011-02-15 | C | 5 | 0.00040831 | 1.5704e-05
2011 | 2011-02-15 | B | 4 | 0.0042464 | 1.2563e-05
2011 | 2011-02-15 | B | 55 | 0.06357 | 0.00017275
2011 | 2011-02-15 | B | 22 | 0.027294 | 6.9098e-05
2011 | 2011-02-15 | B | 83 | 0.11809 | 0.00026069
2011 | 2011-02-15 | C | 3 | 0.0015547 | 9.4225e-06
2011 | 2011-02-15 | B | 8 | 0.0084677 | 2.5127e-05
2011 | 2011-02-15 | C | 1 | 0.0014605 | 3.1408e-06
2011 | 2011-02-15 | B | 77 | 0.013301 | 0.00024184
2011 | 2011-02-16 | B | 243 | 0.035108 | 0.00076322
2011 | 2011-02-16 | B | 33 | 0.027674 | 0.00010365
2011 | 2011-02-16 | B | 31 | 0.031157 | 9.7365e-05
2011 | 2011-02-16 | B | 4 | 0.0035931 | 1.2563e-05
2011 | 2011-02-16 | B | 26 | 0.017231 | 8.1661e-05
2011 | 2011-02-16 | B | 16 | 0.011759 | 5.0253e-05
2011 | 2011-02-16 | B | 19 | 0.022796 | 5.9676e-05
2011 | 2011-02-16 | B | 128 | 0.14111 | 0.00040203
2011 | 2011-02-16 | C | 1.2048 | 0.0048663 | 1.2563e-05
2011 | 2011-02-16 | C | 67.1648 | 0.018564 | 0.00021358
2011 | 2011-02-16 | B | 141 | 0.20194 | 0.00044286
2011 | 2011-02-17 | B | 14 | 0.0047489 | 4.3972e-05
2011 | 2011-02-17 | B | 2 | 0.0006156 | 6.2816e-06
2011 | 2011-02-17 | B | 1 | 0.00092026 | 3.1408e-06
2011 | 2011-02-17 | B | 26 | 0.030378 | 8.1661e-05
2011 | 2011-02-17 | B | 305 | 0.33816 | 0.00095795
2011 | 2011-02-17 | C | 1 | 0.00051509 | 3.1408e-06
2011 | 2011-02-18 | B | 49 | 0.030934 | 0.0001539
2011 | 2011-02-18 | C | 23 | 0.008452 | 7.2239e-05
2011 | 2011-02-18 | B | 32 | 0.028142 | 0.00010051
2011 | 2011-02-18 | B | 19 | 0.020111 | 5.9676e-05
2011 | 2011-02-18 | B | 31 | 0.031449 | 9.7365e-05
2011 | 2011-02-18 | B | 41 | 0.041079 | 0.00012877
2011 | 2011-02-18 | B | 256 | 0.031358 | 0.00080405
2011 | 2011-02-19 | B | 75 | 0.049232 | 0.00023556
2011 | 2011-02-19 | C | 240 | 0.052766 | 0.0007538
2011 | 2011-02-19 | B | 44 | 0.041597 | 0.0001382
2011 | 2011-02-19 | B | 1 | 0.00048683 | 3.1408e-06
2011 | 2011-02-20 | C | 792.1081 | 0.26869 | 0.0032508
2011 | 2011-02-20 | C | 2123 | 0.18004 | 0.006668
2011 | 2011-02-18 | B | 1 | 0.00038318 | 3.1408e-06
2011 | 2011-02-21 | C | 40 | 0.034172 | 0.00012563
2011 | 2011-02-21 | B | 1 | 0.0008543 | 3.1408e-06
2011 | 2011-02-21 | C | 6 | 0.00039574 | 1.8845e-05
2011 | 2011-02-21 | B | 22 | 0.020937 | 6.9098e-05
2011 | 2011-02-21 | B | 8 | 0.0079149 | 2.5127e-05
2011 | 2011-02-21 | B | 42 | 0.031659 | 0.00013191
2011 | 2011-02-21 | B | 52 | 0.041811 | 0.00016332
2011 | 2011-02-21 | B | 6 | 0.0046359 | 1.8845e-05
2011 | 2011-02-21 | B | 7 | 0.0019567 | 2.1986e-05
2011 | 2011-02-21 | B | 3 | 0.0018845 | 9.4225e-06
2011 | 2011-02-21 | C | 36.4009 | 0.049276 | 0.00020415
2011 | 2011-02-21 | B | 165 | 0.20574 | 0.00051824
2011 | 2011-02-21 | C | 313.5 | 0.056125 | 0.0013851
2011 | 2011-02-21 | B | 29 | 0.02441 | 9.1084e-05
2011 | 2011-02-22 | B | 8 | 0.0012815 | 2.5127e-05
2011 | 2011-02-21 | B | 25 | 0.010051 | 7.8521e-05
2011 | 2011-02-22 | C | 4 | 0.00052766 | 1.2563e-05
2011 | 2011-02-22 | C | 428.1129 | 0.4249 | 0.0033041
2011 | 2011-02-22 | B | 32 | 0.037891 | 0.00010051
2011 | 2011-02-22 | C | 101.3765 | 0.080238 | 0.00093911
2011 | 2011-02-22 | B | 60 | 0.095544 | 0.00018845
2011 | 2011-02-22 | B | 32 | 0.035881 | 0.00010051
2011 | 2011-02-22 | B | 64 | 0.078395 | 0.00020101
2011 | 2011-02-22 | B | 360 | 0.29398 | 0.0011307
2011 | 2011-02-22 | B | 31 | 0.035441 | 9.7365e-05
2011 | 2011-02-22 | B | 80 | 0.096235 | 0.00025127
2011 | 2011-02-22 | C | 33 | 0.0036276 | 0.00010365
2011 | 2011-02-22 | C | 675 | 0.069962 | 0.0021201
2011 | 2011-02-22 | C | 168 | 0.014247 | 0.00052766
2011 | 2011-02-22 | B | 74 | 0.002789 | 0.00023242
2011 | 2011-02-22 | B | 42 | 0.046962 | 0.00013191
2011 | 2011-02-23 | C | 265 | 0.029131 | 0.00083232
2011 | 2011-02-23 | B | 9 | 0.0042966 | 2.8267e-05
2011 | 2011-02-23 | B | 13 | 0.010983 | 4.0831e-05
2011 | 2011-02-23 | B | 22 | 0.023977 | 6.9098e-05
2011 | 2011-02-23 | C | 76 | 0.030315 | 0.0002387
2011 | 2011-02-23 | B | 32 | 0.034072 | 0.00010051
2011 | 2011-02-23 | B | 125 | 0.14173 | 0.0003926
2011 | 2011-02-23 | B | 141 | 0.038528 | 0.00044286
2011 | 2011-02-23 | B | 29 | 0.032517 | 9.1084e-05
2011 | 2011-02-23 | B | 10 | 0.01027 | 3.1408e-05
2011 | 2011-02-23 | C | 78.125 | 0.077784 | 0.00037376
2011 | 2011-02-23 | C | 2 | 0.0071862 | 6.2816e-06
2011 | 2011-02-24 | B | 544 | 0.19478 | 0.0017086
2011 | 2011-02-24 | B | 30 | 0.024875 | 9.4225e-05
2011 | 2011-02-24 | B | 22 | 0.021973 | 6.9098e-05
2011 | 2011-02-24 | B | 34.9059 | 0.036946 | 0.00018845
2011 | 2011-02-24 | B | 64 | 0.072968 | 0.00020101
2011 | 2011-02-24 | B | 31 | 0.038362 | 9.7365e-05
2011 | 2011-02-24 | B | 83 | 0.10349 | 0.00026069
2011 | 2011-02-24 | B | 58 | 0.063941 | 0.00018217
2011 | 2011-02-25 | C | 72.1283 | 0.041684 | 0.00026383
2011 | 2011-02-25 | C | 183.35 | 0.28621 | 0.0014354
2011 | 2011-02-25 | B | 158 | 0.14739 | 0.00049625
2011 | 2011-02-25 | B | 26 | 0.033236 | 8.1661e-05
2011 | 2011-02-25 | B | 5 | 0.0025284 | 1.5704e-05
2011 | 2011-02-25 | C | 448.4127 | 0.17323 | 0.0027294
2011 | 2011-02-25 | C | 568.76 | 0.08396 | 0.0018123
2011 | 2011-02-25 | C | 1030.8997 | 0.95841 | 0.024489
2011 | 2011-02-26 | C | 656.2812 | 0.12574 | 0.0021452
2011 | 2011-02-26 | B | 92 | 0.078885 | 0.00028896
2011 | 2011-02-26 | C | 134.0811 | 0.045481 | 0.0021263
2011 | 2011-02-26 | C | 23.9345 | 0.057132 | 0.00019787
2011 | 2011-02-27 | C | 30.6471 | 0.016075 | 0.00023242
2011 | 2011-02-26 | C | 966 | 0.078885 | 0.003034
2011 | 2011-02-27 | C | 320.2647 | 0.13378 | 0.0036434
2011 | 2011-02-27 | C | 137.9268 | 0.016462 | 0.00048055
2011 | 2011-02-27 | B | 224 | 0.50374 | 0.00070354
2011 | 2011-02-27 | C | 79.5979 | 0.0235 | 0.00049625
2011 | 2011-02-27 | C | 786 | 0.022218 | 0.0024687
2011 | 2011-02-27 | C | 125 | 0.014134 | 0.0003926
2011 | 2011-02-26 | B | 3 | 0.0046735 | 9.4225e-06
2011 | 2011-02-28 | B | 130 | 0.046547 | 0.00040831
2011 | 2011-02-28 | B | 53 | 0.033459 | 0.00016646
2011 | 2011-02-28 | B | 35 | 0.03122 | 0.00010993
2011 | 2011-02-28 | B | 12 | 0.0089325 | 3.769e-05
2011 | 2011-02-28 | B | 44 | 0.040906 | 0.0001382
2011 | 2011-02-28 | B | 236.993 | 0.31635 | 0.0011621
2011 | 2011-02-28 | B | 10 | 0.010773 | 3.1408e-05
2011 | 2011-02-28 | C | 817.1868 | 0.22586 | 0.0031534
2011 | 2011-02-28 | C | 18 | 0.0035052 | 5.6535e-05
2011 | 2011-02-28 | C | 135.2692 | 0.031864 | 0.0004774
2011 | 2011-02-20 | B | 33.7383 | 0.042598 | 0.00035491
2011 | 2011-03-01 | B | 1 | 0.00017275 | 3.1408e-06
2011 | 2011-03-01 | B | 12 | 0.0057289 | 3.769e-05
2011 | 2011-03-01 | B | 115 | 0.1145 | 0.00036119
2011 | 2011-03-01 | B | 31 | 0.035538 | 9.7365e-05
2011 | 2011-03-01 | B | 38.6991 | 0.052144 | 0.00025755
2011 | 2011-03-01 | C | 248.2151 | 0.32743 | 0.00080091
2011 | 2011-03-01 | B | 22 | 0.023908 | 6.9098e-05
2011 | 2011-03-01 | C | 64 | 0.0024122 | 0.00020101
2011 | 2011-03-01 | C | 3 | 0.0011024 | 9.4225e-06
2011 | 2011-03-02 | C | 38 | 0.0028644 | 0.00011935
2011 | 2011-03-02 | B | 1 | 0.00059676 | 3.1408e-06
2011 | 2011-03-02 | C | 981.44 | 0.14488 | 0.0038946
2011 | 2011-03-02 | B | 12 | 0.010779 | 3.769e-05
2011 | 2011-03-02 | C | 23 | 0.0016615 | 7.2239e-05
2011 | 2011-03-02 | C | 103.1633 | 0.046659 | 0.00071925
2011 | 2011-03-02 | C | 201.3624 | 0.092337 | 0.0011621
2011 | 2011-03-02 | C | 36 | 0.0173 | 0.00011307
2011 | 2011-03-02 | C | 97.7931 | 0.0079859 | 0.00051509
2011 | 2011-03-02 | C | 3 | 0.00065957 | 9.4225e-06
2011 | 2011-03-02 | C | 14 | 0.0013631 | 4.3972e-05
2011 | 2011-03-02 | C | 675 | 0.050881 | 0.0021201
2011 | 2011-03-02 | C | 168 | 0.035353 | 0.00065957
2011 | 2011-03-02 | C | 46.5207 | 0.017241 | 0.00020415
2011 | 2011-03-02 | C | 34 | 0.012494 | 0.00010679
2011 | 2011-03-02 | C | 155 | 0.028236 | 0.00048683
2011 | 2011-03-02 | C | 405.3 | 0.22532 | 0.0015547
2011 | 2011-03-02 | C | 228 | 0.014322 | 0.00071611
2011 | 2011-03-02 | C | 263 | 0.029737 | 0.00082604
2011 | 2011-03-02 | C | 351 | 0.065043 | 0.0011024
2011 | 2011-03-03 | C | 55 | 0.020038 | 0.00017275
2011 | 2011-03-03 | B | 22 | 0.025083 | 6.9098e-05
2011 | 2011-03-03 | B | 31 | 0.034759 | 9.7365e-05
2011 | 2011-03-03 | B | 12 | 0.019033 | 3.769e-05
2011 | 2011-03-03 | C | 823.6136 | 0.10606 | 0.0035366
2011 | 2011-03-03 | B | 1 | 0.00048683 | 3.1408e-06
2011 | 2011-03-03 | B | 365 | 0.11808 | 0.0011464
2011 | 2011-03-03 | B | 192 | 0.19719 | 0.00060304
2011 | 2011-03-03 | B | 1 | 0.0012249 | 3.1408e-06
2011 | 2011-03-03 | B | 175 | 0.038475 | 0.00054964
2011 | 2011-03-04 | C | 59 | 0.0075976 | 0.00018531
2011 | 2011-03-04 | C | 7 | 0.0011433 | 2.1986e-05
2011 | 2011-03-04 | B | 275 | 0.29712 | 0.00086373
2011 | 2011-03-04 | C | 146.22 | 0.021585 | 0.00051195
2011 | 2011-03-04 | C | 3 | 0.00065957 | 9.4225e-06
2011 | 2011-03-04 | B | 41 | 0.042882 | 0.00012877
2011 | 2011-03-04 | C | 189.8898 | 0.068587 | 0.00071297
2011 | 2011-03-04 | C | 8.6365 | 0.026854 | 0.00015704
2011 | 2011-03-05 | C | 134 | 0.079544 | 0.0010176
2011 | 2011-03-05 | C | 37 | 0.0059267 | 0.00011621
2011 | 2011-03-05 | C | 82 | 0.0038632 | 0.00025755
2011 | 2011-03-05 | C | 746.6915 | 0.21342 | 0.0040831
2011 | 2011-03-05 | C | 162.0722 | 0.04785 | 0.00067528
2011 | 2011-03-06 | C | 2 | 0.0005465 | 6.2816e-06
2011 | 2011-03-06 | C | 139 | 0.023575 | 0.00058419
2011 | 2011-03-06 | C | 132.4898 | 0.16187 | 0.0018311
2011 | 2011-03-06 | C | 117.1625 | 0.028335 | 0.00050253
2011 | 2011-03-06 | C | 159 | 0.026468 | 0.00049939
2011 | 2011-03-06 | B | 238 | 0.16894 | 0.00074752
2011 | 2011-03-06 | C | 297.3465 | 0.11581 | 0.0019756
2011 | 2011-03-06 | C | 13 | 0.0032256 | 4.0831e-05
2011 | 2011-03-06 | C | 10 | 0.0021986 | 3.1408e-05
2011 | 2011-03-07 | C | 24 | 0.011835 | 7.538e-05
2011 | 2011-03-07 | C | 444.9255 | 0.35215 | 0.0019881
2011 | 2011-03-07 | C | 638.0505 | 0.19238 | 0.0036465
2011 | 2011-03-08 | C | 301.3006 | 0.15141 | 0.0026509
2011 | 2011-03-07 | B | 181 | 0.040363 | 0.00056849
2011 | 2011-03-06 | C | 803.6609 | 0.28271 | 0.0030749
2011 | 2011-03-08 | C | 496 | 0.03583 | 0.0015578
2011 | 2011-03-08 | C | 97 | 0.012491 | 0.00030466
2011 | 2011-03-08 | B | 2 | 0.00024498 | 6.2816e-06
2011 | 2011-03-08 | B | 25 | 0.023949 | 7.8521e-05
2011 | 2011-03-08 | B | 13 | 0.014495 | 4.0831e-05
2011 | 2011-03-08 | B | 4 | 0.0042087 | 1.2563e-05
2011 | 2011-03-08 | B | 76 | 0.020051 | 0.00029524
2011 | 2011-03-09 | C | 34.1102 | 0.078422 | 0.00070354
2011 | 2011-03-09 | C | 199 | 0.026251 | 0.00077578
2011 | 2011-03-09 | C | 98 | 0.006156 | 0.0003078
2011 | 2011-03-09 | B | 47 | 0.046057 | 0.00014762
2011 | 2011-03-09 | B | 34 | 0.037376 | 0.00010679
2011 | 2011-03-09 | B | 51 | 0.060389 | 0.00016018
2011 | 2011-03-09 | B | 2 | 0.0023807 | 6.2816e-06
2011 | 2011-03-09 | B | 19 | 0.00017903 | 5.9676e-05
2011 | 2011-03-09 | C | 185.6836 | 0.15863 | 0.0020164
2011 | 2011-03-09 | C | 762 | 0.15796 | 0.0023933
2011 | 2011-03-09 | B | 1 | 0.0008229 | 3.1408e-06
2011 | 2011-03-10 | B | 93 | 0.096976 | 0.0002921
2011 | 2011-03-10 | B | 25 | 0.028424 | 7.8521e-05
2011 | 2011-03-10 | B | 22 | 0.023286 | 6.9098e-05
2011 | 2011-03-10 | B | 20 | 0.02588 | 6.2816e-05
2011 | 2011-03-10 | C | 195.2614 | 0.46977 | 0.0028424
2011 | 2011-03-10 | C | 336 | 0.078093 | 0.0010553
2011 | 2011-03-10 | C | 500.3905 | 0.92098 | 0.0024027
2011 | 2011-03-10 | B | 42.3757 | 0.071871 | 0.00024498
2011 | 2011-03-11 | B | 1 | 0.00034549 | 3.1408e-06
2011 | 2011-03-11 | B | 39 | 0.012494 | 0.00012249
2011 | 2011-03-11 | B | 51 | 0.056064 | 0.00016018
2011 | 2011-03-11 | B | 33 | 0.030472 | 0.00010365
2011 | 2011-03-12 | B | 72 | 0.063319 | 0.00022614
2011 | 2011-03-12 | C | 3 | 0.00044286 | 9.4225e-06
2011 | 2011-03-12 | C | 471.5934 | 0.13034 | 0.0021923
2011 | 2011-03-12 | C | 55 | 0.01261 | 0.00017275
2011 | 2011-03-13 | C | 398 | 0.058752 | 0.00125
2011 | 2011-03-14 | C | 151 | 0.017548 | 0.00047426
2011 | 2011-03-14 | B | 3 | 0.0018656 | 9.4225e-06
2011 | 2011-03-14 | B | 1 | 0.0008386 | 3.1408e-06
2011 | 2011-03-14 | B | 34 | 0.037055 | 0.00010679
2011 | 2011-03-14 | B | 15 | 0.02153 | 4.7112e-05
2011 | 2011-03-14 | C | 10 | 0.00053394 | 3.1408e-05
2011 | 2011-03-14 | C | 20.25 | 0.014565 | 9.4225e-05
2011 | 2011-03-15 | C | 901.2955 | 0.11606 | 0.0034675
2011 | 2011-03-15 | B | 34 | 0.012815 | 0.00010679
2011 | 2011-03-15 | B | 51 | 0.054782 | 0.00016018
2011 | 2011-03-15 | B | 2 | 0.0023745 | 6.2816e-06
2011 | 2011-03-15 | B | 95 | 0.047144 | 0.00029838
2011 | 2011-03-15 | B | 32 | 0.020905 | 0.00010051
2011 | 2011-03-15 | B | 40 | 0.048871 | 0.00012563
2011 | 2011-03-15 | B | 6 | 0.0070103 | 1.8845e-05
2011 | 2011-03-15 | B | 109 | 0.1318 | 0.00034235
2011 | 2011-03-15 | B | 80 | 0.091712 | 0.00025127
2011 | 2011-03-15 | B | 214 | 0.22853 | 0.00067214
2011 | 2011-03-15 | B | 29 | 0.026323 | 9.1084e-05
2011 | 2011-03-15 | B | 14 | 0.021238 | 4.3972e-05
2011 | 2011-03-15 | C | 963 | 0.054443 | 0.0030246
2011 | 2011-03-04 | C | 250 | 0.081661 | 0.00078521
2011 | 2011-03-16 | B | 8 | 0.002588 | 2.5127e-05
2011 | 2011-03-16 | C | 2 | 0.0006847 | 6.2816e-06
2011 | 2011-03-16 | B | 15 | 0.018091 | 4.7112e-05
2011 | 2011-03-16 | B | 71 | 0.082063 | 0.000223
2011 | 2011-03-16 | B | 2 | 0.0017463 | 6.2816e-06
2011 | 2011-03-16 | B | 4 | 0.0022237 | 1.2563e-05
2011 | 2011-03-16 | C | 776.8127 | 0.80026 | 0.0060021
2011 | 2011-03-16 | B | 111 | 0.08402 | 0.00034863
2011 | 2011-03-17 | B | 1 | 0.00041459 | 3.1408e-06
2011 | 2011-03-17 | B | 1 | 0.00021044 | 3.1408e-06
2011 | 2011-03-17 | C | 133.2886 | 0.18587 | 0.0030654
2011 | 2011-03-17 | B | 257 | 0.21552 | 0.00080719
2011 | 2011-03-17 | B | 14 | 0.018336 | 4.3972e-05
2011 | 2011-03-17 | B | 80 | 0.085179 | 0.00025127
2011 | 2011-03-17 | B | 51 | 0.060389 | 0.00016018
2011 | 2011-03-17 | B | 113 | 0.12351 | 0.00035491
2011 | 2011-03-17 | B | 7 | 0.0052106 | 2.1986e-05
2011 | 2011-03-18 | B | 1 | 8.4802e-05 | 3.1408e-06
2011 | 2011-03-18 | B | 177 | 0.1451 | 0.00055593
2011 | 2011-03-18 | B | 95 | 0.037596 | 0.00029838
2011 | 2011-03-18 | B | 43 | 0.044703 | 0.00013506
2011 | 2011-03-18 | C | 19 | 0.0060869 | 5.9676e-05
2011 | 2011-03-18 | B | 32 | 0.018795 | 0.00010051
2011 | 2011-03-18 | B | 5 | 0.0029524 | 1.5704e-05
2011 | 2011-03-18 | B | 22 | 0.027086 | 6.9098e-05
2011 | 2011-03-18 | C | 58 | 0.008744 | 0.00018217
2011 | 2011-03-19 | C | 38 | 0.01647 | 0.00011935
2011 | 2011-03-18 | C | 269.7426 | 0.2279 | 0.00087943
2011 | 2011-03-18 | C | 63 | 0.019391 | 0.00019787
2011 | 2011-03-18 | C | 127.7338 | 0.054562 | 0.0012877
2011 | 2011-03-18 | B | 125.2358 | 0.1656 | 0.00049311
2011 | 2011-03-16 | B | 110.8037 | 0.036194 | 0.00038632
2011 | 2011-03-19 | C | 124.6821 | 0.066573 | 0.0007695
2011 | 2011-03-20 | B | 30 | 0.015076 | 9.4225e-05
2011 | 2011-03-20 | B | 350 | 0.51007 | 0.0010993
2011 | 2011-03-20 | B | 140 | 0.098056 | 0.00043972
2011 | 2011-03-20 | C | 65.0625 | 0.048431 | 0.00096737
2011 | 2011-03-21 | B | 224 | 0.20121 | 0.00070354
2011 | 2011-03-19 | B | 1 | 6.2816e-05 | 3.1408e-06
2011 | 2011-03-21 | B | 5 | 0.005575 | 1.5704e-05
2011 | 2011-03-21 | C | 162 | 0.016791 | 0.00050881
2011 | 2011-03-21 | C | 299 | 0.015965 | 0.00093911
2011 | 2011-03-21 | B | 1 | 0.00017903 | 3.1408e-06
2011 | 2011-03-21 | C | 110.5542 | 0.056599 | 0.00066271
2011 | 2011-03-22 | C | 870.8701 | 0.20241 | 0.0042747
2011 | 2011-03-21 | B | 27.5676 | 0.015758 | 0.00010051
2011 | 2011-03-22 | C | 21 | 0.0087064 | 6.5957e-05
2011 | 2011-03-20 | B | 20 | 0.012312 | 6.2816e-05
2011 | 2011-03-22 | C | 1 | 0.00017903 | 3.1408e-06
2011 | 2011-03-22 | C | 54 | 0.0083106 | 0.0001696
2011 | 2011-03-22 | B | 40 | 0.031534 | 0.00012563
2011 | 2011-03-22 | B | 250 | 0.26147 | 0.00078521
2011 | 2011-03-22 | B | 51 | 0.06199 | 0.00016018
2011 | 2011-03-22 | C | 55 | 0.0086373 | 0.00017275
2011 | 2011-03-22 | C | 39.3117 | 0.018644 | 0.00015704
2011 | 2011-03-23 | C | 391.9667 | 0.03324 | 0.001539
2011 | 2011-03-23 | B | 71 | 0.082955 | 0.000223
2011 | 2011-03-23 | B | 30 | 0.024216 | 9.4225e-05
2011 | 2011-03-23 | B | 2 | 0.0016772 | 6.2816e-06
2011 | 2011-03-23 | C | 90.0606 | 0.064493 | 0.0016238
2011 | 2011-03-23 | B | 40 | 0.046861 | 0.00012563
2011 | 2011-03-23 | B | 197.9897 | 0.23941 | 0.0017117
2011 | 2011-03-23 | B | 37 | 0.028704 | 0.00011621
2011 | 2011-03-24 | B | 8 | 0.0034675 | 2.5127e-05
2011 | 2011-03-24 | B | 49 | 0.045708 | 0.0001539
2011 | 2011-03-24 | C | 23 | 0.022466 | 7.2239e-05
2011 | 2011-03-24 | B | 51 | 0.057986 | 0.00016018
2011 | 2011-03-24 | C | 15 | 0.0014134 | 4.7112e-05
2011 | 2011-03-24 | B | 1 | 0.00056221 | 3.1408e-06
2011 | 2011-03-24 | B | 407 | 0.25183 | 0.0012783
2011 | 2011-03-24 | C | 2 | 0.00032036 | 6.2816e-06
2011 | 2011-03-23 | C | 107.1763 | 0.12118 | 0.0022017
2011 | 2011-03-24 | C | 90.3151 | 0.040564 | 0.00032036
2011 | 2011-03-25 | B | 148 | 0.047414 | 0.00046484
2011 | 2011-03-24 | B | 384.4459 | 0.17508 | 0.00125
2011 | 2011-03-25 | C | 98 | 0.055404 | 0.0003078
2011 | 2011-03-25 | B | 134 | 0.13805 | 0.00042087
2011 | 2011-03-25 | B | 58 | 0.032062 | 0.00018217
2011 | 2011-03-25 | C | 8 | 0.0044223 | 2.5127e-05
2011 | 2011-03-25 | C | 15 | 0.002497 | 4.7112e-05
2011 | 2011-03-25 | C | 179.6667 | 0.055866 | 0.0011338
2011 | 2011-03-26 | B | 2 | 0.00073495 | 6.2816e-06
2011 | 2011-03-26 | C | 34 | 0.0067276 | 0.00010679
2011 | 2011-03-26 | C | 15 | 0.0033921 | 4.7112e-05
2011 | 2011-03-26 | B | 163 | 0.11826 | 0.00051195
2011 | 2011-03-26 | C | 6 | 0.00015076 | 1.8845e-05
2011 | 2011-03-26 | C | 63.438 | 0.053996 | 0.00024498
2011 | 2011-03-27 | C | 96 | 0.011156 | 0.00030152
2011 | 2011-03-27 | C | 6 | 0.00028267 | 1.8845e-05
2011 | 2011-03-27 | C | 433 | 0.16592 | 0.00136
2011 | 2011-03-27 | C | 58.73 | 0.036339 | 0.00063131
2011 | 2011-03-27 | C | 4 | 0.0020101 | 1.2563e-05
2011 | 2011-03-27 | C | 470.9826 | 0.16568 | 0.0015955
2011 | 2011-03-28 | B | 20 | 0.0067842 | 6.2816e-05
2011 | 2011-03-28 | B | 19 | 0.0032822 | 5.9676e-05
2011 | 2011-03-28 | B | 8 | 0.0081159 | 2.5127e-05
2011 | 2011-03-28 | C | 4 | 0.00065329 | 1.2563e-05
2011 | 2011-03-28 | C | 90 | 0.01159 | 0.00028267
2011 | 2011-03-28 | B | 558 | 0.70804 | 0.0017526
2011 | 2011-03-28 | B | 71 | 0.077157 | 0.000223
2011 | 2011-03-28 | C | 3 | 0.0064732 | 9.4225e-06
2011 | 2011-03-28 | B | 101 | 0.16242 | 0.00031722
2011 | 2011-03-28 | C | 103 | 0.013911 | 0.0003235
2011 | 2011-03-28 | C | 478.2621 | 0.15021 | 0.0019819
2011 | 2011-03-29 | C | 71 | 0.00223 | 0.000223
2011 | 2011-03-29 | C | 63.1952 | 0.098051 | 0.00068156
2011 | 2011-03-29 | B | 8 | 0.006156 | 2.5127e-05
2011 | 2011-03-29 | B | 21 | 0.015236 | 6.5957e-05
2011 | 2011-03-29 | B | 1 | 0.0010742 | 3.1408e-06
2011 | 2011-03-29 | C | 9 | 0.00079149 | 2.8267e-05
2011 | 2011-03-29 | B | 163 | 0.18277 | 0.00051195
2011 | 2011-03-29 | B | 239 | 0.30477 | 0.00075066
2011 | 2011-03-29 | C | 60 | 0.00056535 | 0.00018845
2011 | 2011-03-29 | B | 595 | 0.66529 | 0.0018688
2011 | 2011-03-29 | B | 30 | 0.027325 | 9.4225e-05
2011 | 2011-03-29 | B | 87 | 0.10711 | 0.00027325
2011 | 2011-03-29 | B | 29.3422 | 0.027463 | 0.00022614
2011 | 2011-03-27 | B | 25.3125 | 0.037922 | 8.4802e-05
2011 | 2011-03-28 | B | 6 | 0.0010742 | 1.8845e-05
2011 | 2011-03-29 | B | 275 | 0.012956 | 0.00086373
2011 | 2011-03-30 | B | 1 | 0.00057163 | 3.1408e-06
2011 | 2011-03-30 | B | 2 | 0.0009234 | 6.2816e-06
2011 | 2011-03-30 | C | 934.4583 | 0.13207 | 0.0030026
2011 | 2011-03-29 | C | 58.0511 | 0.13857 | 0.0013757
2011 | 2011-03-30 | B | 94 | 0.090638 | 0.00029524
2011 | 2011-03-30 | B | 87 | 0.11395 | 0.00027325
2011 | 2011-03-30 | B | 35 | 0.01616 | 0.00010993
2011 | 2011-03-30 | B | 40 | 0.044725 | 0.00012563
2011 | 2011-03-29 | C | 263 | 0.0090864 | 0.00082604
2011 | 2011-03-30 | B | 1 | 0.0011213 | 3.1408e-06
2011 | 2011-03-30 | B | 26 | 0.02899 | 8.1661e-05
2011 | 2011-03-30 | C | 1 | 0.00012563 | 3.1408e-06
2011 | 2011-03-30 | C | 45.8301 | 0.066502 | 0.00066271
2011 | 2011-03-30 | C | 8 | 0.0018594 | 2.5127e-05
2011 | 2011-03-30 | B | 4 | 0.0020353 | 1.2563e-05
2011 | 2011-03-31 | C | 29 | 0.002186 | 9.1084e-05
2011 | 2011-03-31 | B | 205 | 0.1835 | 0.00064387
2011 | 2011-03-31 | B | 5 | 0.0052923 | 1.5704e-05
2011 | 2011-03-31 | B | 3 | 0.0030058 | 9.4225e-06
2011 | 2011-03-31 | B | 538 | 0.13518 | 0.0016898
2011 | 2011-03-31 | B | 14 | 0.0036936 | 0.0016898
2011 | 2011-03-31 | C | 6 | 0.0033921 | 1.8845e-05
2011 | 2011-03-31 | C | 204 | 0.08842 | 0.00064073
2011 | 2011-03-31 | C | 4 | 0.0018845 | 1.2563e-05
2011 | 2011-03-31 | C | 94 | 0.049895 | 0.0010773
2011 | 2011-03-31 | C | 937 | 0.18246 | 0.002943
2011 | 2011-03-31 | C | 20 | 0.0034549 | 6.2816e-05
2011 | 2011-03-31 | B | 30 | 0.032508 | 9.4225e-05
2011 | 2011-03-31 | C | 5 | 0.011621 | 1.5704e-05
2011 | 2011-03-31 | C | 1098.2598 | 0.42773 | 0.0073589
2011 | 2011-03-31 | C | 438 | 0.012381 | 0.0013757
2011 | 2011-03-31 | C | 599 | 0.0056441 | 0.0018814
2012 | 2011-04-01 | C | 105.8 | 0.0039677 | 0.00033126
2012 | 2011-04-01 | B | 9.9837 | 0.0056473 | 3.1251e-05
2012 | 2011-04-01 | B | 66.9901 | 0.062806 | 0.00020938
2012 | 2011-04-01 | B | 104.9913 | 0.11254 | 0.00032814
2012 | 2011-04-01 | B | 31.9483 | 0.0054913 | 0.0001
2012 | 2011-04-01 | B | 99.9919 | 0.11531 | 0.00031251
2012 | 2011-04-01 | C | 8.88 | 0.00061052 | 2.8126e-05
2012 | 2011-04-01 | B | 92.9805 | 0.043877 | 0.00029064
2012 | 2011-04-02 | C | 3.1816 | 0.0037484 | 5.3127e-05
2012 | 2011-04-02 | B | 3.9924 | 0.0048909 | 1.2501e-05
2012 | 2011-04-02 | C | 29.9625 | 0.00721 | 9.3754e-05
2012 | 2011-04-03 | C | 151.9732 | 0.051768 | 0.00047502
2012 | 2011-04-03 | B | 60.9898 | 0.055274 | 0.00019063
2012 | 2011-04-03 | B | 62.9897 | 0.056496 | 0.00019688
2012 | 2011-04-03 | B | 18.9913 | 0.020238 | 5.9377e-05
2012 | 2011-04-03 | C | 53.9906 | 0.053318 | 0.00016876
2012 | 2011-04-01 | C | 116.5926 | 0.028421 | 0.00037502
2012 | 2011-04-03 | C | 28.9434 | 0.0045226 | 9.0629e-05
2012 | 2011-04-04 | C | 850.4817 | 0.86381 | 0.0062034
2012 | 2011-04-04 | B | 100.9913 | 0.10794 | 0.00031564
2012 | 2011-04-04 | B | 11.9875 | 0.0088786 | 3.7502e-05
2012 | 2011-04-04 | B | 1.9833 | 0.0010971 | 6.2503e-06
2012 | 2011-04-04 | B | 20.9845 | 0.012526 | 6.5628e-05
2012 | 2011-04-05 | B | 15.9926 | 0.020092 | 5.0002e-05
2012 | 2011-04-04 | C | 105.9333 | 0.013904 | 0.00033126
2012 | 2011-04-04 | C | 1406.9559 | 0.2858 | 0.0043971
2012 | 2011-04-04 | C | 118.6026 | 0.056709 | 0.0006094
2012 | 2011-04-01 | B | 25.9916 | 0.028917 | 8.1253e-05
2012 | 2011-04-05 | C | 317.8235 | 0.013905 | 0.00099379
2012 | 2011-04-04 | B | 7.9905 | 0.007816 | 2.5001e-05
2012 | 2011-04-05 | C | 39.9634 | 0.0098664 | 0.00012501
2012 | 2011-04-05 | C | 1305.9412 | 0.1959 | 0.0040814
2012 | 2011-04-05 | C | 239.4822 | 0.14519 | 0.002247
2012 | 2011-04-05 | C | 12.9062 | 0.0011697 | 4.0627e-05
2012 | 2011-04-05 | C | 13.925 | 0.0016101 | 4.3752e-05
2012 | 2011-04-05 | C | 16.9286 | 0.0020633 | 5.3127e-05
2012 | 2011-04-06 | C | 5411.925 | 0.62578 | 0.017888
2012 | 2011-04-06 | C | 4.9268 | 0.00058508 | 1.5626e-05
2012 | 2011-04-06 | C | 37.8235 | 0.0016548 | 0.00011875
2012 | 2011-04-06 | B | 69.986 | 0.046368 | 0.00021876
2012 | 2011-04-06 | C | 33.99 | 0.031548 | 0.00010625
2012 | 2011-04-06 | B | 8.975 | 0.0032816 | 2.8126e-05
2012 | 2011-04-06 | C | 70.7 | 0.0015466 | 0.00022188
2012 | 2011-04-06 | C | 13.9434 | 0.0021787 | 4.3752e-05
2012 | 2011-04-06 | C | 1.9375 | 0.00027247 | 6.2503e-06
2012 | 2011-04-06 | B | 39.9918 | 0.045493 | 0.00012501
2012 | 2011-04-06 | C | 5.9674 | 0.0016597 | 1.8751e-05
2012 | 2011-04-06 | C | 72.5294 | 0.026293 | 0.00086254
2012 | 2011-04-07 | C | 6.9559 | 0.001413 | 2.1876e-05
2012 | 2011-04-07 | C | 34.9388 | 0.0050227 | 0.00010938
2012 | 2011-04-07 | C | 47.9062 | 0.0043417 | 0.00015001
2012 | 2011-04-07 | C | 30.976 | 0.01181 | 9.6879e-05
2012 | 2011-04-07 | B | 29.9877 | 0.022492 | 9.3754e-05
2012 | 2011-04-07 | C | 5.9722 | 0.0019597 | 1.8751e-05
2012 | 2011-04-07 | B | 20.9907 | 0.020926 | 6.5628e-05
2012 | 2011-04-07 | B | 248.991 | 0.25756 | 0.00077816
2012 | 2011-04-07 | C | 4.9118 | 0.00047585 | 1.5626e-05
2012 | 2011-04-07 | B | 15.9936 | 0.023342 | 5.0002e-05
2012 | 2011-04-07 | B | 52.9925 | 0.065415 | 0.00016563
2012 | 2011-04-07 | C | 83.4074 | 0.048483 | 0.00036564
2012 | 2011-04-07 | C | 5.625 | 8.7894e-05 | 1.8751e-05
2012 | 2011-04-08 | B | 86.9684 | 0.025004 | 0.00027189
2012 | 2011-04-08 | B | 98.9806 | 0.047018 | 0.00030939
2012 | 2011-04-08 | C | 21.9595 | 0.0048725 | 6.8753e-05
2012 | 2011-04-07 | C | 116.8421 | 0.0058423 | 0.00036564
2012 | 2011-04-08 | B | 93.925 | 0.010861 | 0.00029376
2012 | 2011-04-07 | B | 57.5982 | 0.099361 | 0.00029376
2012 | 2011-04-08 | B | 87.9891 | 0.074794 | 0.00027501
2012 | 2011-04-08 | C | 589.5053 | 0.34082 | 0.0036689
2012 | 2011-04-09 | C | 1547.2273 | 0.09187 | 0.0096879
2012 | 2011-04-09 | C | 107.2539 | 0.084801 | 0.0005969
2012 | 2011-04-09 | C | 591.403 | 0.11829 | 0.0029782
2012 | 2011-04-10 | C | 245.6499 | 0.28711 | 0.0042189
2012 | 2011-04-10 | C | 991.8125 | 0.040294 | 0.0031001
2012 | 2011-04-09 | C | 31.3875 | 0.086025 | 0.00059377
2012 | 2011-04-09 | C | 186.1277 | 0.080271 | 0.0012282
2012 | 2011-04-11 | C | 10.98 | 0.0050441 | 3.4376e-05
2012 | 2011-04-12 | B | 85.9922 | 0.10239 | 0.00026876
2012 | 2011-04-12 | B | 22.9905 | 0.022417 | 7.1878e-05
2012 | 2011-04-12 | B | 6.9854 | 0.0044097 | 2.1876e-05
2012 | 2011-04-12 | B | 107.9898 | 0.098207 | 0.00033751
2012 | 2011-04-12 | B | 5.925 | 0.00068511 | 1.8751e-05
2012 | 2011-04-12 | B | 248.9904 | 0.24122 | 0.00077816
2012 | 2011-04-12 | B | 19.992 | 0.023179 | 6.2503e-05
2012 | 2011-04-12 | C | 196.473 | 0.08903 | 0.0015282
2012 | 2011-04-12 | C | 23.88 | 0.035224 | 0.00016876
2012 | 2011-04-13 | C | 1.9167 | 0.00019766 | 6.2503e-06
2012 | 2011-04-13 | B | 108.9837 | 0.061646 | 0.00034064
2012 | 2011-04-13 | B | 40.9892 | 0.035227 | 0.00012813
2012 | 2011-04-13 | B | 20.9918 | 0.023682 | 6.5628e-05
2012 | 2011-04-13 | B | 28.2741 | 0.030042 | 0.00026564
2012 | 2011-04-13 | B | 7.9809 | 0.003841 | 2.5001e-05
2012 | 2011-04-13 | B | 39.9921 | 0.047368 | 0.00012501
2012 | 2011-04-13 | C | 156.8571 | 0.1152 | 0.0011063
2012 | 2011-04-14 | B | 19.9735 | 0.0068662 | 6.2503e-05
2012 | 2011-04-14 | B | 94.9914 | 0.10271 | 0.00029689
2012 | 2011-04-14 | B | 4.9474 | 0.0008349 | 1.5626e-05
2012 | 2011-04-14 | B | 38.9916 | 0.043014 | 0.00012188
2012 | 2011-04-13 | C | 229.51 | 0.17644 | 0.0037408
2012 | 2011-04-14 | C | 87.95 | 0.015667 | 0.00027501
2012 | 2011-04-14 | C | 179.4732 | 0.061136 | 0.0007344
2012 | 2011-04-15 | B | 113.8889 | 0.008542 | 0.00035626
2012 | 2011-04-15 | B | 30.9862 | 0.02082 | 9.6879e-05
2012 | 2011-04-15 | C | 183.8846 | 0.013217 | 0.00057502
2012 | 2011-04-16 | C | 1027 | 0.32737 | 0.0050033
2012 | 2011-04-16 | C | 116.8 | 0.0043802 | 0.00036564
2012 | 2011-04-16 | C | 91.8235 | 0.0040174 | 0.00028751
2012 | 2011-04-16 | C | 116.8333 | 0.0054768 | 0.00036564
2012 | 2011-04-16 | C | 145.7783 | 0.091115 | 0.0017469
2012 | 2011-04-16 | C | 1031.2222 | 0.048341 | 0.0034658
2012 | 2011-04-16 | C | 33.9189 | 0.003604 | 0.00010625
2012 | 2011-04-16 | C | 116.8696 | 0.0073046 | 0.00036564
2012 | 2011-04-17 | C | 67.5541 | 0.030612 | 0.00036564
2012 | 2011-04-17 | C | 59.9434 | 0.0093665 | 0.00036564
2012 | 2011-04-17 | C | 62.0544 | 0.045767 | 0.00028751
2012 | 2011-04-16 | C | 144.1708 | 0.18067 | 0.0011313
2012 | 2011-04-18 | C | 86.8 | 0.0032551 | 0.00027189
2012 | 2011-04-18 | C | 86.8 | 0.0032551 | 0.00027189
2012 | 2011-04-18 | C | 86.8 | 0.0032551 | 0.00027189
2012 | 2011-04-18 | B | 105.9773 | 0.042724 | 0.00033126
2012 | 2011-04-18 | C | 37.9795 | 0.016973 | 0.00011875
2012 | 2011-04-18 | C | 113.1678 | 0.049513 | 0.00063753
2012 | 2011-04-18 | C | 91.85 | 0.0048797 | 0.00028751
2012 | 2011-04-18 | C | 162.2819 | 0.093823 | 0.00087191
2012 | 2011-04-18 | C | 78.9 | 0.0066575 | 0.00024689
2012 | 2011-04-18 | C | 58.1321 | 0.050323 | 0.00020626
2012 | 2011-04-18 | C | 81.7667 | 0.029897 | 0.00055002
2012 | 2011-04-18 | B | 16.9927 | 0.021667 | 5.3127e-05
2012 | 2011-04-18 | C | 182.5253 | 0.21219 | 0.004072
2012 | 2011-04-18 | C | 183.6463 | 0.17677 | 0.0012688
2012 | 2011-04-18 | C | 312.2882 | 0.45088 | 0.0029282
2012 | 2011-04-19 | C | 65.875 | 0.0043232 | 0.00020626
2012 | 2011-04-19 | C | 469.9211 | 0.0514 | 0.0014688
2012 | 2011-04-19 | B | 44.9903 | 0.043024 | 0.00014063
2012 | 2011-04-19 | B | 248.9869 | 0.17585 | 0.00077816
2012 | 2011-04-19 | C | 35.2486 | 0.040427 | 0.00014688
2012 | 2011-04-19 | C | 935.7857 | 0.032169 | 0.0029251
2012 | 2011-04-19 | C | 19.625 | 0.00030665 | 6.2503e-05
2012 | 2011-04-19 | B | 45.9911 | 0.048149 | 0.00014376
2012 | 2011-04-19 | B | 1.9915 | 0.0021845 | 6.2503e-06
2012 | 2011-04-18 | B | 100.989 | 0.085213 | 0.00031564
2012 | 2011-04-19 | B | 229.9895 | 0.20341 | 0.00071878
2012 | 2011-04-19 | B | 38.992 | 0.045452 | 0.00012188
2012 | 2011-04-19 | B | 464.987 | 0.33132 | 0.0014532
2012 | 2011-04-17 | C | 1.1333 | 0.0046927 | 9.3754e-06
2012 | 2011-04-20 | C | 28.967 | 0.0079663 | 9.0629e-05
2012 | 2011-04-20 | C | 55.9508 | 0.010141 | 0.00017501
2012 | 2011-04-20 | B | 48.9818 | 0.024798 | 0.00015313
2012 | 2011-04-20 | B | 25.992 | 0.030379 | 8.1253e-05
2012 | 2011-04-20 | B | 13.9933 | 0.01946 | 4.3752e-05
2012 | 2011-04-20 | B | 26.9929 | 0.035176 | 8.4378e-05
2012 | 2011-04-20 | C | 1.9595 | 0.00043477 | 6.2503e-06
2012 | 2011-04-20 | C | 47.5 | 0.00044533 | 0.00015001
2012 | 2011-04-21 | C | 386.5671 | 0.1945 | 0.0014751
2012 | 2011-04-21 | C | 2803.5714 | 0.035046 | 0.0087629
2012 | 2011-04-21 | B | 32.9697 | 0.0098913 | 0.00010313
2012 | 2011-04-21 | B | 20.9908 | 0.021188 | 6.5628e-05
2012 | 2011-04-21 | B | 38.992 | 0.04533 | 0.00012188
2012 | 2011-04-21 | C | 18.9516 | 0.0034943 | 5.9377e-05
2012 | 2011-04-21 | C | 281.3455 | 0.094079 | 0.0011625
2012 | 2011-04-22 | C | 13.8235 | 0.0006048 | 4.3752e-05
2012 | 2011-04-22 | B | 100.9914 | 0.10952 | 0.00031564
2012 | 2011-04-22 | C | 5.7692 | 0.0001803 | 1.8751e-05
2012 | 2011-04-23 | C | 90.9941 | 0.047205 | 0.0006969
2012 | 2011-04-23 | C | 303.4783 | 0.084408 | 0.0034658
2012 | 2011-04-23 | C | 395.8904 | 0.086605 | 0.0016907
2012 | 2011-04-23 | C | 143.3516 | 0.039423 | 0.00053127
2012 | 2011-04-24 | C | 5.8571 | 0.00032948 | 1.8751e-05
2012 | 2011-04-25 | C | 3951.9583 | 0.85218 | 0.012351
2012 | 2011-04-25 | C | 143.9714 | 0.045893 | 0.00045002
2012 | 2011-04-25 | C | 193.7453 | 0.19073 | 0.0018282
2012 | 2011-04-25 | C | 81.88 | 0.0056295 | 0.00025626
2012 | 2011-04-25 | C | 5.967 | 0.001641 | 1.8751e-05
2012 | 2011-04-26 | C | 83.049 | 0.025694 | 0.00041564
2012 | 2011-04-21 | B | 2.975 | 0.0010878 | 9.3754e-06
2012 | 2011-04-26 | C | 78.9864 | 0.053565 | 0.00024689
2012 | 2011-04-26 | C | 1016.8889 | 0.07627 | 0.0031783
2012 | 2011-04-26 | C | 652.8478 | 0.08773 | 0.0020563
2012 | 2011-04-26 | C | 153.8462 | 0.06106 | 0.00073128
2012 | 2011-04-26 | C | 53.9231 | 0.0060666 | 0.00016876
2012 | 2011-04-26 | C | 96.3797 | 0.022891 | 0.00059065
2012 | 2011-04-26 | C | 46.8673 | 0.042622 | 0.00037502
2012 | 2011-04-26 | B | 5.9732 | 0.0020347 | 1.8751e-05
2012 | 2011-04-26 | C | 98.6071 | 0.076732 | 0.00074066
2012 | 2011-04-26 | C | 92.9846 | 0.055793 | 0.00029064
2012 | 2011-04-26 | C | 233.8889 | 0.017542 | 0.00073128
2012 | 2011-04-26 | C | 327.2584 | 0.087954 | 0.0019657
2012 | 2011-04-26 | C | 9.9559 | 0.0020224 | 3.1251e-05
2012 | 2011-04-26 | C | 38.8696 | 0.0024294 | 0.00012188
2012 | 2011-04-26 | C | 172.2747 | 0.047377 | 0.00078753
2012 | 2011-04-26 | C | 73.2985 | 0.045355 | 0.00034689
2012 | 2011-04-26 | C | 8.976 | 0.0034222 | 2.8126e-05
2012 | 2011-04-26 | C | 113.92 | 0.034533 | 0.0005094
2012 | 2011-04-26 | C | 26.566 | 0.028061 | 0.00016251
2012 | 2011-04-27 | C | 1193.8 | 0.044769 | 0.0037314
2012 | 2011-04-26 | C | 5.9885 | 0.0048472 | 1.8751e-05
2012 | 2011-04-26 | C | 239.9827 | 0.1275 | 0.00075003
2012 | 2011-04-26 | C | 67.3012 | 0.069197 | 0.00041252
2012 | 2011-04-26 | C | 675.9865 | 0.46265 | 0.0021126
2012 | 2011-04-26 | C | 22.9904 | 0.022129 | 7.1878e-05
2012 | 2011-04-26 | C | 795.8571 | 0.044769 | 0.0024876
2012 | 2011-04-26 | C | 238.8966 | 0.019411 | 0.00074691
2012 | 2011-04-26 | C | 149.9655 | 0.039368 | 0.00046877
2012 | 2011-04-26 | C | 25.8636 | 0.0015357 | 8.1253e-05
2012 | 2011-04-26 | C | 117.705 | 0.16222 | 0.0010157
2012 | 2011-04-26 | C | 342.8171 | 0.52389 | 0.0017469
2012 | 2011-04-26 | C | 71.2346 | 0.057213 | 0.00037814
2012 | 2011-04-26 | C | 253.5745 | 0.034868 | 0.00084691
2012 | 2011-04-26 | C | 29.6093 | 0.013695 | 0.00083753
2012 | 2011-04-26 | C | 28.9659 | 0.0076944 | 9.0629e-05
2012 | 2011-04-26 | C | 712.8889 | 0.053469 | 0.0022282
2012 | 2011-04-26 | C | 123.7414 | 0.043698 | 0.00062503
2012 | 2011-04-26 | C | 599.4648 | 0.12739 | 0.0045158
2012 | 2011-04-26 | C | 104.9885 | 0.084979 | 0.00032814
2012 | 2011-04-26 | C | 29.985 | 0.01846 | 9.3754e-05
2012 | 2011-04-26 | C | 465.8696 | 0.029118 | 0.0014563
2012 | 2011-04-26 | C | 152.9936 | 0.22137 | 0.00047814
2012 | 2011-04-26 | C | 71.502 | 0.33674 | 0.00071878
2012 | 2011-04-26 | C | 22.85 | 0.001214 | 7.1878e-05
2012 | 2011-04-26 | C | 30.9647 | 0.007935 | 9.6879e-05
2012 | 2011-04-26 | C | 24.9615 | 0.0058506 | 7.8128e-05
2012 | 2011-04-26 | C | 474.3817 | 0.2713 | 0.0023813
2012 | 2011-04-26 | C | 352.8493 | 0.99905 | 0.0012594
2012 | 2011-04-26 | C | 11.961 | 0.0027661 | 3.7502e-05
2012 | 2011-04-26 | C | 49.9333 | 0.006554 | 0.00015626
2012 | 2011-04-26 | C | 57.4917 | 0.12954 | 0.00023438
2012 | 2011-04-26 | C | 88.9965 | 0.23752 | 0.00027814
2012 | 2011-04-26 | C | 204.9091 | 0.019211 | 0.00064065
2012 | 2011-04-26 | C | 206.6748 | 0.20862 | 0.00065315
2012 | 2011-04-26 | C | 41.9595 | 0.0093101 | 0.00013126
2012 | 2011-04-27 | B | 526.9917 | 0.58795 | 0.0016469
2012 | 2011-04-27 | B | 26.9916 | 0.029776 | 8.4378e-05
2012 | 2011-04-26 | C | 200.8333 | 0.0094144 | 0.00062815
2012 | 2011-04-26 | C | 499.9515 | 0.60778 | 0.0020688
2012 | 2011-04-26 | C | 526.2741 | 0.31907 | 0.0020501
2012 | 2011-04-26 | C | 51.2312 | 0.03138 | 0.00038439
2012 | 2011-04-26 | C | 47.9709 | 0.014992 | 0.00015001
2012 | 2011-04-26 | C | 106.9889 | 0.089607 | 0.00033439
2012 | 2011-04-28 | B | 17.9902 | 0.016979 | 5.6252e-05
2012 | 2011-04-26 | C | 217.6278 | 0.36522 | 0.00073753
2012 | 2011-04-26 | C | 154.0282 | 0.066909 | 0.00074378
2012 | 2011-04-26 | C | 8.75 | 0.0002461 | 2.8126e-05
2012 | 2011-04-26 | C | 307.7216 | 0.48757 | 0.0027782
2012 | 2011-04-27 | C | 37.94 | 0.0055727 | 0.00011875
2012 | 2011-04-26 | C | 2.9388 | 0.00042247 | 9.3754e-06
2012 | 2011-04-26 | C | 10.9483 | 0.0018818 | 3.4376e-05
2012 | 2011-04-26 | C | 25.9091 | 0.0024291 | 8.1253e-05
2012 | 2011-04-26 | C | 52.9231 | 0.0059541 | 0.00016563
2012 | 2011-04-26 | C | 68.9641 | 0.23341 | 0.00096254
2012 | 2011-04-26 | C | 204.5493 | 0.82207 | 0.0010375
2012 | 2011-04-26 | C | 77.9286 | 0.0094979 | 0.00024376
2012 | 2011-04-26 | C | 91.6065 | 0.043515 | 0.00047189
2012 | 2011-04-26 | C | 110.3957 | 0.128 | 0.00056565
2012 | 2011-04-26 | C | 2.976 | 0.0011346 | 9.3754e-06
2012 | 2011-04-28 | B | 5.987 | 0.0042659 | 1.8751e-05
2012 | 2011-04-26 | C | 471.8 | 0.017693 | 0.0014751
2012 | 2011-04-26 | C | 29.1789 | 0.0083893 | 0.00017813
2012 | 2011-04-26 | C | 89.0716 | 0.092416 | 0.00060002
2012 | 2011-04-28 | C | 25.9375 | 0.0036476 | 8.1253e-05
2012 | 2011-04-26 | C | 1.9703 | 0.00060343 | 6.2503e-06
2012 | 2011-04-29 | C | 2.9333 | 0.00038502 | 9.3754e-06
2012 | 2011-04-28 | C | 42.8929 | 0.0033511 | 0.00013438
2012 | 2011-04-26 | C | 15.1999 | 0.072582 | 0.00079066
2012 | 2011-04-28 | C | 82.9444 | 0.01322 | 0.00025939
2012 | 2011-04-29 | C | 179.25 | 0.009523 | 0.00085316
2012 | 2011-04-26 | C | 8.9902 | 0.0085411 | 2.8126e-05
2012 | 2011-04-26 | C | 105.247 | 0.38647 | 0.00095629
2012 | 2011-04-27 | C | 38.9219 | 0.18817 | 0.0010657
2012 | 2011-04-26 | C | 12.9577 | 0.0027536 | 4.0627e-05
2012 | 2011-04-26 | C | 3.9681 | 0.0011285 | 1.2501e-05
2012 | 2011-04-26 | C | 290.5828 | 0.26063 | 0.0018063
2012 | 2011-04-26 | C | 192.6954 | 1.7163 | 0.0011094
2012 | 2011-04-26 | C | 77.8387 | 0.38532 | 0.00054065
2012 | 2011-04-26 | C | 1086.7692 | 0.033963 | 0.003397
2012 | 2011-04-26 | C | 34.9799 | 0.01596 | 0.00010938
2012 | 2011-04-26 | C | 31.9615 | 0.0074913 | 0.0001
2012 | 2011-04-29 | C | 9.9717 | 0.0032098 | 3.1251e-05
2012 | 2011-04-29 | C | 231.85 | 0.012318 | 0.00072503
2012 | 2011-04-26 | C | 5800.25 | 0.018127 | 0.018129
2012 | 2011-04-26 | C | 27.5055 | 0.17131 | 0.00024689
2012 | 2011-04-26 | C | 47.1794 | 0.2247 | 0.001897
2012 | 2011-04-26 | C | 2.9976 | 0.011813 | 9.3754e-06
2012 | 2011-04-29 | C | 2.985 | 0.0018377 | 9.3754e-06
2012 | 2011-04-29 | C | 27.4803 | 0.012796 | 0.00011875
2012 | 2011-04-26 | C | 17.9975 | 0.066256 | 5.6252e-05
2012 | 2011-04-29 | C | 3704.375 | 0.79879 | 0.013679
2012 | 2011-04-26 | C | 193.9756 | 0.072744 | 0.00060627
2012 | 2011-04-26 | C | 10.8125 | 0.00043928 | 3.4376e-05
2012 | 2011-04-26 | C | 15.9524 | 0.0029912 | 5.0002e-05
2012 | 2011-04-26 | C | 61.94 | 0.0090978 | 0.00019376
2012 | 2011-04-26 | C | 17.9643 | 0.0045474 | 5.6252e-05
2012 | 2011-04-26 | C | 32.94 | 0.0048383 | 0.00010313
2012 | 2011-04-29 | B | 38.9912 | 0.041064 | 0.00012188
2012 | 2011-04-26 | C | 2.9756 | 0.0011159 | 9.3754e-06
2012 | 2011-04-26 | C | 19.9655 | 0.0052412 | 6.2503e-05
2012 | 2011-04-29 | C | 1376.717 | 0.21512 | 0.0044189
2012 | 2011-04-30 | C | 36.9118 | 0.003576 | 0.00011563
2012 | 2011-04-30 | C | 418.9362 | 0.057606 | 0.0013094
2012 | 2011-04-30 | C | 796.9286 | 0.09713 | 0.0024907
2012 | 2011-04-30 | C | 461.521 | 0.16731 | 0.0030626
2012 | 2011-04-30 | B | 32.9892 | 0.028351 | 0.00010313
2012 | 2011-04-29 | C | 102.9545 | 0.02027 | 0.00032189
2012 | 2011-05-01 | C | 6.9434 | 0.0010849 | 2.1876e-05
2012 | 2011-05-01 | C | 41.88 | 0.0028794 | 0.00013126
2012 | 2011-05-01 | C | 18.9167 | 0.0019509 | 5.9377e-05
2012 | 2011-05-01 | C | 316.9706 | 0.098067 | 0.00099067
2012 | 2011-05-01 | C | 138.9739 | 0.048643 | 0.00043439
2012 | 2011-05-01 | C | 169.0098 | 0.05229 | 0.00097504
2012 | 2011-05-01 | C | 188.0116 | 0.048767 | 0.00098754
2012 | 2011-05-01 | C | 11.9595 | 0.0026536 | 3.7502e-05
2012 | 2011-05-01 | C | 89.1389 | 0.039278 | 0.00045002
2012 | 2011-05-02 | C | 1203.5349 | 0.15045 | 0.0039533
2012 | 2011-05-02 | C | 143.8125 | 0.0058426 | 0.00045002
2012 | 2011-05-01 | C | 189.3473 | 0.15326 | 0.00066878
2012 | 2011-04-29 | B | 8.9941 | 0.014307 | 2.8126e-05
2012 | 2011-04-26 | C | 271.2889 | 0.64603 | 0.0014469
2012 | 2011-05-02 | C | 128.1713 | 0.15782 | 0.0010844
2012 | 2011-05-02 | C | 131.2875 | 0.13293 | 0.00078441
2012 | 2011-05-02 | C | 159.6013 | 0.07731 | 0.00056565
2012 | 2011-05-02 | C | 35.9842 | 0.021029 | 0.0001125
2012 | 2011-05-01 | C | 10.9958 | 0.024604 | 3.4376e-05
2012 | 2011-05-02 | C | 132.022 | 0.036308 | 0.00066253
2012 | 2011-05-02 | C | 2.9691 | 0.0008722 | 9.3754e-06
2012 | 2011-05-02 | C | 72.5867 | 0.060794 | 0
2012 | 2011-05-02 | B | 38.9914 | 0.042283 | 0.00012188
2012 | 2011-05-02 | C | 524.9778 | 0.068906 | 0.0017219
2012 | 2011-05-02 | C | 4376.9524 | 0.82071 | 0.013679
2012 | 2011-05-02 | C | 7.9954 | 0.016066 | 2.5001e-05
2012 | 2011-05-02 | C | 7.9423 | 0.0012162 | 2.5001e-05
2012 | 2011-05-02 | C | 77.5331 | 0.072448 | 0.00024689
2012 | 2011-05-02 | C | 205.9464 | 0.034111 | 0.00064378
2012 | 2011-05-02 | C | 97.8669 | 0.093283 | 0.00046252
2012 | 2011-05-02 | C | 24.9739 | 0.0087412 | 7.8128e-05
2012 | 2011-05-02 | C | 74.912 | 0.028561 | 0.00035626
2012 | 2011-05-02 | C | 1.9949 | 0.0036783 | 6.2503e-06
2012 | 2011-05-02 | C | 214.9545 | 0.042321 | 0.0006719
2012 | 2011-05-02 | C | 73.9571 | 0.015485 | 0.00023126
2012 | 2011-05-02 | C | 1955.1915 | 0.55603 | 0.0078659
2012 | 2011-05-02 | C | 4376.9595 | 0.97118 | 0.013679
2012 | 2011-05-03 | C | 287.5706 | 0.15008 | 0.0013688
2012 | 2011-05-03 | C | 2326.9795 | 1.0399 | 0.0072722
2012 | 2011-05-02 | B | 19.9767 | 0.0078662 | 6.2503e-05
2012 | 2011-05-03 | B | 322.9907 | 0.32199 | 0.0010094
2012 | 2011-05-02 | C | 38.0694 | 0.12135 | 0.00092816
2012 | 2011-05-03 | C | 9.9694 | 0.0029598 | 3.1251e-05
2012 | 2011-05-03 | C | 27.7656 | 0.11931 | 0.00035001
2012 | 2011-05-03 | B | 6.9928 | 0.0090254 | 2.1876e-05
2012 | 2011-05-02 | B | 9.9895 | 0.0088036 | 3.1251e-05
2012 | 2011-05-03 | B | 47.9915 | 0.052193 | 0.00015001
2012 | 2011-05-03 | C | 11.9882 | 0.0094411 | 3.7502e-05
2012 | 2011-05-03 | C | 50.9333 | 0.0066853 | 0.00015938
2012 | 2011-05-03 | C | 38.2793 | 0.0579 | 0.0006594
2012 | 2011-05-03 | B | 73.9907 | 0.073531 | 0.00023126
2012 | 2011-05-03 | C | 31.9412 | 0.0047914 | 0.0001
2012 | 2011-05-03 | C | 214.9483 | 0.036946 | 0.0006719
2012 | 2011-05-04 | B | 40.992 | 0.047527 | 0.00012813
2012 | 2011-05-04 | B | 85.9912 | 0.090832 | 0.00026876
2012 | 2011-05-04 | B | 223.9889 | 0.1869 | 0.00070003
2012 | 2011-05-04 | B | 75.9913 | 0.080981 | 0.00023751
2012 | 2011-05-04 | B | 8.9852 | 0.005616 | 2.8126e-05
2012 | 2011-05-04 | C | 10.8929 | 0.00085104 | 3.4376e-05
2012 | 2011-05-04 | B | 21.2353 | 0.025749 | 0.00024376
2012 | 2011-05-04 | C | 13.9118 | 0.0013478 | 4.3752e-05
2012 | 2011-05-04 | C | 2.9655 | 0.00077848 | 9.3754e-06
2012 | 2011-05-04 | C | 3.9853 | 0.0025034 | 1.2501e-05
2012 | 2011-05-04 | C | 5.9388 | 0.00085373 | 1.8751e-05
2012 | 2011-05-04 | C | 865.4348 | 0.1785 | 0.0039564
2012 | 2011-05-05 | C | 1153.2222 | 0.21624 | 0.0040502
2012 | 2011-05-05 | B | 25.986 | 0.017216 | 8.1253e-05
2012 | 2011-05-05 | B | 47.9922 | 0.057443 | 0.00015001
2012 | 2011-05-05 | B | 14.9911 | 0.015694 | 4.6877e-05
2012 | 2011-05-05 | B | 132.9924 | 0.16375 | 0.00041564
2012 | 2011-05-05 | B | 36.9889 | 0.030979 | 0.00011563
2012 | 2011-05-05 | B | 47.9915 | 0.052493 | 0.00015001
2012 | 2011-05-05 | B | 228.9831 | 0.12523 | 0.00071565
2012 | 2011-05-06 | B | 99.9875 | 0.074056 | 0.00031251
2012 | 2011-05-06 | B | 8.988 | 0.0069098 | 2.8126e-05
2012 | 2011-05-06 | B | 1.9922 | 0.0023783 | 6.2503e-06
2012 | 2011-05-06 | B | 10.9913 | 0.011747 | 3.4376e-05
2012 | 2011-05-06 | B | 1.9862 | 0.0013283 | 6.2503e-06
2012 | 2011-05-06 | C | 68.6609 | 0.024032 | 0.00045002
2012 | 2011-05-06 | C | 1308.9388 | 0.18817 | 0.0040908
2012 | 2011-05-06 | B | 110.7751 | 0.11286 | 0.00040627
2012 | 2011-05-07 | C | 690.9231 | 0.077732 | 0.0021595
2012 | 2011-05-07 | C | 81.9684 | 0.023567 | 0.00025626
2012 | 2011-05-07 | B | 4.9896 | 0.004444 | 1.5626e-05
2012 | 2011-05-07 | C | 792.9454 | 0.44605 | 0.0034064
2012 | 2011-05-07 | C | 3161.5585 | 1.8279 | 0.0099848
2012 | 2011-05-07 | C | 158.9688 | 0.046202 | 0.0004969
2012 | 2011-05-07 | C | 5.1833 | 0.00092332 | 1.8751e-05
2012 | 2011-05-07 | C | 2836.2079 | 0.86862 | 0.0092785
2012 | 2011-05-07 | C | 934.9552 | 0.187 | 0.002922
2012 | 2011-05-08 | C | 323.9559 | 0.065806 | 0.0010125
2012 | 2011-05-08 | C | 4.9779 | 0.002069 | 1.5626e-05
2012 | 2011-05-08 | C | 5.8235 | 0.00025479 | 1.8751e-05
2012 | 2011-05-08 | B | 108.9492 | 0.019067 | 0.00034064
2012 | 2011-05-08 | C | 146.987 | 0.10427 | 0.00045939
2012 | 2011-05-08 | C | 25.9881 | 0.020304 | 8.1253e-05
2012 | 2011-05-08 | C | 24.9492 | 0.0043663 | 7.8128e-05
2012 | 2011-05-08 | C | 201.6443 | 0.092004 | 0.0034626
2012 | 2011-05-08 | C | 1062.8929 | 0.083042 | 0.003322
2012 | 2011-05-08 | C | 211.8833 | 0.28738 | 0.0011844
2012 | 2011-05-08 | B | 73.9875 | 0.054799 | 0.00023126
2012 | 2011-05-08 | C | 8.9 | 0.00075097 | 2.8126e-05
2012 | 2011-05-08 | C | 198.5757 | 0.20727 | 0.00082191
2012 | 2011-05-08 | C | 1401.9412 | 0.2103 | 0.0043814
2012 | 2011-05-08 | C | 1.9674 | 0.0005472 | 6.2503e-06
2012 | 2011-05-08 | C | 11.9831 | 0.006516 | 3.7502e-05
2012 | 2011-05-08 | B | 37.9862 | 0.025404 | 0.00011875
2012 | 2011-05-09 | B | 1.9887 | 0.0016283 | 6.2503e-06
2012 | 2011-05-09 | B | 101.9896 | 0.090838 | 0.00031876
2012 | 2011-05-09 | B | 76.3861 | 0.11244 | 0.00051565
2012 | 2011-05-09 | B | 21.99 | 0.02041 | 6.8753e-05
2012 | 2011-05-09 | C | 97.9667 | 0.026636 | 0.00030626
2012 | 2011-05-09 | C | 96.8696 | 0.0060546 | 0.00030314
2012 | 2011-05-09 | C | 105.963 | 0.016889 | 0.0006344
2012 | 2011-05-10 | B | 73.9814 | 0.03653 | 0.00023126
2012 | 2011-05-10 | B | 30.9871 | 0.022176 | 9.6879e-05
2012 | 2011-05-10 | B | 47.9926 | 0.059993 | 0.00015001
2012 | 2011-05-10 | B | 24.9913 | 0.026632 | 7.8128e-05
2012 | 2011-05-10 | B | 53.9921 | 0.063275 | 0.00016876
2012 | 2011-05-10 | B | 3.7146 | 0.005781 | 9.3754e-05
2012 | 2011-05-10 | B | 105.0473 | 0.14477 | 0.00041564
2012 | 2011-05-10 | C | 11.9434 | 0.0018662 | 3.7502e-05
2012 | 2011-05-11 | C | 15.9677 | 0.0044911 | 5.0002e-05
2012 | 2011-05-11 | C | 140.1254 | 0.12787 | 0.00094379
2012 | 2011-05-11 | C | 191.4615 | 0.11488 | 0.0012938
2012 | 2011-05-11 | B | 7.9866 | 0.005516 | 2.5001e-05
2012 | 2011-05-11 | B | 40.9917 | 0.045733 | 0.00012813
2012 | 2011-05-11 | B | 212.9545 | 0.041927 | 0.00066565
2012 | 2011-05-11 | B | 13.9674 | 0.0038848 | 4.3752e-05
2012 | 2011-05-11 | C | 1.925 | 0.00022259 | 6.2503e-06
2012 | 2011-05-11 | C | 148.8462 | 0.089311 | 0.00080316
2012 | 2011-05-11 | C | 44.9715 | 0.039071 | 0.00025626
2012 | 2011-05-11 | C | 176.02 | 0.053358 | 0.00091566
2012 | 2011-05-11 | C | 1119.8 | 0.041994 | 0.0035001
2012 | 2011-05-11 | C | 1119.8 | 0.041994 | 0.0035001
2012 | 2011-05-11 | C | 80.6443 | 0.048137 | 0.00042502
2012 | 2011-05-12 | C | 81.8 | 0.0030676 | 0.00025626
2012 | 2011-05-12 | C | 46.2054 | 0.042453 | 0.00022501
2012 | 2011-05-12 | C | 82.0186 | 0.040498 | 0.00048752
2012 | 2011-05-12 | C | 48.925 | 0.0056572 | 0.00015313
2012 | 2011-05-12 | C | 61.9423 | 0.0094853 | 0.00019376
2012 | 2011-05-12 | C | 1.9639 | 0.00049098 | 6.2503e-06
2012 | 2011-05-12 | C | 612.4 | 0.0038277 | 0.0019157
2012 | 2011-05-12 | C | 235.4 | 0.0014713 | 0.00073753
2012 | 2011-05-12 | B | 15.9918 | 0.018091 | 5.0002e-05
2012 | 2011-05-12 | B | 132.9919 | 0.15336 | 0.00041564
2012 | 2011-05-12 | B | 5.993 | 0.0079598 | 1.8751e-05
2012 | 2011-05-12 | B | 19.9928 | 0.025992 | 6.2503e-05
2012 | 2011-05-12 | B | 28.9917 | 0.032345 | 9.0629e-05
2012 | 2011-05-12 | C | 21.7857 | 0.00074891 | 6.8753e-05
2012 | 2011-05-11 | C | 1226.4821 | 0.63243 | 0.0041533
2012 | 2011-05-12 | C | 104.4428 | 0.064627 | 0.00115
2012 | 2011-05-13 | C | 44.9559 | 0.009132 | 0.00014063
2012 | 2011-05-13 | B | 24.9893 | 0.02171 | 7.8128e-05
2012 | 2011-05-13 | B | 126.9911 | 0.13295 | 0.00039689
2012 | 2011-05-13 | B | 26.992 | 0.031379 | 8.4378e-05
2012 | 2011-05-17 | B | 4.9895 | 0.0044128 | 1.5626e-05
2012 | 2011-05-13 | B | 4.9797 | 0.0022565 | 1.5626e-05
2012 | 2011-05-13 | C | 81.9268 | 0.0097292 | 0.00025626
2012 | 2011-05-13 | C | 2.99 | 0.0027658 | 9.3754e-06
2012 | 2011-05-13 | C | 84.8966 | 0.0068981 | 0.00026564
2012 | 2011-05-14 | C | 268.9709 | 0.084057 | 0.00084066
2012 | 2011-05-14 | C | 72.4954 | 0.024015 | 0.00034376
2012 | 2011-05-14 | C | 5.8235 | 0.00025479 | 1.8751e-05
2012 | 2011-05-14 | C | 24.9455 | 0.0040538 | 7.8128e-05
2012 | 2011-05-15 | C | 165.9647 | 0.04253 | 0.00051877
2012 | 2011-05-14 | C | 5.9 | 0.00049783 | 1.8751e-05
2012 | 2011-05-15 | B | 52.9879 | 0.040405 | 0.00016563
2012 | 2011-05-15 | C | 81.9571 | 0.01716 | 0.00025626
2012 | 2011-05-15 | C | 24.9639 | 0.0062412 | 7.8128e-05
2012 | 2011-05-15 | C | 81.7692 | 0.0025554 | 0.00025626
2012 | 2011-05-15 | C | 81.8125 | 0.0033238 | 0.00025626
2012 | 2011-05-15 | C | 2.9634 | 0.00073162 | 9.3754e-06
2012 | 2011-05-15 | C | 81.9746 | 0.029461 | 0.00025626
2012 | 2011-05-15 | C | 662.9739 | 0.23205 | 0.002072
2012 | 2011-05-15 | C | 175.3571 | 0.19783 | 0.00071565
2012 | 2011-05-14 | B | 224.9921 | 0.26578 | 0.00070315
2012 | 2011-05-13 | B | 28.9895 | 0.025639 | 9.0629e-05
2012 | 2011-05-16 | C | 348.88 | 0.023986 | 0.0010907
2012 | 2011-05-16 | C | 110.9483 | 0.01907 | 0.00034689
2012 | 2011-05-16 | C | 6.95 | 0.001238 | 2.1876e-05
2012 | 2011-05-16 | C | 3.9939 | 0.0060659 | 1.2501e-05
2012 | 2011-05-16 | C | 160.8929 | 0.01257 | 0.00050315
2012 | 2011-05-16 | C | 44.9842 | 0.026289 | 0.00014063
2012 | 2011-05-16 | C | 680.963 | 0.16599 | 0.0021282
2012 | 2011-05-17 | C | 109.9143 | 0.010992 | 0.00034376
2012 | 2011-05-17 | C | 124.8929 | 0.0097577 | 0.00039064
2012 | 2011-05-16 | C | 53.9474 | 0.009104 | 0.00016876
2012 | 2011-05-16 | C | 210.8 | 0.0079053 | 0.0006594
2012 | 2011-05-16 | C | 34.5522 | 0.0069107 | 0.00029064
2012 | 2011-05-16 | C | 76.5657 | 0.10121 | 0.0006594
2012 | 2011-05-16 | C | 2.9899 | 0.0027377 | 9.3754e-06
2012 | 2011-05-16 | C | 149.8706 | 0.13255 | 0.0013438
2012 | 2011-05-17 | C | 187.7666 | 0.16665 | 0.0007094
2012 | 2011-05-16 | C | 42.9835 | 0.024045 | 0.00013438
2012 | 2011-05-16 | C | 248.1552 | 0.042653 | 0.0010563
2012 | 2011-05-16 | C | 4.97 | 0.0015066 | 1.5626e-05
2012 | 2011-05-17 | C | 7.8966 | 0.00064162 | 2.5001e-05
2012 | 2011-05-16 | C | 484.9577 | 0.10306 | 0.0015157
2012 | 2011-05-17 | C | 210.9559 | 0.042852 | 0.0006594
2012 | 2011-05-17 | C | 42.9565 | 0.0088601 | 0.00013438
2012 | 2011-05-17 | C | 109.8 | 0.0041177 | 0.00034376
2012 | 2011-05-17 | C | 742.8 | 0.027856 | 0.002322
2012 | 2011-05-17 | C | 100.4182 | 0.068099 | 0.00034064
2012 | 2011-05-17 | C | 64.4329 | 0.072893 | 0.00034376
2012 | 2011-05-17 | C | 207.8571 | 0.011692 | 0.00065003
2012 | 2011-05-17 | B | 5.9903 | 0.0057097 | 1.8751e-05
2012 | 2011-05-17 | C | 48.8408 | 0.043653 | 0.0024376
2012 | 2011-05-17 | B | 19.9917 | 0.022492 | 6.2503e-05
2012 | 2011-05-17 | C | 142.1327 | 0.042197 | 0.0005844
2012 | 2011-05-17 | C | 221.2159 | 0.18044 | 0.00095316
2012 | 2011-05-17 | B | 266.991 | 0.27535 | 0.00083441
2012 | 2011-05-17 | B | 123.9907 | 0.12361 | 0.00038752
2012 | 2011-05-17 | C | 210.9483 | 0.036258 | 0.0006594
2012 | 2011-05-17 | C | 67.6923 | 0.065368 | 0.0004969
2012 | 2011-05-17 | C | 137.2689 | 0.049762 | 0.0005719
2012 | 2011-05-17 | C | 80.0741 | 0.16141 | 0.00033751
2012 | 2011-05-17 | C | 80.9914 | 0.087576 | 0.00025314
2012 | 2011-05-17 | C | 63.5475 | 0.043294 | 0.00029689
2012 | 2011-05-17 | C | 141.8846 | 0.010198 | 0.00044377
2012 | 2011-05-17 | C | 261.7172 | 0.15949 | 0.0011469
2012 | 2011-05-17 | C | 41.925 | 0.0048478 | 0.00013126
2012 | 2011-05-17 | C | 114.6027 | 0.23423 | 0.00035939
2012 | 2011-05-18 | C | 163.7429 | 0.14175 | 0.00072503
2012 | 2011-05-17 | C | 512.5567 | 0.15057 | 0.0024376
2012 | 2011-05-17 | C | 401.8824 | 0.10299 | 0.0023782
2012 | 2011-05-18 | C | 291.9423 | 0.044705 | 0.00091254
2012 | 2011-05-18 | C | 241.649 | 0.11177 | 0.0014188
2012 | 2011-05-17 | C | 80.9136 | 0.23643 | 0.00038439
2012 | 2011-05-18 | B | 5.9851 | 0.0037222 | 1.8751e-05
2012 | 2011-05-18 | C | 4.95 | 0.00088175 | 1.5626e-05
2012 | 2011-05-18 | B | 91.9906 | 0.091132 | 0.00028751
2012 | 2011-05-18 | C | 125.1856 | 0.036775 | 0.00086879
2012 | 2011-05-17 | C | 23.3098 | 0.1961 | 0.00042189
2012 | 2011-05-18 | B | 336.9902 | 0.32015 | 0.0010532
2012 | 2011-05-18 | C | 5.75 | 0.00016173 | 1.8751e-05
2012 | 2011-05-18 | C | 24.3182 | 0.0064598 | 0.00014063
2012 | 2011-05-19 | C | 56.018 | 0.13585 | 0.00054065
2012 | 2011-05-18 | C | 48.6142 | 0.059403 | 0.00040939
2012 | 2011-05-18 | B | 18.985 | 0.011688 | 5.9377e-05
2012 | 2011-05-19 | B | 19.9913 | 0.021367 | 6.2503e-05
2012 | 2011-05-19 | B | 120.9912 | 0.12742 | 0.00037814
2012 | 2011-05-19 | C | 35.9625 | 0.0086538 | 0.0001125
2012 | 2011-05-19 | B | 24.99 | 0.023117 | 7.8128e-05
2012 | 2011-05-19 | B | 19.9929 | 0.026054 | 6.2503e-05
2012 | 2011-05-20 | B | 28.9915 | 0.031892 | 9.0629e-05
2012 | 2011-05-20 | B | 26.9932 | 0.036864 | 8.4378e-05
2012 | 2011-05-19 | B | 123.9943 | 0.20227 | 0.00038752
2012 | 2011-05-21 | C | 150.2944 | 0.083135 | 0.00095629
2012 | 2011-05-21 | C | 3.9189 | 0.0004164 | 1.2501e-05
2012 | 2011-05-21 | C | 3.992 | 0.0046659 | 1.2501e-05
2012 | 2011-05-21 | C | 9.9483 | 0.0017099 | 3.1251e-05
2012 | 2011-05-22 | C | 188.9605 | 0.043108 | 0.00059065
2012 | 2011-05-22 | C | 129.7399 | 0.13907 | 0.0010719
2012 | 2011-05-22 | C | 46.9521 | 0.024064 | 0.00016251
2012 | 2011-05-22 | B | 4.9938 | 0.0075379 | 1.5626e-05
2012 | 2011-05-22 | C | 269.8 | 0.010118 | 0.00084378
2012 | 2011-05-22 | C | 464.7654 | 0.11329 | 0.0024814
2012 | 2011-05-22 | C | 228.85 | 0.012158 | 0.00071565
2012 | 2011-05-23 | C | 35.9538 | 0.0069663 | 0.0001125
2012 | 2011-05-23 | C | 2527.4 | 0.015797 | 0.0079003
2012 | 2011-05-23 | B | 52.98 | 0.024339 | 0.00016563
2012 | 2011-05-23 | B | 334.9932 | 0.45749 | 0.0010469
2012 | 2011-05-23 | B | 99.992 | 0.11562 | 0.00031251
2012 | 2011-05-23 | B | 24.9903 | 0.023976 | 7.8128e-05
2012 | 2011-05-23 | B | 59.9891 | 0.050993 | 0.00018751
2012 | 2011-05-23 | B | 4.9926 | 0.0063035 | 1.5626e-05
2012 | 2011-05-23 | C | 144.9302 | 0.018117 | 0.00045314
2012 | 2011-05-23 | C | 33.9455 | 0.0055164 | 0.00010625
2012 | 2011-05-23 | C | 356.732 | 0.10479 | 0.0023626
2012 | 2011-05-23 | B | 105.9 | 0.0089357 | 0.00033126
2012 | 2011-05-24 | B | 19.9888 | 0.016554 | 6.2503e-05
2012 | 2011-05-24 | C | 406.8235 | 0.017799 | 0.0012719
2012 | 2011-05-24 | B | 196.9913 | 0.20993 | 0.00061565
2012 | 2011-05-24 | B | 231.994 | 0.36106 | 0.00072503
2012 | 2011-05-25 | C | 56.9318 | 0.0072947 | 0.00017813
2012 | 2011-05-24 | C | 222.9474 | 0.037624 | 0.0006969
2012 | 2011-05-25 | B | 334.9919 | 0.3863 | 0.0010469
2012 | 2011-05-25 | C | 166.9302 | 0.020867 | 0.0005219
2012 | 2011-05-25 | C | 94.8571 | 0.0053359 | 0.00029689
2012 | 2011-05-25 | B | 29.9852 | 0.018742 | 9.3754e-05
2012 | 2011-05-25 | C | 1.963 | 0.00047849 | 6.2503e-06
2012 | 2011-05-26 | C | 506.9516 | 0.093473 | 0.0015844
2012 | 2011-05-26 | C | 818.9667 | 0.22267 | 0.0025595
2012 | 2011-05-26 | C | 1120.85 | 0.059548 | 0.0035033
2012 | 2011-05-26 | C | 30.6648 | 0.016579 | 0.00014063
2012 | 2011-05-26 | C | 80.2277 | 0.049894 | 0.00045002
2012 | 2011-05-26 | B | 20.9906 | 0.020795 | 6.5628e-05
2012 | 2011-05-26 | B | 2.9917 | 0.0033377 | 9.3754e-06
2012 | 2011-05-26 | C | 135.6897 | 0.134 | 0.0011313
2012 | 2011-05-26 | C | 76.5304 | 0.054291 | 0.00038439
2012 | 2011-05-26 | C | 28.8571 | 0.0016233 | 9.0629e-05
2012 | 2011-05-26 | C | 31.9963 | 0.079894 | 0.0001
2012 | 2011-05-26 | C | 561.9028 | 0.6269 | 0.0050252
2012 | 2011-05-26 | C | 7211.631 | 1.8255 | 0.024601
2012 | 2011-05-26 | C | 835.963 | 0.20377 | 0.0026126
2012 | 2011-05-26 | B | 17.9844 | 0.010622 | 5.6252e-05
2012 | 2011-05-27 | C | 733.4 | 0.0045839 | 0.0022938
2012 | 2011-05-27 | C | 182.9735 | 0.0629 | 0.0005719
2012 | 2011-05-27 | C | 19.9773 | 0.0080537 | 6.2503e-05
2012 | 2011-05-27 | C | 204.8125 | 0.0083208 | 0.00064065
2012 | 2011-05-26 | C | 30.658 | 0.10309 | 0.00079066
2012 | 2011-05-27 | C | 86.9545 | 0.01712 | 0.00027189
2012 | 2011-05-27 | C | 62.8421 | 0.0031422 | 0.00019688
2012 | 2011-05-27 | B | 19.9909 | 0.020429 | 6.2503e-05
2012 | 2011-05-26 | C | 41.1336 | 0.12083 | 0.00037502
2012 | 2011-05-27 | C | 75.9845 | 0.045118 | 0.00023751
2012 | 2011-05-27 | C | 15.9776 | 0.0065411 | 5.0002e-05
2012 | 2011-05-27 | B | 92.9559 | 0.018882 | 0.00029064
2012 | 2011-05-28 | C | 23.9483 | 0.0041163 | 7.5003e-05
2012 | 2011-05-28 | C | 59.9891 | 0.050993 | 0.00018751
2012 | 2011-05-28 | C | 755.9434 | 0.11812 | 0.0023626
2012 | 2011-05-28 | B | 53.9211 | 0.0058979 | 0.00016876
2012 | 2011-05-27 | B | 35.9914 | 0.038917 | 0.0001125
2012 | 2011-05-28 | B | 1.9901 | 0.0018595 | 6.2503e-06
2012 | 2011-05-26 | C | 8.9962 | 0.022351 | 2.8126e-05
2012 | 2011-05-28 | C | 137.9667 | 0.037511 | 0.00091254
2012 | 2011-05-28 | C | 5.8421 | 0.00029212 | 1.8751e-05
2012 | 2011-05-29 | C | 8.9688 | 0.0026066 | 2.8126e-05
2012 | 2011-05-29 | C | 12.9663 | 0.0034848 | 4.0627e-05
2012 | 2011-05-30 | B | 231.9906 | 0.22983 | 0.00072503
2012 | 2011-05-29 | C | 178.5294 | 0.1406 | 0.00077503
2012 | 2011-05-30 | C | 79.9189 | 0.0084917 | 0.00025001
2012 | 2011-05-30 | C | 118.731 | 0.071984 | 0.00077503
2012 | 2011-05-30 | C | 13.9647 | 0.0035786 | 4.3752e-05
2012 | 2011-05-30 | B | 86.6075 | 0.08607 | 0.00030001
2012 | 2011-05-31 | B | 776.9797 | 0.35208 | 0.0024282
2012 | 2011-05-27 | B | 71.9915 | 0.079194 | 0.00022501
2012 | 2011-05-31 | B | 12.9872 | 0.0094161 | 4.0627e-05
2012 | 2011-05-31 | B | 19.9906 | 0.019804 | 6.2503e-05
2012 | 2011-05-31 | B | 28.9901 | 0.02727 | 9.0629e-05
2012 | 2011-05-31 | B | 95.9908 | 0.096895 | 0.00030001
2012 | 2011-05-31 | C | 696.8125 | 0.028309 | 0.0021782
2012 | 2011-06-01 | B | 38.9914 | 0.041917 | 0.00012188
2012 | 2011-06-01 | B | 88.989 | 0.074809 | 0.00027814
2012 | 2011-06-01 | B | 12.9918 | 0.014657 | 4.0627e-05
2012 | 2011-06-01 | B | 74.9898 | 0.067962 | 0.00023438
2012 | 2011-06-01 | B | 14.9883 | 0.011851 | 4.6877e-05
2012 | 2011-06-01 | B | 5.9915 | 0.006516 | 1.8751e-05
2012 | 2011-06-01 | C | 5.9559 | 0.0012098 | 1.8751e-05
2012 | 2011-06-01 | C | 143.4208 | 0.080677 | 0.00086566
2012 | 2011-06-01 | B | 27.9277 | 0.02147 | 0.00029064
2012 | 2011-06-02 | C | 18.9615 | 0.0044443 | 5.9377e-05
2012 | 2011-06-02 | C | 25.9348 | 0.0034851 | 8.1253e-05
2012 | 2011-06-02 | B | 51.9647 | 0.013316 | 0.00016251
2012 | 2011-06-02 | B | 108.9882 | 0.085832 | 0.00034064
2012 | 2011-06-02 | B | 7.9893 | 0.006941 | 2.5001e-05
2012 | 2011-06-02 | B | 20.991 | 0.021713 | 6.5628e-05
2012 | 2011-06-02 | B | 19.9903 | 0.019054 | 6.2503e-05
2012 | 2011-06-02 | B | 24.9913 | 0.026554 | 7.8128e-05
2012 | 2011-06-02 | C | 37.2692 | 0.020848 | 0.00012813
2012 | 2011-06-02 | C | 144.5845 | 0.062806 | 0.00075316
2012 | 2011-06-03 | B | 30.9909 | 0.03167 | 9.6879e-05
2012 | 2011-06-03 | B | 79.992 | 0.092994 | 0.00025001
2012 | 2011-06-03 | C | 4.3063 | 0.0094069 | 2.1876e-05
2012 | 2011-06-03 | C | 62.2635 | 0.053315 | 0.00082503
2012 | 2011-06-03 | C | 23.9062 | 0.10415 | 0.00085316
2012 | 2011-06-04 | C | 126.9348 | 0.017058 | 0.00039689
2012 | 2011-06-04 | C | 119.2337 | 0.067444 | 0.0007219
2012 | 2011-06-04 | C | 576.241 | 0.49523 | 0.0049846
2012 | 2011-06-04 | C | 204.1267 | 0.093774 | 0.0010594
2012 | 2011-06-04 | C | 456.875 | 0.029984 | 0.0014282
2012 | 2011-06-04 | C | 92.3478 | 0.032323 | 0.00077191
2012 | 2011-06-04 | C | 154.9847 | 0.093479 | 0.00048439
2012 | 2011-06-04 | C | 90.9952 | 0.17659 | 0.00028439
2012 | 2011-06-05 | C | 20.9727 | 0.007013 | 6.5628e-05
2012 | 2011-06-05 | C | 372.9189 | 0.039624 | 0.0011657
2012 | 2011-06-05 | C | 90.7281 | 0.031473 | 0.00049064
2012 | 2011-06-05 | C | 289.9273 | 0.047115 | 0.0011563
2012 | 2011-06-05 | C | 362.7 | 0.0079344 | 0.0011344
2012 | 2011-06-06 | C | 248.2821 | 0.088454 | 0.0027376
2012 | 2011-06-06 | C | 100.4625 | 0.024175 | 0.00056252
2012 | 2011-06-06 | C | 201.8852 | 0.075079 | 0.0010719
2012 | 2011-06-07 | B | 30.9143 | 0.0030916 | 9.6879e-05
2012 | 2011-06-07 | C | 986.6032 | 0.185 | 0.0039533
2012 | 2011-06-06 | C | 77.925 | 0.0090104 | 0.00024376
2012 | 2011-06-07 | C | 347.7 | 0.0076062 | 0.0010875
2012 | 2011-06-06 | C | 90.4244 | 0.047757 | 0.00091566
2012 | 2011-06-07 | C | 3.9589 | 0.00086605 | 1.2501e-05
2012 | 2011-06-07 | C | 244.7706 | 0.081084 | 0.0011782
2012 | 2011-06-07 | B | 2.9474 | 0.00049739 | 9.3754e-06
2012 | 2011-06-07 | B | 10.9709 | 0.0034285 | 3.4376e-05
2012 | 2011-06-07 | B | 6.973 | 0.0023535 | 2.1876e-05
2012 | 2011-06-07 | B | 108.9893 | 0.094348 | 0.00034064
2012 | 2011-06-06 | C | 33.4438 | 0.16712 | 0.00091254
2012 | 2011-06-08 | C | 900.7273 | 0.022519 | 0.0028157
2012 | 2011-06-08 | C | 669.8636 | 0.039775 | 0.0020938
2012 | 2011-06-07 | B | 26.9045 | 0.012948 | 0.00034689
2012 | 2011-06-08 | B | 10.9891 | 0.0093411 | 3.4376e-05
2012 | 2011-06-08 | B | 137.9827 | 0.073306 | 0.00043127
2012 | 2011-06-08 | B | 431.9901 | 0.40501 | 0.0013501
2012 | 2011-06-08 | B | 15.9929 | 0.020942 | 5.0002e-05
2012 | 2011-06-08 | B | 109.9862 | 0.073556 | 0.00034376
2012 | 2011-06-08 | B | 3.9934 | 0.0056409 | 1.2501e-05
2012 | 2011-06-07 | C | 1.9 | 0.00016032 | 6.2503e-06
2012 | 2011-06-09 | B | 62.9851 | 0.03917 | 0.00019688
2012 | 2011-06-09 | B | 13.9899 | 0.012854 | 4.3752e-05
2012 | 2011-06-09 | B | 25.9911 | 0.027211 | 8.1253e-05
2012 | 2011-06-09 | B | 27.9888 | 0.023267 | 8.7504e-05
2012 | 2011-06-09 | B | 8.9916 | 0.0099755 | 2.8126e-05
2012 | 2011-06-09 | B | 11.9922 | 0.014241 | 3.7502e-05
2012 | 2011-06-09 | B | 34.9914 | 0.037617 | 0.00010938
2012 | 2011-06-09 | C | 85.9167 | 0.0088605 | 0.00026876
2012 | 2011-06-09 | C | 108.5226 | 0.081395 | 0.00071878
2012 | 2011-06-10 | C | 53.9899 | 0.049436 | 0.00016876
2012 | 2011-06-09 | C | 244.9786 | 0.10489 | 0.00076566
2012 | 2011-06-10 | C | 8.8889 | 0.00066669 | 2.8126e-05
2012 | 2011-06-10 | B | 20.9348 | 0.0028132 | 6.5628e-05
2012 | 2011-06-10 | B | 164.972 | 0.053618 | 0.00051565
2012 | 2011-06-10 | B | 50.9846 | 0.030592 | 0.00015938
2012 | 2011-06-09 | B | 502.7561 | 0.059705 | 0.0016594
2012 | 2011-06-10 | C | 19.8125 | 0.00080492 | 6.2503e-05
2012 | 2011-06-10 | C | 29.5112 | 0.15614 | 0.0011594
2012 | 2011-06-11 | B | 76.9919 | 0.088785 | 0.00024063
2012 | 2011-06-11 | C | 84.4268 | 0.020844 | 0.00043752
2012 | 2011-06-10 | C | 488.7867 | 0.31772 | 0.0036876
2012 | 2011-06-10 | C | 281.1132 | 0.043926 | 0.0028126
2012 | 2011-06-11 | C | 118.7417 | 0.13248 | 0.00039689
2012 | 2011-06-11 | C | 50.3462 | 0.015891 | 0.00019688
2012 | 2011-06-12 | C | 329.4 | 0.012353 | 0.0028126
2012 | 2011-06-12 | C | 234.3333 | 0.0087879 | 0.0028126
2012 | 2011-06-12 | C | 7.9857 | 0.005166 | 2.5001e-05
2012 | 2011-06-12 | B | 1.985 | 0.0012221 | 6.2503e-06
2012 | 2011-06-12 | B | 145.9918 | 0.16607 | 0.00045627
2012 | 2011-06-12 | C | 2.9937 | 0.0044627 | 9.3754e-06
2012 | 2011-06-12 | C | 1.9937 | 0.0029721 | 6.2503e-06
2012 | 2011-06-12 | C | 167.9795 | 0.075069 | 0.00052502
2012 | 2011-06-12 | C | 751.9362 | 0.1034 | 0.0023501
2012 | 2011-06-12 | C | 1237.9286 | 0.15088 | 0.0038689
2012 | 2011-06-12 | C | 1130.9268 | 0.1343 | 0.0035345
2012 | 2011-06-12 | C | 167.9854 | 0.10657 | 0.00052502
2012 | 2011-06-12 | B | 1.3123 | 0.001419 | 9.3754e-06
2012 | 2011-06-12 | C | 167.5257 | 0.090049 | 0.0018845
2012 | 2011-06-13 | C | 7.9655 | 0.002091 | 2.5001e-05
2012 | 2011-06-13 | B | 70.9904 | 0.068553 | 0.00022188
2012 | 2011-06-13 | B | 80.9921 | 0.095676 | 0.00025314
2012 | 2011-06-13 | B | 133.9891 | 0.11431 | 0.00041877
2012 | 2011-06-13 | C | 43.75 | 0.0012305 | 0.00013751
2012 | 2011-06-14 | B | 23.9907 | 0.023842 | 7.5003e-05
2012 | 2011-06-14 | B | 8.991 | 0.0093286 | 2.8126e-05
2012 | 2011-06-14 | B | 48.9913 | 0.052362 | 0.00015313
2012 | 2011-06-14 | B | 69.9913 | 0.074806 | 0.00021876
2012 | 2011-06-14 | B | 22.9885 | 0.018463 | 7.1878e-05
2012 | 2011-06-14 | B | 12.9888 | 0.010757 | 4.0627e-05
2012 | 2011-06-14 | B | 10.962 | 0.0026036 | 3.4376e-05
2012 | 2011-06-15 | C | 5.9677 | 0.0016785 | 1.8751e-05
2012 | 2011-06-15 | B | 48.9906 | 0.04838 | 0.00015313
2012 | 2011-06-15 | B | 67.9927 | 0.087119 | 0.00021251
2012 | 2011-06-15 | B | 393.9919 | 0.45188 | 0.0012313
2012 | 2011-06-15 | C | 663 | 0.018648 | 0.0022376
2012 | 2011-06-15 | C | 177.6211 | 0.051068 | 0.00076253
2012 | 2011-06-16 | B | 50.9797 | 0.023101 | 0.00015938
2012 | 2011-06-16 | B | 6.9892 | 0.0059847 | 2.1876e-05
2012 | 2011-06-16 | B | 22.9881 | 0.01796 | 7.1878e-05
2012 | 2011-06-16 | B | 37.9934 | 0.053549 | 0.00011875
2012 | 2011-06-16 | B | 4.9893 | 0.004319 | 1.5626e-05
2012 | 2011-06-16 | B | 216.8238 | 0.45941 | 0.0030189
2012 | 2011-06-16 | C | 117.528 | 0.058032 | 0.0006719
2012 | 2011-06-16 | C | 2012.9589 | 0.44035 | 0.0062909
2012 | 2011-06-17 | C | 957.9538 | 0.18561 | 0.0029939
2012 | 2011-06-17 | C | 438.4411 | 0.44942 | 0.0032751
2012 | 2011-06-17 | C | 18.9211 | 0.0020696 | 5.9377e-05
2012 | 2011-06-17 | B | 53.9872 | 0.039142 | 0.00016876
2012 | 2011-06-17 | C | 63.8636 | 0.0037921 | 0.00020001
2012 | 2011-06-17 | B | 57.9898 | 0.052918 | 0.00018126
2012 | 2011-06-17 | B | 16.9894 | 0.014866 | 5.3127e-05
2012 | 2011-06-17 | C | 123.1271 | 0.13814 | 0.00076253
2012 | 2011-06-18 | C | 347.4028 | 0.074912 | 0.0034658
2012 | 2011-06-18 | C | 50.6203 | 0.05869 | 0.00041877
2012 | 2011-06-18 | B | 76.9904 | 0.074828 | 0.00024063
2012 | 2011-06-18 | C | 167.3768 | 0.1428 | 0.0013969
2012 | 2011-06-19 | C | 47.9722 | 0.015742 | 0.00015001
2012 | 2011-06-19 | B | 2.9787 | 0.0012846 | 9.3754e-06
2012 | 2011-06-19 | B | 36.9899 | 0.033986 | 0.00011563
2012 | 2011-06-19 | C | 199.1687 | 0.20104 | 0.0027907
2012 | 2011-06-20 | C | 67.9927 | 0.057796 | 0.0010594
2012 | 2011-06-20 | C | 4062.9388 | 0.58407 | 0.012697
2012 | 2011-06-20 | B | 59.9909 | 0.061493 | 0.00018751
2012 | 2011-06-20 | B | 14.9857 | 0.0096943 | 4.6877e-05
2012 | 2011-06-20 | B | 5.9887 | 0.0049034 | 1.8751e-05
2012 | 2011-06-20 | B | 8.9773 | 0.0036191 | 2.8126e-05
2012 | 2011-06-20 | C | 226.725 | 0.0829 | 0.0020938
2012 | 2011-06-20 | C | 1.9739 | 0.0006909 | 6.2503e-06
2012 | 2011-06-21 | B | 11.9852 | 0.0074911 | 3.7502e-05
2012 | 2011-06-21 | B | 33.988 | 0.026236 | 0.00010625
2012 | 2011-06-21 | B | 11.9918 | 0.013566 | 3.7502e-05
2012 | 2011-06-21 | B | 9.9767 | 0.0039285 | 3.1251e-05
2012 | 2011-06-21 | B | 71.9921 | 0.084594 | 0.00022501
2012 | 2011-06-21 | B | 336.9882 | 0.26539 | 0.0010532
2012 | 2011-06-21 | B | 22.9919 | 0.02637 | 7.1878e-05
2012 | 2011-06-21 | C | 150.4918 | 0.055966 | 0.00063753
2012 | 2011-06-21 | B | 31.7024 | 0.041314 | 0.00016876
2012 | 2011-06-21 | C | 88.9725 | 0.029473 | 0.00027814
2012 | 2011-06-22 | B | 10.9189 | 0.0011602 | 3.4376e-05
2012 | 2011-06-22 | B | 17.9732 | 0.0061224 | 5.6252e-05
2012 | 2011-06-22 | C | 1.9895 | 0.0017595 | 6.2503e-06
2012 | 2011-06-22 | B | 26.9912 | 0.028595 | 8.4378e-05
2012 | 2011-06-22 | B | 52.8636 | 0.0031389 | 0.00016563
2012 | 2011-06-22 | B | 20.9792 | 0.0092443 | 6.5628e-05
2012 | 2011-06-22 | B | 15.9899 | 0.014641 | 5.0002e-05
2012 | 2011-06-22 | B | 41.9903 | 0.040024 | 0.00013126
2012 | 2011-06-22 | B | 94.9888 | 0.078963 | 0.00029689
2012 | 2011-06-22 | B | 2.9748 | 0.0010784 | 9.3754e-06
2012 | 2011-06-22 | B | 52.8636 | 0.0031389 | 0.00016563
2012 | 2011-06-22 | B | 38.9973 | 0.045092 | 0.00035314
2012 | 2011-06-23 | C | 2750.3 | 0.060165 | 0.0092566
2012 | 2011-06-23 | B | 6.9474 | 0.0011724 | 2.1876e-05
2012 | 2011-06-23 | C | 2318.4 | 0.086944 | 0.008916
2012 | 2011-06-23 | B | 5.9804 | 0.0028034 | 1.8751e-05
2012 | 2011-06-23 | B | 10.9799 | 0.0050098 | 3.4376e-05
2012 | 2011-06-23 | B | 2.9831 | 0.0016315 | 9.3754e-06
2012 | 2011-06-23 | B | 40.9803 | 0.019082 | 0.00012813
2012 | 2011-06-23 | B | 42.9889 | 0.036005 | 0.00013438
2012 | 2011-06-23 | C | 7.9832 | 0.004391 | 2.5001e-05
2012 | 2011-06-23 | B | 1.9924 | 0.0024283 | 6.2503e-06
2012 | 2011-06-23 | B | 238.625 | 0.0037287 | 0.00074691
2012 | 2011-06-23 | B | 29.9912 | 0.031492 | 9.3754e-05
2012 | 2011-06-24 | B | 9.9727 | 0.0033348 | 3.1251e-05
2012 | 2011-06-24 | C | 75.75 | 0.0021306 | 0.00023751
2012 | 2011-06-24 | C | 3722.4 | 0.37226 | 0.013672
2012 | 2011-06-24 | C | 10.9789 | 0.0047691 | 3.4376e-05
2012 | 2011-06-25 | C | 47.9548 | 0.069238 | 0.00020313
2012 | 2011-06-25 | B | 4.9879 | 0.0038034 | 1.5626e-05
2012 | 2011-06-25 | C | 299.9444 | 0.047806 | 0.00093754
2012 | 2011-06-25 | C | 34.9853 | 0.021976 | 0.00010938
2012 | 2011-06-25 | C | 2.9605 | 0.0006754 | 9.3754e-06
2012 | 2011-06-26 | C | 224.875 | 0.076601 | 0.0014657
2012 | 2011-06-26 | C | 100.925 | 0.01167 | 0.00031564
2012 | 2011-06-27 | B | 104.9838 | 0.059712 | 0.00032814
2012 | 2011-06-27 | B | 35.9915 | 0.039592 | 0.0001125
2012 | 2011-06-24 | B | 8.975 | 0.0032816 | 2.8126e-05
2012 | 2011-06-27 | C | 3.9968 | 0.011704 | 1.2501e-05
2012 | 2011-06-28 | B | 25.9867 | 0.018029 | 8.1253e-05
2012 | 2011-06-28 | B | 357.9893 | 0.31102 | 0.0011188
2012 | 2011-06-28 | B | 162.9911 | 0.16962 | 0.0005094
2012 | 2011-06-28 | B | 50.3696 | 0.057455 | 0.00028751
2012 | 2011-06-28 | B | 25.6848 | 0.033632 | 0.00042502
2012 | 2011-06-28 | C | 519.5 | 0.095787 | 0.0021563
2012 | 2011-06-28 | C | 17.875 | 0.0011731 | 5.6252e-05
2012 | 2011-06-28 | C | 233.875 | 0.015349 | 0.00073128
2012 | 2011-06-28 | C | 8.9934 | 0.012647 | 2.8126e-05
2012 | 2011-06-29 | C | 110.9032 | 0.0097044 | 0.00034689
2012 | 2011-06-27 | B | 175.1761 | 0.18175 | 0.0015344
2012 | 2011-06-28 | B | 352.1148 | 0.063823 | 0.0012313
2012 | 2011-06-29 | C | 40.8 | 0.0015301 | 0.00012813
2012 | 2011-06-29 | C | 110.986 | 0.073531 | 0
2012 | 2011-06-29 | C | 556.9259 | 0.18275 | 0.0026157
2012 | 2011-06-28 | B | 133.9907 | 0.13441 | 0.00041877
2012 | 2011-06-29 | B | 12.99 | 0.012057 | 4.0627e-05
2012 | 2011-06-29 | C | 27.961 | 0.0064663 | 8.7504e-05
2012 | 2011-06-29 | C | 15.9524 | 0.0029912 | 5.0002e-05
2012 | 2011-06-29 | B | 7.6706 | 0.0081503 | 2.5001e-05
2012 | 2011-06-29 | B | 129.9923 | 0.15722 | 0.00040627
2012 | 2011-06-29 | C | 140.9805 | 0.066528 | 0.00044064
2012 | 2011-06-29 | C | 10.9792 | 0.0048379 | 3.4376e-05
2012 | 2011-06-29 | C | 2.95 | 0.00052549 | 9.3754e-06
2012 | 2011-06-29 | C | 353.9892 | 0.30312 | 0.0011063
2012 | 2011-06-30 | C | 202.8421 | 0.010143 | 0.0006344
2012 | 2011-06-30 | B | 22.9878 | 0.017385 | 7.1878e-05
2012 | 2011-06-30 | B | 6.9891 | 0.0059628 | 2.1876e-05
2012 | 2011-06-30 | C | 35.8235 | 0.0015673 | 0.0001125
2012 | 2011-06-30 | B | 1.9764 | 0.00076588 | 6.2503e-06
2012 | 2011-06-28 | B | 53.9906 | 0.053149 | 0.00016876
2012 | 2011-06-14 | B | 37.9923 | 0.046186 | 0.00011875
2012 | 2011-07-01 | C | 2.1469 | 0.030528 | 7.1878e-05
2012 | 2011-07-01 | C | 40.9667 | 0.011138 | 0.00012813
2012 | 2011-07-01 | C | 65.925 | 0.0076229 | 0.00020626
2012 | 2011-07-01 | C | 82.9691 | 0.024373 | 0.00025939
2012 | 2011-07-01 | C | 56.9907 | 0.056993 | 0.00017813
2012 | 2011-07-02 | C | 23.9691 | 0.0070412 | 7.5003e-05
2012 | 2011-07-03 | C | 44.9958 | 0.099838 | 0.00014063
2012 | 2011-07-03 | B | 11.9909 | 0.012254 | 3.7502e-05
2012 | 2011-07-03 | C | 587.96 | 0.1323 | 0.0018376
2012 | 2011-07-03 | C | 40.9904 | 0.039711 | 0.00012813
2012 | 2011-07-03 | C | 378.1698 | 0.059091 | 0.0023563
2012 | 2011-07-04 | C | 28.9589 | 0.006335 | 9.0629e-05
2012 | 2011-07-04 | C | 149.9855 | 0.09562 | 0.00046877
2012 | 2011-07-04 | C | 337.9793 | 0.14998 | 0.0010563
2012 | 2011-07-04 | C | 802.8452 | 0.20323 | 0.0029501
2012 | 2011-07-04 | B | 158.9773 | 0.06409 | 0.0004969
2012 | 2011-07-05 | B | 114.9921 | 0.13584 | 0.00035939
2012 | 2011-07-05 | C | 2.9516 | 0.00054423 | 9.3754e-06
2012 | 2011-07-05 | B | 12.9882 | 0.010229 | 4.0627e-05
2012 | 2011-07-05 | B | 70.6257 | 0.073056 | 0.00030314
2012 | 2011-07-05 | C | 19.5888 | 0.065625 | 0.00020938
2012 | 2011-07-05 | C | 22.9595 | 0.0050943 | 7.1878e-05
2012 | 2011-07-06 | B | 37.9786 | 0.01626 | 0.00011875
2012 | 2011-07-06 | C | 42.9681 | 0.01222 | 0.00013438
2012 | 2011-07-06 | C | 3.9891 | 0.0034034 | 1.2501e-05
2012 | 2011-07-06 | C | 103.9831 | 0.056868 | 0.00032501
2012 | 2011-07-06 | B | 19.9906 | 0.019804 | 6.2503e-05
2012 | 2011-07-06 | C | 816.8085 | 0.11232 | 0.0028407
2012 | 2011-07-06 | C | 34.2662 | 0.01617 | 0.00013751
2012 | 2011-07-06 | C | 67.0761 | 0.11236 | 0.0013063
2012 | 2011-07-06 | B | 1.9691 | 0.00057844 | 6.2503e-06
2012 | 2011-07-06 | C | 154.3636 | 0.014472 | 0.00055315
2012 | 2011-07-06 | C | 37.9778 | 0.015666 | 0.00011875
2012 | 2011-07-06 | C | 43.9964 | 0.1144 | 0.00013751
2012 | 2011-07-07 | C | 78.7815 | 0.036438 | 0.00034064
2012 | 2011-07-06 | C | 199.5459 | 0.1135 | 0.0035158
2012 | 2011-07-07 | B | 36.9831 | 0.020226 | 0.00011563
2012 | 2011-07-07 | C | 69.1282 | 0.024628 | 0.00029689
2012 | 2011-07-07 | C | 153.6854 | 0.041305 | 0.00072815
2012 | 2011-07-07 | C | 56.3482 | 0.019194 | 0.00035001
2012 | 2011-07-07 | B | 19.9923 | 0.024242 | 6.2503e-05
2012 | 2011-07-07 | B | 18.5647 | 0.019552 | 0.00075003
2012 | 2011-07-07 | C | 3.9776 | 0.0016284 | 1.2501e-05
2012 | 2011-07-07 | B | 540.9412 | 0.081144 | 0.0016907
2012 | 2011-07-07 | B | 30.9739 | 0.010841 | 9.6879e-05
2012 | 2011-07-08 | C | 1675.25 | 0.089001 | 0.0056565
2012 | 2011-07-07 | C | 108.8929 | 0.0085076 | 0.00034064
2012 | 2011-07-08 | C | 61.8696 | 0.003867 | 0.00019376
2012 | 2011-07-08 | C | 44.4028 | 0.068133 | 0.00057502
2012 | 2011-07-08 | B | 37.95 | 0.0067601 | 0.00011875
2012 | 2011-07-08 | C | 4.9727 | 0.0016628 | 1.5626e-05
2012 | 2011-07-08 | B | 79.95 | 0.014242 | 0.00025001
2012 | 2011-07-08 | C | 2.9423 | 0.00045056 | 9.3754e-06
2012 | 2011-07-08 | C | 88.3196 | 0.086391 | 0.00039377
2012 | 2011-07-08 | C | 42.9589 | 0.0093976 | 0.00013438
2012 | 2011-07-09 | C | 25.97 | 0.0078725 | 8.1253e-05
2012 | 2011-07-08 | C | 222.4667 | 0.0292 | 0.0014657
2012 | 2011-07-08 | C | 396.9923 | 0.48137 | 0.0012407
2012 | 2011-07-09 | C | 302.9106 | 0.1136 | 0.0014282
2012 | 2011-07-09 | C | 301.4186 | 0.11869 | 0.0024126
2012 | 2011-07-09 | C | 314.8 | 0.011805 | 0.00098441
2012 | 2011-07-09 | C | 185.8 | 0.0069678 | 0.00058127
2012 | 2011-07-09 | C | 699.9762 | 0.26906 | 0.0021876
2012 | 2011-07-09 | C | 237.8 | 0.0089179 | 0.00074378
2012 | 2011-07-09 | C | 94.9817 | 0.04779 | 0.00029689
2012 | 2011-07-12 | C | 1.0412 | 0.013963 | 3.4376e-05
2012 | 2011-07-09 | C | 28.9595 | 0.0064256 | 9.0629e-05
2012 | 2011-07-09 | C | 84.9545 | 0.04593 | 0.00042502
2012 | 2011-07-09 | C | 124.95 | 0.022258 | 0.00039064
2012 | 2011-07-09 | C | 303.7067 | 0.19457 | 0.0018751
2012 | 2011-07-09 | C | 78.9767 | 0.031098 | 0.00024689
2012 | 2011-07-09 | C | 116.925 | 0.01352 | 0.00036564
2012 | 2011-07-10 | C | 93.9752 | 0.034655 | 0.00029376
2012 | 2011-07-09 | C | 94.6301 | 0.085466 | 0.0011594
2012 | 2011-07-10 | C | 1120.8333 | 0.052541 | 0.0035033
2012 | 2011-07-10 | C | 364.8 | 0.013681 | 0.0011407
2012 | 2011-07-09 | C | 43.7768 | 0.045557 | 0.00029376
2012 | 2011-07-09 | C | 1.95 | 0.00034736 | 6.2503e-06
2012 | 2011-07-10 | C | 92.9643 | 0.023533 | 0.00029064
2012 | 2011-07-10 | C | 179.7363 | 0.11122 | 0.0030314
2012 | 2011-07-10 | C | 364.8571 | 0.020524 | 0.0011407
2012 | 2011-07-10 | C | 433.9737 | 0.15054 | 0.0013563
2012 | 2011-07-10 | C | 273.3164 | 0.14862 | 0.0022157
2012 | 2011-07-10 | C | 29.9062 | 0.0027104 | 9.3754e-05
2012 | 2011-07-10 | C | 54.9423 | 0.0084134 | 0.00017188
2012 | 2011-07-10 | C | 50.1657 | 0.026965 | 0.00020938
2012 | 2011-07-10 | C | 5.9524 | 0.0011161 | 1.8751e-05
2012 | 2011-07-09 | C | 185.7857 | 0.0063866 | 0.00058127
2012 | 2011-07-09 | C | 185.9524 | 0.034867 | 0.00058127
2012 | 2011-07-09 | C | 185.8125 | 0.0075489 | 0.00058127
2012 | 2011-07-09 | C | 100.048 | 0.25326 | 0.0006094
2012 | 2011-07-10 | C | 136.5714 | 0.0017072 | 0.00042814
2012 | 2011-07-10 | C | 37.9062 | 0.0034354 | 0.00011875
2012 | 2011-07-10 | C | 16.0304 | 0.088772 | 0.00036564
2012 | 2011-07-10 | C | 154.843 | 0.18969 | 0.00105
2012 | 2011-07-10 | C | 10.9727 | 0.0036692 | 3.4376e-05
2012 | 2011-07-10 | C | 104.8125 | 0.0042582 | 0.00032814
2012 | 2011-07-09 | C | 7.9975 | 0.030092 | 2.5001e-05
2012 | 2011-07-10 | C | 33.2652 | 0.096889 | 0.00042502
2012 | 2011-07-11 | C | 94.925 | 0.010976 | 0.00029689
2012 | 2011-07-11 | C | 115.137 | 0.077721 | 0.00072815
2012 | 2011-07-11 | C | 497.6053 | 0.34989 | 0.0018251
2012 | 2011-07-11 | C | 237.8235 | 0.010405 | 0.00074378
2012 | 2011-07-11 | C | 237.8125 | 0.0096615 | 0
2012 | 2011-07-11 | C | 255.9712 | 0.080794 | 0.00080003
2012 | 2011-07-10 | C | 84.845 | 0.033409 | 0.00077503
2012 | 2011-07-10 | C | 213.9256 | 0.22263 | 0.0011313
2012 | 2011-07-10 | C | 32.9978 | 0.13777 | 0.00010313
2012 | 2011-07-11 | C | 13.9 | 0.0011729 | 4.3752e-05
2012 | 2011-07-11 | B | 48.9813 | 0.024032 | 0.00015313
2012 | 2011-07-11 | C | 58.9231 | 0.0066291 | 0.00018438
2012 | 2011-07-11 | B | 16.9867 | 0.011838 | 5.3127e-05
2012 | 2011-07-11 | C | 135.9949 | 0.24905 | 0.00042502
2012 | 2011-07-11 | C | 38.3492 | 0.05489 | 0.0005094
2012 | 2011-07-11 | C | 957.5 | 0.0089769 | 0.0029939
2012 | 2011-07-11 | C | 10.9032 | 0.00095407 | 3.4376e-05
2012 | 2011-07-11 | C | 34.5705 | 0.14455 | 0.00031564
2012 | 2011-07-12 | C | 555.8333 | 0.026056 | 0.0017376
2012 | 2011-07-11 | C | 141.9132 | 0.095795 | 0.00056252
2012 | 2011-07-11 | C | 168.9464 | 0.027983 | 0.00052815
2012 | 2011-07-11 | C | 9.9681 | 0.0028348 | 3.1251e-05
2012 | 2011-07-11 | C | 37.9764 | 0.014716 | 0.00011875
2012 | 2011-07-11 | C | 61.9268 | 0.0073541 | 0.00019376
2012 | 2011-07-11 | C | 10.9589 | 0.0023974 | 3.4376e-05
2012 | 2011-07-11 | C | 177.9538 | 0.03448 | 0.00055627
2012 | 2011-07-10 | C | 14.689 | 0.05123 | 0.00014063
2012 | 2011-07-12 | C | 24.9032 | 0.0021791 | 7.8128e-05
2012 | 2011-07-11 | C | 146.2339 | 0.055297 | 0.00073753
2012 | 2011-07-11 | C | 197.1012 | 0.10163 | 0
2012 | 2011-07-10 | C | 89.0161 | 0.27596 | 0.00051877
2012 | 2011-07-11 | C | 71.9895 | 0.063668 | 0.00022501
2012 | 2011-07-11 | C | 2.9978 | 0.012544 | 9.3754e-06
2012 | 2011-07-12 | C | 6.9091 | 0.00064775 | 2.1876e-05
2012 | 2011-07-12 | C | 3.963 | 0.00096601 | 1.2501e-05
2012 | 2011-07-12 | C | 181.9706 | 0.056299 | 0.00056877
2012 | 2011-07-11 | C | 61.9318 | 0.0079353 | 0.00019376
2012 | 2011-07-12 | C | 419.8125 | 0.017056 | 0.0013126
2012 | 2011-07-12 | C | 2.989 | 0.0025127 | 9.3754e-06
2012 | 2011-07-12 | C | 116.7551 | 0.052542 | 0.0010625
2012 | 2011-07-12 | C | 154.8 | 0.0058052 | 0.00048439
2012 | 2011-07-12 | C | 30.9388 | 0.0044476 | 9.6879e-05
2012 | 2011-07-12 | C | 2.9375 | 0.0004131 | 9.3754e-06
2012 | 2011-07-12 | C | 16.8889 | 0.0012667 | 5.3127e-05
2012 | 2011-07-13 | C | 206.0462 | 0.15132 | 0.0015501
2012 | 2011-07-12 | C | 27.9858 | 0.018279 | 8.7504e-05
2012 | 2011-07-12 | C | 84.9811 | 0.013279 | 0.0010657
2012 | 2011-07-12 | C | 314.2769 | 0.060894 | 0.0021845
2012 | 2011-07-11 | C | 45.9521 | 0.026567 | 0.00024689
2012 | 2011-07-11 | C | 102.2695 | 0.052415 | 0.00056877
2012 | 2011-07-11 | C | 22.786 | 0.21341 | 0.00020313
2012 | 2011-07-12 | C | 20.9348 | 0.0028132 | 6.5628e-05
2012 | 2011-07-12 | C | 37.9118 | 0.0036729 | 0.00011875
2012 | 2011-07-12 | C | 30.94 | 0.0045445 | 9.6879e-05
2012 | 2011-07-12 | C | 74.212 | 0.041978 | 0.00035939
2012 | 2011-07-12 | C | 540.375 | 0.0084437 | 0.0022313
2012 | 2011-07-13 | C | 9.4 | 5.8752e-05 | 3.1251e-05
2012 | 2011-07-12 | C | 76.2276 | 0.15103 | 0.00051877
2012 | 2011-07-12 | C | 78.8558 | 0.050519 | 0.00038439
2012 | 2011-07-12 | C | 1167.8636 | 0.069345 | 0.0036501
2012 | 2011-07-12 | C | 954.5882 | 0.041765 | 0.0035095
2012 | 2011-07-12 | C | 1146.7302 | 0.21502 | 0.0044096
2012 | 2011-07-11 | C | 294.8209 | 0.058967 | 0.0029189
2012 | 2011-07-11 | C | 177.9681 | 0.050612 | 0.00055627
2012 | 2011-07-13 | C | 429.1912 | 0.087183 | 0.0014094
2012 | 2011-07-13 | C | 53.788 | 0.030425 | 0.00029376
2012 | 2011-07-13 | C | 22.9362 | 0.0031539 | 7.1878e-05
2012 | 2011-07-13 | C | 94.9844 | 0.056102 | 0.00029689
2012 | 2011-07-13 | C | 1.9464 | 0.00032239 | 6.2503e-06
2012 | 2011-07-13 | C | 85.9871 | 0.061537 | 0.00026876
2012 | 2011-07-13 | C | 37.9688 | 0.011035 | 0.00011875
2012 | 2011-07-13 | C | 67.1135 | 0.028944 | 0.00086566
2012 | 2011-07-13 | C | 545.9091 | 0.051181 | 0.0020313
2012 | 2011-07-13 | C | 11.9814 | 0.005916 | 3.7502e-05
2012 | 2011-07-13 | C | 47.6802 | 0.025182 | 0.00054377
2012 | 2011-07-13 | C | 44.8875 | 0.022024 | 0.00038439
2012 | 2011-07-14 | B | 185.9667 | 0.050562 | 0.00058127
2012 | 2011-07-13 | C | 30.9571 | 0.0064819 | 9.6879e-05
2012 | 2011-07-14 | B | 5.9625 | 0.0014348 | 1.8751e-05
2012 | 2011-07-14 | C | 12.9118 | 0.0012509 | 4.0627e-05
2012 | 2011-07-12 | C | 33.4875 | 0.27084 | 0.00022188
2012 | 2011-07-14 | B | 240.9684 | 0.069281 | 0.00075316
2012 | 2011-07-14 | C | 32.5903 | 0.022814 | 0.00044689
2012 | 2011-07-14 | C | 462.986 | 0.30529 | 0.0014469
2012 | 2011-07-14 | C | 102.9612 | 0.12356 | 0.0005219
2012 | 2011-07-14 | C | 11.9977 | 0.04938 | 3.7502e-05
2012 | 2011-07-14 | C | 207.9118 | 0.020142 | 0.00065003
2012 | 2011-07-15 | C | 100.7628 | 0.14643 | 0.00095316
2012 | 2011-07-15 | C | 190.6287 | 0.097701 | 0.002197
2012 | 2011-07-15 | C | 14.9412 | 0.0022413 | 4.6877e-05
2012 | 2011-07-15 | C | 335.9816 | 0.168 | 0.00105
2012 | 2011-07-15 | C | 3.8929 | 0.00030414 | 1.2501e-05
2012 | 2011-07-16 | C | 7.6667 | 0.00014376 | 2.5001e-05
2012 | 2011-07-18 | B | 1.9577 | 0.00041604 | 6.2503e-06
2012 | 2011-07-18 | B | 15.9833 | 0.0088411 | 5.0002e-05
2012 | 2011-07-18 | C | 36.9712 | 0.011669 | 0.00011563
2012 | 2011-07-18 | B | 12.9762 | 0.0049879 | 4.0627e-05
2012 | 2011-07-18 | B | 10.9922 | 0.013122 | 3.4376e-05
2012 | 2011-07-17 | C | 44.8235 | 0.0019611 | 0.00014063
2012 | 2011-07-18 | C | 91.9333 | 0.012067 | 0.00028751
2012 | 2011-07-18 | C | 135.5594 | 0.1093 | 0.0030282
2012 | 2011-07-19 | C | 26.9079 | 0.0061386 | 8.7504e-05
2012 | 2011-07-19 | B | 5.9863 | 0.0040409 | 1.8751e-05
2012 | 2011-07-19 | C | 54.8966 | 0.0044605 | 0.00017188
2012 | 2011-07-19 | C | 45.217 | 0.069241 | 0.0010407
2012 | 2011-07-19 | B | 10.9914 | 0.011851 | 3.4376e-05
2012 | 2011-07-19 | C | 1044.619 | 0.19587 | 0.0040658
2012 | 2011-07-19 | C | 25.9516 | 0.004785 | 8.1253e-05
2012 | 2011-07-20 | C | 278.9812 | 0.13688 | 0.00087191
2012 | 2011-07-20 | B | 4.8889 | 0.00036668 | 1.5626e-05
2012 | 2011-07-20 | C | 8.8235 | 0.00038605 | 2.8126e-05
2012 | 2011-07-20 | B | 42.9912 | 0.045546 | 0.00013438
2012 | 2011-07-20 | B | 19.9915 | 0.021992 | 6.2503e-05
2012 | 2011-07-20 | C | 5.925 | 0.00068511 | 1.8751e-05
2012 | 2011-07-20 | B | 4.1728 | 0.0049423 | 5.9377e-05
2012 | 2011-07-21 | B | 42.9858 | 0.027942 | 0.00013438
2012 | 2011-07-21 | C | 35.8333 | 0.0016798 | 0.0001125
2012 | 2011-07-21 | B | 3.9887 | 0.0032784 | 1.2501e-05
2012 | 2011-07-21 | B | 19.9925 | 0.024679 | 6.2503e-05
2012 | 2011-07-21 | C | 101.4142 | 0.052611 | 0.0014282
2012 | 2011-07-21 | C | 26.9577 | 0.0057288 | 8.4378e-05
2012 | 2011-07-21 | C | 105.0214 | 0.32098 | 0.0042533
2012 | 2011-07-21 | B | 63.9873 | 0.046793 | 0.00020001
2012 | 2011-07-22 | C | 415.4036 | 0.3596 | 0.0044096
2012 | 2011-07-22 | C | 252.9773 | 0.10199 | 0.00079066
2012 | 2011-07-22 | C | 176.8333 | 0.0082894 | 0.00055315
2012 | 2011-07-22 | C | 13.9697 | 0.0041911 | 4.3752e-05
2012 | 2011-07-21 | B | 3.9909 | 0.0040784 | 1.2501e-05
2012 | 2011-07-22 | C | 56.2546 | 0.037446 | 0.00054065
2012 | 2011-07-22 | C | 21.9032 | 0.0019166 | 6.8753e-05
2012 | 2011-07-22 | C | 166.8532 | 0.055272 | 0.00095004
2012 | 2011-07-23 | C | 17.9423 | 0.0027475 | 5.6252e-05
2012 | 2011-07-23 | C | 442.2007 | 0.38141 | 0.0027595
2012 | 2011-07-22 | C | 15.996 | 0.037242 | 5.0002e-05
2012 | 2011-07-23 | C | 63.8696 | 0.003992 | 0.00020001
2012 | 2011-07-23 | C | 10.5211 | 0.010817 | 0.00042502
2012 | 2011-07-24 | C | 68.9914 | 0.024364 | 0.00034689
2012 | 2011-07-24 | C | 211.9605 | 0.048355 | 0.00072815
2012 | 2011-07-24 | C | 121.5957 | 0.05244 | 0.00043752
2012 | 2011-07-25 | C | 7.9987 | 0.055718 | 2.5001e-05
2012 | 2011-07-25 | C | 127.9464 | 0.021192 | 0.00040002
2012 | 2011-07-25 | C | 303.8 | 0.011393 | 0.00095004
2012 | 2011-07-25 | B | 10.99 | 0.010235 | 3.4376e-05
2012 | 2011-07-25 | C | 20.8497 | 0.01238 | 0.00074378
2012 | 2011-07-25 | C | 174.9 | 0.21153 | 0.00070628
2012 | 2011-07-25 | C | 79.466 | 0.16018 | 0.00074066
2012 | 2011-07-25 | C | 507.9776 | 0.20796 | 0.0015876
2012 | 2011-07-25 | C | 15.9941 | 0.025242 | 5.0002e-05
2012 | 2011-07-25 | C | 539.2345 | 0.51229 | 0.0017876
2012 | 2011-07-25 | C | 237.8 | 0.0089179 | 0.00074378
2012 | 2011-07-25 | C | 63.9459 | 0.043765 | 0.00024376
2012 | 2011-07-25 | C | 76.8442 | 0.054754 | 0.00028439
2012 | 2011-07-25 | C | 11.9375 | 0.0016788 | 3.7502e-05
2012 | 2011-07-25 | C | 53.9948 | 0.096688 | 0.00016876
2012 | 2011-07-26 | C | 178.9552 | 0.035792 | 0.0005594
2012 | 2011-07-26 | C | 78.8846 | 0.0056701 | 0.00024689
2012 | 2011-07-26 | B | 8.9871 | 0.0064598 | 2.8126e-05
2012 | 2011-07-26 | B | 224.9674 | 0.062572 | 0.00070315
2012 | 2011-07-26 | B | 43.99 | 0.04083 | 0.00013751
2012 | 2011-07-26 | B | 137.9783 | 0.058212 | 0.00043127
2012 | 2011-07-26 | C | 687.0253 | 0.16318 | 0.0025439
2012 | 2011-07-26 | C | 44.9524 | 0.0084289 | 0.00014063
2012 | 2011-07-27 | C | 90.8 | 0.0034051 | 0.00028439
2012 | 2011-07-27 | C | 90.8 | 0.0034051 | 0.00028439
2012 | 2011-07-27 | C | 178.9915 | 0.19634 | 0.0005594
2012 | 2011-07-27 | C | 406.9799 | 0.18569 | 0.0012719
2012 | 2011-07-27 | C | 53.6433 | 0.028164 | 0.00022501
2012 | 2011-07-27 | C | 6.9 | 0.00058221 | 2.1876e-05
2012 | 2011-07-27 | C | 108.9605 | 0.024858 | 0.00034064
2012 | 2011-07-27 | B | 293.9688 | 0.085438 | 0.00091879
2012 | 2011-07-27 | B | 36.4367 | 0.027556 | 0.00017813
2012 | 2011-07-27 | C | 1536.2222 | 0.072013 | 0.0051315
2012 | 2011-07-28 | C | 133.9819 | 0.06825 | 0.00041877
2012 | 2011-07-28 | C | 6.9 | 0.00058221 | 2.1876e-05
2012 | 2011-07-28 | B | 16.9756 | 0.0063661 | 5.3127e-05
2012 | 2011-07-28 | B | 82.967 | 0.022817 | 0.00025939
2012 | 2011-07-27 | C | 1394.303 | 0.99348 | 0.013676
2012 | 2011-07-28 | C | 205.4245 | 0.066124 | 0.0015126
2012 | 2011-07-29 | C | 33.9286 | 0.0041352 | 0.00010625
2012 | 2011-07-29 | B | 61.9801 | 0.028667 | 0.00019376
2012 | 2011-07-29 | B | 96.9483 | 0.016664 | 0.00030314
2012 | 2011-07-29 | C | 102.9864 | 0.06984 | 0.00032189
2012 | 2011-07-30 | C | 560.9362 | 0.077132 | 0.0017532
2012 | 2011-07-30 | C | 62.95 | 0.011213 | 0.00019688
2012 | 2011-07-30 | C | 80.9118 | 0.0078386 | 0.00025314
2012 | 2011-08-01 | C | 196.9538 | 0.038161 | 0.00061565
2012 | 2011-08-01 | B | 140.9874 | 0.10398 | 0.00044064
2012 | 2011-08-01 | C | 44.96 | 0.010116 | 0.00014063
2012 | 2011-08-01 | C | 28.9333 | 0.0037977 | 9.0629e-05
2012 | 2011-08-01 | B | 22.9909 | 0.023495 | 7.1878e-05
2012 | 2011-08-02 | C | 110.792 | 0.093831 | 0.00068128
2012 | 2011-08-02 | C | 28.9091 | 0.0027103 | 9.0629e-05
2012 | 2011-07-13 | B | 230.8929 | 0.018039 | 0.0007219
2012 | 2011-07-19 | B | 2.9875 | 0.0022127 | 9.3754e-06
2012 | 2011-08-02 | B | 59.9905 | 0.058681 | 0.00018751
2012 | 2011-08-02 | B | 3.9906 | 0.0039284 | 1.2501e-05
2012 | 2011-08-03 | C | 88.9538 | 0.017236 | 0.00027814
2012 | 2011-08-03 | B | 81.8291 | 0.10996 | 0.00043752
2012 | 2011-08-03 | C | 97.9333 | 0.012854 | 0.00030626
2012 | 2011-08-04 | B | 7.9754 | 0.002966 | 2.5001e-05
2012 | 2011-08-04 | B | 31.9895 | 0.028192 | 0.0001
2012 | 2011-08-03 | B | 49.9922 | 0.059681 | 0.00015626
2012 | 2011-08-05 | C | 24.9464 | 0.0041319 | 7.8128e-05
2012 | 2011-08-05 | B | 9.9091 | 0.00092902 | 3.1251e-05
2012 | 2011-08-05 | C | 419.7 | 0.0091813 | 0.0013126
2012 | 2011-08-05 | B | 60.9873 | 0.044408 | 0.00019063
2012 | 2011-08-05 | C | 78.6667 | 0.0014751 | 0.00024689
2012 | 2011-08-07 | C | 377.5942 | 0.077882 | 0.0015407
2012 | 2011-08-07 | C | 177.9854 | 0.11236 | 0.00055627
2012 | 2011-08-07 | C | 212.9871 | 0.15309 | 0.00066565
2012 | 2011-08-06 | C | 19.7589 | 0.18321 | 0.00051252
2012 | 2011-08-07 | C | 143.0891 | 0.28485 | 0.00057502
2012 | 2011-08-07 | C | 146.2868 | 0.057603 | 0.00092504
2012 | 2011-08-07 | C | 41.6654 | 0.16771 | 0.00085316
2012 | 2011-08-07 | C | 5.9647 | 0.0015285 | 1.8751e-05
2012 | 2011-08-07 | C | 197.9762 | 0.0761 | 0.00099379
2012 | 2011-08-07 | C | 18.9976 | 0.074984 | 5.9377e-05
2012 | 2011-08-07 | C | 45.1633 | 0.013408 | 0.00030626
2012 | 2011-08-08 | B | 7.9809 | 0.003841 | 2.5001e-05
2012 | 2011-08-07 | C | 119.85 | 0.0063673 | 0.00037502
2012 | 2011-08-08 | C | 122.6554 | 0.05558 | 0.00074066
2012 | 2011-08-08 | C | 27.9388 | 0.0040164 | 8.7504e-05
2012 | 2011-08-08 | B | 40.9862 | 0.027539 | 0.00012813
2012 | 2011-08-08 | C | 5.9062 | 0.00053528 | 1.8751e-05
2012 | 2011-08-08 | C | 63.2456 | 0.033205 | 0.00024376
2012 | 2011-08-06 | C | 499.961 | 0.11562 | 0.0015626
2012 | 2011-08-09 | C | 186.3444 | 0.086188 | 0.0011782
2012 | 2011-08-09 | B | 7.9825 | 0.004191 | 2.5001e-05
2012 | 2011-08-09 | B | 1.99 | 0.001847 | 6.2503e-06
2012 | 2011-08-09 | B | 1.9923 | 0.002422 | 6.2503e-06
2012 | 2011-08-09 | B | 91.9932 | 0.12563 | 0.00028751
2012 | 2011-08-09 | C | 111.7854 | 0.15686 | 0.00089691
2012 | 2011-08-10 | C | 2521.75 | 0.070927 | 0.0078816
2012 | 2011-08-10 | C | 419.5714 | 0.0052449 | 0.0013126
2012 | 2011-08-11 | C | 3.9722 | 0.0013034 | 1.2501e-05
2012 | 2011-08-12 | C | 107.2561 | 0.12335 | 0.00089066
2012 | 2011-08-11 | B | 82.9908 | 0.083513 | 0.00025939
2012 | 2011-08-12 | C | 317.6299 | 0.12309 | 0.0011313
2012 | 2011-08-12 | C | 419.5714 | 0.0052449 | 0.0013126
2012 | 2011-08-12 | C | 5.9684 | 0.001716 | 1.8751e-05
2012 | 2011-08-12 | C | 57.9538 | 0.011229 | 0.00018126
2012 | 2011-08-12 | B | 23.9855 | 0.015291 | 7.5003e-05
2012 | 2011-08-12 | C | 29.2926 | 0.034146 | 0.00039689
2012 | 2011-08-12 | C | 289.3164 | 0.30018 | 0.00090629
2012 | 2011-08-12 | C | 206.664 | 0.24413 | 0.0023688
2012 | 2011-08-12 | C | 45.925 | 0.0053103 | 0.00014376
2012 | 2011-08-12 | B | 38.9915 | 0.042892 | 0.00012188
2012 | 2011-08-12 | B | 7.9874 | 0.005891 | 2.5001e-05
2012 | 2011-08-12 | B | 53.9829 | 0.029017 | 0.00016876
2012 | 2011-08-12 | C | 14.9189 | 0.0015852 | 4.6877e-05
2012 | 2011-08-13 | C | 419.625 | 0.0065569 | 0.0013126
2012 | 2011-08-13 | C | 395.3333 | 0.059302 | 0.0013969
2012 | 2011-08-14 | C | 150.1466 | 0.12341 | 0.00074066
2012 | 2011-08-14 | C | 668.625 | 0.010448 | 0.0020907
2012 | 2011-08-14 | C | 26.0333 | 0.021722 | 0.0019282
2012 | 2011-08-14 | C | 199.4941 | 0.051122 | 0.00071878
2012 | 2011-08-14 | B | 154.9722 | 0.050852 | 0.00048439
2012 | 2011-08-14 | C | 97.9565 | 0.020204 | 0.00030626
2012 | 2011-08-14 | C | 773.0273 | 0.25849 | 0.0029064
2012 | 2011-08-14 | C | 9.8696 | 0.00061687 | 3.1251e-05
2012 | 2011-08-14 | C | 223.0887 | 0.084359 | 0.00074378
2012 | 2011-08-14 | C | 94.8889 | 0.007117 | 0.00029689
2012 | 2011-08-14 | C | 122.9448 | 0.054559 | 0.00070628
2012 | 2011-08-14 | C | 29.9717 | 0.0096475 | 9.3754e-05
2012 | 2011-08-14 | C | 239.3402 | 0.18026 | 0.0022001
2012 | 2011-08-15 | C | 116.9806 | 0.055568 | 0.00036564
2012 | 2011-08-14 | C | 97.9805 | 0.046236 | 0.00030626
2012 | 2011-08-14 | C | 14.9318 | 0.0019132 | 4.6877e-05
2012 | 2011-08-14 | C | 1416.3151 | 1.7705 | 0.0044314
2012 | 2011-08-14 | C | 14.7754 | 0.040773 | 0.00042814
2012 | 2011-08-14 | C | 225.7525 | 0.20601 | 0.00090004
2012 | 2011-08-15 | C | 92.963 | 0.022661 | 0.00029064
2012 | 2011-08-15 | C | 14.7496 | 0.23218 | 0.00030626
2012 | 2011-08-15 | C | 432.8421 | 0.17585 | 0.0016782
2012 | 2011-08-15 | B | 10.9647 | 0.0028098 | 3.4376e-05
2012 | 2011-08-15 | C | 152.7883 | 0.1294 | 0.00086254
2012 | 2011-08-14 | C | 1279.4211 | 0.063974 | 0.0045533
2012 | 2011-08-15 | C | 16.9552 | 0.0033912 | 5.3127e-05
2012 | 2011-08-15 | C | 68.97 | 0.020907 | 0.00021563
2012 | 2011-08-15 | C | 101.7551 | 0.14055 | 0.00037814
2012 | 2011-08-15 | C | 7.9667 | 0.002166 | 2.5001e-05
2012 | 2011-08-16 | C | 78.4224 | 0.038723 | 0.00024689
2012 | 2011-08-15 | C | 55.9625 | 0.013467 | 0.00017501
2012 | 2011-08-15 | C | 135.9952 | 0.26435 | 0.00042502
2012 | 2011-08-15 | C | 26.9583 | 0.0058131 | 8.4378e-05
2012 | 2011-08-15 | C | 162.8889 | 0.012217 | 0.0005094
2012 | 2011-08-15 | C | 415.7857 | 0.014293 | 0.0013001
2012 | 2011-08-15 | C | 109.4027 | 0.22736 | 0.0007219
2012 | 2011-08-15 | C | 32.7857 | 0.0011271 | 0.00010313
2012 | 2011-08-15 | C | 37.9778 | 0.015666 | 0.00011875
2012 | 2011-08-15 | C | 142.6296 | 0.10698 | 0.00086879
2012 | 2011-08-15 | C | 75.7362 | 0.054911 | 0.00065315
2012 | 2011-08-15 | C | 29.8259 | 0.018456 | 0.00026876
2012 | 2011-08-15 | C | 159.9643 | 0.040493 | 0.00050002
2012 | 2011-08-15 | C | 62.531 | 0.13191 | 0.00024689
2012 | 2011-08-15 | C | 275.2362 | 0.52899 | 0.0025501
2012 | 2011-08-15 | C | 112.0538 | 0.044473 | 0.00059065
2012 | 2011-08-15 | C | 42.1956 | 0.23696 | 0.0010844
2012 | 2011-08-15 | C | 209.94 | 0.030836 | 0.00065628
2012 | 2011-08-16 | B | 4.987 | 0.0035534 | 1.5626e-05
2012 | 2011-08-15 | C | 582.9764 | 0.22591 | 0.0020751
2012 | 2011-08-15 | C | 8.9869 | 0.0063473 | 2.8126e-05
2012 | 2011-08-15 | C | 8.9972 | 0.029861 | 2.8126e-05
2012 | 2011-08-15 | C | 22.9973 | 0.07956 | 7.1878e-05
2012 | 2011-08-15 | C | 28.9739 | 0.010141 | 9.0629e-05
2012 | 2011-08-15 | C | 98.4512 | 0.090456 | 0.00035626
2012 | 2011-08-15 | C | 64.9868 | 0.045696 | 0.00020313
2012 | 2011-08-15 | C | 3.9854 | 0.0025284 | 1.2501e-05
2012 | 2011-08-15 | C | 82.6148 | 0.030724 | 0.00044689
2012 | 2011-08-15 | C | 675.5 | 0.0063331 | 0.0021126
2012 | 2011-08-15 | C | 59.9842 | 0.035055 | 0.00018751
2012 | 2011-08-15 | C | 39.961 | 0.0092414 | 0.00012501
2012 | 2011-08-15 | C | 507.9845 | 0.30163 | 0.0015876
2012 | 2011-08-15 | C | 22.9464 | 0.0038007 | 7.1878e-05
2012 | 2011-08-15 | C | 37.9706 | 0.011748 | 0.00011875
2012 | 2011-08-15 | C | 137.7 | 0.0030123 | 0.00043127
2012 | 2011-08-15 | C | 198.6904 | 0.71407 | 0.00065003
2012 | 2011-08-15 | C | 20.9844 | 0.012394 | 6.5628e-05
2012 | 2011-08-15 | C | 96.9689 | 0.4182 | 0.0020938
2012 | 2011-08-15 | C | 53.1738 | 0.050185 | 0.00031251
2012 | 2011-08-15 | C | 25.9915 | 0.028348 | 8.1253e-05
2012 | 2011-08-15 | C | 239.9915 | 0.264 | 0.00075003
2012 | 2011-08-15 | C | 80.1613 | 0.038078 | 0.00028126
2012 | 2011-08-16 | C | 24.9483 | 0.0042882 | 7.8128e-05
2012 | 2011-08-16 | C | 635.4 | 0.0039714 | 0.0019876
2012 | 2011-08-17 | C | 203.9375 | 0.02868 | 0.00063753
2012 | 2011-08-17 | C | 352.2072 | 0.27297 | 0.0014907
2012 | 2011-08-15 | C | 103.0441 | 0.042829 | 0.00050627
2012 | 2011-08-16 | C | 290.8443 | 0.10816 | 0.00091566
2012 | 2011-08-15 | C | 50.7112 | 0.12409 | 0.00023126
2012 | 2011-08-15 | C | 127.0542 | 0.56263 | 0.00055315
2012 | 2011-08-15 | C | 196.96 | 0.044318 | 0.00072815
2012 | 2011-08-16 | C | 9.9935 | 0.014241 | 3.1251e-05
2012 | 2011-08-15 | C | 94.9893 | 0.082228 | 0.00029689
2012 | 2011-08-15 | C | 118.95 | 0.021189 | 0.00037189
2012 | 2011-08-15 | C | 156.8106 | 0.51603 | 0.00096566
2012 | 2011-08-15 | C | 54.9889 | 0.046055 | 0.00017188
2012 | 2011-08-15 | C | 10.9589 | 0.0023974 | 3.4376e-05
2012 | 2011-08-15 | C | 9.9948 | 0.017991 | 3.1251e-05
2012 | 2011-08-17 | C | 189.7931 | 0.10142 | 0.00074691
2012 | 2011-08-15 | C | 489.5528 | 0.37177 | 0.0020532
2012 | 2011-08-15 | C | 45.9948 | 0.082794 | 0.00014376
2012 | 2011-08-17 | C | 38.9795 | 0.01742 | 0.00012188
2012 | 2011-08-17 | C | 12.9659 | 0.0034442 | 4.0627e-05
2012 | 2011-08-15 | C | 10.9974 | 0.03942 | 3.4376e-05
2012 | 2011-08-17 | C | 358.9338 | 0.16601 | 0.0015751
2012 | 2011-08-17 | C | 1127.75 | 0.0035244 | 0.0035595
2012 | 2011-08-15 | C | 8.8785 | 0.03804 | 5.9377e-05
2012 | 2011-08-17 | C | 115.925 | 0.013404 | 0.00036251
2012 | 2011-08-15 | C | 35.9508 | 0.0065164 | 0.0001125
2012 | 2011-08-15 | C | 21.991 | 0.022817 | 6.8753e-05
2012 | 2011-08-17 | C | 347.8571 | 0.14132 | 0.0023876
2012 | 2011-08-15 | C | 119.8868 | 0.38927 | 0.00090629
2012 | 2011-08-18 | C | 239.8421 | 0.011993 | 0.00075003
2012 | 2011-08-15 | C | 129.9798 | 0.52238 | 0.00065628
2012 | 2011-08-15 | C | 373.6045 | 1.024 | 0.0015782
2012 | 2011-08-15 | C | 916.9895 | 0.811 | 0.0028657
2012 | 2011-08-15 | C | 25.0749 | 0.28861 | 0.0007344
2012 | 2011-08-15 | C | 7.9516 | 0.0014661 | 2.5001e-05
2012 | 2011-08-17 | C | 190.75 | 0.024441 | 0.00071565
2012 | 2011-08-17 | C | 612.9412 | 0.091945 | 0.0019157
2012 | 2011-08-16 | C | 191.573 | 0.53523 | 0.0015219
2012 | 2011-08-15 | C | 293.3907 | 0.74359 | 0.003022
2012 | 2011-08-18 | B | 4.9571 | 0.0010379 | 1.5626e-05
2012 | 2011-08-18 | C | 5.9858 | 0.0039097 | 1.8751e-05
2012 | 2011-08-18 | C | 256.2511 | 0.17938 | 0.00092504
2012 | 2011-08-15 | C | 21.9691 | 0.0064537 | 6.8753e-05
2012 | 2011-08-18 | C | 15.9362 | 0.0021913 | 5.0002e-05
2012 | 2011-08-15 | C | 2.8235 | 0.00012353 | 9.3754e-06
2012 | 2011-08-15 | C | 158.5143 | 0.15456 | 0.00070628
2012 | 2011-08-15 | C | 291.9118 | 0.02828 | 0.00091254
2012 | 2011-08-17 | C | 130.9118 | 0.012683 | 0.00040939
2012 | 2011-08-19 | C | 35.9508 | 0.0065164 | 0.0001125
2012 | 2011-08-19 | C | 10.9508 | 0.0019849 | 3.4376e-05
2012 | 2011-08-19 | C | 124.7118 | 0.065087 | 0.00068753
2012 | 2011-08-20 | C | 238.1034 | 0.14882 | 0.0019063
2012 | 2011-08-15 | C | 3.8483 | 0.039434 | 0.00012188
2012 | 2011-08-15 | C | 6.1095 | 0.034291 | 2.5001e-05
2012 | 2011-08-19 | C | 15.9211 | 0.0017414 | 5.0002e-05
2012 | 2011-08-21 | C | 94.8125 | 0.0038519 | 0.00029689
2012 | 2011-08-21 | C | 94.8125 | 0.0038519 | 0.00029689
2012 | 2011-08-20 | C | 21.8 | 0.00081753 | 6.8753e-05
2012 | 2011-08-15 | C | 11.9971 | 0.038055 | 3.7502e-05
2012 | 2011-08-15 | C | 11.8143 | 0.0024737 | 0.00012813
2012 | 2011-08-21 | C | 33.9348 | 0.0045602 | 0.00010625
2012 | 2011-08-21 | C | 222.9062 | 0.020202 | 0.0006969
2012 | 2011-08-21 | B | 86.6993 | 0.12355 | 0.00071878
2012 | 2011-08-15 | C | 46.2704 | 0.91576 | 0.00044064
2012 | 2011-08-15 | C | 16.0523 | 0.060299 | 0.00034064
2012 | 2011-08-19 | C | 53.9333 | 0.007079 | 0.00016876
2012 | 2011-08-17 | C | 567.77 | 0.17211 | 0.0025407
2012 | 2011-08-17 | C | 992.7917 | 0.065155 | 0.0051502
2012 | 2011-08-22 | B | 11.9877 | 0.0089911 | 3.7502e-05
2012 | 2011-08-22 | B | 14.9912 | 0.015835 | 4.6877e-05
2012 | 2011-08-22 | B | 42.9915 | 0.047293 | 0.00013438
2012 | 2011-08-23 | C | 66.9516 | 0.012345 | 0.00020938
2012 | 2011-08-23 | B | 6.9915 | 0.0076254 | 2.1876e-05
2012 | 2011-08-23 | C | 233.587 | 0.03139 | 0.0026376
2012 | 2011-08-23 | B | 36.9828 | 0.019763 | 0.00011563
2012 | 2011-08-23 | B | 29.9783 | 0.012648 | 9.3754e-05
2012 | 2011-08-23 | C | 15.9927 | 0.020292 | 5.0002e-05
2012 | 2011-08-24 | B | 42.9722 | 0.014101 | 0.00013438
2012 | 2011-08-23 | B | 4.9833 | 0.0027565 | 1.5626e-05
2012 | 2011-08-23 | B | 5.9889 | 0.0049972 | 1.8751e-05
2012 | 2011-08-23 | C | 708.4 | 0.0044277 | 0.0022157
2012 | 2011-08-23 | C | 148.4 | 0.00092754 | 0.00046564
2012 | 2011-08-23 | C | 2.9231 | 0.00032886 | 9.3754e-06
2012 | 2011-08-24 | C | 54.2601 | 0.037305 | 0.00042502
2012 | 2011-08-24 | B | 6.9907 | 0.0070129 | 2.1876e-05
2012 | 2011-08-24 | C | 489 | 0.010697 | 0.0016438
2012 | 2011-08-24 | C | 947.5448 | 0.42049 | 0.0041252
2012 | 2011-08-24 | C | 74.9694 | 0.022257 | 0.00023438
2012 | 2011-08-25 | B | 92.9851 | 0.057537 | 0.00029064
2012 | 2011-08-25 | B | 369.9854 | 0.23356 | 0.0011563
2012 | 2011-08-25 | B | 3.9844 | 0.0023534 | 1.2501e-05
2012 | 2011-08-26 | B | 24.976 | 0.0095225 | 7.8128e-05
2012 | 2011-08-26 | C | 1.1867 | 0.011292 | 2.8126e-05
2012 | 2011-08-26 | C | 1356.6667 | 0.025439 | 0.0042408
2012 | 2011-08-26 | C | 33.9492 | 0.0059413 | 0.00010625
2012 | 2011-08-27 | C | 94.8606 | 0.048025 | 0.00043439
2012 | 2011-08-27 | C | 13.7384 | 0.010047 | 0.002772
2012 | 2011-08-27 | C | 93.9784 | 0.039942 | 0.00029376
2012 | 2011-08-28 | C | 96.8125 | 0.0039332 | 0.00030314
2012 | 2011-08-28 | C | 265.1551 | 0.15247 | 0.0016376
2012 | 2011-08-29 | B | 42.9709 | 0.013429 | 0.00013438
2012 | 2011-08-26 | C | 2979.7 | 0.065184 | 0.0093129
2012 | 2011-08-26 | C | 898.7 | 0.01966 | 0.0028095
2012 | 2011-08-29 | B | 54.9833 | 0.030414 | 0.00017188
2012 | 2011-08-29 | B | 33.4222 | 0.013787 | 0.00017813
2012 | 2011-08-29 | B | 54.9908 | 0.05568 | 0.00017188
2012 | 2011-08-30 | C | 410.7805 | 0.048782 | 0.0016626
2012 | 2011-08-30 | B | 18.9912 | 0.020001 | 5.9377e-05
2012 | 2011-08-30 | B | 21.9571 | 0.0045975 | 6.8753e-05
2012 | 2011-08-30 | C | 1398.9 | 0.11804 | 0.0043721
2012 | 2011-08-30 | C | 11.9362 | 0.0016413 | 3.7502e-05
2012 | 2011-08-30 | B | 23.9875 | 0.017766 | 7.5003e-05
2012 | 2011-08-30 | C | 53.9739 | 0.018892 | 0.00016876
2012 | 2011-08-30 | C | 122.8 | 0.0046052 | 0.00038439
2012 | 2011-08-31 | C | 39.9905 | 0.039242 | 0.00012501
2012 | 2011-08-31 | C | 550.254 | 0.10318 | 0.00091254
2012 | 2011-09-01 | C | 419.625 | 0.0065569 | 0.0013126
2012 | 2011-08-31 | C | 35.9774 | 0.014616 | 0.0001125
2012 | 2011-08-31 | C | 40.9756 | 0.015366 | 0.00012813
2012 | 2011-08-23 | B | 18.9909 | 0.019288 | 5.9377e-05
2012 | 2011-09-01 | B | 62.9858 | 0.041139 | 0.00019688
2012 | 2011-09-01 | B | 2.9659 | 0.00078785 | 9.3754e-06
2012 | 2011-09-01 | B | 236.9822 | 0.12294 | 0.00074066
2012 | 2011-09-01 | C | 241.9806 | 0.11495 | 0.00075628
2012 | 2011-09-01 | B | 18.9934 | 0.026829 | 5.9377e-05
2012 | 2011-09-01 | B | 39.9844 | 0.023617 | 0.00012501
2012 | 2011-09-01 | C | 60.8846 | 0.0043763 | 0.00019063
2012 | 2011-09-01 | B | 18.8 | 0.00070503 | 5.9377e-05
2012 | 2011-09-01 | C | 9.94 | 0.00146 | 3.1251e-05
2012 | 2011-09-01 | B | 48.9921 | 0.057721 | 0.00015313
2012 | 2011-09-02 | B | 4.9838 | 0.0028346 | 1.5626e-05
2012 | 2011-09-02 | C | 187.1062 | 0.091803 | 0.00080003
2012 | 2011-09-02 | C | 123.8571 | 0.0069672 | 0.00038752
2012 | 2011-09-02 | B | 12.9812 | 0.0063692 | 4.0627e-05
2012 | 2011-09-03 | C | 462.313 | 0.18493 | 0.0019782
2012 | 2011-09-03 | C | 121.9918 | 0.13915 | 0.00038127
2012 | 2011-09-04 | C | 390.2866 | 0.19637 | 0.0024438
2012 | 2011-09-05 | B | 2.9815 | 0.0014815 | 9.3754e-06
2012 | 2011-09-05 | B | 5.975 | 0.0021847 | 1.8751e-05
2012 | 2011-09-05 | B | 11.991 | 0.012441 | 3.7502e-05
2012 | 2011-09-05 | B | 38.9727 | 0.013032 | 0.00012188
2012 | 2011-09-05 | C | 129.4405 | 0.032766 | 0.00043439
2012 | 2011-09-06 | B | 197.9709 | 0.061868 | 0.00061878
2012 | 2011-09-06 | C | 46.9677 | 0.01321 | 0.00014688
2012 | 2011-09-06 | B | 170.9189 | 0.018161 | 0.0005344
2012 | 2011-09-05 | B | 18.4538 | 0.022319 | 0.0001125
2012 | 2011-09-07 | B | 6.9902 | 0.0065972 | 2.1876e-05
2012 | 2011-09-08 | C | 19.9583 | 0.0043037 | 6.2503e-05
2012 | 2011-09-08 | C | 2.9831 | 0.0016315 | 9.3754e-06
2012 | 2011-09-09 | B | 17.9915 | 0.019735 | 5.6252e-05
2012 | 2011-09-09 | C | 12.7 | 0.00027782 | 4.0627e-05
2012 | 2011-09-09 | B | 31.9816 | 0.015991 | 0.0001
2012 | 2011-09-09 | C | 14.9062 | 0.0013509 | 4.6877e-05
2012 | 2011-09-09 | B | 30.9892 | 0.026632 | 9.6879e-05
2012 | 2011-09-09 | C | 12.875 | 0.00084496 | 4.0627e-05
2012 | 2011-09-09 | B | 57.9732 | 0.019748 | 0.00018126
2012 | 2011-09-09 | C | 265.129 | 0.048885 | 0.0010313
2012 | 2011-09-09 | C | 933.8 | 0.035019 | 0.0029189
2012 | 2011-09-10 | C | 202.8 | 0.0076053 | 0.0006344
2012 | 2011-09-10 | C | 90.6983 | 0.049886 | 0.00069065
2012 | 2011-09-11 | C | 52.8 | 0.0019801 | 0.00016563
2012 | 2011-09-11 | C | 25.9444 | 0.0041351 | 8.1253e-05
2012 | 2011-09-11 | C | 16.9722 | 0.0055692 | 5.3127e-05
2012 | 2011-09-11 | C | 10.9362 | 0.0015038 | 3.4376e-05
2012 | 2011-09-11 | C | 3.8235 | 0.00016729 | 1.2501e-05
2012 | 2011-09-11 | C | 453.4605 | 0.10345 | 0.0019001
2012 | 2011-09-11 | C | 91.6844 | 0.10172 | 0.00033439
2012 | 2011-09-11 | C | 623.8125 | 0.025343 | 0.0019501
2012 | 2011-09-11 | C | 131.973 | 0.044543 | 0.00041252
2012 | 2011-09-11 | C | 9.4523 | 0.034266 | 0.00062503
2012 | 2011-09-11 | C | 84.6117 | 0.080913 | 0.00074066
2012 | 2011-09-12 | B | 111.9813 | 0.054943 | 0.00035001
2012 | 2011-09-12 | B | 84.9851 | 0.052852 | 0.00026564
2012 | 2011-09-12 | C | 77.0275 | 0.025516 | 0.00025626
2012 | 2011-09-11 | C | 156.5176 | 0.65251 | 0.0031876
2012 | 2011-09-11 | C | 303.9 | 0.14911 | 0.0010125
2012 | 2011-09-12 | C | 339.4685 | 0.11458 | 0.0022563
2012 | 2011-09-12 | B | 24.9846 | 0.014991 | 7.8128e-05
2012 | 2011-09-12 | C | 90.875 | 0.0059639 | 0.00028439
2012 | 2011-09-12 | C | 27.9143 | 0.0027915 | 8.7504e-05
2012 | 2011-09-12 | C | 239.9211 | 0.026242 | 0.00075003
2012 | 2011-09-12 | C | 18.8235 | 0.00082356 | 5.9377e-05
2012 | 2011-09-12 | C | 9.9899 | 0.0091473 | 3.1251e-05
2012 | 2011-09-12 | C | 763.9853 | 0.4799 | 0.0023876
2012 | 2011-09-13 | C | 192.8537 | 0.12174 | 0.0011625
2012 | 2011-09-12 | C | 159.6818 | 0.25101 | 0.0019001
2012 | 2011-09-13 | C | 785.9444 | 0.036843 | 0.0031783
2012 | 2011-09-13 | C | 28.9538 | 0.00561 | 9.0629e-05
2012 | 2011-09-12 | C | 299.8909 | 0.15183 | 0.0016282
2012 | 2011-09-12 | C | 287.9793 | 0.1278 | 0.00090004
2012 | 2011-09-13 | C | 98.4138 | 0.097188 | 0.0005594
2012 | 2011-09-13 | C | 533.8125 | 0.021687 | 0.0016688
2012 | 2011-09-13 | C | 97.9516 | 0.018061 | 0.00030626
2012 | 2011-09-13 | C | 74.9318 | 0.009601 | 0.00023438
2012 | 2011-09-13 | C | 18.048 | 0.069205 | 9.0629e-05
2012 | 2011-09-13 | C | 1.9538 | 0.00037857 | 6.2503e-06
2012 | 2011-09-13 | C | 317.4492 | 0.11409 | 0.0014751
2012 | 2011-09-13 | C | 114.8696 | 0.0071796 | 0.00035939
2012 | 2011-09-13 | C | 30.9727 | 0.010357 | 9.6879e-05
2012 | 2011-09-13 | C | 295.9597 | 0.13504 | 0.0013594
2012 | 2011-09-13 | C | 114.9 | 0.0096951 | 0.00035939
2012 | 2011-09-14 | C | 623.8421 | 0.031193 | 0.0019501
2012 | 2011-09-14 | C | 114.9931 | 0.15489 | 0.00035939
2012 | 2011-09-14 | C | 5997.0143 | 1.2557 | 0.020988
2012 | 2011-09-14 | C | 4379.9625 | 1.054 | 0.013688
2012 | 2011-09-14 | C | 641.8 | 0.024068 | 0.0023501
2012 | 2011-09-14 | C | 185.3967 | 0.10487 | 0.00091879
2012 | 2011-09-14 | C | 211.9236 | 0.093383 | 0.00074066
2012 | 2011-09-14 | C | 6715.7692 | 0.20988 | 0.020988
2012 | 2011-09-14 | C | 4379.75 | 0.12319 | 0.013688
2012 | 2011-09-14 | C | 55.9455 | 0.0090915 | 0.00017501
2012 | 2011-09-14 | C | 195.9515 | 0.099204 | 0.00092191
2012 | 2011-09-14 | C | 43.8 | 0.0016426 | 0.00013751
2012 | 2011-09-15 | C | 301.9706 | 0.029255 | 0.00099692
2012 | 2011-09-14 | C | 17.5094 | 0.037647 | 0.00034064
2012 | 2011-09-14 | C | 60.3265 | 0.0641 | 0.00024689
2012 | 2011-09-14 | C | 243.97 | 0.073956 | 0.00076253
2012 | 2011-09-14 | C | 562.9143 | 0.056294 | 0.0017594
2012 | 2011-09-14 | C | 68.5714 | 0.00085718 | 0.00021563
2012 | 2011-09-15 | C | 4.9286 | 0.00060069 | 1.5626e-05
2012 | 2011-09-15 | C | 13.9923 | 0.016835 | 4.3752e-05
2012 | 2011-09-15 | C | 32.9118 | 0.0031885 | 0.00010313
2012 | 2011-09-15 | C | 162.039 | 0.037473 | 0.00077816
2012 | 2011-09-16 | C | 60.9211 | 0.0066635 | 0.00019063
2012 | 2011-09-16 | C | 155.9348 | 0.020955 | 0.00048752
2012 | 2011-09-17 | C | 287.5309 | 0.14287 | 0.0029376
2012 | 2011-09-18 | C | 288.2667 | 0.05135 | 0.0022595
2012 | 2011-09-19 | C | 131.1322 | 0.070077 | 0.00085316
2012 | 2011-09-19 | C | 791.8904 | 0.17323 | 0.0041283
2012 | 2011-09-19 | C | 861.8696 | 0.053869 | 0.0026939
2012 | 2011-09-19 | C | 840.875 | 0.055185 | 0.0026282
2012 | 2011-09-19 | C | 22.3999 | 0.099753 | 0.00033126
2012 | 2011-09-20 | B | 69.6 | 0.0015226 | 0.00024376
2012 | 2011-09-21 | B | 42.9167 | 0.004426 | 0.00013438
2012 | 2011-09-21 | B | 40.9911 | 0.042914 | 0.00012813
2012 | 2011-09-21 | C | 2.9901 | 0.002794 | 9.3754e-06
2012 | 2011-09-21 | C | 15.9062 | 0.0014416 | 5.0002e-05
2012 | 2011-09-21 | B | 1.9854 | 0.0012533 | 6.2503e-06
2012 | 2011-09-22 | B | 48.985 | 0.030158 | 0.00015313
2012 | 2011-09-22 | B | 4.9919 | 0.0057253 | 1.5626e-05
2012 | 2011-09-24 | C | 28.9538 | 0.00561 | 9.0629e-05
2012 | 2011-09-25 | C | 23.875 | 0.0015669 | 7.5003e-05
2012 | 2011-09-26 | C | 30.8966 | 0.0025104 | 9.6879e-05
2012 | 2011-09-26 | B | 29.9589 | 0.0065538 | 9.3754e-05
2012 | 2011-09-27 | C | 45.9538 | 0.0089039 | 0.00014376
2012 | 2011-09-27 | C | 23.95 | 0.0042663 | 7.5003e-05
2012 | 2011-09-27 | C | 1236.9333 | 0.16235 | 0.0038658
2012 | 2011-09-27 | C | 257.4697 | 0.27679 | 0.0037095
2012 | 2011-09-28 | C | 205.2646 | 0.14113 | 0.00087191
2012 | 2011-09-28 | C | 235.9444 | 0.037605 | 0.00073753
2012 | 2011-09-29 | C | 16.9333 | 0.0022226 | 5.3127e-05
2012 | 2011-09-30 | C | 4.9625 | 0.0011942 | 1.5626e-05
2012 | 2011-09-30 | B | 1.95 | 0.00034736 | 6.2503e-06
2012 | 2011-10-01 | C | 119.9268 | 0.014242 | 0.00037502
2012 | 2011-10-01 | C | 493.9268 | 0.058656 | 0.0015438
2012 | 2011-10-02 | C | 436.8478 | 0.3099 | 0.0020563
2012 | 2011-10-02 | C | 2.9388 | 0.00042247 | 9.3754e-06
2012 | 2011-10-02 | C | 177.8125 | 0.0072239 | 0.00055627
2012 | 2011-10-03 | C | 57.9189 | 0.0061541 | 0.00018126
2012 | 2011-10-03 | B | 17.9778 | 0.0074161 | 5.6252e-05
2012 | 2011-10-04 | C | 142.8 | 0.0053552 | 0.00044689
2012 | 2011-10-03 | C | 63.8 | 0.0023926 | 0.00020001
2012 | 2011-10-03 | C | 1453.9674 | 0.4044 | 0.0045439
2012 | 2011-10-03 | C | 46.9927 | 0.060212 | 0.00014688
2012 | 2011-10-03 | C | 46.9778 | 0.019379 | 0.00014688
2012 | 2011-10-03 | C | 304.8 | 0.01143 | 0.00095316
2012 | 2011-10-04 | B | 1.9639 | 0.00049098 | 6.2503e-06
2012 | 2011-10-03 | B | 28.9799 | 0.013223 | 9.0629e-05
2012 | 2011-10-03 | C | 1.9118 | 0.00018521 | 6.2503e-06
2012 | 2011-10-03 | C | 126.5494 | 0.062882 | 0.001125
2012 | 2011-10-04 | C | 6.75 | 0.00018985 | 2.1876e-05
2012 | 2011-10-04 | B | 12.9889 | 0.010838 | 4.0627e-05
2012 | 2011-10-03 | C | 1.8315 | 0.0061987 | 6.2503e-06
2012 | 2011-10-04 | C | 94.6032 | 0.073616 | 0.00075316
2012 | 2011-10-04 | C | 59.6235 | 0.029627 | 0.00064378
2012 | 2011-10-04 | C | 2.9434 | 0.00045992 | 9.3754e-06
2012 | 2011-10-03 | C | 41.0136 | 0.11254 | 0.00040627
2012 | 2011-10-05 | C | 13.925 | 0.0016101 | 4.3752e-05
2012 | 2011-10-04 | C | 129.8 | 0.0048677 | 0.00040627
2012 | 2011-10-03 | C | 92.5672 | 0.40153 | 0.00093754
2012 | 2011-10-05 | B | 55.9885 | 0.044968 | 0.00017501
2012 | 2011-10-05 | C | 748.9062 | 0.067872 | 0.0023407
2012 | 2011-10-06 | C | 394.338 | 0.0838 | 0.0014563
2012 | 2011-10-06 | C | 14.95 | 0.0026631 | 4.6877e-05
2012 | 2011-10-06 | B | 16.9854 | 0.010722 | 5.3127e-05
2012 | 2011-10-06 | C | 266.9074 | 0.04254 | 0.0027501
2012 | 2011-10-06 | B | 6.9857 | 0.0045191 | 2.1876e-05
2012 | 2011-10-06 | C | 90.8 | 0.0034051 | 0.00028439
2012 | 2011-10-06 | C | 47.9062 | 0.0043417 | 0.00015001
2012 | 2011-10-06 | C | 38.9483 | 0.0066945 | 0.00012188
2012 | 2011-10-06 | B | 58.9907 | 0.058624 | 0.00018438
2012 | 2011-10-06 | C | 164.925 | 0.01907 | 0.00051565
2012 | 2011-10-06 | C | 44.5045 | 0.10765 | 0.0011657
2012 | 2011-10-06 | C | 270.3148 | 0.088701 | 0.0013063
2012 | 2011-10-07 | B | 19.9286 | 0.0024289 | 6.2503e-05
2012 | 2011-10-07 | C | 3.9854 | 0.0025284 | 1.2501e-05
2012 | 2011-10-08 | C | 92.5114 | 0.062448 | 0.00078753
2012 | 2011-10-08 | C | 134.7007 | 0.17175 | 0.001922
2012 | 2011-10-08 | C | 252.5889 | 0.32601 | 0.0021126
2012 | 2011-10-08 | C | 365.9571 | 0.076625 | 0.0013063
2012 | 2011-10-08 | C | 489.5484 | 0.042837 | 0.002172
2012 | 2011-10-08 | C | 289.9032 | 0.025368 | 0.00090629
2012 | 2011-10-08 | C | 62.9639 | 0.015742 | 0.00019688
2012 | 2011-10-08 | C | 22.9714 | 0.0073224 | 7.1878e-05
2012 | 2011-10-09 | C | 15.8235 | 0.00069231 | 5.0002e-05
2012 | 2011-10-09 | C | 414.1688 | 0.09578 | 0.0014626
2012 | 2011-10-10 | C | 61.9712 | 0.01956 | 0.00019376
2012 | 2011-10-10 | C | 48.9605 | 0.01117 | 0.00015313
2012 | 2011-10-11 | C | 678.4853 | 0.13782 | 0.0032158
2012 | 2011-10-10 | C | 166.6589 | 0.065625 | 0.0011563
2012 | 2011-10-10 | C | 18.9789 | 0.0082443 | 5.9377e-05
2012 | 2011-10-11 | B | 2.9864 | 0.0020252 | 9.3754e-06
2012 | 2011-10-11 | C | 18.8636 | 0.0011201 | 5.9377e-05
2012 | 2011-10-10 | C | 9.6521 | 0.029651 | 0.00012501
2012 | 2011-10-11 | C | 68.9824 | 0.036002 | 0.00021563
2012 | 2011-10-11 | C | 74.5498 | 0.062438 | 0.00045314
2012 | 2011-10-12 | C | 419.7297 | 0.093131 | 0.0019438
2012 | 2011-10-12 | C | 69.603 | 0.071128 | 0.00044689
2012 | 2011-10-12 | C | 15.9 | 0.0013416 | 5.0002e-05
2012 | 2011-10-12 | C | 54.5018 | 0.046669 | 0.00040627
2012 | 2011-10-12 | C | 31.8421 | 0.0015922 | 0.0001
2012 | 2011-10-12 | C | 14.9739 | 0.0052411 | 4.6877e-05
2012 | 2011-10-12 | C | 22.9118 | 0.0022197 | 7.1878e-05
2012 | 2011-10-12 | C | 69.7598 | 0.12187 | 0.0010532
2012 | 2011-10-12 | C | 288.3466 | 0.15589 | 0.0016032
2012 | 2011-10-13 | C | 2.9362 | 0.00040374 | 9.3754e-06
2012 | 2011-10-13 | C | 216.1765 | 0.14728 | 0.0020688
2012 | 2011-10-13 | C | 3.9423 | 0.00060369 | 1.2501e-05
2012 | 2011-10-12 | C | 17.0798 | 0.076115 | 0.00026251
2012 | 2011-10-13 | B | 18.9871 | 0.013648 | 5.9377e-05
2012 | 2011-10-13 | C | 3.9871 | 0.0028534 | 1.2501e-05
2012 | 2011-10-13 | B | 14.9904 | 0.014476 | 4.6877e-05
2012 | 2011-10-13 | C | 28.9062 | 0.0026197 | 9.0629e-05
2012 | 2011-10-14 | C | 1.99 | 0.0018533 | 6.2503e-06
2012 | 2011-10-16 | B | 314.9 | 0.026571 | 0.00098441
2012 | 2011-10-16 | C | 59.3187 | 0.071 | 0.00039689
2012 | 2011-10-16 | C | 68.9615 | 0.016164 | 0.00021563
2012 | 2011-10-17 | C | 322.7472 | 0.17651 | 0.0028376
2012 | 2011-10-13 | B | 27.975 | 0.010229 | 8.7504e-05
2012 | 2011-10-17 | C | 96.237 | 0.10316 | 0.00061878
2012 | 2011-10-17 | C | 299.2109 | 0.11688 | 0.0019532
2012 | 2011-10-17 | C | 10.94 | 0.0016069 | 3.4376e-05
2012 | 2011-10-18 | C | 197.5299 | 0.080867 | 0.0019563
2012 | 2011-10-18 | C | 143.7263 | 0.041323 | 0.00053752
2012 | 2011-10-18 | B | 81.982 | 0.042018 | 0.00025626
2012 | 2011-10-18 | C | 1.97 | 0.00059718 | 6.2503e-06
2012 | 2011-10-18 | B | 13.9886 | 0.01141 | 4.3752e-05
2012 | 2011-10-18 | C | 316.9375 | 0.044571 | 0.00099067
2012 | 2011-10-18 | C | 7.9727 | 0.002666 | 2.5001e-05
2012 | 2011-10-18 | B | 27.9918 | 0.031579 | 8.7504e-05
2012 | 2011-10-18 | B | 28.9908 | 0.029173 | 9.0629e-05
2012 | 2011-10-18 | C | 110.9615 | 0.053056 | 0.002447
2012 | 2011-10-18 | C | 150.8333 | 0.0070706 | 0.00047189
2012 | 2011-10-18 | C | 35.9189 | 0.0038165 | 0.0001125
2012 | 2011-10-19 | C | 340.8 | 0.012781 | 0.0010657
2012 | 2011-10-19 | C | 358.8 | 0.013456 | 0.0011219
2012 | 2011-10-19 | C | 340.9062 | 0.030896 | 0.0010657
2012 | 2011-10-19 | C | 358.9062 | 0.032527 | 0.0011219
2012 | 2011-10-19 | C | 7.995 | 0.015041 | 2.5001e-05
2012 | 2011-10-19 | C | 69.9444 | 0.011148 | 0.00021876
2012 | 2011-10-18 | B | 4.9895 | 0.0044284 | 1.5626e-05
2012 | 2011-10-19 | C | 15.96 | 0.0035911 | 5.0002e-05
2012 | 2011-10-19 | B | 27.9913 | 0.029829 | 8.7504e-05
2012 | 2011-10-19 | B | 12.9717 | 0.0041754 | 4.0627e-05
2012 | 2011-10-20 | C | 220.75 | 0.0062088 | 0.00069065
2012 | 2011-10-20 | C | 676.7 | 0.014803 | 0.0021157
2012 | 2011-10-20 | C | 8.9786 | 0.0038441 | 2.8126e-05
2012 | 2011-10-20 | C | 7.9846 | 0.004791 | 2.5001e-05
2012 | 2011-10-20 | C | 28.9474 | 0.0048851 | 9.0629e-05
2012 | 2011-10-20 | B | 7.9908 | 0.008066 | 2.5001e-05
2012 | 2011-10-20 | B | 29.9888 | 0.024929 | 9.3754e-05
2012 | 2011-10-20 | B | 11.9914 | 0.012966 | 3.7502e-05
2012 | 2011-10-20 | C | 19.6014 | 0.017336 | 0.00026251
2012 | 2011-10-21 | B | 4.9811 | 0.0024284 | 1.5626e-05
2012 | 2011-10-21 | C | 1.94 | 0.00028495 | 6.2503e-06
2012 | 2011-10-21 | C | 62.8929 | 0.0049137 | 0.00019688
2012 | 2011-10-21 | B | 5.9832 | 0.0032909 | 1.8751e-05
2012 | 2011-10-22 | C | 38.9694 | 0.01157 | 0.00012188
2012 | 2011-10-22 | C | 1.9231 | 0.00021635 | 6.2503e-06
2012 | 2011-10-22 | C | 230.3765 | 0.11447 | 0.00095941
2012 | 2011-10-22 | C | 133.1732 | 0.073248 | 0.00073128
2012 | 2011-10-22 | C | 220.9268 | 0.026236 | 0.00069065
2012 | 2011-10-22 | C | 42.9 | 0.0036198 | 0.00013438
2012 | 2011-10-25 | B | 12.9875 | 0.0096193 | 4.0627e-05
2012 | 2011-10-25 | C | 101.5738 | 0.076501 | 0.00072815
2012 | 2011-10-20 | B | 1.9939 | 0.0030533 | 6.2503e-06
2012 | 2011-10-25 | B | 5.9848 | 0.0036472 | 1.8751e-05
2012 | 2011-10-25 | C | 50.9881 | 0.039677 | 0.00015938
2012 | 2011-10-26 | B | 2.9897 | 0.0026815 | 9.3754e-06
2012 | 2011-10-26 | B | 1.9909 | 0.0020283 | 6.2503e-06
2012 | 2011-10-26 | C | 1144.3205 | 0.26821 | 0.0045408
2012 | 2011-10-26 | B | 7.9897 | 0.007191 | 2.5001e-05
2012 | 2011-10-26 | B | 26.987 | 0.019145 | 8.4378e-05
2012 | 2011-10-26 | C | 4.9876 | 0.0037096 | 1.5626e-05
2012 | 2011-10-26 | C | 142.8 | 0.0053552 | 0.00044689
2012 | 2011-10-26 | C | 32.9709 | 0.10232 | 0.00097191
2012 | 2011-10-26 | C | 273.8654 | 0.086442 | 0.0011157
2012 | 2011-10-26 | C | 90.4299 | 0.061608 | 0.0010313
2012 | 2011-10-27 | C | 200.5806 | 0.09528 | 0.00073753
2012 | 2011-10-27 | C | 30.9838 | 0.017623 | 9.6879e-05
2012 | 2011-10-27 | B | 12.9804 | 0.0060848 | 4.0627e-05
2012 | 2011-10-27 | B | 1.9901 | 0.001872 | 6.2503e-06
2012 | 2011-10-27 | B | 20.9888 | 0.017448 | 6.5628e-05
2012 | 2011-10-27 | B | 7.9922 | 0.0095911 | 2.5001e-05
2012 | 2011-10-28 | C | 478.8 | 0.017956 | 0.0014969
2012 | 2011-10-28 | C | 58.8058 | 0.018378 | 0.00018751
2012 | 2011-10-28 | C | 172.6745 | 0.18239 | 0.0028032
2012 | 2011-10-28 | B | 4.9667 | 0.0013504 | 1.5626e-05
2012 | 2011-10-28 | C | 81.9774 | 0.033305 | 0.00033439
2012 | 2011-10-28 | C | 18.9651 | 0.0049193 | 5.9377e-05
2012 | 2011-10-29 | C | 304.9545 | 0.06004 | 0.00095316
2012 | 2011-10-29 | B | 7.9737 | 0.002766 | 2.5001e-05
2012 | 2011-10-29 | C | 159.3977 | 0.042342 | 0.00058127
2012 | 2011-10-29 | C | 21.9722 | 0.054109 | 0.00026876
2012 | 2011-10-30 | C | 15.9881 | 0.012441 | 5.0002e-05
2012 | 2011-10-30 | C | 968.7 | 0.021191 | 0.0030282
2012 | 2011-10-30 | C | 178.8235 | 0.0078238 | 0.0005594
2012 | 2011-10-30 | C | 304.5989 | 0.17515 | 0.0020345
2012 | 2011-10-31 | B | 5.9827 | 0.0031784 | 1.8751e-05
2012 | 2011-10-31 | C | 110.1173 | 0.17792 | 0.0012501
2012 | 2011-11-01 | C | 616.85 | 0.032771 | 0.0019282
2012 | 2011-11-01 | B | 14.9892 | 0.012882 | 4.6877e-05
2012 | 2011-11-01 | C | 412.4051 | 0.09795 | 0.0019626
2012 | 2011-11-01 | C | 86.7417 | 0.031716 | 0.00063128
2012 | 2011-11-01 | C | 27.9412 | 0.0041913 | 8.7504e-05
2012 | 2011-11-01 | C | 23.9189 | 0.0025415 | 7.5003e-05
2012 | 2011-11-02 | C | 83.561 | 0.05275 | 0.00057502
2012 | 2011-11-02 | C | 22.0464 | 0.033967 | 0.00043127
2012 | 2011-11-02 | C | 4.9667 | 0.0013504 | 1.5626e-05
2012 | 2011-11-02 | C | 61.8636 | 0.0036733 | 0.00019376
2012 | 2011-11-02 | C | 45.8571 | 0.0025796 | 0.00014376
2012 | 2011-11-02 | C | 60.0023 | 0.081006 | 0.00034376
2012 | 2011-11-03 | C | 194.4318 | 0.15859 | 0.0012876
2012 | 2011-11-03 | C | 53.9739 | 0.018892 | 0.00016876
2012 | 2011-11-03 | B | 16.9916 | 0.018798 | 5.3127e-05
2012 | 2011-11-03 | C | 18.9464 | 0.0031381 | 5.9377e-05
2012 | 2011-11-03 | C | 65.9118 | 0.0063855 | 0.00020626
2012 | 2011-11-03 | B | 11.9889 | 0.010004 | 3.7502e-05
2012 | 2011-11-03 | C | 30.9211 | 0.0033821 | 9.6879e-05
2012 | 2011-11-04 | B | 7.9874 | 0.005866 | 2.5001e-05
2012 | 2011-11-04 | C | 145.9497 | 0.071153 | 0.0005219
2012 | 2011-11-04 | C | 43.9439 | 0.014282 | 0.00016563
2012 | 2011-11-04 | C | 183.9435 | 0.13049 | 0.00093129
2012 | 2011-11-04 | C | 60.4621 | 0.049316 | 0.00040002
2012 | 2011-11-04 | C | 93.6154 | 0.052368 | 0.00033439
2012 | 2011-11-04 | C | 250.2667 | 0.056312 | 0.00078441
2012 | 2011-11-04 | C | 36.3887 | 0.090066 | 0.00055627
2012 | 2011-11-05 | C | 54.9659 | 0.014601 | 0.00017188
2012 | 2011-11-05 | C | 250.9286 | 0.030583 | 0.00078441
2012 | 2011-11-05 | B | 2.9877 | 0.0022502 | 9.3754e-06
2012 | 2011-11-06 | C | 414.0667 | 0.015528 | 0.0061346
2012 | 2011-11-06 | B | 39.996 | 0.093119 | 0.00012501
2012 | 2011-11-06 | C | 942.2581 | 0.44759 | 0.0057315
2012 | 2011-11-07 | C | 210.6218 | 0.33569 | 0.0034345
2012 | 2011-11-07 | B | 51.9758 | 0.019654 | 0.00016251
2012 | 2011-11-06 | C | 494.7857 | 0.017009 | 0.0056346
2012 | 2011-11-07 | B | 39.9861 | 0.026617 | 0.00012501
2012 | 2011-11-07 | B | 3.9864 | 0.0027034 | 1.2501e-05
2012 | 2011-11-06 | C | 1.998 | 0.0093473 | 6.2503e-06
2012 | 2011-11-07 | B | 50.96 | 0.011466 | 0.00015938
2012 | 2011-11-07 | B | 4.9929 | 0.0065222 | 1.5626e-05
2012 | 2011-11-07 | C | 1146.2393 | 0.40836 | 0.0036376
2012 | 2011-11-07 | C | 649.0192 | 0.52126 | 0.002897
2012 | 2011-11-08 | C | 2574.7857 | 0.088512 | 0.0080472
2012 | 2011-11-08 | C | 1061.8125 | 0.043138 | 0.0033189
2012 | 2011-11-08 | C | 6459.5435 | 0.86804 | 0.025398
2012 | 2011-11-08 | B | 20.9919 | 0.024076 | 6.5628e-05
2012 | 2011-11-08 | C | 157.3645 | 0.1618 | 0.0024657
2012 | 2011-11-08 | C | 29.9659 | 0.00796 | 9.3754e-05
2012 | 2011-11-08 | B | 52.9268 | 0.0062853 | 0.00016563
2012 | 2011-11-08 | C | 563.6667 | 0.010569 | 0.0017626
2012 | 2011-11-08 | C | 4858.6 | 0.030367 | 0.024588
2012 | 2011-11-08 | C | 2339.7692 | 0.073121 | 0.0073128
2012 | 2011-11-08 | C | 276.7692 | 0.0086494 | 0.00086566
2012 | 2011-11-09 | C | 1132.7 | 0.024779 | 0.0035408
2012 | 2011-11-09 | B | 20.9894 | 0.018366 | 6.5628e-05
2012 | 2011-11-09 | B | 20.9926 | 0.026439 | 6.5628e-05
2012 | 2011-11-09 | C | 18.9732 | 0.006463 | 5.9377e-05
2012 | 2011-11-09 | C | 207.1884 | 0.042734 | 0.00073753
2012 | 2011-11-10 | C | 178.9524 | 0.033555 | 0.0005594
2012 | 2011-11-10 | C | 25.74 | 0.046173 | 0.00026876
2012 | 2011-11-10 | C | 21.9434 | 0.0034288 | 6.8753e-05
2012 | 2011-11-10 | C | 9.9746 | 0.0035848 | 3.1251e-05
2012 | 2011-11-10 | C | 2.9565 | 0.00060981 | 9.3754e-06
2012 | 2011-11-10 | C | 176.8235 | 0.0077363 | 0.00055315
2012 | 2011-11-10 | C | 2450.2083 | 0.1608 | 0.0080441
2012 | 2011-11-10 | C | 118.95 | 0.021189 | 0.00037189
2012 | 2011-11-10 | C | 419.3187 | 0.11532 | 0.0022095
2012 | 2011-11-10 | C | 1050.9545 | 0.062403 | 0.0033189
2012 | 2011-11-10 | C | 234.3544 | 0.20653 | 0.0031845
2012 | 2011-11-10 | C | 1.991 | 0.0020595 | 6.2503e-06
2012 | 2011-11-11 | C | 4.9764 | 0.0019284 | 1.5626e-05
2012 | 2011-11-09 | B | 10.9882 | 0.0086536 | 3.4376e-05
2012 | 2011-11-09 | B | 64.94 | 0.0095384 | 0.00020313
2012 | 2011-11-11 | C | 32.925 | 0.0038071 | 0.00010313
2012 | 2011-11-10 | B | 3.9856 | 0.0025659 | 1.2501e-05
2012 | 2011-11-10 | B | 20.9663 | 0.0056349 | 6.5628e-05
2012 | 2011-11-10 | B | 4.9867 | 0.0034596 | 1.5626e-05
2012 | 2011-11-12 | C | 22.8696 | 0.0014294 | 7.1878e-05
2012 | 2011-11-12 | C | 133.6122 | 0.19041 | 0.0011188
2012 | 2011-11-12 | C | 128.6491 | 0.067544 | 0.0011188
2012 | 2011-11-12 | C | 106.5523 | 0.12321 | 0.00095316
2012 | 2011-11-12 | C | 2.9767 | 0.0011721 | 9.3754e-06
2012 | 2011-11-13 | C | 53.9725 | 0.017879 | 0.00016876
2012 | 2011-11-13 | B | 2.9674 | 0.00082534 | 9.3754e-06
2012 | 2011-11-14 | C | 85.7775 | 0.1016 | 0.0011782
2012 | 2011-11-14 | C | 64.9595 | 0.014413 | 0.00020313
2012 | 2011-11-14 | B | 3.1629 | 0.0034299 | 1.2501e-05
2012 | 2011-11-14 | B | 31.9915 | 0.034792 | 0.0001
2012 | 2011-11-14 | B | 4.9907 | 0.0049909 | 1.5626e-05
2012 | 2011-11-14 | C | 33 | 0.037333 | 0.00013126
2012 | 2011-11-14 | C | 99.94 | 0.014679 | 0.00031251
2012 | 2011-11-15 | B | 112.9922 | 0.13489 | 0.00035314
2012 | 2011-11-15 | C | 29.9 | 0.0025229 | 9.3754e-05
2012 | 2011-11-15 | C | 26.88 | 0.0018481 | 8.4378e-05
2012 | 2011-11-16 | B | 89.9854 | 0.056806 | 0.00028126
2012 | 2011-11-16 | C | 4.97 | 0.0015066 | 1.5626e-05
2012 | 2011-11-16 | C | 50.7189 | 0.053099 | 0.00044377
2012 | 2011-11-16 | C | 252.5571 | 0.27388 | 0.0022188
2012 | 2011-11-16 | B | 7.9896 | 0.007141 | 2.5001e-05
2012 | 2011-11-16 | B | 6.9852 | 0.0043659 | 2.1876e-05
2012 | 2011-11-16 | C | 116.1963 | 0.13763 | 0.0029001
2012 | 2011-11-16 | C | 43.963 | 0.010716 | 0.00013751
2012 | 2011-11-16 | C | 3.9778 | 0.0016409 | 1.2501e-05
2012 | 2011-11-10 | B | 20.9929 | 0.027423 | 6.5628e-05
2012 | 2011-11-07 | B | 20.9913 | 0.022304 | 6.5628e-05
2012 | 2011-11-03 | B | 17.9921 | 0.021254 | 5.6252e-05
2012 | 2011-11-17 | C | 174.9412 | 0.026242 | 0.0005469
2012 | 2011-11-17 | B | 89.9571 | 0.018836 | 0.00028126
2012 | 2011-11-17 | B | 19.992 | 0.023242 | 6.2503e-05
2012 | 2011-11-17 | C | 1.9659 | 0.00052222 | 6.2503e-06
2012 | 2011-11-17 | B | 16.9918 | 0.019276 | 5.3127e-05
2012 | 2011-11-18 | C | 734.5714 | 0.0091825 | 0.002297
2012 | 2011-11-18 | C | 105.54 | 0.048484 | 0.00051565
2012 | 2011-11-18 | C | 1.9423 | 0.00029743 | 6.2503e-06
2012 | 2011-11-18 | B | 6.988 | 0.005416 | 2.1876e-05
2012 | 2011-11-18 | C | 473.4355 | 0.087293 | 0.0023032
2012 | 2011-11-18 | C | 178.8889 | 0.013417 | 0.0005594
2012 | 2011-11-18 | C | 739.1562 | 0.066989 | 0.0024626
2012 | 2011-11-18 | C | 215.9412 | 0.032392 | 0.0024626
2012 | 2011-11-19 | C | 294.2398 | 0.17747 | 0.0024438
2012 | 2011-11-19 | C | 67.6214 | 0.021133 | 0.0011313
2012 | 2011-11-20 | C | 106.3182 | 0.0721 | 0.00042502
2012 | 2011-11-20 | C | 92.8929 | 0.0072575 | 0.00029064
2012 | 2011-11-21 | B | 11.9886 | 0.0097786 | 3.7502e-05
2012 | 2011-11-21 | B | 7.9921 | 0.0093661 | 2.5001e-05
2012 | 2011-11-21 | C | 234.9091 | 0.022024 | 0.0007344
2012 | 2011-11-21 | C | 54.875 | 0.0036013 | 0.00017188
2012 | 2011-11-21 | C | 2.1736 | 0.0084706 | 0.00015626
2012 | 2011-11-21 | C | 97.3202 | 0.060828 | 0.0016688
2012 | 2011-11-21 | C | 107.9388 | 0.015517 | 0.00033751
2012 | 2011-11-21 | C | 66.0099 | 0.10356 | 0.0010188
2012 | 2011-11-22 | C | 77.9935 | 0.11115 | 0.00024376
2012 | 2011-11-22 | C | 52.925 | 0.0061197 | 0.00016563
2012 | 2011-11-22 | C | 11.9375 | 0.0016788 | 3.7502e-05
2012 | 2011-11-21 | C | 149.95 | 0.026711 | 0.00046877
2012 | 2011-11-22 | C | 64.5 | 0.00060471 | 0.00020313
2012 | 2011-11-22 | C | 176.9434 | 0.027649 | 0.00055315
2012 | 2011-11-21 | C | 173.9858 | 0.11364 | 0.00054377
2012 | 2011-11-21 | C | 79.9302 | 0.0099917 | 0.00025001
2012 | 2011-11-21 | C | 148.5613 | 0.070569 | 0.00055627
2012 | 2011-11-21 | C | 117.0787 | 0.06403 | 0.00062503
2012 | 2011-11-21 | C | 340.219 | 0.14247 | 0.0024438
2012 | 2011-11-21 | C | 153.4433 | 0.09159 | 0.00052502
2012 | 2011-11-21 | C | 70.2257 | 0.055744 | 0.00072815
2012 | 2011-11-21 | C | 106.4049 | 0.081137 | 0.00077816
2012 | 2011-11-21 | C | 126.8566 | 0.19505 | 0.0012313
2012 | 2011-11-22 | C | 20.9839 | 0.012001 | 6.5628e-05
2012 | 2011-11-22 | C | 37.875 | 0.0024856 | 0.00011875
2012 | 2011-11-21 | C | 122.9727 | 0.041121 | 0.00038439
2012 | 2011-11-21 | C | 226.9901 | 0.2121 | 0.0007094
2012 | 2011-11-21 | C | 83.4247 | 0.037282 | 0.00040939
2012 | 2011-11-21 | C | 14.9706 | 0.0046317 | 4.6877e-05
2012 | 2011-11-21 | C | 176.8571 | 0.0099486 | 0.00055315
2012 | 2011-11-21 | C | 61.4049 | 0.038763 | 0.00078753
2012 | 2011-11-21 | C | 304.25 | 0.00095082 | 0.00095316
2012 | 2011-11-21 | C | 565.8571 | 0.031831 | 0.0017688
2012 | 2011-11-21 | C | 46.7251 | 0.047895 | 0.00067815
2012 | 2011-11-21 | C | 56.0077 | 0.022229 | 0.00056252
2012 | 2011-11-22 | C | 16.8125 | 0.00068304 | 5.3127e-05
2012 | 2011-11-22 | C | 29.0909 | 0.0067275 | 0.00068753
2012 | 2011-11-22 | C | 13.94 | 0.0020475 | 4.3752e-05
2012 | 2011-11-21 | C | 2.9976 | 0.011776 | 9.3754e-06
2012 | 2011-11-22 | C | 2.9781 | 0.0012471 | 9.3754e-06
2012 | 2011-11-23 | B | 7.9926 | 0.010066 | 2.5001e-05
2012 | 2011-11-22 | B | 6.9926 | 0.0087848 | 2.1876e-05
2012 | 2011-11-21 | C | 35.4584 | 0.084993 | 0.00021251
2012 | 2011-11-22 | B | 17.982 | 0.0092162 | 5.6252e-05
2012 | 2011-11-21 | C | 13.957 | 0.067869 | 0.00040002
2012 | 2011-11-21 | C | 44.94 | 0.0066008 | 0.00014063
2012 | 2011-11-22 | C | 146.1592 | 0.14205 | 0.0015782
2012 | 2011-11-22 | C | 156.5075 | 0.22695 | 0.00050627
2012 | 2011-11-22 | C | 5.96 | 0.0013411 | 1.8751e-05
2012 | 2011-11-22 | C | 57.7273 | 0.0014432 | 0.00018126
2012 | 2011-11-21 | C | 19.2257 | 0.013398 | 0.0005844
2012 | 2011-11-23 | C | 122.9211 | 0.013445 | 0.00038439
2012 | 2011-11-23 | B | 19.9897 | 0.017991 | 6.2503e-05
2012 | 2011-11-23 | B | 2.9921 | 0.0035065 | 9.3754e-06
2012 | 2011-11-23 | C | 137.4205 | 0.082456 | 0.00073753
2012 | 2011-11-23 | C | 4.9362 | 0.00067875 | 1.5626e-05
2012 | 2011-11-23 | C | 1.9571 | 0.00040979 | 6.2503e-06
2012 | 2011-11-23 | C | 464.0185 | 0.30887 | 0.0024282
2012 | 2011-11-23 | C | 781.8333 | 0.03665 | 0.0024438
2012 | 2011-11-23 | C | 288.9756 | 0.10837 | 0.00090316
2012 | 2011-11-23 | C | 136.0293 | 0.11478 | 0.00095004
2012 | 2011-11-23 | C | 67.9876 | 0.050568 | 0.00021251
2012 | 2011-11-23 | C | 35.9583 | 0.0077538 | 0.0001125
2012 | 2011-11-23 | C | 126.5481 | 0.081073 | 0.001125
2012 | 2011-11-23 | C | 56.925 | 0.0065822 | 0.00017813
2012 | 2011-11-23 | C | 537.2759 | 0.28712 | 0.0040095
2012 | 2011-11-23 | C | 84.9885 | 0.068525 | 0.00026564
2012 | 2011-11-24 | C | 192.2941 | 0.079925 | 0.0022688
2012 | 2011-11-24 | C | 178.875 | 0.011739 | 0.0005594
2012 | 2011-11-24 | C | 116.5315 | 0.050985 | 0.00043439
2012 | 2011-11-24 | C | 16.9538 | 0.0032849 | 5.3127e-05
2012 | 2011-11-24 | C | 37.075 | 0.032094 | 0.00048127
2012 | 2011-11-24 | C | 30.9348 | 0.004157 | 9.6879e-05
2012 | 2011-11-23 | C | 558.9189 | 0.059388 | 0.0017469
2012 | 2011-11-24 | C | 3.94 | 0.00057871 | 1.2501e-05
2012 | 2011-11-23 | C | 639.9444 | 0.102 | 0.0020001
2012 | 2011-11-24 | C | 94.8 | 0.0035551 | 0.00029689
2012 | 2011-11-23 | C | 110.4015 | 0.044507 | 0.00063753
2012 | 2011-11-23 | C | 150.4681 | 0.02069 | 0.00047502
2012 | 2011-11-24 | C | 78.6429 | 0.19612 | 0.00032814
2012 | 2011-11-23 | C | 101.9286 | 0.04364 | 0.00047189
2012 | 2011-11-23 | B | 8.9667 | 0.0024379 | 2.8126e-05
2012 | 2011-11-24 | C | 86 | 0.053483 | 0.00068753
2012 | 2011-11-25 | C | 1356.8 | 0.050882 | 0.0042408
2012 | 2011-11-25 | C | 372.9732 | 0.12705 | 0.0011657
2012 | 2011-11-25 | C | 13.9717 | 0.0044973 | 4.3752e-05
2012 | 2011-11-24 | C | 1072.2426 | 0.44567 | 0.0075284
2012 | 2011-11-25 | B | 2.9667 | 0.0008066 | 9.3754e-06
2012 | 2011-11-24 | C | 781.8125 | 0.031762 | 0.0024438
2012 | 2011-11-25 | C | 4.9 | 0.00041345 | 1.5626e-05
2012 | 2011-11-25 | C | 137.929 | 0.071554 | 0.00096566
2012 | 2011-11-25 | C | 852.0194 | 0.26627 | 0.0051658
2012 | 2011-11-25 | C | 45.0402 | 0.024069 | 0.0006469
2012 | 2011-11-25 | B | 19.9918 | 0.022742 | 6.2503e-05
2012 | 2011-11-25 | C | 227.5682 | 0.06045 | 0.0010688
2012 | 2011-11-25 | C | 1.9189 | 0.00020389 | 6.2503e-06
2012 | 2011-11-25 | C | 25.9516 | 0.004785 | 8.1253e-05
2012 | 2011-11-25 | C | 28.979 | 0.012679 | 9.0629e-05
2012 | 2011-11-25 | C | 122.5 | 0.0011485 | 0.00038439
2012 | 2011-11-25 | C | 37.988 | 0.029323 | 0.00011875
2012 | 2011-11-25 | C | 58.8966 | 0.0047855 | 0.00018438
2012 | 2011-11-26 | C | 14.983 | 0.0081005 | 4.6877e-05
2012 | 2011-11-26 | C | 54.5824 | 0.046056 | 0.00021563
2012 | 2011-11-26 | C | 1310.8333 | 0.061448 | 0.004097
2012 | 2011-11-25 | C | 286.85 | 0.01524 | 0.00089691
2012 | 2011-11-26 | C | 396.7 | 0.0086782 | 0.0012407
2012 | 2011-11-26 | C | 176.578 | 0.17879 | 0.00091879
2012 | 2011-11-26 | C | 286.8421 | 0.014343 | 0.00089691
2012 | 2011-11-26 | C | 97.9 | 0.0082606 | 0.00030626
2012 | 2011-11-26 | C | 12.9559 | 0.0026318 | 4.0627e-05
2012 | 2011-11-26 | C | 139.4232 | 0.11503 | 0.0005844
2012 | 2011-11-26 | C | 209.5469 | 0.33332 | 0.00083753
2012 | 2011-11-25 | C | 94.2139 | 0.29237 | 0.00034064
2012 | 2011-11-26 | C | 7.9748 | 0.002891 | 2.5001e-05
2012 | 2011-11-26 | C | 139.3 | 0.0727 | 0.00071565
2012 | 2011-11-26 | C | 55.9318 | 0.0071666 | 0.00017501
2012 | 2011-11-26 | C | 177.9464 | 0.029474 | 0.00055627
2012 | 2011-11-26 | C | 71.2466 | 0.048984 | 0.00037502
2012 | 2011-11-26 | C | 15.9348 | 0.0021413 | 5.0002e-05
2012 | 2011-11-26 | C | 26.98 | 0.012394 | 8.4378e-05
2012 | 2011-11-26 | C | 118.483 | 0.45655 | 0.0044908
2012 | 2011-11-26 | C | 341.3086 | 0.083197 | 0.0012344
2012 | 2011-11-26 | C | 92.88 | 0.0063858 | 0.00029064
2012 | 2011-11-26 | C | 216.4172 | 0.1001 | 0.0022563
2012 | 2011-11-26 | C | 117.2699 | 0.058637 | 0.00070315
2012 | 2011-11-27 | C | 153.9211 | 0.016836 | 0.00058752
2012 | 2011-11-26 | C | 171.2566 | 0.058872 | 0.00083128
2012 | 2011-11-25 | C | 3.9958 | 0.008966 | 1.2501e-05
2012 | 2011-11-27 | C | 37.9868 | 0.026711 | 0.00011875
2012 | 2011-11-27 | C | 10.9118 | 0.0010571 | 3.4376e-05
2012 | 2011-11-27 | C | 27.8502 | 0.019496 | 0.00022188
2012 | 2011-11-27 | C | 356.925 | 0.041271 | 0.0011157
2012 | 2011-11-27 | C | 339.9703 | 0.10412 | 0.0010625
2012 | 2011-11-28 | C | 133.7273 | 0.0033433 | 0.00041877
2012 | 2011-11-28 | C | 84.85 | 0.0045078 | 0.00026564
2012 | 2011-11-28 | C | 522.3553 | 0.3673 | 0.0029439
2012 | 2011-11-28 | C | 238.1104 | 0.23366 | 0.0031845
2012 | 2011-11-28 | C | 749.1569 | 0.11238 | 0.0024376
2012 | 2011-11-28 | C | 13.8846 | 0.000998 | 4.3752e-05
2012 | 2011-11-28 | C | 373.9143 | 0.037393 | 0.0011688
2012 | 2011-11-17 | B | 15.967 | 0.0043911 | 5.0002e-05
2012 | 2011-11-28 | C | 61.94 | 0.0090978 | 0.00019376
2012 | 2011-11-15 | B | 4.9739 | 0.0017409 | 1.5626e-05
2012 | 2011-11-29 | C | 159.1935 | 0.12189 | 0.00080941
2012 | 2011-11-28 | C | 26.0291 | 0.03327 | 0.00021876
2012 | 2011-11-29 | C | 781.8889 | 0.058644 | 0.0024438
2012 | 2011-11-29 | C | 82.0463 | 0.054614 | 0.00050315
2012 | 2011-11-18 | B | 112.9925 | 0.13948 | 0.00035314
2012 | 2011-11-28 | B | 50.975 | 0.018638 | 0.00015938
2012 | 2011-11-29 | C | 98.9231 | 0.011129 | 0.00030939
2012 | 2011-11-29 | C | 29.95 | 0.0053351 | 9.3754e-05
2012 | 2011-11-29 | B | 11.9914 | 0.012929 | 3.7502e-05
2012 | 2011-11-29 | B | 98.9916 | 0.11013 | 0.00030939
2012 | 2011-11-29 | C | 111.8867 | 0.0514 | 0.00093129
2012 | 2011-11-30 | B | 27.9848 | 0.017054 | 8.7504e-05
2012 | 2011-11-30 | B | 20.99 | 0.019482 | 6.5628e-05
2012 | 2011-11-30 | C | 58.7 | 0.0012841 | 0.00018438
2012 | 2011-11-30 | C | 71.9118 | 0.0069667 | 0.00022501
2012 | 2011-11-30 | C | 485.9717 | 0.15643 | 0.0015188
2012 | 2011-11-30 | C | 473.4815 | 0.11542 | 0.0017688
2012 | 2011-12-01 | B | 6.99 | 0.0064879 | 2.1876e-05
2012 | 2011-12-01 | B | 188.9922 | 0.22562 | 0.00059065
2012 | 2011-12-01 | B | 20.9917 | 0.02342 | 6.5628e-05
2012 | 2011-12-01 | C | 22.9589 | 0.0050225 | 7.1878e-05
2012 | 2011-12-01 | C | 1.9814 | 0.00097834 | 6.2503e-06
2012 | 2011-12-03 | C | 1858.75 | 0.052279 | 0.0058096
2012 | 2011-12-03 | C | 968.7857 | 0.033303 | 0.0030282
2012 | 2011-12-03 | C | 968.9589 | 0.21197 | 0.0030282
2012 | 2011-12-03 | C | 141.9531 | 0.027061 | 0.00044377
2012 | 2011-12-03 | C | 59.9706 | 0.018554 | 0.00018751
2012 | 2011-12-02 | B | 20.987 | 0.014954 | 6.5628e-05
2012 | 2011-12-02 | C | 345.6762 | 0.26035 | 0.0019126
2012 | 2011-12-02 | C | 216.087 | 0.060102 | 0.0024345
2012 | 2011-12-04 | C | 92.6765 | 0.028673 | 0.0006344
2012 | 2011-12-04 | C | 92.9423 | 0.014232 | 0.00029064
2012 | 2011-12-03 | C | 112.0783 | 0.039229 | 0.00050315
2012 | 2011-12-04 | C | 297.597 | 0.12183 | 0.002772
2012 | 2011-12-04 | C | 1.9268 | 0.00022882 | 6.2503e-06
2012 | 2011-12-05 | C | 191.7955 | 0.050948 | 0.0018313
2012 | 2011-12-04 | C | 170.9464 | 0.028314 | 0.0005344
2012 | 2011-12-05 | C | 134.8509 | 0.1711 | 0.001897
2012 | 2011-12-04 | C | 1043.7857 | 0.035882 | 0.0035501
2012 | 2011-12-05 | C | 96.4625 | 0.023212 | 0.0005594
2012 | 2011-12-05 | C | 125.9318 | 0.016136 | 0.00039377
2012 | 2011-12-06 | C | 51.9362 | 0.0071415 | 0.00016251
2012 | 2011-12-06 | B | 21.9901 | 0.020685 | 6.8753e-05
2012 | 2011-12-06 | B | 2.9919 | 0.0034408 | 9.3754e-06
2012 | 2011-12-06 | B | 17.9697 | 0.0053911 | 5.6252e-05
2012 | 2011-12-06 | C | 969.9906 | 0.31223 | 0.0059815
2012 | 2011-12-06 | C | 981.95 | 0.17492 | 0.0030689
2012 | 2011-12-06 | C | 579.7 | 0.23008 | 0.0018188
2012 | 2011-12-06 | B | 1.9754 | 0.00073464 | 6.2503e-06
2012 | 2011-12-06 | C | 456.9615 | 0.1071 | 0.0014282
2012 | 2011-12-07 | C | 1315.8 | 0.049345 | 0.0041127
2012 | 2011-12-05 | C | 1.9973 | 0.0068534 | 6.2503e-06
2012 | 2011-12-07 | C | 759.3443 | 0.13764 | 0.0041439
2012 | 2011-12-07 | C | 565.2742 | 0.10423 | 0.0030845
2012 | 2011-12-07 | B | 21.9916 | 0.024398 | 6.8753e-05
2012 | 2011-12-07 | B | 68.992 | 0.080638 | 0.00021563
2012 | 2011-12-07 | C | 41.9538 | 0.0081289 | 0.00013126
2012 | 2011-12-06 | C | 7.9929 | 0.010416 | 2.5001e-05
2012 | 2011-12-08 | B | 21.9915 | 0.023917 | 6.8753e-05
2012 | 2011-12-06 | C | 1.9915 | 0.0021658 | 6.2503e-06
2012 | 2011-12-08 | B | 3.9869 | 0.0028159 | 1.2501e-05
2012 | 2011-12-08 | C | 12.9758 | 0.0049067 | 4.0627e-05
2012 | 2011-12-09 | C | 24.9659 | 0.0066318 | 7.8128e-05
2012 | 2011-12-08 | C | 1.9979 | 0.0090098 | 6.2503e-06
2012 | 2011-12-07 | B | 23.9901 | 0.022417 | 7.5003e-05
2012 | 2011-12-09 | B | 1.96 | 0.00044102 | 6.2503e-06
2012 | 2011-12-10 | C | 58.9333 | 0.0077353 | 0.00018438
2012 | 2011-12-10 | C | 257.94 | 0.037886 | 0.00080628
2012 | 2011-12-10 | C | 50.0366 | 0.012353 | 0.00034689
2012 | 2011-12-10 | C | 22.9838 | 0.013073 | 7.1878e-05
2012 | 2011-12-11 | B | 15.9667 | 0.0043411 | 5.0002e-05
2012 | 2011-12-08 | C | 6.9942 | 0.011301 | 2.1876e-05
2012 | 2011-12-11 | C | 88.6 | 0.011629 | 0.00031251
2012 | 2011-12-11 | C | 89.6471 | 0.39054 | 0.0030376
2012 | 2011-12-12 | C | 580.3482 | 0.44253 | 0.0036064
2012 | 2011-12-12 | B | 46.9706 | 0.014532 | 0.00014688
2012 | 2011-12-12 | C | 1192.85 | 0.063373 | 0.0037283
2012 | 2011-12-12 | B | 349.9854 | 0.22203 | 0.0010938
2012 | 2011-12-12 | C | 229.1852 | 0.01719 | 0.0015844
2012 | 2011-12-12 | C | 12.8636 | 0.00076381 | 4.0627e-05
2012 | 2011-12-12 | C | 31.9211 | 0.0034915 | 0.0001
2012 | 2011-12-12 | C | 959.9268 | 0.114 | 0.0030001
2012 | 2011-12-12 | C | 141.3029 | 0.1051 | 0.0010563
2012 | 2011-12-12 | B | 81.9853 | 0.051499 | 0.00025626
2012 | 2011-12-13 | C | 450.9231 | 0.63695 | 0.0021813
2012 | 2011-12-12 | B | 8.9667 | 0.0024379 | 2.8126e-05
2012 | 2011-12-13 | B | 2.9921 | 0.003544 | 9.3754e-06
2012 | 2011-12-14 | C | 5.9756 | 0.0022409 | 1.8751e-05
2012 | 2011-12-14 | C | 866.6875 | 0.12188 | 0.0029064
2012 | 2011-12-14 | C | 69.9388 | 0.010054 | 0.00021876
2012 | 2011-12-14 | B | 1.9872 | 0.0014408 | 6.2503e-06
2012 | 2011-12-14 | B | 385.9914 | 0.41858 | 0.0012063
2012 | 2011-12-14 | C | 27.9571 | 0.0058538 | 8.7504e-05
2012 | 2011-12-14 | B | 59.9939 | 0.091682 | 0.00018751
2012 | 2011-12-14 | C | 1.4609 | 0.0053053 | 3.4376e-05
2012 | 2011-12-15 | C | 7.9474 | 0.0013412 | 2.5001e-05
2012 | 2011-12-14 | C | 69.961 | 0.016179 | 0.00021876
2012 | 2011-12-15 | C | 762.2209 | 0.19771 | 0.003247
2012 | 2011-12-15 | B | 47.9881 | 0.037492 | 0.00015001
2012 | 2011-12-15 | C | 7.96 | 0.0017911 | 2.5001e-05
2012 | 2011-12-15 | C | 106.4266 | 0.071508 | 0.00085628
2012 | 2011-12-15 | C | 130.4695 | 0.065645 | 0.00094379
2012 | 2011-12-16 | C | 44.8889 | 0.0033668 | 0.00014063
2012 | 2011-12-16 | C | 180.3443 | 0.13583 | 0.0021032
2012 | 2011-12-16 | B | 43.973 | 0.014841 | 0.00013751
2012 | 2011-12-16 | B | 9.991 | 0.010335 | 3.1251e-05
2012 | 2011-12-16 | C | 36.9833 | 0.020457 | 0.00011563
2012 | 2011-12-16 | C | 6.9771 | 0.002791 | 2.1876e-05
2012 | 2011-12-16 | C | 915.7692 | 0.10303 | 0.0036064
2012 | 2011-12-17 | C | 529.1735 | 0.1571 | 0.0032876
2012 | 2011-12-17 | C | 94.9905 | 0.092619 | 0.00029689
2012 | 2011-12-17 | C | 51.95 | 0.009254 | 0.00016251
2012 | 2011-12-17 | C | 142.951 | 0.044227 | 0.00058127
2012 | 2011-12-17 | C | 1.98 | 0.0009096 | 6.2503e-06
2012 | 2011-12-18 | C | 68.9892 | 0.05929 | 0.00021563
2012 | 2011-12-18 | C | 974.8421 | 0.048744 | 0.003047
2012 | 2011-12-18 | C | 130.9857 | 0.084735 | 0.00040939
2012 | 2011-12-18 | B | 101.0022 | 0.13983 | 0.00094379
2012 | 2011-12-19 | C | 317.8 | 0.011918 | 0.00099379
2012 | 2011-12-19 | B | 165.9677 | 0.04668 | 0.00051877
2012 | 2011-12-19 | B | 60.9903 | 0.058324 | 0.00019063
2012 | 2011-12-19 | B | 131.9615 | 0.03093 | 0.00041252
2012 | 2011-12-19 | B | 66.925 | 0.0077385 | 0.00020938
2012 | 2011-12-19 | B | 183.9856 | 0.11787 | 0.00057502
2012 | 2011-12-19 | B | 165.9625 | 0.039936 | 0.00051877
2012 | 2011-12-20 | C | 289.9508 | 0.052556 | 0.00090629
2012 | 2011-12-21 | B | 55.9841 | 0.032542 | 0.00017501
2012 | 2011-12-21 | B | 17.9916 | 0.019848 | 5.6252e-05
2012 | 2011-12-21 | C | 934.9062 | 0.084729 | 0.002922
2012 | 2011-12-22 | C | 121.6638 | 0.042964 | 0.00063128
2012 | 2011-12-22 | C | 85.9189 | 0.0091293 | 0.00026876
2012 | 2011-12-22 | B | 99.9516 | 0.018429 | 0.00031251
2012 | 2011-12-22 | C | 537.8672 | 0.21011 | 0.001947
2012 | 2011-12-22 | B | 2.9858 | 0.0019408 | 9.3754e-06
2012 | 2011-12-22 | C | 72.9905 | 0.071625 | 0.00022813
2012 | 2011-12-23 | C | 545.8602 | 0.31218 | 0.001947
2012 | 2011-12-22 | C | 56.7684 | 0.030869 | 0.00043439
2012 | 2011-12-23 | C | 47.9167 | 0.0049416 | 0.00015001
2012 | 2011-12-23 | C | 77.4186 | 0.030485 | 0.00045627
2012 | 2011-12-23 | C | 7.9231 | 0.00089138 | 2.5001e-05
2012 | 2011-12-25 | C | 371.0147 | 0.075365 | 0.0021751
2012 | 2011-12-26 | C | 1595.0222 | 0.20936 | 0.0059971
2012 | 2011-12-26 | C | 99.9333 | 0.013117 | 0.00031251
2012 | 2011-12-26 | C | 610.4953 | 0.19842 | 0.0033439
2012 | 2011-12-26 | C | 36.9388 | 0.0053102 | 0.00011563
2012 | 2011-12-26 | C | 6.9605 | 0.0015879 | 2.1876e-05
2012 | 2011-12-27 | C | 749.6325 | 0.26707 | 0.0028782
2012 | 2011-12-27 | C | 520.35 | 0.25531 | 0.0016594
2012 | 2011-12-27 | C | 298.9011 | 0.082201 | 0.00095316
2012 | 2011-12-27 | C | 700.88 | 0.048187 | 0.0021907
2012 | 2011-12-27 | C | 75.9362 | 0.010442 | 0.00023751
2012 | 2011-12-27 | C | 70.5534 | 0.055122 | 0.00071878
2012 | 2011-12-28 | C | 420.8125 | 0.017096 | 0.0013157
2012 | 2011-12-28 | C | 884.9333 | 0.15764 | 0.0032439
2012 | 2011-12-28 | C | 2.987 | 0.002119 | 9.3754e-06
2012 | 2011-12-28 | C | 8.9746 | 0.0032254 | 2.8126e-05
2012 | 2011-12-29 | C | 205.375 | 0.095632 | 0.0028439
2012 | 2011-12-29 | C | 249.9375 | 0.035149 | 0.00078128
2012 | 2011-12-29 | C | 66.1311 | 0.05456 | 0.00093129
2012 | 2011-12-29 | C | 54.9333 | 0.0072103 | 0.00017188
2012 | 2011-12-30 | C | 240.3731 | 0.048077 | 0.0013876
2012 | 2011-12-30 | C | 192.3865 | 0.096197 | 0.0019688
2012 | 2011-12-30 | C | 551.9423 | 0.08452 | 0.0017251
2012 | 2011-12-30 | C | 406.8696 | 0.02543 | 0.0012719
2012 | 2011-12-30 | C | 85.1854 | 0.0394 | 0.00099067
2012 | 2011-12-31 | C | 528.9605 | 0.12067 | 0.0016532
2012 | 2011-12-31 | C | 150.6033 | 0.055537 | 0.00051877
2012 | 2011-12-30 | C | 74.9865 | 0.051555 | 0.00023438
2012 | 2011-12-31 | C | 240.8804 | 0.066998 | 0.00099067
2012 | 2011-12-31 | C | 213.5221 | 0.088749 | 0.0010063
2012 | 2011-12-31 | C | 9.8 | 0.00036751 | 3.1251e-05
2012 | 2011-12-31 | C | 11.9848 | 0.0073036 | 3.7502e-05
2012 | 2011-12-31 | C | 149.0673 | 0.13696 | 0.00091566
2012 | 2011-12-31 | C | 212.973 | 0.071881 | 0.00066565
2012 | 2011-12-31 | C | 69.7432 | 0.015475 | 0.00054065
2012 | 2011-12-31 | C | 680.75 | 0.019147 | 0.0021282
2012 | 2011-12-31 | C | 365.8 | 0.013718 | 0.0011438
2012 | 2011-12-31 | C | 80.0753 | 0.072321 | 0.00099379
2012 | 2011-12-31 | C | 191.5745 | 0.054481 | 0.0011
2012 | 2011-12-31 | C | 286.9477 | 0.13451 | 0.0055033
2012 | 2012-01-01 | C | 183.3506 | 0.042402 | 0.00070315
2012 | 2012-01-01 | C | 239.625 | 0.0037443 | 0.00075003
2012 | 2012-01-01 | C | 4.9318 | 0.00063191 | 1.5626e-05
2012 | 2012-01-01 | C | 18.925 | 0.0021883 | 5.9377e-05
2012 | 2012-01-02 | C | 6.9571 | 0.0014567 | 2.1876e-05
2012 | 2012-01-02 | C | 55.925 | 0.0064666 | 0.00017501
2012 | 2012-01-02 | C | 3.9857 | 0.0025784 | 1.2501e-05
2012 | 2012-01-02 | C | 320.1944 | 0.10507 | 0.0016626
2012 | 2012-01-03 | C | 420.75 | 0.011834 | 0.0013157
2012 | 2012-01-04 | C | 54.9118 | 0.0053198 | 0.00017188
2012 | 2012-01-04 | C | 2.9982 | 0.015198 | 9.3754e-06
2012 | 2012-01-05 | C | 2.9647 | 0.00075974 | 9.3754e-06
2012 | 2012-01-06 | C | 283.9032 | 0.024843 | 0.00088754
2012 | 2012-01-07 | C | 378.6642 | 0.64494 | 0.012441
2012 | 2012-01-07 | C | 138.6786 | 0.047239 | 0.00085628
2012 | 2012-01-07 | C | 627.8929 | 0.049056 | 0.0019626
2012 | 2012-01-07 | C | 237.8235 | 0.010405 | 0.00074378
2012 | 2012-01-08 | C | 7.979 | 0.003491 | 2.5001e-05
2012 | 2012-01-08 | C | 59.9639 | 0.014992 | 0.00018751
2012 | 2012-01-08 | C | 3.9 | 0.00032908 | 1.2501e-05
2012 | 2012-01-08 | C | 719.1467 | 0.16181 | 0.0049127
2012 | 2012-01-08 | C | 12.972 | 0.0042161 | 4.0627e-05
2012 | 2012-01-08 | C | 326.1111 | 0.051976 | 0.0013063
2012 | 2012-01-08 | C | 224.4623 | 0.072252 | 0.00070628
2012 | 2012-01-08 | C | 17.8761 | 0.0061452 | 0.00024063
2012 | 2012-01-08 | C | 142.9639 | 0.035742 | 0.00044689
2012 | 2012-01-08 | C | 242.5149 | 0.099284 | 0.00085941
2012 | 2012-01-08 | C | 379.3354 | 0.19086 | 0.0043658
2012 | 2012-01-08 | C | 167.2755 | 0.049662 | 0.00083128
2012 | 2012-01-08 | C | 447.2 | 0.016771 | 0.0017157
2012 | 2012-01-08 | C | 153.9897 | 0.13812 | 0.00048127
2012 | 2012-01-08 | C | 207.2518 | 0.26814 | 0.00078441
2012 | 2012-01-08 | C | 102.8596 | 0.054004 | 0.0006344
2012 | 2012-01-08 | C | 671.973 | 0.2268 | 0.0021001
2012 | 2012-01-08 | C | 472.457 | 0.2702 | 0.0024345
2012 | 2012-01-08 | C | 122.9722 | 0.040352 | 0.00038439
2012 | 2012-01-08 | C | 169.8565 | 0.1205 | 0.00065315
2012 | 2012-01-08 | C | 36.4271 | 0.010587 | 0.00014063
2012 | 2012-01-08 | C | 65.0576 | 0.06994 | 0.00033439
2012 | 2012-01-08 | C | 63.9762 | 0.024592 | 0.00020001
2012 | 2012-01-08 | C | 12.9688 | 0.0037692 | 4.0627e-05
2012 | 2012-01-09 | C | 74.6602 | 0.083063 | 0.00050002
2012 | 2012-01-08 | C | 48.9348 | 0.0065759 | 0.00015313
2012 | 2012-01-08 | C | 397.8191 | 0.24367 | 0.0012688
2012 | 2012-01-08 | C | 20.9659 | 0.0055693 | 6.5628e-05
2012 | 2012-01-08 | C | 138.95 | 0.024751 | 0.00043439
2012 | 2012-01-08 | C | 514.9189 | 0.054712 | 0.0016094
2012 | 2012-01-08 | C | 37.9409 | 0.029761 | 0.00016563
2012 | 2011-12-19 | B | 32.986 | 0.021751 | 0.00010313
2012 | 2011-12-13 | B | 17.9847 | 0.010847 | 5.6252e-05
2012 | 2011-12-12 | B | 21.9907 | 0.02206 | 6.8753e-05
2012 | 2011-12-20 | B | 11.9916 | 0.013229 | 3.7502e-05
2012 | 2011-12-20 | B | 14.9142 | 0.017245 | 0.00041877
2012 | 2012-01-08 | C | 221.0594 | 0.067702 | 0.00074378
2012 | 2011-12-12 | B | 68.9615 | 0.016164 | 0.00021563
2012 | 2012-01-08 | C | 44 | 0.065453 | 0.00044377
2012 | 2012-01-09 | C | 149.9091 | 0.014055 | 0.00046877
2012 | 2012-01-08 | C | 18.768 | 0.065808 | 0.00044064
2012 | 2012-01-09 | C | 7.9524 | 0.0014911 | 2.5001e-05
2012 | 2012-01-09 | C | 8.967 | 0.002466 | 2.8126e-05
2012 | 2012-01-09 | C | 53.0353 | 0.013591 | 0.00061565
2012 | 2012-01-09 | C | 418.0909 | 0.11106 | 0.0019657
2012 | 2012-01-08 | C | 75.4199 | 0.34671 | 0.00055315
2012 | 2012-01-09 | C | 10.981 | 0.0053191 | 3.4376e-05
2012 | 2012-01-09 | C | 3.9663 | 0.001066 | 1.2501e-05
2012 | 2012-01-09 | C | 1.8929 | 0.00014789 | 6.2503e-06
2012 | 2012-01-09 | C | 4.875 | 0.00031993 | 1.5626e-05
2012 | 2012-01-09 | C | 66.8929 | 0.0052262 | 0.00020938
2012 | 2012-01-09 | C | 2729.9118 | 0.26447 | 0.0085316
2012 | 2012-01-09 | C | 12.9577 | 0.0027536 | 4.0627e-05
2012 | 2012-01-09 | C | 159.1748 | 0.049744 | 0.00098754
2012 | 2012-01-09 | C | 11.9091 | 0.0011165 | 3.7502e-05
2012 | 2012-01-08 | C | 26.998 | 0.12757 | 8.4378e-05
2012 | 2012-01-09 | C | 59.875 | 0.0039295 | 0.00018751
2012 | 2012-01-09 | C | 31.97 | 0.0096913 | 0.0001
2012 | 2012-01-08 | C | 66.9544 | 0.2469 | 0.00033439
2012 | 2012-01-08 | C | 5.0621 | 0.048583 | 1.8751e-05
2012 | 2012-01-09 | C | 73.3333 | 0.070815 | 0.00036564
2012 | 2012-01-09 | C | 35.9091 | 0.0033666 | 0.0001125
2012 | 2012-01-08 | C | 2.9901 | 0.0028127 | 9.3754e-06
2012 | 2012-01-08 | C | 160.6518 | 0.32433 | 0.00051877
2012 | 2012-01-08 | C | 63.5994 | 0.2564 | 0.00033751
2012 | 2012-01-10 | C | 68.9318 | 0.0088322 | 0.00021563
2012 | 2012-01-10 | C | 397.7205 | 0.19638 | 0.0020938
2012 | 2012-01-08 | C | 36.6983 | 0.35473 | 0.00026251
2012 | 2012-01-10 | C | 71.2782 | 0.054575 | 0.00041877
2012 | 2012-01-10 | C | 140.0254 | 0.084894 | 0.0019438
2012 | 2012-01-09 | C | 1.9895 | 0.007691 | 3.4376e-05
2012 | 2012-01-10 | C | 51.9189 | 0.0055166 | 0.00016251
2012 | 2012-01-10 | C | 96.9 | 0.0081763 | 0.00030314
2012 | 2012-01-10 | C | 51.9388 | 0.0074665 | 0.00016251
2012 | 2012-01-10 | C | 465.4231 | 0.10909 | 0.0062909
2012 | 2012-01-10 | C | 110.0241 | 0.084584 | 0.00084066
2012 | 2012-01-11 | C | 205.8235 | 0.0090051 | 0.00064378
2012 | 2012-01-11 | C | 101.8789 | 0.080551 | 0.00071878
2012 | 2012-01-09 | C | 8.9583 | 0.0019317 | 2.8126e-05
2012 | 2012-01-11 | C | 21.9847 | 0.01326 | 6.8753e-05
2012 | 2012-01-11 | C | 1.9834 | 0.0011033 | 6.2503e-06
2012 | 2012-01-11 | C | 95.4222 | 0.09304 | 0.00071878
2012 | 2012-01-12 | C | 112.0084 | 0.08261 | 0.00040939
2012 | 2012-01-12 | C | 1989.8696 | 0.12437 | 0.006219
2012 | 2012-01-12 | C | 150.2763 | 0.069975 | 0.00078128
2012 | 2012-01-12 | B | 7.9892 | 0.006891 | 2.5001e-05
2012 | 2012-01-12 | B | 1.9915 | 0.0021658 | 6.2503e-06
2012 | 2012-01-12 | C | 2.97 | 0.00090032 | 9.3754e-06
2012 | 2012-01-13 | C | 239.3333 | 0.013463 | 0.00090941
2012 | 2012-01-12 | B | 51.9746 | 0.018679 | 0.00016251
2012 | 2012-01-13 | C | 65.7947 | 0.061479 | 0.00049064
2012 | 2012-01-13 | C | 2.9625 | 0.00071288 | 9.3754e-06
2012 | 2012-01-13 | C | 64.9944 | 0.10846 | 0.00020313
2012 | 2012-01-13 | C | 5.9651 | 0.0015473 | 1.8751e-05
2012 | 2012-01-13 | C | 5.9626 | 0.0054224 | 5.6252e-05
2012 | 2012-01-13 | C | 1.9655 | 0.00051597 | 6.2503e-06
2012 | 2012-01-13 | C | 172.7 | 0.003778 | 0.00054065
2012 | 2012-01-13 | C | 39.4437 | 0.034638 | 0.001175
2012 | 2012-01-13 | C | 621.25 | 0.0019415 | 0.0019438
2012 | 2012-01-13 | C | 90.9859 | 0.059712 | 0.00028439
2012 | 2012-01-13 | C | 75.9545 | 0.17162 | 0.0020032
2012 | 2012-01-13 | C | 22.9647 | 0.0058849 | 7.1878e-05
2012 | 2012-01-14 | C | 14.9062 | 0.0013509 | 4.6877e-05
2012 | 2012-01-14 | C | 4.9735 | 0.0017097 | 1.5626e-05
2012 | 2012-01-14 | C | 7.9552 | 0.0015911 | 2.5001e-05
2012 | 2012-01-14 | C | 29.9841 | 0.017429 | 9.3754e-05
2012 | 2012-01-14 | C | 85.3909 | 0.064046 | 0.00043439
2012 | 2012-01-13 | B | 3.9946 | 0.0069035 | 1.2501e-05
2012 | 2012-01-14 | C | 89.6917 | 0.066431 | 0.00048439
2012 | 2012-01-14 | C | 1989.9 | 0.1679 | 0.006219
2012 | 2012-01-14 | C | 1821.9268 | 0.21636 | 0.005694
2012 | 2012-01-13 | C | 19.9888 | 0.016616 | 6.2503e-05
2012 | 2012-01-13 | C | 221.9634 | 0.054799 | 0.00097191
2012 | 2012-01-14 | C | 292.9732 | 0.099798 | 0.00091566
2012 | 2012-01-13 | C | 14.8636 | 0.00088256 | 4.6877e-05
2012 | 2012-01-14 | C | 134.4936 | 0.064307 | 0.00074378
2012 | 2012-01-14 | C | 591.8235 | 0.025893 | 0.0018501
2012 | 2012-01-15 | C | 34.9032 | 0.0030542 | 0.00010938
2012 | 2012-01-15 | C | 9.9231 | 0.0011164 | 3.1251e-05
2012 | 2012-01-15 | C | 12.9773 | 0.0052317 | 4.0627e-05
2012 | 2012-01-15 | C | 32.9348 | 0.0044258 | 0.00010313
2012 | 2012-01-15 | C | 80.96 | 0.018217 | 0.00025314
2012 | 2012-01-15 | C | 44.9 | 0.0037886 | 0.00014063
2012 | 2012-01-13 | C | 153.5753 | 0.1579 | 0.00081566
2012 | 2012-01-13 | C | 74.1331 | 0.12812 | 0.00067503
2012 | 2012-01-13 | C | 104.9456 | 0.30042 | 0.00055315
2012 | 2012-01-14 | C | 201.9184 | 0.23789 | 0.00072815
2012 | 2012-01-15 | C | 166.9692 | 0.032352 | 0.00053752
2012 | 2012-01-16 | C | 635.6122 | 0.091373 | 0.0021657
2012 | 2012-01-14 | C | 206.3605 | 0.092866 | 0.00065628
2012 | 2012-01-16 | C | 18.88 | 0.0012981 | 5.9377e-05
2012 | 2012-01-16 | C | 90.9625 | 0.021889 | 0.00028439
2012 | 2012-01-16 | C | 35.9362 | 0.0049414 | 0.0001125
2012 | 2012-01-16 | C | 3.9667 | 0.0010785 | 1.2501e-05
2012 | 2012-01-17 | C | 150.5806 | 0.027764 | 0.00047814
2012 | 2012-01-17 | C | 132.1703 | 0.15159 | 0.00083753
2012 | 2012-01-13 | C | 588.9531 | 0.11227 | 0.0018407
2012 | 2012-01-16 | C | 759.2254 | 0.16134 | 0.0029782
2012 | 2012-01-13 | C | 190.0818 | 0.092669 | 0.0006469
2012 | 2012-01-13 | C | 330.0519 | 1.2099 | 0.0013063
2012 | 2012-01-16 | C | 16.9971 | 0.055615 | 5.3127e-05
2012 | 2012-01-17 | B | 7.9771 | 0.003191 | 2.5001e-05
2012 | 2012-01-17 | C | 269.8696 | 0.016868 | 0.00084378
2012 | 2012-01-17 | C | 2.9464 | 0.00048802 | 9.3754e-06
2012 | 2012-01-17 | B | 87.9492 | 0.015392 | 0.00027501
2012 | 2012-01-17 | C | 111.9444 | 0.017842 | 0.00035001
2012 | 2012-01-18 | C | 1.9589 | 0.00042853 | 6.2503e-06
2012 | 2012-01-18 | B | 48.972 | 0.015917 | 0.00015313
2012 | 2012-01-18 | B | 12.9899 | 0.011935 | 4.0627e-05
2012 | 2012-01-18 | C | 4.9741 | 0.0017566 | 1.5626e-05
2012 | 2012-01-18 | C | 593.8 | 0.022268 | 0.0018563
2012 | 2012-01-18 | C | 155.8409 | 0.062826 | 0.0016844
2012 | 2012-01-19 | C | 50.7608 | 0.058536 | 0.0017063
2012 | 2012-01-19 | C | 25.9545 | 0.00511 | 8.1253e-05
2012 | 2012-01-19 | C | 77.94 | 0.011448 | 0.00024376
2012 | 2012-01-19 | C | 12.9388 | 0.00186 | 4.0627e-05
2012 | 2012-01-19 | B | 1.9691 | 0.00057844 | 6.2503e-06
2012 | 2012-01-19 | C | 1.9423 | 0.00029743 | 6.2503e-06
2012 | 2012-01-19 | B | 17.9912 | 0.019004 | 5.6252e-05
2012 | 2012-01-19 | C | 7.3548 | 0.0020686 | 2.5001e-05
2012 | 2012-01-19 | C | 69.9167 | 0.0072104 | 0.00021876
2012 | 2012-01-19 | C | 28.9936 | 0.042224 | 9.0629e-05
2012 | 2012-01-20 | C | 52.8 | 0.0019801 | 0.00016563
2012 | 2012-01-20 | C | 99.8912 | 0.044953 | 0.002222
2012 | 2012-01-21 | C | 7.8421 | 0.00039212 | 2.5001e-05
2012 | 2012-01-20 | C | 19.961 | 0.0046162 | 6.2503e-05
2012 | 2012-01-20 | C | 369.3958 | 0.10736 | 0.0012313
2012 | 2012-01-20 | C | 58.94 | 0.0086572 | 0.00018438
2012 | 2012-01-20 | C | 48.9333 | 0.0064228 | 0.00015313
2012 | 2012-01-22 | C | 44.9211 | 0.0049134 | 0.00014063
2012 | 2012-01-22 | C | 68.418 | 0.03977 | 0.00033126
2012 | 2012-01-22 | C | 289.7875 | 0.21463 | 0.002922
2012 | 2012-01-22 | C | 117.9818 | 0.059731 | 0.00054377
2012 | 2012-01-22 | C | 89.9286 | 0.01096 | 0.00028126
2012 | 2012-01-22 | C | 36.263 | 0.13667 | 0.00034376
2012 | 2012-01-23 | C | 35.9492 | 0.0062914 | 0.0001125
2012 | 2012-01-23 | C | 1322.9516 | 0.24393 | 0.0041345
2012 | 2012-01-23 | C | 672.5918 | 0.096689 | 0.0028251
2012 | 2012-01-22 | C | 173.9891 | 0.1479 | 0.00054377
2012 | 2012-01-22 | C | 81.257 | 0.053581 | 0.00034064
2012 | 2012-01-22 | C | 163.9836 | 0.092245 | 0.00051252
2012 | 2012-01-23 | C | 23.9894 | 0.020917 | 7.5003e-05
2012 | 2012-01-22 | C | 162.1772 | 0.20729 | 0.00087191
2012 | 2012-01-22 | C | 385.9254 | 0.077188 | 0.0012501
2012 | 2012-01-23 | C | 128.3231 | 0.090632 | 0.00083128
2012 | 2012-01-23 | C | 15.2575 | 0.0078198 | 0.00015313
2012 | 2012-01-24 | B | 16.9923 | 0.020498 | 5.3127e-05
2012 | 2012-01-24 | B | 7.9908 | 0.008091 | 2.5001e-05
2012 | 2012-01-24 | B | 91.9167 | 0.0094793 | 0.00028751
2012 | 2012-01-24 | B | 44.9903 | 0.043164 | 0.00014063
2012 | 2012-01-24 | C | 16.8 | 0.00063003 | 5.3127e-05
2012 | 2012-01-20 | B | 1.986 | 0.0013158 | 6.2503e-06
2012 | 2012-01-20 | B | 215.9892 | 0.1863 | 0.00067503
2012 | 2012-01-25 | B | 8.9848 | 0.0054754 | 2.8126e-05
2012 | 2012-01-20 | B | 3.9833 | 0.0022034 | 1.2501e-05
2012 | 2012-01-25 | C | 32.9348 | 0.0044258 | 0.00010313
2012 | 2012-01-26 | B | 2.9907 | 0.0029815 | 9.3754e-06
2012 | 2012-01-26 | C | 122.9474 | 0.020748 | 0.00038439
2012 | 2012-01-26 | B | 13.9894 | 0.012197 | 4.3752e-05
2012 | 2012-01-26 | B | 149.9928 | 0.19453 | 0.00046877
2012 | 2012-01-27 | C | 108.8 | 0.0040802 | 0.00034064
2012 | 2012-01-27 | C | 577.9219 | 0.11017 | 0.003047
2012 | 2012-01-27 | C | 94.9362 | 0.013054 | 0.00029689
2012 | 2012-01-27 | C | 155.4405 | 0.039347 | 0.00072815
2012 | 2012-01-27 | C | 94.9388 | 0.013648 | 0.00029689
2012 | 2012-01-27 | C | 195.1681 | 0.067092 | 0.00072815
2012 | 2012-01-27 | B | 2.9912 | 0.003169 | 9.3754e-06
2012 | 2012-01-27 | C | 859.9625 | 0.20694 | 0.0026876
2012 | 2012-01-27 | B | 44.9914 | 0.04879 | 0.00014063
2012 | 2012-01-27 | C | 10.9143 | 0.0010915 | 3.4376e-05
2012 | 2012-01-27 | B | 16.9897 | 0.015291 | 5.3127e-05
2012 | 2012-01-27 | C | 531.7 | 0.011631 | 0.0016626
2012 | 2012-01-27 | C | 1.9712 | 0.00062217 | 6.2503e-06
2012 | 2012-01-27 | C | 60.9781 | 0.060409 | 0.00019063
2012 | 2012-01-28 | C | 23.8571 | 0.001342 | 7.5003e-05
2012 | 2012-01-28 | C | 1615.6915 | 0.45948 | 0.0056565
2012 | 2012-01-28 | C | 182.3571 | 0.16584 | 0.0026095
2012 | 2012-01-28 | C | 105.3234 | 0.087554 | 0.0030845
2012 | 2012-01-29 | C | 187.7971 | 0.07923 | 0.00091879
2012 | 2012-01-30 | C | 3.9333 | 0.00051627 | 1.2501e-05
2012 | 2012-01-30 | C | 28.967 | 0.0079663 | 9.0629e-05
2012 | 2012-01-30 | C | 14.9888 | 0.01246 | 4.6877e-05
2012 | 2012-01-30 | B | 3.9674 | 0.0011035 | 1.2501e-05
2012 | 2012-01-30 | C | 19.9318 | 0.0025539 | 6.2503e-05
2012 | 2012-01-31 | C | 271.8 | 0.010193 | 0.00085003
2012 | 2012-01-30 | C | 26.9028 | 0.023961 | 9.3754e-05
2012 | 2012-01-30 | C | 89.9571 | 0.018836 | 0.00028126
2012 | 2012-01-31 | B | 5.967 | 0.001641 | 1.8751e-05
2012 | 2012-01-31 | C | 461.3083 | 0.18741 | 0.0034783
2012 | 2012-01-31 | C | 93.985 | 0.057862 | 0.00029376
2012 | 2012-01-31 | B | 21.9915 | 0.023917 | 6.8753e-05
2012 | 2012-01-31 | C | 286.732 | 0.13441 | 0.0016344
2012 | 2012-01-31 | C | 13.9655 | 0.0036661 | 4.3752e-05
2012 | 2012-01-31 | C | 54.058 | 0.04612 | 0.00026251
2012 | 2012-02-01 | C | 72.843 | 0.097887 | 0.00035001
2012 | 2012-02-01 | C | 110.7045 | 0.014185 | 0.00057502
2012 | 2012-02-01 | B | 25.975 | 0.0094975 | 8.1253e-05
2012 | 2012-02-01 | C | 29.9722 | 0.009835 | 9.3754e-05
2012 | 2012-02-01 | C | 2.9722 | 0.0009753 | 9.3754e-06
2012 | 2012-02-01 | B | 21.9911 | 0.022954 | 6.8753e-05
2012 | 2012-02-01 | C | 2.9032 | 0.00025404 | 9.3754e-06
2012 | 2012-02-01 | C | 901.9455 | 0.14657 | 0.0028189
2012 | 2012-02-01 | C | 102.7 | 0.0022467 | 0.00032189
2012 | 2012-02-01 | B | 62.9932 | 0.086422 | 0.00019688
2012 | 2012-01-31 | C | 27.0517 | 0.088091 | 0.00026876
2012 | 2012-02-01 | B | 20.85 | 0.0011077 | 6.5628e-05
2012 | 2012-02-01 | B | 16.9911 | 0.017735 | 5.3127e-05
2012 | 2012-02-01 | C | 61.2674 | 0.03523 | 0.00035001
2012 | 2012-02-01 | C | 14.9268 | 0.0017726 | 4.6877e-05
2012 | 2012-02-02 | C | 228.8 | 0.0085803 | 0.00071565
2012 | 2012-01-25 | B | 1.9905 | 0.0019408 | 6.2503e-06
2012 | 2012-02-02 | C | 8.9836 | 0.0050535 | 2.8126e-05
2012 | 2012-02-02 | C | 2.9492 | 0.00051612 | 9.3754e-06
2012 | 2012-02-02 | B | 3.9913 | 0.0042534 | 1.2501e-05
2012 | 2012-02-02 | B | 183.9739 | 0.064393 | 0.00057502
2012 | 2012-02-02 | C | 37.9841 | 0.022079 | 0.00011875
2012 | 2012-02-02 | B | 200.8929 | 0.015695 | 0.00062815
2012 | 2012-02-04 | C | 105.867 | 0.061207 | 0.00034376
2012 | 2012-02-04 | C | 135.9231 | 0.015292 | 0.00042502
2012 | 2012-02-04 | C | 46.6274 | 0.12823 | 0.00075316
2012 | 2012-02-04 | C | 701.25 | 0.0021915 | 0.0021938
2012 | 2012-02-04 | C | 51.9 | 0.0043792 | 0.00016251
2012 | 2012-02-04 | C | 134.94 | 0.01982 | 0.00042189
2012 | 2012-02-06 | C | 7.9167 | 0.00081644 | 2.5001e-05
2012 | 2012-02-07 | C | 121.4434 | 0.039091 | 0.00025626
2012 | 2012-02-07 | C | 452.8333 | 0.021227 | 0.0014157
2012 | 2012-02-07 | B | 11.9583 | 0.0025786 | 3.7502e-05
2012 | 2012-02-07 | B | 36.8846 | 0.0026512 | 0.00011563
2012 | 2012-02-07 | B | 40.9663 | 0.01101 | 0.00012813
2012 | 2012-02-07 | B | 5.9883 | 0.0047347 | 1.8751e-05
2012 | 2012-02-07 | B | 100.9545 | 0.019876 | 0.00031564
2012 | 2012-02-07 | C | 116.0083 | 0.086285 | 0.00048752
2012 | 2012-02-07 | B | 14.988 | 0.011569 | 4.6877e-05
2012 | 2012-02-07 | C | 39.8929 | 0.0031168 | 0.00012501
2012 | 2012-02-08 | C | 408.4074 | 0.2374 | 0.0050658
2012 | 2012-02-08 | C | 118.8 | 0.0044552 | 0.00037189
2012 | 2012-02-08 | C | 5.5714 | 6.9646e-05 | 1.8751e-05
2012 | 2012-02-08 | B | 16.9824 | 0.008863 | 5.3127e-05
2012 | 2012-02-08 | C | 181.6548 | 0.045983 | 0.00057502
2012 | 2012-02-08 | B | 40.9891 | 0.034714 | 0.00012813
2012 | 2012-02-08 | B | 5.9913 | 0.006366 | 1.8751e-05
2012 | 2012-02-08 | B | 11.9929 | 0.015666 | 3.7502e-05
2012 | 2012-02-07 | B | 72.9901 | 0.068659 | 0.00022813
2012 | 2012-02-08 | B | 2.9906 | 0.0029533 | 9.3754e-06
2012 | 2012-02-09 | B | 2.9911 | 0.0031315 | 9.3754e-06
2012 | 2012-02-09 | B | 72.9939 | 0.11178 | 0.00022813
2012 | 2012-02-09 | B | 14.9915 | 0.016444 | 4.6877e-05
2012 | 2012-02-09 | B | 23.9905 | 0.023392 | 7.5003e-05
2012 | 2012-02-09 | B | 34.9559 | 0.0071007 | 0.00010938
2012 | 2012-02-09 | C | 79.9956 | 0.1715 | 0.00025001
2012 | 2012-02-10 | C | 139.9857 | 0.090557 | 0.00043752
2012 | 2012-02-10 | C | 247.4412 | 0.076555 | 0.0010219
2012 | 2012-02-10 | C | 326.9062 | 0.029627 | 0.0010219
2012 | 2012-02-10 | C | 285.1111 | 0.053461 | 0.0013094
2012 | 2012-02-10 | B | 14.7 | 0.00032158 | 4.6877e-05
2012 | 2012-02-10 | C | 552.6489 | 0.22107 | 0.0017563
2012 | 2012-02-11 | C | 19.9767 | 0.0078662 | 6.2503e-05
2012 | 2012-02-11 | B | 2.96 | 0.00066603 | 9.3754e-06
2012 | 2012-02-12 | C | 27.9007 | 0.012905 | 0.00010313
2012 | 2012-02-13 | C | 61.9677 | 0.017429 | 0.00019376
2012 | 2012-02-13 | B | 40.9885 | 0.03292 | 0.00012813
2012 | 2012-02-07 | B | 40.9847 | 0.02472 | 0.00012813
2012 | 2012-02-13 | C | 32.9483 | 0.0056632 | 0.00010313
2012 | 2012-02-14 | B | 5.9778 | 0.0024659 | 1.8751e-05
2012 | 2012-02-14 | C | 3.9559 | 0.00080357 | 1.2501e-05
2012 | 2012-02-13 | C | 915.5472 | 0.14306 | 0.003622
2012 | 2012-02-14 | B | 68.98 | 0.031689 | 0.00021563
2012 | 2012-02-14 | B | 12.9906 | 0.012829 | 4.0627e-05
2012 | 2012-02-14 | B | 5.9876 | 0.0044534 | 1.8751e-05
2012 | 2012-02-14 | C | 45.9278 | 0.025405 | 0.00078128
2012 | 2012-02-15 | C | 155.8 | 0.0058427 | 0.00048752
2012 | 2012-02-15 | C | 6.9892 | 0.0060285 | 2.1876e-05
2012 | 2012-02-15 | B | 10.9883 | 0.0087223 | 3.4376e-05
2012 | 2012-02-15 | B | 9.9892 | 0.0085848 | 3.1251e-05
2012 | 2012-02-15 | B | 46.99 | 0.043614 | 0.00014688
2012 | 2012-02-15 | B | 7.9922 | 0.0095411 | 2.5001e-05
2012 | 2012-02-15 | B | 70.9849 | 0.04348 | 0.00022188
2012 | 2012-02-15 | C | 108.8587 | 0.030278 | 0.00037502
2012 | 2012-02-15 | C | 596.7111 | 0.16224 | 0.0021595
2012 | 2012-02-16 | C | 757.75 | 0.021313 | 0.0023688
2012 | 2012-02-16 | B | 64.9803 | 0.030258 | 0.00020313
2012 | 2012-02-16 | B | 183.9818 | 0.093145 | 0.00057502
2012 | 2012-02-15 | C | 1.8889 | 0.00014167 | 6.2503e-06
2012 | 2012-02-16 | B | 20.9908 | 0.021254 | 6.5628e-05
2012 | 2012-02-16 | B | 7.9789 | 0.003466 | 2.5001e-05
2012 | 2012-02-16 | B | 156.9945 | 0.26396 | 0.00049064
2012 | 2012-02-16 | C | 113.8 | 0.0042677 | 0.00035626
2012 | 2012-02-16 | B | 51.1842 | 0.066382 | 0.00016563
2012 | 2012-02-16 | B | 7.9929 | 0.010466 | 2.5001e-05
2012 | 2012-02-17 | C | 274.8125 | 0.011165 | 0.00085941
2012 | 2012-02-17 | C | 125.85 | 0.0066861 | 0.00039377
2012 | 2012-02-17 | C | 372.9 | 0.031465 | 0.0011657
2012 | 2012-02-17 | B | 26.9919 | 0.030873 | 8.4378e-05
2012 | 2012-02-17 | B | 10.9902 | 0.010372 | 3.4376e-05
2012 | 2012-02-17 | C | 87.9732 | 0.029967 | 0.00027501
2012 | 2012-02-17 | C | 165.961 | 0.03838 | 0.00051877
2012 | 2012-02-17 | C | 112.9647 | 0.028948 | 0.00035314
2012 | 2012-02-18 | C | 694.9423 | 0.10642 | 0.002172
2012 | 2012-02-18 | C | 4.9881 | 0.0038815 | 1.5626e-05
2012 | 2012-02-19 | C | 27.9062 | 0.0025291 | 8.7504e-05
2012 | 2012-02-19 | C | 167.2654 | 0.083113 | 0.00090629
2012 | 2012-02-20 | C | 40.25 | 0.00012579 | 0.00012813
2012 | 2012-02-20 | C | 51.85 | 0.0027546 | 0.00016251
2012 | 2012-02-20 | C | 11.9876 | 0.0089161 | 3.7502e-05
2012 | 2012-02-20 | B | 2.9887 | 0.0024565 | 9.3754e-06
2012 | 2012-02-20 | C | 615.7803 | 0.24825 | 0.0030126
2012 | 2012-02-20 | B | 1.961 | 0.00045351 | 6.2503e-06
2012 | 2012-02-20 | B | 1.9818 | 0.0010033 | 6.2503e-06
2012 | 2012-02-21 | C | 848.8966 | 0.068976 | 0.0026532
2012 | 2012-02-21 | B | 40.9906 | 0.040608 | 0.00012813
2012 | 2012-02-21 | B | 19.9286 | 0.0024289 | 6.2503e-05
2012 | 2012-02-20 | B | 114.9779 | 0.04779 | 0.00035939
2012 | 2012-02-22 | B | 49.9843 | 0.029367 | 0.00015626
2012 | 2012-02-22 | B | 50.9779 | 0.021189 | 0.00015938
2012 | 2012-02-22 | B | 43.9858 | 0.028729 | 0.00013751
2012 | 2012-02-22 | B | 21.9 | 0.0018479 | 6.8753e-05
2012 | 2012-02-22 | C | 454.3299 | 0.13346 | 0.0021688
2012 | 2012-02-22 | C | 82.9531 | 0.015814 | 0.00025939
2012 | 2012-02-23 | C | 70.9091 | 0.006648 | 0.00022188
2012 | 2012-02-23 | C | 44.94 | 0.0066008 | 0.00014063
2012 | 2012-02-23 | C | 39.9583 | 0.0086164 | 0.00012501
2012 | 2012-02-23 | C | 12.9789 | 0.0056379 | 4.0627e-05
2012 | 2012-02-23 | C | 19.9167 | 0.002054 | 6.2503e-05
2012 | 2012-02-23 | C | 535.0408 | 0.076915 | 0.0023032
2012 | 2012-02-23 | C | 654.9118 | 0.063447 | 0.002047
2012 | 2012-02-23 | C | 218.437 | 0.31197 | 0.0022188
2012 | 2012-02-23 | C | 54.9552 | 0.010991 | 0.00017188
2012 | 2012-02-23 | C | 961.0833 | 0.24328 | 0.0050533
2012 | 2012-02-23 | B | 9.9914 | 0.010741 | 3.1251e-05
2012 | 2012-02-23 | C | 6.6628 | 0.030504 | 0.00031251
2012 | 2012-02-21 | B | 260.7468 | 0.06193 | 0.00082816
2012 | 2012-02-23 | C | 92.9009 | 0.031355 | 0.00070315
2012 | 2012-02-24 | C | 544.9583 | 0.11751 | 0.002447
2012 | 2012-02-22 | C | 8.9167 | 0.00091957 | 2.8126e-05
2012 | 2012-02-22 | B | 247.1481 | 0.060245 | 0.00082816
2012 | 2012-02-23 | B | 99.9492 | 0.017492 | 0.00031251
2012 | 2012-02-24 | C | 10.9818 | 0.0055598 | 3.4376e-05
2012 | 2012-02-24 | B | 19.97 | 0.0060537 | 6.2503e-05
2012 | 2012-02-24 | B | 95.9892 | 0.082194 | 0.00030001
2012 | 2012-02-24 | C | 229.9722 | 0.075463 | 0.00071878
2012 | 2012-02-24 | B | 3.9697 | 0.001191 | 1.2501e-05
2012 | 2012-02-24 | C | 127.4642 | 0.11552 | 0.0018563
2012 | 2012-02-25 | C | 416.2778 | 0.23026 | 0.0026845
2012 | 2012-02-25 | C | 2.9877 | 0.0022408 | 9.3754e-06
2012 | 2012-02-25 | C | 4.9926 | 0.0062878 | 1.5626e-05
2012 | 2012-02-25 | B | 5.9856 | 0.0038534 | 1.8751e-05
2012 | 2012-02-25 | B | 1.9833 | 0.0010971 | 6.2503e-06
2012 | 2012-02-26 | C | 9.9893 | 0.0086473 | 3.1251e-05
2012 | 2012-02-26 | C | 108.1719 | 0.063892 | 0.00051877
2012 | 2012-02-27 | B | 1.9655 | 0.00051597 | 6.2503e-06
2012 | 2012-02-27 | C | 157.925 | 0.018261 | 0.00049377
2012 | 2012-02-27 | C | 27.9143 | 0.0027915 | 8.7504e-05
2012 | 2012-02-27 | C | 337.339 | 0.059037 | 0.0011282
2012 | 2012-02-27 | C | 16.963 | 0.0041349 | 5.3127e-05
2012 | 2012-02-27 | C | 16.96 | 0.0038162 | 5.3127e-05
2012 | 2012-02-28 | C | 694.8 | 0.026056 | 0.002172
2012 | 2012-02-28 | C | 2122.8519 | 0.33834 | 0.0082097
2012 | 2012-02-27 | C | 610.9608 | 0.18902 | 0.0049815
2012 | 2012-02-28 | B | 7.9677 | 0.002241 | 2.5001e-05
2012 | 2012-02-28 | C | 6.9538 | 0.0013474 | 2.1876e-05
2012 | 2012-02-28 | C | 2.9796 | 0.0013409 | 9.3754e-06
2012 | 2012-02-28 | B | 1.9444 | 0.00030991 | 6.2503e-06
2012 | 2012-02-28 | B | 93.9893 | 0.081363 | 0.00029376
2012 | 2012-02-28 | B | 9.9905 | 0.0097411 | 3.1251e-05
2012 | 2012-02-28 | B | 1.9524 | 0.00036609 | 6.2503e-06
2012 | 2012-02-28 | B | 2.9922 | 0.0035815 | 9.3754e-06
2012 | 2012-02-28 | B | 45.9879 | 0.035211 | 0.00014376
2012 | 2012-02-28 | B | 47.9878 | 0.036442 | 0.00015001
2012 | 2012-02-28 | B | 17.9891 | 0.015291 | 5.6252e-05
2012 | 2012-02-28 | C | 268.9 | 0.022689 | 0.00084066
2012 | 2012-02-29 | B | 17.9906 | 0.017766 | 5.6252e-05
2012 | 2012-02-29 | C | 4.8929 | 0.00038227 | 1.5626e-05
2012 | 2012-02-29 | B | 5.9924 | 0.007341 | 1.8751e-05
2012 | 2012-02-29 | B | 3.9651 | 0.0010285 | 1.2501e-05
2012 | 2012-02-28 | C | 73.1263 | 0.24544 | 0.00034064
2012 | 2012-02-29 | C | 285.0839 | 0.13542 | 0.0016907
2012 | 2012-02-29 | C | 103.6579 | 0.060578 | 0.00065315
2012 | 2012-02-27 | B | 46.7 | 0.0010216 | 0.00014688
2012 | 2012-02-29 | C | 1112.5833 | 0.11474 | 0.005069
2012 | 2012-02-29 | C | 241.1902 | 0.15226 | 0.0015188
2012 | 2012-03-01 | C | 717.2636 | 0.28243 | 0.0036876
2012 | 2012-03-01 | C | 980.9375 | 0.13795 | 0.0030657
2012 | 2012-03-01 | C | 23.9231 | 0.0026915 | 7.5003e-05
2012 | 2012-03-01 | C | 8.8696 | 0.00055437 | 2.8126e-05
2012 | 2012-03-01 | B | 90.9862 | 0.061134 | 0.00028439
2012 | 2012-03-01 | C | 39.3996 | 0.06649 | 0.00025626
2012 | 2012-03-01 | C | 95.2833 | 0.052706 | 0.00043127
2012 | 2012-03-01 | B | 23.9915 | 0.026092 | 7.5003e-05
2012 | 2012-03-01 | C | 21.9879 | 0.016835 | 6.8753e-05
2012 | 2012-03-01 | C | 178.9492 | 0.031317 | 0.0005594
2012 | 2012-03-01 | C | 104.993 | 0.13978 | 0.00032814
2012 | 2012-03-01 | B | 84.9855 | 0.05418 | 0.00026564
2012 | 2012-03-01 | B | 4.9885 | 0.0040378 | 1.5626e-05
2012 | 2012-03-01 | C | 143.3209 | 0.058674 | 0.0012313
2012 | 2012-03-02 | C | 424.95 | 0.022576 | 0.0019501
2012 | 2012-03-01 | B | 97.9709 | 0.030617 | 0.00030626
2012 | 2012-03-01 | C | 3381.8889 | 0.15853 | 0.012188
2012 | 2012-03-01 | C | 51.9423 | 0.007954 | 0.00016251
2012 | 2012-03-01 | C | 6003.6721 | 2.2327 | 0.027648
2012 | 2012-03-02 | B | 116.9647 | 0.029973 | 0.00036564
2012 | 2012-03-02 | B | 9.9909 | 0.010179 | 3.1251e-05
2012 | 2012-03-02 | C | 253.7 | 0.0055499 | 0.00079378
2012 | 2012-03-02 | C | 144.125 | 0.031078 | 0.00085941
2012 | 2012-03-01 | B | 32.9907 | 0.032992 | 0.00010313
2012 | 2012-03-01 | C | 254.5265 | 0.49317 | 0.0037127
2012 | 2012-03-01 | C | 6.3613 | 0.025088 | 7.8128e-05
2012 | 2012-03-02 | C | 24.9797 | 0.011319 | 7.8128e-05
2012 | 2012-03-02 | C | 11.9062 | 0.001079 | 3.7502e-05
2012 | 2012-03-02 | C | 402.5 | 0.041509 | 0.0019313
2012 | 2012-03-02 | C | 139.8769 | 0.14425 | 0.0017938
2012 | 2012-03-03 | C | 145.6226 | 0.095114 | 0.00071565
2012 | 2012-03-03 | C | 885.1538 | 0.099584 | 0.0035033
2012 | 2012-03-03 | C | 16.8929 | 0.0013198 | 5.3127e-05
2012 | 2012-03-03 | C | 243.1235 | 0.059264 | 0.0014782
2012 | 2012-03-03 | C | 7.9143 | 0.00079146 | 2.5001e-05
2012 | 2012-03-03 | C | 55.9717 | 0.018017 | 0.00017501
2012 | 2012-03-03 | C | 60.94 | 0.0089509 | 0.00019063
2012 | 2012-03-04 | C | 5.9091 | 0.000554 | 1.8751e-05
2012 | 2012-03-03 | C | 184.1839 | 0.19858 | 0.00068753
2012 | 2012-03-03 | B | 124.2591 | 0.073782 | 0.00041564
2012 | 2012-03-03 | C | 16.9697 | 0.0050911 | 5.3127e-05
2012 | 2012-03-03 | C | 127.0352 | 0.088928 | 0.00077503
2012 | 2012-03-03 | C | 240.7313 | 0.14896 | 0.0012813
2012 | 2012-03-03 | C | 901.6074 | 1.3553 | 0.0028189
2012 | 2012-03-03 | C | 178.5534 | 0.1395 | 0.00093754
2012 | 2012-03-03 | C | 190.0563 | 0.09325 | 0.0016719
2012 | 2012-03-03 | C | 138.7901 | 0.33962 | 0.00045627
2012 | 2012-03-03 | C | 168.8605 | 0.11187 | 0.0005969
2012 | 2012-03-03 | B | 384.8136 | 0.067345 | 0.0015594
2012 | 2012-03-03 | C | 861.9896 | 0.76774 | 0.0026939
2012 | 2012-03-03 | C | 473.8366 | 0.68413 | 0.002922
2012 | 2012-03-03 | C | 815.9925 | 1.0149 | 0.0025501
2012 | 2012-03-03 | C | 567.9941 | 0.89463 | 0.0017751
2012 | 2012-03-03 | C | 29.4 | 0.00018376 | 9.3754e-05
2012 | 2012-03-03 | C | 92.9474 | 0.015686 | 0.00029064
2012 | 2012-03-03 | C | 224.1406 | 1.4276 | 0.00072503
2012 | 2012-03-03 | C | 116.1562 | 0.65885 | 0.00087191
2012 | 2012-03-03 | C | 27.2513 | 1.169 | 0.0043346
2012 | 2012-03-03 | C | 659.9844 | 0.38982 | 0.0020626
2012 | 2012-03-03 | C | 2345.9812 | 1.151 | 0.0073315
2012 | 2012-03-03 | B | 6.9806 | 0.0033159 | 2.1876e-05
2012 | 2012-03-03 | C | 61.9779 | 0.025761 | 0.00019376
2012 | 2012-03-03 | C | 40.6263 | 0.035296 | 0.00022813
2012 | 2012-03-03 | C | 740.5717 | 1.3169 | 0.002847
2012 | 2012-03-03 | C | 239.9933 | 0.33225 | 0.00075003
2012 | 2012-03-03 | C | 42.9255 | 0.037427 | 0.00014688
2012 | 2012-03-03 | C | 665.7237 | 0.94245 | 0.0021032
2012 | 2012-03-03 | C | 212.7025 | 0.36892 | 0.00070003
2012 | 2012-03-03 | C | 2.9577 | 0.00062855 | 9.3754e-06
2012 | 2012-03-04 | C | 208.1929 | 0.089136 | 0.0017626
2012 | 2012-03-04 | C | 26.9545 | 0.0053069 | 8.4378e-05
2012 | 2012-03-04 | C | 124.5478 | 0.059941 | 0.00074066
2012 | 2012-03-03 | C | 84.9724 | 0.056828 | 0.0011313
2012 | 2012-03-03 | C | 69.9139 | 0.15666 | 0.0014001
2012 | 2012-03-03 | C | 83.413 | 0.035191 | 0.0023751
2012 | 2012-03-03 | C | 8.9739 | 0.003141 | 2.8126e-05
2012 | 2012-03-03 | C | 2.9333 | 0.00038502 | 9.3754e-06
2012 | 2012-03-03 | C | 14.9362 | 0.0020538 | 4.6877e-05
2012 | 2012-03-03 | C | 28.9455 | 0.0047038 | 9.0629e-05
2012 | 2012-03-03 | C | 110.9951 | 0.21263 | 0.00034689
2012 | 2012-03-03 | C | 366.6473 | 0.25323 | 0.001997
2012 | 2012-03-03 | C | 105.2712 | 0.29017 | 0.00035626
2012 | 2012-03-03 | C | 1132.9866 | 0.7825 | 0.0035408
2012 | 2012-03-03 | C | 19.9538 | 0.0038662 | 6.2503e-05
2012 | 2012-03-03 | C | 336.4628 | 0.78757 | 0.0035439
2012 | 2012-03-03 | C | 179.984 | 0.10349 | 0.00056252
2012 | 2012-03-03 | C | 5.9967 | 0.017035 | 1.8751e-05
2012 | 2012-03-03 | C | 32.6923 | 0.49541 | 0.00062503
2012 | 2012-03-03 | C | 116.3441 | 0.25669 | 0.00047189
2012 | 2012-03-03 | C | 242.9943 | 0.4002 | 0.00075941
2012 | 2012-03-03 | C | 26.9985 | 0.17077 | 8.4378e-05
2012 | 2012-03-03 | C | 118.472 | 0.27028 | 0.00037502
2012 | 2012-03-03 | C | 11.9975 | 0.044392 | 3.7502e-05
2012 | 2012-03-03 | C | 11.2875 | 0.065894 | 0.00042814
2012 | 2012-03-03 | C | 76.6381 | 0.24549 | 0.00024689
2012 | 2012-03-04 | C | 31.9647 | 0.0081913 | 0.0001
2012 | 2012-03-03 | C | 351.6839 | 0.65724 | 0.0019688
2012 | 2012-03-03 | C | 323.1289 | 1.5481 | 0.0020251
2012 | 2012-03-04 | C | 166.9869 | 0.078278 | 0.0015594
2012 | 2012-03-03 | C | 17.9388 | 0.0025788 | 5.6252e-05
2012 | 2012-03-04 | C | 199.9167 | 0.020617 | 0.00062503
2012 | 2012-03-03 | C | 126.8447 | 0.062632 | 0.00065628
2012 | 2012-03-03 | C | 156.7692 | 0.0048992 | 0.00049064
2012 | 2012-03-03 | C | 141.9289 | 0.99088 | 0.0006344
2012 | 2012-03-03 | C | 285.9959 | 0.65514 | 0.00089379
2012 | 2012-03-03 | C | 147.4289 | 0.88369 | 0.0014626
2012 | 2012-03-05 | C | 51.9333 | 0.0068165 | 0.00016251
2012 | 2012-03-03 | C | 196.415 | 0.21852 | 0.0012469
2012 | 2012-03-03 | C | 127.8345 | 0.2353 | 0.00083753
2012 | 2012-03-03 | C | 751.9934 | 1.0599 | 0.0023501
2012 | 2012-03-03 | C | 99.475 | 0.036372 | 0.00036564
2012 | 2012-03-05 | C | 16.94 | 0.0024882 | 5.3127e-05
2012 | 2012-03-03 | C | 54.325 | 0.48164 | 0.0042189
2012 | 2012-03-03 | C | 262.1587 | 1.0298 | 0.0010094
2012 | 2012-03-03 | C | 1.9964 | 0.0051596 | 6.2503e-06
2012 | 2012-03-03 | C | 197.4712 | 0.43816 | 0.00066253
2012 | 2012-03-03 | C | 38.9774 | 0.015835 | 0.00012188
2012 | 2012-03-03 | C | 64.9375 | 0.0091322 | 0.00020313
2012 | 2012-03-03 | C | 49.9434 | 0.007804 | 0.00015626
2012 | 2012-03-03 | C | 513.9375 | 0.072275 | 0.0016063
2012 | 2012-03-03 | C | 34.5031 | 0.29135 | 0.00031564
2012 | 2012-03-03 | C | 387.9355 | 1.0863 | 0.0012469
2012 | 2012-03-03 | C | 232.3247 | 1.8427 | 0.0011313
2012 | 2012-03-03 | C | 41.6418 | 0.034486 | 0.00053127
2012 | 2012-03-03 | C | 59.9434 | 0.0093665 | 0.00018751
2012 | 2012-03-03 | C | 242.9492 | 0.042518 | 0.00075941
2012 | 2012-03-05 | B | 2.9902 | 0.0028408 | 9.3754e-06
2012 | 2012-03-03 | C | 112.2588 | 0.088407 | 0.00071253
2012 | 2012-03-05 | C | 6.8571 | 0.00038573 | 2.1876e-05
2012 | 2012-03-03 | C | 37.9987 | 0.27135 | 0.00011875
2012 | 2012-03-03 | C | 60.0447 | 0.64194 | 0.0011438
2012 | 2012-03-05 | B | 2.9795 | 0.0013315 | 9.3754e-06
2012 | 2012-03-03 | C | 80.5334 | 1.2209 | 0.00096879
2012 | 2012-03-03 | C | 160.3364 | 0.99062 | 0.00084378
2012 | 2012-03-03 | C | 11.9 | 0.0010041 | 3.7502e-05
2012 | 2012-03-03 | C | 5.9722 | 0.0019597 | 1.8751e-05
2012 | 2012-03-03 | C | 1.976 | 0.00075338 | 6.2503e-06
2012 | 2012-03-03 | C | 38.5898 | 0.054028 | 0.00016563
2012 | 2012-03-03 | C | 153.5 | 1.6468 | 0.0011375
2012 | 2012-03-03 | C | 6.997 | 0.02167 | 2.1876e-05
2012 | 2012-03-03 | C | 1883.6897 | 3.3025 | 0.0070722
2012 | 2012-03-01 | C | 191.5879 | 0.096995 | 0.00098754
2012 | 2012-03-03 | C | 1521.662 | 2.0258 | 0.0050502
2012 | 2012-03-05 | C | 1.9674 | 0.0005472 | 6.2503e-06
2012 | 2012-03-03 | C | 665.6337 | 0.85704 | 0.0021095
2012 | 2012-03-05 | B | 22.9552 | 0.0045912 | 7.1878e-05
2012 | 2012-03-05 | B | 14.9538 | 0.0028974 | 4.6877e-05
2012 | 2012-03-03 | C | 2183.9776 | 0.8941 | 0.0068253
2012 | 2012-03-03 | C | 151.979 | 0.066494 | 0.00047502
2012 | 2012-03-03 | C | 1.976 | 0.00075338 | 6.2503e-06
2012 | 2012-03-03 | C | 7.98 | 0.003666 | 2.5001e-05
2012 | 2012-03-03 | C | 3.9856 | 0.0025534 | 1.2501e-05
2012 | 2012-03-03 | C | 1139.9862 | 0.7624 | 0.0035626
2012 | 2012-03-03 | C | 2327.9552 | 0.46561 | 0.0072753
2012 | 2012-03-04 | C | 13.9167 | 0.0014352 | 4.3752e-05
2012 | 2012-03-03 | C | 38.8549 | 0.37873 | 0.00012188
2012 | 2012-03-03 | C | 102.2006 | 1.1613 | 0.0014313
2012 | 2012-03-05 | C | 671.9483 | 0.1155 | 0.0021001
2012 | 2012-03-03 | C | 113.9518 | 0.028489 | 0.0005219
2012 | 2012-03-05 | C | 337.8 | 0.012668 | 0.0010563
2012 | 2012-03-03 | C | 26.3025 | 0.098392 | 9.0629e-05
2012 | 2012-03-06 | B | 2.9634 | 0.00073162 | 9.3754e-06
2012 | 2012-03-03 | C | 209.3822 | 2.4584 | 0.00070628
2012 | 2012-03-03 | C | 111.3208 | 1.6744 | 0.00046252
2012 | 2012-03-03 | C | 164.9992 | 1.9713 | 0.00051565
2012 | 2012-03-06 | B | 200.9917 | 0.22424 | 0.00062815
2012 | 2012-03-06 | C | 3.9492 | 0.00069113 | 1.2501e-05
2012 | 2012-03-06 | C | 7.9595 | 0.0017661 | 2.5001e-05
2012 | 2012-03-03 | C | 50.8024 | 0.76683 | 0.00046564
2012 | 2012-03-03 | C | 861.9894 | 0.75697 | 0.0026939
2012 | 2012-03-03 | C | 66.9964 | 0.411 | 0.00055627
2012 | 2012-03-07 | B | 34.9651 | 0.0090694 | 0.00010938
2012 | 2012-03-06 | C | 73.961 | 0.017104 | 0.00023126
2012 | 2012-03-03 | C | 44.2063 | 0.59819 | 0.00035314
2012 | 2012-03-07 | C | 64.2553 | 0.027711 | 0.00099067
2012 | 2012-03-03 | C | 47.989 | 0.040342 | 0.00015001
2012 | 2012-03-07 | B | 47.9889 | 0.040042 | 0.00015001
2012 | 2012-03-03 | C | 111.195 | 1.6791 | 0.0011407
2012 | 2012-03-05 | C | 167.1011 | 0.14309 | 0.002272
2012 | 2012-03-03 | C | 264.4787 | 6.6866 | 0.0026189
2012 | 2012-03-06 | C | 651.162 | 0.28286 | 0.0026501
2012 | 2012-03-03 | C | 37.1639 | 1.0662 | 0.00074066
2012 | 2012-03-03 | C | 7.9957 | 0.017366 | 2.5001e-05
2012 | 2012-03-06 | C | 1675.9362 | 0.47661 | 0.0058752
2012 | 2012-03-03 | C | 102.8524 | 1.6325 | 0.0011688
2012 | 2012-03-03 | C | 135.5592 | 1.4692 | 0.00096879
2012 | 2012-03-08 | B | 1.985 | 0.0012221 | 6.2503e-06
2012 | 2012-03-03 | C | 39.1115 | 0.92172 | 0.00071878
2012 | 2012-03-07 | C | 4.96 | 0.001116 | 1.5626e-05
2012 | 2012-03-03 | C | 402.1833 | 0.071642 | 0.0019407
2012 | 2012-03-08 | B | 150.6337 | 0.14122 | 0.0014282
2012 | 2012-03-08 | C | 81.4 | 0.090816 | 0.0011032
2012 | 2012-03-09 | C | 140 | 0.10325 | 0.0016594
2012 | 2012-03-03 | C | 66.3736 | 0.71956 | 0.00034064
2012 | 2012-03-08 | C | 96.9739 | 0.033942 | 0.00030314
2012 | 2012-03-08 | C | 7.9677 | 0.002241 | 2.5001e-05
2012 | 2012-03-08 | C | 67.0556 | 0.13118 | 0.0007094
2012 | 2012-03-07 | C | 1430.7778 | 0.1878 | 0.0045377
2012 | 2012-03-09 | C | 114.4576 | 0.083343 | 0.00042189
2012 | 2012-03-08 | C | 60.625 | 0.0009473 | 0.00019063
2012 | 2012-03-03 | C | 28.9 | 0.0024385 | 9.0629e-05
2012 | 2012-03-03 | C | 198.9585 | 6.4764 | 0.0012469
2012 | 2012-03-09 | C | 167.9118 | 0.016267 | 0.00052502
2012 | 2012-03-03 | C | 88.1604 | 2.1113 | 0.00049377
2012 | 2012-03-03 | C | 128.9376 | 6.5132 | 0.00096879
2012 | 2012-03-09 | B | 54.9908 | 0.055337 | 0.00017188
2012 | 2012-03-03 | C | 25.0918 | 0.69052 | 0.00074378
2012 | 2012-03-08 | C | 30.6771 | 0.13422 | 0.0005219
2012 | 2012-03-03 | C | 204.015 | 9.5049 | 0.0022032
2012 | 2012-03-07 | C | 24.875 | 0.0016325 | 7.8128e-05
2012 | 2012-03-09 | C | 113.8846 | 0.0081858 | 0.00035626
2012 | 2012-03-10 | C | 356.5 | 0.30415 | 0.0024376
2012 | 2012-03-05 | C | 673.9268 | 0.080032 | 0.0021063
2012 | 2012-03-03 | C | 14.3484 | 0.28456 | 0.00015313
2012 | 2012-03-10 | B | 26.9909 | 0.027414 | 8.4378e-05
2012 | 2012-03-03 | C | 1920.9143 | 0.1921 | 0.0060034
2012 | 2012-03-08 | C | 10.8235 | 0.00047355 | 3.4376e-05
2012 | 2012-03-06 | C | 795.9247 | 0.45519 | 0.0073253
2012 | 2012-03-09 | C | 4.8 | 0.00018001 | 1.5626e-05
2012 | 2012-03-09 | C | 4.9444 | 0.00078805 | 1.5626e-05
2012 | 2012-03-09 | C | 10.9412 | 0.0016412 | 3.4376e-05
2012 | 2012-03-03 | C | 29.9902 | 0.028304 | 9.3754e-05
2012 | 2012-03-10 | C | 9.975 | 0.0036473 | 3.1251e-05
2012 | 2012-03-03 | C | 2.9474 | 0.00049739 | 9.3754e-06
2012 | 2012-03-03 | C | 18.9934 | 0.026889 | 5.9377e-05
2012 | 2012-03-11 | C | 88.7972 | 0.14014 | 0.0017782
2012 | 2012-03-03 | C | 12.9934 | 0.018313 | 4.0627e-05
2012 | 2012-03-07 | C | 209.5942 | 0.088426 | 0.00071565
2012 | 2012-03-11 | C | 99.8051 | 0.083902 | 0.00056252
2012 | 2012-03-11 | C | 12.88 | 0.00088554 | 4.0627e-05
2012 | 2012-03-11 | C | 143.6404 | 0.12973 | 0.00075628
2012 | 2012-03-11 | C | 78.5155 | 0.038769 | 0.00047189
2012 | 2012-03-11 | C | 538.94 | 0.75286 | 0.0050815
2012 | 2012-03-11 | C | 66.96 | 0.015067 | 0.00020938
2012 | 2012-03-12 | C | 138.0154 | 0.13845 | 0.0015251
2012 | 2012-03-11 | C | 81.0551 | 0.23836 | 0.0019063
2012 | 2012-03-12 | C | 72.9813 | 0.035808 | 0.00022813
2012 | 2012-03-12 | C | 9.9804 | 0.0046785 | 3.1251e-05
2012 | 2012-03-12 | C | 5.9979 | 0.026823 | 1.8751e-05
2012 | 2012-03-12 | B | 7.9778 | 0.003291 | 2.5001e-05
2012 | 2012-03-12 | B | 5.9833 | 0.0033097 | 1.8751e-05
2012 | 2012-03-12 | B | 70.9916 | 0.078538 | 0.00022188
2012 | 2012-03-12 | C | 145.2795 | 0.14483 | 0.00084066
2012 | 2012-03-12 | B | 81.9902 | 0.077381 | 0.00025626
2012 | 2012-03-11 | C | 19.1625 | 0.0046112 | 3.7502e-05
2012 | 2012-03-13 | B | 15.9893 | 0.013841 | 5.0002e-05
2012 | 2012-03-13 | B | 131.9921 | 0.1551 | 0.00041252
2012 | 2012-03-13 | C | 17.9918 | 0.020354 | 5.6252e-05
2012 | 2012-03-13 | B | 47.9571 | 0.010041 | 0.00015001
2012 | 2012-03-03 | C | 52.0047 | 2.418 | 0.00099692
2012 | 2012-03-13 | C | 81.9741 | 0.028948 | 0.00025626
2012 | 2012-03-13 | C | 205.2122 | 0.1552 | 0.0019501
2012 | 2012-03-13 | B | 44.9909 | 0.045836 | 0.00014063
2012 | 2012-03-02 | C | 2.9912 | 0.023257 | 0.00010625
2012 | 2012-03-03 | C | 919.991 | 0.95165 | 0.0028751
2012 | 2012-03-14 | B | 18.9932 | 0.026117 | 5.9377e-05
2012 | 2012-03-03 | C | 112.9866 | 0.078035 | 0.00035314
2012 | 2012-03-14 | C | 114.95 | 0.020476 | 0.00035939
2012 | 2012-03-14 | C | 25.9688 | 0.0075475 | 8.1253e-05
2012 | 2012-03-11 | C | 1.9524 | 0.00036609 | 6.2503e-06
2012 | 2012-03-14 | B | 46.9944 | 0.077984 | 0.00014688
2012 | 2012-03-14 | B | 13.9894 | 0.012197 | 4.3752e-05
2012 | 2012-03-14 | B | 153.95 | 0.027423 | 0.00048127
2012 | 2012-03-14 | B | 68.9941 | 0.10867 | 0.00021563
2012 | 2012-03-12 | C | 87.9864 | 0.059668 | 0.00027501
2012 | 2012-03-13 | C | 82.987 | 0.059131 | 0.00025939
2012 | 2012-03-15 | B | 50.9444 | 0.0081196 | 0.00015938
2012 | 2012-03-03 | C | 1137.9784 | 0.48366 | 0.0035564
2012 | 2012-03-03 | C | 1185.9722 | 0.38916 | 0.0037064
2012 | 2012-03-15 | B | 45.9937 | 0.067556 | 0.00014376
2012 | 2012-03-15 | B | 13.9889 | 0.011716 | 4.3752e-05
2012 | 2012-03-16 | C | 681.8493 | 0.14916 | 0.0030595
2012 | 2012-03-15 | C | 2.9824 | 0.0015565 | 9.3754e-06
2012 | 2012-03-15 | B | 3.9912 | 0.0042034 | 1.2501e-05
2012 | 2012-03-15 | C | 17.9318 | 0.0022976 | 5.6252e-05
2012 | 2012-03-15 | C | 339.9268 | 0.040368 | 0.0010625
2012 | 2012-03-15 | C | 2.9091 | 0.00027274 | 9.3754e-06
2012 | 2012-03-15 | C | 26.8846 | 0.0019324 | 8.4378e-05
2012 | 2012-03-15 | C | 198.94 | 0.02922 | 0.0006219
2012 | 2012-03-15 | C | 150.8333 | 0.0070706 | 0.00047189
2012 | 2012-03-15 | C | 130.6105 | 0.037552 | 0.00067815
2012 | 2012-03-15 | C | 39.8889 | 0.0029918 | 0.00012501
2012 | 2012-03-16 | B | 2.9835 | 0.001669 | 9.3754e-06
2012 | 2012-03-16 | B | 2.9834 | 0.0016596 | 9.3754e-06
2012 | 2012-03-16 | B | 13.9895 | 0.012416 | 4.3752e-05
2012 | 2012-03-16 | B | 79.9882 | 0.062993 | 0.00025001
2012 | 2012-03-16 | B | 98.9891 | 0.084144 | 0.00030939
2012 | 2012-03-16 | C | 39.0064 | 0.17151 | 0.0016719
2012 | 2012-03-18 | C | 122.844 | 0.29407 | 0.001075
2012 | 2012-03-18 | B | 52.9941 | 0.084132 | 0.00016563
2012 | 2012-03-18 | C | 22.9423 | 0.0035132 | 7.1878e-05
2012 | 2012-03-18 | C | 4.0341 | 0.0025467 | 2.8126e-05
2012 | 2012-03-18 | C | 175.9923 | 0.21285 | 0.00055002
2012 | 2012-03-19 | C | 216.5985 | 0.18344 | 0.00095316
2012 | 2012-03-03 | C | 26.8494 | 0.7785 | 0.0010938
2012 | 2012-03-19 | C | 2.7273 | 6.8185e-05 | 9.3754e-06
2012 | 2012-03-19 | C | 319.9375 | 0.044993 | 0.001
2012 | 2012-03-19 | C | 446.8109 | 0.27648 | 0.0036501
2012 | 2012-03-03 | C | 97.13 | 4.5091 | 0.0016469
2012 | 2012-03-19 | C | 98.9813 | 0.048565 | 0.00030939
2012 | 2012-03-19 | C | 13.8966 | 0.0011291 | 4.3752e-05
2012 | 2012-03-19 | C | 118.8235 | 0.0051987 | 0.00037189
2012 | 2012-03-19 | C | 24.875 | 0.0016325 | 7.8128e-05
2012 | 2012-03-19 | C | 236.3815 | 0.12558 | 0.0010594
2012 | 2012-03-20 | C | 118.9844 | 0.070278 | 0.00037189
2012 | 2012-03-20 | C | 639.3897 | 0.26576 | 0.0025001
2012 | 2012-03-19 | C | 97.9891 | 0.083294 | 0.00030626
2012 | 2012-03-19 | C | 347.0437 | 0.17028 | 0.0015407
2012 | 2012-03-19 | C | 59.9091 | 0.0056167 | 0.00018751
2012 | 2012-03-19 | C | 119.4236 | 0.084346 | 0.00072503
2012 | 2012-03-20 | C | 178.1687 | 0.087418 | 0.00095004
2012 | 2012-03-19 | C | 133.9739 | 0.046893 | 0.00041877
2012 | 2012-03-19 | C | 94.5476 | 0.098393 | 0.00061878
2012 | 2012-03-20 | C | 21.9803 | 0.010235 | 6.8753e-05
2012 | 2012-03-20 | C | 96.9797 | 0.043946 | 0.00030314
2012 | 2012-03-20 | C | 1371.5429 | 0.73723 | 0.0050627
2012 | 2012-03-20 | C | 130.9634 | 0.032333 | 0.00040939
2012 | 2012-03-20 | C | 112.4657 | 0.12196 | 0.001972
2012 | 2012-03-19 | C | 20.0919 | 0.061283 | 6.5628e-05
2012 | 2012-03-20 | C | 28.9143 | 0.0028915 | 9.0629e-05
2012 | 2012-03-20 | C | 105.2838 | 0.023361 | 0.00045627
2012 | 2012-03-20 | C | 67.339 | 0.12227 | 0.0005219
2012 | 2012-03-20 | C | 374.865 | 0.50843 | 0.0041095
2012 | 2012-03-20 | B | 50.987 | 0.03617 | 0.00015938
2012 | 2012-03-20 | C | 90.5508 | 0.065935 | 0.00033439
2012 | 2012-03-20 | C | 109.8315 | 0.029518 | 0.00037502
2012 | 2012-03-20 | C | 791.925 | 0.09157 | 0.0024751
2012 | 2012-03-20 | C | 16.9388 | 0.002435 | 5.3127e-05
2012 | 2012-03-21 | C | 178.9659 | 0.04754 | 0.0005594
2012 | 2012-03-20 | C | 48.9348 | 0.0065759 | 0.00015313
2012 | 2012-03-20 | C | 257.1868 | 0.36329 | 0.0010907
2012 | 2012-03-20 | C | 55.9559 | 0.011367 | 0.00017501
2012 | 2012-03-20 | C | 21.0208 | 0.0092627 | 0.00015626
2012 | 2012-03-21 | B | 66.9836 | 0.03768 | 0.00020938
2012 | 2012-03-03 | C | 4.9455 | 0.00080367 | 1.5626e-05
2012 | 2012-03-03 | C | 170.9508 | 0.030986 | 0.0005344
2012 | 2012-03-20 | C | 11.9634 | 0.0029536 | 3.7502e-05
2012 | 2012-03-20 | C | 18.9706 | 0.0058693 | 5.9377e-05
2012 | 2012-03-21 | B | 20.9909 | 0.02132 | 6.5628e-05
2012 | 2012-03-20 | C | 30.9634 | 0.0076444 | 9.6879e-05
2012 | 2012-03-21 | B | 32.9871 | 0.023607 | 0.00010313
2012 | 2012-03-19 | C | 37.3283 | 0.27787 | 0.00012188
2012 | 2012-03-20 | C | 16.9808 | 0.0081193 | 5.3127e-05
2012 | 2012-03-20 | C | 285.9516 | 0.052724 | 0.00089379
2012 | 2012-03-21 | B | 43.9908 | 0.044268 | 0.00013751
2012 | 2012-03-21 | C | 53.9732 | 0.018385 | 0.00016876
2012 | 2012-03-21 | B | 32.9871 | 0.023607 | 0.00010313
2012 | 2012-03-21 | B | 665.9929 | 0.86999 | 0.0020813
2012 | 2012-03-20 | C | 81.9981 | 0.41001 | 0.00025626
2012 | 2012-03-20 | C | 7.9589 | 0.0017411 | 2.5001e-05
2012 | 2012-03-20 | C | 260.427 | 1.0898 | 0.003797
2012 | 2012-03-21 | C | 1.9474 | 0.00032863 | 6.2503e-06
2012 | 2012-03-20 | C | 114.1265 | 0.11734 | 0.0011375
2012 | 2012-03-21 | C | 175.0438 | 0.13566 | 0.0012813
2012 | 2012-03-21 | C | 890.9091 | 0.14478 | 0.0030751
2012 | 2012-03-21 | C | 1008.0606 | 0.40639 | 0.0051565
2012 | 2012-03-21 | C | 39.9712 | 0.012616 | 0.00012501
2012 | 2012-03-21 | C | 446.6622 | 0.51229 | 0.0020595
2012 | 2012-03-20 | C | 60.4716 | 0.3156 | 0.0010063
2012 | 2012-03-20 | C | 247.3411 | 0.29682 | 0.001125
2012 | 2012-03-03 | C | 75.5045 | 0.12978 | 0.00094066
2012 | 2012-03-20 | C | 153.985 | 0.19056 | 0.00070003
2012 | 2012-03-21 | C | 305.0128 | 0.29549 | 0.0012594
2012 | 2012-03-20 | C | 258.9677 | 0.072838 | 0.00080941
2012 | 2012-03-21 | C | 174.7872 | 0.049707 | 0.00061565
2012 | 2012-03-21 | C | 225.5751 | 0.16214 | 0.0023345
2012 | 2012-03-21 | C | 164.9918 | 0.18665 | 0.00051565
2012 | 2012-03-21 | C | 77.485 | 0.088143 | 0.0018595
2012 | 2012-03-20 | C | 12.9786 | 0.0055567 | 4.0627e-05
2012 | 2012-03-20 | C | 55.9965 | 0.1477 | 0.00017501
2012 | 2012-03-20 | C | 22.9615 | 0.0053818 | 7.1878e-05
2012 | 2012-03-20 | C | 44.9062 | 0.0040698 | 0.00014063
2012 | 2012-03-21 | C | 8.9032 | 0.00077906 | 2.8126e-05
2012 | 2012-03-19 | C | 21.3411 | 0.074497 | 6.8753e-05
2012 | 2012-03-21 | C | 258.1184 | 0.058886 | 0.00082191
2012 | 2012-03-20 | C | 59.5836 | 0.069641 | 0.00050315
2012 | 2012-03-20 | C | 402.8696 | 0.02518 | 0.0012594
2012 | 2012-03-20 | C | 188.3243 | 0.76216 | 0.0014657
2012 | 2012-03-21 | C | 443.9062 | 0.040231 | 0.0013876
2012 | 2012-03-20 | C | 28.9524 | 0.0054288 | 9.0629e-05
2012 | 2012-03-21 | C | 10.9538 | 0.0021224 | 3.4376e-05
2012 | 2012-03-20 | C | 186.7812 | 0.20372 | 0.002172
2012 | 2012-03-22 | C | 297.8571 | 0.016755 | 0.00093129
2012 | 2012-03-21 | C | 3.9032 | 0.00034155 | 1.2501e-05
2012 | 2012-03-20 | C | 175.25 | 0.06846 | 0.00085941
2012 | 2012-03-20 | C | 1.9977 | 0.007966 | 6.2503e-06
2012 | 2012-03-21 | C | 154.9967 | 0.43401 | 0.00048439
2012 | 2012-03-20 | C | 15.9714 | 0.0050911 | 5.0002e-05
2012 | 2012-03-20 | C | 15.999 | 0.1455 | 5.0002e-05
2012 | 2012-03-21 | C | 299.6316 | 0.44197 | 0.0041345
2012 | 2012-03-21 | C | 163.2117 | 0.41774 | 0.00065315
2012 | 2012-03-21 | C | 213.1987 | 0.71558 | 0.0035064
2012 | 2012-03-21 | C | 435.0918 | 0.5738 | 0.0029657
2012 | 2012-03-20 | C | 8.9143 | 0.00089146 | 2.8126e-05
2012 | 2012-03-20 | C | 1.9983 | 0.010735 | 6.2503e-06
2012 | 2012-03-21 | C | 304.4982 | 0.7727 | 0.0029376
2012 | 2012-03-22 | C | 24.9674 | 0.0069443 | 7.8128e-05
2012 | 2012-03-21 | C | 450.8571 | 0.025362 | 0.0014094
2012 | 2012-03-22 | C | 15.9455 | 0.0025912 | 5.0002e-05
2012 | 2012-03-20 | C | 8.4457 | 0.043629 | 0.00014063
2012 | 2012-03-21 | C | 34.6776 | 0.095151 | 0.00034689
2012 | 2012-03-03 | C | 155.5783 | 4.6131 | 0.00072503
2012 | 2012-03-20 | C | 3.0011 | 0.016591 | 1.2501e-05
2012 | 2012-03-21 | C | 237.8836 | 0.46389 | 0.0034501
2012 | 2012-03-20 | C | 195.8512 | 1.4047 | 0.0011657
2012 | 2012-03-21 | C | 20.5742 | 0.1493 | 0.00049064
2012 | 2012-03-21 | C | 48.5077 | 0.18555 | 0.00095316
2012 | 2012-03-03 | C | 331.2852 | 5.13 | 0.00105
2012 | 2012-03-19 | C | 240.694 | 0.098538 | 0.0011094
2012 | 2012-03-20 | C | 14.4329 | 0.069777 | 4.6877e-05
2012 | 2012-03-21 | C | 411.9964 | 1.0725 | 0.0012876
2012 | 2012-03-20 | C | 49.5858 | 0.17201 | 0.0011688
2012 | 2012-03-22 | C | 58.75 | 0.0016524 | 0.00018438
2012 | 2012-03-22 | B | 208.9712 | 0.065959 | 0.00065315
2012 | 2012-03-20 | C | 2.9268 | 0.00034758 | 9.3754e-06
2012 | 2012-03-20 | C | 10.9985 | 0.067093 | 3.4376e-05
2012 | 2012-03-21 | C | 124.802 | 0.15445 | 0.0006469
2012 | 2012-03-20 | C | 457.9366 | 1.102 | 0.0014626
2012 | 2012-03-20 | C | 81.2609 | 0.051806 | 0.00062503
2012 | 2012-03-22 | C | 46.9595 | 0.01042 | 0.00014688
2012 | 2012-03-21 | C | 354.575 | 0.83107 | 0.0033845
2012 | 2012-03-21 | C | 128.4101 | 0.30218 | 0.0020626
2012 | 2012-03-21 | C | 109.0242 | 0.19591 | 0.00087816
2012 | 2012-03-21 | C | 4264.6667 | 0.079966 | 0.013329
2012 | 2012-03-24 | C | 58.9423 | 0.0090259 | 0.00018438
2012 | 2012-03-24 | C | 13.9362 | 0.0019163 | 4.3752e-05
2012 | 2012-03-20 | B | 137.9679 | 0.079335 | 0.0015157
2012 | 2012-03-23 | C | 70.7564 | 0.016584 | 0.00035626
2012 | 2012-03-23 | C | 55.9211 | 0.0061166 | 0.00017501
2012 | 2012-03-23 | C | 5.9571 | 0.0012473 | 1.8751e-05
2012 | 2012-03-25 | C | 170.4694 | 0.05061 | 0.00070315
2012 | 2012-03-25 | C | 369.9213 | 0.24624 | 0.0030532
2012 | 2012-03-25 | C | 91.2075 | 0.044465 | 0.0006094
2012 | 2012-03-25 | C | 110.9303 | 0.068641 | 0.00074378
2012 | 2012-03-25 | C | 144.5842 | 0.084495 | 0.00055315
2012 | 2012-03-20 | C | 20.999 | 0.19103 | 6.5628e-05
2012 | 2012-03-20 | C | 1.999 | 0.018335 | 6.2503e-06
2012 | 2012-03-20 | C | 135.0532 | 1.4814 | 0.0038408
2012 | 2012-03-19 | C | 10.9444 | 0.0017443 | 3.4376e-05
2012 | 2012-03-03 | C | 63.5126 | 1.2796 | 0.0017063
2012 | 2012-03-03 | C | 11.9995 | 0.21836 | 3.7502e-05
2012 | 2012-03-20 | C | 79.2778 | 0.51557 | 0.0005469
2012 | 2012-03-03 | C | 19.9995 | 0.36419 | 6.2503e-05
2012 | 2012-03-26 | C | 407.9459 | 0.090517 | 0.0026689
2012 | 2012-03-03 | C | 54.2016 | 0.8305 | 0.0019657
2012 | 2012-03-03 | C | 318.3542 | 0.98296 | 0.0010844
2012 | 2012-03-03 | C | 76.2288 | 0.57293 | 0.00061878
2012 | 2012-03-03 | C | 6.9691 | 0.0020472 | 2.1876e-05
2012 | 2012-03-27 | C | 5.9741 | 0.0021097 | 1.8751e-05
2012 | 2012-03-27 | C | 850.42 | 0.12491 | 0.0037877
2012 | 2012-03-27 | C | 61.85 | 0.0032859 | 0.00019376
2012 | 2012-03-27 | C | 22.75 | 0.00063987 | 7.1878e-05
2012 | 2012-03-27 | C | 2.8929 | 0.00022601 | 9.3754e-06
2012 | 2012-03-27 | C | 7.9691 | 0.002341 | 2.5001e-05
2012 | 2012-03-27 | C | 42.9286 | 0.0052321 | 0.00013438
2012 | 2012-03-28 | C | 5.9769 | 0.0023722 | 1.8751e-05
2012 | 2012-03-28 | C | 29.7857 | 0.0010239 | 9.3754e-05
2012 | 2012-03-28 | C | 123.1879 | 0.056207 | 0.00068128
2012 | 2012-03-28 | C | 54.94 | 0.0080696 | 0.00017188
2012 | 2012-03-28 | C | 47.9846 | 0.028792 | 0.00015001
2012 | 2012-03-29 | C | 274.6983 | 0.097007 | 0.00092816
2012 | 2012-03-28 | C | 28.7934 | 0.018896 | 0.00020938
2012 | 2012-03-27 | C | 2.9727 | 0.00099405 | 9.3754e-06
2012 | 2012-03-20 | C | 1.9998 | 0.080363 | 6.2503e-06
2012 | 2012-03-30 | C | 2369.125 | 0.27394 | 0.01086
2012 | 2012-03-30 | C | 222.7778 | 0.073102 | 0.0026876
2012 | 2012-03-31 | C | 84.9143 | 0.0084918 | 0.00026564
2012 | 2012-03-08 | B | 13.9945 | 0.023704 | 4.3752e-05
2012 | 2012-03-14 | B | 1.9854 | 0.0012596 | 6.2503e-06
2012 | 2012-03-24 | B | 2.9667 | 0.0008066 | 9.3754e-06
2012 | 2012-03-24 | B | 33.9891 | 0.028786 | 0.00010625
2013 | 2012-04-01 | C | 479.4948 | 0.13991 | 0.0020704
2013 | 2012-04-01 | C | 217.8205 | 0.18255 | 0.0020456
2013 | 2012-04-02 | C | 639 | 0.047603 | 0.0019835
2013 | 2012-04-02 | C | 583 | 0.043432 | 0.0018096
2013 | 2012-04-02 | C | 77.8015 | 0.030912 | 0.00047492
2013 | 2012-04-02 | B | 92 | 0.054544 | 0.00028557
2013 | 2012-04-02 | B | 3 | 0.0016948 | 9.3121e-06
2013 | 2012-04-02 | C | 34 | 0.0054879 | 0.00010554
2013 | 2012-04-02 | B | 7.3553 | 0.0071918 | 4.656e-05
2013 | 2012-04-02 | B | 24 | 0.00052148 | 7.4497e-05
2013 | 2012-04-02 | B | 34 | 0.00010554 | 0.00010554
2013 | 2012-04-02 | B | 2 | 0.00063322 | 6.2081e-06
2013 | 2012-04-02 | C | 402 | 0.23085 | 0.0012478
2013 | 2012-04-03 | C | 600.6296 | 0.095083 | 0.0021573
2013 | 2012-04-02 | C | 155.9518 | 0.10892 | 0.0009219
2013 | 2012-04-03 | B | 38 | 0.013801 | 0.00011795
2013 | 2012-04-03 | B | 2 | 0.00066426 | 6.2081e-06
2013 | 2012-04-03 | B | 31 | 0.029252 | 9.6225e-05
2013 | 2012-04-03 | C | 9 | 0.0016762 | 2.7936e-05
2013 | 2012-04-03 | B | 68 | 0.063955 | 0.00021107
2013 | 2012-04-03 | B | 3 | 0.0034082 | 9.3121e-06
2013 | 2012-04-03 | C | 312 | 0.01259 | 0.00096846
2013 | 2012-04-03 | C | 61 | 0.00056804 | 0.00018935
2013 | 2012-04-03 | C | 36 | 0.00033524 | 0.00011175
2013 | 2012-04-03 | C | 1352 | 0.01259 | 0.0041966
2013 | 2012-04-04 | C | 61 | 0.02594 | 0.00018935
2013 | 2012-04-04 | B | 1 | 0.00088465 | 3.104e-06
2013 | 2012-04-04 | B | 19 | 0.011618 | 5.8977e-05
2013 | 2012-04-04 | C | 50 | 0.0065185 | 0.0001552
2013 | 2012-04-04 | C | 62 | 0.013664 | 0.00019245
2013 | 2012-04-04 | C | 4 | 0.00043456 | 1.2416e-05
2013 | 2012-04-04 | C | 28 | 0.0040849 | 8.6913e-05
2013 | 2012-04-04 | C | 27 | 0.0070399 | 8.3809e-05
2013 | 2012-04-04 | C | 8 | 0.017333 | 2.4832e-05
2013 | 2012-04-04 | C | 11 | 0.00037559 | 3.4144e-05
2013 | 2012-04-04 | C | 9 | 0.00097777 | 2.7936e-05
2013 | 2012-04-04 | C | 52.9495 | 0.077576 | 0.0015241
2013 | 2012-04-05 | B | 3 | 0.0023466 | 9.3121e-06
2013 | 2012-04-05 | B | 57 | 0.050956 | 0.00017693
2013 | 2012-04-05 | C | 17 | 0.002744 | 5.2768e-05
2013 | 2012-04-05 | B | 79 | 0.032124 | 0.00024522
2013 | 2012-04-05 | C | 195 | 0.14951 | 0.00060529
2013 | 2012-04-05 | C | 5 | 0.0017383 | 1.552e-05
2013 | 2012-04-06 | C | 3 | 0.00027005 | 9.3121e-06
2013 | 2012-04-06 | C | 151.4083 | 0.11138 | 0.00099019
2013 | 2012-04-06 | C | 35 | 0.039002 | 0.00010864
2013 | 2012-04-06 | C | 361 | 0.024652 | 0.0011206
2013 | 2012-04-07 | C | 25 | 0.0078377 | 7.7601e-05
2013 | 2012-04-06 | B | 1 | 0.00045629 | 3.104e-06
2013 | 2012-04-08 | C | 344 | 0.0074745 | 0.0010678
2013 | 2012-04-08 | C | 239.9364 | 0.07969 | 0.00091879
2013 | 2012-04-08 | C | 4 | 0.0032406 | 1.2416e-05
2013 | 2012-04-08 | C | 32 | 0.0057611 | 9.9329e-05
2013 | 2012-04-06 | C | 3 | 0.00027936 | 9.3121e-06
2013 | 2012-04-09 | C | 681.0808 | 0.20295 | 0.0039359
2013 | 2012-04-08 | C | 274.791 | 0.054589 | 0.00089706
2013 | 2012-04-10 | B | 167 | 0.13685 | 0.00051837
2013 | 2012-04-10 | B | 16 | 0.010181 | 4.9664e-05
2013 | 2012-04-10 | B | 12 | 0.010132 | 3.7248e-05
2013 | 2012-04-10 | B | 19 | 0.027955 | 5.8977e-05
2013 | 2012-04-10 | B | 96 | 0.097144 | 0.00029799
2013 | 2012-04-10 | B | 48 | 0.032779 | 0.00014899
2013 | 2012-04-10 | B | 62 | 0.068512 | 0.00019245
2013 | 2012-04-10 | B | 120 | 0.032406 | 0.00037248
2013 | 2012-04-10 | C | 80 | 0.01043 | 0.00024832
2013 | 2012-04-10 | C | 50 | 0.0099329 | 0.0001552
2013 | 2012-04-10 | C | 1 | 0.0031133 | 3.104e-06
2013 | 2012-04-10 | C | 34 | 0.030711 | 0.00010554
2013 | 2012-04-11 | C | 139.5 | 0.042002 | 0.00054631
2013 | 2012-04-11 | B | 9 | 0.0080177 | 2.7936e-05
2013 | 2012-04-11 | B | 24 | 0.023541 | 7.4497e-05
2013 | 2012-04-11 | C | 694.7 | 0.59731 | 0.0023094
2013 | 2012-04-11 | C | 416.1412 | 0.33455 | 0.0033927
2013 | 2012-04-11 | C | 838.298 | 0.38511 | 0.0039266
2013 | 2012-04-12 | C | 119 | 0.0044326 | 0.00036938
2013 | 2012-04-11 | C | 70.4816 | 0.070665 | 0.00050285
2013 | 2012-04-12 | C | 9 | 0.0050006 | 2.7936e-05
2013 | 2012-04-11 | B | 50 | 0.0343 | 0.0001552
2013 | 2012-04-12 | C | 46 | 0.010281 | 0.00014279
2013 | 2012-04-11 | B | 71 | 0.085289 | 0.00022039
2013 | 2012-04-12 | B | 360 | 0.1598 | 0.0011175
2013 | 2012-04-12 | B | 17 | 0.011978 | 5.2768e-05
2013 | 2012-04-12 | B | 46 | 0.048404 | 0.00014279
2013 | 2012-04-12 | C | 46 | 0.0069965 | 0.00014279
2013 | 2012-04-12 | B | 4 | 0.0043705 | 1.2416e-05
2013 | 2012-04-12 | B | 44 | 0.027862 | 0.00013658
2013 | 2012-04-12 | C | 83 | 0.019065 | 0.00025763
2013 | 2012-04-12 | C | 168.8511 | 0.047695 | 0.00055873
2013 | 2012-04-13 | B | 29 | 0.015033 | 9.0017e-05
2013 | 2012-04-13 | B | 55 | 0.040973 | 0.00017072
2013 | 2012-04-13 | B | 36 | 0.036988 | 0.00011175
2013 | 2012-04-13 | B | 16 | 0.015297 | 4.9664e-05
2013 | 2012-04-13 | C | 13 | 0.0033896 | 4.0352e-05
2013 | 2012-04-13 | C | 167.5667 | 0.029648 | 0.00095294
2013 | 2012-04-13 | C | 1 | 0.0010647 | 3.104e-06
2013 | 2012-04-14 | C | 54 | 0.002179 | 0.00016762
2013 | 2012-04-15 | B | 20 | 0.019493 | 6.2081e-05
2013 | 2012-04-15 | B | 87 | 0.070213 | 0.00027005
2013 | 2012-04-16 | B | 46 | 0.043978 | 0.00014279
2013 | 2012-04-04 | B | 11 | 0.01277 | 3.4144e-05
2013 | 2012-04-16 | B | 73 | 0.080441 | 0.00022659
2013 | 2012-04-16 | C | 121.339 | 0.021092 | 0.00057425
2013 | 2012-04-17 | C | 23 | 0.01228 | 7.1393e-05
2013 | 2012-04-13 | B | 50 | 0.041284 | 0.0001552
2013 | 2012-04-12 | B | 8 | 0.0047678 | 2.4832e-05
2013 | 2012-04-17 | B | 8 | 0.007698 | 2.4832e-05
2013 | 2012-04-17 | B | 50 | 0.040508 | 0.0001552
2013 | 2012-04-17 | C | 38 | 0.015098 | 0.00011795
2013 | 2012-04-17 | B | 343 | 0.3918 | 0.0010647
2013 | 2012-04-17 | B | 49 | 0.068292 | 0.0001521
2013 | 2012-04-18 | B | 8 | 0.0066054 | 2.4832e-05
2013 | 2012-04-18 | B | 14 | 0.013863 | 4.3456e-05
2013 | 2012-04-18 | B | 318 | 0.27441 | 0.00098708
2013 | 2012-04-18 | B | 171 | 0.11359 | 0.00053079
2013 | 2012-04-19 | C | 40 | 0.0033524 | 0.00012416
2013 | 2012-04-19 | C | 73 | 0.025152 | 0.00022659
2013 | 2012-04-19 | B | 2 | 0.0018376 | 6.2081e-06
2013 | 2012-04-19 | B | 37 | 0.042035 | 0.00011485
2013 | 2012-04-19 | B | 33 | 0.036978 | 0.00010243
2013 | 2012-04-19 | B | 324 | 0.15991 | 0.0010057
2013 | 2012-04-19 | B | 50 | 0.037248 | 0.0001552
2013 | 2012-04-19 | B | 101 | 0.086841 | 0.00031351
2013 | 2012-04-17 | B | 312 | 0.15883 | 0.00096846
2013 | 2012-04-20 | B | 62 | 0.032716 | 0.00019245
2013 | 2012-04-20 | B | 4 | 0.00058356 | 1.2416e-05
2013 | 2012-04-20 | B | 114 | 0.12562 | 0.00035386
2013 | 2012-04-20 | B | 3 | 0.00062391 | 9.3121e-06
2013 | 2012-04-20 | B | 11 | 0.0032437 | 3.4144e-05
2013 | 2012-04-20 | B | 11 | 0.0077508 | 3.4144e-05
2013 | 2012-04-20 | B | 16.8711 | 0.023409 | 6.2081e-05
2013 | 2012-04-21 | C | 201.0686 | 0.42565 | 0.0014154
2013 | 2012-04-21 | C | 862 | 0.25151 | 0.0026757
2013 | 2012-04-21 | C | 2 | 0.00032282 | 6.2081e-06
2013 | 2012-04-21 | C | 33 | 0.0046095 | 0.00010243
2013 | 2012-04-22 | C | 3986.1146 | 1.1507 | 0.012621
2013 | 2012-04-22 | C | 67 | 0.011022 | 0.00020797
2013 | 2012-04-22 | C | 194.5287 | 0.050721 | 0.0015831
2013 | 2012-04-22 | B | 17 | 0.017889 | 5.2768e-05
2013 | 2012-04-23 | B | 29 | 0.026915 | 9.0017e-05
2013 | 2012-04-23 | C | 89 | 0.0019338 | 0.00027626
2013 | 2012-04-23 | C | 1 | 3.7248e-05 | 3.104e-06
2013 | 2012-04-24 | C | 292.0583 | 0.18403 | 0.0022504
2013 | 2012-04-24 | C | 50 | 0.00388 | 0.0001552
2013 | 2012-04-24 | C | 1 | 0.00048733 | 3.104e-06
2013 | 2012-04-24 | B | 17 | 0.018575 | 5.2768e-05
2013 | 2012-04-24 | B | 11 | 0.009219 | 3.4144e-05
2013 | 2012-04-24 | B | 2 | 0.0021294 | 6.2081e-06
2013 | 2012-04-24 | B | 23 | 0.022631 | 7.1393e-05
2013 | 2012-04-24 | B | 2 | 0.001105 | 6.2081e-06
2013 | 2012-04-24 | B | 132 | 0.12292 | 0.00040973
2013 | 2012-04-24 | B | 3 | 0.00081015 | 9.3121e-06
2013 | 2012-04-24 | C | 5 | 0.00040352 | 1.552e-05
2013 | 2012-04-25 | B | 1 | 0.00073565 | 3.104e-06
2013 | 2012-04-25 | C | 163 | 0.030357 | 0.00050596
2013 | 2012-04-25 | C | 444.0687 | 0.17644 | 0.0015924
2013 | 2012-04-25 | C | 29 | 0.023854 | 9.0017e-05
2013 | 2012-04-25 | C | 11 | 0.0014341 | 3.4144e-05
2013 | 2012-04-26 | B | 401 | 0.082151 | 0.0012447
2013 | 2012-04-26 | B | 9 | 0.0010057 | 2.7936e-05
2013 | 2012-04-26 | B | 59 | 0.042305 | 0.00018314
2013 | 2012-04-26 | C | 198 | 0.10878 | 0.0006146
2013 | 2012-04-26 | B | 15 | 0.0038645 | 4.656e-05
2013 | 2012-04-26 | B | 75 | 0.075661 | 0.0002328
2013 | 2012-04-26 | B | 10 | 0.010243 | 3.104e-05
2013 | 2012-04-26 | B | 76 | 0.079264 | 0.00023591
2013 | 2012-04-26 | B | 264 | 0.2991 | 0.00081946
2013 | 2012-04-26 | B | 82 | 0.058542 | 0.00025453
2013 | 2012-04-27 | C | 1240.2157 | 0.38112 | 0.0073224
2013 | 2012-04-27 | B | 76 | 0.059212 | 0.00023591
2013 | 2012-04-27 | B | 44 | 0.036056 | 0.00013658
2013 | 2012-04-27 | C | 84.166 | 0.063746 | 0.00049044
2013 | 2012-04-27 | C | 668 | 0.16381 | 0.0020735
2013 | 2012-04-28 | C | 14 | 0.0089955 | 4.3456e-05
2013 | 2012-04-28 | C | 6 | 0.00080084 | 1.8624e-05
2013 | 2012-04-28 | C | 6 | 0.00072634 | 1.8624e-05
2013 | 2012-04-28 | C | 9.9542 | 0.01205 | 4.0352e-05
2013 | 2012-04-28 | C | 27 | 0.0062857 | 8.3809e-05
2013 | 2012-04-28 | C | 139.3971 | 0.089135 | 0.0010523
2013 | 2012-04-29 | B | 18 | 0.016482 | 5.5873e-05
2013 | 2012-04-29 | C | 107 | 0.070412 | 0.00033213
2013 | 2012-04-30 | B | 78 | 0.061013 | 0.00024211
2013 | 2012-04-30 | B | 8 | 0.0062577 | 2.4832e-05
2013 | 2012-04-30 | C | 73.6798 | 0.057176 | 0.000388
2013 | 2012-04-30 | C | 7 | 0.0012385 | 2.1728e-05
2013 | 2012-04-30 | C | 1 | 0.00027626 | 3.104e-06
2013 | 2012-04-30 | C | 148 | 0.065694 | 0.00080394
2013 | 2012-04-27 | B | 44 | 0.03551 | 0.00013658
2013 | 2012-04-30 | B | 4 | 0.0025826 | 1.2416e-05
2013 | 2012-05-01 | B | 164 | 0.0020362 | 0.00050906
2013 | 2012-05-01 | B | 7 | 0.0040632 | 2.1728e-05
2013 | 2012-05-01 | C | 8 | 0.0067295 | 2.4832e-05
2013 | 2012-05-01 | B | 61 | 0.031053 | 0.00018935
2013 | 2012-05-01 | C | 2 | 0.00016762 | 6.2081e-06
2013 | 2012-05-01 | B | 4 | 0.0039111 | 1.2416e-05
2013 | 2012-05-01 | B | 7 | 0.0029768 | 2.1728e-05
2013 | 2012-05-01 | B | 1 | 0.001043 | 3.104e-06
2013 | 2012-05-01 | B | 9 | 0.010281 | 2.7936e-05
2013 | 2012-05-01 | B | 29 | 0.026825 | 9.0017e-05
2013 | 2012-05-01 | C | 4 | 0.00043456 | 1.2416e-05
2013 | 2012-05-01 | C | 31.2857 | 0.0051469 | 0.00017693
2013 | 2012-05-01 | B | 12 | 0.013074 | 3.7248e-05
2013 | 2012-05-02 | C | 264.7983 | 0.095345 | 0.0010088
2013 | 2012-05-02 | C | 64.1745 | 0.071313 | 0.00024522
2013 | 2012-05-02 | C | 6 | 0.0027191 | 1.8624e-05
2013 | 2012-05-02 | C | 304 | 0.024534 | 0.00094362
2013 | 2012-05-02 | C | 418.661 | 0.22612 | 0.0021977
2013 | 2012-05-02 | B | 166 | 0.16334 | 0.00051527
2013 | 2012-05-02 | B | 4 | 0.0036876 | 1.2416e-05
2013 | 2012-05-02 | B | 4 | 0.0033275 | 1.2416e-05
2013 | 2012-05-02 | B | 24 | 0.00037248 | 7.4497e-05
2013 | 2012-05-02 | B | 1 | 0.00098398 | 3.104e-06
2013 | 2012-05-02 | B | 24 | 0.02436 | 7.4497e-05
2013 | 2012-05-02 | C | 7 | 0.0014341 | 2.1728e-05
2013 | 2012-05-03 | C | 95.051 | 0.028029 | 0.00041284
2013 | 2012-05-03 | B | 1 | 0.00022659 | 3.104e-06
2013 | 2012-05-03 | B | 4 | 0.0029426 | 1.2416e-05
2013 | 2012-05-01 | C | 8 | 0.0063819 | 2.4832e-05
2013 | 2012-05-03 | B | 1 | 0.00087534 | 3.104e-06
2013 | 2012-05-03 | C | 87 | 0.0086416 | 0.00027005
2013 | 2012-05-03 | B | 65 | 0.047818 | 0.00020176
2013 | 2012-05-03 | B | 2 | 0.0014341 | 6.2081e-06
2013 | 2012-05-03 | B | 5 | 0.00012416 | 1.552e-05
2013 | 2012-05-03 | B | 172 | 0.19594 | 0.00053389
2013 | 2012-05-04 | C | 88.8585 | 0.028409 | 0.00045319
2013 | 2012-05-04 | C | 8 | 0.00072013 | 2.4832e-05
2013 | 2012-05-04 | B | 3 | 0.00053079 | 9.3121e-06
2013 | 2012-05-04 | B | 26 | 0.024534 | 8.0705e-05
2013 | 2012-05-04 | B | 14 | 0.015036 | 4.3456e-05
2013 | 2012-05-04 | C | 11 | 0.0018779 | 3.4144e-05
2013 | 2012-05-04 | C | 497 | 0.010799 | 0.0015427
2013 | 2012-05-04 | C | 142 | 0.0030854 | 0.00044077
2013 | 2012-05-04 | C | 136 | 0.002955 | 0.00042215
2013 | 2012-05-01 | C | 839 | 0.0052086 | 0.0026043
2013 | 2012-05-01 | C | 672 | 0.0041718 | 0.0020859
2013 | 2012-05-05 | B | 60 | 0.086602 | 0.00018624
2013 | 2012-05-05 | B | 48 | 0.07256 | 0.00014899
2013 | 2012-05-05 | C | 18 | 0.0021232 | 5.5873e-05
2013 | 2012-05-05 | C | 54.3214 | 0.0089366 | 0.00022349
2013 | 2012-05-05 | C | 122 | 0.0045443 | 0.00037869
2013 | 2012-05-06 | C | 171.4786 | 0.1352 | 0.001133
2013 | 2012-05-06 | C | 62 | 0.0071206 | 0.00019245
2013 | 2012-05-05 | B | 14 | 0.011516 | 4.3456e-05
2013 | 2012-05-05 | C | 1207.7323 | 0.73102 | 0.0042215
2013 | 2012-05-06 | C | 312 | 0.06295 | 0.00096846
2013 | 2012-05-07 | B | 1 | 0.00042215 | 3.104e-06
2013 | 2012-05-07 | B | 99 | 0.09219 | 0.0003073
2013 | 2012-05-07 | B | 4 | 0.0038738 | 1.2416e-05
2013 | 2012-05-07 | B | 12 | 0.011547 | 3.7248e-05
2013 | 2012-05-07 | C | 590 | 0.11171 | 0.0018314
2013 | 2012-05-07 | C | 1 | 0.00052458 | 3.104e-06
2013 | 2012-05-07 | C | 626 | 0.20791 | 0.0019431
2013 | 2012-05-07 | C | 29 | 0.0033306 | 8.3809e-05
2013 | 2012-05-07 | C | 2 | 0.00057114 | 6.2081e-06
2013 | 2012-05-08 | C | 14 | 0.00091258 | 4.3456e-05
2013 | 2012-05-08 | C | 31 | 0.0044263 | 9.6225e-05
2013 | 2012-05-08 | B | 14 | 0.011038 | 4.3456e-05
2013 | 2012-05-08 | B | 129 | 0.15216 | 0.00040042
2013 | 2012-05-08 | B | 12 | 0.014862 | 3.7248e-05
2013 | 2012-05-08 | C | 48 | 0.0016389 | 0.00014589
2013 | 2012-05-08 | C | 3 | 0.00055873 | 9.3121e-06
2013 | 2012-05-08 | C | 35 | 0.010973 | 0.00010864
2013 | 2012-05-08 | C | 46 | 0.027272 | 0.00014279
2013 | 2012-05-08 | C | 125.0207 | 0.092748 | 0.0018283
2013 | 2012-05-09 | C | 83.2604 | 0.067712 | 0.00049975
2013 | 2012-05-09 | C | 208.5603 | 0.1968 | 0.0044015
2013 | 2012-05-09 | C | 379.93 | 0.11439 | 0.00185
2013 | 2012-05-09 | B | 2 | 0.00088154 | 6.2081e-06
2013 | 2012-05-09 | C | 192.148 | 0.24812 | 0.0028619
2013 | 2012-05-09 | B | 7 | 0.0061708 | 2.1728e-05
2013 | 2012-05-09 | C | 75 | 0.0041904 | 0.0002328
2013 | 2012-05-09 | C | 1 | 0.00013968 | 3.104e-06
2013 | 2012-05-09 | C | 9 | 0.0017041 | 2.7936e-05
2013 | 2012-05-09 | C | 152 | 0.0089644 | 0.00044698
2013 | 2012-05-09 | B | 163 | 0.092084 | 0.00050596
2013 | 2012-05-09 | B | 3 | 0.00099639 | 9.3121e-06
2013 | 2012-05-09 | B | 97 | 0.099962 | 0.00030109
2013 | 2012-05-09 | C | 1 | 0.00083188 | 3.104e-06
2013 | 2012-05-09 | C | 2185 | 0.094952 | 0.0068071
2013 | 2012-05-10 | B | 17 | 0.0082847 | 5.2768e-05
2013 | 2012-05-10 | B | 69 | 0.0287 | 0.00021418
2013 | 2012-05-10 | B | 14 | 0.011777 | 4.3456e-05
2013 | 2012-05-10 | B | 172 | 0.16017 | 0.00053389
2013 | 2012-05-10 | B | 1 | 0.0012199 | 3.104e-06
2013 | 2012-05-10 | B | 13 | 0.016666 | 4.0352e-05
2013 | 2012-05-10 | B | 6 | 0.0041346 | 1.8624e-05
2013 | 2012-05-10 | B | 3 | 0.0013223 | 9.3121e-06
2013 | 2012-05-10 | C | 160.2448 | 0.069637 | 0.00091569
2013 | 2012-05-10 | B | 20 | 0.020983 | 6.2081e-05
2013 | 2012-05-03 | B | 3 | 0.0036783 | 9.3121e-06
2013 | 2012-05-10 | C | 92 | 0.049404 | 0.00028867
2013 | 2012-05-11 | B | 13 | 0.014809 | 4.0352e-05
2013 | 2012-05-11 | B | 11 | 0.011677 | 3.4144e-05
2013 | 2012-05-11 | B | 29 | 0.030336 | 9.0017e-05
2013 | 2012-05-11 | C | 135.0377 | 0.043174 | 0.00050906
2013 | 2012-05-11 | C | 1 | 0.00023901 | 3.104e-06
2013 | 2012-05-11 | C | 267.3821 | 0.099595 | 0.00091258
2013 | 2012-05-13 | C | 2639.0727 | 0.87652 | 0.0085206
2013 | 2012-05-13 | C | 10 | 0.0029488 | 3.104e-05
2013 | 2012-05-13 | C | 204 | 0.020263 | 0.00063322
2013 | 2012-05-13 | C | 7 | 0.0014558 | 2.1728e-05
2013 | 2012-05-14 | C | 320.0559 | 0.17485 | 0.0023839
2013 | 2012-05-14 | C | 486.1875 | 0.18864 | 0.002418
2013 | 2012-05-14 | B | 33 | 0.022638 | 0.00010243
2013 | 2012-05-14 | B | 20 | 0.011609 | 6.2081e-05
2013 | 2012-05-14 | C | 17 | 0.0023218 | 5.2768e-05
2013 | 2012-05-14 | C | 11 | 0.0017414 | 3.4144e-05
2013 | 2012-05-14 | C | 1 | 0.00054631 | 3.104e-06
2013 | 2012-05-14 | C | 4 | 0.0008443 | 1.2416e-05
2013 | 2012-05-15 | C | 78 | 0.00096846 | 0.00024211
2013 | 2012-05-15 | C | 62 | 0.0063508 | 0.00019555
2013 | 2012-05-15 | C | 2 | 0.00020487 | 6.2081e-06
2013 | 2012-05-15 | B | 8 | 0.0043953 | 2.4832e-05
2013 | 2012-05-15 | B | 8 | 0.0053886 | 2.4832e-05
2013 | 2012-05-15 | B | 41 | 0.029526 | 0.00012727
2013 | 2012-05-15 | B | 6 | 0.004507 | 1.8624e-05
2013 | 2012-05-15 | B | 3 | 0.0043022 | 9.3121e-06
2013 | 2012-05-15 | B | 21 | 0.025031 | 6.5185e-05
2013 | 2012-05-15 | B | 57 | 0.067233 | 0.00017693
2013 | 2012-05-15 | B | 17 | 0.019049 | 5.2768e-05
2013 | 2012-05-14 | B | 41 | 0.030162 | 0.00012727
2013 | 2012-05-15 | C | 191.1111 | 0.030254 | 0.0010926
2013 | 2012-05-14 | C | 2 | 0.0046374 | 6.2081e-06
2013 | 2012-05-15 | C | 220 | 0.019804 | 0.0010895
2013 | 2012-05-15 | C | 139.026 | 0.065163 | 0.001074
2013 | 2012-05-16 | C | 150.4906 | 0.072872 | 0.0006922
2013 | 2012-05-16 | B | 37 | 0.020328 | 0.00011485
2013 | 2012-05-16 | B | 57 | 0.063164 | 0.00017693
2013 | 2012-05-16 | B | 31 | 0.022324 | 9.6225e-05
2013 | 2012-05-16 | C | 5 | 0.0017227 | 1.552e-05
2013 | 2012-05-16 | C | 142.5918 | 0.042048 | 0.00058045
2013 | 2012-05-16 | C | 19 | 0.0091414 | 5.8977e-05
2013 | 2012-05-16 | C | 42 | 0.016166 | 0.00013037
2013 | 2012-05-16 | B | 155 | 0.043782 | 0.00048112
2013 | 2012-05-17 | B | 14 | 0.0040849 | 4.3456e-05
2013 | 2012-05-16 | C | 3 | 0.0042836 | 9.3121e-06
2013 | 2012-05-17 | C | 3 | 0.00087534 | 9.3121e-06
2013 | 2012-05-17 | B | 17 | 0.014775 | 5.2768e-05
2013 | 2012-05-17 | B | 57 | 0.048656 | 0.00017693
2013 | 2012-05-17 | C | 24 | 0.0045443 | 7.4497e-05
2013 | 2012-05-17 | B | 99 | 0.10694 | 0.0003073
2013 | 2012-05-17 | B | 32 | 0.033772 | 9.9329e-05
2013 | 2012-05-17 | B | 4 | 0.0021107 | 1.2416e-05
2013 | 2012-05-17 | B | 8 | 0.002657 | 2.4832e-05
2013 | 2012-05-17 | B | 4 | 0.0043581 | 1.2416e-05
2013 | 2012-05-17 | B | 28 | 0.01999 | 8.6913e-05
2013 | 2012-05-17 | B | 92 | 0.09995 | 0.00028557
2013 | 2012-05-17 | C | 116.1338 | 0.055514 | 0.00067668
2013 | 2012-05-17 | C | 6 | 0.0052148 | 1.8624e-05
2013 | 2012-05-17 | C | 765.4 | 0.076026 | 0.0027936
2013 | 2012-05-17 | C | 5 | 0.0032903 | 1.552e-05
2013 | 2012-05-18 | C | 13 | 0.021185 | 4.0352e-05
2013 | 2012-05-17 | C | 21.121 | 0.060512 | 0.00058666
2013 | 2012-05-18 | B | 14 | 0.012559 | 4.3456e-05
2013 | 2012-05-18 | B | 5 | 0.005432 | 1.552e-05
2013 | 2012-05-18 | B | 5 | 0.0016762 | 1.552e-05
2013 | 2012-05-18 | B | 10.7569 | 0.014324 | 6.2081e-05
2013 | 2012-05-16 | B | 2 | 0.0015458 | 6.2081e-06
2013 | 2012-05-18 | B | 5 | 0.0035541 | 1.552e-05
2013 | 2012-05-18 | C | 3 | 0.0019276 | 9.3121e-06
2013 | 2012-05-18 | C | 51 | 0.005699 | 0.00015831
2013 | 2012-05-18 | C | 78.5212 | 0.039485 | 0.00034144
2013 | 2012-05-19 | C | 42.1304 | 0.029686 | 0.00056804
2013 | 2012-05-19 | B | 17 | 0.014142 | 5.2768e-05
2013 | 2012-05-19 | C | 1 | 1.552e-05 | 3.104e-06
2013 | 2012-05-20 | C | 259.0427 | 0.091665 | 0.0011237
2013 | 2012-05-20 | C | 4 | 0.00024832 | 1.2416e-05
2013 | 2012-05-16 | C | 1141 | 0.0035417 | 0.0035417
2013 | 2012-05-21 | C | 33 | 0.011677 | 0.00010243
2013 | 2012-05-21 | B | 11 | 0.011199 | 3.4144e-05
2013 | 2012-05-21 | B | 17 | 0.0036938 | 5.2768e-05
2013 | 2012-05-21 | B | 8 | 0.0015893 | 2.4832e-05
2013 | 2012-05-20 | C | 7 | 0.00041284 | 2.1728e-05
2013 | 2012-05-21 | C | 3 | 0.024416 | 9.3121e-06
2013 | 2012-05-21 | C | 1 | 0.00053079 | 3.104e-06
2013 | 2012-05-21 | C | 26 | 0.004923 | 8.0705e-05
2013 | 2012-05-21 | C | 17 | 0.0091289 | 5.2768e-05
2013 | 2012-05-22 | B | 89 | 0.062711 | 0.00027626
2013 | 2012-05-22 | B | 9 | 0.0034082 | 2.7936e-05
2013 | 2012-05-22 | B | 1 | 0.000925 | 3.104e-06
2013 | 2012-05-22 | B | 57 | 0.062279 | 0.00017693
2013 | 2012-05-22 | C | 17 | 0.0094456 | 5.2768e-05
2013 | 2012-05-22 | B | 11 | 0.012668 | 3.4144e-05
2013 | 2012-05-22 | B | 39 | 0.039344 | 0.00012106
2013 | 2012-05-23 | C | 483.9836 | 0.087133 | 0.0026353
2013 | 2012-05-23 | C | 12 | 0.0016762 | 3.7248e-05
2013 | 2012-05-23 | B | 92 | 0.095095 | 0.00028557
2013 | 2012-05-23 | B | 1 | 0.00019555 | 3.104e-06
2013 | 2012-05-23 | B | 122 | 0.14504 | 0.00037869
2013 | 2012-05-23 | B | 1 | 0.00018314 | 3.104e-06
2013 | 2012-05-23 | B | 34 | 0.027123 | 0.00010554
2013 | 2012-05-23 | B | 3 | 0.0037248 | 9.3121e-06
2013 | 2012-05-23 | C | 57 | 0.048302 | 0.00017693
2013 | 2012-05-23 | C | 934.5753 | 0.20307 | 0.0032065
2013 | 2012-05-24 | B | 57 | 0.05131 | 0.00017693
2013 | 2012-05-24 | B | 7 | 0.0058449 | 2.1728e-05
2013 | 2012-05-24 | B | 28 | 0.029377 | 8.6913e-05
2013 | 2012-05-24 | B | 50 | 0.038645 | 0.0001552
2013 | 2012-05-24 | B | 74 | 0.082002 | 0.0002297
2013 | 2012-05-24 | B | 12 | 0.015495 | 3.7248e-05
2013 | 2012-05-24 | C | 69.9198 | 0.050786 | 0.0010523
2013 | 2012-05-24 | C | 2 | 0.00039732 | 6.2081e-06
2013 | 2012-05-25 | C | 57 | 0.0092003 | 0.00017693
2013 | 2012-05-25 | B | 1 | 0.00056493 | 3.104e-06
2013 | 2012-05-25 | B | 22 | 0.0063508 | 6.8289e-05
2013 | 2012-05-25 | B | 230 | 0.18134 | 0.00071393
2013 | 2012-05-25 | B | 122 | 0.14769 | 0.00037869
2013 | 2012-05-25 | C | 3 | 0.00024211 | 9.3121e-06
2013 | 2012-05-25 | C | 110.0784 | 0.033827 | 0.00035386
2013 | 2012-05-26 | C | 5 | 0.00060529 | 1.552e-05
2013 | 2012-05-25 | C | 1 | 0.0038614 | 3.104e-06
2013 | 2012-05-26 | B | 1 | 0.0013782 | 3.104e-06
2013 | 2012-05-26 | C | 48.5868 | 0.097728 | 0.001493
2013 | 2012-05-26 | C | 1 | 0.00034144 | 3.104e-06
2013 | 2012-05-27 | C | 3 | 0.00074497 | 9.3121e-06
2013 | 2012-05-27 | C | 36 | 0.006593 | 0.00011175
2013 | 2012-05-27 | C | 731.6786 | 0.056779 | 0.0028029
2013 | 2012-05-27 | C | 159 | 0.014806 | 0.00049354
2013 | 2012-05-27 | C | 45.6116 | 0.033838 | 0.00022039
2013 | 2012-05-25 | B | 1 | 0.00081015 | 3.104e-06
2013 | 2012-05-24 | B | 223 | 0.066451 | 0.0006922
2013 | 2012-05-28 | C | 1134.84 | 0.51782 | 0.0043115
2013 | 2012-05-28 | C | 20 | 0.002297 | 6.2081e-05
2013 | 2012-05-28 | B | 43 | 0.014148 | 0.00013347
2013 | 2012-05-28 | C | 32 | 0.0034765 | 9.9329e-05
2013 | 2012-05-28 | B | 5 | 0.0053544 | 1.552e-05
2013 | 2012-05-28 | B | 31 | 0.029926 | 9.6225e-05
2013 | 2012-05-28 | C | 7.9293 | 0.0023628 | 9.3121e-05
2013 | 2012-05-28 | C | 737.0513 | 0.082362 | 0.0023311
2013 | 2012-05-28 | C | 105.0411 | 0.11021 | 0.00082878
2013 | 2012-05-28 | C | 111 | 0.13403 | 0.00034455
2013 | 2012-05-29 | C | 68 | 0.013298 | 0.00021107
2013 | 2012-05-29 | B | 164 | 0.22602 | 0.00050906
2013 | 2012-05-29 | B | 13 | 0.013316 | 4.0352e-05
2013 | 2012-05-29 | B | 39 | 0.04237 | 0.00012106
2013 | 2012-05-29 | B | 5 | 0.0020487 | 1.552e-05
2013 | 2012-05-29 | C | 41 | 0.008145 | 0.00012727
2013 | 2012-05-29 | C | 45 | 0.010616 | 0.00013968
2013 | 2012-05-29 | B | 3 | 0.0038086 | 9.3121e-06
2013 | 2012-05-18 | B | 36 | 0.047715 | 0.00011175
2013 | 2012-05-30 | C | 4 | 0.0016638 | 1.2416e-05
2013 | 2012-05-30 | B | 54 | 0.060678 | 0.00016762
2013 | 2012-05-30 | B | 17 | 0.012506 | 5.2768e-05
2013 | 2012-05-30 | B | 28 | 0.018686 | 8.6913e-05
2013 | 2012-05-30 | C | 1 | 0.00034765 | 3.104e-06
2013 | 2012-05-30 | B | 6 | 0.0040414 | 1.8624e-05
2013 | 2012-05-30 | C | 33 | 0.0076825 | 0.00010243
2013 | 2012-05-30 | B | 26 | 0.0099267 | 8.0705e-05
2013 | 2012-05-31 | B | 1 | 0.00021418 | 3.104e-06
2013 | 2012-05-31 | B | 1 | 0.0007667 | 3.104e-06
2013 | 2012-05-31 | B | 81 | 0.091771 | 0.00025143
2013 | 2012-05-31 | B | 169 | 0.19987 | 0.00052458
2013 | 2012-05-31 | B | 3 | 0.0026446 | 9.3121e-06
2013 | 2012-05-31 | C | 80 | 0.015148 | 0.00024832
2013 | 2012-05-19 | B | 1 | 0.0015396 | 3.104e-06
2013 | 2012-06-01 | B | 8 | 0.0029054 | 2.4832e-05
2013 | 2012-06-01 | B | 5 | 0.0012882 | 1.552e-05
2013 | 2012-06-01 | C | 421 | 0.006534 | 0.0013068
2013 | 2012-06-01 | B | 188 | 0.072945 | 0.00058356
2013 | 2012-06-01 | B | 2 | 0.001372 | 6.2081e-06
2013 | 2012-06-01 | B | 98 | 0.0097342 | 0.00030419
2013 | 2012-06-01 | B | 29 | 0.025295 | 9.0017e-05
2013 | 2012-06-01 | B | 217 | 0.20881 | 0.00067357
2013 | 2012-06-01 | B | 24 | 0.028383 | 7.4497e-05
2013 | 2012-06-01 | C | 22.6852 | 0.018801 | 7.4497e-05
2013 | 2012-06-01 | B | 164 | 0.23213 | 0.00050906
2013 | 2012-06-02 | C | 118.6052 | 0.12664 | 0.001282
2013 | 2012-06-02 | C | 53.52 | 0.007808 | 0.00024211
2013 | 2012-06-02 | C | 105.6391 | 0.086239 | 0.0009995
2013 | 2012-06-02 | C | 58.6756 | 0.19707 | 0.0030575
2013 | 2012-06-03 | C | 24 | 0.0060342 | 7.4497e-05
2013 | 2012-06-03 | C | 16 | 0.0025329 | 4.9664e-05
2013 | 2012-06-03 | C | 14 | 0.0022597 | 4.3456e-05
2013 | 2012-06-04 | C | 117.6429 | 0.029579 | 0.0004594
2013 | 2012-06-04 | C | 29 | 0.010532 | 9.0017e-05
2013 | 2012-06-04 | C | 7 | 0.0079742 | 2.1728e-05
2013 | 2012-06-04 | C | 58.7907 | 0.022993 | 0.00020797
2013 | 2012-06-04 | C | 61 | 0.0051123 | 0.00018935
2013 | 2012-06-04 | C | 13 | 0.0030264 | 4.0352e-05
2013 | 2012-06-05 | C | 8 | 0.00067047 | 2.4832e-05
2013 | 2012-06-05 | C | 25 | 0.0078377 | 7.7601e-05
2013 | 2012-06-05 | B | 9 | 0.0018717 | 2.7936e-05
2013 | 2012-06-05 | B | 7 | 0.0019121 | 2.1728e-05
2013 | 2012-06-05 | B | 10 | 0.013999 | 3.104e-05
2013 | 2012-06-05 | B | 102 | 0.023113 | 0.00031661
2013 | 2012-06-05 | B | 1 | 0.0005432 | 3.104e-06
2013 | 2012-06-05 | C | 33 | 0.0090141 | 0.00010243
2013 | 2012-06-05 | C | 87.7306 | 0.05174 | 0.00085671
2013 | 2012-06-06 | B | 39 | 0.03317 | 0.00012106
2013 | 2012-06-06 | B | 92 | 0.094524 | 0.00028557
2013 | 2012-06-05 | B | 84 | 0.055277 | 0.00026074
2013 | 2012-06-06 | B | 24 | 0.019742 | 7.4497e-05
2013 | 2012-06-06 | B | 54 | 0.063862 | 0.00016762
2013 | 2012-06-06 | B | 4 | 0.0036628 | 1.2416e-05
2013 | 2012-06-06 | C | 38 | 0.01958 | 0.00011795
2013 | 2012-06-06 | C | 1 | 0.00075738 | 3.104e-06
2013 | 2012-06-07 | B | 39 | 0.03777 | 0.00012106
2013 | 2012-06-06 | C | 6732.2105 | 0.33435 | 0.026204
2013 | 2012-06-07 | B | 3 | 0.0032592 | 9.3121e-06
2013 | 2012-06-07 | B | 50 | 0.035231 | 0.0001552
2013 | 2012-06-07 | C | 13 | 0.0028247 | 4.0352e-05
2013 | 2012-06-07 | B | 13 | 0.0067388 | 4.0352e-05
2013 | 2012-06-07 | B | 37 | 0.044906 | 0.00011485
2013 | 2012-06-07 | C | 118.6371 | 0.086171 | 0.001133
2013 | 2012-06-08 | B | 36 | 0.026037 | 0.00011175
2013 | 2012-06-07 | B | 176 | 0.039881 | 0.00054631
2013 | 2012-06-07 | C | 1 | 0.0051961 | 3.104e-06
2013 | 2012-06-08 | B | 37 | 0.042609 | 0.00011485
2013 | 2012-06-08 | B | 6 | 0.0075987 | 1.8624e-05
2013 | 2012-06-08 | C | 16 | 0.0039732 | 4.9664e-05
2013 | 2012-06-08 | B | 1 | 0.00027005 | 3.104e-06
2013 | 2012-06-09 | B | 3 | 0.0011547 | 9.3121e-06
2013 | 2012-06-08 | C | 4 | 0.010392 | 1.2416e-05
2013 | 2012-06-10 | C | 16 | 0.0015893 | 4.9664e-05
2013 | 2012-06-11 | C | 209 | 0.017516 | 0.00064874
2013 | 2012-06-10 | C | 4 | 0.0034393 | 1.2416e-05
2013 | 2012-06-10 | C | 87.7432 | 0.15933 | 0.00078532
2013 | 2012-06-11 | B | 3 | 0.00062391 | 9.3121e-06
2013 | 2012-06-11 | C | 255 | 0.0055407 | 0.00079153
2013 | 2012-06-11 | B | 5 | 0.0014744 | 1.552e-05
2013 | 2012-06-11 | C | 87.9714 | 0.03741 | 0.00067668
2013 | 2012-06-11 | B | 2 | 0.00057114 | 6.2081e-06
2013 | 2012-06-11 | C | 151.9 | 0.064596 | 0.00093431
2013 | 2012-06-11 | B | 164 | 0.20871 | 0.00050906
2013 | 2012-06-11 | C | 37 | 0.00080394 | 0.00011485
2013 | 2012-06-11 | C | 3 | 0.0013689 | 9.3121e-06
2013 | 2012-06-12 | C | 939 | 0.023317 | 0.0029147
2013 | 2012-06-12 | C | 59.7273 | 0.0014832 | 0.0010057
2013 | 2012-06-12 | C | 93 | 0.08718 | 0.00028867
2013 | 2012-06-12 | B | 6 | 0.0021045 | 1.8624e-05
2013 | 2012-06-12 | C | 15 | 0.0052148 | 4.656e-05
2013 | 2012-06-12 | B | 48 | 0.044251 | 0.00014899
2013 | 2012-06-12 | B | 9 | 0.0054196 | 2.7936e-05
2013 | 2012-06-12 | B | 13 | 0.0081512 | 4.0352e-05
2013 | 2012-06-12 | B | 25 | 0.025375 | 7.7601e-05
2013 | 2012-06-12 | B | 22 | 0.018301 | 6.8289e-05
2013 | 2012-06-12 | B | 22 | 0.021169 | 6.8289e-05
2013 | 2012-06-12 | B | 100 | 0.14496 | 0.0003104
2013 | 2012-06-12 | B | 6 | 0.0014341 | 1.8624e-05
2013 | 2012-06-12 | B | 82 | 0.11734 | 0.00025453
2013 | 2012-06-13 | C | 411.4831 | 0.22352 | 0.0015427
2013 | 2012-06-09 | B | 6 | 0.0056245 | 1.8624e-05
2013 | 2012-06-11 | B | 6 | 0.0016576 | 1.8624e-05
2013 | 2012-06-05 | B | 4 | 0.0038862 | 1.2416e-05
2013 | 2012-06-02 | B | 1 | 0.0012416 | 3.104e-06
2013 | 2012-06-06 | B | 4 | 0.0041346 | 1.2416e-05
2013 | 2012-06-11 | B | 19 | 0.0014744 | 5.8977e-05
2013 | 2012-06-08 | B | 44 | 0.016662 | 0.00013658
2013 | 2012-06-13 | B | 12 | 0.010914 | 3.7248e-05
2013 | 2012-06-13 | B | 5 | 0.0013503 | 1.552e-05
2013 | 2012-06-13 | B | 13 | 0.012711 | 4.0352e-05
2013 | 2012-06-13 | B | 28 | 0.030159 | 8.6913e-05
2013 | 2012-06-13 | B | 124 | 0.081214 | 0.0003849
2013 | 2012-06-13 | B | 9 | 0.0071517 | 2.7936e-05
2013 | 2012-06-13 | B | 5 | 0.00058977 | 1.552e-05
2013 | 2012-06-12 | B | 26 | 0.012267 | 8.0705e-05
2013 | 2012-06-13 | B | 106 | 0.068109 | 0.00032903
2013 | 2012-06-14 | C | 118.7912 | 0.12426 | 0.0041377
2013 | 2012-06-13 | C | 2 | 0.00094362 | 6.2081e-06
2013 | 2012-06-14 | B | 30 | 0.018345 | 9.3121e-05
2013 | 2012-06-14 | B | 17 | 0.0078097 | 5.2768e-05
2013 | 2012-06-14 | B | 6 | 0.0028867 | 1.8624e-05
2013 | 2012-06-14 | B | 24 | 0.026819 | 7.4497e-05
2013 | 2012-06-14 | B | 63 | 0.063946 | 0.00019555
2013 | 2012-06-14 | B | 20 | 0.023466 | 6.2081e-05
2013 | 2012-06-14 | B | 15 | 0.015132 | 4.656e-05
2013 | 2012-06-14 | B | 120 | 0.11026 | 0.00037248
2013 | 2012-06-14 | B | 58 | 0.044648 | 0.00018003
2013 | 2012-06-14 | B | 4 | 0.0017258 | 1.2416e-05
2013 | 2012-06-14 | B | 60 | 0.074683 | 0.00018624
2013 | 2012-06-13 | B | 4 | 0.00039732 | 1.2416e-05
2013 | 2012-06-13 | B | 1 | 0.00068909 | 3.104e-06
2013 | 2012-06-15 | B | 13 | 0.0094425 | 4.0352e-05
2013 | 2012-06-15 | B | 2 | 0.00016762 | 6.2081e-06
2013 | 2012-06-15 | B | 3 | 0.0029985 | 9.3121e-06
2013 | 2012-06-15 | B | 6 | 0.0013223 | 1.8624e-05
2013 | 2012-06-16 | B | 2 | 0.0023342 | 6.2081e-06
2013 | 2012-06-16 | C | 30 | 0.027284 | 9.3121e-05
2013 | 2012-06-17 | B | 3 | 0.00034455 | 9.3121e-06
2013 | 2012-06-17 | B | 2 | 0.00072634 | 6.2081e-06
2013 | 2012-06-17 | C | 22 | 0.0022535 | 6.8289e-05
2013 | 2012-06-17 | C | 4 | 0.00185 | 1.2416e-05
2013 | 2012-05-19 | B | 182 | 0.16779 | 0.00056493
2013 | 2012-06-17 | B | 30 | 0.033244 | 9.3121e-05
2013 | 2012-06-16 | B | 3 | 0.0039483 | 9.3121e-06
2013 | 2012-06-16 | B | 27 | 0.018606 | 8.3809e-05
2013 | 2012-06-16 | B | 2 | 0.0028433 | 6.2081e-06
2013 | 2012-06-16 | C | 41 | 0.012981 | 0.00012727
2013 | 2012-06-15 | C | 125 | 0.0085361 | 0.000388
2013 | 2012-06-18 | B | 16 | 0.0056617 | 4.9664e-05
2013 | 2012-06-18 | C | 87 | 0.0064812 | 0.00027005
2013 | 2012-06-18 | C | 163 | 0.013661 | 0.00050596
2013 | 2012-06-18 | B | 3 | 0.0007729 | 9.3121e-06
2013 | 2012-06-18 | B | 6 | 0.0053638 | 1.8624e-05
2013 | 2012-06-18 | C | 13 | 0.0046002 | 4.0352e-05
2013 | 2012-06-18 | B | 10 | 0.012261 | 3.104e-05
2013 | 2012-06-18 | C | 436 | 0.035187 | 0.0013534
2013 | 2012-06-18 | B | 65 | 0.087161 | 0.00020176
2013 | 2012-06-18 | C | 9 | 0.0018717 | 2.7936e-05
2013 | 2012-06-18 | B | 2 | 6.2081e-06 | 6.2081e-06
2013 | 2012-06-18 | C | 12 | 0.0031661 | 3.7248e-05
2013 | 2012-06-18 | C | 1 | 4.9664e-05 | 3.104e-06
2013 | 2012-06-18 | C | 2188 | 0.27166 | 0.0067916
2013 | 2012-06-18 | C | 152 | 0.0051899 | 0.00047181
2013 | 2012-06-18 | C | 975.321 | 0.9718 | 0.0054072
2013 | 2012-06-18 | C | 675 | 0.12152 | 0.0020952
2013 | 2012-06-18 | C | 182.4437 | 0.083814 | 0.00096535
2013 | 2012-06-19 | B | 2 | 0.00072634 | 6.2081e-06
2013 | 2012-06-19 | B | 2 | 0.00048423 | 6.2081e-06
2013 | 2012-06-19 | C | 2 | 0.0037807 | 6.2081e-06
2013 | 2012-06-19 | B | 7 | 0.00063012 | 2.1728e-05
2013 | 2012-06-19 | B | 11 | 0.00037559 | 3.4144e-05
2013 | 2012-06-19 | B | 17 | 0.019208 | 5.2768e-05
2013 | 2012-06-19 | B | 20 | 0.020921 | 6.2081e-05
2013 | 2012-06-19 | B | 5 | 0.0015831 | 1.552e-05
2013 | 2012-06-19 | B | 93 | 0.064374 | 0.00028867
2013 | 2012-06-19 | C | 107.5342 | 0.052739 | 0.00059908
2013 | 2012-06-19 | C | 289.0328 | 0.10676 | 0.0016607
2013 | 2012-06-19 | B | 28 | 0.039545 | 8.6913e-05
2013 | 2012-06-19 | B | 13 | 0.01485 | 4.0352e-05
2013 | 2012-06-19 | C | 13 | 0.0077477 | 4.0352e-05
2013 | 2012-06-19 | C | 58.273 | 0.052456 | 0.00048733
2013 | 2012-06-19 | B | 8 | 0.00067047 | 2.4832e-05
2013 | 2012-06-19 | B | 5 | 0.00041904 | 1.552e-05
2013 | 2012-06-20 | C | 175.2886 | 0.16051 | 0.00094362
2013 | 2012-06-20 | B | 11 | 0.0095946 | 3.4144e-05
2013 | 2012-06-20 | C | 92 | 0.018848 | 0.00028557
2013 | 2012-06-20 | C | 3 | 0.00039111 | 9.3121e-06
2013 | 2012-06-20 | B | 66 | 0.073547 | 0.00020487
2013 | 2012-06-20 | B | 19 | 0.02135 | 5.8977e-05
2013 | 2012-06-20 | B | 55 | 0.070849 | 0.00017072
2013 | 2012-06-20 | B | 26 | 0.034219 | 8.0705e-05
2013 | 2012-06-21 | B | 173 | 0.030609 | 0.000537
2013 | 2012-06-21 | C | 419 | 0.02211 | 0.0013006
2013 | 2012-06-21 | C | 1 | 0.0010926 | 3.104e-06
2013 | 2012-06-21 | B | 20 | 0.011919 | 6.2081e-05
2013 | 2012-06-21 | B | 17 | 0.016411 | 5.2768e-05
2013 | 2012-06-21 | B | 28 | 0.032245 | 8.6913e-05
2013 | 2012-06-21 | B | 20 | 0.024149 | 6.2081e-05
2013 | 2012-06-21 | B | 172 | 0.1591 | 0.00053389
2013 | 2012-06-20 | B | 26 | 0.044549 | 8.0705e-05
2013 | 2012-06-21 | B | 16 | 0.022945 | 4.9664e-05
2013 | 2012-06-21 | C | 5 | 0.0053855 | 1.552e-05
2013 | 2012-06-21 | C | 168.1231 | 0.032355 | 0.00090948
2013 | 2012-06-21 | B | 3.6957 | 0.0052424 | 8.6913e-05
2013 | 2012-06-15 | B | 1 | 0.00088154 | 3.104e-06
2013 | 2012-06-22 | B | 14 | 0.0057797 | 4.3456e-05
2013 | 2012-06-22 | B | 2 | 0.0011609 | 6.2081e-06
2013 | 2012-06-22 | B | 25 | 0.014744 | 7.7601e-05
2013 | 2012-06-22 | B | 24 | 0.020338 | 7.4497e-05
2013 | 2012-06-22 | B | 5 | 0.0057269 | 1.552e-05
2013 | 2012-06-22 | B | 18 | 0.022014 | 5.5873e-05
2013 | 2012-06-22 | B | 74 | 0.084299 | 0.0002297
2013 | 2012-06-22 | C | 10 | 0.0017693 | 3.104e-05
2013 | 2012-06-22 | C | 421 | 0.030056 | 0.0013068
2013 | 2012-06-22 | C | 825 | 0.058899 | 0.0025608
2013 | 2012-06-22 | B | 33.2678 | 0.047502 | 0.00034144
2013 | 2012-06-22 | C | 18 | 0.0023466 | 5.5873e-05
2013 | 2012-06-22 | C | 5 | 0.0031351 | 1.552e-05
2013 | 2012-06-23 | C | 41.2258 | 0.019451 | 0.0001521
2013 | 2012-06-23 | B | 1 | 0.0014092 | 3.104e-06
2013 | 2012-06-24 | C | 151.7562 | 0.093269 | 0.000537
2013 | 2012-06-23 | B | 46 | 0.029985 | 0.00014279
2013 | 2012-06-23 | C | 33 | 0.0033803 | 0.00010243
2013 | 2012-06-24 | C | 868.3971 | 0.17521 | 0.002924
2013 | 2012-06-24 | C | 19 | 0.0045412 | 5.8977e-05
2013 | 2012-06-24 | C | 376.8551 | 0.077205 | 0.0011795
2013 | 2012-06-24 | C | 187 | 0.03889 | 0.00058045
2013 | 2012-06-23 | C | 110.5802 | 0.277 | 0.0006146
2013 | 2012-06-24 | C | 174 | 0.27923 | 0.0005401
2013 | 2012-06-23 | C | 50.1255 | 0.16819 | 0.00025763
2013 | 2012-06-23 | C | 178 | 0.43096 | 0.00055252
2013 | 2012-06-24 | C | 8 | 0.00094362 | 2.4832e-05
2013 | 2012-06-24 | C | 3 | 0.00056804 | 9.3121e-06
2013 | 2012-06-25 | C | 89 | 0.032875 | 0.00027626
2013 | 2012-06-25 | B | 1 | 0.00065805 | 3.104e-06
2013 | 2012-06-25 | C | 14 | 0.0090389 | 4.3456e-05
2013 | 2012-06-25 | B | 7 | 0.0063012 | 2.1728e-05
2013 | 2012-06-25 | B | 28 | 0.025205 | 8.6913e-05
2013 | 2012-06-25 | B | 24 | 0.025999 | 7.4497e-05
2013 | 2012-06-25 | C | 12 | 0.0016389 | 3.7248e-05
2013 | 2012-06-25 | C | 32 | 0.010926 | 9.9329e-05
2013 | 2012-06-25 | B | 11 | 0.017857 | 3.4144e-05
2013 | 2012-06-25 | C | 785 | 0.024367 | 0.0024367
2013 | 2012-06-25 | B | 19.2 | 0.02664 | 0.00028247
2013 | 2012-06-25 | B | 54.992 | 0.042162 | 0.00043456
2013 | 2012-06-23 | C | 1 | 0.00021728 | 3.104e-06
2013 | 2012-06-26 | C | 82 | 0.011963 | 0.00025453
2013 | 2012-06-26 | B | 8 | 0.0042711 | 2.4832e-05
2013 | 2012-06-26 | B | 3 | 0.0028029 | 9.3121e-06
2013 | 2012-06-26 | B | 2 | 0.0011919 | 6.2081e-06
2013 | 2012-06-26 | B | 90 | 0.072914 | 0.00027936
2013 | 2012-06-26 | B | 5 | 0.0055407 | 1.552e-05
2013 | 2012-06-26 | C | 70.2655 | 0.062596 | 0.0006922
2013 | 2012-06-26 | B | 92 | 0.09281 | 0.00028557
2013 | 2012-06-26 | C | 70.0741 | 0.028712 | 0.00032592
2013 | 2012-06-26 | B | 173 | 0.024702 | 0.000537
2013 | 2012-06-26 | B | 80 | 0.089893 | 0.00024832
2013 | 2012-06-26 | B | 11 | 0.017311 | 3.4144e-05
2013 | 2012-06-26 | C | 20 | 0.0062081 | 6.2081e-05
2013 | 2012-06-26 | C | 716.413 | 0.19792 | 0.0028805
2013 | 2012-06-27 | C | 308 | 0.031549 | 0.00095604
2013 | 2012-06-27 | C | 308 | 0.019121 | 0.00095604
2013 | 2012-06-23 | C | 1 | 0.0014806 | 3.104e-06
2013 | 2012-06-27 | C | 137.8959 | 0.093311 | 0.0009281
2013 | 2012-06-26 | C | 285 | 0.075195 | 0.00088465
2013 | 2012-06-27 | B | 28 | 0.024509 | 8.6913e-05
2013 | 2012-06-27 | C | 22 | 0.006624 | 6.8289e-05
2013 | 2012-06-27 | B | 9 | 0.0070399 | 2.7936e-05
2013 | 2012-06-27 | C | 53 | 0.014313 | 0.00016451
2013 | 2012-06-27 | C | 118.2082 | 0.12402 | 0.00048423
2013 | 2012-06-27 | B | 156 | 0.18788 | 0.00048423
2013 | 2012-06-27 | C | 10 | 0.00086913 | 3.104e-05
2013 | 2012-06-27 | B | 16 | 0.023591 | 4.9664e-05
2013 | 2012-06-27 | B | 5 | 0.0068909 | 1.552e-05
2013 | 2012-06-27 | B | 2 | 0.00035386 | 6.2081e-06
2013 | 2012-06-27 | B | 1 | 0.00039421 | 3.104e-06
2013 | 2012-06-27 | B | 46 | 0.060255 | 0.00014279
2013 | 2012-06-27 | C | 46 | 0.018562 | 0.00014279
2013 | 2012-06-27 | C | 163 | 0.0070834 | 0.00050596
2013 | 2012-06-28 | C | 142.4248 | 0.098586 | 0.00087534
2013 | 2012-06-28 | C | 162 | 0.032183 | 0.00050285
2013 | 2012-06-28 | C | 30 | 0.01611 | 9.3121e-05
2013 | 2012-06-28 | B | 16 | 0.012863 | 4.9664e-05
2013 | 2012-06-28 | B | 76 | 0.057561 | 0.00023591
2013 | 2012-06-28 | C | 47 | 0.011671 | 0.00014589
2013 | 2012-06-28 | B | 23 | 0.028486 | 7.1393e-05
2013 | 2012-06-28 | B | 5 | 0.0064098 | 1.552e-05
2013 | 2012-06-28 | B | 8 | 0.01033 | 2.4832e-05
2013 | 2012-06-28 | B | 3 | 0.0037062 | 9.3121e-06
2013 | 2012-06-28 | B | 70 | 0.047802 | 0.00021728
2013 | 2012-06-28 | C | 59 | 0.013552 | 0.00018314
2013 | 2012-06-28 | B | 300 | 0.33803 | 0.00093121
2013 | 2012-06-28 | C | 58 | 0.00072013 | 0.00018003
2013 | 2012-06-26 | B | 23 | 0.013279 | 7.1393e-05
2013 | 2012-06-25 | B | 1 | 0.0010523 | 3.104e-06
2013 | 2012-06-24 | B | 42 | 0.020729 | 0.00013037
2013 | 2012-06-27 | B | 276 | 0.31527 | 0.00085671
2013 | 2012-06-29 | C | 1 | 2.1728e-05 | 3.104e-06
2013 | 2012-06-29 | C | 19 | 0.0017693 | 5.8977e-05
2013 | 2012-06-29 | B | 6 | 0.0042277 | 1.8624e-05
2013 | 2012-06-29 | B | 1 | 0.00061149 | 3.104e-06
2013 | 2012-06-29 | B | 45 | 0.048469 | 0.00013968
2013 | 2012-06-29 | C | 7 | 0.0043022 | 2.1728e-05
2013 | 2012-06-29 | B | 3 | 0.0016482 | 9.3121e-06
2013 | 2012-06-29 | B | 18 | 0.015365 | 5.5873e-05
2013 | 2012-06-29 | B | 3 | 0.0030451 | 9.3121e-06
2013 | 2012-06-29 | C | 31.6143 | 0.027182 | 0.0028091
2013 | 2012-06-30 | C | 241.533 | 0.1342 | 0.0019866
2013 | 2012-06-30 | C | 190.1267 | 0.21718 | 0.0028278
2013 | 2012-06-30 | C | 446 | 0.035994 | 0.0013844
2013 | 2012-06-30 | C | 554 | 0.055028 | 0.0017196
2013 | 2012-06-30 | B | 4 | 0.00090638 | 1.2416e-05
2013 | 2012-07-01 | C | 1 | 0.00040973 | 3.104e-06
2013 | 2012-06-30 | C | 1 | 0.0024087 | 3.104e-06
2013 | 2012-07-01 | C | 2083 | 0.058191 | 0.0080239
2013 | 2012-07-01 | C | 55 | 0.0025608 | 0.00017072
2013 | 2012-07-02 | C | 1 | 0.0011982 | 3.104e-06
2013 | 2012-07-02 | C | 30.7591 | 0.012794 | 0.00011795
2013 | 2012-07-02 | C | 89 | 0.03398 | 0.00027626
2013 | 2012-07-02 | B | 15 | 0.016063 | 4.656e-05
2013 | 2012-07-02 | C | 17.6018 | 0.012184 | 0.00010243
2013 | 2012-07-02 | C | 9 | 0.0082971 | 2.7936e-05
2013 | 2012-07-02 | B | 4 | 0.0038117 | 1.2416e-05
2013 | 2012-07-02 | C | 1 | 0.0016762 | 3.104e-06
2013 | 2012-07-03 | C | 577 | 0.014328 | 0.001791
2013 | 2012-07-02 | B | 212 | 0.0072386 | 0.00065805
2013 | 2012-06-30 | C | 4 | 0.0036876 | 1.2416e-05
2013 | 2012-07-03 | C | 243 | 0.015086 | 0.00075428
2013 | 2012-07-03 | C | 282.8214 | 0.16943 | 0.0019804
2013 | 2012-07-03 | C | 26 | 0.0058107 | 8.0705e-05
2013 | 2012-06-28 | B | 1 | 0.00064253 | 3.104e-06
2013 | 2012-07-03 | B | 53 | 0.050012 | 0.00016451
2013 | 2012-07-03 | B | 157 | 0.1847 | 0.00048733
2013 | 2012-07-03 | C | 5 | 0.00049664 | 1.552e-05
2013 | 2012-07-03 | C | 6 | 0.00042836 | 1.8624e-05
2013 | 2012-07-03 | B | 128 | 0.1625 | 0.00039732
2013 | 2012-07-03 | B | 144 | 0.037546 | 0.00044698
2013 | 2012-07-03 | C | 7 | 0.0052582 | 2.1728e-05
2013 | 2012-07-03 | C | 275 | 0.011097 | 0.00085361
2013 | 2012-07-03 | C | 88 | 0.01994 | 0.00027315
2013 | 2012-07-03 | C | 233.2549 | 0.1086 | 0.001254
2013 | 2012-07-03 | C | 175.52 | 0.025606 | 0.00086602
2013 | 2012-07-03 | C | 119 | 0.0051713 | 0.00036938
2013 | 2012-07-03 | C | 29.9739 | 0.038984 | 0.00025763
2013 | 2012-07-03 | C | 382.2297 | 0.25983 | 0.002148
2013 | 2012-07-03 | B | 56 | 0.091954 | 0.00017383
2013 | 2012-07-04 | C | 367 | 0.23923 | 0.0011392
2013 | 2012-07-04 | C | 375.4194 | 0.068753 | 0.0011702
2013 | 2012-07-04 | B | 88 | 0.017482 | 0.00027315
2013 | 2012-07-04 | B | 5 | 0.0026695 | 1.552e-05
2013 | 2012-07-04 | B | 24 | 0.018997 | 7.4497e-05
2013 | 2012-07-04 | C | 651.1525 | 0.11319 | 0.0027409
2013 | 2012-07-04 | C | 2 | 0.0011609 | 6.2081e-06
2013 | 2012-07-04 | C | 17 | 0.0034827 | 5.2768e-05
2013 | 2012-07-04 | C | 3782 | 0.058697 | 0.011739
2013 | 2012-07-03 | B | 3 | 0.0020673 | 9.3121e-06
2013 | 2012-07-03 | B | 3 | 0.0027284 | 9.3121e-06
2013 | 2012-07-04 | C | 165.8034 | 0.090065 | 0.0012664
2013 | 2012-07-05 | B | 2 | 0.0006953 | 6.2081e-06
2013 | 2012-07-05 | B | 24 | 0.022126 | 7.4497e-05
2013 | 2012-07-05 | B | 54 | 0.055984 | 0.00016762
2013 | 2012-07-05 | C | 32.3738 | 0.030348 | 0.00024522
2013 | 2012-07-05 | C | 7 | 0.0030419 | 2.1728e-05
2013 | 2012-07-05 | B | 164 | 0.27591 | 0.00050906
2013 | 2012-06-27 | B | 1 | 0.0013534 | 3.104e-06
2013 | 2012-07-05 | B | 62 | 0.06524 | 0.00019245
2013 | 2012-07-05 | B | 61 | 0.049419 | 0.00018935
2013 | 2012-07-05 | B | 22 | 0.021921 | 6.8289e-05
2013 | 2012-07-05 | C | 363.0559 | 0.5815 | 0.001909
2013 | 2012-07-06 | C | 21 | 0.004954 | 6.5185e-05
2013 | 2012-07-06 | C | 5 | 0.0011175 | 1.552e-05
2013 | 2012-07-06 | B | 1 | 0.00029488 | 3.104e-06
2013 | 2012-07-06 | C | 421 | 0.03659 | 0.0013068
2013 | 2012-07-06 | C | 825 | 0.079386 | 0.0025608
2013 | 2012-07-06 | B | 3 | 0.0015365 | 9.3121e-06
2013 | 2012-07-06 | B | 1 | 0.00034765 | 3.104e-06
2013 | 2012-07-06 | C | 237.4375 | 0.0095812 | 0.00073876
2013 | 2012-07-07 | C | 27 | 0.017181 | 8.3809e-05
2013 | 2012-07-07 | C | 24 | 0.0020114 | 7.4497e-05
2013 | 2012-07-08 | B | 17 | 0.036938 | 5.2768e-05
2013 | 2012-07-09 | B | 16 | 0.0028309 | 4.9664e-05
2013 | 2012-07-06 | C | 165.6452 | 0.094093 | 0.00059908
2013 | 2012-07-09 | B | 19 | 0.0031847 | 5.8977e-05
2013 | 2012-07-04 | C | 7 | 0.0026943 | 2.1728e-05
2013 | 2012-07-09 | B | 1 | 0.00070461 | 3.104e-06
2013 | 2012-07-09 | B | 49 | 0.04137 | 0.0001521
2013 | 2012-07-09 | B | 38 | 0.038571 | 0.00011795
2013 | 2012-07-09 | B | 2 | 0.0010988 | 6.2081e-06
2013 | 2012-07-09 | B | 3 | 0.0017879 | 9.3121e-06
2013 | 2012-07-09 | C | 95.9467 | 0.066116 | 0.0019121
2013 | 2012-07-09 | B | 37 | 0.0002297 | 0.00011485
2013 | 2012-07-09 | C | 32.65 | 0.026046 | 0.00021728
2013 | 2012-07-09 | C | 10 | 0.0028247 | 3.104e-05
2013 | 2012-07-09 | C | 359.301 | 0.11153 | 0.0020859
2013 | 2012-07-09 | C | 376 | 0.06069 | 0.0011671
2013 | 2012-07-10 | B | 1 | 0.00022039 | 3.104e-06
2013 | 2012-07-10 | B | 49 | 0.048063 | 0.0001521
2013 | 2012-07-10 | B | 1 | 0.001164 | 3.104e-06
2013 | 2012-07-10 | B | 146 | 0.0639 | 0.00045319
2013 | 2012-07-10 | B | 13 | 0.01376 | 4.0352e-05
2013 | 2012-07-10 | B | 111 | 0.12852 | 0.00034455
2013 | 2012-07-10 | B | 43 | 0.045648 | 0.00013347
2013 | 2012-07-10 | B | 1 | 0.00095914 | 3.104e-06
2013 | 2012-07-10 | C | 3631.6154 | 0.25927 | 0.012624
2013 | 2012-07-07 | C | 6 | 0.0077663 | 1.8624e-05
2013 | 2012-07-10 | C | 12 | 0.0067419 | 3.7248e-05
2013 | 2012-07-11 | C | 32 | 0.0079463 | 9.9329e-05
2013 | 2012-07-11 | B | 19 | 0.0069003 | 5.8977e-05
2013 | 2012-07-11 | C | 114 | 0.002477 | 0.00035386
2013 | 2012-07-11 | C | 371.8038 | 0.23774 | 0.0023963
2013 | 2012-07-11 | C | 74 | 0.017227 | 0.0002297
2013 | 2012-07-10 | C | 41.2073 | 0.020593 | 0.00026695
2013 | 2012-07-11 | B | 8 | 0.0014154 | 2.4832e-05
2013 | 2012-07-11 | B | 18 | 0.021064 | 5.5873e-05
2013 | 2012-07-06 | B | 57 | 0.012385 | 0.00017693
2013 | 2012-07-11 | B | 20 | 0.010367 | 6.2081e-05
2013 | 2012-07-11 | B | 28 | 0.033461 | 8.6913e-05
2013 | 2012-07-11 | B | 11 | 0.0080922 | 3.4144e-05
2013 | 2012-07-02 | B | 56 | 0.010951 | 0.00017383
2013 | 2012-07-12 | C | 38 | 0.0043643 | 0.00011795
2013 | 2012-07-12 | B | 57 | 0.022824 | 0.00017693
2013 | 2012-07-11 | C | 1 | 0.0041501 | 3.104e-06
2013 | 2012-07-12 | B | 5 | 0.0038645 | 1.552e-05
2013 | 2012-07-12 | B | 36 | 0.029277 | 0.00011175
2013 | 2012-07-12 | C | 14 | 0.0017383 | 4.3456e-05
2013 | 2012-07-12 | C | 772.3525 | 0.32605 | 0.0055159
2013 | 2012-07-12 | C | 52 | 0.047616 | 0.00016141
2013 | 2012-07-13 | B | 5 | 0.00091569 | 1.552e-05
2013 | 2012-07-13 | B | 71 | 0.038347 | 0.00022039
2013 | 2012-07-05 | B | 5 | 0.0034455 | 1.552e-05
2013 | 2012-07-14 | C | 34 | 0.014142 | 0.00010554
2013 | 2012-07-14 | C | 39 | 0.010532 | 0.00012106
2013 | 2012-07-14 | B | 1 | 0.0012137 | 3.104e-06
2013 | 2012-07-13 | C | 47 | 0.009191 | 0.00014589
2013 | 2012-07-13 | C | 2 | 0.0004656 | 6.2081e-06
2013 | 2012-07-14 | C | 2836.9552 | 0.56358 | 0.0090203
2013 | 2012-07-15 | C | 2820.9403 | 0.5604 | 0.0090234
2013 | 2012-07-15 | C | 11 | 0.0019804 | 3.4144e-05
2013 | 2012-07-15 | C | 113.2211 | 0.068883 | 0.00057114
2013 | 2012-07-15 | C | 2 | 0.00032282 | 6.2081e-06
2013 | 2012-07-15 | C | 516.5333 | 0.11544 | 0.0021914
2013 | 2012-07-15 | C | 27.9193 | 0.029812 | 0.00036007
2013 | 2012-07-15 | C | 276 | 0.011994 | 0.00085671
2013 | 2012-07-15 | C | 152.1304 | 0.042027 | 0.00087223
2013 | 2012-07-15 | C | 19 | 0.007549 | 5.8977e-05
2013 | 2012-07-16 | C | 9 | 0.0015644 | 2.7936e-05
2013 | 2012-07-16 | B | 3 | 0.0017414 | 9.3121e-06
2013 | 2012-07-14 | C | 47 | 0.030929 | 0.00014589
2013 | 2012-07-14 | C | 2 | 0.0014092 | 6.2081e-06
2013 | 2012-07-16 | C | 30 | 0.003818 | 9.3121e-05
2013 | 2012-07-16 | C | 146 | 0.13641 | 0.00045319
2013 | 2012-07-16 | C | 77.2333 | 0.028049 | 0.00083188
2013 | 2012-07-16 | C | 73.2796 | 0.062779 | 0.00048112
2013 | 2012-07-16 | C | 6 | 0.0016203 | 1.8624e-05
2013 | 2012-07-16 | C | 184.4811 | 0.058981 | 0.00073255
2013 | 2012-07-14 | C | 2899.0851 | 0.39595 | 0.0090203
2013 | 2012-07-17 | B | 27 | 0.0060342 | 8.3809e-05
2013 | 2012-07-17 | B | 27 | 0.013326 | 8.3809e-05
2013 | 2012-07-17 | B | 33 | 0.024277 | 0.00010243
2013 | 2012-07-17 | B | 14 | 0.01534 | 4.3456e-05
2013 | 2012-07-02 | B | 8 | 0.0017134 | 2.4832e-05
2013 | 2012-07-17 | C | 3 | 0.0085671 | 9.3121e-06
2013 | 2012-07-18 | B | 3 | 0.0011361 | 9.3121e-06
2013 | 2012-07-18 | B | 20 | 0.023715 | 6.2081e-05
2013 | 2012-07-18 | B | 243 | 0.04752 | 0.00075428
2013 | 2012-07-18 | C | 1 | 0.00026695 | 3.104e-06
2013 | 2012-07-19 | B | 1 | 0.00042525 | 3.104e-06
2013 | 2012-07-19 | B | 4 | 0.0031289 | 1.2416e-05
2013 | 2012-07-19 | B | 1 | 0.00075117 | 3.104e-06
2013 | 2012-07-19 | B | 27 | 0.024137 | 8.3809e-05
2013 | 2012-07-19 | B | 14 | 0.016644 | 4.3456e-05
2013 | 2012-07-19 | B | 42 | 0.035852 | 0.00013037
2013 | 2012-07-19 | C | 201.8922 | 0.062041 | 0.00070151
2013 | 2012-07-19 | C | 4 | 0.00070772 | 1.2416e-05
2013 | 2012-07-17 | B | 9 | 0.0018717 | 2.7936e-05
2013 | 2012-07-20 | C | 11 | 0.0012975 | 3.4144e-05
2013 | 2012-07-20 | B | 243 | 0.11012 | 0.00075428
2013 | 2012-07-20 | C | 25 | 0.0047336 | 7.7601e-05
2013 | 2012-07-20 | B | 3 | 0.002626 | 9.3121e-06
2013 | 2012-07-20 | B | 2 | 0.0021852 | 6.2081e-06
2013 | 2012-07-20 | C | 4 | 0.00055873 | 1.2416e-05
2013 | 2012-07-21 | C | 6 | 0.0038552 | 1.8624e-05
2013 | 2012-07-21 | C | 7 | 0.0014341 | 2.1728e-05
2013 | 2012-07-21 | C | 5 | 0.00072945 | 1.552e-05
2013 | 2012-07-21 | B | 6 | 0.0025515 | 1.8624e-05
2013 | 2012-07-21 | C | 33 | 0.0079898 | 0.00010243
2013 | 2012-07-22 | C | 373 | 0.015051 | 0.0011578
2013 | 2012-07-22 | C | 1 | 0.00070461 | 3.104e-06
2013 | 2012-07-22 | C | 172.7 | 0.094884 | 0.0022908
2013 | 2012-07-23 | C | 141.2053 | 0.16524 | 0.0014123
2013 | 2012-07-23 | C | 18 | 0.0034641 | 5.5873e-05
2013 | 2012-07-23 | B | 14 | 0.0087782 | 4.3456e-05
2013 | 2012-07-23 | C | 1 | 0.00089086 | 3.104e-06
2013 | 2012-07-23 | C | 144.2663 | 0.08777 | 0.001164
2013 | 2012-07-23 | C | 95 | 0.013859 | 0.00029488
2013 | 2012-07-23 | B | 9 | 0.0015924 | 2.7936e-05
2013 | 2012-07-23 | C | 345.8293 | 0.040792 | 0.0011516
2013 | 2012-07-23 | C | 30 | 0.0040973 | 9.3121e-05
2013 | 2012-07-23 | C | 1 | 0.0014775 | 3.104e-06
2013 | 2012-07-23 | C | 48 | 0.0043208 | 0.00014899
2013 | 2012-07-24 | C | 161 | 0.045977 | 0.00049975
2013 | 2012-07-24 | B | 91 | 0.039545 | 0.00028247
2013 | 2012-07-24 | C | 91 | 0.01836 | 0.00028247
2013 | 2012-07-24 | C | 1 | 0.00013037 | 3.104e-06
2013 | 2012-07-24 | C | 5 | 0.00010864 | 1.552e-05
2013 | 2012-07-24 | B | 19 | 0.018106 | 5.8977e-05
2013 | 2012-07-24 | C | 38 | 0.0056617 | 0.00011795
2013 | 2012-07-25 | B | 7 | 0.0018904 | 2.1728e-05
2013 | 2012-07-25 | C | 79.3083 | 0.091085 | 0.00073255
2013 | 2012-07-25 | C | 11 | 0.0031754 | 3.4144e-05
2013 | 2012-07-25 | B | 42 | 0.036112 | 0.00013037
2013 | 2012-07-25 | C | 116 | 0.013322 | 0.00036007
2013 | 2012-07-25 | C | 21 | 0.0014341 | 6.5185e-05
2013 | 2012-07-25 | C | 9 | 0.00081015 | 2.7936e-05
2013 | 2012-07-26 | C | 169.4444 | 0.093095 | 0.0022194
2013 | 2012-07-24 | C | 100 | 0.017693 | 0.0003104
2013 | 2012-07-26 | B | 37 | 0.0064315 | 0.00011485
2013 | 2012-07-26 | C | 62 | 0.0078904 | 0.00019245
2013 | 2012-07-26 | B | 24 | 0.021679 | 7.4497e-05
2013 | 2012-07-26 | B | 51 | 0.043851 | 0.00015831
2013 | 2012-07-26 | C | 93 | 0.0092376 | 0.00028867
2013 | 2012-07-26 | B | 318 | 0.40372 | 0.00098708
2013 | 2012-07-26 | C | 36.3468 | 0.024708 | 0.00016141
2013 | 2012-07-26 | B | 67.2687 | 0.097303 | 0.00037559
2013 | 2012-07-27 | B | 7 | 0.00067357 | 2.1728e-05
2013 | 2012-07-27 | B | 13 | 0.0029054 | 4.0352e-05
2013 | 2012-07-27 | B | 132 | 0.11227 | 0.00040973
2013 | 2012-07-27 | C | 24.8495 | 0.006942 | 0.00023591
2013 | 2012-07-27 | C | 76 | 0.020524 | 0.00023591
2013 | 2012-07-27 | C | 293.5481 | 0.092029 | 0.0016234
2013 | 2012-07-26 | C | 1 | 0.00034144 | 3.104e-06
2013 | 2012-07-27 | C | 1 | 0.00023901 | 3.104e-06
2013 | 2012-07-28 | C | 735.2637 | 0.20084 | 0.0025608
2013 | 2012-07-29 | B | 86 | 0.041911 | 0.00026695
2013 | 2012-07-29 | C | 168 | 0.0088651 | 0.00052148
2013 | 2012-07-29 | C | 172.0392 | 0.24351 | 0.0017755
2013 | 2012-07-29 | C | 115.4305 | 0.053028 | 0.00061149
2013 | 2012-07-29 | C | 2 | 0.00093742 | 6.2081e-06
2013 | 2012-07-29 | C | 802.1959 | 0.60259 | 0.0041656
2013 | 2012-07-26 | C | 1689.4545 | 0.21501 | 0.0067947
2013 | 2012-07-26 | C | 151.7231 | 0.029199 | 0.00047181
2013 | 2012-07-30 | C | 20 | 0.0074497 | 6.2081e-05
2013 | 2012-07-30 | C | 308.5597 | 0.12547 | 0.0018345
2013 | 2012-07-30 | C | 22 | 0.00081946 | 6.8289e-05
2013 | 2012-07-30 | C | 291 | 0.0027098 | 0.00090327
2013 | 2012-07-30 | C | 40.2466 | 0.0087449 | 0.00012727
2013 | 2012-07-30 | C | 20.5631 | 0.019532 | 6.5185e-05
2013 | 2012-07-30 | C | 64.8085 | 0.14645 | 0.00073255
2013 | 2012-07-30 | C | 2 | 0.00078842 | 6.2081e-06
2013 | 2012-07-30 | C | 513.9315 | 1.0433 | 0.0042556
2013 | 2012-07-30 | C | 191.9849 | 0.23539 | 0.0016576
2013 | 2012-07-30 | C | 1 | 0.00054631 | 3.104e-06
2013 | 2012-07-30 | C | 150 | 0.0032592 | 0.0004656
2013 | 2012-07-30 | C | 97.4375 | 0.028128 | 0.0004625
2013 | 2012-07-30 | C | 20.0518 | 0.077926 | 6.5185e-05
2013 | 2012-07-30 | C | 170.9424 | 0.072163 | 0.00067668
2013 | 2012-07-30 | C | 1056.3291 | 0.24919 | 0.0043394
2013 | 2012-07-30 | C | 83.3986 | 0.21486 | 0.0018997
2013 | 2012-07-30 | C | 573 | 0.26501 | 0.0017786
2013 | 2012-07-31 | B | 3 | 0.00034455 | 9.3121e-06
2013 | 2012-07-31 | C | 4 | 0.001701 | 1.2416e-05
2013 | 2012-07-31 | B | 57 | 0.049894 | 0.00017693
2013 | 2012-07-31 | C | 36 | 0.013186 | 0.00011175
2013 | 2012-08-01 | B | 296 | 0.16722 | 0.00091879
2013 | 2012-08-01 | B | 27 | 0.003939 | 8.3809e-05
2013 | 2012-08-01 | B | 72 | 0.060789 | 0.00022349
2013 | 2012-07-31 | C | 30.9451 | 0.017194 | 0.00016451
2013 | 2012-08-01 | C | 5 | 0.00072945 | 1.552e-05
2013 | 2012-08-01 | C | 224.9286 | 0.056553 | 0.00085671
2013 | 2012-08-01 | B | 51 | 0.048125 | 0.00015831
2013 | 2012-08-01 | B | 200 | 0.19742 | 0.00062081
2013 | 2012-07-31 | C | 700 | 0.65185 | 0.0021728
2013 | 2012-08-01 | C | 76 | 0.011795 | 0.00023591
2013 | 2012-08-01 | B | 45 | 0.055034 | 0.00013968
2013 | 2012-08-01 | B | 76 | 0.077377 | 0.00023591
2013 | 2012-07-31 | C | 287 | 0.0017817 | 0.00089086
2013 | 2012-08-01 | C | 130 | 0.00040352 | 0.00040352
2013 | 2012-08-01 | C | 339 | 0.0010523 | 0.0010523
2013 | 2012-07-23 | B | 234 | 0.053749 | 0.00072634
2013 | 2012-08-02 | B | 3 | 0.00082878 | 9.3121e-06
2013 | 2012-07-31 | C | 66.2363 | 0.19511 | 0.00033834
2013 | 2012-07-30 | C | 3 | 0.0023653 | 9.3121e-06
2013 | 2012-08-02 | B | 22 | 0.019257 | 6.8289e-05
2013 | 2012-08-02 | C | 10 | 0.0022349 | 3.104e-05
2013 | 2012-08-02 | C | 829 | 0.12866 | 0.0025732
2013 | 2012-08-02 | C | 475 | 0.030963 | 0.0014744
2013 | 2012-08-02 | C | 3 | 0.00051216 | 9.3121e-06
2013 | 2012-08-02 | C | 54 | 0.010057 | 0.00016762
2013 | 2012-08-02 | B | 20 | 0.024025 | 6.2081e-05
2013 | 2012-08-02 | B | 1 | 0.0011857 | 3.104e-06
2013 | 2012-08-02 | C | 68 | 0.0025329 | 0.00021107
2013 | 2012-08-02 | C | 368 | 0.028557 | 0.0011423
2013 | 2012-08-03 | C | 7 | 0.0021076 | 2.1728e-05
2013 | 2012-08-03 | B | 1 | 0.00027005 | 3.104e-06
2013 | 2012-08-03 | C | 51 | 0.023113 | 0.00015831
2013 | 2012-08-03 | C | 1 | 3.7248e-05 | 3.104e-06
2013 | 2012-08-03 | B | 1 | 0.00054941 | 3.104e-06
2013 | 2012-08-03 | B | 14 | 0.0071703 | 4.3456e-05
2013 | 2012-08-03 | B | 40 | 0.041718 | 0.00012416
2013 | 2012-08-03 | B | 11 | 0.01376 | 3.4144e-05
2013 | 2012-08-03 | C | 16 | 0.0033772 | 4.9664e-05
2013 | 2012-08-03 | B | 13 | 0.014809 | 4.0352e-05
2013 | 2012-08-04 | C | 129.157 | 0.047307 | 0.00083188
2013 | 2012-08-04 | C | 38 | 0.043996 | 0.00011795
2013 | 2012-08-04 | C | 421 | 0.0039204 | 0.0013068
2013 | 2012-08-04 | C | 74.5616 | 0.016201 | 0.00059908
2013 | 2012-08-04 | C | 1353 | 0.16799 | 0.0041998
2013 | 2012-08-04 | C | 591 | 0.080717 | 0.0018345
2013 | 2012-08-04 | C | 629 | 0.085907 | 0.0019524
2013 | 2012-08-04 | B | 14 | 0.0091693 | 4.3456e-05
2013 | 2012-08-04 | C | 467.5364 | 0.15528 | 0.0043394
2013 | 2012-08-05 | C | 20 | 0.014899 | 6.2081e-05
2013 | 2012-08-06 | C | 569 | 0.097141 | 0.0017662
2013 | 2012-08-06 | C | 99.9504 | 0.080354 | 0.00063633
2013 | 2012-08-06 | C | 11 | 0.0074093 | 3.4144e-05
2013 | 2012-08-06 | B | 95 | 0.059271 | 0.00029488
2013 | 2012-08-06 | B | 4 | 0.0020611 | 1.2416e-05
2013 | 2012-08-06 | B | 4 | 0.0021107 | 1.2416e-05
2013 | 2012-08-06 | C | 2 | 7.4497e-05 | 6.2081e-06
2013 | 2012-08-06 | C | 1 | 1.8624e-05 | 3.104e-06
2013 | 2012-08-06 | B | 3 | 0.0022256 | 9.3121e-06
2013 | 2012-08-06 | B | 13 | 0.014809 | 4.0352e-05
2013 | 2012-08-06 | C | 6 | 0.00031661 | 1.8624e-05
2013 | 2012-08-07 | B | 2 | 0.00073876 | 6.2081e-06
2013 | 2012-08-07 | C | 17 | 0.0015303 | 5.2768e-05
2013 | 2012-08-07 | B | 19 | 0.017811 | 5.8977e-05
2013 | 2012-08-07 | B | 19 | 0.018047 | 5.8977e-05
2013 | 2012-08-07 | C | 124.7761 | 0.10264 | 0.00055562
2013 | 2012-08-07 | B | 19 | 0.020111 | 5.8977e-05
2013 | 2012-08-07 | B | 3 | 0.0031754 | 9.3121e-06
2013 | 2012-08-07 | B | 38 | 0.034324 | 0.00011795
2013 | 2012-08-07 | B | 3 | 0.0044977 | 9.3121e-06
2013 | 2012-08-07 | C | 2 | 0.0014092 | 6.2081e-06
2013 | 2012-08-07 | B | 16 | 0.021356 | 4.9664e-05
2013 | 2012-08-08 | C | 66 | 0.07703 | 0.00020487
2013 | 2012-08-08 | C | 936.7339 | 0.30821 | 0.0036628
2013 | 2012-08-08 | C | 5 | 0.0062081 | 1.552e-05
2013 | 2012-08-08 | B | 102 | 0.068705 | 0.00031661
2013 | 2012-08-08 | B | 47 | 0.038077 | 0.00014589
2013 | 2012-08-08 | C | 53 | 0.024348 | 0.00016451
2013 | 2012-08-08 | C | 124.2932 | 0.072532 | 0.00079774
2013 | 2012-08-08 | C | 294.0124 | 0.14419 | 0.0022753
2013 | 2012-08-09 | C | 51 | 0.0087068 | 0.00015831
2013 | 2012-08-09 | B | 3 | 0.00091258 | 9.3121e-06
2013 | 2012-08-09 | B | 13 | 0.0023001 | 4.0352e-05
2013 | 2012-08-09 | B | 3 | 0.0020952 | 9.3121e-06
2013 | 2012-08-09 | B | 43 | 0.04498 | 0.00013347
2013 | 2012-08-09 | B | 1 | 0.00031661 | 3.104e-06
2013 | 2012-08-09 | B | 30 | 0.025794 | 9.3121e-05
2013 | 2012-08-09 | B | 59 | 0.079115 | 0.00018314
2013 | 2012-08-09 | B | 31 | 0.041377 | 9.6225e-05
2013 | 2012-08-10 | C | 109 | 0.040601 | 0.00033834
2013 | 2012-08-10 | C | 290 | 0.020704 | 0.00090017
2013 | 2012-08-10 | C | 8 | 0.0015396 | 2.4832e-05
2013 | 2012-08-10 | B | 240 | 0.19891 | 0.00074497
2013 | 2012-08-10 | B | 1 | 0.00078842 | 3.104e-06
2013 | 2012-08-11 | B | 1 | 0.00027315 | 3.104e-06
2013 | 2012-08-10 | B | 1 | 0.00050285 | 3.104e-06
2013 | 2012-08-11 | C | 1 | 9.6225e-05 | 3.104e-06
2013 | 2012-08-10 | C | 10 | 0.024677 | 3.104e-05
2013 | 2012-08-10 | C | 560 | 0.081698 | 0.0017383
2013 | 2012-08-11 | C | 60.6063 | 0.071111 | 0.00048112
2013 | 2012-08-12 | C | 77 | 0.023423 | 0.00023901
2013 | 2012-08-12 | C | 1 | 0.0005401 | 3.104e-06
2013 | 2012-08-11 | C | 22.2973 | 0.035644 | 0.0014403
2013 | 2012-08-12 | C | 558.9789 | 0.15963 | 0.0017352
2013 | 2012-08-12 | C | 118.1875 | 0.016509 | 0.00042836
2013 | 2012-08-12 | C | 69.1458 | 0.06117 | 0.00077911
2013 | 2012-08-11 | C | 433.3981 | 0.43183 | 0.0041253
2013 | 2012-08-12 | C | 135.3714 | 0.086981 | 0.0011423
2013 | 2012-08-12 | C | 14 | 0.001521 | 4.3456e-05
2013 | 2012-08-12 | C | 39 | 0.077719 | 0.00012106
2013 | 2012-08-11 | C | 97 | 0.26586 | 0.00030109
2013 | 2012-08-12 | C | 14 | 0.0089955 | 4.3456e-05
2013 | 2012-08-13 | C | 37.8398 | 0.056849 | 0.00057735
2013 | 2012-08-13 | C | 183.8252 | 0.079884 | 0.0013937
2013 | 2012-08-12 | C | 78 | 0.27988 | 0.00024211
2013 | 2012-08-13 | B | 2 | 0.00049664 | 6.2081e-06
2013 | 2012-08-13 | C | 221 | 0.001372 | 0.00068599
2013 | 2012-08-13 | C | 66.5532 | 0.0090897 | 0.00039732
2013 | 2012-08-13 | B | 14 | 0.011212 | 4.3456e-05
2013 | 2012-08-13 | C | 10 | 0.0016141 | 3.104e-05
2013 | 2012-08-13 | C | 19.9638 | 0.023796 | 6.5185e-05
2013 | 2012-08-13 | C | 409.6882 | 0.11445 | 0.0024025
2013 | 2012-08-13 | B | 164 | 0.23111 | 0.00050906
2013 | 2012-08-14 | C | 8 | 0.0008443 | 2.4832e-05
2013 | 2012-08-14 | C | 43 | 0.015082 | 0.00013347
2013 | 2012-08-14 | B | 1 | 0.00076049 | 3.104e-06
2013 | 2012-08-14 | C | 26 | 0.013074 | 8.0705e-05
2013 | 2012-08-14 | B | 233 | 0.1931 | 0.00072324
2013 | 2012-08-14 | B | 49 | 0.051257 | 0.0001521
2013 | 2012-08-14 | B | 3 | 0.003073 | 9.3121e-06
2013 | 2012-08-14 | B | 10 | 0.011485 | 3.104e-05
2013 | 2012-08-14 | C | 7 | 0.002477 | 2.1728e-05
2013 | 2012-08-14 | B | 68 | 0.098572 | 0.00021107
2013 | 2012-08-15 | C | 2 | 0.00037869 | 6.2081e-06
2013 | 2012-08-15 | B | 5 | 0.00072945 | 1.552e-05
2013 | 2012-08-15 | C | 62 | 0.023671 | 0.00019245
2013 | 2012-08-15 | B | 11 | 0.0061118 | 3.4144e-05
2013 | 2012-08-15 | C | 19 | 0.0042463 | 5.8977e-05
2013 | 2012-08-15 | C | 11 | 0.0003073 | 3.4144e-05
2013 | 2012-08-15 | B | 12 | 0.0052893 | 3.7248e-05
2013 | 2012-08-15 | B | 103 | 0.12948 | 0.00031971
2013 | 2012-08-16 | C | 306 | 0.011398 | 0.00094983
2013 | 2012-08-16 | C | 30 | 0.0039111 | 9.3121e-05
2013 | 2012-08-16 | C | 92.0645 | 0.025719 | 0.0011361
2013 | 2012-08-16 | B | 49 | 0.045477 | 0.0001521
2013 | 2012-08-16 | C | 12 | 0.0017879 | 3.7248e-05
2013 | 2012-08-16 | C | 376.0349 | 0.09688 | 0.002418
2013 | 2012-08-16 | B | 240 | 0.19816 | 0.00074497
2013 | 2012-08-16 | B | 2 | 0.0024832 | 6.2081e-06
2013 | 2012-08-16 | C | 401 | 0.24521 | 0.0012447
2013 | 2012-08-16 | C | 110.5588 | 0.057311 | 0.0016544
2013 | 2012-08-16 | C | 175.0326 | 0.098338 | 0.0015613
2013 | 2012-08-16 | C | 63 | 0.011342 | 0.00019555
2013 | 2012-08-16 | C | 13 | 0.004923 | 4.0352e-05
2013 | 2012-08-17 | B | 6 | 0.0010802 | 1.8624e-05
2013 | 2012-08-17 | B | 233 | 0.20034 | 0.00072324
2013 | 2012-08-18 | B | 42 | 0.034417 | 0.00013037
2013 | 2012-08-18 | C | 419.3252 | 0.15619 | 0.0024615
2013 | 2012-08-18 | B | 1 | 0.00062081 | 3.104e-06
2013 | 2012-08-18 | C | 429 | 0.15181 | 0.0013316
2013 | 2012-08-19 | C | 99.9091 | 0.0093036 | 0.00032592
2013 | 2012-08-19 | C | 24.7197 | 0.020027 | 9.3121e-05
2013 | 2012-08-19 | C | 160 | 0.018376 | 0.00049664
2013 | 2012-08-19 | C | 37.6707 | 0.0092376 | 0.00027626
2013 | 2012-08-19 | C | 48.4828 | 0.02137 | 0.0003818
2013 | 2012-08-20 | C | 12 | 0.0017507 | 3.7248e-05
2013 | 2012-08-20 | C | 59.8149 | 0.096733 | 0.00019866
2013 | 2012-08-20 | C | 10 | 0.010926 | 3.104e-05
2013 | 2012-08-20 | C | 1 | 0.00085982 | 3.104e-06
2013 | 2012-08-20 | C | 4 | 0.0032654 | 1.2416e-05
2013 | 2012-08-03 | B | 57.7676 | 0.065808 | 0.00041904
2013 | 2012-08-20 | C | 4 | 0.0018997 | 1.2416e-05
2013 | 2012-08-20 | B | 120 | 0.13298 | 0.00037248
2013 | 2012-08-20 | B | 31 | 0.033486 | 9.6225e-05
2013 | 2012-08-20 | C | 2 | 0.00029799 | 6.2081e-06
2013 | 2012-08-20 | C | 27 | 0.0022628 | 8.3809e-05
2013 | 2012-08-20 | C | 21 | 0.0030637 | 6.5185e-05
2013 | 2012-08-20 | C | 6.1738 | 0.010195 | 9.3121e-06
2013 | 2012-08-21 | B | 2 | 0.00090017 | 6.2081e-06
2013 | 2012-08-21 | C | 139 | 0.0017258 | 0.00043146
2013 | 2012-08-21 | B | 46 | 0.031698 | 0.00014279
2013 | 2012-08-21 | C | 12 | 0.0030544 | 3.7248e-05
2013 | 2012-08-21 | C | 7 | 0.0023684 | 2.1728e-05
2013 | 2012-08-21 | B | 27 | 0.028495 | 8.3809e-05
2013 | 2012-08-21 | C | 1 | 0.0009219 | 3.104e-06
2013 | 2012-08-21 | C | 464.7383 | 0.21061 | 0.0024242
2013 | 2012-08-21 | B | 139 | 0.09449 | 0.00043146
2013 | 2012-08-21 | B | 146 | 0.18445 | 0.00045319
2013 | 2012-08-20 | C | 1 | 0.0065402 | 3.104e-06
2013 | 2012-08-22 | B | 7 | 0.0024336 | 2.1728e-05
2013 | 2012-08-02 | B | 2 | 0.0003849 | 6.2081e-06
2013 | 2012-08-22 | C | 221 | 0.16121 | 0.00068599
2013 | 2012-08-07 | B | 4 | 0.0013906 | 1.2416e-05
2013 | 2012-08-15 | B | 3 | 0.0034362 | 9.3121e-06
2013 | 2012-08-22 | B | 2 | 0.0017196 | 6.2081e-06
2013 | 2012-08-22 | B | 3 | 0.00071703 | 9.3121e-06
2013 | 2012-08-22 | B | 12 | 0.015086 | 3.7248e-05
2013 | 2012-08-23 | B | 15 | 0.0081015 | 4.656e-05
2013 | 2012-08-23 | C | 2 | 0.0010243 | 6.2081e-06
2013 | 2012-08-23 | B | 1.92 | 0.0004291 | 1.2416e-05
2013 | 2012-08-24 | C | 8 | 0.0026322 | 2.4832e-05
2013 | 2012-08-25 | C | 1303 | 0.048535 | 0.0040445
2013 | 2012-08-24 | C | 31.7213 | 0.011717 | 0.0014185
2013 | 2012-08-24 | C | 108 | 0.043245 | 0.00033524
2013 | 2012-08-24 | C | 29 | 0.0037807 | 9.0017e-05
2013 | 2012-08-24 | B | 23 | 0.020704 | 7.1393e-05
2013 | 2012-08-24 | C | 463.9929 | 0.19875 | 0.0022039
2013 | 2012-08-26 | C | 440.8934 | 0.2655 | 0.005013
2013 | 2012-08-27 | C | 82 | 0.021126 | 0.00025453
2013 | 2012-08-27 | B | 38 | 0.021821 | 0.00011795
2013 | 2012-08-27 | C | 94 | 0.089868 | 0.00029178
2013 | 2012-08-27 | C | 33 | 0.0063508 | 0.00010243
2013 | 2012-08-27 | C | 1 | 0.00013968 | 3.104e-06
2013 | 2012-08-27 | C | 2 | 0.00025453 | 6.2081e-06
2013 | 2012-08-28 | B | 32 | 0.011323 | 9.9329e-05
2013 | 2012-08-27 | B | 2 | 0.0006146 | 6.2081e-06
2013 | 2012-08-24 | B | 10 | 0.0071082 | 3.104e-05
2013 | 2012-08-02 | B | 2 | 0.00031661 | 6.2081e-06
2013 | 2012-08-24 | C | 6 | 0.018643 | 1.8624e-05
2013 | 2012-08-28 | C | 5 | 4.656e-05 | 1.552e-05
2013 | 2012-08-28 | B | 6 | 0.0017134 | 1.8624e-05
2013 | 2012-08-28 | B | 33 | 0.017311 | 0.00010243
2013 | 2012-08-28 | B | 64 | 0.058604 | 0.00019866
2013 | 2012-08-28 | B | 12 | 0.013298 | 3.7248e-05
2013 | 2012-08-28 | B | 62 | 0.068705 | 0.00019245
2013 | 2012-08-27 | C | 67 | 0.021005 | 0.00020797
2013 | 2012-08-29 | B | 6 | 0.0016203 | 1.8624e-05
2013 | 2012-08-28 | B | 2 | 0.0005401 | 6.2081e-06
2013 | 2012-08-29 | C | 106 | 0.022045 | 0.00071703
2013 | 2012-08-29 | C | 111 | 0.0017227 | 0.00034455
2013 | 2012-08-29 | B | 5 | 0.0032127 | 1.552e-05
2013 | 2012-08-29 | B | 94 | 0.078488 | 0.00029178
2013 | 2012-08-29 | B | 10 | 0.011175 | 3.104e-05
2013 | 2012-08-29 | B | 2 | 0.0023404 | 6.2081e-06
2013 | 2012-08-29 | C | 132 | 0.071293 | 0.00040973
2013 | 2012-08-29 | B | 1 | 0.00048733 | 3.104e-06
2013 | 2012-08-29 | C | 70.4912 | 0.049232 | 0.00057425
2013 | 2012-08-30 | B | 12 | 0.014862 | 3.7248e-05
2013 | 2012-08-29 | B | 1 | 0.00023901 | 3.104e-06
2013 | 2012-08-31 | C | 247 | 0.030668 | 0.0007667
2013 | 2012-09-01 | C | 45 | 0.010057 | 0.00013968
2013 | 2012-09-01 | C | 114.1318 | 0.044638 | 0.00051837
2013 | 2012-08-31 | B | 3 | 0.0013689 | 9.3121e-06
2013 | 2012-08-31 | C | 849.9333 | 0.071232 | 0.0028961
2013 | 2012-09-01 | C | 232 | 0.05473 | 0.00072013
2013 | 2012-09-01 | C | 1 | 7.7601e-05 | 3.104e-06
2013 | 2012-09-02 | C | 529 | 0.019704 | 0.001642
2013 | 2012-09-02 | C | 55 | 0.0022194 | 0.00017072
2013 | 2012-09-02 | C | 84.0215 | 0.047727 | 0.00040663
2013 | 2012-09-01 | C | 111 | 0.056161 | 0.00051216
2013 | 2012-09-02 | C | 144.2601 | 0.076124 | 0.00062391
2013 | 2012-08-31 | C | 50 | 0.024211 | 0.0001552
2013 | 2012-09-01 | C | 35 | 0.0032592 | 0.00010864
2013 | 2012-09-02 | C | 94 | 0.0040849 | 0.00029178
2013 | 2012-08-30 | B | 1 | 0.0026105 | 3.104e-06
2013 | 2012-09-03 | C | 7 | 0.00058666 | 2.1728e-05
2013 | 2012-09-03 | C | 13 | 0.0020983 | 4.0352e-05
2013 | 2012-09-03 | C | 210.5928 | 0.3994 | 0.0032375
2013 | 2012-09-03 | C | 73 | 0.012916 | 0.00022659
2013 | 2012-09-03 | C | 2 | 0.00029178 | 6.2081e-06
2013 | 2012-09-03 | B | 124 | 0.042724 | 0.0003849
2013 | 2012-09-03 | B | 1 | 0.00034765 | 3.104e-06
2013 | 2012-09-03 | C | 220.2963 | 0.18258 | 0.0029333
2013 | 2012-09-03 | B | 510 | 0.50974 | 0.0015831
2013 | 2012-09-04 | C | 515 | 0.05595 | 0.0015986
2013 | 2012-09-04 | C | 41 | 0.0047088 | 0.00012727
2013 | 2012-09-04 | C | 138.2764 | 0.084126 | 0.0019121
2013 | 2012-09-04 | C | 216.8209 | 0.043073 | 0.0012944
2013 | 2012-09-04 | B | 3 | 0.0033151 | 9.3121e-06
2013 | 2012-09-04 | B | 134 | 0.13393 | 0.00041594
2013 | 2012-09-04 | B | 53 | 0.057415 | 0.00016451
2013 | 2012-09-04 | B | 101 | 0.030097 | 0.00031351
2013 | 2012-09-04 | C | 1079.1163 | 0.13398 | 0.0039483
2013 | 2012-09-04 | B | 33 | 0.043432 | 0.00010243
2013 | 2012-09-04 | C | 105 | 0.011081 | 0.00032592
2013 | 2012-09-04 | C | 56 | 0.0038242 | 0.00017383
2013 | 2012-09-04 | C | 607.4444 | 0.33374 | 0.0041594
2013 | 2012-09-04 | C | 106.4359 | 0.063433 | 0.00072013
2013 | 2012-09-04 | C | 52.248 | 0.20289 | 0.0024242
2013 | 2012-09-05 | C | 7 | 0.00026074 | 2.1728e-05
2013 | 2012-09-05 | C | 27.5676 | 0.041502 | 0.00078532
2013 | 2012-09-05 | B | 77 | 0.048519 | 0.00023901
2013 | 2012-09-05 | B | 49 | 0.027225 | 0.0001521
2013 | 2012-09-05 | C | 178 | 0.0066302 | 0.00055252
2013 | 2012-09-05 | C | 3 | 0.00071703 | 9.3121e-06
2013 | 2012-09-05 | B | 36 | 0.022014 | 0.00011175
2013 | 2012-09-05 | C | 5 | 0.0011175 | 1.552e-05
2013 | 2012-09-05 | B | 17 | 0.014511 | 5.2768e-05
2013 | 2012-09-05 | B | 8 | 0.007847 | 2.4832e-05
2013 | 2012-09-05 | B | 102 | 0.10828 | 0.00031661
2013 | 2012-09-05 | C | 144.8163 | 0.042704 | 0.00079463
2013 | 2012-09-05 | C | 25 | 0.0041904 | 7.7601e-05
2013 | 2012-09-04 | B | 32 | 0.0060591 | 9.9329e-05
2013 | 2012-09-05 | B | 32 | 0.030494 | 9.9329e-05
2013 | 2012-09-05 | B | 82 | 0.083231 | 0.00025453
2013 | 2012-09-05 | B | 55 | 0.041656 | 0.00017072
2013 | 2012-09-05 | C | 197.1805 | 0.079567 | 0.00071082
2013 | 2012-09-06 | C | 445.25 | 0.15617 | 0.0024429
2013 | 2012-09-06 | B | 9 | 0.0028495 | 2.7936e-05
2013 | 2012-09-06 | B | 1 | 0.00017693 | 3.104e-06
2013 | 2012-09-06 | C | 235.5811 | 0.051919 | 0.0010616
2013 | 2012-09-06 | C | 206.0667 | 0.084432 | 0.00070772
2013 | 2012-09-06 | B | 6 | 0.005401 | 1.8624e-05
2013 | 2012-09-06 | B | 53 | 0.0306 | 0.00016451
2013 | 2012-09-06 | B | 16 | 0.012168 | 4.9664e-05
2013 | 2012-09-06 | B | 1 | 0.00036628 | 3.104e-06
2013 | 2012-09-06 | B | 183.0209 | 0.1068 | 0.00080394
2013 | 2012-09-06 | C | 133 | 0.004954 | 0.00041284
2013 | 2012-09-06 | C | 16 | 0.0016886 | 4.9664e-05
2013 | 2012-09-06 | C | 123.15 | 0.082951 | 0.00055252
2013 | 2012-09-07 | C | 347.6142 | 0.1338 | 0.0012292
2013 | 2012-09-06 | B | 38 | 0.027719 | 0.00011795
2013 | 2012-09-07 | C | 17 | 0.002058 | 5.2768e-05
2013 | 2012-09-07 | B | 128 | 0.022647 | 0.00039732
2013 | 2012-09-05 | B | 1 | 0.00025763 | 3.104e-06
2013 | 2012-09-01 | B | 47 | 0.019257 | 0.00014589
2013 | 2012-09-07 | B | 87.1429 | 0.063566 | 0.00040352
2013 | 2012-09-07 | B | 15 | 0.003073 | 4.656e-05
2013 | 2012-09-07 | B | 1 | 4.656e-05 | 3.104e-06
2013 | 2012-09-07 | B | 3 | 0.0019276 | 9.3121e-06
2013 | 2012-09-07 | B | 26 | 0.017513 | 8.0705e-05
2013 | 2012-09-07 | B | 61 | 0.06949 | 0.00018935
2013 | 2012-09-07 | C | 159.2299 | 0.041517 | 0.0006953
2013 | 2012-09-07 | C | 307 | 0.11054 | 0.00095294
2013 | 2012-09-07 | C | 11 | 0.0011268 | 3.4144e-05
2013 | 2012-09-07 | C | 74.1772 | 0.017499 | 0.00023591
2013 | 2012-09-07 | C | 139 | 0.022004 | 0.00043146
2013 | 2012-09-07 | C | 122.6279 | 0.064328 | 0.0009995
2013 | 2012-09-07 | C | 66 | 0.0014341 | 0.00020487
2013 | 2012-09-07 | C | 22.1538 | 0.0096273 | 0.00041284
2013 | 2012-09-07 | C | 367 | 0.01367 | 0.0011392
2013 | 2012-09-07 | C | 222.7812 | 0.042183 | 0.00088154
2013 | 2012-09-08 | C | 117.0208 | 0.051216 | 0.0008505
2013 | 2012-09-08 | B | 49 | 0.024792 | 0.0001521
2013 | 2012-09-08 | C | 215 | 0.0080084 | 0.00066737
2013 | 2012-09-08 | C | 472 | 0.017581 | 0.0014651
2013 | 2012-09-09 | C | 199 | 0.027179 | 0.0006177
2013 | 2012-09-09 | C | 158.5102 | 0.022633 | 0.00063012
2013 | 2012-09-09 | C | 155.7792 | 0.035782 | 0.00057735
2013 | 2012-09-09 | C | 7 | 0.0013689 | 2.1728e-05
2013 | 2012-09-09 | C | 18 | 0.0021232 | 5.5873e-05
2013 | 2012-09-09 | C | 3 | 0.00051216 | 9.3121e-06
2013 | 2012-09-09 | C | 27 | 0.00528 | 8.3809e-05
2013 | 2012-09-09 | C | 56 | 0.0012168 | 0.00017383
2013 | 2012-09-09 | C | 124.4787 | 0.080368 | 0.00063012
2013 | 2012-09-09 | C | 322.7665 | 0.16431 | 0.0030047
2013 | 2012-09-09 | C | 1 | 0.00064564 | 3.104e-06
2013 | 2012-09-09 | C | 12 | 0.00093121 | 3.7248e-05
2013 | 2012-09-08 | C | 49 | 0.024488 | 0.0001521
2013 | 2012-09-09 | C | 165.549 | 0.024666 | 0.0010709
2013 | 2012-09-09 | C | 546 | 0.077961 | 0.0016948
2013 | 2012-09-08 | C | 19 | 0.0037155 | 5.8977e-05
2013 | 2012-09-09 | C | 339 | 0.1852 | 0.0010523
2013 | 2012-09-09 | C | 110 | 0.016048 | 0.00034144
2013 | 2012-09-08 | C | 10 | 0.0026074 | 3.104e-05
2013 | 2012-09-08 | C | 21 | 0.10892 | 6.5185e-05
2013 | 2012-09-08 | C | 155.245 | 0.071319 | 0.00058977
2013 | 2012-09-06 | C | 20.0255 | 0.16566 | 6.5185e-05
2013 | 2012-09-08 | C | 154.1951 | 0.13593 | 0.00083188
2013 | 2012-09-08 | C | 31 | 0.0042339 | 9.6225e-05
2013 | 2012-09-08 | C | 377.2216 | 0.19203 | 0.0024242
2013 | 2012-09-08 | C | 100.6704 | 0.082496 | 0.00050596
2013 | 2012-09-08 | C | 23 | 0.0079246 | 7.1393e-05
2013 | 2012-09-08 | C | 392.9639 | 0.4013 | 0.0012944
2013 | 2012-09-08 | C | 235 | 0.0051061 | 0.00072945
2013 | 2012-09-08 | C | 311 | 0.0086882 | 0.00096535
2013 | 2012-09-08 | C | 43 | 0.0024025 | 0.00013347
2013 | 2012-09-09 | C | 43 | 0.0024025 | 0.00013347
2013 | 2012-09-08 | C | 677 | 0.037826 | 0.0021014
2013 | 2012-09-08 | C | 40.3333 | 0.02216 | 0.00023901
2013 | 2012-09-09 | C | 75.3379 | 0.085122 | 0.00066737
2013 | 2012-09-09 | C | 162.408 | 0.061503 | 0.00054941
2013 | 2012-09-09 | C | 128.0245 | 0.2583 | 0.0017476
2013 | 2012-09-07 | C | 43 | 0.014816 | 0.00013347
2013 | 2012-09-08 | C | 43 | 0.01615 | 0.00013347
2013 | 2012-09-08 | C | 44 | 0.07143 | 0.00013658
2013 | 2012-09-08 | C | 52.0861 | 0.033305 | 0.00039421
2013 | 2012-09-08 | C | 109 | 0.2568 | 0.00033834
2013 | 2012-09-09 | C | 2 | 0.00063943 | 6.2081e-06
2013 | 2012-09-10 | B | 55 | 0.0093897 | 0.00017072
2013 | 2012-09-10 | C | 7 | 0.0014992 | 2.1728e-05
2013 | 2012-09-10 | C | 46 | 0.0091383 | 0.00014279
2013 | 2012-09-08 | C | 105.153 | 0.058752 | 0.00070772
2013 | 2012-09-10 | C | 3 | 0.00025143 | 9.3121e-06
2013 | 2012-09-10 | C | 3 | 0.00051216 | 9.3121e-06
2013 | 2012-09-10 | C | 197.8333 | 0.19712 | 0.00073876
2013 | 2012-09-09 | C | 2 | 0.006177 | 6.2081e-06
2013 | 2012-09-10 | C | 43 | 0.01001 | 0.00013347
2013 | 2012-09-09 | C | 11 | 0.0060435 | 3.4144e-05
2013 | 2012-09-10 | C | 2 | 0.00060218 | 6.2081e-06
2013 | 2012-09-10 | C | 407.2656 | 0.15802 | 0.0012727
2013 | 2012-09-11 | C | 99 | 0.0049168 | 0.0003073
2013 | 2012-09-10 | C | 1 | 0.0031816 | 3.104e-06
2013 | 2012-09-10 | C | 3 | 0.00067978 | 9.3121e-06
2013 | 2012-09-10 | C | 172.0316 | 0.082769 | 0.00066116
2013 | 2012-09-10 | C | 180 | 0.17432 | 0.00055873
2013 | 2012-09-11 | C | 29.7619 | 0.038523 | 0.00023901
2013 | 2012-09-11 | B | 15 | 0.010662 | 4.656e-05
2013 | 2012-09-11 | C | 45.6031 | 0.027037 | 0.00040973
2013 | 2012-09-11 | B | 129 | 0.094899 | 0.00040042
2013 | 2012-09-11 | B | 17 | 0.022796 | 5.2768e-05
2013 | 2012-09-11 | C | 14 | 0.0021728 | 4.3456e-05
2013 | 2012-09-11 | C | 19 | 0.0066054 | 5.8977e-05
2013 | 2012-09-11 | B | 407 | 0.36258 | 0.0012633
2013 | 2012-09-11 | C | 934 | 0.040588 | 0.0028992
2013 | 2012-09-11 | C | 21.2161 | 0.026013 | 0.00036628
2013 | 2012-09-11 | C | 310.3472 | 0.52983 | 0.0028495
2013 | 2012-09-11 | C | 660.2907 | 0.17011 | 0.0030978
2013 | 2012-09-11 | C | 496.1644 | 0.22024 | 0.0020983
2013 | 2012-09-11 | C | 5 | 0.0011951 | 1.552e-05
2013 | 2012-09-12 | B | 1 | 0.0005432 | 3.104e-06
2013 | 2012-09-12 | C | 60.644 | 0.071343 | 0.00027315
2013 | 2012-09-12 | C | 42 | 0.0062577 | 0.00013037
2013 | 2012-09-12 | C | 49.9646 | 0.01706 | 0.00023901
2013 | 2012-09-12 | C | 20 | 0.012664 | 6.2081e-05
2013 | 2012-09-12 | B | 106 | 0.11417 | 0.00032903
2013 | 2012-09-12 | C | 17.375 | 0.0076045 | 8.3809e-05
2013 | 2012-09-12 | C | 2 | 0.00044698 | 6.2081e-06
2013 | 2012-09-12 | C | 3 | 0.00053079 | 9.3121e-06
2013 | 2012-09-12 | B | 7 | 0.0057797 | 2.1728e-05
2013 | 2012-09-12 | C | 12 | 0.0036131 | 3.7248e-05
2013 | 2012-09-12 | C | 36.1184 | 0.0081842 | 0.00023901
2013 | 2012-09-12 | B | 25 | 0.025375 | 7.7601e-05
2013 | 2012-09-12 | C | 164.3445 | 0.10509 | 0.0011702
2013 | 2012-09-12 | C | 918 | 0.0085485 | 0.0028495
2013 | 2012-09-12 | C | 48.3462 | 0.019059 | 0.00033834
2013 | 2012-09-13 | C | 171 | 0.046709 | 0.00053079
2013 | 2012-09-13 | C | 3 | 0.00094983 | 9.3121e-06
2013 | 2012-09-13 | C | 172 | 0.038974 | 0.00053389
2013 | 2012-09-13 | B | 16 | 0.010777 | 4.9664e-05
2013 | 2012-09-13 | B | 8 | 0.0053886 | 2.4832e-05
2013 | 2012-09-13 | B | 171 | 0.13801 | 0.00053079
2013 | 2012-09-13 | C | 90 | 0.012013 | 0.00027936
2013 | 2012-09-13 | C | 410 | 0.1489 | 0.0012727
2013 | 2012-09-13 | C | 14 | 0.0012168 | 4.3456e-05
2013 | 2012-09-13 | C | 3 | 0.0016482 | 9.3121e-06
2013 | 2012-09-13 | C | 318 | 0.058238 | 0.00098708
2013 | 2012-09-14 | C | 525.6957 | 0.070166 | 0.0021759
2013 | 2012-09-14 | C | 53 | 0.013819 | 0.00016451
2013 | 2012-09-14 | B | 91 | 0.012429 | 0.00028247
2013 | 2012-09-14 | B | 23 | 0.011066 | 7.1393e-05
2013 | 2012-09-14 | C | 624.568 | 0.32182 | 0.003849
2013 | 2012-09-16 | C | 26 | 0.0068599 | 8.0705e-05
2013 | 2012-09-16 | C | 5 | 0.00032592 | 1.552e-05
2013 | 2012-09-16 | B | 12 | 0.0043581 | 3.7248e-05
2013 | 2012-09-16 | C | 107.2619 | 0.068919 | 0.00057735
2013 | 2012-09-16 | C | 482.5385 | 0.11234 | 0.0025422
2013 | 2012-09-17 | C | 237 | 0.033104 | 0.00073565
2013 | 2012-09-16 | C | 58 | 0.0045008 | 0.00018003
2013 | 2012-09-11 | C | 191 | 0.023122 | 0.00059287
2013 | 2012-09-15 | C | 31 | 0.015973 | 9.6225e-05
2013 | 2012-09-16 | C | 123 | 0.0080177 | 0.0003818
2013 | 2012-09-17 | C | 15 | 0.0030264 | 4.656e-05
2013 | 2012-09-17 | B | 226 | 0.22518 | 0.00070151
2013 | 2012-09-17 | C | 82 | 0.014508 | 0.00025453
2013 | 2012-09-17 | C | 226 | 0.02806 | 0.00070151
2013 | 2012-09-17 | C | 68.8665 | 0.068191 | 0.00073876
2013 | 2012-09-17 | C | 5 | 0.014387 | 1.552e-05
2013 | 2012-09-17 | C | 67.3265 | 0.030094 | 0.00040663
2013 | 2012-09-11 | B | 8 | 0.00014899 | 2.4832e-05
2013 | 2012-09-17 | C | 15.2621 | 0.038183 | 0.00023901
2013 | 2012-09-18 | B | 20 | 0.017507 | 6.2081e-05
2013 | 2012-09-18 | B | 87 | 0.091277 | 0.00027005
2013 | 2012-09-18 | C | 5 | 0.0035852 | 1.552e-05
2013 | 2012-09-18 | B | 9 | 0.0082691 | 2.7936e-05
2013 | 2012-09-18 | B | 130 | 0.066178 | 0.00040352
2013 | 2012-09-18 | C | 17 | 0.0024801 | 5.2768e-05
2013 | 2012-09-18 | C | 58 | 0.015483 | 0.00018003
2013 | 2012-09-18 | B | 105.7027 | 0.059715 | 0.00044388
2013 | 2012-09-15 | C | 149.6818 | 0.14171 | 0.00088775
2013 | 2012-09-19 | C | 68 | 0.013298 | 0.00021107
2013 | 2012-09-19 | B | 19 | 0.017516 | 5.8977e-05
2013 | 2012-09-19 | B | 32 | 0.026024 | 9.9329e-05
2013 | 2012-09-19 | B | 54 | 0.051459 | 0.00016762
2013 | 2012-09-19 | B | 146.4196 | 0.19361 | 0.0010616
2013 | 2012-09-20 | B | 59 | 0.069959 | 0.00018314
2013 | 2012-09-20 | B | 64 | 0.073901 | 0.00019866
2013 | 2012-09-20 | B | 12 | 0.016278 | 3.7248e-05
2013 | 2012-09-20 | C | 132 | 0.0758 | 0.00040973
2013 | 2012-09-20 | B | 54 | 0.058163 | 0.00016762
2013 | 2012-09-20 | B | 38 | 0.03633 | 0.00011795
2013 | 2012-09-20 | B | 133 | 0.19775 | 0.00041284
2013 | 2012-09-20 | C | 55.698 | 0.18153 | 0.0015055
2013 | 2012-09-21 | C | 858 | 0.1598 | 0.0026633
2013 | 2012-09-21 | B | 4 | 0.003551 | 1.2416e-05
2013 | 2012-09-21 | B | 56 | 0.059622 | 0.00017383
2013 | 2012-09-21 | C | 30.5582 | 0.031491 | 0.0003818
2013 | 2012-09-21 | C | 90 | 0.013689 | 0.00027936
2013 | 2012-09-21 | B | 2 | 0.0022163 | 6.2081e-06
2013 | 2012-09-21 | C | 161 | 0.042479 | 0.00049975
2013 | 2012-09-22 | B | 1 | 5.5873e-05 | 3.104e-06
2013 | 2012-09-23 | B | 200 | 0.040352 | 0.00062081
2013 | 2012-09-23 | C | 89 | 0.017404 | 0.00027626
2013 | 2012-09-16 | B | 200 | 0.042215 | 0.00062081
2013 | 2012-09-24 | C | 38 | 0.0037745 | 0.00011795
2013 | 2012-09-24 | B | 3 | 0.001043 | 9.3121e-06
2013 | 2012-09-24 | C | 16 | 0.0075987 | 4.9664e-05
2013 | 2012-09-24 | B | 3 | 0.002505 | 9.3121e-06
2013 | 2012-09-24 | C | 5 | 0.0011485 | 1.552e-05
2013 | 2012-09-24 | B | 1 | 0.00022349 | 3.104e-06
2013 | 2012-09-24 | B | 165 | 0.16236 | 0.00051216
2013 | 2012-09-24 | B | 10 | 0.011795 | 3.104e-05
2013 | 2012-09-24 | C | 1393 | 0.0043239 | 0.0043239
2013 | 2012-09-25 | B | 28 | 0.012168 | 8.6913e-05
2013 | 2012-09-25 | B | 11 | 0.0069313 | 3.4144e-05
2013 | 2012-09-25 | C | 6 | 0.0022721 | 1.8624e-05
2013 | 2012-09-25 | B | 9 | 0.010532 | 2.7936e-05
2013 | 2012-09-25 | B | 12 | 0.014452 | 3.7248e-05
2013 | 2012-09-25 | C | 136.083 | 0.095464 | 0.0015427
2013 | 2012-09-25 | C | 186.6222 | 0.02433 | 0.00073876
2013 | 2012-09-25 | B | 117 | 0.082077 | 0.00036317
2013 | 2012-09-25 | C | 1 | 0.00026074 | 3.104e-06
2013 | 2012-09-26 | C | 51 | 0.0017414 | 0.00015831
2013 | 2012-09-26 | B | 55 | 0.032779 | 0.00017072
2013 | 2012-09-26 | C | 315.5471 | 0.16357 | 0.002418
2013 | 2012-09-26 | B | 3 | 0.0007729 | 9.3121e-06
2013 | 2012-09-26 | B | 2 | 0.00044698 | 6.2081e-06
2013 | 2012-09-26 | C | 18 | 0.0027378 | 5.5873e-05
2013 | 2012-09-26 | B | 29 | 0.022954 | 9.0017e-05
2013 | 2012-09-26 | B | 1 | 0.00034765 | 3.104e-06
2013 | 2012-09-26 | B | 87 | 0.10856 | 0.00027005
2013 | 2012-09-27 | C | 27 | 0.0043581 | 8.3809e-05
2013 | 2012-09-27 | C | 1 | 0.00040663 | 3.104e-06
2013 | 2012-09-27 | C | 22 | 0.0058045 | 6.8289e-05
2013 | 2012-09-22 | C | 16 | 0.012168 | 4.9664e-05
2013 | 2012-09-27 | B | 20 | 0.026881 | 6.2081e-05
2013 | 2012-09-27 | B | 115 | 0.13279 | 0.00035696
2013 | 2012-09-27 | C | 15 | 0.004237 | 4.656e-05
2013 | 2012-09-28 | C | 59.0867 | 0.067127 | 0.0026943
2013 | 2012-09-28 | C | 150 | 0.0018624 | 0.0004656
2013 | 2012-09-28 | C | 104.573 | 0.027915 | 0.00071082
2013 | 2012-09-28 | C | 197.6564 | 0.098165 | 0.00099329
2013 | 2012-09-28 | B | 289 | 0.019735 | 0.00089706
2013 | 2012-09-28 | C | 105.4911 | 0.072366 | 0.00051216
2013 | 2012-09-28 | C | 38 | 0.012503 | 0.00011795
2013 | 2012-09-28 | B | 37 | 0.026071 | 0.00011485
2013 | 2012-09-28 | B | 14 | 0.014428 | 4.3456e-05
2013 | 2012-09-27 | B | 1 | 0.0058821 | 3.104e-06
2013 | 2012-09-29 | C | 296.5385 | 0.021171 | 0.0018655
2013 | 2012-09-29 | B | 3 | 0.0012013 | 9.3121e-06
2013 | 2012-09-29 | B | 7 | 0.0048237 | 2.1728e-05
2013 | 2012-09-29 | C | 51 | 0.00047492 | 0.00015831
2013 | 2012-09-29 | C | 113.2208 | 0.026007 | 0.00049664
2013 | 2012-09-29 | C | 272 | 0.010132 | 0.0008443
2013 | 2012-09-30 | B | 139 | 0.075074 | 0.00043146
2013 | 2012-09-30 | B | 143 | 0.047051 | 0.00044388
2013 | 2012-10-01 | C | 37 | 0.020213 | 0.00011485
2013 | 2012-10-01 | B | 93 | 0.041858 | 0.00028867
2013 | 2012-10-01 | C | 208 | 0.0038738 | 0.00064564
2013 | 2012-10-01 | B | 49 | 0.04061 | 0.0001521
2013 | 2012-10-01 | C | 698 | 0.0195 | 0.0021666
2013 | 2012-10-01 | C | 1364 | 0.050807 | 0.0042339
2013 | 2012-10-01 | C | 58 | 0.013503 | 0.00018003
2013 | 2012-10-01 | C | 322.5891 | 0.12617 | 0.0017631
2013 | 2012-10-02 | C | 53.1739 | 0.0070973 | 0.00017693
2013 | 2012-10-02 | C | 2 | 0.00097466 | 6.2081e-06
2013 | 2012-10-02 | C | 65.6667 | 0.015899 | 0.00023901
2013 | 2012-10-02 | B | 39 | 0.045396 | 0.00012106
2013 | 2012-10-02 | B | 22 | 0.022194 | 6.8289e-05
2013 | 2012-10-02 | B | 5 | 0.0063477 | 1.552e-05
2013 | 2012-10-02 | B | 240 | 0.12813 | 0.00074497
2013 | 2012-10-02 | C | 640 | 0.047678 | 0.0019866
2013 | 2012-10-02 | B | 76 | 0.076905 | 0.00023591
2013 | 2012-10-02 | B | 247.4764 | 0.20894 | 0.001133
2013 | 2012-10-02 | B | 61 | 0.076496 | 0.00018935
2013 | 2012-10-02 | C | 374 | 0.015092 | 0.0011609
2013 | 2012-10-01 | C | 1 | 0.0003849 | 3.104e-06
2013 | 2012-10-03 | B | 9 | 0.0050844 | 2.7936e-05
2013 | 2012-10-03 | C | 905 | 0.03371 | 0.0028091
2013 | 2012-10-03 | B | 108 | 0.057996 | 0.00033524
2013 | 2012-10-03 | B | 119 | 0.091237 | 0.00036938
2013 | 2012-10-03 | B | 135 | 0.075009 | 0.00041904
2013 | 2012-10-03 | C | 4 | 0.00052148 | 1.2416e-05
2013 | 2012-10-03 | C | 14 | 0.0011733 | 4.3456e-05
2013 | 2012-10-02 | C | 4 | 0.0049292 | 1.2416e-05
2013 | 2012-10-03 | C | 1 | 0.00013968 | 3.104e-06
2013 | 2012-10-03 | C | 4 | 0.00062081 | 1.2416e-05
2013 | 2012-10-03 | B | 76 | 0.0094362 | 0.00023591
2013 | 2012-10-03 | C | 82.0161 | 0.078156 | 0.0017103
2013 | 2012-10-03 | C | 33 | 0.0041998 | 0.00010243
2013 | 2012-10-03 | C | 12 | 0.00078222 | 3.7248e-05
2013 | 2012-10-04 | C | 561 | 0.053982 | 0.0017414
2013 | 2012-10-04 | B | 21 | 0.0088651 | 6.5185e-05
2013 | 2012-10-04 | C | 2 | 0.00066426 | 6.2081e-06
2013 | 2012-10-04 | B | 292 | 0.19668 | 0.00090638
2013 | 2012-10-04 | C | 17 | 0.0034827 | 5.2768e-05
2013 | 2012-10-04 | B | 119 | 0.079786 | 0.00036938
2013 | 2012-10-04 | C | 5 | 0.0039887 | 1.552e-05
2013 | 2012-10-04 | B | 76 | 0.054023 | 0.00023591
2013 | 2012-10-04 | B | 1 | 0.0002328 | 3.104e-06
2013 | 2012-10-04 | B | 20 | 0.02328 | 6.2081e-05
2013 | 2012-10-04 | C | 4 | 0.0017383 | 1.2416e-05
2013 | 2012-10-04 | C | 31.4103 | 0.0073124 | 0.00013968
2013 | 2012-10-04 | B | 5 | 0.0074497 | 1.552e-05
2013 | 2012-10-04 | B | 132 | 0.01475 | 0.00040973
2013 | 2012-10-04 | C | 3 | 0.0018252 | 9.3121e-06
2013 | 2012-10-05 | C | 64 | 0.010926 | 0.00019866
2013 | 2012-10-05 | B | 12 | 0.013298 | 3.7248e-05
2013 | 2012-10-05 | B | 54 | 0.084144 | 0.00016762
2013 | 2012-10-05 | C | 54 | 0.0058666 | 0.00016762
2013 | 2012-10-05 | C | 3 | 0.00078222 | 9.3121e-06
2013 | 2012-10-05 | C | 110 | 0.022194 | 0.00034144
2013 | 2012-10-05 | C | 12.7276 | 0.047606 | 0.00021418
2013 | 2012-10-06 | C | 76 | 0.05072 | 0.00023591
2013 | 2012-10-06 | C | 33 | 0.0069654 | 0.00010243
2013 | 2012-10-06 | C | 15 | 0.0032127 | 4.656e-05
2013 | 2012-10-06 | C | 779.0645 | 0.14268 | 0.0033648
2013 | 2012-10-07 | C | 483.7059 | 0.22522 | 0.0021325
2013 | 2012-10-06 | C | 4 | 0.0096722 | 1.2416e-05
2013 | 2012-10-07 | C | 2 | 0.00032282 | 6.2081e-06
2013 | 2012-10-06 | C | 10 | 0.0019245 | 3.104e-05
2013 | 2012-10-06 | C | 195.9939 | 0.098556 | 0.0018221
2013 | 2012-10-06 | C | 1 | 0.002505 | 3.104e-06
2013 | 2012-10-07 | C | 1 | 0.00021107 | 3.104e-06
2013 | 2012-10-06 | C | 14 | 0.0042153 | 4.3456e-05
2013 | 2012-10-06 | C | 905 | 0.03371 | 0.0033865
2013 | 2012-10-06 | C | 613.9524 | 0.034303 | 0.0022132
2013 | 2012-10-06 | C | 17 | 0.0040632 | 5.2768e-05
2013 | 2012-10-06 | C | 5 | 0.00032592 | 1.552e-05
2013 | 2012-10-05 | C | 8 | 0.023367 | 2.4832e-05
2013 | 2012-10-06 | C | 3.0423 | 0.00064214 | 1.2416e-05
2013 | 2012-10-05 | C | 27 | 0.010225 | 8.3809e-05
2013 | 2012-10-05 | C | 5 | 0.0098398 | 1.552e-05
2013 | 2012-10-05 | C | 3 | 0.00018624 | 9.3121e-06
2013 | 2012-10-05 | C | 34 | 0.0049602 | 0.00010554
2013 | 2012-10-05 | B | 20 | 0.015334 | 6.2081e-05
2013 | 2012-10-06 | C | 22.4881 | 0.085161 | 0.00073876
2013 | 2012-10-07 | C | 137 | 0.040399 | 0.00042525
2013 | 2012-10-06 | C | 25.9705 | 0.087143 | 0.00050596
2013 | 2012-10-07 | C | 91.4886 | 0.06134 | 0.0003073
2013 | 2012-10-07 | C | 3 | 0.001462 | 9.3121e-06
2013 | 2012-10-06 | C | 74.4656 | 0.059866 | 0.00033213
2013 | 2012-10-08 | B | 3 | 0.0023932 | 9.3121e-06
2013 | 2012-10-08 | B | 10 | 0.0027626 | 3.104e-05
2013 | 2012-10-08 | C | 8 | 0.0051403 | 2.4832e-05
2013 | 2012-10-08 | C | 169.9459 | 0.07649 | 0.00063322
2013 | 2012-10-08 | C | 84.8024 | 0.04317 | 0.00042215
2013 | 2012-10-07 | C | 20 | 0.0027936 | 6.2081e-05
2013 | 2012-10-08 | C | 66.9545 | 0.008521 | 0.00027005
2013 | 2012-10-08 | C | 143 | 0.02752 | 0.00044388
2013 | 2012-10-08 | C | 421 | 0.015682 | 0.0013068
2013 | 2012-10-08 | C | 44.1795 | 0.047723 | 0.00090017
2013 | 2012-10-09 | C | 462.2258 | 0.12913 | 0.0025422
2013 | 2012-10-08 | C | 2 | 0.00035386 | 6.2081e-06
2013 | 2012-10-09 | C | 6 | 0.00085671 | 1.8624e-05
2013 | 2012-10-09 | B | 29 | 0.016383 | 9.0017e-05
2013 | 2012-10-09 | C | 133 | 0.015275 | 0.00041284
2013 | 2012-10-09 | B | 36 | 0.025366 | 0.00011175
2013 | 2012-10-09 | B | 3 | 0.0031847 | 9.3121e-06
2013 | 2012-10-09 | B | 276 | 0.18933 | 0.00085671
2013 | 2012-10-08 | C | 1 | 0.0041718 | 3.104e-06
2013 | 2012-10-09 | B | 5 | 0.0052148 | 1.552e-05
2013 | 2012-10-09 | C | 59 | 0.021061 | 0.00018314
2013 | 2012-10-09 | B | 261 | 0.28274 | 0.00081015
2013 | 2012-10-09 | C | 177.1597 | 0.12923 | 0.0020611
2013 | 2012-10-10 | B | 74 | 0.021132 | 0.0002297
2013 | 2012-10-10 | B | 63 | 0.02288 | 0.00019555
2013 | 2012-10-09 | B | 2 | 0.00063322 | 6.2081e-06
2013 | 2012-10-09 | B | 1 | 0.00027005 | 3.104e-06
2013 | 2012-10-10 | C | 11 | 0.0033461 | 3.4144e-05
2013 | 2012-10-10 | C | 7 | 0.0010864 | 2.1728e-05
2013 | 2012-10-10 | B | 12 | 0.011584 | 3.7248e-05
2013 | 2012-10-10 | B | 3 | 0.0029426 | 9.3121e-06
2013 | 2012-10-10 | B | 3 | 0.0016948 | 9.3121e-06
2013 | 2012-10-10 | C | 1 | 0.00012106 | 3.104e-06
2013 | 2012-10-09 | B | 2 | 0.00035386 | 6.2081e-06
2013 | 2012-10-08 | B | 30 | 0.016669 | 9.3121e-05
2013 | 2012-10-11 | C | 34 | 0.0047492 | 0.00010554
2013 | 2012-10-11 | B | 116 | 0.068773 | 0.00036007
2013 | 2012-10-11 | B | 171 | 0.11571 | 0.00053079
2013 | 2012-10-11 | C | 54.049 | 0.016609 | 0.00042215
2013 | 2012-10-11 | B | 3 | 0.0022349 | 9.3121e-06
2013 | 2012-10-11 | B | 36 | 0.036652 | 0.00011175
2013 | 2012-10-11 | B | 2 | 0.0013534 | 6.2081e-06
2013 | 2012-10-10 | B | 121 | 0.020657 | 0.00037559
2013 | 2012-10-11 | B | 184 | 0.24216 | 0.00057114
2013 | 2012-10-11 | C | 4 | 0.0043456 | 1.2416e-05
2013 | 2012-10-12 | B | 16 | 0.010529 | 4.9664e-05
2013 | 2012-10-12 | B | 6 | 0.0013409 | 1.8624e-05
2013 | 2012-10-12 | C | 11 | 0.0036534 | 3.4144e-05
2013 | 2012-10-12 | B | 2 | 0.0022163 | 6.2081e-06
2013 | 2012-10-13 | C | 264.094 | 0.093452 | 0.0011454
2013 | 2012-10-13 | C | 693.5238 | 0.12916 | 0.0028216
2013 | 2012-10-13 | C | 159.7538 | 0.062977 | 0.00049664
2013 | 2012-10-13 | C | 142.6087 | 0.069941 | 0.00095604
2013 | 2012-10-13 | C | 5 | 0.0010709 | 1.552e-05
2013 | 2012-10-13 | C | 411 | 0.049754 | 0.0012758
2013 | 2012-10-13 | B | 16 | 0.006804 | 4.9664e-05
2013 | 2012-10-13 | C | 3 | 0.0017041 | 9.3121e-06
2013 | 2012-10-13 | B | 1 | 0.0009281 | 3.104e-06
2013 | 2012-10-13 | C | 297.4 | 0.27417 | 0.00094673
2013 | 2012-10-13 | C | 170.9857 | 0.072712 | 0.00095294
2013 | 2012-10-13 | C | 276 | 0.013707 | 0.00085671
2013 | 2012-10-13 | C | 2913 | 0.11755 | 0.009042
2013 | 2012-10-13 | C | 819 | 0.19575 | 0.0025422
2013 | 2012-10-13 | C | 366 | 0.16928 | 0.0011361
2013 | 2012-10-13 | C | 123.3235 | 0.050912 | 0.00083498
2013 | 2012-10-13 | C | 133.8926 | 0.049042 | 0.00057114
2013 | 2012-10-13 | C | 127.4624 | 0.06726 | 0.00070461
2013 | 2012-10-13 | C | 4 | 0.0035634 | 1.2416e-05
2013 | 2012-10-13 | C | 95.3427 | 0.094111 | 0.00067047
2013 | 2012-10-13 | C | 155.5438 | 0.13084 | 0.00078532
2013 | 2012-10-13 | C | 188 | 0.019841 | 0.00058356
2013 | 2012-10-13 | C | 68 | 0.0071765 | 0.00021107
2013 | 2012-10-13 | C | 91.75 | 0.021929 | 0.00030109
2013 | 2012-10-13 | C | 60.5365 | 0.074035 | 0.00047181
2013 | 2012-10-13 | C | 19 | 0.015275 | 5.8977e-05
2013 | 2012-10-13 | C | 122 | 0.0071951 | 0.00037869
2013 | 2012-10-13 | C | 5 | 0.00034144 | 1.552e-05
2013 | 2012-10-13 | C | 20 | 0.012168 | 6.2081e-05
2013 | 2012-10-13 | C | 7 | 0.0016513 | 2.1728e-05
2013 | 2012-10-13 | C | 539.3852 | 0.81202 | 0.0018872
2013 | 2012-10-13 | C | 104.9085 | 0.052428 | 0.00052148
2013 | 2012-10-13 | C | 691.4571 | 0.29404 | 0.0041221
2013 | 2012-10-13 | C | 228 | 0.00070772 | 0.00070772
2013 | 2012-10-13 | C | 131.0492 | 0.14766 | 0.00052768
2013 | 2012-10-13 | C | 361.4744 | 0.23787 | 0.0031692
2013 | 2012-10-13 | C | 225.9249 | 0.24054 | 0.0016669
2013 | 2012-10-13 | C | 805.9418 | 0.98065 | 0.0027781
2013 | 2012-10-13 | C | 89 | 0.26466 | 0.00027626
2013 | 2012-10-14 | C | 334 | 0.017625 | 0.0010367
2013 | 2012-10-14 | C | 71.0352 | 0.030649 | 0.00068909
2013 | 2012-10-13 | C | 128 | 0.049664 | 0.00039732
2013 | 2012-10-13 | C | 2742.5448 | 2.2559 | 0.0097839
2013 | 2012-10-13 | C | 42 | 0.019034 | 0.00013037
2013 | 2012-10-14 | C | 13 | 0.0023001 | 4.0352e-05
2013 | 2012-10-13 | C | 234.375 | 0.032738 | 0.00073255
2013 | 2012-10-14 | C | 4 | 0.00070772 | 1.2416e-05
2013 | 2012-10-13 | C | 90.8693 | 0.31647 | 0.00063943
2013 | 2012-10-14 | C | 8 | 0.0038987 | 2.4832e-05
2013 | 2012-10-15 | C | 21 | 0.003194 | 6.5185e-05
2013 | 2012-10-15 | C | 161.4648 | 0.069666 | 0.0012323
2013 | 2012-10-15 | C | 80 | 0.0037248 | 0.00024832
2013 | 2012-10-15 | C | 613.5279 | 0.36946 | 0.0029023
2013 | 2012-10-15 | C | 883 | 0.087707 | 0.0027409
2013 | 2012-10-15 | C | 253 | 0.037695 | 0.00078532
2013 | 2012-10-15 | C | 48 | 0.0092376 | 0.00014899
2013 | 2012-10-16 | B | 10 | 0.0047802 | 3.104e-05
2013 | 2012-10-16 | C | 30 | 0.0045629 | 9.3121e-05
2013 | 2012-10-16 | B | 3 | 0.0016203 | 9.3121e-06
2013 | 2012-10-16 | B | 78 | 0.024696 | 0.00024211
2013 | 2012-10-16 | B | 26 | 0.022759 | 8.0705e-05
2013 | 2012-10-16 | B | 17 | 0.010923 | 5.2768e-05
2013 | 2012-10-16 | C | 4 | 0.0013906 | 1.2416e-05
2013 | 2012-10-16 | B | 24 | 0.029948 | 7.4497e-05
2013 | 2012-10-16 | B | 38 | 0.041519 | 0.00011795
2013 | 2012-10-16 | B | 1 | 0.0010616 | 3.104e-06
2013 | 2012-10-16 | B | 31 | 0.031658 | 9.6225e-05
2013 | 2012-10-16 | B | 119 | 0.13187 | 0.00036938
2013 | 2012-10-16 | C | 48.8448 | 0.03472 | 0.00056183
2013 | 2012-10-16 | B | 23 | 0.025487 | 7.1393e-05
2013 | 2012-10-16 | C | 57 | 0.00053079 | 0.00017693
2013 | 2012-10-16 | C | 2 | 0.00010554 | 6.2081e-06
2013 | 2012-10-16 | C | 3 | 0.00053079 | 9.3121e-06
2013 | 2012-10-07 | B | 636 | 0.22505 | 0.0019742
2013 | 2012-10-17 | B | 8 | 0.0014154 | 2.4832e-05
2013 | 2012-10-17 | B | 9 | 0.0024305 | 2.7936e-05
2013 | 2012-10-17 | B | 57 | 0.0097311 | 0.00017693
2013 | 2012-10-17 | C | 515 | 0.10551 | 0.0015986
2013 | 2012-10-17 | B | 5 | 0.0049354 | 1.552e-05
2013 | 2012-10-17 | C | 820 | 0.19853 | 0.0025453
2013 | 2012-10-17 | B | 47 | 0.049456 | 0.00014589
2013 | 2012-10-17 | C | 50 | 0.040818 | 0.0001552
2013 | 2012-10-17 | C | 79 | 0.0046591 | 0.00024522
2013 | 2012-10-17 | C | 24 | 0.0042463 | 7.4497e-05
2013 | 2012-10-18 | C | 110 | 0.0040973 | 0.00034144
2013 | 2012-10-18 | C | 39 | 0.0049633 | 0.00012106
2013 | 2012-10-18 | C | 153.6429 | 0.065337 | 0.0012292
2013 | 2012-10-18 | C | 70.1758 | 0.019169 | 0.00039111
2013 | 2012-10-18 | B | 63 | 0.014862 | 0.00019555
2013 | 2012-10-17 | C | 55 | 0.043705 | 0.00017072
2013 | 2012-10-18 | C | 7 | 0.00043456 | 2.1728e-05
2013 | 2012-10-17 | C | 456 | 0.47983 | 0.0014154
2013 | 2012-10-18 | C | 22.8605 | 0.0028384 | 0.00031351
2013 | 2012-10-18 | C | 108 | 0.0040228 | 0.00033524
2013 | 2012-10-18 | C | 122 | 0.10073 | 0.00037869
2013 | 2012-10-18 | C | 11 | 0.0016389 | 3.4144e-05
2013 | 2012-10-18 | C | 13 | 0.0018966 | 4.0352e-05
2013 | 2012-10-18 | C | 188 | 0.0070027 | 0.00058356
2013 | 2012-10-18 | C | 27 | 0.0031847 | 8.3809e-05
2013 | 2012-10-18 | C | 125 | 0.004656 | 0.000388
2013 | 2012-10-18 | C | 27 | 0.0057828 | 8.3809e-05
2013 | 2012-10-17 | C | 4 | 0.011572 | 1.2416e-05
2013 | 2012-10-18 | C | 343 | 0.012776 | 0.0010647
2013 | 2012-10-18 | C | 110 | 0.0040973 | 0.00034144
2013 | 2012-10-18 | C | 266 | 0.042109 | 0.00082567
2013 | 2012-10-17 | C | 1 | 0.0028836 | 3.104e-06
2013 | 2012-10-18 | C | 272 | 0.010132 | 0.0008443
2013 | 2012-10-18 | C | 157 | 0.052632 | 0.00048733
2013 | 2012-10-18 | C | 1 | 0.00017693 | 3.104e-06
2013 | 2012-10-18 | C | 107.428 | 0.17273 | 0.00036007
2013 | 2012-10-18 | C | 97 | 0.034324 | 0.00030109
2013 | 2012-10-18 | C | 2 | 0.00057114 | 6.2081e-06
2013 | 2012-10-18 | C | 86.7975 | 0.043108 | 0.0004656
2013 | 2012-10-18 | C | 25 | 0.0056649 | 7.7601e-05
2013 | 2012-10-18 | C | 115.1705 | 0.091161 | 0.0007729
2013 | 2012-10-18 | C | 617.0208 | 0.086186 | 0.0022939
2013 | 2012-10-18 | C | 77 | 0.058079 | 0.00023901
2013 | 2012-10-19 | C | 2 | 0.00011795 | 6.2081e-06
2013 | 2012-10-18 | C | 98.3407 | 0.05464 | 0.00074186
2013 | 2012-10-18 | C | 751.1452 | 0.13756 | 0.0023435
2013 | 2012-10-18 | C | 156.8884 | 0.10324 | 0.00081946
2013 | 2012-10-19 | C | 35 | 0.0035852 | 0.00010864
2013 | 2012-10-18 | C | 120.3824 | 0.024289 | 0.0008505
2013 | 2012-10-19 | C | 13 | 0.0026633 | 4.0352e-05
2013 | 2012-10-18 | C | 28.9052 | 0.10767 | 0.00045008
2013 | 2012-10-18 | C | 115 | 0.40765 | 0.00035696
2013 | 2012-10-19 | C | 70 | 0.0080394 | 0.00021728
2013 | 2012-10-19 | C | 359.5874 | 0.15626 | 0.0025639
2013 | 2012-10-18 | B | 16 | 0.0013906 | 4.9664e-05
2013 | 2012-10-18 | B | 5 | 0.0021107 | 1.552e-05
2013 | 2012-10-18 | B | 33 | 0.029706 | 0.00010243
2013 | 2012-10-19 | B | 4 | 0.0029426 | 1.2416e-05
2013 | 2012-10-19 | B | 5 | 0.0045164 | 1.552e-05
2013 | 2012-10-19 | B | 52 | 0.053265 | 0.00016141
2013 | 2012-10-19 | C | 95 | 0.029488 | 0.00029488
2013 | 2012-10-19 | C | 170 | 0.011609 | 0.00052768
2013 | 2012-10-19 | C | 58 | 0.0073814 | 0.00018003
2013 | 2012-10-19 | B | 23 | 0.01335 | 7.1393e-05
2013 | 2012-10-19 | C | 12 | 0.0042463 | 3.7248e-05
2013 | 2012-10-19 | C | 42.8706 | 0.037659 | 0.00027626
2013 | 2012-10-19 | C | 89 | 0.016299 | 0.00027626
2013 | 2012-10-19 | C | 131.7312 | 0.26497 | 0.0016048
2013 | 2012-10-19 | C | 51 | 0.010606 | 0.00015831
2013 | 2012-10-19 | C | 1220.8235 | 0.053053 | 0.004147
2013 | 2012-10-19 | C | 18 | 0.0060901 | 5.5873e-05
2013 | 2012-10-19 | C | 32 | 0.006953 | 9.9329e-05
2013 | 2012-10-19 | C | 352.4384 | 0.076579 | 0.0012664
2013 | 2012-10-19 | C | 143 | 0.026189 | 0.00044388
2013 | 2012-10-19 | C | 7 | 0.0050192 | 2.1728e-05
2013 | 2012-10-19 | C | 83.5517 | 0.05939 | 0.00027626
2013 | 2012-10-20 | C | 37 | 0.017687 | 0.00011485
2013 | 2012-10-20 | B | 69 | 0.065753 | 0.00021418
2013 | 2012-10-18 | C | 1447 | 0.067373 | 0.0044915
2013 | 2012-10-18 | C | 684.3943 | 0.88799 | 0.0034827
2013 | 2012-10-20 | C | 21.7463 | 0.013365 | 0.00017383
2013 | 2012-10-20 | C | 9 | 0.0018438 | 2.7936e-05
2013 | 2012-10-21 | C | 26 | 0.030264 | 8.0705e-05
2013 | 2012-10-21 | C | 35 | 0.034765 | 0.00010864
2013 | 2012-10-21 | C | 3 | 0.001015 | 9.3121e-06
2013 | 2012-10-21 | C | 2427.4286 | 0.18837 | 0.008654
2013 | 2012-10-21 | C | 174 | 0.0048609 | 0.0005401
2013 | 2012-10-21 | C | 561 | 0.015672 | 0.0017414
2013 | 2012-10-21 | C | 97 | 0.013248 | 0.00030109
2013 | 2012-10-20 | C | 337.5663 | 0.083825 | 0.0011237
2013 | 2012-10-22 | C | 83.1715 | 0.060927 | 0.00054631
2013 | 2012-10-22 | C | 54 | 0.04643 | 0.00016762
2013 | 2012-10-22 | C | 478.0862 | 0.25376 | 0.0023125
2013 | 2012-10-22 | C | 30 | 0.0025143 | 9.3121e-05
2013 | 2012-10-21 | C | 120 | 0.034641 | 0.00037248
2013 | 2012-10-22 | C | 76 | 0.041755 | 0.00023591
2013 | 2012-10-22 | C | 48 | 0.014452 | 0.00014899
2013 | 2012-10-23 | B | 58 | 0.066973 | 0.00018003
2013 | 2012-10-17 | B | 38 | 0.042463 | 0.00011795
2013 | 2012-10-23 | C | 38 | 0.0029488 | 0.00011795
2013 | 2012-10-23 | C | 3 | 0.0010802 | 9.3121e-06
2013 | 2012-10-23 | B | 23 | 0.026558 | 7.1393e-05
2013 | 2012-10-24 | C | 270 | 0.046933 | 0.00083809
2013 | 2012-10-23 | C | 41 | 0.030798 | 0.00012727
2013 | 2012-10-24 | B | 36 | 0.0067047 | 0.00011175
2013 | 2012-10-24 | B | 77 | 0.071464 | 0.00023901
2013 | 2012-10-24 | B | 20 | 0.017817 | 6.2081e-05
2013 | 2012-10-24 | B | 2 | 0.0021852 | 6.2081e-06
2013 | 2012-10-24 | B | 89 | 0.058291 | 0.00027626
2013 | 2012-10-24 | B | 1 | 0.00054941 | 3.104e-06
2013 | 2012-10-24 | B | 8 | 0.0055128 | 2.4832e-05
2013 | 2012-10-24 | B | 2 | 0.0018003 | 6.2081e-06
2013 | 2012-10-24 | B | 17 | 0.02364 | 5.2768e-05
2013 | 2012-10-24 | B | 33 | 0.043227 | 0.00010243
2013 | 2012-10-18 | B | 10 | 0.0096535 | 3.104e-05
2013 | 2012-10-18 | C | 2 | 0.00039732 | 6.2081e-06
2013 | 2012-10-25 | B | 7 | 0.0014341 | 2.1728e-05
2013 | 2012-10-25 | B | 20 | 0.017507 | 6.2081e-05
2013 | 2012-10-25 | B | 87 | 0.022954 | 0.00027005
2013 | 2012-10-25 | B | 54 | 0.047939 | 0.00016762
2013 | 2012-10-25 | B | 70 | 0.015644 | 0.00021728
2013 | 2012-10-25 | C | 561.7405 | 0.22319 | 0.002269
2013 | 2012-10-25 | B | 83 | 0.1046 | 0.00025763
2013 | 2012-10-25 | B | 2 | 0.00063322 | 6.2081e-06
2013 | 2012-10-25 | C | 1 | 0.00020797 | 3.104e-06
2013 | 2012-10-25 | B | 4 | 0.0010802 | 1.2416e-05
2013 | 2012-10-25 | C | 191.9437 | 0.082816 | 0.00093121
2013 | 2012-10-25 | B | 23 | 0.020847 | 7.1393e-05
2013 | 2012-10-25 | B | 14 | 0.0052582 | 4.3456e-05
2013 | 2012-10-25 | C | 8 | 0.001043 | 2.4832e-05
2013 | 2012-10-25 | C | 36.8955 | 0.022676 | 0.00028247
2013 | 2012-10-25 | C | 389.1245 | 0.31646 | 0.0029457
2013 | 2012-10-25 | C | 206 | 0.071616 | 0.00063943
2013 | 2012-10-26 | B | 1 | 0.00057425 | 3.104e-06
2013 | 2012-10-26 | B | 2 | 0.0010988 | 6.2081e-06
2013 | 2012-10-26 | B | 2 | 0.0012292 | 6.2081e-06
2013 | 2012-10-26 | B | 20 | 0.018252 | 6.2081e-05
2013 | 2012-10-26 | C | 126 | 0.0058666 | 0.00039111
2013 | 2012-10-26 | B | 3 | 0.0027378 | 9.3121e-06
2013 | 2012-10-27 | C | 1127.8901 | 0.30809 | 0.0042929
2013 | 2012-10-27 | B | 1 | 0.00070461 | 3.104e-06
2013 | 2012-10-26 | B | 23 | 0.01692 | 7.1393e-05
2013 | 2012-10-26 | C | 48 | 0.0022349 | 0.00014899
2013 | 2012-10-28 | C | 80.1892 | 0.045302 | 0.00041904
2013 | 2012-10-26 | C | 63 | 0.0031289 | 0.00019555
2013 | 2012-10-28 | C | 2 | 0.00072634 | 6.2081e-06
2013 | 2012-10-27 | C | 76.6788 | 0.20231 | 0.0003073
2013 | 2012-10-28 | C | 294.3158 | 0.06669 | 0.0025018
2013 | 2012-10-29 | C | 2 | 0.00019866 | 6.2081e-06
2013 | 2012-10-29 | C | 203.0156 | 0.078771 | 0.00078842
2013 | 2012-10-29 | B | 16 | 0.01475 | 4.9664e-05
2013 | 2012-10-29 | C | 110 | 0.029364 | 0.00034144
2013 | 2012-10-29 | B | 23 | 0.021204 | 7.1393e-05
2013 | 2012-10-29 | C | 143 | 0.020862 | 0.00044388
2013 | 2012-10-29 | B | 79 | 0.10912 | 0.00024522
2013 | 2012-10-30 | C | 2752.5833 | 0.69207 | 0.0092252
2013 | 2012-10-30 | B | 4 | 0.00023591 | 1.2416e-05
2013 | 2012-10-30 | B | 9 | 0.0084367 | 2.7936e-05
2013 | 2012-10-30 | B | 73 | 0.088825 | 0.00022659
2013 | 2012-10-30 | C | 51.3059 | 0.026596 | 0.00061149
2013 | 2012-10-30 | B | 12 | 0.015495 | 3.7248e-05
2013 | 2012-10-30 | B | 137 | 0.17861 | 0.00042525
2013 | 2012-10-30 | B | 9 | 0.0097498 | 2.7936e-05
2013 | 2012-10-30 | B | 54 | 0.059504 | 0.00016762
2013 | 2012-10-30 | B | 16 | 0.015048 | 4.9664e-05
2013 | 2012-10-30 | B | 110 | 0.10312 | 0.00034144
2013 | 2012-10-30 | B | 109 | 0.083231 | 0.00033834
2013 | 2012-10-30 | B | 172 | 0.25467 | 0.00053389
2013 | 2012-10-31 | B | 24 | 0.021381 | 7.4497e-05
2013 | 2012-10-31 | C | 45 | 0.0064253 | 0.00013968
2013 | 2012-10-31 | B | 64 | 0.071318 | 0.00019866
2013 | 2012-10-31 | B | 8 | 0.0069282 | 2.4832e-05
2013 | 2012-10-31 | B | 41 | 0.032071 | 0.00012727
2013 | 2012-11-01 | B | 54 | 0.065706 | 0.00016762
2013 | 2012-11-01 | B | 29 | 0.035287 | 9.0017e-05
2013 | 2012-11-01 | B | 19 | 0.018401 | 5.8977e-05
2013 | 2012-11-01 | B | 12 | 0.013111 | 3.7248e-05
2013 | 2012-11-01 | B | 9 | 0.010923 | 2.7936e-05
2013 | 2012-11-01 | B | 12 | 0.014415 | 3.7248e-05
2013 | 2012-11-01 | B | 20 | 0.010926 | 6.2081e-05
2013 | 2012-11-01 | C | 4 | 0.0026322 | 1.2416e-05
2013 | 2012-11-01 | C | 21 | 0.0053451 | 6.5185e-05
2013 | 2012-11-01 | C | 21 | 0.0056711 | 6.5185e-05
2013 | 2012-11-01 | C | 8 | 0.002955 | 2.4832e-05
2013 | 2012-11-02 | C | 73 | 0.0038521 | 0.00022659
2013 | 2012-11-02 | B | 1 | 0.00095294 | 3.104e-06
2013 | 2012-11-02 | B | 38 | 0.044586 | 0.00011795
2013 | 2012-11-02 | C | 35 | 0.0061925 | 0.00010864
2013 | 2012-11-03 | B | 16.3545 | 0.015026 | 0.00011175
2013 | 2012-11-03 | C | 29 | 0.011882 | 9.0017e-05
2013 | 2012-11-03 | C | 301.4275 | 0.11976 | 0.001462
2013 | 2012-11-03 | C | 450.1638 | 0.39684 | 0.002418
2013 | 2012-11-03 | C | 49.4444 | 0.025784 | 0.00025763
2013 | 2012-11-03 | C | 345 | 0.010709 | 0.0010709
2013 | 2012-11-04 | C | 89.3298 | 0.025233 | 0.00058356
2013 | 2012-11-04 | C | 97 | 0.0084305 | 0.00030109
2013 | 2012-11-03 | C | 2 | 0.00052148 | 6.2081e-06
2013 | 2012-11-03 | C | 53 | 0.01678 | 0.00016451
2013 | 2012-11-03 | B | 73 | 0.050077 | 0.00022659
2013 | 2012-11-03 | C | 198.2868 | 0.077551 | 0.00073565
2013 | 2012-11-05 | B | 57 | 0.042286 | 0.00017693
2013 | 2012-11-05 | B | 15 | 0.019276 | 4.656e-05
2013 | 2012-11-05 | B | 23 | 0.028914 | 7.1393e-05
2013 | 2012-11-05 | C | 171 | 0.023355 | 0.00053079
2013 | 2012-11-04 | C | 1 | 0.0053358 | 3.104e-06
2013 | 2012-11-06 | C | 101 | 0.012227 | 0.00031351
2013 | 2012-11-06 | C | 43 | 0.0020021 | 0.00013347
2013 | 2012-11-06 | B | 4 | 0.0028557 | 1.2416e-05
2013 | 2012-11-06 | B | 38 | 0.0077849 | 0.00011795
2013 | 2012-11-06 | B | 59 | 0.061717 | 0.00018314
2013 | 2012-11-06 | B | 35 | 0.035852 | 0.00010864
2013 | 2012-11-06 | B | 24 | 0.025105 | 7.4497e-05
2013 | 2012-11-06 | B | 4 | 0.0018252 | 1.2416e-05
2013 | 2012-11-06 | C | 86.5152 | 0.034642 | 0.00043767
2013 | 2012-11-07 | B | 135 | 0.01299 | 0.00041904
2013 | 2012-11-07 | C | 62 | 0.0061584 | 0.00019245
2013 | 2012-11-07 | C | 132.0804 | 0.090606 | 0.00051527
2013 | 2012-11-07 | B | 75 | 0.014434 | 0.0002328
2013 | 2012-11-06 | C | 804.9259 | 0.059964 | 0.0025453
2013 | 2012-11-07 | B | 14 | 0.010386 | 4.3456e-05
2013 | 2012-11-07 | C | 41 | 0.01629 | 0.00012727
2013 | 2012-11-07 | B | 99 | 0.11493 | 0.0003073
2013 | 2012-11-07 | B | 23 | 0.024059 | 7.1393e-05
2013 | 2012-11-07 | B | 100 | 0.099329 | 0.0003104
2013 | 2012-11-07 | B | 39 | 0.044065 | 0.00012106
2013 | 2012-11-07 | B | 5 | 0.0018159 | 1.552e-05
2013 | 2012-11-07 | B | 44.4113 | 0.050868 | 0.00016451
2013 | 2012-11-08 | C | 4 | 0.00040973 | 1.2416e-05
2013 | 2012-11-08 | C | 61.3179 | 0.073659 | 0.0006146
2013 | 2012-11-08 | C | 1 | 0.00030419 | 3.104e-06
2013 | 2012-11-08 | B | 1 | 0.0011547 | 3.104e-06
2013 | 2012-11-08 | B | 19 | 0.02017 | 5.8977e-05
2013 | 2012-11-08 | B | 234 | 0.26657 | 0.00072634
2013 | 2012-11-08 | B | 15 | 0.016203 | 4.656e-05
2013 | 2012-11-08 | B | 45 | 0.048469 | 0.00013968
2013 | 2012-11-08 | B | 100 | 0.13006 | 0.0003104
2013 | 2012-11-08 | B | 39 | 0.05036 | 0.00012106
2013 | 2012-11-08 | B | 23 | 0.0019276 | 7.1393e-05
2013 | 2012-11-05 | B | 20 | 0.024584 | 6.2081e-05
2013 | 2012-11-07 | B | 6 | 0.0019928 | 1.8624e-05
2013 | 2012-11-02 | B | 7 | 0.0038242 | 2.1728e-05
2013 | 2012-11-09 | B | 1 | 0.00052768 | 3.104e-06
2013 | 2012-11-09 | B | 91 | 0.074006 | 0.00028247
2013 | 2012-11-09 | B | 5 | 0.0045164 | 1.552e-05
2013 | 2012-11-09 | B | 100 | 0.11143 | 0.0003104
2013 | 2012-11-09 | C | 865.9029 | 0.26878 | 0.0041594
2013 | 2012-11-09 | C | 61 | 0.069869 | 0.00018935
2013 | 2012-11-02 | B | 8 | 0.0029054 | 2.4832e-05
2013 | 2012-11-10 | C | 131.5534 | 0.040835 | 0.00072013
2013 | 2012-11-11 | C | 87.9034 | 0.038745 | 0.00049044
2013 | 2012-11-11 | C | 174.75 | 0.0070516 | 0.00073876
2013 | 2012-11-11 | C | 140 | 0.0052148 | 0.00043456
2013 | 2012-11-10 | C | 417.3909 | 0.13863 | 0.0013006
2013 | 2012-11-10 | C | 36.4 | 0.013784 | 0.0001552
2013 | 2012-11-11 | C | 94.4797 | 0.085927 | 0.00072634
2013 | 2012-11-11 | C | 58 | 0.029886 | 0.00018003
2013 | 2012-11-11 | C | 11 | 0.0046778 | 3.4144e-05
2013 | 2012-11-11 | B | 12 | 0.015458 | 3.7248e-05
2013 | 2012-11-10 | B | 20 | 0.012354 | 6.2081e-05
2013 | 2012-11-12 | C | 1097 | 0.057887 | 0.0034051
2013 | 2012-11-12 | C | 669 | 0.035302 | 0.0020766
2013 | 2012-11-11 | C | 3 | 0.012506 | 9.3121e-06
2013 | 2012-11-12 | C | 10 | 0.006177 | 3.104e-05
2013 | 2012-11-12 | B | 15 | 0.015365 | 4.656e-05
2013 | 2012-11-12 | B | 19 | 0.024298 | 5.8977e-05
2013 | 2012-11-12 | C | 580.0829 | 0.38533 | 0.0021697
2013 | 2012-11-12 | C | 1739.8624 | 0.57246 | 0.0092966
2013 | 2012-11-13 | C | 19 | 0.002477 | 5.8977e-05
2013 | 2012-11-13 | B | 20 | 0.01254 | 6.2081e-05
2013 | 2012-11-13 | B | 9 | 0.0062298 | 2.7936e-05
2013 | 2012-11-13 | B | 6 | 0.0044139 | 1.8624e-05
2013 | 2012-11-13 | B | 54.7165 | 0.076768 | 0.00029799
2013 | 2012-11-13 | B | 67 | 0.073829 | 0.00020797
2013 | 2012-11-13 | B | 300 | 0.3222 | 0.00093121
2013 | 2012-11-13 | C | 340 | 0.053824 | 0.0010554
2013 | 2012-11-13 | C | 129 | 0.020421 | 0.00040042
2013 | 2012-11-13 | C | 159.7571 | 0.033225 | 0.0011112
2013 | 2012-11-13 | C | 304 | 0.40198 | 0.00094362
2013 | 2012-11-14 | C | 121.1859 | 0.073728 | 0.0017631
2013 | 2012-11-14 | C | 1 | 0.0003073 | 3.104e-06
2013 | 2012-11-14 | C | 18 | 0.0062577 | 5.5873e-05
2013 | 2012-11-14 | B | 3 | 0.0012199 | 9.3121e-06
2013 | 2012-11-14 | B | 14 | 0.009995 | 4.3456e-05
2013 | 2012-11-14 | B | 3 | 0.0020859 | 9.3121e-06
2013 | 2012-11-14 | C | 2 | 0.0011299 | 6.2081e-06
2013 | 2012-11-14 | B | 99 | 0.11001 | 0.0003073
2013 | 2012-11-14 | B | 23 | 0.02513 | 7.1393e-05
2013 | 2012-11-14 | B | 4 | 0.0019493 | 1.2416e-05
2013 | 2012-11-15 | C | 84 | 0.013819 | 0.00026074
2013 | 2012-11-15 | B | 23 | 0.010923 | 7.1393e-05
2013 | 2012-11-15 | C | 193.2308 | 0.037187 | 0.00098708
2013 | 2012-11-15 | B | 15 | 0.01448 | 4.656e-05
2013 | 2012-11-15 | B | 16 | 0.018475 | 4.9664e-05
2013 | 2012-11-15 | C | 1 | 0.00026695 | 3.104e-06
2013 | 2012-11-15 | C | 25 | 0.0073721 | 7.7601e-05
2013 | 2012-11-15 | B | 7 | 0.007431 | 2.1728e-05
2013 | 2012-11-16 | B | 16 | 0.0027315 | 4.9664e-05
2013 | 2012-11-16 | B | 4 | 0.00014899 | 1.2416e-05
2013 | 2012-11-16 | B | 2 | 7.4497e-05 | 6.2081e-06
2013 | 2012-11-16 | B | 3 | 0.0037435 | 9.3121e-06
2013 | 2012-11-16 | B | 2 | 0.0029302 | 6.2081e-06
2013 | 2012-11-17 | C | 52.3333 | 0.015595 | 0.0021821
2013 | 2012-11-17 | C | 81 | 0.078194 | 0.00025143
2013 | 2012-11-17 | C | 32 | 0.028309 | 9.9329e-05
2013 | 2012-11-17 | C | 186.4275 | 0.14988 | 0.002297
2013 | 2012-11-18 | C | 278 | 0.0069034 | 0.00086292
2013 | 2012-11-18 | C | 54.8261 | 0.066031 | 0.0007729
2013 | 2012-11-18 | C | 159.4398 | 0.093042 | 0.0013316
2013 | 2012-11-18 | C | 51 | 0.011873 | 0.00015831
2013 | 2012-11-18 | C | 140 | 0.083871 | 0.00043456
2013 | 2012-11-18 | C | 62 | 0.012894 | 0.00019245
2013 | 2012-11-18 | C | 143.1818 | 0.018222 | 0.00048423
2013 | 2012-11-18 | C | 27.1054 | 0.058811 | 0.00041904
2013 | 2012-11-18 | B | 1 | 0.00083809 | 3.104e-06
2013 | 2012-11-13 | B | 15 | 0.01774 | 4.656e-05
2013 | 2012-11-12 | B | 2 | 0.00048423 | 6.2081e-06
2013 | 2012-11-19 | B | 6 | 0.00022349 | 1.8624e-05
2013 | 2012-11-14 | C | 594.1741 | 0.36518 | 0.0024553
2013 | 2012-11-19 | B | 5 | 0.0040663 | 1.552e-05
2013 | 2012-11-19 | B | 6 | 0.0014341 | 1.8624e-05
2013 | 2012-11-11 | B | 12 | 0.014788 | 3.7248e-05
2013 | 2012-11-20 | B | 4 | 7.4497e-05 | 1.2416e-05
2013 | 2012-11-20 | B | 43 | 0.013614 | 0.00013347
2013 | 2012-11-20 | B | 16 | 0.014999 | 4.9664e-05
2013 | 2012-11-20 | B | 1 | 0.00082257 | 3.104e-06
2013 | 2012-11-20 | B | 1 | 0.00096535 | 3.104e-06
2013 | 2012-11-20 | C | 340 | 0.022163 | 0.0010554
2013 | 2012-11-20 | B | 27 | 0.02992 | 8.3809e-05
2013 | 2012-11-20 | B | 7 | 0.0018904 | 2.1728e-05
2013 | 2012-11-20 | B | 6 | 0.0018997 | 1.8624e-05
2013 | 2012-11-20 | B | 14 | 0.012255 | 4.3456e-05
2013 | 2012-11-20 | C | 4 | 0.00029799 | 1.2416e-05
2013 | 2012-11-20 | C | 192.3894 | 0.06569 | 0.0012354
2013 | 2012-11-21 | C | 310.3846 | 0.097308 | 0.0010802
2013 | 2012-11-20 | B | 7 | 0.0022597 | 2.1728e-05
2013 | 2012-11-20 | B | 39 | 0.025059 | 0.00012106
2013 | 2012-11-19 | B | 101 | 0.062388 | 0.00031351
2013 | 2012-11-14 | B | 337.0204 | 0.099381 | 0.0011454
2013 | 2012-11-21 | C | 14 | 0.001521 | 4.3456e-05
2013 | 2012-11-21 | B | 73 | 0.048718 | 0.00022659
2013 | 2012-11-21 | B | 257 | 0.26724 | 0.00079774
2013 | 2012-11-21 | B | 99 | 0.11616 | 0.0003073
2013 | 2012-11-21 | B | 3 | 0.0035852 | 9.3121e-06
2013 | 2012-11-21 | C | 17 | 0.0028495 | 5.2768e-05
2013 | 2012-11-22 | C | 104 | 0.025503 | 0.00032282
2013 | 2012-11-22 | B | 15 | 0.0048888 | 4.656e-05
2013 | 2012-11-22 | B | 22 | 0.012429 | 6.8289e-05
2013 | 2012-11-22 | B | 22 | 0.020691 | 6.8289e-05
2013 | 2012-11-22 | B | 27 | 0.0098056 | 8.3809e-05
2013 | 2012-11-22 | B | 2 | 0.0010243 | 6.2081e-06
2013 | 2012-11-22 | C | 178 | 0.012155 | 0.00055252
2013 | 2012-11-22 | C | 252.7903 | 0.046295 | 0.00095604
2013 | 2012-11-22 | B | 86 | 0.087291 | 0.00026695
2013 | 2012-11-22 | C | 1 | 0.00048112 | 3.104e-06
2013 | 2012-11-23 | C | 178 | 0.018233 | 0.00055252
2013 | 2012-11-23 | C | 313 | 0.022346 | 0.00097156
2013 | 2012-11-23 | B | 85 | 0.070446 | 0.00026384
2013 | 2012-11-23 | C | 4 | 0.0012664 | 1.2416e-05
2013 | 2012-11-23 | B | 116 | 0.068773 | 0.00036007
2013 | 2012-11-23 | B | 4 | 0.00067047 | 1.2416e-05
2013 | 2012-11-22 | C | 1.9845 | 0.0079465 | 0.00017383
2013 | 2012-11-24 | C | 23 | 0.0060684 | 7.1393e-05
2013 | 2012-11-24 | C | 73 | 0.021526 | 0.00022659
2013 | 2012-11-24 | B | 3 | 0.00069841 | 9.3121e-06
2013 | 2012-11-24 | C | 214.1087 | 0.089721 | 0.00094673
2013 | 2012-11-24 | C | 73 | 0.0097435 | 0.00022659
2013 | 2012-11-24 | C | 182.7671 | 0.039712 | 0.00093742
2013 | 2012-11-24 | C | 5 | 0.0022815 | 1.552e-05
2013 | 2012-11-24 | B | 1 | 0.00017072 | 3.104e-06
2013 | 2012-11-25 | C | 313.1429 | 0.037908 | 0.00098708
2013 | 2012-11-25 | C | 58 | 0.025385 | 0.00018003
2013 | 2012-11-21 | B | 162.5932 | 0.05804 | 0.00053389
2013 | 2012-11-25 | C | 37.8371 | 0.036409 | 0.00016451
2013 | 2012-11-24 | B | 2 | 0.0010119 | 6.2081e-06
2013 | 2012-11-20 | B | 22 | 0.021852 | 6.8289e-05
2013 | 2012-11-26 | B | 4 | 0.0027812 | 1.2416e-05
2013 | 2012-11-26 | B | 1 | 0.0014185 | 3.104e-06
2013 | 2012-11-26 | C | 1 | 0.0004625 | 3.104e-06
2013 | 2012-11-26 | C | 751.6667 | 0.055997 | 0.0026105
2013 | 2012-11-26 | C | 109.8333 | 0.037843 | 0.00059908
2013 | 2012-11-26 | C | 3 | 0.00070772 | 9.3121e-06
2013 | 2012-11-26 | B | 62 | 0.026366 | 0.00019245
2013 | 2012-11-27 | B | 389 | 0.13403 | 0.0012075
2013 | 2012-11-27 | C | 10 | 0.0013347 | 3.104e-05
2013 | 2012-11-27 | B | 30 | 0.017134 | 9.3121e-05
2013 | 2012-11-27 | B | 12 | 0.015719 | 3.7248e-05
2013 | 2012-11-27 | C | 331 | 0.022604 | 0.0010274
2013 | 2012-11-28 | C | 237 | 0.0088279 | 0.00073565
2013 | 2012-11-28 | C | 788.92 | 0.17632 | 0.0055221
2013 | 2012-11-27 | C | 53.331 | 0.070024 | 0.0018748
2013 | 2012-11-28 | C | 44 | 0.017892 | 0.00013658
2013 | 2012-11-28 | B | 272 | 0.29466 | 0.0008443
2013 | 2012-11-28 | B | 37 | 0.046629 | 0.00011485
2013 | 2012-11-28 | B | 61 | 0.043739 | 0.00018935
2013 | 2012-11-28 | B | 14 | 0.014254 | 4.3456e-05
2013 | 2012-11-28 | B | 33 | 0.036056 | 0.00010243
2013 | 2012-11-28 | B | 67 | 0.059687 | 0.00020797
2013 | 2012-11-28 | B | 35 | 0.039763 | 0.00010864
2013 | 2012-11-28 | B | 12 | 0.0021977 | 3.7248e-05
2013 | 2012-11-26 | B | 40 | 0.03849 | 0.00012416
2013 | 2012-11-26 | B | 135 | 0.032266 | 0.00041904
2013 | 2012-11-29 | C | 2 | 6.2081e-05 | 6.2081e-06
2013 | 2012-11-29 | C | 107 | 0.023249 | 0.00033213
2013 | 2012-11-29 | B | 20 | 0.021728 | 6.2081e-05
2013 | 2012-11-29 | B | 1 | 0.00045629 | 3.104e-06
2013 | 2012-11-29 | C | 6 | 0.0027936 | 1.8624e-05
2013 | 2012-11-29 | C | 221.5244 | 0.054322 | 0.000925
2013 | 2012-11-30 | C | 1 | 0.00097156 | 3.104e-06
2013 | 2012-11-30 | B | 90 | 0.02207 | 0.00027936
2013 | 2012-11-30 | B | 18 | 0.023746 | 5.5873e-05
2013 | 2012-11-30 | B | 33 | 0.033086 | 0.00010243
2013 | 2012-11-30 | C | 90 | 0.0067047 | 0.00027936
2013 | 2012-11-30 | C | 66 | 0.0053265 | 0.00020487
2013 | 2012-11-30 | C | 1 | 0.00015831 | 3.104e-06
2013 | 2012-11-30 | C | 134.7961 | 0.041841 | 0.00069841
2013 | 2012-11-30 | C | 20 | 0.0017383 | 6.2081e-05
2013 | 2012-11-30 | C | 14 | 0.0045195 | 4.3456e-05
2013 | 2012-11-30 | C | 67.84 | 0.02569 | 0.00033213
2013 | 2012-11-30 | C | 108.6525 | 0.038785 | 0.00070461
2013 | 2012-11-30 | C | 219.0393 | 0.15366 | 0.001881
2013 | 2012-12-01 | B | 2 | 0.0022101 | 6.2081e-06
2013 | 2012-12-01 | B | 75 | 0.066349 | 0.0002328
2013 | 2012-12-01 | C | 1 | 0.00071082 | 3.104e-06
2013 | 2012-12-01 | B | 3 | 0.00079153 | 9.3121e-06
2013 | 2012-12-02 | C | 301 | 0.030832 | 0.00093431
2013 | 2012-12-02 | C | 35 | 0.01597 | 0.00010864
2013 | 2012-12-02 | C | 38 | 0.0062515 | 0.00011795
2013 | 2012-12-02 | C | 36 | 0.013745 | 0.00011175
2013 | 2012-12-02 | C | 6 | 0.0081388 | 1.8624e-05
2013 | 2012-12-02 | C | 142.4638 | 0.059699 | 0.00070461
2013 | 2012-12-02 | C | 230 | 0.009995 | 0.00071393
2013 | 2012-12-02 | C | 147.9362 | 0.063369 | 0.00071393
2013 | 2012-12-02 | C | 21 | 0.0084088 | 6.5185e-05
2013 | 2012-12-02 | C | 25 | 0.0027936 | 7.7601e-05
2013 | 2012-12-02 | C | 45.5091 | 0.022884 | 0.00025763
2013 | 2012-12-02 | C | 269.1389 | 0.11779 | 0.00099639
2013 | 2012-12-02 | C | 121.5609 | 0.085654 | 0.00050596
2013 | 2012-12-02 | C | 2 | 0.0012851 | 6.2081e-06
2013 | 2012-12-02 | C | 69.4831 | 0.1266 | 0.0013316
2013 | 2012-12-02 | C | 163 | 0.09006 | 0.00050596
2013 | 2012-12-02 | C | 202.3478 | 0.0559 | 0.00066737
2013 | 2012-12-02 | C | 152.6316 | 0.1066 | 0.00060529
2013 | 2012-12-02 | C | 66 | 0.11759 | 0.00020487
2013 | 2012-12-03 | C | 3043.9342 | 2.2676 | 0.0097994
2013 | 2012-12-03 | C | 8 | 0.0012913 | 2.4832e-05
2013 | 2012-12-03 | C | 20 | 0.0049664 | 6.2081e-05
2013 | 2012-12-03 | B | 46 | 0.031127 | 0.00014279
2013 | 2012-12-03 | C | 1 | 0.00022039 | 3.104e-06
2013 | 2012-12-03 | C | 167 | 0.024364 | 0.00051837
2013 | 2012-12-03 | C | 417 | 0.055658 | 0.0012944
2013 | 2012-12-03 | C | 294.283 | 0.045673 | 0.0015924
2013 | 2012-12-03 | B | 51 | 0.058415 | 0.00015831
2013 | 2012-12-03 | C | 114.9897 | 0.033552 | 0.0010895
2013 | 2012-12-03 | C | 15 | 0.017367 | 4.656e-05
2013 | 2012-12-04 | C | 4 | 0.0011423 | 1.2416e-05
2013 | 2012-11-29 | B | 62.3407 | 0.034638 | 0.00021728
2013 | 2012-11-26 | B | 41 | 0.019344 | 0.00012727
2013 | 2012-12-03 | C | 19.3977 | 0.0051179 | 0.00042525
2013 | 2012-12-04 | B | 40 | 0.037497 | 0.00012416
2013 | 2012-12-03 | C | 1 | 3.104e-05 | 3.104e-06
2013 | 2012-12-04 | C | 1 | 0.00047802 | 3.104e-06
2013 | 2012-12-05 | B | 363 | 0.15211 | 0.0011268
2013 | 2012-12-04 | B | 19 | 0.026952 | 5.8977e-05
2013 | 2012-12-04 | B | 8 | 0.0096597 | 2.4832e-05
2013 | 2012-12-04 | B | 224 | 0.30385 | 0.0006953
2013 | 2012-12-04 | B | 182.694 | 0.23364 | 0.00088154
2013 | 2012-12-04 | C | 17 | 0.0030078 | 5.2768e-05
2013 | 2012-12-05 | B | 8 | 0.0040228 | 2.4832e-05
2013 | 2012-12-05 | C | 112 | 0.020859 | 0.00034765
2013 | 2012-12-05 | C | 108.9632 | 0.044984 | 0.00036938
2013 | 2012-12-05 | B | 2 | 0.00057114 | 6.2081e-06
2013 | 2012-12-05 | C | 128.3654 | 0.019524 | 0.00042215
2013 | 2012-12-05 | B | 7 | 0.006714 | 2.1728e-05
2013 | 2012-12-05 | B | 18 | 0.013856 | 5.5873e-05
2013 | 2012-12-05 | C | 136.698 | 0.06195 | 0.00064874
2013 | 2012-12-05 | C | 154.0263 | 0.034901 | 0.00158
2013 | 2012-12-05 | B | 7 | 0.0097994 | 2.1728e-05
2013 | 2012-12-05 | C | 477.5 | 0.21788 | 0.002924
2013 | 2012-12-05 | C | 1 | 0.00046871 | 3.104e-06
2013 | 2012-12-05 | C | 244.3426 | 0.27001 | 0.00087844
2013 | 2012-12-05 | C | 22 | 0.0021169 | 6.8289e-05
2013 | 2012-12-05 | B | 89 | 0.035085 | 0.00027626
2013 | 2012-12-04 | B | 33 | 0.004507 | 0.00010243
2013 | 2012-12-06 | C | 2 | 0.00013037 | 6.2081e-06
2013 | 2012-12-06 | C | 115 | 0.02356 | 0.00035696
2013 | 2012-12-06 | B | 284 | 0.22656 | 0.00088154
2013 | 2012-12-06 | C | 45.6061 | 0.027605 | 0.00025763
2013 | 2012-12-06 | B | 8 | 0.0081946 | 2.4832e-05
2013 | 2012-12-06 | B | 275 | 0.31669 | 0.00085361
2013 | 2012-12-06 | B | 44 | 0.027179 | 0.00013658
2013 | 2012-12-06 | B | 26 | 0.017916 | 8.0705e-05
2013 | 2012-12-06 | B | 81 | 0.1144 | 0.00025143
2013 | 2012-12-06 | C | 347 | 0.02585 | 0.0010771
2013 | 2012-12-06 | C | 31.7241 | 0.019695 | 0.00085671
2013 | 2012-12-06 | C | 46.0282 | 0.019859 | 0.00025763
2013 | 2012-12-06 | C | 34.6373 | 0.010644 | 0.00013347
2013 | 2012-12-06 | B | 33.2461 | 0.052114 | 0.0004594
2013 | 2012-12-06 | C | 149.4211 | 0.025046 | 0.001133
2013 | 2012-12-06 | C | 185.514 | 0.059887 | 0.001372
2013 | 2012-12-06 | C | 390.9231 | 0.059458 | 0.0019928
2013 | 2012-12-06 | C | 69.7131 | 0.025751 | 0.0010305
2013 | 2012-12-06 | C | 305 | 0.0037869 | 0.00094673
2013 | 2012-12-06 | C | 272 | 0.013509 | 0.0008443
2013 | 2012-12-07 | C | 145.4286 | 0.042884 | 0.00085982
2013 | 2012-12-06 | C | 1 | 0.00064253 | 3.104e-06
2013 | 2012-12-06 | C | 5 | 0.00088465 | 1.552e-05
2013 | 2012-12-06 | C | 5 | 0.0018159 | 1.552e-05
2013 | 2012-12-06 | C | 7 | 0.0038459 | 2.1728e-05
2013 | 2012-12-07 | C | 8 | 0.0013409 | 2.4832e-05
2013 | 2012-12-07 | C | 2 | 0.0005401 | 6.2081e-06
2013 | 2012-12-06 | C | 5 | 0.0020331 | 1.552e-05
2013 | 2012-12-07 | C | 88.6804 | 0.025875 | 0.00042215
2013 | 2012-12-07 | B | 19 | 0.011736 | 5.8977e-05
2013 | 2012-12-06 | C | 1 | 0.0049075 | 3.104e-06
2013 | 2012-12-07 | C | 250.0759 | 0.058994 | 0.0020456
2013 | 2012-12-07 | C | 2 | 0.00072634 | 6.2081e-06
2013 | 2012-12-07 | B | 161 | 0.17841 | 0.00049975
2013 | 2012-12-07 | B | 13 | 0.0075862 | 4.0352e-05
2013 | 2012-12-07 | B | 4 | 0.0037745 | 1.2416e-05
2013 | 2012-12-07 | C | 2 | 0.00020487 | 6.2081e-06
2013 | 2012-12-07 | C | 122 | 0.036733 | 0.00037869
2013 | 2012-12-07 | C | 122 | 0.04923 | 0.00037869
2013 | 2012-12-07 | C | 75 | 0.034222 | 0.0002328
2013 | 2012-12-07 | C | 81.295 | 0.034318 | 0.00037869
2013 | 2012-12-08 | B | 174 | 0.084796 | 0.0005401
2013 | 2012-12-08 | C | 142.8943 | 0.053226 | 0.00085361
2013 | 2012-12-07 | C | 19 | 0.065287 | 5.8977e-05
2013 | 2012-12-08 | C | 4 | 0.00075738 | 1.2416e-05
2013 | 2012-12-08 | B | 14 | 0.013037 | 4.3456e-05
2013 | 2012-12-08 | C | 202 | 0.0075242 | 0.00062701
2013 | 2012-12-09 | C | 904.9193 | 0.44381 | 0.004296
2013 | 2012-12-09 | C | 95 | 0.020642 | 0.00029488
2013 | 2012-12-09 | C | 89 | 0.014918 | 0.00027626
2013 | 2012-12-09 | C | 201 | 0.078613 | 0.00062391
2013 | 2012-12-09 | B | 193 | 0.14797 | 0.00059908
2013 | 2012-12-09 | C | 65 | 0.00343 | 0.00020176
2013 | 2012-12-09 | C | 8014 | 0.024876 | 0.024876
2013 | 2012-12-09 | C | 4 | 0.00079463 | 1.2416e-05
2013 | 2012-12-09 | C | 201 | 0.046169 | 0.00062391
2013 | 2012-12-07 | C | 7 | 0.0084088 | 2.1728e-05
2013 | 2012-12-10 | B | 24 | 0.021455 | 7.4497e-05
2013 | 2012-12-10 | B | 1 | 0.0012323 | 3.104e-06
2013 | 2012-12-10 | C | 599.96 | 0.087528 | 0.0029519
2013 | 2012-12-10 | B | 167 | 0.1861 | 0.00051837
2013 | 2012-12-11 | C | 4393 | 0.39544 | 0.013636
2013 | 2012-12-11 | C | 6914.0606 | 1.3521 | 0.021654
2013 | 2012-12-10 | C | 100 | 0.014589 | 0.0003104
2013 | 2012-12-11 | C | 129.0307 | 0.064082 | 0.0012602
2013 | 2012-12-10 | B | 12 | 0.0028309 | 3.7248e-05
2013 | 2012-12-06 | C | 3 | 0.0012758 | 9.3121e-06
2013 | 2012-12-11 | B | 8 | 0.0045195 | 2.4832e-05
2013 | 2012-12-11 | C | 1 | 2.1728e-05 | 3.104e-06
2013 | 2012-12-11 | B | 275 | 0.28596 | 0.00085361
2013 | 2012-12-11 | B | 8 | 0.008592 | 2.4832e-05
2013 | 2012-12-11 | B | 83 | 0.094552 | 0.00025763
2013 | 2012-12-11 | B | 98 | 0.13902 | 0.00030419
2013 | 2012-12-11 | B | 43 | 0.062332 | 0.00013347
2013 | 2012-12-11 | B | 26 | 0.027601 | 8.0705e-05
2013 | 2012-12-11 | B | 16 | 0.021256 | 4.9664e-05
2013 | 2012-12-11 | C | 21.4783 | 0.0059336 | 0.00011795
2013 | 2012-12-11 | C | 21 | 0.01245 | 6.5185e-05
2013 | 2012-12-11 | C | 26 | 0.0038738 | 8.0705e-05
2013 | 2012-12-11 | C | 28.1378 | 0.039041 | 0.00049975
2013 | 2012-12-12 | B | 83 | 0.063636 | 0.00025763
2013 | 2012-12-11 | B | 19 | 0.036978 | 5.8977e-05
2013 | 2012-12-12 | B | 39 | 0.04237 | 0.00012106
2013 | 2012-12-12 | B | 1 | 0.0012633 | 3.104e-06
2013 | 2012-12-12 | C | 61 | 0.0060591 | 0.00018935
2013 | 2012-12-12 | C | 998 | 0.12081 | 0.0030978
2013 | 2012-12-12 | B | 98.5161 | 0.027522 | 0.00052458
2013 | 2012-12-13 | B | 34 | 0.017625 | 0.00010554
2013 | 2012-12-13 | B | 15 | 0.0068444 | 4.656e-05
2013 | 2012-12-13 | B | 275 | 0.26206 | 0.00085361
2013 | 2012-12-13 | B | 27 | 0.019025 | 8.3809e-05
2013 | 2012-12-13 | C | 167.6899 | 0.30398 | 0.001105
2013 | 2012-12-13 | B | 78 | 0.09733 | 0.00024211
2013 | 2012-12-13 | B | 1 | 0.0008443 | 3.104e-06
2013 | 2012-12-13 | C | 406 | 0.24197 | 0.0012602
2013 | 2012-12-13 | B | 81.3901 | 0.10156 | 0.00045629
2013 | 2012-12-13 | C | 17.0857 | 0.0091219 | 0.00062081
2013 | 2012-12-13 | B | 106 | 0.010858 | 0.00032903
2013 | 2012-12-13 | B | 2 | 0.00185 | 6.2081e-06
2013 | 2012-12-14 | C | 39 | 0.0012106 | 0.00012106
2013 | 2012-12-14 | C | 80 | 0.0059597 | 0.00024832
2013 | 2012-12-14 | B | 16 | 0.0087906 | 4.9664e-05
2013 | 2012-12-14 | B | 20 | 0.0047802 | 6.2081e-05
2013 | 2012-12-14 | C | 64 | 0.016489 | 0.00019866
2013 | 2012-12-13 | C | 1 | 0.0030295 | 3.104e-06
2013 | 2012-12-14 | B | 11 | 0.011951 | 3.4144e-05
2013 | 2012-12-14 | C | 220.9143 | 0.069944 | 0.0023529
2013 | 2012-12-14 | C | 24.5326 | 0.039522 | 0.00027315
2013 | 2012-12-15 | B | 14 | 0.0037807 | 4.3456e-05
2013 | 2012-12-14 | C | 13 | 0.031959 | 4.0352e-05
2013 | 2012-12-14 | C | 15.0809 | 0.051352 | 0.00036007
2013 | 2012-12-15 | B | 44 | 0.037559 | 0.00013658
2013 | 2012-12-15 | C | 226.3885 | 0.095569 | 0.0011175
2013 | 2012-12-16 | C | 788 | 0.14676 | 0.002446
2013 | 2012-12-16 | C | 300.4 | 0.062474 | 0.0011237
2013 | 2012-12-17 | C | 170.5915 | 0.073603 | 0.0008443
2013 | 2012-12-01 | B | 4 | 0.0028185 | 1.2416e-05
2013 | 2012-12-04 | B | 4 | 0.0043581 | 1.2416e-05
2013 | 2012-12-17 | C | 4 | 0.00083188 | 1.2416e-05
2013 | 2012-12-15 | B | 2 | 0.00042836 | 6.2081e-06
2013 | 2012-12-17 | B | 3 | 0.0038831 | 9.3121e-06
2013 | 2012-12-17 | B | 21 | 0.023858 | 6.5185e-05
2013 | 2012-12-17 | B | 54 | 0.064198 | 0.00016762
2013 | 2012-12-18 | B | 31 | 0.021651 | 9.6225e-05
2013 | 2012-12-18 | B | 12 | 0.011808 | 3.7248e-05
2013 | 2012-12-18 | B | 16 | 0.016489 | 4.9664e-05
2013 | 2012-12-18 | B | 24 | 0.026372 | 7.4497e-05
2013 | 2012-12-18 | B | 110 | 0.13077 | 0.00034144
2013 | 2012-12-18 | B | 86 | 0.13054 | 0.00026695
2013 | 2012-12-18 | B | 14 | 0.015818 | 4.3456e-05
2013 | 2012-12-18 | B | 181 | 0.21125 | 0.00056183
2013 | 2012-12-18 | B | 24 | 0.026744 | 7.4497e-05
2013 | 2012-12-18 | C | 1 | 0.00010864 | 3.104e-06
2013 | 2012-12-06 | B | 11 | 0.004268 | 3.4144e-05
2013 | 2012-12-19 | B | 13 | 0.0013316 | 4.0352e-05
2013 | 2012-12-19 | C | 1 | 0.00013658 | 3.104e-06
2013 | 2012-12-19 | B | 2 | 0.0011361 | 6.2081e-06
2013 | 2012-12-19 | B | 96 | 0.010728 | 0.00029799
2013 | 2012-12-19 | C | 42 | 0.012255 | 0.00013037
2013 | 2012-12-19 | B | 5 | 0.0041904 | 1.552e-05
2013 | 2012-12-19 | B | 1 | 0.0011081 | 3.104e-06
2013 | 2012-12-19 | C | 85 | 0.050394 | 0.00026384
2013 | 2012-12-19 | B | 16 | 0.015446 | 4.9664e-05
2013 | 2012-12-19 | B | 76 | 0.073839 | 0.00023591
2013 | 2012-12-19 | B | 236 | 0.29375 | 0.00073255
2013 | 2012-12-20 | C | 125.787 | 0.088631 | 0.00042525
2013 | 2012-12-20 | C | 36.3045 | 0.034821 | 0.00012727
2013 | 2012-12-20 | B | 23 | 0.010138 | 7.1393e-05
2013 | 2012-12-20 | B | 75 | 0.033291 | 0.0002328
2013 | 2012-12-19 | C | 13 | 0.054355 | 4.0352e-05
2013 | 2012-12-20 | C | 19 | 0.0035976 | 5.8977e-05
2013 | 2012-12-20 | B | 3 | 0.0014527 | 9.3121e-06
2013 | 2012-12-20 | B | 178 | 0.19007 | 0.00055252
2013 | 2012-12-20 | C | 2 | 0.0003849 | 6.2081e-06
2013 | 2012-12-20 | B | 39 | 0.04128 | 0.00012106
2013 | 2012-12-20 | B | 236 | 0.31939 | 0.00073255
2013 | 2012-12-20 | C | 163 | 0.091578 | 0.00050596
2013 | 2012-12-21 | C | 231.412 | 0.30815 | 0.0030668
2013 | 2012-12-21 | C | 11 | 0.0040973 | 3.4144e-05
2013 | 2012-12-21 | B | 178 | 0.11492 | 0.00055252
2013 | 2012-12-21 | C | 18 | 0.0028495 | 5.5873e-05
2013 | 2012-12-21 | C | 819 | 0.091519 | 0.0025422
2013 | 2012-12-21 | C | 819 | 0.068639 | 0.0025422
2013 | 2012-12-21 | C | 516 | 0.27068 | 0.0016017
2013 | 2012-12-21 | C | 421 | 0.014375 | 0.0013068
2013 | 2012-12-22 | C | 421 | 0.010454 | 0.0013068
2013 | 2012-12-22 | C | 2338 | 0.014514 | 0.0072572
2013 | 2012-12-22 | C | 66 | 0.0096287 | 0.00020487
2013 | 2012-12-22 | C | 255.3488 | 0.16803 | 0.002297
2013 | 2012-12-22 | C | 86 | 0.010411 | 0.00026695
2013 | 2012-12-23 | C | 190 | 0.038925 | 0.00058977
2013 | 2012-12-24 | C | 92 | 0.1048 | 0.00028557
2013 | 2012-12-24 | C | 5 | 0.0035541 | 1.552e-05
2013 | 2012-12-24 | C | 1131.3171 | 0.13344 | 0.00352
2013 | 2012-12-24 | C | 394 | 0.063595 | 0.001223
2013 | 2012-12-24 | C | 575.0417 | 0.20884 | 0.0032841
2013 | 2012-12-24 | C | 41 | 0.0085268 | 0.00012727
2013 | 2012-12-25 | C | 11 | 0.0019804 | 3.4144e-05
2013 | 2012-12-25 | C | 8 | 0.0017631 | 2.4832e-05
2013 | 2012-12-25 | C | 810 | 0.18606 | 0.0043394
2013 | 2012-12-25 | C | 133.014 | 0.20561 | 0.0014465
2013 | 2012-12-25 | C | 27 | 0.010895 | 8.3809e-05
2013 | 2012-12-25 | C | 2 | 0.00086913 | 6.2081e-06
2013 | 2012-12-25 | C | 8 | 0.0008443 | 2.4832e-05
2013 | 2012-12-25 | C | 144.6384 | 0.078119 | 0.00082878
2013 | 2012-12-24 | C | 1122.1179 | 1.8217 | 0.0089117
2013 | 2012-12-26 | C | 21 | 0.0016948 | 6.5185e-05
2013 | 2012-12-26 | C | 237.7377 | 0.042801 | 0.0016203
2013 | 2012-12-26 | C | 167 | 0.021772 | 0.00051837
2013 | 2012-12-26 | C | 416 | 0.034864 | 0.0012913
2013 | 2012-12-27 | C | 146 | 0.0054383 | 0.00045319
2013 | 2012-12-27 | C | 254 | 0.013403 | 0.00078842
2013 | 2012-12-26 | C | 120.375 | 0.064641 | 0.0012633
2013 | 2012-12-28 | C | 593 | 0.084672 | 0.0018407
2013 | 2012-12-28 | C | 134.4853 | 0.083907 | 0.0011795
2013 | 2012-12-27 | C | 75.4878 | 0.12419 | 0.00035386
2013 | 2012-12-26 | C | 26 | 0.012509 | 8.0705e-05
2013 | 2012-12-26 | C | 1 | 3.7248e-05 | 3.104e-06
2013 | 2012-12-24 | C | 1 | 0.008415 | 3.104e-06
2013 | 2012-12-26 | C | 204 | 0.010132 | 0.00063322
2013 | 2012-12-26 | C | 1 | 0.00019245 | 3.104e-06
2013 | 2012-12-26 | C | 204 | 0.11398 | 0.00063322
2013 | 2012-12-26 | C | 31 | 0.0046188 | 9.6225e-05
2013 | 2012-12-26 | C | 68.9926 | 0.085662 | 0.00037248
2013 | 2012-12-27 | C | 225.4703 | 0.12738 | 0.001431
2013 | 2012-12-27 | C | 83 | 0.036842 | 0.00025763
2013 | 2012-12-27 | C | 23.1394 | 0.011636 | 0.00010554
2013 | 2012-12-27 | C | 145 | 0.035557 | 0.00045008
2013 | 2012-12-29 | C | 83 | 0.010048 | 0.00025763
2013 | 2012-12-29 | C | 1 | 0.00089086 | 3.104e-06
2013 | 2012-12-29 | C | 2 | 0.00053389 | 6.2081e-06
2013 | 2012-12-26 | C | 1969 | 0.018335 | 0.0061118
2013 | 2012-12-29 | C | 1 | 0.00019555 | 3.104e-06
2013 | 2012-12-27 | C | 983 | 0.1312 | 0.0030513
2013 | 2012-12-26 | C | 99.1884 | 0.17395 | 0.00055873
2013 | 2012-12-26 | C | 616.152 | 0.23333 | 0.0043301
2013 | 2012-12-30 | C | 891.0714 | 0.14659 | 0.0057362
2013 | 2012-12-30 | C | 573.2807 | 0.096092 | 0.0064595
2013 | 2012-12-30 | C | 282.125 | 0.039408 | 0.0010181
2013 | 2012-12-31 | C | 801.5 | 0.017415 | 0.002806
2013 | 2012-12-31 | C | 2 | 0.00013037 | 6.2081e-06
2013 | 2012-12-26 | C | 1377.764 | 0.36779 | 0.004327
2013 | 2012-12-31 | C | 27 | 0.0029333 | 8.3809e-05
2013 | 2012-12-31 | C | 210 | 0.024118 | 0.00065185
2013 | 2012-12-31 | C | 95 | 0.021526 | 0.00029488
2013 | 2013-01-01 | C | 83 | 0.046117 | 0.00025763
2013 | 2013-01-01 | C | 2078.4167 | 0.29032 | 0.0070648
2013 | 2013-01-01 | C | 34 | 0.010026 | 0.00010554
2013 | 2013-01-01 | C | 41 | 0.090613 | 0.00012727
2013 | 2013-01-01 | C | 506.223 | 0.22784 | 0.0028122
2013 | 2013-01-02 | C | 4 | 0.0038614 | 1.2416e-05
2013 | 2013-01-02 | C | 2507 | 0.70036 | 0.0077818
2013 | 2013-01-02 | C | 19 | 0.013093 | 5.8977e-05
2013 | 2013-01-02 | C | 10 | 0.0020176 | 3.104e-05
2013 | 2013-01-02 | C | 5 | 0.00079153 | 1.552e-05
2013 | 2013-01-02 | C | 23 | 0.00049975 | 7.1393e-05
2013 | 2013-01-02 | C | 26.9868 | 0.012398 | 0.00019555
2013 | 2013-01-02 | C | 13 | 0.0017352 | 4.0352e-05
2013 | 2013-01-02 | C | 29.1974 | 0.062625 | 0.00029799
2013 | 2013-01-03 | C | 100.062 | 0.039135 | 0.00043456
2013 | 2013-01-03 | C | 18.3927 | 0.040535 | 0.00013658
2013 | 2013-01-03 | C | 143 | 0.15136 | 0.00044388
2013 | 2013-01-03 | C | 9 | 0.0032965 | 2.7936e-05
2013 | 2013-01-03 | C | 35 | 0.0029333 | 0.00010864
2013 | 2013-01-03 | C | 36 | 0.012292 | 0.00011485
2013 | 2013-01-03 | C | 35 | 0.020968 | 0.00010864
2013 | 2013-01-03 | C | 2 | 0.00024832 | 6.2081e-06
2013 | 2013-01-03 | C | 940 | 0.040849 | 0.0029178
2013 | 2013-01-03 | C | 19 | 0.00082567 | 5.8977e-05
2013 | 2013-01-03 | C | 55.2138 | 0.12374 | 0.00034144
2013 | 2013-01-03 | C | 31 | 0.0023094 | 9.6225e-05
2013 | 2013-01-04 | C | 332 | 0.016489 | 0.0010057
2013 | 2013-01-03 | C | 56.1158 | 0.065668 | 0.00022349
2013 | 2013-01-04 | C | 70.8904 | 0.031467 | 0.0004656
2013 | 2013-01-03 | C | 51.6802 | 0.02711 | 0.00023901
2013 | 2013-01-04 | C | 6 | 0.00057735 | 1.8624e-05
2013 | 2013-01-04 | C | 14 | 0.0072572 | 4.3456e-05
2013 | 2013-01-05 | C | 55 | 0.017755 | 0.00017072
2013 | 2013-01-04 | C | 16 | 0.0015396 | 4.9664e-05
2013 | 2013-01-03 | C | 10.5422 | 0.046434 | 0.00021418
2013 | 2013-01-06 | C | 52 | 0.064402 | 0.00016141
2013 | 2013-01-06 | C | 60 | 0.0070772 | 0.00018624
2013 | 2013-01-06 | C | 812 | 0.098298 | 0.0025205
2013 | 2013-01-06 | C | 1257.7963 | 0.19912 | 0.0084119
2013 | 2013-01-04 | C | 1 | 0.00056493 | 3.104e-06
2013 | 2013-01-07 | C | 16 | 0.0047181 | 4.9664e-05
2013 | 2013-01-03 | C | 1 | 0.0097063 | 3.104e-06
2013 | 2013-01-07 | C | 84 | 0.0070399 | 0.00026074
2013 | 2013-01-07 | C | 271.7126 | 0.070846 | 0.0040508
2013 | 2013-01-07 | C | 1 | 4.3456e-05 | 3.104e-06
2013 | 2013-01-07 | C | 23 | 0.0044977 | 7.1393e-05
2013 | 2013-01-07 | C | 38.5085 | 0.020798 | 0.0011423
2013 | 2013-01-07 | C | 457 | 0.01986 | 0.0014185
2013 | 2013-01-07 | C | 457 | 0.076601 | 0.0014185
2013 | 2013-01-07 | C | 48.686 | 0.017832 | 0.00017072
2013 | 2013-01-07 | C | 204.6261 | 0.14418 | 0.0029085
2013 | 2013-01-07 | C | 168.8291 | 0.081228 | 0.00058666
2013 | 2013-01-07 | C | 1 | 0.0003073 | 3.104e-06
2013 | 2013-01-07 | C | 29 | 0.013322 | 9.0017e-05
2013 | 2013-01-07 | C | 385 | 0.069313 | 0.0011951
2013 | 2013-01-07 | C | 154 | 0.0076483 | 0.00047802
2013 | 2013-01-07 | C | 21.1186 | 0.070535 | 0.00095294
2013 | 2013-01-07 | C | 26 | 0.0033089 | 8.0705e-05
2013 | 2013-01-07 | C | 28 | 0.0064315 | 8.6913e-05
2013 | 2013-01-07 | C | 6 | 0.00081946 | 1.8624e-05
2013 | 2013-01-08 | C | 385 | 0.022706 | 0.0011951
2013 | 2013-01-07 | C | 49.7378 | 0.059594 | 0.00071082
2013 | 2013-01-08 | C | 83.9545 | 0.03935 | 0.0016544
2013 | 2013-01-08 | C | 6 | 0.00089396 | 1.8624e-05
2013 | 2012-12-28 | B | 10 | 0.0045008 | 3.104e-05
2013 | 2012-12-21 | B | 9 | 0.0014806 | 2.7936e-05
2013 | 2013-01-07 | C | 3 | 0.021232 | 9.3121e-06
2013 | 2013-01-08 | B | 7 | 0.00080394 | 2.1728e-05
2013 | 2013-01-08 | C | 35 | 0.0092345 | 0.00010864
2013 | 2013-01-08 | B | 19 | 0.011441 | 5.8977e-05
2013 | 2013-01-08 | C | 631 | 0.0019586 | 0.0019648
2013 | 2013-01-08 | B | 145 | 0.13908 | 0.00045008
2013 | 2013-01-08 | B | 288 | 0.36116 | 0.00089396
2013 | 2013-01-08 | C | 110.0047 | 0.14444 | 0.0012727
2013 | 2013-01-08 | C | 247.226 | 0.29315 | 0.0020983
2013 | 2013-01-08 | C | 204 | 0.011398 | 0.00063322
2013 | 2013-01-08 | C | 168 | 0.010951 | 0.00052148
2013 | 2013-01-09 | C | 20 | 0.0016762 | 6.2081e-05
2013 | 2013-01-09 | C | 31 | 0.0036565 | 9.6225e-05
2013 | 2013-01-09 | B | 6 | 0.00011175 | 1.8624e-05
2013 | 2013-01-09 | B | 49 | 0.060991 | 0.0001521
2013 | 2013-01-09 | B | 195 | 0.22517 | 0.00060529
2013 | 2013-01-09 | B | 184 | 0.23017 | 0.00057114
2013 | 2013-01-09 | B | 19 | 0.023827 | 5.8977e-05
2013 | 2013-01-09 | B | 117 | 0.056655 | 0.00036317
2013 | 2013-01-09 | C | 159.3838 | 0.13259 | 0.0015396
2013 | 2013-01-09 | C | 4 | 0.00064564 | 1.2416e-05
2013 | 2013-01-10 | C | 23.1212 | 0.044784 | 9.3121e-05
2013 | 2013-01-10 | B | 6 | 0.00048423 | 1.8624e-05
2013 | 2013-01-10 | B | 2 | 0.0008505 | 6.2081e-06
2013 | 2013-01-10 | C | 7 | 0.0028681 | 2.1728e-05
2013 | 2013-01-10 | B | 74 | 0.035144 | 0.0002297
2013 | 2013-01-10 | B | 49 | 0.062816 | 0.0001521
2013 | 2013-01-10 | C | 401.3162 | 0.14201 | 0.0018407
2013 | 2013-01-10 | B | 58 | 0.043028 | 0.00018003
2013 | 2013-01-10 | C | 9 | 0.002207 | 2.7936e-05
2013 | 2013-01-10 | B | 36 | 0.020561 | 0.00011175
2013 | 2013-01-10 | B | 11 | 0.009697 | 3.4144e-05
2013 | 2013-01-10 | C | 4.2647 | 0.0022107 | 2.1728e-05
2013 | 2013-01-10 | C | 29 | 0.010892 | 9.0017e-05
2013 | 2013-01-10 | C | 25.8599 | 0.028977 | 0.00027315
2013 | 2013-01-10 | C | 338.5804 | 0.14713 | 0.0026508
2013 | 2013-01-11 | C | 157.4167 | 0.033715 | 0.00057735
2013 | 2013-01-11 | C | 525.6111 | 0.11257 | 0.0017755
2013 | 2013-01-11 | C | 156 | 0.010653 | 0.00048423
2013 | 2013-01-11 | C | 14 | 0.0017383 | 4.656e-05
2013 | 2013-01-11 | C | 2 | 0.00024832 | 6.2081e-06
2013 | 2013-01-11 | C | 274.5404 | 0.19771 | 0.0036596
2013 | 2013-01-11 | C | 22 | 0.0036193 | 6.8289e-05
2013 | 2013-01-11 | B | 50 | 0.063943 | 0.0001552
2013 | 2013-01-11 | C | 59 | 0.011171 | 0.00018314
2013 | 2013-01-12 | C | 1.0925 | 0.0099941 | 1.2416e-05
2013 | 2013-01-13 | C | 71 | 0.012562 | 0.00022039
2013 | 2013-01-13 | C | 20 | 0.003849 | 6.2081e-05
2013 | 2013-01-13 | C | 5 | 0.00066737 | 1.552e-05
2013 | 2013-01-13 | B | 1 | 0.00085982 | 3.104e-06
2013 | 2013-01-13 | C | 231.1502 | 0.16502 | 0.002387
2013 | 2013-01-14 | C | 93 | 0.0025981 | 0.00028867
2013 | 2013-01-14 | B | 16 | 0.017681 | 4.9664e-05
2013 | 2013-01-14 | B | 6 | 0.00016762 | 1.8624e-05
2013 | 2013-01-14 | C | 284 | 0.11196 | 0.00088154
2013 | 2013-01-12 | C | 10 | 0.0064253 | 3.104e-05
2013 | 2013-01-14 | C | 3 | 0.00045629 | 9.3121e-06
2013 | 2013-01-15 | B | 201 | 0.17532 | 0.00062391
2013 | 2013-01-15 | C | 56.4194 | 0.010333 | 0.00028867
2013 | 2013-01-15 | C | 167 | 0.0067388 | 0.00051837
2013 | 2013-01-15 | C | 410.6897 | 0.033145 | 0.0010585
2013 | 2013-01-15 | B | 88 | 0.049714 | 0.00027315
2013 | 2013-01-15 | B | 63 | 0.068248 | 0.00019555
2013 | 2013-01-15 | B | 7 | 0.0064533 | 2.1728e-05
2013 | 2013-01-15 | B | 51 | 0.060314 | 0.00015831
2013 | 2013-01-15 | B | 45 | 0.036736 | 0.00013968
2013 | 2013-01-15 | B | 94 | 0.12284 | 0.00029178
2013 | 2013-01-15 | B | 49 | 0.06601 | 0.0001521
2013 | 2013-01-15 | C | 570 | 0.023001 | 0.0017755
2013 | 2013-01-15 | C | 13 | 0.0018966 | 4.0352e-05
2013 | 2013-01-15 | C | 355.1244 | 0.22708 | 0.0025608
2013 | 2013-01-15 | C | 50.3259 | 0.069983 | 0.00029488
2013 | 2013-01-14 | B | 63 | 0.030702 | 0.00019555
2013 | 2013-01-07 | B | 39 | 0.036075 | 0.00012106
2013 | 2013-01-16 | C | 416.3725 | 0.38127 | 0.004029
2013 | 2013-01-16 | C | 197.3119 | 0.18864 | 0.0007667
2013 | 2013-01-16 | B | 7 | 0.0061708 | 2.1728e-05
2013 | 2013-01-16 | B | 69 | 0.073249 | 0.00021418
2013 | 2013-01-16 | C | 1 | 0.0010119 | 3.104e-06
2013 | 2013-01-16 | B | 297 | 0.16502 | 0.0009219
2013 | 2013-01-16 | B | 3 | 0.0025888 | 9.3121e-06
2013 | 2013-01-16 | B | 4 | 0.0050658 | 1.2416e-05
2013 | 2013-01-16 | B | 334 | 0.35871 | 0.0010367
2013 | 2013-01-16 | B | 19 | 0.018106 | 5.8977e-05
2013 | 2013-01-16 | B | 20 | 0.026819 | 6.2081e-05
2013 | 2013-01-16 | C | 8.4 | 0.0048758 | 6.8289e-05
2013 | 2013-01-16 | C | 96.8636 | 0.0057127 | 0.0003104
2013 | 2013-01-16 | B | 253 | 0.32669 | 0.00078532
2013 | 2013-01-16 | C | 80.1739 | 0.016425 | 0.0003073
2013 | 2013-01-17 | B | 225 | 0.2179 | 0.00069841
2013 | 2013-01-17 | B | 67 | 0.029116 | 0.00020797
2013 | 2013-01-17 | B | 51 | 0.046225 | 0.00015831
2013 | 2013-01-17 | B | 10 | 0.01403 | 3.104e-05
2013 | 2013-01-17 | B | 4 | 0.0049168 | 1.2416e-05
2013 | 2013-01-17 | B | 195 | 0.23425 | 0.00060529
2013 | 2013-01-17 | B | 7 | 0.006953 | 2.1728e-05
2013 | 2013-01-17 | B | 7 | 0.0046064 | 2.1728e-05
2013 | 2013-01-17 | B | 32 | 0.040626 | 9.9329e-05
2013 | 2013-01-17 | C | 1228 | 0.0076235 | 0.0038117
2013 | 2013-01-17 | C | 797.359 | 0.089101 | 0.0032654
2013 | 2013-01-17 | C | 25 | 0.0005432 | 7.7601e-05
2013 | 2013-01-17 | C | 328.2222 | 0.070298 | 0.0012447
2013 | 2013-01-17 | C | 101.8968 | 0.038904 | 0.00034455
2013 | 2013-01-17 | C | 3 | 0.001462 | 9.3121e-06
2013 | 2013-01-17 | C | 75.5627 | 0.14519 | 0.00026074
2013 | 2013-01-18 | C | 334 | 0.061168 | 0.0010367
2013 | 2013-01-17 | C | 224.2787 | 0.12531 | 0.0029985
2013 | 2013-01-18 | C | 89 | 0.010774 | 0.00027626
2013 | 2013-01-17 | C | 79.2272 | 0.24174 | 0.00039111
2013 | 2013-01-17 | C | 43 | 0.18072 | 0.00013347
2013 | 2013-01-18 | C | 1577 | 0.6902 | 0.0048951
2013 | 2013-01-18 | B | 12 | 0.011919 | 3.7248e-05
2013 | 2013-01-18 | B | 6.3067 | 0.0072823 | 3.7248e-05
2013 | 2013-01-18 | B | 14 | 0.014471 | 4.3456e-05
2013 | 2013-01-18 | B | 39 | 0.039828 | 0.00012106
2013 | 2013-01-18 | C | 221.5699 | 0.061898 | 0.0010647
2013 | 2013-01-19 | B | 3 | 0.0023466 | 9.3121e-06
2013 | 2013-01-19 | C | 76 | 0.012267 | 0.00023591
2013 | 2013-01-19 | C | 39 | 0.019853 | 0.00012106
2013 | 2013-01-20 | C | 673 | 0.10445 | 0.002089
2013 | 2013-01-19 | C | 66.1817 | 0.17236 | 0.00034144
2013 | 2013-01-19 | C | 17.1355 | 0.037924 | 0.00012727
2013 | 2013-01-19 | C | 58 | 0.0081015 | 0.00018003
2013 | 2013-01-20 | C | 71.4414 | 0.048565 | 0.00079153
2013 | 2013-01-19 | B | 22 | 0.025745 | 6.8289e-05
2013 | 2013-01-21 | C | 99.1132 | 0.015383 | 0.0010212
2013 | 2013-01-21 | C | 116 | 0.019444 | 0.00036007
2013 | 2013-01-21 | B | 60 | 0.067419 | 0.00018624
2013 | 2013-01-22 | C | 242.8876 | 0.064838 | 0.0010616
2013 | 2013-01-22 | C | 15 | 0.0030264 | 4.656e-05
2013 | 2013-01-22 | B | 27 | 0.0077942 | 8.3809e-05
2013 | 2013-01-22 | B | 20 | 0.012602 | 6.2081e-05
2013 | 2013-01-22 | B | 3 | 0.0017693 | 9.3121e-06
2013 | 2013-01-22 | B | 25 | 0.022271 | 7.7601e-05
2013 | 2013-01-22 | B | 1 | 0.0012013 | 3.104e-06
2013 | 2013-01-22 | B | 51 | 0.061897 | 0.00015831
2013 | 2013-01-22 | B | 53 | 0.06926 | 0.00016451
2013 | 2013-01-22 | B | 2 | 0.00050906 | 6.2081e-06
2013 | 2013-01-22 | B | 43 | 0.053656 | 0.00013347
2013 | 2013-01-22 | C | 7 | 0.00047802 | 2.1728e-05
2013 | 2013-01-22 | C | 571 | 0.023041 | 0.0017755
2013 | 2013-01-22 | C | 65.0818 | 0.021616 | 0.00033213
2013 | 2013-01-23 | C | 52.875 | 0.012638 | 0.00022039
2013 | 2013-01-23 | C | 82 | 0.014508 | 0.00025453
2013 | 2013-01-23 | B | 334 | 0.2343 | 0.0010367
2013 | 2013-01-23 | B | 105 | 0.047911 | 0.00032592
2013 | 2013-01-22 | B | 173 | 0.057996 | 0.000537
2013 | 2013-01-23 | B | 36 | 0.033188 | 0.00011175
2013 | 2013-01-22 | B | 88.5474 | 0.12973 | 0.000537
2013 | 2013-01-23 | B | 173 | 0.014499 | 0.000537
2013 | 2013-01-23 | C | 1 | 6.5185e-05 | 0
2013 | 2013-01-23 | B | 60 | 0.067978 | 0.00018624
2013 | 2013-01-23 | B | 95 | 0.092003 | 0.00029488
2013 | 2013-01-23 | B | 38 | 0.04093 | 0.00011795
2013 | 2013-01-23 | B | 93 | 0.10421 | 0.00028867
2013 | 2013-01-23 | C | 111 | 0.038589 | 0.00034455
2013 | 2013-01-24 | B | 71 | 0.044518 | 0.00022039
2013 | 2013-01-24 | B | 51 | 0.044167 | 0.00015831
2013 | 2013-01-24 | C | 244.1863 | 0.075038 | 0.0033337
2013 | 2013-01-24 | C | 1 | 0.00048733 | 3.104e-06
2013 | 2013-01-24 | B | 19 | 0.015924 | 5.8977e-05
2013 | 2013-01-24 | B | 4 | 0.0048175 | 1.2416e-05
2013 | 2013-01-24 | B | 5 | 0.005789 | 1.552e-05
2013 | 2013-01-26 | C | 498 | 0.052557 | 0.0015458
2013 | 2013-01-27 | C | 990.7037 | 0.15683 | 0.0030916
2013 | 2013-01-27 | C | 120 | 0.017879 | 0.00037248
2013 | 2013-01-28 | C | 417 | 0.015533 | 0.0012913
2013 | 2013-01-28 | C | 963.3158 | 0.047843 | 0.0030326
2013 | 2013-01-28 | C | 32 | 0.0012913 | 9.9329e-05
2013 | 2013-01-28 | B | 1 | 0.00020797 | 3.104e-06
2013 | 2013-01-28 | B | 4 | 0.0052024 | 1.2416e-05
2013 | 2013-01-28 | B | 1 | 0.00062701 | 3.104e-06
2013 | 2013-01-28 | B | 14 | 0.015297 | 4.3456e-05
2013 | 2013-01-29 | C | 2 | 0.0006953 | 6.2081e-06
2013 | 2013-01-29 | B | 23 | 0.0044263 | 7.1393e-05
2013 | 2013-01-29 | B | 6 | 0.0029612 | 1.8624e-05
2013 | 2013-01-29 | B | 5 | 0.0057425 | 1.552e-05
2013 | 2013-01-29 | B | 25 | 0.022737 | 7.7601e-05
2013 | 2013-01-29 | B | 16 | 0.020511 | 4.9664e-05
2013 | 2013-01-29 | B | 38 | 0.047653 | 0.00011795
2013 | 2013-01-29 | B | 10 | 0.013627 | 3.104e-05
2013 | 2013-01-29 | C | 40.2 | 0.012728 | 0.00049975
2013 | 2013-01-30 | C | 35 | 0.0060839 | 0.00010864
2013 | 2013-01-30 | C | 250.0615 | 0.048124 | 0.00080084
2013 | 2013-01-30 | C | 51.4521 | 0.01118 | 0.00019245
2013 | 2013-01-30 | B | 94 | 0.084324 | 0.00029178
2013 | 2013-01-30 | B | 38 | 0.038571 | 0.00011795
2013 | 2013-01-30 | B | 445 | 0.50832 | 0.0013813
2013 | 2013-01-30 | C | 109 | 0.0054134 | 0.00033834
2013 | 2013-01-30 | C | 5 | 0.00041904 | 1.552e-05
2013 | 2013-01-31 | B | 111 | 0.00379 | 0.00034455
2013 | 2013-01-31 | B | 68 | 0.00063322 | 0.00021107
2013 | 2013-01-31 | B | 25 | 0.019788 | 7.7601e-05
2013 | 2013-01-31 | B | 18 | 0.014918 | 5.5873e-05
2013 | 2013-01-31 | B | 5 | 0.0023125 | 1.552e-05
2013 | 2013-01-31 | B | 6 | 0.0073938 | 1.8624e-05
2013 | 2013-01-31 | B | 16 | 0.018227 | 4.9664e-05
2013 | 2013-01-31 | B | 56 | 0.059796 | 0.00017383
2013 | 2013-01-31 | B | 8 | 0.0077477 | 2.4832e-05
2013 | 2013-01-31 | B | 8 | 0.0013161 | 2.4832e-05
2013 | 2013-01-30 | B | 6 | 0.0082133 | 1.8624e-05
2013 | 2013-02-01 | B | 2 | 0.00022349 | 6.2081e-06
2013 | 2013-02-01 | C | 7 | 0.001999 | 2.1728e-05
2013 | 2013-02-01 | C | 3 | 0.00068909 | 9.3121e-06
2013 | 2013-02-01 | B | 64 | 0.067941 | 0.00019866
2013 | 2013-02-01 | B | 94 | 0.11875 | 0.00029178
2013 | 2013-02-01 | C | 3 | 0.0036969 | 9.3121e-06
2013 | 2013-02-01 | B | 6 | 0.0080456 | 1.8624e-05
2013 | 2013-02-02 | B | 3 | 0.0016203 | 9.3121e-06
2013 | 2013-02-02 | C | 78 | 0.020822 | 0.00024211
2013 | 2013-02-02 | C | 4 | 0.0015272 | 1.2416e-05
2013 | 2013-02-02 | C | 22 | 0.0045753 | 6.8289e-05
2013 | 2013-02-03 | C | 25 | 0.005044 | 7.7601e-05
2013 | 2013-02-04 | C | 70.8074 | 0.058683 | 0.00042836
2013 | 2013-02-04 | C | 33 | 0.00379 | 0.00010864
2013 | 2013-02-04 | C | 7 | 0.0030854 | 2.1728e-05
2013 | 2013-02-04 | C | 778.6154 | 0.27552 | 0.0027812
2013 | 2013-02-04 | B | 1 | 0.00078222 | 3.104e-06
2013 | 2013-02-04 | C | 122 | 0.022343 | 0.00037869
2013 | 2013-02-04 | C | 126.3684 | 0.036087 | 0.0006177
2013 | 2013-02-04 | C | 217.0476 | 0.082868 | 0.0010523
2013 | 2013-02-04 | C | 12 | 0.0047678 | 3.7248e-05
2013 | 2013-02-04 | C | 78.8051 | 0.085859 | 0.00078842
2013 | 2013-02-04 | C | 263.4656 | 0.10468 | 0.0010181
2013 | 2013-02-05 | C | 40 | 0.045319 | 0.00012416
2013 | 2013-02-05 | C | 115 | 0.013208 | 0.00036007
2013 | 2013-02-05 | B | 38 | 0.016513 | 0.00011795
2013 | 2013-02-05 | C | 85.2652 | 0.04711 | 0.00036938
2013 | 2013-02-05 | C | 411 | 0.039548 | 0.0012758
2013 | 2013-02-05 | B | 64 | 0.038142 | 0.00019866
2013 | 2013-02-05 | C | 3 | 0.00072634 | 9.3121e-06
2013 | 2013-02-05 | B | 33 | 0.02274 | 0.00010243
2013 | 2013-02-05 | C | 17 | 0.00073876 | 5.2768e-05
2013 | 2013-02-05 | C | 8 | 0.0030295 | 2.4832e-05
2013 | 2013-02-04 | C | 8 | 0.031934 | 2.4832e-05
2013 | 2013-02-05 | C | 422 | 0.10348 | 0.0013099
2013 | 2013-02-05 | B | 89 | 0.098901 | 0.00027626
2013 | 2013-02-05 | C | 4 | 0.0014527 | 1.2416e-05
2013 | 2013-02-05 | C | 3 | 0.00071703 | 9.3121e-06
2013 | 2013-02-05 | C | 81.75 | 0.09668 | 0.00080394
2013 | 2013-02-05 | C | 18 | 0.0022349 | 5.5873e-05
2013 | 2013-02-05 | C | 76.9429 | 0.32529 | 0.00094362
2013 | 2013-02-05 | C | 97.4089 | 0.067124 | 0.00070151
2013 | 2013-02-05 | C | 134.8919 | 0.060713 | 0.00087223
2013 | 2013-02-05 | C | 131.378 | 0.032216 | 0.00068909
2013 | 2013-02-05 | C | 15 | 0.0041904 | 4.656e-05
2013 | 2013-02-05 | C | 33 | 0.040666 | 0.00010243
2013 | 2013-02-05 | C | 276.9574 | 0.078231 | 0.00099329
2013 | 2013-02-05 | C | 835 | 0.088123 | 0.0025919
2013 | 2013-02-06 | C | 2 | 0.00026695 | 6.2081e-06
2013 | 2013-02-06 | C | 5 | 0.00082257 | 1.552e-05
2013 | 2013-02-05 | C | 4 | 0.0093866 | 1.2416e-05
2013 | 2013-02-06 | C | 3 | 0.0024118 | 9.3121e-06
2013 | 2013-02-06 | C | 66.1093 | 0.074489 | 0.00066737
2013 | 2013-02-06 | C | 399.6923 | 0.30272 | 0.0027657
2013 | 2013-02-05 | C | 3 | 0.0087347 | 9.3121e-06
2013 | 2013-02-05 | C | 2 | 0.0086416 | 6.2081e-06
2013 | 2013-02-04 | C | 54.5336 | 0.17841 | 0.0011361
2013 | 2013-02-05 | C | 3 | 0.0004656 | 9.3121e-06
2013 | 2013-02-05 | C | 5 | 0.0011951 | 1.552e-05
2013 | 2013-02-05 | C | 146.9839 | 0.14007 | 0.0012602
2013 | 2013-02-05 | C | 165.6259 | 0.074031 | 0.00082878
2013 | 2013-02-05 | C | 1 | 0.00024211 | 3.104e-06
2013 | 2013-02-07 | B | 33 | 0.031754 | 0.00010243
2013 | 2013-02-07 | B | 43 | 0.054057 | 0.00013347
2013 | 2013-01-08 | B | 39 | 0.041038 | 0.00012106
2013 | 2013-02-07 | B | 69 | 0.065967 | 0.00021418
2013 | 2013-02-07 | B | 52 | 0.043419 | 0.00016141
2013 | 2013-02-07 | B | 165 | 0.17516 | 0.00051216
2013 | 2013-02-07 | C | 12 | 0.0017134 | 3.7248e-05
2013 | 2013-02-07 | C | 1 | 0.00079463 | 3.104e-06
2013 | 2013-02-07 | B | 9 | 0.011035 | 2.7936e-05
2013 | 2013-02-07 | B | 56 | 0.060317 | 0.00017383
2013 | 2013-02-07 | B | 20 | 0.023839 | 6.2081e-05
2013 | 2013-02-07 | B | 3 | 0.0038645 | 9.3121e-06
2013 | 2013-02-07 | B | 175 | 0.21185 | 0.0005432
2013 | 2013-02-07 | B | 38 | 0.040576 | 0.00011795
2013 | 2013-02-07 | B | 16 | 0.013956 | 4.9664e-05
2013 | 2013-02-08 | C | 3 | 0.0021697 | 9.3121e-06
2013 | 2013-02-07 | B | 6 | 0.0095542 | 1.8624e-05
2013 | 2013-02-01 | B | 7 | 0.001999 | 2.1728e-05
2013 | 2013-02-08 | B | 10 | 0.0043767 | 3.104e-05
2013 | 2013-02-08 | C | 2 | 0.00044077 | 9.3121e-06
2013 | 2013-02-08 | B | 48 | 0.048721 | 0.00014899
2013 | 2013-02-08 | C | 1179 | 1.7786 | 0.0036596
2013 | 2013-02-08 | B | 1 | 0.00074497 | 3.104e-06
2013 | 2013-02-08 | C | 1072.6689 | 0.48279 | 0.0032685
2013 | 2013-02-08 | B | 57 | 0.062279 | 0.00017693
2013 | 2013-02-08 | C | 708.9278 | 0.4203 | 0.00059597
2013 | 2013-02-08 | B | 20.4973 | 0.023605 | 0.00014899
2013 | 2013-02-08 | B | 12 | 0.014378 | 3.7248e-05
2013 | 2013-02-08 | B | 31 | 0.043013 | 9.6225e-05
2013 | 2013-02-08 | B | 59 | 0.06538 | 0.00018314
2013 | 2013-02-08 | C | 81 | 0.016091 | 0.00025143
2013 | 2013-02-09 | C | 3 | 0.0012292 | 9.3121e-06
2013 | 2013-02-09 | C | 261.2462 | 0.050277 | 0.001999
2013 | 2013-02-09 | B | 3 | 0.002626 | 9.3121e-06
2013 | 2013-02-09 | C | 198 | 0.13951 | 0.0006146
2013 | 2013-02-09 | C | 698 | 0.045499 | 0.0021666
2013 | 2013-02-09 | C | 194 | 0.053594 | 0.00060218
2013 | 2013-02-10 | C | 25 | 0.002716 | 7.7601e-05
2013 | 2013-02-10 | C | 230 | 0.028557 | 0.00071393
2013 | 2013-02-10 | B | 5 | 0.0040663 | 1.552e-05
2013 | 2013-02-10 | C | 73 | 0.03127 | 0.0002328
2013 | 2013-02-09 | C | 2 | 0.00081946 | 6.2081e-06
2013 | 2013-02-11 | C | 169 | 0.12642 | 0.00052148
2013 | 2013-02-11 | C | 2 | 0.001968 | 6.2081e-06
2013 | 2013-02-11 | B | 2 | 0.0011982 | 6.2081e-06
2013 | 2013-02-11 | B | 40 | 0.033648 | 0.00012416
2013 | 2013-02-11 | B | 65 | 0.060932 | 0.00020176
2013 | 2013-02-11 | B | 6 | 0.0066488 | 1.8624e-05
2013 | 2013-02-11 | B | 7 | 0.0074093 | 2.1728e-05
2013 | 2013-02-11 | B | 4 | 0.0051403 | 1.2416e-05
2013 | 2013-02-11 | B | 28 | 0.036243 | 8.6913e-05
2013 | 2013-02-11 | B | 34 | 0.039049 | 0.00010554
2013 | 2013-02-11 | C | 107.268 | 0.082242 | 0.0012385
2013 | 2013-02-11 | C | 516.1124 | 0.13777 | 0.0016855
2013 | 2013-02-11 | C | 1143 | 0.14546 | 0.003551
2013 | 2013-02-12 | C | 286 | 0.017755 | 0.00089396
2013 | 2013-02-12 | B | 69 | 0.062112 | 0.00021418
2013 | 2013-02-12 | B | 29 | 0.028175 | 9.0017e-05
2013 | 2013-02-12 | B | 8 | 0.0087409 | 2.4832e-05
2013 | 2013-02-12 | B | 199 | 0.22361 | 0.0006177
2013 | 2013-02-12 | B | 11 | 0.013146 | 3.4144e-05
2013 | 2013-02-12 | B | 71 | 0.040771 | 0.00022039
2013 | 2013-02-12 | B | 16 | 0.016985 | 4.9664e-05
2013 | 2013-02-12 | C | 57 | 0.0069003 | 0.00017693
2013 | 2013-02-12 | B | 60 | 0.07729 | 0.00018624
2013 | 2013-02-12 | B | 57 | 0.06971 | 0.00017693
2013 | 2013-02-12 | B | 60 | 0.0758 | 0.00018624
2013 | 2013-02-12 | B | 175 | 0.21348 | 0.0005432
2013 | 2013-02-12 | B | 4 | 0.0039359 | 1.2416e-05
2013 | 2013-02-12 | C | 16 | 0.0020362 | 4.9664e-05
2013 | 2013-02-13 | C | 383.7966 | 0.137 | 0.003551
2013 | 2013-02-13 | C | 64 | 0.012317 | 0.00019866
2013 | 2013-02-13 | B | 6 | 0.0032779 | 1.8624e-05
2013 | 2013-02-13 | B | 39 | 0.035833 | 0.00012106
2013 | 2013-02-13 | B | 1 | 0.0011143 | 3.104e-06
2013 | 2013-02-13 | B | 60 | 0.076732 | 0.00018624
2013 | 2013-02-13 | C | 75.5696 | 0.017827 | 0.00040663
2013 | 2013-02-13 | C | 5 | 0.00057425 | 1.552e-05
2013 | 2013-02-13 | C | 14.6289 | 0.011488 | 0.0006953
2013 | 2013-02-12 | B | 55 | 0.019974 | 0.00017072
2013 | 2013-02-12 | B | 1 | 0.0014713 | 3.104e-06
2013 | 2013-02-14 | C | 37 | 0.019754 | 0.00011485
2013 | 2013-02-14 | B | 29.1319 | 0.020979 | 0.00014899
2013 | 2013-02-14 | B | 38 | 0.04093 | 0.00011795
2013 | 2013-02-14 | B | 69 | 0.074962 | 0.00021418
2013 | 2013-02-14 | B | 26 | 0.028085 | 8.0705e-05
2013 | 2013-02-14 | B | 53 | 0.05067 | 0.00016451
2013 | 2013-02-14 | B | 28 | 0.031115 | 8.6913e-05
2013 | 2013-02-14 | B | 6 | 0.0085112 | 1.8624e-05
2013 | 2013-02-14 | C | 649.6835 | 0.15326 | 0.0028185
2013 | 2013-02-14 | B | 106 | 0.19413 | 0.00032903
2013 | 2013-02-15 | B | 2 | 0.00073255 | 6.2081e-06
2013 | 2013-02-15 | B | 1 | 0.00027005 | 3.104e-06
2013 | 2013-02-15 | C | 8 | 0.002806 | 2.4832e-05
2013 | 2013-02-15 | B | 4 | 0.003253 | 1.2416e-05
2013 | 2013-02-15 | B | 31 | 0.023094 | 9.6225e-05
2013 | 2013-02-15 | B | 9 | 0.0079339 | 2.7936e-05
2013 | 2013-02-15 | B | 16 | 0.018128 | 4.9664e-05
2013 | 2013-02-15 | B | 12 | 0.01367 | 3.7248e-05
2013 | 2013-02-15 | B | 5 | 0.0066116 | 1.552e-05
2013 | 2013-02-15 | C | 396.9145 | 0.32772 | 0.0013937
2013 | 2013-02-16 | C | 107 | 0.025906 | 0.00033213
2013 | 2013-02-17 | C | 10 | 0.0043767 | 3.104e-05
2013 | 2013-02-17 | C | 102 | 0.10923 | 0.00031661
2013 | 2013-02-17 | B | 171 | 0.052548 | 0.00053079
2013 | 2013-02-17 | C | 2092 | 0.058443 | 0.0064936
2013 | 2013-02-17 | C | 8 | 0.0051651 | 2.4832e-05
2013 | 2013-02-16 | C | 45 | 0.00097777 | 0.00013968
2013 | 2013-02-18 | C | 4 | 0.00034765 | 1.2416e-05
2013 | 2013-02-18 | C | 6 | 0.0026074 | 1.8624e-05
2013 | 2013-02-18 | B | 135 | 0.13409 | 0.00041904
2013 | 2013-02-18 | B | 21 | 0.021315 | 6.5185e-05
2013 | 2013-02-18 | B | 48 | 0.053191 | 0.00014899
2013 | 2013-02-18 | B | 6 | 0.0077663 | 1.8624e-05
2013 | 2013-02-18 | B | 58 | 0.064272 | 0.00018003
2013 | 2013-02-19 | C | 140 | 0.018252 | 0.00043456
2013 | 2013-02-18 | C | 1 | 0.0042805 | 3.104e-06
2013 | 2013-02-19 | C | 168.4898 | 0.10094 | 0.0023963
2013 | 2013-02-19 | B | 39 | 0.034259 | 0.00012106
2013 | 2013-02-19 | B | 65 | 0.0458 | 0.00020176
2013 | 2013-02-19 | B | 15 | 0.014247 | 4.656e-05
2013 | 2013-02-19 | B | 34 | 0.022796 | 0.00010554
2013 | 2013-02-19 | B | 16 | 0.014899 | 4.9664e-05
2013 | 2013-02-19 | B | 44 | 0.048758 | 0.00013658
2013 | 2013-02-19 | C | 55.5 | 0.014643 | 0.00029799
2013 | 2013-02-19 | B | 28 | 0.024509 | 8.6913e-05
2013 | 2013-02-19 | B | 124 | 0.15665 | 0.0003849
2013 | 2013-02-19 | B | 13 | 0.015858 | 4.0352e-05
2013 | 2013-02-19 | B | 77 | 0.076005 | 0.00023901
2013 | 2013-02-19 | C | 4 | 0.00064564 | 1.2416e-05
2013 | 2013-02-20 | C | 45 | 0.0072634 | 0.00013968
2013 | 2013-02-20 | B | 12 | 0.0089769 | 3.7248e-05
2013 | 2013-02-20 | B | 2 | 0.0012851 | 6.2081e-06
2013 | 2013-02-20 | B | 49 | 0.050953 | 0.0001521
2013 | 2013-02-20 | C | 34 | 0.0075987 | 0.00010554
2013 | 2013-02-20 | B | 26 | 0.022355 | 8.0705e-05
2013 | 2013-02-20 | B | 6 | 0.0073565 | 1.8624e-05
2013 | 2013-02-20 | B | 340 | 0.41687 | 0.0010554
2013 | 2013-02-20 | C | 40 | 0.003849 | 0.00012416
2013 | 2013-02-20 | C | 71 | 0.018733 | 0.00022039
2013 | 2013-02-20 | C | 22 | 0.0027998 | 6.8289e-05
2013 | 2013-02-20 | C | 67.1259 | 0.055632 | 0.0013099
2013 | 2013-02-21 | B | 124 | 0.097764 | 0.0003849
2013 | 2013-02-21 | C | 6 | 0.00080084 | 1.8624e-05
2013 | 2013-02-21 | B | 22 | 0.024925 | 6.8289e-05
2013 | 2013-02-21 | B | 41 | 0.044161 | 0.00012727
2013 | 2013-02-21 | B | 171 | 0.21072 | 0.00053079
2013 | 2013-02-21 | C | 1 | 0.00070461 | 3.104e-06
2013 | 2013-02-21 | B | 155 | 0.20255 | 0.00048112
2013 | 2013-02-21 | B | 58 | 0.039067 | 0.00018003
2013 | 2013-02-21 | B | 8 | 0.0092376 | 2.4832e-05
2013 | 2013-02-21 | C | 56 | 0.0095604 | 0.00017383
2013 | 2013-02-21 | B | 136.5826 | 0.14499 | 0.00063322
2013 | 2013-02-22 | B | 6 | 0.0016203 | 1.8624e-05
2013 | 2013-02-22 | B | 303 | 0.05361 | 0.00094052
2013 | 2013-02-20 | B | 37 | 0.04215 | 0.00011485
2013 | 2013-02-22 | B | 3 | 0.0028122 | 9.3121e-06
2013 | 2013-02-22 | B | 22 | 0.027725 | 6.8289e-05
2013 | 2013-02-22 | C | 1 | 0.00019245 | 3.104e-06
2013 | 2013-02-22 | B | 26 | 0.028489 | 8.0705e-05
2013 | 2013-02-22 | C | 434.2574 | 0.1321 | 0.0024832
2013 | 2013-02-25 | C | 8 | 0.00057114 | 2.4832e-05
2013 | 2013-02-23 | C | 4 | 0.00064564 | 1.2416e-05
2013 | 2013-02-24 | B | 11 | 0.0016048 | 3.4144e-05
2013 | 2013-02-25 | C | 21 | 0.0033244 | 6.5185e-05
2013 | 2013-02-24 | B | 53 | 0.0085547 | 0.00016451
2013 | 2013-02-23 | B | 2 | 0.001223 | 6.2081e-06
2013 | 2013-02-24 | C | 1361 | 0.067593 | 0.0042246
2013 | 2013-02-25 | B | 365 | 0.24019 | 0.001133
2013 | 2013-02-25 | B | 108 | 0.10761 | 0.00033524
2013 | 2013-02-25 | B | 4 | 0.0050534 | 1.2416e-05
2013 | 2013-02-25 | B | 2 | 0.0023404 | 6.2081e-06
2013 | 2013-02-25 | C | 183.1603 | 0.22173 | 0.0010181
2013 | 2013-02-24 | C | 246.0233 | 0.063384 | 0.0009995
2013 | 2013-02-23 | C | 33 | 0.011165 | 0.00010243
2013 | 2013-02-23 | C | 8 | 0.0037745 | 2.4832e-05
2013 | 2013-02-26 | C | 5 | 0.0015055 | 1.552e-05
2013 | 2013-02-26 | B | 23 | 0.024488 | 7.1393e-05
2013 | 2013-02-26 | B | 25 | 0.028557 | 7.7601e-05
2013 | 2013-02-26 | B | 10 | 0.008443 | 3.104e-05
2013 | 2013-02-26 | B | 38 | 0.03515 | 0.00011795
2013 | 2013-02-25 | C | 27 | 0.0081295 | 8.3809e-05
2013 | 2013-02-26 | C | 2512 | 0.8655 | 0.0077973
2013 | 2013-02-26 | C | 217.3448 | 0.11536 | 0.0011392
2013 | 2013-02-26 | C | 169.9417 | 0.05275 | 0.00093431
2013 | 2013-02-26 | B | 15 | 0.02179 | 4.656e-05
2013 | 2013-02-26 | B | 4 | 0.0063695 | 1.2416e-05
2013 | 2013-02-26 | B | 155 | 0.23286 | 0.00048112
2013 | 2013-02-26 | B | 97 | 0.08009 | 0.00030109
2013 | 2013-02-27 | B | 138 | 0.15292 | 0.00042836
2013 | 2013-02-26 | C | 1 | 0.00023901 | 3.104e-06
2013 | 2013-02-26 | C | 213 | 0.038347 | 0.00066116
2013 | 2013-02-26 | C | 521.6346 | 0.079339 | 0.0016917
2013 | 2013-02-27 | B | 103 | 0.066501 | 0.00031971
2013 | 2013-02-27 | B | 29 | 0.028085 | 9.0017e-05
2013 | 2013-02-27 | B | 3 | 0.0018624 | 9.3121e-06
2013 | 2013-02-27 | B | 32 | 0.03397 | 9.9329e-05
2013 | 2013-02-27 | B | 7 | 0.0079742 | 2.1728e-05
2013 | 2013-02-27 | B | 107 | 0.1189 | 0.00033213
2013 | 2013-02-27 | B | 4 | 0.0052644 | 1.2416e-05
2013 | 2013-02-27 | B | 40 | 0.045195 | 0.00012416
2013 | 2013-02-27 | B | 2 | 0.0028743 | 6.2081e-06
2013 | 2013-02-27 | C | 11 | 0.0087751 | 3.4144e-05
2013 | 2013-02-27 | C | 568 | 0.10755 | 0.0017631
2013 | 2013-02-27 | C | 240 | 0.071517 | 0.00074497
2013 | 2013-02-28 | C | 121.5799 | 0.062646 | 0.00053079
2013 | 2013-02-28 | C | 28 | 0.0038242 | 8.6913e-05
2013 | 2013-02-27 | C | 3 | 0.002207 | 9.3121e-06
2013 | 2013-02-28 | C | 13 | 0.0047212 | 4.0352e-05
2013 | 2013-02-28 | B | 1 | 0.00018624 | 3.104e-06
2013 | 2013-02-28 | B | 138 | 0.086528 | 0.00042836
2013 | 2013-02-27 | C | 105.0462 | 0.27455 | 0.00045319
2013 | 2013-02-28 | B | 2 | 0.001223 | 6.2081e-06
2013 | 2013-02-28 | B | 54 | 0.011398 | 0.00016762
2013 | 2013-02-28 | B | 15 | 0.014015 | 4.656e-05
2013 | 2013-02-28 | B | 42 | 0.039893 | 0.00013037
2013 | 2013-02-28 | B | 32 | 0.036553 | 9.9329e-05
2013 | 2013-02-28 | B | 28 | 0.03407 | 8.6913e-05
2013 | 2013-03-01 | C | 102.5263 | 0.035325 | 0.00060218
2013 | 2013-03-01 | B | 2 | 0.001372 | 6.2081e-06
2013 | 2013-03-01 | C | 44.2568 | 0.08998 | 0.00036628
2013 | 2013-03-01 | B | 129 | 0.10571 | 0.00040042
2013 | 2013-03-01 | C | 81.4216 | 0.025021 | 0.00056183
2013 | 2013-03-01 | B | 2 | 0.00088154 | 6.2081e-06
2013 | 2013-03-01 | B | 8 | 0.0037497 | 2.4832e-05
2013 | 2013-03-01 | B | 121 | 0.14911 | 0.00037559
2013 | 2013-03-01 | B | 4 | 0.0057362 | 1.2416e-05
2013 | 2013-03-01 | B | 7 | 0.011668 | 2.1728e-05
2013 | 2013-03-02 | C | 9 | 0.0029892 | 2.7936e-05
2013 | 2013-03-02 | B | 14 | 0.010603 | 4.3456e-05
2013 | 2013-03-02 | B | 6 | 0.0060901 | 1.8624e-05
2013 | 2013-03-02 | B | 138 | 0.070679 | 0.00042836
2013 | 2013-03-03 | C | 50.3318 | 0.033434 | 0.00030419
2013 | 2013-03-03 | C | 6 | 0.00048423 | 1.8624e-05
2013 | 2013-03-03 | C | 79 | 0.017901 | 0.00024522
2013 | 2013-03-03 | C | 406.7976 | 0.10228 | 0.0036379
2013 | 2013-03-04 | B | 67 | 0.030572 | 0.00020797
2013 | 2013-03-04 | B | 112 | 0.11021 | 0.00034765
2013 | 2013-03-04 | B | 32 | 0.031587 | 9.9329e-05
2013 | 2013-03-04 | B | 28 | 0.034504 | 8.6913e-05
2013 | 2013-03-04 | B | 1 | 0.00011795 | 3.104e-06
2013 | 2013-03-04 | C | 43 | 0.0049385 | 0.00013347
2013 | 2013-03-04 | B | 2 | 0.0017817 | 6.2081e-06
2013 | 2013-03-04 | B | 4 | 0.0054258 | 1.2416e-05
2013 | 2013-03-04 | B | 3 | 0.0028681 | 9.3121e-06
2013 | 2013-03-04 | B | 3 | 0.0026167 | 9.3121e-06
2013 | 2013-03-04 | C | 1 | 0.00017693 | 3.104e-06
2013 | 2013-03-05 | C | 307.7158 | 0.17193 | 0.0030916
2013 | 2013-03-05 | C | 234 | 0.034138 | 0.00072634
2013 | 2013-03-05 | B | 73 | 0.053703 | 0.00022659
2013 | 2013-03-05 | B | 2 | 0.0020673 | 6.2081e-06
2013 | 2013-03-05 | B | 1 | 0.0012416 | 3.104e-06
2013 | 2013-03-05 | B | 139 | 0.19157 | 0.00043146
2013 | 2013-03-05 | B | 4 | 0.0051651 | 1.2416e-05
2013 | 2013-03-05 | C | 215.8209 | 0.13264 | 0.0010523
2013 | 2013-03-05 | B | 162 | 0.11716 | 0.00050285
2013 | 2013-03-05 | C | 64 | 0.0021852 | 0.00019866
2013 | 2013-03-05 | C | 3 | 0.0013689 | 9.3121e-06
2013 | 2013-03-06 | C | 1 | 0.00017693 | 3.104e-06
2013 | 2013-03-06 | B | 9 | 0.0063136 | 2.7936e-05
2013 | 2013-03-06 | B | 228 | 0.18471 | 0.00070772
2013 | 2013-03-06 | C | 310 | 0.0019245 | 0.00096225
2013 | 2013-03-06 | B | 1 | 0.00077601 | 3.104e-06
2013 | 2013-03-06 | C | 169.4333 | 0.061533 | 0.00073876
2013 | 2013-03-06 | B | 3 | 0.002626 | 9.3121e-06
2013 | 2013-03-06 | B | 2 | 0.0022039 | 6.2081e-06
2013 | 2013-03-06 | B | 6 | 9.3121e-05 | 1.8624e-05
2013 | 2013-03-06 | B | 21 | 0.023662 | 6.5185e-05
2013 | 2013-03-06 | B | 28 | 0.032332 | 8.6913e-05
2013 | 2013-03-06 | B | 5 | 0.0052613 | 1.552e-05
2013 | 2013-03-06 | B | 9 | 0.013242 | 2.7936e-05
2013 | 2013-03-06 | B | 82 | 0.095958 | 0.00025453
2013 | 2013-03-06 | B | 444.0095 | 0.57334 | 0.0014123
2013 | 2013-03-06 | B | 83 | 0.066212 | 0.00025763
2013 | 2013-03-07 | C | 95.8326 | 0.068417 | 0.00034765
2013 | 2013-03-07 | B | 4 | 0.0014527 | 1.2416e-05
2013 | 2013-03-07 | B | 23 | 0.026844 | 7.1393e-05
2013 | 2013-03-07 | B | 1 | 0.0010461 | 3.104e-06
2013 | 2013-03-07 | B | 35 | 0.037155 | 0.00010864
2013 | 2013-03-07 | B | 55 | 0.02595 | 0.00017072
2013 | 2013-03-07 | C | 2 | 0.0008505 | 6.2081e-06
2013 | 2013-03-08 | C | 923 | 0.18909 | 0.002865
2013 | 2013-03-07 | B | 9 | 0.0016482 | 2.7936e-05
2013 | 2013-03-08 | B | 9 | 0.0021232 | 2.7936e-05
2013 | 2013-03-08 | B | 16 | 0.014005 | 4.9664e-05
2013 | 2013-03-08 | B | 57 | 0.068295 | 0.00017693
2013 | 2013-03-08 | B | 4 | 0.0051775 | 1.2416e-05
2013 | 2013-03-08 | B | 1 | 0.0012137 | 3.104e-06
2013 | 2013-03-08 | B | 32 | 0.03546 | 9.9329e-05
2013 | 2013-03-08 | B | 30 | 0.023932 | 9.3121e-05
2013 | 2013-03-08 | B | 139 | 0.17949 | 0.00043146
2013 | 2013-03-08 | C | 60 | 0.0016762 | 0.00018624
2013 | 2013-03-08 | C | 84 | 0.079264 | 0.00026074
2013 | 2013-03-08 | C | 15.2807 | 0.025376 | 0.00012416
2013 | 2013-03-09 | C | 279.9048 | 0.19809 | 0.0030854
2013 | 2013-03-09 | C | 600 | 0.059597 | 0.0018624
2013 | 2013-03-09 | C | 182.9706 | 0.036916 | 0.0017786
2013 | 2013-03-09 | C | 3756.8788 | 0.73467 | 0.011982
2013 | 2013-03-09 | C | 209 | 0.040222 | 0.00064874
2013 | 2013-03-09 | C | 7589.5 | 0.070674 | 0.026512
2013 | 2013-03-09 | C | 2665 | 0.0082722 | 0.0082722
2013 | 2013-03-09 | B | 20 | 0.012851 | 6.2081e-05
2013 | 2013-03-09 | B | 64 | 0.023243 | 0.00019866
2013 | 2013-03-09 | C | 97.6092 | 0.02545 | 0.00078222
2013 | 2013-03-10 | B | 338 | 0.16682 | 0.0010492
2013 | 2013-03-10 | C | 40 | 0.010802 | 0.00012416
2013 | 2013-03-10 | C | 24 | 0.0052893 | 7.4497e-05
2013 | 2013-03-10 | C | 103 | 0.016625 | 0.00031971
2013 | 2013-03-10 | C | 89.1293 | 0.063355 | 0.0010523
2013 | 2013-03-10 | C | 49 | 0.0092779 | 0.0001521
2013 | 2013-03-11 | C | 29 | 0.0038707 | 9.0017e-05
2013 | 2013-03-11 | B | 22 | 0.01236 | 6.8289e-05
2013 | 2013-03-08 | C | 158.7365 | 0.071445 | 0.0021449
2013 | 2013-03-11 | B | 28 | 0.029898 | 8.6913e-05
2013 | 2013-03-11 | C | 4 | 0.0012664 | 1.2416e-05
2013 | 2013-03-11 | C | 724.2449 | 0.10341 | 0.0037404
2013 | 2013-03-11 | B | 16 | 0.019667 | 4.9664e-05
2013 | 2013-03-11 | C | 2 | 0.0013037 | 6.2081e-06
2013 | 2013-03-11 | C | 44 | 0.0028681 | 0.00013658
2013 | 2013-03-11 | C | 879 | 0.057297 | 0.0027284
2013 | 2013-03-11 | C | 226 | 0.014732 | 0.00070461
2013 | 2013-03-11 | C | 100.8889 | 0.032882 | 0.00031661
2013 | 2013-03-12 | B | 19 | 0.0095542 | 5.8977e-05
2013 | 2013-03-12 | B | 11 | 0.0092873 | 3.4144e-05
2013 | 2013-03-12 | B | 41 | 0.029907 | 0.00012727
2013 | 2013-03-12 | B | 23 | 0.028843 | 7.1393e-05
2013 | 2013-03-12 | B | 32 | 0.036354 | 9.9329e-05
2013 | 2013-03-12 | B | 422 | 0.43358 | 0.0013099
2013 | 2013-03-12 | C | 6 | 0.003669 | 1.8624e-05
2013 | 2013-03-12 | C | 1455 | 0.23033 | 0.0045164
2013 | 2013-03-12 | C | 283 | 0.11947 | 0.00087844
2013 | 2013-03-12 | B | 1 | 0.00035386 | 3.104e-06
2013 | 2013-03-13 | C | 2 | 0.0002297 | 6.2081e-06
2013 | 2013-03-13 | B | 34 | 0.034088 | 0.00010554
2013 | 2013-03-13 | B | 57 | 0.065818 | 0.00017693
2013 | 2013-03-13 | B | 1 | 0.00091258 | 3.104e-06
2013 | 2013-03-13 | B | 21 | 0.022358 | 6.5185e-05
2013 | 2013-03-13 | B | 24 | 0.026595 | 7.4497e-05
2013 | 2013-03-13 | B | 52 | 0.057623 | 0.00016141
2013 | 2013-03-13 | B | 139 | 0.16395 | 0.00043146
2013 | 2013-03-13 | B | 21 | 0.014732 | 6.5185e-05
2013 | 2013-03-13 | B | 46 | 0.059256 | 0.00014279
2013 | 2013-03-13 | B | 3 | 0.0030357 | 9.3121e-06
2013 | 2013-03-13 | C | 120 | 0.022721 | 0.00037248
2013 | 2013-03-13 | B | 526 | 0.61717 | 0.0016327
2013 | 2013-03-13 | C | 245 | 0.00076049 | 0.00076049
2013 | 2013-03-07 | B | 23.216 | 0.026807 | 0.00011795
2013 | 2013-03-12 | B | 5 | 0.0045474 | 1.552e-05
2013 | 2013-03-14 | B | 52 | 0.041482 | 0.00016141
2013 | 2013-03-14 | B | 32 | 0.027017 | 9.9329e-05
2013 | 2013-03-14 | B | 15 | 0.011966 | 4.656e-05
2013 | 2013-03-14 | B | 35 | 0.036612 | 0.00010864
2013 | 2013-03-14 | B | 2 | 0.001999 | 6.2081e-06
2013 | 2013-03-14 | C | 4 | 0.00078222 | 1.2416e-05
2013 | 2013-03-14 | C | 11 | 0.00075117 | 3.4144e-05
2013 | 2013-03-15 | B | 123 | 0.04467 | 0.0003818
2013 | 2013-03-15 | B | 1 | 0.00045629 | 3.104e-06
2013 | 2013-03-15 | B | 39 | 0.034138 | 0.00012106
2013 | 2013-03-15 | B | 22 | 0.015843 | 6.8289e-05
2013 | 2013-03-15 | C | 4 | 0.00083188 | 1.2416e-05
2013 | 2013-03-15 | B | 16 | 0.01922 | 4.9664e-05
2013 | 2013-03-15 | C | 292 | 0.064353 | 0.00090638
2013 | 2013-03-15 | B | 19 | 0.019875 | 5.8977e-05
2013 | 2013-03-15 | B | 28 | 0.037459 | 8.6913e-05
2013 | 2013-03-15 | B | 19 | 0.019875 | 5.8977e-05
2013 | 2013-03-16 | B | 2 | 0.00039111 | 6.2081e-06
2013 | 2013-03-16 | B | 70 | 0.018034 | 0.00021728
2013 | 2013-03-16 | B | 236 | 0.071057 | 0.00073255
2013 | 2013-03-16 | B | 3 | 0.00067047 | 9.3121e-06
2013 | 2013-03-16 | B | 22 | 0.0090141 | 6.8289e-05
2013 | 2013-03-16 | B | 9 | 0.004386 | 2.7936e-05
2013 | 2013-03-16 | B | 1 | 0.00034765 | 3.104e-06
2013 | 2013-03-16 | C | 10 | 0.0012106 | 3.104e-05
2013 | 2013-03-16 | B | 24 | 0.032183 | 7.4497e-05
2013 | 2013-03-17 | C | 123 | 0.0064905 | 0.0003818
2013 | 2013-03-17 | C | 1280.8728 | 0.89457 | 0.0042774
2013 | 2013-03-17 | C | 238 | 0.0096039 | 0.00073876
2013 | 2013-03-17 | C | 45 | 0.0086602 | 0.00013968
2013 | 2013-03-17 | C | 1393.507 | 0.29413 | 0.006683
2013 | 2013-03-17 | C | 153 | 0.0099732 | 0.00047492
2013 | 2013-03-17 | C | 34.8204 | 0.035776 | 0.00044077
2013 | 2013-03-17 | C | 118.2706 | 0.092513 | 0.0010398
2013 | 2013-03-17 | C | 303.5238 | 0.13567 | 0.0015023
2013 | 2013-03-17 | C | 293.7273 | 0.25802 | 0.0016482
2013 | 2013-03-17 | C | 1542 | 0.23453 | 0.0047864
2013 | 2013-03-17 | C | 184.012 | 0.093102 | 0.00073876
2013 | 2013-03-17 | C | 345.0424 | 0.17351 | 0.0016576
2013 | 2013-03-17 | C | 202 | 0.040129 | 0.00062701
2013 | 2013-03-17 | B | 29 | 0.023134 | 9.0017e-05
2013 | 2013-03-17 | B | 31.931 | 0.0054513 | 9.6225e-05
2013 | 2013-03-17 | C | 677 | 0.31521 | 0.0039049
2013 | 2013-03-17 | C | 67.8893 | 0.058372 | 0.00096846
2013 | 2013-03-17 | C | 5 | 0.00072945 | 1.552e-05
2013 | 2013-03-17 | C | 1 | 0.00064253 | 3.104e-06
2013 | 2013-03-17 | C | 6 | 0.01678 | 1.8624e-05
2013 | 2013-03-18 | C | 17 | 0.00063322 | 5.2768e-05
2013 | 2013-03-17 | C | 138.7517 | 0.12533 | 0.00099019
2013 | 2013-03-18 | C | 406.5939 | 0.20446 | 0.0026074
2013 | 2013-03-18 | C | 122.957 | 0.10534 | 0.00095914
2013 | 2013-03-14 | C | 3 | 0.0044419 | 9.3121e-06
2013 | 2013-03-18 | C | 719.4237 | 0.25681 | 0.004119
2013 | 2013-03-18 | C | 130.0593 | 0.16229 | 0.0016669
2013 | 2013-03-18 | C | 204 | 0.12158 | 0.00063322
2013 | 2013-03-18 | C | 17 | 0.0092873 | 5.2768e-05
2013 | 2013-03-18 | C | 99.1011 | 0.026455 | 0.00059908
2013 | 2013-03-18 | C | 3 | 0.0077477 | 9.3121e-06
2013 | 2013-03-18 | C | 336.2027 | 0.074094 | 0.0015241
2013 | 2013-02-15 | B | 53 | 0.05758 | 0.00016451
2013 | 2013-03-18 | C | 290 | 0.036907 | 0.00090017
2013 | 2013-03-18 | C | 486.9333 | 0.10882 | 0.0015706
2013 | 2013-03-18 | C | 153.6176 | 0.063419 | 0.00051837
2013 | 2013-03-18 | C | 95 | 0.02595 | 0.00029488
2013 | 2013-03-18 | C | 19 | 0.0057207 | 5.8977e-05
2013 | 2013-03-18 | C | 74 | 0.014012 | 0.0002297
2013 | 2013-03-18 | C | 59.633 | 0.05442 | 0.00060839
2013 | 2013-03-18 | C | 420 | 0.16818 | 0.0026726
2013 | 2013-03-19 | C | 126.1057 | 0.087682 | 0.00056493
2013 | 2013-03-18 | C | 180.72 | 0.026365 | 0.00073565
2013 | 2013-03-18 | C | 13 | 0.0016948 | 4.0352e-05
2013 | 2013-03-18 | C | 261 | 0.0024305 | 0.00081015
2013 | 2013-03-18 | B | 127 | 0.093822 | 0.00039421
2013 | 2013-03-18 | C | 3611.4688 | 0.32509 | 0.010554
2013 | 2013-03-18 | C | 17 | 0.002955 | 5.2768e-05
2013 | 2013-03-19 | C | 290 | 0.014403 | 0.00090017
2013 | 2013-03-19 | C | 16.7037 | 0.008244 | 5.2768e-05
2013 | 2013-03-19 | C | 9 | 0.0036876 | 2.7936e-05
2013 | 2013-03-18 | C | 1 | 0.0027129 | 3.104e-06
2013 | 2013-03-19 | C | 3 | 0.003492 | 9.3121e-06
2013 | 2013-03-19 | C | 1689 | 0.047184 | 0.0052458
2013 | 2013-03-19 | C | 4 | 0.0034393 | 1.2416e-05
2013 | 2013-03-19 | C | 132 | 0.0073752 | 0.00040973
2013 | 2013-03-19 | C | 112 | 0.072311 | 0.00034765
2013 | 2013-03-19 | B | 11 | 0.0064533 | 3.4144e-05
2013 | 2013-03-19 | B | 96 | 0.094462 | 0.00029799
2013 | 2013-03-20 | C | 93 | 0.026558 | 0.00028867
2013 | 2013-03-19 | C | 3 | 0.0023839 | 9.3121e-06
2013 | 2013-03-19 | B | 2 | 0.0011299 | 6.2081e-06
2013 | 2013-03-19 | C | 454.9444 | 0.021182 | 0.0014123
2013 | 2013-03-19 | C | 683.0134 | 0.78655 | 0.0076018
2013 | 2013-03-19 | C | 511 | 0.0031723 | 0.0015862
2013 | 2013-03-20 | C | 397.9896 | 0.23349 | 0.0034889
2013 | 2013-03-20 | C | 194 | 0.022281 | 0.00060218
2013 | 2013-03-19 | C | 29 | 0.010892 | 9.0017e-05
2013 | 2013-03-20 | C | 53 | 0.0026322 | 0.00016451
2013 | 2013-03-19 | C | 2 | 0.0017507 | 6.2081e-06
2013 | 2013-03-19 | C | 52.6235 | 0.052434 | 0.00018935
2013 | 2013-03-18 | C | 5.3673 | 0.013012 | 6.5185e-05
2013 | 2013-03-19 | C | 44 | 0.073479 | 0.00013658
2013 | 2013-03-19 | C | 58.4603 | 0.033752 | 0.00040973
2013 | 2013-03-19 | C | 10 | 0.0073255 | 3.104e-05
2013 | 2013-03-19 | C | 7 | 0.018187 | 2.1728e-05
2013 | 2013-03-19 | C | 10 | 0.0036938 | 3.104e-05
2013 | 2013-03-19 | C | 1 | 0.00041594 | 3.104e-06
2013 | 2013-03-20 | B | 176 | 0.1628 | 0.00054631
2013 | 2013-03-19 | C | 4 | 0.012652 | 1.2416e-05
2013 | 2013-03-20 | C | 1 | 0.00014589 | 3.104e-06
2013 | 2013-03-20 | C | 1 | 0.00054631 | 3.104e-06
2013 | 2013-03-21 | C | 897 | 0.12529 | 0.0027843
2013 | 2013-03-20 | B | 7.8 | 0.0011379 | 3.4144e-05
2013 | 2013-03-20 | C | 445.4706 | 0.066372 | 0.0018407
2013 | 2013-03-21 | C | 57 | 0.0054848 | 0.00017693
2013 | 2013-03-21 | B | 6 | 0.0039483 | 1.8624e-05
2013 | 2013-03-21 | C | 70 | 0.028247 | 0.00021728
2013 | 2013-03-21 | C | 996 | 0.1113 | 0.0030916
2013 | 2013-03-21 | B | 6 | 0.00203 | 1.8624e-05
2013 | 2013-03-21 | B | 9 | 0.0095542 | 2.7936e-05
2013 | 2013-03-21 | B | 5 | 0.0028867 | 1.552e-05
2013 | 2013-03-21 | B | 57 | 0.057502 | 0.00017693
2013 | 2013-03-21 | B | 5 | 0.0067978 | 1.552e-05
2013 | 2013-03-21 | B | 6 | 0.0027191 | 1.8624e-05
2013 | 2013-03-21 | B | 49 | 0.035591 | 0.0001521
2013 | 2013-03-20 | C | 2 | 0.0071889 | 6.2081e-06
2013 | 2013-03-18 | C | 1 | 0.0016762 | 3.104e-06
2013 | 2013-03-21 | C | 1 | 0.0033896 | 3.104e-06
2013 | 2013-03-21 | C | 1 | 0.0037869 | 3.104e-06
2013 | 2013-03-22 | B | 8 | 0.0047678 | 2.4832e-05
2013 | 2013-03-22 | C | 88 | 0.0062826 | 0.00027315
2013 | 2013-03-23 | C | 52 | 0.00032282 | 0.00016141
2013 | 2013-03-24 | C | 416 | 0.018078 | 0.0012913
2013 | 2013-03-24 | C | 177 | 0.025273 | 0.00054941
2013 | 2013-03-24 | B | 29 | 0.0018003 | 9.0017e-05
2013 | 2013-03-24 | C | 24 | 0.0051403 | 7.4497e-05
2013 | 2013-03-25 | C | 3 | 0.00045629 | 9.3121e-06
2013 | 2013-03-19 | B | 1 | 0.0001552 | 3.104e-06
2013 | 2013-03-20 | B | 4 | 0.00028557 | 1.2416e-05
2013 | 2013-03-22 | B | 3 | 0.00053079 | 9.3121e-06
2013 | 2013-03-22 | B | 1 | 0.00057425 | 3.104e-06
2013 | 2013-03-25 | B | 2 | 0.0011919 | 6.2081e-06
2013 | 2013-03-25 | B | 9 | 0.0082691 | 2.7936e-05
2013 | 2013-03-25 | C | 5 | 0.0062236 | 1.552e-05
2013 | 2013-03-25 | B | 4 | 0.0053389 | 1.2416e-05
2013 | 2013-03-25 | B | 319 | 0.35647 | 0.00099019
2013 | 2013-03-25 | B | 16 | 0.014353 | 4.9664e-05
2013 | 2013-03-26 | C | 202 | 0.034486 | 0.00062701
2013 | 2013-03-16 | B | 52 | 0.0087161 | 0.00016141
2013 | 2013-03-26 | B | 61 | 0.010793 | 0.00018935
2013 | 2013-03-22 | B | 52 | 0.011137 | 0.00016141
2013 | 2013-03-26 | B | 28 | 0.033201 | 8.6913e-05
2013 | 2013-03-18 | C | 2 | 0.00057114 | 6.2081e-06
2013 | 2013-03-26 | B | 20 | 0.012106 | 6.2081e-05
2013 | 2013-03-26 | B | 230 | 0.20989 | 0.00071393
2013 | 2013-03-26 | C | 8 | 0.0012168 | 2.4832e-05
2013 | 2013-03-26 | B | 22 | 0.020623 | 6.8289e-05
2013 | 2013-03-26 | B | 24 | 0.016911 | 7.4497e-05
2013 | 2013-03-26 | C | 3 | 3.7248e-05 | 9.3121e-06
2013 | 2013-03-26 | B | 116.9253 | 0.1009 | 0.00048423
2013 | 2013-03-26 | B | 13 | 0.0089582 | 4.0352e-05
2013 | 2013-03-26 | B | 47 | 0.059231 | 0.00014589
2013 | 2013-03-26 | B | 2 | 0.0023094 | 6.2081e-06
2013 | 2013-03-26 | B | 1 | 0.0010057 | 3.104e-06
2013 | 2013-03-26 | C | 126.7202 | 0.064902 | 0.0008443
2013 | 2013-03-27 | B | 3 | 0.0012199 | 9.3121e-06
2013 | 2013-03-27 | B | 1 | 0.00070461 | 3.104e-06
2013 | 2013-03-27 | B | 2 | 0.0008505 | 6.2081e-06
2013 | 2013-03-27 | B | 62 | 0.066588 | 0.00019245
2013 | 2013-03-27 | C | 33 | 0.01178 | 0.00010243
2013 | 2013-03-27 | B | 78 | 0.10217 | 0.00024211
2013 | 2013-03-27 | B | 2 | 0.0010926 | 6.2081e-06
2013 | 2013-03-27 | B | 2 | 0.00044698 | 6.2081e-06
2013 | 2013-03-27 | C | 3 | 0.0010895 | 9.3121e-06
2013 | 2013-03-27 | C | 2 | 0.00014899 | 6.2081e-06
2013 | 2013-03-27 | B | 303 | 0.26993 | 0.00094052
2013 | 2013-03-27 | C | 513.8889 | 0.13878 | 0.0017755
2013 | 2013-03-27 | B | 3 | 0.0024956 | 9.3121e-06
2013 | 2013-03-28 | B | 69 | 0.065753 | 0.00021418
2013 | 2013-03-28 | B | 3 | 0.0013968 | 9.3121e-06
2013 | 2013-03-14 | B | 90 | 0.064533 | 0.00027936
2013 | 2013-03-28 | B | 57 | 0.057856 | 0.00017693
2013 | 2013-03-28 | B | 36 | 0.038887 | 0.00011175
2013 | 2013-03-28 | C | 4 | 0.0019866 | 1.2416e-05
2013 | 2013-03-29 | C | 94 | 0.011088 | 0.00029178
2013 | 2013-03-28 | C | 19 | 0.0016513 | 5.8977e-05
2013 | 2013-03-29 | C | 99 | 0.0089117 | 0.0003073
2013 | 2013-03-28 | B | 571 | 0.24459 | 0.0017724
2013 | 2013-03-28 | B | 1 | 0.001043 | 3.104e-06
2013 | 2013-03-28 | C | 202 | 0.12791 | 0.00062701
2013 | 2013-03-30 | C | 154.2564 | 0.073259 | 0.00073255
2013 | 2013-03-28 | C | 94 | 0.018966 | 0.00029178
2013 | 2013-03-28 | C | 33.4602 | 0.046634 | 0.00033524
2013 | 2013-03-28 | C | 226 | 0.010523 | 0.00070151
2013 | 2013-03-28 | C | 481 | 0.031354 | 0.001493
2013 | 2013-03-28 | C | 867 | 0.056515 | 0.0026912
2013 | 2013-03-31 | C | 94.219 | 0.029831 | 0.00036007
2013 | 2013-03-31 | C | 54.8872 | 0.022148 | 0.00040973
2013 | 2013-03-31 | C | 194.5954 | 0.077316 | 0.00099329
2013 | 2013-03-31 | C | 116 | 0.0079215 | 0.00036007
2013 | 2013-03-31 | C | 123.2437 | 0.13542 | 0.00042836
2013 | 2013-03-08 | B | 1 | 0.0089334 | 3.104e-06
2013 | 2013-03-31 | C | 3 | 0.0042742 | 9.3121e-06
2014 | 2013-04-01 | C | 271.8 | 0.085384 | 0.0020358
2014 | 2013-04-02 | B | 26 | 0.009449 | 8.0076e-05
2014 | 2013-04-02 | B | 5 | 0.00084696 | 1.5399e-05
2014 | 2013-04-02 | B | 14 | 0.0030182 | 4.3118e-05
2014 | 2013-04-01 | C | 9.3341 | 0.024177 | 8.3156e-05
2014 | 2013-04-02 | C | 13 | 0.0068865 | 3.6958e-05
2014 | 2013-04-02 | B | 49 | 0.041048 | 0.00015091
2014 | 2013-04-02 | B | 6 | 0.006135 | 1.8479e-05
2014 | 2013-04-02 | B | 15 | 0.022498 | 4.6198e-05
2014 | 2013-04-02 | B | 69 | 0.061415 | 0.00021251
2014 | 2013-04-02 | C | 179 | 0.020398 | 0.00055129
2014 | 2013-04-02 | C | 516.6316 | 0.17662 | 0.0017894
2014 | 2013-04-03 | C | 317 | 0.012692 | 0.00097631
2014 | 2013-04-03 | C | 1 | 4.9277e-05 | 3.0798e-06
2014 | 2013-04-03 | C | 11 | 0.0021343 | 3.3878e-05
2014 | 2013-04-03 | B | 7 | 0.0018756 | 2.1559e-05
2014 | 2013-04-03 | B | 13 | 0.01069 | 4.0038e-05
2014 | 2013-04-03 | B | 4 | 0.0016631 | 1.2319e-05
2014 | 2013-04-03 | C | 233 | 0.027269 | 0.0007176
2014 | 2013-04-03 | B | 11 | 0.0059965 | 3.3878e-05
2014 | 2013-04-03 | B | 7 | 0.0065108 | 2.1559e-05
2014 | 2013-04-03 | B | 7 | 0.00733 | 2.1559e-05
2014 | 2013-04-03 | B | 9 | 0.0097015 | 2.7719e-05
2014 | 2013-04-03 | C | 573.7647 | 0.024739 | 0.0030367
2014 | 2013-04-03 | B | 36 | 0.039582 | 0.00011087
2014 | 2013-04-03 | B | 48 | 0.058098 | 0.00014783
2014 | 2013-04-03 | B | 26 | 0.03115 | 8.0076e-05
2014 | 2013-04-03 | B | 6 | 0.0060426 | 1.8479e-05
2014 | 2013-04-03 | C | 20 | 0.0097323 | 6.1597e-05
2014 | 2013-04-03 | B | 161 | 0.18743 | 0.00049585
2014 | 2013-04-03 | C | 31.5119 | 0.016014 | 0.00020019
2014 | 2013-04-03 | C | 149.9425 | 0.10298 | 0.00049277
2014 | 2013-04-03 | C | 157.7349 | 0.079185 | 0.0012443
2014 | 2013-04-03 | C | 57.7544 | 0.029883 | 0.0003511
2014 | 2013-04-04 | B | 17 | 0.013351 | 5.2357e-05
2014 | 2013-04-04 | B | 5 | 0.0051433 | 1.5399e-05
2014 | 2013-04-04 | C | 483.8821 | 0.41281 | 0.0087098
2014 | 2013-04-04 | B | 2 | 0.0016754 | 6.1597e-06
2014 | 2013-04-04 | B | 6 | 0.0063198 | 1.8479e-05
2014 | 2013-04-05 | C | 3 | 0.00024947 | 9.2395e-06
2014 | 2013-04-05 | B | 4 | 0.00051741 | 1.2319e-05
2014 | 2013-04-05 | B | 1 | 9.2395e-06 | 3.0798e-06
2014 | 2013-04-05 | C | 4 | 0.0017001 | 1.2319e-05
2014 | 2013-04-05 | C | 62 | 0.033798 | 0.00019095
2014 | 2013-04-05 | C | 37 | 0.0045582 | 0.00011395
2014 | 2013-04-06 | B | 22 | 0.0048785 | 6.7757e-05
2014 | 2013-04-06 | C | 1284.3103 | 0.33226 | 0.0066709
2014 | 2013-04-05 | C | 2 | 0.00028335 | 6.1597e-06
2014 | 2013-04-05 | C | 238 | 0.027854 | 0.000733
2014 | 2013-04-07 | B | 29 | 0.020543 | 8.9315e-05
2014 | 2013-04-07 | B | 12 | 0.011864 | 3.6958e-05
2014 | 2013-04-07 | C | 125 | 0.062752 | 0.00066833
2014 | 2013-04-07 | C | 904 | 0.0083525 | 0.0027842
2014 | 2013-04-07 | C | 188.8684 | 0.13088 | 0.001543
2014 | 2013-04-08 | B | 2 | 0.00066525 | 6.1597e-06
2014 | 2013-04-08 | C | 4 | 0.00097323 | 1.2319e-05
2014 | 2013-04-08 | B | 287 | 0.13524 | 0.00088391
2014 | 2013-04-08 | B | 6 | 0.0077058 | 1.8479e-05
2014 | 2013-04-08 | B | 57 | 0.067938 | 0.00017555
2014 | 2013-04-08 | B | 50 | 0.068372 | 0.00015399
2014 | 2013-04-09 | B | 3 | 0.0016908 | 9.2395e-06
2014 | 2013-04-09 | C | 233.0098 | 0.071046 | 0.00091779
2014 | 2013-04-09 | B | 339 | 0.38526 | 0.0010441
2014 | 2013-04-09 | B | 6 | 0.0058394 | 1.8479e-05
2014 | 2013-04-09 | B | 17 | 0.01555 | 5.2357e-05
2014 | 2013-04-09 | B | 131 | 0.14686 | 0.00040346
2014 | 2013-04-09 | B | 37 | 0.033844 | 0.00011395
2014 | 2013-04-09 | C | 9 | 0.0020789 | 2.7719e-05
2014 | 2013-04-09 | B | 31 | 0.037426 | 9.5475e-05
2014 | 2013-04-09 | C | 80 | 0.007638 | 0.00024639
2014 | 2013-04-10 | C | 581 | 0.025051 | 0.0017894
2014 | 2013-04-10 | B | 52 | 0.016015 | 0.00016015
2014 | 2013-04-10 | B | 40 | 0.012566 | 0.00012319
2014 | 2013-04-10 | B | 62 | 0.057094 | 0.00019095
2014 | 2013-04-10 | B | 11 | 0.0094859 | 3.3878e-05
2014 | 2013-04-10 | C | 29 | 0.0075025 | 8.9315e-05
2014 | 2013-04-10 | C | 96 | 0.027201 | 0.00029566
2014 | 2013-04-11 | C | 1539.0952 | 0.28441 | 0.0057162
2014 | 2013-04-11 | B | 62 | 0.064732 | 0.00019095
2014 | 2013-04-11 | B | 37 | 0.036351 | 0.00011395
2014 | 2013-04-11 | B | 54 | 0.061702 | 0.00016631
2014 | 2013-04-11 | B | 9 | 0.011143 | 2.7719e-05
2014 | 2013-04-11 | B | 14 | 0.015609 | 4.3118e-05
2014 | 2013-04-11 | C | 14 | 0.0046136 | 4.3118e-05
2014 | 2013-04-11 | B | 28 | 0.031562 | 8.6236e-05
2014 | 2013-04-11 | B | 3 | 0.001081 | 9.2395e-06
2014 | 2013-04-11 | B | 9 | 0.0040746 | 2.7719e-05
2014 | 2013-04-11 | C | 26 | 0.0065662 | 8.0076e-05
2014 | 2013-04-11 | C | 113.7065 | 0.095604 | 0.00072068
2014 | 2013-04-12 | C | 82.675 | 0.019606 | 0.00026795
2014 | 2013-04-12 | C | 828.1395 | 0.32137 | 0.004127
2014 | 2013-04-12 | B | 5 | 0.0010009 | 1.5399e-05
2014 | 2013-04-12 | B | 3 | 0.00066525 | 9.2395e-06
2014 | 2013-04-12 | B | 6 | 0.0054513 | 1.8479e-05
2014 | 2013-04-12 | B | 55 | 0.0166 | 0.00016939
2014 | 2013-04-12 | C | 31 | 0.013748 | 9.5475e-05
2014 | 2013-04-13 | B | 82 | 0.071218 | 0.00025255
2014 | 2013-04-13 | C | 7 | 0.0011857 | 2.1559e-05
2014 | 2013-04-14 | C | 659.6571 | 0.13612 | 0.0034617
2014 | 2013-04-14 | C | 60.7291 | 0.093331 | 0.0010687
2014 | 2013-04-13 | C | 431.8305 | 0.15295 | 0.0031599
2014 | 2013-04-14 | B | 12 | 0.010422 | 3.6958e-05
2014 | 2013-04-13 | C | 104.377 | 0.038254 | 0.00052049
2014 | 2013-04-14 | C | 577.5 | 0.040908 | 0.0029844
2014 | 2013-04-13 | B | 105 | 0.038159 | 0.00032338
2014 | 2013-04-14 | B | 144 | 0.043019 | 0.0004435
2014 | 2013-04-13 | C | 3 | 0.00051741 | 9.2395e-06
2014 | 2013-04-15 | C | 1412.3333 | 0.11744 | 0.0044011
2014 | 2013-04-15 | C | 245 | 0.036219 | 0.00075456
2014 | 2013-04-15 | C | 157.9032 | 0.013617 | 0.00083772
2014 | 2013-04-15 | B | 10 | 0.007176 | 3.0798e-05
2014 | 2013-04-15 | B | 22 | 0.011722 | 6.7757e-05
2014 | 2013-04-15 | B | 28 | 0.024146 | 8.6236e-05
2014 | 2013-04-15 | C | 3 | 0.0024208 | 9.2395e-06
2014 | 2013-04-16 | C | 120.2606 | 0.060002 | 0.0007176
2014 | 2013-04-16 | C | 189 | 0.020373 | 0.00058209
2014 | 2013-04-15 | C | 226 | 0.014617 | 0.00069604
2014 | 2013-04-15 | C | 481 | 0.037035 | 0.0014814
2014 | 2013-04-15 | C | 867 | 0.082777 | 0.0026702
2014 | 2013-04-15 | C | 17 | 0.0036127 | 5.2357e-05
2014 | 2013-04-15 | C | 22 | 0.012535 | 6.7757e-05
2014 | 2013-04-16 | C | 180.0559 | 0.087618 | 0.0012597
2014 | 2013-04-16 | C | 804.17 | 0.24024 | 0.0051926
2014 | 2013-04-16 | C | 125.7133 | 0.054205 | 0.00065601
2014 | 2013-04-12 | C | 407.0319 | 0.46759 | 0.0030398
2014 | 2013-04-16 | C | 177 | 0.025621 | 0.00054513
2014 | 2013-04-16 | C | 146 | 0.036422 | 0.00045274
2014 | 2013-04-16 | C | 89 | 0.0035634 | 0.00027411
2014 | 2013-04-16 | C | 31 | 0.013176 | 9.5475e-05
2014 | 2013-04-15 | C | 25.9282 | 0.065401 | 0.00057593
2014 | 2013-04-16 | C | 50 | 0.00061597 | 0.00015399
2014 | 2013-04-16 | C | 23 | 0.0094212 | 7.0836e-05
2014 | 2013-04-16 | C | 237.2017 | 0.084743 | 0.0012658
2014 | 2013-04-16 | C | 255.3208 | 0.20602 | 0.00089007
2014 | 2013-04-16 | C | 200.4 | 0.059868 | 0.00094243
2014 | 2013-04-16 | C | 4 | 0.00024639 | 1.2319e-05
2014 | 2013-04-16 | B | 13 | 0.013893 | 4.0038e-05
2014 | 2013-04-16 | B | 45 | 0.049062 | 0.00013859
2014 | 2013-04-12 | B | 4 | 0.0007022 | 1.2319e-05
2014 | 2013-04-12 | B | 4 | 0.0007022 | 1.2319e-05
2014 | 2013-04-16 | C | 260 | 0.040839 | 0.00080076
2014 | 2013-04-16 | C | 17 | 0.00099479 | 5.2357e-05
2014 | 2013-04-16 | C | 307 | 0.011346 | 0.00094551
2014 | 2013-04-16 | C | 675.6667 | 0.0437 | 0.0032585
2014 | 2013-04-16 | C | 23 | 0.0054544 | 7.0836e-05
2014 | 2013-04-17 | C | 109 | 0.0053712 | 0.0003357
2014 | 2013-04-17 | C | 177.7279 | 0.078822 | 0.00084388
2014 | 2013-04-17 | C | 6 | 0.0017001 | 1.8479e-05
2014 | 2013-04-17 | C | 12 | 0.0010348 | 3.6958e-05
2014 | 2013-04-17 | C | 653.1053 | 0.10862 | 0.0035079
2014 | 2013-04-17 | C | 132.375 | 0.054223 | 0.00088699
2014 | 2013-04-17 | C | 521.8305 | 0.090001 | 0.0017617
2014 | 2013-04-17 | C | 5 | 0.00063137 | 1.5399e-05
2014 | 2013-04-17 | C | 43.1824 | 0.019284 | 0.00041578
2014 | 2013-04-17 | B | 71 | 0.071723 | 0.00021867
2014 | 2013-04-17 | B | 35 | 0.028889 | 0.00010779
2014 | 2013-04-17 | C | 9 | 0.00060981 | 2.7719e-05
2014 | 2013-04-17 | B | 57 | 0.065832 | 0.00017555
2014 | 2013-04-17 | C | 9 | 0.0042132 | 2.7719e-05
2014 | 2013-04-17 | C | 390 | 0.030028 | 0.0012011
2014 | 2013-04-17 | B | 3 | 0.0014044 | 9.2395e-06
2014 | 2013-04-17 | C | 3 | 0.00052665 | 9.2395e-06
2014 | 2013-04-17 | C | 22 | 0.0035233 | 6.7757e-05
2014 | 2013-04-17 | C | 36.4352 | 0.021321 | 0.00028951
2014 | 2013-04-18 | B | 5 | 0.0011087 | 1.5399e-05
2014 | 2013-04-18 | B | 35 | 0.0035572 | 0.00010779
2014 | 2013-04-17 | C | 40 | 0.10398 | 0.00012319
2014 | 2013-04-17 | C | 12.8137 | 0.043095 | 0.00016323
2014 | 2013-04-18 | B | 1 | 0.00038806 | 3.0798e-06
2014 | 2013-04-18 | B | 70 | 0.082355 | 0.00021559
2014 | 2013-04-18 | B | 3 | 0.0010533 | 9.2395e-06
2014 | 2013-04-18 | B | 35 | 0.040962 | 0.00010779
2014 | 2013-04-18 | B | 14 | 0.011426 | 4.3118e-05
2014 | 2013-04-18 | C | 67 | 0.013619 | 0.00020635
2014 | 2013-04-18 | C | 684 | 0.13061 | 0.0021066
2014 | 2013-04-19 | B | 2 | 0.00019711 | 6.1597e-06
2014 | 2013-04-19 | C | 10 | 0.0017247 | 3.0798e-05
2014 | 2013-04-19 | C | 1 | 0.00081616 | 3.0798e-06
2014 | 2013-04-18 | C | 418.5123 | 0.41375 | 0.0026086
2014 | 2013-04-19 | B | 19 | 0.016794 | 5.8517e-05
2014 | 2013-04-19 | B | 29 | 0.029563 | 8.9315e-05
2014 | 2013-04-19 | B | 28 | 0.030786 | 8.6236e-05
2014 | 2013-04-19 | B | 9 | 0.0062921 | 2.7719e-05
2014 | 2013-04-19 | B | 5.5829 | 0.0061728 | 4.3118e-05
2014 | 2013-04-19 | C | 9 | 0.0039915 | 2.7719e-05
2014 | 2013-04-19 | C | 609.0857 | 0.12568 | 0.0064122
2014 | 2013-04-19 | C | 381.0236 | 0.14551 | 0.0026795
2014 | 2013-04-20 | C | 10 | 0.0057593 | 3.0798e-05
2014 | 2013-04-20 | C | 39 | 0.0039638 | 0.00012011
2014 | 2013-04-20 | C | 146.2413 | 0.25628 | 0.001272
2014 | 2013-04-20 | C | 86 | 0.045822 | 0.00026487
2014 | 2013-04-20 | C | 6 | 0.010644 | 1.8479e-05
2014 | 2013-04-20 | C | 1 | 0.0024485 | 3.0798e-06
2014 | 2013-04-21 | C | 7 | 0.00099171 | 2.1559e-05
2014 | 2013-04-21 | B | 1 | 0.00064985 | 3.0798e-06
2014 | 2013-04-20 | C | 35 | 0.0567 | 0.00010779
2014 | 2013-04-21 | C | 3 | 0.00048046 | 9.2395e-06
2014 | 2013-04-21 | C | 286.2239 | 0.056418 | 0.0010872
2014 | 2013-04-21 | C | 224.1221 | 0.088353 | 0.0013613
2014 | 2013-04-21 | C | 1 | 0.00026795 | 3.0798e-06
2014 | 2013-04-21 | C | 97 | 0.096196 | 0.00029874
2014 | 2013-04-21 | C | 45 | 0.0022175 | 0.00013859
2014 | 2013-04-21 | C | 485.4894 | 0.20634 | 0.007253
2014 | 2013-04-21 | C | 252.7956 | 0.38617 | 0.00078536
2014 | 2013-04-20 | C | 266.1704 | 0.10821 | 0.00094859
2014 | 2013-04-21 | C | 118.4778 | 0.097426 | 0.0014537
2014 | 2013-04-22 | C | 108 | 0.076171 | 0.00033262
2014 | 2013-04-22 | C | 172.2864 | 0.22074 | 0.00072992
2014 | 2013-04-21 | C | 5 | 0.0038652 | 1.5399e-05
2014 | 2013-04-22 | C | 6 | 0.00088699 | 1.8479e-05
2014 | 2013-04-21 | C | 2 | 0.00028335 | 6.1597e-06
2014 | 2013-04-21 | C | 2 | 0.00044966 | 6.1597e-06
2014 | 2013-04-22 | C | 986.3095 | 0.24605 | 0.0063784
2014 | 2013-04-22 | B | 109 | 0.047334 | 0.0003357
2014 | 2013-04-22 | B | 62 | 0.031125 | 0.00019095
2014 | 2013-04-22 | C | 16 | 0.0090671 | 4.9277e-05
2014 | 2013-04-22 | B | 419 | 0.074846 | 0.0012905
2014 | 2013-04-22 | C | 1 | 0.00026179 | 3.0798e-06
2014 | 2013-04-17 | B | 28 | 0.032338 | 8.6236e-05
2014 | 2013-04-17 | B | 35 | 0.038483 | 0.00010779
2014 | 2013-04-10 | B | 64 | 0.032129 | 0.00019711
2014 | 2013-04-17 | B | 45 | 0.014414 | 0.00013859
2014 | 2013-04-22 | C | 982 | 0.090732 | 0.0030244
2014 | 2013-04-22 | C | 3 | 0.00057285 | 9.2395e-06
2014 | 2013-04-22 | C | 3 | 0.00093319 | 9.2395e-06
2014 | 2013-04-22 | C | 7 | 0.002199 | 2.1559e-05
2014 | 2013-04-22 | C | 4 | 0.0022298 | 1.2319e-05
2014 | 2013-04-22 | B | 65 | 0.08408 | 0.00020019
2014 | 2013-04-22 | B | 69 | 0.035489 | 0.00021251
2014 | 2013-04-22 | B | 5 | 0.00087775 | 1.5399e-05
2014 | 2013-04-22 | C | 1 | 0.00061597 | 3.0798e-06
2014 | 2013-04-22 | C | 94 | 0.1077 | 0.00028951
2014 | 2013-04-22 | C | 286.519 | 0.13678 | 0.00090547
2014 | 2013-04-23 | C | 1 | 0.00036958 | 3.0798e-06
2014 | 2013-04-23 | B | 1 | 0.00023715 | 3.0798e-06
2014 | 2013-04-23 | C | 81.342 | 0.047599 | 0.0008408
2014 | 2013-04-23 | B | 71 | 0.040235 | 0.00021867
2014 | 2013-04-23 | B | 31 | 0.026924 | 9.5475e-05
2014 | 2013-04-23 | B | 40 | 0.034741 | 0.00012319
2014 | 2013-04-23 | B | 65 | 0.080476 | 0.00020019
2014 | 2013-04-23 | B | 143 | 0.17661 | 0.00044042
2014 | 2013-04-23 | C | 38 | 0.0012874 | 0.00011703
2014 | 2013-04-24 | C | 91.4603 | 0.10563 | 0.00085928
2014 | 2013-04-24 | C | 40 | 0.0030798 | 0.00012319
2014 | 2013-04-24 | C | 33 | 0.018294 | 0.00010163
2014 | 2013-04-24 | C | 35 | 0.00043118 | 0.00010779
2014 | 2013-04-24 | C | 432 | 0.035923 | 0.0013305
2014 | 2013-04-24 | B | 87 | 0.099944 | 0.00026795
2014 | 2013-04-24 | B | 4 | 0.005322 | 1.2319e-05
2014 | 2013-04-24 | C | 6 | 0.0012751 | 1.8479e-05
2014 | 2013-04-24 | B | 35 | 0.03126 | 0.00010779
2014 | 2013-04-24 | B | 40 | 0.037204 | 0.00012319
2014 | 2013-04-22 | C | 1 | 0.00010163 | 3.0798e-06
2014 | 2013-04-24 | C | 9 | 0.0004435 | 2.7719e-05
2014 | 2013-04-25 | C | 78 | 0.023783 | 0.00024023
2014 | 2013-04-24 | C | 216.9903 | 0.61951 | 0.0036804
2014 | 2013-04-25 | C | 161 | 0.15124 | 0.00049585
2014 | 2013-04-25 | C | 5.5288 | 0.0088035 | 1.8479e-05
2014 | 2013-04-25 | C | 94.6857 | 0.060365 | 0.00042194
2014 | 2013-04-26 | B | 53 | 0.012569 | 0.00016323
2014 | 2013-04-26 | B | 90 | 0.097847 | 0.00027719
2014 | 2013-04-26 | B | 98 | 0.035313 | 0.00030182
2014 | 2013-04-26 | B | 4 | 0.0023653 | 1.2319e-05
2014 | 2013-04-26 | C | 15 | 0.003049 | 4.6198e-05
2014 | 2013-04-26 | C | 90 | 0.031045 | 0.00027719
2014 | 2013-04-26 | C | 117 | 0.016215 | 0.00035418
2014 | 2013-04-26 | C | 1258 | 0.32545 | 0.0038744
2014 | 2013-04-24 | C | 657.8065 | 0.11953 | 0.0020389
2014 | 2013-04-26 | C | 140.5702 | 0.051086 | 0.00062829
2014 | 2013-04-26 | C | 602 | 0.17984 | 0.0018541
2014 | 2013-04-27 | C | 2 | 0.0010102 | 6.1597e-06
2014 | 2013-04-27 | C | 22 | 0.013822 | 6.7757e-05
2014 | 2013-04-26 | C | 169.8375 | 0.272 | 0.0015584
2014 | 2013-04-28 | C | 11 | 0.0026764 | 3.3878e-05
2014 | 2013-04-28 | C | 6 | 0.00060981 | 2.1559e-05
2014 | 2013-04-26 | C | 259.9513 | 0.17854 | 0.0011734
2014 | 2013-04-28 | C | 39.3443 | 0.021811 | 0.00029566
2014 | 2013-04-21 | C | 3 | 0.0007022 | 9.2395e-06
2014 | 2013-04-21 | C | 9 | 0.0026333 | 2.7719e-05
2014 | 2013-04-29 | B | 24 | 0.024836 | 7.3916e-05
2014 | 2013-04-29 | C | 16 | 0.0024639 | 4.9277e-05
2014 | 2013-04-29 | C | 31 | 0.0064923 | 9.5475e-05
2014 | 2013-04-30 | C | 124.4607 | 0.10618 | 0.0016662
2014 | 2013-04-24 | B | 156 | 0.1278 | 0.00048046
2014 | 2013-04-29 | B | 86 | 0.0034433 | 0.00026487
2014 | 2013-04-30 | B | 2 | 0.001657 | 6.1597e-06
2014 | 2013-04-30 | C | 2 | 0.0020881 | 6.1597e-06
2014 | 2013-04-30 | C | 63 | 0.012806 | 0.00019403
2014 | 2013-04-30 | C | 48.5524 | 0.020935 | 0.00031414
2014 | 2013-05-01 | B | 35 | 0.013151 | 0.00010779
2014 | 2013-04-30 | B | 37 | 0.038061 | 0.00011395
2014 | 2013-04-30 | B | 26 | 0.030189 | 8.0076e-05
2014 | 2013-05-01 | C | 334.3276 | 0.056632 | 0.0011426
2014 | 2013-04-30 | B | 35 | 0.031476 | 0.00010779
2014 | 2013-04-30 | B | 80 | 0.062582 | 0.00024639
2014 | 2013-05-01 | B | 28 | 0.023887 | 8.6236e-05
2014 | 2013-05-01 | C | 47 | 0.0092642 | 0.00014475
2014 | 2013-05-01 | B | 115 | 0.13282 | 0.00035418
2014 | 2013-05-01 | B | 4 | 0.0047676 | 1.2319e-05
2014 | 2013-04-01 | B | 65 | 0.081677 | 0.00020019
2014 | 2013-05-01 | B | 121 | 0.14795 | 0.00037266
2014 | 2013-05-01 | C | 135.7857 | 0.080712 | 0.001195
2014 | 2013-05-01 | C | 364.1053 | 0.10317 | 0.0011395
2014 | 2013-05-02 | C | 375 | 0.012704 | 0.0011549
2014 | 2013-05-01 | C | 1 | 0.00032954 | 3.0798e-06
2014 | 2013-05-02 | C | 1125 | 0.090085 | 0.0034648
2014 | 2013-05-02 | B | 137 | 0.048945 | 0.00042194
2014 | 2013-05-02 | B | 73 | 0.049013 | 0.00022483
2014 | 2013-05-02 | C | 109.3558 | 0.034017 | 0.00066833
2014 | 2013-05-02 | B | 28 | 0.03001 | 8.6236e-05
2014 | 2013-05-02 | B | 10 | 0.0097631 | 3.0798e-05
2014 | 2013-05-02 | C | 184.1097 | 0.086188 | 0.0012073
2014 | 2013-05-02 | B | 137 | 0.15063 | 0.00042194
2014 | 2013-05-02 | B | 433 | 0.61878 | 0.0013336
2014 | 2013-05-02 | C | 1 | 0.00038806 | 3.0798e-06
2014 | 2013-05-03 | C | 98.7664 | 0.040761 | 0.00074532
2014 | 2013-05-03 | C | 19 | 0.0030429 | 5.8517e-05
2014 | 2013-05-03 | B | 3 | 0.0007484 | 9.2395e-06
2014 | 2013-05-03 | B | 26 | 0.02074 | 8.0076e-05
2014 | 2013-05-03 | C | 291 | 0.087831 | 0.00089623
2014 | 2013-05-03 | C | 74 | 0.033958 | 0.00022791
2014 | 2013-05-04 | C | 29 | 0.0064307 | 8.9315e-05
2014 | 2013-05-04 | C | 432 | 0.31533 | 0.0013305
2014 | 2013-05-04 | C | 2 | 2.4639e-05 | 6.1597e-06
2014 | 2013-05-04 | C | 35 | 0.0050663 | 0.00010779
2014 | 2013-05-05 | B | 50 | 0.018171 | 0.00015399
2014 | 2013-05-04 | B | 20 | 0.011519 | 6.1597e-05
2014 | 2013-05-05 | C | 25 | 0.0046968 | 7.6996e-05
2014 | 2013-05-05 | B | 10 | 0.0077304 | 3.0798e-05
2014 | 2013-05-05 | C | 157.5909 | 0.10532 | 0.00072684
2014 | 2013-05-05 | C | 140.0588 | 0.042705 | 0.00064985
2014 | 2013-05-05 | C | 21 | 0.0093134 | 6.7757e-05
2014 | 2013-05-05 | C | 102.6122 | 0.030023 | 0.00064985
2014 | 2013-05-06 | C | 139.75 | 0.060688 | 0.00072992
2014 | 2013-05-05 | B | 5 | 0.0046198 | 1.5399e-05
2014 | 2013-05-05 | C | 135.1325 | 0.12444 | 0.00079152
2014 | 2013-05-05 | B | 45.8814 | 0.01625 | 0.00014783
2014 | 2013-05-06 | B | 60 | 0.018479 | 0.00018479
2014 | 2013-05-06 | C | 452.7561 | 0.28167 | 0.0017278
2014 | 2013-05-06 | B | 22 | 0.01389 | 6.7757e-05
2014 | 2013-05-06 | B | 18 | 0.023838 | 5.5437e-05
2014 | 2013-05-06 | C | 3 | 0.00061905 | 9.2395e-06
2014 | 2013-05-07 | C | 82 | 0.015153 | 0.00025255
2014 | 2013-05-06 | C | 161.8897 | 0.066313 | 0.00059749
2014 | 2013-05-06 | C | 8 | 0.0018479 | 2.4639e-05
2014 | 2013-05-07 | C | 1234.2308 | 0.38392 | 0.0047553
2014 | 2013-05-06 | C | 206.1989 | 0.22799 | 0.0032862
2014 | 2013-05-06 | C | 317.5081 | 0.23958 | 0.0042317
2014 | 2013-05-07 | C | 86.9226 | 0.078706 | 0.00066217
2014 | 2013-05-07 | C | 51 | 0.04131 | 0.00015707
2014 | 2013-05-07 | B | 91 | 0.070627 | 0.00028027
2014 | 2013-05-07 | C | 35.7603 | 0.012996 | 0.00073608
2014 | 2013-05-07 | B | 40 | 0.046198 | 0.00012319
2014 | 2013-05-07 | C | 5 | 0.0011703 | 1.5399e-05
2014 | 2013-05-07 | C | 101 | 0.02053 | 0.00031106
2014 | 2013-05-07 | C | 85.914 | 0.023814 | 0.00033878
2014 | 2013-05-07 | B | 27 | 0.033345 | 8.3156e-05
2014 | 2013-05-07 | C | 2 | 0.00092395 | 6.1597e-06
2014 | 2013-05-08 | B | 14 | 0.0088823 | 4.3118e-05
2014 | 2013-05-08 | C | 84.2018 | 0.027489 | 0.00027103
2014 | 2013-05-08 | B | 16 | 0.01705 | 4.9277e-05
2014 | 2013-05-08 | B | 165 | 0.1184 | 0.00050817
2014 | 2013-05-08 | B | 35 | 0.04204 | 0.00010779
2014 | 2013-05-08 | C | 21.1339 | 0.023627 | 7.3916e-05
2014 | 2013-05-09 | C | 983 | 0.13926 | 0.0030275
2014 | 2013-05-08 | C | 277.25 | 0.28776 | 0.0024546
2014 | 2013-05-08 | B | 174.7086 | 0.22922 | 0.0008408
2014 | 2013-05-08 | C | 44 | 0.0435 | 0.00013551
2014 | 2013-05-09 | B | 2 | 6.7757e-05 | 6.1597e-06
2014 | 2013-05-09 | C | 1 | 5.5437e-05 | 3.0798e-06
2014 | 2013-05-09 | B | 137.0548 | 0.12199 | 0.00035726
2014 | 2013-05-09 | B | 40.2062 | 0.035663 | 0.00012011
2014 | 2013-05-09 | B | 20 | 0.018356 | 6.1597e-05
2014 | 2013-05-09 | B | 37 | 0.037377 | 0.00011395
2014 | 2013-05-09 | B | 8 | 0.009412 | 2.4639e-05
2014 | 2013-05-09 | B | 9 | 0.010977 | 2.7719e-05
2014 | 2013-05-09 | B | 25 | 0.029874 | 7.6996e-05
2014 | 2013-05-09 | C | 1 | 0.00042502 | 3.0798e-06
2014 | 2013-05-09 | C | 136 | 0.002932 | 0.00041886
2014 | 2013-05-09 | C | 4 | 0.0018109 | 1.2319e-05
2014 | 2013-05-10 | C | 246 | 0.0098493 | 0.00075764
2014 | 2013-05-10 | C | 86.8154 | 0.016577 | 0.00028027
2014 | 2013-05-10 | C | 1 | 0.00052357 | 3.0798e-06
2014 | 2013-05-10 | B | 54 | 0.0096461 | 0.00016631
2014 | 2013-05-10 | B | 8 | 0.0052234 | 2.4639e-05
2014 | 2013-05-10 | C | 52.2929 | 0.015461 | 0.00020635
2014 | 2013-05-10 | C | 193.3 | 0.010121 | 0.00063137
2014 | 2013-05-10 | C | 52.2418 | 0.024134 | 0.00043426
2014 | 2013-05-10 | C | 89 | 0.0035634 | 0.00027411
2014 | 2013-05-10 | C | 205.1923 | 0.030966 | 0.00078228
2014 | 2013-05-10 | C | 89 | 0.0071268 | 0.00027411
2014 | 2013-05-11 | C | 26 | 0.0049647 | 8.0076e-05
2014 | 2013-05-11 | B | 1 | 0.00028335 | 3.0798e-06
2014 | 2013-05-10 | C | 263.5312 | 0.12743 | 0.0018571
2014 | 2013-05-11 | C | 138.3351 | 0.081376 | 0.0025624
2014 | 2013-05-12 | B | 9 | 0.0051279 | 2.7719e-05
2014 | 2013-05-13 | C | 2620.2162 | 0.27437 | 0.0083341
2014 | 2013-05-09 | B | 1 | 0.00058825 | 3.0798e-06
2014 | 2013-05-09 | C | 9 | 0.0014691 | 2.7719e-05
2014 | 2013-05-13 | B | 2 | 0.0013367 | 6.1597e-06
2014 | 2013-05-13 | C | 2 | 0.0007022 | 6.1597e-06
2014 | 2013-05-13 | B | 6 | 0.0076134 | 1.8479e-05
2014 | 2013-05-13 | C | 101 | 0.021152 | 0.00031106
2014 | 2013-05-13 | B | 278 | 0.2757 | 0.0008562
2014 | 2013-05-13 | B | 32 | 0.01912 | 9.8555e-05
2014 | 2013-05-13 | B | 60 | 0.0075764 | 0.00018479
2014 | 2013-05-14 | B | 31 | 0.028261 | 9.5475e-05
2014 | 2013-05-14 | B | 25 | 0.026333 | 7.6996e-05
2014 | 2013-05-14 | B | 44 | 0.049056 | 0.00013551
2014 | 2013-05-14 | B | 50 | 0.063599 | 0.00015399
2014 | 2013-05-14 | B | 38 | 0.04775 | 0.00011703
2014 | 2013-05-14 | C | 1 | 0.00011395 | 3.0798e-06
2014 | 2013-05-14 | B | 121 | 0.14534 | 0.00037266
2014 | 2013-05-15 | C | 91 | 0.0072869 | 0.00028027
2014 | 2013-05-15 | B | 13 | 0.0067264 | 4.0038e-05
2014 | 2013-05-09 | B | 5 | 0.0025871 | 1.5399e-05
2014 | 2013-05-13 | B | 6 | 0.0061905 | 1.8479e-05
2014 | 2013-05-06 | B | 3 | 0.0023746 | 9.2395e-06
2014 | 2013-05-07 | B | 69 | 0.064178 | 0.00021251
2014 | 2013-05-15 | C | 13 | 0.025704 | 4.0038e-05
2014 | 2013-05-15 | B | 3 | 0.0033447 | 9.2395e-06
2014 | 2013-05-16 | B | 35 | 0.028673 | 0.00010779
2014 | 2013-05-16 | B | 13 | 0.014654 | 4.0038e-05
2014 | 2013-05-16 | B | 121 | 0.14422 | 0.00037266
2014 | 2013-05-16 | B | 16 | 0.019317 | 4.9277e-05
2014 | 2013-05-16 | B | 8 | 0.0080815 | 2.4639e-05
2014 | 2013-05-16 | B | 38 | 0.027737 | 0.00011703
2014 | 2013-05-16 | B | 7 | 0.0072438 | 2.1559e-05
2014 | 2013-05-16 | B | 8 | 0.0085496 | 2.4639e-05
2014 | 2013-05-16 | C | 87.6667 | 0.02025 | 0.0004589
2014 | 2013-05-16 | C | 231.0206 | 0.37852 | 0.0018017
2014 | 2013-05-17 | B | 30 | 0.02199 | 9.2395e-05
2014 | 2013-05-17 | B | 3 | 0.0016354 | 9.2395e-06
2014 | 2013-05-17 | B | 7 | 0.0061012 | 2.1559e-05
2014 | 2013-05-17 | B | 35 | 0.039884 | 0.00010779
2014 | 2013-05-17 | C | 8 | 0.0021436 | 2.4639e-05
2014 | 2013-05-18 | C | 4 | 0.00083772 | 1.2319e-05
2014 | 2013-05-18 | C | 14 | 0.0072438 | 4.3118e-05
2014 | 2013-05-18 | C | 268 | 0.086667 | 0.0008254
2014 | 2013-05-19 | C | 258 | 0.01033 | 0.0007946
2014 | 2013-05-19 | B | 16 | 0.0095106 | 4.9277e-05
2014 | 2013-05-19 | B | 277 | 0.063984 | 0.00085312
2014 | 2013-05-19 | C | 11 | 0.003049 | 3.3878e-05
2014 | 2013-05-19 | C | 16 | 0.0052727 | 4.9277e-05
2014 | 2013-05-19 | C | 130 | 0.0072068 | 0.00040038
2014 | 2013-05-19 | C | 258 | 0.032579 | 0.0007946
2014 | 2013-05-19 | C | 2 | 0.0018294 | 6.1597e-06
2014 | 2013-05-19 | C | 13 | 0.0024023 | 4.0038e-05
2014 | 2013-05-19 | C | 6 | 0.00077612 | 1.8479e-05
2014 | 2013-05-19 | C | 50.5764 | 0.084114 | 0.0011334
2014 | 2013-05-17 | B | 73 | 0.061603 | 0.00022483
2014 | 2013-05-20 | C | 41 | 0.0045458 | 0.00012627
2014 | 2013-05-20 | B | 4 | 0.003856 | 1.2319e-05
2014 | 2013-05-20 | B | 9 | 0.012584 | 2.7719e-05
2014 | 2013-05-20 | C | 10 | 0.0016631 | 3.0798e-05
2014 | 2013-05-20 | C | 681 | 0.0020974 | 0.0020974
2014 | 2013-05-20 | C | 6.1899 | 0.0014489 | 2.1559e-05
2014 | 2013-05-20 | C | 756 | 0.025612 | 0.0023284
2014 | 2013-05-21 | B | 4 | 0.0026117 | 1.2319e-05
2014 | 2013-05-21 | B | 160 | 0.15375 | 0.00049277
2014 | 2013-05-21 | B | 60 | 0.049339 | 0.00018479
2014 | 2013-05-21 | C | 1 | 0.00022483 | 3.0798e-06
2014 | 2013-05-21 | C | 169.931 | 0.13503 | 0.0007946
2014 | 2013-05-22 | C | 447.3125 | 0.10608 | 0.0020943
2014 | 2013-05-22 | B | 6 | 0.001312 | 1.8479e-05
2014 | 2013-05-22 | B | 27 | 0.021288 | 8.3156e-05
2014 | 2013-05-22 | C | 41.4405 | 0.021059 | 0.00013551
2014 | 2013-05-22 | B | 31 | 0.029693 | 9.5475e-05
2014 | 2013-05-22 | C | 344.7914 | 0.19539 | 0.0016785
2014 | 2013-05-22 | C | 1 | 0.00020019 | 3.0798e-06
2014 | 2013-05-22 | C | 3 | 0.00062829 | 9.2395e-06
2014 | 2013-05-22 | C | 6 | 0.0028088 | 1.8479e-05
2014 | 2013-05-22 | C | 71.3871 | 0.10158 | 0.00044966
2014 | 2013-05-22 | B | 443 | 0.57576 | 0.0013644
2014 | 2013-05-23 | C | 636 | 0.068557 | 0.0020543
2014 | 2013-05-23 | B | 13 | 0.014854 | 4.0038e-05
2014 | 2013-05-23 | B | 199.296 | 0.22833 | 0.0016631
2014 | 2013-05-23 | B | 42 | 0.041134 | 0.00012935
2014 | 2013-05-23 | B | 7 | 0.0080199 | 2.1559e-05
2014 | 2013-05-23 | C | 516 | 0.044498 | 0.0015892
2014 | 2013-05-23 | C | 3 | 0.00036034 | 9.2395e-06
2014 | 2013-05-23 | B | 52 | 0.021781 | 0.00016015
2014 | 2013-05-23 | B | 1 | 0.0006868 | 3.0798e-06
2014 | 2013-05-23 | C | 819 | 0.17909 | 0.0025224
2014 | 2013-05-23 | C | 1 | 0.00065909 | 3.0798e-06
2014 | 2013-05-23 | C | 1 | 1.2319e-05 | 3.0798e-06
2014 | 2013-05-23 | C | 9 | 0.00058209 | 2.7719e-05
2014 | 2013-05-23 | C | 2 | 0.001737 | 6.1597e-06
2014 | 2013-05-23 | C | 4.2397 | 0.023386 | 4.3118e-05
2014 | 2013-05-24 | B | 41 | 0.047353 | 0.00012627
2014 | 2013-05-24 | B | 74 | 0.090252 | 0.00022791
2014 | 2013-05-24 | B | 13 | 0.014694 | 4.0038e-05
2014 | 2013-05-23 | B | 20 | 0.021066 | 6.1597e-05
2014 | 2013-05-24 | C | 1 | 0.00049893 | 3.0798e-06
2014 | 2013-05-24 | C | 751 | 0.048572 | 0.0027811
2014 | 2013-05-24 | C | 15 | 0.0019403 | 4.6198e-05
2014 | 2013-05-24 | C | 178.5664 | 0.27993 | 0.0040469
2014 | 2013-05-25 | C | 30 | 0.0061905 | 9.2395e-05
2014 | 2013-05-25 | C | 288 | 0.030158 | 0.00088699
2014 | 2013-05-25 | C | 16 | 0.0062582 | 4.9277e-05
2014 | 2013-05-25 | C | 156 | 0.0091287 | 0.00048046
2014 | 2013-05-25 | C | 156 | 0.016335 | 0.00048046
2014 | 2013-05-26 | C | 210.037 | 0.10285 | 0.0020912
2014 | 2013-05-26 | C | 569.7759 | 0.096515 | 0.0032924
2014 | 2013-05-26 | C | 8 | 0.0010348 | 2.4639e-05
2014 | 2013-05-26 | C | 735.1111 | 0.19697 | 0.0034309
2014 | 2013-05-26 | C | 227.4489 | 0.24448 | 0.0026887
2014 | 2013-05-26 | C | 5.5873 | 0.026845 | 0.00021251
2014 | 2013-05-26 | C | 155.213 | 0.079353 | 0.00079152
2014 | 2013-05-26 | C | 32.5531 | 0.017645 | 0.00015707
2014 | 2013-05-27 | C | 13 | 0.0010009 | 4.0038e-05
2014 | 2013-05-26 | C | 1 | 0.00032954 | 3.0798e-06
2014 | 2013-05-26 | C | 20.0605 | 0.052886 | 6.7757e-05
2014 | 2013-05-17 | C | 56 | 0.0017247 | 0.00017247
2014 | 2013-05-26 | C | 5 | 0.014475 | 1.5399e-05
2014 | 2013-05-27 | B | 10 | 0.011765 | 3.0798e-05
2014 | 2013-05-27 | C | 15 | 0.0081308 | 4.6198e-05
2014 | 2013-05-27 | C | 363 | 0.15428 | 0.001118
2014 | 2013-05-26 | B | 1 | 0.00072376 | 3.0798e-06
2014 | 2013-05-28 | C | 14 | 0.0027164 | 4.3118e-05
2014 | 2013-05-20 | B | 81 | 0.078832 | 0.00024947
2014 | 2013-05-23 | B | 1 | 0.0007022 | 3.0798e-06
2014 | 2013-05-28 | C | 287 | 0.014143 | 0.00088391
2014 | 2013-05-28 | B | 2 | 0.0019218 | 6.1597e-06
2014 | 2013-05-28 | B | 8 | 0.0070467 | 2.4639e-05
2014 | 2013-05-28 | B | 365.1002 | 0.51275 | 0.001195
2014 | 2013-05-28 | C | 965.9604 | 0.29155 | 0.0031846
2014 | 2013-05-28 | C | 418 | 0.16736 | 0.0012874
2014 | 2013-05-28 | C | 372 | 0.16956 | 0.0011457
2014 | 2013-05-29 | C | 1465.7333 | 0.1896 | 0.006634
2014 | 2013-05-28 | C | 1 | 0.00090239 | 3.0798e-06
2014 | 2013-05-28 | C | 77.17 | 0.081759 | 0.00088699
2014 | 2013-05-29 | C | 28 | 0.0018972 | 8.6236e-05
2014 | 2013-05-27 | C | 12 | 0.095611 | 3.6958e-05
2014 | 2013-05-29 | C | 222.3475 | 0.078751 | 0.0010595
2014 | 2013-05-29 | B | 43 | 0.041452 | 0.00013243
2014 | 2013-05-29 | C | 33 | 0.0054883 | 0.00010163
2014 | 2013-05-29 | C | 1477.3731 | 0.2912 | 0.0054236
2014 | 2013-05-29 | C | 13 | 0.0036435 | 4.0038e-05
2014 | 2013-05-30 | C | 393.17 | 0.11746 | 0.0022883
2014 | 2013-05-29 | C | 108 | 0.0056546 | 0.00033262
2014 | 2013-05-29 | C | 27 | 0.019209 | 8.3156e-05
2014 | 2013-05-30 | C | 87.8951 | 0.081752 | 0.0007022
2014 | 2013-05-30 | C | 1 | 4.0038e-05 | 3.0798e-06
2014 | 2013-05-30 | B | 40 | 0.036096 | 0.00012319
2014 | 2013-05-30 | B | 13 | 0.013893 | 4.0038e-05
2014 | 2013-05-30 | B | 45 | 0.05516 | 0.00013859
2014 | 2013-05-30 | C | 55 | 0.017278 | 0.00016939
2014 | 2013-05-30 | C | 22 | 0.0017617 | 6.7757e-05
2014 | 2013-05-31 | C | 124.1471 | 0.024853 | 0.00051433
2014 | 2013-05-31 | C | 505.3696 | 0.13852 | 0.0021867
2014 | 2013-05-31 | C | 854.3647 | 0.21577 | 0.0040192
2014 | 2013-05-31 | C | 74 | 0.016409 | 0.00022791
2014 | 2013-05-31 | C | 4 | 0.0012566 | 1.2319e-05
2014 | 2013-05-31 | B | 3 | 0.002236 | 9.2395e-06
2014 | 2013-05-31 | C | 4 | 0.0013798 | 1.2319e-05
2014 | 2013-05-31 | C | 7 | 0.0033847 | 2.1559e-05
2014 | 2013-05-31 | C | 4 | 0.0007022 | 1.2319e-05
2014 | 2013-05-31 | C | 94 | 0.030109 | 0.00028951
2014 | 2013-05-31 | C | 406.4507 | 0.174 | 0.0012843
2014 | 2013-05-31 | C | 387 | 0.067938 | 0.0011919
2014 | 2013-05-31 | C | 264 | 0.034149 | 0.00081308
2014 | 2013-06-01 | C | 68.6472 | 0.08626 | 0.0017801
2014 | 2013-06-01 | C | 160 | 0.087221 | 0.00049277
2014 | 2013-06-01 | C | 214 | 0.073159 | 0.00065909
2014 | 2013-06-01 | C | 7 | 0.00012935 | 2.1559e-05
2014 | 2013-06-02 | C | 47 | 0.0039083 | 0.00014475
2014 | 2013-06-02 | C | 540.3472 | 0.11483 | 0.0019495
2014 | 2013-06-04 | B | 50 | 0.0080076 | 0.00015399
2014 | 2013-06-04 | B | 24 | 0.012048 | 7.3916e-05
2014 | 2013-06-04 | C | 133.4474 | 0.10809 | 0.0020666
2014 | 2013-06-04 | B | 14 | 0.015781 | 4.3118e-05
2014 | 2013-06-04 | B | 279 | 0.32395 | 0.00085928
2014 | 2013-06-04 | C | 51.4384 | 0.045784 | 0.0011087
2014 | 2013-06-04 | B | 91 | 0.12107 | 0.00028027
2014 | 2013-06-04 | C | 137.4865 | 0.030064 | 0.00085928
2014 | 2013-06-04 | B | 75 | 0.082463 | 0.00023099
2014 | 2013-06-04 | B | 1 | 0.00082232 | 3.0798e-06
2014 | 2013-06-04 | B | 2 | 0.0010102 | 6.1597e-06
2014 | 2013-06-04 | C | 19 | 0.001814 | 5.8517e-05
2014 | 2013-06-04 | C | 299.5455 | 0.1596 | 0.0030768
2014 | 2013-06-05 | C | 39.2639 | 0.097225 | 0.0011241
2014 | 2013-06-04 | C | 3 | 0.0021343 | 9.2395e-06
2014 | 2013-06-04 | C | 519.009 | 0.35166 | 0.0017771
2014 | 2013-06-05 | C | 27 | 0.0024947 | 8.3156e-05
2014 | 2013-06-05 | B | 3 | 0.0012658 | 9.2395e-06
2014 | 2013-06-05 | B | 1 | 0.00037574 | 3.0798e-06
2014 | 2013-06-05 | B | 76 | 0.055474 | 0.00023407
2014 | 2013-06-05 | B | 9 | 0.0088977 | 2.7719e-05
2014 | 2013-06-05 | B | 25 | 0.022791 | 7.6996e-05
2014 | 2013-06-05 | B | 63 | 0.058597 | 0.00019403
2014 | 2013-06-05 | B | 76 | 0.047984 | 0.00023407
2014 | 2013-06-05 | C | 178 | 0.065237 | 0.00054821
2014 | 2013-06-05 | C | 730.1818 | 0.14168 | 0.0036342
2014 | 2013-06-05 | C | 360 | 0.046567 | 0.0011087
2014 | 2013-06-06 | B | 90 | 0.019403 | 0.00027719
2014 | 2013-06-06 | B | 4 | 0.001195 | 1.2319e-05
2014 | 2013-06-06 | B | 3 | 0.0019495 | 9.2395e-06
2014 | 2013-06-06 | C | 8 | 9.8555e-05 | 2.4639e-05
2014 | 2013-06-05 | B | 31 | 0.028643 | 9.5475e-05
2014 | 2013-06-06 | B | 75 | 0.082001 | 0.00023099
2014 | 2013-06-06 | B | 2 | 0.0010287 | 6.1597e-06
2014 | 2013-06-06 | B | 76 | 0.067178 | 0.00023407
2014 | 2013-06-06 | B | 67 | 0.077794 | 0.00020635
2014 | 2013-06-06 | B | 28 | 0.033373 | 8.6236e-05
2014 | 2013-06-06 | B | 2 | 0.0031846 | 6.1597e-06
2014 | 2013-06-06 | B | 2 | 0.0017678 | 6.1597e-06
2014 | 2013-06-06 | B | 40 | 0.035726 | 0.00012319
2014 | 2013-06-07 | B | 4 | 0.00039422 | 1.2319e-05
2014 | 2013-06-07 | B | 17 | 0.0020943 | 5.2357e-05
2014 | 2013-06-05 | B | 19 | 0.019545 | 5.8517e-05
2014 | 2013-06-07 | B | 2 | 0.0012258 | 6.1597e-06
2014 | 2013-06-07 | B | 20 | 0.011827 | 6.1597e-05
2014 | 2013-06-08 | C | 222.4421 | 0.063028 | 0.0011365
2014 | 2013-05-01 | B | 121 | 0.13304 | 0.00037266
2014 | 2013-06-08 | B | 2 | 0.0013428 | 6.1597e-06
2014 | 2013-06-08 | B | 1 | 0.00080076 | 3.0798e-06
2014 | 2013-06-08 | C | 459.0989 | 0.12443 | 0.0014783
2014 | 2013-06-09 | C | 30 | 0.0020327 | 9.2395e-05
2014 | 2013-06-10 | C | 2414 | 0.28995 | 0.0074347
2014 | 2013-06-10 | B | 31 | 0.02005 | 9.5475e-05
2014 | 2013-06-10 | B | 8 | 0.008796 | 2.4639e-05
2014 | 2013-06-10 | B | 25 | 0.028874 | 7.6996e-05
2014 | 2013-06-10 | C | 1228 | 0.075641 | 0.003782
2014 | 2013-06-10 | C | 84 | 0.026647 | 0.00025871
2014 | 2013-06-10 | C | 71 | 0.0028427 | 0.00021867
2014 | 2013-06-10 | C | 61.9866 | 0.14165 | 0.00080692
2014 | 2013-06-11 | B | 1 | 0.00014167 | 3.0798e-06
2014 | 2013-06-10 | B | 40 | 0.021805 | 0.00012319
2014 | 2013-06-11 | C | 3 | 0.00094243 | 9.2395e-06
2014 | 2013-06-11 | B | 55 | 0.06132 | 0.00016939
2014 | 2013-06-11 | C | 55.228 | 0.032318 | 0.00028643
2014 | 2013-06-11 | B | 44 | 0.062607 | 0.00013551
2014 | 2013-06-11 | C | 55.228 | 0.032318 | 0.00028643
2014 | 2013-06-11 | B | 8 | 0.008796 | 2.4639e-05
2014 | 2013-06-11 | B | 86 | 0.070719 | 0.00026487
2014 | 2013-06-11 | B | 74 | 0.0091163 | 0.00022791
2014 | 2013-06-11 | C | 247.8537 | 0.1542 | 0.00081
2014 | 2013-06-11 | C | 181 | 0.03289 | 0.00055745
2014 | 2013-06-11 | C | 76.9459 | 0.069436 | 0.00035418
2014 | 2013-06-12 | C | 460.9 | 0.1093 | 0.0025409
2014 | 2013-06-12 | B | 62 | 0.068169 | 0.00019095
2014 | 2013-06-11 | B | 28 | 0.030269 | 8.6236e-05
2014 | 2013-06-12 | B | 9 | 0.0095906 | 2.7719e-05
2014 | 2013-06-12 | B | 35 | 0.028134 | 0.00010779
2014 | 2013-06-12 | B | 52 | 0.047085 | 0.00016015
2014 | 2013-06-12 | B | 26 | 0.019218 | 8.0076e-05
2014 | 2013-06-11 | C | 300 | 0.066525 | 0.00092395
2014 | 2013-06-06 | B | 160 | 0.11137 | 0.00049277
2014 | 2013-06-04 | B | 6 | 0.0047122 | 1.8479e-05
2014 | 2013-06-13 | C | 3 | 0.00048046 | 9.2395e-06
2014 | 2013-06-13 | C | 8 | 0.0028088 | 2.4639e-05
2014 | 2013-06-13 | B | 18 | 0.01397 | 5.5437e-05
2014 | 2013-06-13 | B | 46 | 0.050577 | 0.00014167
2014 | 2013-06-13 | B | 44 | 0.029677 | 0.00013551
2014 | 2013-06-13 | C | 4 | 0.002082 | 1.2319e-05
2014 | 2013-06-13 | C | 748.193 | 0.12443 | 0.0025409
2014 | 2013-06-13 | B | 67 | 0.060667 | 0.00020635
2014 | 2013-06-13 | C | 2 | 0.0011519 | 6.1597e-06
2014 | 2013-06-14 | C | 3 | 0.00080384 | 9.2395e-06
2014 | 2013-06-14 | C | 5 | 0.0082848 | 1.5399e-05
2014 | 2013-06-14 | B | 9 | 0.0092303 | 2.7719e-05
2014 | 2013-06-14 | C | 443.7795 | 0.16948 | 0.0024115
2014 | 2013-06-15 | B | 55 | 0.029135 | 0.00016939
2014 | 2013-06-09 | B | 33 | 0.024087 | 0.00010163
2014 | 2013-06-16 | C | 551.8864 | 0.069689 | 0.0018325
2014 | 2013-06-16 | C | 213.0276 | 0.093165 | 0.0014598
2014 | 2013-06-16 | C | 50.8865 | 0.043726 | 0.00059441
2014 | 2013-06-16 | C | 116 | 0.051803 | 0.00035726
2014 | 2013-06-16 | C | 272 | 0.056965 | 0.00083772
2014 | 2013-06-16 | C | 138 | 0.014026 | 0.00042502
2014 | 2013-06-16 | C | 478 | 0.06772 | 0.0014722
2014 | 2013-06-16 | C | 85 | 0.0049739 | 0.00026179
2014 | 2013-06-17 | C | 48 | 0.018775 | 0.00014783
2014 | 2013-06-17 | C | 68.6525 | 0.049265 | 0.00064061
2014 | 2013-06-17 | B | 100 | 0.11365 | 0.00030798
2014 | 2013-06-17 | B | 4 | 0.0018849 | 1.2319e-05
2014 | 2013-06-17 | C | 143.5021 | 0.1043 | 0.00060057
2014 | 2013-06-17 | C | 28.0426 | 0.048365 | 0.00062829
2014 | 2013-06-17 | C | 3 | 0.00012935 | 9.2395e-06
2014 | 2013-06-17 | C | 3 | 0.00061905 | 9.2395e-06
2014 | 2013-06-17 | C | 7 | 0.00030182 | 2.1559e-05
2014 | 2013-06-17 | B | 8 | 0.01126 | 2.4639e-05
2014 | 2013-06-16 | C | 22.3756 | 0.11888 | 0.00029258
2014 | 2013-06-18 | B | 2 | 0.00044966 | 6.1597e-06
2014 | 2013-06-18 | B | 8 | 0.0030798 | 2.4639e-05
2014 | 2013-06-17 | C | 3 | 0.0095167 | 9.2395e-06
2014 | 2013-06-18 | C | 4 | 0.0010964 | 1.2319e-05
2014 | 2013-06-17 | C | 3 | 0.014164 | 9.2395e-06
2014 | 2013-06-18 | B | 159 | 0.18315 | 0.00048969
2014 | 2013-06-18 | C | 1259.7222 | 0.058196 | 0.00409
2014 | 2013-06-19 | C | 4 | 0.00061597 | 1.2319e-05
2014 | 2013-06-19 | B | 67 | 0.063143 | 0.00020635
2014 | 2013-06-18 | B | 6 | 0.0071514 | 1.8479e-05
2014 | 2013-06-19 | B | 9 | 0.0083433 | 2.7719e-05
2014 | 2013-06-19 | C | 95 | 0.0011703 | 0.00029258
2014 | 2013-06-19 | B | 3 | 0.003936 | 9.2395e-06
2014 | 2013-06-19 | C | 165.5481 | 0.051496 | 0.00064061
2014 | 2013-06-18 | C | 31 | 0.0053466 | 9.5475e-05
2014 | 2013-06-18 | C | 1 | 0.00013551 | 3.0798e-06
2014 | 2013-06-19 | C | 47 | 0.02649 | 0.00014475
2014 | 2013-06-19 | C | 131.0466 | 0.076685 | 0.00082848
2014 | 2013-06-18 | C | 53.4286 | 0.019088 | 0.00026487
2014 | 2013-06-19 | C | 116 | 0.0071452 | 0.00035726
2014 | 2013-06-20 | B | 67 | 0.037143 | 0.00020635
2014 | 2013-06-20 | B | 310 | 0.30457 | 0.00095475
2014 | 2013-06-20 | C | 109.1103 | 0.090395 | 0.00084696
2014 | 2013-06-20 | B | 75 | 0.027026 | 0.00023099
2014 | 2013-06-20 | C | 785 | 0.024177 | 0.0024177
2014 | 2013-06-21 | C | 189 | 0.0075672 | 0.00058209
2014 | 2013-06-20 | C | 523.71 | 0.59034 | 0.0023653
2014 | 2013-06-21 | C | 102.6524 | 0.058172 | 0.00068065
2014 | 2013-06-20 | C | 432.0452 | 0.4085 | 0.0016323
2014 | 2013-06-21 | C | 757.1273 | 0.12126 | 0.0023407
2014 | 2013-06-20 | C | 314 | 0.07253 | 0.00096707
2014 | 2013-06-21 | C | 91.8462 | 0.010183 | 0.00033262
2014 | 2013-06-21 | C | 435.875 | 0.12485 | 0.0030798
2014 | 2013-06-21 | B | 4 | 0.0017494 | 1.2319e-05
2014 | 2013-06-21 | B | 31 | 0.0082109 | 9.5475e-05
2014 | 2013-06-21 | C | 210 | 0.086667 | 0.00064677
2014 | 2013-06-21 | C | 335.869 | 0.60514 | 0.0012843
2014 | 2013-06-21 | C | 38 | 0.0095968 | 0.00011703
2014 | 2013-06-21 | C | 289 | 0.22163 | 0.00089007
2014 | 2013-06-21 | C | 229.0707 | 0.68645 | 0.0010133
2014 | 2013-06-21 | C | 20 | 0.0010471 | 6.1597e-05
2014 | 2013-06-21 | C | 315 | 0.52582 | 0.00097015
2014 | 2013-06-23 | C | 92 | 0.0093504 | 0.00028335
2014 | 2013-06-22 | C | 105.4696 | 0.05782 | 0.0010009
2014 | 2013-06-22 | C | 22 | 0.0040654 | 6.7757e-05
2014 | 2013-06-21 | C | 2 | 0.0077427 | 6.1597e-06
2014 | 2013-06-22 | C | 513.2385 | 0.16755 | 0.0019003
2014 | 2013-06-22 | C | 1 | 0.00065601 | 3.0798e-06
2014 | 2013-06-21 | C | 39 | 0.080837 | 0.00012011
2014 | 2013-06-21 | C | 24 | 0.031784 | 7.3916e-05
2014 | 2013-06-23 | C | 71 | 0.012027 | 0.00021867
2014 | 2013-06-23 | C | 177 | 0.029437 | 0.00054513
2014 | 2013-06-16 | B | 11 | 0.0069789 | 3.3878e-05
2014 | 2013-06-21 | C | 91.6575 | 0.48131 | 0.00052049
2014 | 2013-06-22 | C | 61 | 0.03175 | 0.00018787
2014 | 2013-06-22 | C | 260.9627 | 0.40749 | 0.0012381
2014 | 2013-06-23 | C | 16 | 0.0099048 | 4.9277e-05
2014 | 2013-06-21 | C | 202.2946 | 0.51837 | 0.0010964
2014 | 2013-06-21 | C | 334 | 0.40221 | 0.0010287
2014 | 2013-06-21 | C | 14 | 0.0021128 | 4.3118e-05
2014 | 2013-06-21 | C | 52.9262 | 0.039284 | 0.00023099
2014 | 2013-06-20 | C | 110.51 | 0.38936 | 0.00044658
2014 | 2013-06-24 | C | 7 | 0.011965 | 2.1559e-05
2014 | 2013-06-20 | C | 146 | 0.33724 | 0.00044966
2014 | 2013-06-21 | C | 62.4846 | 0.28616 | 0.00020327
2014 | 2013-06-21 | C | 4 | 0.00067757 | 1.2319e-05
2014 | 2013-06-21 | C | 59.2949 | 0.013696 | 0.00032954
2014 | 2013-06-20 | C | 33.4983 | 0.21851 | 0.00026795
2014 | 2013-06-21 | C | 675 | 0.0083156 | 0.0020789
2014 | 2013-06-23 | C | 100.7308 | 0.11199 | 0.0012751
2014 | 2013-06-20 | C | 108 | 0.011309 | 0.00033262
2014 | 2013-06-24 | B | 12 | 0.0042132 | 3.6958e-05
2014 | 2013-06-24 | C | 8 | 0.001158 | 2.4639e-05
2014 | 2013-06-21 | C | 105.6059 | 0.28785 | 0.00034494
2014 | 2013-06-21 | C | 58 | 0.049302 | 0.00017863
2014 | 2013-06-21 | C | 20 | 0.0051125 | 6.1597e-05
2014 | 2013-06-21 | C | 144.8839 | 0.048638 | 0.00064985
2014 | 2013-06-21 | C | 102.6948 | 0.23532 | 0.00078536
2014 | 2013-06-21 | C | 21.4668 | 0.10433 | 0.00021867
2014 | 2013-06-21 | C | 22 | 0.056441 | 6.7757e-05
2014 | 2013-06-23 | C | 2 | 0.005864 | 6.1597e-06
2014 | 2013-06-21 | C | 14 | 0.00051741 | 4.3118e-05
2014 | 2013-06-21 | C | 66 | 0.02053 | 0.00020327
2014 | 2013-06-24 | C | 1 | 8.6236e-05 | 3.0798e-06
2014 | 2013-06-21 | C | 305 | 0.016908 | 0.00093935
2014 | 2013-06-22 | C | 2218 | 0.047818 | 0.0082355
2014 | 2013-06-21 | C | 37 | 0.021765 | 0.00011395
2014 | 2013-06-21 | C | 24.6265 | 0.16914 | 0.00024023
2014 | 2013-06-21 | C | 9 | 0.083017 | 2.7719e-05
2014 | 2013-06-21 | C | 279.6324 | 0.58305 | 0.00094243
2014 | 2013-06-22 | C | 240.8008 | 0.57105 | 0.0010687
2014 | 2013-06-24 | C | 251 | 0.059524 | 0.00077304
2014 | 2013-06-21 | C | 1972 | 0.048588 | 0.0060734
2014 | 2013-06-24 | C | 6 | 0.0010533 | 1.8479e-05
2014 | 2013-06-22 | C | 2104 | 0.0324 | 0.0082355
2014 | 2013-06-23 | C | 1243.783 | 0.39456 | 0.0042563
2014 | 2013-06-24 | C | 19 | 0.025747 | 5.8517e-05
2014 | 2013-06-24 | C | 171.9228 | 0.14243 | 0.0022452
2014 | 2013-06-24 | C | 14 | 0.0031045 | 4.3118e-05
2014 | 2013-06-24 | C | 2386.6667 | 0.15436 | 0.0091625
2014 | 2013-06-23 | C | 594.3943 | 0.57482 | 0.0026363
2014 | 2013-06-24 | C | 1 | 8.0076e-05 | 3.0798e-06
2014 | 2013-06-20 | C | 8 | 0.16732 | 2.4639e-05
2014 | 2013-06-25 | C | 14 | 0.01065 | 4.3118e-05
2014 | 2013-06-25 | C | 5 | 0.0038806 | 1.5399e-05
2014 | 2013-06-25 | C | 16 | 0.0093627 | 4.9277e-05
2014 | 2013-06-26 | C | 893.6338 | 0.18715 | 0.0039299
2014 | 2013-06-26 | C | 637.881 | 0.076618 | 0.002162
2014 | 2013-06-26 | C | 3 | 0.0021713 | 9.2395e-06
2014 | 2013-06-26 | C | 2 | 0.00085004 | 6.1597e-06
2014 | 2013-06-12 | B | 75 | 0.079691 | 0.00023099
2014 | 2013-06-27 | B | 17 | 0.017906 | 5.2357e-05
2014 | 2013-06-20 | B | 123 | 0.13865 | 0.00037882
2014 | 2013-06-27 | B | 98.1449 | 0.16595 | 0.00054205
2014 | 2013-06-28 | C | 128 | 0.011432 | 0.00039422
2014 | 2013-06-29 | C | 1 | 0.00037266 | 3.0798e-06
2014 | 2013-06-28 | C | 46.7068 | 0.0187 | 0.00014475
2014 | 2013-06-28 | C | 578.5 | 0.037415 | 0.0028827
2014 | 2013-06-29 | C | 133.7306 | 0.11038 | 0.0015368
2014 | 2013-06-29 | C | 157 | 0.03143 | 0.00048354
2014 | 2013-06-29 | C | 38 | 0.021417 | 0.00011703
2014 | 2013-06-30 | C | 5155.2062 | 1.4925 | 0.03034
2014 | 2013-06-29 | C | 1 | 0.00069296 | 3.0798e-06
2014 | 2013-06-30 | C | 52 | 0.032351 | 0.00016015
2014 | 2013-06-30 | C | 101.3842 | 0.1096 | 0.00052049
2014 | 2013-06-30 | B | 1 | 0.00045582 | 3.0798e-06
2014 | 2013-06-28 | B | 24 | 0.0048046 | 7.3916e-05
2014 | 2013-07-01 | C | 212.9894 | 0.12136 | 0.0021713
2014 | 2013-07-01 | B | 10 | 0.0053589 | 3.0798e-05
2014 | 2013-07-01 | B | 39 | 0.012852 | 0.00012011
2014 | 2013-07-01 | B | 54 | 0.059373 | 0.00016631
2014 | 2013-07-01 | B | 36 | 0.042465 | 0.00011087
2014 | 2013-07-01 | B | 54 | 0.02162 | 0.00016631
2014 | 2013-07-01 | B | 18 | 0.016188 | 5.5437e-05
2014 | 2013-07-01 | B | 52 | 0.057494 | 0.00016015
2014 | 2013-07-02 | B | 33 | 0.029474 | 0.00010163
2014 | 2013-07-02 | C | 6 | 0.00049893 | 1.8479e-05
2014 | 2013-07-02 | B | 17 | 0.0033509 | 5.2357e-05
2014 | 2013-07-02 | C | 28.1818 | 0.018835 | 0.00013859
2014 | 2013-07-02 | C | 14 | 0.00056053 | 4.3118e-05
2014 | 2013-07-02 | C | 40 | 0.0051741 | 0.00012319
2014 | 2013-07-02 | B | 10 | 0.0047738 | 3.0798e-05
2014 | 2013-07-02 | B | 9 | 0.005322 | 2.7719e-05
2014 | 2013-07-02 | B | 16 | 0.017592 | 4.9277e-05
2014 | 2013-07-02 | B | 340 | 0.37174 | 0.0010471
2014 | 2013-07-02 | B | 46 | 0.046185 | 0.00014167
2014 | 2013-07-02 | C | 26.6566 | 0.029637 | 9.2395e-05
2014 | 2013-07-02 | B | 36 | 0.019514 | 0.00011087
2014 | 2013-07-02 | B | 137 | 0.14135 | 0.00042194
2014 | 2013-07-02 | C | 14.9265 | 0.0092402 | 0.00015399
2014 | 2013-07-02 | B | 28 | 0.028199 | 8.6236e-05
2014 | 2013-07-03 | C | 145.1194 | 0.028604 | 0.00052049
2014 | 2013-07-02 | C | 21 | 0.0098309 | 6.4677e-05
2014 | 2013-07-03 | C | 547.2896 | 0.36745 | 0.0034248
2014 | 2013-07-03 | C | 184.1489 | 0.051611 | 0.00078536
2014 | 2013-07-02 | B | 120 | 0.06172 | 0.00036958
2014 | 2013-07-03 | B | 38 | 0.037568 | 0.00011703
2014 | 2013-07-03 | B | 19.4571 | 0.014502 | 0.00021867
2014 | 2013-07-03 | B | 36 | 0.040136 | 0.00011087
2014 | 2013-07-03 | C | 12 | 0.0032154 | 3.6958e-05
2014 | 2013-07-04 | C | 146.0408 | 0.13089 | 0.00085312
2014 | 2013-07-03 | C | 21.5133 | 0.019679 | 9.2395e-05
2014 | 2013-07-03 | C | 3 | 0.0021898 | 9.2395e-06
2014 | 2013-07-04 | B | 17 | 0.00083772 | 5.2357e-05
2014 | 2013-07-04 | B | 8 | 0.0094613 | 2.4639e-05
2014 | 2013-07-04 | B | 22.51 | 0.027523 | 7.0836e-05
2014 | 2013-07-04 | B | 41 | 0.038135 | 0.00012627
2014 | 2013-07-04 | B | 28 | 0.027768 | 8.6236e-05
2014 | 2013-07-04 | C | 19 | 0.0060273 | 5.8517e-05
2014 | 2013-07-04 | C | 105.0884 | 0.057611 | 0.0004589
2014 | 2013-07-04 | C | 13 | 0.0040038 | 4.0038e-05
2014 | 2013-07-04 | C | 19 | 0.0053836 | 5.8517e-05
2014 | 2013-07-04 | C | 21 | 0.0032338 | 6.4677e-05
2014 | 2013-07-04 | C | 315 | 0.18627 | 0.00097015
2014 | 2013-07-04 | C | 1240.9616 | 1.5823 | 0.024814
2014 | 2013-07-05 | C | 375.0769 | 0.026569 | 0.0016138
2014 | 2013-07-05 | B | 55 | 0.028627 | 0.00016939
2014 | 2013-07-05 | C | 29.8194 | 0.012949 | 0.00018479
2014 | 2013-07-05 | C | 3 | 0.00080384 | 9.2395e-06
2014 | 2013-07-05 | B | 6 | 0.0027164 | 1.8479e-05
2014 | 2013-07-05 | B | 4 | 0.0014414 | 1.2319e-05
2014 | 2013-07-05 | B | 1 | 0.00037882 | 3.0798e-06
2014 | 2013-07-05 | B | 487 | 0.26548 | 0.0014999
2014 | 2013-07-06 | B | 2 | 0.00030798 | 6.1597e-06
2014 | 2013-07-06 | B | 49 | 0.01162 | 0.00015091
2014 | 2013-07-06 | B | 55 | 0.0071144 | 0.00016939
2014 | 2013-07-05 | C | 2 | 0.0019095 | 6.1597e-06
2014 | 2013-07-06 | C | 25 | 0.0050817 | 7.6996e-05
2014 | 2013-07-06 | C | 109.3167 | 0.039391 | 0.00089931
2014 | 2013-07-06 | B | 14 | 0.00086236 | 4.3118e-05
2014 | 2013-07-06 | C | 28.568 | 0.073467 | 0.0011765
2014 | 2013-07-07 | C | 57 | 0.10147 | 0.00017555
2014 | 2013-07-07 | B | 78 | 0.015615 | 0.00024023
2014 | 2013-07-07 | C | 575.7081 | 0.28015 | 0.0028981
2014 | 2013-07-07 | C | 180.5657 | 0.053387 | 0.00072684
2014 | 2013-07-07 | C | 501.375 | 0.069487 | 0.0017494
2014 | 2013-07-07 | C | 450.0256 | 0.158 | 0.0020081
2014 | 2013-07-08 | C | 180 | 0.15023 | 0.00055437
2014 | 2013-07-08 | C | 23 | 0.0060919 | 7.0836e-05
2014 | 2013-07-08 | C | 3 | 0.00037882 | 9.2395e-06
2014 | 2013-07-08 | C | 1 | 2.1559e-05 | 3.0798e-06
2014 | 2013-07-07 | C | 1 | 0.0041732 | 3.0798e-06
2014 | 2013-07-09 | C | 277 | 0.21243 | 0.00085312
2014 | 2013-07-09 | C | 111 | 0.0071791 | 0.00034186
2014 | 2013-07-09 | C | 94.6879 | 0.040244 | 0.00034186
2014 | 2013-07-09 | B | 186 | 0.056139 | 0.00057285
2014 | 2013-07-09 | B | 27 | 0.030186 | 8.3156e-05
2014 | 2013-07-09 | B | 60 | 0.058579 | 0.00018479
2014 | 2013-07-09 | B | 275 | 0.31676 | 0.00084696
2014 | 2013-07-09 | B | 24 | 0.027866 | 7.3916e-05
2014 | 2013-07-09 | B | 31 | 0.03418 | 9.5475e-05
2014 | 2013-07-09 | B | 4 | 0.0025501 | 1.2319e-05
2014 | 2013-07-09 | B | 298 | 0.39924 | 0.00091779
2014 | 2013-07-10 | C | 237 | 0.010219 | 0.00072992
2014 | 2013-07-10 | C | 82.5402 | 0.056181 | 0.00034186
2014 | 2013-07-10 | B | 4 | 0.00092395 | 1.2319e-05
2014 | 2013-07-10 | C | 174 | 0.036441 | 0.00053589
2014 | 2013-07-10 | B | 29 | 0.0037512 | 8.9315e-05
2014 | 2013-07-10 | B | 2 | 0.00020943 | 6.1597e-06
2014 | 2013-07-10 | C | 1 | 3.6958e-05 | 3.0798e-06
2014 | 2013-07-10 | C | 62 | 0.0063014 | 0.00019095
2014 | 2013-07-10 | C | 108.8973 | 0.06104 | 0.00072684
2014 | 2013-07-10 | C | 174 | 0.011254 | 0.00053589
2014 | 2013-07-10 | B | 90 | 0.077612 | 0.00027719
2014 | 2013-07-10 | B | 124.6224 | 0.12589 | 0.00038498
2014 | 2013-07-10 | C | 131 | 0.018559 | 0.00040346
2014 | 2013-07-10 | C | 60 | 0.0085004 | 0.00018479
2014 | 2013-07-10 | B | 17 | 0.0075918 | 5.2357e-05
2014 | 2013-07-10 | C | 25.1439 | 0.021296 | 9.2395e-05
2014 | 2013-07-10 | C | 109.7831 | 0.055113 | 0.00046814
2014 | 2013-07-11 | C | 6 | 0.00042502 | 1.8479e-05
2014 | 2013-07-11 | C | 18 | 0.003049 | 5.5437e-05
2014 | 2013-07-11 | B | 31 | 0.034085 | 9.5475e-05
2014 | 2013-07-11 | B | 5 | 0.00072376 | 1.5399e-05
2014 | 2013-07-11 | C | 10.8696 | 0.015299 | 0.00015399
2014 | 2013-07-11 | B | 12 | 0.012381 | 3.6958e-05
2014 | 2013-07-11 | C | 76 | 0.014512 | 0.00023407
2014 | 2013-07-11 | B | 3 | 0.0026055 | 9.2395e-06
2014 | 2013-07-11 | C | 3 | 0.001081 | 9.2395e-06
2014 | 2013-07-11 | B | 10 | 0.012843 | 3.0798e-05
2014 | 2013-07-11 | C | 748.0635 | 0.28338 | 0.0037143
2014 | 2013-07-11 | C | 54 | 0.011475 | 0.00016631
2014 | 2013-07-12 | C | 10 | 0.0052357 | 3.0798e-05
2014 | 2013-07-12 | C | 50 | 0.032954 | 0.00015399
2014 | 2013-07-12 | C | 47 | 0.022581 | 0.00014475
2014 | 2013-07-12 | C | 2 | 4.3118e-05 | 6.1597e-06
2014 | 2013-07-11 | C | 1 | 0.0031014 | 3.0798e-06
2014 | 2013-07-12 | C | 6 | 0.00096091 | 1.8479e-05
2014 | 2013-07-12 | C | 203 | 0.030635 | 0.00062521
2014 | 2013-07-10 | C | 75.9948 | 1.2571 | 0.0007022
2014 | 2013-07-12 | C | 4 | 0.0019218 | 1.2319e-05
2014 | 2013-07-12 | C | 1 | 0.00082232 | 3.0798e-06
2014 | 2013-07-14 | C | 60 | 0.0083156 | 0.00018479
2014 | 2013-07-14 | C | 18 | 0.045847 | 5.5437e-05
2014 | 2013-07-15 | B | 3 | 0.00038806 | 9.2395e-06
2014 | 2013-07-15 | B | 2 | 0.0012319 | 6.1597e-06
2014 | 2013-07-14 | C | 29 | 0.1053 | 8.9315e-05
2014 | 2013-07-14 | C | 15 | 0.048369 | 4.6198e-05
2014 | 2013-07-15 | C | 2 | 0.00025871 | 6.1597e-06
2014 | 2013-07-14 | C | 119 | 0.087594 | 0.0003665
2014 | 2013-07-15 | B | 16 | 0.013206 | 4.9277e-05
2014 | 2013-07-15 | B | 4 | 0.0035603 | 1.2319e-05
2014 | 2013-07-14 | C | 37.6346 | 0.1202 | 0.0007792
2014 | 2013-07-15 | C | 108.6286 | 0.045835 | 0.0017555
2014 | 2013-07-15 | C | 7 | 0.0019834 | 2.1559e-05
2014 | 2013-07-15 | C | 20.1612 | 0.01484 | 0.0003665
2014 | 2013-07-15 | C | 5 | 0.00095475 | 1.5399e-05
2014 | 2013-07-15 | C | 8 | 0.0022914 | 2.4639e-05
2014 | 2013-07-15 | C | 12 | 0.0022544 | 3.6958e-05
2014 | 2013-07-14 | C | 287.7579 | 2.1571 | 0.0037974
2014 | 2013-07-15 | C | 11 | 0.0019988 | 3.3878e-05
2014 | 2013-07-15 | C | 3 | 0.00069296 | 9.2395e-06
2014 | 2013-07-14 | C | 249 | 0.77378 | 0.00076688
2014 | 2013-07-14 | C | 4.7107 | 0.018614 | 4.3118e-05
2014 | 2013-07-14 | C | 479.245 | 0.21845 | 0.0027657
2014 | 2013-07-15 | C | 21 | 0.0078259 | 6.4677e-05
2014 | 2013-07-15 | C | 10 | 0.0056977 | 3.0798e-05
2014 | 2013-07-14 | C | 53 | 0.17694 | 0.00016323
2014 | 2013-07-15 | C | 15 | 0.0015245 | 4.6198e-05
2014 | 2013-07-15 | C | 9 | 0.003936 | 2.7719e-05
2014 | 2013-07-15 | C | 175.279 | 0.33308 | 0.00078536
2014 | 2013-07-14 | C | 241.9749 | 0.97702 | 0.0022575
2014 | 2013-07-15 | C | 20 | 0.0025871 | 6.1597e-05
2014 | 2013-07-15 | C | 8 | 0.011876 | 2.4639e-05
2014 | 2013-07-14 | C | 252.6131 | 1.0674 | 0.0039946
2014 | 2013-07-15 | C | 25 | 0.027026 | 0
2014 | 2013-07-14 | C | 21 | 0.0053035 | 6.4677e-05
2014 | 2013-07-14 | C | 827.0792 | 2.1474 | 0.0043087
2014 | 2013-07-14 | C | 108 | 0.46501 | 0.00033262
2014 | 2013-07-14 | C | 34.1813 | 0.13959 | 0.00056977
2014 | 2013-07-14 | C | 95.6231 | 0.17022 | 0.00029566
2014 | 2013-07-14 | C | 240.7363 | 1.041 | 0.00084696
2014 | 2013-07-14 | C | 100.6545 | 0.06727 | 0.00066833
2014 | 2013-07-15 | C | 80.2533 | 0.017796 | 0.0004435
2014 | 2013-07-14 | C | 169.6573 | 0.65106 | 0.0032277
2014 | 2013-07-14 | C | 73.999 | 0.23201 | 0.00085312
2014 | 2013-07-14 | C | 285.4969 | 0.85379 | 0.0043395
2014 | 2013-07-14 | C | 75.8073 | 0.31192 | 0.0004127
2014 | 2013-07-14 | C | 27.7398 | 0.075268 | 0.00078536
2014 | 2013-07-14 | C | 142.0214 | 0.080482 | 0.00072684
2014 | 2013-07-14 | C | 35 | 0.0029105 | 0.00010779
2014 | 2013-07-16 | C | 270.6635 | 0.084194 | 0.0013982
2014 | 2013-07-15 | C | 1 | 0.0048415 | 3.0798e-06
2014 | 2013-07-15 | C | 1 | 0.003742 | 3.0798e-06
2014 | 2013-07-16 | B | 37 | 0.040568 | 0.00011395
2014 | 2013-07-16 | B | 27 | 0.031267 | 8.3156e-05
2014 | 2013-07-16 | B | 122 | 0.12813 | 0.00037574
2014 | 2013-07-16 | C | 1 | 0.0003049 | 3.0798e-06
2014 | 2013-07-16 | C | 2 | 0.00049277 | 6.1597e-06
2014 | 2013-07-16 | C | 15 | 0.01118 | 4.6198e-05
2014 | 2013-07-14 | C | 19 | 0.068816 | 5.8517e-05
2014 | 2013-07-14 | B | 216 | 0.071847 | 0.00066525
2014 | 2013-07-14 | C | 16.3823 | 0.080879 | 0.00024639
2014 | 2013-07-16 | C | 8 | 0.0018479 | 2.4639e-05
2014 | 2013-07-14 | C | 44 | 0.41535 | 0.00013551
2014 | 2013-07-15 | C | 28.5833 | 0.15186 | 0.00056361
2014 | 2013-07-14 | C | 18.0124 | 0.14318 | 0.00029258
2014 | 2013-07-15 | C | 2306 | 0.29119 | 0.0071021
2014 | 2013-07-14 | C | 30 | 0.27552 | 9.2395e-05
2014 | 2013-07-14 | C | 16.721 | 0.12813 | 0.00022175
2014 | 2013-07-16 | C | 9 | 0.0011087 | 2.7719e-05
2014 | 2013-07-17 | B | 52 | 0.008488 | 0.00016015
2014 | 2013-07-16 | C | 1 | 8.3156e-05 | 3.0798e-06
2014 | 2013-07-16 | C | 24 | 0.0012566 | 7.3916e-05
2014 | 2013-07-16 | C | 4 | 0.0019341 | 1.2319e-05
2014 | 2013-07-16 | C | 34 | 0.005864 | 0.00010471
2014 | 2013-07-16 | C | 59 | 0.015809 | 0.00018171
2014 | 2013-07-14 | C | 7 | 0.056484 | 2.1559e-05
2014 | 2013-07-14 | C | 32 | 0.0032523 | 9.8555e-05
2014 | 2013-07-16 | C | 166.0909 | 0.037853 | 0.00099479
2014 | 2013-07-16 | C | 22 | 0.0050817 | 6.7757e-05
2014 | 2013-07-14 | C | 101.0174 | 1.2896 | 0.0035357
2014 | 2013-07-15 | C | 40 | 0.0049277 | 0.00012319
2014 | 2013-07-17 | B | 173 | 0.15931 | 0.00053281
2014 | 2013-07-17 | B | 47 | 0.05269 | 0.00014475
2014 | 2013-07-17 | C | 46 | 0.0102 | 0.00014167
2014 | 2013-07-16 | C | 44 | 0.18118 | 0.00013551
2014 | 2013-07-18 | B | 164 | 0.055055 | 0.00050509
2014 | 2013-07-18 | C | 2 | 0.0014044 | 6.1597e-06
2014 | 2013-07-18 | B | 5 | 0.0062367 | 1.5399e-05
2014 | 2013-07-18 | B | 7 | 0.0080846 | 2.1559e-05
2014 | 2013-07-18 | B | 18 | 0.020068 | 5.5437e-05
2014 | 2013-07-18 | C | 47 | 0.018528 | 0.00014475
2014 | 2013-07-19 | C | 193 | 0.0083217 | 0.00059441
2014 | 2013-07-19 | C | 2448 | 0.45991 | 0.0075395
2014 | 2013-07-16 | C | 5 | 0.070559 | 1.5399e-05
2014 | 2013-07-19 | C | 2 | 0.00043118 | 6.1597e-06
2014 | 2013-07-19 | C | 118.9565 | 0.04946 | 0.00059441
2014 | 2013-07-19 | C | 65 | 0.014414 | 0.00020019
2014 | 2013-07-19 | C | 369 | 0.23184 | 0.0011365
2014 | 2013-07-19 | C | 228.6517 | 0.13943 | 0.00085928
2014 | 2013-07-19 | C | 321 | 0.00098863 | 0.00098863
2014 | 2013-07-19 | C | 185.0223 | 0.15158 | 0.0012751
2014 | 2013-07-19 | B | 34 | 0.021257 | 0.00010471
2014 | 2013-07-19 | B | 6 | 0.0068372 | 1.8479e-05
2014 | 2013-07-20 | B | 3 | 0.0018109 | 9.2395e-06
2014 | 2013-07-20 | B | 2 | 0.0021128 | 6.1597e-06
2014 | 2013-07-20 | C | 106.7692 | 0.024662 | 0.00034802
2014 | 2013-07-20 | C | 5.5 | 0.010113 | 6.7757e-05
2014 | 2013-07-19 | C | 595.1212 | 0.11547 | 0.0027934
2014 | 2013-07-21 | C | 22 | 0.0012874 | 6.7757e-05
2014 | 2013-07-21 | B | 37 | 0.028716 | 0.00011395
2014 | 2013-07-21 | C | 24 | 0.0082047 | 7.3916e-05
2014 | 2013-07-21 | C | 116 | 0.016077 | 0.00035726
2014 | 2013-07-19 | C | 425.5726 | 0.31195 | 0.0025255
2014 | 2013-07-22 | C | 11 | 0.0017278 | 3.3878e-05
2014 | 2013-07-22 | B | 30 | 0.021251 | 9.2395e-05
2014 | 2013-07-22 | C | 719.5914 | 0.19946 | 0.0024454
2014 | 2013-07-22 | C | 246 | 0.11516 | 0.00075764
2014 | 2013-07-22 | C | 25.9458 | 0.023333 | 0.00051741
2014 | 2013-07-23 | B | 12 | 0.0080199 | 3.6958e-05
2014 | 2013-07-18 | B | 2 | 0.00090547 | 6.1597e-06
2014 | 2013-07-09 | B | 2 | 0.00012319 | 6.1597e-06
2014 | 2013-07-23 | B | 1 | 0.00033878 | 3.0798e-06
2014 | 2013-07-10 | B | 1 | 0.00053897 | 3.0798e-06
2014 | 2013-07-19 | B | 338 | 0.070787 | 0.001041
2014 | 2013-07-23 | B | 2 | 0.00033878 | 6.1597e-06
2014 | 2013-07-23 | B | 18 | 0.019791 | 5.5437e-05
2014 | 2013-07-23 | C | 794 | 0.017118 | 0.0024454
2014 | 2013-07-24 | C | 324.7608 | 0.25205 | 0.0024454
2014 | 2013-07-24 | C | 482.5259 | 0.19617 | 0.0032277
2014 | 2013-07-24 | C | 219.4461 | 0.13585 | 0.0017186
2014 | 2013-07-24 | B | 16 | 0.0082786 | 4.9277e-05
2014 | 2013-07-24 | C | 66.875 | 0.033984 | 0.00064677
2014 | 2013-07-15 | B | 149 | 0.086731 | 0.0004589
2014 | 2013-07-24 | B | 65.26 | 0.059694 | 0.00029566
2014 | 2013-07-24 | B | 69 | 0.06779 | 0.00021251
2014 | 2013-07-24 | B | 56 | 0.068471 | 0.00017247
2014 | 2013-07-25 | C | 130 | 0.020019 | 0.00040038
2014 | 2013-07-25 | C | 412 | 0.013958 | 0.0012689
2014 | 2013-07-25 | B | 47 | 0.053124 | 0.00014475
2014 | 2013-07-25 | B | 36 | 0.032597 | 0.00011087
2014 | 2013-07-25 | B | 5 | 0.0015707 | 1.5399e-05
2014 | 2013-07-22 | C | 2 | 0.026856 | 6.1597e-06
2014 | 2013-07-25 | C | 904 | 0.025058 | 0.0027842
2014 | 2013-07-25 | B | 2 | 0.00053589 | 6.1597e-06
2014 | 2013-07-25 | C | 629 | 0.091049 | 0.0019372
2014 | 2013-07-25 | C | 25 | 0.0051587 | 7.6996e-05
2014 | 2013-07-25 | C | 11 | 0.0039299 | 3.3878e-05
2014 | 2013-07-25 | C | 32.7514 | 0.017148 | 0.00016631
2014 | 2013-07-25 | C | 509.509 | 0.25735 | 0.0027842
2014 | 2013-07-26 | B | 40 | 0.045458 | 0.00012319
2014 | 2013-07-26 | B | 3 | 0.00080384 | 9.2395e-06
2014 | 2013-07-26 | B | 4 | 0.0013182 | 1.2319e-05
2014 | 2013-07-26 | C | 5 | 0.0029566 | 1.5399e-05
2014 | 2013-07-27 | C | 210 | 0.3499 | 0.00064677
2014 | 2013-07-27 | C | 290 | 0.42425 | 0.00089315
2014 | 2013-07-28 | C | 244.3409 | 0.063965 | 0.0014506
2014 | 2013-07-28 | C | 5 | 0.0010163 | 1.5399e-05
2014 | 2013-07-27 | C | 2 | 0.00056669 | 6.1597e-06
2014 | 2013-07-23 | C | 1 | 0.009218 | 3.0798e-06
2014 | 2013-07-28 | C | 34 | 0.0085866 | 0.00010471
2014 | 2013-07-25 | C | 25 | 0.0019249 | 7.6996e-05
2014 | 2013-07-28 | C | 22 | 0.0014906 | 6.7757e-05
2014 | 2013-07-28 | C | 1 | 0.00098863 | 3.0798e-06
2014 | 2013-07-29 | C | 75.4131 | 0.048775 | 0.00044966
2014 | 2013-07-29 | C | 790.95 | 0.13885 | 0.0034802
2014 | 2013-07-29 | B | 2 | 0.00053589 | 6.1597e-06
2014 | 2013-07-29 | B | 2 | 0.00084388 | 6.1597e-06
2014 | 2013-07-29 | C | 2 | 0.00053589 | 6.1597e-06
2014 | 2013-07-29 | C | 189.7284 | 0.045578 | 0.00068065
2014 | 2013-07-29 | C | 55.6354 | 0.098183 | 0.00085312
2014 | 2013-07-30 | C | 132.436 | 0.068932 | 0.00097323
2014 | 2013-07-19 | B | 10 | 0.0023099 | 3.0798e-05
2014 | 2013-07-19 | B | 2 | 0.0004127 | 6.1597e-06
2014 | 2013-07-30 | C | 9 | 0.0042132 | 2.7719e-05
2014 | 2013-07-30 | C | 123 | 0.0075764 | 0.00037882
2014 | 2013-07-30 | C | 137.798 | 0.040742 | 0.00059133
2014 | 2013-07-30 | B | 2 | 0.0017678 | 6.1597e-06
2014 | 2013-07-30 | B | 8 | 0.0069728 | 2.4639e-05
2014 | 2013-07-20 | B | 20 | 0.012196 | 6.1597e-05
2014 | 2013-07-30 | C | 19 | 0.00058517 | 5.8517e-05
2014 | 2013-07-31 | C | 347 | 0.030992 | 0.0010687
2014 | 2013-07-31 | B | 13 | 0.015415 | 4.0038e-05
2014 | 2013-07-30 | C | 236 | 0.010176 | 0.00072684
2014 | 2013-08-01 | B | 50 | 0.012935 | 0.00015399
2014 | 2013-08-01 | C | 3 | 0.00089623 | 9.2395e-06
2014 | 2013-08-01 | B | 2 | 0.0010163 | 6.1597e-06
2014 | 2013-08-01 | B | 34 | 0.021257 | 0.00010471
2014 | 2013-08-01 | B | 146 | 0.098025 | 0.00044966
2014 | 2013-08-01 | C | 660.8679 | 0.10177 | 0.0020543
2014 | 2013-08-01 | B | 150 | 0.17278 | 0.00046198
2014 | 2013-08-01 | C | 24.0177 | 0.033287 | 9.2395e-05
2014 | 2013-08-02 | C | 198.6381 | 0.062401 | 0.000733
2014 | 2013-08-02 | B | 11 | 0.005285 | 3.3878e-05
2014 | 2013-08-02 | C | 681 | 0.098576 | 0.0020974
2014 | 2013-08-02 | C | 9 | 0.00036034 | 2.7719e-05
2014 | 2013-08-02 | C | 11.9795 | 0.028667 | 0.00044966
2014 | 2013-08-03 | B | 120 | 0.038436 | 0.00036958
2014 | 2013-08-03 | B | 247 | 0.066183 | 0.00076072
2014 | 2013-08-02 | C | 34 | 0.0033509 | 0.00010471
2014 | 2013-08-02 | C | 32 | 0.0013798 | 9.8555e-05
2014 | 2013-08-03 | C | 268 | 0.038794 | 0.0008254
2014 | 2013-08-03 | B | 70 | 0.044627 | 0.00021559
2014 | 2013-08-03 | B | 1 | 0.0011087 | 3.0798e-06
2014 | 2013-08-04 | C | 88.3992 | 0.06398 | 0.00048046
2014 | 2013-08-04 | B | 10 | 0.0036034 | 3.0798e-05
2014 | 2013-08-04 | C | 1 | 0.0012258 | 3.0798e-06
2014 | 2013-08-03 | C | 5 | 0.0057131 | 1.5399e-05
2014 | 2013-08-05 | C | 311 | 0.015325 | 0.00095783
2014 | 2013-08-05 | C | 284 | 0.0017494 | 0.00087468
2014 | 2013-08-05 | C | 27 | 0.0030768 | 8.3156e-05
2014 | 2013-08-05 | B | 3 | 0.0013859 | 9.2395e-06
2014 | 2013-08-05 | C | 38 | 0.0043303 | 0.00011703
2014 | 2013-08-05 | C | 31 | 0.0039145 | 9.5475e-05
2014 | 2013-08-04 | C | 2 | 0.010207 | 6.1597e-06
2014 | 2013-08-05 | C | 55 | 0.0081308 | 0.00016939
2014 | 2013-08-06 | C | 538.1271 | 0.29501 | 0.0032677
2014 | 2013-08-06 | B | 6 | 0.0064307 | 1.8479e-05
2014 | 2013-08-06 | B | 59 | 0.066143 | 0.00018171
2014 | 2013-08-06 | B | 225 | 0.13097 | 0.00069296
2014 | 2013-07-04 | B | 161 | 0.12545 | 0.00049585
2014 | 2013-08-06 | B | 83 | 0.093304 | 0.00025563
2014 | 2013-08-06 | B | 123 | 0.12577 | 0.00037882
2014 | 2013-08-06 | B | 8.241 | 0.010457 | 0.00013859
2014 | 2013-08-06 | C | 342.7544 | 0.17735 | 0.0026425
2014 | 2013-08-06 | C | 327.5195 | 0.15231 | 0.0013151
2014 | 2013-08-06 | C | 617.6857 | 0.12746 | 0.0027842
2014 | 2013-08-06 | C | 286 | 0.038757 | 0.00088083
2014 | 2013-08-06 | C | 175.9649 | 0.12194 | 0.00095167
2014 | 2013-08-07 | C | 236 | 0.009449 | 0.00072684
2014 | 2013-08-07 | B | 125 | 0.0053897 | 0.00038498
2014 | 2013-08-07 | C | 8 | 0.00056669 | 2.4639e-05
2014 | 2013-08-07 | B | 42 | 0.0060796 | 0.00012935
2014 | 2013-08-07 | B | 24 | 0.024984 | 7.3916e-05
2014 | 2013-08-07 | B | 2 | 0.0014537 | 6.1597e-06
2014 | 2013-08-07 | B | 19 | 0.01264 | 5.8517e-05
2014 | 2013-08-07 | B | 50 | 0.052973 | 0.00015399
2014 | 2013-08-07 | B | 155.6667 | 0.17116 | 0.00085004
2014 | 2013-08-08 | C | 5 | 0.00067757 | 1.5399e-05
2014 | 2013-08-08 | C | 6 | 0.0031414 | 1.8479e-05
2014 | 2013-08-08 | C | 135 | 0.025778 | 0.00041578
2014 | 2013-08-08 | B | 38 | 0.028556 | 0.00011703
2014 | 2013-08-08 | B | 43.1026 | 0.051374 | 0.00016631
2014 | 2013-08-09 | C | 18.9569 | 0.04046 | 0.00063137
2014 | 2013-08-09 | B | 193 | 0.091539 | 0.00059441
2014 | 2013-08-09 | C | 5 | 0.0014783 | 1.5399e-05
2014 | 2013-08-09 | C | 34.6719 | 0.0065138 | 0.00013243
2014 | 2013-08-07 | B | 2 | 0.0016508 | 6.1597e-06
2014 | 2013-08-09 | C | 131.5872 | 0.042958 | 0.0011118
2014 | 2013-08-10 | C | 15 | 0.0035572 | 4.6198e-05
2014 | 2013-08-10 | B | 70 | 0.062521 | 0.00021559
2014 | 2013-08-10 | C | 4 | 0.0012566 | 1.2319e-05
2014 | 2013-08-11 | C | 49.2565 | 0.058102 | 0.0015923
2014 | 2013-08-11 | C | 843 | 0.0051926 | 0.0027842
2014 | 2013-08-11 | B | 225 | 0.13236 | 0.00069296
2014 | 2013-08-12 | C | 189.6345 | 0.1133 | 0.0014044
2014 | 2013-08-12 | B | 2 | 0.00059749 | 6.1597e-06
2014 | 2013-08-12 | C | 26 | 0.0057655 | 8.0076e-05
2014 | 2013-08-12 | C | 643 | 0.053469 | 0.0019803
2014 | 2013-08-12 | B | 4 | 0.0014414 | 1.2319e-05
2014 | 2013-08-13 | B | 17 | 0.012409 | 5.2357e-05
2014 | 2013-08-13 | B | 1 | 0.00054513 | 3.0798e-06
2014 | 2013-08-13 | B | 24 | 0.025501 | 7.3916e-05
2014 | 2013-08-13 | B | 6 | 0.0090917 | 1.8479e-05
2014 | 2013-08-13 | C | 12 | 0.0033632 | 3.6958e-05
2014 | 2013-08-13 | C | 15 | 0.0028643 | 4.6198e-05
2014 | 2013-08-12 | C | 38 | 0.0019896 | 0.00011703
2014 | 2013-08-14 | C | 50.3121 | 0.04819 | 0.00058825
2014 | 2013-08-14 | B | 72 | 0.055437 | 0.00022175
2014 | 2013-08-13 | B | 2 | 0.0018356 | 6.1597e-06
2014 | 2013-08-14 | B | 38 | 0.036164 | 0.00011703
2014 | 2013-08-14 | B | 6 | 0.0062829 | 1.8479e-05
2014 | 2013-08-14 | B | 51.9376 | 0.066223 | 0.0003203
2014 | 2013-08-14 | C | 148 | 0.043758 | 0.00045582
2014 | 2013-08-14 | C | 20 | 0.0015399 | 6.1597e-05
2014 | 2013-08-14 | C | 227.68 | 0.13814 | 0.002313
2014 | 2013-08-15 | C | 32 | 0.0065046 | 9.8555e-05
2014 | 2013-08-15 | C | 15 | 0.011642 | 4.6198e-05
2014 | 2013-08-15 | B | 32 | 0.040703 | 9.8555e-05
2014 | 2013-08-14 | B | 67 | 0.073254 | 0.00020635
2014 | 2013-08-15 | B | 1 | 0.001158 | 3.0798e-06
2014 | 2013-08-15 | C | 13 | 0.00048046 | 4.0038e-05
2014 | 2013-08-15 | B | 222 | 0.16615 | 0.00068372
2014 | 2013-08-16 | C | 398 | 0.0012258 | 0.0012258
2014 | 2013-08-16 | C | 5 | 0.0027257 | 1.5399e-05
2014 | 2013-08-16 | C | 134.5 | 0.05178 | 0.00078536
2014 | 2013-08-16 | C | 584.3923 | 0.32037 | 0.0042964
2014 | 2013-08-15 | B | 61 | 0.075524 | 0.00018787
2014 | 2013-08-16 | C | 141.4632 | 0.040083 | 0.00049585
2014 | 2013-08-16 | C | 200.3636 | 0.1407 | 0.0022052
2014 | 2013-08-16 | C | 30 | 0.0020327 | 9.2395e-05
2014 | 2013-08-17 | C | 27 | 0.0070682 | 8.3156e-05
2014 | 2013-08-17 | C | 83 | 0.0071576 | 0.00025563
2014 | 2013-08-17 | C | 268 | 0.0099048 | 0.0008254
2014 | 2013-08-17 | C | 91.4389 | 0.072939 | 0.00086236
2014 | 2013-08-17 | C | 42 | 0.0046567 | 0.00012935
2014 | 2013-08-17 | C | 905 | 0.011149 | 0.0027873
2014 | 2013-08-17 | C | 25 | 0.0063907 | 7.6996e-05
2014 | 2013-08-17 | C | 257.8081 | 0.076225 | 0.0012535
2014 | 2013-08-18 | C | 89 | 0.0082232 | 0.00027411
2014 | 2013-08-18 | B | 338 | 0.08432 | 0.001041
2014 | 2013-08-18 | C | 146 | 0.075992 | 0.00044966
2014 | 2013-08-19 | B | 1 | 6.7757e-05 | 3.0798e-06
2014 | 2013-08-19 | C | 27 | 0.0007484 | 8.3156e-05
2014 | 2013-08-19 | B | 4 | 0.0007022 | 1.2319e-05
2014 | 2013-08-19 | C | 66 | 0.0042687 | 0.00020327
2014 | 2013-08-19 | B | 5 | 0.00482 | 1.5399e-05
2014 | 2013-08-16 | B | 3 | 0.0016631 | 9.2395e-06
2014 | 2013-08-19 | C | 58.122 | 0.0068022 | 0.00029258
2014 | 2013-08-20 | C | 686.6694 | 0.25589 | 0.0075425
2014 | 2013-08-20 | B | 25 | 0.017324 | 7.6996e-05
2014 | 2013-08-20 | B | 43 | 0.011522 | 0.00013243
2014 | 2013-08-20 | C | 37 | 0.0054698 | 0.00011395
2014 | 2013-08-20 | B | 38 | 0.041781 | 0.00011703
2014 | 2013-08-20 | C | 99.3578 | 0.16157 | 0.00051433
2014 | 2013-08-21 | C | 21 | 0.0054975 | 6.4677e-05
2014 | 2013-08-21 | B | 50 | 0.03973 | 0.00015399
2014 | 2013-08-21 | C | 46 | 0.0080753 | 0.00014167
2014 | 2013-08-21 | C | 11.6256 | 0.0080203 | 6.4677e-05
2014 | 2013-08-22 | C | 803 | 0.093978 | 0.0024731
2014 | 2013-08-21 | B | 55.4411 | 0.061811 | 0.00019095
2014 | 2013-08-18 | B | 30.2438 | 0.063898 | 0.00088391
2014 | 2013-08-21 | C | 41.1019 | 0.16861 | 0.00023715
2014 | 2013-08-22 | C | 11 | 0.0063352 | 3.3878e-05
2014 | 2013-08-22 | C | 1 | 0.00019403 | 3.0798e-06
2014 | 2013-08-22 | B | 6 | 0.00401 | 1.8479e-05
2014 | 2013-08-22 | B | 1 | 0.0003819 | 3.0798e-06
2014 | 2013-08-22 | B | 44 | 0.024663 | 0.00013551
2014 | 2013-08-22 | B | 9 | 0.0089808 | 2.7719e-05
2014 | 2013-08-22 | C | 3 | 0.0014506 | 9.2395e-06
2014 | 2013-08-22 | B | 16 | 0.0010841 | 4.9277e-05
2014 | 2013-08-22 | C | 2 | 0.0003511 | 6.1597e-06
2014 | 2013-08-22 | C | 2 | 0.0010287 | 6.1597e-06
2014 | 2013-08-22 | C | 7.7035 | 0.023132 | 0.00037882
2014 | 2013-08-23 | B | 11 | 0.0019311 | 3.3878e-05
2014 | 2013-08-23 | C | 2.0447 | 0.0019522 | 9.2395e-06
2014 | 2013-08-23 | C | 1 | 0.00022175 | 3.0798e-06
2014 | 2013-08-22 | B | 3 | 0.0029751 | 9.2395e-06
2014 | 2013-08-23 | B | 54 | 0.05771 | 0.00016631
2014 | 2013-08-23 | C | 5 | 0.00018479 | 1.5399e-05
2014 | 2013-08-24 | C | 35 | 0.0095937 | 0.00010779
2014 | 2013-08-24 | C | 6 | 0.0024208 | 1.8479e-05
2014 | 2013-08-25 | C | 44 | 0.0013551 | 0.00013551
2014 | 2013-08-25 | C | 432.3721 | 0.22505 | 0.0025286
2014 | 2013-08-24 | C | 200 | 0.15399 | 0.00061597
2014 | 2013-08-26 | B | 89 | 0.086069 | 0.00027411
2014 | 2013-08-26 | B | 2 | 0.0019157 | 6.1597e-06
2014 | 2013-08-26 | B | 98 | 0.041048 | 0.00030182
2014 | 2013-08-26 | C | 4 | 0.0017001 | 1.2319e-05
2014 | 2013-08-26 | B | 123 | 0.03864 | 0.00037882
2014 | 2013-08-27 | B | 28 | 0.020007 | 8.6236e-05
2014 | 2013-08-27 | C | 67 | 0.004746 | 0.00020635
2014 | 2013-08-27 | B | 82 | 0.06642 | 0.00025255
2014 | 2013-08-19 | B | 2 | 0.0020142 | 6.1597e-06
2014 | 2013-08-23 | B | 2 | 0.00099171 | 6.1597e-06
2014 | 2013-08-28 | B | 235 | 0.26273 | 0.00072376
2014 | 2013-08-28 | B | 10 | 0.0016015 | 3.0798e-05
2014 | 2013-08-29 | C | 29 | 0.0036619 | 8.9315e-05
2014 | 2013-08-29 | C | 99 | 0.011891 | 0.0003049
2014 | 2013-08-29 | B | 31 | 0.021768 | 9.5475e-05
2014 | 2013-08-29 | C | 205.7963 | 0.10078 | 0.0018787
2014 | 2013-08-29 | C | 103.3053 | 0.029271 | 0.00071452
2014 | 2013-08-29 | C | 5 | 0.0016939 | 1.5399e-05
2014 | 2013-08-29 | C | 160.1229 | 0.086795 | 0.0012381
2014 | 2013-08-29 | C | 50 | 0.00030798 | 0.00015399
2014 | 2013-08-30 | C | 827.1081 | 0.27512 | 0.0034309
2014 | 2013-08-30 | C | 21 | 0.0070498 | 6.4677e-05
2014 | 2013-08-30 | C | 33.2885 | 0.010355 | 0.00015399
2014 | 2013-08-30 | C | 47 | 0.0070929 | 0.00014475
2014 | 2013-08-30 | C | 334.4583 | 0.24413 | 0.0010964
2014 | 2013-08-31 | B | 18 | 0.0024947 | 5.5437e-05
2014 | 2013-08-31 | C | 32 | 0.0027595 | 9.8555e-05
2014 | 2013-09-01 | C | 304 | 0.058985 | 0.00093627
2014 | 2013-09-01 | C | 59.1679 | 0.023325 | 0.00088083
2014 | 2013-09-01 | C | 10 | 0.00021559 | 3.0798e-05
2014 | 2013-09-02 | B | 9.8387 | 0.0017878 | 3.0798e-05
2014 | 2013-09-02 | B | 3 | 0.0029105 | 9.2395e-06
2014 | 2013-09-02 | B | 76 | 0.055708 | 0.00023407
2014 | 2013-09-03 | C | 14 | 0.0013798 | 4.3118e-05
2014 | 2013-09-03 | C | 11 | 0.0032523 | 3.3878e-05
2014 | 2013-09-03 | B | 25 | 0.011087 | 7.6996e-05
2014 | 2013-09-03 | B | 9 | 0.0075117 | 2.7719e-05
2014 | 2013-09-03 | B | 2 | 0.0014598 | 6.1597e-06
2014 | 2013-09-03 | B | 5 | 0.00405 | 1.5399e-05
2014 | 2013-09-03 | B | 183 | 0.21417 | 0.00056361
2014 | 2013-09-03 | B | 52 | 0.023542 | 0.00016015
2014 | 2013-09-03 | B | 82 | 0.044953 | 0.00025255
2014 | 2013-09-03 | C | 124.7016 | 0.046471 | 0.00091779
2014 | 2013-09-04 | B | 1 | 0.00086852 | 3.0798e-06
2014 | 2013-09-04 | C | 764 | 0.13177 | 0.002353
2014 | 2013-09-03 | B | 8 | 0.0074655 | 2.4639e-05
2014 | 2013-09-04 | C | 38 | 0.014746 | 0.00011703
2014 | 2013-09-04 | B | 7 | 0.0073731 | 2.1559e-05
2014 | 2013-09-04 | C | 2534.6162 | 1.4207 | 0.017016
2014 | 2013-09-04 | C | 96 | 0.028384 | 0.00029566
2014 | 2013-09-05 | C | 155.7143 | 0.15634 | 0.0014783
2014 | 2013-09-05 | C | 6 | 0.0021251 | 1.8479e-05
2014 | 2013-09-05 | C | 139.6398 | 0.1587 | 0.00046198
2014 | 2013-09-05 | C | 188.9738 | 0.13153 | 0.00072684
2014 | 2013-09-05 | C | 40 | 0.0064061 | 0.00012319
2014 | 2013-09-05 | C | 15 | 0.018895 | 4.6198e-05
2014 | 2013-09-05 | C | 34 | 0.0050263 | 0.00010471
2014 | 2013-09-05 | C | 256.6449 | 0.10671 | 0.0012874
2014 | 2013-09-05 | B | 1 | 0.00080076 | 3.0798e-06
2014 | 2013-09-05 | C | 1 | 0.00032954 | 3.0798e-06
2014 | 2013-09-05 | C | 3 | 0.0025686 | 9.2395e-06
2014 | 2013-09-05 | C | 160.2293 | 0.17716 | 0.0010441
2014 | 2013-09-05 | C | 235.766 | 0.16846 | 0.00094551
2014 | 2013-09-04 | B | 14 | 0.0087098 | 4.3118e-05
2014 | 2013-09-04 | B | 113 | 0.095358 | 0.00034802
2014 | 2013-09-05 | C | 114 | 0.016853 | 0.0003511
2014 | 2013-09-05 | C | 95 | 0.016092 | 0.00029258
2014 | 2013-09-05 | C | 6 | 0.0027903 | 1.8479e-05
2014 | 2013-09-05 | C | 30 | 0.0065601 | 9.2395e-05
2014 | 2013-09-05 | C | 6 | 0.0016262 | 1.8479e-05
2014 | 2013-09-05 | B | 56 | 0.069333 | 0.00017247
2014 | 2013-09-05 | C | 1428 | 0.11875 | 0.004398
2014 | 2013-09-05 | B | 25 | 0.018248 | 7.6996e-05
2014 | 2013-09-05 | C | 5 | 0.00098555 | 1.5399e-05
2014 | 2013-09-05 | C | 4 | 0.0010348 | 1.2319e-05
2014 | 2013-09-05 | C | 47 | 0.0082509 | 0.00014475
2014 | 2013-09-05 | C | 30.261 | 0.056851 | 0.00028951
2014 | 2013-09-05 | C | 108 | 0.00066525 | 0.00033262
2014 | 2013-09-05 | C | 74 | 0.0011395 | 0.00022791
2014 | 2013-09-06 | C | 78 | 0.048526 | 0.00024023
2014 | 2013-09-05 | B | 8 | 0.0084264 | 2.4639e-05
2014 | 2013-09-05 | C | 18 | 0.0045458 | 5.5437e-05
2014 | 2013-09-05 | C | 38.4324 | 0.030302 | 0.00012319
2014 | 2013-09-05 | C | 133 | 0.070454 | 0.00040962
2014 | 2013-09-05 | C | 182.1355 | 0.20531 | 0.00098863
2014 | 2013-09-05 | C | 9 | 0.011198 | 2.7719e-05
2014 | 2013-09-05 | C | 75 | 0.0060057 | 0.00023099
2014 | 2013-09-05 | C | 122 | 0.01766 | 0.00037574
2014 | 2013-09-05 | B | 7 | 0.0019834 | 2.1559e-05
2014 | 2013-09-05 | B | 1 | 0.00029566 | 3.0798e-06
2014 | 2013-09-04 | C | 6 | 0.0071514 | 1.8479e-05
2014 | 2013-09-06 | B | 67 | 0.075111 | 0.00020635
2014 | 2013-09-06 | C | 77.5196 | 0.047988 | 0.00072992
2014 | 2013-09-06 | C | 2 | 0.0004743 | 6.1597e-06
2014 | 2013-09-07 | C | 4 | 0.0020943 | 1.2319e-05
2014 | 2013-09-07 | C | 3 | 0.00078536 | 9.2395e-06
2014 | 2013-09-07 | B | 47 | 0.051242 | 0.00014475
2014 | 2013-09-08 | C | 284.1374 | 0.11201 | 0.0011457
2014 | 2013-09-08 | C | 101 | 0.052881 | 0.00031106
2014 | 2013-09-08 | C | 500.6822 | 0.49036 | 0.0029628
2014 | 2013-09-08 | C | 1197.55 | 0.284 | 0.0050756
2014 | 2013-09-08 | B | 41 | 0.020583 | 0.00012627
2014 | 2013-09-08 | C | 8 | 0.00088699 | 2.4639e-05
2014 | 2013-09-07 | C | 91.2157 | 0.070794 | 0.00040654
2014 | 2013-09-07 | C | 288 | 0.052333 | 0.00088699
2014 | 2013-09-08 | C | 194.9545 | 0.10387 | 0.0015769
2014 | 2013-09-08 | C | 90 | 0.019403 | 0.00027719
2014 | 2013-09-08 | C | 48 | 0.010644 | 0.00014783
2014 | 2013-09-08 | C | 149 | 0.028452 | 0.0004589
2014 | 2013-09-06 | C | 342.1556 | 0.091679 | 0.0011488
2014 | 2013-09-05 | B | 25 | 0.018248 | 7.6996e-05
2014 | 2013-09-09 | B | 63 | 0.055881 | 0.00019403
2014 | 2013-09-09 | C | 20 | 0.0034494 | 6.1597e-05
2014 | 2013-08-09 | B | 24 | 0.007096 | 7.3916e-05
2014 | 2013-09-09 | C | 161 | 0.010413 | 0.00049585
2014 | 2013-09-09 | C | 4 | 0.0041516 | 1.2319e-05
2014 | 2013-09-09 | C | 3 | 0.0007484 | 9.2395e-06
2014 | 2013-09-09 | C | 26 | 0.0051249 | 8.0076e-05
2014 | 2013-09-09 | C | 226.5951 | 0.1961 | 0.0019988
2014 | 2013-09-09 | B | 2 | 0.0021128 | 6.1597e-06
2014 | 2013-09-09 | C | 167.2078 | 0.077761 | 0.00067757
2014 | 2013-09-09 | C | 1310 | 0.20576 | 0.0040346
2014 | 2013-09-09 | C | 4 | 0.0010718 | 1.2319e-05
2014 | 2013-09-09 | C | 19 | 0.005091 | 5.8517e-05
2014 | 2013-09-07 | C | 1 | 0.00019711 | 3.0798e-06
2014 | 2013-09-05 | B | 1 | 0.0010687 | 3.0798e-06
2014 | 2013-09-10 | C | 102.4881 | 0.025567 | 0.00051433
2014 | 2013-09-10 | C | 4 | 0.00018479 | 1.2319e-05
2014 | 2013-09-10 | B | 8 | 0.0090917 | 2.4639e-05
2014 | 2013-09-10 | B | 109 | 0.12824 | 0.0003357
2014 | 2013-09-10 | B | 13 | 0.014414 | 4.0038e-05
2014 | 2013-09-10 | B | 52 | 0.019378 | 0.00016015
2014 | 2013-09-10 | B | 80 | 0.076873 | 0.00024639
2014 | 2013-09-10 | B | 74 | 0.067689 | 0.00022791
2014 | 2013-09-10 | B | 7 | 0.0076965 | 2.1559e-05
2014 | 2013-09-10 | C | 974.9798 | 0.28827 | 0.0030121
2014 | 2013-09-10 | C | 1731.9474 | 0.085346 | 0.0058332
2014 | 2013-09-10 | C | 174 | 0.021436 | 0.00053589
2014 | 2013-09-10 | C | 76.9016 | 0.028185 | 0.00024639
2014 | 2013-09-10 | C | 4 | 0.0007022 | 1.2319e-05
2014 | 2013-09-10 | C | 5 | 0.0084234 | 1.5399e-05
2014 | 2013-09-11 | C | 21 | 0.0089901 | 6.4677e-05
2014 | 2013-09-10 | C | 43.3333 | 0.0028027 | 0.00015399
2014 | 2013-09-10 | C | 106.5884 | 0.11785 | 0.0023776
2014 | 2013-09-11 | C | 112 | 0.016902 | 0.00034494
2014 | 2013-09-11 | C | 71.2734 | 0.027439 | 0.0003819
2014 | 2013-09-10 | C | 157.5922 | 0.13542 | 0.00055437
2014 | 2013-09-05 | C | 60 | 0.053035 | 0.00018479
2014 | 2013-09-11 | C | 18 | 0.0043795 | 5.5437e-05
2014 | 2013-09-11 | C | 584.9741 | 0.20358 | 0.0053404
2014 | 2013-09-11 | C | 364 | 0.18161 | 0.0011211
2014 | 2013-09-10 | C | 2 | 0.00060981 | 6.1597e-06
2014 | 2013-09-10 | C | 224 | 0.046912 | 0.00068988
2014 | 2013-09-10 | C | 69 | 0.0063753 | 0.00021251
2014 | 2013-09-10 | C | 27.5376 | 0.007633 | 0.00020327
2014 | 2013-09-11 | B | 56 | 0.042428 | 0.00017247
2014 | 2013-09-11 | B | 7 | 0.0073085 | 2.1559e-05
2014 | 2013-09-11 | C | 55 | 0.0059287 | 0.00016939
2014 | 2013-09-11 | C | 211.53 | 0.20456 | 0.00068065
2014 | 2013-09-11 | C | 97.4152 | 0.91237 | 0.00064369
2014 | 2013-09-11 | C | 672 | 0.22559 | 0.0020697
2014 | 2013-09-11 | C | 57.2734 | 0.048508 | 0.00021867
2014 | 2013-09-11 | C | 103.8182 | 0.048281 | 0.00072068
2014 | 2013-09-11 | C | 8 | 0.0007638 | 2.4639e-05
2014 | 2013-09-11 | C | 160.4276 | 0.1418 | 0.00086852
2014 | 2013-09-11 | C | 232.2483 | 0.20243 | 0.0011211
2014 | 2013-09-11 | C | 762 | 0.08918 | 0.0023468
2014 | 2013-09-11 | C | 239.5822 | 0.10552 | 0.0022729
2014 | 2013-09-11 | C | 1696.9178 | 0.36584 | 0.0057439
2014 | 2013-09-11 | C | 74.2642 | 0.023558 | 0.00029566
2014 | 2013-09-11 | C | 231.8409 | 0.15495 | 0.0012135
2014 | 2013-09-11 | C | 134.821 | 0.43018 | 0.00053589
2014 | 2013-09-11 | C | 526.7955 | 0.06652 | 0.0019649
2014 | 2013-09-11 | C | 161.9678 | 0.41703 | 0.0021436
2014 | 2013-09-11 | C | 27.8475 | 0.06218 | 0.0012135
2014 | 2013-09-12 | C | 516.0606 | 0.10013 | 0.0024054
2014 | 2013-09-11 | C | 209 | 0.0025747 | 0.00064369
2014 | 2013-09-12 | C | 617 | 0.051307 | 0.0019003
2014 | 2013-09-11 | C | 290.899 | 0.18366 | 0.0018448
2014 | 2013-09-12 | C | 10 | 0.00092395 | 3.0798e-05
2014 | 2013-09-11 | C | 1401 | 0.14239 | 0.0043149
2014 | 2013-09-11 | C | 24 | 0.066007 | 7.3916e-05
2014 | 2013-09-12 | B | 54 | 0.066857 | 0.00016631
2014 | 2013-09-11 | B | 27.0235 | 0.035205 | 0.00016631
2014 | 2013-09-12 | C | 225.507 | 0.24447 | 0.0007022
2014 | 2013-09-12 | C | 5 | 0.0055591 | 1.5399e-05
2014 | 2013-09-12 | C | 16 | 0.0028088 | 4.9277e-05
2014 | 2013-09-12 | C | 3 | 0.0042687 | 9.2395e-06
2014 | 2013-09-12 | B | 67 | 0.0024762 | 0.00020635
2014 | 2013-09-12 | C | 321.2248 | 0.12465 | 0.0021313
2014 | 2013-09-12 | C | 193.0469 | 0.12486 | 0.0007946
2014 | 2013-09-12 | C | 130.2069 | 0.11509 | 0.00094551
2014 | 2013-09-11 | C | 171.9353 | 1.407 | 0.00081616
2014 | 2013-09-12 | C | 95 | 0.031307 | 0.00029258
2014 | 2013-09-12 | C | 8 | 0.0020697 | 2.4639e-05
2014 | 2013-09-11 | C | 97.7064 | 0.74207 | 0.00081924
2014 | 2013-09-11 | C | 11.6332 | 0.061231 | 0.00023715
2014 | 2013-09-12 | C | 226 | 0.17401 | 0.00069604
2014 | 2013-09-11 | C | 55.6219 | 0.45482 | 0.0034371
2014 | 2013-09-12 | C | 64 | 0.058739 | 0.00019711
2014 | 2013-09-12 | C | 13 | 0.0040839 | 4.0038e-05
2014 | 2013-09-11 | C | 12 | 0.0023653 | 3.6958e-05
2014 | 2013-09-12 | C | 249 | 0.042178 | 0.00076688
2014 | 2013-09-11 | C | 365.1926 | 1.3688 | 0.0026641
2014 | 2013-09-11 | C | 11.6881 | 0.035674 | 0.00014475
2014 | 2013-09-11 | C | 9 | 0.028661 | 2.7719e-05
2014 | 2013-09-11 | C | 145.4044 | 0.48813 | 0.0022175
2014 | 2013-09-12 | C | 174 | 0.05734 | 0.00053589
2014 | 2013-09-12 | C | 51.0278 | 0.022159 | 0.00026487
2014 | 2013-09-11 | C | 112 | 0.41462 | 0.00034494
2014 | 2013-09-11 | C | 5 | 0.016061 | 1.5399e-05
2014 | 2013-09-12 | C | 91 | 0.014013 | 0.00028027
2014 | 2013-09-12 | B | 40 | 0.016262 | 0.00012319
2014 | 2013-09-13 | C | 76 | 0.013342 | 0.00023407
2014 | 2013-09-13 | B | 2 | 0.0011457 | 6.1597e-06
2014 | 2013-09-12 | B | 86 | 0.088995 | 0.00026487
2014 | 2013-09-13 | C | 8 | 0.0025624 | 2.4639e-05
2014 | 2013-09-13 | C | 128.8182 | 0.046815 | 0.00068065
2014 | 2013-09-13 | C | 4 | 0.00057901 | 1.2319e-05
2014 | 2013-09-14 | C | 7 | 0.0018541 | 2.1559e-05
2014 | 2013-09-14 | C | 7 | 0.0017678 | 2.1559e-05
2014 | 2013-09-14 | C | 10 | 0.0036034 | 3.0798e-05
2014 | 2013-09-14 | C | 64.1243 | 0.032784 | 0.00051433
2014 | 2013-09-14 | C | 72.1472 | 0.043107 | 0.0013521
2014 | 2013-09-14 | C | 38 | 0.0039792 | 0.00011703
2014 | 2013-09-13 | C | 4 | 0.017481 | 1.2319e-05
2014 | 2013-09-14 | C | 2 | 0.00055437 | 6.1597e-06
2014 | 2013-09-14 | C | 39 | 0.0043241 | 0.00012011
2014 | 2013-09-12 | C | 632 | 0.39708 | 0.0019465
2014 | 2013-09-15 | C | 14 | 0.0012073 | 4.3118e-05
2014 | 2013-09-13 | C | 13 | 0.0015214 | 4.0038e-05
2014 | 2013-09-12 | C | 59.2559 | 0.20987 | 0.00019095
2014 | 2013-09-12 | C | 30 | 0.067818 | 9.2395e-05
2014 | 2013-09-11 | C | 3 | 0.021168 | 9.2395e-06
2014 | 2013-09-11 | C | 7.4266 | 0.036711 | 0.00012935
2014 | 2013-09-12 | C | 17.193 | 0.05417 | 0.00015399
2014 | 2013-09-11 | C | 108.3533 | 0.47787 | 0.0011149
2014 | 2013-09-11 | C | 63.2344 | 0.27772 | 0.00078844
2014 | 2013-09-12 | C | 4 | 0.0025871 | 1.2319e-05
2014 | 2013-09-12 | C | 3.4562 | 0.0068977 | 0.00012319
2014 | 2013-09-12 | C | 4 | 0.013206 | 1.2319e-05
2014 | 2013-09-11 | C | 283.2958 | 0.97372 | 0.0012812
2014 | 2013-09-11 | C | 95.4995 | 0.56089 | 0.00043118
2014 | 2013-09-13 | C | 1 | 0.00018787 | 3.0798e-06
2014 | 2013-09-12 | C | 6.1364 | 0.044148 | 0.00020019
2014 | 2013-09-13 | B | 19 | 0.010299 | 5.8517e-05
2014 | 2013-09-16 | C | 45 | 0.013859 | 0.00013859
2014 | 2013-09-12 | B | 6 | 0.0031414 | 1.8479e-05
2014 | 2013-09-16 | C | 34 | 0.011937 | 0.00010471
2014 | 2013-09-16 | B | 30 | 0.028643 | 9.2395e-05
2014 | 2013-09-16 | B | 29 | 0.029028 | 8.9315e-05
2014 | 2013-09-16 | C | 23 | 0.0039668 | 7.0836e-05
2014 | 2013-09-13 | C | 9 | 0.0072345 | 2.7719e-05
2014 | 2013-09-13 | C | 44 | 0.0012196 | 0.00013551
2014 | 2013-09-16 | B | 7 | 0.0067264 | 2.1559e-05
2014 | 2013-09-13 | C | 2 | 0.0026179 | 6.1597e-06
2014 | 2013-09-14 | C | 1 | 0.0097415 | 3.0798e-06
2014 | 2013-09-17 | C | 5 | 0.0034956 | 1.5399e-05
2014 | 2013-09-17 | C | 6 | 0.00031414 | 1.8479e-05
2014 | 2013-09-17 | C | 161 | 0.0957 | 0.00049585
2014 | 2013-09-17 | B | 67 | 0.067476 | 0.00020635
2014 | 2013-09-17 | B | 2 | 0.002236 | 6.1597e-06
2014 | 2013-09-17 | B | 168 | 0.12107 | 0.00051741
2014 | 2013-09-17 | B | 54 | 0.054218 | 0.00016631
2014 | 2013-09-17 | B | 6 | 0.0078166 | 1.8479e-05
2014 | 2013-09-17 | B | 1 | 0.0010194 | 3.0798e-06
2014 | 2013-09-17 | B | 117 | 0.13621 | 0.00036034
2014 | 2013-09-17 | B | 95 | 0.1106 | 0.00029258
2014 | 2013-09-17 | B | 30 | 0.026148 | 9.2395e-05
2014 | 2013-09-17 | C | 2 | 0.00040038 | 6.1597e-06
2014 | 2013-09-17 | C | 118 | 0.020715 | 0.00036342
2014 | 2013-09-17 | C | 3 | 0.00059133 | 9.2395e-06
2014 | 2013-09-17 | C | 93.9737 | 0.06512 | 0.00040654
2014 | 2013-09-18 | B | 25 | 0.028104 | 7.6996e-05
2014 | 2013-09-18 | C | 44 | 0.0046074 | 0.00013551
2014 | 2013-09-18 | C | 2 | 0.0020204 | 6.1597e-06
2014 | 2013-09-18 | C | 214.4323 | 0.10038 | 0.0012412
2014 | 2013-09-17 | C | 5 | 0.019742 | 1.5399e-05
2014 | 2013-09-18 | C | 4 | 0.00052973 | 1.2319e-05
2014 | 2013-09-19 | C | 15 | 0.00073916 | 4.6198e-05
2014 | 2013-09-19 | B | 12 | 0.00972 | 3.6958e-05
2014 | 2013-09-19 | B | 31 | 0.023105 | 9.5475e-05
2014 | 2013-09-19 | B | 15 | 0.013028 | 4.6198e-05
2014 | 2013-09-19 | B | 7 | 0.0034279 | 2.1559e-05
2014 | 2013-09-19 | C | 9 | 0.011087 | 2.7719e-05
2014 | 2013-09-19 | C | 272.146 | 0.11231 | 0.0024023
2014 | 2013-09-20 | C | 299.6846 | 0.13476 | 0.002159
2014 | 2013-09-20 | B | 44 | 0.01843 | 0.00013551
2014 | 2013-09-20 | B | 32 | 0.025329 | 9.8555e-05
2014 | 2013-09-20 | B | 20 | 0.017124 | 6.1597e-05
2014 | 2013-09-20 | B | 150 | 0.14367 | 0.00046198
2014 | 2013-09-20 | C | 1800.6667 | 0.033275 | 0.0062213
2014 | 2013-09-21 | C | 154 | 0.011383 | 0.0004743
2014 | 2013-09-22 | C | 420.0702 | 0.069862 | 0.0021744
2014 | 2013-09-22 | C | 34 | 0.07152 | 0.00010471
2014 | 2013-09-22 | C | 3 | 0.0014968 | 9.2395e-06
2014 | 2013-09-22 | C | 3 | 0.00052665 | 9.2395e-06
2014 | 2013-09-22 | C | 8 | 0.0017001 | 2.4639e-05
2014 | 2013-09-22 | C | 250 | 0.012319 | 0.00076996
2014 | 2013-09-22 | C | 5.6502 | 0.010145 | 2.1559e-05
2014 | 2013-09-22 | C | 6 | 0.0062274 | 1.8479e-05
2014 | 2013-09-22 | C | 1 | 0.00050509 | 3.0798e-06
2014 | 2013-09-22 | C | 713 | 0.026351 | 0.0021959
2014 | 2013-09-21 | B | 9 | 0.0102 | 2.7719e-05
2014 | 2013-09-22 | C | 356.5 | 0.014274 | 0.002199
2014 | 2013-09-20 | C | 9 | 0.0098955 | 2.7719e-05
2014 | 2013-09-21 | C | 2 | 0.00042502 | 6.1597e-06
2014 | 2013-09-23 | C | 1916 | 0.011802 | 0.005901
2014 | 2013-09-23 | C | 44.0132 | 0.081739 | 0.00094243
2014 | 2013-09-23 | C | 784 | 0.041048 | 0.0024146
2014 | 2013-09-20 | C | 9 | 0.0046013 | 2.7719e-05
2014 | 2013-09-23 | B | 9 | 0.0098401 | 2.7719e-05
2014 | 2013-09-23 | C | 29 | 0.0030367 | 8.9315e-05
2014 | 2013-09-23 | C | 53 | 0.0034279 | 0.00016323
2014 | 2013-09-23 | C | 22.1823 | 0.042904 | 0.00014475
2014 | 2013-09-23 | C | 56 | 0.0098309 | 0.00017247
2014 | 2013-09-24 | B | 33 | 0.01738 | 0.00010163
2014 | 2013-09-24 | B | 22 | 0.0092826 | 6.7757e-05
2014 | 2013-09-24 | C | 178 | 0.042761 | 0.00054821
2014 | 2013-09-24 | B | 36 | 0.04313 | 0.00011087
2014 | 2013-09-24 | C | 30 | 0.0028643 | 9.2395e-05
2014 | 2013-09-23 | C | 133.5868 | 0.067474 | 0.0012412
2014 | 2013-09-24 | C | 208.0455 | 0.040367 | 0.0016354
2014 | 2013-09-24 | C | 305.6984 | 1.3332 | 0.0026641
2014 | 2013-09-25 | C | 30 | 9.2395e-05 | 9.2395e-05
2014 | 2013-09-25 | C | 123.3351 | 0.071412 | 0.00072684
2014 | 2013-09-25 | C | 37.5641 | 0.013189 | 0.00031722
2014 | 2013-09-25 | C | 288 | 0.015079 | 0.00088699
2014 | 2013-09-24 | C | 1149 | 0.060159 | 0.0035387
2014 | 2013-09-24 | C | 61 | 0.0075148 | 0.00018787
2014 | 2013-09-25 | C | 20 | 0.0036342 | 6.1597e-05
2014 | 2013-09-25 | C | 42 | 0.0060796 | 0.00012935
2014 | 2013-09-24 | C | 99 | 0.014331 | 0.0003049
2014 | 2013-09-24 | C | 459.9674 | 0.25641 | 0.001851
2014 | 2013-09-24 | C | 1 | 0.0014876 | 3.0798e-06
2014 | 2013-09-24 | C | 6057.9383 | 4.1793 | 0.018781
2014 | 2013-09-25 | C | 37 | 0.020626 | 0.00011395
2014 | 2013-09-25 | C | 12 | 0.0073177 | 3.6958e-05
2014 | 2013-09-25 | C | 775 | 0.045351 | 0.0023869
2014 | 2013-09-25 | C | 73.85 | 0.0721 | 0.00023715
2014 | 2013-09-24 | C | 2166.3415 | 0.52709 | 0.0090825
2014 | 2013-09-25 | C | 19 | 0.006788 | 5.8517e-05
2014 | 2013-09-25 | C | 49 | 0.015695 | 0.00015091
2014 | 2013-09-24 | C | 25.6077 | 0.067511 | 0.0004589
2014 | 2013-09-25 | C | 301 | 0.033373 | 0.00092703
2014 | 2013-09-25 | C | 3 | 0.0060519 | 9.2395e-06
2014 | 2013-09-25 | B | 13 | 0.0096491 | 4.0038e-05
2014 | 2013-09-25 | C | 5 | 0.003588 | 1.5399e-05
2014 | 2013-09-25 | C | 16.5023 | 0.044573 | 0.00015399
2014 | 2013-09-24 | C | 1427 | 0.23293 | 0.0043949
2014 | 2013-09-21 | B | 6 | 0.0078721 | 1.8479e-05
2014 | 2013-09-25 | C | 241.4694 | 0.03421 | 0.00088699
2014 | 2013-09-24 | C | 345.1556 | 0.36568 | 0.001081
2014 | 2013-09-26 | C | 60 | 0.010163 | 0.00018479
2014 | 2013-09-26 | C | 17.9873 | 0.039 | 0.00055745
2014 | 2013-09-25 | C | 8 | 0.0024392 | 2.4639e-05
2014 | 2013-09-25 | C | 19 | 0.0071391 | 5.8517e-05
2014 | 2013-09-25 | C | 19 | 0.0020481 | 5.8517e-05
2014 | 2013-09-25 | C | 10 | 0.0037574 | 3.0798e-05
2014 | 2013-09-25 | C | 3 | 0.00043426 | 9.2395e-06
2014 | 2013-09-24 | C | 409.7046 | 0.40631 | 0.0021774
2014 | 2013-09-26 | C | 77 | 0.0092488 | 0.00023715
2014 | 2013-09-25 | C | 11 | 0.00023715 | 3.3878e-05
2014 | 2013-09-24 | C | 239 | 0.029443 | 0.00073608
2014 | 2013-09-24 | C | 926.2982 | 1.1012 | 0.0037266
2014 | 2013-09-24 | C | 26.1546 | 0.093521 | 0.0015461
2014 | 2013-09-25 | C | 8 | 0.0073177 | 2.4639e-05
2014 | 2013-09-24 | C | 328.5253 | 0.89646 | 0.001426
2014 | 2013-09-24 | C | 31 | 0.091083 | 9.5475e-05
2014 | 2013-09-24 | C | 513 | 0.01896 | 0.00158
2014 | 2013-09-24 | C | 1 | 0.0021405 | 3.0798e-06
2014 | 2013-09-24 | C | 243.3927 | 0.88154 | 0.0013274
2014 | 2013-09-26 | C | 1 | 0.00034802 | 3.0798e-06
2014 | 2013-09-25 | C | 58 | 0.0861 | 0.00017863
2014 | 2013-09-25 | C | 9 | 0.001081 | 2.7719e-05
2014 | 2013-09-26 | C | 11 | 0.0034895 | 3.3878e-05
2014 | 2013-09-25 | C | 59 | 0.0021805 | 0.00018171
2014 | 2013-09-26 | B | 19 | 0.016619 | 5.8517e-05
2014 | 2013-09-24 | C | 1 | 0.0095752 | 3.0798e-06
2014 | 2013-09-26 | B | 100 | 0.096091 | 0.00030798
2014 | 2013-09-26 | C | 19 | 0.0028088 | 5.8517e-05
2014 | 2013-09-26 | C | 238 | 0.010262 | 0.000733
2014 | 2013-09-26 | C | 5 | 0.00064677 | 1.5399e-05
2014 | 2013-09-26 | C | 69 | 0.034426 | 0.00021251
2014 | 2013-09-26 | C | 13 | 0.0026025 | 4.0038e-05
2014 | 2013-09-26 | C | 30 | 0.01081 | 9.2395e-05
2014 | 2013-09-24 | C | 5 | 0.037728 | 1.5399e-05
2014 | 2013-09-24 | C | 3.174 | 0.0248 | 4.9277e-05
2014 | 2013-09-24 | C | 17.2765 | 0.13648 | 6.7757e-05
2014 | 2013-09-24 | C | 8 | 0.064751 | 2.4639e-05
2014 | 2013-09-24 | C | 13 | 0.056774 | 4.0038e-05
2014 | 2013-09-26 | C | 690.6344 | 0.19143 | 0.0052727
2014 | 2013-09-24 | C | 139.5223 | 1.2599 | 0.0011272
2014 | 2013-09-24 | C | 42.5032 | 0.30448 | 0.0010625
2014 | 2013-09-24 | C | 202.2214 | 0.82522 | 0.002162
2014 | 2013-09-24 | C | 3 | 0.009489 | 9.2395e-06
2014 | 2013-09-27 | C | 5 | 0.0030336 | 1.5399e-05
2014 | 2013-09-24 | C | 65.0146 | 0.24689 | 0.0024639
2014 | 2013-09-27 | C | 15 | 0.015615 | 4.6198e-05
2014 | 2013-09-26 | B | 6 | 0.0076688 | 1.8479e-05
2014 | 2013-09-27 | C | 16 | 0.0024146 | 4.9277e-05
2014 | 2013-09-27 | C | 76 | 0.020364 | 0.00023407
2014 | 2013-09-27 | C | 33.3796 | 0.024879 | 0.00052049
2014 | 2013-09-28 | C | 175 | 0.032877 | 0.00053897
2014 | 2013-09-25 | C | 1 | 0.0090917 | 3.0798e-06
2014 | 2013-09-26 | C | 3 | 0.013102 | 9.2395e-06
2014 | 2013-09-28 | C | 327.0889 | 0.13297 | 0.0020389
2014 | 2013-09-28 | B | 116 | 0.028938 | 0.00035726
2014 | 2013-09-28 | C | 22 | 0.0010163 | 6.7757e-05
2014 | 2013-09-28 | C | 64.2056 | 0.035001 | 0.00043734
2014 | 2013-09-28 | C | 3 | 0.00068372 | 9.2395e-06
2014 | 2013-09-28 | C | 45.5429 | 0.019216 | 0.00044658
2014 | 2013-09-28 | C | 237 | 0.015328 | 0.00072992
2014 | 2013-09-28 | C | 514.2067 | 0.27873 | 0.0032338
2014 | 2013-09-28 | C | 238.067 | 0.12904 | 0.0025809
2014 | 2013-09-28 | C | 406 | 0.011254 | 0.0012504
2014 | 2013-09-28 | C | 31 | 0.013844 | 9.5475e-05
2014 | 2013-09-28 | C | 112 | 0.16868 | 0.00034494
2014 | 2013-09-28 | C | 522.5574 | 0.19152 | 0.0027226
2014 | 2013-09-28 | C | 30 | 0.018756 | 9.2395e-05
2014 | 2013-09-29 | C | 173.4286 | 0.076915 | 0.00072992
2014 | 2013-09-28 | C | 5 | 0.019957 | 1.5399e-05
2014 | 2013-09-28 | C | 5 | 0.00061597 | 1.5399e-05
2014 | 2013-09-29 | C | 1 | 0.00045274 | 3.0798e-06
2014 | 2013-09-29 | C | 144.68 | 0.087782 | 0.0007022
2014 | 2013-09-29 | C | 25 | 0.013012 | 7.6996e-05
2014 | 2013-09-30 | C | 217.0388 | 0.084224 | 0.00098863
2014 | 2013-09-29 | C | 208 | 0.067904 | 0.00064061
2014 | 2013-09-30 | C | 8 | 0.0033755 | 2.4639e-05
2014 | 2013-09-30 | C | 2 | 0.00042502 | 6.1597e-06
2014 | 2013-09-30 | C | 3 | 0.0026333 | 9.2395e-06
2014 | 2013-09-30 | C | 436.198 | 0.13166 | 0.0021436
2014 | 2013-09-30 | C | 3 | 0.0013674 | 9.2395e-06
2014 | 2013-09-30 | C | 1 | 0.00069912 | 3.0798e-06
2014 | 2013-09-30 | C | 562.8276 | 0.095338 | 0.0027595
2014 | 2013-09-30 | C | 360.5552 | 0.30871 | 0.0029659
2014 | 2013-09-30 | C | 1.9275 | 0.0060433 | 4.9277e-05
2014 | 2013-09-30 | C | 55 | 0.003896 | 0.00016939
2014 | 2013-09-30 | C | 1192.4098 | 0.213 | 0.0042964
2014 | 2013-10-01 | B | 66 | 0.028254 | 0.00020327
2014 | 2013-09-30 | C | 5 | 0.013351 | 1.5399e-05
2014 | 2013-10-01 | C | 1 | 0.00027719 | 3.0798e-06
2014 | 2013-10-01 | B | 3 | 0.002467 | 9.2395e-06
2014 | 2013-10-01 | B | 6 | 0.0048415 | 1.8479e-05
2014 | 2013-09-29 | C | 234.697 | 0.045538 | 0.001272
2014 | 2013-10-01 | C | 8 | 0.004435 | 2.4639e-05
2014 | 2013-10-01 | C | 55 | 0.021005 | 0.00016939
2014 | 2013-09-30 | C | 1 | 0.0014691 | 3.0798e-06
2014 | 2013-10-01 | B | 5 | 0.0054205 | 1.5399e-05
2014 | 2013-09-30 | C | 29 | 0.00089315 | 8.9315e-05
2014 | 2013-10-01 | C | 3 | 0.0032246 | 9.2395e-06
2014 | 2013-10-01 | B | 144 | 0.17784 | 0.0004435
2014 | 2013-10-01 | C | 447.5385 | 0.049621 | 0.0023592
2014 | 2013-10-02 | B | 10 | 0.00083156 | 3.0798e-05
2014 | 2013-09-30 | C | 2 | 0.00052973 | 6.1597e-06
2014 | 2013-10-02 | B | 43 | 0.040127 | 0.00013243
2014 | 2013-10-02 | C | 17 | 0.0039792 | 5.2357e-05
2014 | 2013-10-02 | B | 72 | 0.076947 | 0.00022175
2014 | 2013-10-02 | B | 857.6178 | 0.67618 | 0.0027103
2014 | 2013-10-02 | C | 449.0909 | 0.056708 | 0.0018972
2014 | 2013-10-02 | C | 268.6063 | 0.10258 | 0.0010287
2014 | 2013-10-02 | C | 35 | 0.0023715 | 0.00010779
2014 | 2013-10-03 | C | 68.3617 | 0.029055 | 0.00055129
2014 | 2013-10-03 | C | 3 | 0.00012011 | 9.2395e-06
2014 | 2013-10-03 | B | 7 | 0.0018756 | 2.1559e-05
2014 | 2013-10-03 | B | 5 | 0.00072376 | 1.5399e-05
2014 | 2013-10-03 | B | 5 | 0.00095475 | 1.5399e-05
2014 | 2013-10-03 | B | 2 | 0.00053589 | 6.1597e-06
2014 | 2013-10-03 | B | 5 | 0.00064677 | 1.5399e-05
2014 | 2013-10-03 | B | 3 | 0.0010348 | 9.2395e-06
2014 | 2013-10-03 | B | 2 | 0.00053589 | 6.1597e-06
2014 | 2013-10-03 | B | 22 | 0.01389 | 6.7757e-05
2014 | 2013-09-25 | C | 2 | 0.0014352 | 6.1597e-06
2014 | 2013-10-03 | C | 17 | 0.0022514 | 5.2357e-05
2014 | 2013-10-03 | B | 17 | 0.015288 | 5.2357e-05
2014 | 2013-10-03 | B | 72 | 0.037032 | 0.00022175
2014 | 2013-10-03 | B | 176 | 0.095943 | 0.00054205
2014 | 2013-10-03 | B | 4 | 0.0045705 | 1.2319e-05
2014 | 2013-10-03 | B | 5 | 0.0016785 | 1.5399e-05
2014 | 2013-10-03 | B | 5 | 0.00041578 | 1.5399e-05
2014 | 2013-10-03 | B | 8 | 0.00056669 | 2.4639e-05
2014 | 2013-10-04 | C | 5 | 7.6996e-05 | 1.5399e-05
2014 | 2013-10-04 | B | 68 | 0.032671 | 0.00020943
2014 | 2013-10-04 | B | 1 | 0.001081 | 3.0798e-06
2014 | 2013-10-04 | C | 65 | 0.0048046 | 0.00020019
2014 | 2013-10-04 | C | 154 | 0.0042687 | 0.0004743
2014 | 2013-09-30 | B | 2 | 0.0014845 | 6.1597e-06
2014 | 2013-10-04 | C | 598 | 0.14181 | 0.0018417
2014 | 2013-10-04 | B | 53 | 0.058274 | 0.00016323
2014 | 2013-10-04 | B | 190 | 0.014629 | 0.00058517
2014 | 2013-10-05 | B | 16 | 0.009412 | 4.9277e-05
2014 | 2013-10-05 | C | 2 | 0.0014414 | 6.1597e-06
2014 | 2013-10-06 | B | 2 | 0.0019526 | 6.1597e-06
2014 | 2013-10-06 | C | 2 | 0.0020019 | 6.1597e-06
2014 | 2013-10-06 | C | 160.0623 | 0.41804 | 0.0040069
2014 | 2013-10-07 | C | 150.3793 | 0.065767 | 0.00085312
2014 | 2013-10-07 | B | 4 | 0.0027349 | 1.2319e-05
2014 | 2013-10-07 | B | 10 | 0.0065601 | 3.0798e-05
2014 | 2013-10-07 | B | 27 | 0.02345 | 8.3156e-05
2014 | 2013-10-07 | C | 64 | 0.013995 | 0.00019711
2014 | 2013-10-07 | C | 552.7619 | 0.10215 | 0.0017524
2014 | 2013-10-07 | C | 10.1091 | 0.068963 | 0.00097323
2014 | 2013-10-07 | C | 77 | 0.029169 | 0.00023715
2014 | 2013-10-08 | B | 40 | 0.043487 | 0.00012319
2014 | 2013-10-08 | B | 28 | 0.028027 | 8.6236e-05
2014 | 2013-10-08 | B | 137 | 0.18017 | 0.00042194
2014 | 2013-10-08 | C | 6 | 0.00048046 | 1.8479e-05
2014 | 2013-10-08 | C | 33 | 0.0083341 | 0.00010163
2014 | 2013-10-08 | C | 137 | 0.016034 | 0.00042194
2014 | 2013-10-08 | C | 6 | 0.002199 | 1.8479e-05
2014 | 2013-10-08 | C | 237.1798 | 0.062821 | 0.0012781
2014 | 2013-10-08 | C | 26 | 0.003203 | 8.0076e-05
2014 | 2013-10-08 | B | 19 | 0.020656 | 5.8517e-05
2014 | 2013-10-09 | C | 172 | 0.0074163 | 0.00052973
2014 | 2013-10-09 | C | 62.5827 | 0.077483 | 0.0010163
2014 | 2013-10-09 | C | 8 | 0.0034987 | 2.4639e-05
2014 | 2013-10-09 | C | 6 | 0.0014598 | 1.8479e-05
2014 | 2013-10-09 | B | 31 | 0.034562 | 9.5475e-05
2014 | 2013-10-09 | B | 18 | 0.012917 | 5.5437e-05
2014 | 2013-10-09 | B | 1 | 0.00062829 | 3.0798e-06
2014 | 2013-10-09 | C | 4 | 0.00040654 | 1.2319e-05
2014 | 2013-10-09 | C | 92 | 0.020118 | 0.00028335
2014 | 2013-10-09 | C | 73 | 0.054184 | 0.00022483
2014 | 2013-10-09 | C | 131 | 0.030259 | 0.00040346
2014 | 2013-10-09 | C | 76.3448 | 0.02657 | 0.00096091
2014 | 2013-10-09 | C | 143.0336 | 0.064316 | 0.00088391
2014 | 2013-10-09 | C | 2 | 0.00084388 | 6.1597e-06
2014 | 2013-10-09 | C | 1 | 8.9315e-05 | 3.0798e-06
2014 | 2013-10-10 | C | 2160 | 0.1397 | 0.0066525
2014 | 2013-10-09 | C | 69.3175 | 0.044405 | 0.00082232
2014 | 2013-10-10 | C | 143 | 0.0074871 | 0.00044042
2014 | 2013-10-10 | C | 22 | 0.0096214 | 6.7757e-05
2014 | 2013-10-10 | B | 15 | 0.01118 | 4.6198e-05
2014 | 2013-10-10 | C | 5 | 3.0798e-05 | 1.5399e-05
2014 | 2013-10-10 | C | 6 | 0.00012935 | 1.8479e-05
2014 | 2013-10-10 | B | 8 | 0.0079583 | 2.4639e-05
2014 | 2013-10-10 | C | 2 | 0.00059749 | 6.1597e-06
2014 | 2013-10-10 | C | 2 | 0.00066525 | 6.1597e-06
2014 | 2013-10-11 | C | 95.5164 | 0.035007 | 0.0007792
2014 | 2013-10-11 | C | 31 | 0.0035326 | 9.5475e-05
2014 | 2013-10-11 | C | 29 | 0.0046444 | 8.9315e-05
2014 | 2013-10-11 | C | 124.4828 | 0.032205 | 0.00057901
2014 | 2013-10-11 | C | 57 | 0.0042132 | 0.00017555
2014 | 2013-10-11 | C | 9 | 0.004435 | 2.7719e-05
2014 | 2013-10-11 | C | 4 | 0.00022175 | 1.2319e-05
2014 | 2013-10-11 | C | 265.033 | 0.14611 | 0.00083464
2014 | 2013-10-11 | C | 82.1043 | 0.040459 | 0.00043426
2014 | 2013-10-12 | C | 156.5661 | 0.27196 | 0.0024054
2014 | 2013-10-12 | C | 59.6805 | 0.10587 | 0.00095783
2014 | 2013-10-12 | C | 423.7643 | 0.20099 | 0.0014229
2014 | 2013-10-12 | C | 128.3524 | 0.24114 | 0.0020912
2014 | 2013-10-12 | C | 26 | 0.0048846 | 8.0076e-05
2014 | 2013-10-12 | C | 108 | 0.038584 | 0.00033262
2014 | 2013-10-12 | C | 3 | 0.0015892 | 9.2395e-06
2014 | 2013-10-13 | C | 18 | 0.0027164 | 5.5437e-05
2014 | 2013-10-13 | C | 14 | 0.0025008 | 4.3118e-05
2014 | 2013-10-13 | C | 1 | 0.00097939 | 3.0798e-06
2014 | 2013-10-14 | C | 17 | 0.0050263 | 5.2357e-05
2014 | 2013-10-14 | C | 4 | 0.00064061 | 1.2319e-05
2014 | 2013-09-27 | B | 2 | 0.00073916 | 6.1597e-06
2014 | 2013-10-14 | C | 2 | 0.00032646 | 6.1597e-06
2014 | 2013-10-14 | B | 4 | 0.0021066 | 1.2319e-05
2014 | 2013-10-14 | B | 5 | 0.0017863 | 1.5399e-05
2014 | 2013-10-14 | B | 6 | 0.00081308 | 1.8479e-05
2014 | 2013-10-14 | B | 4 | 0.00064061 | 1.2319e-05
2014 | 2013-10-14 | B | 5 | 0.00087775 | 1.5399e-05
2014 | 2013-10-14 | B | 4 | 0.00088699 | 1.2319e-05
2014 | 2013-10-14 | B | 7 | 0.0012289 | 2.1559e-05
2014 | 2013-10-14 | B | 15 | 0.0030952 | 4.6198e-05
2014 | 2013-10-14 | B | 8 | 0.0015276 | 2.4639e-05
2014 | 2013-10-14 | B | 6 | 0.00073916 | 1.8479e-05
2014 | 2013-10-14 | B | 2 | 0.00068988 | 6.1597e-06
2014 | 2013-10-14 | B | 3 | 0.0027441 | 9.2395e-06
2014 | 2013-10-14 | B | 12 | 0.0031045 | 3.6958e-05
2014 | 2013-10-14 | C | 11 | 0.0024054 | 3.3878e-05
2014 | 2013-10-14 | C | 144 | 0.007096 | 0.0004435
2014 | 2013-10-14 | C | 54.3616 | 0.058766 | 0.00022175
2014 | 2013-10-14 | C | 184 | 0.020968 | 0.00056669
2014 | 2013-10-14 | C | 132 | 0.0056915 | 0.00040654
2014 | 2013-10-15 | C | 465.9612 | 0.14351 | 0.001657
2014 | 2013-10-14 | C | 16 | 0.0029074 | 4.9277e-05
2014 | 2013-10-15 | C | 157.0923 | 0.029997 | 0.00056977
2014 | 2013-10-14 | C | 115.0413 | 1.2171 | 0.00078844
2014 | 2013-10-15 | C | 10 | 0.00070836 | 3.0798e-05
2014 | 2013-10-14 | C | 4304 | 0.46395 | 0.013256
2014 | 2013-10-14 | C | 634 | 0.046863 | 0.0019526
2014 | 2013-10-14 | C | 594 | 0.043906 | 0.0018294
2014 | 2013-10-14 | C | 3180 | 0.41134 | 0.0097939
2014 | 2013-10-14 | C | 97 | 0.028978 | 0.00029874
2014 | 2013-10-15 | C | 18 | 0.0021066 | 5.5437e-05
2014 | 2013-10-15 | C | 127.7167 | 0.046022 | 0.00095783
2014 | 2013-10-15 | C | 44 | 0.0060981 | 0.00013551
2014 | 2013-10-15 | C | 58 | 0.0066093 | 0.00017863
2014 | 2013-10-15 | B | 12 | 0.009683 | 3.6958e-05
2014 | 2013-10-15 | C | 247 | 0.20844 | 0.00076072
2014 | 2013-09-26 | B | 12 | 0.0098678 | 3.6958e-05
2014 | 2013-10-15 | B | 1 | 0.00079768 | 3.0798e-06
2014 | 2013-10-15 | B | 13 | 0.015254 | 4.0038e-05
2014 | 2013-10-15 | C | 14 | 0.012806 | 4.3118e-05
2014 | 2013-10-14 | C | 1107.3867 | 0.24556 | 0.0043919
2014 | 2013-10-14 | C | 323.3691 | 0.14541 | 0.0020912
2014 | 2013-10-15 | C | 112 | 0.0089685 | 0.00034494
2014 | 2013-10-14 | C | 45.0303 | 0.017891 | 0.00016015
2014 | 2013-10-14 | C | 257 | 0.076777 | 0.00079152
2014 | 2013-10-15 | C | 127.6025 | 0.25191 | 0.00050201
2014 | 2013-10-15 | C | 1082.9192 | 0.32018 | 0.0090794
2014 | 2013-10-14 | C | 22.8493 | 0.087121 | 0.00012935
2014 | 2013-10-15 | C | 103.2219 | 0.25115 | 0.0010502
2014 | 2013-10-14 | C | 85.9872 | 0.28999 | 0.0003357
2014 | 2013-10-15 | C | 6115 | 0.24483 | 0.018833
2014 | 2013-10-15 | C | 307.4 | 0.1155 | 0.011799
2014 | 2013-10-16 | C | 25 | 0.0026949 | 7.6996e-05
2014 | 2013-10-14 | C | 48.69 | 0.044537 | 0.00016323
2014 | 2013-10-15 | C | 5 | 0.0039884 | 1.5399e-05
2014 | 2013-10-15 | C | 5 | 0.003203 | 1.5399e-05
2014 | 2013-10-16 | C | 6 | 0.0010533 | 1.8479e-05
2014 | 2013-10-14 | C | 492.5491 | 0.41262 | 0.001891
2014 | 2013-10-15 | C | 366.9615 | 0.23169 | 0.0022976
2014 | 2013-10-14 | C | 26 | 0.10842 | 8.0076e-05
2014 | 2013-10-15 | C | 10783 | 1.0295 | 0.034661
2014 | 2013-10-15 | C | 142.6268 | 0.090489 | 0.00074532
2014 | 2013-10-14 | C | 56.8974 | 0.21133 | 0.0011149
2014 | 2013-10-14 | C | 137.617 | 0.05849 | 0.00053589
2014 | 2013-10-14 | C | 5 | 0.020589 | 1.5399e-05
2014 | 2013-10-14 | C | 256.8436 | 0.8828 | 0.0044103
2014 | 2013-10-14 | C | 63.3322 | 0.79679 | 0.0011395
2014 | 2013-10-14 | C | 74.7926 | 0.061503 | 0.0023622
2014 | 2013-10-15 | C | 24 | 0.0062829 | 7.3916e-05
2014 | 2013-10-15 | C | 3 | 0.0012751 | 9.2395e-06
2014 | 2013-10-15 | B | 125 | 0.11819 | 0.00038498
2014 | 2013-10-16 | C | 97.9252 | 0.04343 | 0.00085312
2014 | 2013-10-14 | C | 28.08 | 0.0083887 | 0.00036034
2014 | 2013-10-14 | C | 182.4402 | 0.82541 | 0.00087775
2014 | 2013-10-14 | C | 40.5148 | 0.13052 | 0.0013428
2014 | 2013-10-14 | C | 563.1036 | 0.32951 | 0.0034402
2014 | 2013-10-15 | C | 216.0699 | 0.30278 | 0.0012874
2014 | 2013-10-14 | C | 13.6125 | 0.17516 | 0.00088699
2014 | 2013-10-16 | C | 121 | 0.034657 | 0.00037266
2014 | 2013-10-16 | C | 32 | 0.0067017 | 9.8555e-05
2014 | 2013-10-16 | B | 8 | 0.0073177 | 2.4639e-05
2014 | 2013-10-16 | C | 24 | 0.0033262 | 7.3916e-05
2014 | 2013-10-16 | C | 275.6025 | 1.2851 | 0.00096399
2014 | 2013-10-14 | C | 104 | 0.016335 | 0.0003203
2014 | 2013-10-14 | C | 288 | 0.073621 | 0.00088699
2014 | 2013-10-14 | C | 82.7229 | 0.21987 | 0.00069912
2014 | 2013-10-14 | C | 108 | 0.074508 | 0.00033262
2014 | 2013-10-14 | C | 30.4323 | 0.046114 | 0.00016939
2014 | 2013-10-14 | C | 67.2596 | 0.091146 | 0.00052973
2014 | 2013-10-16 | C | 5 | 0.0032338 | 1.5399e-05
2014 | 2013-10-15 | C | 55.6778 | 0.076651 | 0.0004435
2014 | 2013-10-15 | C | 296.5385 | 0.068497 | 0.0010502
2014 | 2013-10-16 | C | 28 | 0.0031045 | 8.6236e-05
2014 | 2013-10-14 | C | 221 | 0.05241 | 0.00068065
2014 | 2013-10-14 | C | 390.5651 | 1.3905 | 0.0020666
2014 | 2013-10-17 | C | 25 | 0.0011549 | 7.6996e-05
2014 | 2013-10-17 | B | 6 | 0.0020697 | 1.8479e-05
2014 | 2013-10-14 | C | 207.228 | 0.19402 | 0.0011488
2014 | 2013-10-14 | C | 7.0213 | 0.060916 | 0.00012935
2014 | 2013-10-14 | C | 43.2662 | 0.16777 | 0.0007176
2014 | 2013-10-17 | B | 3 | 0.0029751 | 9.2395e-06
2014 | 2013-10-17 | B | 6 | 0.0027903 | 1.8479e-05
2014 | 2013-10-17 | C | 288 | 0.043463 | 0.00088699
2014 | 2013-10-17 | C | 55 | 0.0074532 | 0.00016939
2014 | 2013-10-17 | C | 540.2778 | 0.20467 | 0.0041147
2014 | 2013-10-14 | C | 25.8045 | 0.08758 | 0.0003511
2014 | 2013-10-17 | C | 7 | 0.0050879 | 2.1559e-05
2014 | 2013-10-14 | C | 77 | 0.10269 | 0.00023715
2014 | 2013-10-14 | C | 69.9676 | 0.7443 | 0.0008562
2014 | 2013-10-18 | C | 10 | 0.0011395 | 3.0798e-05
2014 | 2013-10-16 | C | 10 | 0.0054205 | 3.0798e-05
2014 | 2013-10-14 | C | 454.6452 | 0.16943 | 0.0032862
2014 | 2013-10-14 | C | 184 | 0.08897 | 0.00056669
2014 | 2013-10-14 | C | 5.4464 | 0.014493 | 7.0836e-05
2014 | 2013-10-14 | C | 69.2524 | 0.04415 | 0.00067757
2014 | 2013-10-15 | C | 111.4098 | 0.12455 | 0.00037574
2014 | 2013-10-18 | C | 66.0469 | 0.051464 | 0.00029566
2014 | 2013-10-16 | C | 6 | 0.0026055 | 1.8479e-05
2014 | 2013-10-18 | C | 27 | 0.0032431 | 8.3156e-05
2014 | 2013-10-16 | C | 24.2322 | 0.063735 | 0.00068065
2014 | 2013-10-15 | B | 3 | 0.0032523 | 9.2395e-06
2014 | 2013-10-14 | C | 301 | 0.039862 | 0.00092703
2014 | 2013-10-14 | C | 4.9092 | 0.047415 | 0.0010595
2014 | 2013-10-19 | C | 123 | 0.074249 | 0.00037882
2014 | 2013-10-18 | C | 302 | 0.013952 | 0.0012997
2014 | 2013-10-18 | C | 111 | 0.078286 | 0.00034186
2014 | 2013-10-17 | B | 3 | 0.00057285 | 9.2395e-06
2014 | 2013-10-19 | B | 3 | 0.00047122 | 9.2395e-06
2014 | 2013-10-19 | B | 8 | 0.010127 | 2.4639e-05
2014 | 2013-10-19 | C | 14 | 0.0085804 | 4.3118e-05
2014 | 2013-10-19 | C | 13.8182 | 0.0036174 | 4.6198e-05
2014 | 2013-10-16 | B | 3 | 0.0033724 | 9.2395e-06
2014 | 2013-10-20 | C | 45 | 0.0092857 | 0.00013859
2014 | 2013-10-20 | C | 93.4643 | 0.12004 | 0.00044042
2014 | 2013-10-17 | C | 42.3611 | 0.2424 | 0.0021282
2014 | 2013-10-18 | C | 26.6087 | 0.0072936 | 0.00012935
2014 | 2013-10-15 | C | 117 | 0.015495 | 0.00036034
2014 | 2013-10-15 | C | 12 | 0.0051372 | 3.6958e-05
2014 | 2013-10-14 | C | 29.5578 | 0.17697 | 0.00040654
2014 | 2013-10-15 | C | 44.8223 | 0.026781 | 0.00020635
2014 | 2013-10-15 | C | 7959.2667 | 0.29416 | 0.035218
2014 | 2013-10-15 | C | 5.9255 | 0.02982 | 3.0798e-05
2014 | 2013-10-21 | C | 20 | 0.0032646 | 6.1597e-05
2014 | 2013-10-14 | C | 66 | 0.071957 | 0.00020327
2014 | 2013-10-14 | C | 14 | 0.00025871 | 4.3118e-05
2014 | 2013-10-16 | C | 13 | 0.007407 | 4.0038e-05
2014 | 2013-10-16 | C | 1 | 0.00019095 | 3.0798e-06
2014 | 2013-10-14 | C | 118 | 0.13156 | 0.00036342
2014 | 2013-10-21 | B | 5 | 0.00064677 | 1.5399e-05
2014 | 2013-10-21 | B | 5 | 0.00056977 | 1.5399e-05
2014 | 2013-10-14 | C | 69.2023 | 0.12681 | 0.00057593
2014 | 2013-10-14 | C | 93.3436 | 0.42663 | 0.00071452
2014 | 2013-10-14 | C | 31.8653 | 0.14103 | 0.00010163
2014 | 2013-10-15 | C | 8 | 0.0012812 | 2.4639e-05
2014 | 2013-10-14 | C | 198.6282 | 0.093597 | 0.0013459
2014 | 2013-10-14 | C | 131.6552 | 0.45859 | 0.000733
2014 | 2013-10-21 | B | 6 | 0.00086852 | 1.8479e-05
2014 | 2013-10-21 | B | 1 | 0.00020635 | 3.0798e-06
2014 | 2013-10-21 | B | 6 | 0.00077612 | 1.8479e-05
2014 | 2013-10-21 | B | 107 | 0.089636 | 0.00032954
2014 | 2013-10-21 | B | 3 | 0.00071144 | 9.2395e-06
2014 | 2013-10-21 | B | 4 | 0.00045582 | 1.2319e-05
2014 | 2013-10-21 | B | 6 | 0.00086852 | 1.8479e-05
2014 | 2013-10-21 | B | 4 | 0.0012566 | 1.2319e-05
2014 | 2013-10-21 | C | 249 | 0.37347 | 0.00076688
2014 | 2013-10-15 | C | 83.1717 | 0.61836 | 0.0026764
2014 | 2013-10-14 | C | 5.6664 | 0.18029 | 0.00062521
2014 | 2013-10-15 | C | 6 | 0.0017925 | 1.8479e-05
2014 | 2013-10-14 | C | 65.7075 | 0.89326 | 0.00052049
2014 | 2013-10-22 | C | 6 | 0.00042502 | 1.8479e-05
2014 | 2013-10-16 | C | 2165.3571 | 0.35345 | 0.0069481
2014 | 2013-10-22 | B | 106 | 0.051581 | 0.00032646
2014 | 2013-10-22 | B | 8 | 0.0066525 | 2.4639e-05
2014 | 2013-10-22 | C | 298 | 0.059657 | 0.00091779
2014 | 2013-10-22 | C | 238.869 | 0.05959 | 0.0010656
2014 | 2013-10-22 | C | 66 | 0.4972 | 0.00020327
2014 | 2013-10-22 | C | 221.6471 | 0.055976 | 0.0012135
2014 | 2013-10-22 | C | 22 | 0.08063 | 6.7757e-05
2014 | 2013-10-22 | B | 4 | 0.00051741 | 1.2319e-05
2014 | 2013-10-22 | B | 2 | 0.0003511 | 6.1597e-06
2014 | 2013-10-22 | B | 10 | 0.0012319 | 3.0798e-05
2014 | 2013-10-22 | B | 2 | 0.00016631 | 6.1597e-06
2014 | 2013-10-22 | B | 3 | 0.00057285 | 9.2395e-06
2014 | 2013-10-22 | B | 5 | 0.00087775 | 1.5399e-05
2014 | 2013-10-22 | B | 8 | 0.0014044 | 2.4639e-05
2014 | 2013-10-22 | B | 2 | 0.0003511 | 6.1597e-06
2014 | 2013-10-23 | B | 3 | 0.00076688 | 9.2395e-06
2014 | 2013-10-23 | B | 2 | 0.0007946 | 6.1597e-06
2014 | 2013-10-23 | B | 2 | 0.00028951 | 6.1597e-06
2014 | 2013-10-23 | B | 2 | 0.00024023 | 6.1597e-06
2014 | 2013-10-23 | B | 161 | 0.14082 | 0.00049585
2014 | 2013-10-23 | B | 17 | 0.018273 | 5.2357e-05
2014 | 2013-10-23 | B | 1 | 0.00087775 | 3.0798e-06
2014 | 2013-10-23 | C | 3 | 0.001543 | 9.2395e-06
2014 | 2013-10-23 | B | 3 | 0.00066525 | 9.2395e-06
2014 | 2013-10-23 | B | 5 | 0.0018017 | 1.5399e-05
2014 | 2013-10-23 | C | 13 | 0.0008408 | 4.0038e-05
2014 | 2013-10-22 | C | 16 | 0.0017247 | 4.9277e-05
2014 | 2013-10-14 | C | 31.7444 | 0.073912 | 0.0003819
2014 | 2013-10-23 | C | 10 | 0.0048662 | 3.0798e-05
2014 | 2013-10-23 | C | 33.5505 | 0.092791 | 0.00045274
2014 | 2013-10-23 | C | 5 | 0.00095475 | 1.5399e-05
2014 | 2013-10-23 | C | 3 | 0.0077335 | 9.2395e-06
2014 | 2013-10-24 | B | 17 | 0.013875 | 5.2357e-05
2014 | 2013-10-24 | C | 28.7879 | 0.017289 | 8.9315e-05
2014 | 2013-10-23 | B | 8 | 0.0017001 | 2.4639e-05
2014 | 2013-10-23 | B | 4 | 0.00094859 | 1.2319e-05
2014 | 2013-10-23 | B | 4 | 0.0011334 | 1.2319e-05
2014 | 2013-10-24 | C | 298 | 0.28268 | 0.00091779
2014 | 2013-10-24 | C | 66 | 0.020937 | 0.00020327
2014 | 2013-10-24 | C | 14 | 0.0023284 | 4.3118e-05
2014 | 2013-10-24 | C | 75 | 0.0055437 | 0.00023099
2014 | 2013-10-24 | C | 298 | 0.059657 | 0.00091779
2014 | 2013-10-24 | C | 314.6111 | 0.34592 | 0.0010779
2014 | 2013-10-24 | B | 1 | 0.00086852 | 3.0798e-06
2014 | 2013-10-25 | C | 85.7278 | 0.094258 | 0.0010379
2014 | 2013-10-14 | C | 72.1153 | 0.33649 | 0.0018879
2014 | 2013-10-25 | C | 91.1913 | 0.076954 | 0.00085004
2014 | 2013-10-25 | C | 6059.7387 | 5.3003 | 0.018876
2014 | 2013-10-25 | C | 617.2429 | 0.12737 | 0.0021466
2014 | 2013-10-25 | C | 23 | 0.023163 | 7.0836e-05
2014 | 2013-10-25 | C | 35 | 0.020265 | 0.00010779
2014 | 2013-10-25 | C | 210.6825 | 0.5457 | 0.00091779
2014 | 2013-10-25 | C | 298 | 0.40199 | 0.00091779
2014 | 2013-10-25 | C | 53 | 0.029871 | 0.00016323
2014 | 2013-10-25 | C | 5 | 0.00018479 | 1.5399e-05
2014 | 2013-10-25 | C | 354 | 0.016354 | 0.0010903
2014 | 2013-10-25 | C | 28 | 0.011469 | 8.6236e-05
2014 | 2013-10-25 | C | 3 | 0.00013859 | 9.2395e-06
2014 | 2013-10-25 | C | 52.3536 | 0.028701 | 0.00022175
2014 | 2013-10-25 | C | 20 | 0.0010471 | 6.1597e-05
2014 | 2013-10-25 | C | 98.8193 | 0.07487 | 0.00036342
2014 | 2013-10-26 | C | 201.3377 | 0.13952 | 0.0013428
2014 | 2013-10-25 | C | 249 | 0.074387 | 0.00076688
2014 | 2013-10-26 | C | 44 | 0.0145 | 0.00013551
2014 | 2013-10-26 | C | 54 | 0.018128 | 0.00016631
2014 | 2013-10-26 | C | 232 | 0.03001 | 0.00071452
2014 | 2013-10-26 | C | 22 | 0.0017617 | 6.7757e-05
2014 | 2013-10-26 | C | 49.1846 | 0.019238 | 0.00019095
2014 | 2013-10-27 | C | 27.2121 | 0.019108 | 9.2395e-05
2014 | 2013-10-27 | C | 30 | 0.014229 | 9.2395e-05
2014 | 2013-10-28 | C | 54 | 0.0039915 | 0.00016631
2014 | 2013-10-27 | C | 23.2458 | 0.063861 | 9.2395e-05
2014 | 2013-10-28 | C | 159.5164 | 0.13363 | 0.001583
2014 | 2013-10-28 | C | 18 | 0.003548 | 5.5437e-05
2014 | 2013-10-29 | C | 270.5164 | 0.099145 | 0.0014198
2014 | 2013-10-25 | C | 126.0547 | 0.076869 | 0.00083464
2014 | 2013-10-29 | C | 28.5356 | 0.033045 | 8.9315e-05
2014 | 2013-10-29 | C | 1 | 0.00028335 | 3.0798e-06
2014 | 2013-10-29 | B | 17 | 0.014869 | 5.2357e-05
2014 | 2013-10-29 | C | 573 | 0.10059 | 0.0017647
2014 | 2013-10-29 | C | 341.6648 | 0.18204 | 0.0027195
2014 | 2013-10-29 | C | 330.5091 | 0.052932 | 0.0010995
2014 | 2013-10-29 | B | 7 | 0.0011211 | 2.1559e-05
2014 | 2013-10-29 | C | 14 | 0.0023715 | 4.3118e-05
2014 | 2013-10-29 | B | 3 | 0.00036034 | 9.2395e-06
2014 | 2013-10-29 | B | 5 | 0.00095475 | 1.5399e-05
2014 | 2013-10-29 | B | 35 | 0.0088391 | 0.00010779
2014 | 2013-10-30 | C | 3 | 0.00017555 | 9.2395e-06
2014 | 2013-10-30 | C | 3 | 0.0016354 | 9.2395e-06
2014 | 2013-10-30 | B | 17 | 0.014136 | 5.2357e-05
2014 | 2013-10-31 | B | 7 | 0.0010348 | 2.1559e-05
2014 | 2013-10-31 | C | 296.819 | 0.093244 | 0.0015184
2014 | 2013-10-31 | C | 1 | 0.0014598 | 3.0798e-06
2014 | 2013-10-31 | B | 6 | 0.0018849 | 1.8479e-05
2014 | 2013-10-31 | B | 4 | 0.0011334 | 1.2319e-05
2014 | 2013-10-31 | B | 7 | 0.00166 | 2.1559e-05
2014 | 2013-10-31 | B | 5 | 0.0015707 | 1.5399e-05
2014 | 2013-10-31 | B | 5 | 0.0011087 | 1.5399e-05
2014 | 2013-10-31 | B | 7 | 0.0034925 | 2.1559e-05
2014 | 2013-10-31 | B | 4 | 0.00051741 | 1.2319e-05
2014 | 2013-10-31 | B | 3 | 0.00066525 | 9.2395e-06
2014 | 2013-10-31 | B | 3 | 0.00080384 | 9.2395e-06
2014 | 2013-10-31 | B | 103 | 0.091995 | 0.00031722
2014 | 2013-10-31 | B | 2 | 0.0012874 | 6.1597e-06
2014 | 2013-10-31 | C | 29.6787 | 0.047805 | 0.0012443
2014 | 2013-10-31 | C | 11 | 0.012772 | 3.3878e-05
2014 | 2013-10-31 | C | 21 | 0.0032985 | 6.4677e-05
2014 | 2013-10-31 | B | 152 | 0.030429 | 0.00046814
2014 | 2013-10-31 | C | 1.0946 | 0.0176 | 6.1597e-05
2014 | 2013-11-01 | C | 941.7313 | 0.18562 | 0.0035572
2014 | 2013-11-01 | C | 30.5583 | 0.015058 | 0.00011395
2014 | 2013-11-01 | C | 181 | 0.027873 | 0.00055745
2014 | 2013-11-01 | B | 26 | 0.018978 | 8.0076e-05
2014 | 2013-11-01 | B | 4 | 0.0029813 | 1.2319e-05
2014 | 2013-11-01 | C | 28 | 0.0018972 | 8.6236e-05
2014 | 2013-11-02 | C | 8 | 0.00061597 | 2.4639e-05
2014 | 2013-11-02 | B | 40 | 0.024885 | 0.00012319
2014 | 2013-11-02 | C | 19 | 0.0030429 | 5.8517e-05
2014 | 2013-11-02 | C | 18 | 0.004823 | 5.5437e-05
2014 | 2013-11-02 | C | 8 | 0.0033262 | 2.4639e-05
2014 | 2013-11-02 | C | 132.8783 | 0.045835 | 0.00056669
2014 | 2013-11-03 | C | 21 | 0.002199 | 6.4677e-05
2014 | 2013-11-04 | C | 14 | 0.0012935 | 4.3118e-05
2014 | 2013-11-04 | B | 173 | 0.11882 | 0.00053281
2014 | 2013-11-04 | B | 3 | 0.002199 | 9.2395e-06
2014 | 2013-11-04 | B | 5 | 0.0053281 | 1.5399e-05
2014 | 2013-11-04 | B | 8 | 0.0063814 | 2.4639e-05
2014 | 2013-11-04 | B | 1 | 0.00069912 | 3.0798e-06
2014 | 2013-11-04 | C | 743 | 0.050343 | 0.0022883
2014 | 2013-11-05 | B | 8 | 0.0047306 | 2.4639e-05
2014 | 2013-11-05 | B | 16 | 0.011383 | 4.9277e-05
2014 | 2013-11-05 | C | 8 | 0.0024146 | 2.4639e-05
2014 | 2013-11-05 | B | 31 | 0.031793 | 9.5475e-05
2014 | 2013-11-05 | B | 14 | 0.014056 | 4.3118e-05
2014 | 2013-11-05 | C | 2 | 0.0003819 | 6.1597e-06
2014 | 2013-11-05 | B | 9 | 0.012945 | 2.7719e-05
2014 | 2013-11-05 | B | 4 | 0.0014414 | 1.2319e-05
2014 | 2013-11-05 | B | 33 | 0.011891 | 0.00010163
2014 | 2013-11-05 | C | 23 | 0.0029043 | 7.0836e-05
2014 | 2013-11-05 | C | 91.1194 | 0.074368 | 0.00090547
2014 | 2013-10-21 | B | 152 | 0.03511 | 0.00046814
2014 | 2013-11-05 | C | 191.9811 | 0.060901 | 0.00098555
2014 | 2013-11-05 | C | 50 | 0.0056977 | 0.00015399
2014 | 2013-11-06 | C | 66.2444 | 0.036112 | 0.00056361
2014 | 2013-11-06 | C | 91.0938 | 0.097913 | 0.00047738
2014 | 2013-11-06 | C | 3 | 0.0003511 | 9.2395e-06
2014 | 2013-11-06 | B | 9 | 0.0089808 | 2.7719e-05
2014 | 2013-11-06 | B | 39 | 0.015254 | 0.00012011
2014 | 2013-11-06 | B | 113 | 0.11206 | 0.00034802
2014 | 2013-11-06 | B | 4 | 0.0039422 | 1.2319e-05
2014 | 2013-11-06 | B | 26 | 0.024263 | 8.0076e-05
2014 | 2013-11-06 | B | 44 | 0.039299 | 0.00013551
2014 | 2013-11-06 | C | 3 | 0.0013674 | 9.2395e-06
2014 | 2013-11-06 | B | 8 | 0.0091163 | 2.4639e-05
2014 | 2013-11-06 | B | 7 | 0.0014444 | 2.1559e-05
2014 | 2013-11-06 | B | 6 | 0.0012381 | 1.8479e-05
2014 | 2013-11-06 | B | 7 | 0.0019834 | 2.1559e-05
2014 | 2013-11-06 | B | 1 | 0.00027719 | 3.0798e-06
2014 | 2013-11-06 | C | 28 | 0.0052604 | 8.6236e-05
2014 | 2013-11-06 | B | 1 | 0.00012935 | 3.0798e-06
2014 | 2013-11-06 | B | 3 | 0.0010071 | 9.2395e-06
2014 | 2013-11-06 | C | 75.8444 | 0.051857 | 0.00034186
2014 | 2013-11-06 | C | 38 | 0.0030429 | 0.00011703
2014 | 2013-11-06 | C | 72 | 0.011974 | 0.00022175
2014 | 2013-11-06 | C | 281 | 0.044137 | 0.002778
2014 | 2013-11-06 | C | 108.2745 | 0.033013 | 0.0010564
2014 | 2013-11-06 | C | 38 | 0.0030429 | 0.00011703
2014 | 2013-11-07 | C | 53.4945 | 0.074799 | 0.00064369
2014 | 2013-11-07 | C | 17.2308 | 0.0081194 | 0.0004127
2014 | 2013-11-06 | C | 13.0987 | 0.033807 | 0.00013859
2014 | 2013-11-07 | C | 14 | 0.0093997 | 4.3118e-05
2014 | 2013-11-07 | B | 42 | 0.053035 | 0.00012935
2014 | 2013-11-07 | B | 4 | 0.0013182 | 1.2319e-05
2014 | 2013-11-07 | B | 2 | 0.00059749 | 6.1597e-06
2014 | 2013-11-07 | B | 3 | 0.00034186 | 9.2395e-06
2014 | 2013-11-07 | C | 55 | 0.0044042 | 0.00016939
2014 | 2013-11-07 | C | 1 | 0.00063445 | 3.0798e-06
2014 | 2013-11-07 | C | 4306 | 0.026524 | 0.013262
2014 | 2013-11-07 | C | 1 | 0.00043426 | 3.0798e-06
2014 | 2013-11-08 | C | 272 | 0.021781 | 0.00083772
2014 | 2013-11-07 | B | 9 | 0.0014414 | 2.7719e-05
2014 | 2013-11-07 | B | 3 | 0.00052665 | 9.2395e-06
2014 | 2013-11-07 | B | 3 | 0.00024947 | 9.2395e-06
2014 | 2013-11-08 | C | 13 | 0.00076072 | 4.0038e-05
2014 | 2013-11-08 | C | 301 | 0.029665 | 0.00092703
2014 | 2013-11-06 | C | 7 | 0.0012289 | 2.1559e-05
2014 | 2013-11-06 | C | 4 | 0.0012566 | 1.2319e-05
2014 | 2013-11-07 | B | 4 | 0.002353 | 1.2319e-05
2014 | 2013-11-08 | B | 7 | 0.002199 | 2.1559e-05
2014 | 2013-11-08 | B | 7 | 0.0052388 | 2.1559e-05
2014 | 2013-11-08 | B | 10 | 0.0022175 | 3.0798e-05
2014 | 2013-11-08 | B | 4 | 0.0010718 | 1.2319e-05
2014 | 2013-11-08 | B | 3 | 0.00071144 | 9.2395e-06
2014 | 2013-11-08 | B | 3 | 0.00062829 | 9.2395e-06
2014 | 2013-11-08 | B | 6 | 0.00083156 | 1.8479e-05
2014 | 2013-11-08 | C | 259 | 0.017549 | 0.00079768
2014 | 2013-11-08 | C | 1 | 0.00048662 | 3.0798e-06
2014 | 2013-11-07 | C | 41.5195 | 0.19603 | 0.00085312
2014 | 2013-11-09 | C | 20 | 0.0030182 | 6.1597e-05
2014 | 2013-11-08 | B | 17 | 0.01555 | 5.2357e-05
2014 | 2013-11-08 | B | 94 | 0.077587 | 0.00028951
2014 | 2013-11-08 | B | 9 | 0.0094798 | 2.7719e-05
2014 | 2013-11-08 | C | 9 | 0.0007484 | 2.7719e-05
2014 | 2013-11-08 | C | 2 | 0.00028951 | 6.1597e-06
2014 | 2013-11-09 | B | 55 | 0.054036 | 0.00016939
2014 | 2013-11-09 | C | 181 | 0.015051 | 0.00055745
2014 | 2013-11-10 | C | 72.3333 | 0.039431 | 0.00077612
2014 | 2013-11-11 | C | 2790.0339 | 0.4812 | 0.0090424
2014 | 2013-11-08 | C | 8 | 0.0010348 | 2.4639e-05
2014 | 2013-11-10 | C | 2 | 0.00078228 | 6.1597e-06
2014 | 2013-11-07 | C | 7 | 0.027552 | 2.1559e-05
2014 | 2013-10-19 | B | 40 | 0.024885 | 0.00012319
2014 | 2013-11-10 | B | 81 | 0.06561 | 0.00024947
2014 | 2013-11-07 | C | 32.6121 | 0.13278 | 0.0008408
2014 | 2013-10-19 | B | 10 | 0.0054513 | 3.0798e-05
2014 | 2013-10-02 | B | 13 | 0.01009 | 4.0038e-05
2014 | 2013-10-05 | B | 1 | 0.00053589 | 3.0798e-06
2014 | 2013-10-08 | B | 20 | 0.02199 | 6.1597e-05
2014 | 2013-10-01 | B | 3 | 0.0015153 | 9.2395e-06
2014 | 2013-10-10 | B | 3 | 0.003779 | 9.2395e-06
2014 | 2013-10-17 | B | 2 | 0.0018048 | 6.1597e-06
2014 | 2013-10-22 | B | 6 | 0.0063014 | 1.8479e-05
2014 | 2013-10-23 | B | 1 | 0.00090855 | 3.0798e-06
2014 | 2013-10-25 | B | 9 | 0.0038529 | 2.7719e-05
2014 | 2013-10-30 | B | 3 | 0.0029659 | 9.2395e-06
2014 | 2013-10-17 | B | 152 | 0.030429 | 0.00046814
2014 | 2013-11-11 | B | 4 | 0.00033262 | 1.2319e-05
2014 | 2013-11-11 | B | 4 | 0.00051741 | 1.2319e-05
2014 | 2013-11-11 | B | 7 | 0.0025224 | 2.1559e-05
2014 | 2013-11-11 | B | 8 | 0.0037451 | 2.4639e-05
2014 | 2013-11-11 | B | 14 | 0.013711 | 4.3118e-05
2014 | 2013-11-11 | C | 1 | 0.00051741 | 3.0798e-06
2014 | 2013-11-11 | B | 42 | 0.040358 | 0.00012935
2014 | 2013-11-11 | C | 378 | 0.017463 | 0.0011642
2014 | 2013-11-11 | C | 2 | 0.0004743 | 6.1597e-06
2014 | 2013-11-11 | C | 9 | 0.0016354 | 2.7719e-05
2014 | 2013-11-11 | C | 8 | 0.002661 | 2.4639e-05
2014 | 2013-11-11 | C | 341 | 0.095571 | 0.0010502
2014 | 2013-11-12 | B | 13 | 0.01105 | 4.0038e-05
2014 | 2013-11-12 | B | 50 | 0.048046 | 0.00015399
2014 | 2013-11-12 | B | 35 | 0.036866 | 0.00010779
2014 | 2013-11-12 | B | 15 | 0.015476 | 4.6198e-05
2014 | 2013-11-12 | B | 15 | 0.016215 | 4.6198e-05
2014 | 2013-11-12 | C | 21 | 0.0049154 | 6.4677e-05
2014 | 2013-11-12 | C | 45.4767 | 0.059806 | 0.002507
2014 | 2013-11-12 | C | 337 | 0.03944 | 0.0010379
2014 | 2013-11-12 | C | 11 | 0.0029474 | 3.3878e-05
2014 | 2013-11-13 | C | 2 | 0.00046198 | 6.1597e-06
2014 | 2013-11-13 | B | 14 | 0.012504 | 4.3118e-05
2014 | 2013-11-13 | C | 4 | 0.0021682 | 1.2319e-05
2014 | 2013-11-13 | B | 72 | 0.072512 | 0.00022175
2014 | 2013-11-14 | B | 1 | 0.00046814 | 3.0798e-06
2014 | 2013-11-14 | B | 9 | 0.0088422 | 2.7719e-05
2014 | 2013-11-14 | B | 22.9545 | 0.027784 | 0.00013243
2014 | 2013-11-14 | C | 8 | 0.0034987 | 2.4639e-05
2014 | 2013-11-15 | C | 7 | 0.0013367 | 2.1559e-05
2014 | 2013-11-15 | B | 13 | 0.0022822 | 4.0038e-05
2014 | 2013-11-15 | B | 2 | 0.0011457 | 6.1597e-06
2014 | 2013-11-15 | B | 2 | 0.00056669 | 6.1597e-06
2014 | 2013-11-15 | C | 831 | 0.21754 | 0.0025593
2014 | 2013-11-15 | B | 7 | 0.00090547 | 2.1559e-05
2014 | 2013-11-15 | B | 5 | 0.00064677 | 1.5399e-05
2014 | 2013-11-15 | B | 9 | 0.0007484 | 2.7719e-05
2014 | 2013-11-15 | B | 16 | 0.0028088 | 4.9277e-05
2014 | 2013-11-15 | C | 1 | 0.00072992 | 3.0798e-06
2014 | 2013-11-15 | B | 32 | 0.021288 | 9.8555e-05
2014 | 2013-11-15 | C | 413.159 | 0.35629 | 0.0024269
2014 | 2013-11-15 | B | 33 | 0.024799 | 0.00010163
2014 | 2013-11-15 | B | 4 | 0.004398 | 1.2319e-05
2014 | 2013-11-15 | C | 14 | 0.0040962 | 4.3118e-05
2014 | 2013-11-16 | C | 361.5455 | 0.057902 | 0.0021744
2014 | 2013-11-16 | C | 101 | 0.0071545 | 0.00031106
2014 | 2013-11-16 | B | 22 | 0.016058 | 6.7757e-05
2014 | 2013-11-17 | C | 3 | 0.0018756 | 9.2395e-06
2014 | 2013-11-17 | C | 4 | 0.0038313 | 1.2319e-05
2014 | 2013-11-18 | B | 2 | 0.00072068 | 6.1597e-06
2014 | 2013-11-18 | C | 3 | 0.00080384 | 9.2395e-06
2014 | 2013-11-18 | B | 2 | 0.00065909 | 6.1597e-06
2014 | 2013-11-18 | B | 2 | 0.0004127 | 6.1597e-06
2014 | 2013-11-18 | B | 4 | 0.0014414 | 1.2319e-05
2014 | 2013-11-18 | B | 2 | 0.0004127 | 6.1597e-06
2014 | 2013-11-18 | B | 4 | 0.0010718 | 1.2319e-05
2014 | 2013-11-18 | B | 2 | 0.00072068 | 6.1597e-06
2014 | 2013-11-18 | B | 3 | 0.001081 | 9.2395e-06
2014 | 2013-11-18 | B | 2 | 0.0004435 | 6.1597e-06
2014 | 2013-11-18 | B | 8 | 0.001158 | 2.4639e-05
2014 | 2013-11-18 | B | 6 | 0.0073547 | 1.8479e-05
2014 | 2013-11-18 | C | 155.9494 | 0.036503 | 0.00075148
2014 | 2013-11-18 | C | 4 | 0.0015522 | 1.2319e-05
2014 | 2013-11-19 | B | 5 | 0.00081616 | 1.5399e-05
2014 | 2013-11-19 | B | 103 | 0.096436 | 0.00031722
2014 | 2013-11-19 | C | 466.44 | 0.21117 | 0.003163
2014 | 2013-11-19 | B | 3 | 0.00080384 | 9.2395e-06
2014 | 2013-11-19 | B | 15 | 0.017232 | 4.6198e-05
2014 | 2013-11-19 | B | 6 | 0.0010533 | 1.8479e-05
2014 | 2013-11-19 | B | 3 | 0.00057285 | 9.2395e-06
2014 | 2013-11-19 | B | 4 | 0.0010718 | 1.2319e-05
2014 | 2013-11-19 | B | 11 | 0.0029474 | 3.3878e-05
2014 | 2013-11-19 | B | 2 | 0.00072068 | 6.1597e-06
2014 | 2013-11-19 | B | 4 | 0.0007022 | 1.2319e-05
2014 | 2013-11-19 | B | 2 | 0.0003511 | 6.1597e-06
2014 | 2013-11-19 | B | 4 | 0.0007022 | 1.2319e-05
2014 | 2013-11-19 | B | 1 | 0.0010071 | 3.0798e-06
2014 | 2013-11-19 | C | 259 | 0.025526 | 0.00079768
2014 | 2013-11-19 | C | 1 | 0.00016323 | 3.0798e-06
2014 | 2013-11-19 | C | 1 | 0.00045274 | 3.0798e-06
2014 | 2013-11-19 | C | 1 | 8.3156e-05 | 3.0798e-06
2014 | 2013-11-19 | C | 3 | 0.00024947 | 9.2395e-06
2014 | 2013-11-19 | C | 232.4082 | 0.25911 | 0.0024762
2014 | 2013-11-20 | C | 32 | 0.023555 | 9.8555e-05
2014 | 2013-11-20 | B | 76 | 0.051261 | 0.00023407
2014 | 2013-11-13 | B | 2 | 0.0013613 | 6.1597e-06
2014 | 2013-11-13 | B | 24 | 0.020253 | 7.3916e-05
2014 | 2013-11-12 | B | 24 | 0.022175 | 7.3916e-05
2014 | 2013-11-04 | B | 8 | 0.0063814 | 2.4639e-05
2014 | 2013-11-20 | C | 13.4138 | 0.0022722 | 6.4677e-05
2014 | 2013-11-20 | B | 37 | 0.037149 | 0.00011395
2014 | 2013-11-20 | B | 4 | 0.00051741 | 1.2319e-05
2014 | 2013-11-20 | B | 5 | 0.0036496 | 1.5399e-05
2014 | 2013-11-20 | B | 4 | 0.001195 | 1.2319e-05
2014 | 2013-11-20 | B | 4 | 0.0012566 | 1.2319e-05
2014 | 2013-11-20 | B | 3 | 0.00080384 | 9.2395e-06
2014 | 2013-11-20 | B | 14 | 0.0050448 | 4.3118e-05
2014 | 2013-11-20 | B | 7 | 0.0018756 | 2.1559e-05
2014 | 2013-11-20 | B | 10 | 0.0017555 | 3.0798e-05
2014 | 2013-11-19 | B | 19 | 0.0091287 | 5.8517e-05
2014 | 2013-11-20 | C | 1 | 3.6958e-05 | 3.0798e-06
2014 | 2013-11-20 | C | 1 | 8.0076e-05 | 3.0798e-06
2014 | 2013-11-20 | C | 2166 | 0.11341 | 0.0066709
2014 | 2013-11-20 | C | 154 | 0.012806 | 0.0004743
2014 | 2013-11-20 | C | 18 | 0.023672 | 5.5437e-05
2014 | 2013-11-20 | C | 1 | 5.2357e-05 | 3.0798e-06
2014 | 2013-11-20 | C | 1 | 0.00017863 | 3.0798e-06
2014 | 2013-11-20 | C | 2547.0222 | 0.32947 | 0.019391
2014 | 2013-11-20 | C | 2309.9178 | 0.49799 | 0.0084388
2014 | 2013-11-20 | C | 55 | 0.004743 | 0.00016939
2014 | 2013-11-20 | C | 47 | 0.0731 | 0.00014475
2014 | 2013-11-20 | C | 11.4602 | 0.011859 | 0.00079768
2014 | 2013-11-21 | C | 282.4717 | 0.043498 | 0.0014475
2014 | 2013-11-21 | C | 25 | 0.0047738 | 7.6996e-05
2014 | 2013-11-21 | B | 6 | 0.0052111 | 1.8479e-05
2014 | 2013-11-21 | B | 9 | 0.0089254 | 2.7719e-05
2014 | 2013-11-21 | C | 15 | 0.0026795 | 4.6198e-05
2014 | 2013-11-21 | B | 2 | 0.0003203 | 6.1597e-06
2014 | 2013-11-21 | B | 2 | 0.0003203 | 6.1597e-06
2014 | 2013-11-21 | B | 5 | 0.00095475 | 1.5399e-05
2014 | 2013-11-21 | B | 1 | 0.00023715 | 3.0798e-06
2014 | 2013-11-21 | B | 7 | 0.0018756 | 2.1559e-05
2014 | 2013-11-21 | B | 9 | 0.0010256 | 2.7719e-05
2014 | 2013-11-21 | B | 23.625 | 0.034707 | 0.00025871
2014 | 2013-11-21 | B | 2 | 0.00057901 | 6.1597e-06
2014 | 2013-11-22 | B | 44 | 0.019243 | 0.00013551
2014 | 2013-11-22 | B | 3 | 0.0010348 | 9.2395e-06
2014 | 2013-11-22 | C | 1 | 0.00010163 | 3.0798e-06
2014 | 2013-11-22 | B | 1 | 0.00026795 | 3.0798e-06
2014 | 2013-11-22 | B | 7 | 0.00030182 | 2.1559e-05
2014 | 2013-11-22 | B | 5 | 0.0012627 | 1.5399e-05
2014 | 2013-11-22 | C | 93 | 0.0045828 | 0.00028643
2014 | 2013-11-22 | C | 49.9524 | 0.006 | 0.00018171
2014 | 2013-11-22 | C | 87.9951 | 0.054202 | 0.00063137
2014 | 2013-11-23 | C | 60 | 0.0049893 | 0.00018479
2014 | 2013-11-22 | C | 45.2084 | 0.16263 | 0.0016416
2014 | 2013-11-23 | B | 35 | 0.027703 | 0.00010779
2014 | 2013-11-23 | C | 49 | 0.0048292 | 0.00015091
2014 | 2013-11-23 | C | 712.9574 | 0.096615 | 0.0025563
2014 | 2013-11-24 | C | 298 | 0.10004 | 0.00091779
2014 | 2013-11-24 | C | 4.1725 | 0.016205 | 8.9315e-05
2014 | 2013-11-24 | C | 2 | 0.00075148 | 6.1597e-06
2014 | 2013-11-25 | C | 29 | 0.003126 | 8.9315e-05
2014 | 2013-11-25 | B | 1 | 0.00023715 | 3.0798e-06
2014 | 2013-11-25 | B | 6 | 0.0016077 | 1.8479e-05
2014 | 2013-11-25 | C | 22 | 0.0058948 | 6.7757e-05
2014 | 2013-11-25 | B | 4 | 0.0013182 | 1.2319e-05
2014 | 2013-11-25 | B | 58 | 0.039299 | 0.00017863
2014 | 2013-11-25 | C | 45 | 0.0031876 | 0.00013859
2014 | 2013-11-25 | C | 5 | 3.0798e-05 | 1.5399e-05
2014 | 2013-11-26 | C | 100.9861 | 0.088641 | 0.00064369
2014 | 2013-11-26 | B | 4 | 0.0023037 | 1.2319e-05
2014 | 2013-11-26 | C | 51 | 0.0031414 | 0.00015707
2014 | 2013-11-26 | C | 140.1818 | 0.02245 | 0.00048662
2014 | 2013-11-26 | B | 2 | 0.0017617 | 6.1597e-06
2014 | 2013-11-26 | B | 29 | 0.034565 | 8.9315e-05
2014 | 2013-11-26 | C | 9 | 0.0015245 | 2.7719e-05
2014 | 2013-11-26 | B | 3 | 0.0032523 | 9.2395e-06
2014 | 2013-11-26 | C | 357 | 0.018692 | 0.0010995
2014 | 2013-11-26 | B | 25 | 0.024793 | 7.6996e-05
2014 | 2013-11-26 | B | 2 | 0.0017432 | 6.1597e-06
2014 | 2013-11-26 | B | 37.0794 | 0.057213 | 0.00065909
2014 | 2013-11-26 | C | 3 | 0.0016908 | 9.2395e-06
2014 | 2013-11-26 | C | 63.8393 | 0.059378 | 0.00060057
2014 | 2013-11-27 | C | 113.4061 | 0.2389 | 0.00052049
2014 | 2013-11-26 | C | 77 | 0.045295 | 0.00023715
2014 | 2013-11-27 | C | 219.0488 | 0.053296 | 0.00096091
2014 | 2013-11-27 | C | 7 | 0.004937 | 2.1559e-05
2014 | 2013-11-27 | B | 2 | 0.0017432 | 6.1597e-06
2014 | 2013-11-27 | B | 2 | 0.00062829 | 6.1597e-06
2014 | 2013-11-27 | B | 3 | 0.0010348 | 9.2395e-06
2014 | 2013-11-27 | B | 4 | 0.00094859 | 1.2319e-05
2014 | 2013-11-27 | B | 7 | 0.0012289 | 2.1559e-05
2014 | 2013-11-27 | B | 9 | 0.0018571 | 2.7719e-05
2014 | 2013-11-27 | C | 1 | 0.00017247 | 3.0798e-06
2014 | 2013-11-27 | C | 698.9474 | 0.034442 | 0.0026487
2014 | 2013-11-27 | C | 61.2914 | 0.051911 | 0.0010933
2014 | 2013-11-27 | C | 127.2839 | 0.059586 | 0.0008408
2014 | 2013-11-27 | C | 3 | 0.00031414 | 9.2395e-06
2014 | 2013-11-27 | C | 8 | 0.00017247 | 2.4639e-05
2014 | 2013-11-28 | C | 261.1772 | 0.061133 | 0.0010564
2014 | 2013-11-27 | B | 15 | 0.012104 | 4.6198e-05
2014 | 2013-11-27 | C | 655.2105 | 0.032287 | 0.002778
2014 | 2013-11-27 | C | 161.7273 | 0.0094638 | 0.00059133
2014 | 2013-11-28 | C | 9 | 0.0043241 | 2.7719e-05
2014 | 2013-11-28 | C | 3 | 0.00059133 | 9.2395e-06
2014 | 2013-11-28 | B | 147.944 | 0.1859 | 0.00065909
2014 | 2013-11-28 | B | 19 | 0.021066 | 5.8517e-05
2014 | 2013-11-28 | C | 5 | 0.0057285 | 1.5399e-05
2014 | 2013-11-28 | C | 681 | 0.050337 | 0.0020974
2014 | 2013-11-28 | B | 25 | 0.028643 | 7.6996e-05
2014 | 2013-11-28 | C | 125 | 0.0084696 | 0.00038498
2014 | 2013-11-28 | C | 13 | 0.0055252 | 4.0038e-05
2014 | 2013-11-29 | B | 157 | 0.10444 | 0.00048354
2014 | 2013-11-28 | C | 15 | 0.0017093 | 4.6198e-05
2014 | 2013-11-28 | C | 79.3856 | 0.11149 | 0.00037266
2014 | 2013-11-27 | C | 187 | 0.0017278 | 0.00057593
2014 | 2013-11-29 | C | 74.5724 | 0.067523 | 0.00040654
2014 | 2013-11-29 | B | 5 | 0.0017709 | 1.5399e-05
2014 | 2013-11-28 | C | 232 | 0.015005 | 0.00071452
2014 | 2013-11-28 | C | 193 | 0.0089161 | 0.00073916
2014 | 2013-11-28 | C | 232 | 0.020007 | 0.00071452
2014 | 2013-11-28 | C | 646.7447 | 0.18126 | 0.0020974
2014 | 2013-11-29 | C | 34 | 0.029425 | 0.00010471
2014 | 2013-11-29 | C | 1 | 0.00062521 | 3.0798e-06
2014 | 2013-11-29 | B | 83 | 0.10557 | 0.00025563
2014 | 2013-11-29 | C | 2000 | 0.20327 | 0.0061597
2014 | 2013-11-30 | C | 21 | 0.0038159 | 6.4677e-05
2014 | 2013-11-30 | C | 63.3981 | 0.039637 | 0.00048662
2014 | 2013-11-30 | C | 192.4455 | 0.058085 | 0.0015368
2014 | 2013-11-30 | C | 126 | 0.037642 | 0.00038806
2014 | 2013-11-30 | C | 6 | 0.00027719 | 1.8479e-05
2014 | 2013-11-30 | C | 6 | 0.0025501 | 1.8479e-05
2014 | 2013-11-30 | C | 1039.6023 | 0.55391 | 0.0058579
2014 | 2013-11-29 | C | 77 | 0.044821 | 0.00023715
2014 | 2013-11-30 | C | 54.2424 | 0.016038 | 0.00018479
2014 | 2013-11-30 | C | 13 | 0.0037636 | 4.0038e-05
2014 | 2013-11-30 | C | 68.7899 | 0.096185 | 0.00049585
2014 | 2013-12-01 | C | 38 | 0.006788 | 0.00011703
2014 | 2013-12-01 | B | 19 | 0.0068465 | 5.8517e-05
2014 | 2013-12-01 | B | 19 | 0.0038621 | 5.8517e-05
2014 | 2013-12-01 | C | 279 | 0.1856 | 0.00085928
2014 | 2013-12-01 | C | 50 | 0.0075456 | 0.00015399
2014 | 2013-12-02 | C | 383.5684 | 0.27289 | 0.0024731
2014 | 2013-12-02 | C | 43 | 0.0029135 | 0.00013243
2014 | 2013-12-01 | C | 1734 | 0.0053404 | 0.0053404
2014 | 2013-11-29 | C | 646 | 0.15121 | 0.0019896
2014 | 2013-12-01 | C | 6 | 0.0175 | 1.8479e-05
2014 | 2013-12-02 | B | 8 | 0.0081061 | 2.4639e-05
2014 | 2013-12-02 | B | 2 | 0.0018849 | 6.1597e-06
2014 | 2013-12-02 | C | 1 | 0.00068988 | 3.0798e-06
2014 | 2013-12-02 | C | 2 | 0.00011087 | 6.1597e-06
2014 | 2013-12-02 | C | 39 | 0.014774 | 0.00012011
2014 | 2013-12-02 | B | 4 | 0.0042255 | 1.2319e-05
2014 | 2013-12-02 | B | 3 | 0.00094243 | 9.2395e-06
2014 | 2013-12-02 | B | 3 | 0.00085004 | 9.2395e-06
2014 | 2013-12-02 | B | 9 | 0.0028273 | 2.7719e-05
2014 | 2013-12-02 | C | 251.5212 | 0.12549 | 0.0022822
2014 | 2013-12-03 | B | 5 | 0.00036958 | 1.5399e-05
2014 | 2013-12-03 | C | 1 | 0.00020635 | 3.0798e-06
2014 | 2013-12-03 | C | 16 | 0.010053 | 4.9277e-05
2014 | 2013-12-03 | C | 11 | 0.0019311 | 3.3878e-05
2014 | 2013-12-03 | B | 3 | 0.00097939 | 9.2395e-06
2014 | 2013-12-03 | B | 1 | 0.00093935 | 3.0798e-06
2014 | 2013-12-03 | B | 2 | 0.00028951 | 6.1597e-06
2014 | 2013-12-03 | B | 11 | 0.0088422 | 3.3878e-05
2014 | 2013-12-03 | B | 3 | 0.00048046 | 9.2395e-06
2014 | 2013-12-03 | B | 3 | 0.0003049 | 9.2395e-06
2014 | 2013-12-03 | B | 9 | 0.0021343 | 2.7719e-05
2014 | 2013-12-03 | B | 4 | 0.00068988 | 1.2319e-05
2014 | 2013-12-03 | B | 2 | 0.00075764 | 6.1597e-06
2014 | 2013-12-03 | B | 26 | 0.035794 | 8.0076e-05
2014 | 2013-12-03 | B | 64 | 0.073325 | 0.00019711
2014 | 2013-12-03 | B | 5 | 0.0068834 | 1.5399e-05
2014 | 2013-12-03 | C | 1 | 0.00045274 | 3.0798e-06
2014 | 2013-12-03 | B | 5 | 0.00087775 | 1.5399e-05
2014 | 2013-12-03 | B | 5 | 0.0014937 | 1.5399e-05
2014 | 2013-12-03 | B | 4 | 0.0010718 | 1.2319e-05
2014 | 2013-12-04 | B | 4 | 0.0007022 | 1.2319e-05
2014 | 2013-12-04 | B | 39 | 0.02138 | 0.00012011
2014 | 2013-12-04 | B | 1 | 0.00028335 | 3.0798e-06
2014 | 2013-12-04 | B | 6 | 0.00077612 | 1.8479e-05
2014 | 2013-12-04 | B | 4 | 0.00045582 | 1.2319e-05
2014 | 2013-12-04 | C | 39 | 0.012372 | 0.00012011
2014 | 2013-12-04 | B | 8 | 0.0016508 | 2.4639e-05
2014 | 2013-12-04 | B | 5 | 0.0010317 | 1.5399e-05
2014 | 2013-12-04 | B | 7 | 0.0014444 | 2.1559e-05
2014 | 2013-12-04 | B | 4 | 0.00064061 | 1.2319e-05
2014 | 2013-12-04 | B | 2 | 0.00025871 | 6.1597e-06
2014 | 2013-12-04 | B | 6 | 0.0016077 | 1.8479e-05
2014 | 2013-12-04 | C | 376 | 0.045163 | 0.001158
2014 | 2013-12-04 | C | 209 | 0.0070806 | 0.00064369
2014 | 2013-12-04 | B | 26 | 0.028587 | 8.0076e-05
2014 | 2013-12-04 | C | 200.6071 | 0.050045 | 0.00074224
2014 | 2013-12-04 | C | 1153 | 0.074572 | 0.0035511
2014 | 2013-12-04 | C | 948.493 | 0.61345 | 0.0037235
2014 | 2013-12-05 | B | 7 | 0.0025224 | 2.1559e-05
2014 | 2013-12-05 | C | 7 | 0.0018972 | 2.1559e-05
2014 | 2013-12-05 | C | 2 | 3.6958e-05 | 6.1597e-06
2014 | 2013-12-05 | B | 6 | 0.0019773 | 1.8479e-05
2014 | 2013-12-05 | C | 2 | 0.0004127 | 6.1597e-06
2014 | 2013-12-05 | B | 64 | 0.038436 | 0.00019711
2014 | 2013-12-05 | B | 32 | 0.029468 | 9.8555e-05
2014 | 2013-12-05 | C | 616.4681 | 0.61895 | 0.003394
2014 | 2013-12-05 | C | 1616 | 0.009954 | 0.004977
2014 | 2013-12-05 | C | 872 | 0.0053712 | 0.0026856
2014 | 2013-12-05 | B | 63 | 0.048119 | 0.00019403
2014 | 2013-12-06 | C | 4 | 0.0011087 | 1.2319e-05
2014 | 2013-12-06 | C | 24 | 0.0087221 | 7.3916e-05
2014 | 2013-12-05 | B | 1 | 0.00067141 | 3.0798e-06
2014 | 2013-12-06 | B | 29 | 0.031528 | 8.9315e-05
2014 | 2013-12-06 | C | 1 | 0.00072992 | 3.0798e-06
2014 | 2013-12-06 | C | 53.5995 | 0.064215 | 0.00031414
2014 | 2013-12-07 | B | 4 | 0.0024269 | 1.2319e-05
2014 | 2013-12-07 | B | 4 | 0.0022544 | 1.2319e-05
2014 | 2013-12-07 | B | 2 | 0.00065909 | 6.1597e-06
2014 | 2013-12-07 | C | 76.3741 | 0.033872 | 0.00037266
2014 | 2013-12-07 | C | 13 | 0.028627 | 4.0038e-05
2014 | 2013-12-08 | C | 5 | 0.0011395 | 1.5399e-05
2014 | 2013-12-09 | C | 2 | 0.00059749 | 6.1597e-06
2014 | 2013-12-06 | B | 3 | 0.00080384 | 9.2395e-06
2014 | 2013-12-09 | C | 1 | 8.3156e-05 | 3.0798e-06
2014 | 2013-12-09 | B | 44 | 0.022766 | 0.00013551
2014 | 2013-12-09 | B | 11 | 0.0079275 | 3.3878e-05
2014 | 2013-12-09 | C | 1 | 0.00018479 | 3.0798e-06
2014 | 2013-12-09 | B | 99 | 0.085068 | 0.0003049
2014 | 2013-12-06 | B | 4 | 0.0007022 | 1.2319e-05
2014 | 2013-12-06 | B | 6 | 0.0010348 | 1.8479e-05
2014 | 2013-12-10 | C | 387 | 0.021454 | 0.0011919
2014 | 2013-12-10 | C | 10 | 0.0016015 | 3.0798e-05
2014 | 2013-12-10 | B | 30 | 0.017925 | 9.2395e-05
2014 | 2013-12-10 | C | 40 | 0.0067757 | 0.00012319
2014 | 2013-12-10 | B | 51 | 0.044451 | 0.00015707
2014 | 2013-12-10 | C | 2 | 0.0017062 | 6.1597e-06
2014 | 2013-12-10 | B | 6 | 0.0024947 | 1.8479e-05
2014 | 2013-12-10 | C | 102.1967 | 0.018255 | 0.00047122
2014 | 2013-12-10 | B | 9 | 0.010006 | 2.7719e-05
2014 | 2013-12-10 | C | 317 | 0.089821 | 0.00097631
2014 | 2013-12-10 | C | 22 | 0.0042687 | 6.7757e-05
2014 | 2013-12-10 | B | 45 | 0.0492 | 0.00013859
2014 | 2013-12-10 | B | 2.2632 | 0.0019656 | 4.0038e-05
2014 | 2013-12-10 | C | 125 | 0.014629 | 0.00038498
2014 | 2013-12-11 | C | 418 | 0.070806 | 0.0012874
2014 | 2013-12-11 | C | 29.1781 | 0.11727 | 0.0003973
2014 | 2013-09-18 | C | 3 | 0.00015707 | 9.2395e-06
2014 | 2013-11-17 | B | 45 | 0.057793 | 0.00013859
2014 | 2013-11-18 | B | 3 | 0.001081 | 9.2395e-06
2014 | 2013-11-18 | B | 154 | 0.028458 | 0.0004743
2014 | 2013-11-21 | B | 154 | 0.027035 | 0.0004743
2014 | 2013-11-19 | B | 44 | 0.039299 | 0.00013551
2014 | 2013-11-25 | B | 188 | 0.043426 | 0.00057901
2014 | 2013-11-28 | B | 188 | 0.044584 | 0.00057901
2014 | 2013-12-11 | C | 8 | 0.0051002 | 2.4639e-05
2014 | 2013-12-11 | B | 99 | 0.10275 | 0.0003049
2014 | 2013-12-10 | B | 18 | 0.021177 | 5.5437e-05
2014 | 2013-12-11 | B | 19 | 0.020364 | 5.8517e-05
2014 | 2013-12-11 | B | 23.6872 | 0.030567 | 0.00045274
2014 | 2013-12-11 | B | 31 | 0.029311 | 9.5475e-05
2014 | 2013-12-10 | C | 2 | 0.00053589 | 6.1597e-06
2014 | 2013-12-12 | C | 7 | 0.00079768 | 2.1559e-05
2014 | 2013-12-12 | B | 4 | 0.0029197 | 1.2319e-05
2014 | 2013-12-12 | B | 182.6313 | 0.098996 | 0.00056669
2014 | 2013-12-12 | B | 18 | 0.020345 | 5.5437e-05
2014 | 2013-12-12 | B | 66 | 0.011586 | 0.00020327
2014 | 2013-12-12 | B | 11 | 0.0024392 | 3.3878e-05
2014 | 2013-12-12 | B | 7 | 0.0070066 | 2.1559e-05
2014 | 2013-12-13 | C | 95.7156 | 0.12764 | 0.0012781
2014 | 2013-12-13 | C | 2 | 0.00037574 | 6.1597e-06
2014 | 2013-12-13 | B | 51 | 0.056075 | 0.00015707
2014 | 2013-12-13 | C | 4 | 0.00087468 | 1.2319e-05
2014 | 2013-10-10 | B | 52.5611 | 0.10279 | 0.00063445
2014 | 2013-12-13 | B | 9 | 0.014192 | 2.7719e-05
2014 | 2013-12-12 | B | 6 | 0.0072253 | 1.8479e-05
2014 | 2013-12-13 | B | 46 | 0.020968 | 0.00014167
2014 | 2013-12-14 | C | 75.7591 | 0.063231 | 0.00035726
2014 | 2013-12-14 | C | 100 | 0.011395 | 0.00030798
2014 | 2013-12-15 | C | 266.25 | 0.01394 | 0.0012473
2014 | 2013-12-15 | B | 1 | 0.0003665 | 3.0798e-06
2014 | 2013-12-15 | C | 1 | 0.00064985 | 3.0798e-06
2014 | 2013-12-07 | B | 64 | 0.048095 | 0.00019711
2014 | 2013-12-14 | C | 228.4316 | 0.3989 | 0.00081924
2014 | 2013-12-15 | C | 2 | 0.0021436 | 6.1597e-06
2014 | 2013-12-12 | C | 1811 | 0.1004 | 0.0055776
2014 | 2013-12-12 | C | 908 | 0.04754 | 0.0027965
2014 | 2013-12-12 | C | 585 | 0.032431 | 0.0018017
2014 | 2013-12-16 | B | 36 | 0.018849 | 0.00011087
2014 | 2013-12-16 | B | 97 | 0.048994 | 0.00029874
2014 | 2013-12-16 | B | 68 | 0.077279 | 0.00020943
2014 | 2013-12-16 | B | 56 | 0.032252 | 0.00017247
2014 | 2013-12-16 | C | 123 | 0.0068188 | 0.00037882
2014 | 2013-12-16 | C | 404.4404 | 0.61284 | 0.018929
2014 | 2013-12-16 | C | 4 | 0.0023776 | 1.2319e-05
2014 | 2013-12-17 | B | 3 | 0.0021528 | 9.2395e-06
2014 | 2013-12-16 | C | 114.1667 | 0.083333 | 0.00059133
2014 | 2013-12-17 | B | 72 | 0.043241 | 0.00022175
2014 | 2013-12-17 | B | 7 | 0.00090547 | 2.1559e-05
2014 | 2013-12-17 | B | 5 | 0.00064677 | 1.5399e-05
2014 | 2013-12-17 | B | 25 | 0.030182 | 7.6996e-05
2014 | 2013-12-17 | B | 5 | 0.0062675 | 1.5399e-05
2014 | 2013-12-18 | B | 9 | 0.0036311 | 2.7719e-05
2014 | 2013-12-18 | B | 1 | 0.00036034 | 3.0798e-06
2014 | 2013-12-18 | B | 35 | 0.018972 | 0.00010779
2014 | 2013-12-17 | B | 13 | 0.011651 | 4.0038e-05
2014 | 2013-12-18 | B | 1 | 0.0011919 | 3.0798e-06
2014 | 2013-12-18 | B | 31 | 0.020718 | 9.5475e-05
2014 | 2013-12-18 | B | 4 | 0.0042132 | 1.2319e-05
2014 | 2013-12-18 | B | 8 | 0.0061597 | 2.4639e-05
2014 | 2013-12-18 | B | 4 | 0.0047553 | 1.2319e-05
2014 | 2013-12-18 | C | 91 | 0.013453 | 0.00028027
2014 | 2013-12-18 | C | 2794.4179 | 0.55081 | 0.0090424
2014 | 2013-12-18 | B | 4 | 0.0047553 | 1.2319e-05
2014 | 2013-12-18 | C | 28 | 0.0078474 | 8.6236e-05
2014 | 2013-12-18 | C | 28 | 0.0078474 | 8.6236e-05
2014 | 2013-12-19 | B | 15 | 0.010625 | 4.6198e-05
2014 | 2013-12-19 | B | 101 | 0.058169 | 0.00031106
2014 | 2013-12-19 | C | 48.1296 | 0.031573 | 0.0004435
2014 | 2013-12-18 | B | 14 | 0.020955 | 4.3118e-05
2014 | 2013-12-19 | B | 26 | 0.027146 | 8.0076e-05
2014 | 2013-12-19 | C | 176.25 | 0.0027141 | 0.00071144
2014 | 2013-12-20 | C | 265.6889 | 0.2553 | 0.0026333
2014 | 2013-12-20 | C | 576.4138 | 0.046157 | 0.0036773
2014 | 2013-12-20 | C | 6 | 0.00073916 | 1.8479e-05
2014 | 2013-12-20 | C | 60 | 0.0064677 | 0.00018479
2014 | 2013-12-20 | C | 8 | 0.00064061 | 2.4639e-05
2014 | 2013-12-21 | C | 846.1608 | 0.51078 | 0.011106
2014 | 2013-12-21 | C | 95.3323 | 0.093661 | 0.00076072
2014 | 2013-12-21 | C | 27 | 0.0039083 | 8.3156e-05
2014 | 2013-12-21 | C | 66.74 | 0.081603 | 0.00040654
2014 | 2013-12-21 | C | 2 | 0.00029566 | 6.1597e-06
2014 | 2013-12-21 | C | 635.6235 | 0.16052 | 0.0029628
2014 | 2013-12-22 | C | 91.9488 | 0.060036 | 0.00045582
2014 | 2013-12-22 | C | 228 | 0.018257 | 0.0007022
2014 | 2013-12-22 | C | 173.1267 | 0.078381 | 0
2014 | 2013-12-22 | C | 98 | 0.0027164 | 0.00030182
2014 | 2013-12-22 | C | 16 | 0.0060611 | 4.9277e-05
2014 | 2013-12-22 | C | 121.3306 | 0.089309 | 0.00099479
2014 | 2013-12-23 | B | 4 | 0.00051741 | 1.2319e-05
2014 | 2013-12-23 | C | 2 | 0.00015399 | 6.1597e-06
2014 | 2013-12-24 | C | 20 | 0.0060365 | 6.1597e-05
2014 | 2013-12-25 | C | 239 | 0.011041 | 0.00073608
2014 | 2013-12-25 | C | 491.4076 | 0.27394 | 0.0020943
2014 | 2013-12-25 | C | 60.7895 | 0.035011 | 0.00034494
2014 | 2013-12-26 | C | 456.7442 | 0.11676 | 0.0020296
2014 | 2013-12-26 | C | 172.7988 | 0.088344 | 0.001466
2014 | 2013-12-26 | C | 65 | 0.015815 | 0.00020019
2014 | 2013-12-26 | C | 28 | 0.0049154 | 8.6236e-05
2014 | 2013-12-25 | C | 2 | 0.0060303 | 6.1597e-06
2014 | 2013-12-26 | C | 59.7181 | 0.026853 | 0.00028951
2014 | 2013-12-26 | C | 25.374 | 0.046576 | 0.00021251
2014 | 2013-12-27 | C | 26 | 0.0045643 | 8.0076e-05
2014 | 2013-12-27 | C | 16 | 0.0010841 | 4.9277e-05
2014 | 2013-12-27 | C | 222.8889 | 0.010297 | 0.00073608
2014 | 2013-12-27 | C | 1 | 0.00072992 | 3.0798e-06
2014 | 2013-12-28 | C | 239 | 0.011041 | 0.00073608
2014 | 2013-12-28 | C | 24 | 0.0098309 | 7.3916e-05
2014 | 2013-12-29 | C | 483 | 0.037189 | 0.0014876
2014 | 2013-12-29 | C | 4 | 0.0041886 | 1.2319e-05
2014 | 2013-12-28 | C | 47 | 0.014475 | 0.00014475
2014 | 2013-12-29 | C | 169.4626 | 0.075156 | 0.0012689
2014 | 2013-12-29 | C | 5 | 0.0022637 | 1.5399e-05
2014 | 2013-12-29 | C | 3 | 0.0015892 | 9.2395e-06
2014 | 2013-12-29 | C | 173.3663 | 0.052326 | 0.0012165
2014 | 2013-12-28 | C | 34 | 0.0030367 | 0.00010471
2014 | 2013-12-29 | C | 502 | 0.018553 | 0.0015461
2014 | 2013-12-30 | C | 62.6341 | 0.023148 | 0.0013089
2014 | 2013-12-28 | C | 2 | 0.0016446 | 6.1597e-06
2014 | 2013-12-30 | C | 94 | 0.0055006 | 0.00028951
2014 | 2013-12-29 | C | 141.3173 | 0.17975 | 0.0013798
2014 | 2013-12-30 | C | 2 | 0.036219 | 6.1597e-06
2014 | 2013-12-29 | C | 56 | 0.00034494 | 0.00017247
2014 | 2013-12-30 | C | 74 | 0.0686 | 0.00022791
2014 | 2013-12-30 | C | 25 | 0.017478 | 7.6996e-05
2014 | 2013-12-30 | C | 3 | 0.00042502 | 9.2395e-06
2014 | 2013-12-31 | C | 357.9744 | 0.12569 | 0.0021867
2014 | 2013-12-31 | C | 242 | 0.014906 | 0.00074532
2014 | 2013-12-31 | C | 125 | 0.032338 | 0.00038498
2014 | 2013-12-31 | C | 7 | 0.0011211 | 2.1559e-05
2014 | 2014-01-01 | C | 65 | 0.0050047 | 0.00020019
2014 | 2014-01-01 | C | 66.7085 | 0.055061 | 0.0013798
2014 | 2014-01-01 | C | 294.2945 | 0.27735 | 0.0020974
2014 | 2014-01-01 | C | 681 | 0.014682 | 0.0020974
2014 | 2014-01-01 | C | 74.129 | 0.034702 | 0.00028951
2014 | 2014-01-01 | C | 45 | 0.014829 | 0.00013859
2014 | 2014-01-01 | C | 131.7451 | 0.04017 | 0.0013798
2014 | 2014-01-02 | C | 741.8205 | 0.17135 | 0.0054544
2014 | 2014-01-01 | C | 2 | 0.0071884 | 6.1597e-06
2014 | 2014-01-02 | C | 203 | 0.047516 | 0.00062521
2014 | 2014-01-03 | C | 58 | 0.0053589 | 0.00017863
2014 | 2014-01-03 | C | 684 | 0.063198 | 0.0021066
2014 | 2014-01-01 | C | 160 | 0.040408 | 0.00049277
2014 | 2014-01-03 | C | 11 | 0.0034556 | 3.3878e-05
2014 | 2014-01-03 | C | 306 | 0.06974 | 0.00094243
2014 | 2014-01-03 | C | 88.722 | 0.055196 | 0.000733
2014 | 2014-01-03 | C | 7 | 0.0024362 | 2.1559e-05
2014 | 2014-01-03 | C | 113 | 0.0010441 | 0.00034802
2014 | 2014-01-03 | C | 53 | 0.037054 | 0.00016323
2014 | 2014-01-03 | C | 8 | 0.0020943 | 2.4639e-05
2014 | 2014-01-03 | C | 36 | 0.0011087 | 0.00011087
2014 | 2014-01-03 | C | 211.9604 | 0.063975 | 0.0010995
2014 | 2014-01-03 | C | 5 | 0.0013397 | 1.5399e-05
2014 | 2014-01-03 | C | 227.7189 | 0.17253 | 0.0020974
2014 | 2014-01-03 | C | 341 | 0.061963 | 0.0010502
2014 | 2014-01-03 | C | 437 | 0.15747 | 0.0013459
2014 | 2014-01-03 | C | 27 | 0.0076503 | 8.3156e-05
2014 | 2014-01-03 | C | 15.3355 | 0.0070374 | 0.00035726
2014 | 2014-01-03 | C | 2 | 0.00018479 | 6.1597e-06
2014 | 2014-01-03 | C | 4 | 0.0007638 | 1.2319e-05
2014 | 2014-01-03 | C | 3 | 0.00075764 | 9.2395e-06
2014 | 2014-01-03 | C | 1 | 0.00025871 | 3.0798e-06
2014 | 2014-01-04 | C | 68.4269 | 0.071442 | 0.0012135
2014 | 2014-01-04 | C | 65 | 0.0038036 | 0.00020019
2014 | 2014-01-04 | C | 76.8551 | 0.06462 | 0.00072992
2014 | 2014-01-04 | C | 446.7791 | 0.11421 | 0.0018479
2014 | 2014-01-04 | C | 109.4538 | 0.039104 | 0.00049893
2014 | 2014-01-04 | C | 53 | 0.0062028 | 0.00016323
2014 | 2014-01-04 | C | 38.6667 | 0.03001 | 0.00020019
2014 | 2014-01-05 | C | 44.5874 | 0.078136 | 0.0004435
2014 | 2014-01-05 | C | 10 | 0.0031722 | 3.0798e-05
2014 | 2014-01-05 | C | 7 | 0.0076534 | 2.1559e-05
2014 | 2014-01-05 | C | 2 | 0.0013798 | 6.1597e-06
2014 | 2014-01-05 | C | 166.8525 | 0.029805 | 0.00069912
2014 | 2014-01-05 | C | 157.2014 | 0.13314 | 0.00082848
2014 | 2014-01-05 | C | 46 | 0.012467 | 0.00014167
2014 | 2014-01-05 | C | 200.49 | 0.059895 | 0.0010287
2014 | 2014-01-05 | C | 7 | 0.0056269 | 2.1559e-05
2014 | 2014-01-05 | C | 6 | 0.0032338 | 1.8479e-05
2014 | 2014-01-05 | C | 2 | 0.0007946 | 6.1597e-06
2014 | 2014-01-05 | C | 2 | 0.00033262 | 6.1597e-06
2014 | 2014-01-05 | C | 108.2072 | 0.035992 | 0.00047738
2014 | 2014-01-06 | C | 94 | 0.0037636 | 0.00028951
2014 | 2013-12-21 | C | 42.1111 | 0.010116 | 0.00016323
2014 | 2014-01-06 | C | 6 | 0.0015522 | 1.8479e-05
2014 | 2014-01-06 | C | 1 | 0.00036034 | 3.0798e-06
2014 | 2014-01-06 | C | 219.7448 | 0.26056 | 0.0039607
2014 | 2014-01-05 | C | 5 | 0.018633 | 1.5399e-05
2014 | 2014-01-06 | C | 1 | 0.0003819 | 3.0798e-06
2014 | 2014-01-06 | C | 170.8611 | 0.03631 | 0.0007946
2014 | 2014-01-06 | C | 5 | 0.00041578 | 1.5399e-05
2014 | 2014-01-07 | C | 6 | 0.0019588 | 1.8479e-05
2014 | 2014-01-06 | C | 4 | 0.0008254 | 1.2319e-05
2014 | 2014-01-07 | B | 14 | 0.016902 | 4.3118e-05
2014 | 2014-01-07 | B | 3 | 0.0028827 | 9.2395e-06
2014 | 2014-01-07 | B | 2 | 0.0004435 | 6.1597e-06
2014 | 2014-01-07 | B | 4 | 0.0007022 | 1.2319e-05
2014 | 2014-01-07 | B | 5 | 0.0018017 | 1.5399e-05
2014 | 2014-01-07 | B | 4 | 0.00051741 | 1.2319e-05
2014 | 2014-01-07 | B | 6 | 0.0010533 | 1.8479e-05
2014 | 2014-01-07 | C | 1 | 0.00011395 | 3.0798e-06
2014 | 2014-01-07 | C | 125.4454 | 0.044817 | 0.00056977
2014 | 2014-01-07 | C | 26 | 0.0053651 | 8.0076e-05
2014 | 2014-01-07 | C | 5 | 0.00029258 | 1.5399e-05
2014 | 2014-01-07 | B | 2 | 0.0020327 | 6.1597e-06
2014 | 2014-01-07 | C | 74.242 | 0.18544 | 0.00045582
2014 | 2014-01-08 | B | 3 | 0.001081 | 9.2395e-06
2014 | 2014-01-08 | B | 2 | 0.00072068 | 6.1597e-06
2014 | 2014-01-08 | C | 95.6597 | 0.041541 | 0.0044196
2014 | 2014-01-01 | C | 8 | 0.0070713 | 2.4639e-05
2014 | 2014-01-01 | C | 5 | 0.0015245 | 1.5399e-05
2014 | 2014-01-08 | B | 2 | 0.00081308 | 6.1597e-06
2014 | 2014-01-08 | B | 1 | 0.00040654 | 3.0798e-06
2014 | 2014-01-08 | B | 3 | 0.0012196 | 9.2395e-06
2014 | 2014-01-08 | B | 5 | 0.0018017 | 1.5399e-05
2014 | 2014-01-08 | B | 72 | 0.072512 | 0.00022175
2014 | 2014-01-08 | C | 55 | 0.0067757 | 0.00016939
2014 | 2014-01-08 | C | 187 | 0.25341 | 0.00057593
2014 | 2014-01-08 | C | 7 | 0.0092056 | 2.1559e-05
2014 | 2014-01-09 | B | 41 | 0.025128 | 0.00012627
2014 | 2014-01-09 | B | 292 | 0.24731 | 0.00089931
2014 | 2014-01-09 | B | 5 | 0.0011087 | 1.5399e-05
2014 | 2014-01-09 | B | 3 | 0.0004435 | 9.2395e-06
2014 | 2014-01-09 | B | 10 | 0.0026795 | 3.0798e-05
2014 | 2014-01-09 | B | 6 | 0.0010533 | 1.8479e-05
2014 | 2014-01-09 | B | 8 | 0.0026363 | 2.4639e-05
2014 | 2014-01-09 | B | 7 | 0.0011211 | 2.1559e-05
2014 | 2014-01-08 | B | 4 | 0.0007022 | 1.2319e-05
2014 | 2014-01-08 | B | 6 | 0.00068372 | 1.8479e-05
2014 | 2014-01-08 | B | 8 | 0.00066525 | 2.4639e-05
2014 | 2014-01-09 | C | 16 | 0.0074409 | 4.9277e-05
2014 | 2014-01-09 | C | 673 | 0.16375 | 0.0020727
2014 | 2014-01-09 | C | 1 | 0.0007792 | 3.0798e-06
2014 | 2014-01-09 | C | 3 | 0.0035295 | 9.2395e-06
2014 | 2014-01-09 | C | 134.5177 | 0.057172 | 0.00082232
2014 | 2014-01-09 | C | 3 | 0.004398 | 9.2395e-06
2014 | 2014-01-10 | C | 7 | 0.016557 | 2.1559e-05
2014 | 2014-01-09 | C | 3002 | 0.21265 | 0.0092457
2014 | 2014-01-09 | C | 4399 | 0.35225 | 0.013548
2014 | 2014-01-09 | C | 5294 | 0.42392 | 0.016305
2014 | 2014-01-09 | B | 57.6 | 0.050913 | 0.00026795
2014 | 2014-01-10 | C | 134 | 0.0057778 | 0.0004127
2014 | 2014-01-10 | B | 4 | 0.00088699 | 1.2319e-05
2014 | 2014-01-10 | B | 7 | 0.0015522 | 2.1559e-05
2014 | 2014-01-10 | B | 4 | 0.00088699 | 1.2319e-05
2014 | 2014-01-10 | B | 2 | 0.0004127 | 6.1597e-06
2014 | 2014-01-10 | B | 86 | 0.0066217 | 0.00026487
2014 | 2014-01-10 | C | 300.9041 | 0.13252 | 0.0024793
2014 | 2014-01-11 | C | 60 | 0.0073916 | 0.00018479
2014 | 2014-01-11 | C | 19 | 0.0024577 | 5.8517e-05
2014 | 2014-01-11 | C | 5 | 0.00056977 | 1.5399e-05
2014 | 2014-01-12 | C | 595.9467 | 0.13215 | 0.002122
2014 | 2014-01-11 | C | 2 | 0.0047861 | 6.1597e-06
2014 | 2014-01-12 | C | 102 | 0.0034556 | 0.0007946
2014 | 2014-01-12 | C | 12 | 0.0025132 | 3.6958e-05
2014 | 2014-01-12 | C | 24.0926 | 0.031832 | 0.002122
2014 | 2014-01-12 | C | 293.5068 | 0.063277 | 0.0020758
2014 | 2014-01-13 | C | 9 | 0.010006 | 2.7719e-05
2014 | 2014-01-13 | C | 3 | 0.0013952 | 9.2395e-06
2014 | 2014-01-13 | C | 49 | 0.0048292 | 0.00015091
2014 | 2014-01-14 | C | 79.363 | 0.073328 | 0.00040654
2014 | 2014-01-13 | C | 630 | 0.0019403 | 0.0019403
2014 | 2014-01-13 | C | 29 | 0.0029474 | 8.9315e-05
2014 | 2014-01-13 | B | 13 | 0.0070867 | 4.0038e-05
2014 | 2014-01-13 | C | 19 | 0.0027503 | 5.8517e-05
2014 | 2014-01-13 | C | 196.28 | 0.058638 | 0.0011457
2014 | 2014-01-13 | C | 18 | 0.001774 | 5.5437e-05
2014 | 2014-01-13 | C | 20 | 0.0023407 | 6.1597e-05
2014 | 2014-01-13 | C | 5 | 0.0011703 | 1.5399e-05
2014 | 2014-01-13 | C | 23.3589 | 0.026043 | 8.6236e-05
2014 | 2014-01-13 | C | 6 | 3.6958e-05 | 1.8479e-05
2014 | 2014-01-14 | C | 244 | 0.059367 | 0.00075148
2014 | 2014-01-14 | B | 118.4017 | 0.16957 | 0.00066833
2014 | 2014-01-14 | B | 15 | 0.014321 | 4.6198e-05
2014 | 2014-01-14 | B | 6 | 0.0028643 | 1.8479e-05
2014 | 2014-01-14 | B | 53 | 0.0475 | 0.00016323
2014 | 2014-01-14 | C | 61.459 | 0.05016 | 0.00033878
2014 | 2014-01-14 | C | 62 | 0.013939 | 0.00019095
2014 | 2014-01-14 | C | 108 | 0.01397 | 0.00033262
2014 | 2014-01-15 | C | 31.8356 | 0.050397 | 0.00048354
2014 | 2014-01-13 | C | 1 | 0.00023715 | 3.0798e-06
2014 | 2014-01-15 | B | 34 | 0.021676 | 0.00010471
2014 | 2014-01-15 | B | 37 | 0.0083187 | 0.00011395
2014 | 2014-01-15 | B | 57 | 0.029317 | 0.00017555
2014 | 2014-01-15 | C | 1 | 0.00065293 | 3.0798e-06
2014 | 2014-01-15 | B | 4 | 0.00033262 | 1.2319e-05
2014 | 2013-12-17 | B | 19 | 0.011586 | 5.8517e-05
2014 | 2013-12-17 | B | 49 | 0.044368 | 0.00015091
2014 | 2013-12-16 | B | 3 | 0.0030213 | 9.2395e-06
2014 | 2013-12-07 | B | 3 | 0.00081308 | 9.2395e-06
2014 | 2013-11-30 | B | 23 | 0.020826 | 7.0836e-05
2014 | 2013-11-30 | B | 33 | 0.023986 | 0.00010163
2014 | 2014-01-15 | B | 70.3 | 0.088121 | 0.00051433
2014 | 2014-01-15 | B | 169 | 0.12492 | 0.00052049
2014 | 2014-01-15 | B | 3 | 0.0014968 | 9.2395e-06
2014 | 2014-01-16 | C | 90.6667 | 0.051938 | 0.002316
2014 | 2014-01-16 | C | 22 | 0.0036589 | 6.7757e-05
2014 | 2014-01-16 | C | 95 | 0.01024 | 0.00029258
2014 | 2014-01-16 | B | 41 | 0.039397 | 0.00012627
2014 | 2014-01-16 | B | 11 | 0.012095 | 3.3878e-05
2014 | 2014-01-16 | B | 26 | 0.018578 | 8.0076e-05
2014 | 2014-01-16 | B | 11 | 0.011417 | 3.3878e-05
2014 | 2014-01-16 | B | 8 | 0.0010348 | 2.4639e-05
2014 | 2014-01-16 | B | 2 | 0.00028951 | 6.1597e-06
2014 | 2014-01-16 | B | 4 | 0.00033262 | 1.2319e-05
2014 | 2014-01-16 | B | 1 | 5.2357e-05 | 3.0798e-06
2014 | 2014-01-16 | B | 4 | 0.00039422 | 1.2319e-05
2014 | 2014-01-16 | C | 12 | 0.013748 | 3.6958e-05
2014 | 2014-01-16 | B | 129.7586 | 0.17264 | 0.00073916
2014 | 2014-01-16 | C | 244 | 0.010521 | 0.00075148
2014 | 2014-01-16 | C | 62.0833 | 0.068261 | 0.0012751
2014 | 2014-01-17 | C | 61.1262 | 0.19184 | 0.00083464
2014 | 2014-01-16 | C | 181.3955 | 0.12123 | 0.0012381
2014 | 2014-01-16 | C | 1 | 0.0007176 | 3.0798e-06
2014 | 2014-01-16 | C | 2560 | 0.49672 | 0.0078844
2014 | 2014-01-16 | B | 1 | 0.00086544 | 3.0798e-06
2014 | 2014-01-16 | B | 53 | 0.051091 | 0.00016323
2014 | 2014-01-16 | B | 105 | 0.12903 | 0.00032338
2014 | 2014-01-16 | B | 114 | 0.14465 | 0.0003511
2014 | 2014-01-16 | C | 95 | 0.02487 | 0.00029258
2014 | 2014-01-17 | C | 371 | 0.051418 | 0.0011426
2014 | 2014-01-17 | C | 5 | 0.00016939 | 1.5399e-05
2014 | 2014-01-16 | C | 68.6292 | 0.068906 | 0.00063753
2014 | 2014-01-17 | C | 41 | 0.0045458 | 0.00012627
2014 | 2014-01-17 | B | 1 | 0.0003357 | 3.0798e-06
2014 | 2014-01-09 | C | 6 | 0.0023099 | 1.8479e-05
2014 | 2014-01-17 | B | 14 | 0.0031045 | 4.3118e-05
2014 | 2014-01-17 | C | 1 | 3.6958e-05 | 3.0798e-06
2014 | 2014-01-17 | B | 9 | 0.0007484 | 2.7719e-05
2014 | 2014-01-17 | B | 8 | 0.00066525 | 2.4639e-05
2014 | 2014-01-17 | B | 52 | 0.035554 | 0.00016015
2014 | 2014-01-17 | C | 399.7692 | 0.14036 | 0.0028489
2014 | 2014-01-17 | B | 20 | 0.025501 | 6.1597e-05
2014 | 2014-01-17 | C | 3 | 0.00019403 | 9.2395e-06
2014 | 2014-01-17 | C | 8 | 0.00071452 | 2.4639e-05
2014 | 2014-01-17 | C | 13 | 0.0039638 | 4.0038e-05
2014 | 2014-01-17 | C | 322.383 | 0.18368 | 0.0015399
2014 | 2014-01-17 | C | 1422 | 0.065693 | 0.0043795
2014 | 2014-01-17 | C | 1221 | 0.082731 | 0.0037605
2014 | 2014-01-17 | C | 2427 | 0.23172 | 0.0074748
2014 | 2014-01-17 | C | 86 | 0.0058271 | 0.00026487
2014 | 2014-01-17 | C | 236.5714 | 0.013115 | 0.00090547
2014 | 2014-01-18 | C | 110 | 0.033201 | 0.00033878
2014 | 2014-01-18 | C | 313 | 0.0057839 | 0.00096399
2014 | 2014-01-17 | C | 27 | 0.0035757 | 8.3156e-05
2014 | 2014-01-17 | C | 104 | 0.02114 | 0.0003203
2014 | 2014-01-18 | C | 228.8716 | 0.15155 | 0.0011057
2014 | 2014-01-18 | C | 54.7513 | 0.063235 | 0.0010009
2014 | 2014-01-17 | B | 82.3926 | 0.10912 | 0.00073916
2014 | 2014-01-17 | B | 3 | 0.0026517 | 9.2395e-06
2014 | 2014-01-18 | C | 614.2442 | 0.15702 | 0.0021189
2014 | 2014-01-17 | C | 148 | 0.061079 | 0.00045582
2014 | 2013-12-07 | B | 16 | 0.013601 | 4.9277e-05
2014 | 2014-01-18 | B | 13 | 0.013493 | 4.0038e-05
2014 | 2014-01-18 | C | 74.7172 | 0.11322 | 0.00093319
2014 | 2014-01-19 | C | 2514 | 0.13937 | 0.0077427
2014 | 2014-01-19 | C | 23.3659 | 0.026339 | 0.00015399
2014 | 2014-01-19 | C | 28 | 0.0025008 | 8.6236e-05
2014 | 2014-01-19 | B | 13 | 0.015294 | 4.0038e-05
2014 | 2014-01-19 | C | 2 | 0.00025871 | 6.1597e-06
2014 | 2014-01-19 | C | 316.9388 | 0.092732 | 0.0019649
2014 | 2014-01-17 | C | 12 | 0.0093504 | 3.6958e-05
2014 | 2014-01-20 | C | 408.9778 | 0.16627 | 0.0020697
2014 | 2014-01-20 | C | 509.5 | 0.34051 | 0.0046074
2014 | 2014-01-20 | B | 8 | 0.00091163 | 2.4639e-05
2014 | 2014-01-20 | B | 4 | 0.00033262 | 1.2319e-05
2014 | 2014-01-20 | C | 101 | 0.012443 | 0.00031106
2014 | 2014-01-20 | C | 394 | 0.020629 | 0.0012135
2014 | 2014-01-20 | C | 163.716 | 0.12807 | 0.0007946
2014 | 2014-01-20 | C | 93 | 0.015753 | 0.00028643
2014 | 2014-01-20 | C | 2453.8571 | 1.1412 | 0.0076072
2014 | 2014-01-20 | C | 266.8641 | 0.08219 | 0.00088391
2014 | 2014-01-20 | C | 798.5634 | 0.34186 | 0.003357
2014 | 2014-01-20 | C | 320.5846 | 0.061216 | 0.0010163
2014 | 2014-01-20 | C | 1 | 8.9315e-05 | 3.0798e-06
2014 | 2014-01-20 | C | 103.1214 | 0.24487 | 0.00033262
2014 | 2014-01-21 | C | 4 | 0.0013798 | 1.2319e-05
2014 | 2014-01-20 | C | 181.4286 | 0.41293 | 0.00069296
2014 | 2014-01-21 | C | 93.5149 | 0.037729 | 0.00052357
2014 | 2014-01-21 | C | 4 | 0.0012443 | 1.2319e-05
2014 | 2014-01-20 | C | 1312.7923 | 0.51349 | 0.0044842
2014 | 2014-01-20 | C | 77 | 0.0004743 | 0.00023715
2014 | 2014-01-20 | C | 293.6744 | 0.15286 | 0.0016231
2014 | 2014-01-20 | C | 88.7243 | 0.049733 | 0.00028951
2014 | 2014-01-20 | C | 16 | 0.0030552 | 4.9277e-05
2014 | 2014-01-21 | C | 193.4809 | 0.076274 | 0.0010564
2014 | 2014-01-20 | C | 1 | 0.0024824 | 3.0798e-06
2014 | 2014-01-20 | C | 9.3355 | 0.022196 | 4.3118e-05
2014 | 2014-01-21 | C | 38 | 0.0066709 | 0.00011703
2014 | 2014-01-20 | C | 75.9333 | 0.065949 | 0.0012781
2014 | 2014-01-21 | C | 308.1395 | 0.11958 | 0.0020142
2014 | 2014-01-21 | B | 63 | 0.063836 | 0.00019403
2014 | 2014-01-21 | C | 191.6013 | 0.091466 | 0.0020419
2014 | 2014-01-21 | C | 478 | 0.022082 | 0.0014722
2014 | 2014-01-21 | B | 5 | 0.0054975 | 1.5399e-05
2014 | 2014-01-21 | C | 1 | 0.00044658 | 3.0798e-06
2014 | 2014-01-20 | C | 65.6331 | 0.16191 | 0.00023715
2014 | 2014-01-21 | C | 4 | 0.00072684 | 1.2319e-05
2014 | 2014-01-21 | C | 88 | 0.01572 | 0.00027103
2014 | 2014-01-21 | C | 155 | 0.036758 | 0.00047738
2014 | 2014-01-20 | C | 4 | 0.013613 | 1.2319e-05
2014 | 2014-01-21 | C | 6 | 0.0012381 | 1.8479e-05
2014 | 2014-01-21 | C | 7 | 0.0020912 | 2.1559e-05
2014 | 2014-01-21 | C | 431.3048 | 0.13549 | 0.0022575
2014 | 2014-01-21 | C | 30 | 0.0015707 | 9.2395e-05
2014 | 2014-01-21 | C | 427.8 | 0.18051 | 0.0014352
2014 | 2014-01-22 | C | 1001.4598 | 0.25908 | 0.0031507
2014 | 2014-01-21 | C | 14.1191 | 0.036005 | 0.00033878
2014 | 2014-01-21 | C | 44.4677 | 0.13956 | 0.00089315
2014 | 2014-01-21 | C | 76.513 | 0.22669 | 0.0024238
2014 | 2014-01-22 | C | 6 | 0.00022175 | 1.8479e-05
2014 | 2014-01-22 | C | 169 | 0.012492 | 0.00052049
2014 | 2014-01-21 | C | 4 | 0.010681 | 1.2319e-05
2014 | 2014-01-22 | C | 1 | 2.7719e-05 | 3.0798e-06
2014 | 2014-01-21 | B | 37 | 0.013105 | 0.00011395
2014 | 2014-01-22 | C | 59 | 0.018534 | 0.00018171
2014 | 2014-01-21 | C | 2 | 0.0078782 | 6.1597e-06
2014 | 2014-01-16 | B | 136 | 0.14032 | 0.00041886
2014 | 2014-01-22 | B | 5 | 0.0053743 | 1.5399e-05
2014 | 2014-01-22 | B | 82 | 0.052782 | 0.00025255
2014 | 2014-01-22 | C | 3 | 9.2395e-05 | 9.2395e-06
2014 | 2014-01-22 | B | 7 | 0.0004743 | 2.1559e-05
2014 | 2014-01-22 | B | 6 | 0.00059133 | 1.8479e-05
2014 | 2014-01-22 | B | 8 | 0.00078844 | 2.4639e-05
2014 | 2014-01-22 | B | 3 | 0.00080384 | 9.2395e-06
2014 | 2014-01-21 | C | 3 | 0.010967 | 9.2395e-06
2014 | 2014-01-22 | B | 5 | 0.0013397 | 1.5399e-05
2014 | 2014-01-22 | B | 2 | 0.00053589 | 6.1597e-06
2014 | 2014-01-23 | B | 2 | 0.00065909 | 6.1597e-06
2014 | 2014-01-23 | C | 229.0182 | 0.036678 | 0.0019834
2014 | 2014-01-23 | B | 85 | 0.015445 | 0.00026179
2014 | 2014-01-23 | B | 14 | 0.015781 | 4.3118e-05
2014 | 2014-01-23 | B | 58 | 0.063771 | 0.00017863
2014 | 2014-01-23 | B | 105 | 0.11803 | 0.00032338
2014 | 2014-01-21 | C | 69.4783 | 0.019044 | 0.00028951
2014 | 2014-01-23 | C | 14 | 0.0018541 | 4.3118e-05
2014 | 2014-01-23 | B | 4 | 0.0026979 | 1.2319e-05
2014 | 2014-01-21 | C | 2 | 0.00010471 | 6.1597e-06
2014 | 2014-01-24 | B | 54 | 0.043906 | 0.00016631
2014 | 2014-01-24 | C | 1 | 0.00034186 | 3.0798e-06
2014 | 2014-01-21 | B | 76 | 0.027854 | 0.00023407
2014 | 2014-01-24 | C | 417 | 0.1554 | 0.0012843
2014 | 2014-01-24 | B | 3 | 0.0021436 | 9.2395e-06
2014 | 2014-01-24 | C | 125 | 0.029258 | 0.00038498
2014 | 2014-01-24 | C | 1 | 0.00015399 | 3.0798e-06
2014 | 2014-01-25 | C | 5 | 0.00060057 | 1.5399e-05
2014 | 2014-01-25 | C | 2 | 0.00053589 | 6.1597e-06
2014 | 2014-01-26 | C | 912.5978 | 0.25015 | 0.0028335
2014 | 2014-01-26 | C | 103.6724 | 0.017561 | 0.00051433
2014 | 2014-01-26 | C | 27 | 0.027774 | 8.3156e-05
2014 | 2014-01-26 | C | 5 | 0.0021867 | 1.5399e-05
2014 | 2014-01-26 | C | 37 | 0.0028489 | 0.00011395
2014 | 2014-01-26 | C | 402 | 0.20057 | 0.0012381
2014 | 2014-01-26 | C | 722.3333 | 0.16685 | 0.0026363
2014 | 2014-01-26 | C | 140.3333 | 0.097246 | 0.00085928
2014 | 2014-01-27 | C | 264 | 0.00081308 | 0.00081308
2014 | 2014-01-26 | C | 44 | 0.17834 | 0.00013551
2014 | 2014-01-27 | C | 42 | 0.0029751 | 0.00012935
2014 | 2014-01-27 | B | 33 | 0.023884 | 0.00010163
2014 | 2014-01-26 | C | 1.1745 | 0.0034724 | 1.2319e-05
2014 | 2014-01-26 | C | 137 | 0.061603 | 0.00042194
2014 | 2014-01-27 | C | 120 | 0.0051741 | 0.00036958
2014 | 2014-01-28 | C | 380 | 0.003511 | 0.0011703
2014 | 2014-01-28 | C | 7401.4103 | 0.82063 | 0.028599
2014 | 2014-01-28 | B | 6 | 0.0040284 | 1.8479e-05
2014 | 2014-01-28 | C | 3 | 0.0003511 | 9.2395e-06
2014 | 2014-01-28 | C | 401.2857 | 0.065503 | 0.0013028
2014 | 2014-01-21 | B | 11 | 0.0099602 | 3.3878e-05
2014 | 2014-01-29 | B | 107 | 0.067556 | 0.00032954
2014 | 2014-01-29 | B | 2 | 0.0018664 | 6.1597e-06
2014 | 2014-01-29 | C | 232 | 0.029295 | 0.00071452
2014 | 2014-01-29 | B | 19 | 0.02013 | 5.8517e-05
2014 | 2014-01-29 | B | 77 | 0.087508 | 0.00023715
2014 | 2014-01-29 | B | 72.2712 | 0.064994 | 0.0003203
2014 | 2014-01-29 | C | 378.3591 | 0.29831 | 0.0013028
2014 | 2014-01-30 | C | 264 | 0.01057 | 0.00081308
2014 | 2014-01-23 | C | 1 | 0.00075456 | 3.0798e-06
2014 | 2014-01-30 | B | 51 | 0.018849 | 0.00015707
2014 | 2014-01-30 | C | 7 | 0.0021343 | 2.1559e-05
2014 | 2014-01-30 | C | 48.196 | 0.036664 | 0.00030182
2014 | 2014-01-30 | C | 26 | 0.0039237 | 8.0076e-05
2014 | 2014-01-21 | B | 2 | 0.0022729 | 6.1597e-06
2014 | 2014-01-30 | C | 54 | 0.0093134 | 0.00016631
2014 | 2014-01-30 | B | 44.9005 | 0.055176 | 0.00038806
2014 | 2014-01-30 | C | 1 | 0.00025255 | 3.0798e-06
2014 | 2014-01-30 | C | 140.6764 | 0.13258 | 0.00049585
2014 | 2014-01-30 | C | 168 | 0.0051741 | 0.00051741
2014 | 2014-01-31 | C | 76 | 0.0046814 | 0.00023407
2014 | 2014-01-30 | B | 11 | 0.007521 | 3.3878e-05
2014 | 2014-01-31 | B | 18 | 0.014691 | 5.5437e-05
2014 | 2014-02-01 | C | 27 | 0.0022452 | 8.3156e-05
2014 | 2014-02-02 | C | 207.125 | 0.038913 | 0.0008562
2014 | 2014-02-02 | C | 4 | 0.0028458 | 1.2319e-05
2014 | 2014-02-02 | C | 27 | 0.010311 | 8.3156e-05
2014 | 2014-02-02 | C | 536.8947 | 0.057874 | 0.0017401
2014 | 2014-01-30 | B | 4 | 0.0027842 | 1.2319e-05
2014 | 2014-01-21 | B | 5 | 0.00064677 | 1.5399e-05
2014 | 2014-02-03 | C | 6 | 0.0010533 | 1.8479e-05
2014 | 2014-02-03 | C | 6 | 0.0024392 | 1.8479e-05
2014 | 2014-02-03 | B | 24.527 | 0.027723 | 0.00038806
2014 | 2014-02-03 | B | 25 | 0.030182 | 7.6996e-05
2014 | 2014-02-04 | B | 35 | 0.0019403 | 0.00010779
2014 | 2014-02-04 | B | 3 | 0.0025409 | 9.2395e-06
2014 | 2014-02-04 | B | 8 | 0.001158 | 2.4639e-05
2014 | 2014-02-04 | B | 6 | 0.0016077 | 1.8479e-05
2014 | 2014-02-04 | B | 5 | 0.00072376 | 1.5399e-05
2014 | 2014-02-04 | B | 13 | 0.011291 | 4.0038e-05
2014 | 2014-02-04 | B | 21.4496 | 0.026689 | 7.0836e-05
2014 | 2014-02-04 | B | 52 | 0.031069 | 0.00016015
2014 | 2014-02-04 | B | 1 | 0.0011026 | 3.0798e-06
2014 | 2014-02-04 | C | 143.1975 | 0.070123 | 0.0012597
2014 | 2014-02-04 | B | 74 | 0.0054698 | 0.00022791
2014 | 2014-02-04 | B | 18 | 0.014913 | 5.5437e-05
2014 | 2014-02-04 | B | 101 | 0.0055992 | 0.00031106
2014 | 2014-02-04 | B | 22 | 0.014364 | 6.7757e-05
2014 | 2014-02-05 | C | 184.338 | 0.078915 | 0.0024485
2014 | 2014-02-05 | C | 2 | 8.0076e-05 | 6.1597e-06
2014 | 2014-02-05 | B | 1 | 0.00020635 | 3.0798e-06
2014 | 2014-02-05 | B | 27 | 0.024531 | 8.3156e-05
2014 | 2014-02-05 | B | 5 | 0.0058055 | 1.5399e-05
2014 | 2014-02-05 | B | 64 | 0.0047306 | 0.00019711
2014 | 2014-02-05 | B | 18 | 0.011309 | 5.5437e-05
2014 | 2014-02-05 | C | 24 | 0.0034741 | 7.3916e-05
2014 | 2014-02-07 | C | 311.0877 | 0.21557 | 0.001503
2014 | 2014-02-07 | C | 4 | 0.00091163 | 1.2319e-05
2014 | 2014-02-07 | B | 33 | 0.033438 | 0.00010163
2014 | 2014-02-07 | C | 16 | 0.00034494 | 4.9277e-05
2014 | 2014-02-08 | C | 357.6667 | 0.016523 | 0.0012504
2014 | 2014-02-08 | C | 110.6591 | 0.10395 | 0.00081
2014 | 2014-02-08 | C | 221.9412 | 0.0095696 | 0.00073608
2014 | 2014-02-08 | C | 2 | 0.00043734 | 6.1597e-06
2014 | 2014-02-08 | C | 146.7069 | 0.10347 | 0.0020666
2014 | 2014-02-09 | C | 588.9453 | 0.82349 | 0.0033693
2014 | 2014-02-09 | C | 183 | 0.056925 | 0.00068065
2014 | 2014-02-08 | C | 64.8093 | 0.050699 | 0.0012504
2014 | 2014-02-08 | C | 2 | 0.0008562 | 6.1597e-06
2014 | 2014-02-08 | C | 18.5372 | 0.027461 | 0.00015399
2014 | 2014-02-08 | C | 3.1683 | 0.004957 | 2.4639e-05
2014 | 2014-02-09 | C | 39 | 0.0030028 | 0.00012011
2014 | 2014-02-10 | B | 181 | 0.012821 | 0.00055745
2014 | 2014-02-10 | C | 63.0488 | 0.047186 | 0.00026179
2014 | 2014-02-10 | C | 159.5882 | 0.040304 | 0.00073608
2014 | 2014-02-10 | B | 20 | 0.022914 | 6.1597e-05
2014 | 2014-02-10 | C | 94 | 0.028661 | 0.00028951
2014 | 2014-02-10 | C | 72.3573 | 0.22575 | 0.00044658
2014 | 2014-02-10 | C | 79 | 0.016058 | 0.00024331
2014 | 2014-02-10 | C | 38 | 0.017789 | 0.00011703
2014 | 2014-02-10 | B | 4 | 0.0033016 | 1.2319e-05
2014 | 2014-02-10 | C | 26 | 0.018978 | 8.0076e-05
2014 | 2014-02-11 | B | 33 | 0.037503 | 0.00010163
2014 | 2014-02-11 | C | 132 | 0.0036589 | 0.00040654
2014 | 2014-02-11 | C | 5 | 0.0015707 | 1.5399e-05
2014 | 2014-02-11 | B | 39 | 0.048886 | 0.00012011
2014 | 2014-02-11 | B | 9 | 0.0055437 | 2.7719e-05
2014 | 2014-02-11 | C | 2493 | 0.43765 | 0.007678
2014 | 2014-02-11 | C | 2170 | 0.060149 | 0.0066833
2014 | 2014-02-12 | B | 48 | 0.01434 | 0.00014783
2014 | 2014-02-12 | B | 33 | 0.039231 | 0.00010163
2014 | 2014-02-12 | B | 217 | 0.060149 | 0.00066833
2014 | 2014-02-13 | C | 649.6575 | 0.14006 | 0.0020974
2014 | 2014-02-13 | C | 73.5978 | 0.039894 | 0.00022791
2014 | 2014-02-13 | C | 183 | 0.012963 | 0.00056361
2014 | 2014-02-13 | B | 3 | 0.0018202 | 9.2395e-06
2014 | 2014-02-13 | B | 12 | 0.0039545 | 3.6958e-05
2014 | 2014-02-13 | B | 42 | 0.044498 | 0.00012935
2014 | 2014-02-13 | C | 29 | 0.0046444 | 8.9315e-05
2014 | 2014-02-14 | B | 6 | 0.00073916 | 1.8479e-05
2014 | 2014-02-14 | B | 7 | 0.0011642 | 2.1559e-05
2014 | 2014-02-14 | B | 10 | 0.0017555 | 3.0798e-05
2014 | 2014-02-14 | B | 4 | 0.001429 | 1.2319e-05
2014 | 2014-02-15 | C | 60 | 0.004435 | 0.00018479
2014 | 2014-02-15 | C | 50.0833 | 0.014345 | 0.00025563
2014 | 2014-02-16 | C | 64.9974 | 0.076069 | 0.00078536
2014 | 2014-02-15 | C | 125 | 0.023869 | 0.00038498
2014 | 2014-02-16 | C | 11 | 0.0015245 | 3.3878e-05
2014 | 2014-02-16 | C | 2 | 0.00042502 | 6.1597e-06
2014 | 2014-02-16 | B | 5 | 0.0016477 | 1.5399e-05
2014 | 2014-02-16 | B | 118 | 0.086131 | 0.00036342
2014 | 2014-02-15 | B | 109 | 0.097354 | 0.0003357
2014 | 2014-02-16 | C | 1 | 0.00022791 | 3.0798e-06
2014 | 2014-02-15 | B | 44 | 0.044042 | 0.00013551
2014 | 2014-02-17 | B | 4 | 0.0007638 | 1.2319e-05
2014 | 2014-02-14 | B | 1 | 0.00037574 | 3.0798e-06
2014 | 2014-02-17 | B | 3 | 0.00050817 | 9.2395e-06
2014 | 2014-02-17 | B | 2 | 0.0004743 | 6.1597e-06
2014 | 2014-02-17 | B | 73 | 0.10387 | 0.00022483
2014 | 2014-02-17 | B | 4 | 0.0026487 | 1.2319e-05
2014 | 2014-02-17 | C | 8 | 0.001774 | 2.4639e-05
2014 | 2014-02-17 | B | 1 | 0.0011919 | 3.0798e-06
2014 | 2014-02-17 | B | 32 | 0.041689 | 9.8555e-05
2014 | 2014-02-17 | C | 55.6667 | 0.0097723 | 0.0003049
2014 | 2014-02-18 | C | 417 | 0.010274 | 0.0012843
2014 | 2014-02-18 | B | 4 | 0.00067757 | 1.2319e-05
2014 | 2014-02-18 | C | 1263.7083 | 0.081732 | 0.0069574
2014 | 2014-02-18 | B | 1 | 0.0012289 | 3.0798e-06
2014 | 2014-02-18 | B | 3 | 0.0027719 | 9.2395e-06
2014 | 2014-02-18 | B | 147 | 0.16072 | 0.00045274
2014 | 2014-02-18 | B | 42 | 0.046179 | 0.00012935
2014 | 2014-02-18 | C | 185.9373 | 0.21761 | 0.00097323
2014 | 2014-02-19 | B | 32 | 0.038338 | 9.8555e-05
2014 | 2014-02-19 | C | 1 | 0.00025871 | 3.0798e-06
2014 | 2014-02-19 | B | 55 | 0.023545 | 0.00016939
2014 | 2014-02-19 | B | 12 | 0.010866 | 3.6958e-05
2014 | 2014-02-19 | B | 3 | 0.00034186 | 9.2395e-06
2014 | 2014-02-19 | B | 4 | 0.00088699 | 1.2319e-05
2014 | 2014-02-19 | B | 5 | 0.00084696 | 1.5399e-05
2014 | 2014-02-19 | B | 5 | 0.00047738 | 1.5399e-05
2014 | 2014-02-19 | B | 3 | 0.00048046 | 9.2395e-06
2014 | 2014-02-19 | B | 5 | 0.0044812 | 1.5399e-05
2014 | 2014-02-19 | B | 19 | 0.0062613 | 5.8517e-05
2014 | 2014-02-19 | C | 62 | 0.0093566 | 0.00019095
2014 | 2014-02-19 | C | 7.233 | 0.0061483 | 0.0003819
2014 | 2014-02-19 | C | 275.849 | 0.29565 | 0.0018972
2014 | 2014-02-20 | C | 218.359 | 0.050438 | 0.0013028
2014 | 2014-02-20 | B | 13 | 0.016295 | 4.0038e-05
2014 | 2014-02-20 | C | 410 | 0.046721 | 0.0016015
2014 | 2014-02-20 | B | 7 | 0.0028458 | 2.1559e-05
2014 | 2014-02-20 | B | 6 | 0.0017001 | 1.8479e-05
2014 | 2014-02-20 | C | 417 | 0.011559 | 0.0012843
2014 | 2014-02-20 | B | 225 | 0.029105 | 0.00069296
2014 | 2014-02-20 | C | 369.03 | 0.11025 | 0.0012535
2014 | 2014-02-21 | C | 146.8618 | 0.067394 | 0.00079152
2014 | 2014-02-21 | C | 480.8333 | 0.10218 | 0.0019588
2014 | 2014-02-21 | C | 208.4751 | 0.16565 | 0.0021405
2014 | 2014-02-21 | C | 1 | 0.00060673 | 3.0798e-06
2014 | 2014-02-11 | C | 154 | 0.0042687 | 0.0004743
2014 | 2014-02-20 | B | 10 | 0.0088391 | 3.0798e-05
2014 | 2014-02-21 | B | 84 | 0.095204 | 0.00025871
2014 | 2014-02-20 | B | 38 | 0.042366 | 0.00011703
2014 | 2014-02-21 | B | 61 | 0.010145 | 0.00018787
2014 | 2014-02-21 | B | 1 | 0.00078228 | 3.0798e-06
2014 | 2014-02-21 | B | 42 | 0.038418 | 0.00012935
2014 | 2014-02-21 | C | 41.2709 | 0.037624 | 0.00020635
2014 | 2014-02-22 | C | 174.6444 | 0.14361 | 0.001004
2014 | 2014-02-23 | C | 63.3103 | 0.016379 | 0.00020327
2014 | 2014-02-22 | C | 357.6443 | 0.16082 | 0.0018602
2014 | 2014-02-23 | C | 18.8072 | 0.0046339 | 0.00078228
2014 | 2014-01-23 | B | 1 | 0.00075456 | 3.0798e-06
2014 | 2014-02-22 | B | 1 | 9.8555e-05 | 3.0798e-06
2014 | 2014-02-23 | C | 116 | 0.073596 | 0.00035726
2014 | 2014-02-24 | B | 1 | 5.2357e-05 | 3.0798e-06
2014 | 2014-02-24 | B | 3 | 0.00015707 | 9.2395e-06
2014 | 2014-02-24 | B | 1 | 5.2357e-05 | 3.0798e-06
2014 | 2014-02-24 | B | 8 | 0.0038683 | 2.4639e-05
2014 | 2014-02-24 | B | 9 | 0.0013028 | 2.7719e-05
2014 | 2014-02-24 | B | 64 | 0.086728 | 0.00019711
2014 | 2014-02-24 | B | 2 | 0.00095475 | 6.1597e-06
2014 | 2014-02-24 | B | 4 | 0.0016878 | 1.2319e-05
2014 | 2014-02-24 | C | 32 | 0.0055191 | 9.8555e-05
2014 | 2014-02-24 | C | 152.8621 | 0.080505 | 0.0037328
2014 | 2014-02-24 | C | 30.683 | 0.05755 | 0.00023099
2014 | 2014-02-24 | B | 2 | 0.0027349 | 6.1597e-06
2014 | 2014-02-24 | C | 21.0658 | 0.0047362 | 7.0836e-05
2014 | 2014-02-24 | C | 77 | 0.074227 | 0.00023715
2014 | 2014-02-25 | B | 26 | 0.012412 | 8.0076e-05
2014 | 2014-02-25 | B | 160 | 0.09954 | 0.00049277
2014 | 2014-02-25 | B | 1 | 0.00032954 | 3.0798e-06
2014 | 2014-02-25 | B | 24 | 0.0082786 | 7.3916e-05
2014 | 2014-02-25 | B | 13 | 0.012972 | 4.0038e-05
2014 | 2014-02-25 | B | 108 | 0.10378 | 0.00033262
2014 | 2014-02-25 | B | 15 | 0.017601 | 4.6198e-05
2014 | 2014-02-25 | B | 64 | 0.095795 | 0.00019711
2014 | 2014-02-25 | B | 111.8835 | 0.14093 | 0.0011488
2014 | 2014-02-25 | C | 5 | 3.0798e-05 | 1.5399e-05
2014 | 2014-02-25 | C | 34 | 0.0062829 | 0.00010471
2014 | 2014-02-26 | C | 155.0381 | 0.048704 | 0.00079152
2014 | 2014-02-26 | B | 7 | 0.0037728 | 2.1559e-05
2014 | 2014-02-26 | B | 71 | 0.066038 | 0.00021867
2014 | 2014-02-26 | B | 59 | 0.0076318 | 0.00018171
2014 | 2014-02-26 | B | 9 | 0.0097569 | 2.7719e-05
2014 | 2014-02-26 | C | 178 | 0.016995 | 0.00054821
2014 | 2014-02-26 | B | 5 | 0.00090855 | 1.5399e-05
2014 | 2014-02-26 | B | 236 | 0.2682 | 0.00072684
2014 | 2014-02-26 | B | 66 | 0.084763 | 0.00020327
2014 | 2014-02-26 | B | 34 | 0.041991 | 0.00010471
2014 | 2014-02-25 | B | 2 | 0.0025932 | 6.1597e-06
2014 | 2014-02-26 | B | 12 | 0.0021066 | 3.6958e-05
2014 | 2014-02-26 | C | 6 | 0.002199 | 1.8479e-05
2014 | 2014-02-26 | C | 9 | 0.0041023 | 2.7719e-05
2014 | 2014-02-26 | C | 111 | 0.080338 | 0.00034186
2014 | 2014-02-26 | C | 244.4293 | 0.13626 | 0.0025655
2014 | 2014-02-24 | B | 8 | 0.0043611 | 2.4639e-05
2014 | 2014-02-26 | B | 3 | 0.00091471 | 9.2395e-06
2014 | 2014-02-27 | B | 4 | 0.00091163 | 1.2319e-05
2014 | 2014-02-27 | B | 36 | 0.011864 | 0.00011087
2014 | 2014-02-27 | C | 12 | 0.014266 | 3.6958e-05
2014 | 2014-02-28 | C | 684.9758 | 0.25526 | 0.0052942
2014 | 2014-02-28 | C | 14 | 0.0048292 | 4.3118e-05
2014 | 2014-02-28 | C | 57.0055 | 0.063029 | 0.0012751
2014 | 2014-02-28 | B | 133 | 0.049564 | 0.00040962
2014 | 2014-02-28 | B | 7 | 0.0038159 | 2.1559e-05
2014 | 2014-02-28 | B | 11 | 0.011925 | 3.3878e-05
2014 | 2014-02-28 | C | 5 | 0.0031876 | 1.5399e-05
2014 | 2014-02-28 | C | 6 | 0.00036958 | 1.8479e-05
2014 | 2014-03-01 | C | 132.9062 | 0.051166 | 0.0027811
2014 | 2014-03-01 | B | 17 | 0.0068588 | 5.2357e-05
2014 | 2014-02-27 | B | 42 | 0.035184 | 0.00012935
2014 | 2014-02-27 | B | 1 | 0.00013243 | 3.0798e-06
2014 | 2014-02-27 | B | 78 | 0.07375 | 0.00024023
2014 | 2014-02-28 | B | 78 | 0.064861 | 0.00024023
2014 | 2014-02-28 | C | 39 | 0.0069666 | 0.00012011
2014 | 2014-03-02 | C | 13 | 0.0096892 | 4.0038e-05
2014 | 2014-03-02 | C | 399.2308 | 0.012296 | 0.0012843
2014 | 2014-02-28 | C | 151 | 0.015812 | 0.00046506
2014 | 2014-03-01 | C | 34 | 0.0012566 | 0.00010471
2014 | 2014-03-03 | C | 3 | 0.00011087 | 9.2395e-06
2014 | 2014-03-03 | C | 239 | 0.011777 | 0.00073608
2014 | 2014-03-03 | B | 4 | 0.0025501 | 1.2319e-05
2014 | 2014-03-03 | C | 143.1731 | 0.021607 | 0.00067757
2014 | 2014-02-28 | C | 173.8235 | 0.071201 | 0.0011272
2014 | 2014-02-28 | C | 318.1519 | 0.15188 | 0.0020974
2014 | 2014-03-03 | C | 76.0342 | 0.1021 | 0.0020881
2014 | 2014-03-03 | C | 49 | 0.0025655 | 0.00015091
2014 | 2014-03-03 | C | 8 | 0.00027103 | 2.4639e-05
2014 | 2014-03-03 | B | 2 | 0.001503 | 6.1597e-06
2014 | 2014-02-27 | B | 155 | 0.17854 | 0.00047738
2014 | 2014-03-03 | B | 6 | 0.0076873 | 1.8479e-05
2014 | 2014-03-03 | C | 1810.1507 | 0.39025 | 0.0063168
2014 | 2014-03-04 | B | 3 | 0.00057285 | 9.2395e-06
2014 | 2014-03-04 | B | 2 | 0.0013736 | 6.1597e-06
2014 | 2014-03-04 | B | 13 | 0.006286 | 4.0038e-05
2014 | 2014-03-04 | B | 18 | 0.014192 | 5.5437e-05
2014 | 2014-03-01 | C | 1 | 0.0046783 | 3.0798e-06
2014 | 2014-03-04 | C | 110.3529 | 0.056758 | 0.0010595
2014 | 2014-03-04 | B | 85 | 0.097385 | 0.00026179
2014 | 2014-03-04 | B | 6 | 0.0075579 | 1.8479e-05
2014 | 2014-03-04 | C | 231 | 0.0085373 | 0.00071144
2014 | 2014-03-04 | C | 152.3529 | 0.0065691 | 0.00048046
2014 | 2014-03-05 | C | 155.759 | 0.038377 | 0.00063753
2014 | 2014-03-05 | C | 58.6644 | 0.10443 | 0.00028951
2014 | 2014-03-04 | C | 79.8164 | 0.050148 | 0.00088083
2014 | 2014-03-04 | C | 170 | 0.0062829 | 0.00052357
2014 | 2014-03-05 | C | 137.312 | 0.051594 | 0.00078228
2014 | 2014-03-05 | C | 202.715 | 0.11862 | 0.0011488
2014 | 2014-03-05 | C | 73.5124 | 0.072224 | 0.00091779
2014 | 2014-03-05 | C | 127.1064 | 0.072421 | 0.00040346
2014 | 2014-03-05 | C | 10 | 0.00089315 | 3.0798e-05
2014 | 2014-03-05 | C | 298 | 0.0018356 | 0.00091779
2014 | 2014-03-05 | B | 114 | 0.10006 | 0.0003511
2014 | 2014-03-05 | C | 2 | 0.00056053 | 6.1597e-06
2014 | 2014-03-05 | C | 464.2111 | 0.12438 | 0.0026394
2014 | 2014-03-05 | C | 116 | 0.21471 | 0.00035726
2014 | 2014-03-05 | C | 480.9378 | 0.30513 | 0.002082
2014 | 2014-03-05 | C | 126 | 0.02406 | 0.00038806
2014 | 2014-03-05 | B | 70 | 0.012504 | 0.00021559
2014 | 2014-03-05 | B | 19 | 0.01656 | 5.8517e-05
2014 | 2014-03-05 | C | 3 | 0.00077612 | 9.2395e-06
2014 | 2014-03-05 | C | 96.0179 | 0.081619 | 0.00037266
2014 | 2014-03-05 | C | 104.2149 | 0.037874 | 0.00032646
2014 | 2014-03-05 | C | 92.4688 | 0.026485 | 0.00037266
2014 | 2014-03-06 | C | 90.0749 | 0.062141 | 0.00037266
2014 | 2014-03-05 | B | 1 | 0.00019095 | 3.0798e-06
2014 | 2014-03-06 | B | 29 | 0.026705 | 8.9315e-05
2014 | 2014-03-05 | C | 24.3715 | 0.085043 | 0.00023099
2014 | 2014-03-06 | B | 6 | 0.0050263 | 1.8479e-05
2014 | 2014-03-06 | B | 55 | 0.050309 | 0.00016939
2014 | 2014-03-06 | B | 80.8126 | 0.12942 | 0.00094551
2014 | 2014-03-07 | B | 25 | 0.0053127 | 7.6996e-05
2014 | 2014-03-07 | B | 4 | 0.00062829 | 1.2319e-05
2014 | 2014-03-07 | B | 2 | 0.00026487 | 6.1597e-06
2014 | 2014-03-06 | C | 21.7143 | 0.024142 | 0.00011395
2014 | 2014-03-08 | C | 22 | 0.0038621 | 6.7757e-05
2014 | 2014-03-07 | C | 54 | 0.0078166 | 0.00016631
2014 | 2014-03-09 | C | 108.8527 | 0.042241 | 0.00049893
2014 | 2014-03-09 | C | 87 | 0.0045551 | 0.00026795
2014 | 2014-03-09 | C | 82.7826 | 0.028555 | 0.00085004
2014 | 2014-03-09 | C | 1202.8235 | 0.051863 | 0.0041147
2014 | 2014-03-08 | C | 105.2965 | 0.054806 | 0.00056053
2014 | 2014-03-07 | B | 3 | 0.0034001 | 9.2395e-06
2014 | 2014-03-08 | B | 124 | 0.087073 | 0.0003819
2014 | 2014-03-08 | B | 29.8438 | 0.017372 | 9.2395e-05
2014 | 2014-03-07 | B | 2.9793 | 0.001303 | 9.2395e-06
2014 | 2014-03-08 | C | 252.8704 | 0.081774 | 0.0020727
2014 | 2014-03-09 | C | 19 | 0.0010533 | 5.8517e-05
2014 | 2014-03-10 | B | 9 | 0.0040746 | 2.7719e-05
2014 | 2014-03-10 | C | 35.7473 | 0.071562 | 0.00017863
2014 | 2014-03-10 | B | 160 | 0.034494 | 0.00049277
2014 | 2014-03-11 | C | 261 | 0.011254 | 0.00080384
2014 | 2014-03-09 | C | 2 | 0.00067757 | 6.1597e-06
2014 | 2014-03-09 | C | 2 | 4.9277e-05 | 6.1597e-06
2014 | 2014-03-11 | B | 449 | 0.087119 | 0.0013828
2014 | 2014-03-11 | B | 51 | 0.049006 | 0.00015707
2014 | 2014-03-11 | B | 6 | 0.0010163 | 1.8479e-05
2014 | 2014-03-11 | B | 3 | 0.002393 | 9.2395e-06
2014 | 2014-03-11 | B | 55 | 0.073346 | 0.00016939
2014 | 2014-03-11 | C | 4 | 0.0019341 | 1.2319e-05
2014 | 2014-03-12 | C | 217.7854 | 0.14488 | 0.00099479
2014 | 2014-03-12 | B | 6 | 0.0014044 | 1.8479e-05
2014 | 2014-03-12 | B | 3 | 0.00034186 | 9.2395e-06
2014 | 2014-03-12 | B | 1 | 0.00065293 | 3.0798e-06
2014 | 2014-03-12 | B | 141 | 0.051677 | 0.00043426
2014 | 2014-03-12 | B | 6 | 0.0018849 | 1.8479e-05
2014 | 2014-03-13 | C | 20 | 0.0043118 | 6.1597e-05
2014 | 2014-03-13 | C | 766 | 0.068416 | 0.0023592
2014 | 2014-03-13 | B | 65 | 0.035434 | 0.00020019
2014 | 2014-03-13 | B | 69 | 0.084154 | 0.00021251
2014 | 2014-03-13 | C | 6 | 0.0033447 | 1.8479e-05
2014 | 2014-03-13 | C | 110.4317 | 0.046255 | 0.00047122
2014 | 2014-03-14 | C | 75 | 0.0094705 | 0.00023099
2014 | 2014-03-15 | C | 262 | 0.013718 | 0.00080692
2014 | 2014-03-15 | C | 64 | 0.013403 | 0.00019711
2014 | 2014-03-15 | C | 1788 | 0.044054 | 0.0055068
2014 | 2014-03-15 | C | 242.352 | 0.091062 | 0.00089931
2014 | 2014-03-15 | C | 194.0395 | 0.089044 | 0.00073608
2014 | 2014-03-15 | C | 281.4328 | 0.055473 | 0.0012627
2014 | 2014-03-15 | C | 2029.4439 | 2.7689 | 0.0081647
2014 | 2014-03-15 | C | 270.1156 | 0.1198 | 0.001235
2014 | 2014-03-15 | C | 446.8085 | 0.12523 | 0.002199
2014 | 2014-03-15 | C | 194.8165 | 0.093001 | 0.000733
2014 | 2014-03-15 | C | 186.8 | 0.021287 | 0.00073916
2014 | 2014-03-15 | C | 122.2876 | 0.056494 | 0.00052357
2014 | 2014-03-15 | C | 15 | 0.0023561 | 4.6198e-05
2014 | 2014-03-15 | C | 9 | 0.0042964 | 2.7719e-05
2014 | 2014-03-15 | C | 168.9257 | 0.16648 | 0.001774
2014 | 2014-03-15 | C | 19.8526 | 0.09312 | 0.00093627
2014 | 2014-03-15 | C | 30.8346 | 0.037037 | 0.00023715
2014 | 2014-03-16 | C | 6 | 0.00068372 | 1.8479e-05
2014 | 2014-03-15 | C | 93.1329 | 0.14801 | 0.0012751
2014 | 2014-03-15 | C | 70.91 | 0.10374 | 0.00086852
2014 | 2014-03-15 | C | 11 | 0.0056238 | 3.3878e-05
2014 | 2014-03-15 | C | 24 | 0.0060611 | 7.3916e-05
2014 | 2014-03-15 | C | 195.3355 | 0.089639 | 0.00162
2014 | 2014-03-15 | C | 103.7353 | 0.0099041 | 0.00033262
2014 | 2014-03-15 | C | 35 | 0.0050663 | 0.00010779
2014 | 2014-03-16 | C | 457 | 0.05067 | 0.0014075
2014 | 2014-03-15 | C | 42.5 | 0.0051048 | 0.00015399
2014 | 2014-03-15 | C | 3 | 0.010348 | 9.2395e-06
2014 | 2014-03-15 | C | 325 | 0.0010009 | 0.0010009
2014 | 2014-03-15 | C | 173 | 0.02078 | 0.00053281
2014 | 2014-03-15 | C | 305.8317 | 0.28257 | 0.0015923
2014 | 2014-03-15 | C | 149.1161 | 0.050059 | 0.00047122
2014 | 2014-03-15 | C | 44 | 0.0094859 | 0.00013551
2014 | 2014-03-15 | C | 186.3746 | 0.20205 | 0.0010009
2014 | 2014-03-16 | C | 2 | 1.8479e-05 | 6.1597e-06
2014 | 2014-03-16 | C | 1351.1792 | 0.42863 | 0.0042101
2014 | 2014-03-16 | C | 41 | 0.06642 | 0.00012627
2014 | 2014-03-15 | C | 94 | 0.23363 | 0.00028951
2014 | 2014-03-15 | C | 76.4724 | 0.20867 | 0.00083772
2014 | 2014-03-15 | C | 390.1694 | 0.1454 | 0.0014383
2014 | 2014-03-15 | C | 57.4198 | 0.022636 | 0.00052357
2014 | 2014-03-16 | C | 1431.8421 | 0.57328 | 0.0044873
2014 | 2014-03-16 | C | 65 | 0.0058055 | 0.00020019
2014 | 2014-03-15 | C | 56 | 0.0070713 | 0.00017247
2014 | 2014-03-15 | C | 8 | 0.001774 | 2.4639e-05
2014 | 2014-03-15 | C | 166.6804 | 0.048255 | 0.0025286
2014 | 2014-03-16 | C | 42 | 0.0069851 | 0.00012935
2014 | 2014-03-15 | C | 947 | 0.16625 | 0.0029166
2014 | 2014-03-16 | C | 5 | 0.0027103 | 1.5399e-05
2014 | 2014-03-16 | C | 11 | 0.00040654 | 3.3878e-05
2014 | 2014-03-16 | C | 8 | 0.00054205 | 2.4639e-05
2014 | 2014-03-16 | C | 2 | 0.0004435 | 6.1597e-06
2014 | 2014-03-16 | C | 29 | 0.0020543 | 8.9315e-05
2014 | 2014-03-16 | C | 4 | 0.00011087 | 1.2319e-05
2014 | 2014-03-16 | C | 3 | 0.00071144 | 9.2395e-06
2014 | 2014-03-16 | C | 19 | 0.016443 | 5.8517e-05
2014 | 2014-03-16 | C | 5 | 0.0024485 | 1.5399e-05
2014 | 2014-03-16 | C | 12 | 0.0022914 | 3.6958e-05
2014 | 2014-03-16 | C | 8 | 0.00098555 | 2.4639e-05
2014 | 2014-03-16 | C | 6 | 0.0019218 | 1.8479e-05
2014 | 2014-03-16 | C | 1362 | 0.11326 | 0.0041947
2014 | 2014-03-16 | C | 18 | 0.013471 | 5.5437e-05
2014 | 2014-03-16 | C | 209.5821 | 0.1278 | 0.001968
2014 | 2014-03-16 | C | 361.7215 | 0.17268 | 0.0060796
2014 | 2014-03-16 | C | 14.4232 | 0.029673 | 0.00019403
2014 | 2014-03-16 | C | 737.8 | 0.0045446 | 0.0033539
2014 | 2014-03-17 | C | 45.4078 | 0.024613 | 0.00022175
2014 | 2014-03-17 | C | 383.977 | 0.46003 | 0.0025224
2014 | 2014-03-16 | C | 6 | 0.0034186 | 1.8479e-05
2014 | 2014-03-15 | C | 107.1759 | 0.070308 | 0.00044042
2014 | 2014-03-16 | C | 937.2336 | 0.3002 | 0.0034741
2014 | 2014-03-17 | C | 28 | 0.0018109 | 8.6236e-05
2014 | 2014-03-17 | C | 14 | 0.0065108 | 4.3118e-05
2014 | 2014-03-17 | C | 80 | 0.016015 | 0.00024639
2014 | 2014-03-17 | C | 1 | 0.00056053 | 3.0798e-06
2014 | 2014-03-17 | C | 72 | 0.0093134 | 0.00022175
2014 | 2014-03-17 | C | 48 | 0.0078351 | 0.00014783
2014 | 2014-03-17 | C | 85 | 0.012042 | 0.00026179
2014 | 2014-03-17 | C | 47 | 0.0060796 | 0.00014475
2014 | 2014-03-17 | C | 5 | 0.00040038 | 1.5399e-05
2014 | 2014-03-18 | C | 94 | 0.02924 | 0.00028951
2014 | 2014-03-18 | C | 144.0066 | 0.065641 | 0.0011395
2014 | 2014-03-18 | B | 1 | 0.0012689 | 3.0798e-06
2014 | 2014-03-18 | C | 74.5966 | 0.039746 | 0.0003511
2014 | 2014-03-18 | B | 6 | 0.0033632 | 1.8479e-05
2014 | 2014-03-19 | C | 210 | 0.0097015 | 0.00064677
2014 | 2014-03-19 | C | 358.7222 | 0.116 | 0.001891
2014 | 2014-03-19 | C | 3 | 9.2395e-06 | 9.2395e-06
2014 | 2014-03-19 | C | 1 | 0.00019095 | 3.0798e-06
2014 | 2014-03-19 | C | 433.2624 | 0.29089 | 0.0049893
2014 | 2014-03-19 | C | 619.5294 | 0.41596 | 0.0071083
2014 | 2014-03-19 | C | 712 | 0.010964 | 0.0021928
2014 | 2014-03-19 | C | 203.3333 | 0.33065 | 0.0021959
2014 | 2014-03-19 | C | 572.5 | 0.022922 | 0.0024639
2014 | 2014-03-20 | B | 2 | 0.00059749 | 6.1597e-06
2014 | 2014-03-21 | C | 49.7454 | 0.090393 | 0.0010564
2014 | 2014-03-22 | C | 42 | 0.0045274 | 0.00012935
2014 | 2014-03-22 | C | 15 | 0.0031876 | 4.6198e-05
2014 | 2014-03-22 | C | 6 | 0.0031414 | 1.8479e-05
2014 | 2014-03-22 | C | 20.8726 | 0.0098998 | 0.00060365
2014 | 2014-03-23 | C | 10 | 0.00067757 | 3.0798e-05
2014 | 2014-03-24 | C | 235.682 | 0.15533 | 0.0024916
2014 | 2014-03-25 | C | 2 | 0.00019711 | 6.1597e-06
2014 | 2014-03-25 | C | 468.9048 | 0.11698 | 0.0034494
2014 | 2014-03-26 | C | 6 | 0.00086852 | 1.8479e-05
2014 | 2014-03-26 | C | 53.5152 | 0.026701 | 0.00058825
2014 | 2014-03-27 | C | 178 | 0.0016446 | 0.00054821
2014 | 2014-03-28 | C | 920 | 0.13884 | 0.0028335
2014 | 2014-03-28 | C | 815.8182 | 0.13065 | 0.0034802
2014 | 2014-03-28 | C | 164 | 0.0070713 | 0.00050509
2014 | 2014-03-30 | C | 27 | 0.024448 | 8.3156e-05
2014 | 2014-03-16 | C | 12 | 0.062311 | 3.6958e-05
2014 | 2014-03-31 | C | 1223.6327 | 0.35802 | 0.0041609
2014 | 2014-03-31 | C | 61 | 0.0065755 | 0.00018787
2014 | 2014-03-31 | C | 22.8143 | 0.019463 | 0.00012011
2015 | 2014-04-01 | C | 6 | 0.00076971 | 1.8327e-05
2015 | 2014-04-01 | B | 54 | 0.047173 | 0.00016494
2015 | 2014-04-01 | C | 1 | 9.4687e-05 | 3.0544e-06
2015 | 2014-04-01 | B | 35 | 0.038379 | 0.0001069
2015 | 2014-04-01 | B | 10 | 0.0077888 | 3.0544e-05
2015 | 2014-04-01 | B | 463 | 0.55012 | 0.0014142
2015 | 2014-04-01 | C | 24 | 0.0055713 | 7.3306e-05
2015 | 2014-04-02 | C | 25 | 0.0028253 | 7.6361e-05
2015 | 2014-04-01 | C | 1 | 0.00060478 | 3.0544e-06
2015 | 2014-04-02 | B | 45 | 0.018143 | 0.00013745
2015 | 2014-04-02 | B | 56 | 0.053367 | 0.00017105
2015 | 2014-04-02 | C | 326 | 0.073068 | 0.00099574
2015 | 2014-04-02 | C | 8644 | 1.2673 | 0.026402
2015 | 2014-04-02 | C | 2651 | 0.88207 | 0.0080973
2015 | 2014-04-02 | B | 69 | 0.037304 | 0.00021076
2015 | 2014-04-02 | B | 35 | 0.022343 | 0.0001069
2015 | 2014-04-02 | B | 35 | 0.025336 | 0.0001069
2015 | 2014-04-03 | B | 2 | 0.00022603 | 6.1088e-06
2015 | 2014-04-03 | C | 2928 | 0.49954 | 0.0089434
2015 | 2014-04-03 | B | 3 | 0.0023091 | 9.1633e-06
2015 | 2014-04-03 | C | 456 | 0.13244 | 0.0013928
2015 | 2014-04-03 | B | 1 | 0.00098352 | 3.0544e-06
2015 | 2014-04-03 | C | 691 | 0.18754 | 0.0021106
2015 | 2014-04-03 | C | 678 | 0.21058 | 0.0020709
2015 | 2014-04-03 | C | 1119 | 0.1333 | 0.0034179
2015 | 2014-04-03 | C | 1336 | 0.38673 | 0.0040807
2015 | 2014-04-04 | B | 1 | 0.00062616 | 3.0544e-06
2015 | 2014-04-04 | C | 20 | 0.0032377 | 6.1088e-05
2015 | 2014-04-04 | B | 25 | 0.035126 | 7.6361e-05
2015 | 2014-04-04 | C | 418 | 0.24135 | 0.0012767
2015 | 2014-04-05 | C | 11 | 0.0022847 | 3.3599e-05
2015 | 2014-04-05 | C | 58 | 0.043089 | 0.00017716
2015 | 2014-04-05 | B | 33 | 0.02409 | 0.0001008
2015 | 2014-04-04 | B | 6 | 0.0033721 | 1.8327e-05
2015 | 2014-04-06 | C | 6 | 0.0082836 | 1.8327e-05
2015 | 2014-04-06 | B | 5 | 0.0012981 | 1.5272e-05
2015 | 2014-04-07 | B | 2 | 0.00085524 | 6.1088e-06
2015 | 2014-04-07 | C | 180 | 0.0071474 | 0.0005498
2015 | 2014-04-07 | B | 5 | 0.00076361 | 1.5272e-05
2015 | 2014-04-07 | B | 35 | 0.025871 | 0.0001069
2015 | 2014-04-07 | C | 810 | 0.20103 | 0.0024741
2015 | 2014-04-03 | B | 125 | 0.047344 | 0.0003818
2015 | 2014-04-07 | C | 1 | 0.0001741 | 3.0544e-06
2015 | 2014-04-07 | C | 862 | 0.17377 | 0.0026329
2015 | 2014-04-08 | C | 705 | 0.070591 | 0.0021534
2015 | 2014-04-08 | C | 766 | 0.12957 | 0.0023397
2015 | 2014-04-07 | B | 6 | 0.0012096 | 1.8327e-05
2015 | 2014-04-08 | C | 87 | 0.026573 | 0.00026573
2015 | 2014-04-08 | C | 371 | 0.10955 | 0.0011332
2015 | 2014-04-08 | C | 232 | 0.070667 | 0.00070863
2015 | 2014-04-08 | B | 4 | 0.0032621 | 1.2218e-05
2015 | 2014-04-08 | C | 42 | 0.0024374 | 0.00012829
2015 | 2014-04-08 | C | 2 | 0.00050093 | 6.1088e-06
2015 | 2014-04-08 | C | 639 | 0.14898 | 0.0019518
2015 | 2014-04-08 | B | 35 | 0.038165 | 0.0001069
2015 | 2014-04-08 | B | 11 | 0.010987 | 3.3599e-05
2015 | 2014-04-08 | C | 2 | 0.00018937 | 6.1088e-06
2015 | 2014-04-08 | B | 104 | 0.12516 | 0.00031766
2015 | 2014-04-08 | C | 21 | 0.0076971 | 6.4143e-05
2015 | 2014-04-08 | C | 59 | 0.0084699 | 0.00018021
2015 | 2014-04-08 | C | 37 | 0.01876 | 0.00011301
2015 | 2014-04-08 | B | 8 | 0.0013928 | 2.4435e-05
2015 | 2014-04-08 | B | 3 | 0.00052231 | 9.1633e-06
2015 | 2014-04-08 | B | 6 | 0.0015944 | 1.8327e-05
2015 | 2014-04-08 | B | 7 | 0.0010049 | 2.1381e-05
2015 | 2014-04-08 | B | 57 | 0.016714 | 0.0001741
2015 | 2014-04-08 | C | 26 | 0.0050826 | 7.9415e-05
2015 | 2014-04-08 | C | 436 | 0.02508 | 0.0013317
2015 | 2014-04-08 | C | 62 | 0.0035981 | 0.00018937
2015 | 2014-04-08 | C | 4 | 0.0023214 | 1.2218e-05
2015 | 2014-04-09 | C | 1088 | 0.036555 | 0.0033232
2015 | 2014-04-09 | C | 244 | 0.054069 | 0.00074528
2015 | 2014-04-09 | B | 4 | 0.00072084 | 1.2218e-05
2015 | 2014-04-09 | B | 14 | 0.0060294 | 4.2762e-05
2015 | 2014-04-09 | C | 62 | 0.0028406 | 0.00018937
2015 | 2014-04-09 | C | 239 | 0.022642 | 0.00073001
2015 | 2014-04-09 | B | 57 | 0.062851 | 0.0001741
2015 | 2014-04-09 | C | 489 | 0.10621 | 0.0014936
2015 | 2014-04-09 | C | 1337 | 0.17139 | 0.0040838
2015 | 2014-04-09 | C | 732 | 0.18349 | 0.0022358
2015 | 2014-04-10 | C | 417 | 0.040758 | 0.0012737
2015 | 2014-04-10 | C | 823 | 0.15588 | 0.0025138
2015 | 2014-04-10 | C | 517 | 0.15002 | 0.0015791
2015 | 2014-04-09 | C | 9 | 0.0098688 | 2.749e-05
2015 | 2014-04-09 | C | 5 | 0.007239 | 1.5272e-05
2015 | 2014-04-10 | C | 115 | 0.085276 | 0.00035126
2015 | 2014-04-10 | C | 489 | 0.12535 | 0.0014936
2015 | 2014-04-10 | C | 21 | 0.01007 | 6.4143e-05
2015 | 2014-04-10 | C | 17 | 0.0079446 | 5.1925e-05
2015 | 2014-04-10 | C | 4 | 0.0009652 | 1.2218e-05
2015 | 2014-04-10 | B | 2 | 0.0006231 | 6.1088e-06
2015 | 2014-04-10 | B | 27 | 0.022844 | 8.2469e-05
2015 | 2014-04-10 | C | 239 | 0.019411 | 0.00073001
2015 | 2014-04-10 | C | 575 | 0.010538 | 0.0017563
2015 | 2014-04-10 | C | 66 | 0.0036287 | 0.00020159
2015 | 2014-04-10 | C | 240 | 0.03592 | 0.00073306
2015 | 2014-04-10 | C | 41 | 0.023919 | 0.00012523
2015 | 2014-04-10 | C | 244 | 0.10162 | 0.00074528
2015 | 2014-04-10 | C | 124 | 0.028473 | 0.00037875
2015 | 2014-04-10 | C | 280 | 0.14447 | 0.00085524
2015 | 2014-04-10 | C | 149 | 0.058807 | 0.00045511
2015 | 2014-04-10 | C | 405 | 0.4251 | 0.001237
2015 | 2014-04-11 | C | 3 | 0.00024741 | 9.1633e-06
2015 | 2014-04-11 | B | 8 | 0.0016616 | 2.4435e-05
2015 | 2014-04-10 | C | 405 | 0.11894 | 0.001237
2015 | 2014-04-11 | B | 4 | 0.00081859 | 1.2218e-05
2015 | 2014-04-08 | B | 13 | 0.0042884 | 3.9708e-05
2015 | 2014-04-11 | B | 58 | 0.00035431 | 0.00017716
2015 | 2014-04-10 | C | 76 | 0.044753 | 0.00023214
2015 | 2014-04-11 | C | 661 | 0.07874 | 0.002019
2015 | 2014-04-11 | B | 65 | 0.048046 | 0.00019854
2015 | 2014-04-11 | C | 1 | 0.0008644 | 3.0544e-06
2015 | 2014-04-10 | B | 1 | 0.00070863 | 3.0544e-06
2015 | 2014-04-10 | B | 1 | 0.00040013 | 3.0544e-06
2015 | 2014-04-11 | C | 96 | 0.017542 | 0.00029322
2015 | 2014-04-12 | B | 40 | 0.010629 | 0.00012218
2015 | 2014-04-11 | C | 20 | 0.010874 | 6.1088e-05
2015 | 2014-04-12 | C | 6 | 0.0045267 | 1.8327e-05
2015 | 2014-04-12 | C | 34 | 0.015477 | 0.00010385
2015 | 2014-04-12 | C | 1118 | 0.27434 | 0.0034148
2015 | 2014-04-13 | B | 10 | 0.011668 | 3.0544e-05
2015 | 2014-04-13 | C | 1 | 2.749e-05 | 3.0544e-06
2015 | 2014-04-12 | C | 134 | 0.014533 | 0.00040929
2015 | 2014-04-12 | C | 6 | 0.008027 | 1.8327e-05
2015 | 2014-04-12 | C | 378 | 0.071583 | 0.0011546
2015 | 2014-04-14 | C | 237 | 0.0094107 | 0.0007239
2015 | 2014-04-09 | C | 72 | 0.061577 | 0.00021992
2015 | 2014-04-12 | C | 45 | 0.020959 | 0.00013745
2015 | 2014-04-13 | C | 35 | 0.017768 | 0.0001069
2015 | 2014-04-14 | C | 2 | 0.00074528 | 6.1088e-06
2015 | 2014-04-14 | C | 221 | 0.046131 | 0.00067503
2015 | 2014-04-14 | B | 28 | 0.031216 | 8.5524e-05
2015 | 2014-04-14 | B | 4 | 0.0032988 | 1.2218e-05
2015 | 2014-04-14 | C | 113 | 0.04731 | 0.00034515
2015 | 2014-04-14 | B | 33 | 0.018849 | 0.0001008
2015 | 2014-04-14 | B | 60 | 0.030789 | 0.00018327
2015 | 2014-04-15 | C | 241 | 0.078111 | 0.00073612
2015 | 2014-04-15 | C | 34 | 0.0019732 | 0.00010385
2015 | 2014-04-15 | B | 1 | 0.00090716 | 3.0544e-06
2015 | 2014-04-15 | B | 37 | 0.040346 | 0.00011301
2015 | 2014-04-15 | B | 18 | 0.019628 | 5.498e-05
2015 | 2014-04-15 | B | 25 | 0.030544 | 7.6361e-05
2015 | 2014-04-15 | B | 32 | 0.023165 | 9.7742e-05
2015 | 2014-04-15 | B | 4 | 0.0039952 | 1.2218e-05
2015 | 2014-04-15 | C | 239 | 0.027713 | 0.00073001
2015 | 2014-04-15 | B | 21 | 0.01905 | 6.4143e-05
2015 | 2014-04-15 | B | 194 | 0.25013 | 0.00059256
2015 | 2014-04-15 | C | 1078 | 0.13185 | 0.0032927
2015 | 2014-04-15 | B | 3 | 0.005278 | 9.1633e-06
2015 | 2014-04-15 | C | 36 | 0.0034087 | 0.00010996
2015 | 2014-04-15 | C | 8 | 0.0039341 | 2.4435e-05
2015 | 2014-04-15 | C | 37 | 0.011414 | 0.00011301
2015 | 2014-04-15 | C | 70 | 0.032908 | 0.00021381
2015 | 2014-04-15 | C | 172 | 0.20331 | 0.00052536
2015 | 2014-04-15 | C | 1686 | 0.043034 | 0.0051498
2015 | 2014-04-14 | C | 2583 | 0.73481 | 0.0078896
2015 | 2014-04-14 | C | 234 | 0.047887 | 0.00071474
2015 | 2014-04-16 | B | 26 | 0.018821 | 7.9415e-05
2015 | 2014-04-16 | C | 5 | 0.00025963 | 1.5272e-05
2015 | 2014-04-16 | C | 9 | 0.0017044 | 2.749e-05
2015 | 2014-04-16 | B | 40 | 0.04545 | 0.00012218
2015 | 2014-04-16 | B | 9 | 0.011463 | 2.749e-05
2015 | 2014-04-16 | B | 67 | 0.048501 | 0.00020465
2015 | 2014-04-16 | B | 35 | 0.018922 | 0.0001069
2015 | 2014-04-16 | B | 2 | 0.0021809 | 6.1088e-06
2015 | 2014-04-16 | B | 24 | 0.018473 | 7.3306e-05
2015 | 2014-04-15 | B | 40 | 0.022114 | 0.00012218
2015 | 2014-04-16 | C | 7 | 0.0040838 | 2.1381e-05
2015 | 2014-04-16 | C | 236 | 0.052961 | 0.00072084
2015 | 2014-04-16 | C | 40 | 0.0072084 | 0.00012218
2015 | 2014-04-16 | C | 5 | 0.00033599 | 1.5272e-05
2015 | 2014-04-16 | B | 13 | 0.012945 | 3.9708e-05
2015 | 2014-04-16 | B | 28 | 0.019328 | 8.5524e-05
2015 | 2014-04-17 | C | 92 | 0.028101 | 0.00028101
2015 | 2014-04-17 | C | 114 | 0.040667 | 0.0003482
2015 | 2014-04-17 | C | 277 | 0.010999 | 0.00084608
2015 | 2014-04-17 | C | 157 | 0.067747 | 0.00047954
2015 | 2014-04-17 | C | 283 | 0.073474 | 0.0008644
2015 | 2014-04-18 | C | 183 | 0.019005 | 0.00055896
2015 | 2014-04-17 | C | 266 | 0.1494 | 0.00081248
2015 | 2014-04-17 | C | 413 | 0.55749 | 0.0012615
2015 | 2014-04-17 | C | 4 | 0.00039097 | 1.2218e-05
2015 | 2014-04-17 | C | 1159 | 0.35844 | 0.0035401
2015 | 2014-04-17 | C | 232 | 0.18034 | 0.00070863
2015 | 2014-04-17 | C | 565 | 0.42971 | 0.0017257
2015 | 2014-04-17 | C | 15 | 0.0038486 | 4.5816e-05
2015 | 2014-04-17 | C | 205 | 0.32707 | 0.00062616
2015 | 2014-04-17 | C | 137 | 0.18061 | 0.00041846
2015 | 2014-04-17 | C | 887 | 0.21251 | 0.0027093
2015 | 2014-04-17 | C | 344 | 0.064949 | 0.0010507
2015 | 2014-04-17 | C | 313 | 0.19684 | 0.00095603
2015 | 2014-04-17 | C | 106 | 0.12864 | 0.00032377
2015 | 2014-04-17 | C | 359 | 0.26545 | 0.0010965
2015 | 2014-04-17 | C | 176 | 0.087708 | 0.00053758
2015 | 2014-04-18 | C | 42 | 0.0039769 | 0.00012829
2015 | 2014-04-17 | C | 125 | 0.066409 | 0.0003818
2015 | 2014-04-17 | C | 272 | 0.13803 | 0.0008308
2015 | 2014-04-17 | C | 59 | 0.016579 | 0.00018021
2015 | 2014-04-17 | C | 1021 | 0.44061 | 0.0031186
2015 | 2014-04-17 | C | 424 | 0.23321 | 0.0012951
2015 | 2014-04-18 | C | 6 | 0.0013012 | 1.8327e-05
2015 | 2014-04-17 | C | 1422 | 0.44303 | 0.0043434
2015 | 2014-04-17 | C | 885 | 0.23247 | 0.0027032
2015 | 2014-04-18 | C | 50 | 0.0072848 | 0.00015272
2015 | 2014-04-17 | C | 693 | 0.35159 | 0.0021167
2015 | 2014-04-17 | C | 1882 | 0.20597 | 0.0057484
2015 | 2014-04-17 | C | 110 | 0.012767 | 0.00033599
2015 | 2014-04-17 | C | 1 | 0.00010996 | 3.0544e-06
2015 | 2014-04-17 | C | 84 | 0.12291 | 0.00025657
2015 | 2014-04-17 | C | 235 | 0.23344 | 0.00071779
2015 | 2014-04-17 | C | 1445 | 0.17775 | 0.0044136
2015 | 2014-04-17 | C | 12 | 0.04578 | 3.6653e-05
2015 | 2014-04-17 | C | 10 | 0.037142 | 3.0544e-05
2015 | 2014-04-18 | C | 118 | 0.12946 | 0.00036042
2015 | 2014-04-18 | C | 116 | 0.01311 | 0.00035431
2015 | 2014-04-17 | C | 216 | 0.043562 | 0.00065976
2015 | 2014-04-17 | C | 326 | 0.13406 | 0.00099574
2015 | 2014-04-17 | C | 412 | 0.091825 | 0.0012584
2015 | 2014-04-19 | C | 43 | 0.0047282 | 0.00013134
2015 | 2014-04-19 | C | 9 | 0.0032163 | 2.749e-05
2015 | 2014-04-17 | C | 76 | 0.022517 | 0.00023214
2015 | 2014-04-19 | C | 4 | 0.00074528 | 1.2218e-05
2015 | 2014-04-19 | C | 126 | 0.0046183 | 0.00038486
2015 | 2014-04-19 | C | 3 | 0.010144 | 9.1633e-06
2015 | 2014-04-19 | C | 245 | 0.12187 | 0.00074833
2015 | 2014-04-19 | C | 5 | 0.0039555 | 1.5272e-05
2015 | 2014-04-19 | C | 6 | 0.0011912 | 1.8327e-05
2015 | 2014-04-19 | C | 3 | 0.00054063 | 9.1633e-06
2015 | 2014-04-17 | C | 2 | 0.008137 | 6.1088e-06
2015 | 2014-04-19 | C | 492 | 0.34508 | 0.0015028
2015 | 2014-04-19 | C | 581 | 0.17844 | 0.0017746
2015 | 2014-04-19 | C | 253 | 0.018546 | 0.00077277
2015 | 2014-04-19 | C | 44 | 0.081712 | 0.00013439
2015 | 2014-04-19 | C | 65 | 0.061812 | 0.00019854
2015 | 2014-04-19 | C | 424 | 0.049311 | 0.0012951
2015 | 2014-04-19 | C | 247 | 0.14758 | 0.00075444
2015 | 2014-04-18 | C | 4 | 0.0013562 | 1.2218e-05
2015 | 2014-04-20 | C | 2 | 0.00028712 | 6.1088e-06
2015 | 2014-04-20 | C | 359 | 0.06031 | 0.0010965
2015 | 2014-04-19 | C | 4 | 0.0021625 | 1.2218e-05
2015 | 2014-04-20 | C | 73 | 0.011372 | 0.00022297
2015 | 2014-04-20 | C | 13 | 0.00087357 | 3.9708e-05
2015 | 2014-04-20 | C | 783 | 0.23185 | 0.0023916
2015 | 2014-04-19 | C | 109 | 0.29996 | 0.00033293
2015 | 2014-04-17 | C | 7 | 0.0047466 | 2.1381e-05
2015 | 2014-04-21 | C | 62 | 0.011741 | 0.00018937
2015 | 2014-04-21 | C | 44 | 0.0018815 | 0.00013439
2015 | 2014-04-20 | C | 1260 | 0.10044 | 0.0038486
2015 | 2014-04-18 | C | 8 | 0.0142 | 2.4435e-05
2015 | 2014-04-21 | C | 337 | 0.01544 | 0.0010293
2015 | 2014-04-17 | B | 14 | 0.005388 | 4.2762e-05
2015 | 2014-04-17 | C | 425 | 0.5206 | 0.0012981
2015 | 2014-04-17 | C | 295 | 0.005049 | 0.00090105
2015 | 2014-04-17 | C | 1094 | 0.24456 | 0.0033415
2015 | 2014-04-17 | C | 471 | 0.1743 | 0.0014386
2015 | 2014-04-17 | C | 490 | 0.13103 | 0.0014967
2015 | 2014-04-17 | C | 303 | 0.25646 | 0.00092549
2015 | 2014-04-17 | C | 711 | 0.41408 | 0.0021717
2015 | 2014-04-17 | C | 45 | 0.0050123 | 0.00013745
2015 | 2014-04-17 | C | 94 | 0.16857 | 0.00028712
2015 | 2014-04-17 | C | 1 | 0.00044289 | 3.0544e-06
2015 | 2014-04-17 | C | 213 | 0.3731 | 0.00065059
2015 | 2014-04-17 | C | 205 | 0.041733 | 0.00062616
2015 | 2014-04-17 | C | 1031 | 0.090811 | 0.0031491
2015 | 2014-04-17 | C | 281 | 0.012358 | 0.00085829
2015 | 2014-04-17 | C | 536 | 0.27718 | 0.0016372
2015 | 2014-04-17 | C | 3 | 0.00032071 | 9.1633e-06
2015 | 2014-04-17 | C | 37 | 0.0075719 | 0.00011301
2015 | 2014-04-17 | C | 413 | 0.46188 | 0.0012615
2015 | 2014-04-17 | C | 2602 | 2.1944 | 0.0079476
2015 | 2014-04-17 | C | 134 | 0.044411 | 0.00040929
2015 | 2014-04-17 | C | 1083 | 0.12065 | 0.0033079
2015 | 2014-04-17 | C | 269 | 0.11386 | 0.00082164
2015 | 2014-04-22 | C | 2 | 0.00045205 | 6.1088e-06
2015 | 2014-04-17 | C | 344 | 0.36579 | 0.0010507
2015 | 2014-04-17 | C | 35 | 0.0054521 | 0.0001069
2015 | 2014-04-17 | C | 69 | 0.19297 | 0.00021076
2015 | 2014-04-22 | C | 1 | 0.00031461 | 3.0544e-06
2015 | 2014-04-17 | C | 289 | 0.32305 | 0.00088273
2015 | 2014-04-17 | C | 5 | 0.00068725 | 1.5272e-05
2015 | 2014-04-19 | C | 213 | 0.12911 | 0.00065059
2015 | 2014-04-17 | C | 38 | 0.019383 | 0.00011607
2015 | 2014-04-17 | C | 1090 | 1.0166 | 0.0033293
2015 | 2014-04-17 | C | 35 | 0.07911 | 0.0001069
2015 | 2014-04-17 | C | 673 | 2.7027 | 0.0020556
2015 | 2014-04-17 | C | 147 | 0.021879 | 0.000449
2015 | 2014-04-17 | C | 257 | 0.064451 | 0.00078499
2015 | 2014-04-22 | B | 31 | 0.025281 | 9.4687e-05
2015 | 2014-04-17 | B | 9 | 0.0040135 | 2.749e-05
2015 | 2014-04-22 | B | 3 | 0.0024649 | 9.1633e-06
2015 | 2014-04-22 | C | 55 | 0.0023519 | 0.00016799
2015 | 2014-04-22 | C | 227 | 0.053126 | 0.00069335
2015 | 2014-04-17 | C | 5 | 0.01179 | 1.5272e-05
2015 | 2014-04-17 | C | 294 | 0.10197 | 0.000898
2015 | 2014-04-17 | C | 176 | 0.25409 | 0.00053758
2015 | 2014-04-17 | C | 22 | 0.004099 | 6.7197e-05
2015 | 2014-04-18 | C | 492 | 0.31301 | 0.0015028
2015 | 2014-04-17 | C | 182 | 0.31884 | 0.00055591
2015 | 2014-04-18 | C | 10 | 0.0029628 | 3.0544e-05
2015 | 2014-04-18 | C | 25 | 0.010461 | 7.6361e-05
2015 | 2014-04-18 | C | 35 | 0.012615 | 0.0001069
2015 | 2014-04-18 | C | 625 | 0.17573 | 0.001909
2015 | 2014-04-18 | C | 23 | 0.0073062 | 7.0252e-05
2015 | 2014-04-18 | C | 3 | 0.0021625 | 9.1633e-06
2015 | 2014-04-18 | C | 160 | 0.016127 | 0.00048871
2015 | 2014-04-18 | C | 19 | 0.0048749 | 5.8034e-05
2015 | 2014-04-17 | C | 53 | 0.2455 | 0.00016188
2015 | 2014-04-18 | C | 66 | 0.063996 | 0.00020159
2015 | 2014-04-17 | C | 385 | 0.6231 | 0.001176
2015 | 2014-04-18 | C | 3 | 0.00045816 | 9.1633e-06
2015 | 2014-04-18 | C | 3 | 0.0003482 | 9.1633e-06
2015 | 2014-04-17 | C | 27 | 0.003702 | 8.2469e-05
2015 | 2014-04-18 | C | 1 | 0.0006231 | 3.0544e-06
2015 | 2014-04-18 | C | 1 | 0.00019548 | 3.0544e-06
2015 | 2014-04-18 | C | 7 | 0.00029933 | 2.1381e-05
2015 | 2014-04-18 | C | 25 | 0.0020617 | 7.6361e-05
2015 | 2014-04-18 | C | 110 | 0.050398 | 0.00033599
2015 | 2014-04-17 | C | 96 | 0.53312 | 0.00029322
2015 | 2014-04-18 | C | 39 | 0.0050031 | 0.00011912
2015 | 2014-04-17 | C | 308 | 0.10295 | 0.00094076
2015 | 2014-04-18 | C | 295 | 0.077414 | 0.00090105
2015 | 2014-04-23 | C | 121 | 0.036959 | 0.00036959
2015 | 2014-04-16 | C | 3 | 0.00070557 | 9.1633e-06
2015 | 2014-04-23 | B | 46 | 0.051143 | 0.0001405
2015 | 2014-04-23 | C | 80 | 0.028021 | 0.00024435
2015 | 2014-04-23 | C | 5 | 0.0023366 | 1.5272e-05
2015 | 2014-04-23 | C | 546 | 0.1854 | 0.0016677
2015 | 2014-04-22 | B | 19 | 0.0025535 | 5.8034e-05
2015 | 2014-04-23 | B | 2 | 0.0021686 | 6.1088e-06
2015 | 2014-04-23 | C | 1 | 0.0001069 | 3.0544e-06
2015 | 2014-04-17 | C | 44 | 0.048516 | 0.00013439
2015 | 2014-04-23 | C | 41 | 0.0030056 | 0.00012523
2015 | 2014-04-23 | B | 8 | 0.0083569 | 2.4435e-05
2015 | 2014-04-23 | B | 8 | 0.012755 | 2.4435e-05
2015 | 2014-04-18 | C | 123 | 0.00075139 | 0.00037569
2015 | 2014-04-17 | C | 434 | 0.44849 | 0.0013256
2015 | 2014-04-17 | B | 24 | 0.011876 | 7.3306e-05
2015 | 2014-04-18 | C | 595 | 0.021809 | 0.0018174
2015 | 2014-04-24 | B | 1 | 0.00046122 | 3.0544e-06
2015 | 2014-04-24 | B | 4 | 0.0019182 | 1.2218e-05
2015 | 2014-04-24 | B | 25 | 0.026879 | 7.6361e-05
2015 | 2014-04-24 | C | 3 | 0.0018052 | 9.1633e-06
2015 | 2014-04-24 | B | 13 | 0.014851 | 3.9708e-05
2015 | 2014-04-24 | C | 36 | 0.0028589 | 0.00010996
2015 | 2014-04-24 | C | 1035 | 0.17498 | 0.0031613
2015 | 2014-04-25 | C | 62 | 0.012688 | 0.00018937
2015 | 2014-04-25 | C | 343 | 0.051323 | 0.0010477
2015 | 2014-04-25 | C | 32 | 0.028076 | 9.7742e-05
2015 | 2014-04-26 | C | 182 | 0.11758 | 0.00055591
2015 | 2014-04-17 | C | 95 | 0.22495 | 0.00029017
2015 | 2014-04-26 | C | 88 | 0.045001 | 0.00026879
2015 | 2014-04-26 | C | 223 | 0.057179 | 0.00068114
2015 | 2014-04-27 | C | 30 | 0.0024741 | 9.1633e-05
2015 | 2014-04-27 | B | 110 | 0.015791 | 0.00033599
2015 | 2014-04-27 | C | 4 | 0.0015516 | 1.2218e-05
2015 | 2014-04-28 | C | 259 | 0.032126 | 0.0007911
2015 | 2014-04-28 | B | 186 | 0.021231 | 0.00056812
2015 | 2014-04-28 | B | 75 | 0.039631 | 0.00022908
2015 | 2014-04-28 | C | 4 | 0.00051314 | 1.2218e-05
2015 | 2014-04-28 | B | 69 | 0.071446 | 0.00021076
2015 | 2014-04-28 | C | 7 | 0.00062005 | 2.1381e-05
2015 | 2014-04-28 | B | 35 | 0.039234 | 0.0001069
2015 | 2014-04-28 | C | 4 | 0.0008308 | 1.2218e-05
2015 | 2014-04-28 | C | 57 | 0.049857 | 0.0001741
2015 | 2014-04-28 | C | 2246 | 1.1871 | 0.0068602
2015 | 2014-04-29 | C | 27 | 0.0018143 | 8.2469e-05
2015 | 2014-04-29 | B | 19 | 0.016075 | 5.8034e-05
2015 | 2014-04-11 | B | 2 | 0.0015089 | 6.1088e-06
2015 | 2014-04-29 | B | 46 | 0.035407 | 0.0001405
2015 | 2014-04-29 | B | 100 | 0.013745 | 0.00030544
2015 | 2014-04-29 | C | 4 | 0.001515 | 1.2218e-05
2015 | 2014-04-29 | B | 65 | 0.067106 | 0.00019854
2015 | 2014-04-29 | B | 41 | 0.043581 | 0.00012523
2015 | 2014-04-29 | C | 149 | 0.029594 | 0.00045511
2015 | 2014-04-29 | C | 7 | 0.0020526 | 2.1381e-05
2015 | 2014-04-29 | C | 9 | 0.0016769 | 2.749e-05
2015 | 2014-04-29 | C | 50 | 0.032218 | 0.00015272
2015 | 2014-04-28 | C | 1090 | 0.36226 | 0.0033293
2015 | 2014-04-30 | C | 985 | 0.12335 | 0.0030086
2015 | 2014-04-30 | B | 2 | 0.00059256 | 6.1088e-06
2015 | 2014-04-30 | B | 52 | 0.051143 | 0.00015883
2015 | 2014-04-30 | B | 46 | 0.038357 | 0.0001405
2015 | 2014-04-30 | B | 3 | 0.0039952 | 9.1633e-06
2015 | 2014-04-29 | C | 3 | 0.0032438 | 9.1633e-06
2015 | 2014-05-01 | B | 12 | 0.0075872 | 3.6653e-05
2015 | 2014-05-01 | B | 4 | 0.0050948 | 1.2218e-05
2015 | 2014-05-01 | C | 21 | 0.00076971 | 6.4143e-05
2015 | 2014-05-01 | C | 118 | 0.03957 | 0.00036042
2015 | 2014-05-02 | B | 13 | 0.0023825 | 3.9708e-05
2015 | 2014-05-01 | B | 114 | 0.09123 | 0.0003482
2015 | 2014-05-02 | B | 3 | 0.00088884 | 9.1633e-06
2015 | 2014-05-02 | C | 229 | 0.023782 | 0.00069946
2015 | 2014-05-02 | B | 21 | 0.021937 | 6.4143e-05
2015 | 2014-05-02 | C | 1993 | 0.04585 | 0.0060875
2015 | 2014-05-02 | B | 7 | 0.002074 | 2.1381e-05
2015 | 2014-05-03 | B | 7 | 0.0027154 | 2.1381e-05
2015 | 2014-05-03 | C | 4 | 0.00032988 | 1.2218e-05
2015 | 2014-05-03 | C | 801 | 0.38181 | 0.0024466
2015 | 2014-05-04 | C | 412 | 0.075264 | 0.0012584
2015 | 2014-05-05 | B | 41 | 0.037319 | 0.00012523
2015 | 2014-05-05 | C | 1 | 9.4687e-05 | 3.0544e-06
2015 | 2014-05-05 | C | 210 | 0.056815 | 0.00064143
2015 | 2014-05-05 | B | 49 | 0.0449 | 0.00014967
2015 | 2014-05-05 | B | 8 | 0.0046916 | 2.4435e-05
2015 | 2014-05-05 | B | 2 | 0.00094076 | 6.1088e-06
2015 | 2014-05-05 | C | 154 | 0.058514 | 0.00047038
2015 | 2014-05-05 | C | 23 | 0.026766 | 7.0252e-05
2015 | 2014-05-05 | C | 207 | 0.09469 | 0.00063227
2015 | 2014-05-05 | C | 1 | 0.00014967 | 3.0544e-06
2015 | 2014-05-05 | B | 1 | 0.00055591 | 3.0544e-06
2015 | 2014-05-05 | C | 1096 | 0.17066 | 0.0033476
2015 | 2014-05-06 | C | 32 | 0.0022481 | 9.7742e-05
2015 | 2014-05-06 | B | 54 | 0.037936 | 0.00016494
2015 | 2014-05-06 | C | 18 | 0.0035737 | 5.498e-05
2015 | 2014-05-06 | B | 80 | 0.06231 | 0.00024435
2015 | 2014-05-06 | B | 6 | 0.0044717 | 1.8327e-05
2015 | 2014-05-06 | B | 8 | 0.0038364 | 2.4435e-05
2015 | 2014-05-06 | C | 26 | 0.0088151 | 7.9415e-05
2015 | 2014-05-06 | B | 12 | 0.014441 | 3.6653e-05
2015 | 2014-05-06 | B | 13 | 0.013183 | 3.9708e-05
2015 | 2014-05-06 | C | 336 | 0.06363 | 0.0010263
2015 | 2014-05-06 | C | 128 | 0.047221 | 0.00039097
2015 | 2014-05-06 | C | 65 | 0.058171 | 0.00019854
2015 | 2014-05-06 | C | 6 | 0.006176 | 1.8327e-05
2015 | 2014-05-06 | C | 80 | 0.031852 | 0.00024435
2015 | 2014-05-06 | C | 287 | 0.088539 | 0.00087662
2015 | 2014-05-06 | C | 783 | 0.12197 | 0.0023916
2015 | 2014-05-06 | C | 250 | 0.063673 | 0.00076361
2015 | 2014-05-06 | C | 272 | 0.042371 | 0.0008308
2015 | 2014-05-07 | C | 3 | 0.00015578 | 9.1633e-06
2015 | 2014-05-07 | B | 163 | 0.032362 | 0.00049787
2015 | 2014-05-07 | C | 2 | 0.0008308 | 6.1088e-06
2015 | 2014-05-07 | B | 75 | 0.088196 | 0.00022908
2015 | 2014-05-07 | B | 77 | 0.067265 | 0.00023519
2015 | 2014-05-07 | C | 783 | 0.10918 | 0.0023916
2015 | 2014-05-07 | C | 27 | 0.015504 | 8.2469e-05
2015 | 2014-05-08 | B | 13 | 0.011912 | 3.9708e-05
2015 | 2014-05-07 | B | 350 | 0.12092 | 0.001069
2015 | 2014-05-09 | C | 2176 | 0.06341 | 0.0066464
2015 | 2014-05-09 | C | 154 | 0.06209 | 0.00047038
2015 | 2014-05-09 | B | 4 | 0.0017349 | 1.2218e-05
2015 | 2014-05-09 | C | 2 | 0.00052536 | 6.1088e-06
2015 | 2014-05-08 | B | 26 | 0.024142 | 7.9415e-05
2015 | 2014-05-08 | B | 35 | 0.024481 | 0.0001069
2015 | 2014-05-09 | C | 122 | 0.0089434 | 0.00037264
2015 | 2014-05-09 | C | 3 | 0.0019151 | 9.1633e-06
2015 | 2014-05-09 | C | 1 | 0.00031155 | 3.0544e-06
2015 | 2014-05-10 | C | 301 | 0.011033 | 0.00091938
2015 | 2014-05-09 | C | 6 | 0.0045267 | 1.8327e-05
2015 | 2014-05-07 | C | 65 | 0.047399 | 0.00019854
2015 | 2014-05-10 | B | 2 | 0.0010813 | 6.1088e-06
2015 | 2014-05-10 | C | 39 | 0.0045267 | 0.00011912
2015 | 2014-05-10 | C | 632 | 0.28005 | 0.0019304
2015 | 2014-05-10 | C | 3 | 0.0011729 | 9.1633e-06
2015 | 2014-05-10 | C | 7 | 0.0034851 | 2.1381e-05
2015 | 2014-05-11 | B | 8 | 0.0046916 | 2.4435e-05
2015 | 2014-05-11 | C | 5 | 0.0003482 | 1.5272e-05
2015 | 2014-05-11 | C | 26 | 0.0030972 | 7.9415e-05
2015 | 2014-05-11 | B | 1 | 0.00012523 | 3.0544e-06
2015 | 2014-05-09 | B | 15 | 0.0059103 | 4.5816e-05
2015 | 2014-05-02 | C | 1183 | 0.028907 | 0.0036134
2015 | 2014-05-12 | C | 105 | 0.025306 | 0.00032071
2015 | 2014-05-12 | C | 11 | 0.0023183 | 3.3599e-05
2015 | 2014-05-12 | B | 553 | 0.31586 | 0.0016891
2015 | 2014-05-13 | C | 857 | 0.13083 | 0.0026176
2015 | 2014-05-13 | C | 118 | 0.041384 | 0.00036042
2015 | 2014-05-12 | B | 28 | 0.023006 | 8.5524e-05
2015 | 2014-05-13 | B | 1 | 0.00028712 | 3.0544e-06
2015 | 2014-05-13 | B | 69 | 0.03056 | 0.00021076
2015 | 2014-05-13 | C | 5 | 0.003314 | 1.5272e-05
2015 | 2014-05-13 | B | 35 | 0.030682 | 0.0001069
2015 | 2014-05-13 | B | 23 | 0.026977 | 7.0252e-05
2015 | 2014-05-13 | B | 30 | 0.029231 | 9.1633e-05
2015 | 2014-05-13 | B | 2 | 3.6653e-05 | 6.1088e-06
2015 | 2014-05-13 | C | 58 | 0.0069091 | 0.00017716
2015 | 2014-05-13 | C | 822 | 0.26112 | 0.0025107
2015 | 2014-05-13 | C | 514 | 0.2471 | 0.00157
2015 | 2014-05-14 | C | 1 | 0.00027184 | 3.0544e-06
2015 | 2014-05-13 | B | 26 | 0.019616 | 7.9415e-05
2015 | 2014-05-14 | C | 2 | 0.00076971 | 6.1088e-06
2015 | 2014-05-14 | B | 80 | 0.093832 | 0.00024435
2015 | 2014-05-14 | B | 130 | 0.14811 | 0.00039708
2015 | 2014-05-14 | B | 343 | 0.17902 | 0.0010477
2015 | 2014-05-14 | C | 96 | 0.018473 | 0.00029322
2015 | 2014-05-15 | B | 2 | 0.0011729 | 6.1088e-06
2015 | 2014-05-15 | C | 2 | 0.0013867 | 6.1088e-06
2015 | 2014-05-15 | B | 40 | 0.035309 | 0.00012218
2015 | 2014-05-15 | B | 4 | 0.0042518 | 1.2218e-05
2015 | 2014-05-14 | C | 106 | 0.29391 | 0.00032377
2015 | 2014-05-15 | B | 61 | 0.087011 | 0.00018632
2015 | 2014-05-15 | C | 59 | 0.021668 | 0.00018021
2015 | 2014-05-16 | C | 4 | 0.00090411 | 1.2218e-05
2015 | 2014-05-16 | C | 139 | 0.083224 | 0.00042456
2015 | 2014-05-16 | B | 1 | 0.00043984 | 3.0544e-06
2015 | 2014-05-15 | B | 55 | 0.055606 | 0.00016799
2015 | 2014-05-09 | B | 1 | 0.00098047 | 3.0544e-06
2015 | 2014-05-17 | C | 1446 | 0.11483 | 0.0044167
2015 | 2014-05-17 | C | 999 | 0.24852 | 0.0030514
2015 | 2014-05-17 | C | 2 | 0.00035431 | 6.1088e-06
2015 | 2014-05-18 | B | 22 | 0.0083325 | 6.7197e-05
2015 | 2014-05-16 | C | 427 | 0.11526 | 0.0013042
2015 | 2014-05-19 | B | 9 | 0.00074222 | 2.749e-05
2015 | 2014-05-19 | B | 6 | 0.0021442 | 1.8327e-05
2015 | 2014-05-19 | C | 6249 | 0.57261 | 0.019087
2015 | 2014-05-19 | C | 1 | 0.0010996 | 3.0544e-06
2015 | 2014-05-19 | C | 2193 | 0.11518 | 0.0066984
2015 | 2014-05-19 | B | 3 | 0.0019609 | 9.1633e-06
2015 | 2014-05-19 | B | 1 | 0.0011271 | 3.0544e-06
2015 | 2014-05-20 | B | 5 | 0.0013287 | 1.5272e-05
2015 | 2014-05-20 | B | 7 | 0.0018815 | 2.1381e-05
2015 | 2014-05-20 | B | 7 | 0.00025657 | 2.1381e-05
2015 | 2014-05-20 | C | 2387 | 0.53204 | 0.0072909
2015 | 2014-05-20 | C | 632 | 0.03168 | 0.0019304
2015 | 2014-05-20 | C | 3 | 0.00025657 | 9.1633e-06
2015 | 2014-05-20 | B | 114 | 0.093319 | 0.0003482
2015 | 2014-05-20 | B | 5 | 0.0032682 | 1.5272e-05
2015 | 2014-05-20 | B | 20 | 0.0051925 | 6.1088e-05
2015 | 2014-05-20 | C | 93 | 0.018556 | 0.00028406
2015 | 2014-05-20 | C | 41 | 0.017212 | 0.00012523
2015 | 2014-04-30 | C | 2 | 4.2762e-05 | 6.1088e-06
2015 | 2014-05-21 | B | 4 | 0.0031277 | 1.2218e-05
2015 | 2014-05-21 | B | 199 | 0.19876 | 0.00060783
2015 | 2014-05-21 | B | 4 | 0.0042884 | 1.2218e-05
2015 | 2014-05-20 | B | 31 | 0.031436 | 9.4687e-05
2015 | 2014-05-21 | B | 1 | 0.00096825 | 3.0544e-06
2015 | 2014-05-21 | C | 109 | 0.026225 | 0.00033293
2015 | 2014-05-21 | C | 52 | 0.015058 | 0.00015883
2015 | 2014-04-09 | B | 69 | 0.063648 | 0.00021076
2015 | 2014-05-22 | B | 35 | 0.0058798 | 0.0001069
2015 | 2014-05-22 | C | 259 | 0.043697 | 0.0007911
2015 | 2014-05-22 | B | 553 | 0.19931 | 0.0016891
2015 | 2014-05-22 | B | 25 | 0.021992 | 7.6361e-05
2015 | 2014-05-22 | B | 25 | 0.016418 | 7.6361e-05
2015 | 2014-05-23 | C | 2 | 0.0012157 | 6.1088e-06
2015 | 2014-05-23 | B | 187 | 0.10852 | 0.00057118
2015 | 2014-05-23 | C | 1091 | 0.036656 | 0.0033324
2015 | 2014-05-23 | C | 2606 | 0.49351 | 0.0079598
2015 | 2014-05-23 | C | 815 | 0.069684 | 0.0024894
2015 | 2014-05-23 | C | 339 | 0.044118 | 0.0010354
2015 | 2014-05-23 | C | 20 | 0.0038486 | 6.1088e-05
2015 | 2014-05-23 | B | 1 | 0.0001741 | 3.0544e-06
2015 | 2014-05-23 | B | 8 | 0.00090411 | 2.4435e-05
2015 | 2014-05-23 | B | 3 | 0.00024741 | 9.1633e-06
2015 | 2014-05-23 | B | 3 | 0.00024741 | 9.1633e-06
2015 | 2014-05-21 | B | 8 | 0.0016372 | 2.4435e-05
2015 | 2014-05-22 | B | 7 | 0.0018601 | 2.1381e-05
2015 | 2014-05-22 | B | 196 | 0.22211 | 0.00059867
2015 | 2014-05-23 | C | 165 | 0.044695 | 0.00050398
2015 | 2014-05-23 | C | 207 | 0.09319 | 0.00063227
2015 | 2014-05-23 | C | 267 | 0.095726 | 0.00081553
2015 | 2014-05-24 | C | 134 | 0.058529 | 0.00040929
2015 | 2014-05-24 | C | 188 | 0.045767 | 0.00057423
2015 | 2014-05-24 | C | 478 | 0.95493 | 0.00146
2015 | 2014-05-24 | C | 23 | 0.0052689 | 7.0252e-05
2015 | 2014-05-24 | C | 86 | 0.0096825 | 0.00026268
2015 | 2014-05-24 | C | 108 | 0.023672 | 0.00032988
2015 | 2014-05-24 | C | 297 | 0.82044 | 0.00090716
2015 | 2014-05-24 | C | 1446 | 0.91453 | 0.0044167
2015 | 2014-05-24 | C | 291 | 0.034827 | 0.00088884
2015 | 2014-05-24 | C | 1120 | 0.61616 | 0.003421
2015 | 2014-05-24 | C | 65 | 0.038779 | 0.00019854
2015 | 2014-05-24 | C | 769 | 0.21745 | 0.0023489
2015 | 2014-05-24 | C | 10 | 0.0018327 | 3.0544e-05
2015 | 2014-05-24 | C | 13 | 0.0040899 | 3.9708e-05
2015 | 2014-05-24 | C | 37 | 0.040459 | 0.00011301
2015 | 2014-05-23 | C | 195 | 0.080997 | 0.00059561
2015 | 2014-05-25 | B | 4 | 0.004435 | 1.2218e-05
2015 | 2014-05-25 | C | 62 | 0.00606 | 0.00018937
2015 | 2014-05-23 | C | 291 | 0.049729 | 0.00088884
2015 | 2014-05-23 | C | 893 | 0.19357 | 0.0027276
2015 | 2014-05-23 | C | 436 | 0.12853 | 0.0013317
2015 | 2014-05-24 | C | 705 | 0.22575 | 0.0021534
2015 | 2014-05-24 | C | 65 | 0.030972 | 0.00019854
2015 | 2014-05-24 | C | 1019 | 0.18641 | 0.0031125
2015 | 2014-05-24 | C | 1064 | 0.17896 | 0.0032499
2015 | 2014-05-24 | C | 59 | 0.16796 | 0.00018021
2015 | 2014-05-24 | C | 232 | 0.98888 | 0.00070863
2015 | 2014-05-25 | C | 24 | 0.009823 | 7.3306e-05
2015 | 2014-05-24 | C | 89 | 0.20857 | 0.00027184
2015 | 2014-05-24 | C | 6 | 0.018382 | 1.8327e-05
2015 | 2014-05-24 | C | 50 | 0.13118 | 0.00015272
2015 | 2014-05-26 | C | 61 | 0.009316 | 0.00018632
2015 | 2014-05-25 | C | 353 | 0.41947 | 0.0010782
2015 | 2014-05-24 | C | 45 | 0.21521 | 0.00013745
2015 | 2014-05-26 | C | 1394 | 0.018287 | 0.0042579
2015 | 2014-05-25 | C | 6 | 0.0011362 | 1.8327e-05
2015 | 2014-05-25 | C | 26 | 0.0072329 | 7.9415e-05
2015 | 2014-05-24 | C | 9 | 0.031503 | 2.749e-05
2015 | 2014-05-26 | C | 299 | 0.13765 | 0.00091327
2015 | 2014-05-25 | C | 222 | 0.014918 | 0.00067808
2015 | 2014-05-25 | C | 40 | 0.015516 | 0.00012218
2015 | 2014-05-24 | C | 66 | 0.13541 | 0.00020159
2015 | 2014-05-24 | C | 230 | 0.64491 | 0.00070252
2015 | 2014-05-26 | B | 9 | 0.001292 | 2.749e-05
2015 | 2014-05-25 | C | 9 | 0.0040135 | 2.749e-05
2015 | 2014-05-24 | C | 86 | 0.057503 | 0.00026268
2015 | 2014-05-26 | C | 32 | 0.0087967 | 9.7742e-05
2015 | 2014-05-26 | B | 10 | 0.010202 | 3.0544e-05
2015 | 2014-05-24 | C | 108 | 0.32295 | 0.00032988
2015 | 2014-05-25 | C | 24 | 0.0043251 | 7.3306e-05
2015 | 2014-05-26 | B | 30 | 0.03088 | 9.1633e-05
2015 | 2014-05-24 | C | 128 | 0.1404 | 0.00039097
2015 | 2014-05-25 | C | 23 | 0.025501 | 7.0252e-05
2015 | 2014-05-24 | C | 113 | 0.46473 | 0.00034515
2015 | 2014-05-25 | C | 1 | 0.00024435 | 3.0544e-06
2015 | 2014-05-24 | C | 462 | 0.58711 | 0.0014111
2015 | 2014-05-25 | C | 9 | 0.00068725 | 2.749e-05
2015 | 2014-05-25 | C | 251 | 0.0046 | 0.00076666
2015 | 2014-05-24 | C | 62 | 0.26307 | 0.00018937
2015 | 2014-05-25 | C | 353 | 0.28249 | 0.0010782
2015 | 2014-05-25 | C | 95 | 0.033996 | 0.00029017
2015 | 2014-05-25 | C | 678 | 0.12871 | 0.0020709
2015 | 2014-05-26 | C | 2 | 0.00052536 | 6.1088e-06
2015 | 2014-05-25 | C | 92 | 0.088798 | 0.00028101
2015 | 2014-05-27 | B | 1 | 6.1088e-06 | 3.0544e-06
2015 | 2014-05-26 | C | 9 | 0.010089 | 2.749e-05
2015 | 2014-05-25 | C | 261 | 0.64277 | 0.0007972
2015 | 2014-05-25 | C | 256 | 0.41068 | 0.00078193
2015 | 2014-05-25 | C | 1445 | 0.46699 | 0.0044136
2015 | 2014-05-24 | C | 77 | 0.20672 | 0.00023519
2015 | 2014-05-25 | C | 104 | 0.30885 | 0.00031766
2015 | 2014-05-25 | C | 4 | 0.015773 | 1.2218e-05
2015 | 2014-05-26 | C | 152 | 0.010214 | 0.00046427
2015 | 2014-05-27 | B | 210 | 0.0025657 | 0.00064143
2015 | 2014-05-27 | B | 30 | 0.027948 | 9.1633e-05
2015 | 2014-05-27 | B | 101 | 0.045658 | 0.0003085
2015 | 2014-05-26 | B | 43 | 0.013003 | 0.00013134
2015 | 2014-05-27 | C | 1 | 2.1381e-05 | 3.0544e-06
2015 | 2014-05-14 | B | 38 | 0.014973 | 0.00011607
2015 | 2014-05-21 | B | 257 | 0.15734 | 0.00078499
2015 | 2014-05-24 | C | 134 | 0.01719 | 0.00040929
2015 | 2014-05-25 | C | 1 | 0.00078804 | 3.0544e-06
2015 | 2014-05-26 | C | 20 | 0.002749 | 6.1088e-05
2015 | 2014-05-26 | C | 175 | 0.091401 | 0.00053452
2015 | 2014-05-25 | C | 113 | 0.44865 | 0.00034515
2015 | 2014-05-28 | C | 949 | 0.10312 | 0.0028986
2015 | 2014-05-25 | C | 17 | 0.0089036 | 5.1925e-05
2015 | 2014-05-26 | C | 50 | 0.013837 | 0.00015272
2015 | 2014-05-28 | B | 1 | 0.00054063 | 3.0544e-06
2015 | 2014-05-26 | C | 47 | 0.0081828 | 0.00014356
2015 | 2014-05-26 | C | 172 | 0.045706 | 0.00052536
2015 | 2014-05-26 | C | 251 | 0.042933 | 0.00076666
2015 | 2014-05-25 | C | 7 | 0.024588 | 2.1381e-05
2015 | 2014-05-25 | C | 632 | 2.2166 | 0.0019304
2015 | 2014-05-26 | C | 3 | 0.0060203 | 9.1633e-06
2015 | 2014-05-28 | C | 1732 | 0.015385 | 0.0052903
2015 | 2014-05-26 | C | 353 | 0.3401 | 0.0010782
2015 | 2014-05-25 | C | 80 | 0.30921 | 0.00024435
2015 | 2014-05-25 | C | 181 | 0.061324 | 0.00055285
2015 | 2014-05-26 | C | 14 | 0.0068969 | 4.2762e-05
2015 | 2014-05-25 | C | 4 | 0.032462 | 1.2218e-05
2015 | 2014-05-24 | C | 26 | 0.0067136 | 7.9415e-05
2015 | 2014-05-27 | C | 21 | 0.0084027 | 6.4143e-05
2015 | 2014-05-25 | C | 55 | 0.17876 | 0.00016799
2015 | 2014-05-25 | C | 133 | 0.028843 | 0.00040624
2015 | 2014-05-26 | C | 92 | 0.23801 | 0.00028101
2015 | 2014-05-27 | C | 9 | 0.0033263 | 2.749e-05
2015 | 2014-05-26 | C | 4 | 0.011326 | 1.2218e-05
2015 | 2014-05-25 | C | 226 | 0.22539 | 0.0006903
2015 | 2014-05-26 | C | 32 | 0.089177 | 9.7742e-05
2015 | 2014-05-26 | C | 121 | 0.033638 | 0.00036959
2015 | 2014-05-25 | C | 55 | 0.22445 | 0.00016799
2015 | 2014-05-24 | C | 124 | 0.013256 | 0.00037875
2015 | 2014-05-28 | B | 81 | 0.083377 | 0.00024741
2015 | 2014-05-23 | C | 148 | 0.024026 | 0.00045205
2015 | 2014-05-28 | B | 3 | 0.0021717 | 9.1633e-06
2015 | 2014-05-26 | C | 1 | 0.0090411 | 3.0544e-06
2015 | 2014-05-24 | C | 256 | 0.35118 | 0.00078193
2015 | 2014-05-28 | C | 53 | 0.01811 | 0.00016188
2015 | 2014-05-28 | C | 251 | 0.072833 | 0.00076666
2015 | 2014-05-27 | C | 2 | 0.01022 | 6.1088e-06
2015 | 2014-05-28 | B | 6 | 0.005443 | 1.8327e-05
2015 | 2014-05-28 | B | 1 | 0.00025046 | 3.0544e-06
2015 | 2014-05-28 | B | 1 | 0.0001741 | 3.0544e-06
2015 | 2014-05-28 | B | 6 | 0.0095848 | 1.8327e-05
2015 | 2014-05-28 | B | 202 | 0.21348 | 0.00061699
2015 | 2014-05-28 | C | 51 | 0.010437 | 0.00015578
2015 | 2014-05-28 | C | 4 | 0.0017105 | 1.2218e-05
2015 | 2014-05-25 | C | 3 | 0.039017 | 9.1633e-06
2015 | 2014-05-26 | C | 1 | 0.0014478 | 3.0544e-06
2015 | 2014-04-10 | B | 1 | 0.0010171 | 3.0544e-06
2015 | 2014-05-29 | B | 6 | 0.0016494 | 1.8327e-05
2015 | 2014-05-29 | B | 25 | 0.0032071 | 7.6361e-05
2015 | 2014-04-10 | B | 54 | 0.024081 | 0.00016494
2015 | 2014-04-11 | B | 24 | 0.0023458 | 7.3306e-05
2015 | 2014-04-10 | B | 91 | 0.088111 | 0.00027795
2015 | 2014-05-29 | C | 175 | 0.027795 | 0.00053452
2015 | 2014-04-16 | B | 28 | 0.0010263 | 8.5524e-05
2015 | 2014-04-30 | B | 69 | 0.072921 | 0.00021076
2015 | 2014-05-29 | C | 205 | 0.080148 | 0.00062616
2015 | 2014-05-29 | C | 607 | 0.18143 | 0.001854
2015 | 2014-04-30 | B | 183 | 0.22414 | 0.00055896
2015 | 2014-04-30 | B | 1 | 0.00063837 | 3.0544e-06
2015 | 2014-05-01 | B | 17 | 0.017655 | 5.1925e-05
2015 | 2014-05-29 | C | 195 | 0.049998 | 0.00059561
2015 | 2014-05-01 | B | 41 | 0.042704 | 0.00012523
2015 | 2014-05-24 | C | 963 | 1.9347 | 0.0029414
2015 | 2014-05-29 | B | 23 | 0.029716 | 7.0252e-05
2015 | 2014-05-29 | C | 23 | 0.0075872 | 7.0252e-05
2015 | 2014-05-28 | C | 108 | 0.085047 | 0.00032988
2015 | 2014-05-29 | C | 51 | 0.0045175 | 0.00015578
2015 | 2014-05-29 | B | 30 | 0.031063 | 9.1633e-05
2015 | 2014-05-29 | B | 54 | 0.051461 | 0.00016494
2015 | 2014-05-29 | B | 7 | 0.0072695 | 2.1381e-05
2015 | 2014-05-29 | C | 113 | 0.018311 | 0.00034515
2015 | 2014-05-29 | C | 231 | 0.048458 | 0.00070557
2015 | 2014-05-29 | B | 34 | 0.01215 | 0.00010385
2015 | 2014-05-29 | B | 23 | 0.0028101 | 7.0252e-05
2015 | 2014-05-30 | C | 795 | 0.14327 | 0.0024283
2015 | 2014-05-30 | C | 92 | 0.023043 | 0.00028101
2015 | 2014-05-05 | B | 2 | 0.0020037 | 6.1088e-06
2015 | 2014-05-06 | B | 110 | 0.020159 | 0.00033599
2015 | 2014-04-17 | B | 91 | 0.069488 | 0.00027795
2015 | 2014-05-13 | B | 23 | 0.034283 | 7.0252e-05
2015 | 2014-05-15 | B | 17 | 0.011527 | 5.1925e-05
2015 | 2014-05-15 | B | 5 | 0.004994 | 1.5272e-05
2015 | 2014-05-15 | B | 78 | 0.093392 | 0.00023825
2015 | 2014-05-30 | C | 6 | 0.00018327 | 1.8327e-05
2015 | 2014-05-30 | B | 88 | 0.075799 | 0.00026879
2015 | 2014-05-29 | C | 1 | 0.0041082 | 3.0544e-06
2015 | 2014-05-28 | C | 287 | 0.035941 | 0.00087662
2015 | 2014-05-30 | B | 59 | 0.019643 | 0.00018021
2015 | 2014-05-31 | C | 5 | 0.0020159 | 1.5272e-05
2015 | 2014-05-31 | C | 395 | 0.13362 | 0.0012065
2015 | 2014-06-02 | C | 1 | 0.00047954 | 3.0544e-06
2015 | 2014-06-03 | B | 49 | 0.042056 | 0.00014967
2015 | 2014-06-03 | B | 5 | 0.0043067 | 1.5272e-05
2015 | 2014-06-03 | B | 1 | 2.4435e-05 | 3.0544e-06
2015 | 2014-06-04 | B | 13 | 0.0060355 | 3.9708e-05
2015 | 2014-06-04 | B | 40 | 0.020404 | 0.00012218
2015 | 2014-06-04 | B | 56 | 0.050801 | 0.00017105
2015 | 2014-06-04 | B | 6 | 0.0062677 | 1.8327e-05
2015 | 2014-06-04 | B | 14 | 0.014625 | 4.2762e-05
2015 | 2014-06-04 | B | 18 | 0.015834 | 5.498e-05
2015 | 2014-06-04 | C | 510 | 0.052964 | 0.0015578
2015 | 2014-06-05 | C | 2573 | 0.75431 | 0.007859
2015 | 2014-06-04 | B | 64 | 0.013293 | 0.00019548
2015 | 2014-06-05 | B | 5 | 0.00064143 | 1.5272e-05
2015 | 2014-06-05 | B | 3 | 0.0021717 | 9.1633e-06
2015 | 2014-06-05 | B | 5 | 0.00064143 | 1.5272e-05
2015 | 2014-06-05 | B | 18 | 0.005333 | 5.498e-05
2015 | 2014-06-05 | B | 2 | 0.00043984 | 6.1088e-06
2015 | 2014-06-05 | B | 4 | 0.00063532 | 1.2218e-05
2015 | 2014-06-05 | C | 43 | 0.0066984 | 0.00013134
2015 | 2014-06-05 | B | 54 | 0.052945 | 0.00016494
2015 | 2014-06-05 | B | 99 | 0.10493 | 0.00030239
2015 | 2014-06-06 | B | 4 | 0.0021625 | 1.2218e-05
2015 | 2014-06-06 | C | 265 | 0.045706 | 0.00080942
2015 | 2014-06-06 | B | 23 | 0.014331 | 7.0252e-05
2015 | 2014-06-06 | B | 20 | 0.016311 | 6.1088e-05
2015 | 2014-06-06 | B | 23 | 0.017352 | 7.0252e-05
2015 | 2014-06-06 | B | 44 | 0.020428 | 0.00013439
2015 | 2014-06-06 | C | 242 | 0.041656 | 0.00073917
2015 | 2014-06-06 | B | 17 | 0.020355 | 5.1925e-05
2015 | 2014-06-06 | B | 5 | 0.0017868 | 1.5272e-05
2015 | 2014-06-06 | B | 1 | 0.0007575 | 3.0544e-06
2015 | 2014-06-06 | B | 52 | 0.028431 | 0.00015883
2015 | 2014-06-06 | B | 34 | 0.011631 | 0.00010385
2015 | 2014-06-06 | C | 39 | 0.0034546 | 0.00011912
2015 | 2014-06-06 | C | 308 | 0.04987 | 0.00094076
2015 | 2014-06-07 | B | 2 | 0.0016922 | 6.1088e-06
2015 | 2014-06-06 | C | 1 | 0.0024466 | 3.0544e-06
2015 | 2014-06-07 | B | 31 | 0.033519 | 9.4687e-05
2015 | 2014-06-08 | C | 262 | 0.21047 | 0.00080026
2015 | 2014-06-08 | B | 1 | 0.00069946 | 3.0544e-06
2015 | 2014-06-08 | B | 28 | 0.032841 | 8.5524e-05
2015 | 2014-06-08 | B | 16 | 0.010458 | 4.8871e-05
2015 | 2014-06-08 | B | 1 | 0.00036042 | 3.0544e-06
2015 | 2014-06-08 | C | 153 | 0.044585 | 0.00046733
2015 | 2014-06-09 | C | 216 | 0.016494 | 0.00065976
2015 | 2014-06-09 | B | 10 | 0.00073306 | 3.0544e-05
2015 | 2014-06-09 | B | 5 | 0.00064143 | 1.5272e-05
2015 | 2014-06-09 | B | 1 | 1.8327e-05 | 3.0544e-06
2015 | 2014-06-09 | C | 93 | 0.032667 | 0.00028406
2015 | 2014-06-09 | C | 231 | 0.060896 | 0.00070557
2015 | 2014-06-10 | C | 7 | 0.00076971 | 2.1381e-05
2015 | 2014-06-10 | C | 368 | 0.15355 | 0.001124
2015 | 2014-06-10 | B | 105 | 0.040089 | 0.00032071
2015 | 2014-06-09 | B | 16 | 0.0072817 | 4.8871e-05
2015 | 2014-06-09 | C | 19 | 0.089314 | 5.8034e-05
2015 | 2014-06-10 | C | 3 | 0.00052231 | 9.1633e-06
2015 | 2014-06-10 | C | 33 | 0.0025199 | 0.0001008
2015 | 2014-06-10 | C | 888 | 0.064115 | 0.0027123
2015 | 2014-06-10 | B | 149 | 0.13335 | 0.00045511
2015 | 2014-06-10 | C | 78 | 0.0026207 | 0.00023825
2015 | 2014-06-10 | C | 21 | 0.0084027 | 6.4143e-05
2015 | 2014-06-10 | C | 95 | 0.020031 | 0.00029017
2015 | 2014-06-09 | B | 19 | 0.0073703 | 5.8034e-05
2015 | 2014-06-10 | C | 2 | 0.0018754 | 6.1088e-06
2015 | 2014-06-10 | C | 44 | 0.02876 | 0.00013439
2015 | 2014-06-11 | C | 73 | 0.0095878 | 0.00022297
2015 | 2014-06-11 | C | 306 | 0.32713 | 0.00093465
2015 | 2014-06-11 | C | 261 | 0.26183 | 0.0007972
2015 | 2014-06-11 | C | 79 | 0.010135 | 0.0002413
2015 | 2014-06-11 | C | 653 | 0.73262 | 0.0019945
2015 | 2014-06-11 | C | 543 | 0.13097 | 0.0016586
2015 | 2014-06-11 | C | 807 | 0.57639 | 0.0024649
2015 | 2014-06-11 | C | 33 | 0.0061486 | 0.0001008
2015 | 2014-06-11 | C | 377 | 0.13008 | 0.0011515
2015 | 2014-06-11 | C | 47 | 0.016078 | 0.00014356
2015 | 2014-06-12 | B | 8 | 0.0012218 | 2.4435e-05
2015 | 2014-06-12 | C | 446 | 0.84349 | 0.0013623
2015 | 2014-06-11 | C | 31 | 0.063346 | 9.4687e-05
2015 | 2014-06-11 | C | 298 | 0.17931 | 0.00091022
2015 | 2014-06-12 | B | 80 | 0.035187 | 0.00024435
2015 | 2014-06-12 | B | 16 | 0.0088945 | 4.8871e-05
2015 | 2014-06-11 | C | 421 | 0.38706 | 0.0012859
2015 | 2014-06-12 | C | 35 | 0.0054521 | 0.0001069
2015 | 2014-06-12 | B | 12 | 0.005388 | 3.6653e-05
2015 | 2014-06-11 | C | 255 | 0.19706 | 0.00077888
2015 | 2014-06-12 | B | 8 | 0.0017105 | 2.4435e-05
2015 | 2014-06-11 | C | 3717 | 2.5259 | 0.011353
2015 | 2014-06-10 | B | 64 | 0.057081 | 0.00019548
2015 | 2014-06-11 | C | 2 | 0.0069458 | 6.1088e-06
2015 | 2014-06-12 | C | 24 | 0.020526 | 7.3306e-05
2015 | 2014-06-12 | C | 848 | 0.15965 | 0.0025902
2015 | 2014-06-11 | C | 154 | 0.24523 | 0.00047038
2015 | 2014-06-12 | B | 16 | 0.073306 | 4.8871e-05
2015 | 2014-06-12 | C | 1 | 0.00040318 | 3.0544e-06
2015 | 2014-06-11 | C | 338 | 0.28022 | 0.0010324
2015 | 2014-06-11 | C | 406 | 0.19035 | 0.0012401
2015 | 2014-06-10 | C | 529 | 0.64805 | 0.0016158
2015 | 2014-06-12 | C | 786 | 0.88938 | 0.0024008
2015 | 2014-06-11 | C | 249 | 0.021109 | 0.00076055
2015 | 2014-06-11 | C | 35 | 0.018495 | 0.0001069
2015 | 2014-06-13 | B | 44 | 0.0065853 | 0.00013439
2015 | 2014-06-11 | C | 10097 | 17.6917 | 0.030841
2015 | 2014-06-11 | C | 232 | 0.034433 | 0.00070863
2015 | 2014-06-12 | C | 3 | 0.0096581 | 9.1633e-06
2015 | 2014-06-13 | B | 5 | 0.001176 | 1.5272e-05
2015 | 2014-06-13 | C | 4 | 0.00035431 | 1.2218e-05
2015 | 2014-06-13 | B | 3 | 0.00068725 | 9.1633e-06
2015 | 2014-06-13 | C | 13 | 0.0094107 | 3.9708e-05
2015 | 2014-06-13 | C | 139 | 0.017013 | 0.00042456
2015 | 2014-06-13 | C | 13 | 0.00019854 | 3.9708e-05
2015 | 2014-06-13 | B | 166 | 0.10749 | 0.00050703
2015 | 2014-06-13 | C | 1024 | 0.11289 | 0.0031277
2015 | 2014-06-14 | C | 3 | 0.00019243 | 9.1633e-06
2015 | 2014-06-14 | C | 235 | 0.032304 | 0.00071779
2015 | 2014-06-14 | C | 14 | 0.00072695 | 4.2762e-05
2015 | 2014-06-14 | C | 2439 | 1.1383 | 0.0074497
2015 | 2014-06-14 | C | 254 | 0.27847 | 0.00077582
2015 | 2014-06-14 | C | 51 | 0.010593 | 0.00015578
2015 | 2014-06-15 | B | 16 | 0.0027856 | 4.8871e-05
2015 | 2014-06-15 | B | 19 | 0.0062096 | 5.8034e-05
2015 | 2014-06-15 | C | 2 | 0.00042151 | 6.1088e-06
2015 | 2014-06-15 | C | 175 | 0.068847 | 0.00053452
2015 | 2014-06-15 | C | 727 | 0.10199 | 0.0022206
2015 | 2014-06-15 | C | 295 | 0.055413 | 0.00090105
2015 | 2014-06-16 | C | 46 | 0.0056201 | 0.0001405
2015 | 2014-06-11 | C | 273 | 0.79772 | 0.00083386
2015 | 2014-06-13 | C | 746 | 0.37551 | 0.0022786
2015 | 2014-06-12 | C | 529 | 0.077558 | 0.0016158
2015 | 2014-06-13 | C | 209 | 0.12959 | 0.00063837
2015 | 2014-06-13 | C | 261 | 0.045593 | 0.0007972
2015 | 2014-06-13 | C | 1 | 0.00036042 | 3.0544e-06
2015 | 2014-06-11 | C | 157 | 0.13677 | 0.00047954
2015 | 2014-06-11 | C | 696 | 1.0757 | 0.0021259
2015 | 2014-06-11 | C | 476 | 0.69061 | 0.0014539
2015 | 2014-06-11 | C | 175 | 0.38994 | 0.00053452
2015 | 2014-06-16 | B | 2 | 0.0020465 | 6.1088e-06
2015 | 2014-06-11 | C | 753 | 1.169 | 0.0023
2015 | 2014-06-12 | C | 7 | 0.0014539 | 2.1381e-05
2015 | 2014-06-16 | B | 6 | 0.0058095 | 1.8327e-05
2015 | 2014-06-16 | C | 1 | 3.6653e-05 | 3.0544e-06
2015 | 2014-06-16 | C | 1 | 0.00039402 | 3.0544e-06
2015 | 2014-06-16 | B | 39 | 0.019417 | 0.00011912
2015 | 2014-06-16 | C | 20 | 0.0024435 | 6.1088e-05
2015 | 2014-06-14 | C | 3 | 0.00077888 | 9.1633e-06
2015 | 2014-06-11 | C | 548 | 0.44555 | 0.0016738
2015 | 2014-06-11 | C | 415 | 0.12057 | 0.0012676
2015 | 2014-06-11 | C | 118 | 0.09889 | 0.00036042
2015 | 2014-06-12 | C | 1 | 0.00075444 | 3.0544e-06
2015 | 2014-06-12 | C | 3 | 0.0013195 | 9.1633e-06
2015 | 2014-06-12 | C | 415 | 0.22743 | 0.0012676
2015 | 2014-06-11 | C | 216 | 0.72375 | 0.00065976
2015 | 2014-06-17 | C | 2 | 0.00086746 | 6.1088e-06
2015 | 2014-06-11 | C | 36 | 0.0045083 | 0.00010996
2015 | 2014-06-13 | B | 3 | 0.00078804 | 9.1633e-06
2015 | 2014-06-11 | C | 458 | 0.6477 | 0.0013989
2015 | 2014-06-12 | C | 3 | 0.00033904 | 9.1633e-06
2015 | 2014-06-11 | C | 326 | 0.036842 | 0.00099574
2015 | 2014-06-17 | B | 5 | 0.0023825 | 1.5272e-05
2015 | 2014-06-17 | C | 211 | 0.0096673 | 0.00064448
2015 | 2014-06-17 | B | 28 | 0.014368 | 8.5524e-05
2015 | 2014-06-17 | B | 76 | 0.016482 | 0.00023214
2015 | 2014-06-12 | C | 891 | 0.035379 | 0.0027215
2015 | 2014-06-11 | C | 326 | 0.36471 | 0.00099574
2015 | 2014-06-11 | C | 325 | 0.22335 | 0.00099269
2015 | 2014-06-10 | C | 1133 | 0.58758 | 0.0034607
2015 | 2014-06-16 | B | 1 | 0.00063227 | 3.0544e-06
2015 | 2014-06-17 | C | 121 | 0.012566 | 0.00036959
2015 | 2014-06-17 | C | 44 | 0.0087357 | 0.00013439
2015 | 2014-06-17 | B | 5 | 0.0041846 | 1.5272e-05
2015 | 2014-06-11 | C | 69 | 0.043416 | 0.00021076
2015 | 2014-06-11 | C | 142 | 0.42635 | 0.00043373
2015 | 2014-06-12 | C | 7 | 0.002245 | 2.1381e-05
2015 | 2014-06-11 | C | 47 | 0.0047374 | 0.00014356
2015 | 2014-06-11 | C | 141 | 0.28798 | 0.00043067
2015 | 2014-06-10 | C | 282 | 0.085893 | 0.00086135
2015 | 2014-06-11 | C | 245 | 0.4803 | 0.00074833
2015 | 2014-06-11 | C | 3 | 0.00012829 | 9.1633e-06
2015 | 2014-06-11 | C | 594 | 0.30576 | 0.0018143
2015 | 2014-06-17 | C | 1 | 0.0011607 | 3.0544e-06
2015 | 2014-06-17 | B | 22 | 0.029029 | 6.7197e-05
2015 | 2014-06-17 | C | 3 | 0.0001741 | 9.1633e-06
2015 | 2014-06-11 | C | 420 | 0.39512 | 0.0012829
2015 | 2014-06-12 | C | 2 | 0.00025657 | 6.1088e-06
2015 | 2014-06-11 | C | 157 | 0.40397 | 0.00047954
2015 | 2014-06-11 | C | 7 | 0.00032071 | 2.1381e-05
2015 | 2014-06-11 | C | 275 | 0.086581 | 0.00083997
2015 | 2014-06-11 | C | 50 | 0.023018 | 0.00015272
2015 | 2014-06-12 | C | 4 | 0.0052536 | 1.2218e-05
2015 | 2014-06-18 | B | 1 | 0.00016799 | 3.0544e-06
2015 | 2014-06-18 | C | 927 | 0.28474 | 0.0028315
2015 | 2014-06-11 | C | 803 | 0.29678 | 0.0024527
2015 | 2014-06-12 | C | 1151 | 0.19413 | 0.0035156
2015 | 2014-06-11 | C | 63 | 0.016552 | 0.00019243
2015 | 2014-06-11 | C | 19 | 0.011534 | 5.8034e-05
2015 | 2014-06-10 | C | 301 | 0.074253 | 0.00091938
2015 | 2014-06-17 | C | 1 | 0.0014417 | 3.0544e-06
2015 | 2014-06-18 | B | 2 | 0.0016616 | 6.1088e-06
2015 | 2014-06-11 | C | 224 | 0.025672 | 0.00068419
2015 | 2014-06-18 | B | 24 | 0.012682 | 7.3306e-05
2015 | 2014-06-18 | B | 291 | 0.03022 | 0.00088884
2015 | 2014-06-18 | B | 2 | 0.0014173 | 6.1088e-06
2015 | 2014-06-11 | C | 272 | 0.13791 | 0.0008308
2015 | 2014-06-11 | C | 1303 | 0.33431 | 0.0039799
2015 | 2014-06-11 | C | 1311 | 1.3709 | 0.0040043
2015 | 2014-06-11 | C | 607 | 0.31493 | 0.001854
2015 | 2014-06-11 | C | 153 | 0.43706 | 0.00046733
2015 | 2014-06-18 | C | 260 | 0.031766 | 0.00079415
2015 | 2014-06-11 | C | 614 | 0.93132 | 0.0018754
2015 | 2014-06-18 | B | 5 | 0.0052536 | 1.5272e-05
2015 | 2014-06-11 | C | 1208 | 3.1034 | 0.0036897
2015 | 2014-06-13 | C | 234 | 0.0096031 | 0.00071474
2015 | 2014-06-13 | C | 267 | 0.025281 | 0.00081553
2015 | 2014-06-11 | C | 432 | 1.2165 | 0.0013195
2015 | 2014-06-11 | C | 1039 | 0.066644 | 0.0031735
2015 | 2014-06-11 | C | 272 | 0.059818 | 0.0008308
2015 | 2014-06-19 | B | 4 | 0.0014906 | 1.2218e-05
2015 | 2014-06-13 | B | 4 | 0.0030789 | 1.2218e-05
2015 | 2014-06-19 | B | 8 | 0.0061333 | 2.4435e-05
2015 | 2014-06-17 | B | 5 | 0.0052078 | 1.5272e-05
2015 | 2014-06-19 | B | 7 | 0.0061363 | 2.1381e-05
2015 | 2014-06-19 | B | 257 | 0.019466 | 0.00078499
2015 | 2014-06-19 | B | 26 | 0.015248 | 7.9415e-05
2015 | 2014-06-19 | C | 2 | 0.00040929 | 6.1088e-06
2015 | 2014-06-19 | C | 179 | 0.047976 | 0.00054674
2015 | 2014-06-19 | C | 1831 | 0.11185 | 0.0055926
2015 | 2014-06-19 | C | 76 | 0.012535 | 0.00023214
2015 | 2014-06-19 | C | 289 | 0.076587 | 0.00088273
2015 | 2014-06-20 | C | 171 | 0.11183 | 0.00052231
2015 | 2014-06-19 | C | 6 | 0.019243 | 1.8327e-05
2015 | 2014-06-16 | C | 4 | 0.0011362 | 1.2218e-05
2015 | 2014-06-13 | C | 31 | 0.0071015 | 9.4687e-05
2015 | 2014-06-20 | B | 6 | 0.0045267 | 1.8327e-05
2015 | 2014-06-20 | C | 108 | 0.041045 | 0.00032988
2015 | 2014-06-20 | B | 2 | 0.00080637 | 6.1088e-06
2015 | 2014-06-20 | C | 43 | 0.0039402 | 0.00013134
2015 | 2014-06-20 | B | 58 | 0.034723 | 0.00017716
2015 | 2014-06-20 | C | 1083 | 0.10518 | 0.0033079
2015 | 2014-06-21 | C | 3 | 0.00056812 | 9.1633e-06
2015 | 2014-06-21 | C | 95 | 0.018937 | 0.00029017
2015 | 2014-06-21 | C | 111 | 0.11833 | 0.00033904
2015 | 2014-06-21 | C | 49 | 0.0088334 | 0.00014967
2015 | 2014-06-22 | C | 527 | 0.18511 | 0.0016097
2015 | 2014-06-21 | C | 221 | 0.095762 | 0.00067503
2015 | 2014-06-22 | C | 144 | 0.034747 | 0.00043984
2015 | 2014-06-23 | B | 83 | 0.01445 | 0.00025352
2015 | 2014-06-22 | C | 19 | 0.011317 | 5.8034e-05
2015 | 2014-06-21 | C | 6 | 0.0015944 | 1.8327e-05
2015 | 2014-06-12 | B | 2 | 0.0019365 | 6.1088e-06
2015 | 2014-06-23 | C | 291 | 0.077301 | 0.00088884
2015 | 2014-06-23 | C | 2049 | 0.046907 | 0.0062585
2015 | 2014-06-23 | C | 154 | 0.015113 | 0.00047038
2015 | 2014-06-23 | C | 632 | 0.13513 | 0.0019304
2015 | 2014-06-11 | C | 584 | 1.1024 | 0.0017838
2015 | 2014-06-24 | B | 26 | 0.023189 | 7.9415e-05
2015 | 2014-06-24 | B | 152 | 0.067857 | 0.00046427
2015 | 2014-06-10 | B | 5 | 0.0054521 | 1.5272e-05
2015 | 2014-06-24 | B | 92 | 0.016473 | 0.00028101
2015 | 2014-06-24 | C | 41 | 0.011647 | 0.00012523
2015 | 2014-06-24 | B | 43 | 0.041109 | 0.00013134
2015 | 2014-06-24 | B | 6 | 0.00021992 | 1.8327e-05
2015 | 2014-06-25 | C | 154 | 0.056589 | 0.00047038
2015 | 2014-06-25 | B | 34 | 0.0049848 | 0.00010385
2015 | 2014-06-25 | B | 5 | 0.0056812 | 1.5272e-05
2015 | 2014-06-24 | B | 5 | 0.00032071 | 1.5272e-05
2015 | 2014-06-25 | B | 1 | 0.00070557 | 3.0544e-06
2015 | 2014-06-25 | C | 580 | 0.091578 | 0.0017716
2015 | 2014-06-25 | C | 197 | 0.11183 | 0.00060172
2015 | 2014-06-25 | B | 37 | 0.020455 | 0.00011301
2015 | 2014-06-25 | B | 66 | 0.018412 | 0.00020159
2015 | 2014-06-25 | C | 26 | 0.0069091 | 7.9415e-05
2015 | 2014-06-26 | B | 40 | 0.022847 | 0.00012218
2015 | 2014-06-26 | B | 34 | 0.002804 | 0.00010385
2015 | 2014-06-11 | C | 666 | 0.90533 | 0.0020342
2015 | 2014-06-26 | C | 308 | 0.051742 | 0.00094076
2015 | 2014-06-11 | C | 2242 | 0.58501 | 0.006848
2015 | 2014-06-11 | C | 698 | 0.91037 | 0.002132
2015 | 2014-06-11 | C | 152 | 0.17928 | 0.00046427
2015 | 2014-05-31 | B | 4 | 0.0023458 | 1.2218e-05
2015 | 2014-06-26 | C | 4 | 0.0012462 | 1.2218e-05
2015 | 2014-06-27 | C | 142 | 0.014179 | 0.00043373
2015 | 2014-06-26 | C | 346 | 0.096648 | 0.0010568
2015 | 2014-06-26 | C | 666 | 0.12978 | 0.0020342
2015 | 2014-06-26 | C | 10 | 0.0020159 | 3.0544e-05
2015 | 2014-06-26 | B | 10 | 0.0020465 | 3.0544e-05
2015 | 2014-06-11 | B | 6 | 0.00076971 | 1.8327e-05
2015 | 2014-06-27 | B | 1 | 0.00031155 | 3.0544e-06
2015 | 2014-06-26 | C | 1 | 0.0047405 | 3.0544e-06
2015 | 2014-06-27 | C | 232 | 0.019842 | 0.00070863
2015 | 2014-06-27 | C | 3 | 0.0011362 | 9.1633e-06
2015 | 2014-06-27 | C | 63 | 0.0051956 | 0.00019243
2015 | 2014-06-27 | B | 77 | 0.089608 | 0.00023519
2015 | 2014-06-27 | C | 8 | 0.003421 | 2.4435e-05
2015 | 2014-06-27 | C | 178 | 0.04611 | 0.00054369
2015 | 2014-06-27 | C | 183 | 0.014533 | 0.00055896
2015 | 2014-06-27 | C | 14 | 0.0026512 | 4.2762e-05
2015 | 2014-06-28 | C | 515 | 0.029888 | 0.001573
2015 | 2014-06-28 | C | 518 | 0.071183 | 0.0015822
2015 | 2014-06-27 | C | 3 | 0.0024283 | 9.1633e-06
2015 | 2014-06-28 | C | 250 | 0.075145 | 0.00076361
2015 | 2014-06-28 | C | 637 | 0.12579 | 0.0019457
2015 | 2014-06-28 | C | 364 | 0.11358 | 0.0011118
2015 | 2014-06-29 | C | 5 | 0.0010996 | 1.5272e-05
2015 | 2014-06-29 | C | 364 | 0.087219 | 0.0011118
2015 | 2014-06-29 | B | 17 | 0.0054002 | 5.1925e-05
2015 | 2014-06-29 | C | 7 | 0.0026299 | 2.1381e-05
2015 | 2014-06-29 | C | 165 | 0.0065517 | 0.00050398
2015 | 2014-06-29 | C | 691 | 0.29407 | 0.0021106
2015 | 2014-06-29 | C | 238 | 0.027026 | 0.00072695
2015 | 2014-06-30 | B | 47 | 0.035459 | 0.00014356
2015 | 2014-06-30 | C | 165 | 0.0055438 | 0.00050398
2015 | 2014-06-30 | C | 619 | 0.020798 | 0.0018907
2015 | 2014-06-30 | C | 205 | 0.038822 | 0.00062616
2015 | 2014-06-30 | C | 74 | 0.007911 | 0.00022603
2015 | 2014-06-30 | C | 597 | 0.045425 | 0.0018235
2015 | 2014-06-30 | C | 639 | 0.046843 | 0.0019518
2015 | 2014-06-30 | B | 224 | 0.21509 | 0.00068419
2015 | 2014-06-30 | B | 5 | 0.0043067 | 1.5272e-05
2015 | 2014-06-30 | C | 1 | 0.00030239 | 3.0544e-06
2015 | 2014-06-30 | C | 162 | 0.034142 | 0.00049482
2015 | 2014-06-30 | C | 31 | 0.0082378 | 9.4687e-05
2015 | 2014-06-30 | C | 589 | 0.3778 | 0.0017991
2015 | 2014-06-30 | C | 41 | 0.027676 | 0.00012523
2015 | 2014-06-30 | C | 250 | 0.065068 | 0.00076361
2015 | 2014-06-30 | C | 114 | 0.027841 | 0.0003482
2015 | 2014-06-30 | C | 249 | 0.075365 | 0.00076055
2015 | 2014-06-30 | C | 227 | 0.20257 | 0.00069335
2015 | 2014-05-14 | B | 26 | 0.020568 | 7.9415e-05
2015 | 2014-06-10 | B | 27 | 0.022844 | 8.2469e-05
2015 | 2014-06-28 | B | 19 | 0.014741 | 5.8034e-05
2015 | 2014-07-01 | C | 1 | 0.0010121 | 3.0544e-06
2015 | 2014-07-01 | C | 947 | 0.39024 | 0.0028925
2015 | 2014-07-01 | B | 91 | 0.076854 | 0.00027795
2015 | 2014-07-01 | C | 1207 | 0.081288 | 0.0036867
2015 | 2014-07-01 | C | 1 | 0.00060554 | 3.0544e-06
2015 | 2014-07-01 | C | 925 | 0.24803 | 0.0028253
2015 | 2014-07-01 | C | 898 | 0.079543 | 0.0027429
2015 | 2014-07-01 | C | 410 | 0.025211 | 0.0012523
2015 | 2014-07-01 | C | 1377 | 0.19926 | 0.0042059
2015 | 2014-07-02 | C | 60 | 0.048624 | 0.00018327
2015 | 2014-07-02 | B | 3 | 0.000449 | 9.1633e-06
2015 | 2014-07-02 | C | 2 | 0.001674 | 6.1088e-06
2015 | 2014-07-02 | B | 4 | 0.0021625 | 1.2218e-05
2015 | 2014-07-02 | C | 8 | 0.001232 | 2.4435e-05
2015 | 2014-07-02 | C | 322 | 0.040325 | 0.00098352
2015 | 2014-07-02 | C | 581 | 0.10825 | 0.0017746
2015 | 2014-07-02 | C | 58 | 0.04033 | 0.00017716
2015 | 2014-07-03 | C | 181 | 0.022833 | 0.00055285
2015 | 2014-07-03 | C | 1 | 0.0054918 | 3.0544e-06
2015 | 2014-07-03 | C | 4 | 0.0014074 | 1.2218e-05
2015 | 2014-07-03 | B | 2 | 0.0017359 | 6.1088e-06
2015 | 2014-07-03 | B | 14 | 0.007911 | 4.2762e-05
2015 | 2014-07-04 | C | 1 | 0.0011789 | 3.0544e-06
2015 | 2014-07-04 | B | 7 | 0.0048535 | 2.1381e-05
2015 | 2014-07-04 | C | 195 | 0.37897 | 0.00059561
2015 | 2014-07-04 | C | 50 | 0.00093414 | 0.00015272
2015 | 2014-07-05 | B | 96 | 0.038999 | 0.00029322
2015 | 2014-07-05 | C | 1 | 0.00051813 | 3.0544e-06
2015 | 2014-07-05 | C | 1 | 0.0004912 | 3.0544e-06
2015 | 2014-07-05 | C | 25 | 0.018209 | 7.6361e-05
2015 | 2014-07-05 | C | 2 | 0.0010963 | 6.1088e-06
2015 | 2014-07-05 | C | 602 | 0.26912 | 0.0018388
2015 | 2014-07-05 | C | 412 | 0.082939 | 0.0012584
2015 | 2014-07-06 | C | 1 | 0.00037468 | 3.0544e-06
2015 | 2014-07-06 | B | 119 | 0.12576 | 0.00036348
2015 | 2014-07-06 | C | 1 | 0.00058156 | 3.0544e-06
2015 | 2014-07-06 | C | 358 | 0.10555 | 0.0010935
2015 | 2014-07-06 | C | 364 | 0.034622 | 0.0011118
2015 | 2014-07-07 | B | 3 | 0.0029964 | 9.1633e-06
2015 | 2014-07-07 | B | 13 | 0.013064 | 3.9708e-05
2015 | 2014-07-07 | C | 1 | 0.00018632 | 3.0544e-06
2015 | 2014-07-07 | C | 6 | 0.0019976 | 1.8327e-05
2015 | 2014-07-07 | C | 1271 | 0.51055 | 0.0038822
2015 | 2014-07-07 | C | 1 | 0.00071692 | 3.0544e-06
2015 | 2014-07-08 | C | 9 | 0.0010321 | 2.749e-05
2015 | 2014-07-08 | B | 9 | 0.0098963 | 2.749e-05
2015 | 2014-07-08 | B | 37 | 0.0070106 | 0.00011301
2015 | 2014-07-08 | B | 9 | 0.003795 | 2.749e-05
2015 | 2014-07-08 | C | 26 | 0.023893 | 7.9415e-05
2015 | 2014-07-08 | C | 1 | 0.0015272 | 3.0544e-06
2015 | 2014-07-08 | C | 2 | 0.00079369 | 6.1088e-06
2015 | 2014-07-08 | C | 1 | 0.00049421 | 3.0544e-06
2015 | 2014-07-08 | C | 1 | 0.00047552 | 3.0544e-06
2015 | 2014-07-08 | C | 865 | 0.16045 | 0.0026421
2015 | 2014-07-08 | C | 819 | 0.18607 | 0.0025016
2015 | 2014-07-08 | C | 1 | 0.00042462 | 3.0544e-06
2015 | 2014-07-08 | C | 676 | 0.16107 | 0.0020648
2015 | 2014-07-08 | C | 453 | 0.079229 | 0.0013837
2015 | 2014-07-08 | C | 580 | 0.21773 | 0.0017716
2015 | 2014-07-09 | C | 77 | 0.0045353 | 0.00023519
2015 | 2014-07-09 | C | 249 | 0.14854 | 0.00076055
2015 | 2014-07-09 | C | 13090 | 0.92025 | 0.039982
2015 | 2014-07-09 | C | 3098 | 1.1876 | 0.0094626
2015 | 2014-07-09 | C | 443 | 0.031009 | 0.0013531
2015 | 2014-07-09 | C | 998 | 0.075039 | 0.0030483
2015 | 2014-07-09 | C | 1106 | 0.078824 | 0.0033782
2015 | 2014-07-09 | C | 1194 | 0.081145 | 0.003647
2015 | 2014-07-09 | C | 1077 | 0.083776 | 0.0032896
2015 | 2014-07-09 | C | 1550 | 0.1182 | 0.0047344
2015 | 2014-07-09 | C | 1763 | 0.13014 | 0.0053849
2015 | 2014-07-09 | C | 1 | 0.00051747 | 3.0544e-06
2015 | 2014-07-09 | C | 348 | 0.028699 | 0.0010629
2015 | 2014-07-09 | C | 4 | 0.019551 | 1.2218e-05
2015 | 2014-07-09 | B | 6 | 0.0068129 | 1.8327e-05
2015 | 2014-07-09 | C | 242 | 0.052507 | 0.00073917
2015 | 2014-07-09 | C | 1 | 0.0019623 | 3.0544e-06
2015 | 2014-07-09 | C | 1 | 0.0016926 | 3.0544e-06
2015 | 2014-07-09 | C | 2 | 0.0053539 | 6.1088e-06
2015 | 2014-07-09 | C | 1 | 0.00012218 | 3.0544e-06
2015 | 2014-07-09 | C | 1020 | 0.16395 | 0.0031155
2015 | 2014-07-09 | C | 1 | 0.010649 | 3.0544e-06
2015 | 2014-07-09 | C | 288 | 0.01485 | 0.00087967
2015 | 2014-07-09 | C | 798 | 0.18528 | 0.0024374
2015 | 2014-07-09 | C | 107 | 0.027199 | 0.00032682
2015 | 2014-07-09 | C | 139 | 0.10854 | 0.00042456
2015 | 2014-07-09 | C | 87 | 0.069573 | 0.00026573
2015 | 2014-07-09 | C | 1425 | 0.21169 | 0.0043526
2015 | 2014-07-10 | C | 107 | 0.016293 | 0.00032682
2015 | 2014-07-10 | C | 835 | 0.14861 | 0.0025504
2015 | 2014-07-10 | B | 21 | 0.01347 | 6.4143e-05
2015 | 2014-07-10 | C | 2 | 0.0016715 | 6.1088e-06
2015 | 2014-07-10 | C | 66 | 0.0070927 | 0.00020159
2015 | 2014-07-10 | C | 2 | 0.023933 | 6.1088e-06
2015 | 2014-07-10 | B | 28 | 0.017578 | 8.5524e-05
2015 | 2014-07-10 | C | 50 | 0.0042762 | 0.00015272
2015 | 2014-07-10 | C | 2 | 0.0014001 | 6.1088e-06
2015 | 2014-07-10 | C | 868 | 0.10985 | 0.0026512
2015 | 2014-07-10 | C | 1 | 0.00085259 | 3.0544e-06
2015 | 2014-07-10 | B | 20 | 0.010813 | 6.1088e-05
2015 | 2014-07-10 | C | 14 | 0.001588 | 4.2762e-05
2015 | 2014-07-10 | C | 10 | 0.0045805 | 3.0544e-05
2015 | 2014-07-10 | C | 241 | 0.082636 | 0.00073612
2015 | 2014-07-11 | C | 420 | 0.10152 | 0.0012829
2015 | 2014-07-11 | B | 235 | 0.03845 | 0.00071779
2015 | 2014-07-11 | C | 24 | 0.012566 | 7.3306e-05
2015 | 2014-07-11 | C | 1 | 0.0004182 | 3.0544e-06
2015 | 2014-07-11 | C | 13 | 0.0039721 | 3.9708e-05
2015 | 2014-07-11 | C | 6 | 0.020056 | 1.8327e-05
2015 | 2014-07-11 | C | 5 | 0.0022755 | 1.5272e-05
2015 | 2014-07-11 | C | 16 | 0.00064265 | 4.8871e-05
2015 | 2014-07-11 | C | 10 | 0.0011205 | 3.0544e-05
2015 | 2014-07-11 | C | 3 | 0.00095797 | 9.1633e-06
2015 | 2014-07-11 | C | 23 | 0.024677 | 7.0252e-05
2015 | 2014-07-11 | C | 1 | 0.0017282 | 3.0544e-06
2015 | 2014-07-12 | B | 16 | 0.0079439 | 4.8871e-05
2015 | 2014-07-12 | C | 10108 | 0.070621 | 0.030874
2015 | 2014-07-12 | B | 1 | 0.0065994 | 3.0544e-06
2015 | 2014-07-12 | C | 729 | 0.12433 | 0.0022267
2015 | 2014-07-12 | C | 3606 | 0.22743 | 0.011014
2015 | 2014-07-13 | C | 3 | 0.0031501 | 9.1633e-06
2015 | 2014-07-13 | C | 569 | 0.085808 | 0.001738
2015 | 2014-07-13 | C | 240 | 0.073742 | 0.00073306
2015 | 2014-07-13 | C | 18 | 0.0032209 | 5.498e-05
2015 | 2014-07-13 | C | 360 | 0.061755 | 0.0010996
2015 | 2014-07-14 | B | 13 | 0.01362 | 3.9708e-05
2015 | 2014-07-14 | C | 8 | 0.0047144 | 2.4435e-05
2015 | 2014-07-14 | C | 1494 | 0.83616 | 0.0045633
2015 | 2014-07-15 | B | 12 | 0.01859 | 3.6653e-05
2015 | 2014-07-15 | B | 6 | 0.002647 | 1.8327e-05
2015 | 2014-07-15 | C | 5222 | 0.51901 | 0.01595
2015 | 2014-07-15 | C | 31 | 0.029235 | 9.4687e-05
2015 | 2014-07-15 | C | 2 | 0.00071565 | 6.1088e-06
2015 | 2014-07-15 | B | 2 | 0.0014224 | 6.1088e-06
2015 | 2014-07-15 | C | 1303 | 0.32523 | 0.0039799
2015 | 2014-07-15 | C | 1 | 0.00028712 | 3.0544e-06
2015 | 2014-07-16 | C | 12 | 0.11626 | 3.6653e-05
2015 | 2014-07-16 | B | 8 | 0.0027636 | 2.4435e-05
2015 | 2014-07-16 | B | 13 | 0.015764 | 3.9708e-05
2015 | 2014-07-16 | B | 50 | 0.056135 | 0.00015272
2015 | 2014-07-16 | C | 1204 | 0.019001 | 0.0036775
2015 | 2014-07-16 | C | 114 | 0.019523 | 0.0003482
2015 | 2014-07-16 | C | 67 | 0.002159 | 0.00020465
2015 | 2014-07-17 | C | 92 | 0.04062 | 0.00028101
2015 | 2014-07-17 | B | 12 | 0.012865 | 3.6653e-05
2015 | 2014-07-17 | C | 1 | 0.00013134 | 3.0544e-06
2015 | 2014-07-17 | C | 1 | 0.00026925 | 3.0544e-06
2015 | 2014-07-17 | C | 659 | 0.069636 | 0.0020129
2015 | 2014-07-17 | C | 2 | 0.0012018 | 6.1088e-06
2015 | 2014-07-17 | C | 1 | 0.00068042 | 3.0544e-06
2015 | 2014-07-17 | C | 32 | 0.03369 | 9.7742e-05
2015 | 2014-07-17 | C | 44 | 0.038183 | 0.00013439
2015 | 2014-07-17 | C | 1070 | 0.14619 | 0.0032682
2015 | 2014-07-17 | C | 81 | 1.4567 | 0.00024741
2015 | 2014-07-18 | C | 6823 | 0.39911 | 0.02084
2015 | 2014-07-18 | B | 120 | 0.059286 | 0.00036653
2015 | 2014-07-18 | C | 182 | 0.044595 | 0.00055591
2015 | 2014-07-18 | B | 15 | 0.013008 | 4.5816e-05
2015 | 2014-07-18 | C | 1 | 0.00091231 | 3.0544e-06
2015 | 2014-07-19 | C | 309 | 0.0028315 | 0.00094382
2015 | 2014-07-19 | C | 311 | 0.083706 | 0.00094993
2015 | 2014-07-19 | C | 1 | 0.00064509 | 3.0544e-06
2015 | 2014-07-19 | C | 3 | 0.0019157 | 9.1633e-06
2015 | 2014-07-19 | C | 74 | 0.022301 | 0.00022603
2015 | 2014-07-19 | C | 1 | 0.0010691 | 3.0544e-06
2015 | 2014-07-20 | C | 3 | 0.0091527 | 9.1633e-06
2015 | 2014-07-20 | C | 110 | 0.070012 | 0.00033599
2015 | 2014-07-21 | C | 141 | 0.14944 | 0.00043067
2015 | 2014-07-21 | C | 1 | 0.00020378 | 3.0544e-06
2015 | 2014-07-21 | B | 12 | 0.00021992 | 3.6653e-05
2015 | 2014-07-21 | C | 5 | 0.0013624 | 1.5272e-05
2015 | 2014-07-21 | C | 509 | 0.10106 | 0.0015547
2015 | 2014-07-22 | B | 12 | 0.013189 | 3.6653e-05
2015 | 2014-07-22 | C | 1 | 0.0015924 | 3.0544e-06
2015 | 2014-07-22 | C | 6 | 0.008368 | 1.8327e-05
2015 | 2014-07-22 | B | 11 | 0.01092 | 3.3599e-05
2015 | 2014-07-22 | C | 3 | 0.0013233 | 9.1633e-06
2015 | 2014-07-23 | B | 3 | 0.0028681 | 9.1633e-06
2015 | 2014-07-23 | B | 50 | 0.051162 | 0.00015272
2015 | 2014-07-23 | C | 1 | 0.00047344 | 3.0544e-06
2015 | 2014-07-23 | C | 62 | 0.021281 | 0.00018937
2015 | 2014-07-23 | C | 55 | 0.0059139 | 0.00016799
2015 | 2014-07-24 | B | 12 | 0.012499 | 3.6653e-05
2015 | 2014-07-24 | C | 1 | 0.00023697 | 3.0544e-06
2015 | 2014-07-24 | C | 8 | 0.003254 | 2.4435e-05
2015 | 2014-07-24 | C | 335 | 0.038229 | 0.0010232
2015 | 2014-07-25 | B | 96 | 0.12345 | 0.00029322
2015 | 2014-07-25 | B | 5 | 0.0038944 | 1.5272e-05
2015 | 2014-07-25 | B | 4 | 0.0024812 | 1.2218e-05
2015 | 2014-07-25 | C | 1 | 0.00029862 | 3.0544e-06
2015 | 2014-07-25 | C | 3698 | 0.55396 | 0.011295
2015 | 2014-07-25 | C | 1 | 0.0004546 | 3.0544e-06
2015 | 2014-07-25 | C | 27 | 0.015842 | 8.2469e-05
2015 | 2014-07-26 | C | 2 | 0.0003421 | 6.1088e-06
2015 | 2014-07-26 | C | 1 | 0.00043373 | 3.0544e-06
2015 | 2014-07-26 | C | 532 | 0.17516 | 0.001625
2015 | 2014-07-27 | C | 323 | 0.32 | 0.00098658
2015 | 2014-07-27 | C | 8 | 0.0020607 | 2.4435e-05
2015 | 2014-07-27 | C | 425 | 0.096925 | 0.0012981
2015 | 2014-07-28 | B | 52 | 0.032176 | 0.00015883
2015 | 2014-07-28 | C | 1 | 0.00022883 | 3.0544e-06
2015 | 2014-07-29 | B | 136 | 0.15958 | 0.0004154
2015 | 2014-07-29 | B | 528 | 0.21675 | 0.0016127
2015 | 2014-07-29 | C | 1037 | 0.092933 | 0.0031674
2015 | 2014-07-30 | C | 1 | 0.00036668 | 3.0544e-06
2015 | 2014-07-30 | B | 12 | 0.010813 | 3.6653e-05
2015 | 2014-07-30 | B | 16 | 0.016772 | 4.8871e-05
2015 | 2014-07-30 | B | 4 | 0.003421 | 1.2218e-05
2015 | 2014-07-30 | B | 7 | 0.0047466 | 2.1381e-05
2015 | 2014-07-30 | C | 43 | 0.00042935 | 0.00013134
2015 | 2014-07-30 | C | 1 | 0.00022445 | 3.0544e-06
2015 | 2014-07-30 | C | 35 | 0.012935 | 0.0001069
2015 | 2014-07-30 | C | 1 | 0.00038119 | 3.0544e-06
2015 | 2014-07-31 | B | 30 | 0.042321 | 9.1633e-05
2015 | 2014-07-31 | B | 79 | 0.096644 | 0.0002413
2015 | 2014-07-31 | C | 1 | 0.00031323 | 3.0544e-06
2015 | 2014-07-31 | B | 13 | 0.00814 | 3.9708e-05
2015 | 2014-07-31 | C | 7 | 0.0040958 | 2.1381e-05
2015 | 2014-07-31 | C | 1 | 0.00074385 | 3.0544e-06
2015 | 2014-07-31 | C | 1 | 0.000351 | 3.0544e-06
2015 | 2014-08-01 | C | 2512 | 0.49045 | 0.0076727
2015 | 2014-08-01 | C | 12 | 0.0016663 | 3.6653e-05
2015 | 2014-08-01 | C | 1 | 0.00030834 | 3.0544e-06
2015 | 2014-08-01 | C | 1 | 0.00068928 | 3.0544e-06
2015 | 2014-08-01 | C | 51 | 0.019878 | 0.00015578
2015 | 2014-08-01 | C | 2 | 0.00054211 | 6.1088e-06
2015 | 2014-08-02 | C | 45 | 0.029373 | 0.00013745
2015 | 2014-08-02 | C | 58 | 0.047127 | 0.00017716
2015 | 2014-08-02 | C | 2 | 0.00038806 | 6.1088e-06
2015 | 2014-08-02 | C | 1 | 0.00029704 | 3.0544e-06
2015 | 2014-08-02 | C | 1 | 0.00034627 | 3.0544e-06
2015 | 2014-08-02 | C | 1 | 0.00022654 | 3.0544e-06
2015 | 2014-08-02 | C | 4 | 0.0049708 | 1.2218e-05
2015 | 2014-08-02 | C | 1 | 0.0012058 | 3.0544e-06
2015 | 2014-08-02 | C | 2 | 0.0007577 | 6.1088e-06
2015 | 2014-08-02 | C | 120 | 0.075508 | 0.00036653
2015 | 2014-08-02 | C | 400 | 0.20517 | 0.0012218
2015 | 2014-08-02 | C | 20 | 0.00091633 | 6.1088e-05
2015 | 2014-08-02 | C | 1 | 0.0032211 | 3.0544e-06
2015 | 2014-08-02 | C | 1 | 0.00046544 | 3.0544e-06
2015 | 2014-08-02 | C | 47 | 0.0069817 | 0.00014356
2015 | 2014-08-03 | C | 133 | 0.052837 | 0.00040624
2015 | 2014-08-03 | C | 5 | 0.011943 | 1.5272e-05
2015 | 2014-08-03 | C | 52 | 0.020439 | 0.00015883
2015 | 2014-08-03 | C | 119 | 0.03484 | 0.00036348
2015 | 2014-08-03 | C | 1 | 0.0006089 | 3.0544e-06
2015 | 2014-08-03 | C | 361 | 0.06017 | 0.0011026
2015 | 2014-08-03 | C | 1 | 0.00020424 | 3.0544e-06
2015 | 2014-08-03 | C | 2 | 0.00010996 | 6.1088e-06
2015 | 2014-08-03 | C | 1 | 0.00020134 | 3.0544e-06
2015 | 2014-08-03 | C | 891 | 0.014447 | 0.0027215
2015 | 2014-08-03 | C | 1 | 0.00012462 | 3.0544e-06
2015 | 2014-08-03 | C | 89 | 0.012777 | 0.00027184
2015 | 2014-08-04 | C | 2 | 0.00065665 | 6.1088e-06
2015 | 2014-08-04 | B | 57 | 0.045622 | 0.0001741
2015 | 2014-08-04 | B | 3 | 0.0016677 | 9.1633e-06
2015 | 2014-08-04 | C | 2 | 0.00051925 | 6.1088e-06
2015 | 2014-08-05 | B | 236 | 0.36087 | 0.00072084
2015 | 2014-08-05 | B | 44 | 0.026595 | 0.00013439
2015 | 2014-08-05 | B | 1 | 0.0010206 | 3.0544e-06
2015 | 2014-08-05 | B | 42 | 0.043615 | 0.00012829
2015 | 2014-08-05 | B | 2 | 0.00082749 | 6.1088e-06
2015 | 2014-08-05 | C | 533 | 0.15192 | 0.001628
2015 | 2014-08-05 | C | 1246 | 0.54014 | 0.0038058
2015 | 2014-08-06 | C | 114 | 0.025768 | 0.0003482
2015 | 2014-08-06 | C | 9 | 0.0010726 | 2.749e-05
2015 | 2014-08-06 | B | 33 | 0.033263 | 0.0001008
2015 | 2014-08-06 | C | 1 | 0.00040619 | 3.0544e-06
2015 | 2014-08-06 | C | 108 | 0.16973 | 0.00032988
2015 | 2014-08-06 | C | 16 | 0.0016127 | 4.8871e-05
2015 | 2014-08-06 | B | 20 | 0.00048871 | 6.1088e-05
2015 | 2014-08-06 | C | 1 | 0.0006003 | 3.0544e-06
2015 | 2014-08-06 | C | 1 | 0.00021875 | 3.0544e-06
2015 | 2014-08-07 | B | 23 | 0.028241 | 7.0252e-05
2015 | 2014-08-07 | B | 95 | 0.088502 | 0.00029017
2015 | 2014-08-07 | B | 17 | 0.017914 | 5.1925e-05
2015 | 2014-08-07 | C | 2 | 0.0006231 | 6.1088e-06
2015 | 2014-08-07 | B | 1 | 0.0012464 | 3.0544e-06
2015 | 2014-08-07 | C | 1 | 0.00021992 | 3.0544e-06
2015 | 2014-08-07 | C | 10 | 0.0032978 | 3.0544e-05
2015 | 2014-08-07 | C | 1 | 0.00039799 | 3.0544e-06
2015 | 2014-08-07 | C | 1 | 5.8034e-05 | 3.0544e-06
2015 | 2014-08-08 | C | 1 | 0.0018354 | 3.0544e-06
2015 | 2014-08-08 | C | 3 | 0.080842 | 9.1633e-06
2015 | 2014-08-08 | C | 258 | 0.16162 | 0.00078804
2015 | 2014-08-08 | B | 13 | 0.052635 | 3.9708e-05
2015 | 2014-08-08 | B | 7 | 0.0012187 | 2.1381e-05
2015 | 2014-08-08 | C | 4 | 0.0044668 | 1.2218e-05
2015 | 2014-08-08 | B | 10 | 0.0026573 | 3.0544e-05
2015 | 2014-08-08 | B | 20 | 0.019402 | 6.1088e-05
2015 | 2014-08-08 | B | 1 | 0.0005161 | 3.0544e-06
2015 | 2014-08-08 | C | 4 | 0.00093582 | 1.2218e-05
2015 | 2014-08-08 | B | 4 | 0.0020452 | 1.2218e-05
2015 | 2014-08-08 | B | 3 | 0.0012134 | 9.1633e-06
2015 | 2014-08-08 | C | 16 | 0.011368 | 4.8871e-05
2015 | 2014-08-08 | C | 1 | 0.00060966 | 3.0544e-06
2015 | 2014-08-08 | B | 2 | 0.00071474 | 6.1088e-06
2015 | 2014-08-08 | C | 108 | 0.021152 | 0.00032988
2015 | 2014-08-08 | C | 1942 | 0.32556 | 0.0059317
2015 | 2014-08-08 | C | 1 | 0.00070796 | 3.0544e-06
2015 | 2014-08-08 | C | 18 | 0.011756 | 5.498e-05
2015 | 2014-08-08 | B | 226 | 0.021399 | 0.0006903
2015 | 2014-08-08 | C | 28 | 0.0031142 | 8.5524e-05
2015 | 2014-08-09 | C | 142 | 0.03897 | 0.00043373
2015 | 2014-08-09 | C | 293 | 0.040941 | 0.00089495
2015 | 2014-08-09 | C | 1 | 0.00025387 | 3.0544e-06
2015 | 2014-08-09 | C | 27 | 0.025978 | 8.2469e-05
2015 | 2014-08-09 | C | 28 | 0.02694 | 8.5524e-05
2015 | 2014-08-09 | C | 27 | 0.011968 | 8.2469e-05
2015 | 2014-08-09 | C | 1 | 0.00033456 | 3.0544e-06
2015 | 2014-08-09 | C | 1 | 0.0001851 | 3.0544e-06
2015 | 2014-08-09 | B | 374 | 0.057308 | 0.0011424
2015 | 2014-08-10 | C | 3 | 0.0056373 | 9.1633e-06
2015 | 2014-08-10 | C | 3 | 0.00077582 | 9.1633e-06
2015 | 2014-08-10 | C | 1 | 0.00048397 | 3.0544e-06
2015 | 2014-08-10 | C | 1 | 0.00040217 | 3.0544e-06
2015 | 2014-08-11 | C | 501 | 0.045367 | 0.0015303
2015 | 2014-08-11 | C | 2 | 0.00057729 | 6.1088e-06
2015 | 2014-08-11 | C | 1 | 0.00092885 | 3.0544e-06
2015 | 2014-08-11 | B | 5 | 0.0055234 | 1.5272e-05
2015 | 2014-08-11 | B | 22 | 0.02237 | 6.7197e-05
2015 | 2014-08-11 | B | 2 | 0.00091093 | 6.1088e-06
2015 | 2014-08-11 | C | 1 | 0.00084231 | 3.0544e-06
2015 | 2014-08-11 | C | 5 | 0.0035341 | 1.5272e-05
2015 | 2014-08-11 | C | 78 | 0.034528 | 0.00023825
2015 | 2014-08-11 | C | 1 | 0.0080349 | 3.0544e-06
2015 | 2014-08-11 | C | 2 | 0.00025423 | 6.1088e-06
2015 | 2014-08-11 | C | 10 | 0.011599 | 3.0544e-05
2015 | 2014-08-11 | C | 20 | 0.023186 | 6.1088e-05
2015 | 2014-08-12 | C | 1 | 0.00060376 | 3.0544e-06
2015 | 2014-08-12 | C | 1 | 0.00077791 | 3.0544e-06
2015 | 2014-08-12 | C | 3 | 0.00018586 | 9.1633e-06
2015 | 2014-08-12 | C | 8 | 0.0042762 | 2.4435e-05
2015 | 2014-08-12 | B | 330 | 0.27299 | 0.001008
2015 | 2014-08-12 | B | 4 | 0.0037997 | 1.2218e-05
2015 | 2014-08-12 | B | 12 | 0.0084388 | 3.6653e-05
2015 | 2014-08-12 | C | 2 | 0.00050729 | 6.1088e-06
2015 | 2014-08-12 | C | 877 | 0.034964 | 0.0026787
2015 | 2014-08-12 | C | 1 | 0.00035436 | 3.0544e-06
2015 | 2014-08-13 | C | 406 | 0.09627 | 0.0012401
2015 | 2014-08-13 | C | 2 | 0.00082154 | 6.1088e-06
2015 | 2014-08-13 | C | 405 | 0.06001 | 0.001237
2015 | 2014-08-13 | C | 12 | 0.010218 | 3.6653e-05
2015 | 2014-08-13 | B | 143 | 0.16117 | 0.00043678
2015 | 2014-08-13 | B | 5 | 0.0021027 | 1.5272e-05
2015 | 2014-08-13 | C | 1 | 0.00032698 | 3.0544e-06
2015 | 2014-08-13 | C | 2 | 0.0011318 | 6.1088e-06
2015 | 2014-08-13 | C | 156 | 0.0014295 | 0.00047649
2015 | 2014-08-13 | C | 2 | 0.00064056 | 6.1088e-06
2015 | 2014-08-13 | C | 94 | 0.019524 | 0.00028712
2015 | 2014-08-13 | C | 877 | 0.033434 | 0.0026787
2015 | 2014-08-13 | C | 1 | 0.00045969 | 3.0544e-06
2015 | 2014-08-13 | C | 877 | 0.013394 | 0.0026787
2015 | 2014-08-13 | C | 146 | 0.057938 | 0.00044595
2015 | 2014-08-13 | C | 1 | 0.00020368 | 3.0544e-06
2015 | 2014-08-14 | C | 1 | 0.0017108 | 3.0544e-06
2015 | 2014-08-14 | C | 1 | 0.0008337 | 3.0544e-06
2015 | 2014-08-14 | C | 1 | 0.00051386 | 3.0544e-06
2015 | 2014-08-14 | C | 1 | 0.0010434 | 3.0544e-06
2015 | 2014-08-14 | C | 2 | 0.0013321 | 6.1088e-06
2015 | 2014-08-14 | C | 2 | 0.0008977 | 6.1088e-06
2015 | 2014-08-14 | C | 3 | 0.00065161 | 9.1633e-06
2015 | 2014-08-14 | C | 1 | 0.00075358 | 3.0544e-06
2015 | 2014-08-14 | B | 136 | 0.083708 | 0.0004154
2015 | 2014-08-14 | C | 325 | 0.089754 | 0.00099269
2015 | 2014-08-14 | C | 1 | 0.00090813 | 3.0544e-06
2015 | 2014-08-14 | C | 2 | 0.00046101 | 6.1088e-06
2015 | 2014-08-14 | B | 12 | 0.0084681 | 3.6653e-05
2015 | 2014-08-14 | C | 42 | 0.030313 | 0.00012829
2015 | 2014-08-14 | C | 1 | 0.00085901 | 3.0544e-06
2015 | 2014-08-14 | C | 3 | 0.0019429 | 9.1633e-06
2015 | 2014-08-14 | C | 209 | 0.14018 | 0.00063837
2015 | 2014-08-14 | C | 17 | 0.0049481 | 5.1925e-05
2015 | 2014-08-14 | C | 231 | 0.077227 | 0.00070557
2015 | 2014-08-14 | C | 193 | 0.049192 | 0.0005895
2015 | 2014-08-14 | C | 307 | 0.071387 | 0.00093771
2015 | 2014-08-14 | C | 25 | 0.031926 | 7.6361e-05
2015 | 2014-08-14 | C | 3 | 0.0025894 | 9.1633e-06
2015 | 2014-08-14 | C | 1 | 0.00063186 | 3.0544e-06
2015 | 2014-08-14 | C | 20 | 0.013766 | 6.1088e-05
2015 | 2014-08-14 | C | 30 | 0.011408 | 9.1633e-05
2015 | 2014-08-14 | C | 14 | 0.40735 | 4.2762e-05
2015 | 2014-08-14 | C | 1 | 0.0026873 | 3.0544e-06
2015 | 2014-08-14 | C | 1 | 0.0019057 | 3.0544e-06
2015 | 2014-08-14 | C | 1 | 0.00060411 | 3.0544e-06
2015 | 2014-08-14 | C | 1 | 0.0028684 | 3.0544e-06
2015 | 2014-08-14 | C | 1 | 0.0031548 | 3.0544e-06
2015 | 2014-08-14 | C | 58 | 0.034088 | 0.00017716
2015 | 2014-08-14 | C | 1 | 0.002609 | 3.0544e-06
2015 | 2014-08-14 | C | 2 | 0.0030782 | 6.1088e-06
2015 | 2014-08-14 | C | 1 | 6.4143e-05 | 3.0544e-06
2015 | 2014-08-14 | C | 292 | 0.069386 | 0.00089189
2015 | 2014-08-14 | C | 1 | 0.0021485 | 3.0544e-06
2015 | 2014-08-14 | C | 593 | 0.2446 | 0.0018113
2015 | 2014-08-14 | C | 2474 | 0.29471 | 0.0075566
2015 | 2014-08-15 | C | 295 | 0.079772 | 0.00090105
2015 | 2014-08-15 | C | 16 | 0.002104 | 4.8871e-05
2015 | 2014-08-15 | C | 109 | 0.035808 | 0.00033293
2015 | 2014-08-15 | C | 4 | 0.0048032 | 1.2218e-05
2015 | 2014-08-15 | C | 1 | 0.00070201 | 3.0544e-06
2015 | 2014-08-15 | C | 287 | 0.32063 | 0.00087662
2015 | 2014-08-15 | C | 2 | 0.0028255 | 6.1088e-06
2015 | 2014-08-15 | C | 1 | 0.00059307 | 3.0544e-06
2015 | 2014-08-15 | C | 1 | 0.0016282 | 3.0544e-06
2015 | 2014-08-15 | C | 8 | 0.015906 | 2.4435e-05
2015 | 2014-08-15 | C | 1 | 0.0045237 | 3.0544e-06
2015 | 2014-08-15 | C | 1 | 0.00074894 | 3.0544e-06
2015 | 2014-08-15 | C | 1 | 0.001554 | 3.0544e-06
2015 | 2014-08-15 | B | 77 | 0.071733 | 0.00023519
2015 | 2014-08-15 | C | 1 | 0.00097823 | 3.0544e-06
2015 | 2014-08-15 | C | 9 | 0.001114 | 2.749e-05
2015 | 2014-08-15 | C | 72 | 0.09063 | 0.00021992
2015 | 2014-08-15 | C | 3 | 0.004157 | 9.1633e-06
2015 | 2014-08-15 | C | 9 | 0.0043709 | 2.749e-05
2015 | 2014-08-15 | C | 1 | 0.0007098 | 3.0544e-06
2015 | 2014-08-15 | C | 1 | 0.0013011 | 3.0544e-06
2015 | 2014-08-15 | C | 2 | 0.00099757 | 6.1088e-06
2015 | 2014-08-15 | C | 244 | 0.056312 | 0.00074528
2015 | 2014-08-15 | C | 1 | 0.0012075 | 3.0544e-06
2015 | 2014-08-15 | B | 18 | 0.023055 | 5.498e-05
2015 | 2014-08-15 | C | 1 | 0.00018327 | 3.0544e-06
2015 | 2014-08-15 | C | 1 | 0.00058054 | 3.0544e-06
2015 | 2014-08-16 | C | 1 | 0.00045053 | 3.0544e-06
2015 | 2014-08-16 | C | 1 | 0.00055815 | 3.0544e-06
2015 | 2014-08-16 | C | 2 | 0.0014025 | 6.1088e-06
2015 | 2014-08-17 | B | 14 | 0.0028237 | 4.2762e-05
2015 | 2014-08-17 | C | 1 | 0.00018815 | 3.0544e-06
2015 | 2014-08-17 | C | 420 | 0.30522 | 0.0012829
2015 | 2014-08-18 | C | 1 | 0.00094422 | 3.0544e-06
2015 | 2014-08-18 | C | 6 | 0.0014111 | 1.8327e-05
2015 | 2014-08-18 | C | 858 | 0.1738 | 0.0026207
2015 | 2014-08-18 | C | 2 | 0.0056711 | 6.1088e-06
2015 | 2014-08-18 | C | 1 | 0.0003508 | 3.0544e-06
2015 | 2014-08-19 | C | 1 | 0.00022567 | 3.0544e-06
2015 | 2014-08-19 | B | 2 | 0.0026818 | 6.1088e-06
2015 | 2014-08-19 | B | 79 | 0.065782 | 0.0002413
2015 | 2014-08-19 | B | 54 | 0.054331 | 0.00016494
2015 | 2014-08-19 | C | 259 | 0.0016349 | 0.0007911
2015 | 2014-08-19 | C | 1 | 0.00047527 | 3.0544e-06
2015 | 2014-08-19 | C | 594 | 0.16438 | 0.0018143
2015 | 2014-08-20 | C | 1 | 0.00055071 | 3.0544e-06
2015 | 2014-08-20 | C | 1 | 0.00019258 | 3.0544e-06
2015 | 2014-08-20 | C | 1 | 0.00085188 | 3.0544e-06
2015 | 2014-08-20 | C | 1 | 0.00048581 | 3.0544e-06
2015 | 2014-08-20 | B | 38 | 0.032615 | 0.00011607
2015 | 2014-08-21 | C | 1 | 0.00026721 | 3.0544e-06
2015 | 2014-08-21 | C | 695 | 0.1465 | 0.0021228
2015 | 2014-08-21 | C | 1 | 0.0003003 | 3.0544e-06
2015 | 2014-08-21 | B | 76 | 0.10144 | 0.00023214
2015 | 2014-08-21 | B | 4 | 0.0043495 | 1.2218e-05
2015 | 2014-08-21 | B | 38 | 0.053511 | 0.00011607
2015 | 2014-08-21 | B | 7 | 0.00068419 | 2.1381e-05
2015 | 2014-08-21 | B | 54 | 0.035173 | 0.00016494
2015 | 2014-08-21 | C | 95 | 0.00075928 | 0.00029017
2015 | 2014-08-21 | C | 49 | 0.015416 | 0.00014967
2015 | 2014-08-21 | C | 177 | 0.014835 | 0.00054063
2015 | 2014-08-21 | C | 21 | 0.0023733 | 6.4143e-05
2015 | 2014-08-22 | B | 2 | 0.00043373 | 6.1088e-06
2015 | 2014-08-22 | B | 13 | 0.011833 | 3.9708e-05
2015 | 2014-08-22 | B | 80 | 0.0606 | 0.00024435
2015 | 2014-08-22 | C | 1 | 0.00037697 | 3.0544e-06
2015 | 2014-08-22 | C | 908 | 0.19406 | 0.0027734
2015 | 2014-08-22 | C | 361 | 0.048551 | 0.0011026
2015 | 2014-08-23 | C | 2 | 0.00073321 | 6.1088e-06
2015 | 2014-08-23 | C | 53 | 0.040281 | 0.00016188
2015 | 2014-08-24 | C | 850 | 0.060565 | 0.0025963
2015 | 2014-08-24 | B | 51 | 0.011683 | 0.00015578
2015 | 2014-08-24 | B | 138 | 0.16523 | 0.00042151
2015 | 2014-08-24 | C | 214 | 0.026701 | 0.00065365
2015 | 2014-08-25 | C | 281 | 0.021186 | 0.00085829
2015 | 2014-08-25 | C | 1 | 0.0011601 | 3.0544e-06
2015 | 2014-08-25 | B | 41 | 0.024765 | 0.00012523
2015 | 2014-08-25 | C | 1 | 0.00091602 | 3.0544e-06
2015 | 2014-08-25 | C | 1 | 0.00029419 | 3.0544e-06
2015 | 2014-08-26 | C | 929 | 0.12417 | 0.0028376
2015 | 2014-08-27 | B | 100 | 0.066321 | 0.00030544
2015 | 2014-08-27 | B | 28 | 0.031397 | 8.5524e-05
2015 | 2014-08-27 | B | 39 | 0.045457 | 0.00011912
2015 | 2014-08-27 | C | 3 | 9.8709e-05 | 9.1633e-06
2015 | 2014-08-27 | C | 1 | 8.5524e-05 | 3.0544e-06
2015 | 2014-08-27 | C | 1 | 0.00045104 | 3.0544e-06
2015 | 2014-08-27 | C | 4 | 0.001041 | 1.2218e-05
2015 | 2014-08-27 | C | 219 | 0.18451 | 0.00066892
2015 | 2014-08-28 | C | 2 | 0.00035447 | 6.1088e-06
2015 | 2014-08-28 | B | 13 | 0.016819 | 3.9708e-05
2015 | 2014-08-28 | B | 26 | 0.019991 | 7.9415e-05
2015 | 2014-08-28 | C | 1 | 0.00019396 | 3.0544e-06
2015 | 2014-08-28 | C | 1 | 0.00031761 | 3.0544e-06
2015 | 2014-08-28 | C | 1 | 0.00020312 | 3.0544e-06
2015 | 2014-08-28 | C | 1 | 0.00032372 | 3.0544e-06
2015 | 2014-08-28 | C | 2 | 0.000651 | 6.1088e-06
2015 | 2014-08-28 | B | 15 | 0.011169 | 4.5816e-05
2015 | 2014-08-30 | C | 90 | 0.064711 | 0.0002749
2015 | 2014-08-31 | C | 1 | 0.00032234 | 3.0544e-06
2015 | 2014-08-31 | C | 544 | 0.19875 | 0.0016616
2015 | 2014-08-31 | C | 2 | 0.0013117 | 6.1088e-06
2015 | 2014-08-31 | C | 1 | 0.00078321 | 3.0544e-06
2015 | 2014-08-31 | C | 1 | 0.00027917 | 3.0544e-06
2015 | 2014-08-31 | C | 1 | 0.00031303 | 3.0544e-06
2015 | 2014-09-01 | C | 619 | 0.195 | 0.0018907
2015 | 2014-09-01 | B | 5 | 0.0025441 | 1.5272e-05
2015 | 2014-09-01 | C | 1 | 0.00034663 | 3.0544e-06
2015 | 2014-09-01 | C | 536 | 0.057283 | 0.0016372
2015 | 2014-09-02 | B | 2 | 0.0013749 | 6.1088e-06
2015 | 2014-09-02 | B | 8 | 0.0023584 | 2.4435e-05
2015 | 2014-09-02 | C | 674 | 0.34339 | 0.0020587
2015 | 2014-09-03 | C | 1 | 0.00055168 | 3.0544e-06
2015 | 2014-09-03 | B | 2 | 0.0020038 | 6.1088e-06
2015 | 2014-09-03 | B | 1 | 0.00075236 | 3.0544e-06
2015 | 2014-09-03 | B | 11 | 0.0083661 | 3.3599e-05
2015 | 2014-09-03 | C | 1 | 0.00095644 | 3.0544e-06
2015 | 2014-09-04 | C | 1 | 0.0017563 | 3.0544e-06
2015 | 2014-09-04 | C | 2 | 0.0010342 | 6.1088e-06
2015 | 2014-09-04 | C | 1 | 0.00031649 | 3.0544e-06
2015 | 2014-09-04 | C | 351 | 0.026064 | 0.0010721
2015 | 2014-09-04 | B | 12 | 0.012139 | 3.6653e-05
2015 | 2014-09-04 | B | 7 | 0.0058659 | 2.1381e-05
2015 | 2014-09-04 | B | 2 | 0.0011329 | 6.1088e-06
2015 | 2014-09-04 | B | 3 | 0.0012844 | 9.1633e-06
2015 | 2014-09-04 | C | 1 | 0.000303 | 3.0544e-06
2015 | 2014-09-04 | C | 1 | 0.00048128 | 3.0544e-06
2015 | 2014-09-04 | B | 1 | 0.00045241 | 3.0544e-06
2015 | 2014-09-04 | C | 1 | 0.00020969 | 3.0544e-06
2015 | 2014-09-04 | C | 354 | 0.11382 | 0.0010813
2015 | 2014-09-05 | C | 2294 | 0.041755 | 0.0070068
2015 | 2014-09-05 | C | 118 | 0.15005 | 0.00036042
2015 | 2014-09-05 | C | 718 | 0.17663 | 0.0021931
2015 | 2014-09-05 | C | 3 | 0.0013806 | 9.1633e-06
2015 | 2014-09-05 | C | 212 | 0.064647 | 0.00064754
2015 | 2014-09-05 | C | 1 | 0.0041957 | 3.0544e-06
2015 | 2014-09-05 | C | 5 | 0.0042441 | 1.5272e-05
2015 | 2014-09-05 | C | 2 | 0.00039845 | 6.1088e-06
2015 | 2014-09-05 | C | 1398 | 0.36708 | 0.0042701
2015 | 2014-09-05 | C | 1 | 0.00030407 | 3.0544e-06
2015 | 2014-09-06 | B | 1 | 1.1301e-05 | 3.0544e-06
2015 | 2014-09-06 | C | 26 | 0.0041296 | 7.9415e-05
2015 | 2014-09-06 | C | 1 | 0.00023397 | 3.0544e-06
2015 | 2014-09-07 | C | 236 | 0.052622 | 0.00072084
2015 | 2014-09-08 | C | 2 | 0.00063812 | 6.1088e-06
2015 | 2014-09-08 | C | 297 | 0.11279 | 0.00090716
2015 | 2014-09-08 | B | 2 | 0.0019352 | 6.1088e-06
2015 | 2014-09-08 | B | 50 | 0.04156 | 0.00015272
2015 | 2014-09-08 | C | 1 | 0.0012888 | 3.0544e-06
2015 | 2014-09-08 | C | 1 | 0.0007183 | 3.0544e-06
2015 | 2014-09-08 | B | 17 | 0.032381 | 5.1925e-05
2015 | 2014-09-08 | C | 1 | 0.0014291 | 3.0544e-06
2015 | 2014-09-09 | B | 10 | 0.010782 | 3.0544e-05
2015 | 2014-09-09 | B | 70 | 0.064977 | 0.00021381
2015 | 2014-09-09 | C | 242 | 0.08563 | 0.00073917
2015 | 2014-09-09 | B | 1 | 0.012134 | 3.0544e-06
2015 | 2014-09-09 | C | 236 | 0.018105 | 0.00072084
2015 | 2014-09-09 | C | 166 | 0.062361 | 0.00050703
2015 | 2014-09-10 | C | 1 | 0.00032127 | 3.0544e-06
2015 | 2014-09-10 | C | 161 | 0.039182 | 0.00049176
2015 | 2014-09-10 | C | 10 | 0.0010554 | 3.0544e-05
2015 | 2014-09-10 | B | 91 | 0.084697 | 0.00027795
2015 | 2014-09-10 | B | 38 | 0.042597 | 0.00011607
2015 | 2014-09-10 | C | 8 | 0.0021259 | 2.4435e-05
2015 | 2014-09-10 | B | 41 | 0.017203 | 0.00012523
2015 | 2014-09-10 | B | 28 | 0.025036 | 8.5524e-05
2015 | 2014-09-10 | B | 35 | 0.021511 | 0.0001069
2015 | 2014-09-10 | C | 2 | 0.002272 | 6.1088e-06
2015 | 2014-09-11 | C | 35 | 0.012927 | 0.0001069
2015 | 2014-09-11 | C | 27 | 0.0030888 | 8.2469e-05
2015 | 2014-09-11 | B | 38 | 0.042284 | 0.00011607
2015 | 2014-09-11 | B | 91 | 0.05623 | 0.00027795
2015 | 2014-09-11 | B | 2 | 0.0022358 | 6.1088e-06
2015 | 2014-09-11 | C | 4 | 0.0057668 | 1.2218e-05
2015 | 2014-09-11 | B | 58 | 0.050144 | 0.00017716
2015 | 2014-09-11 | B | 30 | 0.024411 | 9.1633e-05
2015 | 2014-09-11 | C | 652 | 0.19696 | 0.0019915
2015 | 2014-09-11 | C | 1 | 0.00036587 | 3.0544e-06
2015 | 2014-09-11 | B | 1961 | 0.042303 | 0.0059897
2015 | 2014-09-11 | C | 331 | 0.035089 | 0.001011
2015 | 2014-09-11 | C | 57 | 0.005049 | 0.0001741
2015 | 2014-09-11 | C | 22 | 0.00067197 | 6.7197e-05
2015 | 2014-09-12 | C | 12 | 0.0049836 | 3.6653e-05
2015 | 2014-09-12 | B | 6 | 0.0031134 | 1.8327e-05
2015 | 2014-09-12 | C | 2 | 0.00031939 | 6.1088e-06
2015 | 2014-09-12 | C | 1 | 0.00038532 | 3.0544e-06
2015 | 2014-09-12 | C | 2 | 0.00049227 | 6.1088e-06
2015 | 2014-09-12 | C | 5 | 0.0012029 | 1.5272e-05
2015 | 2014-09-13 | C | 275 | 0.015259 | 0.00083997
2015 | 2014-09-13 | B | 15 | 0.019473 | 4.5816e-05
2015 | 2014-09-13 | C | 1 | 0.00042049 | 3.0544e-06
2015 | 2014-09-13 | C | 4 | 0.0020471 | 1.2218e-05
2015 | 2014-09-13 | C | 237 | 0.11493 | 0.0007239
2015 | 2014-09-13 | C | 6 | 4.7344e-05 | 1.8327e-05
2015 | 2014-09-13 | C | 1 | 0.00028401 | 3.0544e-06
2015 | 2014-09-14 | C | 92 | 0.00076849 | 0.00028101
2015 | 2014-09-14 | C | 1 | 0.00024985 | 3.0544e-06
2015 | 2014-09-14 | C | 1 | 0.0011053 | 3.0544e-06
2015 | 2014-09-14 | C | 1 | 0.00015272 | 3.0544e-06
2015 | 2014-09-14 | C | 1 | 0.00040318 | 3.0544e-06
2015 | 2014-09-14 | C | 6 | 0.0024599 | 1.8327e-05
2015 | 2014-09-14 | C | 1 | 0.0002693 | 3.0544e-06
2015 | 2014-09-15 | C | 140 | 0.043873 | 0.00042762
2015 | 2014-09-15 | C | 1 | 0.00013506 | 3.0544e-06
2015 | 2014-09-15 | C | 4 | 0.002187 | 1.2218e-05
2015 | 2014-09-16 | C | 401 | 0.047444 | 0.0012248
2015 | 2014-09-16 | C | 11 | 0.0044709 | 3.3599e-05
2015 | 2014-09-16 | B | 1 | 0.00071392 | 3.0544e-06
2015 | 2014-09-16 | C | 700 | 0.10195 | 0.0021381
2015 | 2014-09-16 | B | 8 | 0.011546 | 2.4435e-05
2015 | 2014-09-16 | B | 41 | 0.026925 | 0.00012523
2015 | 2014-09-16 | C | 121 | 0.032117 | 0.00036959
2015 | 2014-09-16 | C | 1 | 0.00057489 | 3.0544e-06
2015 | 2014-09-17 | C | 554 | 0.067966 | 0.0016922
2015 | 2014-09-17 | B | 337 | 0.2294 | 0.0010293
2015 | 2014-09-17 | B | 10 | 0.011051 | 3.0544e-05
2015 | 2014-09-17 | B | 33 | 0.038669 | 0.0001008
2015 | 2014-09-17 | B | 25 | 0.021889 | 7.6361e-05
2015 | 2014-09-17 | B | 98 | 0.068174 | 0.00029933
2015 | 2014-09-17 | C | 1 | 0.00052556 | 3.0544e-06
2015 | 2014-09-18 | C | 38 | 0.03885 | 0.00011607
2015 | 2014-09-18 | B | 87 | 0.08752 | 0.00026573
2015 | 2014-09-18 | B | 39 | 0.04584 | 0.00011912
2015 | 2014-09-18 | B | 58 | 0.077149 | 0.00017716
2015 | 2014-09-18 | B | 1 | 0.00099854 | 3.0544e-06
2015 | 2014-09-18 | B | 58 | 0.037333 | 0.00017716
2015 | 2014-09-18 | B | 24 | 0.018962 | 7.3306e-05
2015 | 2014-09-18 | B | 24 | 0.0051314 | 7.3306e-05
2015 | 2014-09-18 | B | 18 | 0.011647 | 5.498e-05
2015 | 2014-09-18 | C | 2 | 0.00063425 | 6.1088e-06
2015 | 2014-09-18 | C | 1 | 0.00026339 | 3.0544e-06
2015 | 2014-09-19 | C | 4 | 0.0080443 | 1.2218e-05
2015 | 2014-09-19 | C | 1 | 0.0008811 | 3.0544e-06
2015 | 2014-09-19 | C | 1 | 0.00097171 | 3.0544e-06
2015 | 2014-09-19 | C | 1 | 0.00076345 | 3.0544e-06
2015 | 2014-09-19 | C | 2 | 0.00032168 | 6.1088e-06
2015 | 2014-09-19 | C | 2 | 0.00083798 | 6.1088e-06
2015 | 2014-09-19 | C | 1 | 0.0010513 | 3.0544e-06
2015 | 2014-09-19 | C | 1 | 0.00068887 | 3.0544e-06
2015 | 2014-09-19 | C | 1 | 0.00072171 | 3.0544e-06
2015 | 2014-09-19 | C | 1 | 0.0010499 | 3.0544e-06
2015 | 2014-09-19 | B | 33 | 0.034378 | 0.0001008
2015 | 2014-09-19 | C | 1 | 0.00049293 | 3.0544e-06
2015 | 2014-09-19 | C | 1 | 0.00067961 | 3.0544e-06
2015 | 2014-09-19 | C | 1 | 0.00028645 | 3.0544e-06
2015 | 2014-09-19 | C | 588 | 0.19432 | 0.001796
2015 | 2014-09-19 | C | 27 | 0.0015458 | 8.2469e-05
2015 | 2014-09-19 | C | 162 | 0.058957 | 0.00049482
2015 | 2014-09-19 | C | 123 | 0.043817 | 0.00037569
2015 | 2014-09-20 | C | 239 | 0.11189 | 0.00073001
2015 | 2014-09-20 | C | 1 | 0.00044656 | 3.0544e-06
2015 | 2014-09-20 | B | 10 | 0.00062819 | 3.0544e-05
2015 | 2014-09-20 | C | 3 | 0.0025486 | 9.1633e-06
2015 | 2014-09-20 | C | 1 | 0.0016319 | 3.0544e-06
2015 | 2014-09-20 | C | 1 | 0.00089561 | 3.0544e-06
2015 | 2014-09-20 | C | 39 | 0.0070978 | 0.00011912
2015 | 2014-09-20 | C | 112 | 0.12746 | 0.0003421
2015 | 2014-09-20 | C | 97 | 0.020443 | 0.00029628
2015 | 2014-09-20 | C | 444 | 0.11504 | 0.0013562
2015 | 2014-09-20 | C | 1008 | 0.14304 | 0.0030789
2015 | 2014-09-20 | C | 1215 | 0.4428 | 0.0037111
2015 | 2014-09-20 | C | 2 | 0.00085208 | 6.1088e-06
2015 | 2014-09-20 | C | 2 | 0.022691 | 6.1088e-06
2015 | 2014-09-20 | C | 595 | 0.10276 | 0.0018174
2015 | 2014-09-20 | C | 11 | 0.011752 | 3.3599e-05
2015 | 2014-09-20 | C | 2 | 0.00055295 | 6.1088e-06
2015 | 2014-09-20 | C | 736 | 0.24741 | 0.0022481
2015 | 2014-09-20 | C | 279 | 0.087867 | 0.00085218
2015 | 2014-09-21 | C | 10 | 0.0024755 | 3.0544e-05
2015 | 2014-09-21 | B | 27 | 0.023999 | 8.2469e-05
2015 | 2014-09-21 | C | 1 | 0.00038893 | 3.0544e-06
2015 | 2014-09-21 | C | 11 | 0.0011463 | 3.3599e-05
2015 | 2014-09-21 | C | 1 | 0.00019614 | 3.0544e-06
2015 | 2014-09-22 | C | 5 | 0.0021544 | 1.5272e-05
2015 | 2014-09-22 | C | 261 | 0.36092 | 0.0007972
2015 | 2014-09-22 | C | 378 | 0.76803 | 0.0011546
2015 | 2014-09-22 | C | 148 | 0.078211 | 0.00045205
2015 | 2014-09-22 | C | 1 | 0.0011605 | 3.0544e-06
2015 | 2014-09-22 | C | 234 | 0.062694 | 0.00071474
2015 | 2014-09-22 | C | 27 | 0.0023273 | 8.2469e-05
2015 | 2014-09-22 | C | 1 | 0.00049029 | 3.0544e-06
2015 | 2014-09-22 | C | 1 | 0.0013462 | 3.0544e-06
2015 | 2014-09-22 | C | 156 | 0.028113 | 0.00047649
2015 | 2014-09-22 | B | 4 | 0.0019182 | 1.2218e-05
2015 | 2014-09-22 | C | 14 | 0.0082887 | 4.2762e-05
2015 | 2014-09-22 | C | 6 | 0.0042654 | 1.8327e-05
2015 | 2014-09-22 | C | 112 | 0.12492 | 0.0003421
2015 | 2014-09-22 | C | 306 | 0.10166 | 0.00093465
2015 | 2014-09-22 | C | 1 | 0.00086119 | 3.0544e-06
2015 | 2014-09-22 | C | 25 | 0.012475 | 7.6361e-05
2015 | 2014-09-22 | C | 157 | 0.073343 | 0.00047954
2015 | 2014-09-22 | C | 295 | 0.085487 | 0.00090105
2015 | 2014-09-22 | C | 295 | 0.18606 | 0.00090105
2015 | 2014-09-22 | C | 953 | 0.33915 | 0.0029109
2015 | 2014-09-22 | C | 1425 | 0.5377 | 0.0043526
2015 | 2014-09-22 | C | 430 | 0.0073769 | 0.0013134
2015 | 2014-09-22 | C | 293 | 0.094722 | 0.00089495
2015 | 2014-09-22 | C | 9 | 0.011007 | 2.749e-05
2015 | 2014-09-22 | C | 156 | 0.042173 | 0.00047649
2015 | 2014-09-22 | C | 438 | 0.1744 | 0.0013378
2015 | 2014-09-22 | C | 261 | 0.073365 | 0.0007972
2015 | 2014-09-22 | C | 23 | 0.0043556 | 7.0252e-05
2015 | 2014-09-22 | C | 7 | 0.0046208 | 2.1381e-05
2015 | 2014-09-22 | C | 548 | 0.17173 | 0.0016738
2015 | 2014-09-22 | C | 30 | 0.010945 | 9.1633e-05
2015 | 2014-09-22 | C | 49 | 0.014222 | 0.00014967
2015 | 2014-09-22 | C | 84 | 0.020614 | 0.00025657
2015 | 2014-09-22 | C | 383 | 0.022446 | 0.0011698
2015 | 2014-09-22 | C | 26 | 0.023856 | 7.9415e-05
2015 | 2014-09-22 | C | 62 | 0.0049237 | 0.00018937
2015 | 2014-09-22 | C | 6 | 0.03465 | 1.8327e-05
2015 | 2014-09-22 | C | 411 | 0.12271 | 0.0012554
2015 | 2014-09-22 | C | 108 | 0.026808 | 0.00032988
2015 | 2014-09-22 | C | 5 | 0.0012523 | 1.5272e-05
2015 | 2014-09-22 | C | 771 | 0.22843 | 0.002355
2015 | 2014-09-22 | C | 13 | 0.00082724 | 3.9708e-05
2015 | 2014-09-22 | C | 9 | 0.031118 | 2.749e-05
2015 | 2014-09-22 | C | 166 | 0.023654 | 0.00050703
2015 | 2014-09-22 | C | 1 | 0.0012584 | 3.0544e-06
2015 | 2014-09-22 | C | 1 | 0.00051554 | 3.0544e-06
2015 | 2014-09-22 | C | 128 | 0.023425 | 0.00039097
2015 | 2014-09-23 | C | 38 | 0.0038382 | 0.00011607
2015 | 2014-09-23 | B | 10 | 0.0067335 | 3.0544e-05
2015 | 2014-09-23 | B | 89 | 0.11608 | 0.00027184
2015 | 2014-09-23 | C | 6 | 0.0065609 | 1.8327e-05
2015 | 2014-09-23 | B | 61 | 0.042878 | 0.00018632
2015 | 2014-09-23 | C | 1 | 0.0016368 | 3.0544e-06
2015 | 2014-09-23 | C | 167 | 0.01931 | 0.00051009
2015 | 2014-09-23 | B | 22 | 0.011639 | 6.7197e-05
2015 | 2014-09-23 | C | 3 | 0.001796 | 9.1633e-06
2015 | 2014-09-23 | C | 1207 | 0.039996 | 0.0036867
2015 | 2014-09-23 | C | 1 | 0.00060895 | 3.0544e-06
2015 | 2014-09-23 | C | 44 | 0.0032255 | 0.00013439
2015 | 2014-09-23 | C | 41 | 0.0097051 | 0.00012523
2015 | 2014-09-23 | C | 11 | 0.0015791 | 3.3599e-05
2015 | 2014-09-23 | C | 303 | 0.072595 | 0.00092549
2015 | 2014-09-23 | C | 1 | 0.00071178 | 3.0544e-06
2015 | 2014-09-24 | B | 49 | 0.056424 | 0.00014967
2015 | 2014-09-24 | B | 228 | 0.27379 | 0.00069641
2015 | 2014-09-24 | C | 3 | 7.6971e-05 | 9.1633e-06
2015 | 2014-09-24 | C | 1 | 0.00015852 | 3.0544e-06
2015 | 2014-09-25 | C | 316 | 0.087525 | 0.0009652
2015 | 2014-09-25 | C | 316 | 0.15216 | 0.0009652
2015 | 2014-09-25 | B | 31 | 0.042953 | 9.4687e-05
2015 | 2014-09-25 | C | 242 | 0.16751 | 0.00073917
2015 | 2014-09-25 | B | 15 | 0.010125 | 4.5816e-05
2015 | 2014-09-25 | C | 565 | 0.020976 | 0.0017257
2015 | 2014-09-25 | B | 10 | 0.0040099 | 3.0544e-05
2015 | 2014-09-25 | B | 10 | 0.0033237 | 3.0544e-05
2015 | 2014-09-25 | B | 39 | 0.010951 | 0.00011912
2015 | 2014-09-25 | C | 191 | 0.18749 | 0.00058339
2015 | 2014-09-25 | C | 2 | 0.0093324 | 6.1088e-06
2015 | 2014-09-25 | C | 98 | 0.021602 | 0.00029933
2015 | 2014-09-26 | C | 12 | 0.010471 | 3.6653e-05
2015 | 2014-09-26 | B | 108 | 0.10309 | 0.00032988
2015 | 2014-09-26 | C | 6 | 0.006176 | 1.8327e-05
2015 | 2014-09-26 | C | 8 | 0.0011485 | 2.4435e-05
2015 | 2014-09-27 | C | 23 | 0.014746 | 7.0252e-05
2015 | 2014-09-27 | C | 293 | 0.005131 | 0.00089495
2015 | 2014-09-27 | C | 12 | 0.0021547 | 3.6653e-05
2015 | 2014-09-27 | C | 2 | 0.0018896 | 6.1088e-06
2015 | 2014-09-27 | B | 4 | 0.0042078 | 1.2218e-05
2015 | 2014-09-27 | C | 171 | 0.035767 | 0.00052231
2015 | 2014-09-28 | C | 118 | 0.065925 | 0.00036042
2015 | 2014-09-28 | C | 1 | 0.00061384 | 3.0544e-06
2015 | 2014-09-28 | C | 105 | 0.034243 | 0.00032071
2015 | 2014-09-28 | C | 15 | 0.0076709 | 4.5816e-05
2015 | 2014-09-28 | C | 45 | 0.020762 | 0.00013745
2015 | 2014-09-28 | C | 1 | 0.00057932 | 3.0544e-06
2015 | 2014-09-28 | C | 11 | 0.008259 | 3.3599e-05
2015 | 2014-09-28 | C | 29 | 0.091874 | 8.8578e-05
2015 | 2014-09-28 | C | 19 | 0.003513 | 5.8034e-05
2015 | 2014-09-28 | C | 1 | 0.00036124 | 3.0544e-06
2015 | 2014-09-28 | C | 332 | 0.025748 | 0.0010141
2015 | 2014-09-28 | C | 98 | 0.013944 | 0.00029933
2015 | 2014-09-28 | C | 25 | 0.075079 | 7.6361e-05
2015 | 2014-09-28 | C | 2 | 0.0046122 | 6.1088e-06
2015 | 2014-09-29 | B | 3 | 0.00048856 | 9.1633e-06
2015 | 2014-09-29 | B | 72 | 0.048162 | 0.00021992
2015 | 2014-09-29 | B | 307 | 0.37991 | 0.00093771
2015 | 2014-09-29 | B | 2 | 0.0022419 | 6.1088e-06
2015 | 2014-09-29 | B | 27 | 0.019916 | 8.2469e-05
2015 | 2014-09-29 | B | 15 | 0.0052536 | 4.5816e-05
2015 | 2014-09-29 | C | 1 | 0.00026624 | 3.0544e-06
2015 | 2014-09-29 | C | 1 | 0.00075887 | 3.0544e-06
2015 | 2014-09-29 | C | 58 | 0.0074125 | 0.00017716
2015 | 2014-09-29 | C | 1 | 0.00033599 | 3.0544e-06
2015 | 2014-09-29 | C | 9 | 0.0012274 | 2.749e-05
2015 | 2014-09-30 | C | 4 | 0.0029887 | 1.2218e-05
2015 | 2014-09-30 | C | 8 | 0.0036775 | 2.4435e-05
2015 | 2014-09-30 | B | 106 | 0.12581 | 0.00032377
2015 | 2014-09-30 | B | 3 | 0.0032255 | 9.1633e-06
2015 | 2014-09-30 | B | 72 | 0.032222 | 0.00021992
2015 | 2014-09-30 | C | 39 | 0.023296 | 0.00011912
2015 | 2014-09-30 | B | 10 | 0.011329 | 3.0544e-05
2015 | 2014-09-30 | B | 44 | 0.033464 | 0.00013439
2015 | 2014-09-30 | B | 52 | 0.019377 | 0.00015883
2015 | 2014-09-30 | C | 1 | 0.0007522 | 3.0544e-06
2015 | 2014-09-30 | C | 1 | 0.0015232 | 3.0544e-06
2015 | 2014-10-01 | B | 2 | 0.0023698 | 6.1088e-06
2015 | 2014-10-01 | B | 119 | 0.13231 | 0.00036348
2015 | 2014-10-01 | B | 95 | 0.11916 | 0.00029017
2015 | 2014-10-01 | C | 1833 | 0.44044 | 0.0055988
2015 | 2014-10-01 | B | 4 | 0.0040929 | 1.2218e-05
2015 | 2014-10-01 | B | 293 | 0.16742 | 0.00089495
2015 | 2014-10-01 | B | 304 | 0.06489 | 0.00092854
2015 | 2014-10-01 | B | 290 | 0.10092 | 0.00088578
2015 | 2014-10-02 | C | 1133 | 0.45404 | 0.0034607
2015 | 2014-10-02 | B | 41 | 0.040074 | 0.00012523
2015 | 2014-10-02 | B | 44 | 0.038168 | 0.00013439
2015 | 2014-10-02 | B | 8 | 0.0082836 | 2.4435e-05
2015 | 2014-10-02 | B | 57 | 0.061632 | 0.0001741
2015 | 2014-10-02 | B | 40 | 0.021992 | 0.00012218
2015 | 2014-10-02 | C | 1 | 0.00027245 | 3.0544e-06
2015 | 2014-10-02 | C | 1 | 0.00019004 | 3.0544e-06
2015 | 2014-10-02 | C | 237 | 0.064266 | 0.0007239
2015 | 2014-10-02 | C | 759 | 0.15749 | 0.0023183
2015 | 2014-10-02 | C | 1 | 0.00033624 | 3.0544e-06
2015 | 2014-10-03 | C | 7 | 0.0011734 | 2.1381e-05
2015 | 2014-10-03 | C | 50 | 0.018124 | 0.00015272
2015 | 2014-10-03 | C | 336 | 0.21703 | 0.0010263
2015 | 2014-10-03 | C | 11 | 0.010263 | 3.3599e-05
2015 | 2014-10-03 | C | 8 | 0.0043251 | 2.4435e-05
2015 | 2014-10-03 | B | 8 | 0.0050789 | 2.4435e-05
2015 | 2014-10-03 | C | 1 | 0.00025881 | 3.0544e-06
2015 | 2014-10-03 | C | 1 | 0.00037244 | 3.0544e-06
2015 | 2014-10-03 | C | 126 | 0.032324 | 0.00038486
2015 | 2014-10-03 | C | 129 | 0.065342 | 0.00039402
2015 | 2014-10-03 | C | 5 | 0.0003818 | 1.5272e-05
2015 | 2014-10-03 | C | 2 | 0.00010385 | 6.1088e-06
2015 | 2014-10-03 | C | 119 | 0.032192 | 0.00036348
2015 | 2014-10-03 | C | 557 | 0.13209 | 0.0017013
2015 | 2014-10-03 | C | 155 | 0.23984 | 0.00047344
2015 | 2014-10-03 | C | 18 | 0.0028589 | 5.498e-05
2015 | 2014-10-03 | C | 816 | 0.087706 | 0.0024924
2015 | 2014-10-03 | C | 1090 | 0.15365 | 0.0033293
2015 | 2014-10-03 | C | 1 | 0.00083829 | 3.0544e-06
2015 | 2014-10-03 | C | 1 | 0.0035075 | 3.0544e-06
2015 | 2014-10-03 | C | 413 | 0.066248 | 0.0012615
2015 | 2014-10-03 | C | 181 | 0.024962 | 0.00055285
2015 | 2014-10-03 | C | 854 | 0.046195 | 0.0026085
2015 | 2014-10-03 | C | 1 | 0.0036792 | 3.0544e-06
2015 | 2014-10-03 | C | 1 | 0.00046219 | 3.0544e-06
2015 | 2014-10-03 | C | 11 | 0.0013932 | 3.3599e-05
2015 | 2014-10-03 | C | 1 | 0.0011942 | 3.0544e-06
2015 | 2014-10-03 | C | 2 | 0.001629 | 6.1088e-06
2015 | 2014-10-03 | C | 105 | 0.035851 | 0.00032071
2015 | 2014-10-03 | C | 1 | 0.0039381 | 3.0544e-06
2015 | 2014-10-03 | C | 1 | 0.0041042 | 3.0544e-06
2015 | 2014-10-03 | C | 480 | 0.19598 | 0.0014661
2015 | 2014-10-03 | C | 2 | 0.0022586 | 6.1088e-06
2015 | 2014-10-03 | C | 126 | 0.027299 | 0.00038486
2015 | 2014-10-03 | C | 1 | 0.00085738 | 3.0544e-06
2015 | 2014-10-03 | C | 1 | 0.00061048 | 3.0544e-06
2015 | 2014-10-03 | C | 1 | 0.0036304 | 3.0544e-06
2015 | 2014-10-03 | C | 121 | 0.079504 | 0.00036959
2015 | 2014-10-03 | C | 32 | 0.013391 | 9.7742e-05
2015 | 2014-10-03 | C | 1 | 0.0028057 | 3.0544e-06
2015 | 2014-10-03 | C | 1 | 0.0031847 | 3.0544e-06
2015 | 2014-10-03 | C | 1 | 0.00024334 | 3.0544e-06
2015 | 2014-10-03 | C | 393 | 0.034311 | 0.0012004
2015 | 2014-10-04 | C | 2 | 0.0013041 | 6.1088e-06
2015 | 2014-10-04 | C | 1 | 0.00042833 | 3.0544e-06
2015 | 2014-10-04 | C | 1 | 0.0017302 | 3.0544e-06
2015 | 2014-10-04 | C | 125 | 0.11664 | 0.0003818
2015 | 2014-10-04 | C | 1 | 0.0013504 | 3.0544e-06
2015 | 2014-10-04 | C | 1 | 0.0024648 | 3.0544e-06
2015 | 2014-10-04 | C | 393 | 0.10023 | 0.0012004
2015 | 2014-10-04 | C | 1 | 0.0018398 | 3.0544e-06
2015 | 2014-10-04 | C | 1 | 0.0022545 | 3.0544e-06
2015 | 2014-10-04 | C | 1 | 0.00045246 | 3.0544e-06
2015 | 2014-10-04 | C | 1 | 0.0015009 | 3.0544e-06
2015 | 2014-10-04 | C | 1 | 0.0011154 | 3.0544e-06
2015 | 2014-10-04 | C | 1 | 0.0023049 | 3.0544e-06
2015 | 2014-10-04 | B | 397 | 0.32297 | 0.0012126
2015 | 2014-10-04 | C | 1 | 0.0020565 | 3.0544e-06
2015 | 2014-10-04 | B | 6 | 0.017782 | 1.8327e-05
2015 | 2014-10-04 | C | 1 | 0.0015804 | 3.0544e-06
2015 | 2014-10-04 | C | 2 | 0.0017798 | 6.1088e-06
2015 | 2014-10-04 | C | 1 | 0.00046356 | 3.0544e-06
2015 | 2014-10-04 | C | 261 | 0.31575 | 0.0007972
2015 | 2014-10-04 | C | 1 | 0.00091363 | 3.0544e-06
2015 | 2014-10-04 | C | 359 | 0.46031 | 0.0010965
2015 | 2014-10-04 | C | 481 | 0.16724 | 0.0014692
2015 | 2014-10-04 | C | 1 | 0.00060528 | 3.0544e-06
2015 | 2014-10-04 | C | 433 | 0.15402 | 0.0013226
2015 | 2014-10-04 | C | 147 | 0.028993 | 0.000449
2015 | 2014-10-04 | C | 1 | 0.0040148 | 3.0544e-06
2015 | 2014-10-04 | C | 527 | 0.15844 | 0.0016097
2015 | 2014-10-04 | C | 16 | 0.0047405 | 4.8871e-05
2015 | 2014-10-04 | C | 1 | 0.00031364 | 3.0544e-06
2015 | 2014-10-04 | C | 149 | 0.009307 | 0.00045511
2015 | 2014-10-04 | C | 1 | 0.00065731 | 3.0544e-06
2015 | 2014-10-05 | C | 6 | 0.0042331 | 1.8327e-05
2015 | 2014-10-05 | C | 1 | 0.00054129 | 3.0544e-06
2015 | 2014-10-05 | C | 224 | 0.15321 | 0.00068419
2015 | 2014-10-05 | C | 2 | 0.00065736 | 6.1088e-06
2015 | 2014-10-05 | C | 1 | 0.00051269 | 3.0544e-06
2015 | 2014-10-05 | C | 2 | 0.00086165 | 6.1088e-06
2015 | 2014-10-05 | C | 432 | 0.18248 | 0.0013195
2015 | 2014-10-05 | C | 100 | 0.021347 | 0.00030544
2015 | 2014-10-05 | C | 40 | 0.0033171 | 0.00012218
2015 | 2014-10-05 | C | 1 | 0.00027296 | 3.0544e-06
2015 | 2014-10-05 | C | 148 | 0.013019 | 0.00045205
2015 | 2014-10-05 | C | 1 | 0.00039784 | 3.0544e-06
2015 | 2014-10-05 | C | 1328 | 0.036277 | 0.0040563
2015 | 2014-10-06 | C | 303 | 0.076816 | 0.00092549
2015 | 2014-10-06 | C | 303 | 0.076214 | 0.00092549
2015 | 2014-10-06 | C | 91 | 0.067961 | 0.00027795
2015 | 2014-10-06 | C | 385 | 0.12864 | 0.001176
2015 | 2014-10-06 | C | 303 | 0.074039 | 0.00092549
2015 | 2014-10-06 | C | 303 | 0.073808 | 0.00092549
2015 | 2014-10-06 | C | 183 | 0.015553 | 0.00055896
2015 | 2014-10-06 | C | 1 | 6.1648e-05 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.0023189 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.00097054 | 3.0544e-06
2015 | 2014-10-06 | B | 471 | 0.039243 | 0.0014386
2015 | 2014-10-06 | C | 92 | 0.0077448 | 0.00028101
2015 | 2014-10-06 | C | 176 | 0.073434 | 0.00053758
2015 | 2014-10-06 | C | 354 | 0.10274 | 0.0010813
2015 | 2014-10-06 | C | 207 | 0.0016786 | 0.00063227
2015 | 2014-10-06 | C | 237 | 0.1358 | 0.0007239
2015 | 2014-10-06 | C | 119 | 0.1732 | 0.00036348
2015 | 2014-10-06 | C | 12 | 0.0060771 | 3.6653e-05
2015 | 2014-10-06 | C | 544 | 0.10639 | 0.0016616
2015 | 2014-10-06 | C | 332 | 0.26556 | 0.0010141
2015 | 2014-10-06 | C | 1180 | 0.22058 | 0.0036042
2015 | 2014-10-06 | C | 26 | 0.039854 | 7.9415e-05
2015 | 2014-10-06 | C | 1263 | 0.30912 | 0.0038577
2015 | 2014-10-06 | C | 1 | 0.0056445 | 3.0544e-06
2015 | 2014-10-06 | C | 83 | 0.52383 | 0.00025352
2015 | 2014-10-06 | C | 336 | 1.4329 | 0.0010263
2015 | 2014-10-06 | C | 1 | 0.0052119 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.009971 | 3.0544e-06
2015 | 2014-10-06 | C | 24 | 0.0065939 | 7.3306e-05
2015 | 2014-10-06 | C | 442 | 0.076953 | 0.0013501
2015 | 2014-10-06 | C | 667 | 0.31456 | 0.0020373
2015 | 2014-10-06 | C | 469 | 0.62344 | 0.0014325
2015 | 2014-10-06 | C | 1 | 0.0012472 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.0014657 | 3.0544e-06
2015 | 2014-10-06 | C | 465 | 0.59009 | 0.0014203
2015 | 2014-10-06 | C | 456 | 0.066916 | 0.0013928
2015 | 2014-10-06 | C | 4 | 0.0020206 | 1.2218e-05
2015 | 2014-10-06 | C | 693 | 0.53291 | 0.0021167
2015 | 2014-10-06 | C | 1 | 0.010034 | 3.0544e-06
2015 | 2014-10-06 | C | 1443 | 0.14895 | 0.0044075
2015 | 2014-10-06 | C | 1 | 0.0015062 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.0054067 | 3.0544e-06
2015 | 2014-10-06 | C | 678 | 0.20744 | 0.0020709
2015 | 2014-10-06 | C | 64 | 0.010641 | 0.00019548
2015 | 2014-10-06 | C | 1 | 0.0013653 | 3.0544e-06
2015 | 2014-10-06 | C | 31 | 0.13247 | 9.4687e-05
2015 | 2014-10-06 | C | 3 | 0.011851 | 9.1633e-06
2015 | 2014-10-06 | C | 943 | 0.20058 | 0.0028803
2015 | 2014-10-06 | C | 241 | 0.25759 | 0.00073612
2015 | 2014-10-06 | C | 27 | 0.16506 | 8.2469e-05
2015 | 2014-10-06 | C | 292 | 0.47142 | 0.00089189
2015 | 2014-10-06 | C | 116 | 0.080886 | 0.00035431
2015 | 2014-10-06 | C | 9 | 0.010247 | 2.749e-05
2015 | 2014-10-06 | C | 533 | 0.12324 | 0.001628
2015 | 2014-10-06 | C | 1 | 0.0055771 | 3.0544e-06
2015 | 2014-10-06 | C | 1215 | 0.21234 | 0.0037111
2015 | 2014-10-06 | C | 1 | 0.0056064 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.018906 | 3.0544e-06
2015 | 2014-10-06 | C | 47 | 0.0054886 | 0.00014356
2015 | 2014-10-06 | C | 1 | 0.00086013 | 3.0544e-06
2015 | 2014-10-06 | C | 393 | 0.089324 | 0.0012004
2015 | 2014-10-06 | C | 2 | 0.0068781 | 6.1088e-06
2015 | 2014-10-06 | C | 202 | 0.053953 | 0.00061699
2015 | 2014-10-06 | C | 66 | 0.32756 | 0.00020159
2015 | 2014-10-06 | C | 759 | 0.59778 | 0.0023183
2015 | 2014-10-06 | C | 466 | 0.20043 | 0.0014234
2015 | 2014-10-06 | C | 102 | 0.056013 | 0.00031155
2015 | 2014-10-06 | C | 54 | 0.0024521 | 0.00016494
2015 | 2014-10-06 | C | 253 | 0.1437 | 0.00077277
2015 | 2014-10-06 | C | 7 | 0.019634 | 2.1381e-05
2015 | 2014-10-06 | C | 22 | 0.010819 | 6.7197e-05
2015 | 2014-10-06 | C | 6 | 0.014203 | 1.8327e-05
2015 | 2014-10-06 | C | 9 | 0.0046375 | 2.749e-05
2015 | 2014-10-06 | C | 1 | 0.0099202 | 3.0544e-06
2015 | 2014-10-06 | C | 4 | 0.0056658 | 1.2218e-05
2015 | 2014-10-06 | C | 2 | 0.0066378 | 6.1088e-06
2015 | 2014-10-06 | C | 1 | 0.0092232 | 3.0544e-06
2015 | 2014-10-06 | C | 54 | 0.023262 | 0.00016494
2015 | 2014-10-06 | C | 143 | 1.0983 | 0.00043678
2015 | 2014-10-06 | C | 1 | 0.0090022 | 3.0544e-06
2015 | 2014-10-06 | C | 943 | 0.78057 | 0.0028803
2015 | 2014-10-06 | C | 217 | 0.079573 | 0.00066281
2015 | 2014-10-06 | C | 341 | 0.13983 | 0.0010416
2015 | 2014-10-06 | C | 1083 | 0.43213 | 0.0033079
2015 | 2014-10-06 | C | 914 | 0.10541 | 0.0027917
2015 | 2014-10-06 | C | 26 | 0.11668 | 7.9415e-05
2015 | 2014-10-06 | C | 1 | 0.0015303 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.0099471 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.005408 | 3.0544e-06
2015 | 2014-10-06 | C | 4 | 0.0011933 | 1.2218e-05
2015 | 2014-10-06 | C | 121 | 0.0034917 | 0.00036959
2015 | 2014-10-06 | C | 107 | 0.068425 | 0.00032682
2015 | 2014-10-06 | C | 2 | 0.0010938 | 6.1088e-06
2015 | 2014-10-06 | C | 11 | 0.0086819 | 3.3599e-05
2015 | 2014-10-06 | C | 903 | 0.38313 | 0.0027581
2015 | 2014-10-06 | C | 719 | 0.57123 | 0.0021961
2015 | 2014-10-06 | C | 1 | 0.0040756 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.0012335 | 3.0544e-06
2015 | 2014-10-06 | C | 1 | 0.01261 | 3.0544e-06
2015 | 2014-10-06 | C | 14 | 0.037416 | 4.2762e-05
2015 | 2014-10-06 | C | 2 | 0.00080896 | 6.1088e-06
2015 | 2014-10-06 | C | 711 | 0.30838 | 0.0021717
2015 | 2014-10-06 | C | 1 | 0.013401 | 3.0544e-06
2015 | 2014-10-06 | C | 14 | 0.084656 | 4.2762e-05
2015 | 2014-10-06 | C | 1 | 0.0028589 | 3.0544e-06
2015 | 2014-10-06 | C | 575 | 0.2994 | 0.0017563
2015 | 2014-10-06 | C | 200 | 0.44804 | 0.00061088
2015 | 2014-10-06 | C | 610 | 1.2647 | 0.0018632
2015 | 2014-10-06 | C | 24 | 0.005278 | 7.3306e-05
2015 | 2014-10-06 | C | 661 | 0.13046 | 0.002019
2015 | 2014-10-06 | C | 550 | 1.4406 | 0.0016799
2015 | 2014-10-06 | C | 1 | 0.0033993 | 3.0544e-06
2015 | 2014-10-06 | C | 653 | 0.13076 | 0.0019945
2015 | 2014-10-06 | C | 6 | 0.018418 | 1.8327e-05
2015 | 2014-10-06 | C | 911 | 0.34516 | 0.0027826
2015 | 2014-10-07 | C | 36 | 0.10301 | 0.00010996
2015 | 2014-10-07 | C | 689 | 0.093986 | 0.0021045
2015 | 2014-10-07 | C | 759 | 0.15086 | 0.0023183
2015 | 2014-10-07 | C | 1 | 0.018075 | 3.0544e-06
2015 | 2014-10-07 | C | 54 | 0.0076359 | 0.00016494
2015 | 2014-10-07 | C | 196 | 0.0029933 | 0.00059867
2015 | 2014-10-07 | C | 1 | 0.0091697 | 3.0544e-06
2015 | 2014-10-07 | C | 9 | 0.0042202 | 2.749e-05
2015 | 2014-10-07 | C | 17 | 0.023714 | 5.1925e-05
2015 | 2014-10-07 | C | 17 | 0.0035828 | 5.1925e-05
2015 | 2014-10-07 | C | 2 | 0.0021064 | 6.1088e-06
2015 | 2014-10-07 | B | 41 | 0.036647 | 0.00012523
2015 | 2014-10-07 | B | 10 | 0.0099086 | 3.0544e-05
2015 | 2014-10-07 | C | 6 | 0.0021259 | 1.8327e-05
2015 | 2014-10-07 | C | 66 | 0.069952 | 0.00020159
2015 | 2014-10-07 | C | 1 | 0.0009036 | 3.0544e-06
2015 | 2014-10-07 | C | 1 | 0.0052603 | 3.0544e-06
2015 | 2014-10-07 | C | 8 | 0.00061088 | 2.4435e-05
2015 | 2014-10-07 | C | 1 | 0.0094215 | 3.0544e-06
2015 | 2014-10-07 | C | 1 | 0.00040929 | 3.0544e-06
2015 | 2014-10-07 | C | 1 | 0.008185 | 3.0544e-06
2015 | 2014-10-07 | C | 1 | 0.00038364 | 3.0544e-06
2015 | 2014-10-07 | C | 41 | 0.012783 | 0.00012523
2015 | 2014-10-07 | C | 35 | 0.041103 | 0.0001069
2015 | 2014-10-07 | C | 1 | 0.0092842 | 3.0544e-06
2015 | 2014-10-07 | C | 1 | 0.0040452 | 3.0544e-06
2015 | 2014-10-07 | B | 367 | 0.11083 | 0.001121
2015 | 2014-10-07 | C | 1 | 0.0034424 | 3.0544e-06
2015 | 2014-10-08 | C | 3 | 0.00035721 | 9.1633e-06
2015 | 2014-10-08 | C | 1 | 0.0053662 | 3.0544e-06
2015 | 2014-10-08 | B | 1 | 0.0007911 | 3.0544e-06
2015 | 2014-10-08 | C | 1 | 0.0024926 | 3.0544e-06
2015 | 2014-10-08 | B | 16 | 0.016616 | 4.8871e-05
2015 | 2014-10-08 | B | 9 | 0.0094647 | 2.749e-05
2015 | 2014-10-08 | B | 33 | 0.036426 | 0.0001008
2015 | 2014-10-08 | B | 10 | 0.011945 | 3.0544e-05
2015 | 2014-10-08 | B | 1 | 0.00092641 | 3.0544e-06
2015 | 2014-10-08 | B | 26 | 0.013651 | 7.9415e-05
2015 | 2014-10-08 | C | 88 | 0.043171 | 0.00026879
2015 | 2014-10-08 | C | 16 | 0.00016168 | 4.8871e-05
2015 | 2014-10-08 | C | 29 | 0.0024964 | 8.8578e-05
2015 | 2014-10-08 | C | 300 | 0.018789 | 0.00091633
2015 | 2014-10-08 | C | 1 | 0.0041575 | 3.0544e-06
2015 | 2014-10-08 | C | 66 | 0.016978 | 0.00020159
2015 | 2014-10-08 | C | 331 | 0.045806 | 0.001011
2015 | 2014-10-08 | C | 109 | 0.45131 | 0.00033293
2015 | 2014-10-08 | C | 1239 | 1.1219 | 0.0037844
2015 | 2014-10-08 | C | 40 | 0.011362 | 0.00012218
2015 | 2014-10-08 | C | 20 | 0.008133 | 6.1088e-05
2015 | 2014-10-08 | C | 211 | 0.084427 | 0.00064448
2015 | 2014-10-08 | C | 49 | 0.03598 | 0.00014967
2015 | 2014-10-08 | C | 43 | 0.28831 | 0.00013134
2015 | 2014-10-08 | C | 242 | 0.076612 | 0.00073917
2015 | 2014-10-08 | C | 5 | 0.018769 | 1.5272e-05
2015 | 2014-10-08 | C | 7 | 0.0072054 | 2.1381e-05
2015 | 2014-10-09 | C | 2 | 0.0015491 | 6.1088e-06
2015 | 2014-10-09 | B | 16 | 0.010104 | 4.8871e-05
2015 | 2014-10-09 | B | 42 | 0.046198 | 0.00012829
2015 | 2014-10-09 | B | 5 | 0.0075808 | 1.5272e-05
2015 | 2014-10-09 | B | 84 | 0.049061 | 0.00025657
2015 | 2014-10-09 | C | 6 | 0.0058828 | 1.8327e-05
2015 | 2014-10-09 | B | 16 | 0.011636 | 4.8871e-05
2015 | 2014-10-09 | C | 8 | 0.0074772 | 2.4435e-05
2015 | 2014-10-09 | B | 7 | 0.0065479 | 2.1381e-05
2015 | 2014-10-09 | C | 1 | 0.00076076 | 3.0544e-06
2015 | 2014-10-09 | C | 1 | 0.0045328 | 3.0544e-06
2015 | 2014-10-09 | C | 35 | 0.010075 | 0.0001069
2015 | 2014-10-09 | C | 141 | 0.0055342 | 0.00043067
2015 | 2014-10-09 | C | 44 | 0.033173 | 0.00013439
2015 | 2014-10-09 | C | 1 | 0.0010685 | 3.0544e-06
2015 | 2014-10-09 | C | 1 | 0.0013679 | 3.0544e-06
2015 | 2014-10-09 | C | 1 | 0.0025745 | 3.0544e-06
2015 | 2014-10-09 | C | 1 | 0.00091918 | 3.0544e-06
2015 | 2014-10-10 | C | 237 | 0.0426 | 0.0007239
2015 | 2014-10-10 | C | 2 | 0.0017803 | 6.1088e-06
2015 | 2014-10-10 | C | 1 | 0.018303 | 3.0544e-06
2015 | 2014-10-10 | B | 2 | 0.011937 | 6.1088e-06
2015 | 2014-10-10 | C | 2539 | 0.3278 | 0.0077552
2015 | 2014-10-10 | C | 10 | 0.012206 | 3.0544e-05
2015 | 2014-10-10 | B | 2 | 0.0015211 | 6.1088e-06
2015 | 2014-10-10 | C | 1 | 0.00098256 | 3.0544e-06
2015 | 2014-10-10 | C | 1 | 0.00020628 | 3.0544e-06
2015 | 2014-10-10 | C | 1 | 0.00021076 | 3.0544e-06
2015 | 2014-10-10 | C | 1 | 0.00040395 | 3.0544e-06
2015 | 2014-10-10 | B | 8 | 0.010148 | 2.4435e-05
2015 | 2014-10-11 | C | 1 | 0.0012753 | 3.0544e-06
2015 | 2014-10-11 | B | 78 | 0.086753 | 0.00023825
2015 | 2014-10-11 | C | 2 | 0.0035621 | 6.1088e-06
2015 | 2014-10-11 | C | 1 | 0.00015287 | 3.0544e-06
2015 | 2014-10-11 | B | 8 | 0.0083997 | 2.4435e-05
2015 | 2014-10-12 | C | 10 | 0.0054814 | 3.0544e-05
2015 | 2014-10-12 | B | 48 | 0.010312 | 0.00014661
2015 | 2014-10-12 | B | 2 | 0.0020281 | 6.1088e-06
2015 | 2014-10-12 | C | 328 | 0.033913 | 0.0010019
2015 | 2014-10-13 | B | 40 | 0.042241 | 0.00012218
2015 | 2014-10-13 | B | 1 | 0.00029358 | 3.0544e-06
2015 | 2014-10-13 | C | 1 | 0.00046051 | 3.0544e-06
2015 | 2014-10-13 | C | 2 | 0.0012946 | 6.1088e-06
2015 | 2014-10-13 | C | 94 | 0.035293 | 0.00028712
2015 | 2014-10-14 | C | 4 | 0.00046646 | 1.2218e-05
2015 | 2014-10-14 | B | 73 | 0.091419 | 0.00022297
2015 | 2014-10-14 | B | 38 | 0.049301 | 0.00011607
2015 | 2014-10-14 | B | 10 | 0.010613 | 3.0544e-05
2015 | 2014-10-14 | B | 20 | 0.018449 | 6.1088e-05
2015 | 2014-10-14 | C | 64 | 0.10735 | 0.00019548
2015 | 2014-10-14 | C | 9 | 0.0014432 | 2.749e-05
2015 | 2014-10-14 | B | 193 | 0.0096644 | 0.0005895
2015 | 2014-10-14 | C | 24 | 0.0030789 | 7.3306e-05
2015 | 2014-10-15 | B | 2 | 0.0022461 | 6.1088e-06
2015 | 2014-10-15 | B | 24 | 0.01884 | 7.3306e-05
2015 | 2014-10-15 | B | 8 | 0.0068932 | 2.4435e-05
2015 | 2014-10-15 | B | 7 | 0.0071334 | 2.1381e-05
2015 | 2014-10-15 | B | 3 | 0.0026024 | 9.1633e-06
2015 | 2014-10-15 | B | 15 | 0.014751 | 4.5816e-05
2015 | 2014-10-15 | C | 1415 | 0.56811 | 0.004322
2015 | 2014-10-15 | C | 11 | 0.0019347 | 3.3599e-05
2015 | 2014-10-16 | C | 1101 | 0.28863 | 0.0033629
2015 | 2014-10-16 | C | 33 | 0.00054593 | 0.0001008
2015 | 2014-10-16 | C | 1 | 0.0014732 | 3.0544e-06
2015 | 2014-10-16 | B | 2 | 0.0014313 | 6.1088e-06
2015 | 2014-10-16 | B | 59 | 0.041129 | 0.00018021
2015 | 2014-10-16 | B | 37 | 0.04125 | 0.00011301
2015 | 2014-10-16 | B | 86 | 0.087735 | 0.00026268
2015 | 2014-10-16 | B | 10 | 0.011583 | 3.0544e-05
2015 | 2014-10-16 | B | 4 | 0.0051559 | 1.2218e-05
2015 | 2014-10-16 | B | 13 | 0.014747 | 3.9708e-05
2015 | 2014-10-16 | B | 2 | 0.0018745 | 6.1088e-06
2015 | 2014-10-16 | C | 4 | 0.0019825 | 1.2218e-05
2015 | 2014-10-17 | B | 239 | 0.20421 | 0.00073001
2015 | 2014-10-17 | B | 5 | 0.0056812 | 1.5272e-05
2015 | 2014-10-17 | B | 2 | 0.00096764 | 6.1088e-06
2015 | 2014-10-17 | B | 118 | 0.093508 | 0.00036042
2015 | 2014-10-17 | C | 1 | 0.0040761 | 3.0544e-06
2015 | 2014-10-17 | C | 196 | 0.076781 | 0.00059867
2015 | 2014-10-18 | C | 466 | 0.16165 | 0.0014234
2015 | 2014-10-18 | C | 371 | 0.011292 | 0.0011332
2015 | 2014-10-18 | C | 1552 | 0.24059 | 0.0047405
2015 | 2014-10-18 | C | 1099 | 0.30007 | 0.0033568
2015 | 2014-10-18 | C | 5 | 0.0012485 | 1.5272e-05
2015 | 2014-10-18 | C | 1 | 0.00013261 | 3.0544e-06
2015 | 2014-10-18 | C | 466 | 0.13148 | 0.0014234
2015 | 2014-10-18 | C | 907 | 0.048416 | 0.0027704
2015 | 2014-10-18 | C | 119 | 0.0040043 | 0.00036348
2015 | 2014-10-19 | C | 270 | 0.067973 | 0.00082469
2015 | 2014-10-19 | C | 19 | 0.0034565 | 5.8034e-05
2015 | 2014-10-19 | C | 215 | 0.066003 | 0.0006567
2015 | 2014-10-19 | B | 43 | 0.011779 | 0.00013134
2015 | 2014-10-20 | C | 215 | 0.044122 | 0.0006567
2015 | 2014-10-20 | B | 71 | 0.013012 | 0.00021686
2015 | 2014-10-20 | B | 5 | 0.0030005 | 1.5272e-05
2015 | 2014-10-20 | B | 1 | 0.00073825 | 3.0544e-06
2015 | 2014-10-20 | B | 4 | 0.0012462 | 1.2218e-05
2015 | 2014-10-20 | C | 31 | 0.037212 | 9.4687e-05
2015 | 2014-10-20 | C | 26 | 0.0060267 | 7.9415e-05
2015 | 2014-10-20 | C | 277 | 0.049193 | 0.00084608
2015 | 2014-10-21 | B | 47 | 0.018562 | 0.00014356
2015 | 2014-10-21 | B | 12 | 0.015061 | 3.6653e-05
2015 | 2014-10-21 | B | 5 | 0.006101 | 1.5272e-05
2015 | 2014-10-21 | B | 24 | 0.023139 | 7.3306e-05
2015 | 2014-10-21 | B | 10 | 0.013378 | 3.0544e-05
2015 | 2014-10-21 | B | 3 | 0.0021673 | 9.1633e-06
2015 | 2014-10-21 | B | 15 | 0.015158 | 4.5816e-05
2015 | 2014-10-21 | B | 3 | 0.0027398 | 9.1633e-06
2015 | 2014-10-21 | B | 175 | 0.15817 | 0.00053452
2015 | 2014-10-22 | B | 428 | 0.034015 | 0.0013073
2015 | 2014-10-22 | B | 12 | 0.014405 | 3.6653e-05
2015 | 2014-10-22 | B | 3 | 0.0031262 | 9.1633e-06
2015 | 2014-10-22 | B | 15 | 0.016366 | 4.5816e-05
2015 | 2014-10-22 | B | 13 | 0.010007 | 3.9708e-05
2015 | 2014-10-22 | B | 110 | 0.082907 | 0.00033599
2015 | 2014-10-22 | C | 93 | 0.03778 | 0.00028406
2015 | 2014-10-22 | C | 6 | 0.00053941 | 1.8327e-05
2015 | 2014-10-22 | C | 1 | 0.00070221 | 3.0544e-06
2015 | 2014-10-22 | C | 35 | 0.0057729 | 0.0001069
2015 | 2014-10-23 | C | 1020 | 0.23063 | 0.0031155
2015 | 2014-10-23 | C | 1 | 0.00034199 | 3.0544e-06
2015 | 2014-10-23 | C | 1 | 0.00033461 | 3.0544e-06
2015 | 2014-10-23 | B | 9 | 0.0063483 | 2.749e-05
2015 | 2014-10-23 | C | 106 | 0.10564 | 0.00032377
2015 | 2014-10-23 | B | 15 | 0.0082928 | 4.5816e-05
2015 | 2014-10-23 | C | 30 | 0.031441 | 9.1633e-05
2015 | 2014-10-23 | B | 35 | 0.036134 | 0.0001069
2015 | 2014-10-23 | B | 3 | 0.0020342 | 9.1633e-06
2015 | 2014-10-23 | C | 1 | 0.00067569 | 3.0544e-06
2015 | 2014-10-23 | B | 37 | 0.028366 | 0.00011301
2015 | 2014-10-23 | C | 27 | 0.00099238 | 8.2469e-05
2015 | 2014-10-23 | C | 141 | 0.048086 | 0.00043067
2015 | 2014-10-23 | C | 1 | 0.022219 | 3.0544e-06
2015 | 2014-10-23 | C | 32 | 0.00779 | 9.7742e-05
2015 | 2014-10-24 | C | 31 | 0.010605 | 9.4687e-05
2015 | 2014-10-24 | B | 30 | 0.041523 | 9.1633e-05
2015 | 2014-10-24 | B | 40 | 0.028787 | 0.00012218
2015 | 2014-10-24 | B | 44 | 0.081604 | 0.00013439
2015 | 2014-10-24 | B | 552 | 0.22037 | 0.001686
2015 | 2014-10-25 | C | 8 | 0.00433 | 2.4435e-05
2015 | 2014-10-25 | C | 509 | 0.14837 | 0.0015547
2015 | 2014-10-26 | C | 132 | 0.043273 | 0.00040318
2015 | 2014-10-26 | C | 126 | 0.010654 | 0.00038486
2015 | 2014-10-26 | C | 1 | 0.00056863 | 3.0544e-06
2015 | 2014-10-26 | C | 323 | 0.052919 | 0.00098658
2015 | 2014-10-26 | C | 42 | 0.0097639 | 0.00012829
2015 | 2014-10-26 | C | 80 | 0.086852 | 0.00024435
2015 | 2014-10-27 | C | 1 | 0.00044264 | 3.0544e-06
2015 | 2014-10-27 | C | 126 | 0.057744 | 0.00038486
2015 | 2014-10-27 | C | 6 | 0.0010403 | 1.8327e-05
2015 | 2014-10-27 | C | 8 | 0.001774 | 2.4435e-05
2015 | 2014-10-27 | C | 231 | 0.044622 | 0.00070557
2015 | 2014-10-28 | C | 12 | 0.012535 | 3.6653e-05
2015 | 2014-10-28 | B | 83 | 0.097786 | 0.00025352
2015 | 2014-10-28 | B | 97 | 0.074972 | 0.00029628
2015 | 2014-10-28 | C | 6 | 0.0021076 | 1.8327e-05
2015 | 2014-10-28 | B | 41 | 0.038947 | 0.00012523
2015 | 2014-10-28 | C | 1 | 0.00029765 | 3.0544e-06
2015 | 2014-10-28 | C | 6 | 0.0031115 | 1.8327e-05
2015 | 2014-10-28 | C | 2 | 0.00022603 | 6.1088e-06
2015 | 2014-10-28 | B | 4 | 0.0011369 | 1.2218e-05
2015 | 2014-10-28 | C | 3 | 0.0016461 | 9.1633e-06
2015 | 2014-10-28 | C | 1316 | 0.027087 | 0.0040196
2015 | 2014-10-29 | C | 7 | 0.0086379 | 2.1381e-05
2015 | 2014-10-29 | C | 817 | 0.040528 | 0.0024955
2015 | 2014-10-29 | C | 1 | 0.00038201 | 3.0544e-06
2015 | 2014-10-29 | C | 1 | 0.00039346 | 3.0544e-06
2015 | 2014-10-29 | C | 250 | 0.087903 | 0.00076361
2015 | 2014-10-29 | C | 64 | 0.077936 | 0.00019548
2015 | 2014-10-29 | B | 5 | 0.001405 | 1.5272e-05
2015 | 2014-10-29 | B | 2 | 0.0016616 | 6.1088e-06
2015 | 2014-10-29 | B | 15 | 0.016524 | 4.5816e-05
2015 | 2014-10-29 | B | 13 | 0.0090136 | 3.9708e-05
2015 | 2014-10-29 | B | 4 | 0.0029145 | 1.2218e-05
2015 | 2014-10-29 | C | 416 | 0.51125 | 0.0012706
2015 | 2014-10-29 | C | 294 | 0.06005 | 0.000898
2015 | 2014-10-29 | C | 195 | 0.0098872 | 0.00059561
2015 | 2014-10-29 | B | 183 | 0.059762 | 0.00055896
2015 | 2014-10-29 | C | 1 | 0.0044198 | 3.0544e-06
2015 | 2014-10-29 | C | 162 | 0.02338 | 0.00049482
2015 | 2014-10-29 | C | 59 | 0.022187 | 0.00018021
2015 | 2014-10-29 | C | 277 | 0.063903 | 0.00084608
2015 | 2014-10-29 | C | 1 | 0.0015503 | 3.0544e-06
2015 | 2014-10-29 | C | 511 | 0.1212 | 0.0015608
2015 | 2014-10-29 | C | 1 | 0.00038084 | 3.0544e-06
2015 | 2014-10-29 | C | 2 | 0.0004825 | 6.1088e-06
2015 | 2014-10-29 | C | 1 | 0.00027856 | 3.0544e-06
2015 | 2014-10-29 | C | 1 | 0.00041092 | 3.0544e-06
2015 | 2014-10-29 | C | 69 | 0.065664 | 0.00021076
2015 | 2014-10-29 | C | 462 | 0.11327 | 0.0014111
2015 | 2014-10-29 | C | 377 | 0.014087 | 0.0011515
2015 | 2014-10-29 | C | 2 | 0.0068786 | 6.1088e-06
2015 | 2014-10-30 | C | 669 | 0.090898 | 0.0020434
2015 | 2014-10-30 | C | 2 | 0.0023168 | 6.1088e-06
2015 | 2014-10-30 | C | 3 | 0.0032163 | 9.1633e-06
2015 | 2014-10-30 | C | 3 | 0.0035462 | 9.1633e-06
2015 | 2014-10-30 | C | 3 | 0.0048107 | 9.1633e-06
2015 | 2014-10-30 | C | 2 | 0.018224 | 6.1088e-06
2015 | 2014-10-30 | C | 1 | 0.00055321 | 3.0544e-06
2015 | 2014-10-30 | C | 3 | 0.0014166 | 9.1633e-06
2015 | 2014-10-30 | C | 2 | 0.0025352 | 6.1088e-06
2015 | 2014-10-30 | C | 1 | 0.00080479 | 3.0544e-06
2015 | 2014-10-30 | C | 1 | 0.00032764 | 3.0544e-06
2015 | 2014-10-30 | C | 1 | 0.00069407 | 3.0544e-06
2015 | 2014-10-30 | B | 8 | 0.01019 | 2.4435e-05
2015 | 2014-10-30 | C | 1 | 0.00029974 | 3.0544e-06
2015 | 2014-10-30 | B | 16 | 0.019868 | 4.8871e-05
2015 | 2014-10-30 | B | 29 | 0.019576 | 8.8578e-05
2015 | 2014-10-30 | B | 13 | 0.0050402 | 3.9708e-05
2015 | 2014-10-30 | B | 10 | 0.013194 | 3.0544e-05
2015 | 2014-10-30 | B | 12 | 0.0090533 | 3.6653e-05
2015 | 2014-10-30 | B | 82 | 0.0077643 | 0.00025046
2015 | 2014-10-30 | C | 1 | 0.00096209 | 3.0544e-06
2015 | 2014-10-30 | B | 22 | 0.0097436 | 6.7197e-05
2015 | 2014-10-30 | B | 3 | 0.0016402 | 9.1633e-06
2015 | 2014-10-30 | C | 1 | 0.00020745 | 3.0544e-06
2015 | 2014-10-30 | B | 4 | 0.00090411 | 1.2218e-05
2015 | 2014-10-30 | C | 341 | 0.014903 | 0.0010416
2015 | 2014-10-30 | C | 1 | 0.00042477 | 3.0544e-06
2015 | 2014-10-30 | C | 1 | 0.00020541 | 3.0544e-06
2015 | 2014-10-30 | C | 1 | 0.00064677 | 3.0544e-06
2015 | 2014-10-30 | C | 3 | 0.0016129 | 9.1633e-06
2015 | 2014-10-30 | B | 5 | 0.0015425 | 1.5272e-05
2015 | 2014-10-30 | C | 3 | 0.001442 | 9.1633e-06
2015 | 2014-10-30 | C | 362 | 0.10652 | 0.0011057
2015 | 2014-10-30 | C | 1 | 0.00066602 | 3.0544e-06
2015 | 2014-10-30 | C | 1 | 0.00050042 | 3.0544e-06
2015 | 2014-10-30 | C | 1 | 0.0008868 | 3.0544e-06
2015 | 2014-10-30 | C | 1 | 0.00086511 | 3.0544e-06
2015 | 2014-10-30 | B | 3 | 0.0023327 | 9.1633e-06
2015 | 2014-10-30 | C | 165 | 0.0081282 | 0.00050398
2015 | 2014-10-30 | C | 1 | 0.00057764 | 3.0544e-06
2015 | 2014-10-30 | C | 1 | 0.00045857 | 3.0544e-06
2015 | 2014-10-30 | C | 131 | 0.0076025 | 0.00040013
2015 | 2014-10-30 | C | 1 | 0.00038145 | 3.0544e-06
2015 | 2014-10-30 | C | 10 | 0.0059246 | 3.0544e-05
2015 | 2014-10-31 | C | 1303 | 0.37973 | 0.0039799
2015 | 2014-10-31 | B | 32 | 0.030752 | 9.7742e-05
2015 | 2014-10-31 | B | 1 | 0.00082469 | 3.0544e-06
2015 | 2014-10-31 | B | 141 | 0.11505 | 0.00043067
2015 | 2014-10-31 | C | 447 | 0.12134 | 0.0013653
2015 | 2014-10-31 | C | 31 | 0.019386 | 9.4687e-05
2015 | 2014-10-31 | C | 7 | 0.024874 | 2.1381e-05
2015 | 2014-11-01 | C | 995 | 0.16368 | 0.0030392
2015 | 2014-11-01 | B | 76 | 0.067319 | 0.00023214
2015 | 2014-11-01 | B | 11 | 0.016667 | 3.3599e-05
2015 | 2014-11-01 | B | 47 | 0.0081948 | 0.00014356
2015 | 2014-11-01 | B | 8 | 0.0075505 | 2.4435e-05
2015 | 2014-11-02 | C | 2 | 0.0002303 | 6.1088e-06
2015 | 2014-11-02 | C | 31 | 0.022021 | 9.4687e-05
2015 | 2014-11-02 | C | 50 | 0.0066841 | 0.00015272
2015 | 2014-11-02 | B | 121 | 0.073899 | 0.00036959
2015 | 2014-11-02 | C | 175 | 0.0274 | 0.00053452
2015 | 2014-11-02 | C | 9 | 0.020989 | 2.749e-05
2015 | 2014-11-02 | C | 1 | 0.00045888 | 3.0544e-06
2015 | 2014-11-02 | C | 2 | 0.00015496 | 6.1088e-06
2015 | 2014-11-03 | C | 293 | 0.039691 | 0.00089495
2015 | 2014-11-03 | C | 4 | 0.0019817 | 1.2218e-05
2015 | 2014-11-03 | B | 1 | 0.00053982 | 3.0544e-06
2015 | 2014-11-03 | C | 2 | 0.00042278 | 6.1088e-06
2015 | 2014-11-03 | C | 1 | 0.0011357 | 3.0544e-06
2015 | 2014-11-03 | C | 10 | 0.0029825 | 3.0544e-05
2015 | 2014-11-03 | C | 1 | 0.00014173 | 3.0544e-06
2015 | 2014-11-04 | B | 1 | 0.00036959 | 3.0544e-06
2015 | 2014-11-04 | B | 4 | 0.0037987 | 1.2218e-05
2015 | 2014-11-04 | B | 12 | 0.0088456 | 3.6653e-05
2015 | 2014-11-04 | B | 15 | 0.015222 | 4.5816e-05
2015 | 2014-11-04 | B | 45 | 0.048469 | 0.00013745
2015 | 2014-11-04 | B | 143 | 0.13054 | 0.00043678
2015 | 2014-11-04 | B | 14 | 0.011293 | 4.2762e-05
2015 | 2014-11-04 | B | 68 | 0.037127 | 0.0002077
2015 | 2014-11-04 | C | 1 | 0.00061598 | 3.0544e-06
2015 | 2014-11-04 | C | 27 | 0.0027319 | 8.2469e-05
2015 | 2014-11-05 | C | 94 | 0.0034454 | 0.00028712
2015 | 2014-11-05 | C | 416 | 0.17671 | 0.0012706
2015 | 2014-11-05 | B | 162 | 0.19513 | 0.00049482
2015 | 2014-11-05 | B | 105 | 0.12688 | 0.00032071
2015 | 2014-11-05 | C | 908 | 0.012928 | 0.0027734
2015 | 2014-11-05 | B | 15 | 0.014416 | 4.5816e-05
2015 | 2014-11-05 | B | 1 | 0.0012873 | 3.0544e-06
2015 | 2014-11-05 | C | 1 | 0.00044645 | 3.0544e-06
2015 | 2014-11-05 | C | 1 | 0.00040125 | 3.0544e-06
2015 | 2014-11-05 | C | 1 | 0.00092183 | 3.0544e-06
2015 | 2014-11-05 | C | 3 | 0.00067157 | 9.1633e-06
2015 | 2014-11-05 | C | 106 | 0.028226 | 0.00032377
2015 | 2014-11-05 | C | 4 | 0.0018435 | 1.2218e-05
2015 | 2014-11-05 | C | 2 | 0.0020821 | 6.1088e-06
2015 | 2014-11-05 | C | 335 | 0.038776 | 0.0010232
2015 | 2014-11-05 | C | 335 | 0.056806 | 0.0010232
2015 | 2014-11-05 | C | 1 | 0.0025183 | 3.0544e-06
2015 | 2014-11-06 | C | 53 | 0.012639 | 0.00016188
2015 | 2014-11-06 | C | 24 | 0.033679 | 7.3306e-05
2015 | 2014-11-06 | B | 84 | 0.087539 | 0.00025657
2015 | 2014-11-06 | B | 10 | 0.011882 | 3.0544e-05
2015 | 2014-11-06 | C | 303 | 0.091624 | 0.00092549
2015 | 2014-11-06 | B | 15 | 0.016157 | 4.5816e-05
2015 | 2014-11-06 | B | 26 | 0.023507 | 7.9415e-05
2015 | 2014-11-06 | B | 43 | 0.048898 | 0.00013134
2015 | 2014-11-06 | B | 54 | 0.041298 | 0.00016494
2015 | 2014-11-06 | C | 46 | 0.097548 | 0.0001405
2015 | 2014-11-06 | C | 137 | 0.065119 | 0.00041846
2015 | 2014-11-06 | C | 1 | 0.00058528 | 3.0544e-06
2015 | 2014-11-06 | C | 149 | 0.011294 | 0.00045511
2015 | 2014-11-06 | C | 1 | 0.00052485 | 3.0544e-06
2015 | 2014-11-06 | C | 1 | 0.00049685 | 3.0544e-06
2015 | 2014-11-07 | C | 460 | 0.077312 | 0.001405
2015 | 2014-11-07 | C | 446 | 0.06359 | 0.0013623
2015 | 2014-11-07 | C | 107 | 0.041763 | 0.00032682
2015 | 2014-11-07 | C | 29 | 0.00084445 | 8.8578e-05
2015 | 2014-11-07 | B | 132 | 0.071474 | 0.00040318
2015 | 2014-11-07 | B | 1 | 0.00071779 | 3.0544e-06
2015 | 2014-11-07 | B | 39 | 0.041693 | 0.00011912
2015 | 2014-11-07 | C | 43 | 0.044516 | 0.00013134
2015 | 2014-11-07 | B | 56 | 0.063195 | 0.00017105
2015 | 2014-11-07 | C | 14 | 0.0022236 | 4.2762e-05
2015 | 2014-11-07 | C | 4404 | 0.78682 | 0.013452
2015 | 2014-11-07 | C | 1 | 0.00028966 | 3.0544e-06
2015 | 2014-11-08 | C | 1336 | 0.15286 | 0.0040807
2015 | 2014-11-08 | C | 120 | 0.023825 | 0.00036653
2015 | 2014-11-08 | B | 121 | 0.024159 | 0.00036959
2015 | 2014-11-08 | C | 1 | 0.00034647 | 3.0544e-06
2015 | 2014-11-08 | B | 75 | 0.087582 | 0.00022908
2015 | 2014-11-08 | B | 10 | 0.0054924 | 3.0544e-05
2015 | 2014-11-08 | B | 25 | 0.0040166 | 7.6361e-05
2015 | 2014-11-08 | C | 1 | 0.0003675 | 3.0544e-06
2015 | 2014-11-09 | C | 1 | 0.00034474 | 3.0544e-06
2015 | 2014-11-09 | C | 2 | 0.00046229 | 6.1088e-06
2015 | 2014-11-09 | C | 9 | 0.0013236 | 2.749e-05
2015 | 2014-11-09 | B | 31 | 0.0065145 | 9.4687e-05
2015 | 2014-11-10 | C | 454 | 0.054082 | 0.0013867
2015 | 2014-11-10 | C | 5424 | 0.94863 | 0.016567
2015 | 2014-11-10 | B | 5 | 0.0052648 | 1.5272e-05
2015 | 2014-11-10 | B | 7 | 0.0090263 | 2.1381e-05
2015 | 2014-11-10 | B | 29 | 0.012224 | 8.8578e-05
2015 | 2014-11-10 | C | 76 | 0.11202 | 0.00023214
2015 | 2014-11-10 | B | 1 | 0.00040609 | 3.0544e-06
2015 | 2014-11-10 | B | 37 | 0.029591 | 0.00011301
2015 | 2014-11-10 | C | 1 | 0.00078015 | 3.0544e-06
2015 | 2014-11-10 | C | 253 | 0.070945 | 0.00077277
2015 | 2014-11-11 | C | 1 | 0.00057668 | 3.0544e-06
2015 | 2014-11-11 | B | 497 | 0.62038 | 0.001518
2015 | 2014-11-11 | B | 47 | 0.050722 | 0.00014356
2015 | 2014-11-11 | C | 48 | 0.0042469 | 0.00014661
2015 | 2014-11-11 | B | 15 | 0.007859 | 4.5816e-05
2015 | 2014-11-11 | B | 1 | 0.00017675 | 3.0544e-06
2015 | 2014-11-11 | B | 94 | 0.05139 | 0.00028712
2015 | 2014-11-11 | B | 8 | 0.0077204 | 2.4435e-05
2015 | 2014-11-11 | B | 73 | 0.033001 | 0.00022297
2015 | 2014-11-11 | B | 2 | 0.00031634 | 6.1088e-06
2015 | 2014-11-11 | B | 10 | 0.0045765 | 3.0544e-05
2015 | 2014-11-11 | B | 4 | 0.00073754 | 1.2218e-05
2015 | 2014-11-11 | C | 40 | 0.012703 | 0.00012218
2015 | 2014-11-11 | C | 3 | 0.0021315 | 9.1633e-06
2015 | 2014-11-11 | C | 1 | 0.0023013 | 3.0544e-06
2015 | 2014-11-12 | C | 7 | 0.0024503 | 2.1381e-05
2015 | 2014-11-12 | C | 12 | 0.0077735 | 3.6653e-05
2015 | 2014-11-12 | C | 1 | 0.00072879 | 3.0544e-06
2015 | 2014-11-12 | C | 35 | 0.0053532 | 0.0001069
2015 | 2014-11-12 | C | 5 | 0.00027398 | 1.5272e-05
2015 | 2014-11-12 | B | 4 | 0.0040441 | 1.2218e-05
2015 | 2014-11-12 | B | 37 | 0.052212 | 0.00011301
2015 | 2014-11-12 | B | 135 | 0.10815 | 0.00041235
2015 | 2014-11-12 | B | 75 | 0.14156 | 0.00022908
2015 | 2014-11-12 | B | 20 | 0.017328 | 6.1088e-05
2015 | 2014-11-12 | B | 3 | 0.002355 | 9.1633e-06
2015 | 2014-11-12 | B | 46 | 0.22706 | 0.0001405
2015 | 2014-11-12 | B | 1 | 0.00034072 | 3.0544e-06
2015 | 2014-11-12 | C | 1 | 0.00032509 | 3.0544e-06
2015 | 2014-11-12 | C | 10 | 0.0045816 | 3.0544e-05
2015 | 2014-11-12 | C | 1 | 0.00079079 | 3.0544e-06
2015 | 2014-11-12 | C | 1097 | 0.050251 | 0.0033507
2015 | 2014-11-12 | C | 41 | 0.00995 | 0.00012523
2015 | 2014-11-13 | B | 8 | 0.008308 | 2.4435e-05
2015 | 2014-11-13 | B | 32 | 0.039242 | 9.7742e-05
2015 | 2014-11-13 | B | 54 | 0.061357 | 0.00016494
2015 | 2014-11-13 | B | 110 | 0.14039 | 0.00033599
2015 | 2014-11-13 | B | 24 | 0.026013 | 7.3306e-05
2015 | 2014-11-13 | C | 80 | 0.0094117 | 0.00024435
2015 | 2014-11-13 | B | 22 | 0.022981 | 6.7197e-05
2015 | 2014-11-13 | C | 1 | 0.00039682 | 3.0544e-06
2015 | 2014-11-13 | C | 5 | 0.018425 | 1.5272e-05
2015 | 2014-11-14 | B | 42 | 0.046439 | 0.00012829
2015 | 2014-11-14 | B | 32 | 0.032755 | 9.7742e-05
2015 | 2014-11-14 | B | 32 | 0.014243 | 9.7742e-05
2015 | 2014-11-14 | C | 4 | 0.0019172 | 1.2218e-05
2015 | 2014-11-14 | B | 2 | 0.00068419 | 6.1088e-06
2015 | 2014-11-14 | C | 3 | 0.016271 | 9.1633e-06
2015 | 2014-11-14 | B | 19 | 0.011136 | 5.8034e-05
2015 | 2014-11-14 | B | 63 | 0.0053816 | 0.00019243
2015 | 2014-11-14 | C | 64 | 0.12826 | 0.00019548
2015 | 2014-11-15 | C | 53 | 0.02709 | 0.00016188
2015 | 2014-11-15 | C | 630 | 0.085276 | 0.0019243
2015 | 2014-11-15 | C | 303 | 0.084852 | 0.00092549
2015 | 2014-11-15 | C | 29 | 0.030182 | 8.8578e-05
2015 | 2014-11-15 | C | 192 | 0.024454 | 0.00058645
2015 | 2014-11-15 | C | 116 | 0.05734 | 0.00035431
2015 | 2014-11-15 | C | 178 | 0.063193 | 0.00054369
2015 | 2014-11-15 | C | 3 | 0.0023733 | 9.1633e-06
2015 | 2014-11-15 | C | 47 | 0.0089186 | 0.00014356
2015 | 2014-11-15 | C | 196 | 0.19901 | 0.00059867
2015 | 2014-11-15 | C | 176 | 0.25737 | 0.00053758
2015 | 2014-11-15 | C | 251 | 0.2875 | 0.00076666
2015 | 2014-11-15 | B | 243 | 0.041565 | 0.00074222
2015 | 2014-11-15 | C | 75 | 0.084574 | 0.00022908
2015 | 2014-11-15 | C | 1 | 0.0090124 | 3.0544e-06
2015 | 2014-11-15 | C | 148 | 0.057221 | 0.00045205
2015 | 2014-11-15 | C | 132 | 0.0064913 | 0.00040318
2015 | 2014-11-15 | C | 399 | 0.11607 | 0.0012187
2015 | 2014-11-15 | C | 584 | 0.14735 | 0.0017838
2015 | 2014-11-15 | C | 32 | 0.01906 | 9.7742e-05
2015 | 2014-11-15 | C | 33 | 0.053019 | 0.0001008
2015 | 2014-11-15 | C | 528 | 0.20219 | 0.0016127
2015 | 2014-11-15 | C | 1 | 0.0015118 | 3.0544e-06
2015 | 2014-11-15 | C | 229 | 0.068501 | 0.00069946
2015 | 2014-11-15 | C | 1 | 0.00097894 | 3.0544e-06
2015 | 2014-11-15 | C | 67 | 0.0013793 | 0.00020465
2015 | 2014-11-15 | C | 1 | 0.00079318 | 3.0544e-06
2015 | 2014-11-15 | C | 40 | 0.013806 | 0.00012218
2015 | 2014-11-15 | C | 176 | 0.10412 | 0.00053758
2015 | 2014-11-15 | C | 26 | 0.0054796 | 7.9415e-05
2015 | 2014-11-15 | C | 431 | 0.17894 | 0.0013165
2015 | 2014-11-15 | C | 658 | 0.10285 | 0.0020098
2015 | 2014-11-15 | C | 1 | 0.00051823 | 3.0544e-06
2015 | 2014-11-15 | C | 1 | 0.0036011 | 3.0544e-06
2015 | 2014-11-15 | C | 3 | 0.0092645 | 9.1633e-06
2015 | 2014-11-16 | C | 4 | 0.0057783 | 1.2218e-05
2015 | 2014-11-16 | C | 228 | 0.10902 | 0.00069641
2015 | 2014-11-16 | B | 1 | 9.7131e-05 | 3.0544e-06
2015 | 2014-11-16 | C | 85 | 0.043473 | 0.00025963
2015 | 2014-11-16 | C | 11 | 0.0019683 | 3.3599e-05
2015 | 2014-11-16 | C | 84 | 0.034637 | 0.00025657
2015 | 2014-11-17 | C | 1 | 0.00054852 | 3.0544e-06
2015 | 2014-11-17 | B | 32 | 0.022692 | 9.7742e-05
2015 | 2014-11-17 | B | 91 | 0.10469 | 0.00027795
2015 | 2014-11-17 | B | 26 | 0.021159 | 7.9415e-05
2015 | 2014-11-17 | B | 14 | 0.0088125 | 4.2762e-05
2015 | 2014-11-17 | C | 235 | 0.049534 | 0.00071779
2015 | 2014-11-17 | B | 17 | 0.013054 | 5.1925e-05
2015 | 2014-11-17 | C | 478 | 0.14501 | 0.00146
2015 | 2014-11-17 | C | 15 | 0.0024191 | 4.5816e-05
2015 | 2014-11-17 | C | 56 | 0.0072125 | 0.00017105
2015 | 2014-11-17 | C | 19 | 0.031524 | 5.8034e-05
2015 | 2014-11-17 | C | 1 | 0.0018711 | 3.0544e-06
2015 | 2014-11-17 | C | 1 | 0.00067559 | 3.0544e-06
2015 | 2014-11-17 | C | 31 | 0.011647 | 9.4687e-05
2015 | 2014-11-18 | C | 416 | 0.052793 | 0.0012706
2015 | 2014-11-18 | B | 43 | 0.026531 | 0.00013134
2015 | 2014-11-18 | B | 103 | 0.097134 | 0.00031461
2015 | 2014-11-18 | C | 231 | 0.032774 | 0.00070557
2015 | 2014-11-18 | B | 48 | 0.065321 | 0.00014661
2015 | 2014-11-18 | B | 29 | 0.03247 | 8.8578e-05
2015 | 2014-11-18 | C | 631 | 0.074877 | 0.0019273
2015 | 2014-11-18 | B | 7 | 0.00083992 | 2.1381e-05
2015 | 2014-11-18 | B | 4 | 0.0032621 | 1.2218e-05
2015 | 2014-11-18 | B | 41 | 0.029277 | 0.00012523
2015 | 2014-11-18 | B | 40 | 0.033065 | 0.00012218
2015 | 2014-11-18 | C | 7 | 0.003265 | 2.1381e-05
2015 | 2014-11-18 | C | 3 | 0.0053137 | 9.1633e-06
2015 | 2014-11-18 | C | 8 | 0.003388 | 2.4435e-05
2015 | 2014-11-18 | C | 233 | 0.037719 | 0.00071168
2015 | 2014-11-18 | C | 16 | 0.0063111 | 4.8871e-05
2015 | 2014-11-18 | C | 207 | 0.0098528 | 0.00063227
2015 | 2014-11-18 | C | 941 | 0.093081 | 0.0028742
2015 | 2014-11-18 | C | 19 | 0.0017362 | 5.8034e-05
2015 | 2014-11-18 | C | 111 | 0.034857 | 0.00033904
2015 | 2014-11-18 | C | 26 | 0.0048853 | 7.9415e-05
2015 | 2014-11-18 | B | 1 | 0.00034612 | 3.0544e-06
2015 | 2014-11-19 | C | 1 | 0.0002188 | 3.0544e-06
2015 | 2014-11-19 | B | 1 | 8.5727e-05 | 3.0544e-06
2015 | 2014-11-19 | C | 121 | 0.064033 | 0.00036959
2015 | 2014-11-19 | C | 292 | 0.18498 | 0.00089189
2015 | 2014-11-19 | C | 69 | 0.0055881 | 0.00021076
2015 | 2014-11-19 | B | 57 | 0.015549 | 0.0001741
2015 | 2014-11-19 | B | 12 | 0.013598 | 3.6653e-05
2015 | 2014-11-19 | B | 32 | 0.025888 | 9.7742e-05
2015 | 2014-11-19 | B | 22 | 0.026005 | 6.7197e-05
2015 | 2014-11-19 | B | 1 | 0.0015598 | 3.0544e-06
2015 | 2014-11-19 | B | 2 | 0.001967 | 6.1088e-06
2015 | 2014-11-19 | C | 3 | 0.00054995 | 9.1633e-06
2015 | 2014-11-19 | C | 1 | 0.0011136 | 3.0544e-06
2015 | 2014-11-19 | C | 24 | 0.026715 | 7.3306e-05
2015 | 2014-11-19 | C | 238 | 0.055981 | 0.00072695
2015 | 2014-11-19 | C | 4 | 0.001542 | 1.2218e-05
2015 | 2014-11-19 | C | 19 | 0.013375 | 5.8034e-05
2015 | 2014-11-19 | C | 1 | 0.00041245 | 3.0544e-06
2015 | 2014-11-19 | C | 69 | 0.012759 | 0.00021076
2015 | 2014-11-19 | C | 1 | 0.00028345 | 3.0544e-06
2015 | 2014-11-19 | C | 238 | 0.031259 | 0.00072695
2015 | 2014-11-19 | C | 9 | 0.0065851 | 2.749e-05
2015 | 2014-11-19 | C | 37 | 0.0071368 | 0.00011301
2015 | 2014-11-19 | C | 14 | 0.0012993 | 4.2762e-05
2015 | 2014-11-19 | C | 8 | 0.001404 | 2.4435e-05
2015 | 2014-11-19 | C | 444 | 0.14695 | 0.0013562
2015 | 2014-11-20 | C | 42 | 0.013699 | 0.00012829
2015 | 2014-11-20 | C | 19 | 0.0018581 | 5.8034e-05
2015 | 2014-11-20 | C | 24 | 0.0050154 | 7.3306e-05
2015 | 2014-11-20 | B | 2 | 0.001967 | 6.1088e-06
2015 | 2014-11-20 | B | 39 | 0.05027 | 0.00011912
2015 | 2014-11-20 | B | 15 | 0.018739 | 4.5816e-05
2015 | 2014-11-20 | B | 646 | 0.69472 | 0.0019732
2015 | 2014-11-20 | B | 6 | 0.0054466 | 1.8327e-05
2015 | 2014-11-20 | B | 29 | 0.030404 | 8.8578e-05
2015 | 2014-11-20 | C | 224 | 0.016335 | 0.00068419
2015 | 2014-11-20 | C | 31 | 0.0025566 | 9.4687e-05
2015 | 2014-11-20 | B | 7 | 0.00498 | 2.1381e-05
2015 | 2014-11-20 | B | 39 | 0.003117 | 0.00011912
2015 | 2014-11-20 | C | 90 | 0.004884 | 0.0002749
2015 | 2014-11-21 | C | 1184 | 0.48844 | 0.0036164
2015 | 2014-11-21 | C | 121 | 0.089128 | 0.00036959
2015 | 2014-11-21 | C | 2 | 0.0024598 | 6.1088e-06
2015 | 2014-11-21 | B | 32 | 0.039222 | 9.7742e-05
2015 | 2014-11-21 | B | 3 | 0.0027035 | 9.1633e-06
2015 | 2014-11-21 | C | 1 | 0.00077537 | 3.0544e-06
2015 | 2014-11-21 | B | 7 | 0.0062678 | 2.1381e-05
2015 | 2014-11-21 | B | 89 | 0.08424 | 0.00027184
2015 | 2014-11-21 | C | 1 | 0.00035711 | 3.0544e-06
2015 | 2014-11-21 | C | 599 | 0.0036592 | 0.0018296
2015 | 2014-11-21 | C | 2 | 0.00068114 | 6.1088e-06
2015 | 2014-11-22 | C | 1 | 0.00069946 | 3.0544e-06
2015 | 2014-11-22 | B | 1 | 0.00080331 | 3.0544e-06
2015 | 2014-11-22 | C | 438 | 0.26054 | 0.0013378
2015 | 2014-11-22 | C | 61 | 0.018073 | 0.00018632
2015 | 2014-11-22 | C | 172 | 0.040453 | 0.00052536
2015 | 2014-11-22 | C | 70 | 0.014753 | 0.00021381
2015 | 2014-11-22 | C | 7 | 0.0038499 | 2.1381e-05
2015 | 2014-11-22 | C | 1 | 0.00091658 | 3.0544e-06
2015 | 2014-11-22 | C | 238 | 0.099733 | 0.00072695
2015 | 2014-11-22 | C | 7 | 0.00025657 | 2.1381e-05
2015 | 2014-11-22 | C | 6 | 0.0021645 | 1.8327e-05
2015 | 2014-11-22 | C | 113 | 0.054262 | 0.00034515
2015 | 2014-11-22 | C | 1 | 0.0008589 | 3.0544e-06
2015 | 2014-11-22 | C | 1 | 0.00021803 | 3.0544e-06
2015 | 2014-11-22 | C | 1 | 0.00043902 | 3.0544e-06
2015 | 2014-11-22 | C | 75 | 0.044041 | 0.00022908
2015 | 2014-11-22 | C | 4 | 0.0050345 | 1.2218e-05
2015 | 2014-11-22 | C | 90 | 0.055804 | 0.0002749
2015 | 2014-11-22 | C | 46 | 0.057018 | 0.0001405
2015 | 2014-11-22 | C | 1 | 0.00075454 | 3.0544e-06
2015 | 2014-11-22 | C | 904 | 0.034526 | 0.0027612
2015 | 2014-11-22 | C | 12 | 0.0020892 | 3.6653e-05
2015 | 2014-11-22 | C | 1 | 0.00079894 | 3.0544e-06
2015 | 2014-11-22 | C | 1 | 0.00024507 | 3.0544e-06
2015 | 2014-11-23 | B | 79 | 0.084455 | 0.0002413
2015 | 2014-11-23 | C | 60 | 0.036836 | 0.00018327
2015 | 2014-11-23 | C | 904 | 0.0060676 | 0.0027612
2015 | 2014-11-23 | C | 1 | 0.00041148 | 3.0544e-06
2015 | 2014-11-23 | C | 68 | 0.0090246 | 0.0002077
2015 | 2014-11-24 | C | 1 | 0.00033751 | 3.0544e-06
2015 | 2014-11-24 | B | 6 | 0.0055679 | 1.8327e-05
2015 | 2014-11-24 | C | 178 | 0.030181 | 0.00054369
2015 | 2014-11-24 | C | 376 | 0.020194 | 0.0011485
2015 | 2014-11-24 | C | 8 | 0.0010996 | 2.4435e-05
2015 | 2014-11-24 | C | 16 | 0.0079366 | 4.8871e-05
2015 | 2014-11-24 | C | 40 | 0.036365 | 0.00012218
2015 | 2014-11-24 | C | 16 | 0.003658 | 4.8871e-05
2015 | 2014-11-24 | B | 30 | 0.021367 | 9.1633e-05
2015 | 2014-11-24 | B | 40 | 0.0060396 | 0.00012218
2015 | 2014-11-25 | C | 1139 | 0.33871 | 0.003479
2015 | 2014-11-25 | C | 1 | 0.00032031 | 3.0544e-06
2015 | 2014-11-25 | C | 39 | 0.044552 | 0.00011912
2015 | 2014-11-25 | B | 14 | 0.016576 | 4.2762e-05
2015 | 2014-11-25 | C | 7 | 0.0066922 | 2.1381e-05
2015 | 2014-11-25 | B | 72 | 0.053184 | 0.00021992
2015 | 2014-11-25 | B | 38 | 0.041136 | 0.00011607
2015 | 2014-11-25 | B | 27 | 0.02938 | 8.2469e-05
2015 | 2014-11-25 | C | 28 | 0.018536 | 8.5524e-05
2015 | 2014-11-25 | C | 904 | 0.039145 | 0.0027612
2015 | 2014-11-25 | C | 163 | 0.075303 | 0.00049787
2015 | 2014-11-25 | B | 4 | 0.0020459 | 1.2218e-05
2015 | 2014-11-25 | C | 303 | 0.079885 | 0.00092549
2015 | 2014-11-25 | C | 61 | 0.023849 | 0.00018632
2015 | 2014-11-25 | C | 1 | 0.00037641 | 3.0544e-06
2015 | 2014-11-26 | C | 96 | 0.056941 | 0.00029322
2015 | 2014-11-26 | C | 53 | 0.011494 | 0.00016188
2015 | 2014-11-26 | C | 237 | 0.075481 | 0.0007239
2015 | 2014-11-26 | C | 23 | 0.0047873 | 7.0252e-05
2015 | 2014-11-26 | C | 679 | 0.14975 | 0.002074
2015 | 2014-11-26 | C | 510 | 0.13231 | 0.0015578
2015 | 2014-11-26 | B | 5 | 0.0053911 | 1.5272e-05
2015 | 2014-11-26 | B | 293 | 0.088212 | 0.00089495
2015 | 2014-11-26 | B | 272 | 0.28132 | 0.0008308
2015 | 2014-11-26 | B | 4 | 0.0028538 | 1.2218e-05
2015 | 2014-11-26 | B | 398 | 0.46201 | 0.0012157
2015 | 2014-11-26 | B | 37 | 0.036974 | 0.00011301
2015 | 2014-11-26 | B | 8 | 0.0021259 | 2.4435e-05
2015 | 2014-11-26 | C | 11 | 0.0012213 | 3.3599e-05
2015 | 2014-11-26 | B | 8 | 0.00089719 | 2.4435e-05
2015 | 2014-11-26 | C | 1 | 0.00021839 | 3.0544e-06
2015 | 2014-11-26 | C | 1759 | 0.24131 | 0.0053727
2015 | 2014-11-26 | C | 2 | 0.0010829 | 6.1088e-06
2015 | 2014-11-26 | C | 5 | 0.0045114 | 1.5272e-05
2015 | 2014-11-27 | C | 1 | 0.00032713 | 3.0544e-06
2015 | 2014-11-27 | C | 1 | 0.00080194 | 3.0544e-06
2015 | 2014-11-27 | B | 58 | 0.070798 | 0.00017716
2015 | 2014-11-27 | B | 24 | 0.020545 | 7.3306e-05
2015 | 2014-11-27 | B | 32 | 0.035995 | 9.7742e-05
2015 | 2014-11-27 | B | 3 | 0.0026299 | 9.1633e-06
2015 | 2014-11-27 | B | 25 | 0.0025627 | 7.6361e-05
2015 | 2014-11-27 | B | 1 | 0.00058645 | 3.0544e-06
2015 | 2014-11-27 | B | 38 | 0.031542 | 0.00011607
2015 | 2014-11-27 | B | 16 | 0.0033338 | 4.8871e-05
2015 | 2014-11-27 | C | 5 | 0.0018123 | 1.5272e-05
2015 | 2014-11-27 | B | 1 | 0.00033599 | 3.0544e-06
2015 | 2014-11-27 | B | 59 | 0.012999 | 0.00018021
2015 | 2014-11-27 | C | 465 | 0.0095857 | 0.0014203
2015 | 2014-11-27 | C | 126 | 0.087689 | 0.00038486
2015 | 2014-11-27 | C | 1 | 0.00077776 | 3.0544e-06
2015 | 2014-11-27 | C | 16 | 0.0040376 | 4.8871e-05
2015 | 2014-11-27 | C | 1 | 0.00018052 | 3.0544e-06
2015 | 2014-11-27 | C | 417 | 0.24 | 0.0012737
2015 | 2014-11-27 | C | 1 | 0.00026014 | 3.0544e-06
2015 | 2014-11-28 | C | 104 | 0.059231 | 0.00031766
2015 | 2014-11-28 | C | 268 | 0.009823 | 0.00081859
2015 | 2014-11-28 | C | 408 | 0.2611 | 0.0012462
2015 | 2014-11-28 | B | 6 | 0.0016656 | 1.8327e-05
2015 | 2014-11-28 | B | 15 | 0.012508 | 4.5816e-05
2015 | 2014-11-28 | B | 4 | 0.0038785 | 1.2218e-05
2015 | 2014-11-28 | B | 4 | 0.0032621 | 1.2218e-05
2015 | 2014-11-28 | C | 1 | 0.0005502 | 3.0544e-06
2015 | 2014-11-28 | C | 38 | 0.010585 | 0.00011607
2015 | 2014-11-28 | C | 344 | 0.062752 | 0.0010507
2015 | 2014-11-28 | C | 6 | 0.0018133 | 1.8327e-05
2015 | 2014-11-28 | C | 31 | 0.0056812 | 9.4687e-05
2015 | 2014-11-28 | C | 4 | 0.00063532 | 1.2218e-05
2015 | 2014-11-28 | C | 118 | 0.013101 | 0.00036042
2015 | 2014-11-28 | B | 117 | 0.048245 | 0.00035737
2015 | 2014-11-29 | C | 510 | 0.081399 | 0.0015578
2015 | 2014-11-29 | B | 42 | 0.051571 | 0.00012829
2015 | 2014-11-29 | B | 29 | 0.017773 | 8.8578e-05
2015 | 2014-11-29 | C | 1 | 0.0003982 | 3.0544e-06
2015 | 2014-11-29 | C | 1 | 0.0003481 | 3.0544e-06
2015 | 2014-11-29 | C | 682 | 0.0815 | 0.0020831
2015 | 2014-11-29 | C | 127 | 0.040624 | 0.00038791
2015 | 2014-11-29 | C | 1 | 0.00033797 | 3.0544e-06
2015 | 2014-11-29 | C | 2 | 0.0006957 | 6.1088e-06
2015 | 2014-11-29 | C | 13 | 0.002581 | 3.9708e-05
2015 | 2014-11-29 | C | 88 | 0.042359 | 0.00026879
2015 | 2014-11-30 | C | 510 | 0.1108 | 0.0015578
2015 | 2014-11-30 | C | 1 | 0.00034571 | 3.0544e-06
2015 | 2014-11-30 | C | 2 | 0.00030544 | 6.1088e-06
2015 | 2014-11-30 | C | 248 | 0.054966 | 0.0007575
2015 | 2014-11-30 | C | 17 | 0.028974 | 5.1925e-05
2015 | 2014-11-30 | C | 6 | 0.01573 | 1.8327e-05
2015 | 2014-11-30 | C | 6 | 0.0019857 | 1.8327e-05
2015 | 2014-11-30 | C | 569 | 0.0098154 | 0.001738
2015 | 2014-11-30 | C | 248 | 0.073581 | 0.0007575
2015 | 2014-12-01 | B | 410 | 0.04884 | 0.0012523
2015 | 2014-12-01 | C | 105 | 0.077918 | 0.00032071
2015 | 2014-12-01 | B | 161 | 0.22519 | 0.00049176
2015 | 2014-12-01 | B | 67 | 0.07958 | 0.00020465
2015 | 2014-12-01 | B | 134 | 0.023708 | 0.00040929
2015 | 2014-12-01 | B | 35 | 0.040089 | 0.0001069
2015 | 2014-12-01 | B | 11 | 0.0043975 | 3.3599e-05
2015 | 2014-12-01 | B | 14 | 0.01201 | 4.2762e-05
2015 | 2014-12-01 | B | 26 | 0.01464 | 7.9415e-05
2015 | 2014-12-01 | C | 1 | 0.0004152 | 3.0544e-06
2015 | 2014-12-01 | C | 4 | 0.0011386 | 1.2218e-05
2015 | 2014-12-01 | B | 78 | 0.084863 | 0.00023825
2015 | 2014-12-01 | C | 19 | 0.0040701 | 5.8034e-05
2015 | 2014-12-01 | C | 5 | 0.00087051 | 1.5272e-05
2015 | 2014-12-01 | B | 32 | 0.0035268 | 9.7742e-05
2015 | 2014-12-02 | C | 331 | 0.019596 | 0.001011
2015 | 2014-12-02 | C | 678 | 0.033928 | 0.0020709
2015 | 2014-12-02 | C | 19 | 0.053892 | 5.8034e-05
2015 | 2014-12-02 | C | 1 | 0.00039453 | 3.0544e-06
2015 | 2014-12-02 | B | 90 | 0.043493 | 0.0002749
2015 | 2014-12-02 | B | 144 | 0.1679 | 0.00043984
2015 | 2014-12-02 | B | 23 | 0.010678 | 7.0252e-05
2015 | 2014-12-02 | B | 293 | 0.26037 | 0.00089495
2015 | 2014-12-02 | C | 6 | 0.00032438 | 1.8327e-05
2015 | 2014-12-02 | B | 27 | 0.024493 | 8.2469e-05
2015 | 2014-12-02 | B | 31 | 0.028596 | 9.4687e-05
2015 | 2014-12-02 | B | 4 | 0.0035676 | 1.2218e-05
2015 | 2014-12-02 | B | 3 | 0.0009988 | 9.1633e-06
2015 | 2014-12-02 | B | 22 | 0.011064 | 6.7197e-05
2015 | 2014-12-02 | C | 1 | 0.00044992 | 3.0544e-06
2015 | 2014-12-02 | C | 1276 | 0.01941 | 0.0038974
2015 | 2014-12-02 | C | 1 | 0.00040227 | 3.0544e-06
2015 | 2014-12-03 | B | 233 | 0.034872 | 0.00071168
2015 | 2014-12-03 | C | 3 | 0.004129 | 9.1633e-06
2015 | 2014-12-03 | B | 97 | 0.10518 | 0.00029628
2015 | 2014-12-03 | B | 14 | 0.013657 | 4.2762e-05
2015 | 2014-12-03 | B | 134 | 0.025859 | 0.00040929
2015 | 2014-12-03 | B | 67 | 0.068761 | 0.00020465
2015 | 2014-12-03 | C | 6 | 0.0063227 | 1.8327e-05
2015 | 2014-12-03 | B | 38 | 0.028147 | 0.00011607
2015 | 2014-12-03 | B | 272 | 0.28458 | 0.0008308
2015 | 2014-12-03 | B | 77 | 0.092195 | 0.00023519
2015 | 2014-12-03 | C | 72 | 0.0023898 | 0.00021992
2015 | 2014-12-03 | C | 1 | 0.00032596 | 3.0544e-06
2015 | 2014-12-03 | C | 1 | 0.00034204 | 3.0544e-06
2015 | 2014-12-03 | C | 83 | 0.025225 | 0.00025352
2015 | 2014-12-03 | C | 8 | 0.00035839 | 2.4435e-05
2015 | 2014-12-03 | C | 2639 | 0.39375 | 0.0080606
2015 | 2014-12-04 | B | 233 | 0.038027 | 0.00071168
2015 | 2014-12-04 | C | 8 | 0.012271 | 2.4435e-05
2015 | 2014-12-04 | B | 2 | 0.0026135 | 6.1088e-06
2015 | 2014-12-04 | C | 1 | 0.00023799 | 3.0544e-06
2015 | 2014-12-04 | B | 22 | 0.027349 | 6.7197e-05
2015 | 2014-12-04 | B | 144 | 0.15271 | 0.00043984
2015 | 2014-12-04 | B | 40 | 0.049698 | 0.00012218
2015 | 2014-12-04 | B | 118 | 0.097644 | 0.00036042
2015 | 2014-12-04 | B | 33 | 0.024493 | 0.0001008
2015 | 2014-12-04 | B | 34 | 0.032555 | 0.00010385
2015 | 2014-12-04 | B | 29 | 0.026897 | 8.8578e-05
2015 | 2014-12-04 | C | 21 | 0.0073069 | 6.4143e-05
2015 | 2014-12-04 | C | 2 | 0.0010035 | 6.1088e-06
2015 | 2014-12-04 | C | 7 | 0.001263 | 2.1381e-05
2015 | 2014-12-05 | C | 4 | 0.0010426 | 1.2218e-05
2015 | 2014-12-05 | C | 2 | 0.0014314 | 6.1088e-06
2015 | 2014-12-05 | B | 76 | 0.064302 | 0.00023214
2015 | 2014-12-05 | B | 153 | 0.12841 | 0.00046733
2015 | 2014-12-05 | B | 3 | 0.0029416 | 9.1633e-06
2015 | 2014-12-05 | B | 9 | 0.0033538 | 2.749e-05
2015 | 2014-12-05 | B | 22 | 0.018991 | 6.7197e-05
2015 | 2014-12-05 | B | 4 | 0.0035633 | 1.2218e-05
2015 | 2014-12-05 | B | 37 | 0.038152 | 0.00011301
2015 | 2014-12-05 | B | 28 | 0.02717 | 8.5524e-05
2015 | 2014-12-05 | C | 3 | 0.00031155 | 9.1633e-06
2015 | 2014-12-05 | C | 29 | 0.0052261 | 8.8578e-05
2015 | 2014-12-05 | B | 3 | 0.0007972 | 9.1633e-06
2015 | 2014-12-05 | B | 46 | 0.0072804 | 0.0001405
2015 | 2014-12-05 | C | 20 | 0.0047038 | 6.1088e-05
2015 | 2014-12-05 | C | 11 | 0.00050378 | 3.3599e-05
2015 | 2014-12-06 | C | 1 | 2.7032e-05 | 3.0544e-06
2015 | 2014-12-06 | B | 45 | 0.033263 | 0.00013745
2015 | 2014-12-06 | B | 6 | 0.0051864 | 1.8327e-05
2015 | 2014-12-06 | C | 1044 | 0.11607 | 0.0031888
2015 | 2014-12-06 | C | 36 | 0.0060896 | 0.00010996
2015 | 2014-12-06 | B | 1 | 0.00035431 | 3.0544e-06
2015 | 2014-12-07 | C | 3 | 0.0013562 | 9.1633e-06
2015 | 2014-12-07 | B | 87 | 0.10576 | 0.00026573
2015 | 2014-12-07 | C | 179 | 0.028977 | 0.00054674
2015 | 2014-12-07 | C | 462 | 0.15268 | 0.0014111
2015 | 2014-12-08 | C | 303 | 0.029616 | 0.00092549
2015 | 2014-12-08 | C | 175 | 0.043989 | 0.00053452
2015 | 2014-12-08 | B | 3 | 0.00075246 | 9.1633e-06
2015 | 2014-12-08 | B | 14 | 0.016245 | 4.2762e-05
2015 | 2014-12-08 | B | 15 | 0.013149 | 4.5816e-05
2015 | 2014-12-08 | B | 35 | 0.019136 | 0.0001069
2015 | 2014-12-08 | B | 134 | 0.13916 | 0.00040929
2015 | 2014-12-08 | B | 369 | 0.14652 | 0.0011271
2015 | 2014-12-08 | B | 9 | 0.0024342 | 2.749e-05
2015 | 2014-12-08 | C | 1 | 0.00053508 | 3.0544e-06
2015 | 2014-12-08 | B | 6 | 0.0024441 | 1.8327e-05
2015 | 2014-12-08 | B | 14 | 0.0032513 | 4.2762e-05
2015 | 2014-12-08 | C | 109 | 0.087439 | 0.00033293
2015 | 2014-12-08 | B | 3 | 0.0010333 | 9.1633e-06
2015 | 2014-12-08 | C | 271 | 0.013824 | 0.00082775
2015 | 2014-12-09 | C | 3 | 0.00058477 | 9.1633e-06
2015 | 2014-12-09 | B | 6 | 0.0034454 | 1.8327e-05
2015 | 2014-12-09 | B | 5 | 0.0015119 | 1.5272e-05
2015 | 2014-12-09 | B | 247 | 0.29883 | 0.00075444
2015 | 2014-12-09 | B | 35 | 0.037417 | 0.0001069
2015 | 2014-12-09 | B | 2 | 0.0016368 | 6.1088e-06
2015 | 2014-12-09 | B | 22 | 0.021202 | 6.7197e-05
2015 | 2014-12-09 | B | 15 | 0.01755 | 4.5816e-05
2015 | 2014-12-09 | C | 6 | 0.00053147 | 1.8327e-05
2015 | 2014-12-09 | C | 1 | 0.00015883 | 3.0544e-06
2015 | 2014-12-09 | C | 528 | 0.22426 | 0.0016127
2015 | 2014-12-09 | C | 2 | 0.00016494 | 6.1088e-06
2015 | 2014-12-09 | B | 3 | 0.0016402 | 9.1633e-06
2015 | 2014-12-09 | C | 197 | 0.041051 | 0.00060172
2015 | 2014-12-10 | C | 1 | 0.00091327 | 3.0544e-06
2015 | 2014-12-10 | C | 1 | 1.9548e-05 | 3.0544e-06
2015 | 2014-12-10 | C | 1 | 0.00043027 | 3.0544e-06
2015 | 2014-12-10 | B | 40 | 0.021014 | 0.00012218
2015 | 2014-12-10 | B | 1 | 0.0008644 | 3.0544e-06
2015 | 2014-12-10 | B | 13 | 0.0061606 | 3.9708e-05
2015 | 2014-12-10 | B | 134 | 0.12452 | 0.00040929
2015 | 2014-12-10 | B | 273 | 0.24033 | 0.00083386
2015 | 2014-12-10 | B | 35 | 0.036859 | 0.0001069
2015 | 2014-12-10 | B | 35 | 0.01914 | 0.0001069
2015 | 2014-12-10 | B | 50 | 0.058655 | 0.00015272
2015 | 2014-12-10 | B | 52 | 0.037325 | 0.00015883
2015 | 2014-12-10 | B | 2 | 0.0016476 | 6.1088e-06
2015 | 2014-12-10 | C | 66 | 0.16389 | 0.00020159
2015 | 2014-12-10 | C | 6 | 0.00091633 | 1.8327e-05
2015 | 2014-12-10 | C | 31 | 0.022034 | 9.4687e-05
2015 | 2014-12-10 | C | 12 | 0.0014118 | 3.6653e-05
2015 | 2014-12-10 | C | 2 | 0.00028101 | 6.1088e-06
2015 | 2014-12-10 | C | 38 | 0.0023214 | 0.00011607
2015 | 2014-12-10 | C | 8 | 0.00083824 | 2.4435e-05
2015 | 2014-12-10 | C | 109 | 0.054313 | 0.00033293
2015 | 2014-12-10 | C | 271 | 0.046452 | 0.00082775
2015 | 2014-12-11 | C | 197 | 0.19491 | 0.00060172
2015 | 2014-12-11 | C | 5 | 0.0016941 | 1.5272e-05
2015 | 2014-12-11 | C | 3 | 0.0010588 | 9.1633e-06
2015 | 2014-12-11 | C | 1151 | 0.53523 | 0.0035156
2015 | 2014-12-11 | B | 1 | 0.001347 | 3.0544e-06
2015 | 2014-12-11 | B | 281 | 0.23958 | 0.00085829
2015 | 2014-12-11 | B | 63 | 0.056568 | 0.00019243
2015 | 2014-12-11 | B | 16 | 0.017105 | 4.8871e-05
2015 | 2014-12-11 | B | 4 | 0.0040074 | 1.2218e-05
2015 | 2014-12-11 | B | 10 | 0.002356 | 3.0544e-05
2015 | 2014-12-11 | B | 14 | 0.0024374 | 4.2762e-05
2015 | 2014-12-11 | B | 27 | 0.025895 | 8.2469e-05
2015 | 2014-12-11 | B | 18 | 0.017208 | 5.498e-05
2015 | 2014-12-11 | B | 180 | 0.075725 | 0.0005498
2015 | 2014-12-11 | C | 65 | 0.011317 | 0.00019854
2015 | 2014-12-11 | B | 29 | 0.023208 | 8.8578e-05
2015 | 2014-12-11 | C | 1 | 0.00051681 | 3.0544e-06
2015 | 2014-12-11 | B | 10 | 0.0099213 | 3.0544e-05
2015 | 2014-12-11 | B | 1 | 9.7742e-05 | 3.0544e-06
2015 | 2014-12-11 | C | 7 | 0.0014553 | 2.1381e-05
2015 | 2014-12-11 | C | 6 | 0.00078804 | 1.8327e-05
2015 | 2014-12-11 | C | 1 | 0.00046188 | 3.0544e-06
2015 | 2014-12-11 | B | 2 | 0.00014152 | 6.1088e-06
2015 | 2014-12-11 | C | 8 | 0.0023898 | 2.4435e-05
2015 | 2014-12-11 | C | 379 | 0.15451 | 0.0011576
2015 | 2014-12-12 | C | 10 | 0.0053452 | 3.0544e-05
2015 | 2014-12-12 | C | 1 | 0.0012981 | 3.0544e-06
2015 | 2014-12-12 | B | 134 | 0.12673 | 0.00040929
2015 | 2014-12-12 | B | 7 | 0.0058908 | 2.1381e-05
2015 | 2014-12-12 | B | 13 | 0.011952 | 3.9708e-05
2015 | 2014-12-12 | B | 130 | 0.11489 | 0.00039708
2015 | 2014-12-12 | B | 43 | 0.039632 | 0.00013134
2015 | 2014-12-12 | B | 10 | 0.0070252 | 3.0544e-05
2015 | 2014-12-12 | C | 98 | 0.005388 | 0.00029933
2015 | 2014-12-12 | C | 1 | 0.00036918 | 3.0544e-06
2015 | 2014-12-12 | B | 1 | 0.00029933 | 3.0544e-06
2015 | 2014-12-12 | C | 1 | 0.00014356 | 3.0544e-06
2015 | 2014-12-12 | B | 2 | 4.5816e-05 | 6.1088e-06
2015 | 2014-12-13 | B | 50 | 0.034385 | 0.00015272
2015 | 2014-12-13 | C | 46 | 0.049598 | 0.0001405
2015 | 2014-12-13 | C | 1 | 0.0021161 | 3.0544e-06
2015 | 2014-12-13 | C | 1 | 0.00037086 | 3.0544e-06
2015 | 2014-12-13 | B | 1 | 0.00026721 | 3.0544e-06
2015 | 2014-12-14 | C | 987 | 0.24578 | 0.0030147
2015 | 2014-12-14 | C | 359 | 0.19603 | 0.0010965
2015 | 2014-12-14 | B | 93 | 0.13862 | 0.00028406
2015 | 2014-12-14 | C | 867 | 0.10987 | 0.0026482
2015 | 2014-12-14 | C | 18 | 0.0041308 | 5.498e-05
2015 | 2014-12-14 | C | 685 | 0.062327 | 0.0020923
2015 | 2014-12-14 | C | 307 | 0.16877 | 0.00093771
2015 | 2014-12-14 | C | 6 | 0.016508 | 1.8327e-05
2015 | 2014-12-14 | C | 685 | 0.026956 | 0.0020923
2015 | 2014-12-14 | C | 854 | 0.1619 | 0.0026085
2015 | 2014-12-14 | C | 359 | 0.13377 | 0.0010965
2015 | 2014-12-14 | C | 645 | 0.55257 | 0.0019701
2015 | 2014-12-14 | C | 35 | 0.0021737 | 0.0001069
2015 | 2014-12-14 | C | 779 | 0.22562 | 0.0023794
2015 | 2014-12-14 | C | 7 | 0.00058334 | 2.1381e-05
2015 | 2014-12-14 | C | 5 | 0.0011355 | 1.5272e-05
2015 | 2014-12-14 | C | 3183 | 0.41715 | 0.0097222
2015 | 2014-12-14 | C | 1 | 0.0046401 | 3.0544e-06
2015 | 2014-12-15 | C | 535 | 0.022878 | 0.0016341
2015 | 2014-12-15 | C | 535 | 0.10054 | 0.0016341
2015 | 2014-12-15 | C | 711 | 0.19239 | 0.0021717
2015 | 2014-12-15 | C | 1 | 0.0017441 | 3.0544e-06
2015 | 2014-12-15 | C | 64 | 0.051951 | 0.00019548
2015 | 2014-12-15 | C | 3 | 0.0025736 | 9.1633e-06
2015 | 2014-12-15 | C | 3 | 0.001331 | 9.1633e-06
2015 | 2014-12-15 | B | 1 | 0.0013348 | 3.0544e-06
2015 | 2014-12-15 | C | 27 | 0.0090583 | 8.2469e-05
2015 | 2014-12-15 | B | 9 | 0.0016494 | 2.749e-05
2015 | 2014-12-15 | C | 2 | 0.0096395 | 6.1088e-06
2015 | 2014-12-15 | B | 133 | 0.15206 | 0.00040624
2015 | 2014-12-15 | B | 3 | 0.0033249 | 9.1633e-06
2015 | 2014-12-15 | B | 9 | 0.0050792 | 2.749e-05
2015 | 2014-12-15 | B | 9 | 0.0073682 | 2.749e-05
2015 | 2014-12-15 | C | 1 | 0.00053167 | 3.0544e-06
2015 | 2014-12-15 | C | 1 | 0.00035986 | 3.0544e-06
2015 | 2014-12-15 | C | 1 | 0.00018184 | 3.0544e-06
2015 | 2014-12-15 | B | 27 | 0.0055983 | 8.2469e-05
2015 | 2014-12-15 | C | 7 | 0.0025016 | 2.1381e-05
2015 | 2014-12-15 | B | 2 | 0.00059826 | 6.1088e-06
2015 | 2014-12-15 | C | 1 | 0.00041581 | 3.0544e-06
2015 | 2014-12-15 | C | 5 | 0.0018783 | 1.5272e-05
2015 | 2014-12-15 | C | 2 | 0.00060381 | 6.1088e-06
2015 | 2014-12-15 | C | 99 | 0.020584 | 0.00030239
2015 | 2014-12-16 | C | 423 | 0.0090441 | 0.001292
2015 | 2014-12-16 | C | 111 | 0.035533 | 0.00033904
2015 | 2014-12-16 | C | 107 | 0.054411 | 0.00032682
2015 | 2014-12-16 | C | 1 | 0.00063827 | 3.0544e-06
2015 | 2014-12-16 | B | 130 | 0.11581 | 0.00039708
2015 | 2014-12-16 | B | 3 | 0.0036589 | 9.1633e-06
2015 | 2014-12-16 | B | 3 | 0.0018968 | 9.1633e-06
2015 | 2014-12-16 | B | 97 | 0.064592 | 0.00029628
2015 | 2014-12-16 | B | 10 | 0.0089931 | 3.0544e-05
2015 | 2014-12-16 | B | 7 | 0.0052597 | 2.1381e-05
2015 | 2014-12-16 | B | 15 | 0.015052 | 4.5816e-05
2015 | 2014-12-16 | C | 1 | 0.0001962 | 3.0544e-06
2015 | 2014-12-16 | C | 1 | 0.00034413 | 3.0544e-06
2015 | 2014-12-16 | C | 215 | 0.0051223 | 0.0006567
2015 | 2014-12-16 | C | 45 | 0.029547 | 0.00013745
2015 | 2014-12-16 | C | 86 | 0.0031697 | 0.00026268
2015 | 2014-12-17 | C | 685 | 0.14131 | 0.0020923
2015 | 2014-12-17 | C | 48 | 0.031619 | 0.00014661
2015 | 2014-12-17 | C | 1 | 0.00029842 | 3.0544e-06
2015 | 2014-12-17 | C | 94 | 0.031861 | 0.00028712
2015 | 2014-12-17 | C | 436 | 0.017423 | 0.0013317
2015 | 2014-12-17 | C | 1 | 0.00050688 | 3.0544e-06
2015 | 2014-12-17 | C | 1281 | 0.070494 | 0.0039127
2015 | 2014-12-17 | C | 120 | 0.085402 | 0.00036653
2015 | 2014-12-17 | C | 436 | 0.15963 | 0.0013317
2015 | 2014-12-17 | C | 1 | 0.0006648 | 3.0544e-06
2015 | 2014-12-17 | C | 5 | 0.0042136 | 1.5272e-05
2015 | 2014-12-17 | C | 348 | 0.1832 | 0.0010629
2015 | 2014-12-17 | C | 224 | 0.092214 | 0.00068419
2015 | 2014-12-17 | B | 116 | 0.060889 | 0.00035431
2015 | 2014-12-17 | B | 224 | 0.2561 | 0.00068419
2015 | 2014-12-17 | B | 90 | 0.046458 | 0.0002749
2015 | 2014-12-17 | C | 3 | 0.0022418 | 9.1633e-06
2015 | 2014-12-17 | C | 179 | 0.016551 | 0.00054674
2015 | 2014-12-17 | C | 50 | 0.0077372 | 0.00015272
2015 | 2014-12-17 | B | 1 | 0.00091633 | 3.0544e-06
2015 | 2014-12-17 | C | 1 | 0.00040995 | 3.0544e-06
2015 | 2014-12-17 | C | 1 | 0.00029363 | 3.0544e-06
2015 | 2014-12-17 | C | 1 | 0.00014758 | 3.0544e-06
2015 | 2014-12-17 | C | 53 | 0.0085799 | 0.00016188
2015 | 2014-12-17 | B | 3 | 0.0022633 | 9.1633e-06
2015 | 2014-12-17 | C | 250 | 0.051385 | 0.00076361
2015 | 2014-12-17 | C | 1 | 0.0032419 | 3.0544e-06
2015 | 2014-12-17 | C | 27 | 0.034865 | 8.2469e-05
2015 | 2014-12-17 | C | 44 | 0.0045089 | 0.00013439
2015 | 2014-12-17 | B | 7 | 0.0023084 | 2.1381e-05
2015 | 2014-12-17 | C | 179 | 0.068978 | 0.00054674
2015 | 2014-12-17 | C | 839 | 0.20582 | 0.0025627
2015 | 2014-12-17 | C | 519 | 0.10476 | 0.0015852
2015 | 2014-12-17 | C | 1 | 0.00017848 | 3.0544e-06
2015 | 2014-12-17 | C | 3 | 0.0005865 | 9.1633e-06
2015 | 2014-12-17 | C | 185 | 0.047372 | 0.00056507
2015 | 2014-12-17 | C | 2 | 0.0021809 | 6.1088e-06
2015 | 2014-12-17 | C | 1 | 0.00081314 | 3.0544e-06
2015 | 2014-12-17 | C | 1 | 0.00086578 | 3.0544e-06
2015 | 2014-12-17 | C | 1 | 0.0018087 | 3.0544e-06
2015 | 2014-12-17 | C | 1 | 0.0012486 | 3.0544e-06
2015 | 2014-12-17 | C | 1 | 0.00049777 | 3.0544e-06
2015 | 2014-12-17 | B | 5 | 0.001709 | 1.5272e-05
2015 | 2014-12-17 | C | 1 | 0.0016794 | 3.0544e-06
2015 | 2014-12-18 | C | 123 | 0.053681 | 0.00037569
2015 | 2014-12-18 | C | 7 | 0.0027836 | 2.1381e-05
2015 | 2014-12-18 | B | 24 | 0.020667 | 7.3306e-05
2015 | 2014-12-18 | C | 3 | 0.00088884 | 9.1633e-06
2015 | 2014-12-18 | C | 1 | 0.00031644 | 3.0544e-06
2015 | 2014-12-18 | C | 527 | 0.062574 | 0.0016097
2015 | 2014-12-18 | B | 16 | 0.0081134 | 4.8871e-05
2015 | 2014-12-18 | B | 12 | 0.010519 | 3.6653e-05
2015 | 2014-12-18 | C | 3 | 0.00069631 | 9.1633e-06
2015 | 2014-12-18 | C | 650 | 0.077913 | 0.0019854
2015 | 2014-12-18 | C | 1 | 0.00016932 | 3.0544e-06
2015 | 2014-12-18 | C | 51 | 0.02416 | 0.00015578
2015 | 2014-12-18 | C | 49 | 0.0011973 | 0.00014967
2015 | 2014-12-18 | C | 99 | 0.0082369 | 0.00030239
2015 | 2014-12-19 | C | 23 | 0.019818 | 7.0252e-05
2015 | 2014-12-19 | C | 2 | 0.00061063 | 6.1088e-06
2015 | 2014-12-19 | B | 33 | 0.01567 | 0.0001008
2015 | 2014-12-19 | C | 5 | 0.00097742 | 1.5272e-05
2015 | 2014-12-19 | B | 81 | 0.06518 | 0.00024741
2015 | 2014-12-19 | C | 1 | 0.00038954 | 3.0544e-06
2015 | 2014-12-19 | C | 50 | 0.016212 | 0.00015272
2015 | 2014-12-20 | B | 98 | 0.019142 | 0.00029933
2015 | 2014-12-20 | C | 10 | 0.0033532 | 3.0544e-05
2015 | 2014-12-20 | C | 175 | 0.019367 | 0.00053452
2015 | 2014-12-20 | C | 1 | 0.00030427 | 3.0544e-06
2015 | 2014-12-20 | C | 120 | 0.0070924 | 0.00036653
2015 | 2014-12-21 | C | 24 | 0.00010477 | 7.3306e-05
2015 | 2014-12-21 | C | 3 | 0.00031934 | 9.1633e-06
2015 | 2014-12-21 | B | 71 | 0.012379 | 0.00021686
2015 | 2014-12-21 | B | 32 | 0.0047209 | 9.7742e-05
2015 | 2014-12-21 | C | 2857 | 0.36628 | 0.0087265
2015 | 2014-12-22 | C | 1 | 0.0076318 | 3.0544e-06
2015 | 2014-12-22 | C | 2 | 7.8601e-05 | 6.1088e-06
2015 | 2014-12-22 | C | 32 | 0.013431 | 9.7742e-05
2015 | 2014-12-22 | C | 10 | 0.0024211 | 3.0544e-05
2015 | 2014-12-22 | C | 47 | 0.045939 | 0.00014356
2015 | 2014-12-22 | C | 292 | 0.051639 | 0.00089189
2015 | 2014-12-22 | C | 1 | 0.0039609 | 3.0544e-06
2015 | 2014-12-22 | C | 1758 | 0.34812 | 0.0053697
2015 | 2014-12-22 | C | 26 | 0.0034776 | 7.9415e-05
2015 | 2014-12-22 | C | 2983 | 0.72516 | 0.0091113
2015 | 2014-12-23 | C | 2 | 0.00044595 | 6.1088e-06
2015 | 2014-12-23 | B | 132 | 0.010886 | 0.00040318
2015 | 2014-12-23 | C | 1 | 0.00027225 | 3.0544e-06
2015 | 2014-12-23 | C | 3 | 0.00084455 | 9.1633e-06
2015 | 2014-12-24 | C | 1 | 0.00029969 | 3.0544e-06
2015 | 2014-12-25 | C | 22 | 0.0052593 | 6.7197e-05
2015 | 2014-12-25 | C | 2 | 0.001599 | 6.1088e-06
2015 | 2014-12-26 | C | 463 | 0.1405 | 0.0014142
2015 | 2014-12-26 | C | 399 | 0.094061 | 0.0012187
2015 | 2014-12-26 | C | 331 | 0.056756 | 0.001011
2015 | 2014-12-27 | C | 2 | 0.0013305 | 6.1088e-06
2015 | 2014-12-27 | C | 5 | 0.002592 | 1.5272e-05
2015 | 2014-12-27 | C | 318 | 0.10492 | 0.00097131
2015 | 2014-12-28 | B | 24 | 0.0062909 | 7.3306e-05
2015 | 2014-12-28 | C | 1 | 0.00037401 | 3.0544e-06
2015 | 2014-12-28 | C | 2984 | 0.34211 | 0.0091144
2015 | 2014-12-28 | C | 7 | 0.004794 | 2.1381e-05
2015 | 2014-12-29 | B | 15 | 0.0035469 | 4.5816e-05
2015 | 2014-12-29 | C | 839 | 0.031876 | 0.0025627
2015 | 2014-12-29 | C | 215 | 0.041762 | 0.0006567
2015 | 2014-12-29 | C | 1 | 0.00071402 | 3.0544e-06
2015 | 2014-12-29 | C | 10 | 0.0025038 | 3.0544e-05
2015 | 2014-12-29 | C | 1 | 0.00025158 | 3.0544e-06
2015 | 2014-12-29 | C | 87 | 0.13286 | 0.00026573
2015 | 2014-12-29 | C | 1 | 0.00019528 | 3.0544e-06
2015 | 2014-12-29 | C | 1 | 0.00040359 | 3.0544e-06
2015 | 2014-12-29 | C | 32 | 0.01898 | 9.7742e-05
2015 | 2014-12-29 | C | 1 | 0.00039046 | 3.0544e-06
2015 | 2014-12-30 | C | 3 | 0.0015256 | 9.1633e-06
2015 | 2014-12-30 | C | 1 | 0.00027133 | 3.0544e-06
2015 | 2014-12-30 | C | 1 | 0.00089678 | 3.0544e-06
2015 | 2014-12-30 | C | 2 | 0.0016188 | 6.1088e-06
2015 | 2014-12-30 | C | 1 | 0.00053157 | 3.0544e-06
2015 | 2014-12-30 | C | 1 | 0.00038862 | 3.0544e-06
2015 | 2014-12-30 | C | 294 | 0.03706 | 0.000898
2015 | 2014-12-30 | C | 1 | 0.00039285 | 3.0544e-06
2015 | 2014-12-31 | C | 1 | 0.00087733 | 3.0544e-06
2015 | 2014-12-31 | C | 4 | 0.0029114 | 1.2218e-05
2015 | 2014-12-31 | B | 1 | 0.00099925 | 3.0544e-06
2015 | 2014-12-31 | C | 1 | 0.00079929 | 3.0544e-06
2015 | 2014-12-31 | C | 1 | 0.00066831 | 3.0544e-06
2015 | 2014-12-31 | C | 462 | 0.085029 | 0.0014111
2015 | 2014-12-31 | C | 13 | 0.00097945 | 3.9708e-05
2015 | 2014-12-31 | C | 237 | 0.06478 | 0.0007239
2015 | 2015-01-01 | C | 4 | 0.00051859 | 1.2218e-05
2015 | 2015-01-01 | C | 1 | 0.00055611 | 3.0544e-06
2015 | 2015-01-01 | C | 2 | 0.00081125 | 6.1088e-06
2015 | 2015-01-01 | C | 666 | 0.25644 | 0.0020342
2015 | 2015-01-02 | C | 1 | 0.00041347 | 3.0544e-06
2015 | 2015-01-02 | C | 15 | 0.0010791 | 4.5816e-05
2015 | 2015-01-02 | C | 268 | 0.15386 | 0.00081859
2015 | 2015-01-02 | C | 33 | 0.014432 | 0.0001008
2015 | 2015-01-02 | C | 1 | 0.00035706 | 3.0544e-06
2015 | 2015-01-02 | C | 2 | 0.00032789 | 6.1088e-06
2015 | 2015-01-02 | C | 333 | 0.052867 | 0.0010171
2015 | 2015-01-03 | C | 2817 | 0.51109 | 0.0086043
2015 | 2015-01-03 | C | 1 | 0.00015746 | 3.0544e-06
2015 | 2015-01-03 | C | 1 | 0.00047634 | 3.0544e-06
2015 | 2015-01-03 | C | 1 | 0.00041393 | 3.0544e-06
2015 | 2015-01-03 | C | 33 | 0.0026997 | 0.0001008
2015 | 2015-01-03 | C | 157 | 0.04847 | 0.00047954
2015 | 2015-01-04 | C | 1 | 0.00044803 | 3.0544e-06
2015 | 2015-01-04 | C | 2 | 0.00061312 | 6.1088e-06
2015 | 2015-01-04 | C | 16 | 0.0062559 | 4.8871e-05
2015 | 2015-01-05 | C | 7 | 0.0039536 | 2.1381e-05
2015 | 2015-01-05 | C | 1 | 0.00022781 | 3.0544e-06
2015 | 2015-01-05 | C | 243 | 0.025087 | 0.00074222
2015 | 2015-01-05 | C | 168 | 0.027197 | 0.00051314
2015 | 2015-01-05 | C | 436 | 0.05987 | 0.0013317
2015 | 2015-01-06 | C | 3016 | 0.21371 | 0.0092121
2015 | 2015-01-06 | B | 13 | 0.017114 | 3.9708e-05
2015 | 2015-01-06 | B | 5 | 0.0052994 | 1.5272e-05
2015 | 2015-01-06 | B | 404 | 0.30474 | 0.001234
2015 | 2015-01-06 | B | 107 | 0.11583 | 0.00032682
2015 | 2015-01-06 | C | 10 | 0.011801 | 3.0544e-05
2015 | 2015-01-06 | C | 1 | 0.00045628 | 3.0544e-06
2015 | 2015-01-07 | B | 385 | 0.51036 | 0.001176
2015 | 2015-01-07 | B | 95 | 0.03453 | 0.00029017
2015 | 2015-01-07 | B | 25 | 0.018708 | 7.6361e-05
2015 | 2015-01-07 | C | 184 | 0.059577 | 0.00056201
2015 | 2015-01-07 | C | 1 | 0.00052215 | 3.0544e-06
2015 | 2015-01-07 | C | 12 | 0.002041 | 3.6653e-05
2015 | 2015-01-07 | C | 1 | 0.00024323 | 3.0544e-06
2015 | 2015-01-08 | C | 6 | 0.0033896 | 1.8327e-05
2015 | 2015-01-08 | B | 29 | 0.030472 | 8.8578e-05
2015 | 2015-01-08 | B | 68 | 0.053189 | 0.0002077
2015 | 2015-01-08 | B | 62 | 0.01817 | 0.00018937
2015 | 2015-01-08 | B | 3 | 0.0034454 | 9.1633e-06
2015 | 2015-01-08 | B | 48 | 0.055566 | 0.00014661
2015 | 2015-01-08 | C | 8 | 0.0062111 | 2.4435e-05
2015 | 2015-01-08 | B | 32 | 0.02943 | 9.7742e-05
2015 | 2015-01-08 | C | 27 | 0.0038761 | 8.2469e-05
2015 | 2015-01-08 | C | 242 | 0.074977 | 0.00073917
2015 | 2015-01-08 | C | 194 | 0.0095882 | 0.00059256
2015 | 2015-01-08 | C | 436 | 0.23501 | 0.0013317
2015 | 2015-01-09 | B | 154 | 0.15031 | 0.00047038
2015 | 2015-01-09 | B | 27 | 0.02639 | 8.2469e-05
2015 | 2015-01-09 | B | 2 | 0.0024274 | 6.1088e-06
2015 | 2015-01-09 | C | 1 | 0.00038007 | 3.0544e-06
2015 | 2015-01-09 | C | 1 | 0.00023198 | 3.0544e-06
2015 | 2015-01-09 | C | 1 | 0.0003114 | 3.0544e-06
2015 | 2015-01-09 | C | 3 | 5.498e-05 | 9.1633e-06
2015 | 2015-01-10 | B | 281 | 0.063785 | 0.00085829
2015 | 2015-01-10 | C | 1 | 0.00028992 | 3.0544e-06
2015 | 2015-01-10 | B | 90 | 0.049207 | 0.0002749
2015 | 2015-01-11 | C | 1 | 0.00038017 | 3.0544e-06
2015 | 2015-01-11 | C | 1 | 0.00050418 | 3.0544e-06
2015 | 2015-01-11 | C | 1 | 0.00044488 | 3.0544e-06
2015 | 2015-01-12 | C | 3 | 0.00109 | 9.1633e-06
2015 | 2015-01-12 | C | 1 | 0.00024272 | 3.0544e-06
2015 | 2015-01-12 | B | 22 | 0.018449 | 6.7197e-05
2015 | 2015-01-12 | B | 1 | 0.00054063 | 3.0544e-06
2015 | 2015-01-12 | B | 2 | 0.0021564 | 6.1088e-06
2015 | 2015-01-12 | B | 27 | 0.026258 | 8.2469e-05
2015 | 2015-01-12 | B | 1 | 0.0011861 | 3.0544e-06
2015 | 2015-01-12 | C | 1 | 0.00017894 | 3.0544e-06
2015 | 2015-01-12 | C | 426 | 0.031228 | 0.0013012
2015 | 2015-01-12 | C | 358 | 0.12508 | 0.0010935
2015 | 2015-01-12 | B | 2 | 0.00094076 | 6.1088e-06
2015 | 2015-01-12 | C | 92 | 0.031418 | 0.00028101
2015 | 2015-01-13 | C | 410 | 0.082048 | 0.0012523
2015 | 2015-01-13 | B | 39 | 0.033978 | 0.00011912
2015 | 2015-01-13 | B | 222 | 0.078013 | 0.00067808
2015 | 2015-01-13 | B | 1 | 0.0010071 | 3.0544e-06
2015 | 2015-01-13 | B | 19 | 0.014379 | 5.8034e-05
2015 | 2015-01-13 | B | 16 | 0.018211 | 4.8871e-05
2015 | 2015-01-13 | B | 12 | 0.0095732 | 3.6653e-05
2015 | 2015-01-13 | B | 73 | 0.079352 | 0.00022297
2015 | 2015-01-13 | B | 18 | 0.014275 | 5.498e-05
2015 | 2015-01-13 | B | 2 | 0.000898 | 6.1088e-06
2015 | 2015-01-14 | C | 11 | 0.0018914 | 3.3599e-05
2015 | 2015-01-14 | C | 84 | 0.014637 | 0.00025657
2015 | 2015-01-14 | B | 14 | 0.02094 | 4.2762e-05
2015 | 2015-01-14 | B | 12 | 0.0083526 | 3.6653e-05
2015 | 2015-01-14 | B | 61 | 0.068047 | 0.00018632
2015 | 2015-01-14 | B | 45 | 0.044396 | 0.00013745
2015 | 2015-01-14 | B | 16 | 0.019399 | 4.8871e-05
2015 | 2015-01-14 | B | 10 | 0.012361 | 3.0544e-05
2015 | 2015-01-14 | B | 3 | 0.0033906 | 9.1633e-06
2015 | 2015-01-14 | B | 18 | 0.019535 | 5.498e-05
2015 | 2015-01-14 | C | 2309 | 0.26176 | 0.0070527
2015 | 2015-01-14 | C | 235 | 0.034009 | 0.00071779
2015 | 2015-01-14 | C | 1 | 0.00030198 | 3.0544e-06
2015 | 2015-01-15 | B | 42 | 0.051212 | 0.00012829
2015 | 2015-01-15 | B | 39 | 0.033517 | 0.00011912
2015 | 2015-01-15 | B | 10 | 0.012754 | 3.0544e-05
2015 | 2015-01-15 | B | 45 | 0.029139 | 0.00013745
2015 | 2015-01-15 | B | 91 | 0.080884 | 0.00027795
2015 | 2015-01-15 | C | 79 | 0.03685 | 0.0002413
2015 | 2015-01-15 | B | 9 | 0.0073402 | 2.749e-05
2015 | 2015-01-15 | C | 773 | 0.08736 | 0.0023611
2015 | 2015-01-15 | B | 3 | 0.0028131 | 9.1633e-06
2015 | 2015-01-15 | C | 1 | 0.0039015 | 3.0544e-06
2015 | 2015-01-15 | C | 1 | 5.0296e-05 | 3.0544e-06
2015 | 2015-01-16 | C | 761 | 0.16072 | 0.0023244
2015 | 2015-01-16 | B | 39 | 0.043148 | 0.00011912
2015 | 2015-01-16 | C | 11 | 0.012902 | 3.3599e-05
2015 | 2015-01-16 | C | 1020 | 0.53936 | 0.0031155
2015 | 2015-01-16 | C | 764 | 0.058339 | 0.0023336
2015 | 2015-01-16 | B | 74 | 0.021118 | 0.00022603
2015 | 2015-01-17 | C | 49 | 0.011763 | 0.00014967
2015 | 2015-01-17 | C | 49 | 0.0061302 | 0.00014967
2015 | 2015-01-17 | C | 854 | 0.087599 | 0.0026085
2015 | 2015-01-17 | C | 9 | 0.00023468 | 2.749e-05
2015 | 2015-01-17 | C | 4 | 0.00094931 | 1.2218e-05
2015 | 2015-01-17 | C | 1 | 6.8114e-05 | 3.0544e-06
2015 | 2015-01-18 | C | 163 | 0.0059745 | 0.00049787
2015 | 2015-01-18 | C | 904 | 0.0082836 | 0.0027612
2015 | 2015-01-18 | B | 52 | 0.06503 | 0.00015883
2015 | 2015-01-18 | B | 14 | 0.0070158 | 4.2762e-05
2015 | 2015-01-18 | B | 4 | 0.0024875 | 1.2218e-05
2015 | 2015-01-18 | C | 1 | 0.00031623 | 3.0544e-06
2015 | 2015-01-18 | C | 2 | 0.0022377 | 6.1088e-06
2015 | 2015-01-18 | C | 855 | 0.11259 | 0.0026115
2015 | 2015-01-19 | C | 2465 | 0.33332 | 0.0075292
2015 | 2015-01-19 | B | 42 | 0.051535 | 0.00012829
2015 | 2015-01-19 | B | 16 | 0.017447 | 4.8871e-05
2015 | 2015-01-19 | B | 175 | 0.073631 | 0.00053452
2015 | 2015-01-19 | B | 33 | 0.031644 | 0.0001008
2015 | 2015-01-19 | C | 2 | 0.00080713 | 6.1088e-06
2015 | 2015-01-19 | C | 42 | 0.02886 | 0.00012829
2015 | 2015-01-19 | C | 1358 | 0.070752 | 0.0041479
2015 | 2015-01-20 | B | 136 | 0.071193 | 0.0004154
2015 | 2015-01-20 | C | 178 | 0.047753 | 0.00054369
2015 | 2015-01-20 | B | 61 | 0.063553 | 0.00018632
2015 | 2015-01-20 | B | 38 | 0.038933 | 0.00011607
2015 | 2015-01-20 | B | 3 | 0.00058462 | 9.1633e-06
2015 | 2015-01-20 | B | 165 | 0.20238 | 0.00050398
2015 | 2015-01-20 | B | 438 | 0.28344 | 0.0013378
2015 | 2015-01-20 | B | 196 | 0.13532 | 0.00059867
2015 | 2015-01-20 | B | 5 | 0.00062488 | 1.5272e-05
2015 | 2015-01-20 | C | 17 | 0.0011943 | 5.1925e-05
2015 | 2015-01-20 | C | 1 | 0.00044177 | 3.0544e-06
2015 | 2015-01-20 | C | 1 | 0.00045903 | 3.0544e-06
2015 | 2015-01-20 | C | 1 | 0.0042118 | 3.0544e-06
2015 | 2015-01-21 | C | 163 | 0.067003 | 0.00049787
2015 | 2015-01-21 | B | 47 | 0.056131 | 0.00014356
2015 | 2015-01-21 | C | 170 | 0.090547 | 0.00051925
2015 | 2015-01-21 | B | 26 | 0.028816 | 7.9415e-05
2015 | 2015-01-21 | B | 2 | 0.0019044 | 6.1088e-06
2015 | 2015-01-21 | B | 1 | 0.0011118 | 3.0544e-06
2015 | 2015-01-21 | B | 3 | 0.0023589 | 9.1633e-06
2015 | 2015-01-21 | C | 1 | 0.00023519 | 3.0544e-06
2015 | 2015-01-21 | C | 44 | 0.021724 | 0.00013439
2015 | 2015-01-21 | C | 132 | 0.069304 | 0.00040318
2015 | 2015-01-22 | C | 22 | 0.042603 | 6.7197e-05
2015 | 2015-01-22 | C | 99 | 0.046243 | 0.00030239
2015 | 2015-01-22 | B | 2 | 0.0039097 | 6.1088e-06
2015 | 2015-01-22 | B | 38 | 0.048284 | 0.00011607
2015 | 2015-01-22 | B | 12 | 0.0026757 | 3.6653e-05
2015 | 2015-01-22 | B | 61 | 0.055045 | 0.00018632
2015 | 2015-01-22 | B | 159 | 0.18234 | 0.00048565
2015 | 2015-01-22 | B | 26 | 0.025889 | 7.9415e-05
2015 | 2015-01-22 | B | 1 | 0.0013012 | 3.0544e-06
2015 | 2015-01-22 | B | 15 | 0.0031155 | 4.5816e-05
2015 | 2015-01-22 | C | 3 | 0.0014844 | 9.1633e-06
2015 | 2015-01-22 | B | 103 | 0.015297 | 0.00031461
2015 | 2015-01-23 | B | 29 | 0.031268 | 8.8578e-05
2015 | 2015-01-23 | B | 58 | 0.023396 | 0.00017716
2015 | 2015-01-23 | B | 1 | 0.00026879 | 3.0544e-06
2015 | 2015-01-23 | C | 1 | 0.00016494 | 3.0544e-06
2015 | 2015-01-24 | C | 1 | 0.00028376 | 3.0544e-06
2015 | 2015-01-24 | B | 89 | 0.030483 | 0.00027184
2015 | 2015-01-24 | C | 26 | 0.00095298 | 7.9415e-05
2015 | 2015-01-24 | C | 73 | 0.037744 | 0.00022297
2015 | 2015-01-25 | C | 2 | 0.0005752 | 6.1088e-06
2015 | 2015-01-25 | C | 1 | 0.00041886 | 3.0544e-06
2015 | 2015-01-25 | C | 1 | 0.0010582 | 3.0544e-06
2015 | 2015-01-25 | C | 471 | 0.24247 | 0.0014386
2015 | 2015-01-26 | B | 10 | 0.013478 | 3.0544e-05
2015 | 2015-01-26 | B | 5 | 0.0031002 | 1.5272e-05
2015 | 2015-01-26 | B | 1 | 0.0017255 | 3.0544e-06
2015 | 2015-01-26 | C | 2 | 0.00017629 | 6.1088e-06
2015 | 2015-01-26 | C | 659 | 0.2771 | 0.0020129
2015 | 2015-01-27 | C | 478 | 0.11535 | 0.00146
2015 | 2015-01-27 | C | 1 | 0.0013552 | 3.0544e-06
2015 | 2015-01-27 | B | 373 | 0.30793 | 0.0011393
2015 | 2015-01-27 | B | 7 | 0.0059332 | 2.1381e-05
2015 | 2015-01-27 | B | 47 | 0.034547 | 0.00014356
2015 | 2015-01-27 | B | 66 | 0.036068 | 0.00020159
2015 | 2015-01-27 | B | 16 | 0.0060642 | 4.8871e-05
2015 | 2015-01-27 | B | 8 | 0.0087605 | 2.4435e-05
2015 | 2015-01-27 | B | 75 | 0.061036 | 0.00022908
2015 | 2015-01-27 | C | 6 | 0.0092916 | 1.8327e-05
2015 | 2015-01-27 | C | 98 | 0.0035371 | 0.00029933
2015 | 2015-01-27 | B | 143 | 0.051104 | 0.00043678
2015 | 2015-01-27 | C | 953 | 0.46159 | 0.0029109
2015 | 2015-01-27 | C | 101 | 0.014449 | 0.0003085
2015 | 2015-01-27 | C | 64 | 0.015671 | 0.00019548
2015 | 2015-01-27 | C | 39 | 0.0060752 | 0.00011912
2015 | 2015-01-28 | C | 2 | 0.00026436 | 6.1088e-06
2015 | 2015-01-28 | B | 112 | 0.10182 | 0.0003421
2015 | 2015-01-28 | C | 1 | 0.00032209 | 3.0544e-06
2015 | 2015-01-28 | B | 61 | 0.072727 | 0.00018632
2015 | 2015-01-28 | B | 91 | 0.07797 | 0.00027795
2015 | 2015-01-28 | B | 20 | 0.018791 | 6.1088e-05
2015 | 2015-01-28 | B | 274 | 0.2854 | 0.00083691
2015 | 2015-01-28 | B | 1 | 0.00081813 | 3.0544e-06
2015 | 2015-01-28 | B | 4 | 0.0033094 | 1.2218e-05
2015 | 2015-01-28 | B | 17 | 0.0081003 | 5.1925e-05
2015 | 2015-01-28 | B | 64 | 0.0031277 | 0.00019548
2015 | 2015-01-28 | C | 1 | 0.00028615 | 3.0544e-06
2015 | 2015-01-28 | C | 132 | 0.042081 | 0.00040318
2015 | 2015-01-28 | C | 1 | 0.00024619 | 3.0544e-06
2015 | 2015-01-28 | C | 2 | 0.0065576 | 6.1088e-06
2015 | 2015-01-28 | C | 1 | 0.00033874 | 3.0544e-06
2015 | 2015-01-29 | B | 3 | 0.0020892 | 9.1633e-06
2015 | 2015-01-29 | B | 27 | 0.031892 | 8.2469e-05
2015 | 2015-01-29 | B | 40 | 0.040441 | 0.00012218
2015 | 2015-01-29 | C | 23 | 0.0024038 | 7.0252e-05
2015 | 2015-01-29 | C | 6 | 0.0088907 | 1.8327e-05
2015 | 2015-01-29 | C | 428 | 0.11504 | 0.0013073
2015 | 2015-01-29 | C | 1316 | 0.29533 | 0.0040196
2015 | 2015-01-29 | C | 429 | 0.026329 | 0.0013103
2015 | 2015-01-29 | C | 2 | 0.00078468 | 6.1088e-06
2015 | 2015-01-29 | C | 16 | 0.012588 | 4.8871e-05
2015 | 2015-01-29 | B | 1 | 0.00012218 | 3.0544e-06
2015 | 2015-01-30 | C | 98 | 0.0033825 | 0.00029933
2015 | 2015-01-30 | C | 98 | 0.0034922 | 0.00029933
2015 | 2015-01-30 | C | 41 | 0.0066107 | 0.00012523
2015 | 2015-01-30 | C | 94 | 0.090441 | 0.00028712
2015 | 2015-01-30 | B | 24 | 0.023825 | 7.3306e-05
2015 | 2015-01-30 | B | 73 | 0.012709 | 0.00022297
2015 | 2015-01-30 | C | 1 | 0.00066434 | 3.0544e-06
2015 | 2015-01-31 | C | 123 | 0.05297 | 0.00037569
2015 | 2015-01-31 | C | 98 | 0.052289 | 0.00029933
2015 | 2015-01-31 | B | 1 | 0.0002413 | 3.0544e-06
2015 | 2015-01-31 | C | 127 | 0.042882 | 0.00038791
2015 | 2015-01-31 | C | 36 | 0.0044643 | 0.00010996
2015 | 2015-01-31 | B | 38 | 0.042017 | 0.00011607
2015 | 2015-01-31 | B | 87 | 0.023686 | 0.00026573
2015 | 2015-01-31 | B | 1 | 0.0010507 | 3.0544e-06
2015 | 2015-01-31 | C | 98 | 0.025398 | 0.00029933
2015 | 2015-01-31 | C | 65 | 0.036134 | 0.00019854
2015 | 2015-01-31 | B | 9 | 0.0082047 | 2.749e-05
2015 | 2015-01-31 | C | 1 | 0.0017228 | 3.0544e-06
2015 | 2015-01-31 | C | 237 | 0.090135 | 0.0007239
2015 | 2015-02-01 | C | 587 | 0.25489 | 0.0017929
2015 | 2015-02-01 | C | 485 | 0.097388 | 0.0014814
2015 | 2015-02-01 | C | 52 | 0.0042375 | 0.00015883
2015 | 2015-02-01 | B | 106 | 0.016134 | 0.00032377
2015 | 2015-02-01 | C | 1 | 0.00018561 | 3.0544e-06
2015 | 2015-02-01 | C | 1 | 0.00026869 | 3.0544e-06
2015 | 2015-02-01 | C | 36 | 0.035535 | 0.00010996
2015 | 2015-02-01 | C | 33 | 0.0063678 | 0.0001008
2015 | 2015-02-01 | C | 342 | 0.079502 | 0.0010446
2015 | 2015-02-01 | C | 177 | 0.091646 | 0.00054063
2015 | 2015-02-01 | C | 3 | 0.00077618 | 9.1633e-06
2015 | 2015-02-01 | C | 108 | 0.041894 | 0.00032988
2015 | 2015-02-01 | C | 1 | 0.00038537 | 3.0544e-06
2015 | 2015-02-01 | C | 108 | 0.25343 | 0.00032988
2015 | 2015-02-02 | C | 1 | 0.0045596 | 3.0544e-06
2015 | 2015-02-02 | C | 2 | 0.00061267 | 6.1088e-06
2015 | 2015-02-02 | C | 16 | 0.0060111 | 4.8871e-05
2015 | 2015-02-02 | B | 9 | 0.0026752 | 2.749e-05
2015 | 2015-02-02 | C | 30 | 0.024488 | 9.1633e-05
2015 | 2015-02-02 | C | 158 | 0.32058 | 0.0004826
2015 | 2015-02-02 | C | 714 | 0.17641 | 0.0021809
2015 | 2015-02-03 | C | 45 | 0.0013859 | 0.00013745
2015 | 2015-02-03 | C | 108 | 0.040562 | 0.00032988
2015 | 2015-02-03 | C | 1 | 0.00026512 | 3.0544e-06
2015 | 2015-02-03 | B | 1 | 0.001159 | 3.0544e-06
2015 | 2015-02-03 | C | 14 | 0.0037404 | 4.2762e-05
2015 | 2015-02-03 | B | 110 | 0.085257 | 0.00033599
2015 | 2015-02-03 | B | 3 | 0.0009232 | 9.1633e-06
2015 | 2015-02-03 | B | 44 | 0.030297 | 0.00013439
2015 | 2015-02-03 | B | 25 | 0.023545 | 7.6361e-05
2015 | 2015-02-03 | C | 665 | 0.18116 | 0.0020312
2015 | 2015-02-03 | C | 1 | 0.00034235 | 3.0544e-06
2015 | 2015-02-03 | C | 1273 | 0.1669 | 0.0038883
2015 | 2015-02-03 | C | 109 | 0.034567 | 0.00033293
2015 | 2015-02-03 | C | 1 | 0.0010518 | 3.0544e-06
2015 | 2015-02-03 | C | 47 | 0.011089 | 0.00014356
2015 | 2015-02-04 | C | 2 | 0.0007241 | 6.1088e-06
2015 | 2015-02-04 | C | 1 | 0.00028111 | 3.0544e-06
2015 | 2015-02-04 | B | 171 | 0.073888 | 0.00052231
2015 | 2015-02-04 | B | 83 | 0.083002 | 0.00025352
2015 | 2015-02-04 | B | 274 | 0.27859 | 0.00083691
2015 | 2015-02-04 | B | 12 | 0.0061443 | 3.6653e-05
2015 | 2015-02-04 | B | 10 | 0.0024016 | 3.0544e-05
2015 | 2015-02-04 | C | 1 | 0.00022817 | 3.0544e-06
2015 | 2015-02-04 | C | 2 | 0.0015959 | 6.1088e-06
2015 | 2015-02-04 | C | 1 | 0.0006316 | 3.0544e-06
2015 | 2015-02-04 | C | 1 | 0.00044544 | 3.0544e-06
2015 | 2015-02-04 | C | 1 | 0.00023209 | 3.0544e-06
2015 | 2015-02-04 | C | 130 | 0.014285 | 0.00039708
2015 | 2015-02-04 | C | 107 | 0.0086532 | 0.00032682
2015 | 2015-02-05 | C | 56 | 0.026733 | 0.00017105
2015 | 2015-02-05 | C | 35 | 0.0072021 | 0.0001069
2015 | 2015-02-05 | B | 3 | 0.0036378 | 9.1633e-06
2015 | 2015-02-05 | B | 44 | 0.056701 | 0.00013439
2015 | 2015-02-05 | B | 56 | 0.015312 | 0.00017105
2015 | 2015-02-05 | B | 52 | 0.046534 | 0.00015883
2015 | 2015-02-05 | B | 230 | 0.23198 | 0.00070252
2015 | 2015-02-05 | B | 4 | 0.0011438 | 1.2218e-05
2015 | 2015-02-05 | C | 1 | 0.00033466 | 3.0544e-06
2015 | 2015-02-05 | B | 4 | 0.0015639 | 1.2218e-05
2015 | 2015-02-05 | B | 2 | 0.00064214 | 6.1088e-06
2015 | 2015-02-05 | C | 632 | 0.18831 | 0.0019304
2015 | 2015-02-05 | C | 1446 | 0.1724 | 0.0044167
2015 | 2015-02-05 | C | 309 | 0.12863 | 0.00094382
2015 | 2015-02-05 | C | 20 | 0.0053758 | 6.1088e-05
2015 | 2015-02-06 | C | 417 | 0.19717 | 0.0012737
2015 | 2015-02-06 | C | 244 | 0.081842 | 0.00074528
2015 | 2015-02-06 | C | 82 | 0.11874 | 0.00025046
2015 | 2015-02-06 | C | 1 | 0.00032239 | 3.0544e-06
2015 | 2015-02-06 | C | 3 | 0.0027798 | 9.1633e-06
2015 | 2015-02-06 | C | 83 | 0.061597 | 0.00025352
2015 | 2015-02-06 | C | 3 | 0.0018866 | 9.1633e-06
2015 | 2015-02-06 | C | 45 | 0.021442 | 0.00013745
2015 | 2015-02-06 | C | 177 | 0.09251 | 0.00054063
2015 | 2015-02-06 | C | 27 | 0.0011298 | 8.2469e-05
2015 | 2015-02-06 | B | 3 | 0.0055413 | 9.1633e-06
2015 | 2015-02-06 | C | 515 | 0.19774 | 0.001573
2015 | 2015-02-06 | C | 405 | 0.16614 | 0.001237
2015 | 2015-02-06 | C | 1021 | 0.33732 | 0.0031186
2015 | 2015-02-06 | C | 52 | 0.010986 | 0.00015883
2015 | 2015-02-06 | C | 32 | 0.019157 | 9.7742e-05
2015 | 2015-02-06 | C | 3 | 0.0012835 | 9.1633e-06
2015 | 2015-02-06 | C | 5 | 0.00056507 | 1.5272e-05
2015 | 2015-02-06 | C | 48 | 0.014705 | 0.00014661
2015 | 2015-02-06 | C | 1 | 0.0024008 | 3.0544e-06
2015 | 2015-02-07 | C | 46 | 0.032393 | 0.0001405
2015 | 2015-02-07 | C | 1 | 0.00055423 | 3.0544e-06
2015 | 2015-02-07 | C | 327 | 0.15834 | 0.0009988
2015 | 2015-02-08 | C | 2 | 0.0003482 | 6.1088e-06
2015 | 2015-02-08 | C | 1 | 0.001787 | 3.0544e-06
2015 | 2015-02-08 | C | 1 | 0.00031812 | 3.0544e-06
2015 | 2015-02-08 | C | 2987 | 0.13596 | 0.0091236
2015 | 2015-02-09 | B | 2 | 0.00053402 | 6.1088e-06
2015 | 2015-02-09 | B | 2 | 0.0014799 | 6.1088e-06
2015 | 2015-02-09 | B | 9 | 0.0066672 | 2.749e-05
2015 | 2015-02-09 | C | 1 | 0.00042283 | 3.0544e-06
2015 | 2015-02-09 | C | 1 | 0.00032295 | 3.0544e-06
2015 | 2015-02-09 | C | 47 | 0.0022012 | 0.00014356
2015 | 2015-02-09 | C | 212 | 0.0077705 | 0.00064754
2015 | 2015-02-09 | C | 824 | 0.29882 | 0.0025168
2015 | 2015-02-09 | C | 32 | 0.014428 | 9.7742e-05
2015 | 2015-02-09 | C | 416 | 0.027868 | 0.0012706
2015 | 2015-02-10 | C | 86 | 0.07509 | 0.00026268
2015 | 2015-02-10 | C | 2 | 3.3904e-05 | 6.1088e-06
2015 | 2015-02-10 | C | 855 | 0.61151 | 0.0026115
2015 | 2015-02-10 | C | 40 | 0.029379 | 0.00012218
2015 | 2015-02-10 | B | 32 | 0.037368 | 9.7742e-05
2015 | 2015-02-10 | B | 43 | 0.050702 | 0.00013134
2015 | 2015-02-10 | B | 133 | 0.13922 | 0.00040624
2015 | 2015-02-10 | B | 14 | 0.017062 | 4.2762e-05
2015 | 2015-02-10 | B | 41 | 0.035635 | 0.00012523
2015 | 2015-02-10 | B | 11 | 0.0095538 | 3.3599e-05
2015 | 2015-02-10 | B | 7 | 0.006776 | 2.1381e-05
2015 | 2015-02-10 | C | 1 | 0.00020149 | 3.0544e-06
2015 | 2015-02-10 | C | 2 | 0.00024048 | 6.1088e-06
2015 | 2015-02-10 | C | 1 | 0.00023147 | 3.0544e-06
2015 | 2015-02-10 | C | 1 | 0.00021493 | 3.0544e-06
2015 | 2015-02-10 | C | 4638 | 0.77656 | 0.014166
2015 | 2015-02-10 | C | 2 | 0.00084373 | 6.1088e-06
2015 | 2015-02-10 | B | 196 | 0.030532 | 0.00059867
2015 | 2015-02-11 | B | 14 | 0.0081941 | 4.2762e-05
2015 | 2015-02-11 | C | 1 | 0.00019665 | 3.0544e-06
2015 | 2015-02-11 | B | 102 | 0.035467 | 0.00031155
2015 | 2015-02-11 | B | 50 | 0.038997 | 0.00015272
2015 | 2015-02-12 | B | 5 | 0.0016952 | 1.5272e-05
2015 | 2015-02-12 | B | 5 | 0.003314 | 1.5272e-05
2015 | 2015-02-12 | B | 32 | 0.04369 | 9.7742e-05
2015 | 2015-02-12 | B | 27 | 0.031916 | 8.2469e-05
2015 | 2015-02-12 | B | 4 | 0.0041504 | 1.2218e-05
2015 | 2015-02-12 | B | 39 | 0.037162 | 0.00011912
2015 | 2015-02-12 | B | 62 | 0.003172 | 0.00018937
2015 | 2015-02-12 | B | 274 | 0.28673 | 0.00083691
2015 | 2015-02-12 | B | 6 | 0.0026152 | 1.8327e-05
2015 | 2015-02-12 | B | 16 | 0.00029322 | 4.8871e-05
2015 | 2015-02-13 | C | 4 | 0.0013693 | 1.2218e-05
2015 | 2015-02-13 | C | 33 | 0.0014873 | 0.0001008
2015 | 2015-02-13 | B | 29 | 0.029864 | 8.8578e-05
2015 | 2015-02-13 | B | 10 | 0.014815 | 3.0544e-05
2015 | 2015-02-13 | B | 39 | 0.037389 | 0.00011912
2015 | 2015-02-13 | B | 11 | 0.00075317 | 3.3599e-05
2015 | 2015-02-13 | B | 7 | 0.0011859 | 2.1381e-05
2015 | 2015-02-13 | B | 220 | 0.23861 | 0.00067197
2015 | 2015-02-13 | B | 17 | 0.0002977 | 5.1925e-05
2015 | 2015-02-13 | B | 6 | 0.00022633 | 1.8327e-05
2015 | 2015-02-13 | B | 11 | 0.0016004 | 3.3599e-05
2015 | 2015-02-13 | C | 1 | 0.00010858 | 3.0544e-06
2015 | 2015-02-13 | B | 16 | 0.0010792 | 4.8871e-05
2015 | 2015-02-13 | C | 276 | 0.14277 | 0.00084302
2015 | 2015-02-13 | C | 678 | 0.65117 | 0.0020709
2015 | 2015-02-14 | B | 49 | 0.0012298 | 0.00014967
2015 | 2015-02-14 | C | 3021 | 0.44479 | 0.0092274
2015 | 2015-02-14 | C | 2 | 0.0026146 | 6.1088e-06
2015 | 2015-02-14 | B | 22 | 0.0011872 | 6.7197e-05
2015 | 2015-02-14 | C | 2824 | 1.1477 | 0.0086257
2015 | 2015-02-14 | B | 57 | 0.033483 | 0.0001741
2015 | 2015-02-14 | B | 16 | 0.017481 | 4.8871e-05
2015 | 2015-02-14 | B | 1 | 0.00040486 | 3.0544e-06
2015 | 2015-02-14 | B | 1 | 0.00070252 | 3.0544e-06
2015 | 2015-02-14 | C | 16 | 0.00058645 | 4.8871e-05
2015 | 2015-02-14 | C | 10 | 0.018194 | 3.0544e-05
2015 | 2015-02-15 | C | 1 | 0.00021956 | 3.0544e-06
2015 | 2015-02-15 | C | 1 | 0.00034815 | 3.0544e-06
2015 | 2015-02-16 | B | 3 | 0.0031797 | 9.1633e-06
2015 | 2015-02-16 | C | 3 | 0.0011179 | 9.1633e-06
2015 | 2015-02-16 | C | 30 | 0.028735 | 9.1633e-05
2015 | 2015-02-16 | C | 147 | 0.034293 | 0.000449
2015 | 2015-02-17 | C | 210 | 0.0071947 | 0.00064143
2015 | 2015-02-17 | C | 2826 | 0.1919 | 0.0086318
2015 | 2015-02-17 | B | 27 | 0.030151 | 8.2469e-05
2015 | 2015-02-17 | B | 11 | 0.0090201 | 3.3599e-05
2015 | 2015-02-17 | B | 4 | 0.0047311 | 1.2218e-05
2015 | 2015-02-17 | B | 5 | 9.036e-05 | 1.5272e-05
2015 | 2015-02-17 | B | 44 | 0.048541 | 0.00013439
2015 | 2015-02-17 | B | 4 | 0.00013175 | 1.2218e-05
2015 | 2015-02-17 | C | 5 | 0.0015758 | 1.5272e-05
2015 | 2015-02-17 | C | 1 | 0.00034143 | 3.0544e-06
2015 | 2015-02-17 | C | 1 | 8.6186e-05 | 3.0544e-06
2015 | 2015-02-18 | B | 1 | 0.00075322 | 3.0544e-06
2015 | 2015-02-18 | B | 20 | 0.0005722 | 6.1088e-05
2015 | 2015-02-18 | B | 46 | 0.047764 | 0.0001405
2015 | 2015-02-18 | C | 76 | 0.086819 | 0.00023214
2015 | 2015-02-18 | B | 158 | 0.023015 | 0.0004826
2015 | 2015-02-18 | B | 3 | 0.0020413 | 9.1633e-06
2015 | 2015-02-18 | B | 26 | 0.029777 | 7.9415e-05
2015 | 2015-02-18 | B | 295 | 0.29023 | 0.00090105
2015 | 2015-02-18 | B | 79 | 0.0032415 | 0.0002413
2015 | 2015-02-19 | C | 7 | 0.0026225 | 2.1381e-05
2015 | 2015-02-19 | B | 105 | 0.0083243 | 0.00032071
2015 | 2015-02-19 | B | 231 | 0.30848 | 0.00070557
2015 | 2015-02-19 | B | 27 | 0.027534 | 8.2469e-05
2015 | 2015-02-19 | B | 13 | 0.014534 | 3.9708e-05
2015 | 2015-02-19 | B | 24 | 0.022424 | 7.3306e-05
2015 | 2015-02-19 | B | 5 | 0.0032334 | 1.5272e-05
2015 | 2015-02-19 | C | 323 | 0.027917 | 0.00098658
2015 | 2015-02-19 | C | 24 | 0.007734 | 7.3306e-05
2015 | 2015-02-19 | C | 2 | 0.001006 | 6.1088e-06
2015 | 2015-02-19 | C | 1 | 0.00023519 | 3.0544e-06
2015 | 2015-02-19 | C | 188 | 0.078765 | 0.00057423
2015 | 2015-02-19 | C | 903 | 0.098461 | 0.0027581
2015 | 2015-02-19 | C | 1 | 0.00045445 | 3.0544e-06
2015 | 2015-02-19 | C | 2 | 0.00093272 | 6.1088e-06
2015 | 2015-02-19 | B | 1 | 1.6443e-05 | 3.0544e-06
2015 | 2015-02-20 | C | 21 | 0.0052111 | 6.4143e-05
2015 | 2015-02-20 | B | 137 | 0.19893 | 0.00041846
2015 | 2015-02-20 | B | 23 | 0.025993 | 7.0252e-05
2015 | 2015-02-20 | B | 38 | 0.0055867 | 0.00011607
2015 | 2015-02-20 | B | 57 | 0.0043322 | 0.0001741
2015 | 2015-02-20 | B | 69 | 0.038695 | 0.00021076
2015 | 2015-02-20 | C | 1 | 0.00092025 | 3.0544e-06
2015 | 2015-02-20 | C | 9 | 0.0027807 | 2.749e-05
2015 | 2015-02-21 | C | 526 | 0.024547 | 0.0016066
2015 | 2015-02-21 | B | 36 | 0.013474 | 0.00010996
2015 | 2015-02-21 | B | 23 | 0.02674 | 7.0252e-05
2015 | 2015-02-21 | B | 433 | 0.35325 | 0.0013226
2015 | 2015-02-21 | C | 30 | 0.0095344 | 9.1633e-05
2015 | 2015-02-22 | C | 429 | 0.18498 | 0.0013103
2015 | 2015-02-22 | C | 1 | 0.00019599 | 3.0544e-06
2015 | 2015-02-22 | C | 6 | 0.0018327 | 1.8327e-05
2015 | 2015-02-22 | C | 29 | 0.0034518 | 8.8578e-05
2015 | 2015-02-22 | C | 528 | 0.28024 | 0.0016127
2015 | 2015-02-23 | C | 246 | 0.046272 | 0.00075139
2015 | 2015-02-23 | C | 216 | 0.070049 | 0.00065976
2015 | 2015-02-23 | B | 17 | 0.019916 | 5.1925e-05
2015 | 2015-02-23 | B | 19 | 0.019267 | 5.8034e-05
2015 | 2015-02-23 | B | 28 | 0.028961 | 8.5524e-05
2015 | 2015-02-23 | C | 2826 | 0.21637 | 0.0086318
2015 | 2015-02-23 | C | 439 | 0.088568 | 0.0013409
2015 | 2015-02-23 | C | 529 | 0.036645 | 0.0016158
2015 | 2015-02-23 | C | 513 | 0.22608 | 0.0015669
2015 | 2015-02-23 | C | 127 | 0.0071699 | 0.00038791
2015 | 2015-02-23 | C | 2 | 0.0022593 | 6.1088e-06
2015 | 2015-02-23 | C | 6 | 0.0073673 | 1.8327e-05
2015 | 2015-02-24 | B | 39 | 0.0076238 | 0.00011912
2015 | 2015-02-24 | B | 12 | 0.014926 | 3.6653e-05
2015 | 2015-02-24 | C | 15 | 0.018052 | 4.5816e-05
2015 | 2015-02-24 | B | 1 | 0.0010446 | 3.0544e-06
2015 | 2015-02-24 | B | 9 | 0.0087322 | 2.749e-05
2015 | 2015-02-24 | C | 22 | 0.004287 | 6.7197e-05
2015 | 2015-02-24 | C | 1 | 0.00023519 | 3.0544e-06
2015 | 2015-02-24 | C | 4 | 0.00042787 | 1.2218e-05
2015 | 2015-02-25 | C | 66 | 0.020701 | 0.00020159
2015 | 2015-02-25 | C | 1 | 0.00019808 | 3.0544e-06
2015 | 2015-02-25 | B | 2 | 0.0013424 | 6.1088e-06
2015 | 2015-02-25 | B | 4 | 0.0045061 | 1.2218e-05
2015 | 2015-02-25 | B | 7 | 0.0055341 | 2.1381e-05
2015 | 2015-02-25 | B | 91 | 0.058926 | 0.00027795
2015 | 2015-02-25 | B | 95 | 0.11176 | 0.00029017
2015 | 2015-02-25 | B | 27 | 0.030694 | 8.2469e-05
2015 | 2015-02-25 | C | 1 | 0.00036119 | 3.0544e-06
2015 | 2015-02-25 | C | 1 | 0.00015537 | 3.0544e-06
2015 | 2015-02-25 | C | 258 | 0.043777 | 0.00078804
2015 | 2015-02-26 | C | 1 | 0.00031959 | 3.0544e-06
2015 | 2015-02-26 | C | 1 | 3.3599e-05 | 3.0544e-06
2015 | 2015-02-26 | B | 125 | 0.13992 | 0.0003818
2015 | 2015-02-26 | B | 17 | 0.017294 | 5.1925e-05
2015 | 2015-02-26 | C | 1 | 0.00015394 | 3.0544e-06
2015 | 2015-02-27 | C | 70 | 0.0056945 | 0.00021381
2015 | 2015-02-27 | C | 1 | 0.00065044 | 3.0544e-06
2015 | 2015-02-27 | B | 42 | 0.052854 | 0.00012829
2015 | 2015-02-27 | C | 1 | 0.00012844 | 3.0544e-06
2015 | 2015-02-27 | C | 4 | 0.0015317 | 1.2218e-05
2015 | 2015-02-27 | C | 1 | 0.00031797 | 3.0544e-06
2015 | 2015-02-27 | C | 7 | 0.026136 | 2.1381e-05
2015 | 2015-02-27 | C | 13 | 0.0010489 | 3.9708e-05
2015 | 2015-02-28 | B | 2 | 0.00051925 | 6.1088e-06
2015 | 2015-02-28 | C | 331 | 0.12762 | 0.001011
2015 | 2015-02-28 | B | 23 | 0.025046 | 7.0252e-05
2015 | 2015-03-01 | C | 2 | 0.00052465 | 6.1088e-06
2015 | 2015-03-01 | B | 27 | 0.0087266 | 8.2469e-05
2015 | 2015-03-01 | C | 676 | 0.13853 | 0.0020648
2015 | 2015-03-01 | C | 11270 | 0.31629 | 0.034423
2015 | 2015-03-01 | C | 3007 | 0.48154 | 0.0091847
2015 | 2015-03-02 | B | 29 | 0.031529 | 8.8578e-05
2015 | 2015-03-02 | C | 88 | 0.015321 | 0.00026879
2015 | 2015-03-02 | C | 1 | 0.00021203 | 3.0544e-06
2015 | 2015-03-02 | C | 118 | 0.06102 | 0.00036042
2015 | 2015-03-02 | B | 17 | 0.012047 | 5.1925e-05
2015 | 2015-03-03 | C | 2 | 0.0014462 | 6.1088e-06
2015 | 2015-03-03 | B | 137 | 0.21268 | 0.00041846
2015 | 2015-03-03 | B | 17 | 0.018382 | 5.1925e-05
2015 | 2015-03-03 | B | 27 | 0.034284 | 8.2469e-05
2015 | 2015-03-03 | B | 2 | 0.0023336 | 6.1088e-06
2015 | 2015-03-03 | B | 63 | 0.071391 | 0.00019243
2015 | 2015-03-03 | B | 46 | 0.056433 | 0.0001405
2015 | 2015-03-03 | B | 116 | 0.12901 | 0.00035431
2015 | 2015-03-03 | C | 185 | 0.0012526 | 0.00056507
2015 | 2015-03-03 | B | 86 | 0.020134 | 0.00026268
2015 | 2015-03-04 | B | 16 | 0.00078193 | 4.8871e-05
2015 | 2015-03-04 | B | 7 | 0.001796 | 2.1381e-05
2015 | 2015-03-04 | C | 4 | 0.00027408 | 1.2218e-05
2015 | 2015-03-04 | B | 15 | 0.015513 | 4.5816e-05
2015 | 2015-03-04 | B | 10 | 0.0095945 | 3.0544e-05
2015 | 2015-03-04 | C | 5 | 0.00044355 | 1.5272e-05
2015 | 2015-03-04 | C | 1 | 0.00074874 | 3.0544e-06
2015 | 2015-03-04 | C | 420 | 0.058125 | 0.0012829
2015 | 2015-03-05 | B | 16 | 0.0003421 | 4.8871e-05
2015 | 2015-03-05 | C | 1 | 0.0004913 | 3.0544e-06
2015 | 2015-03-05 | B | 72 | 0.074047 | 0.00021992
2015 | 2015-03-05 | B | 11 | 0.012767 | 3.3599e-05
2015 | 2015-03-05 | B | 29 | 0.026396 | 8.8578e-05
2015 | 2015-03-05 | B | 131 | 0.14249 | 0.00040013
2015 | 2015-03-05 | B | 29 | 0.021436 | 8.8578e-05
2015 | 2015-03-05 | B | 20 | 0.024523 | 6.1088e-05
2015 | 2015-03-05 | B | 45 | 0.034468 | 0.00013745
2015 | 2015-03-05 | C | 1 | 0.00043246 | 3.0544e-06
2015 | 2015-03-05 | C | 137 | 0.23523 | 0.00041846
2015 | 2015-03-05 | C | 175 | 0.046726 | 0.00053452
2015 | 2015-03-05 | C | 1 | 0.00051345 | 3.0544e-06
2015 | 2015-03-05 | B | 65 | 0.0059561 | 0.00019854
2015 | 2015-03-05 | C | 280 | 0.055173 | 0.00085524
2015 | 2015-03-05 | C | 1 | 0.00014646 | 3.0544e-06
2015 | 2015-03-05 | C | 4 | 0.0030178 | 1.2218e-05
2015 | 2015-03-05 | C | 4 | 0.00098943 | 1.2218e-05
2015 | 2015-03-05 | B | 40 | 0.014561 | 0.00012218
2015 | 2015-03-06 | C | 18 | 0.0029609 | 5.498e-05
2015 | 2015-03-06 | C | 1 | 0.00029353 | 3.0544e-06
2015 | 2015-03-06 | B | 101 | 0.0019538 | 0.0003085
2015 | 2015-03-06 | B | 57 | 0.06803 | 0.0001741
2015 | 2015-03-06 | C | 7 | 0.0012401 | 2.1381e-05
2015 | 2015-03-06 | C | 281 | 0.014949 | 0.00085829
2015 | 2015-03-06 | C | 15 | 0.0027329 | 4.5816e-05
2015 | 2015-03-06 | B | 103 | 0.091833 | 0.00031461
2015 | 2015-03-06 | C | 118 | 0.033712 | 0.00036042
2015 | 2015-03-06 | C | 198 | 0.073188 | 0.00060478
2015 | 2015-03-06 | C | 167 | 0.15405 | 0.00051009
2015 | 2015-03-06 | C | 246 | 0.037033 | 0.00075139
2015 | 2015-03-06 | C | 899 | 0.40868 | 0.0027459
2015 | 2015-03-06 | C | 163 | 0.22803 | 0.00049787
2015 | 2015-03-06 | C | 35 | 0.01204 | 0.0001069
2015 | 2015-03-06 | C | 13 | 0.0063929 | 3.9708e-05
2015 | 2015-03-06 | C | 904 | 0.36319 | 0.0027612
2015 | 2015-03-06 | C | 653 | 0.49075 | 0.0019945
2015 | 2015-03-06 | C | 764 | 0.22117 | 0.0023336
2015 | 2015-03-06 | C | 194 | 0.019967 | 0.00059256
2015 | 2015-03-06 | C | 335 | 0.084117 | 0.0010232
2015 | 2015-03-06 | C | 246 | 0.049961 | 0.00075139
2015 | 2015-03-06 | C | 58 | 0.039485 | 0.00017716
2015 | 2015-03-06 | C | 27 | 0.023012 | 8.2469e-05
2015 | 2015-03-06 | C | 2 | 0.0015534 | 6.1088e-06
2015 | 2015-03-06 | C | 926 | 0.25682 | 0.0028284
2015 | 2015-03-06 | C | 2 | 0.00194 | 6.1088e-06
2015 | 2015-03-06 | C | 143 | 0.040962 | 0.00043678
2015 | 2015-03-06 | C | 3 | 0.0034363 | 9.1633e-06
2015 | 2015-03-06 | C | 80 | 0.03313 | 0.00024435
2015 | 2015-03-06 | C | 115 | 0.05225 | 0.00035126
2015 | 2015-03-06 | C | 28 | 0.0042049 | 8.5524e-05
2015 | 2015-03-06 | C | 40 | 0.0048355 | 0.00012218
2015 | 2015-03-06 | C | 143 | 0.059503 | 0.00043678
2015 | 2015-03-06 | C | 1 | 0.0031933 | 3.0544e-06
2015 | 2015-03-07 | C | 2 | 0.0011907 | 6.1088e-06
2015 | 2015-03-07 | C | 31 | 0.012797 | 9.4687e-05
2015 | 2015-03-07 | C | 2 | 0.0014395 | 6.1088e-06
2015 | 2015-03-07 | C | 1 | 0.00071703 | 3.0544e-06
2015 | 2015-03-07 | C | 23 | 0.021479 | 7.0252e-05
2015 | 2015-03-07 | C | 143 | 0.068396 | 0.00043678
2015 | 2015-03-07 | C | 194 | 0.13495 | 0.00059256
2015 | 2015-03-07 | C | 54 | 0.012041 | 0.00016494
2015 | 2015-03-07 | C | 4 | 0.0011352 | 1.2218e-05
2015 | 2015-03-07 | C | 6 | 0.00095858 | 1.8327e-05
2015 | 2015-03-07 | C | 248 | 0.087014 | 0.0007575
2015 | 2015-03-07 | C | 339 | 0.21458 | 0.0010354
2015 | 2015-03-07 | C | 1 | 0.0015558 | 3.0544e-06
2015 | 2015-03-07 | C | 251 | 0.12922 | 0.00076666
2015 | 2015-03-07 | C | 78 | 0.019298 | 0.00023825
2015 | 2015-03-07 | C | 4 | 0.00067503 | 1.2218e-05
2015 | 2015-03-07 | C | 58 | 0.070018 | 0.00017716
2015 | 2015-03-07 | C | 324 | 0.0010886 | 0.00098963
2015 | 2015-03-07 | C | 1 | 0.00033624 | 3.0544e-06
2015 | 2015-03-07 | C | 1 | 0.00071708 | 3.0544e-06
2015 | 2015-03-07 | C | 3187 | 0.42756 | 0.0097344
2015 | 2015-03-07 | C | 246 | 0.12284 | 0.00075139
2015 | 2015-03-07 | C | 2 | 0.00079843 | 6.1088e-06
2015 | 2015-03-07 | C | 11 | 0.0043683 | 3.3599e-05
2015 | 2015-03-07 | C | 2 | 0.0047996 | 6.1088e-06
2015 | 2015-03-07 | C | 1 | 0.00011821 | 3.0544e-06
2015 | 2015-03-07 | C | 8 | 0.0012914 | 2.4435e-05
2015 | 2015-03-07 | C | 34 | 0.0071293 | 0.00010385
2015 | 2015-03-08 | C | 408 | 0.021851 | 0.0012462
2015 | 2015-03-08 | C | 69 | 0.017673 | 0.00021076
2015 | 2015-03-08 | C | 201 | 0.075941 | 0.00061394
2015 | 2015-03-08 | C | 1 | 0.0014627 | 3.0544e-06
2015 | 2015-03-08 | C | 1 | 0.0014343 | 3.0544e-06
2015 | 2015-03-08 | C | 1 | 0.0012143 | 3.0544e-06
2015 | 2015-03-08 | C | 2 | 9.7742e-05 | 6.1088e-06
2015 | 2015-03-08 | C | 115 | 0.039013 | 0.00035126
2015 | 2015-03-08 | C | 73 | 0.010926 | 0.00022297
2015 | 2015-03-08 | C | 19 | 0.0062153 | 5.8034e-05
2015 | 2015-03-08 | C | 15 | 0.0011819 | 4.5816e-05
2015 | 2015-03-09 | C | 4 | 0.0003003 | 1.2218e-05
2015 | 2015-03-09 | B | 37 | 0.049387 | 0.00011301
2015 | 2015-03-09 | B | 326 | 0.38535 | 0.00099574
2015 | 2015-03-09 | B | 4 | 0.0019182 | 1.2218e-05
2015 | 2015-03-09 | B | 2 | 0.0020612 | 6.1088e-06
2015 | 2015-03-09 | B | 2 | 0.001902 | 6.1088e-06
2015 | 2015-03-09 | B | 4 | 0.0021617 | 1.2218e-05
2015 | 2015-03-09 | C | 7 | 0.0022022 | 2.1381e-05
2015 | 2015-03-09 | C | 1 | 0.00017018 | 3.0544e-06
2015 | 2015-03-09 | B | 1 | 0.00026573 | 3.0544e-06
2015 | 2015-03-09 | B | 2 | 0.00056812 | 6.1088e-06
2015 | 2015-03-09 | C | 65 | 0.015956 | 0.00019854
2015 | 2015-03-09 | C | 18 | 0.0010893 | 5.498e-05
2015 | 2015-03-10 | C | 1900 | 0.26975 | 0.0058034
2015 | 2015-03-10 | B | 16 | 0.00068419 | 4.8871e-05
2015 | 2015-03-10 | C | 1 | 0.00067829 | 3.0544e-06
2015 | 2015-03-10 | B | 9 | 0.0092911 | 2.749e-05
2015 | 2015-03-10 | B | 11 | 0.014111 | 3.3599e-05
2015 | 2015-03-10 | B | 29 | 0.025921 | 8.8578e-05
2015 | 2015-03-10 | B | 26 | 0.027081 | 7.9415e-05
2015 | 2015-03-10 | B | 2 | 0.00062921 | 6.1088e-06
2015 | 2015-03-10 | B | 8 | 0.0026708 | 2.4435e-05
2015 | 2015-03-10 | B | 63 | 0.065618 | 0.00019243
2015 | 2015-03-10 | B | 6 | 0.0049665 | 1.8327e-05
2015 | 2015-03-10 | B | 15 | 0.01394 | 4.5816e-05
2015 | 2015-03-10 | C | 119 | 0.02168 | 0.00036348
2015 | 2015-03-10 | C | 1434 | 0.017545 | 0.00438
2015 | 2015-03-10 | C | 2 | 0.0021965 | 6.1088e-06
2015 | 2015-03-10 | B | 5 | 0.0009316 | 1.5272e-05
2015 | 2015-03-10 | C | 676 | 0.21183 | 0.0020648
2015 | 2015-03-10 | C | 1 | 0.00018861 | 3.0544e-06
2015 | 2015-03-10 | C | 26 | 0.0019854 | 7.9415e-05
2015 | 2015-03-10 | C | 9 | 0.00095344 | 2.749e-05
2015 | 2015-03-11 | B | 101 | 0.20962 | 0.0003085
2015 | 2015-03-11 | C | 1 | 0.0015658 | 3.0544e-06
2015 | 2015-03-11 | C | 1 | 0.00044676 | 3.0544e-06
2015 | 2015-03-11 | B | 27 | 0.036249 | 8.2469e-05
2015 | 2015-03-11 | B | 67 | 0.039043 | 0.00020465
2015 | 2015-03-11 | B | 38 | 0.026098 | 0.00011607
2015 | 2015-03-11 | C | 2 | 0.00018327 | 6.1088e-06
2015 | 2015-03-11 | C | 17 | 0.0071501 | 5.1925e-05
2015 | 2015-03-11 | C | 86 | 0.03953 | 0.00026268
2015 | 2015-03-11 | C | 65 | 0.019742 | 0.00019854
2015 | 2015-03-11 | C | 19 | 0.002107 | 5.8034e-05
2015 | 2015-03-11 | C | 18 | 0.0036836 | 5.498e-05
2015 | 2015-03-12 | B | 81 | 0.026493 | 0.00024741
2015 | 2015-03-12 | C | 379 | 0.1402 | 0.0011576
2015 | 2015-03-12 | B | 9 | 0.0077269 | 2.749e-05
2015 | 2015-03-12 | C | 1 | 0.00037483 | 3.0544e-06
2015 | 2015-03-12 | B | 13 | 0.012826 | 3.9708e-05
2015 | 2015-03-12 | B | 17 | 0.018981 | 5.1925e-05
2015 | 2015-03-12 | B | 75 | 0.096894 | 0.00022908
2015 | 2015-03-12 | C | 1 | 0.0088103 | 3.0544e-06
2015 | 2015-03-12 | B | 23 | 0.017047 | 7.0252e-05
2015 | 2015-03-12 | C | 2 | 0.0031506 | 6.1088e-06
2015 | 2015-03-12 | C | 339 | 0.021885 | 0.0010354
2015 | 2015-03-12 | C | 216 | 0.04561 | 0.00065976
2015 | 2015-03-12 | C | 1 | 0.001071 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.00065227 | 3.0544e-06
2015 | 2015-03-12 | C | 315 | 0.10616 | 0.00096214
2015 | 2015-03-12 | C | 1 | 0.0081322 | 3.0544e-06
2015 | 2015-03-12 | C | 5 | 0.0039281 | 1.5272e-05
2015 | 2015-03-12 | C | 2 | 0.0029551 | 6.1088e-06
2015 | 2015-03-12 | C | 1264 | 1.194 | 0.0038608
2015 | 2015-03-12 | C | 3 | 0.0091237 | 9.1633e-06
2015 | 2015-03-12 | C | 16 | 0.017203 | 4.8871e-05
2015 | 2015-03-12 | C | 1 | 0.0086039 | 3.0544e-06
2015 | 2015-03-12 | C | 20 | 0.0098597 | 6.1088e-05
2015 | 2015-03-12 | C | 1104 | 0.29329 | 0.0033721
2015 | 2015-03-12 | C | 3 | 0.011934 | 9.1633e-06
2015 | 2015-03-12 | C | 270 | 0.099457 | 0.00082469
2015 | 2015-03-12 | C | 1 | 0.00091867 | 3.0544e-06
2015 | 2015-03-12 | C | 2 | 0.015392 | 6.1088e-06
2015 | 2015-03-12 | C | 1 | 0.0042879 | 3.0544e-06
2015 | 2015-03-12 | C | 16 | 0.011513 | 4.8871e-05
2015 | 2015-03-12 | C | 6 | 0.023494 | 1.8327e-05
2015 | 2015-03-12 | C | 1 | 0.00024715 | 3.0544e-06
2015 | 2015-03-12 | C | 2 | 0.00059694 | 6.1088e-06
2015 | 2015-03-12 | C | 1 | 0.00091673 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.0042749 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.00050072 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.00079283 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.0033699 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.0024256 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.0039166 | 3.0544e-06
2015 | 2015-03-12 | C | 5 | 0.023633 | 1.5272e-05
2015 | 2015-03-12 | C | 1459 | 0.2165 | 0.0044564
2015 | 2015-03-12 | C | 186 | 0.12112 | 0.00056812
2015 | 2015-03-12 | C | 1 | 0.0046463 | 3.0544e-06
2015 | 2015-03-12 | C | 2 | 0.0018113 | 6.1088e-06
2015 | 2015-03-12 | C | 1 | 0.0022446 | 3.0544e-06
2015 | 2015-03-12 | C | 6 | 0.0097779 | 1.8327e-05
2015 | 2015-03-12 | C | 1 | 0.00024939 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.0038373 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.0028267 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.0025997 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.00094738 | 3.0544e-06
2015 | 2015-03-12 | C | 3 | 0.01026 | 9.1633e-06
2015 | 2015-03-12 | C | 2 | 0.0075441 | 6.1088e-06
2015 | 2015-03-12 | C | 1 | 0.0031469 | 3.0544e-06
2015 | 2015-03-12 | C | 2 | 0.003526 | 6.1088e-06
2015 | 2015-03-12 | C | 1 | 0.0072242 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.002004 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.0028902 | 3.0544e-06
2015 | 2015-03-12 | C | 1 | 0.00039428 | 3.0544e-06
2015 | 2015-03-12 | C | 3 | 0.0085022 | 9.1633e-06
2015 | 2015-03-12 | C | 48 | 0.012048 | 0.00014661
2015 | 2015-03-12 | C | 2 | 0.0055994 | 6.1088e-06
2015 | 2015-03-13 | C | 2 | 0.0092287 | 6.1088e-06
2015 | 2015-03-13 | C | 1 | 0.0050597 | 3.0544e-06
2015 | 2015-03-13 | C | 4 | 0.0046878 | 1.2218e-05
2015 | 2015-03-13 | C | 1 | 0.00046437 | 3.0544e-06
2015 | 2015-03-13 | C | 1 | 0.0023298 | 3.0544e-06
2015 | 2015-03-13 | C | 1 | 0.00069738 | 3.0544e-06
2015 | 2015-03-13 | B | 125 | 0.14012 | 0.0003818
2015 | 2015-03-13 | B | 71 | 0.076336 | 0.00021686
2015 | 2015-03-13 | B | 46 | 0.050265 | 0.0001405
2015 | 2015-03-13 | C | 1 | 0.0011428 | 3.0544e-06
2015 | 2015-03-13 | B | 5 | 0.0029188 | 1.5272e-05
2015 | 2015-03-13 | B | 7 | 0.001682 | 2.1381e-05
2015 | 2015-03-13 | C | 1 | 0.00053895 | 3.0544e-06
2015 | 2015-03-13 | C | 2 | 0.0089224 | 6.1088e-06
2015 | 2015-03-13 | C | 1 | 0.0015703 | 3.0544e-06
2015 | 2015-03-13 | C | 1 | 0.0035376 | 3.0544e-06
2015 | 2015-03-13 | C | 2 | 0.0035772 | 6.1088e-06
2015 | 2015-03-13 | C | 6 | 0.0035093 | 1.8327e-05
2015 | 2015-03-13 | C | 1 | 0.0039827 | 3.0544e-06
2015 | 2015-03-13 | C | 1 | 0.00030855 | 3.0544e-06
2015 | 2015-03-13 | C | 5 | 0.024512 | 1.5272e-05
2015 | 2015-03-13 | C | 1 | 0.0019105 | 3.0544e-06
2015 | 2015-03-13 | B | 114 | 0.026489 | 0.0003482
2015 | 2015-03-14 | C | 185 | 0.044008 | 0.00056507
2015 | 2015-03-14 | C | 5 | 0.00068506 | 1.5272e-05
2015 | 2015-03-14 | B | 7 | 0.0011008 | 2.1381e-05
2015 | 2015-03-14 | C | 3 | 5.3147e-05 | 9.1633e-06
2015 | 2015-03-14 | C | 1 | 0.004093 | 3.0544e-06
2015 | 2015-03-14 | C | 46 | 0.014767 | 0.0001405
2015 | 2015-03-14 | C | 185 | 0.010548 | 0.00056507
2015 | 2015-03-14 | C | 222 | 0.034582 | 0.00067808
2015 | 2015-03-15 | B | 76 | 0.021106 | 0.00023214
2015 | 2015-03-15 | C | 281 | 0.034387 | 0.00085829
2015 | 2015-03-15 | B | 30 | 0.017065 | 9.1633e-05
2015 | 2015-03-15 | C | 281 | 0.022087 | 0.00085829
2015 | 2015-03-15 | C | 281 | 0.084141 | 0.00085829
2015 | 2015-03-15 | C | 688 | 0.033378 | 0.0021014
2015 | 2015-03-15 | C | 7 | 0.016069 | 2.1381e-05
2015 | 2015-03-16 | C | 480 | 0.010025 | 0.0014661
2015 | 2015-03-16 | C | 92 | 0.024317 | 0.00028101
2015 | 2015-03-16 | C | 1 | 0.0003255 | 3.0544e-06
2015 | 2015-03-16 | C | 1 | 1.4967e-05 | 3.0544e-06
2015 | 2015-03-16 | C | 4 | 0.0007687 | 1.2218e-05
2015 | 2015-03-16 | C | 1 | 0.0005301 | 3.0544e-06
2015 | 2015-03-16 | C | 213 | 0.04486 | 0.00065059
2015 | 2015-03-16 | C | 1 | 0.00089322 | 3.0544e-06
2015 | 2015-03-16 | C | 4 | 0.0031123 | 1.2218e-05
2015 | 2015-03-16 | C | 3 | 0.00024939 | 9.1633e-06
2015 | 2015-03-16 | C | 75 | 0.051788 | 0.00022908
2015 | 2015-03-17 | C | 76 | 0.025249 | 0.00023214
2015 | 2015-03-17 | C | 1 | 0.0014938 | 3.0544e-06
2015 | 2015-03-17 | C | 353 | 0.060847 | 0.0010782
2015 | 2015-03-17 | C | 10 | 0.0025656 | 3.0544e-05
2015 | 2015-03-17 | B | 16 | 0.0303 | 4.8871e-05
2015 | 2015-03-17 | C | 4 | 0.00094076 | 1.2218e-05
2015 | 2015-03-17 | B | 68 | 0.11672 | 0.0002077
2015 | 2015-03-17 | B | 22 | 0.0062135 | 6.7197e-05
2015 | 2015-03-17 | B | 45 | 0.016201 | 0.00013745
2015 | 2015-03-17 | C | 3 | 0.0022874 | 9.1633e-06
2015 | 2015-03-17 | C | 1 | 0.00021977 | 3.0544e-06
2015 | 2015-03-17 | C | 3 | 0.0018618 | 9.1633e-06
2015 | 2015-03-17 | C | 307 | 0.036383 | 0.00093771
2015 | 2015-03-17 | C | 1 | 0.00026803 | 3.0544e-06
2015 | 2015-03-17 | C | 1 | 0.00040985 | 3.0544e-06
2015 | 2015-03-17 | C | 15 | 0.0022908 | 4.5816e-05
2015 | 2015-03-17 | C | 1 | 0.00039682 | 3.0544e-06
2015 | 2015-03-17 | C | 1 | 0.00050556 | 3.0544e-06
2015 | 2015-03-18 | B | 16 | 0.00029974 | 4.8871e-05
2015 | 2015-03-18 | B | 63 | 0.070236 | 0.00019243
2015 | 2015-03-18 | B | 2 | 0.0022664 | 6.1088e-06
2015 | 2015-03-18 | B | 17 | 0.017706 | 5.1925e-05
2015 | 2015-03-18 | B | 43 | 0.045477 | 0.00013134
2015 | 2015-03-18 | C | 4 | 0.0066533 | 1.2218e-05
2015 | 2015-03-18 | C | 15 | 0.0018678 | 4.5816e-05
2015 | 2015-03-18 | C | 1 | 0.00063395 | 3.0544e-06
2015 | 2015-03-18 | B | 2 | 0.0019937 | 6.1088e-06
2015 | 2015-03-19 | C | 1226 | 0.070931 | 0.0037447
2015 | 2015-03-19 | B | 16 | 0.00034291 | 4.8871e-05
2015 | 2015-03-19 | B | 9 | 0.0070727 | 2.749e-05
2015 | 2015-03-19 | B | 28 | 0.024973 | 8.5524e-05
2015 | 2015-03-19 | B | 28 | 0.029848 | 8.5524e-05
2015 | 2015-03-19 | B | 22 | 0.0088521 | 6.7197e-05
2015 | 2015-03-19 | B | 141 | 0.15978 | 0.00043067
2015 | 2015-03-19 | B | 3 | 0.0029964 | 9.1633e-06
2015 | 2015-03-19 | B | 19 | 0.021642 | 5.8034e-05
2015 | 2015-03-19 | B | 189 | 0.12347 | 0.00057729
2015 | 2015-03-19 | C | 163 | 0.15871 | 0.00049787
2015 | 2015-03-19 | C | 3 | 0.0013928 | 9.1633e-06
2015 | 2015-03-19 | C | 1 | 0.00055606 | 3.0544e-06
2015 | 2015-03-19 | C | 52 | 0.0066709 | 0.00015883
2015 | 2015-03-20 | B | 16 | 0.00033802 | 4.8871e-05
2015 | 2015-03-20 | B | 74 | 0.080895 | 0.00022603
2015 | 2015-03-20 | B | 6 | 0.006706 | 1.8327e-05
2015 | 2015-03-20 | C | 1 | 0.001758 | 3.0544e-06
2015 | 2015-03-20 | B | 52 | 0.0056279 | 0.00015883
2015 | 2015-03-20 | C | 10 | 0.0018545 | 3.0544e-05
2015 | 2015-03-21 | C | 218 | 0.069571 | 0.00066586
2015 | 2015-03-21 | C | 306 | 0.028928 | 0.00093465
2015 | 2015-03-22 | C | 66 | 0.11395 | 0.00020159
2015 | 2015-03-22 | C | 547 | 0.11052 | 0.0016708
2015 | 2015-03-22 | B | 1 | 0.0011945 | 3.0544e-06
2015 | 2015-03-23 | C | 213 | 0.0070557 | 0.00065059
2015 | 2015-03-23 | B | 39 | 0.0435 | 0.00011912
2015 | 2015-03-23 | C | 153 | 0.011683 | 0.00046733
2015 | 2015-03-23 | C | 249 | 0.11031 | 0.00076055
2015 | 2015-03-23 | C | 1 | 0.00032682 | 3.0544e-06
2015 | 2015-03-23 | C | 1306 | 0.13036 | 0.0039891
2015 | 2015-03-23 | C | 34 | 0.0056899 | 0.00010385
2015 | 2015-03-23 | C | 775 | 0.29118 | 0.0023672
2015 | 2015-03-24 | B | 158 | 0.1525 | 0.0004826
2015 | 2015-03-24 | B | 108 | 0.091706 | 0.00032988
2015 | 2015-03-24 | B | 14 | 0.015177 | 4.2762e-05
2015 | 2015-03-24 | B | 4 | 0.0037631 | 1.2218e-05
2015 | 2015-03-24 | C | 393 | 0.033706 | 0.0012004
2015 | 2015-03-24 | B | 4 | 0.0012096 | 1.2218e-05
2015 | 2015-03-24 | C | 2990 | 0.21489 | 0.0091327
2015 | 2015-03-24 | C | 8 | 0.0024435 | 2.4435e-05
2015 | 2015-03-25 | B | 49 | 0.049622 | 0.00014967
2015 | 2015-03-25 | B | 50 | 0.061804 | 0.00015272
2015 | 2015-03-25 | B | 37 | 0.042041 | 0.00011301
2015 | 2015-03-25 | B | 52 | 0.025278 | 0.00015883
2015 | 2015-03-25 | C | 3 | 0.00032774 | 9.1633e-06
2015 | 2015-03-25 | C | 216 | 0.0048402 | 0.00065976
2015 | 2015-03-25 | C | 713 | 0.2679 | 0.0021778
2015 | 2015-03-26 | C | 261 | 0.0098189 | 0.0007972
2015 | 2015-03-26 | B | 16 | 0.00080881 | 4.8871e-05
2015 | 2015-03-26 | B | 125 | 0.11263 | 0.0003818
2015 | 2015-03-26 | C | 1 | 0.0006708 | 3.0544e-06
2015 | 2015-03-26 | B | 3 | 0.0022633 | 9.1633e-06
2015 | 2015-03-26 | B | 3 | 0.0010721 | 9.1633e-06
2015 | 2015-03-26 | B | 2 | 0.00050093 | 6.1088e-06
2015 | 2015-03-26 | C | 1 | 0.00070262 | 3.0544e-06
2015 | 2015-03-26 | C | 261 | 0.069978 | 0.0007972
2015 | 2015-03-26 | C | 176 | 0.078486 | 0.00053758
2015 | 2015-03-26 | C | 5 | 0.00091439 | 1.5272e-05
2015 | 2015-03-26 | C | 92 | 0.026191 | 0.00028101
2015 | 2015-03-27 | C | 91 | 0.0064531 | 0.00027795
2015 | 2015-03-27 | B | 2 | 0.00022603 | 6.1088e-06
2015 | 2015-03-27 | B | 2 | 0.0020098 | 6.1088e-06
2015 | 2015-03-27 | B | 3 | 0.0005498 | 9.1633e-06
2015 | 2015-03-27 | C | 1 | 0.00030203 | 3.0544e-06
2015 | 2015-03-27 | B | 16 | 0.00029322 | 4.8871e-05
2015 | 2015-03-28 | C | 6 | 0.00072431 | 1.8327e-05
2015 | 2015-03-28 | C | 176 | 0.034405 | 0.00053758
2015 | 2015-03-28 | C | 10 | 0.00061903 | 3.0544e-05
2015 | 2015-03-28 | C | 1 | 0.00040069 | 3.0544e-06
2015 | 2015-03-28 | C | 23 | 0.0042233 | 7.0252e-05
2015 | 2015-03-28 | C | 601 | 0.043536 | 0.0018357
2015 | 2015-03-28 | C | 1 | 4.5307e-06 | 3.0544e-06
2015 | 2015-03-29 | C | 1 | 0.0012126 | 3.0544e-06
2015 | 2015-03-29 | C | 1100 | 0.46686 | 0.0033599
2015 | 2015-03-29 | C | 1046 | 0.3633 | 0.0031949
2015 | 2015-03-29 | C | 20 | 0.0058401 | 6.1088e-05
2015 | 2015-03-29 | C | 284 | 0.060997 | 0.00086746
2015 | 2015-03-29 | C | 2 | 0.002413 | 6.1088e-06
2015 | 2015-03-29 | B | 14 | 0.016676 | 4.2762e-05
2015 | 2015-03-29 | C | 7 | 0.0014528 | 2.1381e-05
2015 | 2015-03-29 | C | 284 | 0.05498 | 0.00086746
2015 | 2015-03-29 | C | 1 | 0.00022659 | 3.0544e-06
2015 | 2015-03-29 | C | 1 | 0.00020185 | 3.0544e-06
2015 | 2015-03-29 | C | 4 | 8.5524e-05 | 1.2218e-05
2015 | 2015-03-29 | C | 34 | 0.0062535 | 0.00010385
2015 | 2015-03-29 | C | 7 | 0.0022785 | 2.1381e-05
2015 | 2015-03-29 | C | 107 | 0.10156 | 0.00032682
2015 | 2015-03-29 | C | 1046 | 0.32747 | 0.0031949
2015 | 2015-03-30 | C | 2 | 0.00098398 | 6.1088e-06
2015 | 2015-03-30 | C | 7 | 0.00029933 | 2.1381e-05
2015 | 2015-03-30 | C | 662 | 0.11681 | 0.002022
2015 | 2015-03-30 | B | 28 | 0.028799 | 8.5524e-05
2015 | 2015-03-30 | C | 775 | 0.10815 | 0.0023672
2015 | 2015-03-30 | C | 2 | 0.00044213 | 6.1088e-06
2015 | 2015-03-30 | C | 1 | 0.00048346 | 3.0544e-06
2015 | 2015-03-30 | C | 3 | 0.0013765 | 9.1633e-06
2015 | 2015-03-30 | C | 2 | 0.00015791 | 6.1088e-06
2015 | 2015-03-31 | B | 57 | 0.0036271 | 0.0001741
2015 | 2015-03-31 | C | 18 | 0.00074676 | 5.498e-05
2015 | 2015-03-31 | B | 10 | 0.00021381 | 3.0544e-05
2015 | 2015-03-31 | C | 99 | 0.016934 | 0.00030239
2015 | 2015-03-31 | B | 53 | 0.045328 | 0.00016188
2015 | 2015-03-31 | C | 18 | 0.00034179 | 5.498e-05
2015 | 2015-03-31 | C | 6 | 0.0066653 | 1.8327e-05
2015 | 2015-03-31 | C | 4 | 0.011001 | 1.2218e-05
2016 | 2015-09-13 | B | 13 | 0.0022406 | 3.9309e-05
2016 | 2015-04-10 | B | 117 | 0.073843 | 0.00035378
2016 | 2015-04-15 | B | 4 | 0.0017659 | 1.2095e-05
2016 | 2015-04-01 | B | 10 | 0.00021166 | 3.0238e-05
2016 | 2015-04-02 | B | 194 | 0.03443 | 0.00058661
2016 | 2015-04-08 | B | 325 | 0.054503 | 0.00098272
2016 | 2015-04-09 | B | 87 | 0.070502 | 0.00026307
2016 | 2015-04-10 | B | 215 | 0.15723 | 0.00065011
2016 | 2015-04-08 | B | 24 | 0.0209 | 7.257e-05
2016 | 2015-04-01 | B | 32 | 0.021965 | 9.676e-05
2016 | 2015-04-08 | B | 47 | 0.018759 | 0.00014212
2016 | 2015-04-08 | B | 2 | 0.00027819 | 6.0475e-06
2016 | 2015-04-08 | B | 7 | 0.0064981 | 2.1166e-05
2016 | 2015-04-01 | B | 60 | 0.01905 | 0.00018143
2016 | 2015-04-02 | B | 6 | 0.0065174 | 1.8143e-05
2016 | 2015-04-01 | B | 9 | 0.0053775 | 2.7214e-05
2016 | 2015-04-02 | B | 47 | 0.015728 | 0.00014212
2016 | 2015-04-07 | B | 33 | 0.014153 | 9.9784e-05
2016 | 2015-04-07 | B | 23 | 0.015712 | 6.9546e-05
2016 | 2015-04-01 | B | 19 | 0.0001149 | 5.7451e-05
2016 | 2015-04-01 | B | 29 | 0.03262 | 8.7689e-05
2016 | 2015-04-07 | B | 15 | 0.013367 | 4.5356e-05
2016 | 2015-04-07 | B | 15 | 0.015275 | 4.5356e-05
2016 | 2015-04-08 | B | 38 | 0.031319 | 0.0001149
2016 | 2015-04-08 | B | 1 | 0.00026644 | 3.0238e-06
2016 | 2015-04-08 | B | 10 | 0.009224 | 3.0238e-05
2016 | 2015-04-08 | B | 21 | 0.0074019 | 6.3499e-05
2016 | 2015-04-08 | B | 2 | 0.00083637 | 6.0475e-06
2016 | 2015-04-07 | B | 1 | 0.0012005 | 3.0238e-06
2016 | 2015-04-02 | B | 107 | 0.0056877 | 0.00032354
2016 | 2015-04-10 | B | 5 | 0.0035751 | 1.5119e-05
2016 | 2015-04-10 | B | 3 | 0.0028302 | 9.0713e-06
2016 | 2015-04-02 | B | 280 | 0.084893 | 0.00084665
2016 | 2015-04-08 | B | 5 | 0.0014665 | 1.5119e-05
2016 | 2015-04-08 | B | 3 | 0.0010139 | 9.0713e-06
2016 | 2015-04-09 | B | 3 | 0.00094976 | 9.0713e-06
2016 | 2015-04-08 | B | 1 | 0.00027557 | 3.0238e-06
2016 | 2015-04-08 | B | 1 | 7.1008e-05 | 3.0238e-06
2016 | 2015-04-09 | B | 6 | 0.002074 | 1.8143e-05
2016 | 2015-04-08 | B | 103 | 0.10508 | 0.00031145
2016 | 2015-04-10 | B | 18 | 0.0038997 | 5.4428e-05
2016 | 2015-04-09 | B | 96 | 0.045544 | 0.00029028
2016 | 2015-04-08 | B | 4 | 0.001396 | 1.2095e-05
2016 | 2015-04-09 | B | 4 | 0.0041486 | 1.2095e-05
2016 | 2015-04-10 | B | 4 | 0.0012579 | 1.2095e-05
2016 | 2015-04-10 | B | 6 | 0.0030724 | 1.8143e-05
2016 | 2015-04-10 | B | 10 | 0.0095248 | 3.0238e-05
2016 | 2015-04-12 | B | 62 | 0.080685 | 0.00018747
2016 | 2015-04-14 | B | 48 | 0.019497 | 0.00014514
2016 | 2015-04-17 | B | 131 | 0.030684 | 0.00039611
2016 | 2015-04-14 | B | 38 | 0.045157 | 0.0001149
2016 | 2015-04-16 | B | 31 | 0.036089 | 9.3737e-05
2016 | 2015-04-15 | B | 79 | 0.092007 | 0.00023888
2016 | 2015-04-15 | B | 34 | 0.04431 | 0.00010281
2016 | 2015-04-14 | B | 3 | 0.0015107 | 9.0713e-06
2016 | 2015-04-16 | B | 363 | 0.36661 | 0.0010976
2016 | 2015-04-15 | B | 7 | 0.0010932 | 2.1166e-05
2016 | 2015-05-03 | B | 1210 | 0.66955 | 0.0036588
2016 | 2015-04-15 | B | 2 | 0.0012605 | 6.0475e-06
2016 | 2015-04-15 | B | 32 | 0.029152 | 9.676e-05
2016 | 2015-04-16 | B | 59 | 0.043708 | 0.0001784
2016 | 2015-04-01 | B | 71 | 0.016179 | 0.00021469
2016 | 2015-04-16 | B | 1 | 0.00023293 | 3.0238e-06
2016 | 2015-04-14 | B | 398 | 0.44594 | 0.0012035
2016 | 2015-04-17 | B | 57 | 0.039837 | 0.00017235
2016 | 2015-04-16 | B | 1 | 0.0011279 | 3.0238e-06
2016 | 2015-04-16 | B | 26 | 0.02618 | 7.8618e-05
2016 | 2015-04-16 | B | 4 | 0.0017931 | 1.2095e-05
2016 | 2015-04-21 | B | 50 | 0.058419 | 0.00015119
2016 | 2015-04-09 | B | 1 | 0.0088821 | 3.0238e-06
2016 | 2015-04-09 | B | 152 | 0.17419 | 0.00045961
2016 | 2015-04-09 | B | 21 | 0.019452 | 6.3499e-05
2016 | 2015-04-21 | B | 38 | 0.039486 | 0.0001149
2016 | 2015-04-20 | B | 5 | 0.0060576 | 1.5119e-05
2016 | 2015-04-15 | B | 153 | 0.073012 | 0.00046264
2016 | 2015-04-16 | B | 211 | 0.13706 | 0.00063801
2016 | 2015-04-16 | B | 84 | 0.072389 | 0.000254
2016 | 2015-04-14 | B | 2 | 0.00019352 | 6.0475e-06
2016 | 2015-04-17 | B | 1 | 0.00015981 | 3.0238e-06
2016 | 2015-04-21 | B | 29 | 0.02704 | 8.7689e-05
2016 | 2015-04-21 | B | 98 | 0.10679 | 0.00029633
2016 | 2015-04-23 | B | 94 | 0.095502 | 0.00028423
2016 | 2015-04-12 | B | 1 | 0.00043829 | 3.0238e-06
2016 | 2015-04-13 | B | 1 | 0.00026806 | 3.0238e-06
2016 | 2015-04-07 | B | 4 | 0.0019743 | 1.2095e-05
2016 | 2015-04-13 | B | 23 | 0.0096948 | 6.9546e-05
2016 | 2015-05-01 | B | 36 | 0.035378 | 0.00010886
2016 | 2015-04-21 | B | 7 | 0.0018958 | 2.1166e-05
2016 | 2015-04-21 | B | 16 | 0.0041018 | 4.838e-05
2016 | 2015-04-20 | B | 44 | 0.033188 | 0.00013305
2016 | 2015-04-01 | C | 1 | 0.00084 | 3.0238e-06
2016 | 2015-04-01 | C | 1 | 4.964e-05 | 3.0238e-06
2016 | 2015-04-01 | B | 63 | 0.099131 | 0.0001905
2016 | 2015-04-01 | B | 57 | 0.051752 | 0.00017235
2016 | 2015-04-07 | B | 35 | 0.0074082 | 0.00010583
2016 | 2015-04-01 | C | 4 | 0.0022981 | 1.2095e-05
2016 | 2015-05-06 | B | 10 | 0.0090356 | 3.0238e-05
2016 | 2015-05-05 | B | 20 | 0.016747 | 6.0475e-05
2016 | 2015-04-01 | C | 29 | 0.0091898 | 8.7689e-05
2016 | 2015-04-01 | C | 1 | 0.0003753 | 3.0238e-06
2016 | 2015-04-02 | C | 1 | 0.00024901 | 3.0238e-06
2016 | 2015-04-02 | C | 9 | 0.013417 | 2.7214e-05
2016 | 2015-04-02 | C | 1 | 0.00032939 | 3.0238e-06
2016 | 2015-04-02 | C | 1 | 0.00034536 | 3.0238e-06
2016 | 2015-05-05 | B | 34 | 0.042941 | 0.00010281
2016 | 2015-04-22 | B | 4 | 0.0011406 | 1.2095e-05
2016 | 2015-04-28 | B | 22 | 0.019859 | 6.6523e-05
2016 | 2015-05-08 | B | 6 | 0.006368 | 1.8143e-05
2016 | 2015-05-11 | B | 6 | 0.0047171 | 1.8143e-05
2016 | 2015-05-18 | B | 6 | 0.0066946 | 1.8143e-05
2016 | 2015-05-20 | B | 6 | 0.0065464 | 1.8143e-05
2016 | 2015-04-09 | B | 5 | 0.0012415 | 1.5119e-05
2016 | 2015-05-06 | B | 98 | 0.066126 | 0.00029633
2016 | 2015-04-03 | C | 24 | 0.031949 | 7.257e-05
2016 | 2015-04-03 | C | 18 | 0.0049203 | 5.4428e-05
2016 | 2015-04-03 | C | 28 | 0.0032173 | 8.4665e-05
2016 | 2015-04-04 | C | 18 | 0.005616 | 5.4428e-05
2016 | 2015-04-04 | C | 115 | 0.031298 | 0.00034773
2016 | 2015-04-04 | C | 1 | 0.0003184 | 3.0238e-06
2016 | 2015-04-04 | C | 39 | 0.010613 | 0.00011793
2016 | 2015-04-04 | C | 1 | 0.00017563 | 3.0238e-06
2016 | 2015-04-04 | C | 115 | 0.0041554 | 0.00034773
2016 | 2015-04-04 | C | 1 | 0.00015139 | 3.0238e-06
2016 | 2015-04-04 | C | 599 | 0 | 0.0018112
2016 | 2015-04-05 | C | 991 | 0.38431 | 0.0029965
2016 | 2015-04-05 | C | 1 | 0.00028771 | 3.0238e-06
2016 | 2015-04-05 | C | 1182 | 0.61931 | 0.0035741
2016 | 2015-04-06 | C | 26 | 0.010036 | 7.8618e-05
2016 | 2015-04-06 | C | 156 | 0.028248 | 0.00047171
2016 | 2015-04-06 | C | 79 | 0.025906 | 0.00023888
2016 | 2015-04-06 | C | 1 | 0.00020284 | 3.0238e-06
2016 | 2015-04-07 | C | 151 | 0 | 0.00045659
2016 | 2015-04-07 | C | 1 | 0.00024528 | 3.0238e-06
2016 | 2015-04-07 | C | 32 | 0.04307 | 9.676e-05
2016 | 2015-04-07 | C | 137 | 0.029412 | 0.00041426
2016 | 2015-04-25 | B | 24 | 0.0062556 | 7.257e-05
2016 | 2015-04-23 | B | 45 | 0.034834 | 0.00013607
2016 | 2015-04-07 | C | 135 | 0.065681 | 0.00040821
2016 | 2015-04-28 | B | 68 | 0.011843 | 0.00020562
2016 | 2015-04-07 | C | 1 | 0.00024427 | 3.0238e-06
2016 | 2015-04-07 | C | 68 | 0 | 0.00020562
2016 | 2015-04-07 | C | 5 | 0.0035693 | 1.5119e-05
2016 | 2015-04-07 | C | 8 | 0.0021122 | 2.419e-05
2016 | 2015-04-08 | C | 5 | 0.0025914 | 1.5119e-05
2016 | 2015-05-05 | B | 26 | 0.019947 | 7.8618e-05
2016 | 2015-04-08 | C | 60 | 0.043418 | 0.00018143
2016 | 2015-04-29 | B | 99 | 0.11316 | 0.00029935
2016 | 2015-05-01 | B | 68 | 0.0096708 | 0.00020562
2016 | 2015-04-08 | C | 1 | 0.00052019 | 3.0238e-06
2016 | 2015-04-29 | B | 18 | 0.016467 | 5.4428e-05
2016 | 2015-04-08 | C | 121 | 0.063829 | 0.00036588
2016 | 2015-04-08 | C | 1 | 0.00028131 | 3.0238e-06
2016 | 2015-04-08 | C | 211 | 0.065404 | 0.00063801
2016 | 2015-04-08 | C | 211 | 0.013873 | 0.00063801
2016 | 2015-04-08 | C | 829 | 0.12418 | 0.0025067
2016 | 2015-04-08 | C | 364 | 0.073774 | 0.0011006
2016 | 2015-04-09 | C | 716 | 0.12647 | 0.002165
2016 | 2015-04-09 | C | 1 | 0.00016026 | 3.0238e-06
2016 | 2015-05-01 | B | 22 | 0.0050136 | 6.6523e-05
2016 | 2015-04-09 | C | 1 | 0.0012436 | 3.0238e-06
2016 | 2015-04-29 | B | 15 | 0.017009 | 4.5356e-05
2016 | 2015-04-09 | C | 211 | 0.025718 | 0.00063801
2016 | 2015-04-09 | C | 1 | 0.00016298 | 3.0238e-06
2016 | 2015-04-09 | C | 2 | 0.0005477 | 6.0475e-06
2016 | 2015-05-08 | B | 114 | 0.14284 | 0.00034471
2016 | 2015-04-09 | C | 894 | 0.076954 | 0.0027032
2016 | 2015-05-08 | B | 58 | 0.052087 | 0.00017538
2016 | 2015-04-09 | C | 237 | 0.1071 | 0.00071663
2016 | 2015-04-09 | C | 358 | 0.07234 | 0.0010825
2016 | 2015-04-10 | C | 295 | 0.023699 | 0.00089201
2016 | 2015-04-10 | C | 17 | 0.00293 | 5.1404e-05
2016 | 2015-05-04 | B | 3 | 0.0016782 | 9.0713e-06
2016 | 2015-05-01 | B | 3 | 0.0012428 | 9.0713e-06
2016 | 2015-05-04 | B | 1 | 0.00029769 | 3.0238e-06
2016 | 2015-05-11 | B | 8 | 0.0075231 | 2.419e-05
2016 | 2015-05-06 | B | 1 | 0.00083758 | 3.0238e-06
2016 | 2015-04-10 | B | 6 | 0.0038281 | 1.8143e-05
2016 | 2015-04-28 | B | 157 | 0.134 | 0.00047473
2016 | 2015-04-09 | C | 713 | 0.11398 | 0.0021559
2016 | 2015-05-05 | B | 4 | 0.0047802 | 1.2095e-05
2016 | 2015-05-01 | B | 2 | 0.001003 | 6.0475e-06
2016 | 2015-05-01 | B | 1 | 0.00037807 | 3.0238e-06
2016 | 2015-04-10 | C | 1 | 0.00058066 | 3.0238e-06
2016 | 2015-05-12 | B | 10 | 0.011086 | 3.0238e-05
2016 | 2015-05-01 | B | 7 | 0.0048683 | 2.1166e-05
2016 | 2015-05-01 | B | 3 | 0.0051254 | 9.0713e-06
2016 | 2015-05-01 | B | 3 | 0.0032082 | 9.0713e-06
2016 | 2015-05-06 | B | 65 | 0.049133 | 0.00019654
2016 | 2015-05-13 | B | 29 | 0.039811 | 8.7689e-05
2016 | 2015-04-10 | C | 1 | 0.00063917 | 3.0238e-06
2016 | 2015-05-03 | B | 45 | 0.031704 | 0.00013607
2016 | 2015-05-08 | B | 160 | 0.11805 | 0.0004838
2016 | 2015-04-14 | B | 50 | 0.0083607 | 0.00015119
2016 | 2015-04-10 | C | 1 | 0.00039929 | 3.0238e-06
2016 | 2015-04-10 | C | 156 | 0.08817 | 0.00047171
2016 | 2015-04-10 | C | 8 | 0.0026601 | 2.419e-05
2016 | 2015-04-10 | C | 10 | 0.0043245 | 3.0238e-05
2016 | 2015-04-10 | C | 209 | 0.14698 | 0.00063197
2016 | 2015-04-10 | C | 154 | 0.094951 | 0.00046566
2016 | 2015-04-10 | C | 1 | 0.00022366 | 3.0238e-06
2016 | 2015-04-10 | C | 12 | 0.0074276 | 3.6285e-05
2016 | 2015-04-10 | C | 31 | 0.0049462 | 9.3737e-05
2016 | 2015-04-11 | C | 62 | 0.0089737 | 0.00018747
2016 | 2015-04-11 | C | 5 | 0.0036792 | 1.5119e-05
2016 | 2015-04-11 | C | 1 | 0.0005094 | 3.0238e-06
2016 | 2015-04-11 | C | 3 | 0.00056106 | 9.0713e-06
2016 | 2015-04-11 | C | 5 | 0.0037883 | 1.5119e-05
2016 | 2015-04-11 | C | 1 | 0.00127 | 3.0238e-06
2016 | 2015-04-11 | C | 3 | 0.0021033 | 9.0713e-06
2016 | 2015-05-05 | B | 5 | 0.0030636 | 1.5119e-05
2016 | 2015-04-11 | C | 7 | 0.0019872 | 2.1166e-05
2016 | 2015-04-11 | C | 1 | 0.00034189 | 3.0238e-06
2016 | 2015-05-07 | B | 39 | 0.047173 | 0.00011793
2016 | 2015-04-10 | C | 6 | 0.018525 | 1.8143e-05
2016 | 2015-04-10 | C | 2 | 0.0043361 | 6.0475e-06
2016 | 2015-04-10 | C | 4 | 0.012301 | 1.2095e-05
2016 | 2015-04-11 | C | 988 | 0.096313 | 0.0029875
2016 | 2015-04-11 | C | 1 | 0.00057729 | 3.0238e-06
2016 | 2015-04-11 | C | 2 | 0.00022567 | 6.0475e-06
2016 | 2015-04-11 | C | 2 | 0.00064628 | 6.0475e-06
2016 | 2015-04-11 | C | 1 | 0.00026256 | 3.0238e-06
2016 | 2015-04-11 | C | 166 | 0.10498 | 0.00050194
2016 | 2015-04-12 | C | 698 | 0.079792 | 0.0021106
2016 | 2015-05-05 | B | 252 | 0.31793 | 0.00076199
2016 | 2015-05-08 | B | 68 | 0.072377 | 0.00020562
2016 | 2015-05-13 | B | 71 | 0.075233 | 0.00021469
2016 | 2015-05-19 | B | 51 | 0.054899 | 0.00015421
2016 | 2015-04-12 | C | 20 | 0.0036708 | 6.0475e-05
2016 | 2015-05-21 | B | 62 | 0.056726 | 0.00018747
2016 | 2015-05-26 | B | 62 | 0.045931 | 0.00018747
2016 | 2015-04-12 | C | 3 | 0.0013678 | 9.0713e-06
2016 | 2015-04-12 | C | 1 | 0.00023802 | 3.0238e-06
2016 | 2015-04-12 | C | 1 | 0.00029018 | 3.0238e-06
2016 | 2015-04-13 | C | 698 | 0.12743 | 0.0021106
2016 | 2015-04-13 | C | 196 | 0.091189 | 0.00059266
2016 | 2015-04-13 | C | 1 | 0.00026347 | 3.0238e-06
2016 | 2015-04-13 | C | 106 | 0.016512 | 0.00032052
2016 | 2015-04-13 | C | 29 | 0.0060279 | 8.7689e-05
2016 | 2015-04-13 | C | 1 | 0.000114 | 3.0238e-06
2016 | 2015-04-13 | C | 1 | 0.00036537 | 3.0238e-06
2016 | 2015-04-13 | C | 423 | 0.054266 | 0.0012791
2016 | 2015-05-04 | B | 2 | 0.00094946 | 6.0475e-06
2016 | 2015-05-05 | B | 1 | 0.00031145 | 3.0238e-06
2016 | 2015-05-05 | B | 1 | 0.00045961 | 3.0238e-06
2016 | 2015-04-13 | C | 288 | 0.029318 | 0.00087084
2016 | 2015-04-14 | B | 100 | 0.036371 | 0.00030238
2016 | 2015-04-14 | B | 73 | 0.048437 | 0.00022073
2016 | 2015-04-13 | C | 64 | 0.011998 | 0.00019352
2016 | 2015-05-07 | B | 40 | 0.043542 | 0.00012095
2016 | 2015-04-13 | C | 18 | 0.0032159 | 5.4428e-05
2016 | 2015-04-13 | C | 33 | 0.005257 | 9.9784e-05
2016 | 2015-04-13 | C | 13 | 0.006486 | 3.9309e-05
2016 | 2015-05-10 | B | 351 | 0.3132 | 0.0010613
2016 | 2015-04-13 | C | 5 | 0.001642 | 1.5119e-05
2016 | 2015-04-13 | C | 1 | 0.0012261 | 3.0238e-06
2016 | 2015-04-13 | C | 85 | 0 | 0.00025702
2016 | 2015-04-13 | C | 258 | 0.046232 | 0.00078013
2016 | 2015-04-13 | C | 1 | 0.00020582 | 3.0238e-06
2016 | 2015-04-13 | C | 7 | 0.0012089 | 2.1166e-05
2016 | 2015-04-13 | C | 1 | 0.0011339 | 3.0238e-06
2016 | 2015-04-14 | C | 681 | 0.054605 | 0.0020592
2016 | 2015-04-14 | C | 2 | 0.00062864 | 6.0475e-06
2016 | 2015-04-14 | C | 4 | 0.0013028 | 1.2095e-05
2016 | 2015-04-14 | C | 3 | 0.0060749 | 9.0713e-06
2016 | 2015-04-20 | B | 455 | 0.43728 | 0.0013758
2016 | 2015-04-14 | C | 9 | 0.0085996 | 2.7214e-05
2016 | 2015-04-14 | C | 5 | 0.0018135 | 1.5119e-05
2016 | 2015-05-05 | B | 2 | 0.0030925 | 6.0475e-06
2016 | 2015-05-06 | B | 2 | 0.0018899 | 6.0475e-06
2016 | 2015-04-14 | C | 3 | 0.0024988 | 9.0713e-06
2016 | 2015-04-14 | C | 8 | 4.7322e-05 | 2.419e-05
2016 | 2015-05-05 | B | 31 | 0.0073289 | 9.3737e-05
2016 | 2015-05-07 | B | 2 | 0.0025218 | 6.0475e-06
2016 | 2015-05-06 | B | 19 | 0.0083956 | 5.7451e-05
2016 | 2015-05-08 | B | 2 | 0.0024311 | 6.0475e-06
2016 | 2015-04-14 | C | 9 | 0.0022038 | 2.7214e-05
2016 | 2015-05-07 | C | 265 | 0 | 0.0008013
2016 | 2015-04-15 | C | 76 | 0 | 0.00022981
2016 | 2015-04-15 | C | 1 | 0.00025117 | 3.0238e-06
2016 | 2015-05-11 | B | 3 | 0.0018324 | 9.0713e-06
2016 | 2015-05-13 | B | 4 | 0.0061792 | 1.2095e-05
2016 | 2015-04-15 | C | 1 | 0.00021469 | 3.0238e-06
2016 | 2015-04-15 | C | 18 | 0.005743 | 5.4428e-05
2016 | 2015-04-15 | C | 1 | 0.0001331 | 3.0238e-06
2016 | 2015-04-15 | C | 24 | 0.008114 | 7.257e-05
2016 | 2015-04-14 | C | 1247 | 0.025577 | 0.0037706
2016 | 2015-04-16 | C | 54 | 0.039776 | 0.00016328
2016 | 2015-04-16 | C | 1 | 0.0012989 | 3.0238e-06
2016 | 2015-04-16 | C | 912 | 0.03632 | 0.0027577
2016 | 2015-04-16 | C | 1 | 0.00023898 | 3.0238e-06
2016 | 2015-04-16 | C | 6 | 0.0017598 | 1.8143e-05
2016 | 2015-04-17 | C | 99 | 0.022086 | 0.00029935
2016 | 2015-04-17 | C | 835 | 0.092381 | 0.0025248
2016 | 2015-04-17 | C | 1 | 0.00039047 | 3.0238e-06
2016 | 2015-05-06 | B | 160 | 0.18492 | 0.0004838
2016 | 2015-05-02 | B | 2 | 0.0007502 | 6.0475e-06
2016 | 2015-04-17 | C | 44 | 0.013134 | 0.00013305
2016 | 2015-05-05 | B | 66 | 0.082495 | 0.00019957
2016 | 2015-04-17 | C | 2 | 0.00023999 | 6.0475e-06
2016 | 2015-04-17 | C | 65 | 0.0058603 | 0.00019654
2016 | 2015-04-18 | C | 3 | 0.00025017 | 9.0713e-06
2016 | 2015-04-18 | C | 229 | 0.16299 | 0.00069244
2016 | 2015-04-18 | C | 122 | 0 | 0.0003689
2016 | 2015-04-18 | C | 487 | 0.099577 | 0.0014726
2016 | 2015-04-18 | C | 1315 | 0.46776 | 0.0039762
2016 | 2015-04-18 | C | 5 | 0.00086611 | 1.5119e-05
2016 | 2015-04-18 | C | 1 | 0.00057451 | 3.0238e-06
2016 | 2015-04-18 | C | 1 | 0.00029411 | 3.0238e-06
2016 | 2015-04-18 | C | 1 | 0.0002868 | 3.0238e-06
2016 | 2015-04-18 | C | 475 | 0 | 0.0014363
2016 | 2015-04-18 | C | 135 | 0.075544 | 0.00040821
2016 | 2015-04-18 | C | 612 | 0.16343 | 0.0018505
2016 | 2015-04-19 | C | 1 | 0.00026392 | 3.0238e-06
2016 | 2015-04-19 | C | 2 | 0.00096922 | 6.0475e-06
2016 | 2015-04-19 | C | 1 | 0.00054428 | 3.0238e-06
2016 | 2015-04-19 | C | 53 | 0.01545 | 0.00016026
2016 | 2015-04-20 | C | 1 | 0.00038598 | 3.0238e-06
2016 | 2015-04-20 | C | 4 | 0.00038503 | 1.2095e-05
2016 | 2015-04-20 | C | 3 | 0.0017015 | 9.0713e-06
2016 | 2015-04-20 | C | 1 | 0.0008521 | 3.0238e-06
2016 | 2015-04-20 | C | 285 | 0.08611 | 0.00086177
2016 | 2015-04-18 | C | 475 | 0.072688 | 0.0014363
2016 | 2015-05-14 | B | 20 | 0.013005 | 6.0475e-05
2016 | 2015-04-20 | C | 125 | 0.070082 | 0.00037797
2016 | 2015-04-20 | C | 18 | 0.0078376 | 5.4428e-05
2016 | 2015-05-14 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-05-07 | B | 34 | 0.026036 | 0.00010281
2016 | 2015-04-20 | C | 1 | 0.00075735 | 3.0238e-06
2016 | 2015-04-20 | C | 1 | 0.00045447 | 3.0238e-06
2016 | 2015-04-20 | C | 315 | 0.051878 | 0.00095248
2016 | 2015-04-21 | C | 293 | 0.023236 | 0.00088596
2016 | 2015-05-19 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-05-20 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-05-21 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-05-22 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-05-27 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-05-28 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-04-21 | C | 1 | 0.00035947 | 3.0238e-06
2016 | 2015-05-29 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-05-08 | B | 15 | 0.013924 | 4.5356e-05
2016 | 2015-05-01 | B | 47 | 0.056835 | 0.00014212
2016 | 2015-05-12 | B | 43 | 0.0079053 | 0.00013002
2016 | 2015-05-19 | B | 66 | 0.08479 | 0.00019957
2016 | 2015-04-21 | C | 25 | 0.016225 | 7.5594e-05
2016 | 2015-04-21 | C | 26 | 0.0075905 | 7.8618e-05
2016 | 2015-04-22 | C | 15 | 0.0082934 | 4.5356e-05
2016 | 2015-05-02 | B | 1 | 0.00087624 | 3.0238e-06
2016 | 2015-04-22 | C | 2 | 0.0021461 | 6.0475e-06
2016 | 2015-04-30 | B | 127 | 0.1049 | 0.00038402
2016 | 2015-04-22 | C | 370 | 0.0017084 | 0.0011188
2016 | 2015-05-06 | B | 182 | 0.017367 | 0.00055032
2016 | 2015-04-22 | C | 7 | 0.00028821 | 2.1166e-05
2016 | 2015-04-22 | C | 738 | 0.14316 | 0.0022315
2016 | 2015-04-22 | C | 106 | 0.031638 | 0.00032052
2016 | 2015-05-04 | B | 4 | 0.0050436 | 1.2095e-05
2016 | 2015-04-23 | C | 556 | 0.092991 | 0.0016812
2016 | 2015-04-23 | C | 1077 | 0.28864 | 0.0032566
2016 | 2015-04-24 | C | 527 | 0.094878 | 0.0015935
2016 | 2015-04-28 | B | 4 | 0.00093132 | 1.2095e-05
2016 | 2015-04-24 | C | 41 | 0.010017 | 0.00012397
2016 | 2015-05-12 | B | 39 | 0.042432 | 0.00011793
2016 | 2015-05-14 | B | 21 | 0.022962 | 6.3499e-05
2016 | 2015-04-28 | B | 1 | 0.0010916 | 3.0238e-06
2016 | 2015-04-24 | C | 1 | 0.00025334 | 3.0238e-06
2016 | 2015-04-25 | C | 2 | 0.00056635 | 6.0475e-06
2016 | 2015-04-25 | C | 322 | 0.12047 | 0.00097365
2016 | 2015-04-26 | C | 826 | 0.10504 | 0.0024976
2016 | 2015-04-26 | C | 18 | 0.0017943 | 5.4428e-05
2016 | 2015-04-26 | C | 1 | 0.00017029 | 3.0238e-06
2016 | 2015-04-26 | C | 1 | 8.4161e-05 | 3.0238e-06
2016 | 2015-04-26 | C | 30 | 0.011977 | 9.0713e-05
2016 | 2015-04-27 | C | 336 | 0.059799 | 0.001016
2016 | 2015-04-27 | C | 123 | 0.063468 | 0.00037192
2016 | 2015-04-27 | C | 34 | 0.038826 | 0.00010281
2016 | 2015-04-27 | C | 328 | 0.035847 | 0.00099179
2016 | 2015-04-27 | C | 1 | 0.00028368 | 3.0238e-06
2016 | 2015-04-27 | C | 6 | 0.0024495 | 1.8143e-05
2016 | 2015-04-27 | C | 28 | 0.013123 | 8.4665e-05
2016 | 2015-04-27 | C | 29 | 0.02771 | 8.7689e-05
2016 | 2015-04-27 | C | 259 | 0.10571 | 0.00078315
2016 | 2015-04-27 | C | 5 | 0.0018309 | 1.5119e-05
2016 | 2015-04-27 | C | 103 | 0.033051 | 0.00031145
2016 | 2015-04-27 | C | 59 | 0.054579 | 0.0001784
2016 | 2015-04-27 | C | 678 | 0.26569 | 0.0020501
2016 | 2015-04-27 | C | 403 | 0.10692 | 0.0012186
2016 | 2015-04-27 | C | 1 | 0.001137 | 3.0238e-06
2016 | 2015-04-27 | C | 183 | 0.017901 | 0.00055335
2016 | 2015-04-27 | C | 34 | 0.096811 | 0.00010281
2016 | 2015-04-27 | C | 269 | 0.092019 | 0.00081339
2016 | 2015-04-28 | C | 67 | 0.013054 | 0.00020259
2016 | 2015-04-28 | C | 1 | 0.00013688 | 3.0238e-06
2016 | 2015-04-28 | C | 3 | 0.0069608 | 9.0713e-06
2016 | 2015-04-28 | C | 4 | 0.0033999 | 1.2095e-05
2016 | 2015-04-28 | C | 72 | 0.037229 | 0.00021771
2016 | 2015-04-28 | C | 28 | 0.0027671 | 8.4665e-05
2016 | 2015-04-28 | C | 3 | 0.001161 | 9.0713e-06
2016 | 2015-04-28 | C | 641 | 0.051104 | 0.0019382
2016 | 2015-04-28 | C | 1 | 6.2189e-05 | 3.0238e-06
2016 | 2015-04-28 | C | 49 | 0.011124 | 0.00014816
2016 | 2015-04-28 | C | 6 | 0.0029239 | 1.8143e-05
2016 | 2015-04-28 | C | 35 | 0.021847 | 0.00010583
2016 | 2015-05-13 | B | 12 | 0.0073393 | 3.6285e-05
2016 | 2015-05-01 | C | 4 | 0.00012095 | 1.2095e-05
2016 | 2015-04-28 | C | 1227 | 0.24587 | 0.0037102
2016 | 2015-04-28 | C | 1052 | 0.28662 | 0.003181
2016 | 2015-04-28 | C | 9 | 0.0085179 | 2.7214e-05
2016 | 2015-04-29 | C | 1227 | 0.41188 | 0.0037102
2016 | 2015-04-29 | C | 298 | 0.065834 | 0.00090108
2016 | 2015-05-21 | B | 177 | 0.023246 | 0.00053521
2016 | 2015-05-20 | B | 206 | 0.23286 | 0.00062289
2016 | 2015-04-29 | B | 58 | 0.016602 | 0.00017538
2016 | 2015-04-29 | C | 1227 | 0.092104 | 0.0037102
2016 | 2015-04-29 | C | 253 | 0.044392 | 0.00076501
2016 | 2015-04-29 | C | 7 | 0.0017145 | 2.1166e-05
2016 | 2015-04-29 | C | 1 | 0 | 3.0238e-06
2016 | 2015-04-29 | C | 1 | 0.00010029 | 3.0238e-06
2016 | 2015-04-29 | C | 72 | 0.15792 | 0.00021771
2016 | 2015-04-29 | C | 1 | 0.0004258 | 3.0238e-06
2016 | 2015-04-30 | C | 284 | 0.010691 | 0.00085875
2016 | 2015-04-30 | C | 299 | 0.027619 | 0.0009041
2016 | 2015-04-30 | C | 1 | 0.00058893 | 3.0238e-06
2016 | 2015-04-30 | C | 154 | 0 | 0.00046566
2016 | 2015-04-30 | C | 5 | 0.0014514 | 1.5119e-05
2016 | 2015-04-30 | C | 79 | 0.068273 | 0.00023888
2016 | 2015-04-30 | C | 22 | 0.0029425 | 6.6523e-05
2016 | 2015-04-30 | C | 123 | 0.016737 | 0.00037192
2016 | 2015-04-30 | C | 12 | 0.0020489 | 3.6285e-05
2016 | 2015-04-30 | C | 95 | 0.060611 | 0.00028726
2016 | 2015-05-13 | B | 7 | 0.0051223 | 2.1166e-05
2016 | 2015-05-20 | B | 40 | 0.038579 | 0.00012095
2016 | 2015-04-30 | C | 108 | 0 | 0.00032657
2016 | 2015-04-30 | C | 31 | 0.0087909 | 9.3737e-05
2016 | 2015-04-30 | C | 858 | 0.021097 | 0.0025944
2016 | 2015-04-30 | C | 1 | 3.0036e-05 | 3.0238e-06
2016 | 2015-05-01 | C | 296 | 0.08227 | 0.00089503
2016 | 2015-05-01 | B | 51 | 0.056578 | 0.00015421
2016 | 2015-05-05 | B | 8 | 0.0085125 | 2.419e-05
2016 | 2015-05-01 | C | 76 | 0.021323 | 0.00022981
2016 | 2015-05-11 | B | 166 | 0.012975 | 0.00050194
2016 | 2015-05-01 | C | 1 | 0.0001023 | 3.0238e-06
2016 | 2015-05-01 | C | 1128 | 0.23926 | 0.0034108
2016 | 2015-05-01 | C | 3 | 0.00070937 | 9.0713e-06
2016 | 2015-05-01 | C | 24 | 0.0040688 | 7.257e-05
2016 | 2015-05-02 | C | 1 | 0.00028328 | 3.0238e-06
2016 | 2015-05-02 | C | 327 | 0.051732 | 0.00098877
2016 | 2015-05-02 | C | 1 | 0.00019649 | 3.0238e-06
2016 | 2015-05-02 | C | 9 | 0.0020628 | 2.7214e-05
2016 | 2015-05-03 | C | 306 | 0.048438 | 0.00092527
2016 | 2015-05-03 | C | 5 | 0.0014562 | 1.5119e-05
2016 | 2015-05-06 | B | 6 | 0.0014753 | 1.8143e-05
2016 | 2015-05-04 | C | 12 | 0.0018959 | 3.6285e-05
2016 | 2015-05-04 | C | 9 | 0.0020955 | 2.7214e-05
2016 | 2015-05-26 | B | 104 | 0.12472 | 0.00031447
2016 | 2015-05-28 | B | 104 | 0.131 | 0.00031447
2016 | 2015-05-19 | B | 18 | 0.019077 | 5.4428e-05
2016 | 2015-05-26 | B | 107 | 0.081856 | 0.00032354
2016 | 2015-05-13 | B | 103 | 0.11742 | 0.00031145
2016 | 2015-05-04 | C | 1 | 0.00076521 | 3.0238e-06
2016 | 2015-05-04 | C | 1 | 0.00042968 | 3.0238e-06
2016 | 2015-05-04 | C | 1 | 0.000261 | 3.0238e-06
2016 | 2015-05-05 | C | 7 | 0.0023706 | 2.1166e-05
2016 | 2015-06-06 | B | 16 | 0.020175 | 4.838e-05
2016 | 2015-05-11 | B | 4 | 0.0045235 | 1.2095e-05
2016 | 2015-05-15 | B | 54 | 0.01392 | 0.00016328
2016 | 2015-05-05 | C | 37 | 0.0043064 | 0.00011188
2016 | 2015-05-23 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-05-25 | B | 16 | 0.00082246 | 4.838e-05
2016 | 2015-05-21 | B | 19 | 0.013546 | 5.7451e-05
2016 | 2015-05-19 | B | 12 | 0.0016594 | 3.6285e-05
2016 | 2015-05-06 | B | 6 | 0.00062048 | 1.8143e-05
2016 | 2015-05-05 | C | 5 | 0.0010051 | 1.5119e-05
2016 | 2015-05-05 | C | 765 | 0.12428 | 0.0023132
2016 | 2015-05-06 | C | 11 | 0.0070605 | 3.3261e-05
2016 | 2015-05-06 | C | 1 | 0.00023696 | 3.0238e-06
2016 | 2015-05-06 | C | 1 | 0.13554 | 3.0238e-06
2016 | 2015-05-07 | B | 19 | 0.021985 | 5.7451e-05
2016 | 2015-05-29 | B | 2 | 0.00010281 | 6.0475e-06
2016 | 2015-05-06 | C | 1 | 0.0014772 | 3.0238e-06
2016 | 2015-05-06 | C | 1 | 0 | 3.0238e-06
2016 | 2015-05-13 | B | 6 | 0.006749 | 1.8143e-05
2016 | 2015-05-13 | B | 13 | 0.011124 | 3.9309e-05
2016 | 2015-05-07 | B | 265 | 0 | 0.0008013
2016 | 2015-05-06 | C | 1 | 0.00062058 | 3.0238e-06
2016 | 2015-05-07 | C | 19 | 0.00085966 | 5.7451e-05
2016 | 2015-05-26 | B | 5 | 0.0029028 | 1.5119e-05
2016 | 2015-05-07 | C | 1074 | 0.13859 | 0.0032475
2016 | 2015-05-06 | C | 240 | 0.040893 | 0.0007257
2016 | 2015-05-07 | C | 51 | 0.0084816 | 0.00015421
2016 | 2015-05-15 | B | 258 | 0.050565 | 0.00078013
2016 | 2015-05-07 | C | 69 | 0.043877 | 0.00020864
2016 | 2015-05-07 | C | 957 | 0.10595 | 0.0028937
2016 | 2015-05-07 | C | 7 | 0.0050207 | 2.1166e-05
2016 | 2015-05-08 | C | 1 | 9.8272e-06 | 3.0238e-06
2016 | 2015-05-08 | C | 1 | 0.00036285 | 3.0238e-06
2016 | 2015-05-08 | C | 14 | 0.0022061 | 4.2333e-05
2016 | 2015-05-15 | B | 1 | 0.0011611 | 3.0238e-06
2016 | 2015-05-08 | C | 397 | 0.071732 | 0.0012004
2016 | 2015-05-08 | C | 1 | 0.00018793 | 3.0238e-06
2016 | 2015-05-08 | C | 1 | 0.00028383 | 3.0238e-06
2016 | 2015-05-09 | C | 1366 | 0.034498 | 0.0041305
2016 | 2015-05-09 | C | 1 | 0.00013138 | 3.0238e-06
2016 | 2015-05-10 | C | 162 | 0.068235 | 0.00048985
2016 | 2015-05-10 | C | 23 | 0.0021617 | 6.9546e-05
2016 | 2015-05-10 | C | 86 | 0.0097343 | 0.00026004
2016 | 2015-05-10 | C | 1724 | 0.26832 | 0.005213
2016 | 2015-05-10 | C | 2220 | 0.11372 | 0.0067127
2016 | 2015-05-11 | C | 702 | 0.29206 | 0.0021227
2016 | 2015-05-11 | C | 11 | 0.002254 | 3.3261e-05
2016 | 2015-05-17 | B | 27 | 0.0169 | 8.1642e-05
2016 | 2015-06-11 | B | 7 | 0.0068692 | 2.1166e-05
2016 | 2015-05-11 | C | 14 | 0.0020821 | 4.2333e-05
2016 | 2015-05-15 | B | 404 | 0.097181 | 0.0012216
2016 | 2015-05-27 | B | 5 | 0.0019891 | 1.5119e-05
2016 | 2015-05-11 | C | 1 | 0.00036391 | 3.0238e-06
2016 | 2015-05-11 | C | 608 | 0.26041 | 0.0018384
2016 | 2015-05-11 | C | 1 | 0.0004262 | 3.0238e-06
2016 | 2015-05-11 | C | 6 | 0.0022911 | 1.8143e-05
2016 | 2015-05-11 | C | 1 | 0.00035282 | 3.0238e-06
2016 | 2015-05-12 | C | 86 | 0.072003 | 0.00026004
2016 | 2015-05-12 | C | 278 | 0.13156 | 0.00084061
2016 | 2015-05-12 | C | 5 | 0.0012425 | 1.5119e-05
2016 | 2015-05-12 | C | 1 | 0.00031623 | 3.0238e-06
2016 | 2015-05-12 | C | 4 | 0.00056907 | 1.2095e-05
2016 | 2015-05-28 | B | 61 | 0.011989 | 0.00018445
2016 | 2015-05-12 | C | 1 | 0.00023283 | 3.0238e-06
2016 | 2015-05-12 | C | 65 | 0.034727 | 0.00019654
2016 | 2015-06-02 | B | 50 | 0.036349 | 0.00015119
2016 | 2015-05-12 | C | 119 | 0.060296 | 0.00035983
2016 | 2015-06-15 | B | 66 | 0.094795 | 0.00019957
2016 | 2015-05-20 | B | 39 | 0.039079 | 0.00011793
2016 | 2015-05-12 | C | 2 | 0.0011535 | 6.0475e-06
2016 | 2015-05-12 | C | 2383 | 0.23154 | 0.0072056
2016 | 2015-05-13 | C | 6 | 0.0066039 | 1.8143e-05
2016 | 2015-05-13 | C | 527 | 0.068643 | 0.0015935
2016 | 2015-05-28 | B | 13 | 0.015213 | 3.9309e-05
2016 | 2015-05-13 | C | 2 | 0.00060909 | 6.0475e-06
2016 | 2015-06-03 | B | 2 | 0.00095551 | 6.0475e-06
2016 | 2015-06-04 | B | 72 | 0.081674 | 0.00021771
2016 | 2015-05-13 | C | 50 | 0.0052626 | 0.00015119
2016 | 2015-06-02 | B | 88 | 0.04948 | 0.00026609
2016 | 2015-05-19 | B | 19 | 0.0076232 | 5.7451e-05
2016 | 2015-05-13 | C | 119 | 0.020735 | 0.00035983
2016 | 2015-05-13 | C | 6353 | 5.5376 | 0.01921
2016 | 2015-06-02 | B | 9 | 0.0041365 | 2.7214e-05
2016 | 2015-06-02 | B | 38 | 0.042859 | 0.0001149
2016 | 2015-06-05 | B | 38 | 0.045998 | 0.0001149
2016 | 2015-05-14 | C | 86 | 0.03416 | 0.00026004
2016 | 2015-05-14 | C | 8 | 0.0066196 | 2.419e-05
2016 | 2015-06-08 | B | 22 | 0.026343 | 6.6523e-05
2016 | 2015-06-02 | B | 21 | 0.011623 | 6.3499e-05
2016 | 2015-06-03 | B | 3 | 0.00083456 | 9.0713e-06
2016 | 2015-05-14 | C | 149 | 0.007096 | 0.00045054
2016 | 2015-06-03 | B | 3 | 0.00042635 | 9.0713e-06
2016 | 2015-05-14 | C | 1 | 0.0002227 | 3.0238e-06
2016 | 2015-05-14 | C | 28 | 0.011389 | 8.4665e-05
2016 | 2015-05-14 | C | 1080 | 0.32692 | 0.0032657
2016 | 2015-05-14 | C | 1108 | 0.090118 | 0.0033503
2016 | 2015-05-14 | C | 775 | 0.15983 | 0.0023434
2016 | 2015-05-15 | C | 279 | 0.054083 | 0.00084363
2016 | 2015-06-03 | B | 1 | 0.00080039 | 3.0238e-06
2016 | 2015-05-15 | C | 123 | 0.043871 | 0.00037192
2016 | 2015-05-15 | C | 348 | 0.12206 | 0.0010523
2016 | 2015-05-14 | C | 17 | 0.010076 | 5.1404e-05
2016 | 2015-05-15 | C | 3448 | 0.17341 | 0.010426
2016 | 2015-05-21 | B | 146 | 0.070893 | 0.00044147
2016 | 2015-05-15 | C | 187 | 0.046965 | 0.00056544
2016 | 2015-05-15 | C | 440 | 0.17345 | 0.0013305
2016 | 2015-05-15 | C | 522 | 0.17386 | 0.0015784
2016 | 2015-05-15 | C | 314 | 0.12387 | 0.00094946
2016 | 2015-05-15 | C | 200 | 0.066653 | 0.00060475
2016 | 2015-05-15 | C | 678 | 0.23398 | 0.0020501
2016 | 2015-05-15 | C | 159 | 0.065355 | 0.00048078
2016 | 2015-05-15 | C | 78 | 0.0038994 | 0.00023585
2016 | 2015-05-15 | C | 6 | 0.00099703 | 1.8143e-05
2016 | 2015-05-15 | C | 332 | 0.095132 | 0.0010039
2016 | 2015-05-15 | C | 1 | 0.0013102 | 3.0238e-06
2016 | 2015-05-15 | C | 11 | 0.0022695 | 3.3261e-05
2016 | 2015-05-15 | C | 9 | 0.0025703 | 2.7214e-05
2016 | 2015-05-15 | C | 115 | 0.038015 | 0.00034773
2016 | 2015-05-16 | C | 8 | 0.0069845 | 2.419e-05
2016 | 2015-05-15 | C | 4 | 0.008019 | 1.2095e-05
2016 | 2015-05-16 | C | 2383 | 0.13735 | 0.0072056
2016 | 2015-05-16 | C | 17 | 0.0047806 | 5.1404e-05
2016 | 2015-05-16 | C | 1 | 0.00070756 | 3.0238e-06
2016 | 2015-05-16 | C | 1 | 0.00084297 | 3.0238e-06
2016 | 2015-05-16 | C | 7 | 0.0011641 | 2.1166e-05
2016 | 2015-05-17 | C | 177 | 0.042283 | 0.00053521
2016 | 2015-05-17 | C | 277 | 0.043166 | 0.00083758
2016 | 2015-05-17 | C | 32 | 0.0083214 | 9.676e-05
2016 | 2015-05-17 | C | 59 | 0.022602 | 0.0001784
2016 | 2015-05-17 | C | 1 | 0.00067072 | 3.0238e-06
2016 | 2015-05-17 | C | 12 | 0.0017417 | 3.6285e-05
2016 | 2015-05-18 | B | 91 | 0.01706 | 0.00027516
2016 | 2015-05-18 | C | 1 | 0.00012992 | 3.0238e-06
2016 | 2015-06-09 | B | 41 | 0.03087 | 0.00012397
2016 | 2015-06-02 | B | 44 | 0.03233 | 0.00013305
2016 | 2015-05-18 | B | 91 | 0.018161 | 0.00027516
2016 | 2015-05-18 | C | 10 | 0.0047352 | 3.0238e-05
2016 | 2015-05-18 | C | 1 | 0.00036441 | 3.0238e-06
2016 | 2015-05-18 | C | 218 | 0.067132 | 0.00065918
2016 | 2015-05-18 | C | 3 | 0.00039914 | 9.0713e-06
2016 | 2015-06-12 | B | 68 | 0.055547 | 0.00020562
2016 | 2015-06-05 | B | 1 | 0.00064426 | 3.0238e-06
2016 | 2015-06-03 | B | 99 | 0.094745 | 0.00029935
2016 | 2015-06-04 | B | 25 | 0.0063335 | 7.5594e-05
2016 | 2015-05-18 | C | 1 | 0.00033221 | 3.0238e-06
2016 | 2015-06-27 | B | 87 | 0.12893 | 0.00026307
2016 | 2015-05-19 | C | 5 | 0.0050194 | 1.5119e-05
2016 | 2015-06-08 | B | 53 | 0.035906 | 0.00016026
2016 | 2015-06-09 | B | 39 | 0.031431 | 0.00011793
2016 | 2015-05-19 | C | 1 | 0.00053163 | 3.0238e-06
2016 | 2015-06-04 | B | 144 | 0.12105 | 0.00043542
2016 | 2015-05-19 | C | 7 | 0.0019519 | 2.1166e-05
2016 | 2015-05-20 | C | 78 | 0.035035 | 0.00023585
2016 | 2015-05-19 | C | 2 | 0.00058056 | 6.0475e-06
2016 | 2015-05-19 | C | 215 | 0.0209 | 0.00065011
2016 | 2015-05-19 | C | 1 | 5.7451e-05 | 3.0238e-06
2016 | 2015-05-19 | C | 1613 | 0.056953 | 0.0048773
2016 | 2015-05-20 | C | 4 | 0.00073921 | 1.2095e-05
2016 | 2015-05-20 | C | 1 | 0.00088878 | 3.0238e-06
2016 | 2015-05-20 | C | 468 | 0.32838 | 0.0014151
2016 | 2015-05-21 | B | 2 | 0.00034471 | 6.0475e-06
2016 | 2015-06-17 | B | 19 | 0.023442 | 5.7451e-05
2016 | 2015-06-16 | B | 18 | 0.019376 | 5.4428e-05
2016 | 2015-06-09 | B | 26 | 0.030189 | 7.8618e-05
2016 | 2015-06-09 | B | 177 | 0.20124 | 0.00053521
2016 | 2015-06-16 | B | 49 | 0.065343 | 0.00014816
2016 | 2015-06-10 | B | 3 | 0.0022451 | 9.0713e-06
2016 | 2015-06-11 | B | 61 | 0.060684 | 0.00018445
2016 | 2015-06-18 | B | 98 | 0.12088 | 0.00029633
2016 | 2015-06-10 | B | 4 | 0.0038559 | 1.2095e-05
2016 | 2015-06-11 | B | 46 | 0.042147 | 0.00013909
2016 | 2015-05-21 | C | 10 | 0.017145 | 3.0238e-05
2016 | 2015-05-21 | C | 256 | 0.060824 | 0.00077408
2016 | 2015-05-21 | C | 3 | 0.00088112 | 9.0713e-06
2016 | 2015-06-18 | B | 10 | 0.012353 | 3.0238e-05
2016 | 2015-06-17 | B | 26 | 0.027993 | 7.8618e-05
2016 | 2015-05-21 | C | 8 | 0.0031912 | 2.419e-05
2016 | 2015-05-21 | C | 136 | 0.032146 | 0.00041123
2016 | 2015-06-11 | B | 67 | 0.061801 | 0.00020259
2016 | 2015-05-21 | C | 9 | 0.0043542 | 2.7214e-05
2016 | 2015-05-21 | C | 69 | 0.034749 | 0.00020864
2016 | 2015-05-21 | C | 1 | 0.00024412 | 3.0238e-06
2016 | 2015-05-22 | C | 11 | 0.0035135 | 3.3261e-05
2016 | 2015-05-22 | C | 116 | 0.067937 | 0.00035076
2016 | 2015-05-21 | C | 17 | 0.0040192 | 5.1404e-05
2016 | 2015-05-22 | C | 1 | 0.00033196 | 3.0238e-06
2016 | 2015-06-10 | B | 34 | 0.017931 | 0.00010281
2016 | 2015-05-22 | C | 655 | 0.091452 | 0.0019806
2016 | 2015-05-22 | C | 1 | 0.00042076 | 3.0238e-06
2016 | 2015-05-22 | C | 16 | 0.0066055 | 4.838e-05
2016 | 2015-06-09 | B | 1 | 0.00092824 | 3.0238e-06
2016 | 2015-05-22 | C | 80 | 0.05975 | 0.0002419
2016 | 2015-05-22 | C | 253 | 0 | 0.00076501
2016 | 2015-06-03 | B | 42 | 0.035559 | 0.000127
2016 | 2015-05-26 | B | 11 | 0.013172 | 3.3261e-05
2016 | 2015-05-23 | C | 18 | 0.012615 | 5.4428e-05
2016 | 2015-05-24 | C | 67 | 0.019636 | 0.00020259
2016 | 2015-05-23 | C | 158 | 0.094628 | 0.00047775
2016 | 2015-05-23 | C | 1583 | 0 | 0.0047866
2016 | 2015-05-24 | C | 29 | 0.0094149 | 8.7689e-05
2016 | 2015-05-24 | C | 1 | 0.00029779 | 3.0238e-06
2016 | 2015-05-24 | C | 8 | 0.0018143 | 2.419e-05
2016 | 2015-05-24 | C | 5 | 0.0020441 | 1.5119e-05
2016 | 2015-05-24 | C | 1210 | 0.30935 | 0.0036588
2016 | 2015-05-25 | C | 211 | 0 | 0.00063801
2016 | 2015-05-25 | C | 300 | 0.021144 | 0.00090713
2016 | 2015-05-25 | C | 217 | 0.054213 | 0.00065616
2016 | 2015-05-25 | C | 37 | 0.074711 | 0.00011188
2016 | 2015-05-25 | C | 93 | 0.024725 | 0.00028121
2016 | 2015-05-25 | C | 365 | 0.098159 | 0.0011037
2016 | 2015-05-25 | C | 1 | 0.00091867 | 3.0238e-06
2016 | 2015-05-25 | C | 644 | 0.16493 | 0.0019473
2016 | 2015-05-25 | C | 11 | 0.0014302 | 3.3261e-05
2016 | 2015-06-11 | B | 26 | 0.022859 | 7.8618e-05
2016 | 2015-05-25 | C | 510 | 0.12249 | 0.0015421
2016 | 2015-07-04 | B | 195 | 0.20589 | 0.00058963
2016 | 2015-05-25 | C | 1 | 0.00033352 | 3.0238e-06
2016 | 2015-05-25 | C | 15 | 0.002676 | 4.5356e-05
2016 | 2015-05-25 | C | 2 | 0.0007951 | 6.0475e-06
2016 | 2015-05-25 | C | 1 | 0.00039878 | 3.0238e-06
2016 | 2015-05-18 | C | 2 | 6.0475e-06 | 6.0475e-06
2016 | 2015-05-19 | C | 5 | 0.00018143 | 1.5119e-05
2016 | 2015-05-25 | C | 143 | 0.22742 | 0.0004324
2016 | 2015-05-25 | C | 7 | 0.0026401 | 2.1166e-05
2016 | 2015-06-17 | B | 57 | 0.08928 | 0.00017235
2016 | 2015-05-25 | C | 1 | 0.00062133 | 3.0238e-06
2016 | 2015-05-26 | C | 1 | 0.00018747 | 3.0238e-06
2016 | 2015-05-25 | C | 2 | 0.0078194 | 6.0475e-06
2016 | 2015-06-16 | B | 43 | 0.013512 | 0.00013002
2016 | 2015-06-17 | B | 34 | 0.034835 | 0.00010281
2016 | 2015-05-26 | C | 3 | 0.001651 | 9.0713e-06
2016 | 2015-05-26 | C | 37 | 0.0021649 | 0.00011188
2016 | 2015-05-26 | C | 1 | 0.00030238 | 3.0238e-06
2016 | 2015-05-26 | C | 53 | 0.014685 | 0.00016026
2016 | 2015-06-19 | B | 3 | 0.00065313 | 9.0713e-06
2016 | 2015-05-25 | C | 489 | 0.11433 | 0.0014786
2016 | 2015-06-29 | B | 10 | 0.0085079 | 3.0238e-05
2016 | 2015-05-27 | C | 1 | 0.00058565 | 3.0238e-06
2016 | 2015-05-27 | C | 722 | 0 | 0.0021832
2016 | 2015-05-27 | C | 310 | 0.015342 | 0.00093737
2016 | 2015-05-27 | C | 4 | 0.0015119 | 1.2095e-05
2016 | 2015-07-08 | B | 225 | 0.27577 | 0.00068035
2016 | 2015-06-16 | B | 28 | 0.024045 | 8.4665e-05
2016 | 2015-05-27 | C | 78 | 0.012429 | 0.00023585
2016 | 2015-05-29 | B | 68 | 0.072994 | 0.00020562
2016 | 2015-05-27 | C | 72 | 0.0052867 | 0.00021771
2016 | 2015-05-27 | C | 334 | 0.0054368 | 0.0010099
2016 | 2015-05-27 | C | 38 | 0.0015343 | 0.0001149
2016 | 2015-05-28 | C | 18 | 0.0071944 | 5.4428e-05
2016 | 2015-05-28 | C | 2 | 0.00097179 | 6.0475e-06
2016 | 2015-05-25 | C | 676 | 0.28575 | 0.0020441
2016 | 2015-05-26 | B | 200 | 0.23102 | 0.00060475
2016 | 2015-05-28 | C | 6 | 0.00035318 | 1.8143e-05
2016 | 2015-05-28 | C | 7 | 0.000254 | 2.1166e-05
2016 | 2015-06-25 | B | 75 | 0.077106 | 0.00022678
2016 | 2015-05-28 | C | 5 | 0.00022477 | 1.5119e-05
2016 | 2015-05-28 | C | 1026 | 0.043636 | 0.0031024
2016 | 2015-05-29 | C | 5 | 0.0018344 | 1.5119e-05
2016 | 2015-05-29 | C | 44 | 0.047391 | 0.00013305
2016 | 2015-06-14 | B | 57 | 0.09011 | 0.00017235
2016 | 2015-06-18 | B | 19 | 0.02504 | 5.7451e-05
2016 | 2015-09-29 | C | 471 | 0.0014242 | 0.0014242
2016 | 2015-05-30 | C | 365 | 0.10667 | 0.0011037
2016 | 2015-05-30 | C | 19 | 0.00063827 | 5.7451e-05
2016 | 2015-05-30 | C | 22 | 0.010101 | 6.6523e-05
2016 | 2015-05-30 | C | 5 | 0.00071058 | 1.5119e-05
2016 | 2015-05-30 | C | 704 | 0.45422 | 0.0021287
2016 | 2015-05-30 | C | 196 | 0.06565 | 0.00059266
2016 | 2015-05-30 | C | 1 | 9.3585e-05 | 3.0238e-06
2016 | 2015-05-30 | C | 1 | 0.00046445 | 3.0238e-06
2016 | 2015-05-31 | C | 18 | 0.00027214 | 5.4428e-05
2016 | 2015-05-31 | C | 134 | 0.0011551 | 0.00040518
2016 | 2015-06-01 | C | 1 | 0.0002357 | 3.0238e-06
2016 | 2015-06-01 | C | 950 | 0.021454 | 0.0028726
2016 | 2015-06-01 | C | 177 | 0.08662 | 0.00053521
2016 | 2015-05-01 | C | 4 | 0.00099421 | 1.2095e-05
2016 | 2015-06-02 | C | 477 | 0.0085808 | 0.0014423
2016 | 2015-06-02 | C | 60 | 0.24365 | 0.00018143
2016 | 2015-06-02 | C | 22 | 0.0040508 | 6.6523e-05
2016 | 2015-06-02 | C | 1 | 0.00015774 | 3.0238e-06
2016 | 2015-06-02 | C | 12 | 0.0067127 | 3.6285e-05
2016 | 2015-06-02 | C | 154 | 0 | 0.00046566
2016 | 2015-06-02 | C | 2 | 0.00072328 | 6.0475e-06
2016 | 2015-06-02 | C | 1 | 0.00081248 | 3.0238e-06
2016 | 2015-06-02 | C | 1 | 0.00038099 | 3.0238e-06
2016 | 2015-06-02 | C | 162 | 0.07246 | 0.00048985
2016 | 2015-06-02 | C | 3 | 0.0012718 | 9.0713e-06
2016 | 2015-06-02 | C | 1 | 0.00028171 | 3.0238e-06
2016 | 2015-06-02 | C | 1 | 0.00047896 | 3.0238e-06
2016 | 2015-06-02 | C | 1 | 0.00050552 | 3.0238e-06
2016 | 2015-06-02 | C | 1 | 0.00034844 | 3.0238e-06
2016 | 2015-06-02 | C | 4 | 0.0013208 | 1.2095e-05
2016 | 2015-06-02 | C | 2 | 4.6767e-05 | 6.0475e-06
2016 | 2015-06-02 | C | 2 | 0.00041204 | 6.0475e-06
2016 | 2015-06-03 | C | 1 | 0.0012742 | 3.0238e-06
2016 | 2015-06-03 | C | 4 | 0.00041728 | 1.2095e-05
2016 | 2015-06-03 | C | 1 | 0.00045558 | 3.0238e-06
2016 | 2015-06-03 | C | 1 | 0.00027244 | 3.0238e-06
2016 | 2015-06-03 | C | 11 | 0.013556 | 3.3261e-05
2016 | 2015-06-03 | C | 3 | 0.00082413 | 9.0713e-06
2016 | 2015-06-03 | C | 2 | 0.0010704 | 6.0475e-06
2016 | 2015-06-03 | C | 1 | 0.0016277 | 3.0238e-06
2016 | 2015-06-03 | C | 14 | 0.0054609 | 4.2333e-05
2016 | 2015-06-03 | C | 3 | 0 | 9.0713e-06
2016 | 2015-06-03 | C | 3 | 0.002282 | 9.0713e-06
2016 | 2015-06-03 | C | 5 | 0.0018881 | 1.5119e-05
2016 | 2015-06-06 | B | 68 | 0.0057538 | 0.00020562
2016 | 2015-06-03 | C | 6 | 0.0021311 | 1.8143e-05
2016 | 2015-06-03 | C | 1 | 0.00049781 | 3.0238e-06
2016 | 2015-06-03 | C | 2 | 0.0011011 | 6.0475e-06
2016 | 2015-06-25 | B | 34 | 0.032422 | 0.00010281
2016 | 2015-06-03 | C | 5 | 0.0057192 | 1.5119e-05
2016 | 2015-06-03 | C | 9 | 0.011532 | 2.7214e-05
2016 | 2015-06-03 | C | 768 | 0.12599 | 0.0023222
2016 | 2015-06-29 | B | 34 | 0.031368 | 0.00010281
2016 | 2015-06-03 | C | 1 | 0.00020254 | 3.0238e-06
2016 | 2015-06-03 | C | 2825 | 0.11184 | 0.0085421
2016 | 2015-06-03 | C | 1 | 0.0013495 | 3.0238e-06
2016 | 2015-06-03 | C | 2 | 7.6199e-05 | 6.0475e-06
2016 | 2015-06-03 | C | 1 | 0.00037162 | 3.0238e-06
2016 | 2015-06-03 | C | 6 | 0.0065809 | 1.8143e-05
2016 | 2015-06-03 | C | 211 | 0.024829 | 0.00063801
2016 | 2015-06-03 | C | 919 | 0.1833 | 0.0027788
2016 | 2015-06-03 | C | 1 | 0.00059291 | 3.0238e-06
2016 | 2015-06-20 | B | 24 | 0.008342 | 7.257e-05
2016 | 2015-06-03 | C | 417 | 0.095869 | 0.0012609
2016 | 2015-06-03 | C | 305 | 0.057996 | 0.00092225
2016 | 2015-06-03 | C | 3 | 0.00083758 | 9.0713e-06
2016 | 2015-06-03 | C | 597 | 0.15168 | 0.0018052
2016 | 2015-06-03 | C | 712 | 0.078088 | 0.0021529
2016 | 2015-06-03 | C | 358 | 0.024898 | 0.0010825
2016 | 2015-06-03 | C | 5 | 0.0013909 | 1.5119e-05
2016 | 2015-06-03 | C | 681 | 0.26558 | 0.0020592
2016 | 2015-06-04 | C | 640 | 0.091689 | 0.0019352
2016 | 2015-06-04 | C | 1 | 0.00025198 | 3.0238e-06
2016 | 2015-06-04 | C | 364 | 0.092152 | 0.0011006
2016 | 2015-06-04 | C | 1 | 0.00071663 | 3.0238e-06
2016 | 2015-06-04 | C | 2 | 0.0010787 | 6.0475e-06
2016 | 2015-06-04 | C | 1 | 0.0002231 | 3.0238e-06
2016 | 2015-06-05 | C | 240 | 0.19063 | 0.0007257
2016 | 2015-06-05 | C | 1 | 0.00055567 | 3.0238e-06
2016 | 2015-06-05 | C | 87 | 0.00034637 | 0.00026307
2016 | 2015-06-05 | C | 38 | 0.0088724 | 0.0001149
2016 | 2015-06-05 | C | 1 | 0.00039974 | 3.0238e-06
2016 | 2015-06-05 | C | 25 | 0.001333 | 7.5594e-05
2016 | 2015-06-29 | B | 60 | 0.033524 | 0.00018143
2016 | 2015-06-29 | B | 101 | 0.073413 | 0.0003054
2016 | 2015-06-06 | C | 2505 | 0.30534 | 0.0075745
2016 | 2015-06-06 | C | 486 | 0.12009 | 0.0014695
2016 | 2015-06-06 | C | 744 | 0.28929 | 0.0022497
2016 | 2015-06-06 | C | 721 | 0.12324 | 0.0021801
2016 | 2015-06-07 | C | 1 | 0.00020229 | 3.0238e-06
2016 | 2015-06-07 | C | 66 | 0.010637 | 0.00019957
2016 | 2015-06-08 | C | 49 | 0.011616 | 0.00014816
2016 | 2015-06-23 | B | 6 | 0.0052976 | 1.8143e-05
2016 | 2015-06-08 | C | 29 | 0.013345 | 8.7689e-05
2016 | 2015-06-09 | C | 255 | 0.08862 | 0.00077106
2016 | 2015-06-09 | C | 6 | 0.0016691 | 1.8143e-05
2016 | 2015-06-09 | C | 147 | 0.11788 | 0.00044449
2016 | 2015-06-10 | C | 307 | 0 | 0.00092829
2016 | 2015-06-10 | C | 343 | 0.05784 | 0.0010371
2016 | 2015-06-11 | C | 19 | 0.0010667 | 5.7451e-05
2016 | 2015-06-10 | C | 2 | 0.0004958 | 6.0475e-06
2016 | 2015-06-10 | C | 1023 | 0.029203 | 0.0030933
2016 | 2015-06-10 | C | 9 | 0.0036553 | 2.7214e-05
2016 | 2015-06-10 | C | 77 | 0.058132 | 0.00023283
2016 | 2015-06-11 | C | 76 | 0.056438 | 0.00022981
2016 | 2015-06-11 | C | 63 | 0.017751 | 0.0001905
2016 | 2015-06-11 | C | 35 | 0.0022225 | 0.00010583
2016 | 2015-06-11 | C | 1 | 0.00063151 | 3.0238e-06
2016 | 2015-06-11 | C | 2 | 0.00055557 | 6.0475e-06
2016 | 2015-06-11 | C | 2 | 0.0019216 | 6.0475e-06
2016 | 2015-06-19 | B | 13 | 0.008152 | 3.9309e-05
2016 | 2015-06-11 | C | 7 | 0.0012488 | 2.1166e-05
2016 | 2015-06-11 | C | 1047 | 0.10016 | 0.0031659
2016 | 2015-06-11 | C | 5 | 0.0031883 | 1.5119e-05
2016 | 2015-06-11 | C | 1 | 0.0031317 | 3.0238e-06
2016 | 2015-06-11 | C | 5 | 0.0014655 | 1.5119e-05
2016 | 2015-06-11 | C | 4 | 0.0018384 | 1.2095e-05
2016 | 2015-06-11 | C | 3 | 0.004124 | 9.0713e-06
2016 | 2015-06-11 | C | 1 | 0.00040745 | 3.0238e-06
2016 | 2015-06-11 | C | 1 | 0.00036325 | 3.0238e-06
2016 | 2015-06-30 | B | 69 | 0.079419 | 0.00020864
2016 | 2015-06-11 | C | 77 | 0.035701 | 0.00023283
2016 | 2015-06-11 | C | 1 | 0.00081294 | 3.0238e-06
2016 | 2015-06-11 | C | 2 | 0.00028423 | 6.0475e-06
2016 | 2015-06-11 | C | 2 | 0.00043996 | 6.0475e-06
2016 | 2015-06-11 | C | 1 | 0.00093157 | 3.0238e-06
2016 | 2015-06-11 | C | 1 | 0.00040065 | 3.0238e-06
2016 | 2015-06-11 | C | 189 | 0.099911 | 0.00057149
2016 | 2015-06-11 | C | 1 | 0.00017125 | 3.0238e-06
2016 | 2015-06-11 | C | 77 | 0.031327 | 0.00023283
2016 | 2015-06-11 | C | 1 | 0.00017946 | 3.0238e-06
2016 | 2015-06-12 | C | 1 | 8.1642e-05 | 3.0238e-06
2016 | 2015-06-12 | C | 46 | 0.0055637 | 0.00013909
2016 | 2015-06-12 | C | 7 | 0.0027107 | 2.1166e-05
2016 | 2015-06-11 | C | 2 | 0.0025597 | 6.0475e-06
2016 | 2015-06-12 | C | 23 | 0.014655 | 6.9546e-05
2016 | 2015-06-12 | C | 59 | 0.03122 | 0.0001784
2016 | 2015-06-12 | C | 5 | 0.0019624 | 1.5119e-05
2016 | 2015-06-12 | C | 118 | 0 | 0.0003568
2016 | 2015-06-12 | C | 3 | 0.0010886 | 9.0713e-06
2016 | 2015-06-11 | C | 77 | 0.0022414 | 0.00023283
2016 | 2015-06-12 | C | 921 | 0.063873 | 0.0027849
2016 | 2015-06-12 | C | 3 | 0.0003494 | 9.0713e-06
2016 | 2015-06-12 | C | 64 | 0 | 0.00019352
2016 | 2015-06-12 | C | 1 | 0.00021318 | 3.0238e-06
2016 | 2015-06-12 | C | 84 | 0.022792 | 0.000254
2016 | 2015-06-12 | C | 31 | 0.020252 | 9.3737e-05
2016 | 2015-06-12 | C | 103 | 0.27431 | 0.00031145
2016 | 2015-06-12 | C | 6 | 0.0038825 | 1.8143e-05
2016 | 2015-06-12 | C | 1183 | 0.21612 | 0.0035771
2016 | 2015-06-12 | C | 115 | 0.10562 | 0.00034773
2016 | 2015-06-12 | C | 110 | 0.0058315 | 0.00033261
2016 | 2015-06-12 | C | 278 | 0.087582 | 0.00084061
2016 | 2015-06-12 | C | 764 | 0.15086 | 0.0023102
2016 | 2015-06-12 | C | 18 | 0.010678 | 5.4428e-05
2016 | 2015-06-12 | C | 371 | 0.24888 | 0.0011218
2016 | 2015-06-12 | C | 66 | 0 | 0.00019957
2016 | 2015-06-12 | C | 77 | 0.030901 | 0.00023283
2016 | 2015-06-12 | C | 252 | 0.32122 | 0.00076199
2016 | 2015-06-12 | C | 282 | 0.10706 | 0.0008527
2016 | 2015-06-12 | C | 18 | 0.0095022 | 5.4428e-05
2016 | 2015-06-12 | C | 20 | 0.0070625 | 6.0475e-05
2016 | 2015-06-12 | C | 143 | 0.22503 | 0.0004324
2016 | 2015-06-13 | C | 530 | 0 | 0.0016026
2016 | 2015-06-13 | C | 347 | 0.20266 | 0.0010492
2016 | 2015-06-13 | C | 441 | 0.3962 | 0.0013335
2016 | 2015-06-13 | C | 42 | 0.0098064 | 0.000127
2016 | 2015-06-13 | C | 1 | 0.0014708 | 3.0238e-06
2016 | 2015-06-13 | C | 3 | 0.0040038 | 9.0713e-06
2016 | 2015-06-13 | C | 11 | 0.016897 | 3.3261e-05
2016 | 2015-06-13 | C | 15 | 0.0015459 | 4.5356e-05
2016 | 2015-06-13 | C | 606 | 0.0080493 | 0.0018324
2016 | 2015-06-13 | C | 96 | 0.011727 | 0.00029028
2016 | 2015-06-13 | C | 5 | 0.0027312 | 1.5119e-05
2016 | 2015-06-13 | C | 9 | 0.00396 | 2.7214e-05
2016 | 2015-06-15 | C | 10 | 0.003689 | 3.0238e-05
2016 | 2015-06-14 | C | 72 | 0.010388 | 0.00021771
2016 | 2015-06-14 | C | 750 | 0.19847 | 0.0022678
2016 | 2015-06-14 | C | 302 | 0.056356 | 0.00091318
2016 | 2015-06-14 | C | 8475 | 0 | 0.025626
2016 | 2015-06-14 | C | 849 | 0.20375 | 0.0025672
2016 | 2015-06-14 | C | 299 | 0.086086 | 0.0009041
2016 | 2015-06-14 | C | 1 | 3.0238e-06 | 3.0238e-06
2016 | 2015-06-14 | C | 252 | 0 | 0.00076199
2016 | 2015-06-15 | C | 3 | 0.00037903 | 9.0713e-06
2016 | 2015-06-14 | C | 2 | 0.00033584 | 6.0475e-06
2016 | 2015-06-14 | C | 25 | 0.010682 | 7.5594e-05
2016 | 2015-06-15 | C | 1 | 9.1267e-05 | 3.0238e-06
2016 | 2015-06-15 | C | 161 | 0.04809 | 0.00048683
2016 | 2015-06-15 | C | 209 | 0 | 0.00063197
2016 | 2015-06-15 | C | 73 | 0.10003 | 0.00022073
2016 | 2015-06-15 | C | 1 | 0.00058223 | 3.0238e-06
2016 | 2015-06-15 | C | 2 | 0.00037071 | 6.0475e-06
2016 | 2015-06-15 | C | 545 | 0.12369 | 0.0016479
2016 | 2015-06-26 | B | 52 | 0.059121 | 0.00015724
2016 | 2015-06-15 | C | 3 | 0.0042 | 9.0713e-06
2016 | 2015-07-01 | B | 13 | 0.0086106 | 3.9309e-05
2016 | 2015-07-01 | B | 28 | 0.034295 | 8.4665e-05
2016 | 2015-07-01 | B | 13 | 0.013993 | 3.9309e-05
2016 | 2015-06-18 | B | 30 | 0.014986 | 9.0713e-05
2016 | 2015-06-01 | B | 40 | 0.023222 | 0.00012095
2016 | 2015-06-15 | C | 210 | 0 | 0.00063499
2016 | 2015-06-15 | C | 8 | 0.0014277 | 2.419e-05
2016 | 2015-06-15 | C | 6 | 0.0022702 | 1.8143e-05
2016 | 2015-06-15 | C | 47 | 0.019629 | 0.00014212
2016 | 2015-06-30 | B | 42 | 0.040895 | 0.000127
2016 | 2015-07-02 | B | 128 | 0.033105 | 0.00038704
2016 | 2015-07-01 | B | 38 | 0.039904 | 0.0001149
2016 | 2015-07-02 | B | 121 | 0.10995 | 0.00036588
2016 | 2015-07-03 | B | 28 | 0.025154 | 8.4665e-05
2016 | 2015-07-01 | B | 42 | 0.015483 | 0.000127
2016 | 2015-07-01 | B | 46 | 0.044788 | 0.00013909
2016 | 2015-07-01 | B | 5 | 0.0038933 | 1.5119e-05
2016 | 2015-07-03 | B | 3 | 0.00072752 | 9.0713e-06
2016 | 2015-06-16 | C | 13 | 0.0024057 | 3.9309e-05
2016 | 2015-06-16 | C | 1 | 0.00056625 | 3.0238e-06
2016 | 2015-07-03 | B | 2 | 0.0013607 | 6.0475e-06
2016 | 2015-07-01 | B | 16 | 0.01618 | 4.838e-05
2016 | 2015-07-01 | B | 29 | 0.015951 | 8.7689e-05
2016 | 2015-07-06 | B | 225 | 0.11197 | 0.00068035
2016 | 2015-07-02 | B | 59 | 0.060478 | 0.0001784
2016 | 2015-07-03 | B | 4 | 0.00068942 | 1.2095e-05
2016 | 2015-07-06 | B | 112 | 0.14617 | 0.00033866
2016 | 2015-07-08 | B | 47 | 0.056278 | 0.00014212
2016 | 2015-07-07 | B | 19 | 0.019906 | 5.7451e-05
2016 | 2015-07-07 | B | 42 | 0.023845 | 0.000127
2016 | 2015-07-08 | B | 1 | 4.2333e-05 | 3.0238e-06
2016 | 2015-07-07 | B | 28 | 0.030882 | 8.4665e-05
2016 | 2015-07-07 | B | 33 | 0.033479 | 9.9784e-05
2016 | 2015-07-09 | B | 225 | 0.2496 | 0.00068035
2016 | 2015-06-16 | C | 3 | 0.00038926 | 9.0713e-06
2016 | 2015-06-16 | C | 17 | 0.00308 | 5.1404e-05
2016 | 2015-06-15 | C | 358 | 0.078811 | 0.0010825
2016 | 2015-06-16 | C | 240 | 0.038619 | 0.0007257
2016 | 2015-06-17 | C | 37 | 0.0073193 | 0.00011188
2016 | 2015-06-17 | C | 1134 | 0 | 0.0034289
2016 | 2015-06-17 | C | 235 | 0.11597 | 0.00071058
2016 | 2015-06-17 | C | 5 | 0.00067631 | 1.5119e-05
2016 | 2015-07-08 | B | 7 | 0.00048683 | 2.1166e-05
2016 | 2015-07-08 | B | 4 | 0.00052009 | 1.2095e-05
2016 | 2015-07-10 | B | 11 | 0.0010644 | 3.3261e-05
2016 | 2015-07-10 | B | 2 | 0.00086187 | 6.0475e-06
2016 | 2015-07-13 | B | 9 | 0.00087084 | 2.7214e-05
2016 | 2015-07-13 | B | 7 | 0 | 2.1166e-05
2016 | 2015-07-13 | B | 5 | 0.00033261 | 1.5119e-05
2016 | 2015-07-08 | B | 10 | 0.010946 | 3.0238e-05
2016 | 2015-06-17 | C | 4 | 0.00073477 | 1.2095e-05
2016 | 2015-07-15 | B | 9 | 0.0048169 | 2.7214e-05
2016 | 2015-07-02 | B | 107 | 0.005679 | 0.00032354
2016 | 2015-06-17 | C | 1 | 0.00059195 | 3.0238e-06
2016 | 2015-06-17 | C | 40 | 0.0021045 | 0.00012095
2016 | 2015-07-02 | B | 1 | 0.00018747 | 3.0238e-06
2016 | 2015-07-08 | B | 162 | 0.10925 | 0.00048985
2016 | 2015-07-03 | B | 64 | 0.057169 | 0.00019352
2016 | 2015-07-01 | B | 51 | 0.017115 | 0.00015421
2016 | 2015-06-18 | C | 92 | 0.035898 | 0.00027819
2016 | 2015-06-18 | C | 85 | 0 | 0.00025702
2016 | 2015-07-06 | B | 12 | 0.0082367 | 3.6285e-05
2016 | 2015-07-06 | B | 1 | 0.00053521 | 3.0238e-06
2016 | 2015-06-18 | C | 64 | 0 | 0.00019352
2016 | 2015-07-06 | B | 4 | 0.0013788 | 1.2095e-05
2016 | 2015-06-18 | C | 6 | 0.0065779 | 1.8143e-05
2016 | 2015-06-18 | C | 64 | 0.012803 | 0.00019352
2016 | 2015-07-07 | B | 9 | 0.0088889 | 2.7214e-05
2016 | 2015-07-06 | B | 2 | 0.00078618 | 6.0475e-06
2016 | 2015-07-07 | B | 9 | 0.0053643 | 2.7214e-05
2016 | 2015-06-18 | C | 38 | 0.0076985 | 0.0001149
2016 | 2015-06-18 | C | 3 | 0.00082851 | 9.0713e-06
2016 | 2015-06-18 | C | 100 | 0.015421 | 0.00030238
2016 | 2015-06-18 | C | 1 | 0.00027395 | 3.0238e-06
2016 | 2015-06-19 | C | 234 | 0.055706 | 0.00070756
2016 | 2015-06-18 | C | 240 | 0.05353 | 0.0007257
2016 | 2015-06-19 | C | 233 | 0.060339 | 0.00070454
2016 | 2015-06-19 | C | 239 | 0 | 0.00072268
2016 | 2015-06-19 | C | 1 | 0.00067878 | 3.0238e-06
2016 | 2015-06-26 | B | 193 | 0.034274 | 0.00058359
2016 | 2015-06-19 | C | 2 | 0.0016951 | 6.0475e-06
2016 | 2015-07-13 | B | 94 | 0.10923 | 0.00028423
2016 | 2015-06-19 | C | 116 | 0.041251 | 0.00035076
2016 | 2015-07-13 | B | 28 | 0.017815 | 8.4665e-05
2016 | 2015-06-19 | C | 19 | 0.00051898 | 5.7451e-05
2016 | 2015-06-19 | C | 234 | 0.076141 | 0.00070756
2016 | 2015-06-19 | C | 20 | 0.00078517 | 6.0475e-05
2016 | 2015-07-09 | B | 242 | 0.26857 | 0.00073175
2016 | 2015-06-19 | C | 211 | 0.09907 | 0.00063801
2016 | 2015-06-19 | C | 1 | 0.00027945 | 3.0238e-06
2016 | 2015-06-19 | C | 303 | 0 | 0.0009162
2016 | 2015-06-19 | C | 234 | 0.032036 | 0.00070756
2016 | 2015-06-19 | C | 363 | 0.6001 | 0.0010976
2016 | 2015-06-19 | C | 303 | 0 | 0.0009162
2016 | 2015-06-19 | C | 64 | 0 | 0.00019352
2016 | 2015-06-20 | C | 44 | 0.035565 | 0.00013305
2016 | 2015-06-20 | C | 224 | 0.3794 | 0.00067732
2016 | 2015-06-20 | C | 8635 | 8.918 | 0.02611
2016 | 2015-06-20 | C | 4 | 0.055526 | 1.2095e-05
2016 | 2015-06-20 | C | 4 | 0.0062027 | 1.2095e-05
2016 | 2015-06-19 | C | 1420 | 0 | 0.0042937
2016 | 2015-06-20 | C | 86 | 0.21298 | 0.00026004
2016 | 2015-06-20 | C | 3322 | 0.5732 | 0.010045
2016 | 2015-06-20 | C | 592 | 0.08108 | 0.0017901
2016 | 2015-06-20 | C | 17 | 0.23648 | 5.1404e-05
2016 | 2015-06-20 | C | 1 | 0.00042323 | 3.0238e-06
2016 | 2015-06-20 | C | 142 | 1.0584 | 0.00042937
2016 | 2015-06-20 | C | 408 | 0.43604 | 0.0012337
2016 | 2015-06-20 | C | 6 | 0.057004 | 1.8143e-05
2016 | 2015-06-20 | C | 212 | 0.35059 | 0.00064104
2016 | 2015-06-20 | C | 592 | 0.038361 | 0.0017901
2016 | 2015-06-20 | C | 255 | 0.18126 | 0.00077106
2016 | 2015-06-20 | C | 466 | 0.19473 | 0.0014091
2016 | 2015-06-20 | C | 302 | 0.17138 | 0.00091318
2016 | 2015-06-20 | C | 74 | 0.0459 | 0.00022376
2016 | 2015-06-20 | C | 91 | 0.93269 | 0.00027516
2016 | 2015-06-20 | C | 154 | 0 | 0.00046566
2016 | 2015-06-20 | C | 111 | 2.9882 | 0.00033564
2016 | 2015-06-20 | C | 181 | 0.23552 | 0.0005473
2016 | 2015-06-20 | C | 2 | 0.0011081 | 6.0475e-06
2016 | 2015-06-20 | C | 186 | 0.32104 | 0.00056242
2016 | 2015-06-20 | C | 147 | 0.092429 | 0.00044449
2016 | 2015-06-20 | C | 27 | 0.010673 | 8.1642e-05
2016 | 2015-06-20 | C | 190 | 0.042828 | 0.00057451
2016 | 2015-06-20 | C | 858 | 0.53449 | 0.0025944
2016 | 2015-06-20 | C | 606 | 1.501 | 0.0018324
2016 | 2015-06-20 | C | 1 | 0.0019093 | 3.0238e-06
2016 | 2015-06-21 | C | 41 | 0.016616 | 0.00012397
2016 | 2015-06-22 | C | 50 | 0.021053 | 0.00015119
2016 | 2015-06-21 | C | 396 | 0.088307 | 0.0011974
2016 | 2015-06-21 | C | 930 | 0.41409 | 0.0028121
2016 | 2015-06-21 | C | 2 | 0.012059 | 6.0475e-06
2016 | 2015-06-21 | C | 1 | 0.00091534 | 3.0238e-06
2016 | 2015-06-21 | C | 1 | 0.00967 | 3.0238e-06
2016 | 2015-06-21 | C | 67 | 0.32877 | 0.00020259
2016 | 2015-06-21 | C | 237 | 0.094595 | 0.00071663
2016 | 2015-06-21 | C | 217 | 0.054685 | 0.00065616
2016 | 2015-06-21 | C | 4 | 0.041229 | 1.2095e-05
2016 | 2015-06-21 | C | 2 | 0.0028894 | 6.0475e-06
2016 | 2015-06-21 | C | 19 | 0.097389 | 5.7451e-05
2016 | 2015-06-21 | C | 1 | 0.00013138 | 3.0238e-06
2016 | 2015-06-21 | C | 3 | 0.00072177 | 9.0713e-06
2016 | 2015-06-21 | C | 166 | 0.016046 | 0.00050194
2016 | 2015-06-21 | C | 91 | 0.0068791 | 0.00027516
2016 | 2015-06-21 | C | 1 | 0.00042378 | 3.0238e-06
2016 | 2015-06-20 | C | 2372 | 8.9776 | 0.0071724
2016 | 2015-06-21 | C | 18 | 0.05339 | 5.4428e-05
2016 | 2015-06-21 | C | 212 | 0 | 0.00064104
2016 | 2015-06-21 | C | 2 | 0.0060259 | 6.0475e-06
2016 | 2015-07-14 | B | 224 | 0.20154 | 0.00067732
2016 | 2015-07-14 | B | 118 | 0.14429 | 0.0003568
2016 | 2015-07-15 | B | 47 | 0.028719 | 0.00014212
2016 | 2015-06-22 | C | 714 | 0.018345 | 0.002159
2016 | 2015-06-22 | C | 19 | 0.013869 | 5.7451e-05
2016 | 2015-06-21 | C | 40 | 0.028786 | 0.00012095
2016 | 2015-06-22 | C | 14 | 0.011895 | 4.2333e-05
2016 | 2015-07-07 | B | 54 | 0.059922 | 0.00016328
2016 | 2015-07-14 | B | 12 | 0.012228 | 3.6285e-05
2016 | 2015-06-22 | C | 1 | 0.00055113 | 3.0238e-06
2016 | 2015-06-23 | C | 2 | 0.00067732 | 6.0475e-06
2016 | 2015-06-22 | C | 2 | 0.00037802 | 6.0475e-06
2016 | 2015-06-23 | C | 4 | 0.0015794 | 1.2095e-05
2016 | 2015-06-23 | B | 170 | 0.0087387 | 0.00051404
2016 | 2015-06-22 | C | 1 | 0.0034955 | 3.0238e-06
2016 | 2015-06-22 | C | 7 | 0.00083436 | 2.1166e-05
2016 | 2015-06-22 | C | 283 | 0 | 0.00085572
2016 | 2015-07-08 | B | 50 | 0.049696 | 0.00015119
2016 | 2015-07-14 | B | 87 | 0.093871 | 0.00026307
2016 | 2015-06-23 | C | 438 | 0.0017659 | 0.0013244
2016 | 2015-07-15 | B | 87 | 0.078736 | 0.00026307
2016 | 2015-06-23 | C | 1 | 0.00023132 | 3.0238e-06
2016 | 2015-07-08 | B | 83 | 0.082331 | 0.00025097
2016 | 2015-06-23 | C | 1 | 0.00049151 | 3.0238e-06
2016 | 2015-06-23 | C | 474 | 0.18052 | 0.0014333
2016 | 2015-07-08 | B | 48 | 0.043801 | 0.00014514
2016 | 2015-06-23 | C | 9 | 0.0045987 | 2.7214e-05
2016 | 2015-06-23 | C | 726 | 0.031215 | 0.0021953
2016 | 2015-06-30 | C | 3 | 0.00097063 | 9.0713e-06
2016 | 2015-06-23 | C | 1 | 0.00039012 | 3.0238e-06
2016 | 2015-07-16 | B | 1 | 0.0011793 | 3.0238e-06
2016 | 2015-06-23 | C | 3 | 0.001818 | 9.0713e-06
2016 | 2015-07-13 | B | 304 | 0.12766 | 0.00091922
2016 | 2015-06-20 | C | 5 | 0.066028 | 1.5119e-05
2016 | 2015-06-21 | C | 2 | 0.016796 | 6.0475e-06
2016 | 2015-07-13 | B | 30 | 0.024588 | 9.0713e-05
2016 | 2015-06-23 | C | 5 | 0.0011037 | 1.5119e-05
2016 | 2015-06-23 | C | 38 | 0.017452 | 0.0001149
2016 | 2015-06-23 | C | 3 | 0.00015421 | 9.0713e-06
2016 | 2015-06-23 | C | 1141 | 0.2012 | 0.0034501
2016 | 2015-06-24 | C | 114 | 0.075962 | 0.00034471
2016 | 2015-06-24 | C | 2 | 8.4665e-05 | 6.0475e-06
2016 | 2015-06-24 | C | 245 | 0.075244 | 0.00074082
2016 | 2015-06-24 | C | 7 | 0.25338 | 2.1166e-05
2016 | 2015-07-09 | B | 1 | 0.0004959 | 3.0238e-06
2016 | 2015-07-14 | B | 3 | 0.0019685 | 9.0713e-06
2016 | 2015-06-24 | C | 16 | 0.0039156 | 4.838e-05
2016 | 2015-06-24 | C | 9 | 0.0016528 | 2.7214e-05
2016 | 2015-06-25 | C | 1 | 0.00018717 | 3.0238e-06
2016 | 2015-07-10 | B | 48 | 0.03508 | 0.00014514
2016 | 2015-06-25 | C | 214 | 0.0083365 | 0.00064708
2016 | 2015-06-25 | C | 23 | 0.0050073 | 6.9546e-05
2016 | 2015-07-13 | B | 2 | 0.0010704 | 6.0475e-06
2016 | 2015-07-15 | B | 3 | 0.00092527 | 9.0713e-06
2016 | 2015-07-13 | B | 2 | 0.0010281 | 6.0475e-06
2016 | 2015-06-25 | C | 12 | 0.0062083 | 3.6285e-05
2016 | 2015-06-25 | C | 2 | 0.00082922 | 6.0475e-06
2016 | 2015-06-26 | C | 24 | 0.019571 | 7.257e-05
2016 | 2015-06-26 | C | 2 | 3.0238e-05 | 6.0475e-06
2016 | 2015-07-15 | B | 10 | 0.0052981 | 3.0238e-05
2016 | 2015-06-26 | C | 237 | 0.057303 | 0.00071663
2016 | 2015-07-15 | B | 112 | 0.073123 | 0.00033866
2016 | 2015-06-26 | C | 7 | 0.0028391 | 2.1166e-05
2016 | 2015-06-26 | C | 17 | 0.0021372 | 5.1404e-05
2016 | 2015-06-26 | C | 233 | 0.029299 | 0.00070454
2016 | 2015-06-27 | C | 283 | 0.096821 | 0.00085572
2016 | 2015-06-27 | C | 639 | 0.13517 | 0.0019322
2016 | 2015-06-27 | C | 151 | 0.10891 | 0.00045659
2016 | 2015-06-27 | C | 3281 | 0.53147 | 0.009921
2016 | 2015-06-27 | C | 595 | 0 | 0.0017991
2016 | 2015-06-27 | C | 859 | 0.57412 | 0.0025974
2016 | 2015-06-28 | C | 41 | 0.0024079 | 0.00012397
2016 | 2015-06-28 | C | 111 | 0.038644 | 0.00033564
2016 | 2015-06-28 | C | 1 | 0.00018969 | 3.0238e-06
2016 | 2015-06-28 | C | 635 | 0 | 0.0019201
2016 | 2015-06-28 | C | 28 | 0.0055611 | 8.4665e-05
2016 | 2015-06-28 | C | 562 | 0.060398 | 0.0016994
2016 | 2015-06-29 | C | 16 | 0.011855 | 4.838e-05
2016 | 2015-07-16 | B | 1 | 0.0007514 | 3.0238e-06
2016 | 2015-07-09 | B | 16 | 0.001707 | 4.838e-05
2016 | 2015-07-16 | B | 107 | 0.12077 | 0.00032354
2016 | 2015-06-29 | C | 12 | 0.00052911 | 3.6285e-05
2016 | 2015-06-29 | C | 130 | 0.01604 | 0.00039309
2016 | 2015-07-16 | B | 13 | 0.013792 | 3.9309e-05
2016 | 2015-06-29 | C | 35 | 0.0064333 | 0.00010583
2016 | 2015-07-17 | B | 43 | 0.018472 | 0.00013002
2016 | 2015-06-29 | C | 1126 | 0 | 0.0034048
2016 | 2015-06-29 | C | 2684 | 0.4665 | 0.0081158
2016 | 2015-06-29 | C | 1065 | 0.24129 | 0.0032203
2016 | 2015-06-30 | C | 38 | 0.013099 | 0.0001149
2016 | 2015-06-30 | C | 1 | 0.00034562 | 3.0238e-06
2016 | 2015-06-30 | C | 325 | 0.012397 | 0.00098272
2016 | 2015-06-30 | C | 22 | 0.0083874 | 6.6523e-05
2016 | 2015-07-14 | B | 13 | 0.01283 | 3.9309e-05
2016 | 2015-07-01 | C | 1 | 0.00046747 | 3.0238e-06
2016 | 2015-07-01 | C | 23 | 0.019656 | 6.9546e-05
2016 | 2015-07-17 | B | 145 | 0.1346 | 0.00043845
2016 | 2015-07-01 | C | 438 | 0.17156 | 0.0013244
2016 | 2015-07-20 | B | 4 | 0.00050799 | 1.2095e-05
2016 | 2015-07-21 | B | 7 | 0.0061964 | 2.1166e-05
2016 | 2015-07-21 | B | 4 | 0.00050799 | 1.2095e-05
2016 | 2015-07-27 | B | 98 | 0.11705 | 0.00029633
2016 | 2015-07-20 | B | 122 | 0.034105 | 0.0003689
2016 | 2015-07-17 | B | 3 | 0.0016238 | 9.0713e-06
2016 | 2015-07-29 | B | 98 | 0.10431 | 0.00029633
2016 | 2015-07-20 | B | 11 | 0.0020622 | 3.3261e-05
2016 | 2015-07-20 | B | 6 | 0.0008527 | 1.8143e-05
2016 | 2015-07-02 | C | 661 | 0.03328 | 0.0019987
2016 | 2015-07-03 | C | 359 | 0.067338 | 0.0010855
2016 | 2015-07-03 | C | 594 | 0.21059 | 0.0017961
2016 | 2015-08-05 | B | 13 | 0.013201 | 3.9309e-05
2016 | 2015-07-27 | B | 1 | 0.00032334 | 3.0238e-06
2016 | 2015-07-27 | B | 3 | 0.00099648 | 9.0713e-06
2016 | 2015-07-24 | B | 1 | 0.00014212 | 3.0238e-06
2016 | 2015-07-24 | B | 3 | 0.00038099 | 9.0713e-06
2016 | 2015-07-27 | B | 7 | 0.00078315 | 2.1166e-05
2016 | 2015-07-27 | B | 3 | 0.00033564 | 9.0713e-06
2016 | 2015-07-25 | B | 9 | 0.0037283 | 2.7214e-05
2016 | 2015-07-03 | C | 224 | 0 | 0.00067732
2016 | 2015-07-03 | C | 250 | 0.090876 | 0.00075594
2016 | 2015-07-04 | C | 2 | 0.001437 | 6.0475e-06
2016 | 2015-07-04 | C | 4 | 0.001197 | 1.2095e-05
2016 | 2015-07-04 | C | 1 | 0.00051217 | 3.0238e-06
2016 | 2015-07-04 | C | 302 | 0.085045 | 0.00091318
2016 | 2015-07-04 | C | 1645 | 0.12031 | 0.0049741
2016 | 2015-07-04 | C | 7 | 0.00083798 | 2.1166e-05
2016 | 2015-07-04 | C | 75 | 0.0063499 | 0.00022678
2016 | 2015-07-04 | C | 2 | 0.00049408 | 6.0475e-06
2016 | 2015-07-04 | C | 5 | 0.00046868 | 1.5119e-05
2016 | 2015-07-04 | C | 127 | 0.011777 | 0.00038402
2016 | 2015-07-05 | C | 25 | 0.0058582 | 7.5594e-05
2016 | 2015-07-05 | C | 1 | 0.00058359 | 3.0238e-06
2016 | 2015-07-05 | C | 24 | 0.0044268 | 7.257e-05
2016 | 2015-07-06 | C | 2 | 0.00079439 | 6.0475e-06
2016 | 2015-07-06 | C | 96 | 0.0049154 | 0.00029028
2016 | 2015-07-06 | C | 1 | 0.00028262 | 3.0238e-06
2016 | 2015-07-21 | B | 1 | 0.0010106 | 3.0238e-06
2016 | 2015-07-06 | C | 2 | 0.001131 | 6.0475e-06
2016 | 2015-07-06 | C | 132 | 0.014369 | 0.00039914
2016 | 2015-07-07 | B | 86 | 0.062931 | 0.00026004
2016 | 2015-07-23 | B | 53 | 0.0061394 | 0.00016026
2016 | 2015-07-07 | C | 102 | 0.1165 | 0.00030842
2016 | 2015-07-31 | B | 98 | 0.077342 | 0.00029633
2016 | 2015-07-17 | B | 108 | 0.076416 | 0.00032657
2016 | 2015-07-25 | B | 2 | 0.00015119 | 6.0475e-06
2016 | 2015-07-08 | C | 239 | 0.16737 | 0.00072268
2016 | 2015-07-08 | C | 239 | 0.24187 | 0.00072268
2016 | 2015-07-08 | C | 10 | 0.0073461 | 3.0238e-05
2016 | 2015-07-08 | C | 298 | 0.14264 | 0.00090108
2016 | 2015-07-10 | B | 72 | 0.055928 | 0.00021771
2016 | 2015-07-08 | C | 1250 | 0.23341 | 0.0037797
2016 | 2015-07-08 | C | 1 | 0.00038034 | 3.0238e-06
2016 | 2015-07-08 | C | 3 | 0.0017934 | 9.0713e-06
2016 | 2015-07-09 | C | 7 | 0.0014785 | 2.1166e-05
2016 | 2015-07-09 | C | 34 | 0.024761 | 0.00010281
2016 | 2015-07-09 | C | 12 | 0.0062616 | 3.6285e-05
2016 | 2015-07-09 | C | 82 | 0.032853 | 0.00024795
2016 | 2015-07-28 | B | 418 | 0.020862 | 0.0012639
2016 | 2015-07-09 | C | 46 | 0.0039085 | 0.00013909
2016 | 2015-07-17 | C | 3 | 0.0013516 | 9.0713e-06
2016 | 2015-07-09 | C | 3 | 0.002299 | 9.0713e-06
2016 | 2015-07-10 | C | 209 | 0 | 0.00063197
2016 | 2015-07-10 | C | 232 | 0.030594 | 0.00070151
2016 | 2015-07-10 | C | 209 | 0 | 0.00063197
2016 | 2015-07-10 | C | 67 | 0.01354 | 0.00020259
2016 | 2015-07-10 | C | 2 | 0.00052241 | 6.0475e-06
2016 | 2015-07-27 | B | 278 | 0.046233 | 0.00084061
2016 | 2015-07-10 | C | 1 | 0.0014253 | 3.0238e-06
2016 | 2015-07-11 | C | 1 | 0.00011405 | 3.0238e-06
2016 | 2015-07-11 | C | 8 | 0.0002931 | 2.419e-05
2016 | 2015-07-11 | C | 680 | 0.44078 | 0.0020562
2016 | 2015-07-11 | C | 8 | 0.0017428 | 2.419e-05
2016 | 2015-07-11 | C | 1 | 0.00041819 | 3.0238e-06
2016 | 2015-07-11 | C | 30 | 0.0019775 | 9.0713e-05
2016 | 2015-07-12 | C | 16 | 0.0081279 | 4.838e-05
2016 | 2015-07-12 | C | 493 | 0 | 0.0014907
2016 | 2015-07-12 | C | 43 | 0.014079 | 0.00013002
2016 | 2015-07-12 | C | 4 | 0.00090632 | 1.2095e-05
2016 | 2015-07-13 | C | 1 | 0.0010073 | 3.0238e-06
2016 | 2015-07-13 | C | 217 | 0.044319 | 0.00065616
2016 | 2015-07-13 | C | 1 | 7.514e-05 | 3.0238e-06
2016 | 2015-07-13 | C | 3 | 0.00053521 | 9.0713e-06
2016 | 2015-07-13 | C | 1 | 0.00038276 | 3.0238e-06
2016 | 2015-07-21 | B | 96 | 0.010547 | 0.00029028
2016 | 2015-07-13 | C | 703 | 0.12183 | 0.0021257
2016 | 2015-07-13 | C | 1385 | 0 | 0.0041879
2016 | 2015-07-13 | C | 1 | 0.00098272 | 3.0238e-06
2016 | 2015-07-20 | B | 47 | 0.045518 | 0.00014212
2016 | 2015-07-18 | B | 1 | 8.9604e-05 | 3.0238e-06
2016 | 2015-07-27 | B | 11 | 0.0052891 | 3.3261e-05
2016 | 2015-07-13 | C | 32 | 0.016185 | 9.676e-05
2016 | 2015-07-13 | C | 1 | 0.00056746 | 3.0238e-06
2016 | 2015-07-13 | C | 6 | 0.0058963 | 1.8143e-05
2016 | 2015-07-13 | C | 1 | 0.00095662 | 3.0238e-06
2016 | 2015-07-31 | B | 102 | 0.049528 | 0.00030842
2016 | 2015-07-14 | C | 103 | 0.030522 | 0.00031145
2016 | 2015-07-14 | C | 232 | 0.010241 | 0.00070151
2016 | 2015-07-30 | B | 43 | 0.010772 | 0.00013002
2016 | 2015-07-30 | B | 477 | 0.07648 | 0.0014423
2016 | 2015-08-04 | B | 224 | 0.18539 | 0.00067732
2016 | 2015-08-03 | B | 1 | 0.00057789 | 3.0238e-06
2016 | 2015-07-15 | B | 1 | 0.00031749 | 3.0238e-06
2016 | 2015-07-14 | C | 1 | 6.0475e-06 | 3.0238e-06
2016 | 2015-07-14 | C | 4 | 2.0158e-05 | 1.2095e-05
2016 | 2015-07-15 | C | 11 | 0.0035656 | 3.3261e-05
2016 | 2015-08-03 | B | 33 | 0.022252 | 9.9784e-05
2016 | 2015-08-03 | B | 3 | 0.0024674 | 9.0713e-06
2016 | 2015-08-04 | B | 24 | 0.0052492 | 7.257e-05
2016 | 2015-08-03 | B | 8 | 0.0035559 | 2.419e-05
2016 | 2015-07-15 | C | 3 | 0 | 9.0713e-06
2016 | 2015-08-03 | B | 17 | 0.010181 | 5.1404e-05
2016 | 2015-07-15 | C | 5 | 0.0018327 | 1.5119e-05
2016 | 2015-08-03 | B | 7 | 0.00088899 | 2.1166e-05
2016 | 2015-08-04 | B | 201 | 0.028363 | 0.00060778
2016 | 2015-08-03 | B | 4 | 0.00038704 | 1.2095e-05
2016 | 2015-08-04 | B | 4 | 0.0025119 | 1.2095e-05
2016 | 2015-08-04 | B | 222 | 0.29409 | 0.00067127
2016 | 2015-08-05 | B | 25 | 0.016238 | 7.5594e-05
2016 | 2015-08-10 | B | 3 | 0.00086177 | 9.0713e-06
2016 | 2015-08-05 | B | 16 | 0.011886 | 4.838e-05
2016 | 2015-07-21 | B | 508 | 0 | 0.0015361
2016 | 2015-08-06 | B | 21 | 0.02594 | 6.3499e-05
2016 | 2015-08-03 | B | 9 | 0.0056333 | 2.7214e-05
2016 | 2015-07-16 | C | 3 | 0.00097063 | 9.0713e-06
2016 | 2015-07-15 | C | 1 | 0.00030036 | 3.0238e-06
2016 | 2015-07-15 | C | 2 | 0.00069919 | 6.0475e-06
2016 | 2015-07-16 | C | 4 | 0.0048138 | 1.2095e-05
2016 | 2015-07-15 | C | 934 | 0.20651 | 0.0028242
2016 | 2015-07-15 | C | 1 | 0.0010629 | 3.0238e-06
2016 | 2015-07-15 | C | 659 | 0.49521 | 0.0019927
2016 | 2015-07-15 | C | 5 | 0.0030706 | 1.5119e-05
2016 | 2015-07-16 | C | 2 | 0.00077877 | 6.0475e-06
2016 | 2015-07-16 | C | 6 | 0.007378 | 1.8143e-05
2016 | 2015-07-16 | C | 849 | 0.12846 | 0.0025672
2016 | 2015-07-16 | C | 3 | 0.0013258 | 9.0713e-06
2016 | 2015-07-16 | C | 2 | 0.00051046 | 6.0475e-06
2016 | 2015-07-16 | C | 1 | 0.00013184 | 3.0238e-06
2016 | 2015-07-16 | C | 3 | 0.0031855 | 9.0713e-06
2016 | 2015-07-16 | C | 6 | 0.0018974 | 1.8143e-05
2016 | 2015-07-15 | C | 2507 | 0.38702 | 0.0075806
2016 | 2015-07-16 | C | 8 | 0.0035559 | 2.419e-05
2016 | 2015-08-06 | B | 5 | 0.00071058 | 1.5119e-05
2016 | 2015-08-06 | B | 2 | 0.000254 | 6.0475e-06
2016 | 2015-08-06 | B | 9 | 0.001143 | 2.7214e-05
2016 | 2015-08-13 | B | 25 | 0.023681 | 7.5594e-05
2016 | 2015-08-06 | B | 26 | 0.021655 | 7.8618e-05
2016 | 2015-07-16 | C | 782 | 0.15604 | 0.0023646
2016 | 2015-07-16 | C | 3 | 0.0026524 | 9.0713e-06
2016 | 2015-07-16 | C | 1003 | 0.20528 | 0.0030328
2016 | 2015-07-16 | C | 1 | 0.00039778 | 3.0238e-06
2016 | 2015-07-16 | C | 684 | 0.13472 | 0.0020683
2016 | 2015-08-03 | B | 61 | 0.087613 | 0.00018445
2016 | 2015-08-03 | B | 5 | 0.0019957 | 1.5119e-05
2016 | 2015-08-03 | B | 131 | 0.0086982 | 0.00039611
2016 | 2015-08-18 | B | 9 | 0.009797 | 2.7214e-05
2016 | 2015-08-03 | B | 215 | 0.080613 | 0.00065011
2016 | 2015-08-04 | B | 2 | 0.00031306 | 6.0475e-06
2016 | 2015-08-05 | B | 40 | 0.0060294 | 0.00012095
2016 | 2015-08-05 | B | 239 | 0.052634 | 0.00072268
2016 | 2015-08-05 | B | 7 | 0.0038988 | 2.1166e-05
2016 | 2015-08-07 | B | 120 | 0.02555 | 0.00036285
2016 | 2015-08-06 | B | 76 | 0.051017 | 0.00022981
2016 | 2015-08-07 | B | 34 | 0.020589 | 0.00010281
2016 | 2015-08-10 | B | 107 | 0.018927 | 0.00032354
2016 | 2015-08-10 | B | 4 | 0.0025037 | 1.2095e-05
2016 | 2015-08-11 | B | 53 | 0.049435 | 0.00016026
2016 | 2015-08-11 | B | 20 | 0.018929 | 6.0475e-05
2016 | 2015-08-12 | B | 4 | 0.00091056 | 1.2095e-05
2016 | 2015-08-12 | B | 22 | 0.022978 | 6.6523e-05
2016 | 2015-08-12 | B | 176 | 0.18827 | 0.00053218
2016 | 2015-08-13 | B | 268 | 0.1774 | 0.00081037
2016 | 2015-08-14 | B | 83 | 0.054453 | 0.00025097
2016 | 2015-08-17 | B | 20 | 0.012397 | 6.0475e-05
2016 | 2015-08-07 | B | 2 | 0.0014937 | 6.0475e-06
2016 | 2015-08-07 | B | 4 | 0.0028423 | 1.2095e-05
2016 | 2015-08-09 | B | 29 | 0.011838 | 8.7689e-05
2016 | 2015-08-10 | B | 2 | 0.0009797 | 6.0475e-06
2016 | 2015-08-12 | B | 4 | 0.0021408 | 1.2095e-05
2016 | 2015-08-13 | B | 3 | 0.001651 | 9.0713e-06
2016 | 2015-08-14 | B | 6 | 0.0042438 | 1.8143e-05
2016 | 2015-08-15 | B | 283 | 0.20541 | 0.00085572
2016 | 2015-08-18 | B | 8 | 0.0092648 | 2.419e-05
2016 | 2015-08-19 | B | 50 | 0.052364 | 0.00015119
2016 | 2015-08-20 | B | 98 | 0.11007 | 0.00029633
2016 | 2015-09-23 | B | 5 | 0.0044903 | 1.5119e-05
2016 | 2015-08-24 | B | 12 | 0.013317 | 3.6285e-05
2016 | 2015-08-07 | B | 12 | 0.008169 | 3.6285e-05
2016 | 2015-08-07 | B | 44 | 0.025478 | 0.00013305
2016 | 2015-08-07 | B | 2 | 0.00043542 | 6.0475e-06
2016 | 2015-08-07 | B | 29 | 0.023486 | 8.7689e-05
2016 | 2015-08-07 | B | 3 | 0.0021228 | 9.0713e-06
2016 | 2015-08-12 | B | 75 | 0.052613 | 0.00022678
2016 | 2015-08-14 | B | 19 | 0.017931 | 5.7451e-05
2016 | 2015-08-13 | B | 7 | 0.00099482 | 2.1166e-05
2016 | 2015-08-17 | B | 5 | 0.00040821 | 1.5119e-05
2016 | 2015-08-17 | B | 7 | 0.00057149 | 2.1166e-05
2016 | 2015-08-17 | B | 4 | 0.00041123 | 1.2095e-05
2016 | 2015-08-26 | B | 13 | 0.011259 | 3.9309e-05
2016 | 2015-08-06 | B | 12 | 0.011322 | 3.6285e-05
2016 | 2015-08-04 | B | 17 | 0.018781 | 5.1404e-05
2016 | 2015-08-03 | B | 30 | 0.009351 | 9.0713e-05
2016 | 2015-08-18 | B | 50 | 0.048531 | 0.00015119
2016 | 2015-08-01 | B | 101 | 0.096751 | 0.0003054
2016 | 2015-07-30 | C | 230 | 0.051932 | 0.00069546
2016 | 2015-07-30 | C | 35 | 0.011767 | 0.00010583
2016 | 2015-07-31 | C | 441 | 0.065678 | 0.0013335
2016 | 2015-08-18 | B | 69 | 0.049656 | 0.00020864
2016 | 2015-08-20 | B | 53 | 0.04529 | 0.00016026
2016 | 2015-08-29 | B | 59 | 0.06696 | 0.0001784
2016 | 2015-08-18 | B | 18 | 0.00076924 | 5.4428e-05
2016 | 2015-08-19 | B | 6 | 0.00052613 | 1.8143e-05
2016 | 2015-08-19 | B | 3 | 0.00021771 | 9.0713e-06
2016 | 2015-08-19 | B | 9 | 0.00038099 | 2.7214e-05
2016 | 2015-08-25 | B | 23 | 0.017943 | 6.9546e-05
2016 | 2015-07-31 | C | 414 | 0.067295 | 0.0012518
2016 | 2015-08-25 | B | 19 | 0.024245 | 5.7451e-05
2016 | 2015-07-31 | C | 19 | 0.0052482 | 5.7451e-05
2016 | 2015-07-31 | C | 66 | 0.014455 | 0.00019957
2016 | 2015-07-31 | C | 2 | 0.00032143 | 6.0475e-06
2016 | 2015-07-31 | C | 608 | 0.013538 | 0.0018384
2016 | 2015-08-01 | C | 255 | 0.14692 | 0.00077106
2016 | 2015-08-01 | C | 1 | 0.00057991 | 3.0238e-06
2016 | 2015-08-01 | C | 13 | 0.0036557 | 3.9309e-05
2016 | 2015-08-01 | C | 1 | 0.00067415 | 3.0238e-06
2016 | 2015-08-01 | C | 45 | 0.011974 | 0.00013607
2016 | 2015-08-01 | C | 165 | 0.26968 | 0.00049892
2016 | 2015-08-02 | C | 1 | 0.00018878 | 3.0238e-06
2016 | 2015-08-03 | C | 147 | 0.050708 | 0.00044449
2016 | 2015-08-03 | C | 404 | 0.056732 | 0.0012216
2016 | 2015-08-20 | B | 241 | 0.08232 | 0.00072873
2016 | 2015-08-03 | C | 1 | 0.00043845 | 3.0238e-06
2016 | 2015-08-03 | C | 1 | 0.0047341 | 3.0238e-06
2016 | 2015-08-19 | B | 22 | 0.017097 | 6.6523e-05
2016 | 2015-08-03 | C | 1 | 0.00046722 | 3.0238e-06
2016 | 2015-08-03 | C | 26 | 0.021148 | 7.8618e-05
2016 | 2015-08-03 | C | 6 | 0.00032536 | 1.8143e-05
2016 | 2015-08-03 | C | 427 | 0.1363 | 0.0012911
2016 | 2015-08-04 | C | 1277 | 0.54785 | 0.0038613
2016 | 2015-08-03 | C | 52 | 0.013679 | 0.00015724
2016 | 2015-08-04 | C | 36 | 0.0025037 | 0.00010886
2016 | 2015-08-04 | C | 1 | 0.00096614 | 3.0238e-06
2016 | 2015-08-04 | C | 190 | 0.082503 | 0.00057451
2016 | 2015-08-11 | B | 127 | 0.066067 | 0.00038402
2016 | 2015-08-04 | C | 430 | 0.10679 | 0.0013002
2016 | 2015-08-04 | C | 85 | 0.011865 | 0.00025702
2016 | 2015-08-21 | B | 4 | 0.00018143 | 1.2095e-05
2016 | 2015-08-04 | C | 44 | 0.010639 | 0.00013305
2016 | 2015-08-04 | C | 1 | 0.00013305 | 3.0238e-06
2016 | 2015-08-04 | C | 95 | 0.013214 | 0.00028726
2016 | 2015-08-21 | B | 4 | 0.00014514 | 1.2095e-05
2016 | 2015-08-21 | B | 3 | 0.00017235 | 9.0713e-06
2016 | 2015-08-21 | B | 71 | 0.090567 | 0.00021469
2016 | 2015-08-25 | B | 106 | 0.12625 | 0.00032052
2016 | 2015-08-04 | C | 404 | 0.034182 | 0.0012216
2016 | 2015-08-04 | C | 78 | 0.031822 | 0.00023585
2016 | 2015-08-05 | C | 2 | 5.0094e-05 | 6.0475e-06
2016 | 2015-08-05 | C | 3 | 0.00014514 | 9.0713e-06
2016 | 2015-08-25 | B | 8 | 0.0086617 | 2.419e-05
2016 | 2015-08-05 | C | 1 | 0.00035227 | 3.0238e-06
2016 | 2015-08-26 | B | 3 | 0.00076773 | 9.0713e-06
2016 | 2015-08-05 | C | 298 | 0.128 | 0.00090108
2016 | 2015-08-06 | C | 520 | 0.067501 | 0.0015724
2016 | 2015-08-06 | C | 7 | 0.0020747 | 2.1166e-05
2016 | 2015-08-06 | C | 21 | 0.0049392 | 6.3499e-05
2016 | 2015-08-06 | C | 920 | 0.33873 | 0.0027819
2016 | 2015-08-12 | B | 22 | 0.0082488 | 6.6523e-05
2016 | 2015-08-06 | C | 12 | 0.12155 | 3.6285e-05
2016 | 2015-08-06 | C | 1 | 4.8229e-05 | 3.0238e-06
2016 | 2015-08-06 | C | 2 | 0.0035499 | 6.0475e-06
2016 | 2015-08-26 | B | 8 | 0.0029367 | 2.419e-05
2016 | 2015-08-10 | B | 3 | 0.00043542 | 9.0713e-06
2016 | 2015-08-06 | C | 1306 | 0.058087 | 0.003949
2016 | 2015-08-06 | C | 36 | 0.0054526 | 0.00010886
2016 | 2015-08-06 | C | 380 | 0.080087 | 0.001149
2016 | 2015-08-25 | B | 50 | 0.058061 | 0.00015119
2016 | 2015-08-07 | C | 839 | 0.022013 | 0.0025369
2016 | 2015-08-17 | B | 307 | 0.058666 | 0.00092829
2016 | 2015-08-18 | B | 250 | 0.048265 | 0.00075594
2016 | 2015-08-20 | B | 38 | 0.045846 | 0.0001149
2016 | 2015-08-21 | B | 57 | 0.0063771 | 0.00017235
2016 | 2015-08-07 | C | 467 | 0.18829 | 0.0014121
2016 | 2015-08-07 | C | 157 | 0.0057731 | 0.00047473
2016 | 2015-08-07 | C | 24 | 0.0050946 | 7.257e-05
2016 | 2015-08-07 | C | 26 | 0.0026075 | 7.8618e-05
2016 | 2015-08-07 | C | 3 | 0.00048017 | 9.0713e-06
2016 | 2015-08-07 | C | 14 | 0.0088651 | 4.2333e-05
2016 | 2015-08-08 | C | 1 | 0.0003182 | 3.0238e-06
2016 | 2015-08-08 | C | 96 | 0.098927 | 0.00029028
2016 | 2015-08-08 | C | 767 | 0.21189 | 0.0023192
2016 | 2015-08-08 | C | 105 | 0.01615 | 0.00031749
2016 | 2015-08-08 | C | 1 | 0.0013763 | 3.0238e-06
2016 | 2015-08-08 | C | 1573 | 0.42988 | 0.0047564
2016 | 2015-08-08 | C | 2 | 0.0011527 | 6.0475e-06
2016 | 2015-08-08 | C | 52 | 0.01906 | 0.00015724
2016 | 2015-08-08 | C | 2067 | 0.17563 | 0.0062501
2016 | 2015-08-08 | C | 629 | 0.096411 | 0.0019019
2016 | 2015-08-08 | C | 6 | 0.002969 | 1.8143e-05
2016 | 2015-08-08 | C | 1 | 0.00084554 | 3.0238e-06
2016 | 2015-08-08 | C | 143 | 0.096425 | 0.0004324
2016 | 2015-08-09 | C | 60 | 0.012981 | 0.00018143
2016 | 2015-08-09 | C | 3 | 0.00061987 | 9.0713e-06
2016 | 2015-08-09 | C | 1 | 0.0013274 | 3.0238e-06
2016 | 2015-08-09 | C | 1 | 0.00036945 | 3.0238e-06
2016 | 2015-08-09 | C | 1 | 0.0033041 | 3.0238e-06
2016 | 2015-08-09 | C | 148 | 0.080094 | 0.00044752
2016 | 2015-08-09 | C | 1 | 0.00017644 | 3.0238e-06
2016 | 2015-08-10 | C | 122 | 0.06464 | 0.0003689
2016 | 2015-08-10 | C | 1015 | 0.15667 | 0.0030691
2016 | 2015-08-10 | C | 1 | 0.00027214 | 3.0238e-06
2016 | 2015-08-10 | C | 125 | 0.018993 | 0.00037797
2016 | 2015-08-27 | B | 269 | 0.037512 | 0.00081339
2016 | 2015-08-10 | C | 95 | 0.0083305 | 0.00028726
2016 | 2015-08-10 | C | 6 | 0.0019957 | 1.8143e-05
2016 | 2015-08-10 | C | 689 | 0.30929 | 0.0020834
2016 | 2015-08-31 | B | 7 | 0.0041274 | 2.1166e-05
2016 | 2015-08-10 | C | 677 | 0.19415 | 0.0020471
2016 | 2015-08-10 | C | 23 | 0.011873 | 6.9546e-05
2016 | 2015-08-10 | C | 927 | 0.034861 | 0.002803
2016 | 2015-08-10 | C | 979 | 0 | 0.0029603
2016 | 2015-08-11 | B | 10 | 0.00097567 | 3.0238e-05
2016 | 2015-08-28 | B | 30 | 0.024036 | 9.0713e-05
2016 | 2015-08-12 | B | 1 | 0.00042937 | 3.0238e-06
2016 | 2015-08-11 | B | 6 | 0.0031205 | 1.8143e-05
2016 | 2015-08-11 | C | 9 | 0.0066861 | 2.7214e-05
2016 | 2015-08-12 | C | 76 | 0.016255 | 0.00022981
2016 | 2015-08-10 | C | 49 | 0.010075 | 0.00014816
2016 | 2015-09-02 | B | 19 | 0.012927 | 5.7451e-05
2016 | 2015-09-14 | B | 57 | 0.06631 | 0.00017235
2016 | 2015-09-17 | B | 6 | 0.0062704 | 1.8143e-05
2016 | 2015-09-01 | B | 264 | 0.015021 | 0.00079827
2016 | 2015-09-02 | B | 7 | 0.0037041 | 2.1166e-05
2016 | 2015-09-02 | B | 4 | 0.00062894 | 1.2095e-05
2016 | 2015-09-01 | B | 19 | 0.020395 | 5.7451e-05
2016 | 2015-09-02 | B | 6 | 0.00032657 | 1.8143e-05
2016 | 2015-09-01 | B | 3 | 0.00060778 | 9.0713e-06
2016 | 2015-08-13 | B | 157 | 0.010362 | 0.00047473
2016 | 2015-09-08 | B | 2 | 0.0023646 | 6.0475e-06
2016 | 2015-09-10 | B | 26 | 0.014181 | 7.8618e-05
2016 | 2015-09-01 | B | 73 | 0.059102 | 0.00022073
2016 | 2015-08-12 | C | 15 | 0.00031069 | 4.5356e-05
2016 | 2015-09-25 | B | 37 | 0.03729 | 0.00011188
2016 | 2015-08-21 | B | 2 | 0.00073649 | 6.0475e-06
2016 | 2015-09-01 | B | 2 | 0.0021348 | 6.0475e-06
2016 | 2015-08-13 | C | 1 | 0.0002933 | 3.0238e-06
2016 | 2015-09-03 | B | 205 | 0.087485 | 0.00061987
2016 | 2015-09-02 | B | 5 | 0.0045707 | 1.5119e-05
2016 | 2015-09-02 | B | 16 | 0.014652 | 4.838e-05
2016 | 2015-09-02 | B | 13 | 0.0076128 | 3.9309e-05
2016 | 2015-09-04 | B | 19 | 0.02078 | 5.7451e-05
2016 | 2015-09-09 | B | 4 | 0.0029875 | 1.2095e-05
2016 | 2015-09-03 | B | 11 | 0.011874 | 3.3261e-05
2016 | 2015-09-04 | B | 2 | 0.001122 | 6.0475e-06
2016 | 2015-09-04 | B | 9 | 0.0059068 | 2.7214e-05
2016 | 2015-08-13 | C | 149 | 0.026467 | 0.00045054
2016 | 2015-09-03 | B | 28 | 0.032003 | 8.4665e-05
2016 | 2015-09-08 | B | 22 | 0.018802 | 6.6523e-05
2016 | 2015-09-10 | B | 16 | 0.015982 | 4.838e-05
2016 | 2015-09-06 | B | 74 | 0.03605 | 0.00022376
2016 | 2015-08-14 | C | 297 | 0.012153 | 0.00089806
2016 | 2015-09-03 | B | 4 | 0.0012942 | 1.2095e-05
2016 | 2015-09-07 | B | 18 | 0.011381 | 5.4428e-05
2016 | 2015-09-05 | B | 147 | 0.09564 | 0.00044449
2016 | 2015-09-02 | B | 131 | 0.13261 | 0.00039611
2016 | 2015-09-03 | B | 131 | 0.12491 | 0.00039611
2016 | 2015-08-14 | C | 268 | 0.0070367 | 0.00081037
2016 | 2015-08-15 | B | 124 | 0.029405 | 0.00037495
2016 | 2015-08-15 | C | 3 | 0.00094341 | 9.0713e-06
2016 | 2015-08-14 | C | 239 | 0 | 0.00072268
2016 | 2015-08-14 | C | 4 | 0.0008785 | 1.2095e-05
2016 | 2015-08-14 | C | 2 | 0.00071613 | 6.0475e-06
2016 | 2015-08-15 | C | 415 | 0.38176 | 0.0012549
2016 | 2015-08-15 | C | 113 | 0.010166 | 0.00034168
2016 | 2015-08-15 | C | 1453 | 0 | 0.0043935
2016 | 2015-08-15 | C | 235 | 0.058149 | 0.00071058
2016 | 2015-08-16 | C | 3820 | 0.50948 | 0.011551
2016 | 2015-08-17 | C | 365 | 0.065227 | 0.0011037
2016 | 2015-08-20 | B | 8 | 0.010826 | 2.419e-05
2016 | 2015-08-21 | B | 3 | 0.00015421 | 9.0713e-06
2016 | 2015-08-21 | B | 7 | 0.0022648 | 2.1166e-05
2016 | 2015-09-02 | B | 2 | 0.0003689 | 6.0475e-06
2016 | 2015-09-08 | B | 69 | 0.029415 | 0.00020864
2016 | 2015-09-07 | B | 2 | 0.00076289 | 6.0475e-06
2016 | 2015-09-03 | B | 28 | 0.0075352 | 8.4665e-05
2016 | 2015-09-03 | B | 7 | 0.0041486 | 2.1166e-05
2016 | 2015-08-17 | C | 695 | 0.27013 | 0.0021015
2016 | 2015-08-17 | C | 1 | 0.00031744 | 3.0238e-06
2016 | 2015-09-09 | B | 29 | 0.030316 | 8.7689e-05
2016 | 2015-09-16 | B | 29 | 0.027648 | 8.7689e-05
2016 | 2015-09-23 | B | 29 | 0.031106 | 8.7689e-05
2016 | 2015-09-29 | B | 16 | 0.017695 | 4.838e-05
2016 | 2015-09-09 | B | 7 | 0.0044943 | 2.1166e-05
2016 | 2015-09-04 | B | 13 | 0.012186 | 3.9309e-05
2016 | 2015-09-04 | B | 60 | 0.022678 | 0.00018143
2016 | 2015-09-02 | B | 4 | 0.0010523 | 1.2095e-05
2016 | 2015-08-17 | C | 177 | 0.027852 | 0.00053521
2016 | 2015-08-18 | C | 723 | 0.18174 | 0.0021862
2016 | 2015-09-04 | B | 4 | 0.0011127 | 1.2095e-05
2016 | 2015-09-08 | B | 33 | 0.017263 | 9.9784e-05
2016 | 2015-09-10 | B | 8 | 0.0085766 | 2.419e-05
2016 | 2015-09-07 | B | 4 | 0.0011248 | 1.2095e-05
2016 | 2015-09-10 | B | 23 | 0.022788 | 6.9546e-05
2016 | 2015-08-19 | B | 8 | 0.0078376 | 2.419e-05
2016 | 2015-09-07 | B | 4 | 0.0018989 | 1.2095e-05
2016 | 2015-08-18 | C | 365 | 0.08882 | 0.0011037
2016 | 2015-09-15 | B | 16 | 0.017655 | 4.838e-05
2016 | 2015-08-18 | C | 2 | 0.0014543 | 6.0475e-06
2016 | 2015-08-18 | C | 91 | 0.018436 | 0.00027516
2016 | 2015-08-18 | C | 2 | 0.0010597 | 6.0475e-06
2016 | 2015-08-18 | C | 365 | 0.054609 | 0.0011037
2016 | 2015-08-18 | C | 6 | 0.0032657 | 1.8143e-05
2016 | 2015-08-18 | C | 18 | 0.002304 | 5.4428e-05
2016 | 2015-08-18 | C | 278 | 0.074681 | 0.00084061
2016 | 2015-08-18 | C | 97 | 0.059533 | 0.0002933
2016 | 2015-08-19 | C | 187 | 0 | 0.00056544
2016 | 2015-08-19 | B | 3 | 0.00092527 | 9.0713e-06
2016 | 2015-08-31 | B | 58 | 0.052836 | 0.00017538
2016 | 2015-08-19 | C | 19 | 0.0074716 | 5.7451e-05
2016 | 2015-08-19 | C | 3 | 0.0020119 | 9.0713e-06
2016 | 2015-08-19 | C | 704 | 0.096122 | 0.0021287
2016 | 2015-08-19 | C | 704 | 0.028348 | 0.0021287
2016 | 2015-08-19 | C | 39 | 0.012402 | 0.00011793
2016 | 2015-08-19 | C | 111 | 0.045545 | 0.00033564
2016 | 2015-08-19 | C | 61 | 0.024732 | 0.00018445
2016 | 2015-09-07 | B | 42 | 0.035837 | 0.000127
2016 | 2015-08-20 | C | 5 | 0.0010969 | 1.5119e-05
2016 | 2015-08-20 | C | 920 | 0.045555 | 0.0027819
2016 | 2015-09-04 | B | 128 | 0.09269 | 0.00038704
2016 | 2015-09-22 | B | 56 | 0.060299 | 0.00016933
2016 | 2015-08-19 | C | 170 | 0.014907 | 0.00051404
2016 | 2015-08-19 | C | 826 | 0.10567 | 0.0024976
2016 | 2015-09-07 | B | 278 | 0.12277 | 0.00084061
2016 | 2015-08-20 | C | 1 | 0.00040337 | 3.0238e-06
2016 | 2015-08-20 | C | 2 | 0.00041647 | 6.0475e-06
2016 | 2015-08-20 | C | 664 | 0.1349 | 0.0020078
2016 | 2015-09-07 | B | 477 | 0.098586 | 0.0014423
2016 | 2015-09-08 | B | 4 | 0.00044752 | 1.2095e-05
2016 | 2015-09-16 | B | 6 | 0.0032112 | 1.8143e-05
2016 | 2015-08-21 | C | 2 | 0.00055476 | 6.0475e-06
2016 | 2015-09-08 | B | 137 | 0.068814 | 0.00041426
2016 | 2015-09-09 | B | 6 | 0.00019957 | 1.8143e-05
2016 | 2015-09-08 | B | 1 | 5.1404e-05 | 3.0238e-06
2016 | 2015-09-08 | B | 8 | 0.00055637 | 2.419e-05
2016 | 2015-09-09 | B | 9 | 0.0021499 | 2.7214e-05
2016 | 2015-09-09 | B | 1 | 4.5356e-05 | 3.0238e-06
2016 | 2015-09-09 | B | 6 | 0.00032657 | 1.8143e-05
2016 | 2015-08-21 | C | 1 | 0 | 3.0238e-06
2016 | 2015-08-22 | C | 163 | 0.095412 | 0.00049287
2016 | 2015-08-22 | C | 108 | 0.027815 | 0.00032657
2016 | 2015-08-21 | C | 418 | 0.05376 | 0.0012639
2016 | 2015-08-22 | C | 26 | 0.0035129 | 7.8618e-05
2016 | 2015-08-22 | C | 1 | 0.0001716 | 3.0238e-06
2016 | 2015-08-22 | B | 1 | 0.00010664 | 3.0238e-06
2016 | 2015-08-22 | C | 2 | 0.0061019 | 6.0475e-06
2016 | 2015-08-23 | C | 677 | 0.099647 | 0.0020471
2016 | 2015-08-23 | C | 322 | 0 | 0.00097365
2016 | 2015-08-23 | C | 16 | 0.007536 | 4.838e-05
2016 | 2015-08-23 | C | 2 | 0.00041012 | 6.0475e-06
2016 | 2015-08-23 | C | 30 | 0.0045946 | 9.0713e-05
2016 | 2015-08-23 | C | 13 | 0.0034847 | 3.9309e-05
2016 | 2015-08-23 | C | 25 | 0.020869 | 7.5594e-05
2016 | 2015-08-24 | C | 6 | 0.0050497 | 1.8143e-05
2016 | 2015-08-24 | C | 25 | 0.015559 | 7.5594e-05
2016 | 2015-09-09 | B | 30 | 0.030663 | 9.0713e-05
2016 | 2015-08-24 | C | 775 | 0 | 0.0023434
2016 | 2015-09-11 | B | 2 | 0.00010886 | 6.0475e-06
2016 | 2015-09-11 | B | 6 | 0.00034471 | 1.8143e-05
2016 | 2015-09-11 | B | 7 | 0.00035983 | 2.1166e-05
2016 | 2015-09-10 | B | 6 | 0.0021771 | 1.8143e-05
2016 | 2015-09-15 | B | 6 | 0.00058056 | 1.8143e-05
2016 | 2015-09-15 | B | 4 | 0.00038704 | 1.2095e-05
2016 | 2015-09-09 | B | 35 | 0.038334 | 0.00010583
2016 | 2015-09-15 | B | 13 | 0.0012579 | 3.9309e-05
2016 | 2015-09-15 | B | 6 | 0.00023585 | 1.8143e-05
2016 | 2015-09-15 | B | 4 | 0.00019352 | 1.2095e-05
2016 | 2015-09-15 | B | 4 | 0.00019352 | 1.2095e-05
2016 | 2015-09-13 | B | 26 | 0.018711 | 7.8618e-05
2016 | 2015-09-15 | B | 57 | 0.03878 | 0.00017235
2016 | 2015-09-15 | B | 75 | 0.088967 | 0.00022678
2016 | 2015-09-17 | B | 75 | 0.087266 | 0.00022678
2016 | 2015-09-30 | B | 75 | 0.087961 | 0.00022678
2016 | 2015-09-16 | B | 6 | 0.00076199 | 1.8143e-05
2016 | 2015-09-11 | B | 3 | 0.00024492 | 9.0713e-06
2016 | 2015-09-10 | B | 42 | 0.046697 | 0.000127
2016 | 2015-08-24 | C | 1259 | 0.21341 | 0.0038069
2016 | 2015-08-25 | C | 74 | 0.029976 | 0.00022376
2016 | 2015-09-01 | B | 63 | 0.037011 | 0.0001905
2016 | 2015-09-04 | B | 17 | 0.0077637 | 5.1404e-05
2016 | 2015-08-25 | C | 163 | 0.1814 | 0.00049287
2016 | 2015-08-31 | B | 80 | 0.092648 | 0.0002419
2016 | 2015-08-25 | C | 1 | 0.00024588 | 3.0238e-06
2016 | 2015-08-25 | C | 95 | 0.079402 | 0.00028726
2016 | 2015-08-25 | C | 40 | 0.071113 | 0.00012095
2016 | 2015-08-26 | C | 340 | 0.1085 | 0.0010281
2016 | 2015-08-26 | C | 1 | 0.00012604 | 3.0238e-06
2016 | 2015-08-26 | C | 647 | 0.20753 | 0.0019564
2016 | 2015-08-26 | C | 604 | 0.16409 | 0.0018264
2016 | 2015-08-26 | C | 100 | 0.0067732 | 0.00030238
2016 | 2015-08-27 | C | 536 | 0.17775 | 0.0016207
2016 | 2015-08-27 | C | 110 | 0.055958 | 0.00033261
2016 | 2015-08-27 | C | 4 | 0.00049227 | 1.2095e-05
2016 | 2015-09-11 | B | 3 | 0.0034562 | 9.0713e-06
2016 | 2015-09-24 | B | 47 | 0.061366 | 0.00014212
2016 | 2015-09-10 | B | 12 | 0.012457 | 3.6285e-05
2016 | 2015-09-29 | B | 1 | 3.9309e-05 | 3.0238e-06
2016 | 2015-08-27 | C | 1 | 0.00035469 | 3.0238e-06
2016 | 2015-08-27 | C | 1 | 0.00029204 | 3.0238e-06
2016 | 2015-08-28 | C | 9 | 0.001924 | 2.7214e-05
2016 | 2015-08-27 | B | 29 | 0.028877 | 8.7689e-05
2016 | 2015-08-28 | C | 3 | 0.001109 | 9.0713e-06
2016 | 2015-09-29 | B | 3 | 0.001787 | 9.0713e-06
2016 | 2015-08-28 | C | 1 | 0.00085834 | 3.0238e-06
2016 | 2015-08-28 | C | 1 | 0.0006615 | 3.0238e-06
2016 | 2015-08-29 | C | 19 | 0.0036922 | 5.7451e-05
2016 | 2015-08-29 | C | 10 | 0.0022552 | 3.0238e-05
2016 | 2015-08-29 | C | 9 | 0.0025558 | 2.7214e-05
2016 | 2015-08-29 | C | 348 | 0.053524 | 0.0010523
2016 | 2015-08-29 | C | 414 | 0.0041224 | 0.0012518
2016 | 2015-08-29 | C | 348 | 0.017957 | 0.0010523
2016 | 2015-08-30 | C | 291 | 0.049007 | 0.00087991
2016 | 2015-08-30 | C | 3 | 0.0025072 | 9.0713e-06
2016 | 2015-08-30 | C | 8 | 0.0012623 | 2.419e-05
2016 | 2015-08-30 | C | 704 | 0.025545 | 0.0021287
2016 | 2015-08-30 | C | 113 | 0.013159 | 0.00034168
2016 | 2015-08-30 | C | 741 | 0.23013 | 0.0022406
2016 | 2015-08-30 | C | 1 | 0.00029396 | 3.0238e-06
2016 | 2015-09-08 | B | 3 | 0.0022034 | 9.0713e-06
2016 | 2015-10-13 | B | 3 | 0.00010886 | 9.0713e-06
2016 | 2015-08-31 | C | 13 | 0.00037802 | 3.9309e-05
2016 | 2015-08-31 | C | 9 | 0.0018047 | 2.7214e-05
2016 | 2015-08-31 | C | 704 | 0.17076 | 0.0021287
2016 | 2015-09-15 | B | 2 | 0.00078618 | 6.0475e-06
2016 | 2015-08-31 | C | 3 | 0.00084363 | 9.0713e-06
2016 | 2015-09-15 | B | 2 | 0.00042937 | 6.0475e-06
2016 | 2015-09-15 | B | 15 | 0.010024 | 4.5356e-05
2016 | 2015-09-15 | B | 42 | 0.045338 | 0.000127
2016 | 2015-09-07 | B | 15 | 0.0017757 | 4.5356e-05
2016 | 2015-09-15 | B | 67 | 0.058954 | 0.00020259
2016 | 2015-09-01 | C | 168 | 0.033538 | 0.00050799
2016 | 2015-09-01 | C | 1 | 0.00016616 | 3.0238e-06
2016 | 2015-09-01 | C | 385 | 0.019594 | 0.0011641
2016 | 2015-09-01 | C | 34 | 0.013755 | 0.00010281
2016 | 2015-09-01 | C | 19 | 0.017785 | 5.7451e-05
2016 | 2015-09-01 | C | 16 | 0.0052323 | 4.838e-05
2016 | 2015-09-01 | C | 4 | 0.0015832 | 1.2095e-05
2016 | 2015-09-01 | C | 21 | 0.014351 | 6.3499e-05
2016 | 2015-09-01 | C | 357 | 0.027725 | 0.0010795
2016 | 2015-09-01 | C | 58 | 0.023287 | 0.00017538
2016 | 2015-09-01 | C | 313 | 0.044021 | 0.00094644
2016 | 2015-09-01 | C | 631 | 0.09116 | 0.001908
2016 | 2015-09-01 | C | 146 | 0.019233 | 0.00044147
2016 | 2015-09-01 | C | 132 | 0.085146 | 0.00039914
2016 | 2015-09-01 | C | 3 | 0.0019635 | 9.0713e-06
2016 | 2015-09-01 | C | 634 | 0.14279 | 0.0019171
2016 | 2015-09-01 | C | 47 | 0.029847 | 0.00014212
2016 | 2015-09-12 | B | 23 | 0.0024585 | 6.9546e-05
2016 | 2015-09-01 | C | 364 | 0.22429 | 0.0011006
2016 | 2015-09-16 | B | 5 | 0.0024492 | 1.5119e-05
2016 | 2015-09-16 | B | 2 | 0.0017356 | 6.0475e-06
2016 | 2015-09-01 | C | 1 | 0.00052311 | 3.0238e-06
2016 | 2015-09-28 | B | 190 | 0.18387 | 0.00057451
2016 | 2015-09-01 | C | 3 | 0.00057703 | 9.0713e-06
2016 | 2015-09-01 | C | 1 | 0.00013909 | 3.0238e-06
2016 | 2015-09-01 | C | 8 | 0.00014998 | 2.419e-05
2016 | 2015-09-01 | C | 2 | 0.00021166 | 6.0475e-06
2016 | 2015-09-01 | C | 5 | 0.0011647 | 1.5119e-05
2016 | 2015-09-02 | C | 11 | 0.002035 | 3.3261e-05
2016 | 2015-09-25 | B | 4 | 0.00099179 | 1.2095e-05
2016 | 2015-09-25 | B | 6 | 0.00096156 | 1.8143e-05
2016 | 2015-09-02 | C | 5 | 0.0017712 | 1.5119e-05
2016 | 2015-09-02 | C | 679 | 0.067992 | 0.0020531
2016 | 2015-09-02 | C | 116 | 0 | 0.00035076
2016 | 2015-09-09 | B | 21 | 0.013143 | 6.3499e-05
2016 | 2015-09-02 | C | 409 | 0 | 0.0012367
2016 | 2015-09-07 | C | 53 | 0.006982 | 0.00016026
2016 | 2015-09-02 | C | 6 | 0.0030842 | 1.8143e-05
2016 | 2015-09-02 | C | 625 | 0 | 0.0018899
2016 | 2015-09-02 | C | 1 | 5.7955e-06 | 3.0238e-06
2016 | 2015-09-02 | C | 2 | 0.0027992 | 6.0475e-06
2016 | 2015-09-28 | B | 57 | 0.062961 | 0.00017235
2016 | 2015-09-06 | B | 4 | 0.0017852 | 1.2095e-05
2016 | 2015-09-03 | C | 35 | 0.0030691 | 0.00010583
2016 | 2015-09-17 | B | 42 | 0.046052 | 0.000127
2016 | 2015-09-08 | B | 3 | 0.0030117 | 9.0713e-06
2016 | 2015-09-15 | B | 1 | 0.00070811 | 3.0238e-06
2016 | 2015-09-03 | C | 2 | 0.00018747 | 6.0475e-06
2016 | 2015-09-04 | B | 2 | 0.00026609 | 6.0475e-06
2016 | 2015-09-03 | C | 4 | 0.0007257 | 1.2095e-05
2016 | 2015-09-03 | C | 4 | 0.00066482 | 1.2095e-05
2016 | 2015-09-03 | C | 121 | 0.014013 | 0.00036588
2016 | 2015-09-03 | C | 1163 | 0.47995 | 0.0035166
2016 | 2015-09-03 | C | 9 | 0.0018233 | 2.7214e-05
2016 | 2015-09-04 | C | 4 | 0.0049102 | 1.2095e-05
2016 | 2015-09-04 | C | 1 | 0.00055138 | 3.0238e-06
2016 | 2015-09-10 | B | 42 | 0.03909 | 0.000127
2016 | 2015-09-04 | C | 10 | 0.0048506 | 3.0238e-05
2016 | 2015-09-04 | C | 3 | 0.00044994 | 9.0713e-06
2016 | 2015-09-04 | C | 7 | 0.0024077 | 2.1166e-05
2016 | 2015-09-04 | C | 1 | 0.00031694 | 3.0238e-06
2016 | 2015-09-10 | B | 1 | 0.00070287 | 3.0238e-06
2016 | 2015-09-24 | B | 19 | 0.0018384 | 5.7451e-05
2016 | 2015-09-06 | C | 92 | 0.054803 | 0.00027819
2016 | 2015-09-06 | C | 385 | 0.046838 | 0.0011641
2016 | 2015-09-06 | C | 93 | 0.045759 | 0.00028121
2016 | 2015-09-06 | C | 23 | 0.0027334 | 6.9546e-05
2016 | 2015-09-06 | C | 19 | 0.011376 | 5.7451e-05
2016 | 2015-09-06 | C | 90 | 0.018354 | 0.00027214
2016 | 2015-09-06 | C | 1 | 0.00089695 | 3.0238e-06
2016 | 2015-09-06 | C | 161 | 0.02773 | 0.00048683
2016 | 2015-09-06 | C | 2 | 0.00033876 | 6.0475e-06
2016 | 2015-09-07 | C | 266 | 0.061565 | 0.00080432
2016 | 2015-09-25 | B | 12 | 0.0022497 | 3.6285e-05
2016 | 2015-09-25 | B | 15 | 0.0033239 | 4.5356e-05
2016 | 2015-09-21 | B | 30 | 0.006046 | 9.0713e-05
2016 | 2015-09-21 | B | 104 | 0.042496 | 0.00031447
2016 | 2015-09-07 | C | 23 | 0.0058245 | 6.9546e-05
2016 | 2015-09-22 | B | 45 | 0.034548 | 0.00013607
2016 | 2015-09-24 | B | 52 | 0.0097327 | 0.00015724
2016 | 2015-09-23 | B | 15 | 0.010251 | 4.5356e-05
2016 | 2015-09-22 | B | 42 | 0.044195 | 0.000127
2016 | 2015-09-29 | B | 60 | 0.11648 | 0.00018143
2016 | 2015-09-08 | C | 64 | 0.010644 | 0.00019352
2016 | 2015-09-09 | C | 346 | 0.19416 | 0.0010462
2016 | 2015-09-09 | C | 2 | 0.0018668 | 6.0475e-06
2016 | 2015-09-28 | B | 2 | 0.0012993 | 6.0475e-06
2016 | 2015-09-25 | B | 14 | 0.0059978 | 4.2333e-05
2016 | 2015-09-09 | C | 3 | 0.00088883 | 9.0713e-06
2016 | 2015-09-10 | C | 169 | 0.1239 | 0.00051102
2016 | 2015-09-25 | B | 12 | 0.0080474 | 3.6285e-05
2016 | 2015-09-30 | B | 299 | 0.21708 | 0.0009041
2016 | 2015-09-22 | B | 68 | 0.027964 | 0.00020562
2016 | 2015-09-15 | B | 297 | 0.28799 | 0.00089806
2016 | 2015-09-10 | C | 2 | 0.00057451 | 6.0475e-06
2016 | 2015-09-10 | C | 2 | 0.00094946 | 6.0475e-06
2016 | 2015-09-10 | C | 1 | 3.1749e-06 | 3.0238e-06
2016 | 2015-09-10 | C | 145 | 0.065198 | 0.00043845
2016 | 2015-09-10 | C | 297 | 0.070307 | 0.00089806
2016 | 2015-09-11 | C | 473 | 0.046292 | 0.0014302
2016 | 2015-09-10 | C | 177 | 0.091974 | 0.00053521
2016 | 2015-09-11 | C | 73 | 0.040073 | 0.00022073
2016 | 2015-09-11 | C | 108 | 0.016782 | 0.00032657
2016 | 2015-09-10 | C | 22 | 0.10956 | 6.6523e-05
2016 | 2015-09-11 | C | 75 | 0.079011 | 0.00022678
2016 | 2015-09-29 | B | 80 | 0.022748 | 0.0002419
2016 | 2015-09-11 | C | 1 | 0.00062592 | 3.0238e-06
2016 | 2015-09-29 | B | 19 | 0.020277 | 5.7451e-05
2016 | 2015-09-11 | C | 2 | 0.00050235 | 6.0475e-06
2016 | 2015-09-11 | C | 33 | 0.0066756 | 9.9784e-05
2016 | 2015-09-27 | B | 207 | 0.057122 | 0.00062592
2016 | 2015-09-27 | B | 207 | 0.0038145 | 0.00062592
2016 | 2015-09-28 | B | 28 | 0.0052281 | 8.4665e-05
2016 | 2015-09-28 | B | 111 | 0.013649 | 0.00033564
2016 | 2015-09-28 | B | 161 | 0.019044 | 0.00048683
2016 | 2015-09-28 | B | 161 | 0.016306 | 0.00048683
2016 | 2015-09-11 | C | 115 | 0.023283 | 0.00034773
2016 | 2015-09-11 | C | 18 | 0.0023404 | 5.4428e-05
2016 | 2015-09-12 | C | 20 | 0.0052059 | 6.0475e-05
2016 | 2015-09-12 | C | 2 | 0.00022487 | 6.0475e-06
2016 | 2015-09-12 | C | 2 | 0.00022769 | 6.0475e-06
2016 | 2015-09-13 | C | 857 | 0.14245 | 0.0025914
2016 | 2015-09-13 | C | 7 | 0.0018187 | 2.1166e-05
2016 | 2015-09-13 | C | 1 | 0.00017422 | 3.0238e-06
2016 | 2015-09-13 | C | 10 | 0.0030495 | 3.0238e-05
2016 | 2015-09-13 | C | 804 | 0.0038383 | 0.0024311
2016 | 2015-09-14 | C | 2 | 0.00065223 | 6.0475e-06
2016 | 2015-09-30 | B | 7 | 0.0077335 | 2.1166e-05
2016 | 2015-09-20 | B | 1 | 0.0001341 | 3.0238e-06
2016 | 2015-09-14 | C | 10 | 0.0042796 | 3.0238e-05
2016 | 2015-09-22 | B | 180 | 0.14435 | 0.00054428
2016 | 2015-09-24 | B | 180 | 0.056169 | 0.00054428
2016 | 2015-10-01 | B | 5 | 0.0028121 | 1.5119e-05
2016 | 2015-10-01 | B | 2 | 0.00061775 | 6.0475e-06
2016 | 2015-10-01 | B | 31 | 0.0040135 | 9.3737e-05
2016 | 2015-10-02 | B | 1 | 0.00015724 | 3.0238e-06
2016 | 2015-09-14 | C | 34 | 0.0062679 | 0.00010281
2016 | 2015-09-14 | C | 2 | 0.00038029 | 6.0475e-06
2016 | 2015-10-02 | B | 5 | 0.0010432 | 1.5119e-05
2016 | 2015-10-02 | B | 78 | 0.024544 | 0.00023585
2016 | 2015-10-01 | B | 8 | 0.00065313 | 2.419e-05
2016 | 2015-10-05 | B | 5 | 0.0025248 | 1.5119e-05
2016 | 2015-09-15 | B | 52 | 0.0062894 | 0.00015724
2016 | 2015-10-06 | B | 10 | 0.00081642 | 3.0238e-05
2016 | 2015-10-06 | B | 1 | 0.000127 | 3.0238e-06
2016 | 2015-10-01 | B | 8 | 0.0083214 | 2.419e-05
2016 | 2015-10-02 | B | 4 | 0.001118 | 1.2095e-05
2016 | 2015-10-05 | B | 3 | 0.0021136 | 9.0713e-06
2016 | 2015-10-01 | B | 61 | 0.018998 | 0.00018445
2016 | 2015-10-05 | B | 5 | 0.004838 | 1.5119e-05
2016 | 2015-10-01 | B | 4 | 0.0014756 | 1.2095e-05
2016 | 2015-10-01 | B | 86 | 0.062828 | 0.00026004
2016 | 2015-10-06 | B | 60 | 0.045006 | 0.00018143
2016 | 2015-10-01 | B | 6 | 0.0046626 | 1.8143e-05
2016 | 2015-10-08 | B | 8 | 0.0045675 | 2.419e-05
2016 | 2015-09-15 | C | 1 | 0.00020305 | 3.0238e-06
2016 | 2015-10-01 | B | 3 | 0.0013244 | 9.0713e-06
2016 | 2015-10-05 | B | 32 | 0.017709 | 9.676e-05
2016 | 2015-10-07 | B | 1 | 8.1642e-05 | 3.0238e-06
2016 | 2015-10-07 | B | 4 | 0.00062894 | 1.2095e-05
2016 | 2015-10-08 | B | 4 | 0.00038704 | 1.2095e-05
2016 | 2015-10-01 | B | 21 | 0.013398 | 6.3499e-05
2016 | 2015-10-09 | B | 6 | 0.0008527 | 1.8143e-05
2016 | 2015-10-05 | B | 1 | 0.00011188 | 3.0238e-06
2016 | 2015-10-05 | B | 2 | 0.00016328 | 6.0475e-06
2016 | 2015-09-22 | B | 140 | 0.030099 | 0.00042333
2016 | 2015-10-05 | B | 2 | 4.2333e-05 | 6.0475e-06
2016 | 2015-10-05 | B | 4 | 0.00026609 | 1.2095e-05
2016 | 2015-10-05 | B | 1 | 6.6523e-05 | 3.0238e-06
2016 | 2015-10-05 | B | 7 | 0.001905 | 2.1166e-05
2016 | 2015-10-01 | B | 55 | 0.042408 | 0.00016631
2016 | 2015-09-16 | C | 491 | 0.0035385 | 0.0014847
2016 | 2015-10-13 | B | 24 | 0.02667 | 7.257e-05
2016 | 2015-09-29 | B | 237 | 0.041326 | 0.00071663
2016 | 2015-10-15 | B | 24 | 0.026347 | 7.257e-05
2016 | 2015-10-06 | B | 162 | 0.043752 | 0.00048985
2016 | 2015-09-29 | B | 37 | 0.044295 | 0.00011188
2016 | 2015-10-06 | B | 6 | 0.0028572 | 1.8143e-05
2016 | 2015-10-01 | B | 4 | 0.0043784 | 1.2095e-05
2016 | 2015-10-02 | B | 6 | 0.0029028 | 1.8143e-05
2016 | 2015-10-09 | B | 6 | 0.0010341 | 1.8143e-05
2016 | 2015-10-12 | B | 18 | 0.018414 | 5.4428e-05
2016 | 2015-10-15 | B | 6 | 0.0061458 | 1.8143e-05
2016 | 2015-10-02 | B | 2 | 0.0018856 | 6.0475e-06
2016 | 2015-10-12 | B | 3 | 0.0024051 | 9.0713e-06
2016 | 2015-10-22 | B | 5 | 0.0038581 | 1.5119e-05
2016 | 2015-10-19 | B | 1 | 0.00088072 | 3.0238e-06
2016 | 2015-10-06 | B | 51 | 0.065848 | 0.00015421
2016 | 2015-09-16 | C | 624 | 0.038924 | 0.0018868
2016 | 2015-09-16 | C | 2 | 0.0001151 | 6.0475e-06
2016 | 2015-09-16 | C | 4 | 0.0008396 | 1.2095e-05
2016 | 2015-09-16 | C | 2 | 0.006371 | 6.0475e-06
2016 | 2015-10-15 | B | 3 | 0.0026579 | 9.0713e-06
2016 | 2015-10-12 | B | 5 | 0.00063499 | 1.5119e-05
2016 | 2015-10-12 | B | 2 | 0.00022376 | 6.0475e-06
2016 | 2015-10-12 | B | 4 | 0.00038704 | 1.2095e-05
2016 | 2015-10-13 | B | 3 | 0.0014952 | 9.0713e-06
2016 | 2015-10-13 | B | 7 | 0.0018415 | 2.1166e-05
2016 | 2015-10-07 | B | 5 | 0.0040821 | 1.5119e-05
2016 | 2015-10-21 | B | 10 | 0.0055098 | 3.0238e-05
2016 | 2015-10-07 | B | 1 | 0.00030913 | 3.0238e-06
2016 | 2015-09-17 | C | 5 | 0.0014519 | 1.5119e-05
2016 | 2015-09-17 | C | 75 | 0.023132 | 0.00022678
2016 | 2015-10-08 | B | 75 | 0.069237 | 0.00022678
2016 | 2015-10-05 | B | 1 | 0.00052009 | 3.0238e-06
2016 | 2015-10-07 | B | 16 | 0.018474 | 4.838e-05
2016 | 2015-10-13 | B | 16 | 0.013762 | 4.838e-05
2016 | 2015-10-13 | B | 3 | 0.00051706 | 9.0713e-06
2016 | 2015-10-05 | B | 2 | 0.00034471 | 6.0475e-06
2016 | 2015-10-05 | B | 3 | 0.00075292 | 9.0713e-06
2016 | 2015-10-13 | B | 2 | 0.0007378 | 6.0475e-06
2016 | 2015-09-17 | C | 29 | 0.017728 | 8.7689e-05
2016 | 2015-10-09 | B | 37 | 0.018354 | 0.00011188
2016 | 2015-10-06 | B | 33 | 0.040655 | 9.9784e-05
2016 | 2015-10-06 | B | 34 | 0.024114 | 0.00010281
2016 | 2015-10-14 | B | 41 | 0.013771 | 0.00012397
2016 | 2015-10-09 | B | 5 | 0.0016631 | 1.5119e-05
2016 | 2015-09-17 | C | 360 | 0.15161 | 0.0010886
2016 | 2015-09-17 | C | 1033 | 0.16276 | 0.0031235
2016 | 2015-09-17 | C | 20 | 0.00083557 | 6.0475e-05
2016 | 2015-09-17 | C | 2 | 0.0020593 | 6.0475e-06
2016 | 2015-09-18 | C | 8 | 0.004301 | 2.419e-05
2016 | 2015-09-18 | C | 2 | 0.00068151 | 6.0475e-06
2016 | 2015-09-23 | C | 2 | 1.2095e-05 | 6.0475e-06
2016 | 2015-09-18 | C | 62 | 0.038426 | 0.00018747
2016 | 2015-09-19 | C | 93 | 0.017072 | 0.00028121
2016 | 2015-09-19 | C | 14 | 0.0011924 | 4.2333e-05
2016 | 2015-09-19 | C | 53 | 0.0054174 | 0.00016026
2016 | 2015-09-19 | C | 255 | 0.047769 | 0.00077106
2016 | 2015-09-19 | C | 93 | 0.028482 | 0.00028121
2016 | 2015-09-19 | C | 238 | 0.15698 | 0.00071966
2016 | 2015-09-20 | C | 249 | 0.22145 | 0.00075292
2016 | 2015-09-20 | C | 2 | 0.002954 | 6.0475e-06
2016 | 2015-09-20 | C | 1 | 0.001136 | 3.0238e-06
2016 | 2015-09-20 | C | 15 | 0.021588 | 4.5356e-05
2016 | 2015-09-20 | C | 19 | 0.012924 | 5.7451e-05
2016 | 2015-09-20 | C | 2 | 0.00088405 | 6.0475e-06
2016 | 2015-09-20 | C | 1 | 0.00026418 | 3.0238e-06
2016 | 2015-09-20 | C | 21 | 0.10929 | 6.3499e-05
2016 | 2015-09-20 | C | 3 | 0.0032555 | 9.0713e-06
2016 | 2015-09-20 | C | 1 | 0.001286 | 3.0238e-06
2016 | 2015-09-20 | C | 1 | 0.0015194 | 3.0238e-06
2016 | 2015-09-20 | C | 162 | 0.027865 | 0.00048985
2016 | 2015-09-20 | C | 274 | 0.085585 | 0.00082851
2016 | 2015-09-20 | C | 2 | 0.00055607 | 6.0475e-06
2016 | 2015-09-20 | C | 113 | 0.028261 | 0.00034168
2016 | 2015-09-20 | C | 7 | 0.011507 | 2.1166e-05
2016 | 2015-09-20 | C | 5 | 0.0087684 | 1.5119e-05
2016 | 2015-09-20 | C | 11 | 0.013366 | 3.3261e-05
2016 | 2015-09-20 | C | 2 | 0.0029052 | 6.0475e-06
2016 | 2015-09-20 | C | 1 | 3.9158e-05 | 3.0238e-06
2016 | 2015-09-20 | C | 31 | 0.093951 | 9.3737e-05
2016 | 2015-09-20 | C | 6 | 0.031652 | 1.8143e-05
2016 | 2015-09-20 | C | 178 | 0.10591 | 0.00053823
2016 | 2015-09-20 | C | 17 | 0.052884 | 5.1404e-05
2016 | 2015-09-20 | C | 143 | 0.26822 | 0.0004324
2016 | 2015-09-20 | C | 3 | 0.0083968 | 9.0713e-06
2016 | 2015-09-20 | C | 8 | 0.0060786 | 2.419e-05
2016 | 2015-09-20 | C | 10 | 0.0025576 | 3.0238e-05
2016 | 2015-09-20 | C | 423 | 0.085116 | 0.0012791
2016 | 2015-09-20 | C | 5 | 0.0031563 | 1.5119e-05
2016 | 2015-09-20 | C | 10 | 0.01732 | 3.0238e-05
2016 | 2015-09-20 | C | 4 | 0.014046 | 1.2095e-05
2016 | 2015-09-20 | C | 15 | 0.0075413 | 4.5356e-05
2016 | 2015-09-20 | C | 1 | 0.00036421 | 3.0238e-06
2016 | 2015-09-20 | C | 8 | 0.022368 | 2.419e-05
2016 | 2015-09-21 | C | 156 | 0.038428 | 0.00047171
2016 | 2015-09-21 | C | 32 | 0.04123 | 9.676e-05
2016 | 2015-09-21 | C | 9 | 0.020628 | 2.7214e-05
2016 | 2015-09-21 | C | 9 | 0.0092523 | 2.7214e-05
2016 | 2015-09-21 | C | 4 | 0.01123 | 1.2095e-05
2016 | 2015-09-21 | C | 418 | 0.12685 | 0.0012639
2016 | 2015-09-21 | C | 156 | 0.019529 | 0.00047171
2016 | 2015-09-21 | C | 4 | 0.0019255 | 1.2095e-05
2016 | 2015-09-21 | C | 5 | 0.003344 | 1.5119e-05
2016 | 2015-09-21 | C | 1 | 0.00054569 | 3.0238e-06
2016 | 2015-09-21 | C | 235 | 0.15026 | 0.00071058
2016 | 2015-09-21 | C | 357 | 0.10002 | 0.0010795
2016 | 2015-09-21 | C | 1325 | 0.40867 | 0.0040065
2016 | 2015-10-14 | B | 5 | 0.00018143 | 1.5119e-05
2016 | 2015-10-14 | B | 1 | 0.00016384 | 3.0238e-06
2016 | 2015-10-14 | B | 2 | 0.0003568 | 6.0475e-06
2016 | 2015-09-21 | C | 640 | 0.11291 | 0.0019352
2016 | 2015-10-15 | B | 9 | 0.0019594 | 2.7214e-05
2016 | 2015-09-21 | C | 116 | 0.012343 | 0.00035076
2016 | 2015-09-21 | C | 13 | 0.015394 | 3.9309e-05
2016 | 2015-09-21 | C | 1 | 0.00015174 | 3.0238e-06
2016 | 2015-09-21 | C | 5 | 0.0058953 | 1.5119e-05
2016 | 2015-10-07 | B | 161 | 0.095807 | 0.00048683
2016 | 2015-09-21 | C | 1 | 0.00015724 | 3.0238e-06
2016 | 2015-09-21 | C | 6 | 0.0012621 | 1.8143e-05
2016 | 2015-10-16 | B | 5 | 0.00033261 | 1.5119e-05
2016 | 2015-10-16 | B | 1 | 8.1642e-05 | 3.0238e-06
2016 | 2015-10-16 | B | 12 | 0.0093458 | 3.6285e-05
2016 | 2015-10-09 | B | 3 | 0.0035832 | 9.0713e-06
2016 | 2015-10-16 | B | 2 | 0.00040478 | 6.0475e-06
2016 | 2015-10-20 | B | 12 | 0.010863 | 3.6285e-05
2016 | 2015-10-21 | B | 181 | 0.032444 | 0.0005473
2016 | 2015-09-21 | C | 19 | 0.08355 | 5.7451e-05
2016 | 2015-09-29 | B | 29 | 0.033844 | 8.7689e-05
2016 | 2015-10-15 | B | 8 | 0.0090023 | 2.419e-05
2016 | 2015-10-16 | B | 8 | 0.0052992 | 2.419e-05
2016 | 2015-10-07 | B | 10 | 0.010687 | 3.0238e-05
2016 | 2015-09-21 | C | 283 | 0.05638 | 0.00085572
2016 | 2015-10-08 | B | 8 | 0.010695 | 2.419e-05
2016 | 2015-10-09 | B | 8 | 0.0061201 | 2.419e-05
2016 | 2015-10-23 | B | 61 | 0.059826 | 0.00018445
2016 | 2015-10-12 | B | 14 | 0.010504 | 4.2333e-05
2016 | 2015-09-21 | C | 10 | 0.0044102 | 3.0238e-05
2016 | 2015-10-08 | B | 9 | 0.0051978 | 2.7214e-05
2016 | 2015-09-21 | C | 1 | 0.00080518 | 3.0238e-06
2016 | 2015-09-22 | C | 3 | 0.00092527 | 9.0713e-06
2016 | 2015-09-21 | C | 67 | 0.01284 | 0.00020259
2016 | 2015-09-21 | C | 1124 | 0.54439 | 0.0033987
2016 | 2015-09-21 | C | 3 | 0.0010864 | 9.0713e-06
2016 | 2015-09-21 | C | 107 | 0.020827 | 0.00032354
2016 | 2015-09-21 | C | 774 | 0.056773 | 0.0023404
2016 | 2015-09-21 | C | 8 | 0.019119 | 2.419e-05
2016 | 2015-09-21 | C | 5 | 0.0031881 | 1.5119e-05
2016 | 2015-09-21 | C | 809 | 0.1709 | 0.0024462
2016 | 2015-09-20 | C | 238 | 0.064113 | 0.00071966
2016 | 2015-09-22 | C | 19 | 0.033063 | 5.7451e-05
2016 | 2015-09-21 | C | 29 | 0.09242 | 8.7689e-05
2016 | 2015-09-24 | B | 12 | 0.0035922 | 3.6285e-05
2016 | 2015-09-21 | C | 640 | 0.021287 | 0.0019352
2016 | 2015-09-22 | C | 4 | 0.00020562 | 1.2095e-05
2016 | 2015-10-08 | B | 18 | 0.010041 | 5.4428e-05
2016 | 2015-09-22 | C | 1 | 9.7516e-05 | 3.0238e-06
2016 | 2015-09-22 | C | 2 | 0.001697 | 6.0475e-06
2016 | 2015-09-22 | C | 8 | 0.00039752 | 2.419e-05
2016 | 2015-09-23 | C | 3 | 0.00062758 | 9.0713e-06
2016 | 2015-10-13 | B | 129 | 0.13396 | 0.00039007
2016 | 2015-09-23 | C | 2 | 0.0011829 | 6.0475e-06
2016 | 2015-10-08 | B | 2 | 0.0018695 | 6.0475e-06
2016 | 2015-10-13 | B | 5 | 0.0047546 | 1.5119e-05
2016 | 2015-10-08 | B | 6 | 0.0057838 | 1.8143e-05
2016 | 2015-10-02 | B | 2 | 0.0010704 | 6.0475e-06
2016 | 2015-10-13 | B | 9 | 0.010448 | 2.7214e-05
2016 | 2015-10-14 | B | 9 | 0.009636 | 2.7214e-05
2016 | 2015-10-17 | B | 1 | 0.00045961 | 3.0238e-06
2016 | 2015-10-19 | B | 8 | 0.0002798 | 2.419e-05
2016 | 2015-09-23 | C | 854 | 0.04102 | 0.0025823
2016 | 2015-10-21 | B | 8 | 0.0056863 | 2.419e-05
2016 | 2015-10-22 | B | 29 | 0.013937 | 8.7689e-05
2016 | 2015-09-23 | C | 1 | 0.00015038 | 3.0238e-06
2016 | 2015-09-21 | C | 117 | 0.015243 | 0.00035378
2016 | 2015-10-14 | B | 5 | 0.0057794 | 1.5119e-05
2016 | 2015-09-23 | C | 1 | 0.00022794 | 3.0238e-06
2016 | 2015-09-23 | C | 14 | 0.0053085 | 4.2333e-05
2016 | 2015-09-24 | C | 3 | 0.00093056 | 9.0713e-06
2016 | 2015-10-09 | B | 4 | 0.0036769 | 1.2095e-05
2016 | 2015-09-24 | C | 40 | 0.036733 | 0.00012095
2016 | 2015-09-24 | C | 86 | 0.041612 | 0.00026004
2016 | 2015-09-27 | B | 1 | 0.00020713 | 3.0238e-06
2016 | 2015-10-12 | B | 7 | 0.0094525 | 2.1166e-05
2016 | 2015-09-24 | C | 41 | 0.019464 | 0.00012397
2016 | 2015-09-24 | C | 20 | 0.0035358 | 6.0475e-05
2016 | 2015-09-24 | C | 50 | 0.010848 | 0.00015119
2016 | 2015-09-24 | C | 495 | 0.066275 | 0.0014968
2016 | 2015-10-02 | B | 2 | 0.0014635 | 6.0475e-06
2016 | 2015-10-15 | B | 14 | 0.0093703 | 4.2333e-05
2016 | 2015-10-20 | B | 8 | 0.0064588 | 2.419e-05
2016 | 2015-10-16 | B | 5 | 0.0015724 | 1.5119e-05
2016 | 2015-09-24 | C | 17 | 0.0038056 | 5.1404e-05
2016 | 2015-09-24 | C | 2 | 0.00083405 | 6.0475e-06
2016 | 2015-09-24 | C | 2 | 0.00016883 | 6.0475e-06
2016 | 2015-09-25 | C | 1 | 0.00067984 | 3.0238e-06
2016 | 2015-10-16 | B | 10 | 0.010583 | 3.0238e-05
2016 | 2015-10-19 | B | 9 | 0.0047896 | 2.7214e-05
2016 | 2015-10-21 | B | 2 | 0.0011732 | 6.0475e-06
2016 | 2015-10-18 | B | 157 | 0.095294 | 0.00047473
2016 | 2015-09-26 | C | 10 | 0.01288 | 3.0238e-05
2016 | 2015-10-13 | B | 106 | 0.057779 | 0.00032052
2016 | 2015-10-13 | B | 44 | 0.043202 | 0.00013305
2016 | 2015-10-13 | B | 19 | 0.01789 | 5.7451e-05
2016 | 2015-10-13 | B | 11 | 0.004839 | 3.3261e-05
2016 | 2015-10-21 | B | 2 | 0.0019176 | 6.0475e-06
2016 | 2015-10-22 | B | 185 | 0.22164 | 0.0005594
2016 | 2015-09-26 | C | 18 | 0.0072389 | 5.4428e-05
2016 | 2015-10-27 | B | 185 | 0.057469 | 0.0005594
2016 | 2015-10-14 | B | 4 | 0.0026549 | 1.2095e-05
2016 | 2015-09-25 | C | 20 | 0.0036344 | 6.0475e-05
2016 | 2015-09-25 | C | 113 | 0.027257 | 0.00034168
2016 | 2015-09-26 | C | 1 | 0.00028514 | 3.0238e-06
2016 | 2015-09-26 | C | 3 | 0.00085739 | 9.0713e-06
2016 | 2015-09-26 | C | 1 | 0.00023384 | 3.0238e-06
2016 | 2015-09-27 | C | 833 | 0.21855 | 0.0025188
2016 | 2015-09-27 | C | 1 | 0.00026433 | 3.0238e-06
2016 | 2015-09-27 | C | 1 | 0.00029467 | 3.0238e-06
2016 | 2015-09-28 | C | 2 | 0.0019771 | 6.0475e-06
2016 | 2015-09-28 | C | 2 | 0.00074737 | 6.0475e-06
2016 | 2015-10-02 | B | 5 | 0.00063499 | 1.5119e-05
2016 | 2015-10-07 | B | 6 | 0.0055586 | 1.8143e-05
2016 | 2015-10-22 | B | 6 | 0.0039596 | 1.8143e-05
2016 | 2015-10-07 | B | 1 | 0.0018794 | 3.0238e-06
2016 | 2015-10-09 | B | 17 | 0.019916 | 5.1404e-05
2016 | 2015-09-28 | C | 2 | 0.0010842 | 6.0475e-06
2016 | 2015-10-17 | B | 257 | 0.045713 | 0.00077711
2016 | 2015-09-28 | C | 1 | 0.0019467 | 3.0238e-06
2016 | 2015-09-28 | C | 1 | 0.00023742 | 3.0238e-06
2016 | 2015-09-28 | C | 8 | 0.0012091 | 2.419e-05
2016 | 2015-09-28 | C | 6 | 0.0014203 | 1.8143e-05
2016 | 2015-09-29 | C | 12 | 0.0056405 | 3.6285e-05
2016 | 2015-10-22 | B | 24 | 0.031101 | 7.257e-05
2016 | 2015-10-20 | B | 24 | 0.02657 | 7.257e-05
2016 | 2015-09-29 | C | 52 | 0.0075919 | 0.00015724
2016 | 2015-09-29 | C | 7 | 0 | 2.1166e-05
2016 | 2015-10-15 | B | 8 | 0.0083208 | 2.419e-05
2016 | 2015-10-21 | B | 76 | 0.082232 | 0.00022981
2016 | 2015-10-04 | B | 5 | 0.0020126 | 1.5119e-05
2016 | 2015-09-29 | C | 22 | 0.010223 | 6.6523e-05
2016 | 2015-09-29 | C | 1161 | 0.20287 | 0.0035106
2016 | 2015-09-29 | C | 1 | 0.00055153 | 3.0238e-06
2016 | 2015-09-29 | C | 2 | 0.00088294 | 6.0475e-06
2016 | 2015-09-30 | C | 180 | 0.0014786 | 0.00054428
2016 | 2015-09-30 | C | 14 | 0.0037048 | 4.2333e-05
2016 | 2015-10-02 | B | 6 | 0.0044721 | 1.8143e-05
2016 | 2015-10-07 | B | 3 | 0.001888 | 9.0713e-06
2016 | 2015-10-16 | B | 64 | 0.060678 | 0.00019352
2016 | 2015-10-20 | B | 20 | 0.027888 | 6.0475e-05
2016 | 2015-09-30 | C | 2 | 0.00047372 | 6.0475e-06
2016 | 2015-10-01 | C | 67 | 0.027356 | 0.00020259
2016 | 2015-10-01 | C | 4 | 0.0022489 | 1.2095e-05
2016 | 2015-10-27 | B | 7 | 0.0061982 | 2.1166e-05
2016 | 2015-10-28 | B | 7 | 0.0077045 | 2.1166e-05
2016 | 2015-10-31 | B | 7 | 0.0030402 | 2.1166e-05
2016 | 2015-10-02 | B | 40 | 0.0099179 | 0.00012095
2016 | 2015-10-01 | C | 15 | 0.010752 | 4.5356e-05
2016 | 2015-10-01 | C | 82 | 0 | 0.00024795
2016 | 2015-10-17 | B | 14 | 0.013631 | 4.2333e-05
2016 | 2015-10-19 | B | 34 | 0.036675 | 0.00010281
2016 | 2015-10-01 | C | 2 | 0.0004007 | 6.0475e-06
2016 | 2015-10-28 | B | 49 | 0.050356 | 0.00014816
2016 | 2015-10-28 | B | 19 | 0.020317 | 5.7451e-05
2016 | 2015-10-01 | C | 60 | 0.046989 | 0.00018143
2016 | 2015-10-01 | C | 649 | 0.063138 | 0.0019624
2016 | 2015-10-02 | C | 58 | 0.054884 | 0.00017538
2016 | 2015-10-02 | C | 596 | 0.1676 | 0.0018022
2016 | 2015-10-20 | B | 6 | 0.0053883 | 1.8143e-05
2016 | 2015-10-02 | C | 331 | 0.18131 | 0.0010009
2016 | 2015-10-30 | B | 8 | 0.0052452 | 2.419e-05
2016 | 2015-10-17 | B | 5 | 0.0042787 | 1.5119e-05
2016 | 2015-10-02 | C | 421 | 0.14272 | 0.001273
2016 | 2015-10-03 | C | 355 | 0.14279 | 0.0010734
2016 | 2015-10-03 | C | 74 | 0.069898 | 0.00022376
2016 | 2015-10-03 | C | 1 | 0.00042726 | 3.0238e-06
2016 | 2015-10-03 | C | 715 | 0.04355 | 0.002162
2016 | 2015-10-04 | C | 1458 | 0.66949 | 0.0044086
2016 | 2015-10-04 | C | 2 | 0.0015612 | 6.0475e-06
2016 | 2015-10-04 | C | 2 | 0.00064708 | 6.0475e-06
2016 | 2015-10-04 | C | 1 | 3.3261e-05 | 3.0238e-06
2016 | 2015-10-04 | C | 768 | 0.1809 | 0.0023222
2016 | 2015-10-04 | C | 1024 | 0.21186 | 0.0030963
2016 | 2015-10-04 | C | 143 | 0.046015 | 0.0004324
2016 | 2015-10-04 | C | 65 | 0.01533 | 0.00019654
2016 | 2015-10-04 | C | 233 | 0.11634 | 0.00070454
2016 | 2015-10-05 | C | 1 | 0.00021181 | 3.0238e-06
2016 | 2015-10-03 | C | 7 | 0.0010371 | 2.1166e-05
2016 | 2015-10-05 | C | 64 | 0.013466 | 0.00019352
2016 | 2015-10-05 | C | 178 | 0.41675 | 0.00053823
2016 | 2015-10-21 | B | 3 | 0.002803 | 9.0713e-06
2016 | 2015-10-27 | B | 2 | 0.00021922 | 6.0475e-06
2016 | 2015-10-22 | B | 2 | 0.00076804 | 6.0475e-06
2016 | 2015-10-29 | B | 1 | 0.00032354 | 3.0238e-06
2016 | 2015-10-05 | C | 4 | 0.00204 | 1.2095e-05
2016 | 2015-10-05 | C | 160 | 0.13427 | 0.0004838
2016 | 2015-11-03 | B | 72 | 0.08892 | 0.00021771
2016 | 2015-10-27 | B | 97 | 0.11087 | 0.0002933
2016 | 2015-10-05 | C | 1 | 9.676e-05 | 3.0238e-06
2016 | 2015-10-04 | C | 524 | 0.11976 | 0.0015845
2016 | 2015-10-06 | C | 112 | 0.051117 | 0.00033866
2016 | 2015-10-06 | C | 341 | 0.0092376 | 0.0010311
2016 | 2015-10-06 | C | 282 | 0.001208 | 0.0008527
2016 | 2015-10-06 | C | 1 | 0.00036804 | 3.0238e-06
2016 | 2015-10-31 | B | 1 | 0.0016052 | 3.0238e-06
2016 | 2015-10-21 | B | 412 | 0.019134 | 0.0012458
2016 | 2015-10-06 | C | 33 | 0.00099784 | 9.9784e-05
2016 | 2015-10-13 | B | 67 | 0.059221 | 0.00020259
2016 | 2015-10-28 | B | 68 | 0.076561 | 0.00020562
2016 | 2015-10-07 | C | 35 | 0.02233 | 0.00010583
2016 | 2015-10-28 | B | 111 | 0.12589 | 0.00033564
2016 | 2015-10-07 | C | 6 | 0.00076919 | 1.8143e-05
2016 | 2015-11-06 | B | 40 | 0.028608 | 0.00012095
2016 | 2015-10-09 | B | 264 | 0.023818 | 0.00079827
2016 | 2015-10-07 | C | 24 | 0.0063886 | 7.257e-05
2016 | 2015-10-07 | C | 1 | 0.00039173 | 3.0238e-06
2016 | 2015-10-07 | C | 1325 | 0.41667 | 0.0040065
2016 | 2015-10-07 | C | 869 | 0.049575 | 0.0026276
2016 | 2015-10-07 | C | 21 | 0.0063376 | 6.3499e-05
2016 | 2015-10-07 | C | 90 | 0.048622 | 0.00027214
2016 | 2015-10-07 | C | 517 | 0.042938 | 0.0015633
2016 | 2015-10-07 | C | 20 | 0.0056242 | 6.0475e-05
2016 | 2015-10-08 | C | 54 | 0.094821 | 0.00016328
2016 | 2015-10-08 | C | 494 | 0.14289 | 0.0014937
2016 | 2015-10-08 | C | 1 | 0.00048683 | 3.0238e-06
2016 | 2015-10-08 | C | 440 | 0.093535 | 0.0013305
2016 | 2015-10-08 | C | 4 | 0.0012426 | 1.2095e-05
2016 | 2015-10-08 | C | 118 | 0.009361 | 0.0003568
2016 | 2015-10-08 | C | 795 | 0.25739 | 0.0024039
2016 | 2015-10-27 | B | 22 | 0.013164 | 6.6523e-05
2016 | 2015-10-08 | C | 36 | 0.0060959 | 0.00010886
2016 | 2015-10-08 | C | 816 | 0.17975 | 0.0024674
2016 | 2015-10-09 | C | 27 | 0.0079192 | 8.1642e-05
2016 | 2015-10-08 | C | 52 | 0.053599 | 0.00015724
2016 | 2015-10-09 | C | 1716 | 0.065161 | 0.0051888
2016 | 2015-10-30 | B | 5 | 0.0040536 | 1.5119e-05
2016 | 2015-10-22 | B | 15 | 0.011498 | 4.5356e-05
2016 | 2015-10-31 | B | 1 | 0.0014849 | 3.0238e-06
2016 | 2015-10-13 | B | 1 | 0.00011188 | 3.0238e-06
2016 | 2015-10-10 | C | 3 | 0.004393 | 9.0713e-06
2016 | 2015-10-10 | C | 2 | 0.00087689 | 6.0475e-06
2016 | 2015-10-10 | C | 1 | 0.00035378 | 3.0238e-06
2016 | 2015-10-10 | C | 66 | 0.039857 | 0.00019957
2016 | 2015-10-10 | C | 1 | 0.00024467 | 3.0238e-06
2016 | 2015-10-10 | C | 6 | 0.00043089 | 1.8143e-05
2016 | 2015-10-11 | C | 1 | 0.00013511 | 3.0238e-06
2016 | 2015-10-11 | C | 1 | 0.00013511 | 3.0238e-06
2016 | 2015-10-11 | C | 7 | 0.0015864 | 2.1166e-05
2016 | 2015-10-11 | C | 43 | 0.0081338 | 0.00013002
2016 | 2015-10-11 | C | 250 | 0.058465 | 0.00075594
2016 | 2015-10-12 | C | 329 | 0.2325 | 0.00099482
2016 | 2015-10-12 | C | 17 | 0.0019319 | 5.1404e-05
2016 | 2015-10-12 | C | 306 | 0.13542 | 0.00092527
2016 | 2015-10-12 | C | 776 | 0.059579 | 0.0023464
2016 | 2015-10-12 | C | 177 | 0.095545 | 0.00053521
2016 | 2015-10-12 | C | 37 | 0.017196 | 0.00011188
2016 | 2015-10-13 | C | 419 | 0.07134 | 0.001267
2016 | 2015-10-14 | B | 119 | 0.10669 | 0.00035983
2016 | 2015-10-13 | C | 15 | 0.0050081 | 4.5356e-05
2016 | 2015-10-13 | C | 314 | 0.096035 | 0.00094946
2016 | 2015-11-02 | B | 40 | 0.026609 | 0.00012095
2016 | 2015-11-02 | B | 8 | 0.0038374 | 2.419e-05
2016 | 2015-11-02 | B | 4 | 0.0045568 | 1.2095e-05
2016 | 2015-11-02 | B | 28 | 0.029397 | 8.4665e-05
2016 | 2015-10-13 | C | 163 | 0.094599 | 0.00049287
2016 | 2015-10-13 | C | 93 | 0.040513 | 0.00028121
2016 | 2015-10-13 | C | 22 | 0.019296 | 6.6523e-05
2016 | 2015-10-13 | C | 10 | 0.0018178 | 3.0238e-05
2016 | 2015-10-14 | C | 363 | 0.041307 | 0.0010976
2016 | 2015-11-02 | B | 4 | 0.0031931 | 1.2095e-05
2016 | 2015-11-02 | B | 31 | 0.035432 | 9.3737e-05
2016 | 2015-11-03 | B | 2 | 0.0011006 | 6.0475e-06
2016 | 2015-11-05 | B | 1 | 0.0011248 | 3.0238e-06
2016 | 2015-11-02 | B | 33 | 0.035822 | 9.9784e-05
2016 | 2015-11-03 | B | 4 | 0.0034517 | 1.2095e-05
2016 | 2015-11-03 | B | 21 | 0.019902 | 6.3499e-05
2016 | 2015-11-03 | B | 46 | 0.032984 | 0.00013909
2016 | 2015-11-03 | B | 3 | 0.0010613 | 9.0713e-06
2016 | 2015-11-03 | B | 27 | 0.029762 | 8.1642e-05
2016 | 2015-11-11 | B | 27 | 0.02637 | 8.1642e-05
2016 | 2015-11-18 | B | 27 | 0.026697 | 8.1642e-05
2016 | 2015-11-02 | B | 165 | 0.13471 | 0.00049892
2016 | 2015-11-02 | B | 3 | 0.0010795 | 9.0713e-06
2016 | 2015-11-05 | B | 38 | 0.02907 | 0.0001149
2016 | 2015-11-02 | B | 1 | 0.00047473 | 3.0238e-06
2016 | 2015-11-03 | B | 33 | 0.02764 | 9.9784e-05
2016 | 2015-11-05 | B | 200 | 0.086762 | 0.00060475
2016 | 2015-11-03 | B | 43 | 0.048676 | 0.00013002
2016 | 2015-11-05 | B | 3 | 0.002494 | 9.0713e-06
2016 | 2015-11-05 | B | 43 | 0.043068 | 0.00013002
2016 | 2015-11-05 | B | 32 | 0.036203 | 9.676e-05
2016 | 2015-11-10 | B | 18 | 0.018614 | 5.4428e-05
2016 | 2015-11-12 | B | 20 | 0.022277 | 6.0475e-05
2016 | 2015-11-05 | B | 34 | 0.016693 | 0.00010281
2016 | 2015-11-10 | B | 43 | 0.049674 | 0.00013002
2016 | 2015-11-04 | B | 5 | 0.0030986 | 1.5119e-05
2016 | 2015-10-14 | C | 1 | 0.00036905 | 3.0238e-06
2016 | 2015-11-06 | B | 16 | 0.0086713 | 4.838e-05
2016 | 2015-11-08 | B | 83 | 0.056306 | 0.00025097
2016 | 2015-11-09 | B | 136 | 0.079525 | 0.00041123
2016 | 2015-11-09 | B | 2 | 0.0017963 | 6.0475e-06
2016 | 2015-11-05 | B | 24 | 0.011394 | 7.257e-05
2016 | 2015-11-09 | B | 8 | 0.0012188 | 2.419e-05
2016 | 2015-11-14 | B | 190 | 0.054868 | 0.00057451
2016 | 2015-11-09 | B | 10 | 0.0044308 | 3.0238e-05
2016 | 2015-10-14 | C | 170 | 0.042539 | 0.00051404
2016 | 2015-10-15 | C | 319 | 0.098058 | 0.00096458
2016 | 2015-10-16 | C | 31 | 0.0054024 | 9.3737e-05
2016 | 2015-11-10 | B | 13 | 0.0016903 | 3.9309e-05
2016 | 2015-11-10 | B | 6 | 0.0033927 | 1.8143e-05
2016 | 2015-10-15 | C | 777 | 0.072988 | 0.0023495
2016 | 2015-11-11 | B | 40 | 0.014151 | 0.00012095
2016 | 2015-11-11 | B | 6 | 0.0036648 | 1.8143e-05
2016 | 2015-11-05 | B | 27 | 0.028486 | 8.1642e-05
2016 | 2015-11-02 | B | 2 | 0.0012821 | 6.0475e-06
2016 | 2015-11-05 | B | 1 | 0.0011012 | 3.0238e-06
2016 | 2015-11-12 | B | 1 | 0.00085572 | 3.0238e-06
2016 | 2015-10-15 | C | 17 | 0.0079668 | 5.1404e-05
2016 | 2015-10-15 | C | 19 | 0.0044228 | 5.7451e-05
2016 | 2015-11-13 | B | 4 | 0.0060159 | 1.2095e-05
2016 | 2015-11-13 | B | 8 | 0.0064829 | 2.419e-05
2016 | 2015-10-16 | C | 21 | 0.0043211 | 6.3499e-05
2016 | 2015-11-04 | B | 27 | 0.025554 | 8.1642e-05
2016 | 2015-10-28 | B | 113 | 0.058991 | 0.00034168
2016 | 2015-10-16 | C | 291 | 0.054951 | 0.00087991
2016 | 2015-10-16 | C | 2112 | 0.61311 | 0.0063862
2016 | 2015-10-16 | C | 249 | 0.0082821 | 0.00075292
2016 | 2015-11-06 | B | 14 | 0.010414 | 4.2333e-05
2016 | 2015-11-05 | B | 3 | 0.0011067 | 9.0713e-06
2016 | 2015-11-05 | B | 1 | 0.00091318 | 3.0238e-06
2016 | 2015-10-16 | C | 1 | 8.1642e-05 | 3.0238e-06
2016 | 2015-10-16 | C | 6 | 0.056545 | 1.8143e-05
2016 | 2015-10-16 | C | 232 | 0.086267 | 0.00070151
2016 | 2015-10-16 | C | 99 | 0.26511 | 0.00029935
2016 | 2015-10-16 | C | 212 | 0.060758 | 0.00064104
2016 | 2015-10-16 | C | 108 | 0.037392 | 0.00032657
2016 | 2015-10-17 | C | 299 | 0.10674 | 0.0009041
2016 | 2015-10-17 | C | 1 | 0.0013003 | 3.0238e-06
2016 | 2015-10-17 | C | 2 | 0.0018665 | 6.0475e-06
2016 | 2015-10-17 | C | 8 | 0.013245 | 2.419e-05
2016 | 2015-10-17 | C | 424 | 0.48391 | 0.0012821
2016 | 2015-10-17 | C | 1 | 0.00053833 | 3.0238e-06
2016 | 2015-10-17 | C | 2 | 0.00082246 | 6.0475e-06
2016 | 2015-10-17 | C | 1 | 0.00073054 | 3.0238e-06
2016 | 2015-10-17 | C | 7 | 0.0044728 | 2.1166e-05
2016 | 2015-10-17 | C | 774 | 0.19993 | 0.0023404
2016 | 2015-10-18 | C | 38 | 0.038709 | 0.0001149
2016 | 2015-10-18 | C | 7 | 0.0013428 | 2.1166e-05
2016 | 2015-10-18 | C | 1 | 0.00046989 | 3.0238e-06
2016 | 2015-10-18 | C | 302 | 0.2508 | 0.00091318
2016 | 2015-10-18 | C | 197 | 0.029555 | 0.00059568
2016 | 2015-10-18 | C | 1472 | 0.37337 | 0.004451
2016 | 2015-10-18 | C | 36 | 0.0039188 | 0.00010886
2016 | 2015-10-18 | C | 833 | 0.21678 | 0.0025188
2016 | 2015-10-18 | C | 178 | 0.042767 | 0.00053823
2016 | 2015-10-18 | C | 1 | 0.00034743 | 3.0238e-06
2016 | 2015-10-18 | C | 48 | 0.0098768 | 0.00014514
2016 | 2015-10-18 | C | 1 | 0.00061488 | 3.0238e-06
2016 | 2015-10-18 | C | 83 | 0.011034 | 0.00025097
2016 | 2015-10-18 | C | 5 | 0.0013181 | 1.5119e-05
2016 | 2015-10-18 | C | 17 | 0.056657 | 5.1404e-05
2016 | 2015-10-18 | C | 1 | 0.00097199 | 3.0238e-06
2016 | 2015-10-18 | C | 3 | 0.0011398 | 9.0713e-06
2016 | 2015-10-18 | C | 2 | 0.0067721 | 6.0475e-06
2016 | 2015-10-18 | C | 842 | 0.53443 | 0.002546
2016 | 2015-10-19 | C | 75 | 0.019855 | 0.00022678
2016 | 2015-10-19 | C | 1049 | 0.068381 | 0.0031719
2016 | 2015-10-19 | B | 17 | 0.012786 | 5.1404e-05
2016 | 2015-11-16 | B | 12 | 0 | 3.6285e-05
2016 | 2015-10-19 | C | 1 | 0.00021726 | 3.0238e-06
2016 | 2015-10-19 | C | 15 | 0.002357 | 4.5356e-05
2016 | 2015-10-28 | B | 35 | 0.022318 | 0.00010583
2016 | 2015-10-19 | C | 118 | 0.0065044 | 0.0003568
2016 | 2015-11-17 | B | 47 | 0.050025 | 0.00014212
2016 | 2015-11-24 | B | 47 | 0.059921 | 0.00014212
2016 | 2015-10-19 | C | 229 | 0.041724 | 0.00069244
2016 | 2015-11-17 | B | 56 | 0.037052 | 0.00016933
2016 | 2015-10-19 | C | 3 | 0.00020053 | 9.0713e-06
2016 | 2015-10-19 | C | 6 | 0.0020486 | 1.8143e-05
2016 | 2015-10-19 | C | 149 | 0.052658 | 0.00045054
2016 | 2015-10-19 | C | 121 | 0.025859 | 0.00036588
2016 | 2015-10-19 | C | 2 | 0.0013156 | 6.0475e-06
2016 | 2015-10-19 | C | 30 | 0.002986 | 9.0713e-05
2016 | 2015-10-19 | C | 1 | 0.0006425 | 3.0238e-06
2016 | 2015-10-19 | C | 1228 | 0.16814 | 0.0037132
2016 | 2015-10-19 | C | 366 | 0 | 0.0011067
2016 | 2015-10-20 | C | 99 | 0.13237 | 0.00029935
2016 | 2015-10-19 | C | 368 | 0.070736 | 0.0011127
2016 | 2015-10-20 | C | 1 | 0.00059246 | 3.0238e-06
2016 | 2015-11-08 | B | 10 | 0.0095616 | 3.0238e-05
2016 | 2015-10-20 | C | 525 | 0.079006 | 0.0015875
2016 | 2015-10-20 | C | 7 | 0.0019184 | 2.1166e-05
2016 | 2015-11-10 | B | 2 | 0.0018566 | 6.0475e-06
2016 | 2015-11-12 | B | 106 | 0.037759 | 0.00032052
2016 | 2015-11-11 | B | 23 | 0.024202 | 6.9546e-05
2016 | 2015-10-20 | C | 3 | 0.01056 | 9.0713e-06
2016 | 2015-10-20 | C | 11 | 0.0037181 | 3.3261e-05
2016 | 2015-10-21 | C | 10 | 0.0035353 | 3.0238e-05
2016 | 2015-10-21 | C | 5120 | 0.6026 | 0.015482
2016 | 2015-11-08 | B | 2 | 0.0026488 | 6.0475e-06
2016 | 2015-10-21 | C | 2 | 0.00047826 | 6.0475e-06
2016 | 2015-10-30 | B | 37 | 0.036816 | 0.00011188
2016 | 2015-10-21 | C | 7 | 0.011049 | 2.1166e-05
2016 | 2015-11-09 | B | 13 | 0.010142 | 3.9309e-05
2016 | 2015-10-21 | C | 34 | 0.010329 | 0.00010281
2016 | 2015-10-21 | C | 19 | 0.0068406 | 5.7451e-05
2016 | 2015-11-12 | B | 5 | 0.005354 | 1.5119e-05
2016 | 2015-10-21 | C | 178 | 0.25298 | 0.00053823
2016 | 2015-10-21 | C | 231 | 0.32784 | 0.00069849
2016 | 2015-10-22 | C | 35 | 0.0046566 | 0.00010583
2016 | 2015-10-21 | C | 60 | 0.013933 | 0.00018143
2016 | 2015-10-21 | C | 176 | 0.13307 | 0.00053218
2016 | 2015-10-21 | C | 590 | 0.14108 | 0.001784
2016 | 2015-10-21 | C | 4 | 0.012548 | 1.2095e-05
2016 | 2015-10-21 | C | 2 | 0.00012992 | 6.0475e-06
2016 | 2015-10-21 | C | 61 | 0.00055335 | 0.00018445
2016 | 2015-10-22 | C | 1721 | 0.37332 | 0.0052039
2016 | 2015-10-22 | C | 1142 | 0.043322 | 0.0034531
2016 | 2015-10-22 | C | 100 | 0.048555 | 0.00030238
2016 | 2015-10-22 | C | 97 | 0.039259 | 0.0002933
2016 | 2015-10-22 | C | 11 | 0.0044463 | 3.3261e-05
2016 | 2015-10-22 | C | 1 | 0.0011024 | 3.0238e-06
2016 | 2015-10-22 | C | 286 | 0.022485 | 0.0008648
2016 | 2015-11-10 | B | 6 | 0.0065298 | 1.8143e-05
2016 | 2015-11-12 | B | 23 | 0.026636 | 6.9546e-05
2016 | 2015-10-22 | C | 201 | 0.030288 | 0.00060778
2016 | 2015-10-22 | C | 76 | 0.033919 | 0.00022981
2016 | 2015-10-22 | C | 34 | 0.053839 | 0.00010281
2016 | 2015-11-20 | B | 37 | 0.01309 | 0.00011188
2016 | 2015-11-11 | B | 25 | 0.012544 | 7.5594e-05
2016 | 2015-11-20 | B | 4 | 0.0041486 | 1.2095e-05
2016 | 2015-10-22 | C | 142 | 0.05228 | 0.00042937
2016 | 2015-10-22 | C | 2 | 0.00091066 | 6.0475e-06
2016 | 2015-10-23 | C | 818 | 0.16444 | 0.0024734
2016 | 2015-10-23 | C | 141 | 0.039932 | 0.00042635
2016 | 2015-10-23 | C | 142 | 0.045496 | 0.00042937
2016 | 2015-11-11 | B | 85 | 0.054865 | 0.00025702
2016 | 2015-10-23 | C | 1 | 0.00029935 | 3.0238e-06
2016 | 2015-10-23 | C | 255 | 0.067787 | 0.00077106
2016 | 2015-11-11 | B | 8 | 0.00029028 | 2.419e-05
2016 | 2015-10-23 | C | 53 | 0.01688 | 0.00016026
2016 | 2015-11-11 | B | 3 | 0.0011974 | 9.0713e-06
2016 | 2015-10-23 | C | 93 | 0.00028121 | 0.00028121
2016 | 2015-10-23 | C | 337 | 0.16039 | 0.001019
2016 | 2015-10-24 | C | 809 | 0.10415 | 0.0024462
2016 | 2015-10-24 | C | 154 | 0.0053473 | 0.00046566
2016 | 2015-10-24 | C | 1 | 0.00078643 | 3.0238e-06
2016 | 2015-10-24 | C | 1 | 0.00035575 | 3.0238e-06
2016 | 2015-10-25 | C | 886 | 0.21066 | 0.0026791
2016 | 2015-10-25 | C | 250 | 0.051094 | 0.00075594
2016 | 2015-10-25 | C | 3 | 0.0015415 | 9.0713e-06
2016 | 2015-10-25 | C | 6 | 0.0033918 | 1.8143e-05
2016 | 2015-10-25 | C | 70 | 0.011031 | 0.00021166
2016 | 2015-10-25 | C | 20 | 0.0022981 | 6.0475e-05
2016 | 2015-10-26 | C | 1 | 0.00028635 | 3.0238e-06
2016 | 2015-10-26 | C | 171 | 0.04508 | 0.00051706
2016 | 2015-10-26 | C | 809 | 0.10712 | 0.0024462
2016 | 2015-10-26 | C | 1 | 0.00054166 | 3.0238e-06
2016 | 2015-10-26 | C | 2 | 0.00027677 | 6.0475e-06
2016 | 2015-10-27 | C | 740 | 0.2351 | 0.0022376
2016 | 2015-10-27 | C | 1 | 0.00018294 | 3.0238e-06
2016 | 2015-10-27 | C | 3 | 0.001242 | 9.0713e-06
2016 | 2015-11-04 | B | 27 | 0.018092 | 8.1642e-05
2016 | 2015-10-27 | C | 1228 | 0.19252 | 0.0037132
2016 | 2015-11-17 | B | 23 | 0.022394 | 6.9546e-05
2016 | 2015-10-27 | C | 3074 | 0.16095 | 0.009295
2016 | 2015-11-16 | B | 21 | 0.022479 | 6.3499e-05
2016 | 2015-10-27 | C | 1 | 0.00030857 | 3.0238e-06
2016 | 2015-11-18 | B | 5 | 0.0045961 | 1.5119e-05
2016 | 2015-11-03 | B | 15 | 0.021227 | 4.5356e-05
2016 | 2015-11-18 | B | 23 | 0.015092 | 6.9546e-05
2016 | 2015-11-17 | B | 5 | 0.0022225 | 1.5119e-05
2016 | 2015-10-28 | C | 1 | 0.00024563 | 3.0238e-06
2016 | 2015-11-03 | B | 64 | 0.068119 | 0.00019352
2016 | 2015-10-28 | C | 240 | 0.014922 | 0.0007257
2016 | 2015-10-28 | C | 29 | 0.0091366 | 8.7689e-05
2016 | 2015-10-29 | C | 2 | 0.010051 | 6.0475e-06
2016 | 2015-11-04 | B | 65 | 0.058177 | 0.00019654
2016 | 2015-10-28 | C | 5 | 0.0032808 | 1.5119e-05
2016 | 2015-10-29 | C | 322 | 0 | 0.00097365
2016 | 2015-11-20 | B | 13 | 0.011709 | 3.9309e-05
2016 | 2015-11-17 | B | 2 | 0.0010704 | 6.0475e-06
2016 | 2015-10-29 | C | 8644 | 0.1622 | 0.026137
2016 | 2015-10-29 | C | 23 | 0.012128 | 6.9546e-05
2016 | 2015-10-29 | C | 1 | 0.00059316 | 3.0238e-06
2016 | 2015-11-17 | B | 27 | 0.006613 | 8.1642e-05
2016 | 2015-11-01 | B | 74 | 0.051353 | 0.00022376
2016 | 2015-10-29 | C | 72 | 0.054366 | 0.00021771
2016 | 2015-11-04 | B | 51 | 0.014187 | 0.00015421
2016 | 2015-10-29 | C | 5 | 0.0071305 | 1.5119e-05
2016 | 2015-10-30 | C | 23 | 0.0056727 | 6.9546e-05
2016 | 2015-10-30 | C | 680 | 0.69377 | 0.0020562
2016 | 2015-10-30 | C | 904 | 0.025629 | 0.0027335
2016 | 2015-10-30 | C | 577 | 0.13491 | 0.0017447
2016 | 2015-10-30 | C | 1 | 5.1404e-05 | 3.0238e-06
2016 | 2015-10-30 | C | 1 | 0.0009162 | 3.0238e-06
2016 | 2015-10-30 | C | 4 | 3.6285e-05 | 1.2095e-05
2016 | 2015-11-18 | B | 38 | 0.031828 | 0.0001149
2016 | 2015-10-30 | C | 9 | 0.0038644 | 2.7214e-05
2016 | 2015-11-18 | B | 39 | 0.022463 | 0.00011793
2016 | 2015-11-09 | B | 1 | 0.00053521 | 3.0238e-06
2016 | 2015-11-09 | B | 1 | 0.00026911 | 3.0238e-06
2016 | 2015-11-13 | B | 3 | 0.00092527 | 9.0713e-06
2016 | 2015-11-18 | B | 2 | 0.00022376 | 6.0475e-06
2016 | 2015-11-18 | B | 1 | 0.000127 | 3.0238e-06
2016 | 2015-11-19 | B | 8 | 0.0031931 | 2.419e-05
2016 | 2015-11-19 | B | 4 | 0.00044752 | 1.2095e-05
2016 | 2015-11-19 | B | 8 | 0.00099179 | 2.419e-05
2016 | 2015-11-27 | B | 4 | 0.00087084 | 1.2095e-05
2016 | 2015-11-27 | B | 3 | 0.00033564 | 9.0713e-06
2016 | 2015-11-18 | B | 5 | 0.0041577 | 1.5119e-05
2016 | 2015-11-12 | B | 21 | 0.025527 | 6.3499e-05
2016 | 2015-11-17 | B | 21 | 0.021082 | 6.3499e-05
2016 | 2015-11-19 | B | 52 | 0.023978 | 0.00015724
2016 | 2015-10-30 | C | 2 | 0.0021348 | 6.0475e-06
2016 | 2015-10-31 | C | 175 | 0.020998 | 0.00052916
2016 | 2015-10-31 | C | 1 | 2.1166e-05 | 3.0238e-06
2016 | 2015-10-31 | C | 181 | 0.054183 | 0.0005473
2016 | 2015-10-31 | C | 137 | 0.041545 | 0.00041426
2016 | 2015-10-31 | C | 32 | 0.0052761 | 9.676e-05
2016 | 2015-11-01 | C | 361 | 0.096139 | 0.0010916
2016 | 2015-11-01 | C | 95 | 0.015521 | 0.00028726
2016 | 2015-11-01 | C | 1 | 0.00011132 | 3.0238e-06
2016 | 2015-11-01 | C | 4 | 0.00093495 | 1.2095e-05
2016 | 2015-11-02 | C | 5 | 0.00099557 | 1.5119e-05
2016 | 2015-11-02 | C | 2 | 3.6386e-05 | 6.0475e-06
2016 | 2015-11-19 | B | 33 | 0.025645 | 9.9784e-05
2016 | 2015-11-19 | B | 23 | 0.013516 | 6.9546e-05
2016 | 2015-11-02 | B | 126 | 0.1054 | 0.00038099
2016 | 2015-11-26 | B | 11 | 0.011551 | 3.3261e-05
2016 | 2015-11-02 | C | 638 | 0.074699 | 0.0019292
2016 | 2015-11-02 | C | 15 | 0.0027403 | 4.5356e-05
2016 | 2015-11-05 | B | 493 | 0.34183 | 0.0014907
2016 | 2015-11-19 | B | 10 | 0.013492 | 3.0238e-05
2016 | 2015-11-23 | B | 5 | 0.005095 | 1.5119e-05
2016 | 2015-11-02 | C | 690 | 0 | 0.0020864
2016 | 2015-11-02 | C | 286 | 0.20453 | 0.0008648
2016 | 2015-11-03 | C | 21 | 0.0089258 | 6.3499e-05
2016 | 2015-11-03 | C | 5 | 0.00079726 | 1.5119e-05
2016 | 2015-11-23 | B | 1 | 0.00072127 | 3.0238e-06
2016 | 2015-11-25 | B | 19 | 0.014478 | 5.7451e-05
2016 | 2015-11-25 | B | 46 | 0.071077 | 0.00013909
2016 | 2015-11-03 | C | 1 | 0.00032027 | 3.0238e-06
2016 | 2015-11-25 | B | 82 | 0.047606 | 0.00024795
2016 | 2015-11-23 | B | 10 | 0.0099482 | 3.0238e-05
2016 | 2015-11-03 | C | 88 | 0.049769 | 0.00026609
2016 | 2015-11-03 | C | 15 | 0.00058963 | 4.5356e-05
2016 | 2015-11-03 | C | 76 | 0.035524 | 0.00022981
2016 | 2015-11-03 | C | 18 | 0.0040113 | 5.4428e-05
2016 | 2015-11-03 | C | 80 | 0.0053218 | 0.0002419
2016 | 2015-11-03 | C | 1 | 0.00013995 | 3.0238e-06
2016 | 2015-11-04 | C | 4937 | 0.41409 | 0.014928
2016 | 2015-11-04 | C | 924 | 0.15102 | 0.002794
2016 | 2015-11-07 | B | 28 | 0.0043783 | 8.4665e-05
2016 | 2015-11-04 | C | 1 | 0.00015603 | 3.0238e-06
2016 | 2015-11-04 | C | 310 | 0.11663 | 0.00093737
2016 | 2015-11-05 | B | 253 | 0.15261 | 0.00076501
2016 | 2015-11-04 | C | 651 | 0.19651 | 0.0019685
2016 | 2015-11-04 | C | 1 | 0.00030989 | 3.0238e-06
2016 | 2015-11-04 | C | 5 | 0.0008212 | 1.5119e-05
2016 | 2015-11-04 | C | 3 | 0.00036648 | 9.0713e-06
2016 | 2015-11-04 | C | 366 | 0.060999 | 0.0011067
2016 | 2015-11-04 | C | 315 | 0.10132 | 0.00095248
2016 | 2015-11-04 | C | 209 | 0.096419 | 0.00063197
2016 | 2015-11-04 | C | 232 | 0.090995 | 0.00070151
2016 | 2015-11-04 | C | 14 | 0.0026317 | 4.2333e-05
2016 | 2015-11-27 | B | 3 | 0.0015965 | 9.0713e-06
2016 | 2015-11-04 | C | 212 | 0.045901 | 0.00064104
2016 | 2015-11-04 | C | 1 | 0.00048058 | 3.0238e-06
2016 | 2015-11-04 | C | 154 | 0 | 0.00046566
2016 | 2015-11-04 | C | 1 | 3.9309e-05 | 3.0238e-06
2016 | 2015-11-04 | C | 107 | 0.0042061 | 0.00032354
2016 | 2015-11-04 | C | 44 | 0.001752 | 0.00013305
2016 | 2015-11-04 | C | 8 | 0.0021174 | 2.419e-05
2016 | 2015-11-04 | C | 4 | 0.0017119 | 1.2095e-05
2016 | 2015-11-04 | C | 4 | 0.00066402 | 1.2095e-05
2016 | 2015-11-04 | C | 8 | 0.0047481 | 2.419e-05
2016 | 2015-11-05 | C | 1 | 0.00021842 | 3.0238e-06
2016 | 2015-11-05 | C | 3 | 0.00085179 | 9.0713e-06
2016 | 2015-11-05 | C | 1 | 0.00025017 | 3.0238e-06
2016 | 2015-11-05 | C | 19 | 0.0071211 | 5.7451e-05
2016 | 2015-11-05 | C | 1 | 0.00040927 | 3.0238e-06
2016 | 2015-11-05 | C | 4722 | 0.11135 | 0.014278
2016 | 2015-11-05 | C | 302 | 0.075849 | 0.00091318
2016 | 2015-11-05 | C | 4 | 2.419e-05 | 1.2095e-05
2016 | 2015-11-25 | B | 3 | 0.0029028 | 9.0713e-06
2016 | 2015-11-22 | B | 19 | 0.023431 | 5.7451e-05
2016 | 2015-11-26 | B | 7 | 0.0060938 | 2.1166e-05
2016 | 2015-11-05 | C | 508 | 0.31328 | 0.0015361
2016 | 2015-11-06 | C | 317 | 0.051771 | 0.00095853
2016 | 2015-11-06 | C | 1 | 0.00023797 | 3.0238e-06
2016 | 2015-11-06 | C | 1 | 0.00049605 | 3.0238e-06
2016 | 2015-11-06 | C | 90 | 0.038427 | 0.00027214
2016 | 2015-11-06 | C | 8 | 0.0058459 | 2.419e-05
2016 | 2015-11-06 | C | 4 | 0.0057155 | 1.2095e-05
2016 | 2015-11-07 | C | 329 | 0.046756 | 0.00099482
2016 | 2015-11-07 | C | 1 | 0.00058021 | 3.0238e-06
2016 | 2015-11-07 | C | 14 | 0.08626 | 4.2333e-05
2016 | 2015-11-08 | C | 1 | 0.0004005 | 3.0238e-06
2016 | 2015-11-08 | C | 1 | 0.00014544 | 3.0238e-06
2016 | 2015-11-08 | C | 2 | 0.00061856 | 6.0475e-06
2016 | 2015-11-08 | C | 17 | 0.0060828 | 5.1404e-05
2016 | 2015-11-09 | C | 4 | 0.00083879 | 1.2095e-05
2016 | 2015-11-10 | C | 154 | 0.054612 | 0.00046566
2016 | 2015-11-25 | B | 1 | 0.00039309 | 3.0238e-06
2016 | 2015-11-10 | C | 254 | 0 | 0.00076804
2016 | 2015-11-10 | C | 1160 | 0.12067 | 0.0035076
2016 | 2015-11-10 | C | 1090 | 0.031312 | 0.0032959
2016 | 2015-11-10 | C | 3 | 0.00099512 | 9.0713e-06
2016 | 2015-11-10 | C | 3 | 0.0014271 | 9.0713e-06
2016 | 2015-11-10 | C | 4 | 0.0036676 | 1.2095e-05
2016 | 2015-11-10 | C | 1 | 7.9827e-05 | 3.0238e-06
2016 | 2015-11-10 | C | 107 | 0.017878 | 0.00032354
2016 | 2015-11-26 | B | 122 | 0.023978 | 0.0003689
2016 | 2015-11-12 | C | 1 | 0.00062894 | 3.0238e-06
2016 | 2015-12-02 | B | 11 | 0.013371 | 3.3261e-05
2016 | 2015-12-03 | B | 28 | 0.022078 | 8.4665e-05
2016 | 2015-11-11 | C | 1 | 0.004502 | 3.0238e-06
2016 | 2015-11-11 | C | 882 | 0.4075 | 0.002667
2016 | 2015-11-23 | B | 112 | 0.14569 | 0.00033866
2016 | 2015-11-11 | C | 26 | 0.000853 | 7.8618e-05
2016 | 2015-11-12 | C | 26 | 0.011557 | 7.8618e-05
2016 | 2015-11-12 | C | 8 | 0.0014353 | 2.419e-05
2016 | 2015-11-12 | C | 1 | 0.00018143 | 3.0238e-06
2016 | 2015-12-01 | B | 6 | 0.0026125 | 1.8143e-05
2016 | 2015-11-13 | B | 251 | 0.071757 | 0.00075896
2016 | 2015-12-01 | B | 5 | 0.00063499 | 1.5119e-05
2016 | 2015-12-01 | B | 3 | 0.00042635 | 9.0713e-06
2016 | 2015-12-08 | B | 3 | 0.00049726 | 9.0713e-06
2016 | 2015-12-01 | B | 2 | 0.001143 | 6.0475e-06
2016 | 2015-12-02 | B | 5 | 0.0040972 | 1.5119e-05
2016 | 2015-12-01 | B | 10 | 0.0092225 | 3.0238e-05
2016 | 2015-11-12 | C | 22 | 0.0020145 | 6.6523e-05
2016 | 2015-12-01 | B | 5 | 0.00018143 | 1.5119e-05
2016 | 2015-11-12 | C | 332 | 0.25268 | 0.0010039
2016 | 2015-12-01 | B | 49 | 0.059266 | 0.00014816
2016 | 2015-11-12 | C | 1 | 0.00029804 | 3.0238e-06
2016 | 2015-11-12 | C | 232 | 0.041955 | 0.00070151
2016 | 2015-11-12 | C | 2318 | 0.083358 | 0.0070091
2016 | 2015-11-12 | C | 81 | 0.01554 | 0.00024492
2016 | 2015-11-13 | C | 2 | 0.00052523 | 6.0475e-06
2016 | 2015-11-13 | C | 3516 | 0.43073 | 0.010632
2016 | 2015-11-13 | C | 1434 | 0.23813 | 0.0043361
2016 | 2015-12-04 | B | 12 | 0.012954 | 3.6285e-05
2016 | 2015-12-01 | B | 1 | 0.00071058 | 3.0238e-06
2016 | 2015-12-01 | B | 13 | 0.0052281 | 3.9309e-05
2016 | 2015-12-02 | B | 3 | 0.0028393 | 9.0713e-06
2016 | 2015-12-01 | B | 4 | 0.00062894 | 1.2095e-05
2016 | 2015-12-01 | B | 9 | 0.005987 | 2.7214e-05
2016 | 2015-12-07 | B | 12 | 0.0069583 | 3.6285e-05
2016 | 2015-12-03 | B | 11 | 0.011043 | 3.3261e-05
2016 | 2015-12-03 | B | 8 | 0.0096035 | 2.419e-05
2016 | 2015-11-21 | B | 110 | 0.085277 | 0.00033261
2016 | 2015-11-13 | C | 1 | 0.00040075 | 3.0238e-06
2016 | 2015-12-01 | B | 2 | 0.0017961 | 6.0475e-06
2016 | 2015-11-27 | B | 81 | 0.12785 | 0.00024492
2016 | 2015-12-02 | B | 19 | 0.01241 | 5.7451e-05
2016 | 2015-12-03 | B | 20 | 0.0096156 | 6.0475e-05
2016 | 2015-12-02 | B | 28 | 0.0044026 | 8.4665e-05
2016 | 2015-12-02 | B | 18 | 0.014532 | 5.4428e-05
2016 | 2015-11-29 | B | 51 | 0.047035 | 0.00015421
2016 | 2015-12-04 | B | 6 | 0.0022678 | 1.8143e-05
2016 | 2015-12-01 | B | 196 | 0.20802 | 0.00059266
2016 | 2015-12-02 | B | 4 | 0.0017901 | 1.2095e-05
2016 | 2015-11-13 | C | 239 | 0.039696 | 0.00072268
2016 | 2015-11-13 | C | 676 | 0.12597 | 0.0020441
2016 | 2015-11-14 | C | 340 | 0.074843 | 0.0010281
2016 | 2015-11-14 | C | 13 | 0.0044072 | 3.9309e-05
2016 | 2015-11-14 | C | 726 | 0.13459 | 0.0021953
2016 | 2015-11-14 | C | 626 | 0.15965 | 0.0018929
2016 | 2015-11-14 | C | 3 | 4.4046e-05 | 9.0713e-06
2016 | 2015-11-14 | C | 1 | 0.00042922 | 3.0238e-06
2016 | 2015-11-14 | C | 832 | 0.14813 | 0.0025158
2016 | 2015-11-15 | C | 1015 | 0.030765 | 0.0030691
2016 | 2015-11-15 | C | 236 | 0.06296 | 0.00071361
2016 | 2015-11-15 | C | 365 | 0.067236 | 0.0011037
2016 | 2015-11-15 | C | 67 | 0.032617 | 0.00020259
2016 | 2015-11-15 | C | 92 | 0.041419 | 0.00027819
2016 | 2015-11-15 | C | 1 | 0.0004709 | 3.0238e-06
2016 | 2015-11-15 | C | 1 | 4.1375e-05 | 3.0238e-06
2016 | 2015-11-19 | B | 16 | 0.0054315 | 4.838e-05
2016 | 2015-12-02 | B | 9 | 0.011858 | 2.7214e-05
2016 | 2015-12-02 | B | 72 | 0.014804 | 0.00021771
2016 | 2015-12-07 | B | 42 | 0.034306 | 0.000127
2016 | 2015-12-07 | B | 13 | 0.0074294 | 3.9309e-05
2016 | 2015-12-05 | B | 6 | 0.0045901 | 1.8143e-05
2016 | 2015-12-03 | B | 2 | 0.00039914 | 6.0475e-06
2016 | 2015-12-03 | B | 5 | 0.0050799 | 1.5119e-05
2016 | 2015-12-07 | B | 133 | 0.03003 | 0.00040216
2016 | 2015-12-08 | B | 38 | 0.033663 | 0.0001149
2016 | 2015-11-16 | C | 720 | 0.090908 | 0.0021771
2016 | 2015-12-08 | B | 53 | 0.060095 | 0.00016026
2016 | 2015-12-03 | B | 5 | 0.00015119 | 1.5119e-05
2016 | 2015-12-03 | B | 10 | 0.00081642 | 3.0238e-05
2016 | 2015-12-03 | B | 8 | 0.00029028 | 2.419e-05
2016 | 2015-12-03 | B | 3 | 0.00033564 | 9.0713e-06
2016 | 2015-12-03 | B | 4 | 0.00020562 | 1.2095e-05
2016 | 2015-12-03 | B | 1 | 0.043578 | 3.0238e-06
2016 | 2015-12-04 | B | 5 | 0.00040821 | 1.5119e-05
2016 | 2015-12-03 | B | 1 | 0.00024795 | 3.0238e-06
2016 | 2015-12-02 | B | 14 | 0.01651 | 4.2333e-05
2016 | 2015-11-16 | C | 680 | 0.18336 | 0.0020562
2016 | 2015-12-04 | B | 37 | 0.0060415 | 0.00011188
2016 | 2015-12-04 | B | 1 | 5.1404e-05 | 3.0238e-06
2016 | 2015-12-03 | B | 5 | 0.0058056 | 1.5119e-05
2016 | 2015-12-03 | B | 3 | 0.00051706 | 9.0713e-06
2016 | 2015-12-10 | B | 120 | 0.11357 | 0.00036285
2016 | 2015-12-09 | B | 18 | 0.017471 | 5.4428e-05
2016 | 2015-12-09 | B | 15 | 0.019911 | 4.5356e-05
2016 | 2015-11-17 | C | 26 | 0.010771 | 7.8618e-05
2016 | 2015-12-04 | B | 5 | 0.00033261 | 1.5119e-05
2016 | 2015-11-17 | C | 3 | 0.0014695 | 9.0713e-06
2016 | 2015-12-11 | B | 23 | 0.016483 | 6.9546e-05
2016 | 2015-12-06 | B | 6 | 0.0025463 | 1.8143e-05
2016 | 2015-12-07 | B | 5 | 0.00019654 | 1.5119e-05
2016 | 2015-12-04 | B | 1 | 0.00028423 | 3.0238e-06
2016 | 2015-12-04 | B | 1 | 0.00062592 | 3.0238e-06
2016 | 2015-12-07 | B | 4 | 0.00074989 | 1.2095e-05
2016 | 2015-12-04 | B | 1 | 0.00039309 | 3.0238e-06
2016 | 2015-12-02 | B | 41 | 0.004959 | 0.00012397
2016 | 2015-12-08 | B | 4 | 0.0019836 | 1.2095e-05
2016 | 2015-11-17 | C | 2 | 7.257e-05 | 6.0475e-06
2016 | 2015-12-08 | B | 22 | 0.033927 | 6.6523e-05
2016 | 2015-11-18 | C | 3 | 0.00071739 | 9.0713e-06
2016 | 2015-12-10 | B | 128 | 0.15333 | 0.00038704
2016 | 2015-11-18 | C | 2 | 0.002004 | 6.0475e-06
2016 | 2015-11-18 | C | 9 | 0.0057693 | 2.7214e-05
2016 | 2015-11-18 | B | 1 | 0.0040274 | 3.0238e-06
2016 | 2015-12-10 | B | 15 | 0.01846 | 4.5356e-05
2016 | 2015-12-04 | B | 5 | 0.00063499 | 1.5119e-05
2016 | 2015-11-18 | C | 34 | 0.03331 | 0.00010281
2016 | 2015-12-04 | B | 14 | 0.0056726 | 4.2333e-05
2016 | 2015-12-09 | B | 3 | 0.00044449 | 9.0713e-06
2016 | 2015-12-16 | B | 5 | 0.00066523 | 1.5119e-05
2016 | 2015-12-16 | B | 4 | 0.0015724 | 1.2095e-05
2016 | 2015-12-11 | B | 4 | 0.0034955 | 1.2095e-05
2016 | 2015-12-07 | B | 1 | 1.2095e-05 | 3.0238e-06
2016 | 2015-11-18 | C | 1 | 0.00022769 | 3.0238e-06
2016 | 2015-11-18 | C | 398 | 0.031564 | 0.0012035
2016 | 2015-11-19 | C | 1804 | 0.32383 | 0.0054549
2016 | 2015-11-19 | C | 12 | 0.0044425 | 3.6285e-05
2016 | 2015-12-10 | B | 2 | 0.0013425 | 6.0475e-06
2016 | 2015-11-19 | C | 10 | 0.0043638 | 3.0238e-05
2016 | 2015-12-07 | B | 2 | 0.00034471 | 6.0475e-06
2016 | 2015-12-02 | B | 15 | 0.01647 | 4.5356e-05
2016 | 2015-11-19 | C | 21 | 0.0056472 | 6.3499e-05
2016 | 2015-12-12 | B | 21 | 0.026703 | 6.3499e-05
2016 | 2015-11-19 | C | 1 | 0.00047246 | 3.0238e-06
2016 | 2015-11-24 | C | 31 | 0.0043681 | 9.3737e-05
2016 | 2015-12-14 | B | 25 | 0.029406 | 7.5594e-05
2016 | 2015-11-19 | C | 93 | 0.022478 | 0.00028121
2016 | 2015-11-20 | C | 676 | 0.20539 | 0.0020441
2016 | 2015-12-08 | B | 35 | 0.045719 | 0.00010583
2016 | 2015-11-20 | C | 30 | 0.011339 | 9.0713e-05
2016 | 2015-12-09 | B | 39 | 0.057312 | 0.00011793
2016 | 2015-12-15 | B | 4 | 0.000254 | 1.2095e-05
2016 | 2015-12-15 | B | 47 | 0.060258 | 0.00014212
2016 | 2015-11-24 | B | 93 | 0.012799 | 0.00028121
2016 | 2015-12-15 | B | 3 | 0.0029045 | 9.0713e-06
2016 | 2015-12-15 | B | 30 | 0.022064 | 9.0713e-05
2016 | 2015-12-15 | B | 47 | 0.046636 | 0.00014212
2016 | 2015-12-15 | B | 24 | 0.026706 | 7.257e-05
2016 | 2015-12-08 | B | 71 | 0.0037928 | 0.00021469
2016 | 2015-11-26 | B | 2 | 0.0012458 | 6.0475e-06
2016 | 2015-11-20 | C | 7 | 0.0024158 | 2.1166e-05
2016 | 2015-12-07 | B | 39 | 0.017766 | 0.00011793
2016 | 2015-11-24 | B | 34 | 0.0032522 | 0.00010281
2016 | 2015-11-24 | B | 48 | 0.014333 | 0.00014514
2016 | 2015-11-20 | C | 279 | 0.068964 | 0.00084363
2016 | 2015-11-20 | C | 74 | 0.019467 | 0.00022376
2016 | 2015-11-20 | C | 6 | 0.00075231 | 1.8143e-05
2016 | 2015-11-20 | C | 649 | 0.07727 | 0.0019624
2016 | 2015-11-20 | C | 1 | 0.00031951 | 3.0238e-06
2016 | 2015-11-20 | C | 904 | 0.0068746 | 0.0027335
2016 | 2015-11-21 | C | 5 | 0.0010739 | 1.5119e-05
2016 | 2015-11-21 | C | 22 | 0.0045901 | 6.6523e-05
2016 | 2015-11-21 | C | 2 | 0.00063741 | 6.0475e-06
2016 | 2015-11-21 | C | 6 | 0.00038704 | 1.8143e-05
2016 | 2015-11-21 | C | 403 | 0.040285 | 0.0012186
2016 | 2015-11-22 | C | 758 | 0 | 0.002292
2016 | 2015-11-22 | C | 4 | 0.0026492 | 1.2095e-05
2016 | 2015-11-22 | C | 279 | 0.010798 | 0.00084363
2016 | 2015-11-22 | C | 1 | 0.00079011 | 3.0238e-06
2016 | 2015-11-22 | C | 3 | 0.0013929 | 9.0713e-06
2016 | 2015-11-22 | C | 2 | 0.0015301 | 6.0475e-06
2016 | 2015-11-22 | C | 8 | 0.013769 | 2.419e-05
2016 | 2015-11-22 | C | 1 | 0.0007439 | 3.0238e-06
2016 | 2015-11-22 | C | 841 | 0.0086981 | 0.002543
2016 | 2015-11-22 | C | 6 | 0.0046877 | 1.8143e-05
2016 | 2015-11-22 | C | 1 | 0.0002418 | 3.0238e-06
2016 | 2015-11-22 | C | 2 | 0.011719 | 6.0475e-06
2016 | 2015-11-22 | C | 1 | 0.00077398 | 3.0238e-06
2016 | 2015-11-22 | C | 1 | 0.00087785 | 3.0238e-06
2016 | 2015-11-22 | C | 1 | 0.00033821 | 3.0238e-06
2016 | 2015-11-22 | C | 1 | 0.00034123 | 3.0238e-06
2016 | 2015-11-22 | C | 8 | 0.0084794 | 2.419e-05
2016 | 2015-11-22 | C | 1 | 0.00053647 | 3.0238e-06
2016 | 2015-11-22 | C | 2 | 0.0019634 | 6.0475e-06
2016 | 2015-11-22 | C | 1 | 0.0015198 | 3.0238e-06
2016 | 2015-11-22 | C | 1 | 0.0007004 | 3.0238e-06
2016 | 2015-11-22 | C | 1 | 0.00026211 | 3.0238e-06
2016 | 2015-11-22 | C | 163 | 0.0088635 | 0.00049287
2016 | 2015-11-22 | C | 4 | 0.0093092 | 1.2095e-05
2016 | 2015-11-22 | C | 4 | 0.0083893 | 1.2095e-05
2016 | 2015-11-22 | C | 1 | 0.0014927 | 3.0238e-06
2016 | 2015-11-22 | C | 4 | 0.0071522 | 1.2095e-05
2016 | 2015-11-22 | C | 1 | 0.0011111 | 3.0238e-06
2016 | 2015-11-22 | C | 3 | 0.0012443 | 9.0713e-06
2016 | 2015-11-22 | C | 649 | 0.057727 | 0.0019624
2016 | 2015-11-22 | C | 7 | 0.01092 | 2.1166e-05
2016 | 2015-11-22 | C | 2 | 0.0029247 | 6.0475e-06
2016 | 2015-11-22 | C | 1 | 0.00021726 | 3.0238e-06
2016 | 2015-11-22 | C | 1 | 5.8459e-05 | 3.0238e-06
2016 | 2015-11-22 | C | 1 | 0.00044414 | 3.0238e-06
2016 | 2015-11-22 | C | 1 | 0.00040433 | 3.0238e-06
2016 | 2015-11-22 | C | 1 | 0.00032309 | 3.0238e-06
2016 | 2015-11-22 | C | 2 | 0.0016929 | 6.0475e-06
2016 | 2015-11-22 | C | 1 | 0.00047997 | 3.0238e-06
2016 | 2015-11-22 | C | 17 | 0.0040703 | 5.1404e-05
2016 | 2015-11-22 | C | 1 | 0.00015073 | 3.0238e-06
2016 | 2015-11-22 | C | 90 | 0.051188 | 0.00027214
2016 | 2015-11-22 | C | 30 | 0.013432 | 9.0713e-05
2016 | 2015-11-22 | C | 904 | 0.084773 | 0.0027335
2016 | 2015-11-22 | C | 5 | 0.0032196 | 1.5119e-05
2016 | 2015-11-22 | C | 317 | 0.10963 | 0.00095853
2016 | 2015-11-22 | C | 2 | 0.00079434 | 6.0475e-06
2016 | 2015-11-23 | C | 36 | 0.0046808 | 0.00010886
2016 | 2015-11-23 | C | 2 | 0.00089282 | 6.0475e-06
2016 | 2015-11-23 | C | 1 | 0.00013264 | 3.0238e-06
2016 | 2015-11-23 | C | 78 | 0.068468 | 0.00023585
2016 | 2015-12-16 | B | 3 | 0.0036873 | 9.0713e-06
2016 | 2015-12-08 | B | 8 | 0.0053702 | 2.419e-05
2016 | 2015-11-23 | C | 10 | 0.0069849 | 3.0238e-05
2016 | 2015-11-23 | C | 1 | 0.00042373 | 3.0238e-06
2016 | 2015-11-23 | C | 9 | 0.0010886 | 2.7214e-05
2016 | 2015-11-23 | C | 4 | 0.00085109 | 1.2095e-05
2016 | 2015-11-23 | C | 2 | 0.00052966 | 6.0475e-06
2016 | 2015-11-24 | C | 113 | 0.17291 | 0.00034168
2016 | 2015-11-22 | C | 21 | 0.0060631 | 6.3499e-05
2016 | 2015-12-11 | B | 7 | 0.00057149 | 2.1166e-05
2016 | 2015-12-11 | B | 4 | 0.00081037 | 1.2095e-05
2016 | 2015-12-11 | B | 4 | 0.00026609 | 1.2095e-05
2016 | 2015-12-09 | B | 17 | 0.00082246 | 5.1404e-05
2016 | 2015-12-14 | B | 3 | 0.00033564 | 9.0713e-06
2016 | 2015-12-14 | B | 9 | 0.00073477 | 2.7214e-05
2016 | 2015-12-14 | B | 4 | 0.00087084 | 1.2095e-05
2016 | 2015-12-15 | B | 33 | 0.035623 | 9.9784e-05
2016 | 2015-12-09 | B | 204 | 0.24921 | 0.00061685
2016 | 2015-12-09 | B | 4 | 0.0030451 | 1.2095e-05
2016 | 2015-12-11 | B | 204 | 0.19246 | 0.00061685
2016 | 2015-12-03 | B | 34 | 0.047086 | 0.00010281
2016 | 2015-11-24 | C | 4 | 0.0013909 | 1.2095e-05
2016 | 2015-12-15 | B | 4 | 0.0022376 | 1.2095e-05
2016 | 2015-12-15 | B | 12 | 0.00079827 | 3.6285e-05
2016 | 2015-12-15 | B | 3 | 0.00056529 | 9.0713e-06
2016 | 2015-11-22 | C | 1 | 0.00059744 | 3.0238e-06
2016 | 2015-12-15 | B | 4 | 0.00020562 | 1.2095e-05
2016 | 2015-12-16 | B | 51 | 0.066311 | 0.00015421
2016 | 2015-12-16 | B | 3 | 0.0019231 | 9.0713e-06
2016 | 2015-12-16 | B | 4 | 0.00068942 | 1.2095e-05
2016 | 2015-11-24 | C | 9 | 0.0010391 | 2.7214e-05
2016 | 2015-11-24 | C | 857 | 0.27965 | 0.0025914
2016 | 2015-11-25 | C | 10 | 0.0018697 | 3.0238e-05
2016 | 2015-12-16 | B | 17 | 0.010178 | 5.1404e-05
2016 | 2015-11-25 | C | 6 | 0.00022325 | 1.8143e-05
2016 | 2015-11-25 | C | 6 | 0.0026588 | 1.8143e-05
2016 | 2015-12-15 | B | 39 | 0.049042 | 0.00011793
2016 | 2015-12-14 | B | 1 | 0.0049832 | 3.0238e-06
2016 | 2015-11-25 | C | 1 | 0.00018878 | 3.0238e-06
2016 | 2015-11-25 | C | 1 | 0.00068287 | 3.0238e-06
2016 | 2015-12-13 | B | 1 | 0.0015408 | 3.0238e-06
2016 | 2015-12-14 | B | 1 | 0.0011883 | 3.0238e-06
2016 | 2015-12-17 | B | 28 | 0.031092 | 8.4665e-05
2016 | 2015-11-25 | C | 1 | 9.0713e-05 | 3.0238e-06
2016 | 2015-11-25 | C | 1 | 0.00047639 | 3.0238e-06
2016 | 2015-11-26 | C | 649 | 0.06142 | 0.0019624
2016 | 2015-11-26 | C | 689 | 0.20338 | 0.0020834
2016 | 2015-11-26 | C | 649 | 0.10893 | 0.0019624
2016 | 2015-11-26 | C | 6 | 0.0014596 | 1.8143e-05
2016 | 2015-11-26 | C | 25 | 0.01969 | 7.5594e-05
2016 | 2015-11-26 | C | 2 | 0.00037474 | 6.0475e-06
2016 | 2015-12-17 | B | 24 | 0.010305 | 7.257e-05
2016 | 2015-12-17 | B | 2 | 0.00040518 | 6.0475e-06
2016 | 2015-12-17 | B | 7 | 0.00067732 | 2.1166e-05
2016 | 2015-12-10 | B | 122 | 0.0033201 | 0.0003689
2016 | 2015-11-26 | C | 857 | 0.17807 | 0.0025914
2016 | 2015-11-26 | C | 833 | 0.11568 | 0.0025188
2016 | 2015-11-26 | C | 1 | 0.00020083 | 3.0238e-06
2016 | 2015-11-27 | C | 2 | 0.0013728 | 6.0475e-06
2016 | 2015-11-27 | C | 307 | 0.099711 | 0.00092829
2016 | 2015-11-27 | C | 4 | 0.00060475 | 1.2095e-05
2016 | 2015-11-27 | C | 1 | 0.00094341 | 3.0238e-06
2016 | 2015-11-27 | C | 1 | 0.00040544 | 3.0238e-06
2016 | 2015-11-27 | C | 35 | 0.019595 | 0.00010583
2016 | 2015-12-11 | B | 173 | 0.068474 | 0.00052311
2016 | 2015-12-03 | B | 61 | 0.048277 | 0.00018445
2016 | 2015-12-18 | B | 48 | 0.012192 | 0.00014514
2016 | 2015-12-18 | B | 8 | 0.0091491 | 2.419e-05
2016 | 2015-11-27 | C | 9 | 0.010454 | 2.7214e-05
2016 | 2015-12-14 | B | 2 | 0.00065918 | 6.0475e-06
2016 | 2015-12-14 | B | 5 | 0.0013909 | 1.5119e-05
2016 | 2015-11-27 | C | 3 | 0.00044449 | 9.0713e-06
2016 | 2015-11-30 | C | 1 | 0.00042937 | 3.0238e-06
2016 | 2015-11-27 | C | 1832 | 0 | 0.0055395
2016 | 2015-11-27 | C | 181 | 0.009358 | 0.0005473
2016 | 2015-11-27 | C | 273 | 0.087419 | 0.00082549
2016 | 2015-11-28 | C | 59 | 0.017778 | 0.0001784
2016 | 2015-11-28 | C | 27 | 0.00547 | 8.1642e-05
2016 | 2015-12-21 | B | 22 | 0.0069683 | 6.6523e-05
2016 | 2015-11-28 | C | 603 | 0.11305 | 0.0018233
2016 | 2015-11-28 | C | 444 | 0.043814 | 0.0013425
2016 | 2015-11-29 | C | 87 | 0.0034506 | 0.00026307
2016 | 2015-11-29 | C | 46 | 0.038167 | 0.00013909
2016 | 2015-11-29 | C | 65 | 0.0030432 | 0.00019654
2016 | 2015-11-30 | C | 69 | 0.0107 | 0.00020864
2016 | 2015-12-02 | B | 10 | 0.0086782 | 3.0238e-05
2016 | 2015-12-16 | B | 4 | 0.0039067 | 1.2095e-05
2016 | 2015-11-30 | C | 2 | 0.0012518 | 6.0475e-06
2016 | 2015-11-30 | C | 416 | 0.023039 | 0.0012579
2016 | 2015-11-30 | C | 1100 | 0.19524 | 0.0033261
2016 | 2015-12-01 | C | 396 | 0.08825 | 0.0011974
2016 | 2015-12-01 | C | 1 | 0.00025505 | 3.0238e-06
2016 | 2015-12-16 | B | 91 | 0.099414 | 0.00027516
2016 | 2015-12-17 | B | 38 | 0.05314 | 0.0001149
2016 | 2015-12-01 | C | 167 | 0.049151 | 0.00050497
2016 | 2015-12-15 | B | 62 | 0.036745 | 0.00018747
2016 | 2015-12-03 | B | 3 | 0.0013335 | 9.0713e-06
2016 | 2015-12-01 | C | 1 | 0.00018747 | 3.0238e-06
2016 | 2015-12-09 | B | 10 | 0.0044752 | 3.0238e-05
2016 | 2015-12-01 | C | 57 | 0.0022406 | 0.00017235
2016 | 2015-12-02 | C | 19 | 0.0047053 | 5.7451e-05
2016 | 2015-12-02 | C | 1 | 0.00042736 | 3.0238e-06
2016 | 2015-12-02 | C | 76 | 0.022399 | 0.00022981
2016 | 2015-12-21 | B | 10 | 0.010007 | 3.0238e-05
2016 | 2015-12-18 | B | 36 | 0.044386 | 0.00010886
2016 | 2015-12-18 | B | 2 | 0.0010886 | 6.0475e-06
2016 | 2015-12-21 | B | 5 | 0.0011339 | 1.5119e-05
2016 | 2015-12-21 | B | 5 | 0.0013909 | 1.5119e-05
2016 | 2015-12-03 | B | 9 | 0.0072117 | 2.7214e-05
2016 | 2015-12-21 | B | 82 | 0.11843 | 0.00024795
2016 | 2015-12-06 | B | 1 | 0.0018249 | 3.0238e-06
2016 | 2015-12-03 | C | 1643 | 0.013182 | 0.004968
2016 | 2015-12-22 | B | 67 | 0.08598 | 0.00020259
2016 | 2015-12-10 | B | 1 | 0.00039309 | 3.0238e-06
2016 | 2015-12-03 | C | 15 | 0.0066674 | 4.5356e-05
2016 | 2015-12-22 | B | 10 | 0.0021227 | 3.0238e-05
2016 | 2015-12-22 | B | 91 | 0.070166 | 0.00027516
2016 | 2015-12-18 | B | 19 | 0.024813 | 5.7451e-05
2016 | 2015-12-22 | B | 19 | 0.028239 | 5.7451e-05
2016 | 2015-12-03 | C | 1 | 0.00020839 | 3.0238e-06
2016 | 2015-12-04 | C | 1 | 0.00028454 | 3.0238e-06
2016 | 2015-12-11 | B | 58 | 0.053841 | 0.00017538
2016 | 2015-12-17 | B | 13 | 0.010142 | 3.9309e-05
2016 | 2015-12-04 | C | 167 | 0.049855 | 0.00050497
2016 | 2015-12-05 | C | 422 | 0.019413 | 0.001276
2016 | 2015-12-05 | C | 116 | 0.016809 | 0.00035076
2016 | 2015-12-05 | C | 15 | 0.0014499 | 4.5356e-05
2016 | 2015-12-05 | C | 465 | 0.080369 | 0.001406
2016 | 2015-12-05 | C | 12 | 0.0018505 | 3.6285e-05
2016 | 2015-12-05 | C | 28 | 0.0037239 | 8.4665e-05
2016 | 2015-12-06 | C | 132 | 0.067438 | 0.00039914
2016 | 2015-12-06 | C | 56 | 0.0082372 | 0.00016933
2016 | 2015-12-06 | C | 132 | 0.025824 | 0.00039914
2016 | 2015-12-06 | C | 25 | 0.0058535 | 7.5594e-05
2016 | 2015-12-06 | C | 12 | 0.0052329 | 3.6285e-05
2016 | 2015-12-07 | C | 1 | 0.00022703 | 3.0238e-06
2016 | 2015-12-21 | B | 4 | 0.00038704 | 1.2095e-05
2016 | 2015-12-21 | B | 429 | 0.18833 | 0.0012972
2016 | 2015-12-07 | C | 435 | 0.094492 | 0.0013153
2016 | 2015-12-07 | C | 759 | 0.40035 | 0.002295
2016 | 2015-12-07 | C | 15 | 0.0036965 | 4.5356e-05
2016 | 2015-12-07 | C | 511 | 0.076107 | 0.0015451
2016 | 2015-12-07 | C | 22 | 0.0053773 | 6.6523e-05
2016 | 2015-12-07 | C | 28 | 0.0057982 | 8.4665e-05
2016 | 2015-12-08 | C | 1 | 0.00010886 | 3.0238e-06
2016 | 2015-12-22 | B | 1 | 0.00035378 | 3.0238e-06
2016 | 2015-12-08 | C | 284 | 0.08625 | 0.00085875
2016 | 2015-12-09 | C | 6 | 0.0021638 | 1.8143e-05
2016 | 2015-12-16 | B | 40 | 0.034457 | 0.00012095
2016 | 2015-12-22 | B | 17 | 0.016364 | 5.1404e-05
2016 | 2015-12-09 | C | 1240 | 0.31495 | 0.0037495
2016 | 2015-12-09 | C | 1 | 0.00028071 | 3.0238e-06
2016 | 2015-12-10 | C | 6 | 0.0014804 | 1.8143e-05
2016 | 2015-12-10 | B | 592 | 0.0053702 | 0.0017901
2016 | 2015-12-17 | B | 39 | 0.038798 | 0.00011793
2016 | 2015-12-10 | C | 666 | 0.17511 | 0.0020138
2016 | 2016-01-22 | B | 4 | 0.0021287 | 1.2095e-05
2016 | 2016-01-27 | B | 18 | 0.019431 | 5.4428e-05
2016 | 2015-12-10 | C | 15 | 0.0070476 | 4.5356e-05
2016 | 2016-01-28 | B | 9 | 0.011212 | 2.7214e-05
2016 | 2015-12-10 | C | 5 | 0.00095248 | 1.5119e-05
2016 | 2015-12-10 | C | 22 | 0.0083796 | 6.6523e-05
2016 | 2015-12-10 | C | 5167 | 0.1414 | 0.015624
2016 | 2015-12-11 | C | 34 | 0.05047 | 0.00010281
2016 | 2015-12-11 | C | 2 | 0.0020087 | 6.0475e-06
2016 | 2016-01-29 | B | 18 | 0.016083 | 5.4428e-05
2016 | 2016-02-02 | B | 30 | 0.028776 | 9.0713e-05
2016 | 2016-02-04 | B | 48 | 0.050973 | 0.00014514
2016 | 2015-12-11 | C | 52 | 0.010063 | 0.00015724
2016 | 2015-12-11 | C | 4 | 0.00074485 | 1.2095e-05
2016 | 2015-12-11 | C | 93 | 0.036681 | 0.00028121
2016 | 2015-12-11 | C | 2 | 0.00037878 | 6.0475e-06
2016 | 2016-01-11 | B | 3 | 0.0012428 | 9.0713e-06
2016 | 2016-01-07 | B | 24 | 0.00036285 | 7.257e-05
2016 | 2016-01-11 | B | 2 | 0.00058661 | 6.0475e-06
2016 | 2016-01-11 | B | 6 | 0.0023948 | 1.8143e-05
2016 | 2016-01-12 | B | 21 | 0.023304 | 6.3499e-05
2016 | 2016-01-12 | B | 32 | 0.012369 | 9.676e-05
2016 | 2016-01-12 | B | 340 | 0.19739 | 0.0010281
2016 | 2016-01-13 | B | 508 | 0.21044 | 0.0015361
2016 | 2015-12-11 | C | 302 | 0.1714 | 0.00091318
2016 | 2016-01-07 | B | 77 | 0.091603 | 0.00023283
2016 | 2015-12-12 | C | 240 | 0.0082125 | 0.0007257
2016 | 2015-12-12 | C | 5 | 0.0019785 | 1.5119e-05
2016 | 2015-12-12 | C | 240 | 0.048012 | 0.0007257
2016 | 2015-12-12 | C | 110 | 0.019957 | 0.00033261
2016 | 2015-12-12 | C | 110 | 0.017108 | 0.00033261
2016 | 2015-12-12 | C | 240 | 0.088855 | 0.0007257
2016 | 2015-12-12 | C | 116 | 0.066486 | 0.00035076
2016 | 2015-12-13 | C | 51 | 0.011874 | 0.00015421
2016 | 2015-12-13 | C | 236 | 0.09296 | 0.00071361
2016 | 2015-12-13 | C | 2 | 0.00039077 | 6.0475e-06
2016 | 2015-12-13 | C | 31 | 0.0033612 | 9.3737e-05
2016 | 2015-12-13 | C | 719 | 0.83335 | 0.0021741
2016 | 2015-12-13 | C | 2 | 0.00027456 | 6.0475e-06
2016 | 2015-12-13 | C | 20 | 0.004959 | 6.0475e-05
2016 | 2015-12-13 | C | 717 | 0.1854 | 0.002168
2016 | 2015-12-13 | C | 353 | 0.081836 | 0.0010674
2016 | 2015-12-13 | C | 346 | 0.050046 | 0.0010462
2016 | 2015-12-13 | C | 15 | 0.0067642 | 4.5356e-05
2016 | 2015-12-13 | C | 8 | 0.00060475 | 2.419e-05
2016 | 2015-12-13 | C | 229 | 0.076883 | 0.00069244
2016 | 2015-12-13 | C | 1 | 0.00073624 | 3.0238e-06
2016 | 2015-12-14 | C | 4 | 0.0013788 | 1.2095e-05
2016 | 2015-12-13 | C | 132 | 0.039295 | 0.00039914
2016 | 2015-12-13 | C | 54 | 0.013389 | 0.00016328
2016 | 2015-12-14 | C | 32 | 0.00067732 | 9.676e-05
2016 | 2015-12-18 | B | 185 | 0.083275 | 0.0005594
2016 | 2016-01-12 | B | 118 | 0.092412 | 0.0003568
2016 | 2016-01-13 | B | 3 | 0.0037192 | 9.0713e-06
2016 | 2016-01-18 | B | 19 | 0.022808 | 5.7451e-05
2016 | 2015-12-15 | B | 126 | 0.0055762 | 0.00038099
2016 | 2016-01-19 | B | 8 | 0.0097728 | 2.419e-05
2016 | 2016-01-12 | B | 47 | 0.058836 | 0.00014212
2016 | 2015-12-14 | C | 2 | 0.0002419 | 6.0475e-06
2016 | 2016-01-13 | B | 26 | 0.031211 | 7.8618e-05
2016 | 2016-01-12 | B | 64 | 0.014127 | 0.00019352
2016 | 2016-01-13 | B | 66 | 0.069972 | 0.00019957
2016 | 2015-12-14 | C | 87 | 0.0041214 | 0.00026307
2016 | 2016-01-20 | B | 67 | 0.078167 | 0.00020259
2016 | 2015-12-14 | C | 2 | 0.0016687 | 6.0475e-06
2016 | 2016-01-10 | B | 2 | 0.0016147 | 6.0475e-06
2016 | 2016-01-13 | B | 45 | 0.039188 | 0.00013607
2016 | 2016-01-12 | B | 232 | 0.039986 | 0.00070151
2016 | 2016-01-13 | B | 90 | 0.013335 | 0.00027214
2016 | 2016-01-13 | B | 32 | 0.030189 | 9.676e-05
2016 | 2016-01-13 | B | 28 | 0.0095023 | 8.4665e-05
2016 | 2016-01-14 | B | 27 | 0.028983 | 8.1642e-05
2016 | 2016-01-14 | B | 19 | 0.024168 | 5.7451e-05
2016 | 2016-01-14 | B | 2 | 0.0010281 | 6.0475e-06
2016 | 2016-01-15 | B | 2 | 0.0024855 | 6.0475e-06
2016 | 2016-01-27 | B | 47 | 0.057131 | 0.00014212
2016 | 2016-01-14 | B | 2 | 0.0018264 | 6.0475e-06
2016 | 2016-01-14 | B | 2 | 0.0004959 | 6.0475e-06
2016 | 2016-01-14 | B | 106 | 0.052784 | 0.00032052
2016 | 2016-01-14 | B | 12 | 0.01306 | 3.6285e-05
2016 | 2015-12-15 | C | 36 | 0.028738 | 0.00010886
2016 | 2016-01-15 | B | 2 | 0.0004838 | 6.0475e-06
2016 | 2016-01-17 | B | 32 | 0.012482 | 9.676e-05
2016 | 2015-12-22 | B | 6 | 0.0013788 | 1.8143e-05
2016 | 2015-12-18 | B | 7 | 0.0034289 | 2.1166e-05
2016 | 2016-01-18 | B | 9 | 0.0047352 | 2.7214e-05
2016 | 2016-01-15 | B | 8 | 0.0080081 | 2.419e-05
2016 | 2016-01-16 | B | 6 | 0.0035327 | 1.8143e-05
2016 | 2016-01-16 | B | 9 | 0.0093616 | 2.7214e-05
2016 | 2015-12-16 | B | 47 | 0.060755 | 0.00014212
2016 | 2016-01-16 | B | 1 | 7.257e-05 | 3.0238e-06
2016 | 2016-01-15 | B | 167 | 0.077487 | 0.00050497
2016 | 2016-01-18 | B | 18 | 0.015349 | 5.4428e-05
2016 | 2016-01-19 | B | 27 | 0.027023 | 8.1642e-05
2016 | 2016-01-16 | B | 2 | 0.0010402 | 6.0475e-06
2016 | 2016-01-13 | B | 57 | 0.03292 | 0.00017235
2016 | 2016-01-14 | B | 2 | 0.0021106 | 6.0475e-06
2016 | 2016-01-20 | B | 71 | 0.031774 | 0.00021469
2016 | 2016-01-20 | B | 5 | 0.0040367 | 1.5119e-05
2016 | 2016-01-22 | B | 53 | 0.0521 | 0.00016026
2016 | 2016-01-19 | B | 9 | 0.0047611 | 2.7214e-05
2016 | 2016-01-15 | B | 1 | 0.00048683 | 3.0238e-06
2016 | 2016-01-20 | B | 31 | 0.036276 | 9.3737e-05
2016 | 2016-01-20 | B | 184 | 0.2268 | 0.00055637
2016 | 2015-12-15 | C | 21 | 0.0015875 | 6.3499e-05
2016 | 2016-01-21 | B | 48 | 0.049969 | 0.00014514
2016 | 2015-12-15 | C | 61 | 0.012358 | 0.00018445
2016 | 2015-12-15 | C | 61 | 0.051461 | 0.00018445
2016 | 2015-12-16 | C | 4 | 0.00054186 | 1.2095e-05
2016 | 2016-01-13 | B | 168 | 0.1092 | 0.00050799
2016 | 2016-01-21 | B | 4 | 0.0028665 | 1.2095e-05
2016 | 2016-01-20 | B | 27 | 0.029833 | 8.1642e-05
2016 | 2016-01-21 | B | 51 | 0.061222 | 0.00015421
2016 | 2016-01-21 | B | 5 | 0.0044903 | 1.5119e-05
2016 | 2016-01-19 | B | 2 | 0.00068942 | 6.0475e-06
2016 | 2016-01-20 | B | 1 | 0.0006365 | 3.0238e-06
2016 | 2016-01-25 | B | 5 | 0.0025853 | 1.5119e-05
2016 | 2016-01-20 | B | 285 | 0.17839 | 0.00086177
2016 | 2016-01-25 | B | 10 | 0.00021166 | 3.0238e-05
2016 | 2016-01-19 | B | 5 | 0.0051706 | 1.5119e-05
2016 | 2016-01-21 | B | 3 | 0.0014307 | 9.0713e-06
2016 | 2015-12-16 | C | 3652 | 0 | 0.011043
2016 | 2016-01-21 | B | 42 | 0.026289 | 0.000127
2016 | 2016-01-28 | B | 5 | 0.0019806 | 1.5119e-05
2016 | 2016-01-28 | B | 27 | 0.02188 | 8.1642e-05
2016 | 2016-01-21 | B | 34 | 0.041188 | 0.00010281
2016 | 2016-01-27 | B | 4 | 0.00010886 | 1.2095e-05
2016 | 2016-01-27 | B | 57 | 0.060542 | 0.00017235
2016 | 2016-01-21 | B | 151 | 0.18355 | 0.00045659
2016 | 2016-01-26 | B | 5 | 0.00051404 | 1.5119e-05
2016 | 2016-01-20 | B | 28 | 0.010647 | 8.4665e-05
2016 | 2015-12-17 | C | 204 | 0.065815 | 0.00061685
2016 | 2015-12-17 | C | 258 | 0.11536 | 0.00078013
2016 | 2015-12-17 | C | 37 | 0.057344 | 0.00011188
2016 | 2015-12-17 | C | 92 | 0.015388 | 0.00027819
2016 | 2015-12-17 | C | 476 | 0.29609 | 0.0014393
2016 | 2015-12-17 | C | 75 | 0.0082889 | 0.00022678
2016 | 2015-12-17 | C | 1 | 0.0050222 | 3.0238e-06
2016 | 2016-01-20 | B | 7 | 0.0074082 | 2.1166e-05
2016 | 2016-01-22 | B | 3 | 0.0020592 | 9.0713e-06
2016 | 2015-12-20 | C | 1 | 1.8143e-05 | 3.0238e-06
2016 | 2016-01-29 | B | 47 | 0.058694 | 0.00014212
2016 | 2016-01-21 | B | 9 | 0.0095793 | 2.7214e-05
2016 | 2016-01-13 | B | 40 | 0.01911 | 0.00012095
2016 | 2016-01-25 | B | 7 | 0.0031114 | 2.1166e-05
2016 | 2015-12-18 | C | 59 | 0.0024976 | 0.0001784
2016 | 2015-12-18 | C | 1 | 0.0003884 | 3.0238e-06
2016 | 2015-12-18 | C | 43 | 0.0077601 | 0.00013002
2016 | 2016-01-22 | B | 1 | 0.00062592 | 3.0238e-06
2016 | 2016-01-16 | B | 56 | 0.050291 | 0.00016933
2016 | 2015-12-18 | C | 1 | 0.00050577 | 3.0238e-06
2016 | 2016-01-26 | B | 19 | 0.02408 | 5.7451e-05
2016 | 2016-01-26 | B | 82 | 0.087054 | 0.00024795
2016 | 2015-12-18 | C | 1916 | 0.16638 | 0.0057935
2016 | 2015-12-18 | C | 3 | 0.00061654 | 9.0713e-06
2016 | 2015-12-18 | C | 1 | 0.00019891 | 3.0238e-06
2016 | 2015-12-18 | C | 15 | 0.00254 | 4.5356e-05
2016 | 2015-12-18 | C | 1 | 0.00058852 | 3.0238e-06
2016 | 2015-12-18 | C | 1 | 0.00033796 | 3.0238e-06
2016 | 2015-12-19 | C | 3 | 0.0012337 | 9.0713e-06
2016 | 2015-12-19 | C | 1114 | 0.67451 | 0.0033685
2016 | 2015-12-19 | C | 25 | 0.0070781 | 7.5594e-05
2016 | 2015-12-19 | C | 9 | 0.0017893 | 2.7214e-05
2016 | 2015-12-19 | C | 464 | 0.084686 | 0.001403
2016 | 2015-12-19 | C | 2 | 0.00033745 | 6.0475e-06
2016 | 2015-12-19 | C | 1 | 0.00021756 | 3.0238e-06
2016 | 2015-12-20 | C | 1 | 0.00039914 | 3.0238e-06
2016 | 2015-12-21 | C | 16 | 0.0039478 | 4.838e-05
2016 | 2015-12-21 | C | 138 | 0.0037555 | 0.00041728
2016 | 2016-01-27 | B | 21 | 0.020791 | 6.3499e-05
2016 | 2016-01-22 | B | 1 | 0.001019 | 3.0238e-06
2016 | 2015-12-21 | C | 41 | 0.04008 | 0.00012397
2016 | 2016-01-28 | B | 19 | 0.0081591 | 5.7451e-05
2016 | 2016-01-28 | B | 19 | 0.020293 | 5.7451e-05
2016 | 2016-01-28 | B | 7 | 0.0053043 | 2.1166e-05
2016 | 2016-01-29 | B | 7 | 0.0035919 | 2.1166e-05
2016 | 2015-12-21 | C | 108 | 0.0079954 | 0.00032657
2016 | 2015-12-21 | C | 16 | 0.004043 | 4.838e-05
2016 | 2015-12-21 | C | 1 | 3.0238e-06 | 3.0238e-06
2016 | 2015-12-21 | C | 1 | 9.0713e-06 | 3.0238e-06
2016 | 2015-12-21 | C | 1089 | 0.06069 | 0.0032929
2016 | 2015-12-22 | C | 5 | 0.00051404 | 1.5119e-05
2016 | 2016-01-25 | B | 100 | 0.0099784 | 0.00030238
2016 | 2016-01-27 | B | 98 | 0.077638 | 0.00029633
2016 | 2015-12-22 | C | 7 | 0.0052023 | 2.1166e-05
2016 | 2016-01-28 | B | 44 | 0.041776 | 0.00013305
2016 | 2016-01-26 | B | 3 | 0.0011521 | 9.0713e-06
2016 | 2016-01-27 | B | 3 | 0.0010432 | 9.0713e-06
2016 | 2016-01-28 | B | 5 | 0.0025248 | 1.5119e-05
2016 | 2015-12-22 | C | 10 | 0.00045356 | 3.0238e-05
2016 | 2015-12-22 | C | 609 | 0.10712 | 0.0018415
2016 | 2015-12-22 | C | 574 | 0.11956 | 0.0017356
2016 | 2015-12-23 | C | 327 | 0 | 0.00098877
2016 | 2016-01-22 | B | 42 | 0.019295 | 0.000127
2016 | 2015-12-23 | C | 33 | 0.0033777 | 9.9784e-05
2016 | 2015-12-23 | C | 4 | 0.00061775 | 1.2095e-05
2016 | 2015-12-23 | C | 1431 | 0.088811 | 0.004327
2016 | 2015-12-23 | C | 54 | 0.019327 | 0.00016328
2016 | 2015-12-24 | C | 836 | 0.24409 | 0.0025279
2016 | 2015-12-24 | C | 206 | 0.067273 | 0.00062289
2016 | 2015-12-24 | C | 1 | 1.5119e-05 | 3.0238e-06
2016 | 2015-12-25 | C | 903 | 0.06545 | 0.0027305
2016 | 2015-12-25 | C | 215 | 0.010053 | 0.00065011
2016 | 2015-12-25 | C | 684 | 0.096863 | 0.0020683
2016 | 2015-12-25 | C | 1 | 0.00015189 | 3.0238e-06
2016 | 2015-12-25 | C | 1331 | 0.082182 | 0.0040246
2016 | 2015-12-25 | C | 297 | 0.1084 | 0.00089806
2016 | 2015-12-26 | C | 2337 | 0.14872 | 0.0070665
2016 | 2015-12-26 | C | 999 | 0.02355 | 0.0030207
2016 | 2015-12-26 | C | 1 | 0.00027179 | 3.0238e-06
2016 | 2015-12-26 | C | 26 | 0.0036963 | 7.8618e-05
2016 | 2015-12-26 | C | 1 | 0.00010271 | 3.0238e-06
2016 | 2015-12-27 | C | 20 | 0.0046566 | 6.0475e-05
2016 | 2015-12-27 | C | 540 | 0.065667 | 0.0016328
2016 | 2015-12-27 | C | 13 | 0.0022878 | 3.9309e-05
2016 | 2015-12-27 | C | 416 | 0.0067625 | 0.0012579
2016 | 2015-12-28 | C | 348 | 0.032435 | 0.0010523
2016 | 2015-12-28 | C | 1 | 0.00011616 | 3.0238e-06
2016 | 2015-12-28 | C | 566 | 0.14883 | 0.0017114
2016 | 2015-12-29 | C | 1 | 0.00034521 | 3.0238e-06
2016 | 2015-12-29 | C | 2 | 0.00056494 | 6.0475e-06
2016 | 2015-12-25 | C | 1 | 0.047023 | 3.0238e-06
2016 | 2015-12-29 | C | 3 | 0.0019893 | 9.0713e-06
2016 | 2015-12-29 | C | 1 | 0.00020088 | 3.0238e-06
2016 | 2015-12-29 | C | 1527 | 0.36288 | 0.0046173
2016 | 2015-12-29 | C | 1 | 0.001077 | 3.0238e-06
2016 | 2015-12-29 | C | 200 | 0.022457 | 0.00060475
2016 | 2015-12-29 | C | 433 | 0 | 0.0013093
2016 | 2015-12-29 | C | 692 | 0.25263 | 0.0020924
2016 | 2015-12-29 | C | 7 | 0.0036861 | 2.1166e-05
2016 | 2015-12-29 | C | 391 | 0.84037 | 0.0011823
2016 | 2015-12-30 | C | 80 | 0.10376 | 0.0002419
2016 | 2015-12-30 | C | 31 | 0.0099251 | 9.3737e-05
2016 | 2015-12-30 | C | 37 | 0.0092226 | 0.00011188
2016 | 2015-12-30 | C | 131 | 0.31138 | 0.00039611
2016 | 2015-12-30 | C | 1 | 0.00015204 | 3.0238e-06
2016 | 2015-12-30 | C | 38 | 0.0031388 | 0.0001149
2016 | 2015-12-30 | C | 1715 | 0.21464 | 0.0051857
2016 | 2015-12-30 | C | 5 | 0.00037797 | 1.5119e-05
2016 | 2015-12-30 | C | 100 | 0.0031749 | 0.00030238
2016 | 2015-12-30 | C | 3 | 0.00020486 | 9.0713e-06
2016 | 2015-12-30 | C | 1 | 0.0027123 | 3.0238e-06
2016 | 2015-12-30 | C | 4 | 0.0011821 | 1.2095e-05
2016 | 2015-12-31 | C | 3 | 0.0012428 | 9.0713e-06
2016 | 2015-12-31 | C | 10183 | 0.94944 | 0.030791
2016 | 2015-12-31 | C | 15 | 0.0052634 | 4.5356e-05
2016 | 2015-12-31 | C | 1 | 0.0003755 | 3.0238e-06
2016 | 2015-12-31 | C | 118 | 0.055333 | 0.0003568
2016 | 2015-12-31 | C | 48 | 0.0085633 | 0.00014514
2016 | 2015-12-31 | C | 177 | 0.0033177 | 0.00053521
2016 | 2016-01-01 | C | 46 | 0.025119 | 0.00013909
2016 | 2016-01-01 | C | 41 | 0.028082 | 0.00012397
2016 | 2016-01-01 | C | 5688 | 3.6164 | 0.017199
2016 | 2016-01-01 | C | 39 | 0.0094493 | 0.00011793
2016 | 2016-01-01 | C | 5 | 0.00084313 | 1.5119e-05
2016 | 2016-01-01 | C | 769 | 0 | 0.0023253
2016 | 2016-01-01 | C | 4 | 0.0011668 | 1.2095e-05
2016 | 2016-01-01 | C | 5 | 0.0088155 | 1.5119e-05
2016 | 2016-01-01 | C | 6 | 0.0023715 | 1.8143e-05
2016 | 2016-01-02 | C | 138 | 0.03559 | 0.00041728
2016 | 2016-01-02 | C | 1519 | 0 | 0.0045931
2016 | 2016-01-02 | C | 903 | 0.014613 | 0.0027305
2016 | 2016-01-02 | C | 1 | 0.00049025 | 3.0238e-06
2016 | 2016-01-02 | C | 540 | 0.16781 | 0.0016328
2016 | 2016-01-02 | C | 1 | 0.00013461 | 3.0238e-06
2016 | 2016-01-02 | C | 1 | 2.3737e-05 | 3.0238e-06
2016 | 2016-01-02 | C | 72 | 0.0061579 | 0.00021771
2016 | 2016-01-02 | C | 540 | 0.16488 | 0.0016328
2016 | 2016-01-02 | C | 777 | 0.33093 | 0.0023495
2016 | 2016-01-03 | C | 283 | 0.069857 | 0.00085572
2016 | 2016-01-03 | C | 57 | 0.021688 | 0.00017235
2016 | 2016-01-03 | C | 4 | 0.0008785 | 1.2095e-05
2016 | 2016-01-03 | C | 82 | 0.045335 | 0.00024795
2016 | 2016-01-03 | C | 260 | 0.077107 | 0.00078618
2016 | 2016-01-03 | C | 725 | 0.15067 | 0.0021922
2016 | 2016-01-03 | C | 903 | 0 | 0.0027305
2016 | 2016-01-03 | C | 241 | 0 | 0.00072873
2016 | 2016-01-03 | C | 2 | 0.00052684 | 6.0475e-06
2016 | 2016-01-03 | C | 397 | 0.056959 | 0.0012004
2016 | 2016-01-03 | C | 1 | 0.00055295 | 3.0238e-06
2016 | 2016-01-03 | C | 4 | 0.011072 | 1.2095e-05
2016 | 2016-01-04 | C | 92 | 0.022803 | 0.00027819
2016 | 2016-01-04 | C | 23 | 0.026741 | 6.9546e-05
2016 | 2016-01-04 | C | 35 | 0.012045 | 0.00010583
2016 | 2016-01-04 | C | 1 | 0.00019463 | 3.0238e-06
2016 | 2016-01-04 | C | 7 | 0.0030871 | 2.1166e-05
2016 | 2016-01-04 | C | 1 | 0.00068186 | 3.0238e-06
2016 | 2016-01-04 | C | 10 | 0.0033261 | 3.0238e-05
2016 | 2016-01-04 | C | 1023 | 0.11828 | 0.0030933
2016 | 2016-01-04 | C | 1 | 0.00023983 | 3.0238e-06
2016 | 2016-01-04 | C | 38 | 0.0043491 | 0.0001149
2016 | 2016-01-04 | C | 6 | 0 | 1.8143e-05
2016 | 2016-01-04 | C | 3 | 0.00068488 | 9.0713e-06
2016 | 2016-01-05 | C | 5 | 0.00040821 | 1.5119e-05
2016 | 2016-01-04 | C | 6 | 0.0021145 | 1.8143e-05
2016 | 2016-01-05 | C | 3 | 0.001407 | 9.0713e-06
2016 | 2016-01-05 | C | 29 | 0.014333 | 8.7689e-05
2016 | 2016-01-25 | B | 102 | 0.1573 | 0.00030842
2016 | 2016-01-05 | C | 1 | 3.3463e-05 | 3.0238e-06
2016 | 2016-01-25 | B | 6 | 0.0076562 | 1.8143e-05
2016 | 2016-01-06 | B | 227 | 0.021965 | 0.00068639
2016 | 2016-01-06 | C | 22 | 0.013704 | 6.6523e-05
2016 | 2016-01-05 | C | 192 | 0.042962 | 0.00058056
2016 | 2016-01-06 | C | 1 | 0.00019065 | 3.0238e-06
2016 | 2016-01-06 | C | 348 | 0.018318 | 0.0010523
2016 | 2016-01-27 | B | 79 | 0.20132 | 0.00023888
2016 | 2016-01-06 | C | 2757 | 0.079587 | 0.0083365
2016 | 2016-01-28 | B | 5 | 0.0046415 | 1.5119e-05
2016 | 2016-01-07 | C | 1 | 0.0015273 | 3.0238e-06
2016 | 2016-01-07 | C | 1 | 0.00022562 | 3.0238e-06
2016 | 2016-01-07 | C | 1386 | 0 | 0.0041909
2016 | 2016-01-07 | C | 31 | 0.0035557 | 9.3737e-05
2016 | 2016-01-07 | C | 21 | 0.0063608 | 6.3499e-05
2016 | 2016-01-07 | C | 75 | 0.067465 | 0.00022678
2016 | 2016-01-08 | C | 362 | 0.073841 | 0.0010946
2016 | 2016-01-08 | C | 307 | 0.033976 | 0.00092829
2016 | 2016-01-08 | C | 333 | 0.053305 | 0.0010069
2016 | 2016-01-08 | C | 32 | 0.011321 | 9.676e-05
2016 | 2016-01-08 | C | 154 | 0.040568 | 0.00046566
2016 | 2016-01-08 | C | 1 | 0.00062607 | 3.0238e-06
2016 | 2016-01-08 | C | 944 | 0.20082 | 0.0028544
2016 | 2016-01-08 | C | 169 | 0.036683 | 0.00051102
2016 | 2016-01-08 | C | 1 | 4.5356e-05 | 3.0238e-06
2016 | 2016-01-13 | B | 5 | 0.0047927 | 1.5119e-05
2016 | 2016-01-08 | C | 12 | 0.0029028 | 3.6285e-05
2016 | 2016-01-08 | C | 4 | 0.0055827 | 1.2095e-05
2016 | 2016-01-08 | C | 65 | 0.052205 | 0.00019654
2016 | 2016-01-08 | C | 1082 | 0.12635 | 0.0032717
2016 | 2016-01-08 | C | 2 | 0.00040387 | 6.0475e-06
2016 | 2016-01-08 | C | 113 | 0.033627 | 0.00034168
2016 | 2016-01-08 | C | 1 | 0.0012475 | 3.0238e-06
2016 | 2016-01-08 | C | 5 | 0.0020743 | 1.5119e-05
2016 | 2016-01-08 | C | 2 | 0.0014088 | 6.0475e-06
2016 | 2016-01-08 | C | 1 | 0.0002933 | 3.0238e-06
2016 | 2016-01-08 | C | 177 | 0.068685 | 0.00053521
2016 | 2016-01-08 | C | 46 | 0.036959 | 0.00013909
2016 | 2016-01-08 | C | 944 | 0 | 0.0028544
2016 | 2016-01-08 | C | 204 | 0.013982 | 0.00061685
2016 | 2016-01-08 | C | 2 | 0.0025854 | 6.0475e-06
2016 | 2016-01-08 | C | 40 | 0.0099179 | 0.00012095
2016 | 2016-01-08 | C | 102 | 0.03313 | 0.00030842
2016 | 2016-01-08 | C | 93 | 0.017716 | 0.00028121
2016 | 2016-01-08 | C | 204 | 0.034284 | 0.00061685
2016 | 2016-01-08 | C | 163 | 0.05668 | 0.00049287
2016 | 2016-01-09 | C | 7 | 0.0011641 | 2.1166e-05
2016 | 2016-01-08 | C | 536 | 0.1552 | 0.0016207
2016 | 2016-01-08 | C | 1 | 0.00040377 | 3.0238e-06
2016 | 2016-01-08 | C | 536 | 0.25008 | 0.0016207
2016 | 2016-01-08 | C | 5 | 0.00378 | 1.5119e-05
2016 | 2016-01-08 | C | 4 | 8.4665e-05 | 1.2095e-05
2016 | 2016-01-08 | C | 5 | 0.0074203 | 1.5119e-05
2016 | 2016-01-08 | C | 424 | 0.042432 | 0.0012821
2016 | 2016-01-08 | C | 109 | 0.017139 | 0.00032959
2016 | 2016-01-08 | C | 4 | 0.0025037 | 1.2095e-05
2016 | 2016-01-08 | C | 38 | 0.036782 | 0.0001149
2016 | 2016-01-08 | C | 3 | 0.002422 | 9.0713e-06
2016 | 2016-01-08 | C | 81 | 0.04049 | 0.00024492
2016 | 2016-01-08 | C | 1 | 0.0003945 | 3.0238e-06
2016 | 2016-01-08 | C | 5 | 0.001304 | 1.5119e-05
2016 | 2016-01-08 | C | 14 | 0.006108 | 4.2333e-05
2016 | 2016-01-08 | C | 398 | 0.17216 | 0.0012035
2016 | 2016-01-08 | C | 1 | 0.003235 | 3.0238e-06
2016 | 2016-01-09 | C | 1 | 0.0013705 | 3.0238e-06
2016 | 2016-01-09 | C | 1 | 0.0060333 | 3.0238e-06
2016 | 2016-01-09 | C | 1 | 2.7214e-05 | 3.0238e-06
2016 | 2016-01-09 | C | 19 | 0.011298 | 5.7451e-05
2016 | 2016-01-09 | C | 103 | 0.049832 | 0.00031145
2016 | 2016-01-09 | C | 10 | 0.0062879 | 3.0238e-05
2016 | 2016-01-09 | C | 15 | 0.0059069 | 4.5356e-05
2016 | 2016-01-09 | C | 114 | 0.0027979 | 0.00034471
2016 | 2016-01-09 | C | 17 | 0.010384 | 5.1404e-05
2016 | 2016-01-09 | C | 297 | 0.066212 | 0.00089806
2016 | 2016-01-09 | C | 9 | 0.0028575 | 2.7214e-05
2016 | 2016-01-09 | C | 334 | 0.046587 | 0.0010099
2016 | 2016-01-10 | C | 35 | 0.0044449 | 0.00010583
2016 | 2016-01-10 | C | 362 | 0.016072 | 0.0010946
2016 | 2016-01-10 | C | 1 | 0.00040816 | 3.0238e-06
2016 | 2016-01-10 | C | 1 | 0.00022446 | 3.0238e-06
2016 | 2016-01-10 | C | 15 | 0.0071663 | 4.5356e-05
2016 | 2016-01-10 | C | 2 | 0.0015955 | 6.0475e-06
2016 | 2016-01-10 | C | 1 | 5.4428e-05 | 3.0238e-06
2016 | 2016-01-10 | C | 1 | 0.00023792 | 3.0238e-06
2016 | 2016-01-10 | C | 16 | 0.0018925 | 4.838e-05
2016 | 2016-01-10 | C | 6 | 0.0017752 | 1.8143e-05
2016 | 2016-01-10 | C | 726 | 0.026343 | 0.0021953
2016 | 2016-01-10 | C | 4 | 0.00068942 | 1.2095e-05
2016 | 2016-01-11 | C | 53 | 0.11282 | 0.00016026
2016 | 2016-01-11 | C | 306 | 0.078491 | 0.00092527
2016 | 2016-01-11 | C | 1 | 0.00019957 | 3.0238e-06
2016 | 2016-01-09 | C | 13 | 0.008648 | 3.9309e-05
2016 | 2016-01-11 | C | 1295 | 0.21896 | 0.0039158
2016 | 2016-01-11 | C | 1 | 0.00047513 | 3.0238e-06
2016 | 2016-01-11 | C | 1 | 0.0003494 | 3.0238e-06
2016 | 2016-01-11 | C | 24 | 0.0025327 | 7.257e-05
2016 | 2016-01-12 | C | 268 | 0.049689 | 0.00081037
2016 | 2016-01-12 | C | 268 | 0.11777 | 0.00081037
2016 | 2016-01-25 | B | 4 | 0.0018143 | 1.2095e-05
2016 | 2016-01-12 | C | 17 | 0.00293 | 5.1404e-05
2016 | 2016-01-12 | C | 717 | 0.067565 | 0.002168
2016 | 2016-02-02 | B | 2 | 0.0027032 | 6.0475e-06
2016 | 2016-01-12 | C | 268 | 0 | 0.00081037
2016 | 2016-02-11 | B | 2 | 0.0017267 | 6.0475e-06
2016 | 2016-02-09 | B | 110 | 0.14843 | 0.00033261
2016 | 2016-02-02 | B | 9 | 0.009035 | 2.7214e-05
2016 | 2016-01-13 | C | 58 | 0.0087806 | 0.00017538
2016 | 2016-02-03 | B | 12 | 0.012337 | 3.6285e-05
2016 | 2016-02-09 | B | 20 | 0.027395 | 6.0475e-05
2016 | 2016-02-01 | B | 101 | 0.050712 | 0.0003054
2016 | 2016-02-01 | B | 46 | 0.01501 | 0.00013909
2016 | 2016-02-03 | B | 21 | 0.022323 | 6.3499e-05
2016 | 2016-02-05 | B | 23 | 0.0054246 | 6.9546e-05
2016 | 2016-02-09 | B | 14 | 0.017991 | 4.2333e-05
2016 | 2016-02-10 | B | 3 | 0.002667 | 9.0713e-06
2016 | 2016-02-11 | B | 13 | 0.017964 | 3.9309e-05
2016 | 2016-02-15 | B | 26 | 0.031211 | 7.8618e-05
2016 | 2016-01-19 | B | 7 | 0.0024765 | 2.1166e-05
2016 | 2016-02-18 | B | 26 | 0.027359 | 7.8618e-05
2016 | 2016-02-24 | B | 26 | 0.030032 | 7.8618e-05
2016 | 2016-01-14 | C | 40 | 0.025553 | 0.00012095
2016 | 2016-02-26 | B | 26 | 0.026101 | 7.8618e-05
2016 | 2016-01-14 | C | 65 | 0.018475 | 0.00019654
2016 | 2016-02-03 | B | 20 | 0.024251 | 6.0475e-05
2016 | 2016-01-14 | C | 717 | 0.007552 | 0.002168
2016 | 2016-02-11 | B | 4 | 0.0049469 | 1.2095e-05
2016 | 2016-02-10 | B | 3 | 0.0029028 | 9.0713e-06
2016 | 2016-02-11 | B | 12 | 0.0096881 | 3.6285e-05
2016 | 2016-02-10 | B | 180 | 0.1974 | 0.00054428
2016 | 2016-02-04 | B | 27 | 0.027921 | 8.1642e-05
2016 | 2016-02-16 | B | 17 | 0.019379 | 5.1404e-05
2016 | 2016-02-18 | B | 14 | 0.015197 | 4.2333e-05
2016 | 2016-02-04 | B | 71 | 0.054373 | 0.00021469
2016 | 2016-01-14 | C | 1 | 0.00017785 | 3.0238e-06
2016 | 2016-01-14 | C | 6 | 0.00048985 | 1.8143e-05
2016 | 2016-01-14 | C | 6 | 0.0028106 | 1.8143e-05
2016 | 2016-01-14 | C | 302 | 0.042331 | 0.00091318
2016 | 2016-01-15 | C | 178 | 0.047479 | 0.00053823
2016 | 2016-01-15 | C | 70 | 0.013575 | 0.00021166
2016 | 2016-01-15 | C | 356 | 0.074156 | 0.0010765
2016 | 2016-01-15 | C | 28 | 0.012454 | 8.4665e-05
2016 | 2016-02-10 | B | 17 | 0.025188 | 5.1404e-05
2016 | 2016-01-15 | C | 99 | 0.030394 | 0.00029935
2016 | 2016-01-15 | C | 7 | 0.0014908 | 2.1166e-05
2016 | 2016-01-15 | C | 21 | 0.0054577 | 6.3499e-05
2016 | 2016-02-11 | B | 39 | 0.031604 | 0.00011793
2016 | 2016-02-12 | B | 14 | 0.0079162 | 4.2333e-05
2016 | 2016-01-15 | C | 237 | 0.058229 | 0.00071663
2016 | 2016-02-02 | B | 4 | 0.0026367 | 1.2095e-05
2016 | 2016-02-11 | B | 14 | 0.014393 | 4.2333e-05
2016 | 2016-01-15 | C | 10 | 0.0034829 | 3.0238e-05
2016 | 2016-02-11 | B | 62 | 0.063928 | 0.00018747
2016 | 2016-02-15 | B | 19 | 0.025845 | 5.7451e-05
2016 | 2016-02-17 | B | 31 | 0.014239 | 9.3737e-05
2016 | 2016-01-15 | C | 26 | 0.0021109 | 7.8618e-05
2016 | 2016-02-11 | B | 45 | 0.033473 | 0.00013607
2016 | 2016-01-15 | C | 76 | 0.039879 | 0.00022981
2016 | 2016-01-15 | C | 2 | 0.00058822 | 6.0475e-06
2016 | 2016-01-16 | C | 635 | 0 | 0.0019201
2016 | 2016-01-17 | C | 1027 | 0.053972 | 0.0031054
2016 | 2016-01-17 | C | 1 | 0.00011959 | 3.0238e-06
2016 | 2016-01-17 | C | 1 | 0.00071406 | 3.0238e-06
2016 | 2016-01-19 | C | 55 | 0.019125 | 0.00016631
2016 | 2016-01-17 | C | 720 | 0.1321 | 0.0021771
2016 | 2016-01-17 | C | 93 | 0 | 0.00028121
2016 | 2016-01-18 | C | 769 | 0.01253 | 0.0023253
2016 | 2016-01-18 | C | 283 | 0.088887 | 0.00085572
2016 | 2016-02-11 | B | 51 | 0.029763 | 0.00015421
2016 | 2016-01-18 | C | 433 | 0.10206 | 0.0013093
2016 | 2016-01-18 | C | 4 | 0.0016128 | 1.2095e-05
2016 | 2016-01-18 | C | 2 | 0.0008912 | 6.0475e-06
2016 | 2016-01-18 | C | 362 | 0.10217 | 0.0010946
2016 | 2016-02-15 | B | 47 | 0.051761 | 0.00014212
2016 | 2016-01-18 | C | 20 | 0.011126 | 6.0475e-05
2016 | 2016-02-09 | B | 94 | 0.09357 | 0.00028423
2016 | 2016-02-09 | B | 1 | 0.00080734 | 3.0238e-06
2016 | 2016-01-18 | C | 268 | 0.16815 | 0.00081037
2016 | 2016-01-18 | C | 726 | 0.18776 | 0.0021953
2016 | 2016-01-20 | B | 8 | 0.010205 | 2.419e-05
2016 | 2016-02-03 | B | 37 | 0.042626 | 0.00011188
2016 | 2016-01-18 | C | 215 | 0.083964 | 0.00065011
2016 | 2016-01-18 | C | 160 | 0.15438 | 0.0004838
2016 | 2016-01-18 | C | 524 | 0.22427 | 0.0015845
2016 | 2016-01-18 | C | 93 | 0.063825 | 0.00028121
2016 | 2016-01-18 | C | 106 | 0.10257 | 0.00032052
2016 | 2016-01-19 | C | 524 | 0.023083 | 0.0015845
2016 | 2016-01-19 | C | 28 | 0.0071401 | 8.4665e-05
2016 | 2016-01-19 | C | 1 | 0.0012602 | 3.0238e-06
2016 | 2016-01-19 | C | 119 | 0.035741 | 0.00035983
2016 | 2016-01-19 | C | 946 | 0.18955 | 0.0028605
2016 | 2016-01-19 | C | 1 | 0.00044333 | 3.0238e-06
2016 | 2016-01-19 | C | 1 | 0.00028489 | 3.0238e-06
2016 | 2016-01-19 | C | 3 | 0.0014089 | 9.0713e-06
2016 | 2016-01-19 | C | 60 | 0.06241 | 0.00018143
2016 | 2016-01-18 | C | 2 | 0.0010425 | 6.0475e-06
2016 | 2016-01-19 | C | 1 | 0.00035852 | 3.0238e-06
2016 | 2016-01-19 | B | 3268 | 0.14535 | 0.0098817
2016 | 2016-01-19 | C | 1 | 0.00017039 | 3.0238e-06
2016 | 2016-02-11 | B | 41 | 0.0082319 | 0.00012397
2016 | 2016-01-21 | B | 111 | 0.011076 | 0.00033564
2016 | 2016-02-12 | B | 17 | 0.021692 | 5.1404e-05
2016 | 2016-01-19 | C | 4 | 0.0026399 | 1.2095e-05
2016 | 2016-02-16 | B | 11 | 0.011708 | 3.3261e-05
2016 | 2016-02-10 | B | 61 | 0.056995 | 0.00018445
2016 | 2016-02-17 | B | 16 | 0.01674 | 4.838e-05
2016 | 2016-02-18 | B | 11 | 0.015134 | 3.3261e-05
2016 | 2016-02-14 | B | 1 | 0.00097667 | 3.0238e-06
2016 | 2016-01-19 | C | 5 | 0.0022416 | 1.5119e-05
2016 | 2016-02-15 | B | 84 | 0.084154 | 0.000254
2016 | 2016-02-02 | B | 597 | 0.18331 | 0.0018052
2016 | 2016-02-13 | B | 20 | 0.020822 | 6.0475e-05
2016 | 2016-01-19 | C | 1 | 3.6285e-05 | 3.0238e-06
2016 | 2016-01-19 | C | 1 | 0.00043915 | 3.0238e-06
2016 | 2016-01-19 | C | 1 | 0.00024377 | 3.0238e-06
2016 | 2016-01-20 | C | 97 | 0.029687 | 0.0002933
2016 | 2016-02-10 | B | 2 | 0.00024795 | 6.0475e-06
2016 | 2016-01-21 | B | 233 | 0.1247 | 0.00070454
2016 | 2016-01-20 | C | 5 | 0.011415 | 1.5119e-05
2016 | 2016-02-12 | B | 2 | 3.9712e-05 | 6.0475e-06
2016 | 2016-01-20 | C | 1 | 0.00038195 | 3.0238e-06
2016 | 2016-01-20 | C | 508 | 0 | 0.0015361
2016 | 2016-01-21 | C | 1 | 6.0475e-05 | 3.0238e-06
2016 | 2016-01-21 | C | 2 | 0.00023585 | 6.0475e-06
2016 | 2016-01-22 | B | 83 | 0.063245 | 0.00025097
2016 | 2016-01-22 | C | 15 | 0.0028575 | 4.5356e-05
2016 | 2016-01-21 | C | 40 | 0.0076199 | 0.00012095
2016 | 2016-01-21 | C | 1 | 0.00065752 | 3.0238e-06
2016 | 2016-01-21 | C | 14 | 0.0046305 | 4.2333e-05
2016 | 2016-01-21 | C | 14 | 0.0028673 | 4.2333e-05
2016 | 2016-01-29 | B | 54 | 0.059598 | 0.00016328
2016 | 2016-02-02 | B | 47 | 0.033255 | 0.00014212
2016 | 2016-01-22 | C | 2 | 0.00043955 | 6.0475e-06
2016 | 2016-01-22 | C | 75 | 0.12691 | 0.00022678
2016 | 2016-01-22 | C | 1997 | 0.12822 | 0.0060385
2016 | 2016-01-22 | C | 238 | 0.052974 | 0.00071966
2016 | 2016-01-23 | C | 1 | 0.00035025 | 3.0238e-06
2016 | 2016-01-23 | C | 1 | 0.00047896 | 3.0238e-06
2016 | 2016-01-23 | C | 3 | 0.0026939 | 9.0713e-06
2016 | 2016-01-23 | C | 122 | 0.013631 | 0.0003689
2016 | 2016-01-23 | C | 61 | 0.011488 | 0.00018445
2016 | 2016-01-24 | C | 7 | 0.0020531 | 2.1166e-05
2016 | 2016-01-25 | C | 24 | 0.0089987 | 7.257e-05
2016 | 2016-02-24 | B | 3 | 0.00039914 | 9.0713e-06
2016 | 2016-01-30 | B | 120 | 0.062205 | 0.00036285
2016 | 2016-02-16 | B | 41 | 0.04054 | 0.00012397
2016 | 2016-02-25 | B | 35 | 0.04631 | 0.00010583
2016 | 2016-02-16 | B | 51 | 0.031459 | 0.00015421
2016 | 2016-02-16 | B | 19 | 0.021142 | 5.7451e-05
2016 | 2016-02-03 | B | 58 | 0.050182 | 0.00017538
2016 | 2016-02-16 | B | 7 | 0.0023706 | 2.1166e-05
2016 | 2016-02-16 | B | 1 | 0.00040518 | 3.0238e-06
2016 | 2016-01-25 | C | 272 | 0.050389 | 0.00082246
2016 | 2016-01-25 | C | 9 | 0.005514 | 2.7214e-05
2016 | 2016-01-26 | C | 2 | 0.00082952 | 6.0475e-06
2016 | 2016-01-26 | C | 71 | 0.014813 | 0.00021469
2016 | 2016-01-26 | C | 1 | 0.00030374 | 3.0238e-06
2016 | 2016-01-26 | C | 1 | 0.0011743 | 3.0238e-06
2016 | 2016-01-26 | C | 2 | 0.001006 | 6.0475e-06
2016 | 2016-01-26 | C | 1886 | 0.23728 | 0.0057028
2016 | 2016-01-26 | C | 14 | 0.0052432 | 4.2333e-05
2016 | 2016-01-26 | C | 575 | 0.0734 | 0.0017387
2016 | 2016-01-26 | C | 474 | 0.099683 | 0.0014333
2016 | 2016-02-19 | B | 19 | 0.016201 | 5.7451e-05
2016 | 2016-01-26 | C | 1 | 1.5119e-05 | 3.0238e-06
2016 | 2016-01-26 | C | 1079 | 0.10519 | 0.0032626
2016 | 2016-01-26 | C | 393 | 0.21564 | 0.0011883
2016 | 2016-01-26 | C | 6 | 0.0026431 | 1.8143e-05
2016 | 2016-01-27 | C | 424 | 0.010903 | 0.0012821
2016 | 2016-01-27 | C | 1794 | 0 | 0.0054246
2016 | 2016-01-27 | C | 405 | 0 | 0.0012246
2016 | 2016-02-19 | B | 18 | 0.01232 | 5.4428e-05
2016 | 2016-01-27 | C | 250 | 0.053515 | 0.00075594
2016 | 2016-02-11 | B | 2 | 0.0020803 | 6.0475e-06
2016 | 2016-01-27 | C | 1 | 0.00037706 | 3.0238e-06
2016 | 2016-02-12 | B | 2 | 0.00026004 | 6.0475e-06
2016 | 2016-02-19 | B | 56 | 0.044938 | 0.00016933
2016 | 2016-02-23 | B | 10 | 0.009162 | 3.0238e-05
2016 | 2016-02-02 | B | 3 | 0.0021274 | 9.0713e-06
2016 | 2016-02-16 | B | 118 | 0.10442 | 0.0003568
2016 | 2016-02-20 | B | 21 | 0.0082549 | 6.3499e-05
2016 | 2016-02-21 | B | 1 | 0.00048007 | 3.0238e-06
2016 | 2016-01-27 | C | 10 | 0.0017235 | 3.0238e-05
2016 | 2016-01-27 | C | 14 | 0.0015361 | 4.2333e-05
2016 | 2016-01-27 | C | 19 | 0.0036002 | 5.7451e-05
2016 | 2016-01-27 | C | 7 | 0.0084965 | 2.1166e-05
2016 | 2016-01-27 | C | 4 | 0.0035414 | 1.2095e-05
2016 | 2016-01-27 | C | 121 | 0.025998 | 0.00036588
2016 | 2016-01-27 | C | 29 | 0.012256 | 8.7689e-05
2016 | 2016-01-28 | C | 43 | 0.008252 | 0.00013002
2016 | 2016-01-28 | C | 2 | 0.00074264 | 6.0475e-06
2016 | 2016-01-28 | C | 268 | 0.27923 | 0.00081037
2016 | 2016-02-17 | B | 187 | 0.034492 | 0.00056544
2016 | 2016-02-17 | B | 6 | 0.0042272 | 1.8143e-05
2016 | 2016-01-28 | C | 1 | 0.00037147 | 3.0238e-06
2016 | 2016-02-27 | B | 40 | 0.030881 | 0.00012095
2016 | 2016-01-28 | C | 9 | 0.0034149 | 2.7214e-05
2016 | 2016-02-19 | B | 21 | 0.029591 | 6.3499e-05
2016 | 2016-01-28 | C | 1 | 0.00024891 | 3.0238e-06
2016 | 2016-01-28 | C | 1526 | 0.077983 | 0.0046143
2016 | 2016-01-28 | C | 1 | 0.00040362 | 3.0238e-06
2016 | 2016-01-29 | C | 304 | 0.05329 | 0.00091922
2016 | 2016-01-29 | C | 283 | 0.11107 | 0.00085572
2016 | 2016-01-29 | C | 380 | 0.1034 | 0.001149
2016 | 2016-02-23 | B | 9 | 0.0047352 | 2.7214e-05
2016 | 2016-02-23 | B | 17 | 0.022155 | 5.1404e-05
2016 | 2016-02-24 | B | 11 | 0.010372 | 3.3261e-05
2016 | 2016-01-29 | C | 4 | 0.0015522 | 1.2095e-05
2016 | 2016-01-29 | C | 1 | 0.00053667 | 3.0238e-06
2016 | 2016-01-29 | C | 1 | 0.00047952 | 3.0238e-06
2016 | 2016-01-29 | C | 2 | 0.0020864 | 6.0475e-06
2016 | 2016-01-29 | C | 425 | 0.093366 | 0.0012851
2016 | 2016-01-30 | C | 2 | 0.00043139 | 6.0475e-06
2016 | 2016-01-30 | C | 144 | 0.12827 | 0.00043542
2016 | 2016-01-30 | C | 1 | 0.00018788 | 3.0238e-06
2016 | 2016-01-31 | C | 33 | 0.020201 | 9.9784e-05
2016 | 2016-02-01 | C | 83 | 0.031972 | 0.00025097
2016 | 2016-02-01 | C | 4 | 0.0010873 | 1.2095e-05
2016 | 2016-02-18 | B | 21 | 0.011113 | 6.3499e-05
2016 | 2016-03-01 | B | 9 | 0.0091711 | 2.7214e-05
2016 | 2016-03-03 | B | 9 | 0.0082458 | 2.7214e-05
2016 | 2016-02-24 | B | 20 | 0.009168 | 6.0475e-05
2016 | 2016-02-01 | C | 26 | 0.0029809 | 7.8618e-05
2016 | 2016-02-16 | B | 48 | 0.054234 | 0.00014514
2016 | 2016-02-01 | C | 64 | 0.014042 | 0.00019352
2016 | 2016-02-01 | C | 1 | 0.00036114 | 3.0238e-06
2016 | 2016-02-24 | B | 24 | 0.02605 | 7.257e-05
2016 | 2016-02-01 | C | 1 | 0.00030238 | 3.0238e-06
2016 | 2016-02-01 | C | 348 | 0.047343 | 0.0010523
2016 | 2016-02-01 | C | 183 | 0.10717 | 0.00055335
2016 | 2016-02-02 | C | 15 | 0.0056355 | 4.5356e-05
2016 | 2016-02-02 | C | 12 | 0.005955 | 3.6285e-05
2016 | 2016-02-17 | B | 250 | 0.26382 | 0.00075594
2016 | 2016-02-02 | C | 1 | 0.00026639 | 3.0238e-06
2016 | 2016-02-02 | C | 1 | 0.00020259 | 3.0238e-06
2016 | 2016-02-22 | B | 3 | 0.0028121 | 9.0713e-06
2016 | 2016-02-17 | B | 16 | 0.0015965 | 4.838e-05
2016 | 2016-02-04 | C | 4 | 0.0028383 | 1.2095e-05
2016 | 2016-02-02 | C | 2 | 0.00050638 | 6.0475e-06
2016 | 2016-02-03 | C | 115 | 0.016784 | 0.00034773
2016 | 2016-02-03 | C | 1 | 1.2095e-05 | 3.0238e-06
2016 | 2016-02-04 | B | 9 | 0.0095793 | 2.7214e-05
2016 | 2016-02-10 | B | 7 | 0.0062017 | 2.1166e-05
2016 | 2016-02-03 | C | 587 | 0.12587 | 0.0017749
2016 | 2016-02-12 | B | 9 | 0.0083002 | 2.7214e-05
2016 | 2016-02-23 | B | 64 | 0.062507 | 0.00019352
2016 | 2016-02-16 | B | 9 | 0.0068035 | 2.7214e-05
2016 | 2016-02-17 | B | 9 | 0.0057965 | 2.7214e-05
2016 | 2016-02-03 | C | 14 | 0.0028786 | 4.2333e-05
2016 | 2016-02-03 | C | 1793 | 0.10969 | 0.0054216
2016 | 2016-02-04 | C | 10 | 0.00063499 | 3.0238e-05
2016 | 2016-02-25 | B | 19 | 0.010148 | 5.7451e-05
2016 | 2016-02-26 | B | 11 | 0.013172 | 3.3261e-05
2016 | 2016-02-25 | B | 16 | 0.015385 | 4.838e-05
2016 | 2016-02-04 | C | 723 | 0.16135 | 0.0021862
2016 | 2016-02-04 | C | 1 | 0.00026821 | 3.0238e-06
2016 | 2016-02-04 | C | 6 | 0.0065927 | 1.8143e-05
2016 | 2016-02-04 | C | 663 | 0.34531 | 0.0020048
2016 | 2016-02-05 | C | 1793 | 0.12056 | 0.0054216
2016 | 2016-02-11 | B | 9 | 0.0076471 | 2.7214e-05
2016 | 2016-02-05 | C | 121 | 0.064438 | 0.00036588
2016 | 2016-02-05 | C | 1 | 0.0031138 | 3.0238e-06
2016 | 2016-02-06 | C | 5 | 0.00057451 | 1.5119e-05
2016 | 2016-02-06 | C | 926 | 0 | 0.0028
2016 | 2016-02-06 | C | 3 | 0.0020168 | 9.0713e-06
2016 | 2016-02-06 | C | 4 | 0.0026881 | 1.2095e-05
2016 | 2016-02-06 | C | 926 | 0 | 0.0028
2016 | 2016-02-06 | C | 1 | 0.00018899 | 3.0238e-06
2016 | 2016-02-06 | C | 433 | 0.24836 | 0.0013093
2016 | 2016-02-06 | C | 16 | 0.0050315 | 4.838e-05
2016 | 2016-02-07 | C | 10 | 0 | 3.0238e-05
2016 | 2016-02-07 | C | 68 | 0.0012166 | 0.00020562
2016 | 2016-02-07 | C | 992 | 0.16316 | 0.0029996
2016 | 2016-02-07 | C | 18 | 0.01045 | 5.4428e-05
2016 | 2016-02-07 | C | 465 | 0.021708 | 0.001406
2016 | 2016-02-07 | C | 12 | 0.0015699 | 3.6285e-05
2016 | 2016-02-08 | C | 4799 | 3.9411 | 0.014511
2016 | 2016-02-08 | C | 1 | 0.00023505 | 3.0238e-06
2016 | 2016-02-08 | C | 5 | 0.0023701 | 1.5119e-05
2016 | 2016-02-09 | C | 149 | 0.058072 | 0.00045054
2016 | 2016-02-09 | C | 1 | 0.00015774 | 3.0238e-06
2016 | 2016-02-09 | C | 17 | 0.0063484 | 5.1404e-05
2016 | 2016-02-09 | C | 2 | 0.00092406 | 6.0475e-06
2016 | 2016-02-23 | B | 12 | 0.011248 | 3.6285e-05
2016 | 2016-02-25 | B | 77 | 0.081956 | 0.00023283
2016 | 2016-02-25 | B | 21 | 0.0062356 | 6.3499e-05
2016 | 2016-02-09 | C | 179 | 0.0892 | 0.00054125
2016 | 2016-02-09 | C | 113 | 0.032368 | 0.00034168
2016 | 2016-02-10 | C | 598 | 0.092388 | 0.0018082
2016 | 2016-02-10 | C | 178 | 0.067697 | 0.00053823
2016 | 2016-02-10 | C | 238 | 0.11071 | 0.00071966
2016 | 2016-02-10 | C | 4 | 0.00015724 | 1.2095e-05
2016 | 2016-02-25 | B | 76 | 0.07641 | 0.00022981
2016 | 2016-02-10 | C | 25 | 0.032808 | 7.5594e-05
2016 | 2016-02-10 | B | 37 | 0.021609 | 0.00011188
2016 | 2016-02-10 | C | 68 | 0.027009 | 0.00020562
2016 | 2016-02-29 | B | 3 | 0.0027214 | 9.0713e-06
2016 | 2016-02-19 | B | 116 | 0.15066 | 0.00035076
2016 | 2016-02-10 | C | 1 | 0.00045961 | 3.0238e-06
2016 | 2016-02-10 | C | 8 | 8.1843e-05 | 2.419e-05
2016 | 2016-02-10 | C | 1 | 0.00026307 | 3.0238e-06
2016 | 2016-02-10 | C | 4 | 0.00073598 | 1.2095e-05
2016 | 2016-02-11 | C | 105 | 0.020517 | 0.00031749
2016 | 2016-02-12 | B | 72 | 0.027156 | 0.00021771
2016 | 2016-03-08 | B | 1 | 0.00028146 | 3.0238e-06
2016 | 2016-03-01 | B | 40 | 0.037132 | 0.00012095
2016 | 2016-03-01 | B | 25 | 0.023585 | 7.5594e-05
2016 | 2016-03-02 | B | 43 | 0.027513 | 0.00013002
2016 | 2016-03-02 | B | 224 | 0.1226 | 0.00067732
2016 | 2016-03-01 | B | 3 | 0.0022406 | 9.0713e-06
2016 | 2016-03-02 | B | 97 | 0.024263 | 0.0002933
2016 | 2016-03-02 | B | 24 | 0.0034108 | 7.257e-05
2016 | 2016-03-01 | B | 8 | 0.0019594 | 2.419e-05
2016 | 2016-03-02 | B | 141 | 0.10019 | 0.00042635
2016 | 2016-03-02 | B | 17 | 0.020407 | 5.1404e-05
2016 | 2016-03-02 | B | 690 | 0.0062138 | 0.0020864
2016 | 2016-03-01 | B | 28 | 0.032003 | 8.4665e-05
2016 | 2016-03-03 | B | 40 | 0.055516 | 0.00012095
2016 | 2016-03-02 | B | 1 | 0.0008527 | 3.0238e-06
2016 | 2016-02-11 | C | 530 | 0.13302 | 0.0016026
2016 | 2016-02-11 | C | 303 | 0.022802 | 0.0009162
2016 | 2016-02-11 | C | 133 | 0.055081 | 0.00040216
2016 | 2016-03-02 | B | 1615 | 0.052076 | 0.0048834
2016 | 2016-02-12 | C | 1 | 0 | 3.0238e-06
2016 | 2016-03-03 | B | 42 | 0.0135 | 0.000127
2016 | 2016-03-02 | B | 30 | 0.010523 | 9.0713e-05
2016 | 2016-03-03 | B | 62 | 0.060963 | 0.00018747
2016 | 2016-02-17 | B | 4 | 0.0011127 | 1.2095e-05
2016 | 2016-02-12 | C | 33 | 0.0080825 | 9.9784e-05
2016 | 2016-03-03 | B | 3 | 0.0018959 | 9.0713e-06
2016 | 2016-03-03 | B | 53 | 0.054168 | 0.00016026
2016 | 2016-03-07 | B | 48 | 0.025158 | 0.00014514
2016 | 2016-03-04 | B | 19 | 0.013846 | 5.7451e-05
2016 | 2016-03-04 | B | 10 | 0.0048904 | 3.0238e-05
2016 | 2016-03-03 | B | 2 | 0.00044752 | 6.0475e-06
2016 | 2016-03-11 | B | 1 | 0.00076199 | 3.0238e-06
2016 | 2016-03-03 | B | 43 | 0.039698 | 0.00013002
2016 | 2016-03-05 | B | 100 | 0.03878 | 0.00030238
2016 | 2016-03-01 | B | 6 | 0.0033564 | 1.8143e-05
2016 | 2016-03-05 | B | 1 | 0.00051404 | 3.0238e-06
2016 | 2016-03-06 | B | 5 | 0.0016646 | 1.5119e-05
2016 | 2016-03-07 | B | 29 | 0.036451 | 8.7689e-05
2016 | 2016-03-07 | B | 60 | 0.059804 | 0.00018143
2016 | 2016-03-07 | B | 2 | 0.0015542 | 6.0475e-06
2016 | 2016-03-07 | B | 37 | 0.023383 | 0.00011188
2016 | 2016-03-14 | B | 1 | 0.0020017 | 3.0238e-06
2016 | 2016-02-12 | C | 344 | 0.30269 | 0.0010402
2016 | 2016-02-12 | C | 17 | 0.050781 | 5.1404e-05
2016 | 2016-02-13 | C | 16 | 0.0042897 | 4.838e-05
2016 | 2016-02-13 | C | 778 | 0.15188 | 0.0023525
2016 | 2016-02-13 | C | 850 | 0.081899 | 0.0025702
2016 | 2016-02-14 | C | 29 | 0.0099191 | 8.7689e-05
2016 | 2016-02-14 | C | 34 | 0.0043231 | 0.00010281
2016 | 2016-02-14 | C | 1 | 5.0749e-05 | 3.0238e-06
2016 | 2016-02-15 | C | 199 | 0.020227 | 0.00060173
2016 | 2016-02-15 | C | 250 | 0.072365 | 0.00075594
2016 | 2016-02-23 | B | 1802 | 0.44949 | 0.0054488
2016 | 2016-03-03 | B | 30 | 0.033564 | 9.0713e-05
2016 | 2016-02-19 | B | 6 | 0.0048441 | 1.8143e-05
2016 | 2016-03-04 | B | 43 | 0.042127 | 0.00013002
2016 | 2016-02-16 | C | 2 | 3.0238e-05 | 6.0475e-06
2016 | 2016-02-16 | C | 12 | 0.0028302 | 3.6285e-05
2016 | 2016-02-29 | B | 49 | 0.036962 | 0.00014816
2016 | 2016-02-19 | B | 19 | 0.0098817 | 5.7451e-05
2016 | 2016-03-03 | B | 6 | 0.0015838 | 1.8143e-05
2016 | 2016-02-16 | C | 12 | 0.015086 | 3.6285e-05
2016 | 2016-03-04 | B | 84 | 0.037591 | 0.000254
2016 | 2016-02-16 | C | 898 | 0.08137 | 0.0027153
2016 | 2016-02-17 | C | 199 | 0.10426 | 0.00060173
2016 | 2016-02-17 | C | 1 | 0.00043053 | 3.0238e-06
2016 | 2016-02-17 | C | 22 | 0.015699 | 6.6523e-05
2016 | 2016-02-17 | C | 25 | 0.0074989 | 7.5594e-05
2016 | 2016-03-04 | B | 3 | 0.0016963 | 9.0713e-06
2016 | 2016-02-17 | C | 386 | 0.080451 | 0.0011672
2016 | 2016-03-08 | B | 25 | 0.0078618 | 7.5594e-05
2016 | 2016-03-04 | B | 7 | 0.001524 | 2.1166e-05
2016 | 2016-03-10 | B | 598 | 0.57741 | 0.0018082
2016 | 2016-02-17 | C | 1 | 6.6523e-05 | 3.0238e-06
2016 | 2016-02-17 | C | 142 | 0.04152 | 0.00042937
2016 | 2016-02-17 | C | 233 | 0.059387 | 0.00070454
2016 | 2016-02-17 | C | 1 | 0.00082297 | 3.0238e-06
2016 | 2016-02-17 | C | 6 | 0.0015911 | 1.8143e-05
2016 | 2016-02-17 | C | 65 | 0.0074723 | 0.00019654
2016 | 2016-02-17 | C | 2 | 0.0069365 | 6.0475e-06
2016 | 2016-02-17 | C | 32 | 0.022158 | 9.676e-05
2016 | 2016-02-17 | C | 13 | 0.0023585 | 3.9309e-05
2016 | 2016-02-17 | C | 5 | 0.0016258 | 1.5119e-05
2016 | 2016-02-17 | C | 122 | 0.020905 | 0.0003689
2016 | 2016-02-17 | C | 13 | 0.037933 | 3.9309e-05
2016 | 2016-02-17 | C | 1 | 0.000229 | 3.0238e-06
2016 | 2016-02-17 | C | 239 | 0.066276 | 0.00072268
2016 | 2016-02-18 | C | 72 | 0.017417 | 0.00021771
2016 | 2016-02-18 | C | 551 | 0.05142 | 0.0016661
2016 | 2016-02-18 | C | 152 | 0.0057758 | 0.00045961
2016 | 2016-02-18 | C | 211 | 0.079954 | 0.00063801
2016 | 2016-02-18 | C | 496 | 0.15133 | 0.0014998
2016 | 2016-02-18 | C | 178 | 0.096484 | 0.00053823
2016 | 2016-02-18 | C | 205 | 0.012697 | 0.00061987
2016 | 2016-02-18 | C | 133 | 0 | 0.00040216
2016 | 2016-02-18 | C | 235 | 0 | 0.00071058
2016 | 2016-02-18 | C | 252 | 0.080043 | 0.00076199
2016 | 2016-02-18 | C | 5 | 0.030152 | 1.5119e-05
2016 | 2016-02-18 | C | 142 | 0 | 0.00042937
2016 | 2016-02-18 | C | 33 | 0.042204 | 9.9784e-05
2016 | 2016-02-18 | C | 122 | 0.02843 | 0.0003689
2016 | 2016-02-18 | C | 149 | 0 | 0.00045054
2016 | 2016-02-18 | C | 154 | 0 | 0.00046566
2016 | 2016-02-18 | C | 175 | 0.11604 | 0.00052916
2016 | 2016-02-18 | C | 1 | 0.0010371 | 3.0238e-06
2016 | 2016-02-18 | C | 114 | 0 | 0.00034471
2016 | 2016-02-18 | C | 1 | 0.0016111 | 3.0238e-06
2016 | 2016-02-18 | C | 6 | 0.0026721 | 1.8143e-05
2016 | 2016-02-18 | C | 86 | 0.024704 | 0.00026004
2016 | 2016-02-18 | C | 6 | 0.0056786 | 1.8143e-05
2016 | 2016-02-18 | C | 27 | 0.012993 | 8.1642e-05
2016 | 2016-02-18 | C | 1 | 0.00027819 | 3.0238e-06
2016 | 2016-03-03 | B | 1 | 0.0008395 | 3.0238e-06
2016 | 2016-03-06 | B | 15 | 0.0062471 | 4.5356e-05
2016 | 2016-03-09 | B | 37 | 0.036543 | 0.00011188
2016 | 2016-02-18 | C | 146 | 0.014411 | 0.00044147
2016 | 2016-02-18 | C | 1 | 0.00028383 | 3.0238e-06
2016 | 2016-02-18 | C | 105 | 0.013708 | 0.00031749
2016 | 2016-03-08 | B | 1 | 0.00035847 | 3.0238e-06
2016 | 2016-02-18 | C | 40 | 0.0037495 | 0.00012095
2016 | 2016-02-18 | C | 16 | 0.0084117 | 4.838e-05
2016 | 2016-03-07 | B | 5 | 0.0026609 | 1.5119e-05
2016 | 2016-02-18 | C | 291 | 0.043414 | 0.00087991
2016 | 2016-02-18 | C | 75 | 0.079241 | 0.00022678
2016 | 2016-02-18 | C | 27 | 0.0080476 | 8.1642e-05
2016 | 2016-02-19 | C | 44 | 0.036987 | 0.00013305
2016 | 2016-02-18 | C | 69 | 0.0031296 | 0.00020864
2016 | 2016-02-18 | C | 1 | 0.00022678 | 3.0238e-06
2016 | 2016-02-18 | C | 179 | 0.0081278 | 0.00054125
2016 | 2016-02-18 | C | 152 | 0.027451 | 0.00045961
2016 | 2016-02-18 | C | 3 | 0.01192 | 9.0713e-06
2016 | 2016-02-18 | C | 274 | 0.1953 | 0.00082851
2016 | 2016-02-19 | C | 638 | 0.11955 | 0.0019292
2016 | 2016-02-19 | C | 6 | 0.003715 | 1.8143e-05
2016 | 2016-03-07 | B | 19 | 0.016433 | 5.7451e-05
2016 | 2016-02-19 | C | 534 | 0.42448 | 0.0016147
2016 | 2016-03-07 | B | 187 | 0.16085 | 0.00056544
2016 | 2016-02-19 | C | 13 | 0.0029482 | 3.9309e-05
2016 | 2016-02-19 | C | 285 | 0.04148 | 0.00086177
2016 | 2016-02-19 | C | 1 | 0.00014212 | 3.0238e-06
2016 | 2016-02-19 | C | 1 | 0.00021968 | 3.0238e-06
2016 | 2016-02-19 | C | 2 | 0.00055365 | 6.0475e-06
2016 | 2016-02-19 | C | 11 | 0.0043953 | 3.3261e-05
2016 | 2016-02-20 | C | 132 | 0.067496 | 0.00039914
2016 | 2016-02-20 | C | 1 | 0.00030348 | 3.0238e-06
2016 | 2016-02-20 | C | 6 | 0.0046082 | 1.8143e-05
2016 | 2016-02-20 | C | 7 | 0.00078315 | 2.1166e-05
2016 | 2016-02-20 | C | 2 | 0.00032914 | 6.0475e-06
2016 | 2016-02-20 | C | 54 | 0.064497 | 0.00016328
2016 | 2016-02-21 | C | 142 | 0.058284 | 0.00042937
2016 | 2016-03-08 | B | 3 | 0.0033432 | 9.0713e-06
2016 | 2016-03-08 | B | 3 | 0.0029061 | 9.0713e-06
2016 | 2016-03-09 | B | 11 | 0.011941 | 3.3261e-05
2016 | 2016-02-22 | C | 2998 | 0.23509 | 0.0090652
2016 | 2016-02-22 | C | 4 | 0.0018669 | 1.2095e-05
2016 | 2016-02-22 | C | 25 | 0.011716 | 7.5594e-05
2016 | 2016-03-09 | B | 20 | 0.020051 | 6.0475e-05
2016 | 2016-03-09 | B | 39 | 0.044437 | 0.00011793
2016 | 2016-02-22 | C | 5 | 0.0060369 | 1.5119e-05
2016 | 2016-02-22 | C | 533 | 0.05592 | 0.0016117
2016 | 2016-03-09 | B | 29 | 0.028682 | 8.7689e-05
2016 | 2016-03-09 | B | 20 | 0.024427 | 6.0475e-05
2016 | 2016-02-22 | C | 1227 | 0.14606 | 0.0037102
2016 | 2016-02-22 | C | 10 | 0.0033866 | 3.0238e-05
2016 | 2016-02-25 | B | 1 | 0.00033866 | 3.0238e-06
2016 | 2016-02-22 | C | 1 | 0.00033261 | 3.0238e-06
2016 | 2016-03-09 | B | 27 | 0.025577 | 8.1642e-05
2016 | 2016-02-22 | C | 1 | 0.00024906 | 3.0238e-06
2016 | 2016-02-22 | C | 1 | 0.0003176 | 3.0238e-06
2016 | 2016-02-22 | C | 92 | 0.022639 | 0.00027819
2016 | 2016-02-22 | C | 31 | 0.028773 | 9.3737e-05
2016 | 2016-03-09 | B | 1 | 0.00040594 | 3.0238e-06
2016 | 2016-02-23 | C | 542 | 0.11225 | 0.0016389
2016 | 2016-03-08 | B | 6 | 0.0059574 | 1.8143e-05
2016 | 2016-02-23 | C | 81 | 0.018124 | 0.00024492
2016 | 2016-03-10 | B | 8 | 0.0069426 | 2.419e-05
2016 | 2016-03-08 | B | 30 | 0.036092 | 9.0713e-05
2016 | 2016-03-16 | B | 6 | 0.0060052 | 1.8143e-05
2016 | 2016-02-23 | C | 26 | 0.0046384 | 7.8618e-05
2016 | 2016-03-12 | B | 1 | 0.00045356 | 3.0238e-06
2016 | 2016-03-11 | B | 15 | 0.0084816 | 4.5356e-05
2016 | 2016-03-01 | B | 21 | 0.0052069 | 6.3499e-05
2016 | 2016-03-15 | B | 12 | 0.0042091 | 3.6285e-05
2016 | 2016-02-24 | C | 5 | 0.0011825 | 1.5119e-05
2016 | 2016-03-15 | B | 1 | 0.0010251 | 3.0238e-06
2016 | 2016-03-14 | B | 113 | 0.12604 | 0.00034168
2016 | 2016-03-11 | B | 65 | 0.055426 | 0.00019654
2016 | 2016-02-24 | C | 4 | 2.419e-05 | 1.2095e-05
2016 | 2016-03-09 | B | 13 | 0.0081369 | 3.9309e-05
2016 | 2016-03-03 | B | 12 | 0.010559 | 3.6285e-05
2016 | 2016-03-09 | B | 1 | 0.00033035 | 3.0238e-06
2016 | 2016-02-24 | C | 2 | 0.00077741 | 6.0475e-06
2016 | 2016-02-24 | C | 18 | 0.0024683 | 5.4428e-05
2016 | 2016-03-10 | B | 1 | 0.00087689 | 3.0238e-06
2016 | 2016-03-16 | B | 127 | 0.1659 | 0.00038402
2016 | 2016-03-12 | B | 31 | 0.0048743 | 9.3737e-05
2016 | 2016-03-15 | B | 5 | 0.00036285 | 1.5119e-05
2016 | 2016-03-15 | B | 3 | 0.0027758 | 9.0713e-06
2016 | 2016-03-16 | B | 35 | 0.035083 | 0.00010583
2016 | 2016-03-15 | B | 15 | 0.013335 | 4.5356e-05
2016 | 2016-03-15 | B | 18 | 0.005314 | 5.4428e-05
2016 | 2016-03-12 | B | 1 | 0.00096458 | 3.0238e-06
2016 | 2016-03-11 | B | 17 | 0.0064769 | 5.1404e-05
2016 | 2016-03-16 | B | 117 | 0.1021 | 0.00035378
2016 | 2016-03-10 | B | 109 | 0.062622 | 0.00032959
2016 | 2016-03-14 | B | 62 | 0.054555 | 0.00018747
2016 | 2016-03-16 | B | 34 | 0.026483 | 0.00010281
2016 | 2016-03-12 | B | 32 | 0.0087084 | 9.676e-05
2016 | 2016-02-24 | C | 543 | 0.11458 | 0.0016419
2016 | 2016-02-25 | C | 631 | 2.2424 | 0.001908
2016 | 2016-02-25 | C | 811 | 0.13551 | 0.0024523
2016 | 2016-03-16 | B | 24 | 0.0049239 | 7.257e-05
2016 | 2016-03-06 | B | 4 | 0.0045296 | 1.2095e-05
2016 | 2016-03-11 | B | 4 | 0.0018264 | 1.2095e-05
2016 | 2016-03-11 | B | 4 | 0.00042333 | 1.2095e-05
2016 | 2016-03-15 | B | 5 | 0.0010281 | 1.5119e-05
2016 | 2016-03-04 | B | 1 | 0.00022678 | 3.0238e-06
2016 | 2016-03-15 | B | 2 | 0.0016812 | 6.0475e-06
2016 | 2016-03-17 | B | 4 | 0.0009166 | 1.2095e-05
2016 | 2016-03-21 | B | 27 | 0.010368 | 8.1642e-05
2016 | 2016-03-18 | B | 4 | 0.0035743 | 1.2095e-05
2016 | 2016-02-25 | C | 332 | 0.2608 | 0.0010039
2016 | 2016-02-25 | C | 165 | 0.06065 | 0.00049892
2016 | 2016-02-26 | C | 423 | 0.01122 | 0.0012791
2016 | 2016-02-26 | C | 757 | 0.19161 | 0.002289
2016 | 2016-03-21 | B | 124 | 0.097396 | 0.00037495
2016 | 2016-03-22 | B | 64 | 0.043736 | 0.00019352
2016 | 2016-03-19 | B | 17 | 0.0088415 | 5.1404e-05
2016 | 2016-02-26 | C | 61 | 0.021568 | 0.00018445
2016 | 2016-02-26 | C | 39 | 0.012736 | 0.00011793
2016 | 2016-03-23 | B | 2 | 0.0010402 | 6.0475e-06
2016 | 2016-03-22 | B | 42 | 0.017329 | 0.000127
2016 | 2016-03-24 | B | 64 | 0.084956 | 0.00019352
2016 | 2016-03-14 | B | 136 | 0.1728 | 0.00041123
2016 | 2016-03-22 | B | 112 | 0.0254 | 0.00033866
2016 | 2016-03-19 | B | 7 | 0.001524 | 2.1166e-05
2016 | 2016-03-19 | B | 51 | 0.02064 | 0.00015421
2016 | 2016-02-26 | C | 7 | 0.00052916 | 2.1166e-05
2016 | 2016-02-26 | C | 1 | 0.00011475 | 3.0238e-06
2016 | 2016-02-26 | C | 851 | 0.114 | 0.0025732
2016 | 2016-02-27 | C | 4 | 0.00038704 | 1.2095e-05
2016 | 2016-02-27 | C | 1 | 0.0021166 | 3.0238e-06
2016 | 2016-02-27 | C | 273 | 0.032602 | 0.00082549
2016 | 2016-02-27 | C | 4 | 0.0084665 | 1.2095e-05
2016 | 2016-02-27 | C | 8 | 0.0082246 | 2.419e-05
2016 | 2016-02-28 | C | 327 | 0.073492 | 0.00098877
2016 | 2016-02-28 | C | 115 | 0.018526 | 0.00034773
2016 | 2016-02-28 | C | 23 | 0.006622 | 6.9546e-05
2016 | 2016-03-16 | B | 57 | 0.023785 | 0.00017235
2016 | 2016-02-29 | C | 12 | 0.00351 | 3.6285e-05
2016 | 2016-02-29 | C | 196 | 0.045039 | 0.00059266
2016 | 2016-02-29 | C | 240 | 0.050344 | 0.0007257
2016 | 2016-03-21 | B | 62 | 0.029808 | 0.00018747
2016 | 2016-03-22 | B | 435 | 0.21407 | 0.0013153
2016 | 2016-03-08 | B | 23 | 0.021319 | 6.9546e-05
2016 | 2016-02-29 | C | 562 | 0.089068 | 0.0016994
2016 | 2016-03-10 | B | 23 | 0.027054 | 6.9546e-05
2016 | 2016-03-14 | B | 23 | 0.025315 | 6.9546e-05
2016 | 2016-03-16 | B | 23 | 0.024341 | 6.9546e-05
2016 | 2016-02-29 | C | 12 | 0.039398 | 3.6285e-05
2016 | 2016-02-29 | C | 39 | 0.025707 | 0.00011793
2016 | 2016-03-21 | B | 9 | 0.010284 | 2.7214e-05
2016 | 2016-03-23 | B | 9 | 0.0090894 | 2.7214e-05
2016 | 2016-03-29 | B | 9 | 0.0095793 | 2.7214e-05
2016 | 2016-03-29 | B | 165 | 0.023449 | 0.00049892
2016 | 2016-03-30 | B | 39 | 0.042689 | 0.00011793
2016 | 2016-02-29 | C | 2527 | 0.6393 | 0.007641
2016 | 2016-03-31 | B | 165 | 0.02794 | 0.00049892
2016 | 2016-03-29 | B | 40 | 0.047292 | 0.00012095
2016 | 2016-03-29 | B | 41 | 0.041407 | 0.00012397
2016 | 2016-03-29 | B | 22 | 0.02774 | 6.6523e-05
2016 | 2016-03-30 | B | 14 | 0.017018 | 4.2333e-05
2016 | 2016-02-29 | C | 1 | 0.00018354 | 3.0238e-06
2016 | 2016-03-02 | C | 1 | 0.00016328 | 3.0238e-06
2016 | 2016-02-29 | C | 999 | 0.20759 | 0.0030207
2016 | 2016-03-01 | C | 303 | 0.057057 | 0.0009162
2016 | 2016-03-01 | C | 1 | 0.00011188 | 3.0238e-06
2016 | 2016-03-01 | C | 1 | 0.00013305 | 3.0238e-06
2016 | 2016-03-31 | B | 4 | 0.0027577 | 1.2095e-05
2016 | 2016-03-08 | B | 142 | 0.064821 | 0.00042937
2016 | 2016-03-01 | C | 66 | 0.028284 | 0.00019957
2016 | 2016-03-01 | C | 115 | 0.0031615 | 0.00034773
2016 | 2016-03-02 | C | 524 | 0.10067 | 0.0015845
2016 | 2016-03-02 | C | 2 | 0.0011165 | 6.0475e-06
2016 | 2016-03-02 | C | 7 | 0.0010184 | 2.1166e-05
2016 | 2016-03-31 | B | 48 | 0.038317 | 0.00014514
2016 | 2016-03-03 | B | 1 | 0.00077711 | 3.0238e-06
2016 | 2016-03-02 | C | 4 | 0.0012285 | 1.2095e-05
2016 | 2016-03-01 | C | 2 | 0.000254 | 6.0475e-06
2016 | 2016-03-02 | C | 2 | 0.0012547 | 6.0475e-06
2016 | 2016-03-03 | C | 21 | 0.0055244 | 6.3499e-05
2016 | 2016-03-03 | C | 1 | 0.0013537 | 3.0238e-06
2016 | 2016-03-30 | B | 80 | 0.051767 | 0.0002419
2016 | 2016-03-03 | C | 4 | 0.0016395 | 1.2095e-05
2016 | 2016-03-31 | B | 13 | 0.0072721 | 3.9309e-05
2016 | 2016-03-10 | B | 1 | 0.0010281 | 3.0238e-06
2016 | 2016-03-03 | C | 1 | 0.00027819 | 3.0238e-06
2016 | 2016-03-03 | C | 22 | 0.0025279 | 6.6523e-05
2016 | 2016-03-09 | B | 9 | 0.010208 | 2.7214e-05
2016 | 2016-03-07 | B | 118 | 0.048579 | 0.0003568
2016 | 2016-03-23 | B | 61 | 0.048879 | 0.00018445
2016 | 2016-03-21 | B | 30 | 0.035106 | 9.0713e-05
2016 | 2016-03-03 | C | 2 | 0.0010522 | 6.0475e-06
2016 | 2016-03-03 | C | 15 | 0.0034494 | 4.5356e-05
2016 | 2016-03-06 | B | 258 | 0.2638 | 0.00078013
2016 | 2016-03-04 | C | 579 | 0.19362 | 0.0017508
2016 | 2016-03-19 | B | 1 | 0.00090108 | 3.0238e-06
2016 | 2016-03-21 | B | 47 | 0.074185 | 0.00014212
2016 | 2016-03-20 | B | 49 | 0.076749 | 0.00014816
2016 | 2016-03-04 | C | 1 | 0.00054322 | 3.0238e-06
2016 | 2016-03-04 | C | 1 | 0.00030842 | 3.0238e-06
2016 | 2016-03-05 | C | 2 | 0.0012518 | 6.0475e-06
2016 | 2016-03-05 | C | 24 | 0.0037325 | 7.257e-05
2016 | 2016-03-05 | C | 717 | 0.13478 | 0.002168
2016 | 2016-03-06 | C | 420 | 0.082852 | 0.00127
2016 | 2016-03-06 | C | 1 | 0.00023429 | 3.0238e-06
2016 | 2016-03-06 | C | 114 | 0.057867 | 0.00034471
2016 | 2016-03-07 | C | 463 | 0.089817 | 0.0014
2016 | 2016-03-22 | B | 98 | 0.092455 | 0.00029633
2016 | 2016-03-08 | B | 51 | 0.052758 | 0.00015421
2016 | 2016-03-07 | B | 4 | 0.038193 | 1.2095e-05
2016 | 2016-03-24 | B | 10 | 0.0074989 | 3.0238e-05
2016 | 2016-03-29 | B | 3 | 0.0016419 | 9.0713e-06
2016 | 2016-03-30 | B | 23 | 0.017108 | 6.9546e-05
2016 | 2016-03-17 | B | 14 | 0.017018 | 4.2333e-05
2016 | 2016-03-07 | C | 40 | 0.0078618 | 0.00012095
2016 | 2016-03-22 | B | 63 | 0.083819 | 0.0001905
2016 | 2016-03-20 | B | 8 | 0.0041353 | 2.419e-05
2016 | 2016-03-07 | C | 319 | 0.10689 | 0.00096458
2016 | 2016-03-07 | C | 1 | 0.00033498 | 3.0238e-06
2016 | 2016-03-08 | C | 28 | 0.024496 | 8.4665e-05
2016 | 2016-03-08 | C | 34 | 0.0090334 | 0.00010281
2016 | 2016-03-08 | C | 7 | 0.0014129 | 2.1166e-05
2016 | 2016-03-08 | C | 37 | 0.019691 | 0.00011188
2016 | 2016-03-08 | C | 4 | 0.00015461 | 1.2095e-05
2016 | 2016-03-10 | B | 193 | 0.23577 | 0.00058359
2016 | 2016-03-29 | B | 255 | 0.30137 | 0.00077106
2016 | 2016-03-08 | C | 1 | 0 | 3.0238e-06
2016 | 2016-03-08 | C | 2 | 0.0017326 | 6.0475e-06
2016 | 2016-03-31 | B | 14 | 0.0068579 | 4.2333e-05
2016 | 2016-03-08 | C | 237 | 0.027652 | 0.00071663
2016 | 2016-03-08 | C | 641 | 0.080685 | 0.0019382
2016 | 2016-03-08 | C | 12 | 0.0055831 | 3.6285e-05
2016 | 2016-03-08 | C | 3 | 0.00056 | 9.0713e-06
2016 | 2016-03-08 | C | 1 | 4.8279e-05 | 3.0238e-06
2016 | 2016-03-09 | C | 3 | 0.00073553 | 9.0713e-06
2016 | 2016-03-11 | B | 3 | 0.002803 | 9.0713e-06
2016 | 2016-03-09 | C | 110 | 0.031856 | 0.00033261
2016 | 2016-03-09 | C | 1 | 0.00027148 | 3.0238e-06
2016 | 2016-03-10 | C | 3394 | 0.6461 | 0.010263
2016 | 2016-03-10 | C | 17 | 0.0069575 | 5.1404e-05
2016 | 2016-03-10 | C | 304 | 0.055582 | 0.00091922
2016 | 2016-03-29 | B | 18 | 0.021172 | 5.4428e-05
2016 | 2016-03-10 | C | 766 | 0.12313 | 0.0023162
2016 | 2016-03-14 | B | 1 | 0.00037797 | 3.0238e-06
2016 | 2016-03-31 | B | 312 | 0.2471 | 0.00094341
2016 | 2016-03-10 | C | 981 | 0.14477 | 0.0029663
2016 | 2016-03-31 | B | 24 | 0.01045 | 7.257e-05
2016 | 2016-03-31 | B | 15 | 0.011883 | 4.5356e-05
2016 | 2016-03-10 | C | 179 | 0.093603 | 0.00054125
2016 | 2016-03-10 | C | 233 | 0.020281 | 0.00070454
2016 | 2016-03-21 | B | 532 | 0.59123 | 0.0016086
2016 | 2016-03-10 | C | 92 | 0.036954 | 0.00027819
2016 | 2016-03-10 | C | 36 | 0.0075341 | 0.00010886
2016 | 2016-03-10 | C | 181 | 0.014804 | 0.0005473
2016 | 2016-03-10 | C | 6 | 0.00024009 | 1.8143e-05
2016 | 2016-03-10 | C | 11 | 0.0053784 | 3.3261e-05
2016 | 2016-03-10 | C | 294 | 0.30122 | 0.00088899
2016 | 2016-03-10 | C | 62 | 0.0012748 | 0.00018747
2016 | 2016-03-11 | C | 8 | 0.0042788 | 2.419e-05
2016 | 2016-03-10 | C | 179 | 0.48832 | 0.00054125
2016 | 2016-03-10 | C | 61 | 0.02447 | 0.00018445
2016 | 2016-03-10 | C | 240 | 0.085447 | 0.0007257
2016 | 2016-03-11 | C | 327 | 0.084992 | 0.00098877
2016 | 2016-03-11 | C | 66 | 0.011931 | 0.00019957
2016 | 2016-03-11 | C | 1 | 0.00045356 | 3.0238e-06
2016 | 2016-03-11 | C | 8 | 0.0025783 | 2.419e-05
2016 | 2016-03-11 | C | 229 | 0.14195 | 0.00069244
2016 | 2016-03-11 | C | 6 | 0.0021136 | 1.8143e-05
2016 | 2016-03-11 | C | 113 | 0.065229 | 0.00034168
2016 | 2016-03-11 | C | 1 | 0.00042181 | 3.0238e-06
2016 | 2016-03-15 | B | 3 | 0.00034471 | 9.0713e-06
2016 | 2016-03-11 | C | 48 | 0.0034834 | 0.00014514
2016 | 2016-03-11 | C | 59 | 0.0068982 | 0.0001784
2016 | 2016-03-11 | C | 54 | 0.019447 | 0.00016328
2016 | 2016-03-11 | C | 1 | 0.00032354 | 3.0238e-06
2016 | 2016-03-11 | C | 1555 | 0 | 0.0047019
2016 | 2016-03-12 | C | 54 | 0.046009 | 0.00016328
2016 | 2016-03-12 | C | 1142 | 0.039008 | 0.0034531
2016 | 2016-03-12 | C | 635 | 0 | 0.0019201
2016 | 2016-03-12 | C | 4 | 0.001172 | 1.2095e-05
2016 | 2016-03-12 | C | 3 | 0.0019927 | 9.0713e-06
2016 | 2016-03-12 | C | 327 | 0.07497 | 0.00098877
2016 | 2016-03-13 | C | 776 | 0.12978 | 0.0023464
2016 | 2016-03-14 | C | 178 | 0.14107 | 0.00053823
2016 | 2016-03-14 | C | 3 | 0.0010629 | 9.0713e-06
2016 | 2016-03-14 | C | 1 | 0.00027224 | 3.0238e-06
2016 | 2016-03-14 | C | 623 | 0.10515 | 0.0018838
2016 | 2016-03-14 | C | 6 | 0.00018682 | 1.8143e-05
2016 | 2016-03-14 | C | 2 | 0.0029633 | 6.0475e-06
2016 | 2016-03-14 | C | 578 | 0.08549 | 0.0017477
2016 | 2016-03-14 | C | 1 | 0.00028202 | 3.0238e-06
2016 | 2016-03-15 | C | 3 | 0.00062834 | 9.0713e-06
2016 | 2016-03-11 | C | 4 | 0.00026609 | 1.2095e-05
2016 | 2016-03-22 | B | 3 | 0.0028937 | 9.0713e-06
2016 | 2016-03-31 | B | 18 | 0.021934 | 5.4428e-05
2016 | 2016-03-19 | B | 1 | 0.0010916 | 3.0238e-06
2016 | 2016-03-23 | B | 126 | 0.15642 | 0.00038099
2016 | 2016-03-15 | C | 18 | 0.0034235 | 5.4428e-05
2016 | 2016-03-16 | C | 320 | 0.077101 | 0.0009676
2016 | 2016-03-16 | C | 61 | 0.023133 | 0.00018445
2016 | 2016-03-16 | C | 3391 | 0 | 0.010254
2016 | 2016-03-16 | C | 4 | 0.0010464 | 1.2095e-05
2016 | 2016-03-16 | C | 46 | 0.00056564 | 0.00013909
2016 | 2016-03-16 | C | 120 | 0.02955 | 0.00036285
2016 | 2016-03-16 | C | 308 | 0.48715 | 0.00093132
2016 | 2016-03-16 | C | 1099 | 0.16359 | 0.0033231
2016 | 2016-03-17 | C | 218 | 0.1419 | 0.00065918
2016 | 2016-03-16 | C | 1535 | 0.3372 | 0.0046415
2016 | 2016-03-17 | C | 362 | 0.35824 | 0.0010946
2016 | 2016-03-17 | C | 17 | 0.0065283 | 5.1404e-05
2016 | 2016-03-17 | C | 7 | 0.00046566 | 2.1166e-05
2016 | 2016-03-17 | C | 135 | 0.054029 | 0.00040821
2016 | 2016-03-18 | C | 10 | 0.0057099 | 3.0238e-05
2016 | 2016-03-17 | C | 585 | 0.074294 | 0.0017689
2016 | 2016-03-17 | C | 379 | 0.083144 | 0.001146
2016 | 2016-03-18 | C | 1 | 0.00071124 | 3.0238e-06
2016 | 2016-03-18 | C | 779 | 0.10111 | 0.0023555
2016 | 2016-03-23 | B | 55 | 0.032793 | 0.00016631
2016 | 2016-03-18 | B | 23 | 0.01527 | 6.9546e-05
2016 | 2016-03-18 | C | 160 | 0.047469 | 0.0004838
2016 | 2016-03-18 | C | 379 | 0.097207 | 0.001146
2016 | 2016-03-18 | C | 2 | 0.00066578 | 6.0475e-06
2016 | 2016-03-19 | C | 14 | 0.0040639 | 4.2333e-05
2016 | 2016-03-19 | C | 1 | 0.00036971 | 3.0238e-06
2016 | 2016-03-20 | C | 3 | 0.00092527 | 9.0713e-06
2016 | 2016-03-20 | C | 70 | 0.089322 | 0.00021166
2016 | 2016-03-20 | C | 3 | 0.00033564 | 9.0713e-06
2016 | 2016-03-20 | C | 593 | 0.13096 | 0.0017931
2016 | 2016-03-20 | C | 198 | 0.025146 | 0.0005987
2016 | 2016-03-20 | C | 1 | 7.5292e-05 | 3.0238e-06
2016 | 2016-03-20 | C | 47 | 0.022409 | 0.00014212
2016 | 2016-03-20 | C | 379 | 0 | 0.001146
2016 | 2016-03-21 | C | 3 | 0.0033205 | 9.0713e-06
2016 | 2016-03-21 | C | 143 | 0.0054482 | 0.0004324
2016 | 2016-03-21 | C | 133 | 0.0092497 | 0.00040216
2016 | 2016-03-21 | C | 445 | 0.066417 | 0.0013456
2016 | 2016-03-30 | B | 133 | 0.14277 | 0.00040216
2016 | 2016-03-21 | C | 71 | 0.0086769 | 0.00021469
2016 | 2016-03-21 | C | 394 | 0.096544 | 0.0011914
2016 | 2016-03-21 | C | 20 | 0.0050396 | 6.0475e-05
2016 | 2016-03-21 | C | 52 | 0.0078618 | 0.00015724
2016 | 2016-03-22 | C | 257 | 0.070121 | 0.00077711
2016 | 2016-03-22 | C | 1 | 0.00011465 | 3.0238e-06
2016 | 2016-03-22 | C | 257 | 0 | 0.00077711
2016 | 2016-03-22 | C | 1 | 0.0002356 | 3.0238e-06
2016 | 2016-03-22 | C | 2 | 6.4507e-06 | 6.0475e-06
2016 | 2016-03-22 | C | 11 | 0.0023205 | 3.3261e-05
2016 | 2016-03-22 | C | 11 | 0.0039581 | 3.3261e-05
2016 | 2016-03-22 | C | 3 | 0.00020864 | 9.0713e-06
2016 | 2016-03-22 | C | 16 | 0.0056323 | 4.838e-05
2016 | 2016-03-22 | C | 283 | 0.042704 | 0.00085572
2016 | 2016-03-22 | C | 7 | 0.001524 | 2.1166e-05
2016 | 2016-03-22 | C | 1 | 0.00030812 | 3.0238e-06
2016 | 2016-03-22 | C | 6 | 0.0013676 | 1.8143e-05
2016 | 2016-03-22 | C | 198 | 0.076733 | 0.0005987
2016 | 2016-03-23 | C | 311 | 0.42198 | 0.00094039
2016 | 2016-03-23 | C | 1 | 0.0013436 | 3.0238e-06
2016 | 2016-03-23 | C | 41 | 0.014142 | 0.00012397
2016 | 2016-03-23 | C | 5 | 0.0015421 | 1.5119e-05
2016 | 2016-03-23 | C | 3 | 0.0013823 | 9.0713e-06
2016 | 2016-03-23 | C | 12 | 0.023476 | 3.6285e-05
2016 | 2016-03-23 | C | 388 | 0.044711 | 0.0011732
2016 | 2016-03-23 | C | 167 | 0.023998 | 0.00050497
2016 | 2016-03-23 | C | 144 | 0.053781 | 0.00043542
2016 | 2016-03-23 | C | 651 | 0.16372 | 0.0019685
2016 | 2016-03-23 | C | 26 | 0.010632 | 7.8618e-05
2016 | 2016-03-23 | C | 4 | 0.002982 | 1.2095e-05
2016 | 2016-03-30 | C | 2 | 0.00029028 | 6.0475e-06
2016 | 2016-03-23 | C | 123 | 0.053451 | 0.00037192
2016 | 2016-03-23 | C | 1 | 0.0028544 | 3.0238e-06
2016 | 2016-03-23 | C | 285 | 0.0804 | 0.00086177
2016 | 2016-03-23 | C | 284 | 0.062838 | 0.00085875
2016 | 2016-03-23 | C | 170 | 0.055387 | 0.00051404
2016 | 2016-03-23 | C | 236 | 0.08331 | 0.00071361
2016 | 2016-03-23 | C | 327 | 0.1948 | 0.00098877
2016 | 2016-03-24 | C | 2 | 0.0015365 | 6.0475e-06
2016 | 2016-03-24 | C | 108 | 0 | 0.00032657
2016 | 2016-03-24 | C | 790 | 0.29379 | 0.0023888
2016 | 2016-03-24 | C | 638 | 0.14814 | 0.0019292
2016 | 2016-03-24 | C | 153 | 0.12816 | 0.00046264
2016 | 2016-03-24 | C | 338 | 0.15902 | 0.001022
2016 | 2016-03-24 | C | 301 | 0.066003 | 0.00091015
2016 | 2016-03-24 | C | 1026 | 0.16029 | 0.0031024
2016 | 2016-03-24 | C | 143 | 0.064681 | 0.0004324
2016 | 2016-03-24 | C | 6 | 0.010481 | 1.8143e-05
2016 | 2016-03-24 | C | 498 | 0.26483 | 0.0015058
2016 | 2016-03-24 | C | 1209 | 0.34514 | 0.0036557
2016 | 2016-03-24 | C | 402 | 0.2225 | 0.0012156
2016 | 2016-03-24 | C | 2221 | 0.95721 | 0.0067158
2016 | 2016-03-24 | C | 4 | 0.002488 | 1.2095e-05
2016 | 2016-03-24 | C | 112 | 0.070825 | 0.00033866
2016 | 2016-03-24 | C | 1026 | 0.1895 | 0.0031024
2016 | 2016-03-24 | C | 601 | 0.23789 | 0.0018173
2016 | 2016-03-24 | C | 717 | 0.18813 | 0.002168
2016 | 2016-03-24 | C | 123 | 0.071611 | 0.00037192
2016 | 2016-03-24 | C | 207 | 0.020812 | 0.00062592
2016 | 2016-03-24 | C | 751 | 0.30062 | 0.0022708
2016 | 2016-03-24 | C | 439 | 0.14993 | 0.0013274
2016 | 2016-03-24 | C | 257 | 0.067465 | 0.00077711
2016 | 2016-03-24 | C | 20 | 0.021128 | 6.0475e-05
2016 | 2016-03-24 | C | 1 | 0.0002933 | 3.0238e-06
2016 | 2016-03-24 | C | 20 | 0.025892 | 6.0475e-05
2016 | 2016-03-24 | C | 24 | 0.0052639 | 7.257e-05
2016 | 2016-03-24 | C | 1 | 0.00087372 | 3.0238e-06
2016 | 2016-03-24 | C | 891 | 0.058222 | 0.0026942
2016 | 2016-03-24 | C | 201 | 0.089758 | 0.00060778
2016 | 2016-03-24 | C | 197 | 0.065495 | 0.00059568
2016 | 2016-03-24 | C | 1 | 0.0051211 | 3.0238e-06
2016 | 2016-03-24 | C | 1116 | 0.24376 | 0.0033745
2016 | 2016-03-24 | C | 4 | 0.002368 | 1.2095e-05
2016 | 2016-03-24 | C | 28 | 0.0034642 | 8.4665e-05
2016 | 2016-03-24 | C | 1 | 0.00058258 | 3.0238e-06
2016 | 2016-03-24 | C | 1 | 0.00063131 | 3.0238e-06
2016 | 2016-03-24 | C | 11 | 0.014882 | 3.3261e-05
2016 | 2016-03-24 | C | 4 | 0.0014198 | 1.2095e-05
2016 | 2016-03-24 | C | 1 | 5.342e-05 | 3.0238e-06
2016 | 2016-03-24 | C | 1 | 0.0010136 | 3.0238e-06
2016 | 2016-03-24 | C | 1 | 0.00025279 | 3.0238e-06
2016 | 2016-03-24 | C | 2 | 0.0016345 | 6.0475e-06
2016 | 2016-03-24 | C | 3 | 0.0018599 | 9.0713e-06
2016 | 2016-03-24 | C | 1 | 0.00031981 | 3.0238e-06
2016 | 2016-03-24 | C | 1 | 0.0012692 | 3.0238e-06
2016 | 2016-03-24 | C | 586 | 0.2772 | 0.0017719
2016 | 2016-03-24 | C | 297 | 0.057603 | 0.00089806
2016 | 2016-03-24 | C | 319 | 0.11202 | 0.00096458
2016 | 2016-03-24 | C | 16 | 0.0015667 | 4.838e-05
2016 | 2016-03-24 | C | 482 | 0.10541 | 0.0014575
2016 | 2016-03-24 | C | 2 | 8.4665e-05 | 6.0475e-06
2016 | 2016-03-24 | C | 1 | 0.0026276 | 3.0238e-06
2016 | 2016-03-24 | C | 3 | 0.0018026 | 9.0713e-06
2016 | 2016-03-24 | C | 1409 | 0.14537 | 0.0042605
2016 | 2016-03-25 | C | 1 | 0.00077045 | 3.0238e-06
2016 | 2016-03-25 | C | 1 | 0.0020168 | 3.0238e-06
2016 | 2016-03-25 | C | 297 | 0.075909 | 0.00089806
2016 | 2016-03-25 | C | 178 | 0.054374 | 0.00053823
2016 | 2016-03-25 | C | 82 | 0.056742 | 0.00024795
2016 | 2016-03-25 | C | 2 | 0.00088737 | 6.0475e-06
2016 | 2016-03-25 | C | 11 | 0.0047869 | 3.3261e-05
2016 | 2016-03-25 | C | 1 | 0.00050265 | 3.0238e-06
2016 | 2016-03-25 | C | 1 | 0.00099376 | 3.0238e-06
2016 | 2016-03-25 | C | 1 | 0.00011793 | 3.0238e-06
2016 | 2016-03-25 | C | 10 | 0.00071462 | 3.0238e-05
2016 | 2016-03-25 | C | 355 | 0.024796 | 0.0010734
2016 | 2016-03-24 | C | 15 | 0.063021 | 4.5356e-05
2016 | 2016-03-25 | C | 41 | 0.041637 | 0.00012397
2016 | 2016-03-25 | C | 5 | 0.0032883 | 1.5119e-05
2016 | 2016-03-25 | C | 187 | 0.061045 | 0.00056544
2016 | 2016-03-26 | C | 474 | 0.096814 | 0.0014333
2016 | 2016-03-26 | C | 362 | 0.050172 | 0.0010946
2016 | 2016-03-26 | C | 2 | 0.00065323 | 6.0475e-06
2016 | 2016-03-27 | C | 6 | 0.0019104 | 1.8143e-05
2016 | 2016-03-27 | C | 2 | 0.00043547 | 6.0475e-06
2016 | 2016-03-27 | C | 2 | 0.00097436 | 6.0475e-06
2016 | 2016-03-27 | C | 4 | 0.01091 | 1.2095e-05
2016 | 2016-03-28 | C | 6 | 0.002422 | 1.8143e-05
2016 | 2016-03-28 | C | 6 | 0.00083879 | 1.8143e-05
2016 | 2016-03-28 | C | 1750 | 0.085129 | 0.0052916
2016 | 2016-03-28 | C | 1005 | 0.0090895 | 0.0030389
2016 | 2016-03-28 | C | 1 | 0.00029462 | 3.0238e-06
2016 | 2016-03-28 | C | 1 | 0.00034829 | 3.0238e-06
2016 | 2016-03-29 | C | 30 | 0.014333 | 9.0713e-05
2016 | 2016-03-29 | C | 10 | 0.0027884 | 3.0238e-05
2016 | 2016-03-29 | C | 3 | 0.0054128 | 9.0713e-06
2016 | 2016-03-24 | C | 316 | 0.025762 | 0.00095551
2016 | 2016-03-29 | C | 4 | 0.0017187 | 1.2095e-05
2016 | 2016-03-29 | C | 86 | 0.014822 | 0.00026004
2016 | 2016-03-29 | C | 8 | 8.3859e-05 | 2.419e-05
2016 | 2016-03-29 | C | 4 | 0.00037495 | 1.2095e-05
2016 | 2016-03-30 | B | 255 | 0.38861 | 0.00077106
2016 | 2016-03-29 | C | 1 | 0.00034466 | 3.0238e-06
2016 | 2016-03-30 | C | 3 | 0 | 9.0713e-06
2016 | 2016-03-30 | C | 1 | 0.00036315 | 3.0238e-06
2016 | 2016-03-31 | C | 107 | 0.021647 | 0.00032354
2016 | 2016-03-31 | C | 2 | 7.8618e-05 | 6.0475e-06
2016 | 2016-03-31 | C | 8 | 0.010268 | 2.419e-05
2016 | 2016-03-31 | C | 5 | 0.0055657 | 1.5119e-05
2016 | 2016-03-31 | C | 1 | 0.0008527 | 3.0238e-06
2016 | 2016-03-31 | C | 23 | 0.0051233 | 6.9546e-05
2016 | 2016-03-31 | C | 119 | 0.049656 | 0.00035983
2016 | 2015-08-06 | B | 103 | 0.12339 | 0.00031145
2016 | 2015-07-16 | C | 1 | 0 | 3.0238e-06
2016 | 2015-07-16 | C | 1066 | 0.094605 | 0.0032233
2016 | 2015-07-16 | C | 1 | 0.00017235 | 3.0238e-06
2016 | 2015-07-16 | C | 1 | 0.00061483 | 3.0238e-06
2016 | 2015-07-16 | C | 61 | 0.0069046 | 0.00018445
2016 | 2015-07-17 | C | 5 | 0.00077449 | 1.5119e-05
2016 | 2015-07-17 | C | 1 | 0.00037318 | 3.0238e-06
2016 | 2015-07-17 | C | 1 | 0.00041174 | 3.0238e-06
2016 | 2015-07-17 | C | 293 | 0.16489 | 0.00088596
2016 | 2015-07-18 | C | 1 | 0.00037797 | 3.0238e-06
2016 | 2015-07-17 | C | 103 | 0.092733 | 0.00031145
2016 | 2015-07-18 | C | 30 | 0.013584 | 9.0713e-05
2016 | 2015-07-18 | C | 1773 | 2.0489 | 0.0053611
2016 | 2015-07-18 | C | 327 | 0.051922 | 0.00098877
2016 | 2015-07-18 | C | 143 | 0.018912 | 0.0004324
2016 | 2015-07-19 | C | 63 | 0.020483 | 0.0001905
2016 | 2015-07-18 | C | 4 | 0.00088858 | 1.2095e-05
2016 | 2015-07-18 | C | 867 | 0.6111 | 0.0026216
2016 | 2015-07-18 | C | 1023 | 0.54657 | 0.0030933
2016 | 2015-07-18 | C | 839 | 0.60372 | 0.0025369
2016 | 2015-07-18 | C | 4548 | 0.92993 | 0.013752
2016 | 2015-07-18 | C | 562 | 0.27388 | 0.0016994
2016 | 2015-07-19 | C | 29 | 0.0035428 | 8.7689e-05
2016 | 2015-07-18 | C | 149 | 0 | 0.00045054
2016 | 2015-07-18 | C | 141 | 0.11784 | 0.00042635
2016 | 2015-07-18 | C | 420 | 0.42009 | 0.00127
2016 | 2015-07-18 | C | 1 | 0.0013506 | 3.0238e-06
2016 | 2015-07-18 | C | 11 | 0.0048862 | 3.3261e-05
2016 | 2015-07-18 | C | 2 | 0.001143 | 6.0475e-06
2016 | 2015-07-18 | C | 1 | 0.00020758 | 3.0238e-06
2016 | 2015-07-18 | C | 3 | 0.0010241 | 9.0713e-06
2016 | 2015-07-18 | C | 2 | 0.0010427 | 6.0475e-06
2016 | 2015-07-18 | C | 28 | 0.0013546 | 8.4665e-05
2016 | 2015-07-18 | C | 7 | 0.008934 | 2.1166e-05
2016 | 2015-07-18 | C | 4 | 0.0013524 | 1.2095e-05
2016 | 2015-07-18 | C | 236 | 0.047803 | 0.00071361
2016 | 2015-07-18 | C | 472 | 0.0015937 | 0.0014272
2016 | 2015-07-18 | C | 472 | 0.19608 | 0.0014272
2016 | 2015-07-19 | C | 3 | 0.01534 | 9.0713e-06
2016 | 2015-07-18 | C | 2 | 0.0054005 | 6.0475e-06
2016 | 2015-07-18 | C | 301 | 0.1689 | 0.00091015
2016 | 2015-07-19 | C | 154 | 0.18515 | 0.00046566
2016 | 2015-07-18 | C | 521 | 0 | 0.0015754
2016 | 2015-07-19 | C | 212 | 0.18934 | 0.00064104
2016 | 2015-07-19 | C | 105 | 0 | 0.00031749
2016 | 2015-07-19 | C | 296 | 0.13125 | 0.00089503
2016 | 2015-07-19 | C | 9 | 0.0026434 | 2.7214e-05
2016 | 2015-07-19 | C | 8 | 0.00254 | 2.419e-05
2016 | 2015-07-19 | C | 2 | 0.0015723 | 6.0475e-06
2016 | 2015-07-19 | C | 1 | 0.00090733 | 3.0238e-06
2016 | 2015-07-19 | C | 4 | 0.00075271 | 1.2095e-05
2016 | 2015-07-19 | C | 370 | 0.17128 | 0.0011188
2016 | 2015-07-19 | C | 29 | 0.015959 | 8.7689e-05
2016 | 2015-07-19 | C | 1 | 0.000395 | 3.0238e-06
2016 | 2015-07-20 | C | 11 | 0.032264 | 3.3261e-05
2016 | 2015-07-20 | C | 15 | 0.0060877 | 4.5356e-05
2016 | 2015-07-20 | C | 75 | 0.033564 | 0.00022678
2016 | 2015-07-20 | C | 62 | 0.032952 | 0.00018747
2016 | 2015-07-20 | C | 28 | 0.014886 | 8.4665e-05
2016 | 2015-07-20 | C | 26 | 0.0041694 | 7.8618e-05
2016 | 2015-07-20 | C | 33 | 0.0021953 | 9.9784e-05
2016 | 2015-07-20 | C | 4 | 0.00076602 | 1.2095e-05
2016 | 2015-07-20 | C | 1 | 0.0004517 | 3.0238e-06
2016 | 2015-07-20 | C | 58 | 0.10912 | 0.00017538
2016 | 2015-07-21 | C | 296 | 0.0082045 | 0.00089503
2016 | 2015-07-21 | C | 33 | 0.011848 | 9.9784e-05
2016 | 2015-07-21 | C | 1 | 0.00017956 | 3.0238e-06
2016 | 2015-07-21 | C | 5 | 0.0011765 | 1.5119e-05
2016 | 2015-07-21 | C | 149 | 0.038601 | 0.00045054
2016 | 2015-07-22 | C | 1 | 8.1642e-05 | 3.0238e-06
2016 | 2015-07-21 | C | 2 | 0.00051187 | 6.0475e-06
2016 | 2015-07-21 | C | 139 | 0.041526 | 0.0004203
2016 | 2015-07-22 | C | 37 | 0.0055129 | 0.00011188
2016 | 2015-07-22 | C | 7 | 0.0011006 | 2.1166e-05
2016 | 2015-07-22 | C | 1 | 0.00056454 | 3.0238e-06
2016 | 2015-07-22 | C | 35 | 0.0068791 | 0.00010583
2016 | 2015-07-22 | C | 19 | 0.0069191 | 5.7451e-05
2016 | 2015-07-22 | C | 1 | 0.00023222 | 3.0238e-06
2016 | 2015-07-22 | C | 4 | 0.0049195 | 1.2095e-05
2016 | 2015-07-22 | C | 137 | 0.038077 | 0.00041426
2016 | 2015-07-22 | C | 19 | 0.0050969 | 5.7451e-05
2016 | 2015-07-22 | C | 5 | 0.0013456 | 1.5119e-05
2016 | 2015-07-23 | C | 770 | 0.19266 | 0.0023283
2016 | 2015-07-24 | C | 22 | 0.0081457 | 6.6523e-05
2016 | 2015-07-24 | C | 472 | 0.082452 | 0.0014272
2016 | 2015-07-24 | B | 68 | 0.050787 | 0.00020562
2016 | 2015-07-24 | C | 35 | 0.014181 | 0.00010583
2016 | 2015-07-20 | B | 3 | 0.00078678 | 9.0713e-06
2016 | 2015-07-24 | C | 46 | 0.08663 | 0.00013909
2016 | 2015-07-25 | B | 3 | 0.0012428 | 9.0713e-06
2016 | 2015-07-25 | C | 799 | 0.13354 | 0.002416
2016 | 2015-07-25 | C | 2 | 0.00040801 | 6.0475e-06
2016 | 2015-07-25 | C | 189 | 0 | 0.00057149
2016 | 2015-07-25 | C | 1 | 0.0003749 | 3.0238e-06
2016 | 2015-07-25 | C | 10 | 0.0014454 | 3.0238e-05
2016 | 2015-07-26 | C | 235 | 0.057973 | 0.00071058
2016 | 2015-07-26 | C | 1 | 0.0002159 | 3.0238e-06
2016 | 2015-07-26 | C | 1 | 0.00038734 | 3.0238e-06
2016 | 2015-07-27 | C | 1 | 0.0012063 | 3.0238e-06
2016 | 2015-07-27 | C | 1 | 0.00035338 | 3.0238e-06
2016 | 2015-07-27 | C | 1 | 0.00050205 | 3.0238e-06
2016 | 2015-07-27 | C | 1394 | 0.25695 | 0.0042151
2016 | 2015-07-28 | C | 4 | 0.00068715 | 1.2095e-05
2016 | 2015-07-28 | C | 7 | 0.0021611 | 2.1166e-05
2016 | 2015-07-28 | C | 189 | 0.00057149 | 0.00057149
2016 | 2015-07-28 | C | 38 | 0.0095052 | 0.0001149
2016 | 2015-07-28 | C | 1 | 0.00040528 | 3.0238e-06
2016 | 2015-07-28 | C | 3 | 0 | 9.0713e-06
2016 | 2015-07-28 | B | 41 | 0.054741 | 0.00012397
2016 | 2015-07-28 | C | 3 | 3.7343e-05 | 9.0713e-06
2016 | 2015-07-28 | C | 44 | 0.0011553 | 0.00013305
2016 | 2015-07-28 | C | 47 | 0.0017696 | 0.00014212
2016 | 2015-07-28 | C | 118 | 0.072788 | 0.0003568
2016 | 2015-07-28 | C | 113 | 0.064237 | 0.00034168
2016 | 2015-07-28 | C | 118 | 0.029445 | 0.0003568
2016 | 2015-07-28 | C | 3 | 0.0011619 | 9.0713e-06
2016 | 2015-07-29 | C | 471 | 0.031568 | 0.0014242
2016 | 2015-07-29 | C | 1230 | 0.080039 | 0.0037192
2016 | 2015-07-29 | C | 2 | 6.6321e-05 | 6.0475e-06
2016 | 2015-07-29 | C | 15 | 0.0022043 | 4.5356e-05
2016 | 2015-07-29 | C | 9544 | 1.493 | 0.028859
2016 | 2015-07-29 | C | 1 | 0.00018873 | 3.0238e-06
2017 | 2016-04-01 | B | 9 | 0.004848 | 2.7084e-05
2017 | 2016-04-01 | B | 22 | 6.6e-05 | 6.6206e-05
2017 | 2016-04-02 | B | 16 | 0.009533 | 4.8149e-05
2017 | 2016-04-04 | B | 17 | 0.006432 | 5.1156e-05
2017 | 2016-04-05 | B | 50 | 0.042428 | 0.00015046
2017 | 2016-04-05 | B | 64 | 0.083196 | 0.00019258
2017 | 2016-04-06 | B | 23 | 0.025607 | 6.9209e-05
2017 | 2016-04-12 | B | 9 | 0.010046 | 2.708e-05
2017 | 2016-04-04 | B | 3 | 0.00092 | 9.0274e-06
2017 | 2016-04-07 | B | 9 | 0.004879 | 2.7082e-05
2017 | 2016-04-06 | B | 53 | 0.062198 | 0.00015948
2017 | 2016-04-04 | B | 4 | 0.002371 | 1.2037e-05
2017 | 2016-04-05 | B | 20 | 0.020582 | 6.0183e-05
2017 | 2016-04-07 | B | 28 | 0.028567 | 8.4254e-05
2017 | 2016-04-08 | B | 48 | 0.021628 | 0.00014443
2017 | 2016-04-05 | B | 37 | 0.009463 | 0.00011134
2017 | 2016-04-20 | B | 441 | 0.17726 | 0.0024249
2017 | 2016-04-11 | B | 1 | 0.000855 | 3.0089e-06
2017 | 2016-04-08 | B | 15 | 0.00686 | 4.5136e-05
2017 | 2016-04-09 | B | 1 | 0.000592 | 3.0089e-06
2017 | 2016-04-04 | B | 3 | 0.000758 | 9.0274e-06
2017 | 2016-04-12 | B | 133 | 0.11725 | 0.00040018
2017 | 2016-04-07 | B | 41 | 0.027018 | 0.00012337
2017 | 2016-04-11 | B | 53 | 0.045449 | 0.00015947
2017 | 2016-04-12 | B | 19 | 0.024468 | 5.7169e-05
2017 | 2016-04-11 | B | 36 | 0.035745 | 0.00010832
2017 | 2016-04-07 | B | 132 | 0.15769 | 0.0003972
2017 | 2016-04-13 | B | 1 | 0.000186 | 3.0088e-06
2017 | 2016-04-12 | B | 12 | 0.004152 | 3.6106e-05
2017 | 2016-04-05 | B | 135 | 0.01828 | 0.00040623
2017 | 2016-04-05 | B | 1 | 0.000848 | 3.0091e-06
2017 | 2016-04-11 | B | 8 | 0.002166 | 2.4071e-05
2017 | 2016-04-15 | B | 19 | 0.012576 | 5.7167e-05
2017 | 2016-04-13 | B | 1 | 0.000974 | 3.0088e-06
2017 | 2016-04-12 | B | 362 | 0.34439 | 0.0010892
2017 | 2016-04-06 | B | 221 | 0.20493 | 0.00066501
2017 | 2016-04-13 | B | 28 | 0.025442 | 8.4248e-05
2017 | 2016-04-14 | B | 11 | 0.009753 | 3.3097e-05
2017 | 2016-04-12 | B | 1 | 0.000306 | 3.0088e-06
2017 | 2016-04-12 | B | 9 | 0.001083 | 2.708e-05
2017 | 2016-04-13 | B | 8 | 0.000505 | 2.4071e-05
2017 | 2016-04-13 | B | 87 | 0.093456 | 0.00026177
2017 | 2016-04-07 | B | 11 | 0.012779 | 3.31e-05
2017 | 2016-04-07 | B | 125 | 0.13861 | 0.00037613
2017 | 2016-04-08 | B | 48 | 0.043041 | 0.00014443
2017 | 2016-04-16 | B | 3 | 0.002557 | 9.0262e-06
2017 | 2016-04-15 | B | 9 | 0.003628 | 2.7079e-05
2017 | 2016-04-14 | B | 24 | 0.003105 | 7.2212e-05
2017 | 2016-04-19 | B | 22 | 0.012044 | 6.619e-05
2017 | 2016-04-19 | B | 195 | 0.22278 | 0.00058668
2017 | 2016-04-11 | B | 23 | 0.013633 | 6.9205e-05
2017 | 2016-04-12 | B | 77 | 0.068346 | 0.00023168
2017 | 2016-04-13 | B | 48 | 0.040296 | 0.00014442
2017 | 2016-04-15 | B | 48 | 0.036827 | 0.00014442
2017 | 2016-04-13 | B | 5 | 0.002286 | 1.5044e-05
2017 | 2016-04-20 | B | 49 | 0.053955 | 0.00014742
2017 | 2016-04-15 | B | 27 | 0.020693 | 8.1237e-05
2017 | 2016-04-06 | B | 47 | 0.023477 | 0.00014143
2017 | 2016-04-20 | B | 1 | 0.000652 | 3.0085e-06
2017 | 2016-04-20 | B | 14 | 0.008761 | 4.212e-05
2017 | 2016-04-21 | B | 23 | 0.021371 | 6.9196e-05
2017 | 2016-04-22 | B | 23 | 0.016964 | 6.9195e-05
2017 | 2016-04-26 | B | 23 | 0.022348 | 6.9191e-05
2017 | 2016-04-14 | B | 29 | 0.01588 | 8.7256e-05
2017 | 2016-04-19 | B | 16 | 0.004284 | 4.8138e-05
2017 | 2016-04-26 | B | 66 | 0.054203 | 0.00019855
2017 | 2016-04-18 | B | 31 | 0.031618 | 9.3269e-05
2017 | 2016-04-18 | B | 27 | 0.033874 | 8.1234e-05
2017 | 2016-04-21 | B | 36 | 0.025737 | 0.00010831
2017 | 2016-04-21 | B | 61 | 0.075038 | 0.00018352
2017 | 2016-04-06 | B | 5 | 0.002888 | 1.5046e-05
2017 | 2016-04-19 | B | 3 | 0.002601 | 9.0259e-06
2017 | 2016-04-22 | B | 75 | 0.041968 | 0.00022564
2017 | 2016-04-22 | B | 2 | 0.001596 | 6.0169e-06
2017 | 2016-04-01 | C | 2496 | 0.020531 | 0.0075114
2017 | 2016-04-01 | C | 256 | 0.006604 | 0.00031298
2017 | 2016-04-21 | B | 7 | 0.00467 | 2.106e-05
2017 | 2016-04-21 | B | 21 | 0.01154 | 6.3179e-05
2017 | 2016-04-18 | B | 45 | 0.0322 | 0.00013539
2017 | 2016-04-19 | B | 48 | 0.029893 | 0.00014441
2017 | 2016-04-26 | B | 58 | 0.058756 | 0.00017448
2017 | 2016-04-27 | B | 57 | 0.073904 | 0.00017147
2017 | 2016-04-26 | B | 2 | 0.001486 | 6.0166e-06
2017 | 2016-04-05 | B | 101 | 0.12065 | 0.00030392
2017 | 2016-04-07 | B | 71 | 0.07563 | 0.00021364
2017 | 2016-04-01 | C | 31 | 0.000743 | 9.3291e-05
2017 | 2016-04-02 | C | 51 | 0.007903 | 0.00015347
2017 | 2016-04-02 | C | 8 | 0.002902 | 2.4074e-05
2017 | 2016-04-02 | C | 83 | 0.067891 | 0.00043635
2017 | 2016-04-02 | C | 29 | 0.034862 | 8.7269e-05
2017 | 2016-04-02 | C | 10 | 0.003871 | 3.0093e-05
2017 | 2016-04-03 | C | 51 | 0.005064 | 0.00015347
2017 | 2016-04-03 | C | 4 | 0.001087 | 1.2037e-05
2017 | 2016-04-03 | C | 16 | 0.001107 | 4.8147e-05
2017 | 2016-04-03 | C | 52 | 0.005946 | 0.00015648
2017 | 2016-04-03 | C | 508 | 0.064295 | 0.0014956
2017 | 2016-04-03 | C | 9 | 0.007742 | 2.7083e-05
2017 | 2016-04-03 | C | 2 | 0.000228 | 6.0184e-06
2017 | 2016-04-04 | B | 9 | 0.008314 | 2.7082e-05
2017 | 2016-04-19 | B | 28 | 0.017438 | 8.4242e-05
2017 | 2016-04-21 | B | 7 | 0.005875 | 2.106e-05
2017 | 2016-04-27 | B | 37 | 0.039994 | 0.00011131
2017 | 2016-04-21 | B | 25 | 0.004146 | 7.5213e-05
2017 | 2016-04-27 | B | 1 | 0.00077 | 3.0082e-06
2017 | 2016-04-27 | B | 9 | 0.009886 | 2.7074e-05
2017 | 2016-04-27 | B | 12 | 0.009005 | 3.6099e-05
2017 | 2016-04-22 | B | 3 | 0.001101 | 9.0254e-06
2017 | 2016-04-22 | B | 8 | 0.000577 | 2.4068e-05
2017 | 2016-04-22 | B | 2 | 0.000794 | 6.0169e-06
2017 | 2016-04-26 | B | 1 | 0.000595 | 3.0083e-06
2017 | 2016-04-22 | B | 21 | 0.004801 | 6.3178e-05
2017 | 2016-04-26 | B | 1 | 0.000249 | 3.0083e-06
2017 | 2016-04-26 | B | 4 | 0.002815 | 1.2033e-05
2017 | 2016-04-27 | B | 11 | 0.006849 | 3.3091e-05
2017 | 2016-04-04 | C | 317 | 0.073623 | 0.0018205
2017 | 2016-04-20 | B | 43 | 0.042361 | 0.00012937
2017 | 2016-04-21 | B | 3 | 0.003086 | 9.0256e-06
2017 | 2016-04-27 | B | 45 | 0.049816 | 0.00013537
2017 | 2016-04-05 | C | 4 | 0.087168 | 1.2037e-05
2017 | 2016-04-05 | C | 1 | 0.00133 | 3.0091e-06
2017 | 2016-04-29 | B | 3 | 0.001173 | 9.0245e-06
2017 | 2016-04-29 | B | 2 | 0.000872 | 6.0163e-06
2017 | 2016-04-06 | C | 1556 | 0.097877 | 0.0046822
2017 | 2016-04-06 | C | 6 | 0.001209 | 1.8055e-05
2017 | 2016-04-29 | B | 9 | 0.009897 | 2.7074e-05
2017 | 2016-04-06 | C | 67 | 0.012859 | 0.00020161
2017 | 2016-04-06 | C | 4 | 0.002792 | 1.2036e-05
2017 | 2016-05-02 | B | 36 | 0.030104 | 0.00010829
2017 | 2016-04-22 | B | 14 | 0.014194 | 4.2119e-05
2017 | 2016-04-28 | B | 131 | 0.13289 | 0.00039408
2017 | 2016-04-29 | B | 4 | 0.000144 | 1.2033e-05
2017 | 2016-04-06 | C | 3 | 0.0007 | 9.0273e-06
2017 | 2016-04-06 | C | 6 | 0.000938 | 1.8055e-05
2017 | 2016-04-07 | C | 1546 | 0.38581 | 0.0055758
2017 | 2016-04-26 | B | 76 | 0.090297 | 0.00022863
2017 | 2016-04-07 | C | 2 | 0 | 6.0181e-06
2017 | 2016-04-29 | B | 75 | 0.022335 | 0.00022561
2017 | 2016-04-29 | B | 1 | 0.000105 | 3.0081e-06
2017 | 2016-04-08 | C | 1268 | 0.31497 | 0.0040141
2017 | 2016-04-08 | C | 115 | 0.057494 | 0.00034604
2017 | 2016-04-08 | C | 1 | 0.000388 | 3.009e-06
2017 | 2016-04-08 | C | 144 | 0.007161 | 0.0004333
2017 | 2016-04-27 | B | 79 | 0.052488 | 0.00036099
2017 | 2016-04-08 | C | 1 | 0.000444 | 3.009e-06
2017 | 2016-04-08 | C | 1000 | 0.20509 | 0.003009
2017 | 2016-05-03 | B | 92 | 0.049558 | 0.00027674
2017 | 2016-04-09 | C | 2 | 0.000789 | 6.0179e-06
2017 | 2016-04-09 | C | 1 | 0.000302 | 3.0089e-06
2017 | 2016-04-09 | C | 3 | 0.001516 | 9.0269e-06
2017 | 2016-04-10 | C | 1 | 0.000427 | 3.0089e-06
2017 | 2016-04-11 | C | 2 | 8.1e-05 | 6.0178e-06
2017 | 2016-04-08 | C | 3 | 0.000442 | 9.0271e-06
2017 | 2016-05-03 | B | 79 | 0.047185 | 0.00023763
2017 | 2016-04-27 | B | 393 | 0.39251 | 0.0011822
2017 | 2016-04-11 | C | 1 | 0.000444 | 3.0089e-06
2017 | 2016-04-22 | B | 22 | 0.0045 | 0.00013237
2017 | 2016-04-11 | C | 39 | 0.00487 | 0.00011735
2017 | 2016-04-13 | B | 4 | 0.002551 | 1.2035e-05
2017 | 2016-04-29 | B | 111 | 0.002587 | 0.00033391
2017 | 2016-04-11 | C | 4 | 0.000929 | 1.2036e-05
2017 | 2016-04-28 | B | 15 | 0.017237 | 4.5123e-05
2017 | 2016-04-12 | C | 658 | 0.076916 | 0.0019798
2017 | 2016-04-21 | B | 5 | 0.002587 | 1.5043e-05
2017 | 2016-04-12 | C | 2644 | 0.33834 | 0.0079555
2017 | 2016-04-12 | C | 3 | 0.002247 | 9.0266e-06
2017 | 2016-04-17 | B | 1 | 0.000167 | 3.0087e-06
2017 | 2016-04-12 | C | 255 | 0.051176 | 0.00076726
2017 | 2016-04-13 | C | 1 | 0.000363 | 3.0088e-06
2017 | 2016-04-13 | C | 8 | 0.002753 | 2.4071e-05
2017 | 2016-04-26 | B | 29 | 0.005333 | 8.7241e-05
2017 | 2016-05-02 | B | 28 | 0.02055 | 8.4225e-05
2017 | 2016-04-13 | C | 1 | 0.00013 | 3.0088e-06
2017 | 2016-05-02 | B | 42 | 0.031079 | 0.00012634
2017 | 2016-05-04 | B | 302 | 0.24913 | 0.00062264
2017 | 2016-05-04 | B | 9 | 0.010205 | 2.7071e-05
2017 | 2016-05-02 | B | 38 | 0.038177 | 0.00011431
2017 | 2016-05-04 | B | 37 | 0.009682 | 0.00011129
2017 | 2016-04-13 | C | 3 | 0.001281 | 9.0265e-06
2017 | 2016-04-14 | C | 923 | 0.080426 | 0.0027771
2017 | 2016-05-02 | B | 10 | 0.002165 | 3.008e-05
2017 | 2016-04-30 | B | 46 | 0.033094 | 0.00013837
2017 | 2016-05-03 | B | 70 | 0.048639 | 0.00021056
2017 | 2016-05-03 | B | 31 | 0.024151 | 9.3248e-05
2017 | 2016-04-14 | C | 700 | 0.13534 | 0.0021122
2017 | 2016-05-03 | B | 5 | 0.001173 | 1.504e-05
2017 | 2016-05-03 | B | 2 | 0.000661 | 6.0159e-06
2017 | 2016-05-04 | B | 6 | 0.005811 | 1.8048e-05
2017 | 2016-05-05 | B | 208 | 0.018143 | 0.00062564
2017 | 2016-05-03 | B | 37 | 0.035152 | 0.0001113
2017 | 2016-05-05 | B | 3 | 0.00268 | 9.0236e-06
2017 | 2016-05-01 | B | 95 | 0.14117 | 0.00028577
2017 | 2016-05-06 | B | 2 | 0.001906 | 6.0157e-06
2017 | 2016-05-02 | B | 2 | 0.000854 | 6.016e-06
2017 | 2016-05-02 | B | 1 | 0.000282 | 3.008e-06
2017 | 2016-05-05 | B | 2 | 0.001726 | 6.0157e-06
2017 | 2016-05-05 | B | 28 | 0.000421 | 8.4221e-05
2017 | 2016-05-06 | B | 2 | 0.00107 | 6.0157e-06
2017 | 2016-05-02 | B | 5 | 0.002361 | 1.504e-05
2017 | 2016-05-09 | B | 2 | 0.000553 | 6.0154e-06
2017 | 2016-05-09 | B | 19 | 0.018115 | 5.7147e-05
2017 | 2016-05-09 | B | 8 | 0.003705 | 2.4062e-05
2017 | 2016-05-05 | B | 4 | 0.001287 | 1.2031e-05
2017 | 2016-05-09 | B | 66 | 0.056575 | 0.00019851
2017 | 2016-05-05 | B | 7 | 0.000357 | 2.1055e-05
2017 | 2016-05-09 | B | 27 | 0.017978 | 8.1208e-05
2017 | 2016-05-06 | B | 3 | 0.002174 | 9.0235e-06
2017 | 2016-05-02 | B | 41 | 0.018992 | 0.00012333
2017 | 2016-04-15 | C | 343 | 0.034881 | 0.001032
2017 | 2016-05-03 | B | 17 | 0.012374 | 5.1136e-05
2017 | 2016-04-15 | C | 479 | 0.14913 | 0.0014412
2017 | 2016-04-15 | C | 2030 | 0.009405 | 0.0053947
2017 | 2016-05-04 | B | 17 | 0.015749 | 5.1135e-05
2017 | 2016-05-12 | B | 15 | 0.021835 | 4.5114e-05
2017 | 2016-04-15 | C | 3 | 0.000451 | 9.0263e-06
2017 | 2016-05-11 | B | 34 | 0.012884 | 0.00010226
2017 | 2016-05-17 | B | 17 | 0.019193 | 5.1125e-05
2017 | 2016-05-05 | B | 1 | 0.000487 | 3.0078e-06
2017 | 2016-05-03 | B | 39 | 0.038126 | 0.00011731
2017 | 2016-05-10 | B | 39 | 0.006686 | 0.0001173
2017 | 2016-05-06 | B | 30 | 0.040064 | 9.0236e-05
2017 | 2016-05-06 | B | 2 | 0.001245 | 6.0157e-06
2017 | 2016-05-04 | B | 1 | 0.001073 | 3.0079e-06
2017 | 2016-05-08 | B | 46 | 0.022651 | 0.00013836
2017 | 2016-05-09 | B | 26 | 0.020488 | 7.8201e-05
2017 | 2016-04-15 | C | 1 | 0.000377 | 3.0087e-06
2017 | 2016-04-15 | C | 8 | 9.6e-05 | 2.407e-05
2017 | 2016-04-16 | C | 41 | 0.006897 | 0.00012336
2017 | 2016-04-16 | C | 306 | 0.12669 | 0.0015525
2017 | 2016-04-16 | C | 26 | 0.009787 | 7.8227e-05
2017 | 2016-04-16 | C | 153 | 0.009194 | 0.00046034
2017 | 2016-04-16 | C | 6 | 0.001597 | 1.8052e-05
2017 | 2016-04-16 | C | 48 | 0.007509 | 0.00014442
2017 | 2016-04-16 | C | 1 | 0.000231 | 3.0087e-06
2017 | 2016-04-16 | C | 5 | 0.002987 | 1.5044e-05
2017 | 2016-04-17 | C | 964 | 0.22198 | 0.0029004
2017 | 2016-04-17 | C | 543 | 0.050579 | 0.0016337
2017 | 2016-04-17 | C | 19 | 0.002515 | 5.7165e-05
2017 | 2016-04-17 | C | 218 | 0.21262 | 0.0006559
2017 | 2016-04-17 | C | 2832 | 0.1697 | 0.0024822
2017 | 2016-04-17 | C | 1 | 0.000115 | 3.0087e-06
2017 | 2016-05-11 | B | 26 | 0.020879 | 7.8198e-05
2017 | 2016-04-18 | C | 2 | 0.000523 | 6.0173e-06
2017 | 2016-05-12 | B | 46 | 0.041781 | 0.00013835
2017 | 2016-05-11 | B | 23 | 0.022412 | 6.9176e-05
2017 | 2016-05-12 | B | 10 | 0.00412 | 3.0076e-05
2017 | 2016-05-12 | B | 49 | 0.042443 | 0.00014737
2017 | 2016-05-16 | B | 20 | 0.022346 | 6.0148e-05
2017 | 2016-05-09 | B | 79 | 0.083808 | 0.00023761
2017 | 2016-04-18 | C | 1 | 0.000142 | 3.0086e-06
2017 | 2016-04-19 | C | 6 | 0.001145 | 1.8052e-05
2017 | 2016-04-19 | C | 31 | 0.005689 | 9.3268e-05
2017 | 2016-05-19 | B | 6 | 0.005449 | 1.8044e-05
2017 | 2016-05-18 | B | 14 | 0.014188 | 4.2103e-05
2017 | 2016-05-06 | B | 1 | 0.000637 | 3.0078e-06
2017 | 2016-04-19 | C | 304 | 0 | 0.00091463
2017 | 2016-04-22 | B | 1 | 0.000341 | 3.0084e-06
2017 | 2016-04-19 | C | 110 | 0.12219 | 0.00033095
2017 | 2016-05-10 | B | 1 | 6.9e-05 | 3.0076e-06
2017 | 2016-04-19 | C | 24 | 0.00851 | 7.2207e-05
2017 | 2016-04-19 | C | 42 | 0.006709 | 0.00012636
2017 | 2016-04-20 | C | 3 | 0.001735 | 9.0257e-06
2017 | 2016-04-20 | C | 1 | 0.000561 | 3.0085e-06
2017 | 2016-04-20 | C | 18 | 0.008757 | 5.4154e-05
2017 | 2016-04-20 | C | 31 | 0.027314 | 9.3266e-05
2017 | 2016-05-04 | B | 226 | 0.075605 | 0.0006798
2017 | 2016-05-10 | B | 37 | 0.015357 | 0.00011128
2017 | 2016-04-20 | C | 28 | 0.011854 | 0.00011733
2017 | 2016-05-11 | B | 43 | 0.03272 | 0.00012933
2017 | 2016-05-12 | B | 1 | 0.000499 | 3.0075e-06
2017 | 2016-05-03 | B | 29 | 0.032886 | 8.7232e-05
2017 | 2016-05-05 | B | 29 | 0.032327 | 8.7229e-05
2017 | 2016-04-21 | C | 191 | 0.091557 | 0.00057463
2017 | 2016-04-21 | C | 1 | 0.000593 | 3.0085e-06
2017 | 2016-04-21 | C | 3 | 0.001487 | 9.0256e-06
2017 | 2016-05-11 | B | 19 | 0.022058 | 5.7145e-05
2017 | 2016-04-28 | B | 4 | 0.003754 | 1.2033e-05
2017 | 2016-04-21 | C | 3 | 0.000379 | 9.0256e-06
2017 | 2016-05-13 | B | 126 | 0.15651 | 0.00037895
2017 | 2016-05-10 | B | 29 | 0.028957 | 8.7223e-05
2017 | 2016-05-19 | B | 29 | 0.02939 | 8.7211e-05
2017 | 2016-05-24 | B | 6 | 0.005755 | 1.8042e-05
2017 | 2016-05-10 | B | 2 | 0.003001 | 6.0153e-06
2017 | 2016-05-10 | B | 17 | 0.016055 | 5.1131e-05
2017 | 2016-05-16 | B | 42 | 0.031451 | 0.00012631
2017 | 2016-05-16 | B | 7 | 0.003831 | 2.1052e-05
2017 | 2016-05-16 | B | 32 | 0.001636 | 9.6237e-05
2017 | 2016-05-16 | B | 4 | 0.000324 | 1.203e-05
2017 | 2016-04-22 | C | 1 | 0.000643 | 3.0084e-06
2017 | 2016-05-12 | B | 19 | 0.015486 | 5.7144e-05
2017 | 2016-05-16 | B | 2 | 0.000493 | 6.0148e-06
2017 | 2016-05-16 | B | 4 | 0.000685 | 1.203e-05
2017 | 2016-05-17 | B | 362 | 0.31403 | 0.0010887
2017 | 2016-05-27 | B | 42 | 0.033087 | 0.00012629
2017 | 2016-05-04 | B | 1 | 0.001008 | 3.0079e-06
2017 | 2016-05-04 | B | 67 | 0.063281 | 0.00020153
2017 | 2016-04-22 | C | 502 | 0.64497 | 0.0015103
2017 | 2016-04-24 | C | 255 | 0.034577 | 0.00076714
2017 | 2016-04-24 | C | 212 | 0 | 3.6101e-05
2017 | 2016-04-24 | C | 6 | 0.002152 | 1.805e-05
2017 | 2016-04-24 | C | 4 | 0.000663 | 1.2034e-05
2017 | 2016-04-24 | C | 529 | 0.11157 | 0.0015914
2017 | 2016-04-25 | C | 278 | 0.13435 | 0.00083632
2017 | 2016-04-25 | C | 1 | 0.000396 | 3.0083e-06
2017 | 2016-04-25 | C | 278 | 0.062686 | 0.00083632
2017 | 2016-04-25 | C | 24 | 0.004263 | 7.2201e-05
2017 | 2016-04-25 | C | 700 | 0.084314 | 0.0023766
2017 | 2016-04-25 | C | 455 | 0.14561 | 0.0013688
2017 | 2016-04-25 | C | 1 | 0.000365 | 3.0083e-06
2017 | 2016-04-25 | C | 254 | 0.038934 | 0.00076412
2017 | 2016-04-26 | C | 2 | 0.001089 | 6.0166e-06
2017 | 2016-04-25 | C | 9 | 0.002524 | 2.7075e-05
2017 | 2016-04-25 | C | 15 | 0.004435 | 4.5125e-05
2017 | 2016-04-27 | C | 7 | 0.003053 | 2.1058e-05
2017 | 2016-04-26 | C | 24 | 0.004818 | 7.2199e-05
2017 | 2016-04-26 | C | 1131 | 0.21948 | 0.0034024
2017 | 2016-05-18 | B | 19 | 0.008856 | 5.7139e-05
2017 | 2016-05-27 | B | 29 | 0.020666 | 8.72e-05
2017 | 2016-05-25 | B | 3 | 0.001163 | 9.021e-06
2017 | 2016-04-26 | C | 4 | 0.004596 | 1.2033e-05
2017 | 2016-04-26 | C | 1 | 0.000183 | 3.0083e-06
2017 | 2016-04-26 | C | 3 | 0.001784 | 9.0249e-06
2017 | 2016-04-26 | C | 217 | 0.0485 | 0.0010409
2017 | 2016-05-24 | B | 10 | 0.011246 | 3.007e-05
2017 | 2016-04-27 | C | 264 | 0.024474 | 0.00079719
2017 | 2016-05-19 | B | 7 | 0.000147 | 2.1051e-05
2017 | 2016-05-19 | B | 2 | 0.00104 | 6.0145e-06
2017 | 2016-05-16 | B | 25 | 0.017142 | 7.5185e-05
2017 | 2016-05-10 | B | 129 | 0.15636 | 0.00038799
2017 | 2016-05-17 | B | 54 | 0.065771 | 0.0001624
2017 | 2016-05-18 | B | 54 | 0.056026 | 0.0001624
2017 | 2016-05-23 | B | 54 | 0.063816 | 0.00016238
2017 | 2016-05-24 | B | 54 | 0.056573 | 0.00016238
2017 | 2016-04-27 | C | 260 | 0.035239 | 0.0014771
2017 | 2016-04-28 | C | 951 | 0.064971 | 0.001832
2017 | 2016-04-28 | C | 90 | 0.017868 | 0.00027074
2017 | 2016-05-12 | B | 22 | 0.017137 | 6.6167e-05
2017 | 2016-05-30 | B | 54 | 0.056511 | 0.00016237
2017 | 2016-04-28 | C | 178 | 0 | 0.00053546
2017 | 2016-05-06 | B | 1 | 0.000496 | 3.0078e-06
2017 | 2016-04-28 | C | 414 | 0.05251 | 0.0012454
2017 | 2016-04-28 | C | 21 | 0.002563 | 6.3173e-05
2017 | 2016-04-28 | C | 5 | 0.001654 | 1.5041e-05
2017 | 2016-05-12 | B | 193 | 0.20157 | 0.00058046
2017 | 2016-05-31 | B | 54 | 0.064458 | 0.00016236
2017 | 2016-06-02 | B | 54 | 0.07095 | 0.00016236
2017 | 2016-04-28 | C | 1 | 0.000613 | 3.0082e-06
2017 | 2016-04-29 | C | 1 | 0.000339 | 3.0081e-06
2017 | 2016-04-29 | B | 66 | 0.000992 | 0.00019854
2017 | 2016-04-29 | C | 2 | 0.000832 | 6.0163e-06
2017 | 2016-04-29 | C | 13 | 0.005115 | 3.9106e-05
2017 | 2016-04-29 | C | 398 | 0.044822 | 0.0011973
2017 | 2016-05-23 | B | 30 | 0.030312 | 9.0213e-05
2017 | 2016-05-07 | B | 162 | 0.00164 | 0.00048726
2017 | 2016-04-29 | C | 115 | 0.028298 | 0.00040911
2017 | 2016-04-29 | C | 167 | 0.079693 | 0.00050236
2017 | 2016-04-30 | C | 18 | 0.000546 | 5.4146e-05
2017 | 2016-04-30 | C | 8 | 0.005005 | 2.4065e-05
2017 | 2016-04-30 | C | 37 | 0.00178 | 0.0001113
2017 | 2016-04-30 | C | 60 | 0.006346 | 0.00018049
2017 | 2016-04-30 | C | 10 | 0.006369 | 3.0081e-05
2017 | 2016-05-01 | C | 139 | 0.0347 | 0.00041812
2017 | 2016-05-01 | C | 629 | 0.13868 | 0.0037842
2017 | 2016-05-01 | C | 212 | 0.073617 | 0.00063771
2017 | 2016-05-01 | C | 28 | 0.010444 | 8.4226e-05
2017 | 2016-05-01 | C | 34 | 0.008509 | 3.6097e-05
2017 | 2016-05-01 | C | 499 | 0.10849 | 0.001501
2017 | 2016-05-01 | C | 19 | 0.01926 | 5.7154e-05
2017 | 2016-05-02 | C | 24 | 0.001732 | 7.2193e-05
2017 | 2016-05-19 | B | 24 | 0.020497 | 7.2175e-05
2017 | 2016-05-02 | C | 1 | 0.001013 | 3.008e-06
2017 | 2016-05-02 | C | 6 | 0.000667 | 1.8048e-05
2017 | 2016-05-13 | B | 3 | 0.000604 | 9.0226e-06
2017 | 2016-05-17 | B | 71 | 0.074946 | 0.00021352
2017 | 2016-05-02 | C | 98 | 0 | 0.00029479
2017 | 2016-05-18 | B | 116 | 0.044824 | 0.00055034
2017 | 2016-05-05 | B | 1362 | 0.10412 | 0.0028936
2017 | 2016-05-25 | B | 49 | 0.046855 | 0.00014734
2017 | 2016-05-26 | B | 49 | 0.039634 | 0.00014734
2017 | 2016-05-02 | C | 1 | 0.00029 | 3.008e-06
2017 | 2016-05-02 | C | 4 | 0.002667 | 1.2032e-05
2017 | 2016-05-02 | C | 2 | 0.000199 | 6.016e-06
2017 | 2016-05-20 | B | 24 | 0.011403 | 7.2174e-05
2017 | 2016-05-23 | B | 31 | 0.016033 | 9.322e-05
2017 | 2016-05-03 | C | 613 | 0.085801 | 0.0018439
2017 | 2016-05-25 | B | 7 | 0.000673 | 2.1049e-05
2017 | 2016-05-19 | B | 32 | 0.040129 | 9.6233e-05
2017 | 2016-05-27 | B | 1 | 0.000138 | 3.0069e-06
2017 | 2016-05-03 | C | 254 | 0.04246 | 0.0015281
2017 | 2016-05-31 | B | 270 | 0.29469 | 0.00081182
2017 | 2016-05-03 | C | 110 | 0.078792 | 0.00034592
2017 | 2016-05-03 | C | 254 | 0.047629 | 0.0014799
2017 | 2016-05-04 | C | 1 | 0.00033 | 3.0079e-06
2017 | 2016-05-21 | B | 221 | 0.29357 | 0.00066459
2017 | 2016-05-11 | B | 26 | 0.010322 | 7.8198e-05
2017 | 2016-05-04 | C | 37 | 0.012331 | 0.00011129
2017 | 2016-05-04 | C | 56 | 0.013697 | 0.00016844
2017 | 2016-05-05 | C | 4 | 0.000692 | 1.2031e-05
2017 | 2016-05-24 | B | 1 | 0.00073 | 3.007e-06
2017 | 2016-05-25 | B | 6 | 0.006657 | 1.8042e-05
2017 | 2016-05-05 | C | 659 | 0.046292 | 0.0020965
2017 | 2016-05-27 | B | 10 | 0.009682 | 3.0069e-05
2017 | 2016-05-05 | C | 375 | 0 | 9.0236e-06
2017 | 2016-05-05 | C | 186 | 0 | 6.0157e-06
2017 | 2016-05-20 | B | 66 | 0.005557 | 0.00019848
2017 | 2016-05-05 | C | 1 | 0.000495 | 3.0078e-06
2017 | 2016-05-05 | C | 2475 | 0.27966 | 0.0074445
2017 | 2016-05-05 | C | 1 | 0.000164 | 3.0078e-06
2017 | 2016-05-20 | B | 5 | 0.004811 | 1.5036e-05
2017 | 2016-05-06 | C | 541 | 0.18226 | 0.0016272
2017 | 2016-05-06 | C | 4 | 0.0003 | 1.2031e-05
2017 | 2016-05-06 | C | 422 | 0.044907 | 0.0012693
2017 | 2016-05-06 | C | 65 | 0.006563 | 7.5196e-05
2017 | 2016-05-06 | C | 6842 | 0.9128 | 0.02058
2017 | 2016-05-06 | C | 89 | 0.019876 | 0.0002677
2017 | 2016-05-07 | C | 422 | 0.04575 | 0.0012723
2017 | 2016-05-07 | C | 234 | 0.057147 | 0.0014077
2017 | 2016-05-08 | C | 205 | 0.001654 | 0.00061659
2017 | 2016-05-08 | C | 1 | 0.000155 | 3.0077e-06
2017 | 2016-05-08 | C | 599 | 0.15307 | 0.0018016
2017 | 2016-05-08 | C | 45 | 0.022332 | 0.00013535
2017 | 2016-05-08 | C | 61 | 0.011262 | 0.00018347
2017 | 2016-05-25 | B | 38 | 0.048905 | 0.00011427
2017 | 2016-05-09 | C | 78 | 0.024438 | 0.0002346
2017 | 2016-05-27 | B | 15 | 0.01556 | 4.5103e-05
2017 | 2016-05-26 | B | 15 | 0.009336 | 4.5104e-05
2017 | 2016-05-20 | B | 46 | 0.049502 | 0.00013833
2017 | 2016-05-24 | B | 202 | 0.16218 | 0.00060742
2017 | 2016-05-31 | B | 25 | 0.025331 | 7.5168e-05
2017 | 2016-05-24 | B | 10 | 0.000285 | 3.007e-05
2017 | 2016-05-09 | C | 1491 | 0.18139 | 0.0044845
2017 | 2016-05-10 | B | 8 | 0.009985 | 2.4061e-05
2017 | 2016-05-09 | C | 1 | 0.000321 | 3.0077e-06
2017 | 2016-05-23 | B | 217 | 0.00882 | 0.0013051
2017 | 2016-05-10 | C | 3 | 0.000697 | 9.023e-06
2017 | 2016-05-10 | C | 422 | 0.078141 | 0.0012692
2017 | 2016-05-10 | C | 1 | 9.9e-05 | 3.0076e-06
2017 | 2016-05-11 | C | 421 | 0.065607 | 0.0012662
2017 | 2016-05-11 | C | 1 | 0.000184 | 3.0076e-06
2017 | 2016-05-11 | C | 3 | 0.000897 | 9.0229e-06
2017 | 2016-05-11 | C | 1 | 0.000349 | 3.0076e-06
2017 | 2016-05-24 | B | 173 | 0.02601 | 0.0010404
2017 | 2016-05-11 | C | 1 | 0.000282 | 3.0076e-06
2017 | 2016-05-12 | B | 26 | 0.004302 | 7.8197e-05
2017 | 2016-05-11 | C | 116 | 0.000348 | 0.00034889
2017 | 2016-06-02 | B | 24 | 0.022441 | 7.2159e-05
2017 | 2016-06-07 | B | 24 | 0.022151 | 7.2154e-05
2017 | 2016-06-09 | B | 11 | 0.00959 | 3.3069e-05
2017 | 2016-06-14 | B | 49 | 0.057741 | 0.0001473
2017 | 2016-06-16 | B | 24 | 0.022076 | 7.2144e-05
2017 | 2016-06-21 | B | 118 | 0.1189 | 0.00035468
2017 | 2016-06-02 | B | 8 | 0.006686 | 2.4053e-05
2017 | 2016-05-11 | C | 322 | 0.29441 | 0.00096846
2017 | 2016-05-11 | C | 3 | 0.000563 | 9.0229e-06
2017 | 2016-05-12 | C | 6 | 0.003409 | 1.8045e-05
2017 | 2016-05-12 | C | 230 | 0.053188 | 0.00082408
2017 | 2016-06-01 | B | 4 | 0.000745 | 1.2027e-05
2017 | 2016-06-01 | B | 3 | 0.000378 | 9.02e-06
2017 | 2016-06-01 | B | 2 | 0.000252 | 6.0133e-06
2017 | 2016-06-03 | B | 7 | 0.001199 | 2.1046e-05
2017 | 2016-06-03 | B | 3 | 0.000423 | 9.0197e-06
2017 | 2016-06-03 | B | 3 | 0.000378 | 9.0197e-06
2017 | 2016-06-07 | B | 3 | 0.000514 | 9.0192e-06
2017 | 2016-06-01 | B | 82 | 0.10601 | 0.00024655
2017 | 2016-06-07 | B | 4 | 0.000324 | 1.2026e-05
2017 | 2016-05-12 | C | 1491 | 0.10919 | 0.0044843
2017 | 2016-06-07 | B | 9 | 0.001542 | 2.7058e-05
2017 | 2016-06-08 | B | 3 | 0.000559 | 9.0191e-06
2017 | 2016-05-12 | C | 1 | 0.00027 | 3.0075e-06
2017 | 2016-05-12 | C | 6 | 0.001028 | 1.8045e-05
2017 | 2016-05-12 | C | 304 | 0.0665 | 0.00091431
2017 | 2016-05-12 | C | 7 | 0.008673 | 2.1053e-05
2017 | 2016-06-08 | B | 5 | 0.000781 | 1.5032e-05
2017 | 2016-06-08 | B | 4 | 0.000925 | 1.2025e-05
2017 | 2016-06-01 | B | 6 | 0.006765 | 1.804e-05
2017 | 2016-06-09 | B | 9 | 0.000595 | 2.7057e-05
2017 | 2016-06-09 | B | 8 | 0.000408 | 2.4051e-05
2017 | 2016-06-09 | B | 12 | 0.000974 | 3.6076e-05
2017 | 2016-06-07 | B | 6 | 0.005646 | 1.8038e-05
2017 | 2016-06-10 | B | 2 | 0.001159 | 6.0125e-06
2017 | 2016-06-14 | B | 3 | 0.000486 | 9.0183e-06
2017 | 2016-05-12 | C | 43 | 0.008406 | 0.00012933
2017 | 2016-06-01 | B | 98 | 0.002525 | 0.00029465
2017 | 2016-05-12 | C | 296 | 0.078242 | 0.00089025
2017 | 2016-06-03 | B | 10 | 0.005321 | 3.0066e-05
2017 | 2016-06-02 | B | 9 | 0.003301 | 2.706e-05
2017 | 2016-06-07 | B | 6 | 0.001569 | 1.8038e-05
2017 | 2016-05-12 | C | 23 | 0.009287 | 6.9175e-05
2017 | 2016-05-12 | C | 868 | 0.12651 | 0.0044573
2017 | 2016-05-12 | C | 110 | 0.034616 | 0.00033084
2017 | 2016-05-12 | C | 46 | 0.012345 | 0.00013835
2017 | 2016-06-08 | B | 66 | 0.068324 | 0.00019842
2017 | 2016-06-09 | B | 22 | 0.015542 | 6.6139e-05
2017 | 2016-06-15 | B | 94 | 0.075446 | 0.00028257
2017 | 2016-06-16 | B | 16 | 0.015102 | 4.8096e-05
2017 | 2016-06-24 | B | 16 | 0.014864 | 4.809e-05
2017 | 2016-06-03 | B | 16 | 0.011208 | 4.8105e-05
2017 | 2016-06-05 | B | 227 | 0.078484 | 0.00068247
2017 | 2016-06-08 | B | 90 | 0.050867 | 0.00027057
2017 | 2016-06-02 | B | 66 | 0.04187 | 0.00019844
2017 | 2016-06-08 | B | 19 | 0.01725 | 5.7121e-05
2017 | 2016-06-01 | B | 5 | 0.004404 | 1.5033e-05
2017 | 2016-05-12 | C | 110 | 0.026997 | 0.00033084
2017 | 2016-05-12 | C | 46 | 0.001634 | 0.00013835
2017 | 2016-05-13 | C | 1 | 0.000915 | 3.0075e-06
2017 | 2016-05-13 | C | 90 | 0.12836 | 0.00039098
2017 | 2016-05-13 | C | 604 | 0.18362 | 0.0022316
2017 | 2016-05-13 | C | 3 | 0.000677 | 9.0226e-06
2017 | 2016-05-13 | C | 112 | 0.070243 | 0.00067369
2017 | 2016-05-13 | C | 65 | 0.095666 | 0.00039098
2017 | 2016-05-13 | C | 256 | 0.023282 | 0.00079098
2017 | 2016-05-13 | C | 3 | 0.00286 | 9.0226e-06
2017 | 2016-05-13 | C | 6 | 0.002345 | 1.8045e-05
2017 | 2016-05-13 | C | 238 | 0.052175 | 0.0013775
2017 | 2016-05-13 | C | 254 | 0.061531 | 0.00076392
2017 | 2016-05-13 | C | 7 | 0.003475 | 2.1053e-05
2017 | 2016-05-13 | C | 47 | 0.006785 | 0.00014135
2017 | 2016-05-13 | C | 69 | 0.010024 | 0.00020752
2017 | 2016-05-13 | C | 66 | 0.037178 | 0.0001985
2017 | 2016-05-13 | C | 23 | 0.040412 | 6.9174e-05
2017 | 2016-05-13 | C | 101 | 0.029768 | 0.00030376
2017 | 2016-05-13 | C | 5 | 0.002635 | 1.5038e-05
2017 | 2016-05-15 | B | 58 | 0.065261 | 0.00017443
2017 | 2016-05-17 | B | 34 | 0.040695 | 0.00010225
2017 | 2016-06-07 | B | 51 | 0.037565 | 0.00015333
2017 | 2016-05-19 | B | 34 | 0.024334 | 0.00010225
2017 | 2016-06-03 | B | 22 | 0.017594 | 6.6145e-05
2017 | 2016-05-13 | C | 1 | 0.000845 | 3.0075e-06
2017 | 2016-06-01 | B | 16 | 0.005387 | 4.8107e-05
2017 | 2016-05-30 | B | 6 | 0.006891 | 1.8041e-05
2017 | 2016-05-13 | C | 117 | 0.16377 | 0.00059249
2017 | 2016-06-07 | B | 3 | 0.003337 | 9.0192e-06
2017 | 2016-05-13 | C | 1 | 0.000539 | 3.0075e-06
2017 | 2016-06-02 | B | 17 | 0.019587 | 5.1113e-05
2017 | 2016-05-13 | C | 4 | 0.00027 | 1.203e-05
2017 | 2016-06-08 | B | 23 | 0.009334 | 6.9146e-05
2017 | 2016-06-08 | B | 20 | 0.020503 | 6.0127e-05
2017 | 2016-05-13 | C | 31 | 0.018449 | 9.3234e-05
2017 | 2016-05-13 | C | 10 | 0.034261 | 3.0075e-05
2017 | 2016-05-13 | C | 6 | 0.003737 | 1.8045e-05
2017 | 2016-05-13 | C | 240 | 0.031479 | 0.00072181
2017 | 2016-05-12 | C | 1 | 0.002433 | 3.0075e-06
2017 | 2016-05-14 | C | 1 | 0.000513 | 3.0075e-06
2017 | 2016-05-14 | C | 353 | 0.036821 | 0.0010617
2017 | 2016-05-14 | C | 64 | 0.008084 | 0.00019248
2017 | 2016-05-16 | C | 13 | 0.002694 | 3.9096e-05
2017 | 2016-05-14 | C | 6 | 0.00101 | 1.8045e-05
2017 | 2016-05-14 | C | 63 | 0.055066 | 0.00018947
2017 | 2016-05-14 | C | 1 | 0.000237 | 3.0075e-06
2017 | 2016-05-14 | C | 8 | 0.000168 | 2.406e-05
2017 | 2016-05-14 | C | 10 | 0.002167 | 3.0075e-05
2017 | 2016-05-15 | C | 26 | 0.002342 | 7.8194e-05
2017 | 2016-05-15 | C | 284 | 0 | 0.00085412
2017 | 2016-06-03 | B | 8 | 0.010462 | 2.4053e-05
2017 | 2016-05-16 | C | 9 | 0.005196 | 2.7067e-05
2017 | 2016-06-08 | B | 5 | 0.00686 | 1.5032e-05
2017 | 2016-06-09 | B | 36 | 0.032468 | 0.00010823
2017 | 2016-06-02 | B | 28 | 0.011196 | 8.4185e-05
2017 | 2016-06-01 | B | 25 | 0.025105 | 7.5167e-05
2017 | 2016-06-01 | B | 128 | 0.085822 | 0.00038485
2017 | 2016-06-01 | B | 64 | 0.023701 | 0.00019243
2017 | 2016-06-01 | B | 40 | 0.047625 | 0.00012027
2017 | 2016-06-02 | B | 40 | 0.035117 | 0.00012026
2017 | 2016-06-02 | B | 125 | 0.10598 | 0.00037583
2017 | 2016-05-16 | C | 957 | 0.10766 | 0.0028781
2017 | 2016-05-16 | C | 1134 | 0.50203 | 0.0034104
2017 | 2016-05-16 | C | 18 | 0.00617 | 5.4133e-05
2017 | 2016-05-16 | C | 21 | 0.004733 | 6.3156e-05
2017 | 2016-05-16 | C | 4 | 0.001034 | 1.203e-05
2017 | 2016-05-16 | C | 261 | 0.093005 | 0.0016902
2017 | 2016-05-16 | C | 2 | 0.000645 | 6.0148e-06
2017 | 2016-05-16 | C | 205 | 0.015423 | 0.00061652
2017 | 2016-05-16 | C | 329 | 0.12928 | 0.00098944
2017 | 2016-05-16 | C | 5 | 0.003443 | 1.5037e-05
2017 | 2016-05-16 | C | 727 | 0.31399 | 0.0031127
2017 | 2016-05-16 | C | 2723 | 0.12019 | 0.0073862
2017 | 2016-05-16 | C | 5 | 0.002043 | 1.5037e-05
2017 | 2016-05-16 | C | 4 | 0.003361 | 1.203e-05
2017 | 2016-05-16 | C | 1 | 0.000284 | 3.0074e-06
2017 | 2016-05-16 | C | 1 | 0.000954 | 3.0074e-06
2017 | 2016-05-16 | C | 1 | 0.000308 | 3.0074e-06
2017 | 2016-05-16 | C | 14 | 0.006652 | 4.2104e-05
2017 | 2016-05-16 | C | 6 | 0.001854 | 1.8044e-05
2017 | 2016-05-16 | C | 8 | 0.002963 | 2.4059e-05
2017 | 2016-05-16 | C | 1 | 0.00017 | 3.0074e-06
2017 | 2016-05-16 | C | 1 | 0.00038 | 3.0074e-06
2017 | 2016-05-16 | C | 3 | 0.001665 | 9.0222e-06
2017 | 2016-05-16 | C | 39 | 0.014653 | 0.00011729
2017 | 2016-05-17 | C | 631 | 0.78822 | 0.0018977
2017 | 2016-05-17 | C | 3 | 0.004282 | 9.0221e-06
2017 | 2016-05-17 | C | 18 | 0.001872 | 5.4133e-05
2017 | 2016-05-17 | C | 49 | 0.003566 | 0.00014736
2017 | 2016-05-17 | C | 3 | 0.000926 | 9.0221e-06
2017 | 2016-05-17 | C | 45 | 0 | 0.00013533
2017 | 2016-05-17 | C | 117 | 0.070784 | 0.00035186
2017 | 2016-05-17 | C | 93 | 0.026481 | 0.00028871
2017 | 2016-05-17 | C | 956 | 0.11118 | 0.002875
2017 | 2016-05-17 | C | 4 | 0.00125 | 1.2029e-05
2017 | 2016-05-17 | C | 3 | 0.000719 | 9.0221e-06
2017 | 2016-05-17 | C | 1 | 0.000296 | 3.0073e-06
2017 | 2016-05-17 | C | 2 | 0.001678 | 6.0147e-06
2017 | 2016-05-17 | C | 5 | 0.002564 | 1.5037e-05
2017 | 2016-05-17 | C | 5 | 0.001423 | 1.5037e-05
2017 | 2016-05-17 | C | 1 | 0.001342 | 3.0073e-06
2017 | 2016-05-17 | C | 3 | 0.000986 | 9.0221e-06
2017 | 2016-05-17 | C | 2 | 0.000906 | 6.0147e-06
2017 | 2016-06-03 | B | 1 | 0.000502 | 3.0065e-06
2017 | 2016-05-17 | C | 1 | 0.00024 | 3.0073e-06
2017 | 2016-06-02 | B | 27 | 0.027194 | 8.1179e-05
2017 | 2016-06-02 | B | 26 | 0.025562 | 7.8172e-05
2017 | 2016-06-13 | B | 370 | 0.051743 | 0.0016534
2017 | 2016-06-07 | B | 8 | 0.00885 | 2.4051e-05
2017 | 2016-06-02 | B | 74 | 0.024251 | 0.00022249
2017 | 2016-06-09 | B | 8 | 0.008658 | 2.4051e-05
2017 | 2016-06-03 | B | 19 | 0.018848 | 5.7125e-05
2017 | 2016-06-13 | B | 42 | 0.040907 | 0.00012626
2017 | 2016-05-17 | C | 868 | 0.010441 | 0.0026104
2017 | 2016-06-15 | B | 42 | 0.049365 | 0.00012625
2017 | 2016-06-17 | B | 39 | 0.044431 | 0.00011723
2017 | 2016-06-11 | B | 2 | 0.000384 | 6.0124e-06
2017 | 2016-05-17 | C | 19 | 0.006113 | 5.714e-05
2017 | 2016-05-17 | C | 5 | 0.001082 | 1.5037e-05
2017 | 2016-06-07 | B | 7 | 0.005808 | 2.1045e-05
2017 | 2016-05-17 | C | 1 | 0.000356 | 3.0073e-06
2017 | 2016-05-18 | C | 1 | 0.002433 | 3.0073e-06
2017 | 2016-05-18 | C | 14 | 0.007788 | 4.2103e-05
2017 | 2016-05-18 | C | 30 | 0.01245 | 9.022e-05
2017 | 2016-05-18 | C | 6 | 0.00196 | 1.8044e-05
2017 | 2016-05-18 | C | 363 | 0.057275 | 0.0010917
2017 | 2016-05-18 | C | 4 | 0.003016 | 1.2029e-05
2017 | 2016-05-18 | C | 23 | 0.003942 | 6.9168e-05
2017 | 2016-05-18 | C | 362 | 0.033881 | 0.0010887
2017 | 2016-05-18 | C | 2 | 0.000949 | 6.0146e-06
2017 | 2016-05-18 | C | 77 | 0.046559 | 0.00023156
2017 | 2016-05-18 | C | 15 | 0.002741 | 4.511e-05
2017 | 2016-05-18 | C | 2 | 0.00027 | 6.0146e-06
2017 | 2016-05-18 | C | 1 | 0.004933 | 3.0073e-06
2017 | 2016-05-18 | C | 1 | 0.000264 | 3.0073e-06
2017 | 2016-05-18 | C | 4 | 0.001462 | 1.2029e-05
2017 | 2016-05-18 | C | 65 | 0.018374 | 0.00019548
2017 | 2016-05-18 | C | 1 | 0.001434 | 3.0073e-06
2017 | 2016-05-18 | C | 3 | 0.001076 | 9.0219e-06
2017 | 2016-05-18 | C | 41 | 0.002835 | 0.0001233
2017 | 2016-05-18 | C | 349 | 0.019227 | 0.00027968
2017 | 2016-05-18 | C | 2 | 0.001093 | 6.0146e-06
2017 | 2016-05-18 | C | 199 | 0.029324 | 0.00059846
2017 | 2016-05-20 | B | 11 | 0.00473 | 3.308e-05
2017 | 2016-05-18 | C | 10 | 0.004563 | 3.0073e-05
2017 | 2016-05-18 | C | 1 | 0.00043 | 3.0073e-06
2017 | 2016-05-18 | C | 351 | 0.077922 | 0.0010556
2017 | 2016-05-18 | C | 1 | 0 | 3.0073e-06
2017 | 2016-06-13 | B | 30 | 0.030843 | 9.0185e-05
2017 | 2016-05-18 | C | 178 | 0.13148 | 0.0005353
2017 | 2016-05-18 | C | 2 | 0.001394 | 6.0146e-06
2017 | 2016-05-18 | C | 4 | 0.000739 | 1.2029e-05
2017 | 2016-05-18 | C | 617 | 0.15594 | 0.0018555
2017 | 2016-05-18 | C | 1578 | 0.2007 | 0.0047456
2017 | 2016-05-18 | C | 92 | 0.053974 | 0.00027667
2017 | 2016-05-18 | C | 1 | 0.000299 | 3.0073e-06
2017 | 2016-05-18 | C | 870 | 0.05128 | 0.0026164
2017 | 2016-05-18 | C | 7 | 0.002405 | 2.1051e-05
2017 | 2016-05-19 | C | 495 | 0.07554 | 0.0016841
2017 | 2016-05-19 | C | 44 | 0.013366 | 0.00013232
2017 | 2016-05-19 | C | 254 | 0.031318 | 0.00076385
2017 | 2016-06-01 | B | 114 | 0.12648 | 0.00034276
2017 | 2016-06-07 | B | 45 | 0.013287 | 0.00013529
2017 | 2016-06-15 | B | 22 | 0.026916 | 6.6133e-05
2017 | 2016-06-16 | B | 22 | 0.024601 | 6.6132e-05
2017 | 2016-06-15 | B | 10 | 0.0102 | 3.0061e-05
2017 | 2016-05-19 | C | 4 | 0.000469 | 1.2029e-05
2017 | 2016-05-19 | C | 17 | 0.001738 | 5.1124e-05
2017 | 2016-06-14 | B | 52 | 0.053773 | 0.00015632
2017 | 2016-05-19 | C | 39 | 0.001133 | 0.00011728
2017 | 2016-06-08 | B | 35 | 0.038827 | 0.00010522
2017 | 2016-06-10 | B | 2 | 0.001364 | 6.0125e-06
2017 | 2016-05-19 | C | 1 | 0.000569 | 3.0072e-06
2017 | 2016-06-14 | B | 43 | 0.042139 | 0.00012926
2017 | 2016-05-19 | C | 90 | 0.029878 | 0.00027066
2017 | 2016-06-16 | B | 41 | 0.049347 | 0.00012325
2017 | 2016-06-21 | B | 19 | 0.019131 | 5.711e-05
2017 | 2016-06-17 | B | 5 | 0.005293 | 1.503e-05
2017 | 2016-05-20 | C | 8 | 0.013988 | 2.4058e-05
2017 | 2016-06-15 | B | 51 | 0.037714 | 0.00015331
2017 | 2016-05-20 | C | 1 | 0.000788 | 3.0072e-06
2017 | 2016-05-20 | C | 495 | 0.094778 | 0.0027576
2017 | 2016-05-20 | C | 3 | 0.000679 | 9.0217e-06
2017 | 2016-05-18 | C | 2 | 0.002514 | 6.0146e-06
2017 | 2016-05-18 | C | 1 | 0.001257 | 3.0073e-06
2017 | 2016-05-18 | C | 1 | 0.001257 | 3.0073e-06
2017 | 2016-06-13 | B | 71 | 0.0286 | 0.00021344
2017 | 2016-05-16 | C | 6 | 0.003266 | 1.8044e-05
2017 | 2016-06-16 | B | 5 | 0.00511 | 1.503e-05
2017 | 2016-06-09 | B | 9 | 0.009578 | 2.7057e-05
2017 | 2016-05-20 | C | 4 | 0.000767 | 1.2029e-05
2017 | 2016-05-20 | C | 3 | 0.001193 | 9.0217e-06
2017 | 2016-05-20 | C | 4 | 0.000693 | 1.2029e-05
2017 | 2016-05-20 | C | 296 | 0.079362 | 0.0018976
2017 | 2016-05-21 | C | 166 | 0.011385 | 0.00010224
2017 | 2016-05-20 | C | 470 | 0.35017 | 0.0014134
2017 | 2016-05-20 | C | 170 | 0.1078 | 0.00071272
2017 | 2016-05-21 | C | 115 | 0.022571 | 0.00034583
2017 | 2016-05-20 | C | 35 | 0.00442 | 0.00010525
2017 | 2016-05-21 | C | 3398 | 1.4021 | 0.010218
2017 | 2016-05-21 | C | 115 | 0.024812 | 0.00034583
2017 | 2016-05-21 | C | 2 | 0.003146 | 6.0143e-06
2017 | 2016-05-21 | C | 2 | 0.000723 | 6.0143e-06
2017 | 2016-05-21 | C | 7 | 0.002229 | 2.105e-05
2017 | 2016-05-21 | C | 29 | 0.007592 | 8.7209e-05
2017 | 2016-05-21 | C | 3 | 0.002722 | 9.0215e-06
2017 | 2016-05-21 | C | 4 | 0.002313 | 1.2029e-05
2017 | 2016-05-21 | C | 1 | 0.000131 | 3.0071e-06
2017 | 2016-05-21 | C | 1 | 0.000341 | 3.0071e-06
2017 | 2016-05-21 | C | 1 | 0.000269 | 3.0071e-06
2017 | 2016-05-21 | C | 55 | 0.007112 | 0.0001654
2017 | 2016-05-21 | C | 1 | 0.000296 | 3.0071e-06
2017 | 2016-05-21 | C | 5 | 0.001368 | 1.5036e-05
2017 | 2016-05-21 | C | 101 | 0.058457 | 0.00030373
2017 | 2016-05-21 | C | 4 | 0.004751 | 1.2029e-05
2017 | 2016-05-21 | C | 2 | 0.001731 | 6.0143e-06
2017 | 2016-05-21 | C | 1 | 0.003347 | 3.0071e-06
2017 | 2016-05-21 | C | 1 | 5.1e-05 | 3.0071e-06
2017 | 2016-05-22 | C | 2 | 0.000971 | 6.0142e-06
2017 | 2016-05-22 | C | 1 | 0.000529 | 3.0071e-06
2017 | 2016-05-22 | C | 1 | 0.000223 | 3.0071e-06
2017 | 2016-05-22 | C | 1 | 0.000657 | 3.0071e-06
2017 | 2016-05-22 | C | 115 | 0.01267 | 0.00034582
2017 | 2016-05-22 | C | 1 | 0.000169 | 3.0071e-06
2017 | 2016-05-22 | C | 1 | 0.000334 | 3.0071e-06
2017 | 2016-05-22 | C | 15 | 0.008457 | 4.5107e-05
2017 | 2016-05-22 | C | 115 | 0.020016 | 0.00034582
2017 | 2016-05-22 | C | 6 | 0.018349 | 1.8043e-05
2017 | 2016-05-22 | C | 752 | 0.081292 | 0.0022614
2017 | 2016-05-23 | C | 254 | 0.038813 | 0.00086003
2017 | 2016-06-16 | B | 32 | 0.022893 | 9.6192e-05
2017 | 2016-05-23 | C | 4 | 0.003328 | 1.2028e-05
2017 | 2016-05-23 | C | 1 | 0.000808 | 3.007e-06
2017 | 2016-06-17 | B | 48 | 0.055117 | 0.00014429
2017 | 2016-05-23 | C | 1001 | 0.10581 | 0.0030101
2017 | 2016-05-23 | C | 1 | 0.00066 | 3.007e-06
2017 | 2016-05-24 | B | 35 | 0.007893 | 0.00010525
2017 | 2016-05-23 | C | 112 | 0.088606 | 0.0010044
2017 | 2016-05-24 | C | 1 | 0.000345 | 3.007e-06
2017 | 2016-05-24 | C | 4 | 0.003046 | 1.2028e-05
2017 | 2016-05-24 | C | 51 | 0.020384 | 0.00015336
2017 | 2016-06-10 | B | 69 | 0.097493 | 0.00020743
2017 | 2016-05-24 | C | 149 | 0.11105 | 0.0013051
2017 | 2016-05-24 | C | 1 | 0.000156 | 3.007e-06
2017 | 2016-06-09 | B | 9 | 0.006277 | 2.7057e-05
2017 | 2016-05-24 | C | 11 | 0.003704 | 3.3078e-05
2017 | 2016-05-24 | C | 13 | 0.006258 | 3.9092e-05
2017 | 2016-05-24 | C | 1 | 0.000788 | 3.007e-06
2017 | 2016-05-24 | C | 3 | 0.001015 | 9.0211e-06
2017 | 2016-05-24 | C | 3 | 0.00066 | 9.0211e-06
2017 | 2016-05-24 | C | 1 | 0.000282 | 3.007e-06
2017 | 2016-05-24 | C | 1 | 9.6e-05 | 3.007e-06
2017 | 2016-05-25 | C | 51 | 0.015489 | 0.00015336
2017 | 2016-05-24 | C | 7 | 0.003031 | 2.1049e-05
2017 | 2016-05-24 | C | 3 | 0.009478 | 9.0211e-06
2017 | 2016-05-24 | C | 4 | 0.001142 | 1.2028e-05
2017 | 2016-05-24 | C | 4 | 0.001207 | 1.2028e-05
2017 | 2016-05-24 | C | 279 | 0.10575 | 0.00083897
2017 | 2016-05-24 | C | 3 | 0.007901 | 9.0211e-06
2017 | 2016-05-25 | C | 5 | 0.001639 | 1.5035e-05
2017 | 2016-05-25 | C | 243 | 0.05761 | 0.0007307
2017 | 2016-05-25 | C | 1 | 0.000509 | 3.007e-06
2017 | 2016-05-25 | C | 115 | 0.007976 | 0.00034581
2017 | 2016-05-25 | C | 2 | 0.000556 | 6.014e-06
2017 | 2016-05-25 | C | 2 | 0.001051 | 6.014e-06
2017 | 2016-05-25 | C | 115 | 0.024435 | 0.00069161
2017 | 2016-05-25 | C | 1 | 0.000635 | 3.007e-06
2017 | 2016-05-25 | C | 1 | 0.000387 | 3.007e-06
2017 | 2016-05-25 | C | 3 | 0.003356 | 9.021e-06
2017 | 2016-05-25 | C | 1 | 0.000168 | 3.007e-06
2017 | 2016-05-25 | C | 5 | 0.001656 | 1.5035e-05
2017 | 2016-05-25 | C | 5 | 0.004916 | 1.5035e-05
2017 | 2016-05-25 | C | 1 | 0.000405 | 3.007e-06
2017 | 2016-05-25 | C | 2 | 0.000212 | 6.014e-06
2017 | 2016-06-17 | B | 78 | 0.037983 | 0.00023447
2017 | 2016-05-25 | C | 3 | 0.00092 | 9.021e-06
2017 | 2016-05-25 | C | 2 | 0.00056 | 6.014e-06
2017 | 2016-05-25 | C | 4 | 0.003431 | 1.2028e-05
2017 | 2016-05-25 | C | 2 | 0.001367 | 6.014e-06
2017 | 2016-05-26 | C | 34 | 0.007054 | 0.00010224
2017 | 2016-06-14 | B | 6 | 0.002038 | 1.8037e-05
2017 | 2016-06-14 | B | 71 | 0.079091 | 0.00021343
2017 | 2016-05-25 | C | 3 | 0.001993 | 9.021e-06
2017 | 2016-05-25 | C | 4 | 0.001201 | 1.2028e-05
2017 | 2016-05-25 | C | 61 | 0.007851 | 0.00018343
2017 | 2016-05-25 | C | 1 | 0.000316 | 3.007e-06
2017 | 2016-05-25 | C | 1 | 0.001434 | 3.007e-06
2017 | 2016-05-25 | C | 6 | 0.005708 | 1.8042e-05
2017 | 2016-05-25 | C | 2 | 0.002281 | 6.014e-06
2017 | 2016-05-25 | C | 1 | 0.001202 | 3.007e-06
2017 | 2016-05-25 | C | 1 | 0.000372 | 3.007e-06
2017 | 2016-05-25 | C | 1 | 0.00088 | 3.007e-06
2017 | 2016-05-25 | C | 4 | 0.003286 | 1.2028e-05
2017 | 2016-05-25 | C | 405 | 0.090392 | 0.0012178
2017 | 2016-05-25 | C | 1 | 0.000543 | 3.007e-06
2017 | 2016-05-25 | C | 4 | 0.000832 | 1.2028e-05
2017 | 2016-05-25 | C | 4 | 0.001098 | 1.2028e-05
2017 | 2016-06-22 | B | 3 | 0.001956 | 9.0172e-06
2017 | 2016-05-25 | C | 60 | 0.014072 | 0.00018042
2017 | 2016-05-25 | C | 139 | 0.028756 | 0.00041797
2017 | 2016-05-25 | C | 119 | 0.026442 | 0.00071266
2017 | 2016-05-25 | C | 2 | 0.001073 | 6.014e-06
2017 | 2016-05-25 | C | 2 | 0.000506 | 6.014e-06
2017 | 2016-05-25 | C | 52 | 0.007036 | 0.00015636
2017 | 2016-05-25 | C | 1 | 1e-05 | 3.007e-06
2017 | 2016-06-23 | B | 5 | 0.004162 | 1.5028e-05
2017 | 2016-06-18 | B | 46 | 0.008158 | 0.00013827
2017 | 2016-06-22 | B | 65 | 0.084576 | 0.00019537
2017 | 2016-05-25 | C | 3 | 0.000426 | 9.021e-06
2017 | 2016-05-25 | C | 134 | 0.026298 | 0.00040294
2017 | 2016-06-23 | B | 65 | 0.075998 | 0.00019537
2017 | 2016-05-25 | C | 362 | 0.10392 | 0.0019756
2017 | 2016-05-25 | C | 1042 | 0.21044 | 0.0031333
2017 | 2016-05-25 | C | 1 | 7.1e-05 | 3.007e-06
2017 | 2016-05-25 | C | 4 | 0.002916 | 1.2028e-05
2017 | 2016-05-25 | C | 4 | 0.003013 | 1.2028e-05
2017 | 2016-05-26 | C | 355 | 0.2088 | 0.0010675
2017 | 2016-05-28 | B | 19 | 0.010112 | 5.713e-05
2017 | 2016-06-22 | B | 9 | 0.00871 | 2.7052e-05
2017 | 2016-05-25 | C | 2 | 0.000595 | 6.014e-06
2017 | 2016-05-26 | C | 1 | 0.000494 | 3.0069e-06
2017 | 2016-05-26 | C | 182 | 0.01004 | 6.3146e-05
2017 | 2016-06-23 | B | 20 | 0.02146 | 6.0114e-05
2017 | 2016-06-14 | B | 65 | 0.026183 | 0.0001954
2017 | 2016-05-26 | C | 249 | 0.076597 | 0.00074873
2017 | 2016-05-26 | C | 1 | 0.000588 | 3.0069e-06
2017 | 2016-06-29 | B | 9 | 0.009223 | 2.7049e-05
2017 | 2016-06-30 | B | 6 | 0.006058 | 1.8032e-05
2017 | 2016-06-17 | B | 10 | 0.011591 | 3.006e-05
2017 | 2016-05-26 | C | 1 | 0 | 3.0069e-06
2017 | 2016-05-26 | C | 100 | 0.029768 | 0.0003007
2017 | 2016-05-26 | C | 1 | 0.000105 | 3.0069e-06
2017 | 2016-06-20 | B | 22 | 0.009059 | 6.6128e-05
2017 | 2016-05-26 | C | 21 | 0.005935 | 6.3146e-05
2017 | 2016-05-26 | C | 111 | 0.018107 | 0.00033377
2017 | 2016-05-26 | C | 24 | 0.006968 | 7.2167e-05
2017 | 2016-05-27 | C | 16 | 0.00424 | 4.811e-05
2017 | 2016-05-27 | C | 422 | 0.025282 | 0.001759
2017 | 2016-05-27 | C | 1 | 0.000315 | 3.0069e-06
2017 | 2016-06-02 | B | 205 | 0.21776 | 0.00061636
2017 | 2016-05-27 | C | 1 | 0.0004 | 3.0069e-06
2017 | 2016-06-15 | B | 1363 | 0 | 0
2017 | 2016-06-15 | B | 2 | 0.000174 | 6.0121e-06
2017 | 2016-05-27 | C | 11505 | 0.35435 | 0.034594
2017 | 2016-05-29 | C | 12 | 0.011363 | 3.6082e-05
2017 | 2016-05-28 | C | 283 | 0.06872 | 0.0016087
2017 | 2016-05-28 | C | 1 | 9e-06 | 3.0068e-06
2017 | 2016-05-28 | C | 5 | 0.001082 | 1.5034e-05
2017 | 2016-05-28 | C | 1043 | 0.25842 | 0.0031362
2017 | 2016-05-28 | C | 11505 | 1.7109 | 0.034594
2017 | 2016-05-28 | C | 240 | 0.059635 | 0.00072165
2017 | 2016-05-28 | C | 6 | 0.002906 | 1.8041e-05
2017 | 2016-05-28 | C | 862 | 0.31877 | 0.0025919
2017 | 2016-05-28 | C | 4 | 0.001371 | 1.2027e-05
2017 | 2016-05-28 | C | 287 | 0.085865 | 0.0034519
2017 | 2016-05-28 | C | 772 | 0.16805 | 0.0021589
2017 | 2016-05-28 | C | 5 | 0.003195 | 1.5034e-05
2017 | 2016-05-28 | C | 2 | 0.000669 | 6.0137e-06
2017 | 2016-05-28 | C | 4 | 0.003606 | 1.2027e-05
2017 | 2016-05-28 | C | 3 | 0.004554 | 9.0205e-06
2017 | 2016-05-28 | C | 18 | 0.007373 | 5.4123e-05
2017 | 2016-05-28 | C | 2 | 0.002084 | 6.0137e-06
2017 | 2016-05-28 | C | 15 | 0.006627 | 4.5103e-05
2017 | 2016-05-28 | C | 2 | 0.000511 | 6.0137e-06
2017 | 2016-05-28 | C | 1 | 0.000194 | 3.0068e-06
2017 | 2016-05-28 | C | 1 | 0.000346 | 3.0068e-06
2017 | 2016-05-28 | C | 44 | 0.32796 | 0.00028264
2017 | 2016-05-28 | C | 1 | 0.00022 | 3.0068e-06
2017 | 2016-05-29 | C | 366 | 0.18834 | 0.0011005
2017 | 2016-05-29 | C | 1061 | 0.29775 | 0.0031902
2017 | 2016-05-29 | C | 308 | 0.086681 | 0.00036082
2017 | 2016-05-29 | C | 256 | 0.12439 | 0.001302
2017 | 2016-05-29 | C | 59 | 0.002321 | 0.0001774
2017 | 2016-05-29 | C | 1 | 0.000668 | 3.0068e-06
2017 | 2016-05-29 | C | 3 | 0.002264 | 9.0204e-06
2017 | 2016-05-29 | C | 4 | 0.001629 | 1.2027e-05
2017 | 2016-05-29 | C | 59 | 0.046048 | 0.0001774
2017 | 2016-05-29 | C | 296 | 0.13254 | 0.00043899
2017 | 2016-05-29 | C | 1 | 0.00481 | 3.0068e-06
2017 | 2016-05-29 | C | 8 | 0.030837 | 2.4055e-05
2017 | 2016-05-29 | C | 4 | 0.000797 | 1.2027e-05
2017 | 2016-05-29 | C | 4 | 0.000486 | 1.2027e-05
2017 | 2016-05-29 | C | 1 | 0.002999 | 3.0068e-06
2017 | 2016-05-29 | C | 3 | 0.001075 | 9.0204e-06
2017 | 2016-05-29 | C | 684 | 0.033248 | 0.00036683
2017 | 2016-05-30 | C | 9 | 0.003165 | 2.7061e-05
2017 | 2016-05-30 | C | 6 | 0.004299 | 1.8041e-05
2017 | 2016-05-30 | C | 1 | 0.000178 | 3.0067e-06
2017 | 2016-05-30 | C | 1 | 0.000356 | 3.0067e-06
2017 | 2016-06-02 | B | 6 | 0.000992 | 1.804e-05
2017 | 2016-05-30 | C | 23 | 0.00631 | 6.9156e-05
2017 | 2016-05-30 | C | 3 | 0.001422 | 9.0203e-06
2017 | 2016-05-30 | C | 186 | 0.2658 | 0.00055926
2017 | 2016-05-31 | C | 873 | 0.08112 | 0.00043597
2017 | 2016-05-31 | C | 1 | 8.1e-05 | 3.0067e-06
2017 | 2016-05-31 | C | 482 | 0.06843 | 0.0021077
2017 | 2016-06-21 | B | 109 | 0.086494 | 0.00032763
2017 | 2016-06-08 | B | 410 | 0.097331 | 0.0014581
2017 | 2016-06-09 | B | 595 | 0.03821 | 0.0017888
2017 | 2016-05-31 | C | 145 | 0.073243 | 0.00043597
2017 | 2016-05-31 | C | 5 | 0.002223 | 1.5034e-05
2017 | 2016-05-31 | C | 829 | 0.068635 | 0.0024926
2017 | 2016-06-01 | C | 11 | 0.005442 | 3.3073e-05
2017 | 2016-06-01 | C | 3 | 0.000493 | 9.02e-06
2017 | 2016-06-21 | B | 11 | 0.009985 | 3.3064e-05
2017 | 2016-06-01 | C | 1 | 0.000179 | 3.0066e-06
2017 | 2016-06-01 | C | 7 | 0.002273 | 2.1047e-05
2017 | 2016-06-01 | C | 1411 | 0.28818 | 0.0037884
2017 | 2016-06-02 | C | 1214 | 0.28647 | 0.00365
2017 | 2016-06-16 | B | 10 | 0.008957 | 3.006e-05
2017 | 2016-06-21 | B | 137 | 0.069797 | 0.00069434
2017 | 2016-06-02 | C | 1 | 0.00105 | 3.0066e-06
2017 | 2016-06-02 | C | 21 | 0.008211 | 6.3139e-05
2017 | 2016-06-23 | B | 160 | 0.14187 | 0.00048091
2017 | 2016-06-02 | C | 1 | 0.000358 | 3.0066e-06
2017 | 2016-06-23 | B | 2 | 0.000703 | 6.0113e-06
2017 | 2016-06-17 | B | 108 | 0.019478 | 0.00032464
2017 | 2016-06-02 | C | 5 | 0.000789 | 1.5033e-05
2017 | 2016-06-02 | C | 217 | 0.039125 | 0.0011545
2017 | 2016-07-01 | B | 16 | 0.016877 | 4.8085e-05
2017 | 2016-06-02 | C | 348 | 0.09521 | 0.0030878
2017 | 2016-06-03 | C | 57 | 0.058621 | 0.00017137
2017 | 2016-06-03 | C | 846 | 0.23819 | 0.0040859
2017 | 2016-06-03 | C | 5703 | 0.27851 | 0.021984
2017 | 2016-06-03 | C | 1 | 0.000371 | 3.0065e-06
2017 | 2016-06-03 | C | 1 | 3.2e-05 | 3.0065e-06
2017 | 2016-06-03 | C | 2 | 3.4e-05 | 6.0131e-06
2017 | 2016-06-04 | C | 2062 | 0.43566 | 0.020051
2017 | 2016-06-04 | C | 24 | 0.009072 | 7.2157e-05
2017 | 2016-06-04 | C | 2017 | 0.49685 | 0.0060642
2017 | 2016-06-04 | C | 5 | 0.002776 | 1.5033e-05
2017 | 2016-06-04 | C | 432 | 0.075461 | 0.0012988
2017 | 2016-06-04 | C | 1032 | 0.10549 | 0.0031027
2017 | 2016-06-04 | C | 1 | 8.4e-05 | 3.0065e-06
2017 | 2016-06-04 | C | 37 | 0.011614 | 0.00011124
2017 | 2016-06-09 | C | 1 | 0.000219 | 3.0063e-06
2017 | 2016-06-04 | C | 369 | 0.051348 | 0.0011094
2017 | 2016-06-04 | C | 980 | 0.10238 | 0.0058928
2017 | 2016-06-04 | C | 302 | 0.21942 | 0.0020865
2017 | 2016-06-05 | C | 22 | 0.037172 | 6.6143e-05
2017 | 2016-06-05 | C | 22 | 0.001521 | 6.6143e-05
2017 | 2016-06-05 | C | 424 | 0.1097 | 0.0012748
2017 | 2016-06-05 | C | 11 | 0.03855 | 3.3071e-05
2017 | 2016-06-05 | C | 138 | 0.34174 | 0.0004149
2017 | 2016-06-07 | C | 3 | 0.000703 | 9.0192e-06
2017 | 2016-06-06 | C | 320 | 0.037781 | 0.00050809
2017 | 2016-06-07 | C | 1 | 0.000527 | 3.0064e-06
2017 | 2016-06-28 | B | 37 | 0.032248 | 0.0001112
2017 | 2016-06-28 | B | 66 | 0.076765 | 0.00019836
2017 | 2016-06-07 | C | 6 | 0.000932 | 1.8038e-05
2017 | 2016-06-24 | B | 225 | 0.086171 | 0.0013525
2017 | 2016-06-08 | C | 1 | 0.000295 | 3.0063e-06
2017 | 2016-06-08 | C | 49 | 0.01174 | 0.00014731
2017 | 2016-07-04 | B | 42 | 0.035468 | 0.00012622
2017 | 2016-06-08 | C | 28 | 0.004629 | 8.4178e-05
2017 | 2016-06-08 | C | 629 | 0.014581 | 0.001891
2017 | 2016-06-29 | B | 9 | 0.007654 | 2.7049e-05
2017 | 2016-06-29 | B | 7 | 0.005301 | 2.1038e-05
2017 | 2016-06-10 | B | 1 | 0.001028 | 3.0062e-06
2017 | 2016-06-08 | C | 3 | 0.000524 | 9.0191e-06
2017 | 2016-06-24 | B | 21 | 0.00972 | 6.3118e-05
2017 | 2016-06-20 | B | 399 | 0.031531 | 0.0018005
2017 | 2016-06-09 | C | 10 | 0.006433 | 3.0063e-05
2017 | 2016-06-24 | B | 3 | 0.002553 | 9.0169e-06
2017 | 2016-07-04 | B | 5 | 0.000826 | 1.5026e-05
2017 | 2016-07-04 | B | 32 | 0.017117 | 9.6168e-05
2017 | 2016-06-30 | B | 80 | 0.020993 | 0.00046283
2017 | 2016-07-04 | B | 3 | 0.001054 | 9.0157e-06
2017 | 2016-07-04 | B | 6 | 0.00238 | 1.8031e-05
2017 | 2016-07-06 | B | 3 | 0.001505 | 9.0156e-06
2017 | 2016-07-06 | B | 2 | 0.000402 | 6.0104e-06
2017 | 2016-07-06 | B | 4 | 0.000625 | 1.2021e-05
2017 | 2016-07-08 | B | 5 | 0.004026 | 1.5026e-05
2017 | 2016-07-01 | B | 72 | 0.065351 | 0.00021638
2017 | 2016-06-09 | C | 1 | 0.000246 | 3.0063e-06
2017 | 2016-07-01 | B | 23 | 0.014308 | 6.9123e-05
2017 | 2016-06-10 | C | 1409 | 0.3553 | 0.0042358
2017 | 2016-06-10 | C | 7 | 0.001711 | 2.1044e-05
2017 | 2016-07-01 | B | 2 | 0.00122 | 6.0106e-06
2017 | 2016-06-10 | C | 302 | 0.039039 | 0.0009079
2017 | 2016-06-10 | C | 1 | 7.9e-05 | 3.0062e-06
2017 | 2016-07-13 | B | 46 | 0.047136 | 0.00013823
2017 | 2016-06-10 | C | 55 | 0.003155 | 0.00016535
2017 | 2016-07-02 | B | 28 | 0.022804 | 8.4149e-05
2017 | 2016-07-06 | B | 61 | 0.057797 | 0.00018332
2017 | 2016-06-10 | C | 3398 | 0.6444 | 0.010215
2017 | 2016-07-05 | B | 29 | 0.016645 | 8.7152e-05
2017 | 2016-07-05 | B | 6 | 0.007609 | 1.8031e-05
2017 | 2016-07-05 | B | 60 | 0.031374 | 0.00018031
2017 | 2016-06-10 | C | 132 | 0.041031 | 0.00039683
2017 | 2016-06-10 | C | 500 | 0.10071 | 0.0015031
2017 | 2016-07-06 | B | 58 | 0.043282 | 0.0001743
2017 | 2016-06-10 | C | 1 | 0.000372 | 3.0062e-06
2017 | 2016-06-10 | C | 6 | 0.002136 | 1.8038e-05
2017 | 2016-06-11 | C | 5 | 0.001788 | 1.5031e-05
2017 | 2016-06-11 | C | 10 | 0.003086 | 3.0062e-05
2017 | 2016-06-11 | C | 132 | 0.084907 | 0.00039682
2017 | 2016-06-11 | C | 3 | 0.002362 | 9.0187e-06
2017 | 2016-06-11 | C | 45 | 0.023617 | 0.00013528
2017 | 2016-06-11 | C | 422 | 0.01141 | 0.0012746
2017 | 2016-06-11 | C | 46 | 0.006918 | 0.00014129
2017 | 2016-06-11 | C | 13 | 0.001614 | 3.9081e-05
2017 | 2016-06-11 | C | 132 | 0.034488 | 0.0010943
2017 | 2016-06-11 | C | 132 | 0.005747 | 0.00039682
2017 | 2016-06-11 | C | 132 | 0.057816 | 0.00039682
2017 | 2016-06-12 | C | 422 | 0.004761 | 0.0012746
2017 | 2016-06-12 | C | 3445 | 0.83507 | 0.010356
2017 | 2016-06-12 | C | 177 | 0.028706 | 0.0005321
2017 | 2016-06-12 | C | 33 | 0.004067 | 9.9205e-05
2017 | 2016-06-12 | C | 282 | 0.033062 | 0.00084775
2017 | 2016-06-12 | C | 17 | 0.020391 | 5.1105e-05
2017 | 2016-06-12 | C | 208 | 0.006442 | 3.3068e-05
2017 | 2016-06-12 | C | 432 | 0.13004 | 0.0012987
2017 | 2016-06-12 | C | 6 | 0.001659 | 1.8037e-05
2017 | 2016-06-12 | C | 3 | 0.000532 | 9.0185e-06
2017 | 2016-06-12 | C | 8 | 0.021841 | 2.405e-05
2017 | 2016-06-13 | C | 170 | 0.006107 | 0.00051105
2017 | 2016-06-13 | C | 137 | 0.066752 | 0.00041184
2017 | 2016-06-13 | C | 3 | 0.00277 | 9.0184e-06
2017 | 2016-06-13 | C | 156 | 0.048982 | 0.00046896
2017 | 2016-06-13 | C | 6 | 0.002486 | 1.8037e-05
2017 | 2016-07-05 | B | 78 | 0.036333 | 0.00023441
2017 | 2016-07-05 | B | 104 | 0.080412 | 0.00031254
2017 | 2016-06-28 | B | 7 | 0.007931 | 2.1038e-05
2017 | 2016-06-29 | B | 7 | 0.005995 | 2.1038e-05
2017 | 2016-06-13 | C | 18 | 0.003403 | 5.4111e-05
2017 | 2016-06-13 | C | 14 | 0.002496 | 4.2086e-05
2017 | 2016-06-12 | C | 200 | 0.15727 | 0.00060124
2017 | 2016-06-28 | B | 246 | 0.31496 | 0.00073934
2017 | 2016-07-01 | B | 2 | 0.001454 | 6.0106e-06
2017 | 2016-06-30 | B | 256 | 0.26697 | 0.00076937
2017 | 2016-07-06 | B | 82 | 0.090114 | 0.00024643
2017 | 2016-06-30 | B | 32 | 0.04318 | 9.6171e-05
2017 | 2016-07-06 | B | 2 | 0.002265 | 6.0104e-06
2017 | 2016-07-06 | B | 19 | 0.020791 | 5.7099e-05
2017 | 2016-06-13 | C | 13 | 0.006083 | 3.908e-05
2017 | 2016-06-13 | C | 13 | 0.003317 | 3.908e-05
2017 | 2016-06-14 | C | 9 | 0.001533 | 2.7055e-05
2017 | 2016-06-14 | C | 285 | 0.071966 | 0.00085674
2017 | 2016-07-04 | B | 20 | 0.018752 | 6.0105e-05
2017 | 2016-07-06 | B | 94 | 0.066978 | 0.00028249
2017 | 2016-06-14 | C | 2 | 0.000162 | 6.0122e-06
2017 | 2016-07-04 | B | 1 | 0.00131 | 3.0052e-06
2017 | 2016-07-05 | B | 56 | 0.052002 | 0.00016829
2017 | 2016-07-05 | B | 32 | 0.034043 | 9.6167e-05
2017 | 2016-07-06 | B | 22 | 0.017718 | 6.6115e-05
2017 | 2016-07-07 | B | 7 | 0.003945 | 2.1036e-05
2017 | 2016-07-06 | B | 12 | 0.014873 | 3.6063e-05
2017 | 2016-07-07 | B | 170 | 0.10863 | 0.00051088
2017 | 2016-07-07 | B | 3 | 0.003801 | 9.0155e-06
2017 | 2016-06-14 | C | 65 | 0.049097 | 0.0001954
2017 | 2016-06-21 | B | 39 | 0.052048 | 0.00011723
2017 | 2016-07-06 | B | 3 | 0.001041 | 9.0156e-06
2017 | 2016-07-06 | B | 3 | 0.001649 | 9.0156e-06
2017 | 2016-07-06 | B | 3 | 6.3e-05 | 9.0156e-06
2017 | 2016-07-07 | B | 6 | 0.005806 | 1.8031e-05
2017 | 2016-07-08 | B | 5 | 0.002133 | 1.5026e-05
2017 | 2016-06-14 | C | 2 | 0.000583 | 6.0122e-06
2017 | 2016-06-15 | C | 2 | 0.000773 | 6.0121e-06
2017 | 2016-06-15 | C | 356 | 0.1209 | 0.0010702
2017 | 2016-06-15 | C | 948 | 0.0219 | 0.0026694
2017 | 2016-06-15 | C | 1 | 0.000382 | 3.006e-06
2017 | 2016-06-16 | B | 41 | 0.03192 | 0.00012325
2017 | 2016-06-20 | B | 92 | 0.058027 | 0.00018336
2017 | 2016-06-15 | C | 27 | 0.009983 | 8.1164e-05
2017 | 2016-07-06 | B | 22 | 0.003992 | 6.6115e-05
2017 | 2016-06-15 | C | 12 | 0.004761 | 3.6073e-05
2017 | 2016-06-15 | C | 4 | 0.002476 | 1.2024e-05
2017 | 2016-07-07 | B | 27 | 0.021664 | 8.114e-05
2017 | 2016-06-15 | C | 1 | 0.000428 | 3.006e-06
2017 | 2016-06-21 | B | 363 | 0.42336 | 0.0010911
2017 | 2016-06-17 | B | 234 | 0.053458 | 0.0007034
2017 | 2016-07-05 | B | 3 | 0.001721 | 9.0156e-06
2017 | 2016-07-07 | B | 12 | 0.003173 | 3.6062e-05
2017 | 2016-06-19 | B | 1 | 0.000447 | 3.0058e-06
2017 | 2016-06-16 | C | 208 | 0 | 0
2017 | 2016-07-05 | B | 20 | 0.010037 | 6.0105e-05
2017 | 2016-07-07 | B | 27 | 0.013823 | 8.114e-05
2017 | 2016-07-05 | B | 246 | 0.25875 | 0.00073929
2017 | 2016-07-08 | B | 21 | 0.003597 | 6.3108e-05
2017 | 2016-07-12 | B | 6 | 0.004309 | 1.803e-05
2017 | 2016-07-13 | B | 8 | 0.009183 | 2.404e-05
2017 | 2016-07-14 | B | 55 | 0.032611 | 0.00016527
2017 | 2016-06-17 | B | 2 | 0.001154 | 6.0119e-06
2017 | 2016-07-12 | B | 17 | 0.005823 | 5.1086e-05
2017 | 2016-07-08 | B | 2 | 0.000306 | 6.0103e-06
2017 | 2016-06-16 | C | 314 | 0.066383 | 0.00094389
2017 | 2016-06-16 | C | 1 | 0.000471 | 3.006e-06
2017 | 2016-06-17 | C | 4 | 0.000589 | 1.2024e-05
2017 | 2016-06-17 | C | 728 | 0.049355 | 0.0025431
2017 | 2016-07-08 | B | 5 | 0.003485 | 1.5026e-05
2017 | 2016-07-04 | B | 69 | 0.027993 | 0.00020736
2017 | 2016-06-17 | C | 5 | 1.5e-05 | 1.503e-05
2017 | 2016-06-17 | C | 3 | 0.000369 | 9.0179e-06
2017 | 2016-06-27 | B | 4 | 0.002139 | 1.2022e-05
2017 | 2016-06-17 | C | 3 | 0.000784 | 9.0179e-06
2017 | 2016-06-17 | C | 24 | 0.00646 | 7.2143e-05
2017 | 2016-06-17 | C | 254 | 0.046054 | 0.00076352
2017 | 2016-06-18 | C | 42 | 0.009549 | 0.00012625
2017 | 2016-06-18 | C | 35 | 0.004523 | 0.00010521
2017 | 2016-06-18 | C | 1 | 0.000425 | 3.0059e-06
2017 | 2016-06-19 | C | 8 | 0.012793 | 2.4047e-05
2017 | 2016-06-19 | C | 6 | 0.001053 | 1.8035e-05
2017 | 2016-06-19 | C | 270 | 0 | 0.00081159
2017 | 2016-06-19 | C | 674 | 0.22986 | 0.002026
2017 | 2016-06-19 | C | 1761 | 0.93756 | 0.0095828
2017 | 2016-06-19 | C | 6 | 0.001794 | 1.8035e-05
2017 | 2016-06-19 | C | 4 | 0.001285 | 1.2023e-05
2017 | 2016-06-20 | C | 4 | 0.000517 | 1.2023e-05
2017 | 2016-07-11 | B | 3 | 0.000145 | 9.0152e-06
2017 | 2016-07-11 | B | 8 | 0.00125 | 2.4041e-05
2017 | 2016-07-11 | B | 8 | 0.000721 | 2.4041e-05
2017 | 2016-07-13 | B | 6 | 0.001929 | 1.803e-05
2017 | 2016-07-13 | B | 1 | 0.000171 | 3.005e-06
2017 | 2016-07-25 | B | 7 | 0.00063 | 2.1032e-05
2017 | 2016-07-15 | B | 107 | 0.009967 | 0.00032153
2017 | 2016-07-13 | B | 7 | 0.001304 | 2.1035e-05
2017 | 2016-07-13 | B | 7 | 0.000883 | 2.1035e-05
2017 | 2016-07-11 | B | 99 | 0.05236 | 0.0002975
2017 | 2016-07-12 | B | 3 | 0.000793 | 9.0151e-06
2017 | 2016-07-12 | B | 33 | 0.032129 | 9.9166e-05
2017 | 2016-07-13 | B | 36 | 0.01526 | 0.00010818
2017 | 2016-07-18 | B | 64 | 0.0225 | 0.00019231
2017 | 2016-06-20 | C | 6 | 0.005732 | 1.8035e-05
2017 | 2016-06-21 | C | 2 | 0.000438 | 6.0115e-06
2017 | 2016-06-27 | B | 48 | 0.01356 | 0.00014426
2017 | 2016-06-20 | C | 5 | 0.000976 | 1.5029e-05
2017 | 2016-07-10 | B | 1 | 0.000993 | 3.005e-06
2017 | 2016-06-21 | C | 17 | 0.002912 | 5.1098e-05
2017 | 2016-06-21 | C | 23 | 0.000138 | 6.9133e-05
2017 | 2016-06-21 | C | 4 | 0.000264 | 1.2023e-05
2017 | 2016-06-21 | C | 11 | 0.002876 | 3.3064e-05
2017 | 2016-07-12 | B | 1365 | 0.25271 | 0.010268
2017 | 2016-06-21 | C | 1 | 0.00039 | 3.0057e-06
2017 | 2016-06-22 | C | 39 | 0.049146 | 0.00011722
2017 | 2016-07-12 | B | 26 | 0.030392 | 7.8131e-05
2017 | 2016-06-22 | C | 1 | 0.000323 | 3.0057e-06
2017 | 2016-07-19 | B | 18 | 0.019363 | 5.4087e-05
2017 | 2016-06-22 | C | 8 | 0.001226 | 2.4046e-05
2017 | 2016-07-17 | B | 37 | 0.027016 | 0.00011118
2017 | 2016-07-12 | B | 19 | 0.001499 | 5.7096e-05
2017 | 2016-07-19 | B | 90 | 0.028666 | 0.00027043
2017 | 2016-07-19 | B | 16 | 0.015673 | 4.8077e-05
2017 | 2016-07-19 | B | 58 | 0.023702 | 0.00017428
2017 | 2016-07-18 | B | 7 | 0.000988 | 2.1034e-05
2017 | 2016-07-13 | B | 51 | 0.046436 | 0.00015326
2017 | 2016-07-18 | B | 2 | 0.000282 | 6.0097e-06
2017 | 2016-07-18 | B | 7 | 0.001262 | 2.1034e-05
2017 | 2016-07-20 | B | 2 | 0.000192 | 6.0095e-06
2017 | 2016-07-07 | B | 11 | 0.006965 | 3.3057e-05
2017 | 2016-07-20 | B | 5 | 0.000631 | 1.5024e-05
2017 | 2016-07-20 | B | 1 | 0.000177 | 3.0047e-06
2017 | 2016-07-22 | B | 4 | 0.001526 | 1.2019e-05
2017 | 2016-07-12 | B | 70 | 0.056164 | 0.00021035
2017 | 2016-07-22 | B | 5 | 0.000285 | 1.5024e-05
2017 | 2016-06-23 | C | 240 | 0.099491 | 0.00094379
2017 | 2016-06-23 | C | 264 | 0.076204 | 0.0010159
2017 | 2016-06-23 | C | 5 | 0.002136 | 1.5028e-05
2017 | 2016-06-23 | C | 367 | 0.1825 | 0.0011031
2017 | 2016-06-23 | C | 3 | 0.000459 | 9.017e-06
2017 | 2016-06-23 | C | 575 | 0.19298 | 0.0017283
2017 | 2016-06-23 | C | 179 | 0.03215 | 0.00053802
2017 | 2016-06-23 | C | 13 | 0.005534 | 3.9074e-05
2017 | 2016-07-01 | B | 7 | 0.006984 | 2.1037e-05
2017 | 2016-06-23 | C | 3 | 0.000402 | 9.017e-06
2017 | 2016-07-15 | B | 8 | 0.006009 | 2.404e-05
2017 | 2016-06-23 | C | 372 | 0.016024 | 0.0011181
2017 | 2016-06-23 | C | 199 | 0.0127 | 0.00059813
2017 | 2016-06-23 | C | 427 | 0.046381 | 0.0012834
2017 | 2016-06-23 | C | 1 | 0.000471 | 3.0056e-06
2017 | 2016-06-24 | C | 2 | 0.001766 | 6.0112e-06
2017 | 2016-06-24 | C | 629 | 0.10539 | 0.0018905
2017 | 2016-06-27 | B | 4 | 0.002368 | 1.2022e-05
2017 | 2016-06-24 | C | 69 | 0.020795 | 0.00020739
2017 | 2016-06-24 | C | 8 | 0.002358 | 2.4045e-05
2017 | 2016-06-25 | C | 1 | 0.000108 | 3.0055e-06
2017 | 2016-06-24 | C | 20 | 0.003185 | 6.0113e-05
2017 | 2016-06-24 | C | 291 | 0.029451 | 0.00087464
2017 | 2016-06-25 | C | 24 | 0.036932 | 7.2134e-05
2017 | 2016-06-25 | C | 145 | 0 | 0.00043581
2017 | 2016-06-25 | C | 131 | 0.081181 | 0.00039373
2017 | 2016-06-25 | C | 786 | 0.19843 | 0.0023624
2017 | 2016-06-25 | C | 201 | 0.082765 | 0.00060412
2017 | 2016-06-25 | C | 144 | 0.032532 | 0.00043281
2017 | 2016-06-26 | C | 4 | 0.001018 | 1.2022e-05
2017 | 2016-06-26 | C | 1 | 0.00028 | 3.0055e-06
2017 | 2016-06-26 | C | 1 | 0.000106 | 3.0055e-06
2017 | 2016-06-26 | C | 1 | 0.000485 | 3.0055e-06
2017 | 2016-06-26 | C | 5 | 0.001643 | 1.5028e-05
2017 | 2016-06-26 | C | 2 | 0.000372 | 6.011e-06
2017 | 2016-06-26 | C | 144 | 0.023225 | 0.0004328
2017 | 2016-06-26 | C | 235 | 0.055669 | 0.00088363
2017 | 2016-06-26 | C | 1 | 0.000465 | 3.0055e-06
2017 | 2016-06-26 | C | 1929 | 0.45675 | 0.0057977
2017 | 2016-06-26 | C | 43 | 0.071468 | 0.00012924
2017 | 2016-06-26 | C | 482 | 0.1405 | 0.0025938
2017 | 2016-06-26 | C | 71 | 0.031549 | 0.00021339
2017 | 2016-06-26 | C | 273 | 0.71227 | 0.00082051
2017 | 2016-06-26 | C | 587 | 0.14234 | 0.0017643
2017 | 2016-06-27 | C | 3 | 0.000553 | 9.0165e-06
2017 | 2016-06-27 | C | 24 | 0.005548 | 7.2132e-05
2017 | 2016-07-14 | B | 6 | 0.005625 | 1.803e-05
2017 | 2016-07-19 | B | 21 | 0.022779 | 6.3101e-05
2017 | 2016-06-27 | C | 2 | 0.000845 | 6.011e-06
2017 | 2016-07-21 | B | 88 | 0.069127 | 0.00026442
2017 | 2016-07-21 | B | 1 | 0.001024 | 3.0047e-06
2017 | 2016-06-27 | C | 341 | 0.068875 | 0.0010249
2017 | 2016-06-27 | C | 72 | 0.078551 | 0.0002164
2017 | 2016-06-27 | C | 4 | 0.000168 | 1.2022e-05
2017 | 2016-06-27 | C | 2 | 0.001094 | 6.011e-06
2017 | 2016-06-27 | C | 4 | 0.003558 | 1.2022e-05
2017 | 2016-06-27 | C | 1 | 0.000334 | 3.0055e-06
2017 | 2016-06-27 | C | 1 | 9.6e-05 | 3.0055e-06
2017 | 2016-06-27 | C | 31 | 0.023624 | 9.317e-05
2017 | 2016-06-28 | C | 51 | 0.050824 | 0.00015328
2017 | 2016-07-25 | B | 2 | 0.001784 | 6.0092e-06
2017 | 2016-07-22 | B | 11 | 0.007424 | 3.3052e-05
2017 | 2016-06-28 | C | 34 | 0.008047 | 0.00010219
2017 | 2016-07-14 | B | 15 | 0.004552 | 4.5075e-05
2017 | 2016-07-12 | B | 127 | 0.065025 | 0.00038164
2017 | 2016-07-14 | B | 7 | 0.000988 | 2.1035e-05
2017 | 2016-07-19 | B | 7 | 0.005384 | 2.1034e-05
2017 | 2016-07-15 | B | 139 | 0.10561 | 0.00041769
2017 | 2016-07-27 | B | 8 | 0.005288 | 2.4036e-05
2017 | 2016-06-28 | C | 1 | 0.003817 | 3.0054e-06
2017 | 2016-06-28 | C | 880 | 0 | 0.00025546
2017 | 2016-06-29 | C | 134 | 0.009578 | 0.00040272
2017 | 2016-06-29 | C | 227 | 0.035314 | 0.00068223
2017 | 2016-07-12 | B | 6 | 0.004543 | 1.803e-05
2017 | 2016-06-29 | C | 143 | 0.07866 | 0.00056802
2017 | 2016-07-12 | B | 57 | 0.030053 | 0.00017129
2017 | 2016-06-29 | C | 3 | 0.002267 | 9.0162e-06
2017 | 2016-06-29 | C | 54 | 0.00407 | 0.00016229
2017 | 2016-07-13 | B | 76 | 0.064491 | 0.00022838
2017 | 2016-07-21 | B | 25 | 0.019455 | 7.5119e-05
2017 | 2016-07-20 | B | 48 | 0.052644 | 0.00014423
2017 | 2016-06-29 | C | 4 | 0.001235 | 1.2022e-05
2017 | 2016-06-29 | C | 120 | 0.12965 | 0.00090763
2017 | 2016-06-29 | C | 2 | 0.000108 | 6.0108e-06
2017 | 2016-06-30 | C | 122 | 0.049943 | 0.00057703
2017 | 2016-06-30 | C | 1089 | 0.076214 | 0.0027138
2017 | 2016-06-30 | C | 21 | 0.003678 | 6.3112e-05
2017 | 2016-06-30 | C | 51 | 0.013706 | 0.00015327
2017 | 2016-07-01 | B | 262 | 0.16456 | 0.0007874
2017 | 2016-07-20 | B | 42 | 0.033064 | 0.0001262
2017 | 2016-06-30 | C | 7 | 0.001283 | 2.1037e-05
2017 | 2016-06-30 | C | 6 | 0.002921 | 1.8032e-05
2017 | 2016-06-30 | C | 1 | 0.000761 | 3.0053e-06
2017 | 2016-07-19 | B | 2 | 0.001838 | 6.0096e-06
2017 | 2016-06-30 | C | 254 | 0.05196 | 0.00076336
2017 | 2016-06-30 | C | 45 | 0.009061 | 0.00013524
2017 | 2016-07-01 | C | 2 | 0.000534 | 6.0106e-06
2017 | 2016-07-01 | C | 182 | 0.10064 | 0.00054697
2017 | 2016-06-30 | C | 708 | 0.07148 | 0.0021278
2017 | 2016-07-01 | C | 10 | 0.003936 | 3.0053e-05
2017 | 2016-07-01 | C | 25 | 0.032842 | 8.7155e-05
2017 | 2016-07-01 | C | 112 | 0.01109 | 0.0003366
2017 | 2016-07-01 | C | 3 | 0.000198 | 9.0159e-06
2017 | 2016-07-01 | C | 20 | 0.007393 | 6.0107e-05
2017 | 2016-07-02 | C | 440 | 0.10125 | 0.0013223
2017 | 2016-07-02 | C | 361 | 0.13595 | 0.0010849
2017 | 2016-07-02 | C | 330 | 0.002148 | 0.00099175
2017 | 2016-07-02 | C | 22 | 0.005884 | 6.6117e-05
2017 | 2016-07-02 | C | 171 | 0.038814 | 0.00051391
2017 | 2016-07-02 | C | 1 | 0.000525 | 3.0053e-06
2017 | 2016-07-03 | C | 238 | 0.046473 | 0.00071526
2017 | 2016-07-03 | C | 1 | 0.000508 | 3.0052e-06
2017 | 2016-07-03 | C | 228 | 0.041538 | 0.0013253
2017 | 2016-07-03 | C | 4 | 0.00143 | 1.2021e-05
2017 | 2016-07-03 | C | 190 | 0.081463 | 0.000571
2017 | 2016-07-04 | C | 28 | 0.007068 | 8.4147e-05
2017 | 2016-07-04 | C | 1 | 0.000338 | 3.0052e-06
2017 | 2016-07-11 | B | 113 | 0.10362 | 0.00049584
2017 | 2016-07-14 | B | 94 | 0.099993 | 0.00028247
2017 | 2016-07-04 | C | 89 | 0.005135 | 0.00026747
2017 | 2016-07-17 | B | 1 | 4e-06 | 3.0048e-06
2017 | 2016-07-05 | C | 7 | 0.002713 | 2.1037e-05
2017 | 2016-07-04 | C | 1 | 0.00034 | 3.0052e-06
2017 | 2016-07-05 | C | 362 | 0.085179 | 0.0028309
2017 | 2016-07-25 | B | 63 | 0.061885 | 0.00018929
2017 | 2016-07-05 | C | 2 | 0.001899 | 6.0104e-06
2017 | 2016-07-05 | C | 1 | 0.000519 | 3.0052e-06
2017 | 2016-07-05 | C | 3 | 0.001866 | 9.0156e-06
2017 | 2016-07-05 | C | 254 | 0.0632 | 0.0014305
2017 | 2016-07-05 | C | 6 | 0.00213 | 1.8031e-05
2017 | 2016-07-06 | C | 10 | 0.003561 | 3.0052e-05
2017 | 2016-07-21 | B | 21 | 0.018172 | 6.31e-05
2017 | 2016-07-26 | B | 67 | 0.075692 | 0.00020131
2017 | 2016-07-28 | B | 67 | 0.028987 | 0.0002013
2017 | 2016-07-06 | C | 178 | 0.022776 | 0.00053493
2017 | 2016-07-15 | B | 20 | 0.015252 | 6.0099e-05
2017 | 2016-07-09 | B | 32 | 0.018383 | 9.6164e-05
2017 | 2016-07-26 | B | 5 | 0.003335 | 1.5023e-05
2017 | 2016-07-22 | B | 76 | 0.06085 | 0.00022836
2017 | 2016-07-07 | C | 324 | 0.07047 | 0.00097368
2017 | 2016-07-24 | B | 47 | 0.000442 | 0.00014122
2017 | 2016-07-26 | B | 3 | 0.003001 | 9.0138e-06
2017 | 2016-07-08 | C | 183 | 0.09514 | 0.00054994
2017 | 2016-07-07 | C | 288 | 0.050662 | 0.00086549
2017 | 2016-07-07 | C | 97 | 0.026011 | 0.00053492
2017 | 2016-07-08 | C | 2524 | 0.18886 | 0.007585
2017 | 2016-07-08 | C | 6 | 0.003033 | 1.8031e-05
2017 | 2016-07-08 | C | 33 | 0.043522 | 9.917e-05
2017 | 2016-07-07 | C | 1 | 0.000658 | 3.0051e-06
2017 | 2016-07-11 | C | 59 | 0.006648 | 0.0001773
2017 | 2016-07-08 | C | 86 | 0.019228 | 0.00025844
2017 | 2016-07-08 | C | 2 | 0.002325 | 6.0103e-06
2017 | 2016-07-08 | C | 50 | 0.006511 | 0.00015026
2017 | 2016-07-08 | C | 79 | 0.019399 | 0.00023741
2017 | 2016-07-08 | C | 792 | 0.062792 | 0.0023801
2017 | 2016-07-09 | C | 41 | 0.012813 | 0.00012321
2017 | 2016-07-08 | C | 115 | 0.009507 | 0.00015026
2017 | 2016-08-01 | B | 9 | 0.00995 | 2.704e-05
2017 | 2016-07-08 | C | 14 | 0.00122 | 4.2072e-05
2017 | 2016-08-05 | B | 4 | 0.000684 | 1.2017e-05
2017 | 2016-08-05 | B | 2 | 0.000342 | 6.0085e-06
2017 | 2016-07-25 | B | 3 | 0.00082 | 9.0139e-06
2017 | 2016-07-08 | C | 1139 | 0.3412 | 0.0037504
2017 | 2016-07-27 | B | 113 | 0.080638 | 0.00067903
2017 | 2016-07-08 | C | 1015 | 0.19468 | 0.0034349
2017 | 2016-07-08 | C | 86 | 0.056125 | 0.00025844
2017 | 2016-07-08 | C | 196 | 0.13819 | 0.0007002
2017 | 2016-07-08 | C | 316 | 0.15352 | 0.00094963
2017 | 2016-07-08 | C | 154 | 0.1039 | 0.00088952
2017 | 2016-07-08 | C | 324 | 0.021209 | 0.00097367
2017 | 2016-07-08 | C | 72 | 0.008222 | 0.00021637
2017 | 2016-07-08 | C | 792 | 0.13142 | 0.0024823
2017 | 2016-07-08 | C | 1 | 0.003872 | 3.0051e-06
2017 | 2016-07-08 | C | 15 | 0.008142 | 4.5077e-05
2017 | 2016-07-10 | C | 49 | 0.009187 | 0.00014725
2017 | 2016-07-08 | C | 22 | 0.010698 | 6.6113e-05
2017 | 2016-07-08 | C | 208 | 0.10069 | 0.00062507
2017 | 2016-07-08 | C | 7 | 0.003175 | 2.1036e-05
2017 | 2016-07-08 | C | 2 | 0.006424 | 6.0103e-06
2017 | 2016-07-08 | C | 7 | 0.003256 | 2.1036e-05
2017 | 2016-07-08 | C | 1 | 0.00093 | 3.0051e-06
2017 | 2016-07-08 | C | 4 | 0.011903 | 1.2021e-05
2017 | 2016-07-08 | C | 1 | 0.004146 | 3.0051e-06
2017 | 2016-07-08 | C | 6 | 0.000239 | 3.0051e-06
2017 | 2016-07-08 | C | 1 | 0.002467 | 3.0051e-06
2017 | 2016-07-08 | C | 103 | 0.008188 | 0.00030953
2017 | 2016-07-08 | C | 2 | 0.000634 | 6.0103e-06
2017 | 2016-07-08 | C | 295 | 0.12849 | 0.0016498
2017 | 2016-07-08 | C | 258 | 0 | 9.0154e-06
2017 | 2016-07-09 | C | 784 | 0.14413 | 0.00528
2017 | 2016-07-09 | C | 891 | 0.034049 | 0.0026776
2017 | 2016-07-09 | C | 2 | 0.000606 | 6.0102e-06
2017 | 2016-07-09 | C | 9 | 0.001406 | 2.7046e-05
2017 | 2016-07-09 | C | 6 | 0.000739 | 1.8031e-05
2017 | 2016-07-09 | C | 1 | 0.001714 | 3.0051e-06
2017 | 2016-07-09 | C | 1 | 0.000945 | 3.0051e-06
2017 | 2016-07-09 | C | 19 | 0.025198 | 5.7097e-05
2017 | 2016-07-09 | C | 280 | 0.02168 | 0.00084143
2017 | 2016-07-09 | C | 9 | 0.006807 | 2.7046e-05
2017 | 2016-07-09 | C | 4 | 0.015189 | 1.202e-05
2017 | 2016-07-09 | C | 367 | 0.063189 | 0.0011029
2017 | 2016-07-10 | C | 427 | 0.20136 | 0.0036692
2017 | 2016-07-10 | C | 1 | 0.000565 | 3.005e-06
2017 | 2016-07-10 | C | 507 | 0.002301 | 0.0015236
2017 | 2016-07-12 | C | 4 | 0.003497 | 1.202e-05
2017 | 2016-08-05 | B | 2 | 0.000342 | 6.0085e-06
2017 | 2016-08-02 | B | 34 | 0.031768 | 0.00010215
2017 | 2016-07-19 | B | 178 | 0.14334 | 0.00053486
2017 | 2016-08-09 | B | 22 | 0.02485 | 6.6091e-05
2017 | 2016-08-16 | B | 22 | 0.020222 | 6.6086e-05
2017 | 2016-08-23 | B | 12 | 0.013516 | 3.6044e-05
2017 | 2016-08-25 | B | 12 | 0.011606 | 3.6044e-05
2017 | 2016-08-01 | B | 8 | 0.011464 | 2.4035e-05
2017 | 2016-07-11 | C | 53 | 0.010989 | 0.00015927
2017 | 2016-07-28 | B | 21 | 0.024354 | 6.3095e-05
2017 | 2016-08-01 | B | 16 | 0.013555 | 4.807e-05
2017 | 2016-07-09 | C | 3 | 0.000411 | 9.0153e-06
2017 | 2016-08-01 | B | 18 | 0.01601 | 5.4079e-05
2017 | 2016-08-01 | B | 336 | 0.074829 | 0.0015593
2017 | 2016-08-02 | B | 61 | 0.065976 | 0.00018327
2017 | 2016-08-04 | B | 22 | 0.022934 | 6.6095e-05
2017 | 2016-08-04 | B | 61 | 0.065791 | 0.00018326
2017 | 2016-08-02 | B | 4 | 0.004085 | 1.2017e-05
2017 | 2016-08-11 | B | 22 | 0.022602 | 6.609e-05
2017 | 2016-08-02 | B | 1 | 0.000576 | 3.0043e-06
2017 | 2016-08-03 | B | 29 | 0.028315 | 8.7126e-05
2017 | 2016-08-03 | B | 1 | 0.000351 | 3.0043e-06
2017 | 2016-08-03 | B | 5 | 0.003155 | 1.5022e-05
2017 | 2016-07-11 | C | 158 | 0.10591 | 0.00057998
2017 | 2016-07-12 | C | 2669 | 0.49989 | 0.0080205
2017 | 2016-08-18 | B | 12 | 0.01276 | 3.6046e-05
2017 | 2016-07-12 | C | 86 | 0 | 0.00025843
2017 | 2016-08-01 | B | 25 | 0.027941 | 7.511e-05
2017 | 2016-08-04 | B | 2 | 0.002439 | 6.0086e-06
2017 | 2016-08-10 | B | 39 | 0.020503 | 0.00011716
2017 | 2016-08-08 | B | 2 | 0.002503 | 6.0083e-06
2017 | 2016-08-09 | B | 2 | 0.002298 | 6.0083e-06
2017 | 2016-07-12 | C | 15 | 0.002208 | 4.5076e-05
2017 | 2016-07-12 | C | 2 | 0.000384 | 6.01e-06
2017 | 2016-07-26 | B | 61 | 0.051504 | 0.00018328
2017 | 2016-08-09 | B | 61 | 0.057358 | 0.00018325
2017 | 2016-07-13 | B | 86 | 0.064866 | 0.00025843
2017 | 2016-08-01 | B | 34 | 0.017059 | 0.00010215
2017 | 2016-07-12 | C | 4 | 0.000793 | 1.202e-05
2017 | 2016-07-12 | C | 301 | 0.15086 | 0.00090452
2017 | 2016-07-13 | C | 33 | 0.01775 | 9.9165e-05
2017 | 2016-07-13 | C | 287 | 0.082673 | 0.0019623
2017 | 2016-07-13 | C | 2061 | 0.1887 | 0.0061933
2017 | 2016-08-04 | B | 81 | 0.026135 | 0.00024335
2017 | 2016-07-13 | C | 3 | 0.000369 | 9.015e-06
2017 | 2016-07-13 | C | 4 | 0.000838 | 1.202e-05
2017 | 2016-08-01 | B | 16 | 0.011633 | 4.807e-05
2017 | 2016-07-28 | B | 4 | 0.001802 | 1.2018e-05
2017 | 2016-07-28 | B | 6 | 0.001838 | 1.8027e-05
2017 | 2016-08-01 | B | 28 | 0.00498 | 8.4123e-05
2017 | 2016-07-13 | C | 1647 | 0.024216 | 0.0049492
2017 | 2016-07-13 | C | 76 | 0.063729 | 0.00023139
2017 | 2016-07-13 | C | 1 | 0.000411 | 3.005e-06
2017 | 2016-07-13 | C | 249 | 0.02862 | 0.00074825
2017 | 2016-07-13 | C | 274 | 0.13821 | 0.00082337
2017 | 2016-07-13 | C | 1 | 0.00018 | 3.005e-06
2017 | 2016-07-14 | C | 77 | 0.105 | 0.00044474
2017 | 2016-07-14 | C | 256 | 0.089507 | 0.00086243
2017 | 2016-07-14 | C | 238 | 0.043276 | 0.00073021
2017 | 2016-07-14 | C | 17 | 0.006589 | 5.1085e-05
2017 | 2016-07-14 | C | 125 | 0.061768 | 0.00075124
2017 | 2016-07-14 | C | 340 | 0.10804 | 0.0010217
2017 | 2016-07-14 | C | 903 | 0.083987 | 0.0027135
2017 | 2016-07-14 | C | 226 | 0.07599 | 0.00067913
2017 | 2016-07-14 | C | 27 | 0.008681 | 8.1134e-05
2017 | 2016-07-14 | C | 145 | 0.097723 | 0.00086543
2017 | 2016-07-14 | C | 17 | 0.008057 | 5.1085e-05
2017 | 2016-07-14 | C | 39 | 0.026851 | 0.00011719
2017 | 2016-07-14 | C | 22 | 0.004873 | 6.6109e-05
2017 | 2016-07-14 | C | 6 | 0.002601 | 1.803e-05
2017 | 2016-07-14 | C | 66 | 0.041252 | 0.00019833
2017 | 2016-07-14 | C | 1 | 0.000706 | 3.0049e-06
2017 | 2016-07-14 | C | 3 | 0.004182 | 9.0149e-06
2017 | 2016-07-14 | C | 1 | 0.000276 | 3.0049e-06
2017 | 2016-07-14 | C | 2 | 0.002269 | 6.0099e-06
2017 | 2016-07-14 | C | 168 | 0.039654 | 0.00050484
2017 | 2016-07-14 | C | 35 | 0.006205 | 0.00010517
2017 | 2016-08-04 | B | 40 | 0.020068 | 0.00012017
2017 | 2016-07-14 | C | 5 | 0.001307 | 1.5025e-05
2017 | 2016-07-14 | C | 42 | 0.002397 | 0.00012621
2017 | 2016-07-14 | C | 1 | 0.001063 | 3.0049e-06
2017 | 2016-07-14 | C | 40 | 0.036033 | 0.0001202
2017 | 2016-07-14 | C | 5 | 0.003832 | 1.5025e-05
2017 | 2016-07-14 | C | 23 | 0.004561 | 6.9114e-05
2017 | 2016-07-14 | C | 408 | 0.024929 | 0.001226
2017 | 2016-07-14 | C | 10 | 0.001021 | 3.005e-05
2017 | 2016-08-02 | B | 29 | 0.022304 | 8.7127e-05
2017 | 2016-07-14 | C | 780 | 0.09513 | 0.0023439
2017 | 2016-07-14 | C | 155 | 0.032627 | 0.00046577
2017 | 2016-07-14 | C | 8 | 0.000614 | 2.404e-05
2017 | 2016-07-14 | C | 1 | 0.001033 | 3.0049e-06
2017 | 2016-07-14 | C | 7 | 0.020118 | 2.1035e-05
2017 | 2016-07-14 | C | 20 | 0.003388 | 6.01e-05
2017 | 2016-07-14 | C | 18 | 0.003852 | 5.409e-05
2017 | 2016-07-14 | C | 1 | 0.000364 | 3.0049e-06
2017 | 2016-07-14 | C | 33 | 0.009005 | 9.9164e-05
2017 | 2016-07-14 | C | 780 | 0.51402 | 0.0023439
2017 | 2016-07-14 | C | 33 | 0.031822 | 9.9164e-05
2017 | 2016-07-14 | C | 4044 | 0.14977 | 0.012152
2017 | 2016-07-15 | C | 6 | 0.002702 | 1.803e-05
2017 | 2016-08-08 | B | 3 | 0.000558 | 9.0125e-06
2017 | 2016-08-08 | B | 7 | 0.003091 | 2.1029e-05
2017 | 2016-08-08 | B | 6 | 0.001027 | 1.8025e-05
2017 | 2016-08-09 | B | 4 | 0.000684 | 1.2017e-05
2017 | 2016-08-09 | B | 4 | 0.000204 | 1.2017e-05
2017 | 2016-08-11 | B | 3 | 0.000243 | 9.0122e-06
2017 | 2016-08-12 | B | 3 | 0.000919 | 9.0122e-06
2017 | 2016-08-11 | B | 4 | 0.000324 | 1.2016e-05
2017 | 2016-08-12 | B | 7 | 0.000462 | 2.1028e-05
2017 | 2016-08-12 | B | 7 | 0.000567 | 2.1028e-05
2017 | 2016-08-15 | B | 7 | 0.004983 | 2.1028e-05
2017 | 2016-08-15 | B | 1 | 0.000216 | 3.0039e-06
2017 | 2016-08-17 | B | 3 | 0.002944 | 9.0117e-06
2017 | 2016-08-17 | B | 1 | 0.000171 | 3.0039e-06
2017 | 2016-07-15 | C | 257 | 0.015767 | 0.00077227
2017 | 2016-07-15 | C | 35 | 0.008715 | 0.00010517
2017 | 2016-07-15 | C | 163 | 0.017204 | 0.00048981
2017 | 2016-07-15 | C | 2 | 0.0006 | 6.0099e-06
2017 | 2016-07-15 | C | 120 | 0.068129 | 0.00036059
2017 | 2016-08-18 | B | 5 | 0.001156 | 1.5019e-05
2017 | 2016-08-18 | B | 2 | 0.000384 | 6.0077e-06
2017 | 2016-07-15 | C | 3 | 0.000873 | 9.0148e-06
2017 | 2016-08-18 | B | 6 | 0.000594 | 1.8023e-05
2017 | 2016-07-15 | C | 1 | 0.000517 | 3.0049e-06
2017 | 2016-08-29 | B | 6 | 0.000576 | 1.8021e-05
2017 | 2016-07-15 | C | 243 | 0.048448 | 0.00092252
2017 | 2016-08-09 | B | 50 | 0.053173 | 0.00015021
2017 | 2016-08-07 | B | 1 | 0.000943 | 3.0042e-06
2017 | 2016-07-15 | C | 422 | 0.10414 | 0.0012681
2017 | 2016-07-15 | C | 12 | 0.001375 | 3.6059e-05
2017 | 2016-08-07 | B | 1 | 0.000292 | 3.0042e-06
2017 | 2016-07-15 | C | 414 | 0.10469 | 0.0012441
2017 | 2016-07-15 | C | 674 | 0.06616 | 0.0020253
2017 | 2016-07-15 | C | 13 | 0.009318 | 3.9064e-05
2017 | 2016-07-15 | C | 6 | 0.001374 | 1.803e-05
2017 | 2016-07-15 | C | 1 | 0.001109 | 3.0049e-06
2017 | 2016-07-15 | C | 2 | 0.000658 | 6.0099e-06
2017 | 2016-07-15 | C | 7 | 0.000862 | 2.1035e-05
2017 | 2016-07-16 | C | 674 | 0.21709 | 0.0020253
2017 | 2016-07-16 | C | 7 | 0.001493 | 2.1034e-05
2017 | 2016-07-16 | C | 1 | 0.000335 | 3.0049e-06
2017 | 2016-07-16 | C | 27 | 0.000574 | 8.1133e-05
2017 | 2016-07-16 | C | 522 | 0.095185 | 0.0015686
2017 | 2016-07-16 | C | 3 | 0.001956 | 9.0147e-06
2017 | 2016-07-16 | C | 120 | 0.067003 | 0.00036059
2017 | 2016-07-17 | C | 1 | 0.000495 | 3.0048e-06
2017 | 2016-07-17 | C | 155 | 0.055552 | 0.00046576
2017 | 2016-07-17 | C | 25 | 0.004179 | 7.5122e-05
2017 | 2016-07-17 | C | 16 | 0.002098 | 4.8078e-05
2017 | 2016-07-17 | C | 17 | 0.05115 | 5.1083e-05
2017 | 2016-07-17 | C | 2347 | 0.020172 | 0.0070525
2017 | 2016-07-17 | C | 195 | 0.11948 | 0.0011629
2017 | 2016-07-17 | C | 3 | 0.000774 | 9.0146e-06
2017 | 2016-07-18 | C | 5 | 0.014071 | 1.5024e-05
2017 | 2016-07-18 | C | 289 | 0.082666 | 0.00086841
2017 | 2016-07-18 | C | 107 | 0.07878 | 0.00048378
2017 | 2016-07-18 | C | 143 | 0.058026 | 0.0004297
2017 | 2016-07-18 | C | 2 | 0.001604 | 6.0097e-06
2017 | 2016-08-10 | B | 99 | 0.11777 | 0.00029741
2017 | 2016-07-20 | B | 11 | 0.012163 | 3.3053e-05
2017 | 2016-07-18 | C | 82 | 0.01158 | 0.0002464
2017 | 2016-07-16 | C | 2 | 0.000318 | 6.0098e-06
2017 | 2016-07-18 | C | 96 | 0.000288 | 0.00028847
2017 | 2016-08-12 | B | 5 | 0.003536 | 1.502e-05
2017 | 2016-07-18 | C | 9 | 0.000192 | 2.7044e-05
2017 | 2016-07-19 | C | 6 | 0.001424 | 1.8029e-05
2017 | 2016-07-19 | C | 14 | 0.002818 | 4.2068e-05
2017 | 2016-07-19 | C | 408 | 0.052596 | 0.001226
2017 | 2016-08-15 | B | 16 | 0.011871 | 4.8063e-05
2017 | 2016-08-17 | B | 11 | 0.005352 | 3.3043e-05
2017 | 2016-08-09 | B | 4 | 0.003052 | 1.2017e-05
2017 | 2016-08-22 | B | 8 | 0.001754 | 2.403e-05
2017 | 2016-07-19 | C | 3 | 0.002397 | 9.0144e-06
2017 | 2016-07-19 | C | 17 | 0.00521 | 5.1082e-05
2017 | 2016-07-20 | B | 6 | 0.000667 | 1.8029e-05
2017 | 2016-07-20 | B | 4 | 0.001072 | 1.2019e-05
2017 | 2016-07-19 | C | 110 | 0.03011 | 0.00051383
2017 | 2016-07-19 | C | 51 | 0.028634 | 0.00015325
2017 | 2016-07-19 | C | 3 | 0.001532 | 9.0144e-06
2017 | 2016-07-19 | C | 41 | 0.036309 | 0.00019832
2017 | 2016-07-19 | C | 110 | 0.15643 | 0.0010908
2017 | 2016-07-19 | C | 429 | 0.063921 | 0.0012891
2017 | 2016-07-19 | C | 42 | 0.017276 | 0.0001262
2017 | 2016-07-19 | C | 5 | 0.000706 | 1.5024e-05
2017 | 2016-07-19 | C | 51 | 0.034428 | 0.00017728
2017 | 2016-07-19 | C | 43 | 0.045764 | 0.00012921
2017 | 2016-07-19 | C | 1 | 0.003064 | 6.0096e-06
2017 | 2016-07-19 | C | 1425 | 0.12007 | 0.0033864
2017 | 2016-07-19 | C | 383 | 0.10322 | 0.0011508
2017 | 2016-07-20 | C | 122 | 0.01359 | 0.00036659
2017 | 2016-07-20 | C | 256 | 0.036192 | 0.00076923
2017 | 2016-07-20 | C | 3 | 0.001181 | 9.0143e-06
2017 | 2016-07-20 | C | 1 | 0.000521 | 3.0047e-06
2017 | 2016-07-20 | C | 9 | 0.008031 | 2.7043e-05
2017 | 2016-07-20 | C | 3 | 0.00451 | 9.0143e-06
2017 | 2016-07-20 | C | 4 | 0.005212 | 1.2019e-05
2017 | 2016-07-20 | C | 4 | 0.006318 | 1.2019e-05
2017 | 2016-07-20 | C | 41 | 0.035497 | 0.0001232
2017 | 2016-07-20 | C | 2 | 0.000903 | 6.0095e-06
2017 | 2016-07-20 | C | 1 | 0.001528 | 3.0047e-06
2017 | 2016-07-20 | C | 7 | 0.002456 | 2.1034e-05
2017 | 2016-08-02 | B | 66 | 0.022208 | 0.00019829
2017 | 2016-07-20 | C | 4 | 0.003753 | 1.2019e-05
2017 | 2016-07-20 | C | 767 | 0 | 0.0023047
2017 | 2016-08-02 | B | 129 | 0.14224 | 0.00038756
2017 | 2016-08-04 | B | 26 | 0.020855 | 7.8112e-05
2017 | 2016-08-02 | B | 170 | 0.22319 | 0.00051074
2017 | 2016-07-20 | C | 58 | 0.015685 | 0.00017428
2017 | 2016-08-04 | B | 170 | 0.16492 | 0.00051073
2017 | 2016-07-20 | C | 127 | 0.030796 | 0.00038161
2017 | 2016-07-20 | C | 2 | 0.001469 | 6.0095e-06
2017 | 2016-08-09 | B | 2 | 0.002367 | 6.0083e-06
2017 | 2016-07-20 | C | 1 | 0.000198 | 3.0047e-06
2017 | 2016-08-03 | B | 23 | 0.014994 | 6.91e-05
2017 | 2016-07-20 | C | 28 | 0.026346 | 8.4134e-05
2017 | 2016-08-03 | B | 2 | 0.000582 | 6.0086e-06
2017 | 2016-08-04 | B | 4 | 0.003605 | 1.2017e-05
2017 | 2016-08-15 | B | 35 | 0.01167 | 0.00010514
2017 | 2016-07-20 | C | 70 | 0.013882 | 0.00021034
2017 | 2016-08-15 | B | 52 | 0.023587 | 0.00015621
2017 | 2016-08-10 | B | 1 | 0.000733 | 3.0041e-06
2017 | 2016-07-20 | C | 3 | 0.002271 | 9.0143e-06
2017 | 2016-07-20 | C | 2 | 0.000865 | 1.2019e-05
2017 | 2016-07-20 | C | 83 | 0.003898 | 0.0002494
2017 | 2016-07-21 | C | 41 | 0.016809 | 0.0001232
2017 | 2016-07-21 | C | 498 | 0.13606 | 0.0016286
2017 | 2016-08-09 | B | 4 | 0.003522 | 1.2017e-05
2017 | 2016-08-09 | B | 25 | 0.027241 | 7.5104e-05
2017 | 2016-08-16 | B | 25 | 0.029185 | 7.5098e-05
2017 | 2016-08-23 | B | 25 | 0.027409 | 7.5092e-05
2017 | 2016-08-11 | B | 40 | 0.045902 | 0.00012016
2017 | 2016-07-21 | C | 5 | 0.001592 | 1.5024e-05
2017 | 2016-08-15 | B | 11 | 0.0114 | 3.3044e-05
2017 | 2016-07-21 | C | 95 | 0.008849 | 0.00028545
2017 | 2016-08-17 | B | 6 | 0.006197 | 1.8023e-05
2017 | 2016-08-17 | B | 10 | 0.006368 | 3.0039e-05
2017 | 2016-07-21 | C | 12 | 0.001658 | 3.6057e-05
2017 | 2016-07-21 | C | 1 | 0.000353 | 3.0047e-06
2017 | 2016-07-21 | C | 1 | 0.000178 | 3.0047e-06
2017 | 2016-07-22 | C | 661 | 0.14128 | 0.0019861
2017 | 2016-07-22 | C | 103 | 0.019807 | 0.00030949
2017 | 2016-07-22 | C | 37 | 0.012075 | 0.00011118
2017 | 2016-08-03 | B | 148 | 0.021787 | 0.00088929
2017 | 2016-08-07 | B | 1 | 0.000408 | 3.0042e-06
2017 | 2016-07-22 | C | 1 | 0.000847 | 3.0047e-06
2017 | 2016-07-22 | C | 345 | 0.003936 | 0.00020132
2017 | 2016-07-23 | C | 15 | 0.002553 | 4.507e-05
2017 | 2016-07-22 | C | 24 | 0.004177 | 7.2114e-05
2017 | 2016-07-23 | C | 111 | 0.036688 | 0.00033352
2017 | 2016-07-23 | C | 433 | 0.2393 | 0.0015895
2017 | 2016-07-23 | C | 32 | 0.016959 | 9.615e-05
2017 | 2016-07-23 | C | 5 | 0.00054 | 1.5023e-05
2017 | 2016-07-23 | C | 43 | 0.012728 | 0.0001292
2017 | 2016-07-23 | C | 22 | 0.018919 | 6.6103e-05
2017 | 2016-07-23 | C | 314 | 0.08474 | 0.00094348
2017 | 2016-07-23 | C | 1 | 0.000432 | 3.0046e-06
2017 | 2016-07-23 | C | 274 | 0.16031 | 0.00082329
2017 | 2016-07-23 | C | 3402 | 1.9342 | 0.010222
2017 | 2016-07-24 | C | 58 | 0.20895 | 0.00017427
2017 | 2016-07-24 | C | 411 | 0.097737 | 0.0012349
2017 | 2016-07-24 | C | 63 | 0.047059 | 0.00028244
2017 | 2016-07-24 | C | 227 | 0.072041 | 0.00093746
2017 | 2016-07-24 | C | 679 | 0.10385 | 0.0036116
2017 | 2016-07-24 | C | 2 | 0.000676 | 6.0093e-06
2017 | 2016-07-24 | C | 2 | 0.001003 | 6.0093e-06
2017 | 2016-07-24 | C | 631 | 0 | 1.2019e-05
2017 | 2016-07-24 | C | 780 | 0.10339 | 0.0023436
2017 | 2016-07-24 | C | 105 | 0.06456 | 0.00031549
2017 | 2016-07-24 | C | 19 | 0.006893 | 5.7089e-05
2017 | 2016-07-24 | C | 101 | 0.04168 | 0.00030347
2017 | 2016-07-24 | C | 2 | 0.000398 | 6.0093e-06
2017 | 2016-07-24 | C | 7 | 0.000841 | 2.1033e-05
2017 | 2016-07-25 | C | 32 | 0.002596 | 9.6148e-05
2017 | 2016-07-24 | C | 18 | 0.003245 | 5.4084e-05
2017 | 2016-07-25 | C | 17 | 0.002749 | 5.1079e-05
2017 | 2016-07-24 | C | 117 | 0.098069 | 0.00035155
2017 | 2016-07-24 | C | 9 | 0.012323 | 2.7042e-05
2017 | 2016-07-24 | C | 37 | 0.015119 | 0.00011117
2017 | 2016-07-25 | C | 1 | 0.000384 | 3.0046e-06
2017 | 2016-07-24 | C | 1033 | 0.30612 | 0.0031038
2017 | 2016-07-24 | C | 26 | 0.016667 | 7.8121e-05
2017 | 2016-07-24 | C | 8 | 0.00801 | 2.4037e-05
2017 | 2016-07-24 | C | 10 | 0.018494 | 3.0047e-05
2017 | 2016-07-24 | C | 92 | 0.050591 | 0.00055286
2017 | 2016-07-24 | C | 51 | 0.10882 | 0.00015324
2017 | 2016-07-24 | C | 145 | 0.069089 | 0.00079323
2017 | 2016-07-24 | C | 3000 | 1.0007 | 0.009014
2017 | 2016-07-24 | C | 109 | 0.082107 | 0.00032751
2017 | 2016-07-24 | C | 873 | 0.38241 | 0.0052462
2017 | 2016-07-24 | C | 9 | 0.052111 | 2.7042e-05
2017 | 2016-07-24 | C | 918 | 0.31199 | 0.0027583
2017 | 2016-07-24 | C | 5 | 0.002342 | 1.5023e-05
2017 | 2016-07-24 | C | 1093 | 0.28772 | 0.0065682
2017 | 2016-07-24 | C | 40 | 0.18065 | 0.00012019
2017 | 2016-07-24 | C | 1 | 0.001446 | 3.0046e-06
2017 | 2016-07-24 | C | 2 | 0.000286 | 6.0093e-06
2017 | 2016-07-24 | C | 514 | 0.004803 | 0.0015444
2017 | 2016-07-24 | C | 324 | 0.28112 | 0.0028604
2017 | 2016-07-24 | C | 186 | 0.050807 | 0.00055887
2017 | 2016-07-24 | C | 41 | 0.04932 | 0.00012319
2017 | 2016-07-24 | C | 20 | 0.009749 | 6.0093e-05
2017 | 2016-07-24 | C | 12 | 0.004196 | 3.6056e-05
2017 | 2016-07-24 | C | 235 | 0.044237 | 0.00084732
2017 | 2016-07-24 | C | 6 | 0.004766 | 1.8028e-05
2017 | 2016-07-24 | C | 92 | 0.05207 | 0.00027643
2017 | 2016-07-24 | C | 211 | 0.13226 | 0.00067004
2017 | 2016-07-24 | C | 11 | 0.032059 | 3.3051e-05
2017 | 2016-07-24 | C | 132 | 0.10095 | 0.00039662
2017 | 2016-07-24 | C | 1 | 0.004217 | 3.0046e-06
2017 | 2016-07-25 | C | 37 | 0.001334 | 0.00011117
2017 | 2016-07-24 | C | 902 | 0.051157 | 0.0027102
2017 | 2016-07-25 | C | 68 | 0.019818 | 0.00020432
2017 | 2016-07-24 | C | 17 | 0.00959 | 5.1079e-05
2017 | 2016-07-24 | C | 33 | 0.095305 | 9.9154e-05
2017 | 2016-07-25 | C | 26 | 0.054749 | 7.812e-05
2017 | 2016-07-25 | C | 498 | 0.078505 | 0.0014963
2017 | 2016-07-25 | C | 5 | 0.003759 | 1.5023e-05
2017 | 2016-07-25 | C | 4 | 0.002732 | 1.2019e-05
2017 | 2016-07-25 | C | 3 | 0.002196 | 9.0139e-06
2017 | 2016-07-25 | C | 1 | 0.001137 | 3.0046e-06
2017 | 2016-07-25 | C | 1 | 0.002129 | 3.0046e-06
2017 | 2016-07-25 | C | 1 | 0.000554 | 3.0046e-06
2017 | 2016-08-02 | B | 136 | 0.13309 | 0.00040859
2017 | 2016-07-25 | C | 5 | 0.002809 | 1.5023e-05
2017 | 2016-07-25 | C | 902 | 0.062279 | 0.0027102
2017 | 2016-08-10 | B | 9 | 0.007921 | 2.7037e-05
2017 | 2016-07-25 | C | 13 | 0.003182 | 3.906e-05
2017 | 2016-08-02 | B | 3 | 0.003154 | 9.0131e-06
2017 | 2016-07-25 | C | 4 | 0.000861 | 1.2019e-05
2017 | 2016-08-03 | B | 81 | 0.007543 | 0.0004867
2017 | 2016-07-25 | C | 498 | 0.12011 | 0.0014963
2017 | 2016-07-25 | C | 2 | 0.000601 | 6.0092e-06
2017 | 2016-07-24 | C | 13 | 0.041983 | 3.9061e-05
2017 | 2016-07-25 | C | 1 | 0.001222 | 3.0046e-06
2017 | 2016-07-24 | C | 7 | 0.028249 | 2.1033e-05
2017 | 2016-07-25 | C | 2 | 0.002386 | 6.0092e-06
2017 | 2016-07-25 | C | 4 | 0.001289 | 1.2019e-05
2017 | 2016-07-25 | C | 2 | 0.003255 | 6.0092e-06
2017 | 2016-07-25 | C | 1 | 0 | 3.0046e-06
2017 | 2016-07-25 | C | 2 | 0.003007 | 6.0092e-06
2017 | 2016-07-25 | C | 1 | 0.003057 | 3.0046e-06
2017 | 2016-07-26 | C | 51 | 0.018084 | 0.00015323
2017 | 2016-07-25 | C | 9 | 0.021065 | 2.7042e-05
2017 | 2016-07-26 | C | 430 | 0.090931 | 0.001292
2017 | 2016-07-25 | C | 2 | 0.001454 | 6.0092e-06
2017 | 2016-07-26 | C | 1 | 0.000395 | 3.0046e-06
2017 | 2016-08-12 | B | 5 | 0.00033 | 1.502e-05
2017 | 2016-07-26 | C | 74 | 0.00667 | 0.00022234
2017 | 2016-07-26 | C | 99 | 0.070234 | 0.00029746
2017 | 2016-08-10 | B | 232 | 0.039726 | 0.0013939
2017 | 2016-07-26 | C | 1 | 0.000654 | 3.0046e-06
2017 | 2016-08-22 | B | 9 | 0.007758 | 2.7034e-05
2017 | 2016-07-26 | C | 1 | 0.000375 | 3.0046e-06
2017 | 2016-08-11 | B | 74 | 0.074249 | 0.0002223
2017 | 2016-07-26 | C | 43 | 0.007463 | 0.0001292
2017 | 2016-08-20 | B | 47 | 0.002765 | 0.00028236
2017 | 2016-08-22 | B | 7 | 0.005151 | 2.1026e-05
2017 | 2016-07-26 | C | 4 | 0.002787 | 1.2018e-05
2017 | 2016-07-26 | C | 1 | 0.003988 | 3.0046e-06
2017 | 2016-08-12 | B | 30 | 0.003514 | 9.0122e-05
2017 | 2016-07-26 | C | 2014 | 0.58645 | 0.0062886
2017 | 2016-07-27 | C | 403 | 0.073444 | 0.0012108
2017 | 2016-08-16 | B | 49 | 0.049309 | 0.00014719
2017 | 2016-08-18 | B | 11 | 0.002213 | 3.3043e-05
2017 | 2016-07-27 | C | 1253 | 0.15039 | 0.0039781
2017 | 2016-07-27 | C | 26 | 0.014765 | 7.8119e-05
2017 | 2016-08-18 | B | 37 | 0.038233 | 0.00011114
2017 | 2016-08-14 | B | 7 | 0.001324 | 2.1028e-05
2017 | 2016-07-27 | C | 17 | 0.15538 | 5.1078e-05
2017 | 2016-07-27 | C | 2 | 0.000353 | 6.0091e-06
2017 | 2016-08-31 | B | 4 | 0.003758 | 1.2014e-05
2017 | 2016-07-27 | C | 1 | 7.8e-05 | 3.0045e-06
2017 | 2016-07-27 | C | 1 | 0.000193 | 3.0045e-06
2017 | 2016-07-28 | C | 29 | 0.008887 | 8.7132e-05
2017 | 2016-07-28 | C | 168 | 0.22457 | 0.00091338
2017 | 2016-07-28 | C | 1026 | 0.28623 | 0.0030827
2017 | 2016-07-28 | C | 680 | 0.15706 | 0.0023886
2017 | 2016-07-28 | C | 178 | 0.033929 | 0.00053481
2017 | 2016-07-28 | C | 46 | 0.035321 | 0.00013821
2017 | 2016-07-28 | C | 7 | 0.002471 | 2.1032e-05
2017 | 2016-07-28 | C | 53 | 0.038734 | 0.00015924
2017 | 2016-08-22 | B | 10 | 0.00036 | 3.0037e-05
2017 | 2016-07-28 | C | 1 | 0.001004 | 3.0045e-06
2017 | 2016-08-24 | B | 3 | 0.000648 | 9.0109e-06
2017 | 2016-08-26 | B | 3 | 0.000243 | 9.0107e-06
2017 | 2016-07-28 | C | 42 | 0.066107 | 0.00015924
2017 | 2016-08-29 | B | 4 | 0.001645 | 1.2014e-05
2017 | 2016-07-28 | C | 6 | 0.00806 | 1.8027e-05
2017 | 2016-08-16 | B | 17 | 0.018486 | 5.1067e-05
2017 | 2016-07-28 | C | 167 | 0.51933 | 0.00050176
2017 | 2016-07-28 | C | 195 | 0.030195 | 0.00058589
2017 | 2016-07-28 | C | 5 | 0.00356 | 1.5023e-05
2017 | 2016-07-28 | C | 324 | 0.11084 | 0.00097347
2017 | 2016-07-28 | C | 1 | 0.000413 | 3.0045e-06
2017 | 2016-07-28 | C | 11 | 0.002148 | 3.305e-05
2017 | 2016-07-28 | C | 82 | 0.15524 | 0.00024637
2017 | 2016-07-28 | C | 1 | 0.001183 | 3.0045e-06
2017 | 2016-07-28 | C | 1 | 0.000404 | 3.0045e-06
2017 | 2016-07-28 | C | 3 | 0.001174 | 9.0136e-06
2017 | 2016-07-29 | C | 152 | 0.04226 | 0.00045669
2017 | 2016-07-28 | C | 1347 | 0.42982 | 0.0040471
2017 | 2016-07-28 | C | 2 | 0.00089 | 6.009e-06
2017 | 2016-07-29 | C | 1 | 6.6e-05 | 3.0045e-06
2017 | 2016-07-28 | C | 195 | 0.075396 | 0.00058589
2017 | 2016-07-28 | C | 1 | 0.00037 | 3.0045e-06
2017 | 2016-07-28 | C | 10 | 0.003661 | 3.0045e-05
2017 | 2016-07-28 | C | 788 | 0.20112 | 0.0023676
2017 | 2016-07-29 | C | 154 | 0.1153 | 0.00046269
2017 | 2016-07-29 | C | 320 | 0.18171 | 0.00096144
2017 | 2016-07-29 | C | 228 | 0.32401 | 0.00068503
2017 | 2016-07-29 | C | 1 | 0.00154 | 3.0045e-06
2017 | 2016-07-29 | C | 50 | 0.047951 | 0.00015023
2017 | 2016-07-29 | C | 337 | 0.12553 | 0.0010125
2017 | 2016-07-29 | C | 1646 | 0.23788 | 0.0049454
2017 | 2016-07-29 | C | 243 | 0.0784 | 0.0007301
2017 | 2016-07-29 | C | 7 | 0.004101 | 2.1032e-05
2017 | 2016-07-30 | C | 1 | 0.000186 | 3.0044e-06
2017 | 2016-07-29 | C | 84 | 0.01918 | 0.00025238
2017 | 2016-07-29 | C | 2 | 0.003397 | 6.009e-06
2017 | 2016-07-29 | C | 5 | 0.003906 | 1.5023e-05
2017 | 2016-07-29 | C | 8 | 0.097712 | 4.8072e-05
2017 | 2016-07-29 | C | 4 | 0.001384 | 1.2018e-05
2017 | 2016-07-29 | C | 2 | 0.000993 | 6.009e-06
2017 | 2016-07-29 | C | 1 | 0.000129 | 3.0045e-06
2017 | 2016-07-29 | C | 3 | 0.005161 | 9.0135e-06
2017 | 2016-07-29 | C | 3 | 0.001292 | 9.0135e-06
2017 | 2016-07-29 | C | 1 | 0.000911 | 3.0045e-06
2017 | 2016-07-29 | C | 4 | 0.003369 | 1.2018e-05
2017 | 2016-07-29 | C | 4 | 0.007893 | 1.2018e-05
2017 | 2016-07-29 | C | 1 | 0.000732 | 3.0045e-06
2017 | 2016-07-29 | C | 8 | 0.007292 | 2.4036e-05
2017 | 2016-07-29 | C | 3 | 0.00374 | 9.0135e-06
2017 | 2016-07-29 | C | 1 | 0.00125 | 3.0045e-06
2017 | 2016-07-29 | C | 4 | 0.001909 | 1.2018e-05
2017 | 2016-07-29 | C | 1 | 0.004476 | 3.0045e-06
2017 | 2016-07-29 | C | 64 | 0.010383 | 0.00019229
2017 | 2016-07-29 | C | 2 | 0.003086 | 6.009e-06
2017 | 2016-07-29 | C | 1 | 0.000246 | 3.0045e-06
2017 | 2016-07-29 | C | 1 | 0.000367 | 3.0045e-06
2017 | 2016-07-29 | C | 9 | 0.004569 | 2.704e-05
2017 | 2016-07-29 | C | 744 | 0.08159 | 0.0022354
2017 | 2016-07-29 | C | 68 | 0.006537 | 0.00020431
2017 | 2016-08-30 | B | 26 | 0.024285 | 7.8089e-05
2017 | 2016-07-29 | C | 4 | 0.00453 | 1.2018e-05
2017 | 2016-07-29 | C | 342 | 0.002505 | 0.00024036
2017 | 2016-07-29 | C | 4 | 0.001642 | 1.2018e-05
2017 | 2016-07-29 | C | 12 | 0.011864 | 3.6054e-05
2017 | 2016-07-29 | C | 47 | 0.004236 | 0.00014121
2017 | 2016-07-29 | C | 403 | 0.054474 | 0.0012108
2017 | 2016-07-29 | C | 1 | 0.002253 | 3.0045e-06
2017 | 2016-07-29 | C | 34 | 0.004544 | 0.00010215
2017 | 2016-07-29 | C | 1 | 0.000322 | 3.0045e-06
2017 | 2016-07-29 | C | 1 | 0.000301 | 3.0045e-06
2017 | 2016-07-29 | C | 1412 | 0.020157 | 0.0042424
2017 | 2016-07-29 | C | 312 | 0.24566 | 0.00093741
2017 | 2016-07-29 | C | 1 | 0.000366 | 3.0045e-06
2017 | 2016-07-29 | C | 183 | 0.038781 | 0.0010997
2017 | 2016-07-29 | C | 71 | 0.031144 | 0.00021332
2017 | 2016-07-29 | C | 5 | 0.001982 | 1.5023e-05
2017 | 2016-07-29 | C | 8 | 0.004254 | 2.4036e-05
2017 | 2016-07-29 | C | 5 | 0.000856 | 1.5023e-05
2017 | 2016-07-29 | C | 23 | 0.010942 | 6.9104e-05
2017 | 2016-07-29 | C | 5 | 0.006988 | 1.5023e-05
2017 | 2016-07-29 | C | 10 | 0.010094 | 3.0045e-05
2017 | 2016-07-29 | C | 1 | 0.000507 | 3.0045e-06
2017 | 2016-07-29 | C | 10 | 0.005126 | 3.0045e-05
2017 | 2016-07-29 | C | 112 | 0.045957 | 0.00048974
2017 | 2016-07-29 | C | 1 | 0.000369 | 3.0045e-06
2017 | 2016-07-29 | C | 4 | 0.001132 | 1.2018e-05
2017 | 2016-07-29 | C | 11 | 0.057208 | 3.305e-05
2017 | 2016-07-30 | C | 2 | 0.000746 | 6.0089e-06
2017 | 2016-07-30 | C | 109 | 0.026003 | 0.00057986
2017 | 2016-07-30 | C | 1 | 0.000943 | 3.0044e-06
2017 | 2016-07-30 | C | 1 | 0.000328 | 3.0044e-06
2017 | 2016-07-30 | C | 680 | 0.11863 | 0.002043
2017 | 2016-07-30 | C | 423 | 0.090769 | 0.0012709
2017 | 2016-07-30 | C | 46 | 0.044067 | 0.00013821
2017 | 2016-07-30 | C | 1646 | 0.030164 | 0.0049454
2017 | 2016-07-30 | C | 22 | 0.068437 | 6.6098e-05
2017 | 2016-07-30 | C | 4 | 0.003866 | 1.2018e-05
2017 | 2016-07-30 | C | 1 | 0.001024 | 3.0044e-06
2017 | 2016-07-30 | C | 1 | 0.000144 | 3.0044e-06
2017 | 2016-07-30 | C | 468 | 0.11424 | 0.0014061
2017 | 2016-07-30 | C | 108 | 0.011345 | 0.00012318
2017 | 2016-07-30 | C | 288 | 0.023101 | 0.00086529
2017 | 2016-07-30 | C | 1 | 0.00022 | 3.0044e-06
2017 | 2016-07-30 | C | 108 | 0.13723 | 0.0010065
2017 | 2016-07-31 | C | 2 | 0.00029 | 6.0088e-06
2017 | 2016-07-31 | C | 430 | 0.1132 | 0.0012919
2017 | 2016-07-31 | C | 8 | 0.005148 | 2.4036e-05
2017 | 2016-07-31 | C | 222 | 0.18286 | 0.00066699
2017 | 2016-07-31 | C | 1 | 0.000643 | 3.0044e-06
2017 | 2016-07-31 | C | 32 | 0.014354 | 9.6142e-05
2017 | 2016-07-31 | C | 42 | 0.014511 | 0.00012619
2017 | 2016-07-31 | C | 2 | 0.001122 | 6.0088e-06
2017 | 2016-07-31 | C | 1 | 0.000522 | 3.0044e-06
2017 | 2016-07-31 | C | 373 | 0.061176 | 0.0011207
2017 | 2016-07-31 | C | 1412 | 0.11477 | 0.0042423
2017 | 2016-07-31 | C | 1 | 0.007964 | 3.0044e-06
2017 | 2016-07-31 | C | 3 | 0.000487 | 9.0133e-06
2017 | 2016-07-31 | C | 1 | 0.00056 | 3.0044e-06
2017 | 2016-07-31 | C | 1 | 0.000302 | 3.0044e-06
2017 | 2016-07-31 | C | 1 | 0.000236 | 3.0044e-06
2017 | 2016-07-31 | C | 4 | 0.005431 | 1.2018e-05
2017 | 2016-07-31 | C | 379 | 0.12791 | 0.0021332
2017 | 2016-07-31 | C | 122 | 0.024287 | 0.00064295
2017 | 2016-07-31 | C | 1 | 0.000322 | 3.0044e-06
2017 | 2016-07-31 | C | 1 | 0.000434 | 3.0044e-06
2017 | 2016-07-31 | C | 1 | 0.000187 | 3.0044e-06
2017 | 2016-07-31 | C | 4 | 0.00106 | 1.2018e-05
2017 | 2016-07-31 | C | 6 | 0.000433 | 1.8027e-05
2017 | 2016-07-31 | C | 4 | 0.016052 | 1.2018e-05
2017 | 2016-07-31 | C | 45 | 0.007841 | 0.0001352
2017 | 2016-07-31 | C | 108 | 0.11596 | 0.00012318
2017 | 2016-07-31 | C | 171 | 0.014353 | 0.00051376
2017 | 2016-08-01 | C | 19 | 0.003583 | 5.7084e-05
2017 | 2016-08-01 | C | 38 | 0.012526 | 0.00011417
2017 | 2016-08-01 | C | 172 | 0.034622 | 0.00051676
2017 | 2016-08-01 | C | 1 | 0.000731 | 3.0044e-06
2017 | 2016-08-01 | C | 198 | 0.001566 | 0.00059487
2017 | 2016-08-16 | B | 30 | 0.03118 | 9.0118e-05
2017 | 2016-08-01 | C | 1 | 0.001997 | 3.0044e-06
2017 | 2016-08-23 | B | 11 | 0.010962 | 3.3041e-05
2017 | 2016-08-25 | B | 11 | 0.009978 | 3.304e-05
2017 | 2016-08-01 | C | 70 | 0.01198 | 0.00021031
2017 | 2016-08-24 | B | 3 | 0.000513 | 9.0109e-06
2017 | 2016-08-01 | C | 42 | 0.006126 | 0.00012619
2017 | 2016-08-01 | C | 62 | 0.014343 | 0.00018627
2017 | 2016-08-01 | C | 2 | 0.001262 | 6.0088e-06
2017 | 2016-08-01 | C | 2 | 0.000102 | 6.0088e-06
2017 | 2016-08-16 | B | 260 | 0.11491 | 0.00078102
2017 | 2016-08-23 | B | 7 | 0.005653 | 2.1026e-05
2017 | 2016-08-23 | B | 24 | 0.026986 | 7.2089e-05
2017 | 2016-08-26 | B | 24 | 0.025446 | 7.2086e-05
2017 | 2016-08-29 | B | 24 | 0.030779 | 7.2084e-05
2017 | 2016-08-31 | B | 24 | 0.029121 | 7.2082e-05
2017 | 2016-08-01 | C | 2 | 0.000628 | 6.0088e-06
2017 | 2016-08-03 | B | 29 | 0.009148 | 8.7126e-05
2017 | 2016-08-01 | C | 3 | 0.001126 | 9.0132e-06
2017 | 2016-08-02 | C | 942 | 0.24255 | 0.0035992
2017 | 2016-08-02 | C | 953 | 0.43282 | 0.0028632
2017 | 2016-08-02 | C | 253 | 0.032159 | 0.00076011
2017 | 2016-08-02 | C | 127 | 0.027828 | 0.00038156
2017 | 2016-08-02 | C | 1 | 0.000304 | 3.0043e-06
2017 | 2016-07-30 | C | 1 | 4.5e-05 | 3.0044e-06
2017 | 2016-08-02 | C | 2 | 0.00036 | 6.0087e-06
2017 | 2016-08-02 | C | 7 | 0.001972 | 2.1031e-05
2017 | 2016-08-02 | C | 2 | 0.000519 | 6.0087e-06
2017 | 2016-08-02 | C | 3 | 0.000243 | 9.0131e-06
2017 | 2016-08-24 | B | 322 | 0.25769 | 0.00096718
2017 | 2016-08-24 | B | 212 | 0.030437 | 0.00063678
2017 | 2016-08-25 | B | 10 | 0.001009 | 3.0036e-05
2017 | 2016-08-24 | B | 9 | 0.011676 | 2.7033e-05
2017 | 2016-08-02 | C | 28 | 0.003953 | 8.4122e-05
2017 | 2016-08-03 | C | 59 | 0.003988 | 0.00017726
2017 | 2016-08-02 | C | 62 | 0.05281 | 0.00018627
2017 | 2016-08-03 | C | 57 | 0.008379 | 0.00017125
2017 | 2016-08-03 | C | 32 | 0.026648 | 9.6139e-05
2017 | 2016-08-18 | B | 73 | 0.058251 | 0.00021928
2017 | 2016-08-03 | C | 680 | 0.060687 | 0.0026378
2017 | 2016-08-28 | B | 206 | 0 | 0
2017 | 2016-07-28 | C | 3 | 0.001813 | 9.0136e-06
2017 | 2016-08-26 | B | 2 | 0.000222 | 6.0071e-06
2017 | 2016-08-03 | C | 2 | 0.000343 | 6.0086e-06
2017 | 2016-08-03 | C | 573 | 0.13116 | 0.0021121
2017 | 2016-08-04 | C | 499 | 0.03919 | 0.0012438
2017 | 2016-08-04 | C | 56 | 0.051543 | 0.00016824
2017 | 2016-08-04 | C | 20 | 0.004578 | 6.0086e-05
2017 | 2016-08-04 | C | 1 | 0.000213 | 3.0043e-06
2017 | 2016-08-23 | B | 15 | 0.01684 | 4.5055e-05
2017 | 2016-08-04 | C | 1 | 0.000425 | 3.0043e-06
2017 | 2016-08-04 | C | 44 | 0.044201 | 0.00013219
2017 | 2016-08-04 | C | 5 | 0.000165 | 1.5022e-05
2017 | 2016-08-04 | C | 4 | 0.001057 | 1.2017e-05
2017 | 2016-08-04 | C | 4 | 0.000127 | 1.2017e-05
2017 | 2016-08-05 | C | 17 | 0.002809 | 5.1073e-05
2017 | 2016-08-05 | C | 109 | 0.02103 | 0.00032747
2017 | 2016-08-05 | C | 19 | 0.001027 | 5.7081e-05
2017 | 2016-08-29 | B | 7 | 0.000567 | 2.1024e-05
2017 | 2016-08-15 | B | 3 | 0.002685 | 9.0119e-06
2017 | 2016-08-29 | B | 2 | 0.000342 | 6.0069e-06
2017 | 2016-08-05 | C | 1 | 0.000267 | 3.0042e-06
2017 | 2016-08-05 | C | 11 | 0.00262 | 3.3047e-05
2017 | 2016-08-05 | C | 220 | 0.075136 | 0.0016824
2017 | 2016-08-05 | C | 8 | 0.063109 | 2.4034e-05
2017 | 2016-08-05 | C | 8 | 0.021905 | 2.4034e-05
2017 | 2016-08-05 | C | 59 | 0.8872 | 0.00030944
2017 | 2016-08-06 | C | 163 | 0.41394 | 0.00057982
2017 | 2016-08-06 | C | 1 | 0.00062 | 3.0042e-06
2017 | 2016-08-06 | C | 115 | 0.051079 | 0.00034549
2017 | 2016-08-06 | C | 1 | 0.001035 | 3.0042e-06
2017 | 2016-08-06 | C | 161 | 0.21838 | 0.00048368
2017 | 2016-08-06 | C | 5 | 0.001126 | 1.5021e-05
2017 | 2016-08-06 | C | 1 | 0.001518 | 3.0042e-06
2017 | 2016-08-06 | C | 1 | 0.000633 | 3.0042e-06
2017 | 2016-08-06 | C | 163 | 0.050012 | 0.00043261
2017 | 2016-08-06 | C | 147 | 0.044397 | 0.00088325
2017 | 2016-08-06 | C | 39 | 0.017692 | 0.00011717
2017 | 2016-08-06 | C | 2 | 0.009054 | 6.0084e-06
2017 | 2016-08-06 | C | 1 | 0.000512 | 3.0042e-06
2017 | 2016-08-06 | C | 132 | 0.11141 | 0.00039656
2017 | 2016-08-06 | C | 1 | 0.000828 | 3.0042e-06
2017 | 2016-08-06 | C | 66 | 0.008724 | 0.00019828
2017 | 2016-08-06 | C | 18 | 0.007084 | 5.4076e-05
2017 | 2016-08-06 | C | 1 | 0.000293 | 3.0042e-06
2017 | 2016-08-06 | C | 872 | 0.046651 | 0.0004957
2017 | 2016-08-06 | C | 7 | 0.002816 | 2.103e-05
2017 | 2016-08-06 | C | 1 | 0.00083 | 3.0042e-06
2017 | 2016-08-06 | C | 826 | 0.15929 | 0.0024815
2017 | 2016-08-06 | C | 121 | 0.056323 | 0.00036351
2017 | 2016-08-06 | C | 176 | 0.008369 | 0.00046566
2017 | 2016-08-06 | C | 46 | 0.026604 | 0.0001382
2017 | 2016-08-06 | C | 71 | 0.004692 | 0.0002133
2017 | 2016-08-06 | C | 1 | 0.000292 | 3.0042e-06
2017 | 2016-08-06 | C | 144 | 0.13009 | 0.00043261
2017 | 2016-08-06 | C | 156 | 0.10087 | 0.00046866
2017 | 2016-08-06 | C | 747 | 0.32342 | 0.0040467
2017 | 2016-08-06 | C | 6 | 0.003921 | 1.8025e-05
2017 | 2016-08-06 | C | 161 | 0.059011 | 0.00027639
2017 | 2016-08-07 | C | 29 | 0.006521 | 8.7122e-05
2017 | 2016-08-07 | C | 11 | 0.002504 | 3.3046e-05
2017 | 2016-08-07 | C | 342 | 0.06446 | 0.0010274
2017 | 2016-08-07 | C | 10 | 0.004569 | 3.0042e-05
2017 | 2016-08-07 | C | 8 | 0.003917 | 2.4034e-05
2017 | 2016-08-07 | C | 1 | 0.000327 | 3.0042e-06
2017 | 2016-08-07 | C | 2 | 0.000522 | 6.0084e-06
2017 | 2016-08-07 | C | 8 | 0.001798 | 2.4034e-05
2017 | 2016-08-07 | C | 9 | 0.004891 | 2.7038e-05
2017 | 2016-08-07 | C | 8 | 0.002581 | 2.4034e-05
2017 | 2016-08-08 | C | 23 | 0.010616 | 6.9096e-05
2017 | 2016-08-08 | C | 214 | 0.096637 | 0.0010665
2017 | 2016-08-08 | C | 2 | 0.000861 | 6.0083e-06
2017 | 2016-08-08 | C | 1 | 0.000135 | 3.0041e-06
2017 | 2016-08-08 | C | 2 | 0.001384 | 6.0083e-06
2017 | 2016-08-08 | C | 51 | 0.0104 | 0.00015321
2017 | 2016-08-25 | B | 16 | 0.007545 | 4.8058e-05
2017 | 2016-08-08 | C | 1 | 0.00025 | 3.0041e-06
2017 | 2016-08-07 | C | 1 | 0.00035 | 3.0042e-06
2017 | 2016-08-07 | C | 19 | 0.007795 | 5.708e-05
2017 | 2016-08-30 | B | 33 | 0.007631 | 0.00019823
2017 | 2016-09-01 | B | 6 | 0.004955 | 1.802e-05
2017 | 2016-08-08 | C | 3 | 0.000576 | 9.0125e-06
2017 | 2016-09-01 | B | 5 | 0.002883 | 1.5017e-05
2017 | 2016-08-08 | C | 16 | 0.006056 | 4.8067e-05
2017 | 2016-09-01 | B | 38 | 0.033713 | 0.00011413
2017 | 2016-09-02 | B | 3 | 0.000513 | 9.01e-06
2017 | 2016-08-24 | B | 1 | 0.000255 | 3.0036e-06
2017 | 2016-08-09 | C | 1 | 0.000307 | 3.0041e-06
2017 | 2016-09-03 | B | 13 | 0.011791 | 3.9043e-05
2017 | 2016-09-05 | B | 32 | 0.024218 | 9.6105e-05
2017 | 2016-08-10 | C | 18 | 0.014071 | 5.4074e-05
2017 | 2016-08-10 | C | 2 | 0.002142 | 6.0082e-06
2017 | 2016-08-10 | C | 12 | 0.000612 | 3.605e-05
2017 | 2016-08-10 | C | 1 | 0.000129 | 3.0041e-06
2017 | 2016-08-23 | B | 119 | 0.089872 | 0.00035744
2017 | 2016-08-10 | C | 2 | 0.002011 | 6.0082e-06
2017 | 2016-08-10 | C | 1 | 0.00032 | 3.0041e-06
2017 | 2016-09-05 | B | 98 | 0.13421 | 0.00029432
2017 | 2016-09-07 | B | 51 | 0.061572 | 0.00015316
2017 | 2016-08-14 | B | 280 | 0.1632 | 0.00084112
2017 | 2016-08-11 | C | 17 | 0.003217 | 5.107e-05
2017 | 2016-08-11 | C | 171 | 0.030699 | 0.0005137
2017 | 2016-08-12 | C | 120 | 0.064488 | 0.00067592
2017 | 2016-08-12 | C | 1 | 0.000487 | 3.004e-06
2017 | 2016-09-07 | B | 65 | 0.010463 | 0.00019521
2017 | 2016-08-24 | B | 29 | 0.024128 | 8.7106e-05
2017 | 2016-08-12 | C | 48 | 0 | 0.0001442
2017 | 2016-08-12 | C | 3 | 0.001207 | 9.0122e-06
2017 | 2016-08-12 | C | 1 | 0.002655 | 3.004e-06
2017 | 2016-08-12 | C | 4 | 0.000348 | 1.2016e-05
2017 | 2016-08-13 | C | 716 | 0.12031 | 0.0021509
2017 | 2016-08-13 | C | 61 | 0.021583 | 0.00018325
2017 | 2016-08-13 | C | 486 | 0.041892 | 0.00035748
2017 | 2016-08-13 | C | 4 | 0.001173 | 3.004e-06
2017 | 2016-08-13 | C | 39 | 0.014117 | 0.00011716
2017 | 2016-08-14 | C | 18 | 0.004343 | 5.4072e-05
2017 | 2016-08-14 | C | 6 | 0.001308 | 1.8024e-05
2017 | 2016-08-14 | C | 218 | 0.052678 | 0.0010003
2017 | 2016-08-14 | C | 46 | 0.012934 | 0.00013818
2017 | 2016-08-14 | C | 5 | 0.001529 | 1.502e-05
2017 | 2016-08-15 | C | 1 | 0.000231 | 3.0039e-06
2017 | 2016-08-14 | C | 581 | 0.038468 | 0.00084713
2017 | 2016-09-01 | B | 15 | 0.004059 | 4.5051e-05
2017 | 2016-09-01 | B | 17 | 0.005105 | 5.1058e-05
2017 | 2016-09-01 | B | 34 | 0.030328 | 0.00010212
2017 | 2016-09-01 | B | 104 | 0.015648 | 0.00031235
2017 | 2016-09-02 | B | 52 | 0.018301 | 0.00015617
2017 | 2016-09-08 | B | 33 | 0.034885 | 9.9106e-05
2017 | 2016-09-01 | B | 23 | 0.010495 | 6.9078e-05
2017 | 2016-09-01 | B | 17 | 0.019161 | 5.1058e-05
2017 | 2016-09-06 | B | 7 | 0.000988 | 2.1023e-05
2017 | 2016-08-31 | B | 118 | 0.065972 | 0.0003544
2017 | 2016-09-06 | B | 10 | 0.002913 | 3.0033e-05
2017 | 2016-09-06 | B | 4 | 0.000324 | 1.2013e-05
2017 | 2016-09-07 | B | 4 | 0.000144 | 1.2013e-05
2017 | 2016-09-07 | B | 9 | 0.002756 | 2.7029e-05
2017 | 2016-10-03 | B | 4 | 0.000216 | 1.2009e-05
2017 | 2016-10-03 | B | 12 | 0.001513 | 3.6028e-05
2017 | 2016-09-09 | B | 4 | 0.000324 | 1.2013e-05
2017 | 2016-09-09 | B | 5 | 0.001156 | 1.5016e-05
2017 | 2016-09-09 | B | 4 | 0.000384 | 1.2013e-05
2017 | 2016-09-12 | B | 5 | 0.001306 | 1.5015e-05
2017 | 2016-09-12 | B | 3 | 0.000108 | 9.0092e-06
2017 | 2016-09-12 | B | 3 | 0.000378 | 9.0092e-06
2017 | 2016-09-12 | B | 7 | 0.000252 | 2.1021e-05
2017 | 2016-08-15 | C | 28 | 0.00227 | 8.4111e-05
2017 | 2016-08-16 | C | 1442 | 0.022885 | 0.0043317
2017 | 2016-08-16 | C | 3 | 0.002472 | 1.2016e-05
2017 | 2016-09-13 | B | 6 | 0.004396 | 1.8018e-05
2017 | 2016-09-06 | B | 48 | 0.05968 | 0.00014416
2017 | 2016-09-13 | B | 3 | 0.000153 | 9.0091e-06
2017 | 2016-09-14 | B | 2 | 0.001879 | 6.006e-06
2017 | 2016-08-21 | B | 17 | 0.009807 | 5.1064e-05
2017 | 2016-09-01 | B | 40 | 0.004805 | 0.00012014
2017 | 2016-09-06 | B | 3 | 0.001324 | 9.0097e-06
2017 | 2016-09-07 | B | 4 | 0.004084 | 1.2013e-05
2017 | 2016-09-12 | B | 6 | 0.002857 | 1.8019e-05
2017 | 2016-09-06 | B | 11 | 0.00587 | 3.3036e-05
2017 | 2016-09-19 | B | 10 | 0.009338 | 3.0028e-05
2017 | 2016-09-06 | B | 52 | 0.032483 | 0.00015617
2017 | 2016-08-16 | C | 191 | 0.070339 | 0.00085312
2017 | 2016-09-05 | B | 6 | 0.004054 | 1.802e-05
2017 | 2016-08-30 | B | 67 | 0.071141 | 0.00020123
2017 | 2016-08-16 | C | 4 | 0.000167 | 1.2016e-05
2017 | 2016-08-30 | B | 1 | 0.000687 | 3.0034e-06
2017 | 2016-09-02 | B | 97 | 0.019876 | 0.00029133
2017 | 2016-08-16 | C | 603 | 0.078372 | 0.0018114
2017 | 2016-08-16 | C | 120 | 0.04188 | 0.00036047
2017 | 2016-09-06 | B | 9 | 0.008325 | 2.7029e-05
2017 | 2016-08-26 | B | 6 | 0.004738 | 1.8022e-05
2017 | 2016-09-06 | B | 29 | 0.020989 | 8.7094e-05
2017 | 2016-09-07 | B | 46 | 0.053877 | 0.00013815
2017 | 2016-08-18 | C | 27 | 0.004532 | 8.1104e-05
2017 | 2016-08-18 | C | 12 | 0.004674 | 3.6046e-05
2017 | 2016-09-07 | B | 5 | 0.001561 | 1.5016e-05
2017 | 2016-08-18 | C | 242 | 0.18297 | 0.00072694
2017 | 2016-09-07 | B | 7 | 0.000231 | 2.1023e-05
2017 | 2016-09-01 | B | 40 | 0.046372 | 0.00012014
2017 | 2016-09-12 | B | 81 | 0.072245 | 0.00024325
2017 | 2016-09-12 | B | 130 | 0.18154 | 0.0003904
2017 | 2016-09-07 | B | 32 | 0.006535 | 9.6103e-05
2017 | 2016-09-06 | B | 82 | 0.077081 | 0.00024627
2017 | 2016-09-06 | B | 90 | 0.017298 | 0.00027029
2017 | 2016-08-18 | C | 149 | 0.030444 | 0.00044758
2017 | 2016-08-19 | C | 253 | 0.040761 | 0.00075997
2017 | 2016-08-19 | C | 26 | 0.007035 | 7.81e-05
2017 | 2016-08-19 | B | 4 | 0.000744 | 1.2015e-05
2017 | 2016-09-09 | B | 2 | 0.002114 | 6.0063e-06
2017 | 2016-09-12 | B | 1 | 0.000388 | 3.003e-06
2017 | 2016-08-23 | B | 5 | 0.004616 | 1.5018e-05
2017 | 2016-08-20 | B | 120 | 0.025952 | 0.00036046
2017 | 2016-09-13 | B | 11 | 0.005714 | 3.3034e-05
2017 | 2016-08-19 | C | 20 | 0.012224 | 6.0077e-05
2017 | 2016-08-20 | C | 38 | 0.020471 | 0.00011414
2017 | 2016-08-20 | C | 68 | 0.004289 | 0.00020426
2017 | 2016-08-20 | C | 3403 | 0.39208 | 0.010222
2017 | 2016-08-20 | C | 8 | 0.001625 | 2.403e-05
2017 | 2016-08-20 | C | 48 | 0.002345 | 0.00014418
2017 | 2016-08-20 | C | 4 | 0.001228 | 1.2015e-05
2017 | 2016-08-21 | C | 415 | 0.096164 | 0.0023159
2017 | 2016-08-21 | C | 469 | 0.25929 | 0.0014088
2017 | 2016-08-22 | C | 197 | 0.07263 | 0.00059174
2017 | 2016-08-22 | C | 496 | 0 | 0.00095218
2017 | 2016-09-01 | B | 235 | 0.19127 | 0.0007058
2017 | 2016-09-08 | B | 48 | 0.046129 | 0.00014415
2017 | 2016-08-27 | B | 39 | 0.01593 | 0.00011714
2017 | 2016-08-22 | C | 5 | 0.000961 | 1.5019e-05
2017 | 2016-08-22 | C | 420 | 0.044277 | 0.0012616
2017 | 2016-09-08 | B | 714 | 0.063358 | 0.0021443
2017 | 2016-09-18 | B | 462 | 0.001387 | 0.0013873
2017 | 2016-09-12 | B | 1 | 0.000396 | 3.003e-06
2017 | 2016-08-22 | C | 8 | 0.002691 | 2.403e-05
2017 | 2016-08-22 | C | 861 | 0.051724 | 0.0025862
2017 | 2016-08-23 | C | 2 | 0.001062 | 6.0073e-06
2017 | 2016-09-07 | B | 27 | 0.044354 | 8.1087e-05
2017 | 2016-09-13 | B | 365 | 0.055499 | 0.0010961
2017 | 2016-09-01 | B | 14 | 0.017812 | 4.2047e-05
2017 | 2016-08-23 | C | 16 | 0.006237 | 4.8059e-05
2017 | 2016-08-23 | C | 3001 | 0.32849 | 0.0090141
2017 | 2016-09-23 | B | 3 | 0.000256 | 9.0081e-06
2017 | 2016-09-23 | B | 1 | 9.6e-05 | 3.0027e-06
2017 | 2016-09-23 | B | 4 | 0.000264 | 1.2011e-05
2017 | 2016-09-26 | B | 2 | 0.000204 | 6.0052e-06
2017 | 2016-09-26 | B | 4 | 0.000384 | 1.201e-05
2017 | 2016-09-26 | B | 4 | 0.000204 | 1.201e-05
2017 | 2016-09-15 | B | 365 | 0.01096 | 0.0010961
2017 | 2016-09-28 | B | 5 | 0.000555 | 1.5013e-05
2017 | 2016-09-28 | B | 5 | 0.00033 | 1.5013e-05
2017 | 2016-09-26 | B | 64 | 0.012647 | 0.00019217
2017 | 2016-09-13 | B | 2 | 0.001513 | 6.006e-06
2017 | 2016-08-23 | C | 622 | 0 | 0.0002403
2017 | 2016-08-23 | C | 2 | 0.000628 | 6.0073e-06
2017 | 2016-08-23 | C | 170 | 0.027423 | 0.00051063
2017 | 2016-08-24 | C | 6 | 0.000453 | 1.8022e-05
2017 | 2016-09-20 | B | 187 | 0.15554 | 0.00056153
2017 | 2016-08-24 | C | 4 | 0.001461 | 1.2015e-05
2017 | 2016-09-09 | B | 40 | 0.018579 | 0.00012013
2017 | 2016-08-24 | C | 294 | 0.072919 | 0.00088308
2017 | 2016-08-24 | C | 1 | 0.000429 | 3.0036e-06
2017 | 2016-08-25 | C | 265 | 0.079967 | 0.00079596
2017 | 2016-08-25 | C | 622 | 0.18885 | 0.0018683
2017 | 2016-09-16 | B | 5 | 0.005495 | 1.5015e-05
2017 | 2016-08-25 | C | 7 | 0.003826 | 2.1025e-05
2017 | 2016-09-19 | B | 188 | 0.097382 | 0.00056454
2017 | 2016-08-25 | C | 1 | 0.000375 | 3.0036e-06
2017 | 2016-09-13 | B | 4 | 0.000504 | 1.2012e-05
2017 | 2016-08-25 | C | 56 | 0.007737 | 0.0001682
2017 | 2016-08-25 | C | 4 | 0.001302 | 1.2014e-05
2017 | 2016-08-25 | C | 294 | 0.074516 | 0.00088307
2017 | 2016-08-25 | C | 392 | 0.044301 | 0.0011774
2017 | 2016-08-25 | C | 1 | 0.00015 | 3.0036e-06
2017 | 2016-08-25 | C | 801 | 0.1187 | 0.0024059
2017 | 2016-08-25 | C | 294 | 0.063174 | 0.00088307
2017 | 2016-08-26 | C | 144 | 0.060297 | 0.00076592
2017 | 2016-08-26 | C | 2 | 0.001502 | 6.0071e-06
2017 | 2016-08-26 | C | 382 | 0.08698 | 0.0013456
2017 | 2016-08-26 | C | 260 | 0.082302 | 0.00078093
2017 | 2016-08-26 | C | 34 | 0.028241 | 0.00010212
2017 | 2016-08-26 | C | 1 | 0.000632 | 3.0035e-06
2017 | 2016-08-26 | C | 2 | 0.000953 | 6.0071e-06
2017 | 2016-08-26 | C | 2 | 0.000484 | 6.0071e-06
2017 | 2016-09-15 | B | 3 | 0.002918 | 9.0089e-06
2017 | 2016-09-19 | B | 3 | 0.003738 | 9.0085e-06
2017 | 2016-09-22 | B | 16 | 0.015326 | 4.8044e-05
2017 | 2016-08-26 | C | 415 | 0.068543 | 0.0012465
2017 | 2016-09-23 | B | 1 | 0.000441 | 3.0027e-06
2017 | 2016-09-26 | B | 6 | 0.004323 | 1.8016e-05
2017 | 2016-09-27 | B | 14 | 0.006767 | 4.2036e-05
2017 | 2016-08-26 | C | 3 | 0.000539 | 9.0107e-06
2017 | 2016-08-26 | C | 1 | 7.8e-05 | 3.0035e-06
2017 | 2016-08-26 | C | 401 | 0.23457 | 0.0021356
2017 | 2016-08-26 | C | 2 | 0.000439 | 6.0071e-06
2017 | 2016-08-26 | C | 236 | 0.032823 | 0.00070885
2017 | 2016-08-26 | C | 17 | 0.001843 | 5.1061e-05
2017 | 2016-08-26 | C | 277 | 0.36639 | 0.00083199
2017 | 2016-08-26 | C | 171 | 0.07192 | 0.00051361
2017 | 2016-08-26 | C | 788 | 0.12861 | 0.0023668
2017 | 2016-08-26 | C | 1 | 0.001146 | 3.0035e-06
2017 | 2016-08-26 | C | 1235 | 0.142 | 0.0037094
2017 | 2016-08-26 | C | 581 | 0.31297 | 0.0017451
2017 | 2016-08-26 | C | 1 | 0.00046 | 3.0035e-06
2017 | 2016-08-27 | C | 35 | 0.012194 | 0.00010512
2017 | 2016-08-27 | C | 236 | 0.048067 | 0.0013906
2017 | 2016-08-27 | C | 144 | 0.10347 | 0.00043251
2017 | 2016-08-27 | C | 194 | 0.01952 | 0.00058269
2017 | 2016-08-27 | C | 873 | 0.28453 | 0.003364
2017 | 2016-08-27 | C | 5 | 0.001435 | 3.0035e-06
2017 | 2016-08-27 | C | 7 | 0.00103 | 2.1025e-05
2017 | 2016-08-27 | C | 27 | 0.006328 | 8.1096e-05
2017 | 2016-08-27 | C | 442 | 0.31617 | 0.0013276
2017 | 2016-08-27 | C | 4 | 0.0027 | 1.2014e-05
2017 | 2016-08-27 | C | 122 | 0.062415 | 0.00036643
2017 | 2016-08-27 | C | 4 | 0.004802 | 1.2014e-05
2017 | 2016-08-27 | C | 3 | 0.002126 | 9.0106e-06
2017 | 2016-08-27 | C | 241 | 0.099602 | 0.00072386
2017 | 2016-08-27 | C | 181 | 0.096908 | 0.0010212
2017 | 2016-08-27 | C | 10 | 0.00365 | 3.0036e-05
2017 | 2016-08-27 | C | 239 | 0.057951 | 0.00072986
2017 | 2016-08-27 | C | 1 | 0.000919 | 3.0035e-06
2017 | 2016-08-28 | C | 212 | 0.048475 | 0.00063675
2017 | 2016-08-28 | C | 114 | 0.11779 | 0.0003424
2017 | 2016-08-28 | C | 208 | 0.073472 | 0.00062473
2017 | 2016-08-28 | C | 429 | 0.11151 | 0.0013155
2017 | 2016-08-29 | C | 429 | 0.20468 | 0.002577
2017 | 2016-09-20 | B | 90 | 0.11294 | 0.00027025
2017 | 2016-08-29 | C | 107 | 0.033615 | 0.00032137
2017 | 2016-08-29 | C | 64 | 0.047286 | 0.00019222
2017 | 2016-09-12 | B | 10 | 0.009429 | 3.0031e-05
2017 | 2016-09-14 | B | 21 | 0.014063 | 6.3063e-05
2017 | 2016-09-13 | B | 108 | 0.13952 | 0.00032433
2017 | 2016-09-13 | B | 44 | 0.047568 | 0.00013213
2017 | 2016-08-29 | C | 3 | 0.000432 | 9.0104e-06
2017 | 2016-09-14 | B | 44 | 0.048096 | 0.00013213
2017 | 2016-09-14 | B | 67 | 0.080883 | 0.0002012
2017 | 2016-09-11 | B | 21 | 0.019631 | 6.3065e-05
2017 | 2016-09-16 | B | 14 | 0.01526 | 4.2041e-05
2017 | 2016-09-19 | B | 53 | 0.053793 | 0.00015915
2017 | 2016-09-20 | B | 6 | 0.006017 | 1.8017e-05
2017 | 2016-08-30 | C | 2046 | 0.04966 | 0.006145
2017 | 2016-09-21 | B | 8 | 0.003363 | 2.4022e-05
2017 | 2016-08-30 | C | 431 | 0.059251 | 0.0005226
2017 | 2016-09-22 | B | 6 | 0.006053 | 1.8016e-05
2017 | 2016-09-28 | B | 8 | 0.00723 | 2.402e-05
2017 | 2016-09-20 | B | 70 | 0.089122 | 0.0002102
2017 | 2016-08-30 | C | 2 | 0.001429 | 6.0068e-06
2017 | 2016-09-13 | B | 50 | 0.027778 | 0.00015015
2017 | 2016-09-20 | B | 91 | 0.056564 | 0.00027326
2017 | 2016-09-23 | B | 2 | 0.001393 | 6.0054e-06
2017 | 2016-08-30 | C | 38 | 0.001711 | 0.00011413
2017 | 2016-09-21 | B | 2 | 0.001596 | 6.0055e-06
2017 | 2016-08-30 | C | 40 | 0.035961 | 0.00012014
2017 | 2016-08-30 | C | 1 | 0.000397 | 3.0034e-06
2017 | 2016-08-31 | C | 1065 | 0.12726 | 0.00080191
2017 | 2016-08-31 | C | 1 | 0.00028 | 3.0034e-06
2017 | 2016-09-22 | B | 32 | 0.038146 | 9.6088e-05
2017 | 2016-08-31 | C | 5 | 0.003273 | 1.5017e-05
2017 | 2016-09-26 | B | 13 | 0.012178 | 3.9034e-05
2017 | 2016-09-15 | B | 244 | 0.21982 | 0.00073273
2017 | 2016-09-01 | C | 171 | 0.00451 | 0.00051358
2017 | 2016-09-01 | C | 8 | 0.01444 | 2.4027e-05
2017 | 2016-09-01 | C | 241 | 0.044481 | 0.00072382
2017 | 2016-09-02 | C | 1 | 0.000211 | 3.0033e-06
2017 | 2016-09-02 | C | 1 | 0.000231 | 3.0033e-06
2017 | 2016-09-02 | C | 2 | 5.5e-05 | 6.0067e-06
2017 | 2016-09-22 | B | 14 | 0.018496 | 4.2039e-05
2017 | 2016-09-22 | B | 5 | 0.004759 | 1.5014e-05
2017 | 2016-09-27 | B | 2 | 0.00239 | 6.0051e-06
2017 | 2016-09-29 | B | 2 | 0.001014 | 6.0049e-06
2017 | 2016-09-02 | C | 8 | 0.004709 | 2.4027e-05
2017 | 2016-09-02 | C | 59 | 0.049792 | 0.0001772
2017 | 2016-09-02 | C | 17 | 0.009255 | 5.1057e-05
2017 | 2016-09-02 | C | 219 | 0.050009 | 0.00065774
2017 | 2016-09-03 | C | 6 | 0.001387 | 1.802e-05
2017 | 2016-09-03 | C | 697 | 0.18599 | 0.0020933
2017 | 2016-09-03 | C | 26 | 0.005622 | 7.8087e-05
2017 | 2016-09-03 | C | 967 | 0.26808 | 0.0029042
2017 | 2016-09-03 | C | 525 | 0.30469 | 0.0015768
2017 | 2016-09-04 | C | 219 | 0.079451 | 0.0016338
2017 | 2016-09-04 | C | 2 | 0.000754 | 6.0066e-06
2017 | 2016-09-04 | C | 19 | 0.004716 | 5.7063e-05
2017 | 2016-09-05 | C | 3 | 0.002811 | 9.0098e-06
2017 | 2016-09-05 | C | 155 | 0.10769 | 0.00053458
2017 | 2016-09-05 | C | 4 | 0.00182 | 1.2013e-05
2017 | 2016-09-05 | C | 28 | 0.006526 | 8.4092e-05
2017 | 2016-09-28 | B | 9 | 0.008824 | 2.7023e-05
2017 | 2016-09-05 | C | 1 | 0.000495 | 3.0032e-06
2017 | 2016-09-05 | C | 185 | 0.040698 | 0.0010481
2017 | 2016-09-05 | C | 1 | 0.000714 | 3.0032e-06
2017 | 2016-09-05 | C | 23 | 0.004359 | 6.9075e-05
2017 | 2016-09-05 | B | 112 | 0.050741 | 0.00067274
2017 | 2016-09-05 | C | 4 | 0.00018 | 1.2013e-05
2017 | 2016-09-27 | B | 41 | 0.006557 | 0.00012311
2017 | 2016-09-05 | C | 362 | 0.010527 | 0.0010872
2017 | 2016-09-06 | C | 451 | 0.12186 | 0.0013545
2017 | 2016-09-06 | C | 9 | 0.015325 | 2.7029e-05
2017 | 2016-09-06 | C | 66 | 0.008721 | 0.00019821
2017 | 2016-09-27 | B | 42 | 0.062045 | 0.00012611
2017 | 2016-09-06 | C | 2 | 0.002537 | 6.0065e-06
2017 | 2016-09-06 | C | 109 | 0.019004 | 0.00032735
2017 | 2016-09-09 | B | 8 | 0.004012 | 2.4025e-05
2017 | 2016-09-06 | C | 1 | 0.000363 | 3.0032e-06
2017 | 2016-09-28 | B | 28 | 0.015637 | 8.4071e-05
2017 | 2016-09-07 | C | 1412 | 0.042556 | 0.0042406
2017 | 2016-09-07 | C | 82 | 0.043876 | 0.0005616
2017 | 2016-09-07 | C | 501 | 0.056247 | 0.0023996
2017 | 2016-09-07 | C | 931 | 0.28238 | 0.002796
2017 | 2016-09-07 | C | 1 | 0.000213 | 3.0032e-06
2017 | 2016-09-07 | C | 44 | 0.010674 | 0.00013214
2017 | 2016-09-07 | C | 1 | 0.004293 | 3.0032e-06
2017 | 2016-09-07 | C | 296 | 0.024389 | 0.00088896
2017 | 2016-09-07 | C | 9 | 0.012796 | 2.7029e-05
2017 | 2016-09-07 | C | 22 | 0.012682 | 6.6071e-05
2017 | 2016-09-07 | C | 3 | 0.001033 | 9.0096e-06
2017 | 2016-09-07 | C | 155 | 0.019544 | 0.0004655
2017 | 2016-09-07 | C | 1 | 0.000186 | 3.0032e-06
2017 | 2016-09-07 | C | 496 | 0.086634 | 0.0016998
2017 | 2016-09-07 | C | 23 | 0.059281 | 6.9074e-05
2017 | 2016-09-07 | C | 173 | 0.07688 | 0.0011412
2017 | 2016-09-07 | C | 237 | 0.17236 | 0.00071177
2017 | 2016-09-08 | C | 3767 | 0.75577 | 0.019124
2017 | 2016-09-08 | C | 171 | 0.16206 | 0.00051355
2017 | 2016-09-08 | C | 12 | 0.002724 | 3.6038e-05
2017 | 2016-09-08 | C | 1016 | 0 | 0.0030513
2017 | 2016-09-08 | C | 1016 | 0 | 0.0030513
2017 | 2016-09-08 | C | 248 | 0.072849 | 0.0013454
2017 | 2016-09-08 | C | 8 | 0.005915 | 2.4026e-05
2017 | 2016-09-08 | C | 19 | 0.00251 | 5.7061e-05
2017 | 2016-09-08 | C | 2 | 0.002457 | 6.0064e-06
2017 | 2016-09-08 | C | 75 | 0.09118 | 0.00022524
2017 | 2016-09-08 | C | 77 | 0.050878 | 0.00023125
2017 | 2016-09-08 | C | 242 | 0.10912 | 0.0010151
2017 | 2016-09-08 | C | 2 | 0.0028 | 6.0064e-06
2017 | 2016-09-08 | C | 82 | 0.045312 | 0.00024626
2017 | 2016-09-08 | C | 1 | 0.001862 | 3.0032e-06
2017 | 2016-09-08 | C | 1 | 0.000487 | 3.0032e-06
2017 | 2016-09-08 | C | 2137 | 0.13945 | 0.0064178
2017 | 2016-09-08 | C | 22 | 0.000198 | 6.607e-05
2017 | 2016-09-08 | C | 474 | 0.1116 | 0.002817
2017 | 2016-09-09 | B | 6 | 0.00126 | 1.8019e-05
2017 | 2016-09-08 | C | 13 | 0.002514 | 3.9042e-05
2017 | 2016-09-08 | B | 145 | 0.013499 | 0.00043546
2017 | 2016-09-08 | C | 3 | 0.005716 | 9.0096e-06
2017 | 2016-09-08 | C | 87 | 0.081357 | 0.00026128
2017 | 2016-09-08 | C | 42 | 0.000372 | 0.00012613
2017 | 2016-09-08 | C | 17 | 0.004799 | 5.1054e-05
2017 | 2016-09-08 | C | 411 | 0.33878 | 0.0012343
2017 | 2016-09-08 | C | 108 | 0.045657 | 0.00032435
2017 | 2016-09-08 | C | 161 | 0.06889 | 0.00048352
2017 | 2016-09-08 | C | 118 | 0.024422 | 0.00035438
2017 | 2016-09-08 | C | 421 | 0.093223 | 0.0012643
2017 | 2016-09-08 | C | 3 | 0.0028 | 9.0096e-06
2017 | 2016-09-08 | C | 120 | 0.017965 | 0.00036038
2017 | 2016-09-08 | C | 1 | 0.000415 | 3.0032e-06
2017 | 2016-09-08 | C | 2 | 0.001101 | 6.0064e-06
2017 | 2016-09-08 | C | 206 | 0.032701 | 0.00061866
2017 | 2016-09-08 | C | 289 | 0.065208 | 0.00085291
2017 | 2016-09-08 | C | 6 | 0.00457 | 1.8019e-05
2017 | 2016-09-08 | C | 5 | 0.002159 | 1.5016e-05
2017 | 2016-09-08 | C | 219 | 0.18921 | 0.0006577
2017 | 2016-09-08 | C | 316 | 0.23152 | 0.0011562
2017 | 2016-09-08 | C | 1 | 0.003581 | 3.0032e-06
2017 | 2016-09-08 | C | 13 | 0.031303 | 3.9042e-05
2017 | 2016-09-08 | C | 115 | 0.05332 | 0.00034537
2017 | 2016-09-09 | C | 5 | 0.001563 | 1.5016e-05
2017 | 2016-09-08 | C | 120 | 0.2233 | 0.00036038
2017 | 2016-09-08 | C | 868 | 0.24965 | 0.0026068
2017 | 2016-09-08 | C | 493 | 0.31782 | 0.0015947
2017 | 2016-09-08 | C | 180 | 0.27632 | 0.00035438
2017 | 2016-09-09 | C | 7 | 0.012627 | 2.1022e-05
2017 | 2016-09-09 | C | 1 | 0.001947 | 3.0031e-06
2017 | 2016-09-09 | C | 1 | 0.002476 | 3.0031e-06
2017 | 2016-09-09 | C | 1 | 0.0005 | 3.0031e-06
2017 | 2016-09-09 | C | 3 | 0.003488 | 9.0094e-06
2017 | 2016-09-09 | C | 104 | 0.045085 | 0.00031233
2017 | 2016-09-09 | C | 29 | 0.029974 | 8.7092e-05
2017 | 2016-09-09 | C | 14 | 0.00597 | 4.2044e-05
2017 | 2016-09-09 | C | 7 | 0.00679 | 2.1022e-05
2017 | 2016-09-09 | C | 2 | 0.001764 | 6.0063e-06
2017 | 2016-09-09 | C | 47 | 0.01722 | 0.00014115
2017 | 2016-09-09 | C | 281 | 0.079982 | 0.00084389
2017 | 2016-09-11 | B | 3 | 9e-05 | 9.0093e-06
2017 | 2016-09-09 | C | 493 | 0.13528 | 0.0019881
2017 | 2016-09-09 | C | 4 | 0.000324 | 1.2013e-05
2017 | 2016-09-09 | C | 2 | 0.00027 | 6.0063e-06
2017 | 2016-09-30 | B | 8 | 0.008551 | 2.402e-05
2017 | 2016-09-08 | C | 4 | 0.010071 | 1.2013e-05
2017 | 2016-09-09 | C | 206 | 0.061061 | 0.00086191
2017 | 2016-09-09 | C | 256 | 0.10123 | 0.00090395
2017 | 2016-09-27 | B | 26 | 0.018033 | 7.8067e-05
2017 | 2016-09-09 | C | 1 | 0.000679 | 3.0031e-06
2017 | 2016-09-09 | C | 967 | 0.23187 | 0.0029041
2017 | 2016-09-09 | C | 47 | 0.003013 | 0.00014115
2017 | 2016-10-03 | B | 4 | 0.000984 | 1.2009e-05
2017 | 2016-10-03 | B | 2 | 0.000882 | 6.0046e-06
2017 | 2016-09-08 | C | 20 | 0.096371 | 6.0064e-05
2017 | 2016-10-03 | B | 3 | 0.000594 | 9.007e-06
2017 | 2016-10-03 | B | 7 | 0.001387 | 2.1016e-05
2017 | 2016-10-04 | B | 7 | 0.005401 | 2.1016e-05
2017 | 2016-09-12 | B | 38 | 0.007075 | 0.00011412
2017 | 2016-09-09 | C | 1 | 0.000221 | 3.0031e-06
2017 | 2016-10-05 | B | 5 | 0.00033 | 1.5011e-05
2017 | 2016-10-05 | B | 3 | 0.000846 | 9.0068e-06
2017 | 2016-10-05 | B | 6 | 0.004719 | 1.8014e-05
2017 | 2016-09-09 | C | 72 | 0.005838 | 0.00021623
2017 | 2016-10-09 | B | 1 | 0.001134 | 3.0021e-06
2017 | 2016-09-09 | C | 5 | 0.00075 | 1.5016e-05
2017 | 2016-09-09 | C | 26 | 0.007886 | 7.8082e-05
2017 | 2016-09-09 | C | 1 | 0.000303 | 3.0031e-06
2017 | 2016-09-09 | C | 6 | 0.002741 | 1.8019e-05
2017 | 2016-09-09 | C | 3 | 0.000919 | 9.0094e-06
2017 | 2016-09-09 | C | 665 | 0.14302 | 0.0016127
2017 | 2016-09-09 | C | 172 | 0.032936 | 0.00051654
2017 | 2016-09-10 | C | 1 | 0.000476 | 3.0031e-06
2017 | 2016-09-10 | C | 122 | 0.089727 | 0.00036638
2017 | 2016-09-10 | C | 1 | 0.00041 | 3.0031e-06
2017 | 2016-09-10 | C | 496 | 0.08855 | 0.0014896
2017 | 2016-09-10 | C | 1 | 0.000563 | 3.0031e-06
2017 | 2016-09-10 | C | 342 | 0.087679 | 0.0010271
2017 | 2016-09-10 | C | 32 | 0.003171 | 9.61e-05
2017 | 2016-09-10 | C | 24 | 0.004324 | 7.2075e-05
2017 | 2016-09-10 | C | 25 | 0.007306 | 7.5078e-05
2017 | 2016-09-11 | C | 84 | 0.02031 | 0.00025226
2017 | 2016-09-12 | C | 34 | 0.006738 | 0.0001021
2017 | 2016-09-12 | C | 48 | 0.009369 | 0.00014415
2017 | 2016-09-12 | C | 7965 | 0.54018 | 0.02392
2017 | 2016-10-03 | B | 25 | 0.008631 | 7.5059e-05
2017 | 2016-10-07 | B | 4 | 0.000684 | 1.2009e-05
2017 | 2016-10-03 | B | 4 | 0.00293 | 1.2009e-05
2017 | 2016-10-03 | B | 338 | 0.002121 | 0.0010148
2017 | 2016-10-11 | B | 81 | 0.065217 | 0.00024317
2017 | 2016-10-03 | B | 3 | 0.001278 | 9.007e-06
2017 | 2016-10-04 | B | 11 | 0.003996 | 3.3025e-05
2017 | 2016-10-04 | B | 9 | 0.007403 | 2.7021e-05
2017 | 2016-09-12 | C | 1 | 0.000787 | 3.003e-06
2017 | 2016-09-12 | C | 26 | 0.007808 | 7.808e-05
2017 | 2016-10-05 | B | 12 | 0.005115 | 3.6027e-05
2017 | 2016-09-12 | C | 5 | 0.000207 | 3.003e-06
2017 | 2016-10-06 | B | 4 | 0.003578 | 1.2009e-05
2017 | 2016-09-12 | C | 3 | 0.001135 | 9.0092e-06
2017 | 2016-09-09 | C | 53 | 0.017826 | 0.00015917
2017 | 2016-09-09 | C | 1 | 0.000222 | 3.0031e-06
2017 | 2016-10-04 | B | 12 | 0.01351 | 3.6028e-05
2017 | 2016-09-12 | C | 178 | 0.14352 | 0.0014775
2017 | 2016-10-01 | B | 61 | 0.020146 | 0.00018315
2017 | 2016-09-28 | B | 129 | 0.032219 | 0.00038733
2017 | 2016-09-13 | C | 49 | 0.031048 | 0.00014715
2017 | 2016-09-13 | C | 25 | 0.007003 | 7.5076e-05
2017 | 2016-09-13 | C | 9 | 0.0041 | 2.7027e-05
2017 | 2016-09-15 | C | 5 | 0.001456 | 1.5015e-05
2017 | 2016-10-04 | B | 149 | 0.11273 | 0.00044734
2017 | 2016-09-29 | B | 65 | 0.079935 | 0.00019516
2017 | 2016-10-03 | B | 3 | 0.003026 | 9.007e-06
2017 | 2016-10-03 | B | 1 | 0.000408 | 3.0023e-06
2017 | 2016-10-04 | B | 10 | 0.004563 | 3.0023e-05
2017 | 2016-10-03 | B | 3 | 0.00045 | 9.007e-06
2017 | 2016-10-03 | B | 38 | 0.035253 | 0.00011409
2017 | 2016-10-04 | B | 14 | 0.019334 | 4.2032e-05
2017 | 2016-09-13 | C | 1569 | 0 | 0.0047118
2017 | 2016-09-27 | B | 16 | 0.00711 | 4.8041e-05
2017 | 2016-10-04 | B | 88 | 0.089776 | 0.0002642
2017 | 2016-09-13 | C | 244 | 0.052629 | 0.00083785
2017 | 2016-09-13 | C | 155 | 0.058188 | 0.0011201
2017 | 2016-09-13 | C | 297 | 0.097341 | 0.0012222
2017 | 2016-09-14 | C | 317 | 0.044062 | 0.0012703
2017 | 2016-09-14 | C | 714 | 0.27113 | 0.0035946
2017 | 2016-09-14 | C | 353 | 0.0602 | 0.0010601
2017 | 2016-09-14 | C | 317 | 0.01385 | 0.00095196
2017 | 2016-10-04 | B | 4 | 0.005043 | 1.2009e-05
2017 | 2016-09-29 | B | 3 | 0.001985 | 9.0074e-06
2017 | 2016-09-14 | C | 18 | 0.005975 | 5.4054e-05
2017 | 2016-10-04 | B | 19 | 0.018276 | 5.7044e-05
2017 | 2016-10-04 | B | 4 | 0.003486 | 1.2009e-05
2017 | 2016-10-04 | B | 9 | 0.005187 | 2.7021e-05
2017 | 2016-10-04 | B | 20 | 0.009674 | 6.0046e-05
2017 | 2016-09-14 | C | 1 | 0.000165 | 3.003e-06
2017 | 2016-10-04 | B | 61 | 0.034247 | 0.00018314
2017 | 2016-09-14 | C | 2 | 0.002434 | 6.006e-06
2017 | 2016-09-15 | C | 1 | 0.000342 | 3.0029e-06
2017 | 2016-10-04 | B | 18 | 0.021778 | 5.4042e-05
2017 | 2016-10-05 | B | 220 | 0.23051 | 0.0006605
2017 | 2016-10-05 | B | 34 | 0.029296 | 0.00010208
2017 | 2016-09-14 | C | 1 | 6e-06 | 3.003e-06
2017 | 2016-10-12 | B | 18 | 0.017507 | 5.4036e-05
2017 | 2016-10-05 | B | 5 | 0.006002 | 1.5011e-05
2017 | 2016-10-05 | B | 3 | 0.001143 | 9.0068e-06
2017 | 2016-10-05 | B | 5 | 0.002206 | 1.5011e-05
2017 | 2016-09-14 | C | 317 | 0.062036 | 0.00095196
2017 | 2016-10-31 | B | 23 | 0.026369 | 6.903e-05
2017 | 2016-10-06 | B | 2 | 0.001122 | 6.0044e-06
2017 | 2016-10-05 | B | 11 | 0.000852 | 3.3025e-05
2017 | 2016-09-14 | C | 1 | 0.000188 | 3.003e-06
2017 | 2016-09-14 | C | 1 | 9.1e-05 | 3.003e-06
2017 | 2016-09-15 | C | 76 | 0.054705 | 0.00022823
2017 | 2016-09-15 | C | 714 | 0.14277 | 0.0021441
2017 | 2016-09-15 | B | 1 | 0.000354 | 3.0029e-06
2017 | 2016-10-13 | B | 267 | 0.089771 | 0.00080153
2017 | 2016-10-06 | B | 3 | 0.001684 | 9.0067e-06
2017 | 2016-10-06 | B | 67 | 0.017902 | 0.00020115
2017 | 2016-10-05 | B | 301 | 0.094886 | 0.00090368
2017 | 2016-10-06 | B | 17 | 0.015158 | 5.1038e-05
2017 | 2016-10-06 | B | 14 | 0.014164 | 4.2031e-05
2017 | 2016-09-15 | C | 2 | 0.00024 | 6.0059e-06
2017 | 2016-09-16 | C | 238 | 0.065406 | 0.0007147
2017 | 2016-10-05 | B | 55 | 0.090323 | 0.00016512
2017 | 2016-09-16 | C | 10 | 0.005026 | 3.0029e-05
2017 | 2016-10-05 | B | 26 | 0.023964 | 7.8059e-05
2017 | 2016-09-16 | C | 32 | 0.005908 | 9.6094e-05
2017 | 2016-10-07 | B | 66 | 0.032171 | 0.00019815
2017 | 2016-10-06 | B | 119 | 0.12933 | 0.00035727
2017 | 2016-09-16 | C | 161 | 0.53437 | 0.001069
2017 | 2016-09-16 | C | 3 | 0.001567 | 9.0088e-06
2017 | 2016-09-16 | C | 606 | 0.14965 | 0.0018198
2017 | 2016-10-06 | B | 99 | 0.10016 | 0.00029722
2017 | 2016-10-07 | B | 61 | 0.037908 | 0.00018313
2017 | 2016-09-16 | C | 10 | 0.006843 | 3.0029e-05
2017 | 2016-09-16 | C | 430 | 0.12913 | 0.0023843
2017 | 2016-10-07 | B | 70 | 0.080699 | 0.00021015
2017 | 2016-09-16 | C | 6 | 0.001639 | 1.8018e-05
2017 | 2016-10-11 | B | 7 | 0.007186 | 2.1014e-05
2017 | 2016-10-13 | B | 7 | 0.006136 | 2.1014e-05
2017 | 2016-10-20 | B | 24 | 0.026727 | 7.2041e-05
2017 | 2016-09-16 | C | 155 | 0.039109 | 0.00046546
2017 | 2016-09-16 | C | 83 | 0.000684 | 0.00024924
2017 | 2016-10-26 | B | 57 | 0.06621 | 0.00017109
2017 | 2016-10-28 | B | 55 | 0.058206 | 0.00016508
2017 | 2016-09-16 | C | 18 | 0.005189 | 5.4053e-05
2017 | 2016-09-17 | C | 9 | 0.002648 | 2.7026e-05
2017 | 2016-09-16 | C | 352 | 0.075683 | 0.0019279
2017 | 2016-09-16 | C | 316 | 0.069254 | 0.00094893
2017 | 2016-09-17 | C | 27 | 0.053917 | 8.1079e-05
2017 | 2016-09-17 | C | 6396 | 0.15778 | 0.0017567
2017 | 2016-09-17 | C | 329 | 0.005765 | 0.00017117
2017 | 2016-09-17 | C | 1 | 0.000177 | 3.0029e-06
2017 | 2016-09-17 | C | 430 | 0.16492 | 0.0023843
2017 | 2016-09-17 | C | 570 | 0.30511 | 0.0017117
2017 | 2016-09-17 | C | 10 | 0.003467 | 3.0029e-05
2017 | 2016-09-18 | C | 1 | 0.000711 | 3.0028e-06
2017 | 2016-09-18 | C | 11 | 0.002312 | 3.3032e-05
2017 | 2016-09-18 | C | 2 | 0.000991 | 6.0057e-06
2017 | 2016-09-18 | C | 202 | 0.035714 | 0.00060658
2017 | 2016-09-18 | C | 2 | 0.000611 | 6.0057e-06
2017 | 2016-09-18 | C | 76 | 0.006618 | 0.00022822
2017 | 2016-09-18 | C | 135 | 0.017627 | 0.00040539
2017 | 2016-09-18 | C | 79 | 0.0325 | 0.00023723
2017 | 2016-09-18 | C | 3 | 0.00126 | 9.0086e-06
2017 | 2016-09-18 | C | 20 | 0.007077 | 6.0058e-05
2017 | 2016-09-18 | C | 7 | 0.001411 | 2.102e-05
2017 | 2016-09-18 | C | 11 | 0.002868 | 3.3032e-05
2017 | 2016-09-19 | C | 26 | 0.005009 | 7.8074e-05
2017 | 2016-09-19 | C | 5 | 0.001384 | 1.5014e-05
2017 | 2016-10-16 | B | 13 | 0.006634 | 3.9024e-05
2017 | 2016-09-30 | B | 15 | 0.011529 | 4.5037e-05
2017 | 2016-09-19 | C | 37 | 0.006221 | 0.00011111
2017 | 2016-10-17 | B | 75 | 0.019586 | 0.00022514
2017 | 2016-10-12 | B | 5 | 0.006229 | 1.501e-05
2017 | 2016-10-13 | B | 14 | 0.003236 | 4.2028e-05
2017 | 2016-10-05 | B | 308 | 0.18906 | 0.0012519
2017 | 2016-10-11 | B | 40 | 0.056318 | 0.00012008
2017 | 2016-09-19 | C | 82 | 0.003648 | 0.00024623
2017 | 2016-09-19 | C | 5 | 0.001209 | 1.5014e-05
2017 | 2016-10-10 | B | 88 | 0.022455 | 0.00026418
2017 | 2016-10-18 | B | 3 | 0.001972 | 9.0053e-06
2017 | 2016-10-11 | B | 11 | 0.007066 | 3.3023e-05
2017 | 2016-09-30 | B | 28 | 0.011181 | 8.4069e-05
2017 | 2016-10-05 | B | 46 | 0.046679 | 0.0001381
2017 | 2016-09-20 | C | 422 | 0.17164 | 0.0012672
2017 | 2016-10-10 | B | 122 | 0.025271 | 0.00036626
2017 | 2016-10-08 | B | 1 | 0.000108 | 3.0021e-06
2017 | 2016-10-11 | B | 18 | 0.012266 | 5.4037e-05
2017 | 2016-10-08 | B | 2 | 0.00012 | 6.0043e-06
2017 | 2016-10-10 | B | 46 | 0.053995 | 0.0001381
2017 | 2016-10-04 | B | 71 | 0.05393 | 0.00021316
2017 | 2016-10-18 | B | 7 | 0.000252 | 2.1012e-05
2017 | 2016-10-18 | B | 3 | 0.000153 | 9.0053e-06
2017 | 2016-09-27 | B | 1 | 0.000711 | 3.0025e-06
2017 | 2016-10-18 | B | 3 | 0.000108 | 9.0053e-06
2017 | 2016-10-11 | B | 6 | 0.003188 | 1.8012e-05
2017 | 2016-09-20 | C | 169 | 0.073655 | 0.00050748
2017 | 2016-09-20 | C | 202 | 0.067068 | 0.00060657
2017 | 2016-09-20 | C | 202 | 0.042465 | 0.00060657
2017 | 2016-09-21 | C | 186 | 0.076369 | 0.00055852
2017 | 2016-10-11 | B | 1 | 0.000342 | 3.002e-06
2017 | 2016-10-12 | B | 395 | 0.13389 | 0.0011858
2017 | 2016-09-21 | C | 95 | 0.003965 | 0.00028526
2017 | 2016-09-21 | C | 640 | 0.021725 | 0.0019218
2017 | 2016-09-21 | C | 324 | 0.40296 | 0.0009729
2017 | 2016-09-21 | C | 23 | 0.002348 | 6.9064e-05
2017 | 2016-09-21 | C | 68 | 0.026081 | 0.00020419
2017 | 2016-09-22 | C | 4206 | 0.68164 | 0.01263
2017 | 2016-10-11 | B | 172 | 0.1957 | 0.00051635
2017 | 2016-09-22 | C | 17 | 0.0047 | 5.1047e-05
2017 | 2016-09-27 | B | 15 | 0.004116 | 4.5038e-05
2017 | 2016-10-13 | B | 24 | 0.020893 | 7.2048e-05
2017 | 2016-09-22 | C | 1 | 0.000482 | 3.0027e-06
2017 | 2016-09-22 | C | 68 | 0.010294 | 0.00040837
2017 | 2016-09-23 | B | 93 | 0.030717 | 0.00027925
2017 | 2016-09-23 | C | 445 | 0.16979 | 0.0014293
2017 | 2016-10-17 | B | 5 | 0.004247 | 1.5009e-05
2017 | 2016-09-25 | B | 23 | 6.9e-05 | 6.9061e-05
2017 | 2016-09-23 | C | 2 | 0.000655 | 6.0054e-06
2017 | 2016-10-13 | B | 1 | 0.000591 | 3.0019e-06
2017 | 2016-10-13 | B | 11 | 0.00449 | 3.3022e-05
2017 | 2016-10-13 | B | 52 | 0.052294 | 0.0001561
2017 | 2016-09-23 | C | 5 | 0.001981 | 1.5013e-05
2017 | 2016-10-15 | B | 78 | 0.087805 | 0.00023415
2017 | 2016-10-20 | B | 52 | 0.036837 | 0.00015609
2017 | 2016-10-17 | B | 2 | 0.00096 | 6.0036e-06
2017 | 2016-09-23 | C | 4 | 0.001352 | 1.2011e-05
2017 | 2016-10-18 | B | 20 | 0.020858 | 6.0036e-05
2017 | 2016-09-23 | C | 5 | 0.000789 | 1.5013e-05
2017 | 2016-09-24 | C | 7 | 0.011556 | 2.1019e-05
2017 | 2016-09-24 | C | 2 | 0.00186 | 6.0053e-06
2017 | 2016-09-24 | C | 25 | 0.003077 | 7.5067e-05
2017 | 2016-09-24 | C | 1 | 0.000168 | 3.0026e-06
2017 | 2016-09-24 | C | 313 | 0.032099 | 0.00093984
2017 | 2016-09-24 | C | 15 | 0.039907 | 5.4048e-05
2017 | 2016-09-25 | C | 26 | 0.092071 | 0.00010209
2017 | 2016-09-25 | C | 1138 | 0.17226 | 0.003417
2017 | 2016-09-25 | C | 927 | 0.14153 | 0.0027834
2017 | 2016-09-26 | C | 2 | 0.000417 | 6.0052e-06
2017 | 2016-09-26 | C | 1 | 0.000249 | 3.0026e-06
2017 | 2016-09-26 | C | 7 | 0.000777 | 2.1018e-05
2017 | 2016-09-26 | C | 2 | 0.000378 | 6.0052e-06
2017 | 2016-09-26 | C | 214 | 0.042353 | 0.0010089
2017 | 2016-10-07 | B | 7 | 0.000819 | 2.1015e-05
2017 | 2016-09-26 | C | 5 | 0.000795 | 1.5013e-05
2017 | 2016-09-26 | C | 35 | 0.00197 | 0.00010509
2017 | 2016-09-27 | B | 166 | 0.061161 | 0.00049843
2017 | 2016-09-26 | C | 1 | 0.000569 | 3.0026e-06
2017 | 2016-09-27 | C | 4 | 0.000998 | 1.201e-05
2017 | 2016-10-18 | B | 100 | 0.061426 | 0.00075645
2017 | 2016-10-19 | B | 6 | 0.006285 | 1.801e-05
2017 | 2016-09-27 | C | 5 | 0.001756 | 1.5013e-05
2017 | 2016-10-03 | B | 22 | 0.009115 | 6.6052e-05
2017 | 2016-09-27 | C | 83 | 0.021885 | 0.00024921
2017 | 2016-09-27 | C | 4 | 0.000751 | 1.201e-05
2017 | 2016-09-28 | C | 638 | 0.013879 | 0.0019156
2017 | 2016-10-19 | B | 54 | 0.021212 | 0.00016209
2017 | 2016-09-28 | C | 4 | 0.000923 | 1.201e-05
2017 | 2016-09-28 | C | 316 | 0.11495 | 0.0009488
2017 | 2016-10-19 | B | 32 | 0.006435 | 9.6056e-05
2017 | 2016-10-19 | B | 19 | 0.005817 | 5.7033e-05
2017 | 2016-09-28 | C | 241 | 0.071384 | 0.0013001
2017 | 2016-09-28 | C | 1 | 0.001069 | 3.0025e-06
2017 | 2016-09-28 | C | 2 | 0.002783 | 6.005e-06
2017 | 2016-09-28 | C | 2 | 0.00033 | 6.005e-06
2017 | 2016-09-28 | C | 1566 | 0.35268 | 0.0063864
2017 | 2016-09-28 | C | 48 | 0.099936 | 0.00028824
2017 | 2016-09-28 | C | 5 | 0.016706 | 1.5013e-05
2017 | 2016-09-28 | C | 4 | 0.000948 | 1.201e-05
2017 | 2016-09-28 | C | 1 | 0.001108 | 3.0025e-06
2017 | 2016-09-28 | C | 252 | 0.22657 | 0.00075664
2017 | 2016-09-28 | C | 1 | 0.001283 | 3.0025e-06
2017 | 2016-09-28 | C | 2 | 0.000737 | 6.005e-06
2017 | 2016-09-28 | C | 1 | 0.000368 | 3.0025e-06
2017 | 2016-09-28 | C | 451 | 0.22067 | 0.0013541
2017 | 2016-09-29 | C | 80 | 0.011615 | 0.0002402
2017 | 2016-09-29 | C | 14 | 0.00084 | 4.2035e-05
2017 | 2016-09-29 | C | 1 | 5.1e-05 | 3.0024e-06
2017 | 2016-09-29 | B | 3 | 0.000909 | 9.0074e-06
2017 | 2016-10-04 | B | 172 | 0.044926 | 0.0005164
2017 | 2016-10-04 | B | 61 | 0.038459 | 0.00018314
2017 | 2016-09-29 | C | 2 | 0.000419 | 6.0049e-06
2017 | 2016-10-07 | B | 7 | 0.007733 | 2.1015e-05
2017 | 2016-10-12 | B | 7 | 0.007775 | 2.1014e-05
2017 | 2016-10-27 | B | 7 | 0.005861 | 2.101e-05
2017 | 2016-09-29 | C | 92 | 0.062185 | 0.00033328
2017 | 2016-09-29 | C | 751 | 0.050589 | 0.0022549
2017 | 2016-09-29 | C | 1412 | 0.021608 | 0.0042395
2017 | 2016-09-30 | C | 76 | 0.067984 | 0.00022819
2017 | 2016-09-30 | C | 1 | 0.000491 | 3.0024e-06
2017 | 2016-09-30 | C | 143 | 0.062519 | 0.00042935
2017 | 2016-10-20 | B | 6 | 0.000504 | 1.801e-05
2017 | 2016-10-20 | B | 2 | 0.000342 | 6.0034e-06
2017 | 2016-10-20 | B | 7 | 0.003403 | 2.1012e-05
2017 | 2016-09-30 | C | 423 | 0.002837 | 0.00127
2017 | 2016-10-19 | B | 9 | 0.012512 | 2.7016e-05
2017 | 2016-09-30 | C | 1 | 0.000332 | 3.0024e-06
2017 | 2016-09-30 | C | 140 | 0.04125 | 0.001165
2017 | 2016-10-01 | C | 317 | 0.052081 | 0.00127
2017 | 2016-10-01 | C | 317 | 0.06552 | 0.0028283
2017 | 2016-10-01 | C | 5 | 0.00027 | 1.5012e-05
2017 | 2016-10-01 | C | 559 | 0.10631 | 0.0017714
2017 | 2016-10-01 | C | 1 | 0.000388 | 3.0024e-06
2017 | 2016-10-01 | C | 2 | 0.000281 | 6.0048e-06
2017 | 2016-10-01 | C | 3 | 0.000325 | 9.0072e-06
2017 | 2016-10-01 | C | 1 | 0.000162 | 3.0024e-06
2017 | 2016-10-01 | C | 1 | 0.002695 | 3.0024e-06
2017 | 2016-10-01 | C | 123 | 0.001772 | 0.0003693
2017 | 2016-10-01 | C | 1088 | 0.071121 | 0.0027082
2017 | 2016-10-02 | C | 1188 | 0.34901 | 0.0035668
2017 | 2016-10-02 | C | 1 | 0.000374 | 3.0023e-06
2017 | 2016-10-02 | C | 36 | 0.005997 | 0.00010809
2017 | 2016-10-02 | C | 53 | 0.00716 | 0.00015913
2017 | 2016-10-02 | C | 4 | 0.001188 | 1.201e-05
2017 | 2016-10-03 | C | 19 | 0.001483 | 5.7044e-05
2017 | 2016-10-03 | C | 1 | 0.000348 | 3.0023e-06
2017 | 2016-10-18 | B | 2 | 0.00018 | 6.0035e-06
2017 | 2016-10-20 | B | 6 | 0.001206 | 1.801e-05
2017 | 2016-10-26 | B | 7 | 0.005651 | 2.101e-05
2017 | 2016-10-03 | C | 9 | 0.002081 | 2.7021e-05
2017 | 2016-10-03 | C | 8 | 0.001943 | 2.4019e-05
2017 | 2016-10-03 | C | 8 | 0.001465 | 2.4019e-05
2017 | 2016-10-03 | C | 50 | 0.002702 | 0.00015012
2017 | 2016-10-04 | C | 7 | 0.001135 | 2.1016e-05
2017 | 2016-10-04 | C | 1 | 0.000359 | 3.0023e-06
2017 | 2016-10-04 | C | 2 | 0.000252 | 6.0046e-06
2017 | 2016-10-03 | C | 2 | 0.000552 | 6.0046e-06
2017 | 2016-10-04 | C | 4 | 0.000979 | 1.2009e-05
2017 | 2016-10-25 | B | 6 | 0.005708 | 1.8009e-05
2017 | 2016-10-25 | B | 6 | 0.000324 | 1.8009e-05
2017 | 2016-10-25 | B | 1 | 0.000474 | 3.0015e-06
2017 | 2016-10-03 | C | 2 | 0.000606 | 6.0046e-06
2017 | 2016-10-25 | B | 9 | 0.011129 | 2.7014e-05
2017 | 2016-10-28 | B | 4 | 0.004958 | 1.2006e-05
2017 | 2016-10-04 | C | 8 | 0.000528 | 2.4018e-05
2017 | 2016-10-27 | B | 34 | 0.030308 | 0.00010205
2017 | 2016-10-04 | C | 13 | 3.9e-05 | 3.903e-05
2017 | 2016-10-28 | B | 25 | 0.02191 | 7.5036e-05
2017 | 2016-10-04 | C | 171 | 0.043638 | 0.00051339
2017 | 2016-10-31 | B | 4 | 0.003409 | 1.2005e-05
2017 | 2016-10-07 | B | 69 | 0.098034 | 0.00020715
2017 | 2016-10-04 | C | 1 | 0.000162 | 3.0023e-06
2017 | 2016-10-25 | B | 55 | 0.038959 | 0.00016508
2017 | 2016-10-27 | B | 55 | 0.053155 | 0.00016508
2017 | 2016-10-04 | C | 3 | 0.000698 | 9.0069e-06
2017 | 2016-10-05 | C | 26 | 0.002888 | 7.8059e-05
2017 | 2016-10-04 | C | 208 | 0 | 6.0046e-06
2017 | 2016-11-01 | B | 60 | 0.060325 | 0.00018008
2017 | 2016-10-05 | C | 2 | 0.000667 | 6.0045e-06
2017 | 2016-10-19 | B | 357 | 0.069655 | 0.0010716
2017 | 2016-10-05 | C | 8 | 0.001964 | 2.4018e-05
2017 | 2016-10-26 | B | 18 | 0.020638 | 5.4027e-05
2017 | 2016-10-25 | B | 93 | 0.081509 | 0.00027914
2017 | 2016-10-07 | B | 207 | 0.29706 | 0.00062146
2017 | 2016-10-25 | B | 1 | 0.000954 | 3.0015e-06
2017 | 2016-10-26 | B | 1 | 0.000909 | 3.0014e-06
2017 | 2016-10-05 | C | 3 | 0.00045 | 9.0068e-06
2017 | 2016-11-01 | B | 86 | 0.095758 | 0.00025811
2017 | 2016-10-27 | B | 92 | 0.10797 | 0.00027613
2017 | 2016-11-02 | B | 61 | 0.033499 | 0.00018308
2017 | 2016-10-05 | C | 873 | 0.18534 | 0.00084364
2017 | 2016-11-08 | B | 95 | 0.10149 | 0.0002851
2017 | 2016-10-06 | C | 59 | 0.009565 | 0.00017713
2017 | 2016-10-05 | C | 24 | 0.011033 | 7.2055e-05
2017 | 2016-10-05 | C | 1 | 0.00067 | 3.0022e-06
2017 | 2016-10-05 | C | 262 | 0.035396 | 0.0007866
2017 | 2016-10-05 | C | 1 | 0.000176 | 3.0022e-06
2017 | 2016-10-05 | C | 145 | 0.091848 | 0.00068752
2017 | 2016-10-05 | C | 101 | 0.000368 | 0.00030323
2017 | 2016-10-05 | C | 2 | 0.000282 | 6.0045e-06
2017 | 2016-10-05 | C | 91 | 0.026927 | 0.00032725
2017 | 2016-10-06 | C | 345 | 0.085695 | 0.0011619
2017 | 2016-10-06 | C | 10 | 0.005773 | 3.0022e-05
2017 | 2016-10-06 | C | 1 | 0.00046 | 3.0022e-06
2017 | 2016-10-27 | B | 5 | 0.005507 | 1.5007e-05
2017 | 2016-10-06 | C | 16 | 0.001873 | 4.8036e-05
2017 | 2016-10-06 | C | 7 | 0.001621 | 2.1016e-05
2017 | 2016-10-06 | C | 4 | 0.000803 | 1.2009e-05
2017 | 2016-10-06 | C | 1 | 0.000459 | 3.0022e-06
2017 | 2016-10-06 | C | 7 | 0.001855 | 2.1016e-05
2017 | 2016-11-09 | B | 3 | 0.002007 | 9.0029e-06
2017 | 2016-11-07 | B | 23 | 0.007523 | 6.9024e-05
2017 | 2016-11-08 | B | 20 | 0.019986 | 6.002e-05
2017 | 2016-11-10 | B | 20 | 0.020886 | 6.0019e-05
2017 | 2016-10-13 | B | 27 | 0.027477 | 8.1054e-05
2017 | 2016-11-29 | B | 25 | 0.024226 | 7.5004e-05
2017 | 2016-11-03 | B | 9 | 0.000459 | 2.7011e-05
2017 | 2016-11-03 | B | 2 | 0.000132 | 6.0024e-06
2017 | 2016-11-03 | B | 8 | 0.000408 | 2.401e-05
2017 | 2016-11-07 | B | 10 | 0.00087 | 3.0011e-05
2017 | 2016-11-08 | B | 7 | 0.000777 | 2.1007e-05
2017 | 2016-11-08 | B | 3 | 0.000198 | 9.003e-06
2017 | 2016-11-08 | B | 2 | 0.00033 | 6.002e-06
2017 | 2016-11-09 | B | 3 | 0.000378 | 9.0029e-06
2017 | 2016-11-09 | B | 4 | 0.000684 | 1.2004e-05
2017 | 2016-10-06 | C | 1 | 0.000168 | 3.0022e-06
2017 | 2016-11-09 | B | 6 | 0.000306 | 1.8006e-05
2017 | 2016-10-06 | C | 334 | 0.005498 | 0.0010027
2017 | 2016-11-10 | B | 4 | 0.000864 | 1.2004e-05
2017 | 2016-11-30 | B | 4 | 0.000804 | 1.2e-05
2017 | 2016-11-30 | B | 8 | 0.001632 | 2.4001e-05
2017 | 2016-10-06 | C | 7 | 0.005659 | 2.1016e-05
2017 | 2016-10-30 | B | 253 | 0.33639 | 0.00075934
2017 | 2016-11-11 | B | 4 | 0.001656 | 1.2004e-05
2017 | 2016-11-14 | B | 8 | 0.007051 | 2.4006e-05
2017 | 2016-11-04 | B | 60 | 0.04047 | 0.00018007
2017 | 2016-10-26 | B | 11 | 0.011522 | 3.3016e-05
2017 | 2016-10-07 | C | 17 | 0.003674 | 5.1037e-05
2017 | 2016-10-05 | C | 34 | 0.005818 | 0.00010208
2017 | 2016-10-07 | C | 26 | 0.006629 | 7.8057e-05
2017 | 2016-10-07 | C | 138 | 0.000835 | 0.0004143
2017 | 2016-11-04 | B | 2 | 0.001998 | 6.0023e-06
2017 | 2016-10-07 | C | 15 | 0.00108 | 4.5033e-05
2017 | 2016-10-07 | C | 630 | 0.095924 | 0.0018914
2017 | 2016-10-07 | C | 475 | 0.055902 | 0.001426
2017 | 2016-10-08 | C | 1 | 0.000244 | 3.0021e-06
2017 | 2016-10-08 | C | 143 | 0.086484 | 0.00042931
2017 | 2016-10-08 | C | 1 | 0.00022 | 3.0021e-06
2017 | 2016-10-08 | C | 25 | 0.003829 | 7.5054e-05
2017 | 2016-10-09 | C | 5 | 0.001756 | 1.5011e-05
2017 | 2016-10-09 | C | 23 | 0.005426 | 6.9049e-05
2017 | 2016-10-09 | C | 1 | 0.000624 | 3.0021e-06
2017 | 2016-10-09 | C | 18 | 0.010406 | 5.4038e-05
2017 | 2016-10-09 | C | 121 | 0.012818 | 0.00036626
2017 | 2016-10-09 | C | 82 | 0.036202 | 0.00049535
2017 | 2016-10-09 | C | 1 | 0.005838 | 3.0021e-06
2017 | 2016-10-09 | C | 4 | 0.002425 | 1.2009e-05
2017 | 2016-10-09 | C | 1099 | 0.36109 | 0.0034645
2017 | 2016-10-09 | C | 19 | 0.003251 | 5.704e-05
2017 | 2016-10-09 | C | 9 | 0.005698 | 2.7019e-05
2017 | 2016-10-09 | C | 1 | 0.000689 | 3.0021e-06
2017 | 2016-10-09 | C | 1 | 0.000482 | 3.0021e-06
2017 | 2016-10-09 | C | 2 | 0.001152 | 6.0042e-06
2017 | 2016-10-09 | C | 13 | 0.002227 | 3.9028e-05
2017 | 2016-10-09 | C | 2 | 0.000666 | 6.0042e-06
2017 | 2016-10-09 | C | 1 | 0.000396 | 3.0021e-06
2017 | 2016-10-09 | C | 2 | 0.000952 | 6.0042e-06
2017 | 2016-10-09 | C | 3 | 0.014939 | 9.0063e-06
2017 | 2016-10-09 | C | 639 | 0.1639 | 0.0019184
2017 | 2016-10-09 | C | 3 | 0.001707 | 9.0063e-06
2017 | 2016-10-09 | C | 62 | 0.017305 | 0.00018613
2017 | 2016-10-09 | C | 2 | 0.00081 | 6.0042e-06
2017 | 2016-10-09 | C | 4 | 0.000804 | 1.2009e-05
2017 | 2016-10-10 | C | 1 | 0.0001 | 3.002e-06
2017 | 2016-10-10 | C | 205 | 0.044345 | 0.00061543
2017 | 2016-10-10 | C | 241 | 0.037127 | 0.0007235
2017 | 2016-11-01 | B | 36 | 0.024418 | 0.00010805
2017 | 2016-11-01 | B | 13 | 0.002926 | 3.9017e-05
2017 | 2016-10-16 | B | 205 | 0 | 0
2017 | 2016-10-10 | C | 1 | 0.00028 | 3.002e-06
2017 | 2016-11-01 | B | 17 | 0.017296 | 5.1022e-05
2017 | 2016-10-10 | C | 5 | 0.001531 | 1.501e-05
2017 | 2016-10-10 | C | 2 | 0.000762 | 6.0041e-06
2017 | 2016-10-10 | C | 83 | 0.081738 | 0.00044731
2017 | 2016-10-11 | C | 21 | 0.004467 | 6.3043e-05
2017 | 2016-10-11 | C | 48 | 0.068996 | 0.0001441
2017 | 2016-10-11 | C | 2 | 0.001174 | 6.0041e-06
2017 | 2016-10-11 | C | 17 | 0.014253 | 5.1035e-05
2017 | 2016-10-11 | C | 28 | 0.003026 | 8.4058e-05
2017 | 2016-10-11 | C | 702 | 0.10105 | 0.0021074
2017 | 2016-10-28 | B | 65 | 0.06516 | 0.00019509
2017 | 2016-10-11 | C | 17 | 0.002889 | 5.1035e-05
2017 | 2016-11-02 | B | 7 | 0.002962 | 2.1009e-05
2017 | 2016-10-27 | B | 33 | 0.011489 | 9.9048e-05
2017 | 2016-11-02 | B | 5 | 0.003736 | 1.5006e-05
2017 | 2016-11-02 | B | 2 | 0.00063 | 6.0024e-06
2017 | 2016-11-02 | B | 33 | 0.030405 | 9.9041e-05
2017 | 2016-10-11 | C | 8 | 0.005134 | 2.4016e-05
2017 | 2016-10-11 | C | 14 | 0.00311 | 4.2029e-05
2017 | 2016-10-11 | C | 5 | 0.00081 | 1.501e-05
2017 | 2016-10-11 | C | 1413 | 0.11729 | 0.0042419
2017 | 2016-10-12 | C | 387 | 0.047893 | 0.0011618
2017 | 2016-10-12 | C | 387 | 0.035305 | 0.001417
2017 | 2016-10-12 | C | 7 | 0.002523 | 2.1014e-05
2017 | 2016-10-12 | C | 2 | 0.000672 | 6.004e-06
2017 | 2016-11-03 | B | 25 | 0.01328 | 7.503e-05
2017 | 2016-10-12 | C | 746 | 0.017916 | 0.0022395
2017 | 2016-10-12 | C | 1 | 0.000568 | 3.002e-06
2017 | 2016-10-12 | C | 1188 | 0.3781 | 0.0090631
2017 | 2016-10-13 | C | 67 | 0.015021 | 0.00020113
2017 | 2016-10-27 | B | 37 | 0.029678 | 0.00017108
2017 | 2016-11-01 | B | 65 | 0.073741 | 0.00019508
2017 | 2016-10-13 | C | 419 | 0 | 0.0012578
2017 | 2016-11-02 | B | 2 | 0.000462 | 6.0024e-06
2017 | 2016-10-13 | C | 1 | 0.000459 | 3.0019e-06
2017 | 2016-10-14 | C | 16 | 0.003362 | 4.8031e-05
2017 | 2016-10-14 | C | 8 | 0.000624 | 3.0019e-06
2017 | 2016-10-31 | B | 129 | 0.12184 | 0.00066029
2017 | 2016-11-09 | B | 4 | 0.004393 | 1.2004e-05
2017 | 2016-10-29 | B | 20 | 0.005522 | 6.0028e-05
2017 | 2016-10-14 | C | 1 | 7.2e-05 | 3.0019e-06
2017 | 2016-10-14 | C | 83 | 0.06475 | 0.00024916
2017 | 2016-11-01 | B | 118 | 0.15087 | 0.00035415
2017 | 2016-10-18 | C | 42 | 0.002773 | 0.00012608
2017 | 2016-11-03 | B | 118 | 0.10376 | 0.00035414
2017 | 2016-11-08 | B | 118 | 0.021601 | 0.00035412
2017 | 2016-11-03 | B | 38 | 0.045276 | 0.00011405
2017 | 2016-10-14 | B | 23 | 0 | 6.9045e-05
2017 | 2016-11-03 | B | 9 | 0.006941 | 2.7011e-05
2017 | 2016-11-03 | B | 6 | 0.004627 | 1.8007e-05
2017 | 2016-10-15 | C | 1 | 0.000279 | 3.0019e-06
2017 | 2016-10-15 | C | 1 | 8.5e-05 | 3.0019e-06
2017 | 2016-10-15 | C | 4 | 0.001072 | 1.2008e-05
2017 | 2016-10-16 | C | 16 | 0.005107 | 4.803e-05
2017 | 2016-10-16 | C | 7 | 0.002507 | 2.1013e-05
2017 | 2016-10-16 | C | 4 | 0.00057 | 1.2007e-05
2017 | 2016-10-16 | C | 1024 | 0.067709 | 0.0030739
2017 | 2016-10-17 | C | 337 | 0.30575 | 0.0020232
2017 | 2016-10-21 | B | 8 | 0.007641 | 2.4013e-05
2017 | 2016-11-03 | B | 5 | 0.005177 | 1.5006e-05
2017 | 2016-11-09 | B | 5 | 0.005356 | 1.5005e-05
2017 | 2016-10-17 | C | 2 | 0.00064 | 6.0036e-06
2017 | 2016-11-18 | B | 5 | 0.00483 | 1.5003e-05
2017 | 2016-10-17 | C | 75 | 0.021613 | 0.00022514
2017 | 2016-10-26 | B | 37 | 0.047309 | 0.00033317
2017 | 2016-10-17 | C | 2 | 0.000719 | 6.0036e-06
2017 | 2016-10-17 | C | 1026 | 0.14808 | 0.0031189
2017 | 2016-10-17 | C | 8 | 0.002113 | 2.4015e-05
2017 | 2016-10-19 | B | 5 | 0.004382 | 1.5009e-05
2017 | 2016-10-17 | C | 309 | 0.011728 | 5.4033e-05
2017 | 2016-11-02 | B | 3 | 0.000603 | 9.0037e-06
2017 | 2016-11-23 | B | 12 | 0.006192 | 3.6005e-05
2017 | 2016-11-02 | B | 15 | 0.014721 | 4.5019e-05
2017 | 2016-11-24 | B | 2 | 0.000342 | 6.0007e-06
2017 | 2016-11-24 | B | 2 | 0.000312 | 6.0007e-06
2017 | 2016-10-17 | C | 1 | 0.003256 | 3.0018e-06
2017 | 2016-10-17 | C | 12 | 0.002946 | 3.6022e-05
2017 | 2016-10-17 | C | 7 | 0.002946 | 2.1013e-05
2017 | 2016-10-18 | C | 3 | 0.001401 | 9.0053e-06
2017 | 2016-10-18 | C | 4 | 0.000324 | 1.2007e-05
2017 | 2016-10-27 | B | 189 | 0.21727 | 0.00056728
2017 | 2016-11-03 | B | 29 | 0.017929 | 8.7035e-05
2017 | 2016-11-07 | B | 12 | 0.001512 | 7.2025e-05
2017 | 2016-11-04 | B | 4 | 0.003637 | 1.2005e-05
2017 | 2016-11-04 | B | 21 | 0.013928 | 6.3024e-05
2017 | 2016-11-09 | B | 5 | 0.003781 | 1.5005e-05
2017 | 2016-10-18 | C | 32 | 0.010374 | 9.6057e-05
2017 | 2016-10-18 | C | 240 | 0.03997 | 0.00072043
2017 | 2016-10-18 | C | 9 | 0.002755 | 2.7016e-05
2017 | 2016-11-12 | B | 197 | 0.19154 | 0.00059117
2017 | 2016-10-18 | C | 60 | 0.025935 | 0.00018011
2017 | 2016-10-18 | C | 1915 | 0 | 0.0057484
2017 | 2016-10-18 | C | 595 | 0.17118 | 0.0017861
2017 | 2016-10-18 | C | 5 | 0.001696 | 1.5009e-05
2017 | 2016-10-19 | C | 315 | 0.142 | 0.00094555
2017 | 2016-10-19 | C | 1 | 0.000455 | 3.0017e-06
2017 | 2016-11-05 | B | 24 | 0.00641 | 7.2027e-05
2017 | 2016-11-04 | B | 18 | 0.013343 | 5.4021e-05
2017 | 2016-11-07 | B | 26 | 0.016474 | 7.8027e-05
2017 | 2016-11-09 | B | 114 | 0.13265 | 0.00034211
2017 | 2016-10-20 | B | 8 | 0.006099 | 2.4014e-05
2017 | 2016-11-09 | B | 462 | 0.18301 | 0.0027729
2017 | 2016-10-20 | C | 5 | 0.003497 | 1.5009e-05
2017 | 2016-11-01 | B | 33 | 0.035358 | 9.9042e-05
2017 | 2016-11-03 | B | 33 | 0.036644 | 9.904e-05
2017 | 2016-11-08 | B | 70 | 0.030049 | 0.00036612
2017 | 2016-11-08 | B | 33 | 0.034463 | 9.9034e-05
2017 | 2016-11-10 | B | 33 | 0.034066 | 9.9031e-05
2017 | 2016-11-18 | B | 45 | 0.014447 | 0.00013503
2017 | 2016-11-05 | B | 2 | 0.001788 | 6.0022e-06
2017 | 2016-11-08 | B | 3 | 0.00325 | 9.003e-06
2017 | 2016-11-08 | B | 27 | 0.023741 | 8.1028e-05
2017 | 2016-11-10 | B | 16 | 0.012195 | 4.8015e-05
2017 | 2016-10-21 | B | 16 | 0.002977 | 4.8027e-05
2017 | 2016-11-14 | B | 2 | 0.00153 | 6.0015e-06
2017 | 2016-11-08 | B | 143 | 0.082052 | 0.00042915
2017 | 2016-10-30 | B | 210 | 0.024431 | 1.5007e-05
2017 | 2016-11-10 | B | 11 | 0.009639 | 3.301e-05
2017 | 2016-10-21 | C | 227 | 0.1371 | 0.0011526
2017 | 2016-10-21 | B | 79 | 0.000304 | 0.00023713
2017 | 2016-10-21 | C | 17 | 0.006671 | 5.1029e-05
2017 | 2016-11-10 | B | 86 | 0.06581 | 0.00025808
2017 | 2016-11-03 | B | 109 | 0.12071 | 0.00032713
2017 | 2016-11-02 | B | 46 | 0.0312 | 0.00013806
2017 | 2016-10-21 | C | 1 | 0.000387 | 3.0016e-06
2017 | 2016-10-21 | C | 5 | 0.00033 | 1.5008e-05
2017 | 2016-10-21 | C | 4 | 0.002245 | 1.2007e-05
2017 | 2016-10-21 | C | 50 | 0.009575 | 0.00015008
2017 | 2016-10-21 | C | 12 | 0.002773 | 3.602e-05
2017 | 2016-10-21 | C | 1332 | 0.00959 | 0.00011406
2017 | 2016-10-22 | C | 1 | 0.000123 | 3.0016e-06
2017 | 2016-10-22 | C | 109 | 0.013414 | 0.00032718
2017 | 2016-10-22 | C | 755 | 0.14674 | 0.0022662
2017 | 2016-10-22 | C | 7 | 0.000712 | 2.1011e-05
2017 | 2016-10-22 | C | 219 | 0.045256 | 0.00065736
2017 | 2016-10-22 | C | 37 | 0.001036 | 0.00011106
2017 | 2016-10-22 | C | 19 | 0.005189 | 5.7031e-05
2017 | 2016-10-22 | C | 882 | 0.19732 | 0.001864
2017 | 2016-10-23 | C | 566 | 0.3607 | 0.0016989
2017 | 2016-10-24 | C | 24 | 0.005513 | 7.2038e-05
2017 | 2016-10-25 | C | 1 | 0.00018 | 3.0015e-06
2017 | 2016-11-09 | B | 233 | 0.20867 | 0.0010113
2017 | 2016-11-12 | B | 29 | 0.029936 | 8.7025e-05
2017 | 2016-10-25 | C | 1 | 0.000106 | 3.0015e-06
2017 | 2016-10-25 | C | 179 | 0.040953 | 0.00053727
2017 | 2016-10-26 | C | 1 | 0.000243 | 3.0014e-06
2017 | 2016-10-26 | C | 1 | 0.000311 | 3.0014e-06
2017 | 2016-10-26 | C | 3 | 0.00146 | 9.0044e-06
2017 | 2016-10-26 | C | 1 | 3.3e-05 | 3.0014e-06
2017 | 2016-10-26 | C | 15 | 0.006323 | 4.5022e-05
2017 | 2016-10-26 | C | 630 | 0.021444 | 0.0018909
2017 | 2016-10-26 | C | 160 | 0.094126 | 0.00048024
2017 | 2016-10-26 | C | 21 | 0.006975 | 6.3031e-05
2017 | 2016-11-11 | B | 4 | 0.003625 | 1.2004e-05
2017 | 2016-11-11 | B | 75 | 0.046138 | 0.00022507
2017 | 2016-10-26 | C | 61 | 0.002927 | 0.00018309
2017 | 2016-10-26 | C | 1 | 0.000214 | 3.0014e-06
2017 | 2016-10-26 | C | 246 | 0.073098 | 0.00073837
2017 | 2016-10-27 | C | 1 | 0.000288 | 3.0014e-06
2017 | 2016-11-14 | B | 237 | 0.1598 | 0.0011343
2017 | 2016-10-27 | C | 237 | 0.05152 | 0.00071135
2017 | 2016-11-18 | B | 4 | 0.00444 | 1.2002e-05
2017 | 2016-11-16 | B | 88 | 0.009161 | 0.00026406
2017 | 2016-11-21 | B | 7 | 0.005964 | 2.1003e-05
2017 | 2016-11-01 | B | 70 | 0.10838 | 0.00042018
2017 | 2016-10-27 | C | 2 | 0.001223 | 6.0029e-06
2017 | 2016-11-10 | B | 104 | 0.083017 | 0.0003121
2017 | 2016-10-27 | C | 334 | 0.064838 | 0.0010025
2017 | 2016-11-22 | B | 77 | 0.007162 | 0.00023103
2017 | 2016-10-31 | B | 247 | 0.030128 | 0.00074133
2017 | 2016-11-23 | B | 2 | 0.001452 | 6.0008e-06
2017 | 2016-10-28 | C | 1 | 0.000435 | 3.0014e-06
2017 | 2016-11-24 | B | 37 | 0.030639 | 0.00011101
2017 | 2016-10-28 | C | 57 | 0.069421 | 0.00017108
2017 | 2016-10-28 | C | 703 | 0.3211 | 0.004301
2017 | 2016-10-29 | C | 26 | 0.016149 | 7.8036e-05
2017 | 2016-10-30 | C | 5 | 0 | 1.5007e-05
2017 | 2016-11-28 | B | 9 | 0.003051 | 2.7002e-05
2017 | 2016-11-28 | B | 2 | 0.000252 | 6.0003e-06
2017 | 2016-11-28 | B | 4 | 0.000504 | 1.2001e-05
2017 | 2016-11-28 | B | 5 | 0.000855 | 1.5001e-05
2017 | 2016-11-28 | B | 3 | 0.000513 | 9.0005e-06
2017 | 2016-11-30 | B | 5 | 0.00093 | 1.5e-05
2017 | 2016-11-30 | B | 1 | 8.7e-05 | 3.0001e-06
2017 | 2016-11-30 | B | 5 | 0.000225 | 1.5e-05
2017 | 2016-11-30 | B | 3 | 0.000288 | 9.0003e-06
2017 | 2016-11-30 | B | 3 | 0.000198 | 9.0003e-06
2017 | 2016-11-30 | B | 3 | 0.001638 | 9.0003e-06
2017 | 2016-11-24 | B | 2 | 0.00112 | 6.0007e-06
2017 | 2016-11-25 | B | 9 | 0.010877 | 2.7003e-05
2017 | 2016-11-29 | B | 5 | 0.000255 | 1.5001e-05
2017 | 2016-10-30 | C | 33 | 0.006068 | 9.9045e-05
2017 | 2016-10-30 | C | 6 | 0.001926 | 1.8008e-05
2017 | 2016-11-30 | B | 42 | 0.02457 | 0.000126
2017 | 2016-10-30 | C | 179 | 0.05416 | 0.00053724
2017 | 2016-11-15 | B | 17 | 0.019435 | 5.1013e-05
2017 | 2016-11-18 | B | 55 | 0.047271 | 0.00016503
2017 | 2016-10-31 | C | 203 | 0.034694 | 0.00071431
2017 | 2016-11-01 | C | 13 | 0.012263 | 3.9017e-05
2017 | 2016-11-17 | B | 25 | 0.02483 | 7.5016e-05
2017 | 2016-11-15 | B | 9 | 0.008939 | 2.7007e-05
2017 | 2016-11-01 | C | 4 | 0.001837 | 1.2005e-05
2017 | 2016-11-17 | B | 9 | 0.004347 | 2.7006e-05
2017 | 2016-11-16 | B | 13 | 0.016227 | 3.9009e-05
2017 | 2016-11-17 | B | 5 | 0.004786 | 1.5003e-05
2017 | 2016-11-01 | C | 11 | 0.011189 | 3.3014e-05
2017 | 2016-11-18 | B | 7 | 0.005587 | 2.1004e-05
2017 | 2016-11-01 | C | 92 | 0.00142 | 0.00027612
2017 | 2016-11-01 | C | 2 | 0.000288 | 6.0025e-06
2017 | 2016-11-01 | C | 9 | 0.002192 | 2.7012e-05
2017 | 2016-11-02 | C | 283 | 0.040811 | 0.00084935
2017 | 2016-11-02 | C | 1 | 0.000424 | 3.0012e-06
2017 | 2016-11-16 | B | 238 | 0.33887 | 0.00071417
2017 | 2016-11-02 | C | 1 | 0.000288 | 3.0012e-06
2017 | 2016-11-04 | B | 81 | 0.13783 | 0.00024309
2017 | 2016-11-18 | B | 167 | 0.26106 | 0.0010022
2017 | 2016-11-03 | C | 4 | 0.000791 | 1.2005e-05
2017 | 2016-11-03 | C | 1 | 0.000546 | 3.0012e-06
2017 | 2016-11-18 | B | 5 | 0.004966 | 1.5003e-05
2017 | 2016-11-22 | B | 5 | 0.005955 | 1.5002e-05
2017 | 2016-11-22 | B | 30 | 0.039065 | 9.0013e-05
2017 | 2016-11-03 | C | 22 | 0.002839 | 6.6027e-05
2017 | 2016-11-03 | C | 1 | 0.000317 | 3.0012e-06
2017 | 2016-11-04 | C | 2 | 0.001177 | 6.0023e-06
2017 | 2016-11-22 | B | 25 | 0.021153 | 7.5011e-05
2017 | 2016-11-04 | C | 1 | 0.00021 | 3.0011e-06
2017 | 2016-11-04 | C | 29 | 0.005182 | 8.7034e-05
2017 | 2016-11-23 | B | 5 | 0.002235 | 1.5002e-05
2017 | 2016-11-24 | B | 31 | 0.04111 | 9.3011e-05
2017 | 2016-11-04 | C | 1 | 0.001007 | 3.0011e-06
2017 | 2016-11-04 | C | 918 | 0.37673 | 0.0027551
2017 | 2016-11-05 | C | 107 | 0 | 3.0011e-06
2017 | 2016-11-05 | C | 91 | 0.039596 | 0.0002731
2017 | 2016-11-05 | C | 37 | 0.006116 | 0.00011104
2017 | 2016-11-06 | C | 424 | 0.10799 | 0.0012725
2017 | 2016-11-06 | C | 54 | 0.013436 | 0.00016206
2017 | 2016-11-06 | C | 1 | 0.000298 | 3.001e-06
2017 | 2016-11-06 | C | 4 | 0.002535 | 1.2004e-05
2017 | 2016-11-06 | C | 179 | 0.045198 | 0.0005372
2017 | 2016-11-06 | C | 3 | 0.000615 | 9.0032e-06
2017 | 2016-11-06 | C | 69 | 0.043901 | 0.00020708
2017 | 2016-11-07 | C | 1111 | 0.14637 | 0.0034242
2017 | 2016-11-07 | C | 637 | 1.2354 | 0.0019117
2017 | 2016-11-07 | C | 195 | 0.050321 | 0.00058521
2017 | 2016-11-07 | C | 300 | 0.1941 | 0.00090032
2017 | 2016-11-23 | B | 304 | 0.36979 | 0.00091212
2017 | 2016-11-07 | C | 71 | 0.024077 | 0.00021307
2017 | 2016-11-07 | C | 8 | 0.002953 | 2.4008e-05
2017 | 2016-11-25 | B | 110 | 0.12805 | 0.00033003
2017 | 2016-11-29 | B | 110 | 0.12607 | 0.00033002
2017 | 2016-11-22 | B | 189 | 0.32664 | 0.00056708
2017 | 2016-11-07 | C | 6 | 0.002753 | 1.8006e-05
2017 | 2016-11-07 | C | 45 | 0.030115 | 0.00013505
2017 | 2016-11-24 | B | 2 | 0.002202 | 6.0007e-06
2017 | 2016-11-24 | B | 16 | 0.017282 | 4.8006e-05
2017 | 2016-11-07 | C | 1 | 0.000225 | 3.001e-06
2017 | 2016-11-07 | C | 1 | 0.000226 | 3.001e-06
2017 | 2016-11-07 | C | 3 | 0.0005 | 9.0031e-06
2017 | 2016-11-07 | C | 4 | 0.002124 | 1.2004e-05
2017 | 2016-11-07 | C | 197 | 0.12993 | 0.00059121
2017 | 2016-11-07 | C | 1 | 0.000212 | 3.001e-06
2017 | 2016-11-07 | C | 1 | 0.000134 | 3.001e-06
2017 | 2016-11-07 | C | 3 | 0.001674 | 9.0031e-06
2017 | 2016-11-07 | C | 91 | 0.012617 | 0.00018907
2017 | 2016-11-07 | C | 10 | 0.005785 | 3.0011e-05
2017 | 2016-11-08 | C | 18 | 0.004429 | 5.4018e-05
2017 | 2016-11-07 | C | 627 | 0.28755 | 0.0021578
2017 | 2016-11-08 | C | 181 | 0.055605 | 0.00054318
2017 | 2016-11-08 | C | 258 | 0.015238 | 0.00014705
2017 | 2016-11-08 | C | 1 | 0.000216 | 3.001e-06
2017 | 2016-11-08 | C | 497 | 0.076525 | 0.0014915
2017 | 2016-11-08 | C | 1 | 0.000399 | 3.001e-06
2017 | 2016-11-08 | C | 11 | 0.003136 | 3.3011e-05
2017 | 2016-11-08 | C | 52 | 0.010995 | 0.00015605
2017 | 2016-11-08 | C | 33 | 0.031233 | 9.9034e-05
2017 | 2016-11-08 | C | 2 | 0.000804 | 6.002e-06
2017 | 2016-11-08 | C | 2 | 0.001018 | 6.002e-06
2017 | 2016-11-08 | C | 59 | 0.04957 | 0.00017706
2017 | 2016-11-08 | C | 15 | 0.010025 | 4.5015e-05
2017 | 2016-11-08 | C | 577 | 0.11197 | 0.0017316
2017 | 2016-11-08 | C | 9 | 0.008345 | 2.7009e-05
2017 | 2016-11-25 | B | 16 | 0.006576 | 4.8005e-05
2017 | 2016-11-08 | C | 438 | 0 | 0.0013144
2017 | 2016-11-08 | C | 4 | 0.000676 | 1.2004e-05
2017 | 2016-11-08 | C | 320 | 0.021403 | 0.00096033
2017 | 2016-11-08 | C | 928 | 0.16919 | 0.0027849
2017 | 2016-11-08 | C | 7 | 0.000315 | 2.1007e-05
2017 | 2016-11-07 | C | 2 | 0.000912 | 6.0021e-06
2017 | 2016-11-08 | C | 624 | 0.10538 | 0.0018726
2017 | 2016-11-08 | C | 117 | 0.098732 | 0.00045015
2017 | 2016-11-09 | C | 1 | 0.000264 | 3.0009e-06
2017 | 2016-11-09 | C | 74 | 0.013796 | 0.00022207
2017 | 2016-11-09 | C | 5 | 0.002232 | 1.5005e-05
2017 | 2016-11-25 | B | 5 | 0.003264 | 1.5002e-05
2017 | 2016-11-09 | C | 3 | 0.004031 | 9.0029e-06
2017 | 2016-11-09 | C | 298 | 0.045908 | 0.00089429
2017 | 2016-11-29 | B | 3 | 0.003753 | 9.0004e-06
2017 | 2016-11-09 | B | 67 | 0.064944 | 0.00020107
2017 | 2016-11-21 | B | 38 | 0.044353 | 0.00011402
2017 | 2016-12-05 | B | 6 | 0.000395 | 1.7999e-05
2017 | 2016-12-05 | B | 7 | 0.001196 | 2.0999e-05
2017 | 2016-12-05 | B | 1 | 0.000788 | 2.9998e-06
2017 | 2016-12-05 | B | 6 | 0.000935 | 1.7999e-05
2017 | 2016-12-06 | B | 9 | 0.000458 | 2.6998e-05
2017 | 2016-11-15 | B | 2 | 0.000294 | 6.0014e-06
2017 | 2016-12-06 | B | 6 | 0.000665 | 1.7999e-05
2017 | 2016-12-06 | B | 4 | 0.000503 | 1.1999e-05
2017 | 2016-12-06 | B | 8 | 0.000287 | 2.3999e-05
2017 | 2016-12-07 | B | 4 | 0.000323 | 1.1999e-05
2017 | 2016-12-07 | B | 3 | 0.000332 | 8.9993e-06
2017 | 2016-11-30 | B | 69 | 0.07949 | 0.00020701
2017 | 2016-12-07 | B | 7 | 0.000776 | 2.0998e-05
2017 | 2016-12-12 | B | 4 | 0.001523 | 1.1998e-05
2017 | 2016-11-30 | B | 1 | 0.00072 | 3.0001e-06
2017 | 2016-12-12 | B | 1 | 2.3e-05 | 2.9995e-06
2017 | 2016-12-12 | B | 5 | 0.000554 | 1.4998e-05
2017 | 2016-12-01 | B | 19 | 0.028272 | 5.7001e-05
2017 | 2016-11-09 | C | 411 | 0.11142 | 0.0012334
2017 | 2016-11-09 | C | 15 | 0.005224 | 4.5015e-05
2017 | 2016-11-09 | C | 211 | 0.022542 | 0.00063321
2017 | 2016-11-10 | C | 12 | 0.004321 | 3.6011e-05
2017 | 2016-11-10 | C | 66 | 0.002772 | 0.00019806
2017 | 2016-11-10 | C | 1 | 0.000215 | 3.0009e-06
2017 | 2016-11-10 | C | 316 | 0.10972 | 0.0009483
2017 | 2016-12-13 | B | 4 | 0.003095 | 1.1998e-05
2017 | 2016-12-13 | B | 1 | 8e-05 | 2.9995e-06
2017 | 2016-12-13 | B | 5 | 0.000254 | 1.4998e-05
2017 | 2016-11-10 | C | 1214 | 0.42758 | 0.0036431
2017 | 2016-11-10 | C | 1 | 0.000147 | 3.0009e-06
2017 | 2016-11-10 | C | 4 | 0.003362 | 1.2004e-05
2017 | 2016-11-27 | B | 2 | 0.001968 | 6.0004e-06
2017 | 2016-12-13 | B | 7 | 0.001091 | 2.0997e-05
2017 | 2016-11-10 | C | 1 | 0.00025 | 3.0009e-06
2017 | 2016-12-13 | B | 6 | 0.002195 | 1.7997e-05
2017 | 2016-11-10 | C | 12 | 0.003637 | 3.6011e-05
2017 | 2016-12-14 | B | 4 | 0.000263 | 1.1998e-05
2017 | 2016-12-14 | B | 3 | 0.000422 | 8.9984e-06
2017 | 2016-12-14 | B | 5 | 0.000779 | 1.4997e-05
2017 | 2016-12-15 | B | 4 | 0.000503 | 1.1998e-05
2017 | 2016-12-15 | B | 5 | 0.000779 | 1.4997e-05
2017 | 2016-12-16 | B | 4 | 0.002387 | 1.1997e-05
2017 | 2016-12-01 | B | 26 | 0.013806 | 7.8001e-05
2017 | 2016-12-16 | B | 2 | 0.000221 | 5.9987e-06
2017 | 2016-11-10 | C | 51 | 0.021579 | 0.00015305
2017 | 2016-12-16 | B | 17 | 0.001223 | 5.099e-05
2017 | 2016-12-19 | B | 7 | 0.005647 | 2.0995e-05
2017 | 2016-11-10 | C | 241 | 0.042665 | 0.0010623
2017 | 2016-11-10 | C | 1 | 0.000707 | 3.0009e-06
2017 | 2016-12-01 | B | 10 | 0.01095 | 3e-05
2017 | 2016-11-10 | C | 485 | 0.024199 | 0.0014555
2017 | 2016-11-10 | C | 1 | 0.000204 | 3.0009e-06
2017 | 2016-11-11 | C | 10 | 0.003162 | 3.0009e-05
2017 | 2016-11-11 | C | 2 | 0.000256 | 6.0018e-06
2017 | 2016-12-07 | B | 20 | 0.019972 | 5.9996e-05
2017 | 2016-12-01 | B | 11 | 0.011779 | 3.3001e-05
2017 | 2016-12-02 | B | 3 | 0.001179 | 9e-06
2017 | 2016-12-02 | B | 1 | 0.000885 | 3e-06
2017 | 2016-11-29 | B | 40 | 0.038865 | 0.00012001
2017 | 2016-12-02 | B | 26 | 0.03042 | 7.8e-05
2017 | 2016-11-23 | B | 124 | 0 | 0.00018002
2017 | 2016-12-05 | B | 1 | 0.001136 | 2.9998e-06
2017 | 2016-12-02 | B | 4 | 0.003204 | 1.2e-05
2017 | 2016-12-02 | B | 54 | 0.018954 | 0.000162
2017 | 2016-11-16 | B | 3 | 0.001269 | 9.002e-06
2017 | 2016-11-23 | B | 35 | 0.039485 | 0.00010501
2017 | 2016-11-19 | B | 45 | 0.050094 | 0.00013503
2017 | 2016-11-11 | C | 168 | 0.072325 | 0.00064219
2017 | 2016-11-11 | C | 240 | 0.002076 | 0.00072022
2017 | 2016-11-12 | C | 7 | 0.00315 | 2.1006e-05
2017 | 2016-12-01 | B | 20 | 0.019483 | 6.0001e-05
2017 | 2016-11-12 | C | 6 | 0.002682 | 1.8005e-05
2017 | 2016-11-12 | C | 5 | 0.000649 | 1.5004e-05
2017 | 2016-11-12 | C | 5 | 0.00051 | 1.5004e-05
2017 | 2016-11-12 | C | 4 | 0.009783 | 1.2003e-05
2017 | 2016-11-12 | C | 242 | 0.076141 | 0.00078923
2017 | 2016-11-12 | C | 299 | 0.062391 | 0.0024097
2017 | 2016-11-12 | C | 768 | 0.70677 | 0.0023047
2017 | 2016-11-13 | C | 172 | 0.094982 | 0.00092125
2017 | 2016-11-13 | C | 53 | 0.046339 | 0.00015904
2017 | 2016-11-13 | C | 21303 | 7.935 | 0.063927
2017 | 2016-11-13 | C | 1 | 0.000167 | 3.0008e-06
2017 | 2016-11-14 | C | 44 | 0 | 0.00013203
2017 | 2016-11-14 | C | 586 | 0 | 0.0017585
2017 | 2016-11-14 | C | 253 | 0.25597 | 0.0020165
2017 | 2016-11-14 | C | 228 | 0 | 0.00068418
2017 | 2016-11-14 | C | 72 | 0.06424 | 0.00021606
2017 | 2016-11-14 | C | 91 | 0.096607 | 0.00027307
2017 | 2016-11-14 | C | 693 | 0.67285 | 0.0020795
2017 | 2016-11-14 | C | 200 | 0.11373 | 0.00060016
2017 | 2016-11-14 | C | 212 | 0.059629 | 0.00063616
2017 | 2016-11-14 | C | 841 | 0.18226 | 0.0025237
2017 | 2016-11-14 | C | 2515 | 0.73596 | 0.007547
2017 | 2016-11-14 | C | 386 | 0.13639 | 0.0011583
2017 | 2016-11-14 | C | 861 | 0.5905 | 0.0025837
2017 | 2016-11-14 | C | 791 | 0.22217 | 0.0023736
2017 | 2016-11-14 | C | 2678 | 1.5068 | 0.0087893
2017 | 2016-11-14 | C | 1935 | 1.2449 | 0.0058065
2017 | 2016-11-14 | C | 602 | 0.38305 | 0.0018065
2017 | 2016-11-14 | C | 257 | 0.3486 | 0.0007712
2017 | 2016-11-14 | C | 1413 | 1.3336 | 0.0034479
2017 | 2016-11-14 | C | 219 | 0.11949 | 0.00065717
2017 | 2016-11-14 | C | 582 | 0.17572 | 0.0017465
2017 | 2016-11-14 | C | 461 | 0.25105 | 0.00097225
2017 | 2016-11-14 | C | 316 | 0.2208 | 0.00094825
2017 | 2016-11-14 | C | 716 | 0.49746 | 0.0021486
2017 | 2016-11-14 | C | 48 | 0.013938 | 0.00014404
2017 | 2016-11-14 | C | 2546 | 1.0635 | 0.00764
2017 | 2016-11-14 | C | 4 | 0.003266 | 1.2003e-05
2017 | 2016-11-14 | C | 255 | 0.090816 | 0.0007652
2017 | 2016-11-14 | C | 249 | 0.3085 | 0.00096025
2017 | 2016-11-14 | C | 566 | 0.64263 | 0.0064067
2017 | 2016-11-14 | C | 340 | 0.45586 | 0.0010203
2017 | 2016-11-14 | C | 847 | 0.43683 | 0.0025417
2017 | 2016-11-14 | C | 1529 | 1.0257 | 0.0045882
2017 | 2016-11-14 | C | 1173 | 1.0419 | 0.0035199
2017 | 2016-11-14 | C | 185 | 0.42861 | 0.00055514
2017 | 2016-11-14 | C | 1 | 0.000761 | 3.0007e-06
2017 | 2016-11-14 | C | 2244 | 0.86509 | 0.0067337
2017 | 2016-11-14 | C | 4075 | 0.95583 | 0.012228
2017 | 2016-11-14 | C | 219 | 0.17108 | 0.00065717
2017 | 2016-11-14 | C | 249 | 0.29875 | 0.00080421
2017 | 2016-11-14 | C | 1280 | 0.3953 | 0.003841
2017 | 2016-11-14 | C | 64 | 0.000217 | 0.00019205
2017 | 2016-11-14 | C | 244 | 0.25993 | 0.0007802
2017 | 2016-11-14 | C | 1 | 0.000793 | 3.0007e-06
2017 | 2016-11-14 | C | 4 | 0.002249 | 1.2003e-05
2017 | 2016-11-14 | C | 330 | 0.14188 | 0.00099026
2017 | 2016-11-14 | C | 954 | 0.081011 | 0.00097225
2017 | 2016-11-14 | C | 129 | 0.062877 | 0.0003871
2017 | 2016-11-14 | C | 13 | 0.011475 | 3.901e-05
2017 | 2016-11-14 | C | 133 | 0.015964 | 0.0003991
2017 | 2016-11-14 | C | 14 | 0.014878 | 4.2011e-05
2017 | 2016-11-14 | C | 73 | 0.058108 | 0.00021906
2017 | 2016-11-14 | C | 68 | 0.11856 | 0.00020405
2017 | 2016-11-14 | C | 86 | 0.094082 | 0.00025807
2017 | 2016-11-14 | C | 12 | 0.075383 | 3.6009e-05
2017 | 2016-11-14 | C | 33 | 0.028355 | 9.9026e-05
2017 | 2016-11-14 | C | 73 | 0.10086 | 0.00021906
2017 | 2016-11-14 | C | 4 | 0.033102 | 1.2003e-05
2017 | 2016-11-14 | C | 296 | 0.054788 | 0.00088823
2017 | 2016-11-14 | C | 3 | 0.001348 | 9.0023e-06
2017 | 2016-11-14 | C | 25 | 0.042908 | 7.5019e-05
2017 | 2016-11-14 | C | 225 | 0.32454 | 0.0017675
2017 | 2016-11-14 | C | 1 | 0.000791 | 3.0007e-06
2017 | 2016-11-14 | C | 95 | 0.077521 | 0.00028507
2017 | 2016-11-14 | C | 14 | 0.005912 | 4.2011e-05
2017 | 2016-11-14 | C | 23 | 0.028122 | 6.9018e-05
2017 | 2016-11-14 | C | 4 | 0.006517 | 1.2003e-05
2017 | 2016-11-14 | C | 1 | 0.004905 | 3.0007e-06
2017 | 2016-11-14 | C | 8 | 0.051228 | 2.4006e-05
2017 | 2016-11-14 | C | 3 | 0.003395 | 9.0023e-06
2017 | 2016-11-29 | B | 100 | 0.0132 | 0.00060003
2017 | 2016-11-14 | C | 105 | 0.010397 | 0.00031508
2017 | 2016-11-14 | C | 17 | 0.018354 | 5.1013e-05
2017 | 2016-11-14 | C | 43 | 0.035686 | 0.00012903
2017 | 2016-11-14 | C | 7 | 0.004297 | 2.1005e-05
2017 | 2016-11-14 | C | 9 | 0.001404 | 2.7007e-05
2017 | 2016-11-14 | C | 7 | 0.006631 | 2.1005e-05
2017 | 2016-11-14 | C | 18 | 0.00575 | 5.4014e-05
2017 | 2016-11-14 | C | 48 | 0.21448 | 0.00014404
2017 | 2016-11-14 | C | 1 | 0.002219 | 3.0007e-06
2017 | 2016-11-14 | C | 2 | 0.008848 | 6.0015e-06
2017 | 2016-11-14 | C | 1 | 0.000879 | 3.0007e-06
2017 | 2016-11-14 | C | 4 | 0.006211 | 1.2003e-05
2017 | 2016-11-14 | C | 21 | 0.10694 | 6.3016e-05
2017 | 2016-11-14 | C | 1044 | 0.30895 | 0.0031328
2017 | 2016-11-14 | C | 455 | 0.13498 | 0.0014104
2017 | 2016-11-14 | C | 1 | 0.000339 | 3.0007e-06
2017 | 2016-11-14 | C | 9 | 0.005912 | 2.7007e-05
2017 | 2016-11-14 | C | 2 | 0.004909 | 6.0015e-06
2017 | 2016-11-14 | C | 1528 | 0.46606 | 0.0058515
2017 | 2016-11-14 | C | 1 | 0.000196 | 3.0007e-06
2017 | 2016-11-30 | B | 2 | 0.002777 | 6.0002e-06
2017 | 2016-11-14 | C | 297 | 0.093363 | 0.00089123
2017 | 2016-11-14 | C | 2 | 0.000132 | 6.0015e-06
2017 | 2016-11-14 | C | 1 | 0.004405 | 3.0007e-06
2017 | 2016-11-14 | C | 1 | 0.001086 | 3.0007e-06
2017 | 2016-12-02 | B | 35 | 0.00651 | 0.000105
2017 | 2016-11-14 | C | 6 | 0.001987 | 1.8005e-05
2017 | 2016-11-14 | C | 1 | 0.004055 | 3.0007e-06
2017 | 2016-11-14 | C | 282 | 0.10688 | 0.00084622
2017 | 2016-11-14 | C | 19 | 0.013807 | 5.7015e-05
2017 | 2016-11-14 | C | 5 | 0.001388 | 1.5004e-05
2017 | 2016-11-14 | C | 2 | 0.0007 | 6.0015e-06
2017 | 2016-11-16 | C | 16 | 0.004897 | 4.8011e-05
2017 | 2016-11-14 | C | 4 | 0.008302 | 3.0007e-06
2017 | 2016-11-14 | C | 42 | 0.018934 | 0.00012603
2017 | 2016-11-14 | C | 17 | 0.042143 | 5.1013e-05
2017 | 2016-12-01 | B | 5 | 0.003378 | 1.5e-05
2017 | 2016-11-14 | C | 2 | 0.01245 | 6.0015e-06
2017 | 2016-11-14 | C | 56 | 0.000787 | 0.00016804
2017 | 2016-11-14 | C | 94 | 0.030106 | 0.00028207
2017 | 2016-11-15 | C | 18 | 0.003348 | 5.4013e-05
2017 | 2016-12-06 | B | 29 | 0.007133 | 8.6995e-05
2017 | 2016-11-14 | C | 5 | 0.007395 | 1.5004e-05
2017 | 2016-11-14 | C | 1 | 0.000248 | 3.0007e-06
2017 | 2016-11-14 | C | 1 | 0.000743 | 3.0007e-06
2017 | 2016-12-06 | B | 33 | 0.032371 | 9.8995e-05
2017 | 2016-11-14 | C | 2 | 0.00317 | 6.0015e-06
2017 | 2016-11-14 | C | 1 | 0.003668 | 3.0007e-06
2017 | 2016-11-14 | C | 1 | 0.008197 | 3.0007e-06
2017 | 2016-11-14 | C | 1 | 0.005252 | 3.0007e-06
2017 | 2016-11-14 | C | 1 | 0.00861 | 3.0007e-06
2017 | 2016-11-14 | C | 1 | 0.009233 | 3.0007e-06
2017 | 2016-11-14 | C | 236 | 0.070296 | 0.00070818
2017 | 2016-11-14 | C | 1 | 0.004778 | 3.0007e-06
2017 | 2016-11-14 | C | 82 | 0.005815 | 0.00024606
2017 | 2016-11-14 | C | 24 | 0.051254 | 7.2019e-05
2017 | 2016-11-14 | C | 512 | 0.32817 | 0.0031628
2017 | 2016-11-14 | C | 241 | 0.37442 | 0.0011703
2017 | 2016-11-14 | C | 596 | 0.78341 | 0.0024546
2017 | 2016-11-14 | C | 33 | 0.037892 | 9.9026e-05
2017 | 2016-11-14 | C | 9 | 0.01253 | 2.7007e-05
2017 | 2016-11-14 | C | 298 | 0.50535 | 0.0012363
2017 | 2016-11-14 | C | 307 | 0.44171 | 0.00092124
2017 | 2016-11-14 | C | 417 | 0.96377 | 0.0024246
2017 | 2016-11-14 | C | 305 | 0.073901 | 0.00091524
2017 | 2016-11-14 | C | 1 | 0.000143 | 3.0007e-06
2017 | 2016-11-14 | C | 334 | 0.27512 | 0.0010023
2017 | 2016-11-14 | C | 535 | 0.16161 | 0.0016054
2017 | 2016-11-14 | C | 249 | 0.14947 | 0.0007802
2017 | 2016-11-14 | C | 7 | 0.021358 | 2.1005e-05
2017 | 2016-11-17 | C | 1 | 0.000132 | 3.0006e-06
2017 | 2016-11-14 | C | 100 | 0.022505 | 0.00030008
2017 | 2016-11-14 | C | 91 | 0.10902 | 0.00044111
2017 | 2016-11-14 | C | 2 | 0.007076 | 6.0015e-06
2017 | 2016-11-14 | C | 152 | 0.11031 | 0.00045612
2017 | 2016-11-14 | C | 2 | 0.023189 | 6.0015e-06
2017 | 2016-11-14 | C | 197 | 0.52431 | 0.00094524
2017 | 2016-11-14 | C | 275 | 0.14038 | 0.0017645
2017 | 2016-11-14 | C | 214 | 0.19819 | 0.0003961
2017 | 2016-11-14 | C | 98 | 0.24198 | 0.00057015
2017 | 2016-11-15 | C | 412 | 0.3982 | 0.0014824
2017 | 2016-11-15 | C | 376 | 0.50875 | 0.0013743
2017 | 2016-11-15 | C | 234 | 0.19408 | 0.00070217
2017 | 2016-11-15 | C | 1730 | 2.092 | 0.0051913
2017 | 2016-11-15 | C | 26 | 0.1893 | 7.8019e-05
2017 | 2016-11-15 | C | 66 | 0.14005 | 0.00019805
2017 | 2016-11-15 | C | 82 | 0.30904 | 0.00024906
2017 | 2016-11-15 | C | 61 | 0.025482 | 0.00018305
2017 | 2016-11-15 | C | 440 | 0.16292 | 0.0013203
2017 | 2016-11-15 | C | 4 | 0.023121 | 1.2003e-05
2017 | 2016-11-15 | C | 84 | 0 | 0.00025206
2017 | 2016-11-15 | C | 10 | 0.0119 | 3.0007e-05
2017 | 2016-11-15 | C | 27 | 0.057325 | 8.102e-05
2017 | 2016-11-15 | C | 5 | 0.030022 | 1.5004e-05
2017 | 2016-11-14 | C | 2 | 0.004201 | 6.0015e-06
2017 | 2016-11-17 | C | 3 | 6.3e-05 | 9.0019e-06
2017 | 2016-11-15 | C | 5 | 0.031325 | 1.5004e-05
2017 | 2016-11-15 | C | 191 | 0.2439 | 0.00077419
2017 | 2016-11-14 | C | 102 | 0.01867 | 0.00030608
2017 | 2016-12-07 | B | 7 | 0.002498 | 2.0998e-05
2017 | 2016-11-15 | C | 8 | 0.00959 | 2.4006e-05
2017 | 2016-12-01 | B | 25 | 0.018224 | 7.5001e-05
2017 | 2016-11-15 | C | 5 | 0.040459 | 1.5004e-05
2017 | 2016-12-08 | B | 4 | 0.000935 | 1.1999e-05
2017 | 2016-11-15 | C | 1 | 0.007154 | 3.0007e-06
2017 | 2016-11-15 | C | 52 | 0 | 0.00015604
2017 | 2016-11-16 | C | 1 | 0.000291 | 3.0006e-06
2017 | 2016-12-01 | B | 65 | 0.059281 | 0.000195
2017 | 2016-11-15 | C | 62 | 0.023658 | 0.00018605
2017 | 2016-11-15 | C | 2 | 0.011053 | 6.0014e-06
2017 | 2016-11-15 | C | 3 | 0.000549 | 9.0022e-06
2017 | 2016-11-15 | C | 1 | 0.003203 | 3.0007e-06
2017 | 2016-11-15 | C | 190 | 0.24819 | 0.00057014
2017 | 2016-11-19 | B | 46 | 0.01403 | 0.00013803
2017 | 2016-11-15 | C | 4 | 0.019154 | 1.2003e-05
2017 | 2016-11-15 | C | 1 | 0.003089 | 3.0007e-06
2017 | 2016-12-09 | B | 174 | 0.06419 | 0.00074693
2017 | 2016-11-15 | C | 6 | 0.001782 | 1.8004e-05
2017 | 2016-11-15 | C | 3 | 0.014758 | 9.0022e-06
2017 | 2016-12-13 | B | 40 | 0.014877 | 0.00011998
2017 | 2016-11-15 | C | 1 | 0.000862 | 3.0007e-06
2017 | 2016-11-15 | C | 1 | 0.002069 | 3.0007e-06
2017 | 2016-11-15 | C | 1 | 0 | 3.0007e-06
2017 | 2016-11-15 | C | 2 | 3.1e-05 | 6.0014e-06
2017 | 2016-11-15 | C | 4 | 0.004067 | 1.2003e-05
2017 | 2016-12-01 | B | 79 | 0.08935 | 0.000237
2017 | 2016-12-05 | B | 1 | 0.000281 | 2.9998e-06
2017 | 2016-11-15 | C | 1 | 0.001189 | 3.0007e-06
2017 | 2016-12-04 | B | 18 | 0.019871 | 5.3999e-05
2017 | 2016-12-05 | B | 5 | 0.00633 | 1.4999e-05
2017 | 2016-12-05 | B | 4 | 0.003635 | 1.1999e-05
2017 | 2016-11-15 | C | 572 | 0.13155 | 0.0017164
2017 | 2016-12-08 | B | 5 | 0.003059 | 1.4999e-05
2017 | 2016-12-08 | B | 39 | 0.03884 | 0.00011699
2017 | 2016-12-05 | B | 47 | 0.02707 | 0.00014099
2017 | 2016-12-08 | B | 138 | 0.11084 | 0.00041397
2017 | 2016-12-05 | B | 15 | 0.005174 | 4.4998e-05
2017 | 2016-12-03 | B | 7 | 0.002351 | 2.1e-05
2017 | 2016-11-23 | B | 128 | 0.18511 | 0.00038405
2017 | 2016-11-15 | C | 5 | 0 | 1.5004e-05
2017 | 2016-11-15 | C | 149 | 0.15959 | 0.00044711
2017 | 2016-11-15 | C | 1 | 0.003383 | 3.0007e-06
2017 | 2016-11-15 | C | 129 | 0.031588 | 0.0003871
2017 | 2016-11-15 | C | 25 | 0.011994 | 7.5019e-05
2017 | 2016-11-15 | C | 36 | 0.012098 | 0.00010803
2017 | 2016-11-15 | C | 234 | 0.040676 | 0.00070217
2017 | 2016-11-15 | C | 3 | 0.00056 | 9.0022e-06
2017 | 2016-11-15 | C | 113 | 0.23163 | 0.00033908
2017 | 2016-11-15 | C | 12 | 0.003685 | 3.6009e-05
2017 | 2016-11-15 | C | 1 | 0.004363 | 3.0007e-06
2017 | 2016-11-15 | C | 453 | 0.042219 | 0.0010893
2017 | 2016-11-16 | C | 1 | 0.00199 | 3.0006e-06
2017 | 2016-11-16 | C | 9 | 0.005802 | 2.7006e-05
2017 | 2016-11-15 | C | 47 | 0.025668 | 0.00014103
2017 | 2016-11-16 | C | 2 | 0.000929 | 6.0013e-06
2017 | 2016-11-16 | C | 4 | 0.011726 | 1.2003e-05
2017 | 2016-11-16 | C | 1 | 0.00049 | 3.0006e-06
2017 | 2016-11-16 | C | 20 | 0.002706 | 6.0014e-05
2017 | 2016-11-16 | C | 2 | 0.000766 | 6.0013e-06
2017 | 2016-11-30 | B | 14 | 0.01449 | 4.2001e-05
2017 | 2016-11-14 | C | 1 | 0.006691 | 3.0007e-06
2017 | 2016-12-06 | B | 5 | 0.005054 | 1.4999e-05
2017 | 2016-12-02 | B | 3 | 0.003393 | 9e-06
2017 | 2016-11-16 | C | 4 | 0.003602 | 1.2003e-05
2017 | 2016-12-06 | B | 2 | 0.001739 | 5.9996e-06
2017 | 2016-11-16 | C | 67 | 0.034668 | 0.00020105
2017 | 2016-11-16 | C | 1 | 0.001622 | 3.0006e-06
2017 | 2016-11-16 | C | 2 | 0 | 6.0013e-06
2017 | 2016-12-03 | B | 42 | 0.033011 | 0.000126
2017 | 2016-12-12 | B | 1 | 0.000416 | 2.9995e-06
2017 | 2016-12-20 | B | 14 | 0.010875 | 4.1989e-05
2017 | 2016-11-16 | C | 31 | 0 | 9.3021e-05
2017 | 2016-11-16 | C | 301 | 0.034144 | 0.00090321
2017 | 2016-11-16 | C | 1 | 0.000857 | 3.0006e-06
2017 | 2016-11-16 | C | 439 | 0.085508 | 0.0013173
2017 | 2016-11-14 | C | 2 | 0.000312 | 6.0015e-06
2017 | 2016-11-16 | C | 1 | 0.00049 | 3.0006e-06
2017 | 2016-11-16 | C | 5 | 0.018259 | 1.5003e-05
2017 | 2016-12-07 | B | 17 | 0.017419 | 5.0996e-05
2017 | 2016-12-13 | B | 2 | 0.000311 | 5.999e-06
2017 | 2016-11-16 | C | 79 | 0.040219 | 0.00023705
2017 | 2016-12-07 | B | 45 | 0.048326 | 0.00013499
2017 | 2016-12-05 | B | 7 | 0.006089 | 2.0999e-05
2017 | 2016-11-16 | C | 91 | 0.02387 | 0.00027306
2017 | 2016-12-05 | B | 63 | 0.074085 | 0.00018899
2017 | 2016-11-16 | C | 97 | 0.031198 | 0.00029107
2017 | 2016-11-16 | C | 2 | 0.000948 | 6.0013e-06
2017 | 2016-12-07 | B | 12 | 0.010957 | 3.5998e-05
2017 | 2016-12-06 | B | 4 | 0.004307 | 1.1999e-05
2017 | 2016-12-07 | B | 6 | 0.006335 | 1.7999e-05
2017 | 2016-12-02 | B | 47 | 0.050807 | 0.000141
2017 | 2016-12-08 | B | 9 | 0.006506 | 2.6998e-05
2017 | 2016-12-09 | B | 7 | 0.00611 | 2.0998e-05
2017 | 2016-11-17 | B | 12 | 0.002628 | 3.6008e-05
2017 | 2016-12-08 | B | 6 | 0.006155 | 1.7999e-05
2017 | 2016-11-16 | C | 4 | 0.001209 | 1.2003e-05
2017 | 2016-11-15 | C | 11 | 0.066289 | 3.3008e-05
2017 | 2016-11-17 | C | 2 | 0.00117 | 6.0013e-06
2017 | 2016-11-16 | C | 5 | 0.001218 | 1.5003e-05
2017 | 2016-11-16 | C | 1 | 0.000546 | 3.0006e-06
2017 | 2016-11-16 | C | 501 | 0.047708 | 0.0022685
2017 | 2016-11-16 | C | 4 | 0.013379 | 1.2003e-05
2017 | 2016-11-16 | C | 323 | 0.21555 | 0.00096922
2017 | 2016-11-16 | C | 2 | 0.001251 | 6.0013e-06
2017 | 2016-11-16 | C | 91 | 0.073468 | 0.00018904
2017 | 2016-11-16 | C | 2 | 0.000318 | 6.0013e-06
2017 | 2016-11-16 | C | 167 | 0.13938 | 0.00078918
2017 | 2016-11-16 | C | 495 | 0.28528 | 0.0014853
2017 | 2016-11-17 | C | 25 | 0.003309 | 7.5016e-05
2017 | 2016-11-17 | C | 26 | 0.014596 | 7.8017e-05
2017 | 2016-11-17 | C | 209 | 0.037553 | 0.00062714
2017 | 2016-11-17 | C | 21 | 0.010152 | 6.3014e-05
2017 | 2016-11-17 | C | 31 | 0.012343 | 9.302e-05
2017 | 2016-12-09 | B | 36 | 0.011554 | 0.00010799
2017 | 2016-11-17 | C | 1 | 0.000589 | 3.0006e-06
2017 | 2016-12-06 | B | 115 | 0.11764 | 0.00034498
2017 | 2016-11-16 | C | 8 | 0.01289 | 2.4005e-05
2017 | 2016-11-17 | C | 34 | 0.009794 | 0.00010202
2017 | 2016-11-17 | C | 3 | 0.014412 | 9.0019e-06
2017 | 2016-11-17 | C | 284 | 0.032645 | 0.00085219
2017 | 2016-12-06 | B | 54 | 0.009233 | 0.00016199
2017 | 2016-12-08 | B | 49 | 0 | 0.00014699
2017 | 2016-12-06 | B | 5 | 0.007559 | 1.4999e-05
2017 | 2016-12-07 | B | 5 | 0.006549 | 1.4999e-05
2017 | 2016-12-01 | B | 1 | 0.000606 | 3e-06
2017 | 2016-12-05 | B | 1 | 0.000755 | 2.9998e-06
2017 | 2016-11-17 | C | 8 | 0.002556 | 2.4005e-05
2017 | 2016-12-06 | B | 79 | 0.082234 | 0.00023699
2017 | 2016-11-17 | C | 3 | 0.000153 | 9.0019e-06
2017 | 2016-12-02 | B | 12 | 0.017712 | 3.6e-05
2017 | 2016-11-17 | C | 23 | 0.005314 | 6.9015e-05
2017 | 2016-12-09 | B | 7 | 0.002876 | 2.0998e-05
2017 | 2016-12-09 | B | 3 | 0.003257 | 8.9991e-06
2017 | 2016-12-09 | B | 25 | 0.009953 | 7.4993e-05
2017 | 2016-12-08 | B | 2 | 0 | 5.9995e-06
2017 | 2016-12-08 | B | 3 | 0.000926 | 8.9992e-06
2017 | 2016-12-09 | B | 1 | 0.00053 | 2.9997e-06
2017 | 2016-12-06 | B | 37 | 0.0525 | 0.00011099
2017 | 2016-11-17 | C | 29 | 0.004616 | 8.7019e-05
2017 | 2016-11-17 | C | 1 | 0.000375 | 3.0006e-06
2017 | 2016-11-17 | C | 5 | 0.000225 | 1.5003e-05
2017 | 2016-11-17 | C | 8 | 0.001665 | 2.4005e-05
2017 | 2016-11-17 | C | 307 | 0.066275 | 0.0009242
2017 | 2016-11-17 | C | 3 | 0.001507 | 9.0019e-06
2017 | 2016-11-17 | C | 4 | 0.011198 | 1.2003e-05
2017 | 2016-11-17 | C | 1 | 0.000178 | 3.0006e-06
2017 | 2016-11-17 | C | 1939 | 0.3662 | 0.0058183
2017 | 2016-11-18 | C | 43 | 0.009335 | 0.00012903
2017 | 2016-11-18 | C | 1355 | 0.1853 | 0.0040658
2017 | 2016-12-14 | B | 2 | 0.001181 | 5.9989e-06
2017 | 2016-12-15 | B | 2 | 0.001241 | 5.9988e-06
2017 | 2016-11-18 | C | 1 | 0.00047 | 3.0006e-06
2017 | 2016-12-08 | B | 57 | 0.026844 | 0.00017099
2017 | 2016-12-08 | B | 4 | 0.004643 | 1.1999e-05
2017 | 2016-12-05 | B | 27 | 0.015065 | 8.0997e-05
2017 | 2016-11-18 | C | 25 | 0.010202 | 7.5015e-05
2017 | 2016-11-18 | C | 13 | 0.001702 | 3.9008e-05
2017 | 2016-12-15 | B | 5 | 0.003764 | 1.4997e-05
2017 | 2016-11-18 | C | 54 | 0.023008 | 0.00016203
2017 | 2016-12-19 | B | 108 | 0.069318 | 0.00032392
2017 | 2016-12-07 | B | 3 | 0.002861 | 8.9993e-06
2017 | 2016-12-11 | B | 29 | 0.006002 | 8.6989e-05
2017 | 2016-12-15 | B | 12 | 0.007963 | 3.5993e-05
2017 | 2016-12-12 | B | 86 | 0.10525 | 0.00025796
2017 | 2016-11-19 | B | 13 | 0.009283 | 3.9007e-05
2017 | 2016-12-11 | B | 30 | 0.002249 | 8.9988e-05
2017 | 2016-12-07 | B | 7 | 0.004829 | 2.0998e-05
2017 | 2016-11-18 | C | 367 | 0.022156 | 0.0011012
2017 | 2016-11-18 | C | 1 | 0.002346 | 3.0006e-06
2017 | 2016-11-18 | C | 15 | 0.001665 | 4.5009e-05
2017 | 2016-11-18 | C | 257 | 0.12309 | 0.00085818
2017 | 2016-11-19 | C | 1 | 0.000182 | 3.0005e-06
2017 | 2016-11-19 | C | 1047 | 0.23001 | 0.0047139
2017 | 2016-11-19 | C | 19 | 0.00597 | 5.7011e-05
2017 | 2016-11-19 | C | 2334 | 0.23611 | 0.0033096
2017 | 2016-11-19 | C | 3 | 0.00067 | 9.0017e-06
2017 | 2016-11-19 | C | 237 | 0.051969 | 0.00071114
2017 | 2016-11-19 | C | 1528 | 0.2482 | 0.0069823
2017 | 2016-11-19 | C | 62 | 0.014167 | 0.00018604
2017 | 2016-11-20 | C | 589 | 0.24157 | 0.0039907
2017 | 2016-11-20 | C | 41 | 0.004166 | 0.00012302
2017 | 2016-11-20 | C | 190 | 0.066483 | 0.0005701
2017 | 2016-11-20 | C | 12 | 0.003132 | 3.6006e-05
2017 | 2016-11-20 | C | 1 | 0.004431 | 3.0005e-06
2017 | 2016-11-20 | C | 15 | 0.004412 | 4.5008e-05
2017 | 2016-11-20 | C | 2 | 0.001057 | 6.001e-06
2017 | 2016-11-20 | C | 424 | 0.077542 | 0.0018243
2017 | 2016-11-20 | C | 27 | 0.009947 | 8.1014e-05
2017 | 2016-11-20 | C | 17 | 0.003561 | 5.1009e-05
2017 | 2016-11-21 | C | 1528 | 0.16825 | 0.0045847
2017 | 2016-11-21 | C | 27 | 0.012844 | 8.1013e-05
2017 | 2016-12-01 | B | 95 | 0.04845 | 0.00028501
2017 | 2016-11-21 | C | 27 | 0.019675 | 8.1013e-05
2017 | 2016-11-21 | C | 1 | 0.000667 | 3.0004e-06
2017 | 2016-12-05 | B | 15 | 0.013859 | 4.4998e-05
2017 | 2016-12-08 | B | 25 | 0.008774 | 7.4994e-05
2017 | 2016-12-13 | B | 62 | 0.06323 | 0.00018597
2017 | 2016-11-21 | C | 7 | 0.000651 | 2.1003e-05
2017 | 2016-11-21 | C | 20 | 0.006085 | 6.001e-05
2017 | 2016-11-21 | C | 1 | 0.000339 | 3.0004e-06
2017 | 2016-11-21 | C | 15 | 0.001305 | 4.5007e-05
2017 | 2016-11-22 | C | 1130 | 0.41908 | 0.0033905
2017 | 2016-11-22 | C | 30 | 0.008821 | 9.0013e-05
2017 | 2016-11-16 | C | 6 | 0.002106 | 1.8004e-05
2017 | 2016-12-01 | B | 12 | 0.013752 | 3.6001e-05
2017 | 2016-11-22 | C | 41 | 0.028663 | 0.00012302
2017 | 2016-11-22 | C | 228 | 0.033294 | 0.0006841
2017 | 2016-11-23 | C | 6 | 0.001476 | 1.8002e-05
2017 | 2016-12-08 | B | 4 | 0.000959 | 1.1999e-05
2017 | 2016-12-07 | B | 15 | 0.007216 | 4.4997e-05
2017 | 2016-12-08 | B | 7 | 0.003947 | 2.0998e-05
2017 | 2016-11-23 | C | 2 | 0.001436 | 6.0008e-06
2017 | 2016-12-09 | B | 8 | 0.001727 | 2.3998e-05
2017 | 2016-12-08 | B | 92 | 0.013522 | 0.00027598
2017 | 2016-11-23 | C | 186 | 0.058111 | 0.00055808
2017 | 2016-12-07 | B | 12 | 0.012023 | 3.5998e-05
2017 | 2016-12-07 | B | 32 | 0.012575 | 9.5993e-05
2017 | 2016-11-29 | B | 37 | 0.049841 | 0.00011101
2017 | 2016-11-23 | C | 109 | 0.018031 | 0.00032704
2017 | 2016-11-24 | C | 3 | 0.00198 | 1.8002e-05
2017 | 2016-11-30 | B | 37 | 0.044845 | 0.000111
2017 | 2016-12-16 | B | 96 | 0.11028 | 0.00028794
2017 | 2016-11-24 | C | 1210 | 0.034946 | 0.0036304
2017 | 2016-12-13 | B | 54 | 0.032556 | 0.00016197
2017 | 2016-12-09 | B | 187 | 0.001214 | 0.00056094
2017 | 2016-12-13 | B | 3 | 0.001502 | 8.9985e-06
2017 | 2016-12-12 | B | 26 | 0.007798 | 7.7989e-05
2017 | 2016-12-13 | B | 41 | 0.034891 | 0.00012298
2017 | 2016-12-10 | B | 1 | 0.000343 | 2.9996e-06
2017 | 2016-11-24 | C | 1 | 0.000966 | 3.0003e-06
2017 | 2016-12-11 | B | 422 | 0.055738 | 0.0012658
2017 | 2016-12-21 | B | 46 | 0.040008 | 0.00013796
2017 | 2016-12-12 | B | 7 | 0.003296 | 2.0997e-05
2017 | 2016-12-06 | B | 37 | 0.02131 | 0.00011099
2017 | 2016-12-20 | B | 8 | 0.006766 | 2.3994e-05
2017 | 2016-12-14 | B | 30 | 0.041122 | 8.9984e-05
2017 | 2016-12-15 | B | 30 | 0.039682 | 8.9983e-05
2017 | 2016-12-22 | B | 8 | 0.004246 | 2.3993e-05
2017 | 2016-12-13 | B | 5 | 0.004169 | 1.4998e-05
2017 | 2016-12-09 | B | 56 | 0.072904 | 0.00016798
2017 | 2016-12-20 | B | 11 | 0.014291 | 3.2991e-05
2017 | 2016-12-22 | B | 1 | 0.000951 | 2.9991e-06
2017 | 2016-12-21 | B | 3 | 0.003212 | 8.9974e-06
2017 | 2016-12-14 | B | 2 | 0.000167 | 5.9989e-06
2017 | 2016-12-15 | B | 2 | 0.002873 | 5.9988e-06
2017 | 2016-12-14 | B | 71 | 0.02087 | 0.00021296
2017 | 2016-11-24 | C | 1 | 0.000325 | 3.0003e-06
2017 | 2016-11-24 | C | 55 | 0.004455 | 0.00016502
2017 | 2016-11-24 | C | 79 | 0.011519 | 0.00023703
2017 | 2016-11-24 | C | 868 | 0.10448 | 0.0026043
2017 | 2016-11-24 | C | 85 | 0.024886 | 0.00025503
2017 | 2016-11-25 | C | 30 | 0.009845 | 9.001e-05
2017 | 2016-11-25 | C | 1 | 0.000462 | 3.0003e-06
2017 | 2016-11-25 | C | 334 | 0.008457 | 0.0010021
2017 | 2016-11-25 | C | 635 | 0.1637 | 0.0019052
2017 | 2016-11-25 | C | 2 | 0.000762 | 6.0006e-06
2017 | 2016-12-10 | B | 5 | 0.003329 | 1.4998e-05
2017 | 2016-11-25 | C | 91 | 0.034527 | 0.00043505
2017 | 2016-11-25 | C | 21 | 0.003081 | 6.3007e-05
2017 | 2016-11-25 | C | 1047 | 0.20516 | 0.0031413
2017 | 2016-11-25 | C | 3080 | 0.14139 | 0.009241
2017 | 2016-11-25 | C | 11 | 0.003168 | 3.3003e-05
2017 | 2016-11-25 | C | 148 | 0.008688 | 0.00044405
2017 | 2016-11-25 | C | 3 | 0.000852 | 9.0009e-06
2017 | 2016-11-25 | C | 329 | 0.028832 | 0.00027303
2017 | 2016-12-15 | B | 3 | 0.002987 | 8.9983e-06
2017 | 2016-12-15 | B | 8 | 0.010126 | 2.3995e-05
2017 | 2016-12-13 | B | 23 | 0.003847 | 6.8989e-05
2017 | 2016-12-15 | B | 31 | 0.022966 | 9.2983e-05
2017 | 2016-12-15 | B | 48 | 0.026922 | 0.00014397
2017 | 2016-11-25 | C | 37 | 0.00128 | 0.00011101
2017 | 2016-12-15 | B | 8 | 0.005854 | 2.3995e-05
2017 | 2016-11-25 | C | 149 | 0.007167 | 0.00044705
2017 | 2016-12-22 | B | 4 | 0.002111 | 1.1996e-05
2017 | 2016-11-25 | C | 1 | 0.000183 | 3.0003e-06
2017 | 2016-11-25 | C | 661 | 0.12778 | 0.0039664
2017 | 2016-11-25 | C | 2 | 0.000506 | 6.0006e-06
2017 | 2016-12-20 | B | 212 | 0.07312 | 0.0012717
2017 | 2016-12-14 | B | 20 | 0.019316 | 5.999e-05
2017 | 2016-11-25 | C | 30 | 0.007127 | 9.001e-05
2017 | 2016-11-25 | C | 76 | 0.019021 | 0.00022802
2017 | 2016-11-25 | C | 5 | 0.002748 | 1.5002e-05
2017 | 2016-11-25 | C | 382 | 0.10407 | 0.0011461
2017 | 2016-11-26 | C | 171 | 0.064159 | 0.00094209
2017 | 2016-11-26 | C | 8 | 0.006102 | 2.4002e-05
2017 | 2016-11-26 | C | 24 | 0.003277 | 7.5007e-05
2017 | 2016-11-26 | C | 2 | 0.000522 | 6.0005e-06
2017 | 2016-11-26 | C | 246 | 0.092479 | 0.00073807
2017 | 2016-11-26 | C | 726 | 0.14201 | 0.0021782
2017 | 2016-11-26 | C | 2 | 0.000971 | 6.0005e-06
2017 | 2016-11-26 | C | 1041 | 0.072982 | 0.0031233
2017 | 2016-11-26 | C | 1 | 0.000156 | 3.0002e-06
2017 | 2016-11-26 | C | 316 | 0.074939 | 0.00094809
2017 | 2016-11-27 | C | 2 | 0.001778 | 6.0004e-06
2017 | 2016-11-27 | C | 94 | 0.036404 | 0.00028202
2017 | 2016-11-27 | C | 586 | 0.35102 | 0.0017581
2017 | 2016-11-27 | C | 109 | 0.074708 | 0.00040803
2017 | 2016-11-27 | C | 97 | 0.064245 | 0.00050404
2017 | 2016-11-27 | C | 12 | 0.008875 | 3.6003e-05
2017 | 2016-11-27 | C | 298 | 0.099599 | 0.00089407
2017 | 2016-11-27 | C | 2 | 0.000601 | 6.0004e-06
2017 | 2016-11-27 | C | 237 | 0.19857 | 0.00071105
2017 | 2016-11-27 | C | 20 | 0.029392 | 6.0004e-05
2017 | 2016-11-27 | C | 63 | 0.067206 | 0.00018901
2017 | 2016-11-27 | C | 28 | 0.015245 | 8.4006e-05
2017 | 2016-11-27 | C | 1456 | 0.40972 | 0.0043683
2017 | 2016-11-30 | C | 10 | 0.0015 | 3.0001e-05
2017 | 2016-11-27 | C | 9 | 0.009128 | 2.7002e-05
2017 | 2016-11-27 | C | 78 | 0.074805 | 0.00023402
2017 | 2016-11-27 | C | 316 | 0.18172 | 0.00094807
2017 | 2016-11-27 | C | 31 | 0.008858 | 9.3007e-05
2017 | 2016-11-27 | C | 360 | 0.10873 | 0.0010801
2017 | 2016-11-27 | C | 8 | 0.001815 | 2.4002e-05
2017 | 2016-11-27 | C | 218 | 0.024199 | 0.00065405
2017 | 2016-11-27 | C | 1 | 0.001074 | 3.0002e-06
2017 | 2016-11-27 | C | 15 | 0.00711 | 4.5003e-05
2017 | 2016-11-27 | C | 373 | 0.036692 | 0.0011191
2017 | 2016-11-28 | C | 29 | 0.005655 | 8.7006e-05
2017 | 2016-11-27 | C | 24 | 0.00339 | 7.2005e-05
2017 | 2016-11-27 | C | 1 | 0.001224 | 3.0002e-06
2017 | 2016-11-27 | C | 342 | 0.19705 | 0.0010261
2017 | 2016-11-27 | C | 1 | 0.003298 | 3.0002e-06
2017 | 2016-11-27 | C | 29 | 0.14273 | 8.7007e-05
2017 | 2016-11-27 | C | 2 | 0.001243 | 6.0004e-06
2017 | 2016-11-27 | C | 1 | 0.000493 | 3.0002e-06
2017 | 2016-11-27 | C | 83 | 0.033742 | 0.00024902
2017 | 2016-11-27 | C | 91 | 0.009916 | 0.00027302
2017 | 2016-11-27 | C | 106 | 0.089521 | 0.00031802
2017 | 2016-11-27 | C | 93 | 0.001827 | 0.00027902
2017 | 2016-11-27 | C | 204 | 0.004341 | 0.00021302
2017 | 2016-11-27 | C | 54 | 0.066943 | 0.00016201
2017 | 2016-11-27 | C | 480 | 0.14865 | 0.0014401
2017 | 2016-11-28 | C | 4 | 0.001464 | 1.2001e-05
2017 | 2016-11-28 | C | 347 | 0.055984 | 0.00081005
2017 | 2016-11-28 | C | 1120 | 0.18789 | 0.0033602
2017 | 2016-11-25 | C | 19 | 0.007524 | 5.7006e-05
2017 | 2016-12-14 | B | 1 | 0.000926 | 2.9994e-06
2017 | 2016-11-28 | C | 1 | 0.000704 | 3.0001e-06
2017 | 2016-12-16 | B | 4 | 0.004343 | 1.1997e-05
2017 | 2016-11-28 | C | 7 | 0.001449 | 2.1001e-05
2017 | 2016-12-21 | B | 6 | 0.005291 | 1.7995e-05
2017 | 2016-11-28 | C | 2 | 0.001079 | 6.0003e-06
2017 | 2016-11-28 | C | 771 | 0.21144 | 0.0023131
2017 | 2016-11-28 | C | 2 | 0.002318 | 6.0003e-06
2017 | 2016-11-28 | C | 1 | 0.000388 | 3.0001e-06
2017 | 2016-11-28 | C | 688 | 0.15016 | 0.0020641
2017 | 2016-11-28 | C | 41 | 0.011542 | 0.00012301
2017 | 2016-12-14 | B | 20 | 0.021836 | 5.999e-05
2017 | 2016-12-16 | B | 11 | 0.009733 | 3.2993e-05
2017 | 2016-12-01 | B | 41 | 0.032339 | 0.000123
2017 | 2016-11-28 | C | 527 | 0.034694 | 0.0015811
2017 | 2016-12-20 | B | 20 | 0.016015 | 5.9984e-05
2017 | 2016-11-28 | C | 49 | 0.00735 | 0.00014701
2017 | 2016-11-28 | C | 2 | 0.001062 | 6.0003e-06
2017 | 2016-12-14 | B | 20 | 0.019616 | 5.999e-05
2017 | 2016-12-16 | B | 20 | 0.019915 | 5.9988e-05
2017 | 2016-11-28 | C | 8 | 0.002684 | 2.4002e-05
2017 | 2016-12-20 | B | 93 | 0.074254 | 0.00027893
2017 | 2016-11-28 | C | 48 | 0.00072 | 0.00014401
2017 | 2016-11-28 | C | 93 | 0.04359 | 0.00039303
2017 | 2016-11-28 | C | 1 | 0.000319 | 3.0001e-06
2017 | 2016-11-28 | C | 9 | 0.004838 | 2.7002e-05
2017 | 2016-11-28 | C | 1 | 0.00081 | 3.0001e-06
2017 | 2016-11-28 | C | 1 | 0.00228 | 3.0001e-06
2017 | 2016-11-28 | C | 546 | 0.011717 | 0.0016381
2017 | 2016-12-13 | B | 146 | 0.050566 | 0.00087586
2017 | 2016-12-14 | B | 5 | 0.004739 | 1.4997e-05
2017 | 2016-11-29 | C | 223 | 0.06143 | 0.00066903
2017 | 2016-12-15 | B | 43 | 0.060231 | 0.00012898
2017 | 2016-12-12 | B | 422 | 0.062553 | 0.0012658
2017 | 2016-12-01 | B | 26 | 0.017823 | 7.8001e-05
2017 | 2016-11-29 | C | 3 | 0.001385 | 9.0004e-06
2017 | 2016-12-15 | B | 43 | 0.024683 | 0.00012898
2017 | 2016-11-29 | C | 93 | 0.040858 | 0.00055803
2017 | 2016-11-29 | C | 1 | 0.000281 | 3.0001e-06
2017 | 2016-11-29 | C | 21 | 0.002268 | 6.3003e-05
2017 | 2016-11-29 | C | 1 | 0.000742 | 3.0001e-06
2017 | 2016-12-04 | B | 19 | 0.01004 | 5.6998e-05
2017 | 2016-11-29 | C | 351 | 0.003897 | 0.0010531
2017 | 2016-11-29 | C | 110 | 0.033437 | 0.00033002
2017 | 2016-11-30 | C | 28 | 0.004701 | 8.4003e-05
2017 | 2016-11-30 | C | 6 | 0.006116 | 1.8001e-05
2017 | 2016-11-30 | C | 5 | 0.004769 | 1.5e-05
2017 | 2016-12-05 | B | 69 | 0.042254 | 0.00020699
2017 | 2016-11-30 | C | 1 | 0.000192 | 3.0001e-06
2017 | 2016-12-20 | B | 74 | 0.059036 | 0.00022194
2017 | 2016-12-20 | B | 12 | 0.008737 | 3.5991e-05
2017 | 2016-12-01 | B | 33 | 0.075564 | 9.9002e-05
2017 | 2016-12-21 | B | 109 | 0.0257 | 0.00065382
2017 | 2016-11-30 | C | 8 | 0.002541 | 2.4001e-05
2017 | 2016-12-21 | B | 9 | 0.008817 | 2.6992e-05
2017 | 2016-12-14 | B | 40 | 0.009838 | 0.00011998
2017 | 2016-11-30 | C | 7 | 0.00323 | 2.1001e-05
2017 | 2016-11-30 | C | 1 | 0.000343 | 3.0001e-06
2017 | 2016-11-30 | C | 25 | 0.005321 | 7.5003e-05
2017 | 2016-12-01 | C | 6 | 0.002074 | 1.8e-05
2017 | 2016-12-22 | B | 2 | 0.001189 | 5.9982e-06
2017 | 2016-12-19 | B | 32 | 0.025913 | 9.5976e-05
2017 | 2016-12-15 | B | 65 | 0.039382 | 0.00019496
2017 | 2016-12-21 | B | 20 | 0.024923 | 5.9983e-05
2017 | 2016-12-01 | C | 3064 | 0.29433 | 0.0091922
2017 | 2016-12-01 | C | 182 | 0.086017 | 0.00054601
2017 | 2016-12-05 | B | 7 | 0.007475 | 2.0999e-05
2017 | 2016-12-02 | C | 3 | 0.000567 | 9e-06
2017 | 2016-12-20 | B | 12 | 0.011962 | 3.5991e-05
2017 | 2016-12-16 | B | 3 | 0.001025 | 8.9981e-06
2017 | 2016-12-09 | B | 1 | 4.7e-05 | 2.9997e-06
2017 | 2016-12-17 | B | 17 | 0.017693 | 5.0989e-05
2017 | 2016-12-03 | C | 1 | 0.000713 | 2.9999e-06
2017 | 2016-12-03 | C | 2 | 0.000647 | 5.9999e-06
2017 | 2016-12-03 | C | 45 | 0.007247 | 0.000135
2017 | 2016-12-03 | C | 2 | 0.001175 | 5.9999e-06
2017 | 2016-12-03 | C | 2 | 0.000744 | 5.9999e-06
2017 | 2016-12-04 | C | 1 | 0.000847 | 2.9999e-06
2017 | 2016-12-04 | C | 149 | 0.044502 | 0.00044699
2017 | 2016-12-05 | C | 17 | 0.006005 | 5.0998e-05
2017 | 2016-12-05 | C | 1 | 0.000253 | 2.9998e-06
2017 | 2016-12-12 | B | 26 | 0.016923 | 7.7989e-05
2017 | 2016-12-19 | B | 422 | 0.036704 | 0.0012657
2017 | 2016-12-14 | B | 61 | 0.001646 | 0.00018297
2017 | 2016-12-06 | C | 2 | 0.00047 | 5.9996e-06
2017 | 2016-12-20 | B | 106 | 0.17326 | 0.00031792
2017 | 2016-12-07 | B | 184 | 0.23293 | 0.00055196
2017 | 2016-12-10 | B | 3 | 0.001682 | 8.9989e-06
2017 | 2016-12-07 | C | 547 | 0.097674 | 0.0016409
2017 | 2016-12-07 | C | 5 | 0.000926 | 1.4999e-05
2017 | 2016-12-08 | B | 12 | 0.012418 | 3.5997e-05
2017 | 2016-12-07 | C | 176 | 0.11388 | 0.00052796
2017 | 2016-12-07 | C | 25 | 0.005999 | 7.4995e-05
2017 | 2016-12-09 | B | 45 | 0.052104 | 0.00013499
2017 | 2016-12-07 | C | 19 | 0.00416 | 5.6996e-05
2017 | 2016-12-09 | B | 4 | 0.002147 | 1.1999e-05
2017 | 2016-12-07 | C | 265 | 0.072999 | 0.00079495
2017 | 2016-12-07 | C | 9 | 0.003898 | 2.6998e-05
2017 | 2016-12-07 | C | 29 | 0.003479 | 8.6994e-05
2017 | 2016-12-07 | C | 138 | 0.01611 | 0.00041397
2017 | 2016-12-07 | C | 161 | 0.41124 | 0.00048297
2017 | 2016-12-08 | C | 440 | 0.053398 | 0.0014219
2017 | 2016-12-08 | C | 7 | 0.003695 | 2.0998e-05
2017 | 2017-01-09 | B | 5 | 0.000704 | 1.4991e-05
2017 | 2017-01-10 | B | 4 | 0.002842 | 1.1993e-05
2017 | 2017-01-10 | B | 4 | 0.000323 | 1.1993e-05
2017 | 2017-01-12 | B | 6 | 0.007303 | 1.7989e-05
2017 | 2017-01-10 | B | 5 | 0.000314 | 1.4991e-05
2017 | 2017-01-14 | B | 6 | 0.00554 | 1.7988e-05
2017 | 2016-12-08 | C | 2 | 0.000199 | 5.9995e-06
2017 | 2017-01-11 | B | 133 | 0.15193 | 0.00039876
2017 | 2017-01-10 | B | 7 | 0.000167 | 2.0988e-05
2017 | 2016-12-08 | C | 1 | 0.000351 | 2.9997e-06
2017 | 2016-12-17 | B | 10 | 0.003491 | 2.9993e-05
2017 | 2017-01-10 | B | 15 | 0.013474 | 4.4974e-05
2017 | 2017-01-12 | B | 24 | 0.025112 | 7.1956e-05
2017 | 2017-01-17 | B | 24 | 0.025686 | 7.1951e-05
2017 | 2017-01-18 | B | 24 | 0.024772 | 7.195e-05
2017 | 2017-01-11 | B | 1 | 0.000167 | 2.9982e-06
2017 | 2017-01-11 | B | 8 | 0.007123 | 2.3986e-05
2017 | 2017-01-12 | B | 17 | 0.011518 | 5.0969e-05
2017 | 2017-01-11 | B | 1 | 0.00017 | 2.9982e-06
2017 | 2017-01-12 | B | 3 | 0.001187 | 8.9945e-06
2017 | 2017-01-12 | B | 1 | 0.00098 | 2.9981e-06
2017 | 2017-01-12 | B | 46 | 0.035168 | 0.00013792
2017 | 2017-01-12 | B | 47 | 0.023955 | 0.00014091
2017 | 2016-12-08 | C | 8 | 0.001987 | 2.3998e-05
2017 | 2016-12-08 | C | 408 | 0.099107 | 0.0018838
2017 | 2016-12-08 | C | 180 | 0.031074 | 0.00053996
2017 | 2017-01-23 | B | 11 | 0.004847 | 3.2975e-05
2017 | 2017-01-24 | B | 2 | 0.001241 | 5.9952e-06
2017 | 2017-01-13 | B | 2 | 0.000305 | 5.9962e-06
2017 | 2016-12-09 | C | 742 | 0.17063 | 0.0022258
2017 | 2016-12-09 | C | 422 | 0.0141 | 0.0012659
2017 | 2017-01-13 | B | 1 | 0.000365 | 2.9981e-06
2017 | 2016-12-09 | C | 874 | 0.16212 | 0.0026217
2017 | 2017-01-16 | B | 3 | 0.00259 | 8.9939e-06
2017 | 2017-01-16 | B | 3 | 0.000377 | 8.9939e-06
2017 | 2017-01-10 | B | 10 | 0.011153 | 2.9982e-05
2017 | 2017-01-16 | B | 5 | 0.001304 | 1.499e-05
2017 | 2016-12-09 | C | 50 | 0.006999 | 0.00014999
2017 | 2017-01-16 | B | 8 | 0.001367 | 2.3984e-05
2017 | 2017-01-16 | B | 1 | 5e-05 | 2.9979e-06
2017 | 2017-01-12 | B | 26 | 0.001325 | 7.7952e-05
2017 | 2017-01-14 | B | 143 | 0.044623 | 0.00042873
2017 | 2016-12-10 | C | 3 | 0.002762 | 8.9989e-06
2017 | 2016-12-15 | B | 57 | 0.043727 | 0.00017097
2017 | 2017-01-17 | B | 12 | 0.009605 | 3.5975e-05
2017 | 2017-01-18 | B | 5 | 0.004571 | 1.4989e-05
2017 | 2016-12-10 | C | 3 | 0.000611 | 8.9989e-06
2017 | 2017-01-19 | B | 26 | 0.013359 | 7.7944e-05
2017 | 2016-12-10 | C | 17 | 0.008851 | 5.0994e-05
2017 | 2017-01-20 | B | 11 | 0.010849 | 3.2976e-05
2017 | 2017-01-21 | B | 27 | 0.018049 | 8.094e-05
2017 | 2016-12-10 | C | 1418 | 0.14204 | 0.0042535
2017 | 2016-12-10 | C | 22 | 0.003101 | 6.5992e-05
2017 | 2016-12-11 | C | 149 | 0.051883 | 0.0010169
2017 | 2016-12-11 | C | 178 | 0.14808 | 0.00053393
2017 | 2016-12-11 | C | 2 | 0.00036 | 5.9992e-06
2017 | 2016-12-11 | C | 158 | 0.014129 | 0.00047394
2017 | 2016-12-11 | C | 74 | 0.011764 | 0.00022197
2017 | 2016-12-11 | C | 213 | 0.038525 | 0.00063892
2017 | 2016-12-11 | C | 49 | 0.00083 | 0.00014698
2017 | 2016-12-11 | C | 1 | 0.00023 | 2.9996e-06
2017 | 2016-12-11 | C | 56 | 0.020493 | 0.00016798
2017 | 2016-12-11 | C | 1 | 0.000584 | 2.9996e-06
2017 | 2016-12-11 | C | 117 | 0.04617 | 0.00044994
2017 | 2016-12-12 | C | 1 | 0.000355 | 2.9995e-06
2017 | 2017-01-17 | B | 4 | 0.001343 | 1.1992e-05
2017 | 2016-12-12 | C | 2 | 0.000353 | 5.9991e-06
2017 | 2016-12-15 | B | 92 | 0.023867 | 0.00027595
2017 | 2016-12-12 | C | 4 | 0.001555 | 1.1998e-05
2017 | 2016-12-09 | C | 2 | 0.000419 | 5.9994e-06
2017 | 2016-12-09 | C | 3 | 0.000161 | 8.9991e-06
2017 | 2016-12-14 | B | 248 | 0.21811 | 0.00089085
2017 | 2017-01-17 | B | 7 | 0.002266 | 2.0986e-05
2017 | 2017-01-17 | B | 2 | 0.001097 | 5.9959e-06
2017 | 2016-12-29 | B | 29 | 0.007743 | 0.00016493
2017 | 2016-12-12 | C | 765 | 0.063944 | 0.0022947
2017 | 2017-01-31 | B | 2 | 0.001916 | 5.9947e-06
2017 | 2017-01-19 | B | 1 | 4.1e-05 | 2.9978e-06
2017 | 2017-01-20 | B | 5 | 0.001319 | 1.4989e-05
2017 | 2016-12-12 | C | 93 | 0.038635 | 0.0006689
2017 | 2017-01-10 | B | 2 | 0.001685 | 5.9964e-06
2017 | 2016-12-12 | C | 92 | 0.026226 | 0.00027596
2017 | 2017-01-24 | B | 46 | 0.031163 | 0.00013789
2017 | 2016-12-12 | C | 76 | 0.020406 | 0.00032695
2017 | 2017-01-25 | B | 3 | 0.00169 | 8.9928e-06
2017 | 2016-12-12 | C | 1 | 0.000494 | 2.9995e-06
2017 | 2017-01-18 | B | 211 | 0.15457 | 0.00063256
2017 | 2017-01-25 | B | 17 | 0.02023 | 5.0959e-05
2017 | 2016-12-12 | C | 566 | 0.16042 | 0.0025136
2017 | 2017-01-25 | B | 43 | 0.040215 | 0.0001289
2017 | 2017-01-25 | B | 17 | 0.019364 | 5.0959e-05
2017 | 2016-12-12 | C | 1 | 0.000486 | 2.9995e-06
2017 | 2016-12-12 | C | 1 | 0.000631 | 2.9995e-06
2017 | 2016-12-12 | C | 293 | 0.13328 | 0.0020307
2017 | 2016-12-12 | C | 185 | 0.038116 | 0.00055492
2017 | 2016-12-12 | C | 1120 | 0.22417 | 0.0037945
2017 | 2016-12-12 | C | 2 | 0.005579 | 5.9991e-06
2017 | 2016-12-13 | C | 180 | 0.007963 | 0.0010798
2017 | 2016-12-13 | C | 3 | 0.000731 | 8.9985e-06
2017 | 2017-01-16 | B | 33 | 0.035319 | 9.8934e-05
2017 | 2017-01-17 | B | 66 | 0.085418 | 0.00019786
2017 | 2016-12-13 | C | 1604 | 0.22723 | 0.0073158
2017 | 2016-12-29 | B | 14 | 0.011167 | 4.1983e-05
2017 | 2017-01-19 | B | 35 | 0.038717 | 0.00010493
2017 | 2017-01-11 | B | 59 | 0.020637 | 0.00017689
2017 | 2017-01-18 | B | 37 | 0.04215 | 0.00011092
2017 | 2017-01-23 | B | 11 | 0.012398 | 3.2975e-05
2017 | 2017-01-24 | B | 12 | 0.011726 | 3.5972e-05
2017 | 2017-01-25 | B | 23 | 0.018063 | 6.8945e-05
2017 | 2016-12-14 | C | 12 | 0.002869 | 3.5994e-05
2017 | 2017-01-25 | B | 32 | 0.026666 | 9.5923e-05
2017 | 2017-01-12 | B | 4 | 0.003972 | 1.1993e-05
2017 | 2016-12-14 | C | 1433 | 0 | 2.9994e-06
2017 | 2016-12-14 | C | 324 | 0.12981 | 0.0023186
2017 | 2017-01-16 | B | 13 | 0.008769 | 3.8974e-05
2017 | 2017-01-18 | B | 1 | 0.001295 | 2.9979e-06
2017 | 2017-01-29 | B | 47 | 0.020746 | 0.00028176
2017 | 2016-12-18 | B | 1 | 0.000539 | 2.9993e-06
2017 | 2017-01-16 | B | 6 | 0.006781 | 1.7988e-05
2017 | 2017-01-24 | B | 34 | 0.043112 | 0.00010192
2017 | 2016-12-14 | C | 3 | 0.000441 | 8.9984e-06
2017 | 2016-12-15 | C | 6 | 0.002908 | 1.7997e-05
2017 | 2017-01-25 | B | 128 | 0.17676 | 0.00038369
2017 | 2016-12-15 | C | 283 | 0.073756 | 0.0015387
2017 | 2016-12-15 | C | 3 | 0.00071 | 8.9983e-06
2017 | 2016-12-15 | C | 1609 | 0.004899 | 0.0048261
2017 | 2016-12-15 | C | 3 | 0.001304 | 8.9983e-06
2017 | 2017-01-17 | B | 3 | 0.000665 | 8.9938e-06
2017 | 2017-01-24 | B | 3 | 0.00285 | 8.9929e-06
2017 | 2017-01-17 | B | 22 | 0.013322 | 6.5955e-05
2017 | 2017-01-25 | B | 3 | 0.002805 | 8.9928e-06
2017 | 2016-12-15 | C | 1379 | 0.26826 | 0.0041362
2017 | 2016-12-15 | C | 9 | 0.003879 | 2.6995e-05
2017 | 2017-01-17 | B | 3 | 0.001591 | 8.9938e-06
2017 | 2017-01-24 | B | 145 | 0.18697 | 0.00043466
2017 | 2016-12-15 | C | 4 | 0.001067 | 1.1998e-05
2017 | 2017-01-13 | B | 11 | 0.007387 | 3.2979e-05
2017 | 2017-01-13 | B | 2 | 0.000977 | 5.9962e-06
2017 | 2016-12-15 | C | 93 | 0.030948 | 0.00027895
2017 | 2016-12-15 | C | 1 | 0.000423 | 2.9994e-06
2017 | 2016-12-15 | C | 3 | 0.000499 | 8.9983e-06
2017 | 2016-12-15 | C | 2 | 0.006955 | 5.9988e-06
2017 | 2016-12-15 | C | 271 | 0.027894 | 0.00081285
2017 | 2016-12-15 | C | 1070 | 0.6787 | 0.0032094
2017 | 2016-12-15 | C | 360 | 0.12669 | 0.0010798
2017 | 2016-12-15 | C | 230 | 0.10046 | 0.00068987
2017 | 2017-01-17 | B | 62 | 0.028494 | 0.00018587
2017 | 2016-12-21 | B | 78 | 0.015007 | 0.00045887
2017 | 2016-12-16 | C | 26 | 0.024112 | 7.7984e-05
2017 | 2016-12-16 | C | 1 | 0.000266 | 2.9993e-06
2017 | 2016-12-16 | C | 84 | 0.010165 | 0.00025195
2017 | 2016-12-16 | C | 195 | 0.012779 | 0.00058488
2017 | 2017-01-26 | B | 15 | 0.012589 | 4.4963e-05
2017 | 2016-12-16 | C | 17 | 0.008107 | 5.099e-05
2017 | 2017-01-30 | B | 18 | 0.016494 | 5.3953e-05
2017 | 2017-01-16 | B | 101 | 0.11264 | 0.0003028
2017 | 2016-12-16 | C | 36 | 0 | 0.00010798
2017 | 2016-12-17 | C | 20 | 0.007509 | 5.9987e-05
2017 | 2016-12-17 | C | 42 | 0.010707 | 0.00012597
2017 | 2016-12-17 | C | 47 | 0.016761 | 0.00014097
2017 | 2017-01-26 | B | 22 | 0.024136 | 6.5946e-05
2017 | 2016-12-17 | C | 360 | 0.086429 | 0.0010798
2017 | 2016-12-17 | C | 1 | 0.000273 | 2.9993e-06
2017 | 2016-12-17 | C | 7 | 0.000783 | 2.0995e-05
2017 | 2016-12-18 | C | 21 | 0.010014 | 6.2985e-05
2017 | 2016-12-18 | C | 3 | 0.00108 | 8.9979e-06
2017 | 2016-12-18 | C | 9 | 0.004265 | 2.6994e-05
2017 | 2016-12-18 | C | 365 | 0.053429 | 0.0010947
2017 | 2016-12-18 | C | 1 | 0.000138 | 2.9993e-06
2017 | 2016-12-18 | C | 17 | 0.000119 | 5.0988e-05
2017 | 2016-12-18 | C | 164 | 0.055702 | 0.00049189
2017 | 2016-12-19 | C | 1 | 0.000518 | 2.9992e-06
2017 | 2016-12-19 | C | 2002 | 0.71013 | 0.0060045
2017 | 2016-12-19 | C | 678 | 0.15866 | 0.0020335
2017 | 2016-12-19 | C | 109 | 0.031957 | 0.00032692
2017 | 2016-12-19 | C | 2 | 0.000633 | 5.9985e-06
2017 | 2016-12-19 | C | 109 | 0.015366 | 0.00050987
2017 | 2016-12-20 | B | 79 | 0.063499 | 0.00023694
2017 | 2016-12-19 | C | 241 | 0.050484 | 0.00072282
2017 | 2017-01-18 | B | 40 | 0.047846 | 0.00011992
2017 | 2017-01-17 | B | 2 | 0.00217 | 5.9959e-06
2017 | 2017-01-13 | B | 1 | 0.000419 | 2.9981e-06
2017 | 2017-01-16 | B | 30 | 0.01457 | 8.994e-05
2017 | 2016-12-19 | C | 39 | 0.034155 | 0.00011697
2017 | 2016-12-19 | C | 55 | 0.009072 | 0.00016496
2017 | 2016-12-19 | C | 1 | 0.001043 | 2.9992e-06
2017 | 2016-12-19 | C | 182 | 0.0937 | 0.00054586
2017 | 2017-01-09 | B | 2 | 0.000161 | 5.9965e-06
2017 | 2017-01-17 | B | 11 | 0.011674 | 3.2977e-05
2017 | 2016-12-19 | C | 1 | 0.000146 | 2.9992e-06
2017 | 2016-12-20 | C | 6 | 0.001403 | 1.7995e-05
2017 | 2017-01-18 | B | 5 | 0.003252 | 1.4989e-05
2017 | 2017-01-19 | B | 10 | 0.011391 | 2.9979e-05
2017 | 2016-12-20 | C | 1 | 0.000545 | 2.9992e-06
2017 | 2017-01-13 | B | 13 | 0.017967 | 3.8976e-05
2017 | 2016-12-20 | C | 40 | 0.007917 | 0.00011997
2017 | 2016-12-21 | B | 12 | 0.00802 | 3.599e-05
2017 | 2017-01-06 | B | 57 | 0.00664 | 0.00017991
2017 | 2017-01-27 | B | 3 | 0.002535 | 8.9925e-06
2017 | 2017-01-18 | B | 3 | 0.001636 | 8.9937e-06
2017 | 2017-01-18 | B | 2 | 0.000491 | 5.9958e-06
2017 | 2017-01-24 | B | 7 | 0.006819 | 2.0983e-05
2017 | 2016-12-22 | B | 28 | 0.004519 | 8.3975e-05
2017 | 2016-12-20 | C | 11 | 0.00221 | 3.2991e-05
2017 | 2017-01-20 | B | 3 | 0.00303 | 8.9934e-06
2017 | 2017-01-13 | B | 37 | 0.027843 | 0.00011093
2017 | 2016-12-21 | C | 1 | 0.000336 | 2.9991e-06
2017 | 2016-12-21 | C | 14 | 0.034754 | 4.1988e-05
2017 | 2017-01-19 | B | 226 | 0.19919 | 0.00067752
2017 | 2017-01-31 | B | 19 | 0.017138 | 5.695e-05
2017 | 2017-01-17 | B | 5 | 0.005651 | 1.499e-05
2017 | 2016-12-21 | C | 101 | 0.025313 | 0.00030291
2017 | 2016-12-21 | C | 4 | 0.001811 | 1.1997e-05
2017 | 2016-12-21 | C | 43 | 0.010347 | 0.00012896
2017 | 2016-12-21 | C | 28 | 0.02662 | 8.3976e-05
2017 | 2017-01-25 | B | 72 | 0.020287 | 0.00021583
2017 | 2017-01-17 | B | 226 | 0.048189 | 0.0010193
2017 | 2016-12-22 | C | 1 | 0.000644 | 2.9991e-06
2017 | 2017-01-25 | B | 10 | 0.007194 | 2.9976e-05
2017 | 2017-01-20 | B | 58 | 0.067984 | 0.00017387
2017 | 2017-01-23 | B | 7 | 0.003189 | 2.0984e-05
2017 | 2017-01-24 | B | 18 | 0.0203 | 5.3958e-05
2017 | 2017-01-26 | B | 17 | 0.021582 | 5.0959e-05
2017 | 2016-12-22 | C | 59 | 0.011678 | 0.00017695
2017 | 2017-01-18 | B | 112 | 0.016788 | 0.00033577
2017 | 2016-12-22 | C | 18 | 0.001507 | 5.3984e-05
2017 | 2017-01-20 | B | 5 | 0.001379 | 1.4989e-05
2017 | 2017-01-24 | B | 79 | 0.009088 | 0.00024281
2017 | 2016-12-22 | C | 358 | 0.13788 | 0.0010737
2017 | 2016-12-22 | C | 1 | 0.000244 | 2.9991e-06
2017 | 2016-12-22 | C | 25 | 0.008837 | 7.4978e-05
2017 | 2017-01-23 | B | 16 | 0.013669 | 4.7963e-05
2017 | 2016-12-31 | B | 4 | 0.001643 | 1.1995e-05
2017 | 2016-12-23 | B | 38 | 0.007434 | 0.00011396
2017 | 2016-12-22 | C | 145 | 0.017386 | 0.00043487
2017 | 2016-12-22 | C | 2 | 0.000471 | 5.9982e-06
2017 | 2016-12-23 | C | 241 | 0.13369 | 0.0014605
2017 | 2016-12-23 | C | 93 | 0.043001 | 0.00039288
2017 | 2016-12-23 | C | 120 | 0.11327 | 0.00059981
2017 | 2016-12-23 | C | 8 | 0.004897 | 2.3993e-05
2017 | 2016-12-23 | C | 16 | 0.006948 | 4.7985e-05
2017 | 2016-12-23 | C | 14 | 0.004134 | 4.1987e-05
2017 | 2017-02-02 | B | 1 | 0.00059 | 2.9972e-06
2017 | 2017-02-02 | B | 1 | 0.00029 | 2.9972e-06
2017 | 2016-12-23 | C | 6 | 0.001005 | 1.7994e-05
2017 | 2016-12-23 | C | 1 | 0.000494 | 2.999e-06
2017 | 2017-01-26 | B | 38 | 0.008734 | 0.00011391
2017 | 2016-12-23 | C | 1 | 0.000501 | 2.999e-06
2017 | 2016-12-23 | C | 223 | 0.054828 | 0.00066879
2017 | 2016-12-23 | C | 250 | 0.002941 | 2.3993e-05
2017 | 2016-12-23 | C | 2 | 0.000522 | 5.9981e-06
2017 | 2016-12-23 | C | 1 | 0.000407 | 2.999e-06
2017 | 2016-12-23 | C | 95 | 0.023296 | 0.00028491
2017 | 2016-12-23 | C | 62 | 0.013347 | 0.00018594
2017 | 2016-12-23 | C | 228 | 0.093114 | 0.00083074
2017 | 2016-12-24 | C | 17 | 0.004846 | 5.0983e-05
2017 | 2016-12-24 | C | 3 | 0.000287 | 8.997e-06
2017 | 2016-12-24 | C | 95 | 0.028398 | 0.00028491
2017 | 2016-12-24 | C | 6 | 0.001295 | 1.7994e-05
2017 | 2016-12-24 | C | 105 | 0.024729 | 0.0003149
2017 | 2016-12-24 | C | 6 | 0.000296 | 2.999e-06
2017 | 2016-12-25 | C | 34 | 0.008663 | 0.00010196
2017 | 2016-12-26 | C | 42 | 0.020952 | 0.00012595
2017 | 2016-12-26 | C | 174 | 0.052404 | 0.00052181
2017 | 2016-12-27 | C | 3 | 0.000872 | 8.9966e-06
2017 | 2016-12-27 | C | 202 | 0.023525 | 0.00038686
2017 | 2016-12-27 | C | 1 | 0.000315 | 2.9988e-06
2017 | 2016-12-27 | C | 42 | 0.013997 | 0.00012895
2017 | 2016-12-27 | C | 93 | 0.046256 | 0.0002789
2017 | 2016-12-27 | C | 3 | 0.000882 | 8.9966e-06
2017 | 2016-12-27 | C | 1 | 0.001071 | 2.9988e-06
2017 | 2016-12-27 | C | 439 | 0.11588 | 0.0013165
2017 | 2016-12-28 | C | 5 | 0.002459 | 1.4994e-05
2017 | 2016-12-27 | C | 10 | 0.001979 | 2.9989e-05
2017 | 2016-12-27 | C | 81 | 0.023889 | 0.00024291
2017 | 2016-12-27 | C | 223 | 0.008208 | 0.00066875
2017 | 2016-12-27 | C | 1 | 0.000576 | 2.9988e-06
2017 | 2016-12-27 | C | 20 | 0.007983 | 5.9977e-05
2017 | 2016-12-27 | C | 120 | 0.048835 | 0.00035987
2017 | 2016-12-27 | C | 157 | 0.018142 | 0.00047082
2017 | 2016-12-27 | C | 1 | 0.000221 | 2.9988e-06
2017 | 2016-12-27 | C | 167 | 0.13303 | 0.0010886
2017 | 2016-12-28 | C | 23 | 0.001655 | 6.8973e-05
2017 | 2016-12-28 | C | 197 | 0.050058 | 0.00059077
2017 | 2016-12-28 | C | 2 | 0.000174 | 2.9988e-06
2017 | 2016-12-28 | C | 2 | 0.000317 | 5.9976e-06
2017 | 2016-12-28 | C | 41 | 0.009457 | 0.00012295
2017 | 2016-12-28 | C | 17 | 0.000141 | 5.098e-05
2017 | 2016-12-29 | C | 4 | 0.001223 | 1.1995e-05
2017 | 2016-12-29 | C | 20 | 0.00735 | 5.9976e-05
2017 | 2016-12-29 | C | 2 | 0.000579 | 5.9975e-06
2017 | 2016-12-29 | C | 22 | 0.004516 | 6.5973e-05
2017 | 2016-12-29 | C | 688 | 0.13396 | 0.0041263
2017 | 2016-12-29 | C | 186 | 0.059937 | 0.00055777
2017 | 2016-12-30 | C | 79 | 0.01299 | 0.0002369
2017 | 2016-12-30 | C | 4 | 0.000978 | 1.1995e-05
2017 | 2016-12-30 | C | 1 | 0.000298 | 2.9987e-06
2017 | 2016-12-30 | C | 2 | 1.6e-05 | 5.9974e-06
2017 | 2016-12-30 | C | 7 | 0.003799 | 2.0991e-05
2017 | 2016-12-30 | C | 970 | 0.12092 | 0.0029088
2017 | 2016-12-30 | C | 563 | 0.1345 | 0.0016883
2017 | 2016-12-31 | C | 5 | 0.001397 | 1.4993e-05
2017 | 2016-12-31 | C | 11 | 0.006115 | 3.2985e-05
2017 | 2016-12-31 | C | 4 | 0.003331 | 1.1995e-05
2017 | 2016-12-31 | C | 174 | 0.029314 | 0.00052177
2017 | 2016-12-31 | C | 52 | 0.000423 | 0.00015593
2017 | 2016-12-31 | C | 41 | 0.013606 | 0.00012295
2017 | 2017-01-01 | C | 418 | 0.099677 | 0.00029087
2017 | 2017-01-01 | C | 7 | 0.001825 | 2.099e-05
2017 | 2017-01-01 | C | 4 | 0.000359 | 1.1995e-05
2017 | 2017-01-01 | C | 213 | 0.068815 | 0.00039582
2017 | 2017-01-01 | C | 15 | 0.005554 | 4.498e-05
2017 | 2017-01-01 | C | 299 | 0.11495 | 0.00096556
2017 | 2017-01-01 | C | 289 | 0.15431 | 0.00086661
2017 | 2017-01-01 | C | 44 | 0.013627 | 0.00013194
2017 | 2017-01-02 | C | 762 | 0.11235 | 0.0018891
2017 | 2017-01-02 | C | 674 | 0.27225 | 0.0020211
2017 | 2017-01-02 | C | 3 | 0.001923 | 8.9957e-06
2017 | 2017-01-02 | C | 288 | 0.045772 | 0.0008636
2017 | 2017-01-02 | C | 295 | 0.079116 | 0.0012804
2017 | 2017-01-02 | C | 1 | 0.000674 | 2.9985e-06
2017 | 2017-01-02 | C | 4807 | 1.1166 | 0.014414
2017 | 2017-01-02 | C | 1 | 0.00029 | 2.9985e-06
2017 | 2017-01-02 | C | 1 | 0.00044 | 2.9985e-06
2017 | 2017-01-02 | C | 1 | 0.000339 | 2.9985e-06
2017 | 2017-01-02 | C | 27 | 0.001024 | 8.0962e-05
2017 | 2017-01-02 | C | 50 | 0.047597 | 0.00014993
2017 | 2017-01-02 | C | 1 | 0.000351 | 2.9985e-06
2017 | 2017-01-02 | C | 500 | 0.16506 | 0.0016492
2017 | 2017-01-02 | C | 4 | 0.009242 | 1.1994e-05
2017 | 2017-01-02 | C | 1 | 0.00036 | 2.9985e-06
2017 | 2017-01-03 | C | 5 | 0.000455 | 1.4993e-05
2017 | 2017-01-03 | C | 2 | 0.000932 | 5.9971e-06
2017 | 2017-01-03 | C | 301 | 0.026482 | 0.00090256
2017 | 2017-01-03 | C | 313 | 0.39726 | 0.00093855
2017 | 2017-01-03 | C | 1 | 0.000256 | 2.9985e-06
2017 | 2017-01-03 | C | 3 | 0.001454 | 8.9956e-06
2017 | 2017-01-04 | C | 164 | 0.025817 | 0.00049176
2017 | 2017-01-04 | C | 50 | 0.026804 | 0.00014993
2017 | 2017-01-04 | C | 1 | 0.00026 | 2.9985e-06
2017 | 2017-01-04 | C | 7 | 0.001815 | 2.0989e-05
2017 | 2017-01-04 | C | 1 | 0.000463 | 2.9985e-06
2017 | 2017-01-04 | C | 68 | 0.016655 | 0.0002039
2017 | 2017-01-04 | C | 4 | 0.002898 | 1.1994e-05
2017 | 2017-01-05 | C | 29 | 0.045027 | 8.6955e-05
2017 | 2017-01-05 | C | 250 | 0.092863 | 0.00074962
2017 | 2017-01-05 | C | 420 | 0.23531 | 0.0015352
2017 | 2017-01-05 | C | 14 | 0.00193 | 4.1978e-05
2017 | 2017-01-05 | C | 95 | 0.050874 | 0.00028485
2017 | 2017-01-05 | C | 1 | 0.000179 | 2.9984e-06
2017 | 2017-01-05 | C | 17 | 0.00474 | 5.0974e-05
2017 | 2017-01-05 | C | 422 | 0.033082 | 0.0013133
2017 | 2017-01-05 | C | 2 | 0.000775 | 5.9969e-06
2017 | 2017-01-05 | C | 44 | 0.003502 | 0.00013193
2017 | 2017-01-05 | C | 6 | 0.00277 | 1.7991e-05
2017 | 2017-01-06 | C | 4 | 0.001522 | 1.1994e-05
2017 | 2017-01-06 | C | 1142 | 0.22676 | 0.0034242
2017 | 2017-01-06 | C | 2 | 0.000346 | 5.9968e-06
2017 | 2017-01-06 | C | 241 | 0.033312 | 0.00072262
2017 | 2017-01-06 | C | 7 | 0.002046 | 2.0989e-05
2017 | 2017-01-07 | C | 19 | 0.002335 | 5.6969e-05
2017 | 2017-01-07 | C | 1 | 0.000275 | 2.9983e-06
2017 | 2017-01-07 | C | 7 | 0.001737 | 2.0989e-05
2017 | 2017-01-07 | C | 9 | 0.002153 | 2.6985e-05
2017 | 2017-01-08 | C | 954 | 0.16385 | 0.0028604
2017 | 2017-01-08 | C | 1 | 0.000575 | 2.9983e-06
2017 | 2017-01-08 | C | 21 | 0.00617 | 6.2965e-05
2017 | 2017-01-08 | C | 1 | 0.00016 | 2.9983e-06
2017 | 2017-01-08 | C | 297 | 0.10926 | 0.00089051
2017 | 2017-01-09 | C | 135 | 0.024301 | 0.00080954
2017 | 2017-01-09 | C | 11 | 0.002657 | 3.2981e-05
2017 | 2017-01-19 | B | 43 | 0.01057 | 0.00012891
2017 | 2017-01-26 | B | 3 | 0.003318 | 8.9926e-06
2017 | 2017-02-01 | B | 39 | 0.043134 | 0.00011689
2017 | 2017-01-25 | B | 7 | 0.006441 | 2.0983e-05
2017 | 2017-02-03 | B | 5 | 0.006024 | 1.4986e-05
2017 | 2017-01-24 | B | 109 | 0.04313 | 0.00032674
2017 | 2017-02-08 | B | 5 | 0.002382 | 1.4985e-05
2017 | 2017-02-08 | B | 3 | 0.001456 | 8.991e-06
2017 | 2017-01-09 | C | 106 | 0.019614 | 0.00031782
2017 | 2017-02-08 | B | 2 | 0.000971 | 5.994e-06
2017 | 2017-02-08 | B | 7 | 0.002874 | 2.0979e-05
2017 | 2017-02-09 | B | 4 | 0.001762 | 1.1988e-05
2017 | 2017-02-09 | B | 2 | 0.000791 | 5.9939e-06
2017 | 2017-02-09 | B | 5 | 0.001843 | 1.4985e-05
2017 | 2017-02-09 | B | 2 | 0.000971 | 5.9939e-06
2017 | 2017-01-09 | C | 1 | 0.000314 | 2.9982e-06
2017 | 2017-02-10 | B | 3 | 0.000647 | 8.9907e-06
2017 | 2017-02-10 | B | 3 | 0.001051 | 8.9907e-06
2017 | 2017-02-10 | B | 3 | 0.001366 | 8.9907e-06
2017 | 2017-01-09 | C | 11 | 0.002652 | 3.2981e-05
2017 | 2017-02-09 | B | 21 | 0.012585 | 6.2936e-05
2017 | 2017-02-14 | B | 64 | 0.023896 | 0.00019179
2017 | 2017-01-09 | C | 6 | 0.002407 | 1.799e-05
2017 | 2017-02-15 | B | 74 | 0.049083 | 0.00022176
2017 | 2017-02-16 | B | 33 | 0.01231 | 9.889e-05
2017 | 2017-02-08 | B | 11 | 0.014208 | 3.2967e-05
2017 | 2017-01-10 | B | 62 | 0.01989 | 0.00018589
2017 | 2017-01-09 | C | 25 | 0.014316 | 7.4957e-05
2017 | 2017-02-14 | B | 2 | 0.000251 | 5.9934e-06
2017 | 2017-01-09 | C | 83 | 0.038379 | 0.00036879
2017 | 2017-02-15 | B | 3 | 0.001905 | 8.9901e-06
2017 | 2017-01-09 | C | 247 | 0.029623 | 0.00074058
2017 | 2017-02-09 | B | 20 | 0.021518 | 5.9939e-05
2017 | 2017-01-09 | C | 1 | 0.000564 | 2.9982e-06
2017 | 2017-01-09 | C | 661 | 0.058714 | 0.0031452
2017 | 2017-01-10 | C | 688 | 0.21765 | 0.0020628
2017 | 2017-01-10 | C | 2 | 0.012646 | 1.1993e-05
2017 | 2017-02-15 | B | 2 | 0.001081 | 5.9934e-06
2017 | 2017-02-15 | B | 6 | 0.000485 | 1.798e-05
2017 | 2017-01-26 | B | 4 | 0.003093 | 1.199e-05
2017 | 2017-02-22 | B | 6 | 0.003811 | 1.7978e-05
2017 | 2017-01-10 | C | 1 | 0.000416 | 2.9982e-06
2017 | 2017-01-10 | C | 2 | 0.000802 | 5.9964e-06
2017 | 2017-02-12 | B | 1 | 0.000776 | 2.9968e-06
2017 | 2017-02-15 | B | 16 | 0.015524 | 4.7947e-05
2017 | 2017-01-10 | C | 128 | 0.017205 | 0.00038378
2017 | 2017-01-10 | C | 761 | 0.099494 | 0.0023566
2017 | 2017-01-31 | B | 60 | 0.045941 | 0.00035069
2017 | 2017-02-13 | B | 8 | 0.006568 | 2.3974e-05
2017 | 2017-01-10 | C | 38 | 0.004575 | 0.00011393
2017 | 2017-01-10 | C | 83 | 0.027589 | 0.00024885
2017 | 2017-01-10 | C | 43 | 0.010829 | 0.00012892
2017 | 2017-01-11 | C | 7 | 0.006233 | 2.0987e-05
2017 | 2017-02-01 | B | 39 | 0.00865 | 0.00011689
2017 | 2017-01-11 | C | 858 | 0 | 0.0025725
2017 | 2017-02-07 | B | 35 | 0.005454 | 0.0001049
2017 | 2017-02-14 | B | 91 | 0.026529 | 0.0002727
2017 | 2017-01-11 | C | 310 | 0 | 0.00092945
2017 | 2017-01-30 | B | 26 | 0.03203 | 7.7932e-05
2017 | 2017-01-11 | C | 35 | 0.007555 | 0.00010494
2017 | 2017-02-02 | B | 2 | 0.002349 | 5.9945e-06
2017 | 2017-01-11 | C | 1 | 0.000482 | 2.9982e-06
2017 | 2017-01-11 | C | 225 | 0.03293 | 0.00098641
2017 | 2017-01-11 | C | 175 | 0.03194 | 0.00023086
2017 | 2017-01-11 | C | 6 | 0.002015 | 1.7989e-05
2017 | 2017-01-12 | C | 15 | 0.00688 | 0.00013492
2017 | 2017-01-12 | C | 6 | 0.002504 | 1.7989e-05
2017 | 2017-01-12 | C | 104 | 0.020783 | 0.00031181
2017 | 2017-01-12 | C | 4 | 0.002198 | 1.1993e-05
2017 | 2017-02-19 | B | 46 | 0.034322 | 0.00013784
2017 | 2017-01-12 | C | 98 | 0.027649 | 0.00085448
2017 | 2017-01-12 | C | 1 | 0.000772 | 2.9981e-06
2017 | 2017-01-12 | C | 1 | 0.000531 | 2.9981e-06
2017 | 2017-01-12 | C | 42 | 0.009219 | 0.00012592
2017 | 2017-01-12 | C | 62 | 0.029934 | 0.00018589
2017 | 2017-01-12 | C | 58 | 0.023469 | 0.00017389
2017 | 2017-01-13 | C | 42 | 0.010325 | 0.00012592
2017 | 2017-01-14 | B | 5 | 0.004392 | 1.499e-05
2017 | 2017-01-13 | C | 124 | 0.030988 | 0.00037177
2017 | 2017-01-13 | C | 1 | 0.00044 | 2.9981e-06
2017 | 2017-01-13 | C | 586 | 0.084879 | 0.00085746
2017 | 2017-01-13 | C | 2 | 0.000259 | 5.9962e-06
2017 | 2017-01-13 | C | 3 | 0.0025 | 8.9943e-06
2017 | 2017-02-14 | B | 90 | 0.083339 | 0.00026971
2017 | 2017-02-02 | B | 6 | 0.005143 | 1.7984e-05
2017 | 2017-02-02 | B | 6 | 0.005574 | 1.7984e-05
2017 | 2017-01-13 | C | 102 | 0 | 0.00030581
2017 | 2017-01-13 | C | 25 | 0.008041 | 7.4953e-05
2017 | 2017-01-14 | C | 1 | 1e-05 | 2.998e-06
2017 | 2017-01-14 | C | 23 | 0.002827 | 6.8956e-05
2017 | 2017-01-14 | C | 202 | 0.033849 | 0.00060561
2017 | 2017-01-14 | C | 1 | 0.002301 | 5.9961e-06
2017 | 2017-01-15 | C | 15 | 0.002847 | 4.497e-05
2017 | 2017-02-01 | B | 275 | 0.32641 | 0.00082426
2017 | 2017-02-08 | B | 166 | 0.18842 | 0.0004975
2017 | 2017-02-07 | B | 18 | 0.018426 | 5.3947e-05
2017 | 2017-02-28 | B | 18 | 0.016556 | 5.393e-05
2017 | 2017-01-15 | C | 2686 | 0.29882 | 0.0080497
2017 | 2017-02-07 | B | 3 | 0.002217 | 8.9911e-06
2017 | 2017-01-15 | C | 51 | 0.000945 | 0.0001529
2017 | 2017-01-15 | C | 85 | 0.01111 | 0.00025483
2017 | 2017-01-15 | C | 213 | 0.038959 | 0.00063858
2017 | 2017-01-15 | C | 1 | 4.1e-05 | 2.998e-06
2017 | 2017-01-15 | C | 1038 | 0.15601 | 0.003112
2017 | 2017-01-15 | C | 181 | 0.071086 | 0.00054264
2017 | 2017-01-15 | C | 10 | 0.002664 | 2.998e-05
2017 | 2017-02-02 | B | 21 | 0.011746 | 0.00010191
2017 | 2017-01-14 | C | 1 | 0.000229 | 2.998e-06
2017 | 2017-01-15 | C | 4 | 0.001668 | 1.1992e-05
2017 | 2017-01-16 | C | 5605 | 0.97114 | 0.01681
2017 | 2017-01-16 | C | 111 | 0.02315 | 0.00033278
2017 | 2017-01-16 | C | 1 | 0.000573 | 2.9979e-06
2017 | 2017-01-16 | C | 1 | 0.000754 | 2.9979e-06
2017 | 2017-01-28 | B | 45 | 0.042265 | 0.00020683
2017 | 2017-01-27 | B | 7 | 0.004115 | 2.0983e-05
2017 | 2017-01-16 | C | 1 | 3.2e-05 | 2.9979e-06
2017 | 2017-02-03 | B | 38 | 0.013642 | 0.00011389
2017 | 2017-01-17 | C | 288 | 0.060044 | 0.00086341
2017 | 2017-01-17 | C | 453 | 0.097616 | 0.0013581
2017 | 2017-01-17 | C | 10 | 0.003469 | 2.9979e-05
2017 | 2017-01-17 | C | 1 | 0.000173 | 2.9979e-06
2017 | 2017-01-17 | C | 111 | 0.063082 | 0.00033277
2017 | 2017-01-17 | C | 4 | 0.000816 | 1.1992e-05
2017 | 2017-01-17 | C | 10 | 0.001655 | 2.9979e-05
2017 | 2017-01-18 | C | 1 | 0.0003 | 2.9979e-06
2017 | 2017-02-03 | B | 4 | 0.001354 | 1.1989e-05
2017 | 2017-02-03 | B | 3 | 0.000728 | 8.9916e-06
2017 | 2017-01-18 | C | 2 | 0.000413 | 5.9958e-06
2017 | 2017-01-18 | C | 2 | 0.000609 | 5.9958e-06
2017 | 2017-01-18 | C | 55 | 0.002803 | 0.00016488
2017 | 2017-01-18 | C | 6 | 0.002109 | 1.7987e-05
2017 | 2017-01-19 | C | 5 | 0.001673 | 1.4989e-05
2017 | 2017-01-19 | C | 1139 | 0.12585 | 0.0034146
2017 | 2017-01-19 | C | 6 | 0.002393 | 1.7987e-05
2017 | 2017-02-07 | B | 24 | 0.021537 | 7.1929e-05
2017 | 2017-01-19 | C | 174 | 0.024133 | 0.00052163
2017 | 2017-02-07 | B | 7 | 0.006121 | 2.0979e-05
2017 | 2017-01-19 | C | 4 | 0.001397 | 1.1991e-05
2017 | 2017-01-19 | C | 7 | 0.013168 | 2.0985e-05
2017 | 2017-01-19 | C | 4 | 0.003438 | 2.0985e-05
2017 | 2017-01-19 | C | 149 | 0.026113 | 0.00044668
2017 | 2017-01-19 | C | 5 | 0.00235 | 1.4989e-05
2017 | 2017-01-19 | C | 100 | 0.062776 | 0.00029979
2017 | 2017-01-19 | C | 129 | 0.038605 | 0.00044968
2017 | 2017-01-19 | C | 3 | 0.002224 | 8.9935e-06
2017 | 2017-01-19 | C | 3 | 0.002917 | 8.9935e-06
2017 | 2017-01-19 | C | 5 | 0.001064 | 1.4989e-05
2017 | 2017-01-19 | C | 56 | 0.003693 | 0.00016788
2017 | 2017-01-19 | C | 6 | 0.000809 | 1.7987e-05
2017 | 2017-01-19 | C | 230 | 0.10218 | 0.00094133
2017 | 2017-01-19 | C | 10 | 0.006835 | 2.9979e-05
2017 | 2017-01-19 | C | 737 | 0.26836 | 0.0040981
2017 | 2017-01-19 | C | 31 | 0.003159 | 9.2934e-05
2017 | 2017-01-19 | C | 6 | 0.003219 | 1.7987e-05
2017 | 2017-01-19 | C | 2 | 0.000969 | 5.9957e-06
2017 | 2017-01-19 | C | 52 | 0.032901 | 0.00015589
2017 | 2017-01-19 | C | 117 | 0.028358 | 0.00035075
2017 | 2017-01-19 | C | 7 | 0.003168 | 2.0985e-05
2017 | 2017-01-19 | C | 186 | 0.07444 | 0.0005576
2017 | 2017-01-19 | C | 1 | 0.003811 | 2.9978e-06
2017 | 2017-01-19 | C | 27 | 0.003804 | 8.0942e-05
2017 | 2017-01-19 | C | 93 | 0.012546 | 0.0002788
2017 | 2017-01-19 | C | 9 | 0.002662 | 2.6981e-05
2017 | 2017-01-20 | C | 11 | 0.00366 | 3.2976e-05
2017 | 2017-01-19 | C | 76 | 0.050522 | 0.00060557
2017 | 2017-01-19 | C | 20 | 0.007299 | 5.9957e-05
2017 | 2017-01-19 | C | 1047 | 0.68322 | 0.0031388
2017 | 2017-01-19 | C | 2 | 0.000425 | 5.9957e-06
2017 | 2017-01-20 | C | 420 | 0.22982 | 0.0025182
2017 | 2017-01-19 | C | 4 | 0.001846 | 1.1991e-05
2017 | 2017-01-20 | C | 43 | 0.004898 | 0.00012891
2017 | 2017-01-20 | C | 9 | 0.006155 | 2.698e-05
2017 | 2017-02-09 | B | 7 | 0.004615 | 2.0979e-05
2017 | 2017-02-14 | B | 4 | 0.004327 | 1.1987e-05
2017 | 2017-02-10 | B | 4 | 0.004219 | 1.1988e-05
2017 | 2017-02-15 | B | 15 | 0.016541 | 4.4951e-05
2017 | 2017-01-20 | C | 755 | 0.11407 | 0.0022634
2017 | 2017-01-20 | C | 357 | 0.044485 | 0.0010702
2017 | 2017-01-20 | C | 3 | 0.001627 | 8.9934e-06
2017 | 2017-01-21 | C | 334 | 0.056817 | 0.0010013
2017 | 2017-01-21 | C | 1 | 0.00065 | 2.9977e-06
2017 | 2017-01-21 | C | 34 | 0.022452 | 0.00010192
2017 | 2017-01-21 | C | 20 | 0.009472 | 5.9956e-05
2017 | 2017-01-21 | C | 15 | 0.02078 | 4.4967e-05
2017 | 2017-01-21 | C | 11613 | 1.0859 | 0.034813
2017 | 2017-01-21 | C | 400 | 0.25425 | 0.0011991
2017 | 2017-01-22 | C | 171 | 0.078429 | 0.00051261
2017 | 2017-01-21 | C | 894 | 0.10091 | 0.00268
2017 | 2017-01-21 | C | 841 | 0.12806 | 0.0025211
2017 | 2017-01-21 | C | 113 | 0.13026 | 0.00033875
2017 | 2017-01-22 | C | 13 | 0.007807 | 3.8971e-05
2017 | 2017-01-22 | C | 240 | 0.10069 | 0.0014149
2017 | 2017-01-22 | C | 772 | 0.47125 | 0.0023143
2017 | 2017-01-22 | C | 874 | 0.15099 | 0.00043467
2017 | 2017-01-22 | C | 87 | 0.14687 | 0.0002608
2017 | 2017-01-22 | C | 208 | 0.41725 | 0.00062353
2017 | 2017-01-22 | C | 119 | 0.061274 | 0.0006595
2017 | 2017-01-22 | C | 213 | 0.38151 | 0.00067449
2017 | 2017-01-22 | C | 812 | 0.36681 | 0.0027759
2017 | 2017-01-22 | C | 3 | 0.00246 | 8.9932e-06
2017 | 2017-01-22 | C | 14 | 0.018843 | 4.1968e-05
2017 | 2017-01-22 | C | 159 | 0.006315 | 0.00047664
2017 | 2017-01-22 | C | 241 | 0.25945 | 0.0020714
2017 | 2017-01-22 | C | 2 | 0.002321 | 5.9954e-06
2017 | 2017-01-22 | C | 1462 | 0.99622 | 0.0043827
2017 | 2017-01-22 | C | 307 | 0.4205 | 0.00092031
2017 | 2017-01-22 | C | 161 | 0.2312 | 0.00068648
2017 | 2017-01-22 | C | 271 | 0.23563 | 0.00081239
2017 | 2017-01-22 | C | 4 | 0.002074 | 1.1991e-05
2017 | 2017-01-22 | C | 685 | 0.58333 | 0.0020534
2017 | 2017-01-22 | C | 2 | 0.00194 | 5.9954e-06
2017 | 2017-01-22 | C | 42 | 0.082132 | 0.0001259
2017 | 2017-01-22 | C | 2 | 0.002132 | 5.9954e-06
2017 | 2017-01-22 | C | 42 | 0.03135 | 0.0001259
2017 | 2017-01-22 | C | 21 | 0.064791 | 6.2952e-05
2017 | 2017-01-22 | C | 741 | 0.11155 | 0.0022213
2017 | 2017-01-22 | C | 3 | 0.015998 | 8.9932e-06
2017 | 2017-01-22 | C | 1 | 0.000695 | 2.9977e-06
2017 | 2017-01-22 | C | 169 | 0.047249 | 0.00050662
2017 | 2017-01-22 | C | 129 | 0.03309 | 0.00038671
2017 | 2017-01-22 | C | 22 | 0.009035 | 6.595e-05
2017 | 2017-01-22 | C | 43 | 0.001136 | 0.0001289
2017 | 2017-01-22 | C | 2 | 0.001782 | 5.9954e-06
2017 | 2017-01-22 | C | 11 | 0.003493 | 3.2975e-05
2017 | 2017-01-22 | C | 8 | 0.010469 | 2.3982e-05
2017 | 2017-01-22 | C | 41 | 0.007251 | 0.00012291
2017 | 2017-01-22 | C | 8 | 0.009452 | 2.3982e-05
2017 | 2017-01-22 | C | 147 | 0.32868 | 0.00044067
2017 | 2017-01-22 | C | 7 | 0.010905 | 2.0984e-05
2017 | 2017-01-22 | C | 32 | 0.186 | 9.5927e-05
2017 | 2017-01-22 | C | 3 | 0.003938 | 8.9932e-06
2017 | 2017-01-22 | C | 68 | 0.12029 | 0.00020385
2017 | 2017-01-22 | C | 2 | 0.001152 | 5.9954e-06
2017 | 2017-01-22 | C | 1029 | 0.50153 | 0.0040859
2017 | 2017-01-22 | C | 682 | 0.58667 | 0.007983
2017 | 2017-01-22 | C | 92 | 0.054271 | 0.00029678
2017 | 2017-01-22 | C | 214 | 0.12339 | 0.001265
2017 | 2017-01-22 | C | 1079 | 0.060843 | 0.0034774
2017 | 2017-01-22 | C | 92 | 0.015995 | 0.00027579
2017 | 2017-01-22 | C | 70 | 0.002203 | 0.00020984
2017 | 2017-01-22 | C | 114 | 0.043403 | 0.00084536
2017 | 2017-01-22 | C | 6 | 0.000935 | 1.7986e-05
2017 | 2017-01-22 | C | 19 | 0.002262 | 5.6957e-05
2017 | 2017-01-22 | C | 31 | 0.02714 | 9.293e-05
2017 | 2017-01-22 | C | 6 | 0.019659 | 1.7986e-05
2017 | 2017-01-22 | C | 84 | 0.019284 | 0.00025181
2017 | 2017-01-22 | C | 5 | 0.004855 | 1.4989e-05
2017 | 2017-01-22 | C | 2 | 0.002915 | 5.9954e-06
2017 | 2017-01-22 | C | 27 | 0.10289 | 8.0939e-05
2017 | 2017-01-22 | C | 12 | 0.014233 | 3.5973e-05
2017 | 2017-01-22 | C | 1 | 0.00419 | 2.9977e-06
2017 | 2017-01-22 | C | 230 | 0.066179 | 0.00085435
2017 | 2017-01-22 | C | 5 | 0.021657 | 1.4989e-05
2017 | 2017-01-23 | C | 107 | 0.048775 | 0.00032075
2017 | 2017-01-22 | C | 1 | 0.000875 | 2.9977e-06
2017 | 2017-01-22 | C | 4 | 0.009189 | 1.1991e-05
2017 | 2017-01-22 | C | 18 | 0.02194 | 5.3959e-05
2017 | 2017-01-22 | C | 1 | 0.000384 | 2.9977e-06
2017 | 2017-01-23 | C | 2 | 0.000521 | 5.9953e-06
2017 | 2017-01-22 | C | 6 | 0.001086 | 1.7986e-05
2017 | 2017-01-22 | C | 35 | 0.1088 | 0.00010492
2017 | 2017-01-22 | C | 2 | 0.005515 | 5.9954e-06
2017 | 2017-01-22 | C | 130 | 0.12138 | 0.00077941
2017 | 2017-01-22 | C | 49 | 0.001615 | 0.00014689
2017 | 2017-01-22 | C | 302 | 0.055013 | 0.00090532
2017 | 2017-01-22 | C | 65 | 0.079866 | 0.00022483
2017 | 2017-01-23 | C | 2 | 0.004636 | 5.9953e-06
2017 | 2017-01-23 | C | 830 | 0.11152 | 0.0024881
2017 | 2017-01-22 | C | 4 | 0.004004 | 1.1991e-05
2017 | 2017-01-23 | C | 1 | 0.001166 | 2.9976e-06
2017 | 2017-01-23 | C | 7 | 0.003684 | 2.0984e-05
2017 | 2017-01-23 | C | 11 | 0.011297 | 3.2975e-05
2017 | 2017-01-23 | C | 2 | 0.002162 | 5.9953e-06
2017 | 2017-01-23 | C | 830 | 0.23995 | 0.0024881
2017 | 2017-01-23 | C | 685 | 0.059711 | 0.0020954
2017 | 2017-01-23 | C | 74 | 0.039534 | 0.00022183
2017 | 2017-01-22 | C | 14 | 0.040852 | 4.1968e-05
2017 | 2017-01-23 | C | 1 | 0.001018 | 2.9976e-06
2017 | 2017-01-23 | C | 35 | 0.01984 | 0.00010492
2017 | 2017-01-23 | C | 112 | 0.054675 | 0.00033574
2017 | 2017-01-23 | C | 3 | 0.003125 | 8.993e-06
2017 | 2017-01-23 | C | 17 | 0.007987 | 5.0961e-05
2017 | 2017-02-22 | B | 149 | 0.00047 | 5.9927e-06
2017 | 2017-02-14 | B | 9 | 0.009277 | 2.6971e-05
2017 | 2017-01-23 | C | 6 | 0.027726 | 1.7986e-05
2017 | 2017-02-09 | B | 3 | 0.002841 | 8.9908e-06
2017 | 2017-02-01 | B | 46 | 0.029091 | 0.00013788
2017 | 2017-02-09 | B | 3 | 0.002895 | 8.9908e-06
2017 | 2017-01-23 | C | 406 | 0.10469 | 0.0012171
2017 | 2017-01-23 | C | 1 | 0.000617 | 2.9976e-06
2017 | 2017-01-23 | C | 1 | 0.000179 | 2.9976e-06
2017 | 2017-01-23 | C | 1204 | 0.32542 | 0.0036092
2017 | 2017-02-09 | B | 24 | 0.015104 | 7.1927e-05
2017 | 2017-02-13 | B | 24 | 0.023734 | 7.1923e-05
2017 | 2017-02-21 | B | 24 | 0.024163 | 7.1915e-05
2017 | 2017-02-23 | B | 24 | 0.025888 | 7.1912e-05
2017 | 2017-02-28 | B | 24 | 0.02567 | 7.1907e-05
2017 | 2017-01-23 | C | 1 | 0.000812 | 2.9976e-06
2017 | 2017-01-23 | C | 3 | 0.000485 | 8.993e-06
2017 | 2017-01-23 | C | 30 | 0.001888 | 8.9931e-05
2017 | 2017-01-23 | C | 14 | 0.00986 | 4.1968e-05
2017 | 2017-01-23 | C | 4 | 0.001618 | 1.1991e-05
2017 | 2017-01-23 | C | 316 | 0.1171 | 0.00094727
2017 | 2017-01-24 | C | 66 | 0.009625 | 0.00019784
2017 | 2017-01-23 | C | 4 | 0.001666 | 1.1991e-05
2017 | 2017-01-24 | C | 10 | 0.003356 | 2.9976e-05
2017 | 2017-01-26 | B | 108 | 0.036906 | 0.00032374
2017 | 2017-01-24 | C | 39 | 0.0083 | 0.00011691
2017 | 2017-02-10 | B | 13 | 0.011454 | 3.896e-05
2017 | 2017-01-24 | C | 10 | 0.006624 | 2.9976e-05
2017 | 2017-01-27 | B | 3 | 0.003 | 8.9925e-06
2017 | 2017-01-24 | C | 1 | 0.000627 | 2.9976e-06
2017 | 2017-02-13 | B | 2 | 0.001012 | 5.9935e-06
2017 | 2017-01-25 | C | 10 | 0.003524 | 2.9976e-05
2017 | 2017-02-14 | B | 18 | 0.02163 | 5.3941e-05
2017 | 2017-01-25 | C | 254 | 0.009352 | 0.00076139
2017 | 2017-01-25 | C | 130 | 0.038449 | 0.00038969
2017 | 2017-01-25 | C | 241 | 0.04102 | 0.00072242
2017 | 2017-02-08 | B | 12 | 0.000539 | 7.1928e-05
2017 | 2017-01-25 | C | 2 | 0.000867 | 5.9952e-06
2017 | 2017-01-25 | C | 231 | 0.060627 | 0.00069245
2017 | 2017-02-24 | B | 1 | 0.00029 | 2.9963e-06
2017 | 2017-01-25 | C | 10 | 0.002419 | 2.9976e-05
2017 | 2017-01-25 | C | 238 | 0.011224 | 0.00071343
2017 | 2017-01-25 | C | 1 | 0.000413 | 2.9976e-06
2017 | 2017-01-25 | C | 241 | 0.060677 | 0.00072242
2017 | 2017-01-25 | C | 830 | 0.12382 | 0.002488
2017 | 2017-01-26 | B | 34 | 0.033428 | 0.00010192
2017 | 2017-01-25 | C | 111 | 0.021724 | 0.00044964
2017 | 2017-01-25 | C | 44 | 0.035906 | 0.00013189
2017 | 2017-01-25 | C | 357 | 0.081449 | 0.0010701
2017 | 2017-01-25 | C | 830 | 0.10274 | 0.002488
2017 | 2017-01-25 | C | 10 | 0.003181 | 2.9976e-05
2017 | 2017-01-25 | C | 6 | 0.0309 | 1.7986e-05
2017 | 2017-01-26 | C | 5 | 0.002042 | 1.4988e-05
2017 | 2017-02-16 | B | 4 | 0.004099 | 1.1987e-05
2017 | 2017-02-17 | B | 15 | 0.016046 | 4.4949e-05
2017 | 2017-02-24 | B | 15 | 0.014607 | 4.4945e-05
2017 | 2017-01-26 | C | 47 | 0.012565 | 0.00014089
2017 | 2017-02-09 | B | 10 | 0.011957 | 2.997e-05
2017 | 2017-01-26 | C | 14 | 0.004406 | 4.1966e-05
2017 | 2017-01-26 | C | 1 | 0.000423 | 2.9975e-06
2017 | 2017-02-22 | B | 15 | 0.01627 | 4.4946e-05
2017 | 2017-02-16 | B | 22 | 0.01892 | 6.5926e-05
2017 | 2017-02-17 | B | 71 | 0.038464 | 0.00021276
2017 | 2017-02-20 | B | 3 | 0.003389 | 8.9894e-06
2017 | 2017-01-27 | C | 563 | 0.056816 | 0.0016876
2017 | 2017-01-27 | C | 120 | 0.092039 | 0.0004796
2017 | 2017-01-27 | C | 3003 | 0.10732 | 0.0090016
2017 | 2017-02-14 | B | 5 | 0.00388 | 1.4984e-05
2017 | 2017-02-15 | B | 10 | 0.004729 | 5.9934e-05
2017 | 2017-01-27 | C | 218 | 0.021712 | 0.00065346
2017 | 2017-02-15 | B | 54 | 0.00469 | 0.00032364
2017 | 2017-01-27 | C | 11 | 0.006924 | 3.2973e-05
2017 | 2017-02-15 | B | 1 | 0.000806 | 2.9967e-06
2017 | 2017-01-27 | C | 316 | 0.066658 | 0.00094722
2017 | 2017-01-27 | C | 57 | 0.008885 | 0.00017086
2017 | 2017-01-27 | C | 4 | 0.001429 | 1.199e-05
2017 | 2017-01-27 | C | 10 | 0.00446 | 5.6953e-05
2017 | 2017-01-28 | C | 361 | 0.056713 | 0.0010821
2017 | 2017-01-28 | C | 24 | 0.019639 | 7.1939e-05
2017 | 2017-01-28 | C | 24 | 0.00442 | 7.1939e-05
2017 | 2017-01-28 | C | 75 | 0.018127 | 0.00022481
2017 | 2017-01-29 | C | 1047 | 0.60553 | 0.0031383
2017 | 2017-01-29 | C | 1 | 0.00027 | 2.9974e-06
2017 | 2017-01-29 | C | 1 | 0.000259 | 2.9974e-06
2017 | 2017-01-29 | C | 7 | 0.001154 | 2.0982e-05
2017 | 2017-01-29 | C | 53 | 0.038235 | 0.00015886
2017 | 2017-01-29 | C | 1040 | 0.015925 | 0.00071938
2017 | 2017-01-30 | C | 241 | 0.034427 | 0.00072237
2017 | 2017-02-20 | B | 46 | 0.035286 | 0.00013784
2017 | 2017-02-21 | B | 31 | 0.031396 | 9.289e-05
2017 | 2017-01-30 | C | 1094 | 0.049702 | 0.0014597
2017 | 2017-02-24 | B | 6 | 0.002462 | 1.7978e-05
2017 | 2017-01-30 | C | 241 | 0.047656 | 0.00072237
2017 | 2017-01-30 | C | 31 | 0.007301 | 9.2919e-05
2017 | 2017-01-30 | C | 1 | 0.000326 | 2.9973e-06
2017 | 2017-02-02 | B | 35 | 0.03252 | 0.0001049
2017 | 2017-01-30 | C | 1 | 0.000329 | 2.9973e-06
2017 | 2017-01-31 | C | 254 | 0.048547 | 0.00076133
2017 | 2017-02-21 | B | 25 | 0.026818 | 7.4911e-05
2017 | 2017-01-31 | C | 65 | 0.006702 | 0.00019483
2017 | 2017-02-17 | B | 108 | 0.12075 | 0.00032363
2017 | 2017-01-31 | C | 447 | 0.15417 | 0.0013398
2017 | 2017-02-01 | B | 4 | 0.002913 | 1.1989e-05
2017 | 2017-02-23 | B | 25 | 0.02854 | 7.4909e-05
2017 | 2017-02-28 | B | 1 | 0.001054 | 2.9961e-06
2017 | 2017-02-16 | B | 4 | 0.003835 | 1.1987e-05
2017 | 2017-02-01 | B | 2 | 0.002182 | 5.9946e-06
2017 | 2017-01-31 | C | 81 | 0.020262 | 0.00024279
2017 | 2017-01-31 | C | 1 | 0.000338 | 2.9973e-06
2017 | 2017-01-31 | C | 2 | 0.000379 | 5.9947e-06
2017 | 2017-01-31 | C | 65 | 0.013391 | 0.00019483
2017 | 2017-02-01 | C | 12 | 0.004306 | 3.5968e-05
2017 | 2017-02-01 | C | 5622 | 0.17944 | 0.016851
2017 | 2017-02-01 | C | 69 | 0.011677 | 0.00020681
2017 | 2017-02-01 | B | 17 | 0.002343 | 5.0954e-05
2017 | 2017-02-01 | C | 1023 | 0.22505 | 0.0030662
2017 | 2017-02-12 | B | 196 | 0.15984 | 0.00058738
2017 | 2017-02-01 | C | 164 | 0.11296 | 0.00049156
2017 | 2017-02-21 | B | 90 | 0.087637 | 0.00026968
2017 | 2017-02-01 | C | 10 | 0.003178 | 2.9973e-05
2017 | 2017-02-01 | C | 112 | 0.015173 | 0.0003357
2017 | 2017-02-01 | C | 23 | 0.004894 | 6.8938e-05
2017 | 2017-02-01 | C | 40 | 0.019662 | 0.00011989
2017 | 2017-02-01 | C | 52 | 0.008572 | 0.00015586
2017 | 2017-02-22 | B | 111 | 0.12891 | 0.00033859
2017 | 2017-02-01 | C | 231 | 0.092881 | 0.0013158
2017 | 2017-02-01 | C | 95 | 0.007403 | 0.00028474
2017 | 2017-02-02 | C | 58 | 0.019817 | 0.00017384
2017 | 2017-02-02 | C | 3 | 0.000341 | 8.9917e-06
2017 | 2017-02-02 | C | 3 | 0.001481 | 8.9917e-06
2017 | 2017-03-02 | B | 28 | 0.010402 | 8.3889e-05
2017 | 2017-02-02 | C | 16 | 0.008459 | 5.3951e-05
2017 | 2017-02-02 | C | 186 | 0.047147 | 0.00097411
2017 | 2017-03-02 | B | 9 | 0.004044 | 2.6964e-05
2017 | 2017-02-03 | B | 65 | 0.056844 | 0.00019482
2017 | 2017-02-20 | B | 40 | 0.004416 | 0.00011986
2017 | 2017-02-21 | B | 7 | 0.007682 | 2.0975e-05
2017 | 2017-02-02 | C | 30 | 0.015221 | 8.9918e-05
2017 | 2017-02-02 | C | 166 | 0.026031 | 0.00049755
2017 | 2017-02-02 | C | 44 | 0.019518 | 0.00013188
2017 | 2017-02-22 | B | 79 | 0.076222 | 0.00023672
2017 | 2017-02-20 | B | 3 | 0.002714 | 8.9894e-06
2017 | 2017-02-02 | C | 1 | 0.000329 | 2.9972e-06
2017 | 2017-02-24 | B | 4 | 0.002732 | 1.1985e-05
2017 | 2017-02-02 | C | 166 | 0.027236 | 0.00049755
2017 | 2017-02-24 | B | 16 | 0.015197 | 4.7941e-05
2017 | 2017-02-02 | C | 34 | 0.004585 | 0.00010191
2017 | 2017-02-15 | B | 33 | 0.0271 | 9.8891e-05
2017 | 2017-02-03 | C | 2 | 0.000569 | 5.9944e-06
2017 | 2017-02-03 | B | 2 | 0.000701 | 5.9944e-06
2017 | 2017-02-02 | C | 120 | 0.03814 | 0.0012559
2017 | 2017-02-02 | C | 6 | 0.001871 | 1.7984e-05
2017 | 2017-02-02 | C | 1960 | 0.33059 | 0.0058746
2017 | 2017-02-02 | C | 46 | 0.045055 | 0.00013787
2017 | 2017-02-02 | C | 145 | 0.028922 | 0.0004346
2017 | 2017-02-02 | C | 166 | 0.078582 | 0.00049755
2017 | 2017-02-02 | C | 46 | 0.001748 | 0.00013787
2017 | 2017-02-02 | C | 10 | 0.004084 | 2.9973e-05
2017 | 2017-02-02 | C | 69 | 0.020362 | 0.00020681
2017 | 2017-02-03 | C | 83 | 0.044201 | 0.00046457
2017 | 2017-02-03 | C | 11 | 0.003329 | 3.2969e-05
2017 | 2017-02-03 | C | 10 | 0.000221 | 2.9972e-05
2017 | 2017-02-03 | C | 18 | 0.008684 | 5.395e-05
2017 | 2017-02-22 | B | 1 | 0.001609 | 2.9963e-06
2017 | 2017-02-25 | B | 1 | 0 | 2.9962e-06
2017 | 2017-02-04 | C | 3 | 0.001654 | 8.9915e-06
2017 | 2017-02-03 | C | 10 | 0.000606 | 2.9972e-05
2017 | 2017-02-04 | C | 12 | 0.001834 | 3.5966e-05
2017 | 2017-02-04 | C | 10 | 0.003343 | 2.9972e-05
2017 | 2017-02-04 | C | 1 | 0.000461 | 2.9971e-06
2017 | 2017-02-04 | C | 196 | 0.017848 | 0.00058745
2017 | 2017-02-04 | C | 1 | 0.000295 | 2.9971e-06
2017 | 2017-02-05 | C | 3004 | 0.033786 | 0.0090034
2017 | 2017-02-05 | C | 115 | 0.082171 | 0.00039262
2017 | 2017-02-05 | C | 1 | 0.00857 | 2.9971e-06
2017 | 2017-02-05 | C | 18 | 0.005608 | 5.3948e-05
2017 | 2017-02-05 | C | 4 | 0.001814 | 1.1989e-05
2017 | 2017-02-06 | C | 58 | 0.007127 | 0.00017383
2017 | 2017-02-06 | C | 43 | 0.013394 | 0.00012887
2017 | 2017-02-06 | C | 18 | 0.006456 | 5.3948e-05
2017 | 2017-02-06 | C | 1040 | 0.21521 | 0.0067405
2017 | 2017-02-06 | C | 10 | 0.001203 | 2.9971e-05
2017 | 2017-02-06 | C | 12 | 0.027765 | 3.5965e-05
2017 | 2017-02-06 | C | 106 | 0.067604 | 0.00055146
2017 | 2017-02-07 | C | 10 | 0.00923 | 2.997e-05
2017 | 2017-02-23 | B | 90 | 0.025888 | 0.00053934
2017 | 2017-02-21 | B | 27 | 0.032523 | 8.0904e-05
2017 | 2017-02-21 | B | 2 | 0.001743 | 5.9928e-06
2017 | 2017-02-22 | B | 13 | 0.010166 | 3.8953e-05
2017 | 2017-02-20 | B | 181 | 0.13307 | 0.00078208
2017 | 2017-02-08 | B | 64 | 0.039788 | 0.00038362
2017 | 2017-02-08 | C | 213 | 0.025064 | 0.00063836
2017 | 2017-02-08 | C | 213 | 0.059774 | 0.00063836
2017 | 2017-02-08 | C | 217 | 0.020269 | 0.00065035
2017 | 2017-02-23 | B | 21 | 0.00711 | 6.2923e-05
2017 | 2017-02-23 | B | 3 | 0.000647 | 8.989e-06
2017 | 2017-02-08 | C | 102 | 0.009113 | 0.00030569
2017 | 2017-02-23 | B | 6 | 0.00556 | 1.7978e-05
2017 | 2017-02-16 | B | 18 | 0.01735 | 5.394e-05
2017 | 2017-02-08 | C | 199 | 0.11152 | 0.0020709
2017 | 2017-02-08 | C | 844 | 0.25057 | 0.0072737
2017 | 2017-02-08 | C | 353 | 0.073198 | 0.0010579
2017 | 2017-02-09 | C | 239 | 0.033117 | 0.00071927
2017 | 2017-02-09 | C | 1034 | 0.29715 | 0.0030989
2017 | 2017-02-09 | C | 957 | 0.21219 | 0.0028681
2017 | 2017-02-25 | B | 9 | 0.004907 | 2.6966e-05
2017 | 2017-02-09 | C | 13 | 0.007784 | 3.896e-05
2017 | 2017-03-02 | B | 13 | 0.015774 | 3.8949e-05
2017 | 2017-03-01 | B | 2 | 0.00082 | 5.9921e-06
2017 | 2017-03-03 | B | 33 | 0.025606 | 9.8868e-05
2017 | 2017-02-24 | B | 122 | 0.074265 | 0.00036555
2017 | 2017-02-27 | B | 2 | 0.001971 | 5.9923e-06
2017 | 2017-02-09 | C | 35 | 0.004195 | 0.00010489
2017 | 2017-02-09 | C | 6 | 0.002983 | 1.7982e-05
2017 | 2017-03-03 | B | 19 | 0.002447 | 5.6924e-05
2017 | 2017-02-09 | C | 7 | 0.000419 | 2.0979e-05
2017 | 2017-02-09 | C | 3 | 8.9e-05 | 8.9908e-06
2017 | 2017-02-09 | C | 837 | 0.099946 | 0.0025085
2017 | 2017-02-09 | C | 1 | 0.000505 | 2.9969e-06
2017 | 2017-02-09 | C | 555 | 0.10532 | 0.0016633
2017 | 2017-03-01 | B | 15 | 0.015504 | 4.4941e-05
2017 | 2017-03-02 | B | 1 | 0.000949 | 2.996e-06
2017 | 2017-03-03 | B | 1 | 0.000428 | 2.9959e-06
2017 | 2017-03-03 | B | 1 | 0.000895 | 2.9959e-06
2017 | 2017-03-03 | B | 10 | 0.008238 | 2.996e-05
2017 | 2017-03-03 | B | 13 | 0.004128 | 3.8948e-05
2017 | 2017-03-04 | B | 1 | 0.000389 | 2.9959e-06
2017 | 2017-03-07 | B | 8 | 0.0052 | 2.3967e-05
2017 | 2017-03-07 | B | 2 | 0.00112 | 5.9916e-06
2017 | 2017-03-07 | B | 2 | 0.001731 | 5.9916e-06
2017 | 2017-03-09 | B | 1 | 0.000545 | 2.9957e-06
2017 | 2017-02-10 | C | 32 | 0.019314 | 9.5901e-05
2017 | 2017-03-03 | B | 22 | 0.004284 | 6.5912e-05
2017 | 2017-03-06 | B | 7 | 0.00741 | 2.0971e-05
2017 | 2017-03-07 | B | 33 | 0.034107 | 9.8862e-05
2017 | 2017-03-07 | B | 37 | 0.043118 | 0.00011085
2017 | 2017-02-15 | B | 19 | 0.018618 | 5.6937e-05
2017 | 2017-03-07 | B | 6 | 0.002804 | 1.7975e-05
2017 | 2017-02-10 | C | 256 | 0.0572 | 0.00076721
2017 | 2017-02-10 | C | 43 | 0.007732 | 0.00012887
2017 | 2017-02-11 | C | 149 | 0.001258 | 0.00044653
2017 | 2017-02-11 | C | 3 | 0.000647 | 8.9906e-06
2017 | 2017-02-11 | C | 36 | 0.002897 | 0.00010789
2017 | 2017-02-11 | C | 689 | 0.20235 | 0.0020648
2017 | 2017-02-11 | B | 10 | 0.003056 | 2.9969e-05
2017 | 2017-02-11 | C | 9 | 0.008199 | 2.6972e-05
2017 | 2017-03-17 | B | 4 | 0.003067 | 1.1981e-05
2017 | 2017-03-19 | B | 130 | 0.023752 | 0.00038938
2017 | 2017-03-15 | B | 64 | 0.068139 | 0.00019171
2017 | 2017-02-11 | C | 247 | 0.049123 | 0.0011718
2017 | 2017-02-12 | C | 3 | 0.002315 | 8.9904e-06
2017 | 2017-02-12 | C | 7 | 0.001794 | 2.0978e-05
2017 | 2017-02-12 | C | 111 | 0.02569 | 0.00033265
2017 | 2017-02-12 | C | 87 | 0.007039 | 0.00026072
2017 | 2017-02-13 | C | 1430 | 0.033222 | 0.00066529
2017 | 2017-02-13 | C | 10 | 0.001215 | 2.9968e-05
2017 | 2017-02-13 | C | 6 | 0.002173 | 1.7981e-05
2017 | 2017-02-16 | B | 24 | 0.027041 | 7.192e-05
2017 | 2017-02-13 | C | 29 | 0.019169 | 8.6907e-05
2017 | 2017-02-13 | C | 9 | 0.001294 | 2.6971e-05
2017 | 2017-02-13 | C | 302 | 0.052162 | 0.00090503
2017 | 2017-02-13 | C | 117 | 0.044637 | 0.00035062
2017 | 2017-02-13 | C | 13 | 0.008086 | 3.8958e-05
2017 | 2017-02-13 | C | 123 | 0.050372 | 0.0003686
2017 | 2017-02-13 | C | 398 | 0.20044 | 0.0011927
2017 | 2017-02-28 | B | 3 | 0.003074 | 8.9883e-06
2017 | 2017-02-13 | C | 183 | 0.047892 | 0.00054841
2017 | 2017-02-13 | C | 1343 | 0.20016 | 0.0063562
2017 | 2017-02-13 | C | 1343 | 0.13282 | 0.0042854
2017 | 2017-02-13 | C | 1 | 0.000338 | 2.9967e-06
2017 | 2017-02-13 | C | 480 | 0.058672 | 0.0014385
2017 | 2017-03-08 | B | 39 | 0.046149 | 0.00011684
2017 | 2017-03-10 | B | 15 | 0.015277 | 4.4935e-05
2017 | 2017-02-13 | C | 6 | 0.000665 | 1.7981e-05
2017 | 2017-02-13 | C | 2 | 0.000753 | 5.9935e-06
2017 | 2017-02-13 | C | 2 | 0.000365 | 5.9935e-06
2017 | 2017-02-13 | C | 4 | 0.006496 | 1.1987e-05
2017 | 2017-02-13 | C | 6 | 0.002662 | 1.7981e-05
2017 | 2017-02-13 | C | 44 | 0.018594 | 0.00013186
2017 | 2017-02-13 | C | 822 | 0.12119 | 0.0024634
2017 | 2017-02-13 | C | 38 | 0.009721 | 0.00011388
2017 | 2017-02-13 | C | 33 | 0.01233 | 9.8894e-05
2017 | 2017-02-13 | C | 4 | 0.003919 | 1.1987e-05
2017 | 2017-02-13 | C | 105 | 0.1655 | 0.00031466
2017 | 2017-02-14 | C | 68 | 0.014896 | 0.00020378
2017 | 2017-02-14 | C | 145 | 0.036649 | 0.00043453
2017 | 2017-02-14 | C | 15 | 0.00755 | 4.4951e-05
2017 | 2017-02-14 | C | 7 | 0.002244 | 2.0977e-05
2017 | 2017-03-15 | B | 2 | 0.002534 | 5.9908e-06
2017 | 2017-03-17 | B | 15 | 0.011142 | 4.493e-05
2017 | 2017-02-14 | C | 138 | 0.025789 | 0.00041355
2017 | 2017-03-21 | B | 15 | 0.014915 | 4.4927e-05
2017 | 2017-02-14 | C | 5 | 0.001902 | 1.4984e-05
2017 | 2017-03-28 | B | 46 | 0.042445 | 0.00013776
2017 | 2017-02-14 | C | 355 | 0.009574 | 0.0010638
2017 | 2017-03-09 | B | 14 | 0.011617 | 4.194e-05
2017 | 2017-02-14 | C | 446 | 0.14318 | 0.0013365
2017 | 2017-03-22 | B | 13 | 0.016353 | 3.8936e-05
2017 | 2017-02-14 | C | 58 | 0.01599 | 0.00017381
2017 | 2017-03-14 | B | 1 | 0.000608 | 2.9954e-06
2017 | 2017-03-14 | B | 13 | 0.014369 | 3.8941e-05
2017 | 2017-03-15 | B | 6 | 0.003617 | 1.7973e-05
2017 | 2017-03-01 | B | 60 | 0.045684 | 0.00017976
2017 | 2017-02-14 | C | 3 | 0.00105 | 8.9902e-06
2017 | 2017-03-10 | B | 3 | 0.002776 | 8.987e-06
2017 | 2017-03-17 | B | 10 | 0.009292 | 2.9953e-05
2017 | 2017-02-14 | C | 48 | 0.006041 | 0.00014384
2017 | 2017-02-14 | C | 191 | 0.10789 | 0.00057238
2017 | 2017-02-15 | C | 563 | 0.060765 | 0.0016871
2017 | 2017-02-15 | C | 1 | 0.000592 | 2.9967e-06
2017 | 2017-02-20 | B | 196 | 0.10958 | 0.00058731
2017 | 2017-03-01 | B | 200 | 0.1444 | 0.00059922
2017 | 2017-03-01 | B | 5 | 0.003308 | 1.498e-05
2017 | 2017-02-15 | C | 288 | 0.045602 | 0.00086305
2017 | 2017-03-02 | B | 93 | 0.043142 | 0.00027863
2017 | 2017-03-03 | B | 2 | 0.001605 | 5.9919e-06
2017 | 2017-02-15 | C | 6422 | 0.57018 | 0.019245
2017 | 2017-03-07 | B | 9 | 0.008816 | 2.6962e-05
2017 | 2017-03-09 | B | 9 | 0.009571 | 2.6961e-05
2017 | 2017-03-14 | B | 9 | 0.009678 | 2.6959e-05
2017 | 2017-03-16 | B | 9 | 0.009543 | 2.6959e-05
2017 | 2017-03-21 | B | 9 | 0.009758 | 2.6956e-05
2017 | 2017-03-23 | B | 9 | 0.009808 | 2.6956e-05
2017 | 2017-03-28 | B | 24 | 0.015956 | 7.1876e-05
2017 | 2017-02-15 | C | 3 | 0.000529 | 8.9901e-06
2017 | 2017-02-15 | C | 4 | 0 | 1.1987e-05
2017 | 2017-02-15 | C | 21 | 0.004841 | 6.2931e-05
2017 | 2017-02-15 | C | 40 | 0.004195 | 0.00011987
2017 | 2017-02-16 | C | 12 | 0.001051 | 3.596e-05
2017 | 2017-03-06 | B | 12 | 0.001581 | 3.595e-05
2017 | 2017-03-02 | B | 135 | 0.050962 | 0.00080893
2017 | 2017-02-16 | C | 138 | 0.019701 | 0.00041354
2017 | 2017-03-03 | B | 22 | 0.021157 | 6.5912e-05
2017 | 2017-02-16 | C | 1 | 0.000232 | 2.9966e-06
2017 | 2017-02-16 | C | 37 | 0.004732 | 0.00011088
2017 | 2017-02-16 | C | 292 | 0.028576 | 0.00087502
2017 | 2017-02-16 | C | 439 | 0.075948 | 0.00041354
2017 | 2017-02-16 | C | 1 | 0.000218 | 2.9966e-06
2017 | 2017-02-16 | C | 231 | 0.052832 | 0.0013245
2017 | 2017-02-17 | C | 231 | 0.20528 | 0.00090198
2017 | 2017-02-17 | C | 301 | 0.068654 | 0.00090198
2017 | 2017-03-15 | B | 5 | 0.003485 | 1.4977e-05
2017 | 2017-02-17 | C | 5 | 0.0014 | 1.4983e-05
2017 | 2017-02-17 | C | 86 | 0.03144 | 0.00025771
2017 | 2017-02-17 | C | 129 | 0.074567 | 0.00038656
2017 | 2017-02-21 | B | 10 | 0.012405 | 2.9964e-05
2017 | 2017-02-17 | C | 3 | 0.000854 | 8.9898e-06
2017 | 2017-02-17 | C | 1 | 0.000175 | 2.9966e-06
2017 | 2017-03-09 | B | 106 | 0.025086 | 0.00031755
2017 | 2017-02-17 | C | 136 | 0 | 0.00040754
2017 | 2017-03-19 | B | 4 | 0.002923 | 1.1981e-05
2017 | 2017-03-17 | B | 1 | 0.001 | 2.9953e-06
2017 | 2017-02-21 | B | 16 | 0.020136 | 4.7943e-05
2017 | 2017-02-17 | C | 2 | 0.001147 | 5.9932e-06
2017 | 2017-02-17 | C | 2 | 0.000606 | 5.9932e-06
2017 | 2017-02-17 | C | 1 | 0.000488 | 2.9966e-06
2017 | 2017-02-17 | C | 4 | 0.000619 | 1.1986e-05
2017 | 2017-02-17 | C | 2 | 0.000635 | 5.9932e-06
2017 | 2017-02-17 | C | 3 | 0.001561 | 8.9898e-06
2017 | 2017-02-17 | C | 114 | 0.095609 | 0.00058734
2017 | 2017-02-17 | C | 4 | 0.000425 | 1.1986e-05
2017 | 2017-02-17 | C | 204 | 0.015408 | 0.00061131
2017 | 2017-02-18 | C | 3 | 0.001345 | 8.9897e-06
2017 | 2017-02-18 | C | 1 | 0.001124 | 2.9965e-06
2017 | 2017-02-18 | C | 3 | 0.001645 | 8.9897e-06
2017 | 2017-02-18 | C | 1 | 0.000392 | 2.9965e-06
2017 | 2017-02-18 | C | 2 | 0.001613 | 5.9931e-06
2017 | 2017-02-18 | C | 4 | 0.00137 | 1.1986e-05
2017 | 2017-02-18 | C | 201 | 0.03046 | 0.00038656
2017 | 2017-02-18 | C | 218 | 0.039623 | 0.00065325
2017 | 2017-02-18 | C | 2 | 0.001447 | 5.9931e-06
2017 | 2017-02-18 | C | 1 | 0.000262 | 2.9965e-06
2017 | 2017-02-18 | C | 2 | 0.000466 | 5.9931e-06
2017 | 2017-02-18 | C | 2694 | 0.34925 | 0.0080728
2017 | 2017-02-18 | C | 1 | 0.000421 | 2.9965e-06
2017 | 2017-02-19 | C | 1760 | 0.026284 | 0.0031613
2017 | 2017-02-19 | C | 2 | 0.002044 | 5.993e-06
2017 | 2017-02-19 | C | 7 | 0.001908 | 2.0976e-05
2017 | 2017-02-19 | C | 1 | 0.000205 | 2.9965e-06
2017 | 2017-02-19 | C | 1 | 0.000338 | 2.9965e-06
2017 | 2017-02-19 | C | 1420 | 0.21052 | 0.0042551
2017 | 2017-02-19 | C | 1 | 0.000465 | 2.9965e-06
2017 | 2017-02-20 | C | 396 | 0.010829 | 0.0011866
2017 | 2017-02-20 | C | 6 | 0.006724 | 1.7979e-05
2017 | 2017-03-09 | B | 38 | 0.03715 | 0.00011384
2017 | 2017-02-20 | C | 7 | 4.1e-05 | 2.0975e-05
2017 | 2017-03-20 | B | 15 | 0.013568 | 4.4928e-05
2017 | 2017-02-19 | C | 1 | 0.000465 | 2.9965e-06
2017 | 2017-03-28 | B | 15 | 0.015498 | 4.4922e-05
2017 | 2017-02-20 | C | 5 | 0.002021 | 1.4982e-05
2017 | 2017-03-30 | B | 15 | 0.014239 | 4.4921e-05
2017 | 2017-02-20 | C | 5 | 0.004541 | 1.4982e-05
2017 | 2017-02-20 | C | 1 | 0.000359 | 2.9964e-06
2017 | 2017-02-20 | C | 3 | 0.000827 | 8.9894e-06
2017 | 2017-02-20 | C | 1 | 0.000324 | 2.9964e-06
2017 | 2017-02-20 | C | 1567 | 0.10987 | 0.0046955
2017 | 2017-02-21 | C | 8 | 0.002653 | 2.3971e-05
2017 | 2017-03-17 | B | 1 | 0.000652 | 2.9953e-06
2017 | 2017-03-18 | B | 2 | 0.002048 | 5.9906e-06
2017 | 2017-02-21 | C | 3 | 0.000956 | 8.9893e-06
2017 | 2017-03-18 | B | 4 | 0.004217 | 1.1981e-05
2017 | 2017-03-20 | B | 4 | 0.002791 | 1.1981e-05
2017 | 2017-03-16 | B | 3 | 0.001967 | 8.9862e-06
2017 | 2017-02-21 | C | 1 | 0.000474 | 2.9964e-06
2017 | 2017-02-21 | C | 75 | 0.065257 | 0.00022473
2017 | 2017-02-21 | C | 660 | 0.019974 | 0.0019777
2017 | 2017-02-21 | C | 4 | 0.000628 | 1.1986e-05
2017 | 2017-02-21 | C | 5 | 0.001446 | 1.4982e-05
2017 | 2017-02-21 | C | 423 | 0.010197 | 0.0012675
2017 | 2017-02-21 | C | 28 | 0.002768 | 8.39e-05
2017 | 2017-02-22 | C | 5 | 0.000239 | 1.4982e-05
2017 | 2017-02-22 | C | 11 | 0.003747 | 3.296e-05
2017 | 2017-02-22 | C | 2 | 0.001448 | 5.9927e-06
2017 | 2017-02-22 | C | 1261 | 0.014582 | 0.0028735
2017 | 2017-03-21 | B | 24 | 0.025374 | 7.1884e-05
2017 | 2017-03-13 | B | 74 | 0.01596 | 0.00022167
2017 | 2017-02-22 | C | 1 | 0.000304 | 2.9963e-06
2017 | 2017-02-22 | C | 3004 | 0.12195 | 0.0090012
2017 | 2017-03-27 | B | 17 | 0.000958 | 5.0913e-05
2017 | 2017-02-23 | C | 279 | 0.062336 | 0.0011656
2017 | 2017-03-14 | B | 14 | 0.018116 | 4.1937e-05
2017 | 2017-02-23 | C | 33 | 0.006229 | 9.888e-05
2017 | 2017-02-23 | C | 412 | 0.10323 | 0.0012345
2017 | 2017-02-23 | C | 86 | 0.016874 | 0.00025769
2017 | 2017-02-23 | C | 2 | 0.00133 | 5.9927e-06
2017 | 2017-03-01 | B | 55 | 0.019529 | 0.00016478
2017 | 2017-03-18 | B | 55 | 0.014907 | 0.00016474
2017 | 2017-03-19 | B | 15 | 0.00434 | 4.4929e-05
2017 | 2017-02-24 | C | 297 | 0.27772 | 0.0008899
2017 | 2017-02-24 | C | 300 | 0.007415 | 0.00089889
2017 | 2017-03-13 | B | 75 | 0.011092 | 0.00028158
2017 | 2017-02-24 | C | 263 | 0.066124 | 0.00078803
2017 | 2017-03-20 | B | 4 | 0.00357 | 1.1981e-05
2017 | 2017-02-25 | C | 4 | 0.001461 | 1.1985e-05
2017 | 2017-02-25 | C | 330 | 0.027474 | 0.00098877
2017 | 2017-02-25 | C | 12 | 0.001164 | 3.5955e-05
2017 | 2017-03-24 | B | 88 | 0.10516 | 0.00026356
2017 | 2017-03-30 | B | 10 | 0.00524 | 2.9947e-05
2017 | 2017-02-25 | C | 5 | 0.000735 | 1.4981e-05
2017 | 2017-02-25 | C | 504 | 0.11348 | 0.0012734
2017 | 2017-02-26 | C | 165 | 0.14337 | 0.00049438
2017 | 2017-02-26 | C | 3 | 0.000988 | 8.9886e-06
2017 | 2017-03-18 | B | 3 | 0.002821 | 8.9859e-06
2017 | 2017-02-27 | C | 10 | 0.000838 | 2.9962e-05
2017 | 2017-03-10 | B | 42 | 0.043658 | 0.00012582
2017 | 2017-03-21 | B | 59 | 0.26559 | 0.00035343
2017 | 2017-02-27 | C | 4 | 0.00141 | 1.1985e-05
2017 | 2017-02-27 | C | 16 | 0.004973 | 4.7939e-05
2017 | 2017-02-27 | C | 532 | 0.1356 | 0.001594
2017 | 2017-02-27 | C | 1 | 0.000286 | 2.9961e-06
2017 | 2017-02-28 | C | 36 | 0.014683 | 0.00010786
2017 | 2017-03-22 | B | 8 | 0.001293 | 4.7922e-05
2017 | 2017-02-28 | C | 140 | 0.003702 | 0.00042245
2017 | 2017-02-28 | C | 4 | 0.002708 | 1.1985e-05
2017 | 2017-02-28 | C | 4 | 0.001761 | 1.1985e-05
2017 | 2017-02-28 | C | 4 | 0.000371 | 1.1985e-05
2017 | 2017-02-28 | C | 2 | 0.000456 | 5.9922e-06
2017 | 2017-03-01 | C | 109 | 0.070264 | 0.00032657
2017 | 2017-03-01 | C | 4 | 0.001522 | 1.1984e-05
2017 | 2017-03-21 | B | 41 | 0.041384 | 0.0001228
2017 | 2017-03-22 | B | 7 | 0.003501 | 2.0966e-05
2017 | 2017-03-01 | C | 392 | 0.12034 | 0.0011745
2017 | 2017-03-01 | C | 39 | 0.00222 | 0.00011685
2017 | 2017-03-04 | B | 1 | 0.000307 | 2.9959e-06
2017 | 2017-03-01 | C | 601 | 0.10001 | 0.0018006
2017 | 2017-03-24 | B | 36 | 0.047117 | 0.00010782
2017 | 2017-03-01 | C | 20 | 0.00441 | 5.9922e-05
2017 | 2017-03-01 | C | 498 | 0.11486 | 0.001492
2017 | 2017-03-01 | C | 27 | 0.012642 | 8.0894e-05
2017 | 2017-03-02 | C | 30 | 0.005302 | 0.00017976
2017 | 2017-03-02 | C | 1 | 0.000434 | 2.996e-06
2017 | 2017-03-02 | C | 584 | 0.037045 | 0.00095274
2017 | 2017-03-15 | B | 56 | 0.017459 | 0.00033549
2017 | 2017-03-03 | B | 58 | 0.003649 | 0.00017377
2017 | 2017-03-02 | C | 1 | 0.00069 | 2.996e-06
2017 | 2017-03-03 | C | 3 | 0.000359 | 8.9879e-06
2017 | 2017-03-29 | B | 144 | 0.078918 | 0.00043125
2017 | 2017-03-17 | B | 3 | 0.001725 | 8.986e-06
2017 | 2017-03-03 | C | 337 | 0.20083 | 0.0011325
2017 | 2017-03-03 | C | 836 | 0.060069 | 0.0025047
2017 | 2017-03-04 | C | 23 | 0.005099 | 6.8907e-05
2017 | 2017-03-04 | C | 54 | 0.002912 | 0.00016178
2017 | 2017-03-04 | C | 1 | 0.00063 | 2.9959e-06
2017 | 2017-03-04 | C | 2 | 0.000598 | 5.9918e-06
2017 | 2017-03-04 | C | 2 | 0.000671 | 5.9918e-06
2017 | 2017-03-04 | C | 10 | 0.004234 | 2.9959e-05
2017 | 2017-03-05 | C | 64 | 0.042358 | 0.00038348
2017 | 2017-03-05 | C | 669 | 0.10945 | 0.0020043
2017 | 2017-03-05 | C | 3 | 0.00014 | 8.9877e-06
2017 | 2017-03-05 | C | 257 | 0.014137 | 0.00076995
2017 | 2017-03-05 | C | 6 | 0.002488 | 1.7975e-05
2017 | 2017-03-05 | C | 396 | 0.069716 | 0.0011864
2017 | 2017-03-06 | C | 306 | 0.20014 | 0.0013541
2017 | 2017-03-28 | B | 16 | 0.000239 | 4.7917e-05
2017 | 2017-03-26 | B | 35 | 0.015118 | 0.00010482
2017 | 2017-03-06 | C | 3 | 0.001168 | 8.9875e-06
2017 | 2017-03-20 | B | 8 | 0.000215 | 2.3962e-05
2017 | 2017-03-24 | B | 11 | 0.012676 | 3.2945e-05
2017 | 2017-03-06 | C | 37 | 0.01053 | 0.00011085
2017 | 2017-03-06 | C | 6 | 0.001455 | 1.7975e-05
2017 | 2017-03-07 | C | 84 | 0.01233 | 0.00025165
2017 | 2017-03-07 | C | 1786 | 0.082552 | 0.0053505
2017 | 2017-03-07 | C | 257 | 0.035194 | 0.00076992
2017 | 2017-03-07 | C | 654 | 0 | 0.0019593
2017 | 2017-03-28 | B | 3 | 0.000736 | 1.7969e-05
2017 | 2017-03-14 | B | 47 | 0.066451 | 0.00014079
2017 | 2017-03-07 | C | 75 | 0.024703 | 0.00022469
2017 | 2017-03-07 | C | 46 | 0.009569 | 0.00013781
2017 | 2017-03-07 | C | 38 | 0.003836 | 0.00011384
2017 | 2017-03-08 | C | 199 | 0.57436 | 0.00059616
2017 | 2017-03-08 | C | 6064 | 2.033 | 0.018166
2017 | 2017-03-08 | C | 3 | 0.002026 | 8.9873e-06
2017 | 2017-03-08 | C | 33 | 0.005832 | 9.886e-05
2017 | 2017-03-08 | C | 941 | 0.19616 | 0.002819
2017 | 2017-03-08 | C | 7 | 0.002136 | 2.097e-05
2017 | 2017-03-08 | C | 3 | 0.000476 | 8.9873e-06
2017 | 2017-03-08 | C | 537 | 0.32252 | 0.0044937
2017 | 2017-03-08 | C | 71 | 0.008271 | 0.0002127
2017 | 2017-03-29 | B | 34 | 0.003258 | 0.00010182
2017 | 2017-03-08 | C | 153 | 0.041635 | 0.00045835
2017 | 2017-03-08 | C | 8 | 0.009083 | 2.3966e-05
2017 | 2017-03-08 | C | 27 | 0.053459 | 8.0886e-05
2017 | 2017-03-08 | C | 19 | 0.00299 | 5.692e-05
2017 | 2017-03-08 | C | 555 | 0.25076 | 0.0016627
2017 | 2017-03-09 | B | 52 | 0.010281 | 0.00015578
2017 | 2017-03-08 | C | 845 | 0.21908 | 0.00352
2017 | 2017-03-08 | C | 8 | 0.002104 | 2.3966e-05
2017 | 2017-03-08 | C | 1 | 0.000466 | 2.9957e-06
2017 | 2017-03-08 | C | 927 | 0.22382 | 0.0027771
2017 | 2017-03-08 | C | 114 | 0.048514 | 0.00061114
2017 | 2017-03-08 | C | 5 | 0.000314 | 1.4979e-05
2017 | 2017-03-08 | C | 1048 | 0.038608 | 0.0031396
2017 | 2017-03-08 | C | 6 | 0.001905 | 5.9915e-06
2017 | 2017-03-08 | C | 44 | 0.008172 | 0.00013181
2017 | 2017-03-20 | B | 104 | 0.11806 | 0.0003115
2017 | 2017-03-08 | C | 9 | 0.000938 | 2.6962e-05
2017 | 2017-03-28 | B | 9 | 0.010053 | 2.6953e-05
2017 | 2017-03-08 | C | 5 | 0.001411 | 1.4979e-05
2017 | 2017-03-08 | C | 86 | 0.007986 | 0.00025764
2017 | 2017-03-08 | C | 537 | 0.31901 | 0.0016087
2017 | 2017-03-30 | B | 129 | 0.047778 | 0.00038632
2017 | 2017-03-08 | C | 10 | 0.007878 | 2.9958e-05
2017 | 2017-03-08 | C | 2 | 0.002196 | 5.9915e-06
2017 | 2017-03-08 | C | 98 | 0.033444 | 0.00029359
2017 | 2017-03-08 | C | 147 | 0.15033 | 0.0004943
2017 | 2017-03-08 | C | 7 | 0.007284 | 2.097e-05
2017 | 2017-03-08 | C | 1 | 0.003919 | 2.9957e-06
2017 | 2017-03-08 | C | 891 | 0 | 0.00014679
2017 | 2017-03-08 | C | 2 | 0.000131 | 5.9915e-06
2017 | 2017-03-08 | C | 891 | 0.24343 | 0.0020611
2017 | 2017-03-08 | C | 15 | 0.011638 | 4.4936e-05
2017 | 2017-03-08 | C | 7 | 0.002146 | 2.097e-05
2017 | 2017-03-08 | C | 7 | 0.013401 | 2.097e-05
2017 | 2017-03-08 | C | 894 | 0.041512 | 0.0026782
2017 | 2017-03-09 | C | 440 | 0.073399 | 0.0013181
2017 | 2017-03-09 | C | 666 | 0.17229 | 0.0023816
2017 | 2017-03-09 | C | 4 | 0.003964 | 1.1983e-05
2017 | 2017-03-09 | C | 894 | 0.043698 | 0.0026782
2017 | 2017-03-09 | C | 3 | 0.001105 | 8.9871e-06
2017 | 2017-03-09 | C | 43 | 0.019193 | 0.00012882
2017 | 2017-03-09 | C | 15 | 0.008533 | 4.4936e-05
2017 | 2017-03-09 | C | 1 | 0.000481 | 2.9957e-06
2017 | 2017-03-09 | C | 2 | 0.000602 | 5.9914e-06
2017 | 2017-03-09 | C | 3 | 0.001907 | 8.9871e-06
2017 | 2017-03-09 | C | 98 | 0.017003 | 0.00036248
2017 | 2017-03-09 | C | 86 | 0.020022 | 0.00025763
2017 | 2017-03-30 | B | 22 | 0.002833 | 0.00013177
2017 | 2017-03-09 | C | 11 | 0.016454 | 3.2953e-05
2017 | 2017-03-09 | C | 8 | 0.003697 | 2.3966e-05
2017 | 2017-03-09 | C | 11 | 0.007216 | 3.2953e-05
2017 | 2017-03-09 | C | 1 | 8e-05 | 2.9957e-06
2017 | 2017-03-09 | C | 7 | 0.007947 | 2.097e-05
2017 | 2017-03-09 | C | 2 | 0.000794 | 5.9914e-06
2017 | 2017-03-09 | C | 86 | 0.046605 | 0.00025763
2017 | 2017-03-10 | C | 325 | 0.12843 | 0.00097359
2017 | 2017-03-10 | C | 50 | 0.000299 | 0.00014978
2017 | 2017-03-10 | C | 739 | 0.20799 | 0.0026572
2017 | 2017-03-10 | C | 2 | 0.002343 | 5.9913e-06
2017 | 2017-03-30 | B | 29 | 0.030945 | 8.6847e-05
2017 | 2017-03-10 | C | 1 | 0.000526 | 2.9956e-06
2017 | 2017-03-10 | C | 1 | 0.000172 | 2.9956e-06
2017 | 2017-03-11 | C | 22 | 0.006722 | 6.5904e-05
2017 | 2017-03-11 | C | 213 | 0.0503 | 0.00063807
2017 | 2017-03-11 | C | 418 | 0.011193 | 0.0012522
2017 | 2017-03-11 | C | 120 | 0.058556 | 0.00035948
2017 | 2017-03-11 | C | 140 | 0.052711 | 0.00058115
2017 | 2017-03-11 | C | 2 | 9.5e-05 | 5.9912e-06
2017 | 2017-03-11 | C | 261 | 0.12201 | 0.00078186
2017 | 2017-03-11 | C | 42 | 0.02856 | 0.00012582
2017 | 2017-03-11 | C | 480 | 0.064743 | 0.0021509
2017 | 2017-03-11 | C | 153 | 0.04727 | 0.00045833
2017 | 2017-03-11 | C | 17 | 0 | 5.0926e-05
2017 | 2017-03-11 | C | 2 | 0.000456 | 5.9912e-06
2017 | 2017-03-11 | C | 677 | 0.24522 | 0.002028
2017 | 2017-03-12 | C | 2248 | 0.18842 | 0.0067341
2017 | 2017-03-12 | C | 85 | 0.044678 | 0.00025462
2017 | 2017-03-12 | C | 6 | 0.001312 | 1.7973e-05
2017 | 2017-03-12 | C | 5 | 0.00235 | 1.4978e-05
2017 | 2017-03-12 | C | 5 | 0.003883 | 1.4978e-05
2017 | 2017-03-12 | C | 489 | 0.11441 | 0.0015517
2017 | 2017-03-12 | C | 2 | 0.000613 | 5.9911e-06
2017 | 2017-03-12 | C | 76 | 0.035443 | 0.00022766
2017 | 2017-03-13 | C | 4 | 0.000643 | 1.1982e-05
2017 | 2017-03-13 | C | 19 | 0.003244 | 5.6915e-05
2017 | 2017-03-13 | C | 500 | 0.14233 | 0.0016985
2017 | 2017-03-13 | C | 1432 | 0.00936 | 0.0042896
2017 | 2017-03-13 | C | 171 | 0.042594 | 0.00082377
2017 | 2017-03-13 | C | 1 | 3.1e-05 | 2.9955e-06
2017 | 2017-03-13 | C | 1049 | 0.17074 | 0.0033909
2017 | 2017-03-14 | C | 181 | 0.026519 | 0.00054218
2017 | 2017-03-14 | C | 423 | 0.055394 | 0.0012671
2017 | 2017-03-14 | C | 500 | 0.053952 | 0.0014977
2017 | 2017-03-14 | C | 6 | 0.001222 | 1.7973e-05
2017 | 2017-03-14 | C | 2 | 0.000581 | 5.9909e-06
2017 | 2017-03-14 | C | 34 | 0.009879 | 0.00010185
2017 | 2017-03-14 | C | 6 | 0.001294 | 1.7973e-05
2017 | 2017-03-14 | C | 374 | 0.067843 | 0.0011203
2017 | 2017-03-14 | C | 254 | 0.040534 | 0.00076085
2017 | 2017-03-15 | C | 173 | 0.032958 | 0.00051821
2017 | 2017-03-15 | C | 1 | 0.000107 | 2.9954e-06
2017 | 2017-03-15 | C | 7 | 0.000315 | 2.0968e-05
2017 | 2017-03-16 | B | 70 | 0.010483 | 0.00020968
2017 | 2017-03-16 | B | 42 | 0.009435 | 0.00012581
2017 | 2017-03-15 | C | 115 | 0.019521 | 0.00034448
2017 | 2017-03-19 | B | 83 | 0.021101 | 0.00024861
2017 | 2017-03-15 | C | 385 | 0.074381 | 0.0011532
2017 | 2017-03-15 | C | 34 | 0.035065 | 0.00010185
2017 | 2017-03-16 | C | 2 | 0.000738 | 5.9908e-06
2017 | 2017-03-30 | B | 24 | 0.022999 | 7.1874e-05
2017 | 2017-03-16 | C | 4 | 0.002388 | 1.1982e-05
2017 | 2017-03-16 | C | 9 | 0.002614 | 2.6959e-05
2017 | 2017-03-16 | C | 4 | 0.003042 | 1.1982e-05
2017 | 2017-03-17 | C | 16 | 0.004552 | 4.7926e-05
2017 | 2017-03-17 | C | 1 | 0.000487 | 2.9953e-06
2017 | 2017-03-17 | C | 291 | 0.02242 | 0.0001258
2017 | 2017-03-17 | C | 1 | 0.000146 | 2.9953e-06
2017 | 2017-03-17 | C | 806 | 0.2774 | 0.0042893
2017 | 2017-03-17 | C | 45 | 0.017428 | 0.00013479
2017 | 2017-03-17 | C | 27 | 0.010936 | 8.0874e-05
2017 | 2017-03-18 | C | 666 | 0.005696 | 0.0019949
2017 | 2017-03-18 | C | 4 | 0.001485 | 1.1981e-05
2017 | 2017-03-18 | C | 254 | 0.046839 | 0.0014497
2017 | 2017-03-18 | C | 3 | 0.000752 | 8.9859e-06
2017 | 2017-03-19 | C | 18 | 0.004878 | 5.3915e-05
2017 | 2017-03-19 | C | 4 | 0.003316 | 1.1981e-05
2017 | 2017-03-19 | C | 2 | 0.001757 | 5.9905e-06
2017 | 2017-03-20 | C | 236 | 0.073549 | 0.00070687
2017 | 2017-03-20 | C | 108 | 0.02835 | 0.00032348
2017 | 2017-03-18 | C | 40 | 0.002396 | 0.00011981
2017 | 2017-03-20 | C | 19 | 0.006829 | 5.6909e-05
2017 | 2017-03-21 | B | 40 | 0.009225 | 0.00011981
2017 | 2017-03-20 | C | 26 | 0.004984 | 7.7875e-05
2017 | 2017-03-20 | C | 16 | 0.008242 | 4.7923e-05
2017 | 2017-03-20 | C | 7 | 0.001341 | 2.0966e-05
2017 | 2017-03-20 | C | 3 | 0.002768 | 8.9856e-06
2017 | 2017-03-21 | C | 242 | 0.009487 | 0.00072483
2017 | 2017-03-21 | C | 7 | 0.000796 | 2.0966e-05
2017 | 2017-03-25 | B | 58 | 0.005558 | 0.00017371
2017 | 2017-03-21 | C | 1 | 0.000792 | 2.9951e-06
2017 | 2017-03-21 | C | 2 | 0.000413 | 5.9903e-06
2017 | 2017-03-21 | C | 1 | 0.000702 | 2.9951e-06
2017 | 2017-03-21 | C | 4 | 0.000698 | 1.1981e-05
2017 | 2017-03-21 | C | 59 | 0.031357 | 0.00017671
2017 | 2017-03-22 | C | 5573 | 1.6332 | 0.042614
2017 | 2017-03-22 | C | 246 | 0.12793 | 0.0010363
2017 | 2017-03-22 | C | 306 | 0.09584 | 0.00091651
2017 | 2017-03-22 | C | 10 | 0.006554 | 2.9951e-05
2017 | 2017-03-22 | C | 306 | 0.053351 | 0.00091651
2017 | 2017-03-22 | C | 2 | 0.000476 | 5.9902e-06
2017 | 2017-03-22 | C | 14 | 0.013035 | 4.1932e-05
2017 | 2017-03-23 | C | 22 | 0.006041 | 6.5892e-05
2017 | 2017-03-23 | C | 861 | 0.10025 | 0.0025788
2017 | 2017-03-27 | B | 36 | 0.023372 | 0.00010782
2017 | 2017-03-23 | B | 10 | 0.00118 | 2.9951e-05
2017 | 2017-03-23 | C | 17 | 0.007693 | 5.0916e-05
2017 | 2017-03-23 | C | 10 | 0.001846 | 2.9951e-05
2017 | 2017-03-26 | B | 10 | 0.001168 | 2.9949e-05
2017 | 2017-03-27 | B | 10 | 0.001756 | 2.9949e-05
2017 | 2017-03-25 | C | 2523 | 0.21375 | 0.0075563
2017 | 2017-03-25 | C | 86 | 0.01611 | 0.00025757
2017 | 2017-03-25 | C | 398 | 0.066872 | 0.001192
2017 | 2017-03-26 | C | 423 | 0.004382 | 0.0012698
2017 | 2017-03-26 | C | 176 | 0.10243 | 0.0010452
2017 | 2017-03-26 | C | 6 | 0.002218 | 1.797e-05
2017 | 2017-03-26 | C | 86 | 0.015166 | 0.00025756
2017 | 2017-03-27 | C | 23 | 0.004615 | 6.8882e-05
2017 | 2017-03-27 | C | 557 | 0.11962 | 0.0016681
2017 | 2017-03-27 | C | 1 | 0.000279 | 2.9948e-06
2017 | 2017-03-27 | C | 16 | 0.003833 | 4.7918e-05
2017 | 2017-03-27 | C | 559 | 0.10554 | 0.0026654
2017 | 2017-03-27 | C | 11 | 0.003129 | 3.2944e-05
2017 | 2017-03-27 | C | 5 | 0.001642 | 1.4974e-05
2017 | 2017-03-27 | C | 5 | 0.000314 | 1.4974e-05
2017 | 2017-03-27 | C | 1422 | 0.041492 | 0.0047708
2017 | 2017-03-27 | C | 2 | 0.001226 | 5.9897e-06
2017 | 2017-03-27 | C | 5 | 0.001078 | 1.4974e-05
2017 | 2017-03-27 | C | 97 | 0.018065 | 0.0002905
2017 | 2017-03-27 | C | 2 | 0.000869 | 5.9897e-06
2017 | 2017-03-28 | C | 1933 | 0.46909 | 0.005789
2017 | 2017-03-28 | C | 2 | 0.00076 | 5.9896e-06
2017 | 2017-03-28 | C | 2 | 0.000592 | 5.9896e-06
2017 | 2017-03-28 | C | 3 | 0.001306 | 8.9844e-06
2017 | 2017-03-28 | C | 58 | 0.022374 | 0.0001737
2017 | 2017-03-30 | B | 44 | 0.016866 | 0.00013177
2017 | 2017-03-28 | C | 57 | 0.011175 | 0.00017071
2017 | 2017-03-28 | C | 57 | 0.015141 | 0.00017071
2017 | 2017-03-28 | C | 705 | 0.21865 | 0.0021114
2017 | 2017-03-28 | C | 98 | 0.013063 | 0.00029349
2017 | 2017-03-29 | C | 559 | 0.10812 | 0.0012878
2017 | 2017-03-29 | C | 78 | 0.002569 | 0.00023359
2017 | 2017-03-29 | C | 55 | 0.006725 | 0.00016471
2017 | 2017-03-29 | C | 140 | 0.010013 | 0.0001168
2017 | 2017-03-29 | C | 5 | 0.001004 | 1.4974e-05
2017 | 2017-03-29 | C | 1 | 0.000251 | 2.9947e-06
2017 | 2017-03-29 | C | 1 | 0.000321 | 2.9947e-06
2017 | 2017-03-29 | C | 1 | 0.002519 | 2.9947e-06
2017 | 2017-03-29 | C | 629 | 0.12042 | 0.0018837
2017 | 2017-03-30 | C | 59 | 0.008481 | 0.00017669
2017 | 2017-03-30 | C | 634 | 0.15335 | 0.0018987
2017 | 2017-03-30 | C | 1 | 0.001062 | 2.9947e-06
2017 | 2017-03-30 | C | 26 | 0.003581 | 7.7863e-05
2017 | 2017-03-30 | C | 4 | 0.001473 | 1.1979e-05
2017 | 2017-03-31 | C | 425 | 0.008371 | 0.0012727
2017 | 2017-03-31 | C | 1 | 0.000101 | 2.9946e-06
2017 | 2017-03-31 | C | 1421 | 0.049951 | 0.0042554

## 2017
Count | Job ID | Reg Outage Start Date Time | Reg Outage End Date Time | Outage Duration Minutes | Customers Affected | Sum of Customer Minutes | SAIDI | Adjusted SAIDI using ICP Count Avg YTD | SAIFI | Job Description | Voltage | Planned/Unplanned | Napa ID | System | MOC Classification | Job Cause Description | Site ID | Faulted Equipment Name | Comments | Feeder Security | Feeder Name | GXP Name | Network Name | Substation Name | Region | Owner | SAIDI with planned at 50% weighting | SAIFI with planned at 50% weighting | disc_yr | date | class | customers affected | saidi_indiv | saifi_indiv
1 | 10148635 | 2016-04-01 09:24 | 2016-04-01 12:26 | 182 | 9 | 1638 | 0.0049294 | 0.004848 | 2.7084e-05 | NAPA ID:17515 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | 017515 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses U35 | NONE | To replace 11kv pole and to cut trees away from 11kv line. Works location: West Rd, Mauriceville. WO 30017439 | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.002424 | 5.5 | 2017 | 2016-04-01 | B | 9 | 0.004848 | 2.7084e-05
1 | 10188049 | 2016-04-01 09:00 | 2016-04-01 09:04 | 4 | 22 | 88 | 0.00026483 | 6.6e-05 | 6.6206e-05 | NAPA ID:17521 TP_BRUNSWICK GXP > ROBERTS AVE SUB > MAKIRIKIRI | 11 | Planned | 017521 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 909 | NONE | Replace Fuses 909 with solid links. Works location: Parihauhau Rd. WO 30019671 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 3.3e-05 | 5.5 | 2017 | 2016-04-01 | B | 22 | 6.6e-05 | 6.6206e-05
1 | 10188091 | 2016-04-02 09:27 | 2016-04-02 12:48 | 201 | 16 | 3216 | 0.0096779 | 0.009533 | 4.8149e-05 | NAPA ID:17684 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | 017684 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9/74 | NONE | Changing LV Fusing in underground transformer T9/74. Works location: Tui St, Pongaroa. WO 10162821. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.0047665 | 5.5 | 2017 | 2016-04-02 | B | 16 | 0.009533 | 4.8149e-05
1 | 10188231 | 2016-04-04 09:41 | 2016-04-04 11:50 | 128 | 17 | 2188.75 | 0.0065863 | 0.006432 | 5.1156e-05 | NAPA ID:17367 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | 017367 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V17 | NONE | Redig pole to depth and straighten, replace insulators. Works location: Pahiatua Pongaroa Rd. WO 30019049 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.003216 | 5.5 | 2017 | 2016-04-04 | B | 17 | 0.006432 | 5.1156e-05
1 | 10188287 | 2016-04-05 09:30 | 2016-04-05 14:15 | 285 | 50 | 14250 | 0.04288 | 0.042428 | 0.00015046 | NAPA ID:17387 TP_BRUNSWICK GXP > PEAT ST SUB > ST JOHNS | 11 | Planned | 017387 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X3228 | NONE | Replace 400V switchgear for X3228. Works location: Perrett Dr. WO 30019045 | F3 | ST JOHNS | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.021214 | 5.5 | 2017 | 2016-04-05 | B | 50 | 0.042428 | 0.00015046
1 | 10188332 | 2016-04-05 08:15 | 2016-04-05 15:30 | 435 | 64 | 27840 | 0.083774 | 0.083196 | 0.00019258 | NAPA ID:16028 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | 016028 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 74 | NONE | 11kv pole and hardware replacements. Works location: Mania Rd, Masterton. WO 30017189 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.041598 | 5.5 | 2017 | 2016-04-05 | B | 64 | 0.083196 | 0.00019258
1 | 10188577 | 2016-04-06 09:45 | 2016-04-06 15:58 | 373 | 23 | 8579 | 0.025815 | 0.025607 | 6.9209e-05 | NAPA ID:17235 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | 017235 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 778444 | NONE | Install temporary Fuses 46 at Pole 854923, Also upgrade pole 778444 & move links 1175 to new location. Works location: Parapara Rd. WO 30002305 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.012804 | 5.5 | 2017 | 2016-04-06 | B | 23 | 0.025607 | 6.9209e-05
1 | 10188596 | 2016-04-12 09:00 | 2016-04-12 15:14 | 374 | 9 | 3366 | 0.010128 | 0.010046 | 2.708e-05 | NAPA ID:17240 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | 017240 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 014 | NONE | Replace & upgrade 11kv poles. Works location: Parapara Rd. WO 30002305 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.005023 | 5.5 | 2017 | 2016-04-12 | B | 9 | 0.010046 | 2.708e-05
1 | 10189554 | 2016-04-04 09:15 | 2016-04-04 11:00 | 105 | 3 | 315 | 0.00094789 | 0.00092 | 9.0274e-06 | NAPA ID:17545 TP_HINUERA GXP > TOWER ROAD SUB > GORDON | 11 | Planned | 017545 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC350 | NONE | To replace the 11kV pin arm and 11kV Fuse arm with Transformer TC350 Isolated. Works location: Okauia Springs Rd, Matamata. WO 30018758 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.00046 | 5.5 | 2017 | 2016-04-04 | B | 3 | 0.00092 | 9.0274e-06
1 | 10189571 | 2016-04-07 10:42 | 2016-04-07 13:45 | 183 | 9 | 1648.65 | 0.0049609 | 0.004879 | 2.7082e-05 | NAPA ID:17368 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | 017368 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V42 | NONE | Starighten pole and install new stay wire. Works location: Soldiers Rd. WO 30012046 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.0024395 | 5.5 | 2017 | 2016-04-07 | B | 9 | 0.004879 | 2.7082e-05
1 | 10189614 | 2016-04-06 08:30 | 2016-04-06 15:03 | 393 | 53 | 20829 | 0.062677 | 0.062198 | 0.00015948 | NAPA ID:17214 TP_WANGANUI GXP > WANGANUI EAST SUB > NO 3 LINE | 11 | Planned | 017214 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 177 | NONE | Replace 11kV two pole structure number 709881. Works location: Longacre Valley Rd, Wanganui. WO 30020318 | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.031099 | 5.5 | 2017 | 2016-04-06 | B | 53 | 0.062198 | 0.00015948
1 | 10189642 | 2016-04-04 09:20 | 2016-04-04 12:40 | 200 | 4 | 800 | 0.0024073 | 0.002371 | 1.2037e-05 | NAPA ID:17786 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | 017786 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4153 | NONE | To replace the 11kV Pin arm and 11kV Transformer fuses, Install a 400V fuse dis-connector. Note Transformer to be isolated. Works location: Settlement Rd, Morrinsvile. WO 30019182. | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0011855 | 5.5 | 2017 | 2016-04-04 | B | 4 | 0.002371 | 1.2037e-05
1 | 10189795 | 2016-04-05 09:00 | 2016-04-05 14:45 | 345 | 20 | 6900 | 0.020763 | 0.020582 | 6.0183e-05 | NAPA ID:17567 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MAUNGAKAWA ROAD | 11 | Planned | 017567 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC856 | NONE | To replace an existing pole, relocate the transformer, re-arm 5 poles & re-conductor the LV lines (TC856). The new transformer number is TP2942. Works location: Baker Rd, Manawaru. WO 30024501 | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.010291 | 5.5 | 2017 | 2016-04-05 | B | 20 | 0.020582 | 6.0183e-05
1 | 10190950 | 2016-04-07 09:04 | 2016-04-07 14:46 | 342 | 28 | 9577.8667 | 0.028821 | 0.028567 | 8.4254e-05 | NAPA ID:17393 TP_BRUNSWICK GXP > KAI IWI SUB > WATERWORKS RD | 6.6 | Planned | 017393 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1472 | NONE | Replace three 11kv poles, two pole structure 782908, 782909, pole 782915, pole 782885 helicopter . Works location: Tokomaru West Rd. WO 30024332 | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.014283 | 3.3 | 2017 | 2016-04-07 | B | 28 | 0.028567 | 8.4254e-05
1 | 10190991 | 2016-04-08 08:32 | 2016-04-08 11:04 | 152 | 48 | 7332 | 0.022062 | 0.021628 | 0.00014443 | NAPA ID:17373 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | 017373 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1380 | NONE | Replace pole 785806. Pole leaning and bent, resag 11kV lines. Works location: Ruanui Rd, Taihape. WO 30001686 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.010814 | 5.5 | 2017 | 2016-04-08 | B | 48 | 0.021628 | 0.00014443
1 | 10270950 | 2016-04-05 23:00 | 2016-04-06 00:28 | 88 | 37 | 3256 | 0.0097977 | 0.009463 | 0.00011134 | NAPA ID:17712 TP_PIAKO GXP > MORRINSVILLE SUB > LORNE ST | 11 | Planned | 017712 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Switch IC2076 | NONE | Disconnect 11kV cables from right hand side box of switch 3086 and cover terminals so switch safe to liven. Also disconnect 11kV cable from Source A of TC3770. Switch T-Blade switch to position 2 to make safe to liven. Remove disconnected 11kV cables from HV cabinet of TC3770. Works location: Lorne St, Morrinsville. WO 30019222 | F1/F3 | LORNE ST | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 0.0047315 | 5.5 | 2017 | 2016-04-05 | B | 37 | 0.009463 | 0.00011134
1 | 10274991 | 2016-04-20 08:33 | 2016-04-20 15:35 | 421 | 441 | 60241.75 | 0.18124 | 0.17726 | 0.0024249 | NAPA ID:18058 TP_MT MAUNGANUI 33 GXP > MATAPIHI SUB > TE MAUNGA | 11 | Planned | 018058 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-290 | NONE | Connect Tx TD4-282 to new RMU13053/ and through joint in cable towards TD4-290, SD4-693 to be new open point. Matapihi Road, Te Munga. W/O 30002519. | F3 | TE MAUNGA | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 0.088631 | 5.5 | 2017 | 2016-04-20 | B | 441 | 0.17726 | 0.0024249
1 | 10280911 | 2016-04-11 09:30 | 2016-04-11 14:17 | 287 | 1 | 287.3333 | 0.00086456 | 0.000855 | 3.0089e-06 | NAPA ID:17687 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | 017687 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T9/97 | NONE | Replace transformer pole T9/97, glove and barrier off jumpers at P00305. Works location: Route 52, Pongaroa. WO 30000175 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.0004275 | 5.5 | 2017 | 2016-04-11 | B | 1 | 0.000855 | 3.0089e-06
1 | 10282107 | 2016-04-08 09:47 | 2016-04-08 12:22 | 155 | 15 | 2325 | 0.006996 | 0.00686 | 4.5136e-05 | NAPA ID:18009 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11 | Planned | 018009 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P21359 | NONE | Replace 11kV arrestors P21359. Works location: North Range Rd, Palmerston North. WO 30017525 | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.00343 | 5.5 | 2017 | 2016-04-08 | B | 15 | 0.00686 | 4.5136e-05
1 | 10282181 | 2016-04-09 09:14 | 2016-04-09 12:34 | 200 | 1 | 200 | 0.0006018 | 0.000592 | 3.0089e-06 | NAPA ID:17695 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | 017695 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses R75 | NONE | To replace fusing on tx T2/495 , resag 11kv. Works location: Dougherty Rd. WO 30018987 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000296 | 5.5 | 2017 | 2016-04-09 | B | 1 | 0.000592 | 3.0089e-06
1 | 10282183 | 2016-04-04 09:33 | 2016-04-04 11:00 | 87 | 3 | 261 | 0.00078539 | 0.000758 | 9.0274e-06 | NAPA ID:17341 TP_TAURANGA 33 GXP > AONGATETE SUB > MATAKANA RD | 11 | Planned | 017341 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3-149 | NONE | Upgrade 10/11/1 to a 30/11/1 Polemount transformer. Works location: Matakan Rd. WO 30020608 | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.000379 | 5.5 | 2017 | 2016-04-04 | B | 3 | 0.000758 | 9.0274e-06
1 | 10282380 | 2016-04-12 09:30 | 2016-04-12 14:26 | 296 | 133 | 39368 | 0.11845 | 0.11725 | 0.00040018 | NAPA ID:16915 TP_MASTERTON GXP > TE ORE ORE SUB > COLOMBO RD | 11 | Planned | 016915 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 833074 | NONE | Replace 11kv pole. Works location: Columbo Rd, Masterton. WO 30008302 | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.058626 | 5.5 | 2017 | 2016-04-12 | B | 133 | 0.11725 | 0.00040018
1 | 10282451 | 2016-04-07 09:30 | 2016-04-07 13:12 | 222 | 41 | 9102 | 0.027389 | 0.027018 | 0.00012337 | NAPA ID:16914 TP_GREYTOWN GXP > MARTINBOROUGH SUB > DYERVILLE | 11 | Planned | 016914 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 813702 | NONE | Replace damaged 11kV and LV conductor. Works location: Jellicoe St. WO 30016703 | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.013509 | 5.5 | 2017 | 2016-04-07 | B | 41 | 0.027018 | 0.00012337
1 | 10306703 | 2016-04-11 08:57 | 2016-04-11 13:45 | 288 | 53 | 15264 | 0.045928 | 0.045449 | 0.00015947 | NAPA ID:18024 TP_HINUERA GXP > TIRAU SUB > PROSPECT ST | 11 | Planned | 018024 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D12380 | NONE | Install line break at pole D12380. Relace all cross arms at Pole D12393 (TC3721) & pole D12393. Reinstate line break at pole D12380. Works location: Rose St, Main Rd TIrau. WO 30012332 | F4 | PROSPECT ST | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.022725 | 5.5 | 2017 | 2016-04-11 | B | 53 | 0.045449 | 0.00015947
1 | 10310381 | 2016-04-12 08:20 | 2016-04-12 15:31 | 431 | 19 | 8189 | 0.02464 | 0.024468 | 5.7169e-05 | NAPA ID:17898 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | 017898 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7122 | NONE | Upgrade 11Kv conductor from pole 829373 to 829378 in 11kv shutdown. Works location: Lees Pakaraka Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.012234 | 5.5 | 2017 | 2016-04-12 | B | 19 | 0.024468 | 5.7169e-05
1 | 10310480 | 2016-04-11 23:01 | 2016-04-12 04:34 | 333 | 36 | 11988 | 0.036071 | 0.035745 | 0.00010832 | NAPA ID:17717 TP_PIAKO GXP > MORRINSVILLE SUB > LORNE ST | 11 | Planned | 017717 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2076 | NONE | Replace transformer TC3770 with a new 500kVA transformer and change 11kV connection point for the transformer to fuse switch 13070/2. Works location: Allen St, Morrinsville. WO 30019222 | F1/F3 | LORNE ST | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 0.017872 | 5.5 | 2017 | 2016-04-11 | B | 36 | 0.035745 | 0.00010832
1 | 10310538 | 2016-04-07 08:45 | 2016-04-07 15:25 | 400 | 132 | 52800 | 0.15888 | 0.15769 | 0.0003972 | NAPA ID:16980 TP_MASTERTON GXP | 11 | Planned | 016980 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 831547 | NONE | Replace 33kv/11kv termination pole 831547. Works location: Oak St, Masterton. WO 30013012 | F3 | EDITH ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.078843 | 5.5 | 2017 | 2016-04-07 | B | 132 | 0.15769 | 0.0003972
1 | 10310546 | 2016-04-13 23:00 | 2016-04-14 00:05 | 65 | 1 | 65 | 0.00019558 | 0.000186 | 3.0088e-06 | NAPA ID:17720 TP_PIAKO GXP > MORRINSVILLE SUB > LORNE ST | 11 | Planned | 017720 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Switch IC1542 | NONE | Reconnect 11kV cable to right hand side box of switch 3086. Works location; Lorne St, Morrinsville. WO 30019222 | F1/F3 | LORNE ST | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 9.3e-05 | 5.5 | 2017 | 2016-04-13 | B | 1 | 0.000186 | 3.0088e-06
1 | 10312393 | 2016-04-12 10:30 | 2016-04-12 12:28 | 118 | 12 | 1416 | 0.0042606 | 0.004152 | 3.6106e-05 | NAPA ID:17369 TP_MANGAMAIRE GXP > PONGAROA SUB > COAST ROAD | 11 | Planned | 017369 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V64 | NONE | Replace burnt off softwood pole. Works location: Owahanga Rd. WO 30013312 | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.002076 | 5.5 | 2017 | 2016-04-12 | B | 12 | 0.004152 | 3.6106e-05
1 | 10317739 | 2016-04-05 08:40 | 2016-04-05 09:28 | 48 | 135 | 6480 | 0.019499 | 0.01828 | 0.00040623 | NAPA ID:15866 TP_WAIKINO GXP > WHANGAMATA SUB > ACHILLES AVE | 11 | Planned | 015866 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3935 | NONE | To install LV generator at TC3935 and replace Pole # R12525 L/Line. Works location: Ocean Rd, Whangamata. WO 30003265 | F3 | ACHILLES AVE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.00914 | 5.5 | 2017 | 2016-04-05 | B | 135 | 0.01828 | 0.00040623
1 | 10318157 | 2016-04-05 09:15 | 2016-04-05 14:00 | 285 | 1 | 285 | 0.0008576 | 0.000848 | 3.0091e-06 | NAPA ID:18002 TP_KOPU GXP > KEREPEHI SUB > HAURAKI RD | 11 | Planned | 018002 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1065 | NONE | Upgrade TC1065 to 50kVA. Works location: Oparia Rd, Turua. WO 30019768 | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000424 | 5.5 | 2017 | 2016-04-05 | B | 1 | 0.000848 | 3.0091e-06
1 | 10318162 | 2016-04-11 12:02 | 2016-04-11 13:35 | 93 | 8 | 744 | 0.0022386 | 0.002166 | 2.4071e-05 | NAPA ID:17787 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | 017787 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2649 | NONE | To replace the 11kV Arm, 11kV Fuse arm & install a 400V Fuse Disconnector. Works location: Settlement Rd, Morrinsville. WO 30019182 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.001083 | 5.5 | 2017 | 2016-04-11 | B | 8 | 0.002166 | 2.4071e-05
1 | 10319624 | 2016-04-15 08:19 | 2016-04-15 12:02 | 223 | 19 | 4237 | 0.012748 | 0.012576 | 5.7167e-05 | NAPA ID:17900 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | 017900 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7122 | NONE | Upgrade 11kV conductor from pole 829373 to T2178 in 11kV shutdown. Works location; Lees Pakaraka Rd. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.006288 | 5.5 | 2017 | 2016-04-15 | B | 19 | 0.012576 | 5.7167e-05
1 | 10329628 | 2016-04-13 10:18 | 2016-04-13 15:45 | 327 | 1 | 327 | 0.00098389 | 0.000974 | 3.0088e-06 | NAPA ID:17716 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | 017716 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T8/291 | UNKNOWN | Change existing transformer pole with all new hardware, earths. Reuse existing TX T8/291 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000487 | 5.5 | 2017 | 2016-04-13 | B | 1 | 0.000974 | 3.0088e-06
1 | 10339518 | 2016-04-12 09:15 | 2016-04-12 14:52 | 337 | 362 | 115544 | 0.34766 | 0.34439 | 0.0010892 | NAPA ID:17294 TP_LINTON GXP > KAIRANGA SUB > TAKARO | 11 | Planned | 017294 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P43472 | NONE | Replace double crossarms & 11KV ABS A36. Install new ABS TEMP 04 on pole P43472 (this will become new ABS A40, old A40 will be removed next day NAPA 17637). Works Location: Monrad Street, Palmerston North. W/O 30017988. | F3 | TAKARO | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.17219 | 5.5 | 2017 | 2016-04-12 | B | 362 | 0.34439 | 0.0010892
1 | 10339851 | 2016-04-06 09:01 | 2016-04-06 14:12 | 311 | 221 | 68767.8333 | 0.20693 | 0.20493 | 0.00066501 | NAPA ID:17544 TP_HINUERA GXP > TIRAU SUB > CAMBRIDGE RD TIRAU | 11 | Planned | 017544 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | NONE | To replace the 11kV arms and Hardware on poles D1301 Luck at Last Rd & D1407 Hicks Rd | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.10247 | 5.5 | 2017 | 2016-04-06 | B | 221 | 0.20493 | 0.00066501
1 | 10340833 | 2016-04-13 09:50 | 2016-04-13 14:55 | 305 | 28 | 8540 | 0.025696 | 0.025442 | 8.4248e-05 | NAPA ID:18073 TP_STRATFORD GXP > KAPONGA SUB > DUTHIE RD | 11 | Planned | 018073 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2181T | NONE | Lower transformer structure 2181T down bank to better ground & remove redundant LV span & stay. Works Location: 678 Eltham Road. W/O 30015924. | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.012721 | 5.5 | 2017 | 2016-04-13 | B | 28 | 0.025442 | 8.4248e-05
1 | 10341075 | 2016-04-14 09:46 | 2016-04-14 14:44 | 297 | 11 | 3274.7 | 0.009853 | 0.009753 | 3.3097e-05 | NAPA ID:18078 TP_BUNNYTHORPE GXP > SANSON SUB | 11 | Planned | 018078 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | NONE | Swap OH lines L2 - L4 and O48 - O49. (On completion Interchange ABS numbers L2 and O48 so schematic remains correct) Cable from CB6 will transfer from ABS L2 to ABS O48. Cable from CB8 will transfer from ABS O48 to ABS L2. At Four Pole structure in Penny Rd Swap jumpers to reinstate correct feeder schematic | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.0048765 | 5.5 | 2017 | 2016-04-14 | B | 11 | 0.009753 | 3.3097e-05
1 | 10343316 | 2016-04-12 09:15 | 2016-04-12 11:00 | 105 | 1 | 105 | 0.00031593 | 0.000306 | 3.0088e-06 | NAPA ID:17789 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017789 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5981 | NONE | Replace the 11kV Fuse arm & Install a 400V Fuse Disconnector. Works Location: 82 Walton Road, Walton. W/O 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000153 | 5.5 | 2017 | 2016-04-12 | B | 1 | 0.000306 | 3.0088e-06
1 | 10343396 | 2016-04-12 13:00 | 2016-04-12 13:43 | 43 | 9 | 387 | 0.0011644 | 0.001083 | 2.708e-05 | NAPA ID:17790 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017790 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC321 | NONE | To install a 400V Fuse Disconnector. Works Location: Harper Road, Walton. W/O 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0005415 | 5.5 | 2017 | 2016-04-12 | B | 9 | 0.001083 | 2.708e-05
1 | 10343443 | 2016-04-13 14:26 | 2016-04-13 14:50 | 24 | 8 | 192 | 0.0005777 | 0.000505 | 2.4071e-05 | NAPA ID:17792 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017792 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1935 | NONE | To install a 400V Fuse Disconnector. Works location: Harper Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0002525 | 5.5 | 2017 | 2016-04-13 | B | 8 | 0.000505 | 2.4071e-05
1 | 10345787 | 2016-04-13 08:15 | 2016-04-13 14:15 | 360 | 87 | 31321.45 | 0.094242 | 0.093456 | 0.00026177 | NAPA ID:18195 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 018195 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 798492 | NONE | Replace 3 poles ,T1031,798492,S505 and replace 11kV conductor between S505 and 798397. Works location; Western Lake Rd, Featherston. WO 30024461 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.046728 | 5.5 | 2017 | 2016-04-13 | B | 87 | 0.093456 | 0.00026177
1 | 10345929 | 2016-04-07 09:16 | 2016-04-07 15:45 | 389 | 11 | 4280.1 | 0.012879 | 0.012779 | 3.31e-05 | NAPA ID:16946 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | 016946 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole V13485 | NONE | Isolate TC1242 LV and replace Pole V13485 Live Line. Works location: Colville Rd, Coromandel. WO 30012346 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.0063895 | 5.5 | 2017 | 2016-04-07 | B | 11 | 0.012779 | 3.31e-05
1 | 10361474 | 2016-04-07 08:30 | 2016-04-07 14:41 | 371 | 125 | 46437.5 | 0.13973 | 0.13861 | 0.00037613 | NAPA ID:17910 TP_TAURANGA 33 GXP > KAURI POINT > BOWENTOWN | 11 | Planned | 017910 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 207103 | NONE | Replace poles, cross arms and reconductor feeder. Install TEMP ABS # 23 during shutdown at pole 207099. Works location: Taupiro Rd. WO 30019164 | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.069303 | 5.5 | 2017 | 2016-04-07 | B | 125 | 0.13861 | 0.00037613
1 | 10363143 | 2016-04-08 09:09 | 2016-04-08 14:10 | 301 | 48 | 14448 | 0.043475 | 0.043041 | 0.00014443 | NAPA ID:17941 TP_TAURANGA 33 GXP > KAURI POINT > BOWENTOWN | 11 | Planned | 017941 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SA2-009 | NONE | Replace cross arm and re-conductor. Works location: Taupiro Rd, Kauri Point. WO 30019164 | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.021521 | 5.5 | 2017 | 2016-04-08 | B | 48 | 0.043041 | 0.00014443
1 | 10370392 | 2016-04-16 08:31 | 2016-04-16 13:25 | 294 | 3 | 859 | 0.0025845 | 0.002557 | 9.0262e-06 | NAPA ID:17907 TP_MASTERTON GXP > TE ORE ORE SUB > CHURCH ST | 11 | Planned | 017907 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 845260 | NONE | Replace Poles 829405, 829404, 829402, T1101 Pole, 829400. Works location: Te Whiti Rd, Masterton. WO 30014083 | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.0012785 | 5.5 | 2017 | 2016-04-16 | B | 3 | 0.002557 | 9.0262e-06
1 | 10371697 | 2016-04-15 09:57 | 2016-04-15 12:14 | 137 | 9 | 1233 | 0.0037098 | 0.003628 | 2.7079e-05 | NAPA ID:18261 TP_MANGAMAIRE GXP | 11 | Planned | 018261 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I42 | NONE | Repair 33kV conductor on H structure P26451 & P26853. Works location: Alfredton Rd. WO 30016665 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.001814 | 5.5 | 2017 | 2016-04-15 | B | 9 | 0.003628 | 2.7079e-05
1 | 10372494 | 2016-04-14 09:07 | 2016-04-14 09:53 | 46 | 24 | 1104 | 0.0033217 | 0.003105 | 7.2212e-05 | NAPA ID:18237 TP_HINUERA GXP > BROWNE STREET SUB > SMITH ST | 11 | Planned | 018237 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 9352/3 | NONE | Carry out SF6 Gas Leak detection of Safelink unit 9432. Works location: Eldonwood Dr, Matamata. WO 30007683 | F3 | SMITH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0015525 | 5.5 | 2017 | 2016-04-14 | B | 24 | 0.003105 | 7.2212e-05
1 | 10412087 | 2016-04-19 09:44 | 2016-04-19 12:49 | 184 | 22 | 4069.2667 | 0.012243 | 0.012044 | 6.619e-05 | NAPA ID:18219 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11 | Planned | 018219 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P66 | NONE | Replace 11kV ABS P68. Works location: Main South Rd, Kimbolton. WO 30025055 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.006022 | 5.5 | 2017 | 2016-04-19 | B | 22 | 0.012044 | 6.619e-05
1 | 10412217 | 2016-04-19 08:45 | 2016-04-19 15:08 | 382 | 195 | 74633 | 0.22454 | 0.22278 | 0.00058668 | NAPA ID:17805 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 2 | 11 | Planned | 017805 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Q8 | NONE | Change 7 x HV poles. Works location: Albert St. WO 30024426 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.11139 | 5.5 | 2017 | 2016-04-19 | B | 195 | 0.22278 | 0.00058668
1 | 10413016 | 2016-04-11 10:04 | 2016-04-11 13:24 | 200 | 23 | 4600 | 0.013841 | 0.013633 | 6.9205e-05 | NAPA ID:18004 TP_KOPU GXP > TAIRUA SUB > HIKUAI | 11 | Planned | 018004 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | U0545 | NONE | Replace pole U0545. Works location: Tairua Rd. WO 30024328 | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.0068165 | 5.5 | 2017 | 2016-04-11 | B | 23 | 0.013633 | 6.9205e-05
1 | 10422218 | 2016-04-12 09:30 | 2016-04-12 14:28 | 298 | 77 | 22946 | 0.069042 | 0.068346 | 0.00023168 | NAPA ID:17945 TP_TAURANGA 33 GXP > KAURI POINT > BOWENTOWN | 11 | Planned | 017945 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | UNKNOWN | Replace pole and cross arms and recon feeder | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.034173 | 5.5 | 2017 | 2016-04-12 | B | 77 | 0.068346 | 0.00023168
1 | 10422401 | 2016-04-13 09:22 | 2016-04-13 14:04 | 282 | 48 | 13536.8 | 0.04073 | 0.040296 | 0.00014442 | NAPA ID:17946 TP_TAURANGA 33 GXP > KAURI POINT > BOWENTOWN | 11 | Planned | 017946 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SA2-009 | POLE | Replace poles and conductor between ABS SA2-009 and ABS TEMP23. Work Location: Taupiro Road. W/O 30019164 | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.020148 | 5.5 | 2017 | 2016-04-13 | B | 48 | 0.040296 | 0.00014442
1 | 10422484 | 2016-04-15 09:17 | 2016-04-15 13:35 | 258 | 48 | 12384 | 0.037261 | 0.036827 | 0.00014442 | NAPA ID:17948 TP_TAURANGA 33 GXP > KAURI POINT > BOWENTOWN | 11 | Planned | 017948 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SA2-009 | POLE | Replace pole and arms and reconductor between ABS SA2-009 and ABS TEMP 23. Works Location: Taupiro Road. Work Order 30019164. | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.018413 | 5.5 | 2017 | 2016-04-15 | B | 48 | 0.036827 | 0.00014442
1 | 10522495 | 2016-04-13 08:45 | 2016-04-13 11:20 | 155 | 5 | 775 | 0.0023319 | 0.002286 | 1.5044e-05 | NAPA ID:18356 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 018356 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3166 | NONE | Replace rusty leaking transformer. 34 Taihoa North Road, Matamata. W/O 30019458. | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.001143 | 5.5 | 2017 | 2016-04-13 | B | 5 | 0.002286 | 1.5044e-05
1 | 10522634 | 2016-04-20 08:45 | 2016-04-20 14:54 | 369 | 49 | 18081 | 0.054398 | 0.053955 | 0.00014742 | NAPA ID:16842 TP_WANGANUI GXP > BLINK BONNIE SUB > UNION LINE | 11 | Planned | 016842 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 370893 | NONE | Replace all cross arms at transformer site X2050. Works Location: Union Line, Wanganui. W/O 30002717. | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.026978 | 5.5 | 2017 | 2016-04-20 | B | 49 | 0.053955 | 0.00014742
1 | 10522643 | 2016-04-15 09:13 | 2016-04-15 13:31 | 257 | 27 | 6958.8 | 0.020937 | 0.020693 | 8.1237e-05 | NAPA ID:17507 TP_KINLEITH GXP > MARAETAI ROAD SUB > OLD CAMBRIDGE RD | 11 | Planned | 017507 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | A0070 | NONE | Replace poles and new conductor. Whakamaru Road, 1km South of Old Taupo Road. W/O 30002541. | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.010346 | 5.5 | 2017 | 2016-04-15 | B | 27 | 0.020693 | 8.1237e-05
1 | 10522709 | 2016-04-06 11:56 | 2016-04-06 14:45 | 169 | 47 | 7943 | 0.023901 | 0.023477 | 0.00014143 | NAPA ID:18347 TP_WAIKINO GXP > WHANGAMATA SUB > ACHILLES AVE | 11 | Planned | 018347 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole R12610 | NONE | AP1: To isolate TC4101 and remove the 11kV Cable for the isolated side of the fuses. LLP: To replace the 11kV Fuses FP1727. AP2: To connect the new 11kV Cable to the Isolated side of FP1727.Ocean Road, Whangamata. W/O 30002527. | F3 | ACHILLES AVE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.011739 | 5.5 | 2017 | 2016-04-06 | B | 47 | 0.023477 | 0.00014143
1 | 10525807 | 2016-04-20 09:30 | 2016-04-20 13:10 | 220 | 1 | 220 | 0.00066189 | 0.000652 | 3.0085e-06 | NAPA ID:16925 TP_BRUNSWICK GXP > PEAT ST SUB > ST JOHNS | 11 | Planned | 016925 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 4768 | NONE | Replace 400V switchgear for X1739. Works Location: Peat Street, Wanganui. W/O 30019525. | F3 | ST JOHNS | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.000326 | 5.5 | 2017 | 2016-04-20 | B | 1 | 0.000652 | 3.0085e-06
1 | 10526263 | 2016-04-20 08:59 | 2016-04-20 12:30 | 211 | 14 | 2954 | 0.0088874 | 0.008761 | 4.212e-05 | NAPA ID:17630 TP_MASTERTON GXP > TINUI SUB > LANGDALE | 11 | Planned | 017630 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 848181 | NONE | Replace transformer and structure. Works Location: Post Office Road, Langdale, Masterton. W/O 30014835. | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.0043805 | 5.5 | 2017 | 2016-04-20 | B | 14 | 0.008761 | 4.212e-05
1 | 10526323 | 2016-04-21 09:50 | 2016-04-21 15:02 | 311 | 23 | 7172.55 | 0.021579 | 0.021371 | 6.9196e-05 | NAPA ID:17700 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | 017700 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P10841 | NONE | To change 11kV cross arms. Works Location: Mangaroa Road, Parkville. W/O 30001378. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.010686 | 5.5 | 2017 | 2016-04-21 | B | 23 | 0.021371 | 6.9196e-05
1 | 10526713 | 2016-04-22 09:30 | 2016-04-22 13:38 | 248 | 23 | 5707.8333 | 0.017172 | 0.016964 | 6.9195e-05 | NAPA ID:17701 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | 017701 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P10841 | NONE | To change 11kv cross arms and poles. Works Location: Mangaroa Road, Parkville. W/O 30001378 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.008482 | 5.5 | 2017 | 2016-04-22 | B | 23 | 0.016964 | 6.9195e-05
1 | 10526921 | 2016-04-26 09:29 | 2016-04-26 14:55 | 326 | 23 | 7498 | 0.022556 | 0.022348 | 6.9191e-05 | NAPA ID:17702 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | 017702 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P10841 | NONE | To replace 11kV conductor. Works Location: Mangroa Road Parkville. W/O 30001378. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.011174 | 5.5 | 2017 | 2016-04-26 | B | 23 | 0.022348 | 6.9191e-05
1 | 10529302 | 2016-04-14 09:00 | 2016-04-14 12:05 | 185 | 29 | 5365 | 0.016142 | 0.01588 | 8.7256e-05 | NAPA ID:16955 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 016955 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4469 | NONE | Replace defected DDOs at TC4469 Live Line, and LV work de energised on cable of same transformer | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.00794 | 5.5 | 2017 | 2016-04-14 | B | 29 | 0.01588 | 8.7256e-05
1 | 10531992 | 2016-04-19 10:08 | 2016-04-19 11:40 | 92 | 16 | 1472 | 0.0044287 | 0.004284 | 4.8138e-05 | NAPA ID:18301 TP_STRATFORD GXP > KAPONGA SUB > MANAIA RD | 11 | Planned | 018301 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 730688 | NONE | Replace old wooden pole 730688. Works Location: Rowan Road, Kaponga. Work Order 30015885. | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.002142 | 5.5 | 2017 | 2016-04-19 | B | 16 | 0.004284 | 4.8138e-05
1 | 10533871 | 2016-04-26 09:08 | 2016-04-26 13:44 | 276 | 66 | 18216 | 0.054799 | 0.054203 | 0.00019855 | NAPA ID:17854 TP_BUNNYTHORPE GXP > MAIN ST SUB > MAIN ST 23 | 11 | Planned | 017854 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10291 | NONE | Cut in new fully automated CFCC safelink switch 10291 and remove old magnefix from G91. Work Location: Ruahine Street. Work Order 30002198 | F2 | MAIN ST 23 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 0.027102 | 5.5 | 2017 | 2016-04-26 | B | 66 | 0.054203 | 0.00019855
1 | 10533933 | 2016-04-18 09:47 | 2016-04-18 15:29 | 342 | 31 | 10602 | 0.031898 | 0.031618 | 9.3269e-05 | NAPA ID:17283 TP_LINTON GXP > KAIRANGA SUB > KOPANE | 11 | Planned | 017283 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10299 | NONE | Install ABS DDOs for TEMP Regulator 10299. Job is for the Feilding Sanson 33kV arm change J/N 10140843. Works Location: Kopane Feeder - Rongotea Road. Work Order 10157896. | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.015809 | 5.5 | 2017 | 2016-04-18 | B | 31 | 0.031618 | 9.3269e-05
1 | 10534990 | 2016-04-18 09:05 | 2016-04-18 16:05 | 420 | 27 | 11340 | 0.034118 | 0.033874 | 8.1234e-05 | NAPA ID:17519 TP_KINLEITH GXP > MARAETAI ROAD SUB > OLD CAMBRIDGE RD | 11 | Planned | 017519 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IP648 | NONE | Install new RMU and conductor upgrade. Works Location: Whakamaru Road. Work Order: 30002541. | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.016937 | 5.5 | 2017 | 2016-04-18 | B | 27 | 0.033874 | 8.1234e-05
1 | 10535000 | 2016-04-21 09:00 | 2016-04-21 13:01 | 240 | 36 | 8662.8 | 0.026062 | 0.025737 | 0.00010831 | NAPA ID:17829 TP_BUNNYTHORPE GXP > MILSON SUB > RANGITIKEI | 11 | Planned | 017829 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/883 | NONE | 33kV Cross arm replacement for BPE-MIL line from Z35 to Z36. Work Location: Palmerston North. Work Order 30019577. | F2 | RANGITIKEI | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.012868 | 5.5 | 2017 | 2016-04-21 | B | 36 | 0.025737 | 0.00010831
1 | 10536502 | 2016-04-21 08:48 | 2016-04-21 15:40 | 411 | 61 | 25124.8833 | 0.075589 | 0.075038 | 0.00018352 | NAPA ID:17833 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 2 | 11 | Planned | 017833 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10257/3 | NONE | Change 2 x 11kV poles, fit TEMP DDOs # 29. Run out conductor (3 span of o/h wire). Works Location: Tui St / Albert Street. Work Order 30024426. | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.037519 | 5.5 | 2017 | 2016-04-21 | B | 61 | 0.075038 | 0.00018352
1 | 10536506 | 2016-04-06 10:30 | 2016-04-06 13:45 | 195 | 5 | 975 | 0.0029339 | 0.002888 | 1.5046e-05 | NAPA ID:18426 TP_KINLEITH GXP > BAIRD ROAD SUB > HARRIS BLOCK | 11 | Planned | 018426 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2894 | NONE | Install S/Anchor , remove span conductor, replace rotten X arms. 390 Newell Road, Tokaroa. W/O 30007220. | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.001444 | 5.5 | 2017 | 2016-04-06 | B | 5 | 0.002888 | 1.5046e-05
1 | 10537934 | 2016-04-19 08:30 | 2016-04-19 13:21 | 291 | 3 | 873.55 | 0.0026282 | 0.002601 | 9.0259e-06 | NAPA ID:18413 TP_MATAROA GXP > WAIOURU SUB | 11 | Planned | 018413 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 779134 | NONE | Replace 33 cross arms and 5 poles on Waiouru 33kV feeder from pole no 779134 to 779010 end of line & carry out substation maintenance also change 11kV arm on pole 779086. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.0013005 | 5.5 | 2017 | 2016-04-19 | B | 3 | 0.002601 | 9.0259e-06
1 | 10538621 | 2016-04-22 09:02 | 2016-04-22 12:11 | 189 | 75 | 14175 | 0.042645 | 0.041968 | 0.00022564 | NAPA ID:17831 TP_BUNNYTHORPE GXP > MILSON SUB > TE ARAKURA | 11 | Planned | 017831 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P42041 | NONE | 33kV Crossam replacement on BPE-MIL line. Milson Line, Palmerston North. W/O 30019577. | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.020984 | 5.5 | 2017 | 2016-04-22 | B | 75 | 0.041968 | 0.00022564
1 | 10538624 | 2016-04-22 08:51 | 2016-04-22 13:19 | 268 | 2 | 536.6333 | 0.0016145 | 0.001596 | 6.0169e-06 | NAPA ID:17853 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 017853 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7468 | NONE | Pole and crossarm replacements. Works Location: Jacksons Line, Masterton. W/O 30019523. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000798 | 5.5 | 2017 | 2016-04-22 | B | 2 | 0.001596 | 6.0169e-06
1 | 10538691 | 2016-04-01 11:22 | 2016-04-01 11:27 | 5 | 2496 | 14310.4 | 0.043065 | 0.020531 | 0.0075114 |  | 11 | Unplanned |  | ZONE SUB EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 37 | NONE | CB 37 tripped during SCADA testing on new CB 38 & CB 1. Established the error, cleared site and relivened. Refer to Safety Manager Incident 10538691. | S4 | KATIKATI 33KV | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.020531 | 11 | 2017 | 2016-04-01 | C | 2496 | 0.020531 | 0.0075114
1 | 10542789 | 2016-04-01 12:09 | 2016-04-01 15:09 | 179 | 256 | 2962.5333 | 0.0089154 | 0.006604 | 0.00031298 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | TF6-053 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | SVS hub and Control advised 11:33. Recloser S6031 A/R, Sectionaliser 9834 tripped. Outage required past Fuses SF6-008 to remove trees from the lines. No backfeeds available. Trees removed, relivened OK. Replace 10m wire, 4 x links, 1x 15kV Transformer 2 x cross arms, 2 x Fuses, 2 x 63A fuses. NDR 400112. | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.006604 | 11 | 2017 | 2016-04-01 | C | 256 | 0.006604 | 0.00031298
1 | 10543199 | 2016-04-21 10:34 | 2016-04-21 14:19 | 224 | 7 | 1573.4833 | 0.0047339 | 0.00467 | 2.106e-05 | NAPA ID:18398 TP_BRUNSWICK GXP > KAI IWI SUB > MISSION RD | 11 | Planned | 018398 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X1484 | NONE | Upgrading transformer from 30kV to 50kV and change all cross arms. Works Location: Mission Road, Whanganui. W/O 30019890. | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.002335 | 5.5 | 2017 | 2016-04-21 | B | 7 | 0.00467 | 2.106e-05
1 | 10543773 | 2016-04-21 11:30 | 2016-04-21 14:36 | 185 | 21 | 3899 | 0.01173 | 0.01154 | 6.3179e-05 | NAPA ID:18302 TP_HAWERA GXP > MANAIA SUB > OTAKEHO | 11 | Planned | 018302 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | MA298 | NONE | Replace burnt out HV cross arms at transformer M2055. Lower Normanby Road, Manaia. W/O 300105. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.00577 | 5.5 | 2017 | 2016-04-21 | B | 21 | 0.01154 | 6.3179e-05
1 | 10543931 | 2016-04-18 10:05 | 2016-04-18 14:06 | 240 | 45 | 10837.5 | 0.032606 | 0.0322 | 0.00013539 | NAPA ID:18298 TP_HAWERA GXP > LIVINGSTONE SUB > PORTLAND QUAY | 11 | Planned | 018298 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer L3225 | NONE | Repair Hv cable and replace Hv fuses at Tx L3225. Works location: Dorset St, Patea. WO 30017082 | F3 | PORTLAND QUAY | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.0161 | 5.5 | 2017 | 2016-04-18 | B | 45 | 0.0322 | 0.00013539
1 | 10544129 | 2016-04-19 09:30 | 2016-04-19 13:00 | 210 | 48 | 10080 | 0.030327 | 0.029893 | 0.00014441 | NAPA ID:18454 TP_MASTERTON GXP > TINUI SUB > ANNEDALE | 11 | Planned | 018454 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S198 | NONE | replace leaning and broken transformer structure attached to unfused spur line. Annedale Road, Tinui, Wairarapa. W/O 30020639. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.014946 | 5.5 | 2017 | 2016-04-19 | B | 48 | 0.029893 | 0.00014441
1 | 10544270 | 2016-04-26 09:20 | 2016-04-26 15:00 | 339 | 58 | 19705.5 | 0.05928 | 0.058756 | 0.00017448 | NAPA ID:17832 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11 | Planned | 017832 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P39165 | NONE | 33kV crossarm replacement for BPE-MIL Line. Settlers Line, Palmerston North.W/O 300019577. | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.029378 | 5.5 | 2017 | 2016-04-26 | B | 58 | 0.058756 | 0.00017448
1 | 10544323 | 2016-04-27 09:15 | 2016-04-27 16:29 | 434 | 57 | 24738 | 0.074419 | 0.073904 | 0.00017147 | NAPA ID:17835 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11 | Planned | 017835 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P41931 | CROSSARM - WHOLE ASSEMBLY | 33kV Crossarm replacement for BPE-MIL line | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.036952 | 5.5 | 2017 | 2016-04-27 | B | 57 | 0.073904 | 0.00017147
1 | 10544372 | 2016-04-26 09:30 | 2016-04-26 13:40 | 250 | 2 | 500 | 0.0015042 | 0.001486 | 6.0166e-06 | NAPA ID:17852 TP_MASTERTON GXP > AWATOITOI SUB > BLAIRLOGIE | 11 | Planned | 017852 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7130 | NONE | Replace 11kV transformer pole. Works Location: Homewood Road, Masterton. W/O 30017530. | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.000743 | 5.5 | 2017 | 2016-04-26 | B | 2 | 0.001486 | 6.0166e-06
1 | 10544437 | 2016-04-05 09:31 | 2016-04-05 16:11 | 400 | 101 | 40397.55 | 0.12156 | 0.12065 | 0.00030392 | NAPA ID:18491 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 018491 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 209405 | NONE | Replace poles, hardware and conductor between poles 209405 & 205669 Install TEMP 66 on pole 209405 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.060325 | 5.5 | 2017 | 2016-04-05 | B | 101 | 0.12065 | 0.00030392
1 | 10544605 | 2016-04-07 08:45 | 2016-04-07 14:42 | 357 | 71 | 25347 | 0.076271 | 0.07563 | 0.00021364 | NAPA ID:16206 TP_TAURANGA 33 GXP | 11 | Planned | 016206 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 209405 | UNKNOWN | Replace poles, hardware and conductor between poles 209405 & 205669 | F3 | CENTRAL OTUMOETAI | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 0.037815 | 5.5 | 2017 | 2016-04-07 | B | 71 | 0.07563 | 0.00021364
1 | 10545145 | 2016-04-01 21:15 | 2016-04-01 21:26 | 10 | 31 | 339.9667 | 0.0010231 | 0.000743 | 9.3291e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | T2156 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman has found a Opossum on the lv bushings of transformer T2156, transformer was isolated to remove Opossum from the bushings.Customer reported Opossum on transformer, customer only lost supply while Opossum was been removed. | F3 | WEST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000743 | 11 | 2017 | 2016-04-01 | C | 31 | 0.000743 | 9.3291e-05
1 | 10546251 | 2016-04-02 08:33 | 2016-04-02 09:28 | 54 | 51 | 2779.5 | 0.0083643 | 0.007903 | 0.00015347 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | SD6-014 | FUSE - ELEMENT/LINK (HV) | 8.35am - called hub to advise 999. Replaced 2 x 20 amp fuses & barrels | F3 | TARA RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.007903 | 11 | 2017 | 2016-04-02 | C | 51 | 0.007903 | 0.00015347
1 | 10546335 | 2016-04-02 08:43 | 2016-04-02 10:47 | 123 | 8 | 988.5333 | 0.0029748 | 0.002902 | 2.4074e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2584 | FUSE - ELEMENT/LINK (HV) | replaced 2x 8a HV fuses @ fuses 2584 | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.002902 | 11 | 2017 | 2016-04-02 | C | 8 | 0.002902 | 2.4074e-05
1 | 10547424 | 2016-04-02 14:49 | 2016-04-03 10:56 | 1206 | 83 | 22809.5667 | 0.068641 | 0.067891 | 0.00043635 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | ABS5479 | UNKNOWN | During sectionalising and Patrol found tree over lines @ pole 739364 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.067891 | 11 | 2017 | 2016-04-02 | C | 83 | 0.067891 | 0.00043635
1 | 10547847 | 2016-04-02 16:58 | 2016-04-02 23:40 | 402 | 29 | 11672.0167 | 0.035125 | 0.034862 | 8.7269e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TP497 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 2 blown fuses at FP481 reloaded & closed but blew again. Suspected cable fault to transformer TP497 or transformer itself. Cable & transfomer to be tested. Generator being arranged to connect at LV bus at TP497. Faulty 300kVA transformer replaced. All supply restored. Generator not connected due to time taken to change transformer. | F2 | POOLES RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.034862 | 11 | 2017 | 2016-04-02 | C | 29 | 0.034862 | 8.7269e-05
1 | 10548385 | 2016-04-02 21:37 | 2016-04-02 23:49 | 131 | 10 | 1316.5 | 0.0039617 | 0.003871 | 3.0093e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 736028 | INSULATOR | Faultman found a broken insulator at pole 736028, line was isolated at Fuses 6061 to replace the insulator. 1 X 11kV Insulator replaced & binder. | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.003871 | 11 | 2017 | 2016-04-02 | C | 10 | 0.003871 | 3.0093e-05
1 | 10557148 | 2016-04-03 01:34 | 2016-04-03 02:10 | 36 | 51 | 1836 | 0.0055249 | 0.005064 | 0.00015347 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 462 | FUSE - ELEMENT/LINK (HV) | Explosion at transformer, reported by fire service F2050802, this was reported to fire services by a customer. Faultman found blown fuses at Fuses 462 and at Fused ABS 1451, the cause was a opossum. 1 X 30 amp HV fuse replaced - Fuses 462. 2 X 20 amp HV fuses replaced at - Fused ABS 1451 & fuse holder replaced | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.005064 | 11 | 2017 | 2016-04-03 | C | 51 | 0.005064 | 0.00015347
1 | 10557224 | 2016-04-03 06:27 | 2016-04-03 08:00 | 93 | 4 | 373.3333 | 0.0011234 | 0.001087 | 1.2037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | TC832 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 20amp Fuses on TC832 caused by rat. | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.001087 | 11 | 2017 | 2016-04-03 | C | 4 | 0.001087 | 1.2037e-05
1 | 10557387 | 2016-04-03 12:19 | 2016-04-03 12:45 | 26 | 16 | 416 | 0.0012518 | 0.001107 | 4.8147e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 0228920 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replaced faulty DDO unit at pole 0228920 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.001107 | 11 | 2017 | 2016-04-03 | C | 16 | 0.001107 | 4.8147e-05
1 | 10567191 | 2016-04-03 10:21 | 2016-04-03 11:02 | 41 | 52 | 2132 | 0.0064156 | 0.005946 | 0.00015648 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7300 | JUMPER | Put Wire back into top of Fuse | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.005946 | 11 | 2017 | 2016-04-03 | C | 52 | 0.005946 | 0.00015648
1 | 10567336 | 2016-04-03 11:46 | 2016-04-03 16:50 | 303 | 508 | 22890.3167 | 0.068882 | 0.064295 | 0.0014956 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N1972 | INSULATOR | Found crossarm burnt & insulator faulty at pole S12825 between 9688 & IC526 Isolated & backfeed rest of area. via 9696. Recloser R17 which was used to backfeed auto relosed after 2 minutes. Sectionaliser 9696 tripped open. Re-checked suspect site and decided safe to reliven. Sectionalised between IC526 & 9696. 3.45pm - sent notification to retail contacts that Wharepoa, Factory and Townsend Roads are affected. (ONE is not working). Found 2 insulators on pole N1972 Faulty. Replaced & relivened | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.064295 | 11 | 2017 | 2016-04-03 | C | 508 | 0.064295 | 0.0014956
1 | 10569027 | 2016-04-03 13:19 | 2016-04-03 18:08 | 288 | 9 | 2599.8 | 0.0078233 | 0.007742 | 2.7083e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | 812980 | POLE | 1 X Pole 1 X Crossarm 3 X HV Insulators | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.007742 | 11 | 2017 | 2016-04-03 | C | 9 | 0.007742 | 2.7083e-05
1 | 10569570 | 2016-04-03 20:42 | 2016-04-03 21:23 | 41 | 2 | 82 | 0.00024676 | 0.000228 | 6.0184e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1117 | JUMPER | Arcing reported on pole by employee at Airport. Any trouble locating arcing pole, contact Caleer, John Gribble phone number 0223513418. He will direct fault man to location. Isolated and Repaired jumper on ABS 414 supply to transformer X1117. | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.000228 | 11 | 2017 | 2016-04-03 | C | 2 | 0.000228 | 6.0184e-06
1 | 10572003 | 2016-04-04 09:05 | 2016-04-04 14:15 | 310 | 9 | 2790 | 0.0083956 | 0.008314 | 2.7082e-05 |  | 11 | Planned | 017525 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP1778 | NONE | No ICP's associated with this relocated Transformer | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.004157 | 5.5 | 2017 | 2016-04-04 | B | 9 | 0.008314 | 2.7082e-05
1 | 10572234 | 2016-04-19 09:00 | 2016-04-19 12:30 | 210 | 28 | 5880 | 0.017691 | 0.017438 | 8.4242e-05 | NAPA ID:17738 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | 017738 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1990 | NONE | Replace TC1990. Works location: McMahon Ave, Whangapoua. WO 30012344 | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.008719 | 5.5 | 2017 | 2016-04-19 | B | 28 | 0.017438 | 8.4242e-05
1 | 10572272 | 2016-04-21 08:58 | 2016-04-21 13:40 | 282 | 7 | 1974 | 0.0059389 | 0.005875 | 2.106e-05 | NAPA ID:17784 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017784 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP179 | NONE | Replace 3 poles and complete line maintenance. Works location; Piakonui Rd, Matamata. WO 30024595 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0029375 | 5.5 | 2017 | 2016-04-21 | B | 7 | 0.005875 | 2.106e-05
1 | 10573384 | 2016-04-27 10:07 | 2016-04-27 16:09 | 362 | 37 | 13405.7167 | 0.040328 | 0.039994 | 0.00011131 | NAPA ID:18448 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | 018448 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S19 | NONE | Replace T8/281 complete with pole and all required hardware. Works location: Pukehoi Rd. WO 30015364 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.019997 | 5.5 | 2017 | 2016-04-27 | B | 37 | 0.039994 | 0.00011131
1 | 10573401 | 2016-04-21 09:44 | 2016-04-21 10:52 | 68 | 25 | 1453.35 | 0.0043725 | 0.004146 | 7.5213e-05 | NAPA ID:18395 TP_STRATFORD GXP > KAPONGA SUB > DUTHIE RD | 11 | Planned | 018395 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 731779 | NONE | Close line break @ pole 731779. Works location: Palmer Rd, Kaponga. WO 30007226 | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.002073 | 5.5 | 2017 | 2016-04-21 | B | 25 | 0.004146 | 7.5213e-05
1 | 10573405 | 2016-04-27 08:33 | 2016-04-27 12:52 | 259 | 1 | 259 | 0.00077914 | 0.00077 | 3.0082e-06 | NAPA ID:17850 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 017850 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7469 | NONE | Pole and crossarm replacements. Works location: Donavans Rd, Masterton. WO 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000385 | 5.5 | 2017 | 2016-04-27 | B | 1 | 0.00077 | 3.0082e-06
1 | 10573461 | 2016-04-27 09:04 | 2016-04-27 15:12 | 368 | 9 | 3313.35 | 0.0099675 | 0.009886 | 2.7074e-05 | NAPA ID:17617 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | 017617 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 014 | NONE | Replacing 11kV Poles & hardware. Works location: Parapara Rd. WO 30002307 | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.004943 | 5.5 | 2017 | 2016-04-27 | B | 9 | 0.009886 | 2.7074e-05
1 | 10573531 | 2016-04-27 09:39 | 2016-04-27 13:52 | 252 | 12 | 3029.6 | 0.0091139 | 0.009005 | 3.6099e-05 | NAPA ID:17891 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 017891 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T4/173 | NONE | Remove 2 pole transformer structure and install new pole and transformer T4/173. Works location; Taonui Rd, Feilding. WO 10162791 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.0045025 | 5.5 | 2017 | 2016-04-27 | B | 12 | 0.009005 | 3.6099e-05
1 | 10573566 | 2016-04-22 09:30 | 2016-04-22 11:35 | 125 | 3 | 375 | 0.0011282 | 0.001101 | 9.0254e-06 | NAPA ID:17793 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017793 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3554 | NONE | Replace the 400V arm & install a 400V Fuse Disconnector. Works location: Walton Rd. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0005505 | 5.5 | 2017 | 2016-04-22 | B | 3 | 0.001101 | 9.0254e-06
1 | 10574526 | 2016-04-22 13:18 | 2016-04-22 13:45 | 27 | 8 | 216 | 0.00064984 | 0.000577 | 2.4068e-05 | NAPA ID:17797 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017797 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC302 | NONE | To install a 400V Fuse Disconnector. Works location: Landsdown Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0002885 | 5.5 | 2017 | 2016-04-22 | B | 8 | 0.000577 | 2.4068e-05
1 | 10574616 | 2016-04-22 12:25 | 2016-04-22 14:40 | 135 | 2 | 270 | 0.00081229 | 0.000794 | 6.0169e-06 | NAPA ID:17795 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017795 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4535 | NONE | To replace the 400V and install a 400V Fuse Disconnector. Works location: Walton Rd. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000397 | 5.5 | 2017 | 2016-04-22 | B | 2 | 0.000794 | 6.0169e-06
1 | 10574712 | 2016-04-26 08:30 | 2016-04-26 11:51 | 201 | 1 | 201 | 0.00060467 | 0.000595 | 3.0083e-06 | NAPA ID:18190 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | 018190 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V12884 | NONE | Break jumpers live line at pole V12884 to straighten poles V12886 & V12887. NOTE: 11kV Transformer TC6156 will be off loaded prior to live line works commencing. Works location; Colville Rd. WO 30012346 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.0002975 | 5.5 | 2017 | 2016-04-26 | B | 1 | 0.000595 | 3.0083e-06
1 | 10574718 | 2016-04-22 09:16 | 2016-04-22 10:35 | 79 | 21 | 1659 | 0.0049911 | 0.004801 | 6.3178e-05 | NAPA ID:18389 TP_HAWERA GXP > MANAIA SUB > OTAKEHO | 11 | Planned | 018389 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | MA232 | NONE | Replace burning out HV fuses MA232. Works location; Mid Normanby Rd, Manaia. WO 30011235 | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.0024005 | 5.5 | 2017 | 2016-04-22 | B | 21 | 0.004801 | 6.3178e-05
1 | 10574914 | 2016-04-26 14:04 | 2016-04-26 15:30 | 86 | 1 | 86 | 0.00025872 | 0.000249 | 3.0083e-06 | NAPA ID:17801 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017801 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC631 | NONE | To replace the transformer and install a 400V Fuse Disconnector. Works location; Hutchinson Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0001245 | 5.5 | 2017 | 2016-04-26 | B | 1 | 0.000249 | 3.0083e-06
1 | 10575910 | 2016-04-26 09:09 | 2016-04-26 13:06 | 237 | 4 | 948 | 0.0028519 | 0.002815 | 1.2033e-05 | NAPA ID:17798 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017798 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC2328 | NONE | To replace the 11kV arms and install a 400V Fuse Disconnector. Works location: Walton Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0014075 | 5.5 | 2017 | 2016-04-26 | B | 4 | 0.002815 | 1.2033e-05
1 | 10575998 | 2016-04-27 09:15 | 2016-04-27 12:45 | 210 | 11 | 2310 | 0.0069491 | 0.006849 | 3.3091e-05 | NAPA ID:18294 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 018294 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1323 | NONE | Replace 11 kV cross arms at various locations. Works location: Taotaoroa Rd, Hinuera. WO 30018274 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0034245 | 5.5 | 2017 | 2016-04-27 | B | 11 | 0.006849 | 3.3091e-05
1 | 10576553 | 2016-04-04 19:29 | 2016-04-04 23:38 | 249 | 317 | 25417.5 | 0.076485 | 0.073623 | 0.0018205 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P35199 | CONDUCTOR - REPAIR/REHANG | CB 23 A/R and tripped. Repaired conductor @ pole P35199. Materials used 10m copper conductor and 5 sleeves. 2r 2002 line patrol. 2r repair 2130 | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.073623 | 11 | 2017 | 2016-04-04 | C | 317 | 0.073623 | 0.0018205
1 | 10579414 | 2016-04-20 09:08 | 2016-04-20 14:39 | 330 | 43 | 14209.35 | 0.04275 | 0.042361 | 0.00012937 | NAPA ID:17769 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 017769 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9459 | NONE | Replace HV cross arms at various locations. Works location: Kaihere Rd. WO 30002467 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.021181 | 5.5 | 2017 | 2016-04-20 | B | 43 | 0.042361 | 0.00012937
1 | 10579523 | 2016-04-21 09:00 | 2016-04-21 14:45 | 345 | 3 | 1035 | 0.0031138 | 0.003086 | 9.0256e-06 | NAPA ID:16981 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 016981 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5802 | NONE | Switching to isolate transformer TC5802 to allow live line replacement of cross arms and lightning arrestors. Works location: Rangihau Rd, Coroglen. WO 30013423 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.001543 | 5.5 | 2017 | 2016-04-21 | B | 3 | 0.003086 | 9.0256e-06
1 | 10589079 | 2016-04-27 09:02 | 2016-04-27 15:13 | 371 | 45 | 16695 | 0.050223 | 0.049816 | 0.00013537 | NAPA ID:17785 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017785 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 773 | NONE | To complete line maintenance. Works location: Piakonui Rd, Matamata. WO 30024595 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.024908 | 5.5 | 2017 | 2016-04-27 | B | 45 | 0.049816 | 0.00013537
1 | 10589281 | 2016-04-05 10:40 | 2016-04-10 11:25 | 7245 | 4 | 28980 | 0.087205 | 0.087168 | 1.2037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | ( CAR Q11 ) Switching to isolate & eath cable to Manganui ski field ( cable exposed & requires cover ) Isolation at Fused/sw 8837/2. Cable covered all service restored. Customer requested power disconnected for safety. Close Approach Consent: 29357. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.087168 | 11 | 2017 | 2016-04-05 | C | 4 | 0.087168 | 1.2037e-05
1 | 10589636 | 2016-04-05 14:10 | 2016-04-05 21:35 | 445 | 1 | 445 | 0.0013391 | 0.00133 | 3.0091e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | TP2542 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | NDR - cust has backed into Tx - enclosed - HV is still on but is leaking, taking power away from LV side. NDR # 51765. Replaced trany from a 30KVa for a 15KVA To be replace when a bigger one turns up | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.00133 | 11 | 2017 | 2016-04-05 | C | 1 | 0.00133 | 3.0091e-06
1 | 10590944 | 2016-04-29 09:15 | 2016-04-29 11:28 | 133 | 3 | 399 | 0.0012003 | 0.001173 | 9.0245e-06 | NAPA ID:18296 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 018296 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC2151 | NONE | Straighten pole & replace X-Arms. Works location: Hwy 29, Hinuera. WO 30018274 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0005865 | 5.5 | 2017 | 2016-04-29 | B | 3 | 0.001173 | 9.0245e-06
1 | 10590989 | 2016-04-29 10:05 | 2016-04-29 12:33 | 148 | 2 | 296 | 0.00089042 | 0.000872 | 6.0163e-06 | NAPA ID:17802 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017802 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP580 | NONE | To replace 11kV arms & Install 400V Fuse Disconnector. Works location: Piakoiti Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000436 | 5.5 | 2017 | 2016-04-29 | B | 2 | 0.000872 | 6.0163e-06
1 | 10592101 | 2016-04-06 04:47 | 2016-04-06 05:30 | 43 | 1556 | 37195.2167 | 0.11192 | 0.097877 | 0.0046822 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | 33kV CB 3722 and 33kV CB 3738 and 11kV CB WH6 all tripped locked out, Flags, Diff trip (onT2) Loss of supply to entire sub. Limited back feeds applied. On inspection, no cause found, unknown as to why CB's tripped on 'Diff'. T2 re-livened and all load restored. Requires Safety manager for Protection review. Sub tech to send protection data to Mike Allpress for review. 2r Line patrol 0515. 2r repair nothing found. PROTECTION REVIEW: 608658. | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.097877 | 11 | 2017 | 2016-04-06 | C | 1556 | 0.097877 | 0.0046822
1 | 10593692 | 2016-04-06 06:20 | 2016-04-06 07:30 | 70 | 6 | 420 | 0.0012638 | 0.001209 | 1.8055e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC202 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp duck strike on LV. Job sucked up but only at TC202. 2 phase. | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.001209 | 11 | 2017 | 2016-04-06 | C | 6 | 0.001209 | 1.8055e-05
1 | 10596082 | 2016-04-29 08:30 | 2016-04-29 14:39 | 368 | 9 | 3317.1 | 0.0099784 | 0.009897 | 2.7074e-05 | NAPA ID:17851 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 017851 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7153 | NONE | Replace poles and crossarms. Works location: Millers Rd, Masterton. WO 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0049485 | 5.5 | 2017 | 2016-04-29 | B | 9 | 0.009897 | 2.7074e-05
1 | 10596247 | 2016-04-06 10:10 | 2016-04-06 11:17 | 66 | 67 | 4474.4833 | 0.013464 | 0.012859 | 0.00020161 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228176 | INSULATOR | 11kv Pin broke please fix at te7-164. Materials used 11kv pin insulator. Found during site visits | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.012859 | 11 | 2017 | 2016-04-06 | C | 67 | 0.012859 | 0.00020161
1 | 10596837 | 2016-04-06 10:10 | 2016-04-06 14:05 | 235 | 4 | 940 | 0.0028286 | 0.002792 | 1.2036e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | Planned LV ourtage - NAPA 18365-1 | NONE | This is a planned LV outage for tree cutting - NAPA 18365-1. Transformer hardwired, HV fuses used for isolation. HV outage was not planned but HV fuses T2705 had to be opened for isolation. | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.002792 | 11 | 2017 | 2016-04-06 | C | 4 | 0.002792 | 1.2036e-05
1 | 10596994 | 2016-05-02 09:44 | 2016-05-02 14:25 | 281 | 36 | 10116 | 0.030429 | 0.030104 | 0.00010829 | NAPA ID:18322 TP_WAIKINO GXP > WHANGAMATA SUB > PORT RD | 11 | Planned | 018322 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3358 | NONE | Replace damaged unit TC3358. Repair and transfer LV frame and cables to the new unit. Works location; Chartwell AVe, Whangamata. WO 30025069 | F2/F3 | PORT RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.015052 | 5.5 | 2017 | 2016-05-02 | B | 36 | 0.030104 | 0.00010829
1 | 10597843 | 2016-04-22 08:45 | 2016-04-22 14:25 | 340 | 14 | 4760 | 0.01432 | 0.014194 | 4.2119e-05 | NAPA ID:16976 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | 016976 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4789 | NONE | Replace SWER TX TC4789 and Lightning Arrestors at various sites on SWER Line. Works location: Port Jackson Rd, Coromandel. WO 30013541 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.007097 | 5.5 | 2017 | 2016-04-22 | B | 14 | 0.014194 | 4.2119e-05
1 | 10597866 | 2016-04-28 09:30 | 2016-04-28 15:10 | 340 | 131 | 44568.3833 | 0.13407 | 0.13289 | 0.00039408 | NAPA ID:18585 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 7 | 11 | Planned | 018585 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1417 | NONE | Replacing rusted old SD unit with new Safelink unit. Switchgear received and shut to be done in school holidays due to transformer X369 supplying School on Dillon Dr. Works location: Dillon Dr. WO 30014521 | F3 | MANGATI RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.066445 | 5.5 | 2017 | 2016-04-28 | B | 131 | 0.13289 | 0.00039408
1 | 10597980 | 2016-04-29 14:10 | 2016-04-29 14:25 | 15 | 4 | 60 | 0.00018049 | 0.000144 | 1.2033e-05 | NAPA ID:17804 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 017804 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3924 | NONE | To install a 400V Fuse Disconnector. Works location: Piakoiti Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 7.2e-05 | 5.5 | 2017 | 2016-04-29 | B | 4 | 0.000144 | 1.2033e-05
1 | 10598195 | 2016-04-06 16:04 | 2016-04-06 17:25 | 80 | 3 | 241.8 | 0.0007276 | 0.0007 | 9.0273e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 5264 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3Amp HV Links | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.0007 | 11 | 2017 | 2016-04-06 | C | 3 | 0.0007 | 9.0273e-06
1 | 10601643 | 2016-04-06 22:00 | 2016-04-06 22:55 | 55 | 6 | 330 | 0.000993 | 0.000938 | 1.8055e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5282E | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replaced all 3 DDOs at Transformer 5282E & 3x 3 amp fuses | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000938 | 11 | 2017 | 2016-04-06 | C | 6 | 0.000938 | 1.8055e-05
1 | 10602696 | 2016-04-07 01:58 | 2016-04-07 05:48 | 230 | 1546 | 132852.2167 | 0.39976 | 0.38581 | 0.0055758 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 9820 | CABLE - REPLACE LESS THAN 5 METRES | At 01:57, Maraetai Sub, CB 4 Arawa St Feeder, Tripped, A + B O/C, E/F, L/O. Faultmen dispatched and investigation began. Feeder sectionalised. Backfeed supplied from MAR 2, Sw/gear 1577 Closed. Have an 11kV Cable Fault Between Sw/gear IC1450 & Sw/gear 9820/3. 11kV Cable Fault Between Sw/gear IC1450 & Sw/gear 9820/3. This is now a DNO 160404. 2r 0421 2r repair 0551 NOC PAY 1R PATROL AND 2R PATROL - REPAIR TO BE CHARGED TO THE DNO 160404 | F3 | ARAWA ST | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.38581 | 11 | 2017 | 2016-04-07 | C | 1546 | 0.38581 | 0.0055758
1 | 10605072 | 2016-04-26 09:42 | 2016-04-26 16:28 | 406 | 76 | 30244 | 0.090983 | 0.090297 | 0.00022863 | NAPA ID:17820 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 017820 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 220013 | NONE | Replace poles, hardware and conductor. Works location: Welcome Bay Rd. WO 30017823 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.045149 | 5.5 | 2017 | 2016-04-26 | B | 76 | 0.090297 | 0.00022863
1 | 10608943 | 2016-04-07 13:52 | 2016-04-07 13:53 | 1 | 2 | 2.0333 | 6.1184e-06 | 0 | 6.0181e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2394 | FUSE - ELEMENT/LINK (HV) | 2 x amp fuses. Cause: Black bird (got no foot now). | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-04-07 | C | 2 | 0 | 6.0181e-06
1 | 10609223 | 2016-04-29 13:30 | 2016-04-29 15:12 | 102 | 75 | 7650 | 0.023013 | 0.022335 | 0.00022561 | NAPA ID:18673 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 6 | 11 | Planned | 018673 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 8376 | NONE | Tx 594 has leak. Shutting down to investigate and possible repair leak. Works location: Doralto Rd. WO 10150320 | F4 | BROOKLANDS 6 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.011168 | 5.5 | 2017 | 2016-04-29 | B | 75 | 0.022335 | 0.00022561
1 | 10609284 | 2016-04-29 10:00 | 2016-04-29 10:38 | 38 | 1 | 38 | 0.00011431 | 0.000105 | 3.0081e-06 | NAPA ID:18672 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 4 | 11 | Planned | 018672 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 8715 | NONE | Repair oil leak on switchgear 8715. Works location: Swans Rd. WO 30014521 | F1 | AIRPORT DRIVE | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 5.25e-05 | 5.5 | 2017 | 2016-04-29 | B | 1 | 0.000105 | 3.0081e-06
1 | 10610514 | 2016-04-08 00:34 | 2016-04-08 15:00 | 865 | 1268 | 108477.6333 | 0.32641 | 0.31497 | 0.0040141 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | CB 5 Cable fault | CABLE - REPLACE LESS THAN 5 METRES | CB 5 Welcome Bay sub tripped at 00:34. Feeder sectionalised. Faulted cable identified between CB 5 & Sw/gear SD4-435. All supply restored at 02:29. 2 r requested for repairs etc. AP issued at 11:25 to repair faulted cable. 11kV cable to transformer TD4-681 (Beyond Fuse/Sw SD4-441) in same trench as faulted cable also found to be damaged. Revised AP issued to repair both cables. Supply to transformer TD4-681 disconnected between 14:03 & 15:00 to connect generator. Cable to transformer TD4-681 repaired 09/04/16. Supply to TD4-681disconnected between 09:50 & 10:15 to disconnect generator & restore cable. Cable between CB 5 & Sw/gear SD4-435 repaired also on 09/04/16. To remain out of service until Monday 11th for Techs to complete joint testing. Fault began on Friday 8th and was worked. All charges from Saturday 9th to be to DNO 160411 | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.31497 | 11 | 2017 | 2016-04-08 | C | 1268 | 0.31497 | 0.0040141
1 | 10612086 | 2016-04-08 03:39 | 2016-04-08 06:28 | 169 | 115 | 19452.25 | 0.058533 | 0.057494 | 0.00034604 |  | 6.6 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 776099 | CONDUCTOR - REPAIR/REHANG | Faultman attending "No Power" callout advised live 6.6kV Conductor on ground caused by tree branch. (No trippings). CB 1022 open from NOC and isolation made at recloer. Required 2 sleeves to rejoint 8 metres conductor. 1 HT fuse (10A) had also blown at 2637. Reloaded OK. (Fault caused by tree branch falling onto conductor). | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.057494 | 6.6 | 2017 | 2016-04-08 | C | 115 | 0.057494 | 0.00034604
1 | 10613920 | 2016-04-08 10:18 | 2016-04-08 12:30 | 132 | 1 | 132.2333 | 0.0003979 | 0.000388 | 3.009e-06 | 2 x 3A | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | PU240 | FUSE - ELEMENT/LINK (HV) | Reload reliven 2 x 3A Fuses due to Bird Strike. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000388 | 11 | 2017 | 2016-04-08 | C | 1 | 0.000388 | 3.009e-06
1 | 10614683 | 2016-04-08 15:20 | 2016-04-08 15:51 | 30 | 144 | 2811.85 | 0.008461 | 0.007161 | 0.0004333 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4620 | FUSE - LV ELEMENT/LINK - HRC (LV) | Hv to transformer isolated for safety to access and replace LV fuses at Transformer TC4620. Reload reliven at TC4620. Used 1 x 200A HRC LV Fuse. Cause - Overheated | F3 | BUFFALO BEACH | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.007161 | 11 | 2017 | 2016-04-08 | C | 144 | 0.007161 | 0.0004333
1 | 10614746 | 2016-04-27 08:42 | 2016-04-27 15:41 | 419 | 79 | 17685 | 0.053201 | 0.052488 | 0.00036099 | NAPA ID:17981 TP_TE MATAI GXP > PAENGAROA SUB > MAUNGARANGI RD | 11 | Planned | 017981 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 852939 | NONE | 1/ CUT GAP UNDER LLWP AT POLE 393957 [ SF6-009 TO BE OPEN ]. 2/ CUT GAP UNDER CACD AT POLE 852939 [ SF6-039 TO BE OPEN TO CUT GAP AND CLOSE TO BACK FEED AREA ]. 3/ AP FROM LL GAP AT POLES 852939 TO 393957 INSTALL TEMP LINKS #20 & ABS #26 DURING SHUTDOWN. 4/ RESTORE GAP AT POLE 393957 [ SF6-009 TO BE CHECKED OPENED ]. 5/ RESTORE GAP AT POLE 852939 [ SF6-039 TO BE RE-OPENED TO RESTORE GAP ]. Works location: Hwy 33, Paengaroa. WO 30014831 | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.026244 | 5.5 | 2017 | 2016-04-27 | B | 79 | 0.052488 | 0.00036099
1 | 10614933 | 2016-04-08 14:07 | 2016-04-08 16:38 | 150 | 1 | 150.7167 | 0.00045351 | 0.000444 | 3.009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 2972 | UNKNOWN | Replace 2 x 6 Amp fuse due to Bird. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000444 | 11 | 2017 | 2016-04-08 | C | 1 | 0.000444 | 3.009e-06
1 | 10615060 | 2016-04-08 14:17 | 2016-04-08 15:48 | 90 | 1000 | 71157.05 | 0.21411 | 0.20509 | 0.003009 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Feeder sectionalised, no fault found. Restored OK. Tree contractors had a CAC out for the area and a HLT applied to CB 8. Contacted tree contractors who were finished their work and they returned their CAC to enable us to reliven. 2r line patrol 1527. 2r repair no fault complete | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.20509 | 11 | 2017 | 2016-04-08 | C | 1000 | 0.20509 | 0.003009
1 | 10619994 | 2016-05-03 09:58 | 2016-05-03 13:00 | 182 | 92 | 16751.6667 | 0.050389 | 0.049558 | 0.00027674 | NAPA ID:18710 TP_MANGAMAIRE GXP > PARKVILLE SUB > EKETAHUNA | 11 | Planned | 018710 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P12314 | NONE | To replace ABS U3 and remove DNO # 160319. Septimus Road, Eketahuna, Parkville. W/O 30024956. | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.024779 | 5.5 | 2017 | 2016-05-03 | B | 92 | 0.049558 | 0.00027674
1 | 10621984 | 2016-04-09 06:30 | 2016-04-09 08:44 | 134 | 2 | 268.3 | 0.00080731 | 0.000789 | 6.0179e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | B1-37 | FUSE - ELEMENT/LINK (HV) | replaced x2 HV fuse links 3amp at fuse B1-37 cause unknown. No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 0.000789 | 11 | 2017 | 2016-04-09 | C | 2 | 0.000789 | 6.0179e-06
1 | 10623343 | 2016-04-09 12:28 | 2016-04-09 14:11 | 103 | 1 | 103.3667 | 0.00031103 | 0.000302 | 3.0089e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2904 | FUSE - ELEMENT/LINK (HV) | Replaced 2 x 3a HV fuses | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.000302 | 11 | 2017 | 2016-04-09 | C | 1 | 0.000302 | 3.0089e-06
1 | 10623988 | 2016-04-09 21:15 | 2016-04-10 00:06 | 171 | 3 | 513 | 0.0015436 | 0.001516 | 9.0269e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 739345 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, ALL PHASES | Faultman found Fuses 8834 blown and found tree through the line at pole 739345, line was isolated at Fuses 8834 to remove the tree and repair the lines.Tree out side notice zone on other side of the road. 20 meters of squirrel conductor was used. 4 X sleeves used. NDR: N100137 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001516 | 11 | 2017 | 2016-04-09 | C | 3 | 0.001516 | 9.0269e-06
1 | 10627846 | 2016-04-10 19:35 | 2016-04-10 22:00 | 145 | 1 | 145 | 0.0004363 | 0.000427 | 3.0089e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1993 | CONDUCTOR - REPAIR/REHANG | Faultman found the neutral screen cable at transformer T1993 had been ripped off on the LV side, suspect high load has gone past as cable runs across the road, transformer was isolated to connect new neutral screen cable to the transformer. NDR 21820 .38 meters of Neutral screen cable used. 1 X 2 amp HV fuses replaced. 2 X dead-ends & 4 connector used. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000427 | 11 | 2017 | 2016-04-10 | C | 1 | 0.000427 | 3.0089e-06
1 | 10629116 | 2016-04-11 01:00 | 2016-04-11 01:17 | 16 | 2 | 32.9667 | 9.9194e-05 | 8.1e-05 | 6.0178e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2782 | UNKNOWN | Stradford GXP CB 2782 tripped on Neutral time O/C flags, at same time Recloser 6942 tripped on A & B phase O/C & E/F flags, spoke to Cheal all OK at plant so Recloser 6942 was closed, line was patrolled and sectionalised and fault found the fault indicators flash passed ABS 403 towards Kaponga Sub. Need a line patrol in morning as goes cross country fault man cannot follow line in the dark. 2r line patrol 0130. 2r line patrol Reece from start. 2r repair nothing found. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 8.1e-05 | 11 | 2017 | 2016-04-11 | C | 2 | 8.1e-05 | 6.0178e-06
1 | 10629645 | 2016-04-08 20:08 | 2016-04-08 21:00 | 52 | 3 | 156 | 0.00046941 | 0.000442 | 9.0271e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T3/492 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Fuses M84 fiund tripped. Defective Transformer T3/492 to be changed. Customer on LV Generator from 2100 on 8/4/16. | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000442 | 11 | 2017 | 2016-04-08 | C | 3 | 0.000442 | 9.0271e-06
1 | 10629698 | 2016-05-03 09:41 | 2016-05-03 13:03 | 201 | 79 | 15923.7667 | 0.047899 | 0.047185 | 0.00023763 | NAPA ID:18806 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | 018806 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC484 | NONE | REPLACE DNO 160329 ABS IC484 AND STRAIN XARMS. Works location: Mangawhero Rd, Patetonga. WO 30025339 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.023592 | 5.5 | 2017 | 2016-05-03 | B | 79 | 0.047185 | 0.00023763
1 | 10629701 | 2016-04-27 09:02 | 2016-04-27 14:37 | 335 | 393 | 131655 | 0.39605 | 0.39251 | 0.0011822 | NAPA ID:17739 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 017739 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2125 | NONE | Replace cross arms at various sites. Works location: Cathedral Court, Whitianga. WO 30012345 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.19625 | 5.5 | 2017 | 2016-04-27 | B | 393 | 0.39251 | 0.0011822
1 | 10629995 | 2016-04-11 09:17 | 2016-04-11 11:48 | 150 | 1 | 150.7 | 0.00045344 | 0.000444 | 3.0089e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W13525 | FUSE - ELEMENT/LINK (HV) | Trees in line at pole W13525. NDR 247810. Found 2 fuses blown. Isolate 3rd fuse to remove trees. | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000444 | 11 | 2017 | 2016-04-11 | C | 1 | 0.000444 | 3.0089e-06
1 | 10630710 | 2016-04-22 08:40 | 2016-04-22 17:14 | 514 | 22 | 1562 | 0.0046993 | 0.0045 | 0.00013237 | NAPA ID:18808 TP_KINLEITH GXP > MARAETAI ROAD SUB > ARAWA ST | 11 | Planned | 018808 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 9784 | NONE | Install Safe link to replace Magnefix unit. Works location: Tainui St, Tokoroa. WO 30002496 | F3 | ARAWA ST | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.00225 | 5.5 | 2017 | 2016-04-22 | B | 22 | 0.0045 | 0.00013237
1 | 10630809 | 2016-04-11 14:29 | 2016-04-11 15:14 | 44 | 39 | 1735.7 | 0.0052226 | 0.00487 | 0.00011735 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 324 | INSULATOR | Red Defect needs repairing today. Broken insulator on ABS. Emergency switching to cut jumpers from both sides of ABS 324 as a temporary repair. All repairs to be completed under DNO 160406. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.00487 | 11 | 2017 | 2016-04-11 | C | 39 | 0.00487 | 0.00011735
1 | 10631487 | 2016-04-13 09:00 | 2016-04-13 12:35 | 215 | 4 | 860 | 0.0025876 | 0.002551 | 1.2035e-05 | NAPA ID:16947 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | 016947 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | V1303 | CROSSARM - WHOLE ASSEMBLY | LLP to break Jumpers Pole V1303. AP to replace cross arms. LLP to restore jumpers Pole V1303. Works Location: 1534 Colville Road, Waitete Bay, Coromandel. W/O 30012346 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.0012755 | 5.5 | 2017 | 2016-04-13 | B | 4 | 0.002551 | 1.2035e-05
1 | 10631670 | 2016-04-29 08:30 | 2016-04-29 08:41 | 10 | 111 | 1193.25 | 0.0035895 | 0.002587 | 0.00033391 | NAPA ID:18805 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 3 | 11 | Planned | 018805 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8778 | NONE | Replacing defective Magnefix Links at 58/3. Works location: South Rd. WO 30015277 | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.0012935 | 5.5 | 2017 | 2016-04-29 | B | 111 | 0.002587 | 0.00033391
1 | 10631688 | 2016-04-11 14:40 | 2016-04-11 16:00 | 80 | 4 | 320.8 | 0.00096526 | 0.000929 | 1.2036e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2892T | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuse. Cause unknown. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000929 | 6.6 | 2017 | 2016-04-11 | C | 4 | 0.000929 | 1.2036e-05
1 | 10631913 | 2016-04-28 08:58 | 2016-04-28 15:23 | 385 | 15 | 5775 | 0.017372 | 0.017237 | 4.5123e-05 | NAPA ID:17843 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 017843 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 220013 | NONE | Replace poles, hardware and conductor. Works location: Waitao Rd. WO 30017823 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.0086185 | 5.5 | 2017 | 2016-04-28 | B | 15 | 0.017237 | 4.5123e-05
1 | 10633539 | 2016-04-12 09:08 | 2016-04-12 14:49 | 341 | 658 | 27537.0667 | 0.082856 | 0.076916 | 0.0019798 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 752524 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, NOT ALL PHASES | ( MA 5 ) tripped A, B & C Ph O/C, L/O Report of trees on line at pole 752524. Isolation between ABS 6741, ABS 208 & CB 5 with back feed via MSW/Gear 12026/3. Large tree branch snapped & fell into lines. 2 x O/H H/V lines repaired all service restored. NDR No 100138. Materials 10 x meters conductor, 1 x H/V arm complete, 1 x link arm, 4 x H/V sleeves, 2 x jumpers. 2r line patrol 0940. 2r repair 0940 found fault during power off so times are the same. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.076916 | 11 | 2017 | 2016-04-12 | C | 658 | 0.076916 | 0.0019798
1 | 10635166 | 2016-04-21 09:00 | 2016-04-21 11:55 | 175 | 5 | 875 | 0.0026325 | 0.002587 | 1.5043e-05 | NAPA ID:16556 TP_HUIRANGI GXP > WAITARA EAST SUB > WAITARA EAST TOWN | 11 | Planned | 016556 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 3468T | NONE | Replace existing transformer 3468T with new 100kVA Ground Mounted transformer with new earthing system, new 185 3 core HV cable and new HV fuses (12142). Works location: Manukorihi Rd. WO 10159770 | F4 | WAITARA EAST TOWN | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.0012935 | 5.5 | 2017 | 2016-04-21 | B | 5 | 0.002587 | 1.5043e-05
1 | 10635615 | 2016-04-12 09:51 | 2016-04-12 15:30 | 339 | 2644 | 120380.8667 | 0.36221 | 0.33834 | 0.0079555 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | - | SWITCH (HV) | CB7 tripped on oC E/F and L/O. Rec 9207 tripped on U/V, L/O. Investigate and repair faulted SDAF switch. Jumpers at S6070 to restore oms job. 2r line patrol 1027. 2r repair 1050 | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.33834 | 11 | 2017 | 2016-04-12 | C | 2644 | 0.33834 | 0.0079555
1 | 10638823 | 2016-04-12 10:17 | 2016-04-12 14:29 | 252 | 3 | 756 | 0.0022747 | 0.002247 | 9.0266e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 1376 | NONE | ( BBK2 ) Em switching to remove trees from transformer structure 1376. Trees removed all service restored Isolation at fuses 8170. NDR No 38765. OMS No 10630549 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.002247 | 11 | 2017 | 2016-04-12 | C | 3 | 0.002247 | 9.0266e-06
1 | 10639405 | 2016-04-17 07:45 | 2016-04-17 08:43 | 58 | 1 | 58.5833 | 0.00017626 | 0.000167 | 3.0087e-06 | NAPA ID:18367 TP_CARRINGTON GXP > BELL BLOCK SUB | 11 | Planned | 018367 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 966/21 | SWITCH (HV) | Outage negotiated with major consumer for date. This is to repair oil leak on switch 966/21. | F1 | PARAITE RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 8.35e-05 | 5.5 | 2017 | 2016-04-17 | B | 1 | 0.000167 | 3.0087e-06
1 | 10660190 | 2016-04-12 23:17 | 2016-04-13 00:47 | 89 | 255 | 17773.55 | 0.053478 | 0.051176 | 0.00076726 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | H131 | UNKNOWN | Line sectionalised and patrolled with nothing obvious found . Supply restored. 2r line patrol 0013. No repair. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.051176 | 11 | 2017 | 2016-04-12 | C | 255 | 0.051176 | 0.00076726
1 | 10661052 | 2016-04-13 00:44 | 2016-04-13 02:48 | 123 | 1 | 123.6667 | 0.00037209 | 0.000363 | 3.0088e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 6772/2 | RECLOSER (HV) | On arrival found CB 6772/2 open . After checking all ok @ Taranaki by Products closed on load with no apparent reason for tripping. | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.000363 | 11 | 2017 | 2016-04-13 | C | 1 | 0.000363 | 3.0088e-06
1 | 10661149 | 2016-04-13 03:25 | 2016-04-13 05:22 | 117 | 8 | 939.0667 | 0.0028255 | 0.002753 | 2.4071e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4572 | FUSE - ELEMENT/LINK (HV) | Replaced 3 x 3amp ht fuse Suspect Weather | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002753 | 11 | 2017 | 2016-04-13 | C | 8 | 0.002753 | 2.4071e-05
1 | 10661435 | 2016-04-26 10:08 | 2016-04-26 15:16 | 308 | 29 | 1860 | 0.0055955 | 0.005333 | 8.7241e-05 | NAPA ID:18869 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 7 | 11 | Planned | 018869 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X525 | NONE | Replace old transformer with new 50kVA transformer X525. Works location: Frankley Rd, New Plymouth. WO 30026097 | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.0026665 | 5.5 | 2017 | 2016-04-26 | B | 29 | 0.005333 | 8.7241e-05
1 | 10662620 | 2016-05-02 09:40 | 2016-05-02 13:47 | 247 | 28 | 6916 | 0.020804 | 0.02055 | 8.4225e-05 | NAPA ID:18547 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 018547 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links T32 | NONE | To change 11kv larch pole. Works location: Ruatea Rd, Pori. WO 30016664 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.010275 | 5.5 | 2017 | 2016-05-02 | B | 28 | 0.02055 | 8.4225e-05
1 | 10662700 | 2016-04-13 13:48 | 2016-04-13 14:34 | 46 | 1 | 46.2167 | 0.00013906 | 0.00013 | 3.0088e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | no fault | UNKNOWN | E-map update in progress. Part of Planned outage happening - OMS 10661805 - didn't roll up as Emap update in progress. Manual checks not carried out by dispatcher. Powerco error. | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.00013 | 11 | 2017 | 2016-04-13 | C | 1 | 0.00013 | 3.0088e-06
1 | 10662899 | 2016-05-02 10:00 | 2016-05-02 14:09 | 249 | 42 | 10458 | 0.031458 | 0.031079 | 0.00012634 | NAPA ID:18023 TP_CARRINGTON GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | 018023 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 159 | NONE | Replace ABS159 & Xarms. Works location: Hwy 3 Mountain Rd, Bell Block. WO 30017990 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.015539 | 5.5 | 2017 | 2016-05-02 | B | 42 | 0.031079 | 0.00012634
1 | 10662988 | 2016-05-04 08:33 | 2016-05-04 15:56 | 442 | 302 | 83730.3167 | 0.25186 | 0.24913 | 0.00062264 | NAPA ID:18501 TP_MASTERTON GXP > TINUI SUB > CASTLEPOINT | 11 | Planned | 018501 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S168 | NONE | Change RMU to new Safelink CFC RMU (New Label 11072). Works location: Jetty Rd, Castlepoint. WO 30002199 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.12456 | 5.5 | 2017 | 2016-05-04 | B | 302 | 0.24913 | 0.00062264
1 | 10663008 | 2016-05-04 09:05 | 2016-05-04 15:25 | 380 | 9 | 3420 | 0.010287 | 0.010205 | 2.7071e-05 | NAPA ID:17620 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | 017620 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 014 | NONE | Replacing 11kV poles. Works location: Parapara Rd. WO 30002307. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.0051025 | 5.5 | 2017 | 2016-05-04 | B | 9 | 0.010205 | 2.7071e-05
1 | 10663081 | 2016-05-02 09:13 | 2016-05-02 14:50 | 337 | 38 | 12806 | 0.038521 | 0.038177 | 0.00011431 | NAPA ID:17254 TP_KINLEITH GXP > MARAETAI ROAD SUB > OLD CAMBRIDGE RD | 11 | Planned | 017254 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole A0179 | NONE | Switching and issue CACD to Asplund for tree cutting. Works location: Campbell Rd, Tokoroa. WO 10152355 | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.019089 | 5.5 | 2017 | 2016-05-02 | B | 38 | 0.038177 | 0.00011431
1 | 10663108 | 2016-05-04 10:45 | 2016-05-04 12:15 | 90 | 37 | 3330 | 0.010016 | 0.009682 | 0.00011129 | NAPA ID:18222 TP_BUNNYTHORPE GXP | 11 | Planned | 018222 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D70 | NONE | Change 3 x 33kV insulators only. Works location: Bunnythorpe West feeder line. WO 30011213 | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.004841 | 5.5 | 2017 | 2016-05-04 | B | 37 | 0.009682 | 0.00011129
1 | 10663122 | 2016-04-13 18:15 | 2016-04-13 20:40 | 145 | 3 | 435 | 0.0013088 | 0.001281 | 9.0265e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/254 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced 1 X 3 Phase 15 kvA Transformer | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.001281 | 11 | 2017 | 2016-04-13 | C | 3 | 0.001281 | 9.0265e-06
1 | 10664586 | 2016-04-14 05:13 | 2016-04-14 07:12 | 118 | 923 | 29499.1333 | 0.088758 | 0.080426 | 0.0027771 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | 1 x A/R on CB 4 Thames sub. E/F & O/C flags. Trip L/O on sectionaliser 9871/2. Line sectionalised & patrolled. No fault found. Possible bird strike. All supply restored. 2r line patrol 0627. 2r repair no fault found | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.080426 | 11 | 2017 | 2016-04-14 | C | 923 | 0.080426 | 0.0027771
1 | 10667122 | 2016-05-02 10:10 | 2016-05-02 11:25 | 75 | 10 | 750 | 0.002256 | 0.002165 | 3.008e-05 | NAPA ID:18515 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018515 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2935 | NONE | To replace the 11kV Fuse arm 7 Install a 400V Fuse Disconnector. Works location: Morrinsville-Walton Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0010825 | 5.5 | 2017 | 2016-05-02 | B | 10 | 0.002165 | 3.008e-05
1 | 10667376 | 2016-04-30 09:01 | 2016-04-30 13:03 | 242 | 46 | 11139.6667 | 0.03351 | 0.033094 | 0.00013837 | NAPA ID:17953 TP_LINTON GXP > TURITEA SUB | 11 | Planned | 017953 | ZONE SUB EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB 6 | NONE | Connect Linton and Linton Express Feeders together (Temporary) at Pole #00184 to allow 11kV Switchboard Replacement at Turitea. PHASING TO BE CONFIRMED. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.016547 | 5.5 | 2017 | 2016-04-30 | B | 46 | 0.033094 | 0.00013837
1 | 10667465 | 2016-05-03 08:36 | 2016-05-03 12:30 | 234 | 70 | 16380 | 0.049271 | 0.048639 | 0.00021056 | NAPA ID:18374 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 018374 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1069 | NONE | Replace X arms at ABS 1069 & Fuses FP1214. Works location: Buckland Rd, Hinuera. WO 30018274 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.02432 | 5.5 | 2017 | 2016-05-03 | B | 70 | 0.048639 | 0.00021056
1 | 10667501 | 2016-05-03 09:48 | 2016-05-03 14:10 | 262 | 31 | 8122 | 0.024431 | 0.024151 | 9.3248e-05 | NAPA ID:18671 TP_HAWERA GXP > LIVINGSTONE SUB > PATEA | 11 | Planned | 018671 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse LI281 | NONE | Replace old rusted tx with new unit of same size. Works location: Gloucester St. WO 30001134 | F4 | PATEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.012075 | 5.5 | 2017 | 2016-05-03 | B | 31 | 0.024151 | 9.3248e-05
1 | 10667507 | 2016-04-14 09:53 | 2016-04-14 12:30 | 157 | 700 | 47081.6 | 0.14166 | 0.13534 | 0.0021122 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 738850 | STAY WIRE | Initial trip on Cloton Rd 11kV S21 on O/C. Fault caused by Hedge Mulcher coming into contact with a stay wire which broke and wound around 33kV cross arm above. Outage also required outage on SFD GXP CB2842 with isolation at ABS 526, 529 and CB2842. 11kV Isolation between ABS 5740 and 5732. The stay wire was able to be removed using a fuse stick safely. The stay wire will need to be rpaired later. Feeders restored OK. NDR 38863. NOTE: Cheal Recloser CB6942 tripped coincident with S21 tripping (O/C, EF Flags). Spur line checked OK and reclosed. CHEAL later requested CB open as they were having trouble synchronising. Could find no problem in Powerco Network. Reclosed when requested. | F4 | CLOTON RD NORTH EAST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.13534 | 11 | 2017 | 2016-04-14 | C | 700 | 0.13534 | 0.0021122
1 | 10668228 | 2016-05-03 12:43 | 2016-05-03 14:04 | 81 | 5 | 405 | 0.0012182 | 0.001173 | 1.504e-05 | NAPA ID:18540 TP_HAWERA GXP > WHAREROA SUB > MANAWAPOU RD | 11 | Planned | 018540 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | W5093 | NONE | Replace transformer W5093 at end of life. Works location: Manawapou Rd, Hawera. WO 30018768 | S1 | WHITE 33KV | HAWERA | Taranaki | TP_HAWERA | Western Electricity | POWERCO | 0.0005865 | 5.5 | 2017 | 2016-05-03 | B | 5 | 0.001173 | 1.504e-05
1 | 10668268 | 2016-05-03 09:18 | 2016-05-03 11:11 | 113 | 2 | 226 | 0.00067981 | 0.000661 | 6.0159e-06 | NAPA ID:18533 TP_STRATFORD GXP > KAPONGA SUB > MANAIA RD | 11 | Planned | 018533 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 3758T | NONE | Replace TX 3758T Due to end of life. Works location: Opunake Rd. WO 30018768 | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.0003305 | 5.5 | 2017 | 2016-05-03 | B | 2 | 0.000661 | 6.0159e-06
1 | 10668564 | 2016-05-04 09:35 | 2016-05-04 15:00 | 325 | 6 | 1950 | 0.0058655 | 0.005811 | 1.8048e-05 | NAPA ID:18654 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 4 | 11 | Planned | 018654 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X577 | NONE | Replace transformer X577 with like for like. Works location: Breakwater Rd. WO 30018769 | F4 | MOTUROA 4 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.0029055 | 5.5 | 2017 | 2016-05-04 | B | 6 | 0.005811 | 1.8048e-05
1 | 10668591 | 2016-05-05 13:00 | 2016-05-05 13:32 | 32 | 208 | 6656 | 0.020021 | 0.018143 | 0.00062564 | NAPA ID:18807 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 8 | 11 | Planned | 018807 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 389 | NONE | Replacing defective Magnefix Links at 560/1, 560/3, 399/4. Works location: South Rd. WO 30015277 | F3 | MOTUROA 8 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.0090715 | 5.5 | 2017 | 2016-05-05 | B | 208 | 0.018143 | 0.00062564
1 | 10668689 | 2016-05-03 10:02 | 2016-05-03 15:21 | 318 | 37 | 11797.45 | 0.035487 | 0.035152 | 0.0001113 | NAPA ID:18440 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | 018440 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1068 | NONE | Overhead Line Maintenance. Works location: Alexandra Rd, Walton. WO 30024596 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.017576 | 5.5 | 2017 | 2016-05-03 | B | 37 | 0.035152 | 0.0001113
1 | 10668715 | 2016-05-05 10:15 | 2016-05-05 15:15 | 300 | 3 | 900 | 0.0027071 | 0.00268 | 9.0236e-06 | NAPA ID:18441 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | 018441 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Fuses FC1410 | NONE | To complete line maint. on the 11kV Service line beyond FC1410. Works location: Alexandra Rd, Walton. WO 30024596 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.00134 | 5.5 | 2017 | 2016-05-05 | B | 3 | 0.00268 | 9.0236e-06
1 | 10668718 | 2016-05-01 08:19 | 2016-05-01 16:36 | 497 | 95 | 47215 | 0.14203 | 0.14117 | 0.00028577 | NAPA ID:17376 TP_KOPU GXP > MATATOKI SUB > KOPU | 11 | Planned | 017376 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole LC4014 | NONE | Install New High Voltage Cable from LC4014 on O/H Line to TC4940. Plus new 400 volt underground cable across Road as well. Plus replace Cross Arms etc on Pole with LC4014. Works location: Kopu, Thames. WO 10148373 | F1/F4 | KOPU | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.070584 | 5.5 | 2017 | 2016-05-01 | B | 95 | 0.14117 | 0.00028577
1 | 10668730 | 2016-05-06 09:15 | 2016-05-06 14:35 | 320 | 2 | 640 | 0.001925 | 0.001906 | 6.0157e-06 | NAPA ID:18444 TP_PIAKO GXP > WALTON SUB > WAIRERE RD | 11 | Planned | 018444 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC1405 | NONE | To complete line maintenance on the 11kV Service line beyond FC1405. Works location: Alexandra Rd. WO 30024596 | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000953 | 5.5 | 2017 | 2016-05-06 | B | 2 | 0.001906 | 6.0157e-06
1 | 10668742 | 2016-05-02 12:55 | 2016-05-02 15:20 | 145 | 2 | 290 | 0.00087233 | 0.000854 | 6.016e-06 | NAPA ID:18521 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018521 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC379 | NONE | To replace the 11kV Fuse arm & install a 400V Disconnector. Works location: Morrinsville-Walton Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000427 | 5.5 | 2017 | 2016-05-02 | B | 2 | 0.000854 | 6.016e-06
1 | 10668826 | 2016-05-02 13:10 | 2016-05-02 14:47 | 97 | 1 | 97 | 0.00029178 | 0.000282 | 3.008e-06 | NAPA ID:18525 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018525 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4381 | NONE | To install a 400V Fuse Disconnector on TC4381. Works location: Henry Watson Rd. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000141 | 5.5 | 2017 | 2016-05-02 | B | 1 | 0.000282 | 3.008e-06
1 | 10668864 | 2016-05-05 09:20 | 2016-05-05 14:10 | 290 | 2 | 580 | 0.0017446 | 0.001726 | 6.0157e-06 | NAPA ID:18546 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | 018546 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links L1135 | NONE | Replace t.x L1135, replace transformer hangar arm and fly arm.Replace stay wire. Works location: Ball Rd. WO 30018768 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000863 | 5.5 | 2017 | 2016-05-05 | B | 2 | 0.001726 | 6.0157e-06
1 | 10668903 | 2016-05-05 09:45 | 2016-05-05 09:53 | 8 | 28 | 224 | 0.00067377 | 0.000421 | 8.4221e-05 | NAPA ID:18803 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 8 | 11 | Planned | 018803 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/G 785 | NONE | Replacing defective Magnefix Links at 785/1. Works location: Popular Gr. WO 30015277 | F3 | MOTUROA 8 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.0002105 | 5.5 | 2017 | 2016-05-05 | B | 28 | 0.000421 | 8.4221e-05
1 | 10668910 | 2016-05-06 10:19 | 2016-05-06 13:20 | 181 | 2 | 362 | 0.0010888 | 0.00107 | 6.0157e-06 | NAPA ID:18587 TP_HUIRANGI GXP > WAITARA WEST SUB > BROWNE ST | 11 | Planned | 018587 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 3564T | NONE | Replace 30kVA Transformer @ Transformer Structure 3564T. Upgrade Earths. Install Lightning Arrestors. Works location: McNaughton St, Waitara. WO 30018768 | F2 | BROWNE ST | HUIRANGI | Taranaki | WAITARA WEST SUB | Western Electricity | POWERCO | 0.000535 | 5.5 | 2017 | 2016-05-06 | B | 2 | 0.00107 | 6.0157e-06
1 | 10668939 | 2016-05-02 09:30 | 2016-05-02 12:10 | 160 | 5 | 800 | 0.0024064 | 0.002361 | 1.504e-05 | NAPA ID:18522 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018522 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2531 | NONE | To replace the 11kV & 400V arms and hardware on TC2531. Works location: Piakoiti Rd. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0011805 | 5.5 | 2017 | 2016-05-02 | B | 5 | 0.002361 | 1.504e-05
1 | 10669015 | 2016-05-09 13:05 | 2016-05-09 14:40 | 95 | 2 | 190 | 0.00057147 | 0.000553 | 6.0154e-06 | NAPA ID:18550 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018550 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4382 | NONE | To install a 400V Fuse Disconnector. Works location: Ruakawa Rd. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0002765 | 5.5 | 2017 | 2016-05-09 | B | 2 | 0.000553 | 6.0154e-06
1 | 10669025 | 2016-05-09 10:15 | 2016-05-09 15:35 | 320 | 19 | 6080 | 0.018287 | 0.018115 | 5.7147e-05 | NAPA ID:18536 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018536 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP781 | NONE | To complete arm replacements on TC943, TC2669 & TC2970. Works location: Piakonui South Rd. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0090575 | 5.5 | 2017 | 2016-05-09 | B | 19 | 0.018115 | 5.7147e-05
1 | 10669054 | 2016-05-09 09:35 | 2016-05-09 12:12 | 157 | 8 | 1256 | 0.0037777 | 0.003705 | 2.4062e-05 | NAPA ID:18543 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018543 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2878 | NONE | Replace 11kV Fuses on TC2878. Works location: Rohe Rd, Waltoh. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0018525 | 5.5 | 2017 | 2016-05-09 | B | 8 | 0.003705 | 2.4062e-05
1 | 10669187 | 2016-05-05 10:00 | 2016-05-05 11:50 | 110 | 4 | 440 | 0.0013235 | 0.001287 | 1.2031e-05 | NAPA ID:18528 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018528 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC659 | NONE | To replace the 11kV Fuse arm, 400V Arm & Install a 400V Fuse Disconnector. Works location: Hutchinson Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0006435 | 5.5 | 2017 | 2016-05-05 | B | 4 | 0.001287 | 1.2031e-05
1 | 10669212 | 2016-05-09 09:00 | 2016-05-09 13:48 | 288 | 66 | 19008 | 0.057171 | 0.056575 | 0.00019851 | NAPA ID:18097 TP_CARRINGTON GXP > OAKURA SUB > SEAWARD COAST | 11 | Planned | 018097 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 169 | NONE | Replace ABS169. Note 11kV conducter is 16mm Cu [to displace G&B needs to be isolated]. Works location: Leith Rd, Okato. WO 30017990 | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.028288 | 5.5 | 2017 | 2016-05-09 | B | 66 | 0.056575 | 0.00019851
1 | 10669840 | 2016-05-05 14:05 | 2016-05-05 14:25 | 20 | 7 | 140 | 0.00042111 | 0.000357 | 2.1055e-05 | NAPA ID:18529 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018529 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4159 | NONE | To replace Install a 400V Fuse Disconnector. Works location: Hutchinson Rd. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0001785 | 5.5 | 2017 | 2016-05-05 | B | 7 | 0.000357 | 2.1055e-05
1 | 10669882 | 2016-05-09 11:39 | 2016-05-09 15:23 | 224 | 27 | 6058.35 | 0.018222 | 0.017978 | 8.1208e-05 | NAPA ID:18548 TP_STRATFORD GXP > KAPONGA SUB > RIVERLEA | 11 | Planned | 018548 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5977 | NONE | Replace pole, transformer and hardware. Works location: Auroa Rd. WO 30018768 | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.008989 | 5.5 | 2017 | 2016-05-09 | B | 27 | 0.017978 | 8.1208e-05
1 | 10670008 | 2016-05-06 09:33 | 2016-05-06 13:37 | 244 | 3 | 732 | 0.0022017 | 0.002174 | 9.0235e-06 | NAPA ID:18530 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018530 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3175 | NONE | To replace the 11kV fuses, 400V Arm & Fuses. Works location: Piakoiti Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.001087 | 5.5 | 2017 | 2016-05-06 | B | 3 | 0.002174 | 9.0235e-06
1 | 10670129 | 2016-05-02 08:59 | 2016-05-02 11:36 | 157 | 41 | 6437 | 0.019363 | 0.018992 | 0.00012333 | NAPA ID:18488 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 018488 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole S12825 | NONE | Replace damaged 11KV cross arms at pole S12825. Works location: Paeroa Kopu Rd. WO 30019720 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.009496 | 5.5 | 2017 | 2016-05-02 | B | 41 | 0.018992 | 0.00012333
1 | 10672245 | 2016-04-15 11:15 | 2016-04-15 11:52 | 36 | 343 | 12622.4 | 0.037978 | 0.034881 | 0.001032 |  | 22 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 806546 | POLE | Check for safety - car vs pole - thinks happened last night near the 100km sign on the outskirts. Paul 0274457177. Called hub and emailed, also told control. Isolation required between ABS 1231 & ABS 487 to replace Pole 806546. No backfeeds available. Replace pole, reliven OK. NDR N200039 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.034881 | 22 | 2017 | 2016-04-15 | C | 343 | 0.034881 | 0.001032
1 | 10672380 | 2016-05-03 09:23 | 2016-05-03 13:28 | 245 | 17 | 4165 | 0.012528 | 0.012374 | 5.1136e-05 | NAPA ID:17856 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 017856 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 220038 | NONE | Replace poles, hardware and conductor. Works location: Waitao Rd. WO 30017823 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.006187 | 5.5 | 2017 | 2016-05-03 | B | 17 | 0.012374 | 5.1136e-05
1 | 10673410 | 2016-04-15 09:00 | 2016-04-15 19:30 | 630 | 479 | 51000.5667 | 0.15345 | 0.14913 | 0.0014412 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | CB 8 Feeder Tripping | CABLE - REPAIR | CB 8 that tripped on reclosing on A & B Ph O/C & E/F flags. Line sectionalised & patrolled. Cable fault identified beyond fuses SF5-022. It appears the fault on CB 8 was purely coincidental that it followed during restoration of bus zone trip. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.14913 | 11 | 2017 | 2016-04-15 | C | 479 | 0.14913 | 0.0014412
1 | 10674204 | 2016-04-15 09:00 | 2016-04-15 09:25 | 25 | 2030 | 9216.1833 | 0.027729 | 0.009405 | 0.0053947 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SF5-022 | CABLE - REPAIR | Accidental T7 bus trip while technicians working on outstanding AP. Bus zone protection was operated losing supply to CB 2, 4, 6 & 8. all CB's reclosed successfully except CB 8 that tripped on reclosing on A & B Ph O/C & E/F flags. Line sectionalised & patrolled. Cable fault identified beyond fuses SF5-022. It appears the fault on CB 8 was purely coincidental that it followed during restoration of bus zone trip.Marc Askin Attended. 1x HV Joint Repair Kit Used & 2x Zipper Heat Shrink Sleeves. 2r line patrol 1031. 2r repair 1239. Cable repair undertaken under OMS 10678544. | S2 | TE MATAI1082-TE PUKE76 33KV | TE MATAI | Tauranga | TP_TE MATAI | Eastern Electricity | POWERCO | 0.009405 | 11 | 2017 | 2016-04-15 | C | 2030 | 0.009405 | 0.0053947
1 | 10674871 | 2016-05-04 09:15 | 2016-05-04 14:26 | 311 | 17 | 5287 | 0.015903 | 0.015749 | 5.1135e-05 | NAPA ID:17989 TP_TE MATAI GXP > PAENGAROA SUB > MAUNGARANGI RD | 11 | Planned | 017989 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 230189 | NONE | Replace poles and reconductor feeder. Works location: State Highway 33, Paengaroa. WO 30014831 | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.0078745 | 5.5 | 2017 | 2016-05-04 | B | 17 | 0.015749 | 5.1135e-05
1 | 10675251 | 2016-05-12 09:13 | 2016-05-12 17:20 | 487 | 15 | 7305 | 0.02197 | 0.021835 | 4.5114e-05 | NAPA ID:17874 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 017874 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 220013 | NONE | Replace poles, hardware and conductor. Works location: Waitao Rd. WO 30017823. Job went well over expected restoration. Crew advised they we having unexpected problems? | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.010918 | 5.5 | 2017 | 2016-05-12 | B | 15 | 0.021835 | 4.5114e-05
1 | 10675345 | 2016-04-15 10:02 | 2016-04-15 10:55 | 53 | 3 | 159 | 0.0004784 | 0.000451 | 9.0263e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 209520 | CABLE - SERVICE CABLE | TC2-253 Pole 209520. Has been damaged transformer TC2-253 and LV Cable at Pole 209520 and dropped HV Fuse at Transformer. 1 x Fuse Closed at 14:20 - DDO dropped open when truck hit pole. Brian reported that Oil is still visible in sight glass but maintenance required as Transformer. TC5-253 is Leaking. Dave Joynt to repair damaged LV Cable. NDR 53355. Repaired cable 4 x sleeves 4 x connectors. 1 x PVC duct. Transformer has been inspected and deemed safe for weekend, 18/4 Joanne at SMC advised to go ahead and replace all assets under original OMS | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.000451 | 11 | 2017 | 2016-04-15 | C | 3 | 0.000451 | 9.0263e-06
1 | 10675358 | 2016-05-11 09:00 | 2016-05-11 11:09 | 129 | 34 | 4386 | 0.013191 | 0.012884 | 0.00010226 | NAPA ID:17992 TP_TE MATAI GXP > PAENGAROA SUB > MAUNGARANGI RD | 11 | Planned | 017992 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SF6-009 | NONE | Replace poles and re-conductor feeder. Remove TEMP ABS 26, remove TEMP LINKS 24 and remove TEMP LINKS 20. Works location: Hwy 33, Paengaroa. WO 30014831 | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.006442 | 5.5 | 2017 | 2016-05-11 | B | 34 | 0.012884 | 0.00010226
1 | 10675720 | 2016-05-17 09:00 | 2016-05-17 15:18 | 378 | 17 | 6433.0833 | 0.019347 | 0.019193 | 5.1125e-05 | NAPA ID:17876 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 017876 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 220038 | NONE | Replace poles, hardware and conductor. Works location: Waitao Rd. WO 30017823 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.0095965 | 5.5 | 2017 | 2016-05-17 | B | 17 | 0.019193 | 5.1125e-05
1 | 10676305 | 2016-05-05 10:08 | 2016-05-05 12:53 | 165 | 1 | 165 | 0.0004963 | 0.000487 | 3.0078e-06 | NAPA ID:18358 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 018358 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P13188 | NONE | Cut 11KV jumpers to spur line live line replace 11KV cross arms and tx fuses reconnect 11KV jumpers. Works location: Pohongina East Rd, Palmerston North. WO 10159960 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.0002435 | 5.5 | 2017 | 2016-05-05 | B | 1 | 0.000487 | 3.0078e-06
1 | 10676802 | 2016-05-03 09:00 | 2016-05-03 14:28 | 328 | 39 | 12792 | 0.038478 | 0.038126 | 0.00011731 | NAPA ID:18727 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 018727 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 854053 | NONE | Reconductor between poles 854053 and T1582. Remove TEMP16. Works location: Waikawau Te Mata, Thames Coast. WO 30002482 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.019063 | 5.5 | 2017 | 2016-05-03 | B | 39 | 0.038126 | 0.00011731
1 | 10677010 | 2016-05-10 09:06 | 2016-05-10 10:06 | 60 | 39 | 2340 | 0.007038 | 0.006686 | 0.0001173 | NAPA ID:18732 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 018732 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 854053 | NONE | Reconductor between poles 854053 and T1582. Remove TEMP16. Works location: Waikawau Te Mata, Thames Coast. WO 30002482 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.003343 | 5.5 | 2017 | 2016-05-10 | B | 39 | 0.006686 | 0.0001173
1 | 10677134 | 2016-05-06 09:18 | 2016-05-06 16:45 | 447 | 30 | 13410 | 0.040335 | 0.040064 | 9.0236e-05 | NAPA ID:17809 TP_MANGAMAIRE GXP > MANGAMUTU SUB > RUAWHATA | 11 | Planned | 017809 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/415 | NONE | Change 3 x 11kV poles and reconductor 3 spans of overhead wire. Works location: Tui St. WO 30024426 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.020032 | 5.5 | 2017 | 2016-05-06 | B | 30 | 0.040064 | 9.0236e-05
1 | 10677180 | 2016-05-06 10:00 | 2016-05-06 13:30 | 210 | 2 | 420 | 0.0012633 | 0.001245 | 6.0157e-06 | NAPA ID:18795 TP_BRUNSWICK GXP > ROBERTS AVE SUB > MAKIRIKIRI | 11 | Planned | 018795 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2446 | NONE | Replace transformer X2446 because of rust on base and support brackets. Works Location: Makirikiri Valley Road. Work Order 30018785 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.0006225 | 5.5 | 2017 | 2016-05-06 | B | 2 | 0.001245 | 6.0157e-06
1 | 10677229 | 2016-05-04 08:50 | 2016-05-04 14:50 | 360 | 1 | 360 | 0.0010829 | 0.001073 | 3.0079e-06 | NAPA ID:18558 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11 | Planned | 018558 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5082 | NONE | AP install new Transformer Structure TC5082. Works location: Pipiroa Rd, Kerepehi. WO 30017017 | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0005365 | 5.5 | 2017 | 2016-05-04 | B | 1 | 0.001073 | 3.0079e-06
1 | 10677357 | 2016-05-08 09:00 | 2016-05-08 11:47 | 166 | 46 | 7668.9667 | 0.023066 | 0.022651 | 0.00013836 | NAPA ID:18452 TP_MASTERTON GXP > NORFOLK SUB > WAINGAWA RD | 11 | Planned | 018452 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C881 | NONE | Move 11kV line. Works location: Norfolk Rd, Carterton. WO 30009880 | F4 | WAINGAWA RD | MASTERTON | Wairarapa | NORFOLK SUB | Western Electricity | POWERCO | 0.011326 | 5.5 | 2017 | 2016-05-08 | B | 46 | 0.022651 | 0.00013836
1 | 10677492 | 2016-05-09 09:55 | 2016-05-09 14:20 | 265 | 26 | 6890 | 0.020723 | 0.020488 | 7.8201e-05 | NAPA ID:18662 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11 | Planned | 018662 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P39463 | NONE | This is to install Bird B Gone to existing 33kV cross arms, and install new 11kV insulators P39463. Works location: Bunnythorpe to Milson. WO 30014403 | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.010244 | 5.5 | 2017 | 2016-05-09 | B | 26 | 0.020488 | 7.8201e-05
1 | 10677564 | 2016-04-15 15:47 | 2016-04-15 17:56 | 128 | 1 | 128.3833 | 0.00038628 | 0.000377 | 3.0087e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1516 | LOAD TAP CHANGER (HV) | Transformer involved with job was T1516 not TC1023 as provided by retailer. High output voltage confirmed. Faultman isolated transformer, lowered taps from 3 to 2, restored supply and voltage now satisfactory (235-237 Phase to Earth) T1516 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000377 | 11 | 2017 | 2016-04-15 | C | 1 | 0.000377 | 3.0087e-06
1 | 10678544 | 2016-04-15 19:23 | 2016-04-15 19:30 | 7 | 8 | 56 | 0.00016849 | 9.6e-05 | 2.407e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SF5-022 | CABLE - REPAIR | Cable fault identified beyond fuses SF5-022. It appears the fault on CB 8 was purely coincidental that it followed during restoration of bus zone trip.Marc Askin Attended. 1x HV Joint Repair Kit Used & 2x Zipper Heat Shrink Sleeves. 2r line patrol 1031. 2r repair 1239. Originally linked to 10674204 | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 9.6e-05 | 11 | 2017 | 2016-04-15 | C | 8 | 9.6e-05 | 2.407e-05
1 | 10680340 | 2016-04-16 05:09 | 2016-04-16 06:08 | 58 | 41 | 2415.5833 | 0.0072679 | 0.006897 | 0.00012336 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 9454 | RECLOSER (HV) | at 00:46, Waihi Sub, CB 6 Waitawheta Feeder, Tripped, E/F, Auto Reclosed. Left job open for someone to line patrol in daylight. Calls came in later of No Powers. Found that Recloser 9454 had tripped, but was still indicating closed (power on source side but not load side). Faultman patrolled line. Isolated at Links 9454/4 and Closed Bypass ABS 9454/1. All Power Restored. Recloser has been tagged DNO 160412. Hayden Taunoa Attended. No Materials Used. 2r line patrol 0607 2r repair n/a | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.006897 | 11 | 2017 | 2016-04-16 | C | 41 | 0.006897 | 0.00012336
1 | 10680574 | 2016-04-16 06:29 | 2016-04-16 10:25 | 236 | 306 | 43024.1 | 0.12945 | 0.12669 | 0.0015525 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Fuses 4876 | CONDUCTOR - REPAIR/REHANG | CB D31 tripped on no flags, line was sectionalised and patrolled and a line down and fuse blown at Fuses 4876, line was isolated at ABS' 5723, 5687 & Links 6275 to repair the line. 1 X 30 amp HV Fuses replaced. 1 X Sleeve used. 2r line patrol 0744. 2r repair 0936. | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.12669 | 11 | 2017 | 2016-04-16 | C | 306 | 0.12669 | 0.0015525
1 | 10681435 | 2016-04-16 10:15 | 2016-04-16 12:23 | 128 | 26 | 3331.0333 | 0.010022 | 0.009787 | 7.8227e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844107 | CONDUCTOR - REPAIR/REHANG | Check supply at transformer X2923, Maewa Repeater site, after tripping, Faultman found line down at pole 844107, line was isolated at ABS 2846 & Links 2536 to repair line down. 2 X Sleeves used, 10 meters squirrel conductor replaced. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.009787 | 11 | 2017 | 2016-04-16 | C | 26 | 0.009787 | 7.8227e-05
1 | 10681882 | 2016-04-16 09:38 | 2016-04-16 12:29 | 170 | 153 | 3514.85 | 0.010575 | 0.009194 | 0.00046034 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 201158 | JUMPER | ( AON4 ) Emergency switching to repair blown jumper at pole 201158. Isolation at ABS SB1 012 ( spur no back feed ). Jumper replaced, all service restored. Materials 1 x jumper, 2 x H/V sleeves. No OMS job created when ABS SB1 012 was opened. | F3/F4 | WILLS RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.009194 | 11 | 2017 | 2016-04-16 | C | 153 | 0.009194 | 0.00046034
1 | 10682006 | 2016-04-16 10:17 | 2016-04-16 11:49 | 91 | 6 | 549 | 0.0016518 | 0.001597 | 1.8052e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4612 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 4612, line was patrolled no fault found. 2 X 6 amp HV fuses replaced. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.001597 | 11 | 2017 | 2016-04-16 | C | 6 | 0.001597 | 1.8052e-05
1 | 10682027 | 2016-04-16 12:15 | 2016-04-16 13:10 | 55 | 48 | 2640 | 0.0079431 | 0.007509 | 0.00014442 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | TC2887 | CABLE - REPAIR | Temp repair made to break out boot at transformer TC2887. Will nead to be re terminated at later date. Residual fault form completed. | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.007509 | 11 | 2017 | 2016-04-16 | C | 48 | 0.007509 | 0.00014442
1 | 10683126 | 2016-04-16 15:15 | 2016-04-16 16:35 | 80 | 1 | 80.0167 | 0.00024075 | 0.000231 | 3.0087e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 822251 | FUSE - ELEMENT/LINK (HV) | Faultman found 2 blown fuses at Fuses 7598, line was patrolled and faultman found a fresh dead swan under the lines at pole 822251.2 X 6 amp HV fuses replaced | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000231 | 11 | 2017 | 2016-04-16 | C | 1 | 0.000231 | 3.0087e-06
1 | 10683411 | 2016-04-16 19:07 | 2016-04-16 22:29 | 201 | 5 | 1007.9167 | 0.0030326 | 0.002987 | 1.5044e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 725027 | CONDUCTOR - REPAIR/REHANG | Tree Branch broke off and fell onto lines bringing down 1x HV line and blowing all three fuses at Fuses CA465. Repaired using 40metres of 16mm cu wire, 4x 16mm sleeves, & 3x 10Amp HV Links NDR# 43438 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.002987 | 11 | 2017 | 2016-04-16 | C | 5 | 0.002987 | 1.5044e-05
1 | 10685128 | 2016-04-17 06:56 | 2016-04-17 12:18 | 322 | 964 | 76672.0333 | 0.23068 | 0.22198 | 0.0029004 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P32880 | POLE | Report from fire service of car vs pole north of Lake road Ref No : F2060209. Replaced pole P32880. 2r line patrol 0800. 2r repair 0806 | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.22198 | 11 | 2017 | 2016-04-17 | C | 964 | 0.22198 | 0.0029004
1 | 10686439 | 2016-04-17 06:56 | 2016-04-17 08:28 | 91 | 543 | 18439.95 | 0.05548 | 0.050579 | 0.0016337 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 219981 | CIRCUIT BREAKER (HV) | PMA CB8 tripped A Ph O/C, L/O. CB RP09 opened & back feed closed via sectionaliser 9462/2. Feeder sectionalised with possum found at base of pole 219981. All service restored no other fault found. Possum guard was fitted to pole. 2r line patrol 0808. no 2r repair was possum | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.050579 | 11 | 2017 | 2016-04-17 | C | 543 | 0.050579 | 0.0016337
1 | 10698308 | 2016-04-17 11:08 | 2016-04-17 11:55 | 47 | 19 | 893 | 0.0026868 | 0.002515 | 5.7165e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | v12531 | SURGE ARRESTOR (HV) | Blown H/V fuse at Fuses FC2336. Found blown surge arrestor at transformer TC761. Surge arrestor cut free all service restored. New surge arrestor to be fitted in future. Faultman to defect | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.002515 | 11 | 2017 | 2016-04-17 | C | 19 | 0.002515 | 5.7165e-05
1 | 10701780 | 2016-04-17 14:53 | 2016-04-18 00:21 | 567 | 218 | 71323.8333 | 0.21459 | 0.21262 | 0.0006559 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 268745 | POLE | Fire Comms F2060440. Check for safety - Car vs Pole, pole is broken and being held up by the lines. Advised control and SMC of 999. Pole Replaced. See NDR# 53356 for materials detail 2r line patrol dont think so 2r repair 1637? | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.21262 | 11 | 2017 | 2016-04-17 | C | 218 | 0.21262 | 0.0006559
1 | 10704982 | 2016-04-17 15:47 | 2016-04-17 23:16 | 448 | 2832 | 64899.9833 | 0.19526 | 0.1697 | 0.0024822 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | HINTWR100 | POLE | Car vs 33/11 kV Pole. Isolated via 11kV ABS IP520. Tower Rd Sub was then backfed & 33kV Isolated. Pole Replaced. See NDR# 55708 for materials used 2r line oatrol 1703 2r repair 2023 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.1697 | 11 | 2017 | 2016-04-17 | C | 2832 | 0.1697 | 0.0024822
1 | 10706316 | 2016-04-17 21:18 | 2016-04-17 21:59 | 41 | 1 | 41.4667 | 0.00012476 | 0.000115 | 3.0087e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Faultman could not get to property due to flooded roads. Genesis advised. | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000115 | 11 | 2017 | 2016-04-17 | C | 1 | 0.000115 | 3.0087e-06
1 | 10711712 | 2016-05-11 09:50 | 2016-05-11 14:20 | 270 | 26 | 7020 | 0.021114 | 0.020879 | 7.8198e-05 | NAPA ID:18790 TP_MANGAMAIRE GXP > ALFREDTON SUB > RONGOMAI | 11 | Planned | 018790 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses I41 | NONE | To repair and resag 11kv conductor and straighten poles. Works location: Tawataia Rd. WO 30000998 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.01044 | 5.5 | 2017 | 2016-05-11 | B | 26 | 0.020879 | 7.8198e-05
1 | 10711720 | 2016-04-18 11:45 | 2016-04-18 13:15 | 90 | 2 | 180 | 0.00054156 | 0.000523 | 6.0173e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TF8-026 | JUMPER | Replaced broken cast bolt on the transformer bushing at transformer TF8-026. Needed to go back to workshop to get parts before carrying out repairs. Own Access permit due to no comms at site. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000523 | 11 | 2017 | 2016-04-18 | C | 2 | 0.000523 | 6.0173e-06
1 | 10711748 | 2016-05-12 09:26 | 2016-05-12 14:31 | 305 | 46 | 14030 | 0.042197 | 0.041781 | 0.00013835 | NAPA ID:18624 TP_MARTON GXP > ARAHINA SUB > TUTAENUI | 11 | Planned | 018624 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X1213 | NONE | Replace transformer pole X1213. Works location: Mangatipona Rd, Turakina Valley. WO 10162317 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.02089 | 5.5 | 2017 | 2016-05-12 | B | 46 | 0.041781 | 0.00013835
1 | 10711771 | 2016-05-11 09:33 | 2016-05-11 15:00 | 327 | 23 | 7521 | 0.02262 | 0.022412 | 6.9176e-05 | NAPA ID:18319 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11 | Planned | 018319 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1/346 | NONE | Replace pole with double pole & upgrade transformer T1/346 with new 100 kva tx. Works location: Omanuka Rd, Himitangi. WO 30007016 | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.011206 | 5.5 | 2017 | 2016-05-11 | B | 23 | 0.022412 | 6.9176e-05
1 | 10711919 | 2016-05-12 09:35 | 2016-05-12 11:55 | 140 | 10 | 1400 | 0.0042106 | 0.00412 | 3.0076e-05 | NAPA ID:18321 TP_LINTON GXP > KAIRANGA SUB > KOPANE | 11 | Planned | 018321 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1/69 | NONE | Replace Transfomer & Trani crossarms T1/69. Works location: Banks Rd, Rongotea. WO 30018419 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.00206 | 5.5 | 2017 | 2016-05-12 | B | 10 | 0.00412 | 3.0076e-05
1 | 10712343 | 2016-05-12 10:22 | 2016-05-12 15:13 | 291 | 49 | 14259 | 0.042885 | 0.042443 | 0.00014737 | NAPA ID:18692 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 018692 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV RP19 | NONE | Tree Work at various sites 309 Road. Works location: 309 Rd, Coromandel. WO 10152354 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.021222 | 5.5 | 2017 | 2016-05-12 | B | 49 | 0.042443 | 0.00014737
1 | 10712993 | 2016-05-16 09:17 | 2016-05-16 15:32 | 374 | 20 | 7490.3333 | 0.022527 | 0.022346 | 6.0148e-05 | NAPA ID:18817 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 018817 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S123 | NONE | To replace multiple poles and crossarms. Works location: Opaki Kaiparoro Rd, Masterton. WO 30019523. Outage area was reduced on the day of the outage. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.011173 | 5.5 | 2017 | 2016-05-16 | B | 20 | 0.022346 | 6.0148e-05
1 | 10713098 | 2016-05-09 09:10 | 2016-05-09 15:06 | 355 | 79 | 28101.6167 | 0.084522 | 0.083808 | 0.00023761 | NAPA ID:18741 TP_KOPU GXP > THAMES SUB > ROLLESTON ST | 11 | Planned | 018741 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC2720 | NONE | Pole T12462 ABS IC2720 DNO160308: Replace all arms on pole. Works location: Bella St, Thames. WO 30024895 | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.041904 | 5.5 | 2017 | 2016-05-09 | B | 79 | 0.083808 | 0.00023761
1 | 10713652 | 2016-04-18 16:45 | 2016-04-18 17:36 | 50 | 1 | 50.5167 | 0.00015199 | 0.000142 | 3.0086e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | UNKNOWN | no possum guard required up this pole, tony advised customer that its not required | F3 | WEST QUAY | HUIRANGI | Taranaki | WAITARA WEST SUB | Western Electricity | POWERCO | 0.000142 | 11 | 2017 | 2016-04-18 | C | 1 | 0.000142 | 3.0086e-06
1 | 10714603 | 2016-04-19 06:41 | 2016-04-19 07:48 | 66 | 6 | 398.7 | 0.0011995 | 0.001145 | 1.8052e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8276 | FUSE - ELEMENT/LINK (HV) | 2 x 10amp fuse bird | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.001145 | 11 | 2017 | 2016-04-19 | C | 6 | 0.001145 | 1.8052e-05
1 | 10714627 | 2016-04-19 08:21 | 2016-04-19 09:25 | 64 | 31 | 1984 | 0.0059691 | 0.005689 | 9.3268e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712414 | CONDUCTOR - REPAIR/REHANG | Check to see if OMS 10714721 (139 Manihi Road) LV - is related - poss HV fuse Fuse NG375 8:06am - Brett advised HV line down in Paddock he is working with control also OMS 10714831 - (196 Manihi Road) Isolated at fuses NG375, repaired conductor & relivened pole 712414 cause old age | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.005689 | 11 | 2017 | 2016-04-19 | C | 31 | 0.005689 | 9.3268e-05
1 | 10714908 | 2016-05-19 09:40 | 2016-05-19 14:45 | 305 | 6 | 1830 | 0.0055033 | 0.005449 | 1.8044e-05 | NAPA ID:18768 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | 018768 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 443818 | NONE | Replace 11kV pole 443818. Works location: Rangikura Rd, Waverley. WO 30024000 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.0027245 | 5.5 | 2017 | 2016-05-19 | B | 6 | 0.005449 | 1.8044e-05
1 | 10714914 | 2016-05-18 08:45 | 2016-05-18 14:25 | 340 | 14 | 4760 | 0.014315 | 0.014188 | 4.2103e-05 | NAPA ID:18664 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 018664 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 1260 | NONE | Replace old hardwood pole and xarms. Works location: Napier Taihape Rd, Tauarua Hill. WO 30014017 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.007094 | 5.5 | 2017 | 2016-05-18 | B | 14 | 0.014188 | 4.2103e-05
1 | 10716503 | 2016-05-06 10:50 | 2016-05-06 14:25 | 215 | 1 | 215 | 0.00064669 | 0.000637 | 3.0078e-06 | NAPA ID:18346 TP_HUIRANGI GXP > WAITARA EAST SUB > TIKORANGI | 11 | Planned | 018346 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 764572 | NONE | Shift Pole 764572 @ replace cross arm. Works location: Mataro Rd, Urenui. WO 30016094 | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.0003185 | 5.5 | 2017 | 2016-05-06 | B | 1 | 0.000637 | 3.0078e-06
1 | 10716509 | 2016-04-19 10:31 | 2016-04-19 10:35 | 3 | 304 | 1180.5333 | 0.0035518 | 0 | 0.00091463 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 6561-1 | UNKNOWN | CB 6561 tripped when doing ABS Maintenance on LLP 18831. Closed again by controller after safety investigation done. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-04-19 | C | 304 | 0 | 0.00091463
1 | 10717097 | 2016-04-22 09:31 | 2016-04-22 11:27 | 116 | 1 | 116.6667 | 0.00035099 | 0.000341 | 3.0084e-06 | NAPA ID:19042 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11 | Planned | 019042 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | H84 | NONE | Rebind insulators on poles P21352 & P21353 to eliminate radio interference at Airways Corp radar site. Works location: North Range Rd, Palmerston North. WO 30026347 | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0001705 | 5.5 | 2017 | 2016-04-22 | B | 1 | 0.000341 | 3.0084e-06
1 | 10718295 | 2016-04-19 12:47 | 2016-04-19 19:06 | 379 | 110 | 40944.2 | 0.12319 | 0.12219 | 0.00033095 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5003 | FUSE - ELEMENT/LINK (HV) | ********Pls check if 10718405 is related (24 waiotahi Rd, Thames)********** To be decided at invoicing level if meets criteria of 2R work after scope of work. 2 HV fuses blown at fuse switch FC5003. (R & W) Replacement fuses bought to site Isolation of fuse switch at Sw/Gear 3203 & IC1924. FM advises at 1638 wrong fuses have been bought to site & needs to drive to Paeroa depot to get new fuses. Fuses replaced at 1850. Fuse switch relivened & restored. Possible tree branch accross lines on overhead component. Joe extended outage due to replacement fuses needed. Materials 3 x 30A SD fuses | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.12219 | 11 | 2017 | 2016-04-19 | C | 110 | 0.12219 | 0.00033095
1 | 10719045 | 2016-05-10 13:27 | 2016-05-10 13:53 | 26 | 1 | 26 | 7.82e-05 | 6.9e-05 | 3.0076e-06 | NAPA ID:18601 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018601 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1734 | NONE | To install a 400V Fuse Disconnector. Works location: Maiseys Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 3.45e-05 | 5.5 | 2017 | 2016-05-10 | B | 1 | 6.9e-05 | 3.0076e-06
1 | 10722701 | 2016-04-19 19:27 | 2016-04-19 21:28 | 120 | 24 | 2900.8 | 0.0087275 | 0.00851 | 7.2207e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 997 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 20a fuses, OH due to birds, nothing else repaired or replaced, adjacent assets up to Powerco standard. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.00851 | 11 | 2017 | 2016-04-19 | C | 24 | 0.00851 | 7.2207e-05
1 | 10722810 | 2016-04-19 22:09 | 2016-04-19 23:16 | 67 | 42 | 2356.2 | 0.007089 | 0.006709 | 0.00012636 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WH140 | FUSE - ELEMENT/LINK (HV) | Check OMS 10722829. Replaced 2x 15a HV fuses @ WH140. Cause unknown. | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.006709 | 11 | 2017 | 2016-04-19 | C | 42 | 0.006709 | 0.00012636
1 | 10723021 | 2016-04-20 04:55 | 2016-04-20 08:10 | 195 | 3 | 585.9 | 0.0017627 | 0.001735 | 9.0257e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP595 | FUSE - ELEMENT/LINK (HV) | FP595 2 x 6amp unknown cause. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.001735 | 11 | 2017 | 2016-04-20 | C | 3 | 0.001735 | 9.0257e-06
1 | 10723036 | 2016-04-20 05:33 | 2016-04-20 08:43 | 189 | 1 | 189.7 | 0.00057073 | 0.000561 | 3.0085e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8725 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuses at Fuses 8725. Outage was at the cowshed not the farmers house, as reported by retailer. Outage is recorded on child job, parent should have no outage associated. | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.000561 | 11 | 2017 | 2016-04-20 | C | 1 | 0.000561 | 3.0085e-06
1 | 10723053 | 2016-04-20 07:43 | 2016-04-20 10:28 | 164 | 18 | 2964.9 | 0.0089202 | 0.008757 | 5.4154e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | V83 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuse & 1 x holder due to bird. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.008757 | 11 | 2017 | 2016-04-20 | C | 18 | 0.008757 | 5.4154e-05
1 | 10724277 | 2016-04-20 10:00 | 2016-04-20 14:56 | 295 | 31 | 9171.8667 | 0.027594 | 0.027314 | 9.3266e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 738507 | CONDUCTOR - REPAIR/REHANG | Trees in the lines; branches smoking. Just past the hall on Wingrove Road. Contact is G J Sole @ 06 755 2866. Before signing off, check if 10724349 and 10724360 are related (814 and 836 Wingrove part powers). Found line down Isolated at fuses 6130. Repaired line & relivened. NDR 43439. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.027314 | 11 | 2017 | 2016-04-20 | C | 31 | 0.027314 | 9.3266e-05
1 | 10725646 | 2016-05-04 08:34 | 2016-05-04 14:36 | 361 | 226 | 25813.2 | 0.077645 | 0.075605 | 0.0006798 | NAPA ID:18773 TP_WAIHOU GXP > TAHUNA SUB > HOE-O-TAINUI | 11 | Planned | 018773 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC529 | NONE | 1: Create 11kV Line/Span break at pole K0916 & K12834. 2: Replace 11kV ABS IC529 and remove DNO 160313. Prepare replacement conductors from pole K12834 to K0916. - this is to be completed at the end of the AP to avoid working around Live line crew. 3: Live line to replace pole K0916. 4: Live line to reinstate spur line conductors and connect up to main line. Works location: Waiti Rd, Tahuna. WO 30024955 | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.037803 | 5.5 | 2017 | 2016-05-04 | B | 226 | 0.075605 | 0.0006798
1 | 10726319 | 2016-05-10 09:38 | 2016-05-10 11:59 | 141 | 37 | 5217 | 0.015691 | 0.015357 | 0.00011128 | NAPA ID:18600 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018600 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2527 | NONE | To replace the 11kV pin arm, 11kV Fuse arm, 400V arm & Install a 400V Fuse Disconector. Works location; Maisey Rd. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0076785 | 5.5 | 2017 | 2016-05-10 | B | 37 | 0.015357 | 0.00011128
1 | 10727247 | 2016-04-20 12:00 | 2016-04-20 16:00 | 240 | 28 | 4024.3333 | 0.012108 | 0.011854 | 0.00011733 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 831506 | POLE | Truck has hit HV/LV pole outside Downer depot - Gavin Grey onsite since 8:30am. Will need to replace pole - will need to isolate and take power off Commercial area. NDR 54353. Pole # 831506 has both HV and LV and HV underground pot head. Replaced Pole 831506. Materials Used: 1 X Pole, 1 X LV Arms & Insulators, 1 X HT Arms & Insulators. Put Old Pot Head back on new Pole. | F2 | RENALL ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.011854 | 11 | 2017 | 2016-04-20 | C | 28 | 0.011854 | 0.00011733
1 | 10728235 | 2016-05-11 10:00 | 2016-05-11 14:16 | 256 | 43 | 11008 | 0.033108 | 0.03272 | 0.00012933 | NAPA ID:18593 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 018593 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 752245 | NONE | Replace all Xarms @ Pole752245 upgrade earths. replace 15Kva Transformer at Structure 1061. Works location: Kent Rd, Egmont Village. WO 30018768 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.01636 | 5.5 | 2017 | 2016-05-11 | B | 43 | 0.03272 | 0.00012933
1 | 10729199 | 2016-05-12 09:15 | 2016-05-12 12:04 | 169 | 1 | 169 | 0.00050828 | 0.000499 | 3.0075e-06 | NAPA ID:18932 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 8 | 11 | Planned | 018932 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 745092 | NONE | Replace 11kV Rotten cross arm at pole 745092. Application created for Neil Woodhead by Mike Reid. Works location: Cross Rd, Bell Block. WO 30007226 | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.0002495 | 5.5 | 2017 | 2016-05-12 | B | 1 | 0.000499 | 3.0075e-06
1 | 10729235 | 2016-05-03 09:10 | 2016-05-03 15:30 | 380 | 29 | 11020 | 0.033148 | 0.032886 | 8.7232e-05 | NAPA ID:17834 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 017834 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6289 | NONE | Pole & wire replacement as per IR 8370 Paora Road reconstruction. Works location: Paora Rd. WO 30018540 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.016443 | 5.5 | 2017 | 2016-05-03 | B | 29 | 0.032886 | 8.7232e-05
1 | 10729674 | 2016-05-05 09:09 | 2016-05-05 15:23 | 373 | 29 | 10834.4 | 0.032589 | 0.032327 | 8.7229e-05 | NAPA ID:17841 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 017841 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6289 | NONE | Pole & wire replacement as per IR 8370 Paora Road reconstruction. Works location: Paora Rd. WO 30018540 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.016164 | 5.5 | 2017 | 2016-05-05 | B | 29 | 0.032327 | 8.7229e-05
1 | 10731926 | 2016-04-21 09:27 | 2016-04-21 12:09 | 162 | 191 | 31005.6667 | 0.093282 | 0.091557 | 0.00057463 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 219476 | POLE | at 09:25, Papamoa Sub, CB 5 Papamoa Beach West Feeder. Report came in of Car v Pole. Faultmen attended and found HV Pole 219476 had broken from vehicle strike. Isolated lines at Sw/gear 9583/1, SD5-204 & ABS SD5-023. Permit Issued and repairs carried out. All Power restored on completion. Clint Johnstone Attended. Materials Used. 1x Pole, 1x HV Crossarm, 1x LV Crossarm, 3x HV Insulators, 5x LV Insulators, 4x 63A Fuses & Carriers, 12m of Cable All 3 Phases + Neutral, 8x PG Clamps. NDR: 52981 | F3 | PAPAMOA BEACH WEST | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.091557 | 11 | 2017 | 2016-04-21 | C | 191 | 0.091557 | 0.00057463
1 | 10733514 | 2016-04-21 11:00 | 2016-04-21 14:20 | 200 | 1 | 200.4167 | 0.00060296 | 0.000593 | 3.0085e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T2609 | NONE | Resag line and replace transformer pole. This was originally a planned job under NAPA 18890 but inspection showed lines too low and must be done immediately. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000593 | 11 | 2017 | 2016-04-21 | C | 1 | 0.000593 | 3.0085e-06
1 | 10734566 | 2016-04-21 14:00 | 2016-04-21 16:48 | 167 | 3 | 503.4 | 0.0015145 | 0.001487 | 9.0256e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E1360 | CROSSARM - WHOLE ASSEMBLY | An outage was required from fuses FC2151 to replace a rotten crossarm. Associated hardware (6 Insulators) also replaced. Relivened OK. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.001487 | 11 | 2017 | 2016-04-21 | C | 3 | 0.001487 | 9.0256e-06
1 | 10734620 | 2016-05-11 09:46 | 2016-05-11 16:15 | 389 | 19 | 7391 | 0.022229 | 0.022058 | 5.7145e-05 | NAPA ID:18619 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > LAKES EXPRESS | 11 | Planned | 018619 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Various sites | NONE | Install 1 new pole and several LV and HV arms in de-energized section of line. | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.011029 | 5.5 | 2017 | 2016-05-11 | B | 19 | 0.022058 | 5.7145e-05
1 | 10734819 | 2016-04-28 09:15 | 2016-04-28 14:30 | 315 | 4 | 1260 | 0.0037904 | 0.003754 | 1.2033e-05 | NAPA ID:19153 TP_TE MATAI GXP > PAENGAROA SUB > MAUNGARANGI RD | 11 | Planned | 019153 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp 24 | NONE | 1/ RE POLE AND RECON FEEDER 2/ INSTALL TEMPORARY LINKS TEMP24 AT POLE 230200 DURING SHUT | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.001877 | 5.5 | 2017 | 2016-04-28 | B | 4 | 0.003754 | 1.2033e-05
1 | 10734827 | 2016-04-21 15:45 | 2016-04-21 16:30 | 45 | 3 | 135 | 0.00040615 | 0.000379 | 9.0256e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5802 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | at 15:45, Whitianga Sub, CB 4 Coroglen Feeder. Found Transformer TC5802 was leaking badly out of LV bushing. Own Isolation & AP Issued to replace transformer. All Power Restored on completion. Andrew King Attended. 1x Transformer Replaced. Guys did planned work today near this transformer, have since inspected and found it to be leaking badly from LV bushings - they are going to replace the transformer. | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000379 | 11 | 2017 | 2016-04-21 | C | 3 | 0.000379 | 9.0256e-06
1 | 10734875 | 2016-05-13 09:07 | 2016-05-13 16:03 | 416 | 126 | 52416 | 0.15764 | 0.15651 | 0.00037895 | NAPA ID:17827 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11 | Planned | 017827 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Q44 | NONE | Change 5 x HV poles. Works location: Mangahao Rd. WO 30024426 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.078253 | 5.5 | 2017 | 2016-05-13 | B | 126 | 0.15651 | 0.00037895
1 | 10736284 | 2016-05-10 09:50 | 2016-05-10 15:25 | 335 | 29 | 9715 | 0.02922 | 0.028957 | 8.7223e-05 | NAPA ID:17844 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 017844 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6289 | NONE | Pole & wire replacement as per IR 8370 Paora Road reconstruction. Works location: Paora Rd. WO 30018540 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.014479 | 5.5 | 2017 | 2016-05-10 | B | 29 | 0.028957 | 8.7223e-05
1 | 10736326 | 2016-05-19 08:48 | 2016-05-19 14:28 | 340 | 29 | 9860 | 0.029652 | 0.02939 | 8.7211e-05 | NAPA ID:17862 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 017862 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6289 | NONE | Pole & wire replacement as per IR 8370 Paora Road reconstruction. Works location: Paora Rd. WO 30018540 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.014695 | 5.5 | 2017 | 2016-05-19 | B | 29 | 0.02939 | 8.7211e-05
1 | 10736400 | 2016-05-24 09:08 | 2016-05-24 14:30 | 322 | 6 | 1932 | 0.0058096 | 0.005755 | 1.8042e-05 | NAPA ID:18110 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 018110 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | PU208 | NONE | Replace various arms and poles within work area. Works location: Komene Rd. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.0028775 | 5.5 | 2017 | 2016-05-24 | B | 6 | 0.005755 | 1.8042e-05
1 | 10736521 | 2016-05-10 08:55 | 2016-05-10 17:17 | 502 | 2 | 1004 | 0.0030197 | 0.003001 | 6.0153e-06 | NAPA ID:18688 TP_PIAKO GXP > PIAKO SUB > MVILLE SOUTH | 11 | Planned | 018688 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I13627 | NONE | Replace pole I13627 at ABS 362 Site with a new 11M Busck pole Live Line. Works Location: Morrinsville Tahuna Rd. WO 30002543 | F3 | MVILLE SOUTH | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0015005 | 5.5 | 2017 | 2016-05-10 | B | 2 | 0.003001 | 6.0153e-06
1 | 10736658 | 2016-05-10 09:30 | 2016-05-10 14:47 | 317 | 17 | 5389 | 0.016208 | 0.016055 | 5.1131e-05 | NAPA ID:19168 TP_TE MATAI GXP > PAENGAROA SUB > MAUNGARANGI RD | 11 | Planned | 019168 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 20 | NONE | Reconductor and replace poles. Works location: State Highway 33, Paengaroa. Works Order: 30014831 | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.0080275 | 5.5 | 2017 | 2016-05-10 | B | 17 | 0.016055 | 5.1131e-05
1 | 10736964 | 2016-05-16 10:00 | 2016-05-16 14:12 | 252 | 42 | 10584 | 0.031831 | 0.031451 | 0.00012631 | NAPA ID:19102 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | 019102 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LI749 | NONE | Install cross arms & replace DNO ABS LI749. Works location: Ball Rd. WO 30020397 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.015725 | 5.5 | 2017 | 2016-05-16 | B | 42 | 0.031451 | 0.00012631
1 | 10738309 | 2016-05-16 09:10 | 2016-05-16 12:15 | 185 | 7 | 1295 | 0.0038946 | 0.003831 | 2.1052e-05 | NAPA ID:18603 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018603 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC364 | NONE | To replace the 11kV Fuse arm & install a 400V Fuse Disconnector. Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0019155 | 5.5 | 2017 | 2016-05-16 | B | 7 | 0.003831 | 2.1052e-05
1 | 10738399 | 2016-05-16 14:02 | 2016-05-16 14:22 | 20 | 32 | 640 | 0.0019247 | 0.001636 | 9.6237e-05 | NAPA ID:18604 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018604 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2794 | NONE | To install a 400V Fuse Disconnector. Works location: Pitt St, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000818 | 5.5 | 2017 | 2016-05-16 | B | 32 | 0.001636 | 9.6237e-05
1 | 10738412 | 2016-05-16 10:00 | 2016-05-16 10:30 | 30 | 4 | 120 | 0.00036089 | 0.000324 | 1.203e-05 | NAPA ID:18649 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018649 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1938 | NONE | To install a 400V Fuse Disconnector. Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000162 | 5.5 | 2017 | 2016-05-16 | B | 4 | 0.000324 | 1.203e-05
1 | 10738416 | 2016-04-22 11:48 | 2016-04-22 15:25 | 217 | 1 | 217.0167 | 0.00065289 | 0.000643 | 3.0084e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC272 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer found to be faulty. To be replaced. Transformer TC272 Replaced. | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000643 | 11 | 2017 | 2016-04-22 | C | 1 | 0.000643 | 3.0084e-06
1 | 10738423 | 2016-05-12 09:18 | 2016-05-12 13:52 | 274 | 19 | 5206 | 0.015658 | 0.015486 | 5.7144e-05 | NAPA ID:18713 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 018713 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC1450 | NONE | Install new SWER Recloser. Works location: Otamakiti Rd, Puriri. WO 10148359 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.007743 | 5.5 | 2017 | 2016-05-12 | B | 19 | 0.015486 | 5.7144e-05
1 | 10738432 | 2016-05-16 11:35 | 2016-05-16 13:00 | 85 | 2 | 170 | 0.00051126 | 0.000493 | 6.0148e-06 | NAPA ID:18652 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018652 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3283 | NONE | To install a 400v fuse Disconnector. Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0002465 | 5.5 | 2017 | 2016-05-16 | B | 2 | 0.000493 | 6.0148e-06
1 | 10738459 | 2016-05-16 13:30 | 2016-05-16 14:30 | 60 | 4 | 240 | 0.00072178 | 0.000685 | 1.203e-05 | NAPA ID:18656 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018656 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1804 | NONE | To install a 400V Fuse Disconnector. Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0003425 | 5.5 | 2017 | 2016-05-16 | B | 4 | 0.000685 | 1.203e-05
1 | 10739326 | 2016-05-17 09:15 | 2016-05-17 14:06 | 291 | 362 | 105504.9 | 0.31729 | 0.31403 | 0.0010887 | NAPA ID:18815 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 5 | 11 | Planned | 018815 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8806 | NONE | Tree cutting Waimea Str 11kV lines. Works location: Waimea St. WO 10152358 | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.15701 | 5.5 | 2017 | 2016-05-17 | B | 362 | 0.31403 | 0.0010887
1 | 10739460 | 2016-05-27 09:30 | 2016-05-27 13:55 | 265 | 42 | 11130 | 0.033467 | 0.033087 | 0.00012629 | NAPA ID:18718 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 018718 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 319 | NONE | Install SWER Recloser and new pole. Works location: Coroglen, Whitianga. WO 10148359 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.016543 | 5.5 | 2017 | 2016-05-27 | B | 42 | 0.033087 | 0.00012629
1 | 10743575 | 2016-05-04 20:01 | 2016-05-05 01:39 | 338 | 1 | 338.4 | 0.0010179 | 0.001008 | 3.0079e-06 | NAPA ID:17855 TP_BUNNYTHORPE GXP > MAIN ST SUB > MAIN ST 15 | 11 | Planned | 017855 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10292 | NONE | Cut in new CCC safelink 10292 commission and test, at this stage will only be SCADA ready, not fully automated. Works location: Rangitikei Line. WO 30002198 | F2 | MAIN ST 15 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 0.000504 | 5.5 | 2017 | 2016-05-04 | B | 1 | 0.001008 | 3.0079e-06
1 | 10743612 | 2016-05-04 10:00 | 2016-05-04 15:17 | 317 | 67 | 21239 | 0.063886 | 0.063281 | 0.00020153 | NAPA ID:18453 TP_WAIKINO GXP > WAIHI BEACH SUB > WILSON RD | 11 | Planned | 018453 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP311 | NONE | To reterminate 11kV Cables beyond FP311 and replace LV Joints. Works location: 62 Seaforth Road, Waihi Beach. Work Order 30002297 | F3 | WILSON RD | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.031641 | 5.5 | 2017 | 2016-05-04 | B | 67 | 0.063281 | 0.00020153
1 | 10744503 | 2016-04-22 19:07 | 2016-04-23 02:30 | 443 | 502 | 215890 | 0.6495 | 0.64497 | 0.0015103 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 215818 | CROSSARM - WHOLE ASSEMBLY | At 19:07, Taraunga GXP, CB 13 Oropi Rd Feeder. Police Comms advised of Car V Pole. Faultmen dispatched. Car v Pole at Pole 215818. Isolated Lines at ABS IP425, 9694/1 & Links 9694/4. Permit Issued & Repairs carried out. All Power Restored on Completion. Tom Tanoa Attended. 1x Pole, 1 HV Crossarm with insulators, 3x LV Crossarm with insulators, 14 shakels all complete, 6m 70mm Cu Conductor 3 Phases + Neutral, Less than 1 span., 6x Sleeves. NDR: ?? Child Job for Outage: 10744547 F2064111 - Fire comms Auckland - SMC advised ETA 10 mins and Control advised. | F2 | 18TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 0.64497 | 11 | 2017 | 2016-04-22 | C | 502 | 0.64497 | 0.0015103
1 | 10746380 | 2016-04-24 04:12 | 2016-04-24 05:27 | 75 | 255 | 12258.7333 | 0.036879 | 0.034577 | 0.00076714 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | RS H131 A/R, L/O, E/F. Sectionalised & Patrolled with no fault found. Les Robinson identified some trees in Scotts Rd growing near the 11kV & he will contact Treescape about them. 2r line patrol 0441 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.034577 | 11 | 2017 | 2016-04-24 | C | 255 | 0.034577 | 0.00076714
1 | 10747152 | 2016-04-24 05:29 | 2016-04-24 08:08 | 158 | 212 | 564.8 | 0.0016991 | 0 | 3.6101e-05 |  | 22 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 850112 | FUSE - ELEMENT/LINK (HV) | RS 4137 A/R, E/F, O/C B & C Phase. Faultman found blown fuse at Fuses 757 & Fuses 2855, Line was patrolled and faultman found a branch on the lines between poles 850112 & 850113, line was isolated at Fuses 2855 and branch was removed from the line with hot sticks. 2r line patrol from request | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0 | 22 | 2017 | 2016-04-24 | C | 212 | 0 | 3.6101e-05
1 | 10747394 | 2016-04-24 06:57 | 2016-04-24 08:59 | 122 | 6 | 733.5 | 0.0022067 | 0.002152 | 1.805e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 4612 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 4612, line was patrolled and no fault found suspect bird strike. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.002152 | 11 | 2017 | 2016-04-24 | C | 6 | 0.002152 | 1.805e-05
1 | 10756812 | 2016-04-24 18:10 | 2016-04-24 19:08 | 58 | 4 | 232.6 | 0.00069976 | 0.000663 | 1.2034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1666 | FUSE - ELEMENT/LINK (HV) | 2 x HV Fuses at FP1666 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.000663 | 11 | 2017 | 2016-04-24 | C | 4 | 0.000663 | 1.2034e-05
1 | 10757387 | 2016-04-24 23:39 | 2016-04-25 01:19 | 100 | 529 | 38672.8333 | 0.11634 | 0.11157 | 0.0015914 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 4 | UNKNOWN | Feeder Sectionalised. No Fault Found. Cause Unknown 2 r line patrol 0030 | F3 | CAMPBELL ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.11157 | 11 | 2017 | 2016-04-24 | C | 529 | 0.11157 | 0.0015914
1 | 10758241 | 2016-04-25 01:43 | 2016-04-25 04:36 | 173 | 278 | 45493.7833 | 0.13686 | 0.13435 | 0.00083632 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | RS C1024 A/R, L/O, O/C B & C Phase. Patrolled with no fault found. Re Livened ok. 2r line poatrol 0423 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.13435 | 11 | 2017 | 2016-04-25 | C | 278 | 0.13435 | 0.00083632
1 | 10759403 | 2016-04-25 02:31 | 2016-04-25 04:46 | 134 | 1 | 134.7167 | 0.00040528 | 0.000396 | 3.0083e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | N/A - NOT APPLICABLE | UNKNOWN | GIS appears to be wrong. This property is actually on Mt Bruce feeder. Part of feeder fault. See OMS 10758241. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000396 | 11 | 2017 | 2016-04-25 | C | 1 | 0.000396 | 3.0083e-06
1 | 10759479 | 2016-04-25 05:20 | 2016-04-25 06:55 | 94 | 278 | 21671.3333 | 0.065195 | 0.062686 | 0.00083632 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 831739 | CONDUCTOR - REPAIR/REHANG | Faultman found line down when patrolling for cause of earlier fault. Isolated at Recloser C1024 & ABS S170 and backfeed installed via ABS 11063/1. Materials used: 10metres of 10mm Cu. & 3 sleeves 2r line patrol and repiar same time 0616 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.062686 | 11 | 2017 | 2016-04-25 | C | 278 | 0.062686 | 0.00083632
1 | 10759811 | 2016-04-25 06:58 | 2016-04-25 08:00 | 62 | 24 | 1489.2 | 0.0044801 | 0.004263 | 7.2201e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B0223 | JUMPER | Line isolated at Sw/gear 9086/3 to repair jumper at pole B0223. Blown jumper possibly the cause of CB 4 tripping at Baird Rd @23:39 24/04/16. 1 x connector only material required. | F3 | CAMPBELL ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.004263 | 11 | 2017 | 2016-04-25 | C | 24 | 0.004263 | 7.2201e-05
1 | 10759973 | 2016-04-25 08:43 | 2016-04-25 12:40 | 237 | 700 | 30126.8667 | 0.090632 | 0.084314 | 0.0023766 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 8 | NONE | CB 8 Papamoa tripped to L/O. E/F flag. Line sectionalised & patrolled. No apparent fault found. Back feeds from sectionaliser 9954/2 to Sectionaliser 9876/2 and Recloser 9462/2 to RP09 established for duration of line patrolling etc. A/R occured on recloser 9274/2 and L/O on sectionaliser 9954/2 @ 10:18 while backfeed in place. This section of line was also sectionalised & patrolled with problem identified to be faulty sectionaliser 9876/2. Sectionaliser isolated on load side and backfeed left in place. DNO created for repairs/replacement. Not thought to be any correlation between both faults. 2r line patrol 0944 2r repair n/a | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.084314 | 11 | 2017 | 2016-04-25 | C | 700 | 0.084314 | 0.0023766
1 | 10760600 | 2016-04-25 09:24 | 2016-04-25 13:03 | 219 | 455 | 49765.2833 | 0.14971 | 0.14561 | 0.0013688 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | IC1915 | CABLE - REPAIR | CB 5 tripped to L/O. EF, INV O/C, C Ph O/C flags. Report received of transformer explosion on cnr Elizabeth Dr & Cobham Crescent. RMU IC1915, IC1828 isolated at IP122 & 9083/1 for inspection. Faulted cable identified on IC1915 termination. Cable isolated and all supply restored. DNO created to repair cable fault. 2r line patrol 1057 2r repair 1118 Related to 10761069 | F3 | THOMPSON DR | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.14561 | 11 | 2017 | 2016-04-25 | C | 455 | 0.14561 | 0.0013688
1 | 10761086 | 2016-04-25 09:41 | 2016-04-25 11:46 | 124 | 1 | 124.5833 | 0.00037479 | 0.000365 | 3.0083e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/17 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3s HV Fuses @ T8/17 and repaired an lv jumper which was toutching a bracing strap | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.000365 | 11 | 2017 | 2016-04-25 | C | 1 | 0.000365 | 3.0083e-06
1 | 10761727 | 2016-04-25 10:48 | 2016-04-25 12:11 | 83 | 254 | 13704.2167 | 0.041227 | 0.038934 | 0.00076412 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | H131 | UNKNOWN | Line sectionalised and patrolled with nothing obvious found . supply restored 2r line patrol 1139 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.038934 | 11 | 2017 | 2016-04-25 | C | 254 | 0.038934 | 0.00076412
1 | 10772682 | 2016-04-26 09:28 | 2016-04-26 12:32 | 184 | 2 | 368 | 0.0011071 | 0.001089 | 6.0166e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OTHER | SE5-199 | FUSE - ELEMENT/LINK (HV) | 1 HV Fuse Blown. Customer is happy to run one phase down until tomorrow. Reload, reliven 2x 8amp Fuses and 1x barrel. Cause was due to rat. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.001089 | 11 | 2017 | 2016-04-26 | C | 2 | 0.001089 | 6.0166e-06
1 | 10772719 | 2016-04-25 18:39 | 2016-04-25 20:15 | 96 | 9 | 866.1 | 0.0026055 | 0.002524 | 2.7075e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 245 | FUSE - ELEMENT/LINK (HV) | Advised svs hub and Control 6:46pm. Faultman found blown fuses at Fuses 245, line was patrolled no fault found. 2 X 15 amp hv fuses replaced | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.002524 | 11 | 2017 | 2016-04-25 | C | 9 | 0.002524 | 2.7075e-05
1 | 10772731 | 2016-04-25 18:50 | 2016-04-25 20:32 | 101 | 15 | 1519.25 | 0.0045705 | 0.004435 | 4.5125e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 7379 | FUSE - ELEMENT/LINK (HV) | Check for safety - Heard a loud bang coming from a pole at the start of the road (where meets with the main road) Faultman found blown fuses at Fuses 7379, line was patrolled and no fault found, suspect bird strike. 2 X 10 amp HV fuses replaced | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.004435 | 11 | 2017 | 2016-04-25 | C | 15 | 0.004435 | 4.5125e-05
1 | 10772790 | 2016-04-27 12:00 | 2016-04-27 14:28 | 148 | 7 | 1036 | 0.0031166 | 0.003053 | 2.1058e-05 | Referral | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 258 Gladstone Braes, Carterton | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | (2R) Replace transformer tomorrow (26/04) email sent to SMC for Follow up 27/4 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.003053 | 11 | 2017 | 2016-04-27 | C | 7 | 0.003053 | 2.1058e-05
1 | 10781584 | 2016-04-26 02:15 | 2016-04-26 03:25 | 69 | 24 | 1673.6 | 0.0050347 | 0.004818 | 7.2199e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 952 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 952, line was patrolled and no fault was found. 2 x 15 amp hv fuses replaced. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.004818 | 6.6 | 2017 | 2016-04-26 | C | 24 | 0.004818 | 7.2199e-05
1 | 10782117 | 2016-04-26 08:57 | 2016-04-26 10:05 | 68 | 1131 | 76351.55 | 0.22969 | 0.21948 | 0.0034024 |  | 11 | Unplanned |  | UNDERGROUND CABLE | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 9000/1 | CABLE - REPLACE LESS THAN 5 METRES | 09.30 Joe from place makers advised contractors have hit power cable opposite place makers on Joan Gaskell Drive. Have advised control. Cable fault, isolation at Sw/Gear 9000/1 & Sw/Gear 9268/1. Back fed from Sw/Gear 9116/3. Cable repairs completed & Network restored to normal. Materials required were 5 metres 185mm 3c cable and 2 joint repair kits. Downer hub to provide an NDR number 27/04/16. Job then needs to be closed off. 2r line patrol 1005 2r repair 1005 NDR 047908 | F3 | JOAN GASKELL DR | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.21948 | 11 | 2017 | 2016-04-26 | C | 1131 | 0.21948 | 0.0034024
1 | 10785332 | 2016-05-18 10:00 | 2016-05-18 12:38 | 158 | 19 | 3002 | 0.009028 | 0.008856 | 5.7139e-05 | NAPA ID:19127 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > RANGIWAHIA | 11 | Planned | 019127 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N30 | NONE | Replace burnt 11kV crossarm. Works location: Peka Rd, Rangawahia. WO 30014923 | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.004428 | 5.5 | 2017 | 2016-05-18 | B | 19 | 0.008856 | 5.7139e-05
1 | 10786340 | 2016-05-27 10:15 | 2016-05-27 14:15 | 240 | 29 | 6960 | 0.020928 | 0.020666 | 8.72e-05 | NAPA ID:18620 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 018620 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 752075 | NONE | To replace all xarms on pole 752075 plus replace 30kva transformer, upgrade earths and new lighting arrestors. Works location: Hill Rd, Egmont Village. WO 30018768 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.010333 | 5.5 | 2017 | 2016-05-27 | B | 29 | 0.020666 | 8.72e-05
1 | 10786349 | 2016-05-25 09:23 | 2016-05-25 11:35 | 132 | 3 | 396 | 0.0011908 | 0.001163 | 9.021e-06 | NAPA ID:18609 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018609 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC678 | NONE | To replace 11kV Arms, 400V Arm & install fuse disconnector. Works location: Pohlen Rd, Matamata. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0005815 | 5.5 | 2017 | 2016-05-25 | B | 3 | 0.001163 | 9.021e-06
1 | 10786541 | 2016-04-26 17:30 | 2016-04-26 23:55 | 385 | 4 | 1540 | 0.0046328 | 0.004596 | 1.2033e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | SC3-052 | CABLE - REPLACE LESS THAN 5 METRES | Hit cable , while back ramming alarm is going off, contractor still on machine. Karl Loveridge 021 676 461. Advised hub per email and phone call Sammy. LV mains cable has been hit and also blown some HV fuses, will required 2R to get cable jointer onsite, dig up and repair cable SC3-052. Transformer TC3-143 Isolated at fuses SC3-052 to allow hand digging around cables to confirm whether HV cable damaged or not. Cable repairs completed & all supply restored 23:55. Materials required 2 m 25mm single core HV cable. 2 x joint kits. NDR number 44877. | F3 | OMOKOROA RD | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.004596 | 11 | 2017 | 2016-04-26 | C | 4 | 0.004596 | 1.2033e-05
1 | 10786684 | 2016-04-26 16:36 | 2016-04-26 17:40 | 63 | 1 | 63.9 | 0.00019223 | 0.000183 | 3.0083e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8466 | CONDUCTOR - REPAIR/REHANG | Isolated at fuses 8466. Replaced 1 x 6 amp HT Fuse at 6510, repaired line down & relivened | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.000183 | 11 | 2017 | 2016-04-26 | C | 1 | 0.000183 | 3.0083e-06
1 | 10787002 | 2016-04-26 16:05 | 2016-04-26 19:26 | 200 | 3 | 602.3 | 0.0018119 | 0.001784 | 9.0249e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | SE6-226 | FUSE - ELEMENT/LINK (HV) | 2 fuses blown at SE6-226. Line patrolled. 2 x 10 amp fuses reloaded & relivened successfully following line patrol. NDR N400122 27/4/2016: Fault was caused by Tree contractors working onsite - when FM got to site last night 26/4 the tree contractors had already left site. FM is heading to site today to check if the contractors on site have a CAC - and if not issue them one. Invoicing note: Another visit today, will note on site/off site times. Mike went to site today and contractors were not on site - he spoke to ppty/land owner and they advised the contractors on site yesterday were Total Tree Removal - Orchard Removal & Tree Services Bay of Plenty, 154 Jellicoe St, Te Puke 3119. Mike rang them and informed them in future they need CAC - they said they didn't recall touching the line - but Mike said he walked the entire line yesterday and they were the only ones working under the line. Mike said fresh stump close to 11KV in the orchard. - where the stumps are stacked they are all under 11KV line and within 4 meters. Land owner details are included on NDR form. | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.001784 | 11 | 2017 | 2016-04-26 | C | 3 | 0.001784 | 9.0249e-06
1 | 10787486 | 2016-04-26 21:47 | 2016-04-27 00:32 | 164 | 217 | 16773.15 | 0.050459 | 0.0485 | 0.0010409 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730290 | CONDUCTOR - REPAIR/REHANG | CB T31 tripped on A phase O/C & E/F flags. Line was patrolled and sectionalised and lines down was found at pole 730290 caused by a duck, lines were isolated at ABS's 5968 & 5977 to repair the lines. 10 meters 16mm copper conductor used. 8 x 16mm sleeves used. 2R line patrol 2255. 2R repair 2322. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.0485 | 11 | 2017 | 2016-04-26 | C | 217 | 0.0485 | 0.0010409
1 | 10790783 | 2016-05-24 08:45 | 2016-05-24 15:02 | 377 | 10 | 3770 | 0.011337 | 0.011246 | 3.007e-05 | NAPA ID:18797 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 018797 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S69 | NONE | To replace multiple 11kV poles and crossarms. Works Location: Bruces Road and Fenmore Road, Masterton. Work Order 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.005623 | 5.5 | 2017 | 2016-05-24 | B | 10 | 0.011246 | 3.007e-05
1 | 10791495 | 2016-04-27 13:26 | 2016-04-27 15:45 | 139 | 264 | 8927.6667 | 0.026857 | 0.024474 | 0.00079719 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SC4-630 | JUMPER | Possible blown jumper lots of part powers past SC4630. CB5 opened due to reports of 2 phases lost found blown jumper at ABS SC4-630 top be repaired later. | F3 | FLYOVER | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 0.024474 | 11 | 2017 | 2016-04-27 | C | 264 | 0.024474 | 0.00079719
1 | 10791615 | 2016-05-19 13:55 | 2016-05-19 14:05 | 10 | 7 | 70 | 0.00021051 | 0.000147 | 2.1051e-05 | NAPA ID:18606 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018606 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3385 | NONE | To install a 400V Fuse Disconnector. Works location: Waharoa East d, Matamata. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 7.35e-05 | 5.5 | 2017 | 2016-05-19 | B | 7 | 0.000147 | 2.1051e-05
1 | 10791646 | 2016-05-19 09:45 | 2016-05-19 12:41 | 176 | 2 | 352 | 0.0010586 | 0.00104 | 6.0145e-06 | NAPA ID:18605 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018605 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3123 | NONE | Replace 11kV cross arms and hardware. Works location: Pahlen Rd, Matamata. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.00052 | 5.5 | 2017 | 2016-05-19 | B | 2 | 0.00104 | 6.0145e-06
1 | 10791672 | 2016-05-16 09:30 | 2016-05-16 13:21 | 231 | 25 | 5775 | 0.017368 | 0.017142 | 7.5185e-05 | NAPA ID:18716 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | 018716 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC680 | NONE | Install SWER Recloser 9927/6. Works location: Stony Bay Rd, Port Charles Coromandel. WO 10148359 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.008571 | 5.5 | 2017 | 2016-05-16 | B | 25 | 0.017142 | 7.5185e-05
1 | 10792065 | 2016-05-10 09:35 | 2016-05-10 16:21 | 406 | 129 | 52374 | 0.15752 | 0.15636 | 0.00038799 | NAPA ID:17824 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11 | Planned | 017824 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/12 | NONE | Change 6 x HV poles. Works location: Arthur St. WO 30024426 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.07818 | 5.5 | 2017 | 2016-05-10 | B | 129 | 0.15636 | 0.00038799
1 | 10792283 | 2016-05-17 09:31 | 2016-05-17 16:19 | 408 | 54 | 22032 | 0.066258 | 0.065771 | 0.0001624 | NAPA ID:18631 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > LAKES EXPRESS | 11 | Planned | 018631 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-019 | NONE | New Poles and hardware on Merrick Road in Tauranga. Works location: Merrick Rd, Tauranga. WO 30017843 | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.032885 | 5.5 | 2017 | 2016-05-17 | B | 54 | 0.065771 | 0.0001624
1 | 10792301 | 2016-05-18 09:57 | 2016-05-18 15:45 | 348 | 54 | 18792 | 0.056514 | 0.056026 | 0.0001624 | NAPA ID:18633 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > LAKES EXPRESS | 11 | Planned | 018633 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE3-019 | NONE | New Poles and hardware on Merrick and Edward road in Tauranga. Works location: Merrick Rd, Tauranga. WO 30017843 | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.028013 | 5.5 | 2017 | 2016-05-18 | B | 54 | 0.056026 | 0.0001624
1 | 10792387 | 2016-05-23 09:20 | 2016-05-23 15:56 | 396 | 54 | 21384 | 0.064304 | 0.063816 | 0.00016238 | NAPA ID:18634 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > LAKES EXPRESS | 11 | Planned | 018634 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE3-019 | NONE | New Poles and hardware on Merrick road in Tauranga. Works location: Merrick Rd, Tauranga. WO 30017843 | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.031908 | 5.5 | 2017 | 2016-05-23 | B | 54 | 0.063816 | 0.00016238
1 | 10793859 | 2016-05-24 09:28 | 2016-05-24 15:19 | 351 | 54 | 18975.6 | 0.057061 | 0.056573 | 0.00016238 | NAPA ID:18636 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > LAKES EXPRESS | 11 | Planned | 018636 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-019 | NONE | New Poles and hardware on Merrick road in Tauranga. Works location: Merrick Rd, Tauranga. WO 30017843 | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.028286 | 5.5 | 2017 | 2016-05-24 | B | 54 | 0.056573 | 0.00016238
1 | 10794239 | 2016-04-27 21:22 | 2016-04-28 01:36 | 254 | 260 | 12494.2 | 0.037586 | 0.035239 | 0.0014771 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 210935 | POLE | Damaged pole in HV line between ABS SD4-670 & SE4-025. (Pole 210935) Line isolated between these points and temp line break created at pole 249545. (Line isolated - break created using G & B methods) Isolations for pole replacement was this break and ABS SE4-025. fire comms reporting car v pole and lines down, ETA required 09 486 7948. ETA 15 -20 mins fire comms advised. Same isolations and methods used to close break following repairs.Materials required - 1 x 11m pole, 1 x HV arm, pins & ins, 1 x d/arm LV & road crossing hardware. NDR number 35546. No tripping so no 2r line patrol | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.035239 | 11 | 2017 | 2016-04-27 | C | 260 | 0.035239 | 0.0014771
1 | 10796424 | 2016-04-28 00:53 | 2016-04-28 02:03 | 69 | 951 | 24451 | 0.073554 | 0.064971 | 0.001832 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9507/2 | NONE | Recloser 9507/2 tripped to L/O. O/C flag. 9507/2 was backfeeding to recloser 9182/2 at time due to fault on WBY CB 1. (OMS 10794239). Line sectionalised and patrolled. No fault found. All supply restored. Network configuration restored to normal after fault repairs completed on OMS 10794239. 2r line patrol 0129. No repair | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.064971 | 11 | 2017 | 2016-04-28 | C | 951 | 0.064971 | 0.001832
1 | 10797457 | 2016-04-28 10:42 | 2016-04-28 11:51 | 69 | 90 | 6210 | 0.018681 | 0.017868 | 0.00027074 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD4-567 | FUSE - ELEMENT/LINK (HV) | at 10:42, Tauranga Sub, CB 13 Oropi Feeder. Found Blown Fuse at Fuses SD4-567. Requested to reload, reliven. Permission granted. Reload Reliven Unsuccessful. Isolated Cables at Fuses SD4-467. Permit issued to test cable - all OK. Believe the original faultman may have been putting in the incorrect fuse size and was causing it to blow on inrush current (fuse rating was too low). Another faultman attended and relivened with correct fuse rating. All OK. All Power Restored on Completion. Brian Sperling Attended. check for safety - Loud bang and flash from TX outside address - Flickering power on the street. Advised control and SMC of 999. 10.30 FM advised power will be off from 10.30 - 11.30 while working on lv side of the tx. Have put through a emergency outage. low fusing size | F3 | OROPI RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.017868 | 11 | 2017 | 2016-04-28 | C | 90 | 0.017868 | 0.00027074
1 | 10797475 | 2016-05-12 09:00 | 2016-05-12 13:22 | 262 | 22 | 5764 | 0.017336 | 0.017137 | 6.6167e-05 | NAPA ID:18602 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018602 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole H12515 | NONE | To replace the arms and hardware on pole H12515 - TC3401. Works location: Casey St, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0085685 | 5.5 | 2017 | 2016-05-12 | B | 22 | 0.017137 | 6.6167e-05
1 | 10797604 | 2016-05-30 08:49 | 2016-05-30 14:40 | 351 | 54 | 18956.7 | 0.056998 | 0.056511 | 0.00016237 | NAPA ID:18637 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > LAKES EXPRESS | 11 | Planned | 018637 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE3-019 | NONE | Conductor the end of Merrick Road and Edward Avenue. Works location: Merrick Rd, Tauranga. WO 30017843 | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.028255 | 5.5 | 2017 | 2016-05-30 | B | 54 | 0.056511 | 0.00016237
1 | 10797623 | 2016-04-28 08:40 | 2016-04-28 08:42 | 2 | 178 | 450.9333 | 0.0013565 | 0 | 0.00053546 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | Operator error | NONE | Operator Error - Incorrect Operation led to LOS to 178 customers. Cause due to applying CAC safety measure 19045-01. Incorrectly selected wrong action in control box. ASW | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-04-28 | C | 178 | 0 | 0.00053546
1 | 10798248 | 2016-05-06 09:15 | 2016-05-06 12:03 | 168 | 1 | 168 | 0.00050532 | 0.000496 | 3.0078e-06 | NAPA ID:19112 TP_WANGANUI GXP > BEACH RD SUB > KINGS AVENUE | 11 | Planned | 019112 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 4692 | NONE | Shut down transformers 4691w,4692w,4693w to install power monitoring equipment during plant shutdown. Works location: Open Country Dairy Factory, Wanganui. WO 10141920 | F2 | KINGS AVENUE | WANGANUI | Wanganui | BEACH RD SUB | Western Electricity | POWERCO | 0.000248 | 5.5 | 2017 | 2016-05-06 | B | 1 | 0.000496 | 3.0078e-06
1 | 10798763 | 2016-04-28 10:40 | 2016-04-28 11:54 | 74 | 414 | 18697.6 | 0.056247 | 0.05251 | 0.0012454 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2111 | JUMPER | CB 5 tripped on O/C A & B phase E/F. . Blown jumper CB side ABS 2111. Suspected this was caused by Combine Contactors who were trimming hedges at the time in the area. 027 495 6106 Hm07 8847 974 - NDR 55709. 2r line patrol 1152 | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.05251 | 11 | 2017 | 2016-04-28 | C | 414 | 0.05251 | 0.0012454
1 | 10799819 | 2016-04-28 11:34 | 2016-04-28 12:18 | 43 | 21 | 915.25 | 0.0027533 | 0.002563 | 6.3173e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6060 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Fuses 6060 required replacing. They broke during NAPA 19251 OMS 10785818. and were replaced under this OMS. Used 3 x HV Fuses carriers and 3 x 3A Fuses. | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.002563 | 6.6 | 2017 | 2016-04-28 | C | 21 | 0.002563 | 6.3173e-05
1 | 10801009 | 2016-04-28 14:55 | 2016-04-28 16:48 | 113 | 5 | 565 | 0.0016996 | 0.001654 | 1.5041e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1282 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced Transformer T1282 has a broken hanger arm (15kvA) | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001654 | 11 | 2017 | 2016-04-28 | C | 5 | 0.001654 | 1.5041e-05
1 | 10801116 | 2016-05-12 08:46 | 2016-05-12 14:37 | 350 | 193 | 67599.5 | 0.20331 | 0.20157 | 0.00058046 | NAPA ID:18102 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 018102 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 837431 | NONE | Replace various arms and poles within work area. Reconductor from abs 6392 to 837431. Install line break at pole 704479. Works location: South Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.10078 | 5.5 | 2017 | 2016-05-12 | B | 193 | 0.20157 | 0.00058046
1 | 10801515 | 2016-05-31 08:50 | 2016-05-31 15:30 | 400 | 54 | 21600 | 0.064945 | 0.064458 | 0.00016236 | NAPA ID:18639 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > LAKES EXPRESS | 11 | Planned | 018639 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-019 | NONE | Reconductor The Valley spur plus Merrick Road. Works location: Merrick Rd, Tauranga. WO 30017843 | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.032229 | 5.5 | 2017 | 2016-05-31 | B | 54 | 0.064458 | 0.00016236
1 | 10801532 | 2016-06-02 08:30 | 2016-06-02 15:50 | 440 | 54 | 23760 | 0.071437 | 0.07095 | 0.00016236 | NAPA ID:18640 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > LAKES EXPRESS | 11 | Planned | 018640 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE3-019 | NONE | Reconductor The Valley spur plus Merrick Road. Works location: Merrick Rd, Tauranga. WO 30017843 | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.035475 | 5.5 | 2017 | 2016-06-02 | B | 54 | 0.07095 | 0.00016236
1 | 10802787 | 2016-04-28 17:13 | 2016-04-28 20:40 | 207 | 1 | 207.1 | 0.000623 | 0.000613 | 3.0082e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | fc4038 | FUSE - ELEMENT/LINK (HV) | 2 fuses blown at FC4038 Line patrolled fuses relivened. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.000613 | 11 | 2017 | 2016-04-28 | C | 1 | 0.000613 | 3.0082e-06
1 | 10807223 | 2016-04-29 09:54 | 2016-04-29 11:50 | 115 | 1 | 115.7333 | 0.00034815 | 0.000339 | 3.0081e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 827680 - Sent to Steph | FUSE - ELEMENT/LINK (HV) | replaced x2 HV fuses reload and reliven x2 10amp at links 7105 cause -unknown power back on @ 11:50am (Frank going to check at the pump about 13ks away to see if it is working - tried to call John on 06 3722804 at the pump site but no answer) No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000339 | 11 | 2017 | 2016-04-29 | C | 1 | 0.000339 | 3.0081e-06
1 | 10807485 | 2016-04-29 22:00 | 2016-04-29 22:08 | 8 | 66 | 528 | 0.0015883 | 0.000992 | 0.00019854 | NAPA ID:19335 TP_BUNNYTHORPE GXP > MAIN ST SUB > MAIN ST 23 | 11 | Planned | 019335 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer G91 | NONE | isolate tx G91 to tap it up as voltage is low once load comes on. Works location: Ruahine St. WO 30002198 | F2 | MAIN ST 23 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 0.000496 | 5.5 | 2017 | 2016-04-29 | B | 66 | 0.000992 | 0.00019854
1 | 10807658 | 2016-04-29 10:55 | 2016-04-29 13:17 | 141 | 2 | 282.8333 | 0.00085081 | 0.000832 | 6.0163e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | NNF Two contacts for this this morning from TrustPower. FM has confirmed with customers this was resolved yesterday under 10801044 appears these contacts didn't come through with the original job yesterday. | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000832 | 11 | 2017 | 2016-04-29 | C | 2 | 0.000832 | 6.0163e-06
1 | 10808151 | 2016-04-29 12:31 | 2016-04-29 14:45 | 133 | 13 | 1739.4 | 0.0052324 | 0.005115 | 3.9106e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | R27 | FUSE - ELEMENT/LINK (HV) | Replaced x2 sectionaliser fuses at fuse R27 cause due to wind (x2 10amp). Power back on @ 14:45 No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORED | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.005115 | 11 | 2017 | 2016-04-29 | C | 13 | 0.005115 | 3.9106e-05
1 | 10808574 | 2016-04-29 13:52 | 2016-04-29 15:12 | 80 | 398 | 16094.3333 | 0.048414 | 0.044822 | 0.0011973 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P39358 | CONDUCTOR - REPAIR/REHANG | Truck flipped hit lines and dragged down. Fire ref F2067987. ETA required. 04 801 0812. Truck hit S/L which fell over into HV Lines tripping feeder. Lines isolated & earthed, backfeeds installed, and truck & S/L cleared from lines. Relivened ok. Nil materials used. NDR# N300187. 2r line patrol 1428. 2r repair 1444 | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.044822 | 11 | 2017 | 2016-04-29 | C | 398 | 0.044822 | 0.0011973
1 | 10809138 | 2016-05-23 08:45 | 2016-05-23 14:24 | 339 | 30 | 10170.1667 | 0.030583 | 0.030312 | 9.0213e-05 | NAPA ID:18714 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | 018714 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P05019 | NONE | Replace 11kV pole P05019 and fittings and install a new SCADA controlled Recloser 10300, test and commission. Works location: Tokorangi Rd. WO 30016187 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.015156 | 5.5 | 2017 | 2016-05-23 | B | 30 | 0.030312 | 9.0213e-05
1 | 10809469 | 2016-05-07 07:01 | 2016-05-07 07:07 | 6 | 162 | 1031.4 | 0.0031023 | 0.00164 | 0.00048726 | NAPA ID:18802 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | 018802 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X406 | NONE | Replacing defective Magnefix Links at 411/3. Works location: Morley St, New Plymouth. WO 30015277 | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.00082 | 5.5 | 2017 | 2016-05-07 | B | 162 | 0.00164 | 0.00048726
1 | 10809547 | 2016-04-29 16:51 | 2016-04-29 18:40 | 109 | 115 | 9752.2 | 0.029336 | 0.028298 | 0.00040911 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | RS 1022 A/R, L/O, E/F, O/C B & C Phase. Line patrolled with no fault found possible bird strike. 2 r line patrol 1750 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.028298 | 6.6 | 2017 | 2016-04-29 | C | 115 | 0.028298 | 0.00040911
1 | 10810183 | 2016-04-29 19:53 | 2016-04-29 23:04 | 191 | 167 | 26993.4167 | 0.081201 | 0.079693 | 0.00050236 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 762847 | NONE | RS 6286 Tripped E/F L/O. Possum found on lines at Pole 762847 during sectionlising, cleared using hot sticks 2r line patrol 2116 no repair. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.079693 | 11 | 2017 | 2016-04-29 | C | 167 | 0.079693 | 0.00050236
1 | 10811331 | 2016-04-30 07:21 | 2016-04-30 09:13 | 112 | 18 | 235.6667 | 0.00070891 | 0.000546 | 5.4146e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | V83 | FUSE - ELEMENT/LINK (HV) | Check related OMS: 10811511. Replaced 2x 10Amp HV fuse links | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.000546 | 11 | 2017 | 2016-04-30 | C | 18 | 0.000546 | 5.4146e-05
1 | 10811628 | 2016-04-30 08:14 | 2016-04-30 11:45 | 211 | 8 | 1688 | 0.0050777 | 0.005005 | 2.4065e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE4-041 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer TE4-041 Faulty. Replaced | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.005005 | 11 | 2017 | 2016-04-30 | C | 8 | 0.005005 | 2.4065e-05
1 | 10811701 | 2016-04-30 10:37 | 2016-04-30 10:56 | 19 | 37 | 703 | 0.0021147 | 0.00178 | 0.0001113 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 447663 | JOINT - CONDUCTOR JOINT | New Ampac connection on line was loose. Replaced with PT joint | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.00178 | 11 | 2017 | 2016-04-30 | C | 37 | 0.00178 | 0.0001113
1 | 10812617 | 2016-04-30 12:05 | 2016-04-30 12:43 | 38 | 60 | 2289.8333 | 0.0068881 | 0.006346 | 0.00018049 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W1030 | JUMPER | Repaired HV Jumper using 1mtr x 16mm cu. conductor, 1x sleeve, and 1x EP connector | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.006346 | 11 | 2017 | 2016-04-30 | C | 60 | 0.006346 | 0.00018049
1 | 10813335 | 2016-04-30 14:30 | 2016-04-30 18:05 | 214 | 10 | 2147.5 | 0.0064599 | 0.006369 | 3.0081e-05 |  | 22 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 855 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10Amp HV fuse links - suspected bird strike | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.006369 | 22 | 2017 | 2016-04-30 | C | 10 | 0.006369 | 3.0081e-05
1 | 10814111 | 2016-05-01 02:29 | 2016-05-01 04:27 | 118 | 139 | 11952.65 | 0.035955 | 0.0347 | 0.00041812 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | G0421 | NONE | at 02:29, Browne St Sub, CB 5 Station Rd Feeder, Recloser 9664 Tripped, E/F, B + C O/C, L/O. Faultmen dispatched and investigation began. Line Patrolled & Sectionalised. While Patrolling, found possum on line at Pole G0421. Removed with hot stick. Line relivened. All OK. Perry Hicks Attended. Faultman advised that none of the poles in this area had possum guards on them. 2r line patrol 0328 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0347 | 11 | 2017 | 2016-05-01 | C | 139 | 0.0347 | 0.00041812
1 | 10814611 | 2016-05-01 03:21 | 2016-05-01 04:57 | 96 | 629 | 47989.9167 | 0.14436 | 0.13868 | 0.0037842 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | NONE | CB XT 30 Tripped E/F no audible alarms, Transpower advised of A/R on CB 1332 N O/T. No job raised due to CB XT50 not shown on network at the moment, ABS Dressed open to create job. Due to RTU issues at sub required faultman on site before closing CB XT 30. Faultman checked sub all ok. 2r line patrol 0455 | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.13868 | 33 | 2017 | 2016-05-01 | C | 629 | 0.13868 | 0.0037842
1 | 10819139 | 2016-05-01 12:25 | 2016-05-01 15:49 | 203 | 212 | 25109.2667 | 0.075531 | 0.073617 | 0.00063771 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 793149 | CONDUCTOR - REPAIR/REHANG | Have advised fire comms eta 20 mins. CB 3 tripped on B & C phase O/C flags, received a call from fire comms of a fire at intersection SH 3 & Pauri Rd, faultman found a line down at pole 793149, line was isolated at ABS's 680 & 716 to repair the line.Tree contractor called in by faultman to cut trees. NDR: 30472. 2 metres. Rabbit conductor used & 3 rabbit sleeves used. 2r line patrol 1258. 2r repair 1307. | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.073617 | 11 | 2017 | 2016-05-01 | C | 212 | 0.073617 | 0.00063771
1 | 10819800 | 2016-05-01 15:00 | 2016-05-01 17:07 | 127 | 28 | 3556 | 0.010697 | 0.010444 | 8.4226e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P06841 | BINDER | 184 RANGE ROAD. Faultman found blown fuses at V16, line was patrolled and a floating wire was found at pole P06841, line was isolated at Fuses V16, ABS's V15 & V19 to rebinding conductor. Pole been defected by faultman. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.010444 | 11 | 2017 | 2016-05-01 | C | 28 | 0.010444 | 8.4226e-05
1 | 10820116 | 2016-05-01 18:30 | 2016-05-01 22:43 | 253 | 34 | 2931 | 0.0088167 | 0.008509 | 3.6097e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 850107 | CONDUCTOR - REPAIR/REHANG | Untangled HV Lines. Nil materials used. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.008509 | 11 | 2017 | 2016-05-01 | C | 34 | 0.008509 | 3.6097e-05
1 | 10820541 | 2016-05-01 21:39 | 2016-05-02 01:57 | 257 | 499 | 37563.7667 | 0.11299 | 0.10849 | 0.001501 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 756921 | POLE | CB 6 A/R, L/O, E/F A & B Phase. Car vs pole. Isolation at ABS 151 & ABS 257. Backfeed installed via ABS 187. 11kV Pole replaced complete with crossarm & all hardware. NDR# N100143. 2r line patrol 2228. 2r repair 2308 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.10849 | 11 | 2017 | 2016-05-01 | C | 499 | 0.10849 | 0.001501
1 | 10821830 | 2016-05-01 18:30 | 2016-05-02 00:10 | 340 | 19 | 6460 | 0.019432 | 0.01926 | 5.7154e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Replaced 1x 10Amp HV Link | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.01926 | 11 | 2017 | 2016-05-01 | C | 19 | 0.01926 | 5.7154e-05
1 | 10822211 | 2016-05-02 10:41 | 2016-05-02 11:08 | 27 | 24 | 648 | 0.0019492 | 0.001732 | 7.2193e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5165 | JUMPER | Blown jumper replaced. 1m 16mm Cu conductor and 1 joint. Isolated at TA 823 unknown cause | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001732 | 11 | 2017 | 2016-05-02 | C | 24 | 0.001732 | 7.2193e-05
1 | 10822505 | 2016-05-19 09:30 | 2016-05-19 14:17 | 287 | 24 | 6888 | 0.020714 | 0.020497 | 7.2175e-05 | NAPA ID:18108 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 018108 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6392 | NONE | Replace various arms and poles within work area. Works location: South Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.010249 | 5.5 | 2017 | 2016-05-19 | B | 24 | 0.020497 | 7.2175e-05
1 | 10824494 | 2016-05-02 09:40 | 2016-05-02 15:20 | 340 | 1 | 340 | 0.0010227 | 0.001013 | 3.008e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc1-021 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | replaced tx TC1-021 And 2 x 100amp and 60amp lv HRC fuse 1 x 3amp hv fuse due to old age | F4 | KATIKATI | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.001013 | 11 | 2017 | 2016-05-02 | C | 1 | 0.001013 | 3.008e-06
1 | 10824599 | 2016-05-02 10:35 | 2016-05-02 11:15 | 40 | 6 | 240 | 0.00072193 | 0.000667 | 1.8048e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1177 | FUSE - ELEMENT/LINK (HV) | lv fuseway replaced isolated on hv for safety. Materials 1 hv fuse 3 amp and holder 1 x lv stanger breaker | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000667 | 11 | 2017 | 2016-05-02 | C | 6 | 0.000667 | 1.8048e-05
1 | 10825079 | 2016-05-13 11:20 | 2016-05-13 12:30 | 70 | 3 | 210 | 0.00063158 | 0.000604 | 9.0226e-06 | NAPA ID:19357 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 7 | 11 | Planned | 019357 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 525 | NONE | We have to replace 2 - 11kv fuses live line but have to off load transformer 525 first. These have real rusty bolts with lightning arrestors attached. Works location: Frankley Rd, New Plymouth. WO 30026840 | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000302 | 5.5 | 2017 | 2016-05-13 | B | 3 | 0.000604 | 9.0226e-06
1 | 10826053 | 2016-05-17 09:30 | 2016-05-17 15:24 | 354 | 71 | 25134 | 0.075587 | 0.074946 | 0.00021352 | NAPA ID:18691 TP_KAITIMAKO GXP > WELCOME BAY SUB > WELCOME BAY | 11 | Planned | 018691 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 268846 | NONE | Replace pole and reconductor feeder wire. Install ABS 23. Place GenSet on at TD4-536. Works location: Ranginui Rd. WO 30017840 | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.037473 | 5.5 | 2017 | 2016-05-17 | B | 71 | 0.074946 | 0.00021352
1 | 10826086 | 2016-05-02 14:19 | 2016-05-02 14:22 | 3 | 98 | 294 | 0.00088436 | 0 | 0.00029479 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3120 | NONE | 12.18pm advised Tarns & emailed svs hub. Transformer offloaded & dropped 2 x taps voltage reading now correct & taps match nearby transformers | F3 | OTAHU RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-05-02 | C | 98 | 0 | 0.00029479
1 | 10826662 | 2016-05-18 09:15 | 2016-05-18 15:43 | 388 | 116 | 15253 | 0.045871 | 0.044824 | 0.00055034 | NAPA ID:18694 TP_KAITIMAKO GXP > WELCOME BAY SUB > WELCOME BAY | 11 | Planned | 018694 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-536 | NONE | Replace pole and recon feeder wire, connect gen set up to supply TD4-536. Works location: Ranginui Rd. WO 30017840 | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.022412 | 5.5 | 2017 | 2016-05-18 | B | 116 | 0.044824 | 0.00055034
1 | 10826853 | 2016-05-05 02:00 | 2016-05-06 02:03 | 1443 | 1362 | 38702.05 | 0.11641 | 0.10412 | 0.0028936 | NAPA ID:19393 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | 019393 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SA2-010 | NONE | Change HV Poles and Xarms Between SA2 010 and Temp ABS 42. Backfeed required from KPT2 via 9405/2 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.052061 | 5.5 | 2017 | 2016-05-05 | B | 1362 | 0.10412 | 0.0028936
1 | 10826857 | 2016-05-25 09:15 | 2016-05-25 14:36 | 321 | 49 | 15729 | 0.047297 | 0.046855 | 0.00014734 | NAPA ID:18695 TP_KAITIMAKO GXP > WELCOME BAY SUB > WELCOME BAY | 11 | Planned | 018695 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 23 | NONE | Replace pole recon feeder wire. Works location: Ranginui Rd. WO 30017840 | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.023428 | 5.5 | 2017 | 2016-05-25 | B | 49 | 0.046855 | 0.00014734
1 | 10826920 | 2016-05-26 09:45 | 2016-05-26 14:17 | 272 | 49 | 13328 | 0.040077 | 0.039634 | 0.00014734 | NAPA ID:18696 TP_KAITIMAKO GXP > WELCOME BAY SUB > WELCOME BAY | 11 | Planned | 018696 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD4-171 | NONE | Replace pole and reconductor feeder wire. Works location: Ranginui Rd. WO 30017840 | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.019817 | 5.5 | 2017 | 2016-05-26 | B | 49 | 0.039634 | 0.00014734
1 | 10828394 | 2016-05-02 17:10 | 2016-05-02 18:50 | 99 | 1 | 99.65 | 0.00029975 | 0.00029 | 3.008e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | T873 | FUSE - ELEMENT/LINK (HV) | retailer now advising that there are two poles down in his paddock, he is staying away from these area is secure please see customer while on site - advised svs hub of this Disconnected LV Jumpers to line with LV Poles Down as no LV fusing. Replaced 2x 3Amp HV Links at Transformer | F3 | WEST ST | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.00029 | 11 | 2017 | 2016-05-02 | C | 1 | 0.00029 | 3.008e-06
1 | 10828805 | 2016-05-02 18:15 | 2016-05-02 22:00 | 225 | 4 | 898.65 | 0.0027032 | 0.002667 | 1.2032e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD5-175 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer TD5-175 Faulty. Replaced | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.002667 | 11 | 2017 | 2016-05-02 | C | 4 | 0.002667 | 1.2032e-05
1 | 10829118 | 2016-05-02 21:34 | 2016-05-02 22:10 | 36 | 2 | 72.4 | 0.00021778 | 0.000199 | 6.016e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T8/267 | JUMPER | Repaired 2x HV Jumpers between DDO's & Transformer. Replaced 2x 3Amp HV Fuse Links | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.000199 | 11 | 2017 | 2016-05-02 | C | 2 | 0.000199 | 6.016e-06
1 | 10831181 | 2016-05-20 10:05 | 2016-05-20 12:46 | 161 | 24 | 3864 | 0.01162 | 0.011403 | 7.2174e-05 | NAPA ID:18698 TP_KAITIMAKO GXP > WELCOME BAY SUB > WELCOME BAY | 11 | Planned | 018698 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 215252 | NONE | Replace pole 215252 and arm at 215249. Works location: Welcome Bay Rd. WO 30017840 | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.0057015 | 5.5 | 2017 | 2016-05-20 | B | 24 | 0.011403 | 7.2174e-05
1 | 10831362 | 2016-05-23 09:31 | 2016-05-23 12:26 | 175 | 31 | 5425 | 0.016313 | 0.016033 | 9.322e-05 | NAPA ID:18700 TP_KAITIMAKO GXP > WELCOME BAY SUB > WELCOME BAY | 11 | Planned | 018700 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-156 | NONE | Replace under LLWP HV and DDO arm/fuses to TX TD4-156. Works location: Welcome Bay Rd. WO 30017840 | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.0080165 | 5.5 | 2017 | 2016-05-23 | B | 31 | 0.016033 | 9.322e-05
1 | 10832480 | 2016-05-03 10:14 | 2016-05-03 11:19 | 65 | 613 | 30363.6 | 0.091333 | 0.085801 | 0.0018439 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | CB 7 | FUSE - ELEMENT/LINK (HV) | CB 7 tripped, no flags. Bird found under the lines at Fused BAS 2825 with 3 x fuses blown at Fuses 2653. Lines checked OK, Relivened and Fuses replaced. Call from retailer. Address 19 Tawa Street, Gonville saw sparks and heard large bang outside this ppty. TX 3044. Replaced 3 x 50A Fuses. 2R line patrol 10:56 no 2R repair | F1 | GONVILLE | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 0.085801 | 11 | 2017 | 2016-05-03 | C | 613 | 0.085801 | 0.0018439
1 | 10833151 | 2016-05-25 14:05 | 2016-05-25 14:40 | 35 | 7 | 245 | 0.00073672 | 0.000673 | 2.1049e-05 | NAPA ID:18610 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11.00000000 | Planned | 018610 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2061 | NONE | To install a 400V Fuse Disconnector. Works location: Waharoa East Rd, Matamata. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0003365 | 5.5 | 2017 | 2016-05-25 | B | 7 | 0.000673 | 2.1049e-05
1 | 10833455 | 2016-05-19 09:05 | 2016-05-19 16:05 | 420 | 32 | 13440 | 0.040418 | 0.040129 | 9.6233e-05 | NAPA ID:18595 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018595 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 213064 | NONE | Replace poles ,hardware and conductor between poles 213064 & TEMP32. Works location: Minden Rd. WO 30002520 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.020064 | 5.5 | 2017 | 2016-05-19 | B | 32 | 0.040129 | 9.6233e-05
1 | 10833501 | 2016-05-27 09:11 | 2016-05-27 10:00 | 49 | 1 | 49 | 0.00014734 | 0.000138 | 3.0069e-06 | NAPA ID:18677 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | 018677 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 854185 | NONE | Replace Deadends @ pole#854185. Works location: Wood Rd, Colville. WO 30025273 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 6.9e-05 | 5.5 | 2017 | 2016-05-27 | B | 1 | 0.000138 | 3.0069e-06
1 | 10833799 | 2016-05-03 12:32 | 2016-05-03 15:24 | 171 | 254 | 14877.8 | 0.044752 | 0.04246 | 0.0015281 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | H131 | UNKNOWN | Feeder sectionalised, patrolled and no fault found. 2r feeder fault 1307 no repair | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.04246 | 11 | 2017 | 2016-05-03 | C | 254 | 0.04246 | 0.0015281
1 | 10834583 | 2016-05-31 09:00 | 2016-05-31 15:06 | 366 | 270 | 98820 | 0.29712 | 0.29469 | 0.00081182 | NAPA ID:16246 TP_LINTON GXP > KAIRANGA SUB > TAKARO | 11 | Planned | 016246 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P43448 | NONE | connect new 11KV U/G Cable from new switch 10288 to poles p43446, P43448 and Tx T6/176. Remove ABS's A32, A34 and A33 and associated buswork, liven new switch, phase and commission. Works location: Monrad St. WO 10159894 | F3 | TAKARO | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.14734 | 5.5 | 2017 | 2016-05-31 | B | 270 | 0.29469 | 0.00081182
1 | 10836280 | 2016-05-03 23:00 | 2016-05-04 08:40 | 579 | 110 | 26524.5667 | 0.079786 | 0.078792 | 0.00034592 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P46563 | BINDER | Recloser T42/2 tripped on A phase O/C & E/F flags line was patrolled but faultman cannot see low hanging mist and feed goes cross country, faultman will return in morning. Repair conductor on the cross arm at Pole P46563 2r line patrol 0026 2r repair 0811 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.078792 | 11 | 2017 | 2016-05-03 | C | 110 | 0.078792 | 0.00034592
1 | 10837142 | 2016-05-03 23:20 | 2016-05-04 02:11 | 170 | 254 | 16596.3667 | 0.049922 | 0.047629 | 0.0014799 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P01673 | INSULATOR | Recloser tripped on E/F flags, line was patrolled and sectionalised and a cracked insulator was found at pole P01673, line was isolated at Fuses H140 to replace the insulator. 1 X 11KV insulator replaced. 1 X binder used. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.047629 | 11 | 2017 | 2016-05-03 | C | 254 | 0.047629 | 0.0014799
1 | 10838154 | 2016-05-04 05:47 | 2016-05-04 07:40 | 112 | 1 | 112.7333 | 0.0003391 | 0.00033 | 3.0079e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FP1627 | FUSE - ELEMENT/LINK (HV) | 2 x 6 amp HT fuses, FP1627, bird strike, spur line, | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.00033 | 11 | 2017 | 2016-05-04 | C | 1 | 0.00033 | 3.0079e-06
1 | 10839330 | 2016-05-21 09:12 | 2016-05-21 16:37 | 444 | 221 | 98284.1167 | 0.29556 | 0.29357 | 0.00066459 | NAPA ID:16337 TP_KOPU GXP > KEREPEHI SUB | 11 | Planned | 016337 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole O13353 | NONE | 11kV Cross arm replacement at pole O13353 (ABS IC419). Works location: Kerepehi Town Rd. WO 30002579 | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.14678 | 5.5 | 2017 | 2016-05-21 | B | 221 | 0.29357 | 0.00066459
1 | 10839510 | 2016-05-11 09:10 | 2016-05-11 11:25 | 135 | 26 | 3510 | 0.010557 | 0.010322 | 7.8198e-05 | NAPA ID:19443 TP_HAWERA GXP > MANAIA SUB > OKAIAWA | 11 | Planned | 019443 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 718897 | NONE | Replace cracked 11Kv xarm at pole 718897. Works location: Scott Rd, Hawera. WO 30007226 | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.005161 | 5.5 | 2017 | 2016-05-11 | B | 26 | 0.010322 | 7.8198e-05
1 | 10841672 | 2016-05-04 19:25 | 2016-05-04 21:20 | 115 | 37 | 4210.6333 | 0.012665 | 0.012331 | 0.00011129 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 107 | UNKNOWN | Recloser 107 tripped on B phase O/C flags, line was patrolled and a blown fuse was found at Fuses Temp 02 following a few part power jobs, line was also patrolled and sectionalised past Recloser 107 and no found was found, suspect bird strike as lots of ducks in area. 1 X 20 Amp HV fuse replaced. 2r line patrol 2116. No repair. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.012331 | 11 | 2017 | 2016-05-04 | C | 37 | 0.012331 | 0.00011129
1 | 10842183 | 2016-05-04 23:48 | 2016-05-05 01:12 | 84 | 56 | 4721.7333 | 0.014203 | 0.013697 | 0.00016844 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T25 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses T25, line was patrolled no fault could be found. 2 X 10 amp hv fuses replaced | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.013697 | 11 | 2017 | 2016-05-04 | C | 56 | 0.013697 | 0.00016844
1 | 10845156 | 2016-05-05 06:51 | 2016-05-05 07:52 | 60 | 4 | 242.1333 | 0.00072831 | 0.000692 | 1.2031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | FC2422 | FUSE - ELEMENT/LINK (HV) | 2x6amp fuses blown at FC2422. Line patrolled no cause found. (FM thinks possible birds) | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.000692 | 11 | 2017 | 2016-05-05 | C | 4 | 0.000692 | 1.2031e-05
1 | 10845222 | 2016-05-24 09:15 | 2016-05-24 13:21 | 246 | 1 | 246 | 0.00073973 | 0.00073 | 3.007e-06 | NAPA ID:18726 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 018726 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV TC4408 | NONE | Install recloser in SWER line. Works location: Tapu Coroglen Rd, Coroglen. WO 10148359 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000365 | 5.5 | 2017 | 2016-05-24 | B | 1 | 0.00073 | 3.007e-06
1 | 10845691 | 2016-05-25 09:15 | 2016-05-25 15:27 | 372 | 6 | 2232 | 0.0067116 | 0.006657 | 1.8042e-05 | NAPA ID:17610 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | 017610 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P22148 | NONE | Run 11kv to new pole at P22148. Works location: Awahuri Rd. WO 10157896 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.0033285 | 5.5 | 2017 | 2016-05-25 | B | 6 | 0.006657 | 1.8042e-05
1 | 10846539 | 2016-05-05 09:00 | 2016-05-05 11:25 | 145 | 659 | 17367.2333 | 0.052239 | 0.046292 | 0.0020965 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752332 | CONDUCTOR - REPAIR/REHANG | 1 X HT Insulator. 2M Conductor. 1 X 15 Amp HT Fuse. CB5 trip caused by lines down at pole, 752332, unknown cause of lines down. Isolated at fuses 8253, no back feed. 2R line patrol 0914. 2R repair 1007 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.046292 | 11 | 2017 | 2016-05-05 | C | 659 | 0.046292 | 0.0020965
1 | 10848508 | 2016-05-27 09:15 | 2016-05-27 14:40 | 325 | 10 | 3250 | 0.0097724 | 0.009682 | 3.0069e-05 | NAPA ID:18811 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 018811 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S69 | NONE | To replace multiple poles and crossarms | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.004841 | 5.5 | 2017 | 2016-05-27 | B | 10 | 0.009682 | 3.0069e-05
1 | 10850193 | 2016-05-05 12:46 | 2016-05-05 16:30 | 223 | 375 | 670.5 | 0.0020168 | 0 | 9.0236e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP1385 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Notified Hub ETA required. 12.26pm advised Travis in control 12.40 notified Fire of ETA 12.55 Notified Hub ETA required. 12.26pm advised Travis in control 12.40 notified Fire of ETA 12.55 NOC rep - when signing this job off, please request cause - and confirm the brand of TX (If E-tel as their Core's can become unstable in transit) NOTE: this TX was replaced on 09/02/2016 by Downer under OMS 9569304 - NAPA ID 16208 * investigation as to the TX in question as they may be different* 2 generators are arriving on site 1.2MVA for coolstore & 500kVA for offices. Old transformer was 750kVA installed in 2006. Generators will be in over night as Downer staff tied up on Kinlieth Shutdowns. Fiona H please note for billing: Murray Lipinski advises the transformer failure may be related to loading issues, this aspect is still under investigation for final clarification. The site is being reviewed to install a 1 MVA replacement transformer to handle the loads. Powerco's Bev H has been advised of the issue as this may affect what party pays for what, i.e generation, transformer, other required repairs, labour etc. Therefore costs to Powerco may need to be re-aligned based on the outcomes from Murray and Bev. ASW. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-05-05 | C | 375 | 0 | 9.0236e-06
1 | 10850934 | 2016-05-05 13:26 | 2016-05-05 15:45 | 138 | 186 | 277.1 | 0.00083349 | 0 | 6.0157e-06 |  | 22 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 804868 | FUSE - ELEMENT/LINK (HV) | CB1133 Auto reclose A/R O/C E/F. Magpie found at TX Z31. x2 2amp HV fuses | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0 | 22 | 2017 | 2016-05-05 | C | 186 | 0 | 6.0157e-06
1 | 10851396 | 2016-05-20 08:30 | 2016-05-20 09:01 | 31 | 66 | 2046 | 0.0061528 | 0.005557 | 0.00019848 | NAPA ID:19449 TP_KAITIMAKO GXP > WELCOME BAY SUB > POIKE | 11 | Planned | 019449 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD4-435 | NONE | This is DNO 160411, Part 1 of 2 installing a new CFC and replacing 300m of 3 core 185 & 280m of 35mm to TD4-681. Part 2 of this job is to replace series 1 SDAF unit 435, 437,438 & 488 with CFCF (Separate switching). Due to cable fault this cable is already isolated & earthed and installing the new RMU will not require SADI but there will be small outage to swop over TD4-681 onto new CFC. Works location: Welcome Bay Rd. WO 30026288 | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.0027785 | 5.5 | 2017 | 2016-05-20 | B | 66 | 0.005557 | 0.00019848
1 | 10851901 | 2016-05-05 17:00 | 2016-05-05 19:48 | 167 | 1 | 167.7833 | 0.00050468 | 0.000495 | 3.0078e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7105 | FUSE - ELEMENT/LINK (HV) | Replaced 2x HV Fuses | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000495 | 11 | 2017 | 2016-05-05 | C | 1 | 0.000495 | 3.0078e-06
1 | 10852777 | 2016-05-05 21:33 | 2016-05-05 22:49 | 75 | 2475 | 100401.8167 | 0.302 | 0.27966 | 0.0074445 |  | 33 | Unplanned |  | ZONE SUB EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB3162 | UNKNOWN | PKO LHS bus breakers tripped CB's 3118, 3122, 3132, 3142, 3162 & 11kV CB19 ( BZ trip, C Ph O/C, E/F ) Loss of FRM, WLN & WAH T1. FRM back feed via PKO 3252 WAH T1 & WLN CB,s 1, 2 & 3 via BRN 3112 ( HIN GXP ) WLN CB4 via MIK5 PKO 33kV CB,s 3118, 3122, 3132, 3142, 3162 remove from service position & tagged only. Bus to be tested 6/5/16 for possible fault. Omicron test set Protection tech and fitters needed urgent to investigate fault at piako | S2 | PIAKO3162-KEREONE 33KV | WAIHOU | Valley | TP_WAIHOU | Eastern Electricity | POWERCO | 0.27966 | 33 | 2017 | 2016-05-05 | C | 2475 | 0.27966 | 0.0074445
1 | 10855455 | 2016-05-05 23:23 | 2016-05-06 00:21 | 57 | 1 | 57.5833 | 0.0001732 | 0.000164 | 3.0078e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 744131 | UNKNOWN | Faultman discussed with person reporting and stayed to observe pole pointed out and several either side with nothing untoward found | F3 | DOMETT ST | HUIRANGI | Taranaki | WAITARA WEST SUB | Western Electricity | POWERCO | 0.000164 | 11 | 2017 | 2016-05-05 | C | 1 | 0.000164 | 3.0078e-06
1 | 10857696 | 2016-05-20 08:48 | 2016-05-20 14:11 | 323 | 5 | 1615 | 0.0048567 | 0.004811 | 1.5036e-05 | NAPA ID:19407 TP_KINLEITH GXP > MARAETAI ROAD SUB > OLD CAMBRIDGE RD | 11 | Planned | 019407 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 263161 | NONE | Change crossarms. Works location: Whakamaru Rd. WO 30014399 | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.0024055 | 5.5 | 2017 | 2016-05-20 | B | 5 | 0.004811 | 1.5036e-05
1 | 10858200 | 2016-05-06 09:41 | 2016-05-06 12:31 | 169 | 541 | 62217 | 0.18714 | 0.18226 | 0.0016272 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | IP518 | JUMPER | 9.49am called Jo at svs hub & advised to send FM to transformer TC635 as per notes, not to send FM to address. Repaired Blown Jumper at ABS IP518. Back feed applied from 9790 (break before make less than 1 minute) also applied from 9718. 2r line patrol from start / 2r repair 1207. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.18226 | 11 | 2017 | 2016-05-06 | C | 541 | 0.18226 | 0.0016272
1 | 10858642 | 2016-05-06 13:07 | 2016-05-06 13:35 | 28 | 4 | 112 | 0.00033688 | 0.0003 | 1.2031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6268 | FUSE - ELEMENT/LINK (HV) | Reports of a broken DDO at Transformer received. Faultman found broken DDO Fuse and replaced 1 x 3amp Fuse. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.0003 | 11 | 2017 | 2016-05-06 | C | 4 | 0.0003 | 1.2031e-05
1 | 10859064 | 2016-05-06 11:26 | 2016-05-06 12:48 | 81 | 422 | 16195.9833 | 0.048715 | 0.044907 | 0.0012693 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2742 | UNKNOWN | CB 2742 Trip O/C. Line patrolled with no cause located. 2r line patrol 1245. No repair. | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.044907 | 33 | 2017 | 2016-05-06 | C | 422 | 0.044907 | 0.0012693
1 | 10862796 | 2016-05-06 19:10 | 2016-05-06 20:46 | 96 | 65 | 2377.0833 | 0.0071499 | 0.006563 | 7.5196e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | B0899 | POLE | Check for safety. Excavator has hit a pole and now there are cracks in it. Pole replaced. Isolation at ABS 930, 1110 & 1376. Had to break before make to create back feed from PUT CB 4 due to Baird Rd sub on T5 at Kinleith. 2r repair 1915. | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.006563 | 11 | 2017 | 2016-05-06 | C | 65 | 0.006563 | 7.5196e-05
1 | 10867586 | 2016-05-06 16:54 | 2016-05-06 18:12 | 78 | 6842 | 323998.1667 | 0.97454 | 0.9128 | 0.02058 |  | 33 | Unplanned |  | ZONE SUB EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 2212 A/W | CIRCUIT BREAKER (HV) | At Kinleith GXP, 33kV CB 2241 Tripped, O/C Neutral Time. Loss of Supply occured to Baird Rd Sub and also Maraetai Sub. This tripping occured during planned switching under NAPA 18940. Switching was for planned maintenance on Transpower Kinleith GXP 33kV CB 2242, as part of the planned Kinleith Shutdown Maintenance. Part of this planned switching was to close 33kV ABS PC43 at Kinleith Injection Plant so CB 2242 could be opened for maintenance. Maintenance was completed on CB 2242, and Transpower advised NOC that CB 2242 was ready for service. CB 2242 was closed on NOC's request to transpower - transpower advised that it had closed. Instruction was then given to field switching operator to Open ABS PC43. On opening this ABS, A flashover occured and supply was lost to Baird Rd & Maraetai Rd Subs. CB 2242 still indicated closed. NOC requested transpower to confirm status of CB 2242. It was found that CB 2242 had been closed without it being fully in the service position, thus, was not actually closed into circuit. This meant that all of Maraetai Sub load was broken with ABS PC43 when it was opened. Staff welfare checks carried out by NOC and other Downer staff. Equipment checked - All OK. New switching operator arrived to carry out required restoration switching. All Power Restored to Baird Rd at 17:13. All Power Restored to Maraetai Rd at 18:12. Safety Manager Report is still to be completed for this incident. | S4 | KINLEITH2242-MARAETAI 33KV | KINLEITH 33 | Valley | TP_KINLEITH | Eastern Electricity | POWERCO | 0.9128 | 33 | 2017 | 2016-05-06 | C | 6842 | 0.9128 | 0.02058
1 | 10873310 | 2016-05-06 19:48 | 2016-05-06 21:06 | 77 | 89 | 6875.25 | 0.02068 | 0.019876 | 0.0002677 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 214043 | NONE | Palm tree in the lines and lines are arcing. 2R to cut tree, needing bucket and switching as working on the HV. Isolated at CB 8 Sw/Gear 9565/3 & ABS IP455. Tree trimmed clear of lines. Pole 214043. 2r line patrol / 2r repair 2020. | F3 | TUI ST | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 0.019876 | 11 | 2017 | 2016-05-06 | C | 89 | 0.019876 | 0.0002677
1 | 10874234 | 2016-05-07 10:49 | 2016-05-07 13:05 | 135 | 422 | 16476.45 | 0.049558 | 0.04575 | 0.0012723 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | UNKNOWN | CB 2742 Trip, O/C. Simultaneously with Motukawa CB H11 & H21. Caused total outage to Motukawa Substation. Backfeed to Motukawa Sub installed via ABS 253. 33kV Line sectionalised with no fault found. Suspect Bird Strike. Feeder & Motukawa Sub restored to normal configuration. 2r line patrol 1127. No 2r repair. | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.04575 | 33 | 2017 | 2016-05-07 | C | 422 | 0.04575 | 0.0012723
1 | 10876200 | 2016-05-07 17:42 | 2016-05-07 20:12 | 149 | 234 | 19701.6333 | 0.059259 | 0.057147 | 0.0014077 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C1798 | CONDUCTOR - REPAIR/REHANG | Found line down beyond ABS IC610, isolated at ABS IC 610, repaired line & relivened. Materials Used: 5m of wire, 3 crimp sleeves. 2r line patrol 1911 / 2r repair 1923. | F4 | THOMAS ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.057147 | 11 | 2017 | 2016-05-07 | C | 234 | 0.057147 | 0.0014077
1 | 10877403 | 2016-05-08 01:43 | 2016-05-08 01:49 | 5 | 205 | 1165.0833 | 0.0035043 | 0.001654 | 0.00061659 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Transpower switching recloser 9198 L/O, reclosed | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.001654 | 11 | 2017 | 2016-05-08 | C | 205 | 0.001654 | 0.00061659
1 | 10877639 | 2016-05-08 07:35 | 2016-05-08 08:30 | 54 | 1 | 54.6667 | 0.00016442 | 0.000155 | 3.0077e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4641 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 8Amp HV Fuse Links | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.000155 | 11 | 2017 | 2016-05-08 | C | 1 | 0.000155 | 3.0077e-06
1 | 10877786 | 2016-05-08 11:35 | 2016-05-08 13:13 | 98 | 599 | 52689.5 | 0.15848 | 0.15307 | 0.0018016 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | IC2095 | SWITCH (HV) | CB 1 Trip. E/F. O/C. L/O. Sw/gear IC2095 Faulty. To be worked on Monday 9th. Back feeds via Sw/gear IC1890 and IC1438. DNO 160508. 2r line patrol 1247 no repair | F3 | TAINUI ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.15307 | 11 | 2017 | 2016-05-08 | C | 599 | 0.15307 | 0.0018016
1 | 10879085 | 2016-05-08 20:12 | 2016-05-08 23:00 | 168 | 45 | 7560 | 0.022739 | 0.022332 | 0.00013535 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VANDALISM | 716099 | POLE | Car hit pole 716099, fatal accident please check structural security of pole. Event number F2073407 Pole checked and requires replacement. As it is the scene of a fatal accident police are not allowing Downer onto site until after approx 6pm to commence pole replacement. Materials Used: 2 X 10m Poles, 2 X Cross arms, 6 X H/T Insulators and Blocks etc. Had to get Crane truck in to lift pole as it was a double Pole. NDR N100146. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.022332 | 11 | 2017 | 2016-05-08 | C | 45 | 0.022332 | 0.00013535
1 | 10879759 | 2016-05-08 21:00 | 2016-05-08 22:04 | 64 | 61 | 3927.3833 | 0.011813 | 0.011262 | 0.00018347 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C641 | UNKNOWN | CB C641 found open after reports of no power. Maybe Bird strike but not sure. No 2R | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.011262 | 11 | 2017 | 2016-05-08 | C | 61 | 0.011262 | 0.00018347
1 | 10880353 | 2016-05-25 09:09 | 2016-05-25 16:20 | 431 | 38 | 16378 | 0.049249 | 0.048905 | 0.00011427 | NAPA ID:18621 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018621 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 209866 | NONE | Replace poles ,hardware and conductor between 11kv switches TEMP32 & TEMP33 & 9302/3. Minden Road, Bethlehem. W/O 30002520. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.024452 | 5.5 | 2017 | 2016-05-25 | B | 38 | 0.048905 | 0.00011427
1 | 10880461 | 2016-05-09 08:48 | 2016-05-09 11:25 | 157 | 78 | 8359.1 | 0.025142 | 0.024438 | 0.0002346 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | C281 | UNKNOWN | Recloser C281 Trip flag Ph B OC & OC 1. 1R - Requested line patrol. Line was patrolled and sectionalised and no fault was found, faultman suspect duck strike as is hunting season and lots of ducks flying around. 2r line patrol 1003. No repair. | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.024438 | 11 | 2017 | 2016-05-09 | C | 78 | 0.024438 | 0.0002346
1 | 10881012 | 2016-05-27 09:05 | 2016-05-27 14:53 | 348 | 15 | 5220 | 0.015696 | 0.01556 | 4.5103e-05 | NAPA ID:18635 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018635 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 209866 | NONE | Replace poles ,hardware and conductor between TEMP32 & TEMP33. Install Temporary ABS TEMP 34 on pole 213082. Minden Road, Bethlehem. W/O 30002520. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.00778 | 5.5 | 2017 | 2016-05-27 | B | 15 | 0.01556 | 4.5103e-05
1 | 10881026 | 2016-05-26 09:15 | 2016-05-26 12:45 | 210 | 15 | 3150 | 0.0094719 | 0.009336 | 4.5104e-05 | NAPA ID:18729 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | 018729 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4789 | NONE | Install Recloser 9929/2 into SWER line. Change Fuse FC2434 for Link 9929/6. Port Jackson Road, Port Jackson, Colville. W/O 10148359. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.004668 | 5.5 | 2017 | 2016-05-26 | B | 15 | 0.009336 | 4.5104e-05
1 | 10881137 | 2016-05-20 09:15 | 2016-05-20 15:16 | 360 | 46 | 16599.1 | 0.049917 | 0.049502 | 0.00013833 | NAPA ID:20561 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 020561 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S69 | POLE | 11kV pole and hardware replacements. Works Location: Opaki Kaiparoro Road, Masterton. Work Order 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.024751 | 5.5 | 2017 | 2016-05-20 | B | 46 | 0.049502 | 0.00013833
1 | 10881462 | 2016-05-24 09:40 | 2016-05-24 14:10 | 270 | 202 | 54540 | 0.164 | 0.16218 | 0.00060742 | NAPA ID:16162 TP_LINTON GXP > KAIRANGA SUB > TAKARO | 11 | Planned | 016162 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/174 | NONE | Connecting new 11KV cable between T6/174 and T6/176. and making cable redundant between T6/174 and A33, and, T6/176 and A34 | F3 | TAKARO | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.081091 | 5.5 | 2017 | 2016-05-24 | B | 202 | 0.16218 | 0.00060742
1 | 10881486 | 2016-05-31 09:18 | 2016-05-31 14:58 | 340 | 25 | 8500 | 0.025557 | 0.025331 | 7.5168e-05 | NAPA ID:18653 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018653 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp 34 | NONE | Replace poles ,hardware and conductor between TEMP34 & TEMP's 35-36. Minden Road. Bethlehem. W/O 30002520. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.012665 | 5.5 | 2017 | 2016-05-31 | B | 25 | 0.025331 | 7.5168e-05
1 | 10881492 | 2016-05-24 10:00 | 2016-05-24 11:00 | 60 | 10 | 125 | 0.00037588 | 0.000285 | 3.007e-05 | NAPA ID:19447 TP_BUNNYTHORPE GXP > SANSON SUB > OROUA DOWNS | 11 | Planned | 019447 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/514 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Correct voltages at 3 TXs on Puke Puke Rd | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.0001425 | 5.5 | 2017 | 2016-05-24 | B | 10 | 0.000285 | 3.007e-05
1 | 10881545 | 2016-05-09 11:04 | 2016-05-09 12:24 | 80 | 1491 | 64780.4 | 0.19484 | 0.18139 | 0.0044845 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C838 | UNKNOWN | CB C838 tripped on O/C flags, line was patrolled and sectionalised and no fault was found. 2r line patrol 1130 - no repair. | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.18139 | 11 | 2017 | 2016-05-09 | C | 1491 | 0.18139 | 0.0044845
1 | 10884023 | 2016-05-10 09:20 | 2016-05-10 16:18 | 418 | 8 | 3344 | 0.010058 | 0.009985 | 2.4061e-05 | NAPA ID:20582 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > REID RD | 11 | Planned | 020582 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 220013 | NONE | Replace poles, hardware and conductor. Works Location: Welcome Bay Road and Waitao Road. Works Order 30017823 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.0049925 | 5.5 | 2017 | 2016-05-10 | B | 8 | 0.009985 | 2.4061e-05
1 | 10884363 | 2016-05-09 12:53 | 2016-05-09 14:43 | 110 | 1 | 110.0167 | 0.0003309 | 0.000321 | 3.0077e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7105 | FUSE - ELEMENT/LINK (HV) | Reload Reliven at 7105. Used 2 x 10 A Fuse. Cause: Bird strike. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000321 | 11 | 2017 | 2016-05-09 | C | 1 | 0.000321 | 3.0077e-06
1 | 10884948 | 2016-05-23 06:16 | 2016-05-23 16:24 | 608 | 217 | 3584.1167 | 0.010778 | 0.00882 | 0.0013051 | NAPA ID:16939 TP_WAIKINO GXP > WHANGAMATA SUB > ACHILLES AVE | 11 | Planned | 016939 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB 9 | NONE | The access portion of the works is to replace LV and 11kV cross arms at Pole #'s R0003, R12594 and replace 11kV connections at Pole # 861242. Works location: Achilles Ave, Wanganui. WO 30003265 | F3 | ACHILLES AVE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.00441 | 5.5 | 2017 | 2016-05-23 | B | 217 | 0.00882 | 0.0013051
1 | 10886022 | 2016-05-10 07:27 | 2016-05-10 08:47 | 80 | 3 | 240.8 | 0.00072425 | 0.000697 | 9.023e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI748 | FUSE - ELEMENT/LINK (HV) | 2 x3amp cause bird strike LI748 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000697 | 11 | 2017 | 2016-05-10 | C | 3 | 0.000697 | 9.023e-06
1 | 10887243 | 2016-05-10 10:43 | 2016-05-10 16:11 | 328 | 422 | 27246.7 | 0.081949 | 0.078141 | 0.0012692 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2742 | UNKNOWN | 10:43 SFD GXP CB 2742 Trip Flag E/F. Supply lost initially to Motukawa. Restored at 11:48 via Motukawa bus from CB 1342 Huirangi. Decision to Fly the Lines. 13:54 Kane Reported Helicopter in Hawera. Himself and Jared are to Fly the 33kV Line out of Motukawa. 14:25 - Wes reported line patrolled from Motukawa end as much as can be seen from road. Nothing found. Helicopter line patrol completed. No fault found. CB 2742 reclosed successfully. Network restored to normal. 2r line patrol 1147 no repair. | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.078141 | 33 | 2017 | 2016-05-10 | C | 422 | 0.078141 | 0.0012692
1 | 10903330 | 2016-05-10 14:34 | 2016-05-10 15:10 | 35 | 1 | 35.9833 | 0.00010823 | 9.9e-05 | 3.0076e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | T7/596 | FUSE - ELEMENT/LINK (HV) | Reload Reliven 2 x 3 A Fuse. Cause: Bird strike. | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 9.9e-05 | 11 | 2017 | 2016-05-10 | C | 1 | 9.9e-05 | 3.0076e-06
1 | 10904398 | 2016-05-11 02:43 | 2016-05-11 03:58 | 75 | 421 | 23076.5667 | 0.069406 | 0.065607 | 0.0012662 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | S113 | UNKNOWN | RS S113 A/R, L/O, O/C, B Phase. Sectionalised & Patrolled. No fault found. 2r line patrol 0324 | F2/F3 | SOUTH RD CHAPEL | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.065607 | 11 | 2017 | 2016-05-11 | C | 421 | 0.065607 | 0.0012662
1 | 10905081 | 2016-05-11 08:10 | 2016-05-11 09:14 | 64 | 1 | 64.25 | 0.00019324 | 0.000184 | 3.0076e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | l76 | JUMPER | Blown jumper at fuses l76 2 repaired Isolated at l76 outage on linked job. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000184 | 11 | 2017 | 2016-05-11 | C | 1 | 0.000184 | 3.0076e-06
1 | 10905116 | 2016-05-11 06:49 | 2016-05-11 08:31 | 102 | 3 | 307.5 | 0.00092485 | 0.000897 | 9.0229e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD5-168 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp fuses. Bird Strike. Full power restored no other assets replaced; adjacent assets were checked and confirmed as being ok. | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.000897 | 11 | 2017 | 2016-05-11 | C | 3 | 0.000897 | 9.0229e-06
1 | 10905191 | 2016-05-11 07:21 | 2016-05-11 09:21 | 119 | 1 | 119.2333 | 0.00035861 | 0.000349 | 3.0076e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 748640 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 15a HV fuses @ 8146 Caused by bird strike @ pole 748640 | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.000349 | 11 | 2017 | 2016-05-11 | C | 1 | 0.000349 | 3.0076e-06
1 | 10905227 | 2016-05-24 08:20 | 2016-05-24 16:32 | 492 | 173 | 9169 | 0.027572 | 0.02601 | 0.0010404 | NAPA ID:19452 TP_KAITIMAKO GXP > WELCOME BAY SUB > POIKE | 11 | Planned | 019452 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV TD4-680 | NONE | Replace Series 1 Anderlect unit with CFCF Part 2 0f 2 other outage Napa19449. Works location: Welcome Bay Rd. WO 30026288 | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.013005 | 5.5 | 2017 | 2016-05-24 | B | 173 | 0.02601 | 0.0010404
1 | 10905233 | 2016-05-11 07:38 | 2016-05-11 09:15 | 97 | 1 | 97 | 0.00029174 | 0.000282 | 3.0076e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | FP186 | FUSE - ELEMENT/LINK (HV) | Universal underground truck has hit lines, lines are still up but there was a big bang and everyone near this address has no power 7.38am advised Jo at svs hub & emailed. Truck hit lines, isolated at fuses FP186. NDR: 44159. 3 x 10amp fuses. No outage at this address, outage at linked job. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.000282 | 11 | 2017 | 2016-05-11 | C | 1 | 0.000282 | 3.0076e-06
1 | 10908813 | 2016-05-12 10:02 | 2016-05-12 11:00 | 58 | 26 | 1508.4333 | 0.0045368 | 0.004302 | 7.8197e-05 | NAPA ID:20696 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | 020696 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9561/2 | NONE | Replace broken 11kV strain insulator 16mm Cu | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.002151 | 5.5 | 2017 | 2016-05-12 | B | 26 | 0.004302 | 7.8197e-05
1 | 10908933 | 2016-05-11 12:00 | 2016-05-11 12:04 | 4 | 116 | 464 | 0.0013955 | 0.000348 | 0.00034889 |  | 11 | Unplanned |  | UNDERGROUND CABLE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | Sw/Gear 4646/4 | NONE | Refer to NAPA 18590. Planned switching carried out to Relace Sw/Gear 4155. When the back feed was being removed (Item 22 - Open Sw/Gear 4646/4) a loss of supply was noticed by the faultman (B.Wilson). Sw/gear closed again and power restored. (4 minute loss). It appears that Sw/Gear Status had changed after switching written and not picked up at NOC. | F2 | GUYTON | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 0.000348 | 11 | 2017 | 2016-05-11 | C | 116 | 0.000348 | 0.00034889
1 | 10909157 | 2016-06-02 09:00 | 2016-06-02 14:14 | 314 | 24 | 7536 | 0.022658 | 0.022441 | 7.2159e-05 | NAPA ID:18130 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 018130 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 704479 | NONE | Replace various arms and poles within work area. Works location: South Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.01122 | 5.5 | 2017 | 2016-06-02 | B | 24 | 0.022441 | 7.2159e-05
1 | 10909160 | 2016-06-07 09:30 | 2016-06-07 14:40 | 310 | 24 | 7440 | 0.022368 | 0.022151 | 7.2154e-05 | NAPA ID:18134 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 018134 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 704479 | NONE | Replace various arms and poles within work area. Works location: South Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.011076 | 5.5 | 2017 | 2016-06-07 | B | 24 | 0.022151 | 7.2154e-05
1 | 10909173 | 2016-06-09 09:15 | 2016-06-09 14:08 | 293 | 11 | 3223 | 0.0096894 | 0.00959 | 3.3069e-05 | NAPA ID:18128 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 018128 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6415 | NONE | Replace various arms and poles within work area. Works location; Mirikau Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.004795 | 5.5 | 2017 | 2016-06-09 | B | 11 | 0.00959 | 3.3069e-05
1 | 10909202 | 2016-06-14 09:00 | 2016-06-14 15:35 | 395 | 49 | 19355 | 0.058183 | 0.057741 | 0.0001473 | NAPA ID:18105 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 018105 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6402 | NONE | Replace various arms and poles within work area. Works location: South Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.028871 | 5.5 | 2017 | 2016-06-14 | B | 49 | 0.057741 | 0.0001473
1 | 10909213 | 2016-06-16 09:15 | 2016-06-16 14:24 | 309 | 24 | 7416 | 0.022293 | 0.022076 | 7.2144e-05 | NAPA ID:18121 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 018121 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 704479 | NONE | Replace various arms and poles within work area. Works location: South Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.011038 | 5.5 | 2017 | 2016-06-16 | B | 24 | 0.022076 | 7.2144e-05
1 | 10910046 | 2016-06-21 09:16 | 2016-06-21 14:59 | 343 | 118 | 39910 | 0.11996 | 0.1189 | 0.00035468 | NAPA ID:18137 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 018137 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 704518 | NONE | Reconductor between abs 6392 and pole 704518. Remove line break at pole 704479. Works location: South Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.059449 | 5.5 | 2017 | 2016-06-21 | B | 118 | 0.1189 | 0.00035468
1 | 10910070 | 2016-06-02 08:45 | 2016-06-02 13:26 | 281 | 8 | 2248 | 0.0067589 | 0.006686 | 2.4053e-05 | NAPA ID:17867 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 017867 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6297 | NONE | Pole & wire replacement as per IR 8370 Paora Road reconstruction. Works location: Paora Rd, WO 30018540 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.003343 | 5.5 | 2017 | 2016-06-02 | B | 8 | 0.006686 | 2.4053e-05
1 | 10919907 | 2016-05-11 17:23 | 2016-05-11 22:30 | 307 | 322 | 98854 | 0.29732 | 0.29441 | 0.00096846 |  | 6.6 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 707718 | POLE | Fire comms advising car vs pole, F2075425 ETA required 04 801 0812. svs hub advise 25mins, Fire comms advised. Faultman isolated line at ABS 4851 and Sw/Gear 12105/3 to replace pole 707718 hit by car. 1 X pole & all hardware ndr N100147 | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.29441 | 6.6 | 2017 | 2016-05-11 | C | 322 | 0.29441 | 0.00096846
1 | 10920606 | 2016-05-11 18:42 | 2016-05-11 19:47 | 65 | 3 | 196.25 | 0.00059025 | 0.000563 | 9.0229e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7997 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 7997, section of line crosses a lake full of ducks, suspect a duck strike. 2 X 10 amp hv fuses replaced | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.000563 | 11 | 2017 | 2016-05-11 | C | 3 | 0.000563 | 9.0229e-06
1 | 10921116 | 2016-05-12 03:08 | 2016-05-12 06:20 | 191 | 6 | 1151.5 | 0.0034632 | 0.003409 | 1.8045e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 4612 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuse at Fuses 4612. 2 X 10 amp hv fuses replaced | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.003409 | 11 | 2017 | 2016-05-12 | C | 6 | 0.003409 | 1.8045e-05
1 | 10921344 | 2016-05-12 07:50 | 2016-05-12 11:19 | 208 | 230 | 18374.8 | 0.055264 | 0.053188 | 0.00082408 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 818645 | POLE | 0802 Fire Service advsie they have arrived and pole down, advised ONC. Replace 1 pole 2 x cross arms and 100m of conductor at this stage. branch fell over onto lines at pole 818645 isolated at Swgear11020/3 no backfeed | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.053188 | 11 | 2017 | 2016-05-12 | C | 230 | 0.053188 | 0.00082408
1 | 10921577 | 2016-06-01 09:50 | 2016-06-01 10:55 | 65 | 4 | 260 | 0.00078173 | 0.000745 | 1.2027e-05 | NAPA ID:18701 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018701 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1233 | NONE | To install a 400V fuse disconnector. Works location: Mawbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0003725 | 5.5 | 2017 | 2016-06-01 | B | 4 | 0.000745 | 1.2027e-05
1 | 10922037 | 2016-06-01 11:30 | 2016-06-01 12:15 | 45 | 3 | 135 | 0.0004059 | 0.000378 | 9.02e-06 | NAPA ID:18707 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018707 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4971 | NONE | To install a 400V Fuse Disconnector. Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000189 | 5.5 | 2017 | 2016-06-01 | B | 3 | 0.000378 | 9.02e-06
1 | 10922072 | 2016-06-01 13:45 | 2016-06-01 14:30 | 45 | 2 | 90 | 0.0002706 | 0.000252 | 6.0133e-06 | NAPA ID:18711 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018711 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP1733 | NONE | To install a 400V Fuse Disconnector. Works location: Maiseys Rd. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000126 | 5.5 | 2017 | 2016-06-01 | B | 2 | 0.000252 | 6.0133e-06
1 | 10922090 | 2016-06-03 10:00 | 2016-06-03 11:00 | 60 | 7 | 420 | 0.0012628 | 0.001199 | 2.1046e-05 | NAPA ID:18945 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018945 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC378 | NONE | To install a 400V Fuse Disconnector. Works location: Maiseys Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0005995 | 5.5 | 2017 | 2016-06-03 | B | 7 | 0.001199 | 2.1046e-05
1 | 10922155 | 2016-06-03 11:40 | 2016-06-03 12:30 | 50 | 3 | 150 | 0.00045099 | 0.000423 | 9.0197e-06 | NAPA ID:18953 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018953 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1568 | NONE | To install a 400V Fuse Disconnector. Works location: Maiseys Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0002115 | 5.5 | 2017 | 2016-06-03 | B | 3 | 0.000423 | 9.0197e-06
1 | 10922667 | 2016-06-03 13:30 | 2016-06-03 14:15 | 45 | 3 | 135 | 0.00040589 | 0.000378 | 9.0197e-06 | NAPA ID:18955 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018955 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1028 | NONE | To install a 400V Fuse Disconnector. Works location: Harding Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000189 | 5.5 | 2017 | 2016-06-03 | B | 3 | 0.000378 | 9.0197e-06
1 | 10922683 | 2016-06-07 09:30 | 2016-06-07 10:30 | 60 | 3 | 180 | 0.00054115 | 0.000514 | 9.0192e-06 | NAPA ID:18958 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018958 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2073 | NONE | To install a 400V Fuse Disconnector. Works location: Maiseys Rd, Waharoa. WO 30019182 | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000257 | 5.5 | 2017 | 2016-06-07 | B | 3 | 0.000514 | 9.0192e-06
1 | 10922706 | 2016-06-01 09:00 | 2016-06-01 16:13 | 433 | 82 | 35506 | 0.10675 | 0.10601 | 0.00024655 | NAPA ID:18161 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11 | Planned | 018161 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS D73 | NONE | 33kV Crossarm replacement for BPE-MIL line from Z35 to Z36. 11kV crossarms and 400V underneath 33kV also needed to be replaced. Line is between P39685 - P39691. Works location: Palmerston North. WO 30019577 | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.053007 | 5.5 | 2017 | 2016-06-01 | B | 82 | 0.10601 | 0.00024655
1 | 10922722 | 2016-06-07 11:30 | 2016-06-07 12:00 | 30 | 4 | 120 | 0.00036077 | 0.000324 | 1.2026e-05 | NAPA ID:18959 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018959 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1667 | NONE | To install a 400V Fuse Disconnector. Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000162 | 5.5 | 2017 | 2016-06-07 | B | 4 | 0.000324 | 1.2026e-05
1 | 10922737 | 2016-05-12 08:52 | 2016-05-12 09:19 | 27 | 1491 | 40778.85 | 0.12265 | 0.10919 | 0.0044843 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 821348 | CONDUCTOR - REPAIR/REHANG | CB 838 trip o/c. Line patrolled, found tree branch at pole 821348. Removed by hotstick. 2R line patrol NA 2R repair NA | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.10919 | 11 | 2017 | 2016-05-12 | C | 1491 | 0.10919 | 0.0044843
1 | 10924243 | 2016-06-07 13:30 | 2016-06-07 14:30 | 60 | 9 | 540 | 0.0016235 | 0.001542 | 2.7058e-05 | NAPA ID:18960 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018960 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC8039 | NONE | To install a 400V Fuse Disconnector. Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000771 | 5.5 | 2017 | 2016-06-07 | B | 9 | 0.001542 | 2.7058e-05
1 | 10925454 | 2016-06-08 09:10 | 2016-06-08 10:15 | 65 | 3 | 195 | 0.00058624 | 0.000559 | 9.0191e-06 | NAPA ID:18992 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018992 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2263 | NONE | To install a 400V Fuse Disconnector. Works location: Maiseys Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0002795 | 5.5 | 2017 | 2016-06-08 | B | 3 | 0.000559 | 9.0191e-06
1 | 10925791 | 2016-05-12 10:12 | 2016-05-12 11:45 | 93 | 1 | 93 | 0.00027971 | 0.00027 | 3.0075e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5870 | INSULATOR | Advised SMC. 10.05 FM requested 2R to replace 1 x insulator and requires a bucket truck. Bucket Truck is not 2R work and advised Reece to contact hub to organise. actually isolated at fuses 5870 but no ICP on tx 2016 as only a pump shed | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.00027 | 11 | 2017 | 2016-05-12 | C | 1 | 0.00027 | 3.0075e-06
1 | 10926141 | 2016-05-12 15:20 | 2016-05-12 16:20 | 60 | 6 | 360 | 0.0010827 | 0.001028 | 1.8045e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T800 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer faulty, needs replacing. Replaced / relivened OK by Frank Martin. | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.001028 | 11 | 2017 | 2016-05-12 | C | 6 | 0.001028 | 1.8045e-05
1 | 10926163 | 2016-05-12 09:42 | 2016-05-12 10:58 | 75 | 304 | 23022.9333 | 0.069244 | 0.0665 | 0.00091431 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | XT40 | UNKNOWN | Tripping on 33kV CB XT40 causing loss of supply to Alfredton. (CB XT40 had HLT applied at time due to Tree Contractors, contractors stood down). Area patrolled and supply restored OK from Parkville. Patrol from Alfredton to Pongaroa may be carried out by hellicopter. Unable to supply from Pongaroa as ABS XT51 is open and has DNO applied. | S3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.0665 | 33 | 2017 | 2016-05-12 | C | 304 | 0.0665 | 0.00091431
1 | 10926475 | 2016-05-12 09:00 | 2016-05-12 15:55 | 415 | 7 | 2905 | 0.0087371 | 0.008673 | 2.1053e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 818722 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Fuses 7215 found tripped after reports of lines down. Suspect line hanging low (extreme winds) and hit by truck which dragged down line and broke conductor and transformer structure. Repairs included replacing transformer T3367 and structure along with 1 cross arm with another 2 repaired. Relivened OK. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.008673 | 11 | 2017 | 2016-05-12 | C | 7 | 0.008673 | 2.1053e-05
1 | 10926525 | 2016-06-08 11:50 | 2016-06-08 12:45 | 55 | 5 | 275 | 0.00082675 | 0.000781 | 1.5032e-05 | NAPA ID:18993 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018993 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC669 | NONE | To install a 400V Fuse Disconnector. Works location: Harding Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0003905 | 5.5 | 2017 | 2016-06-08 | B | 5 | 0.000781 | 1.5032e-05
1 | 10927001 | 2016-06-08 13:40 | 2016-06-08 15:00 | 80 | 4 | 320 | 0.00096204 | 0.000925 | 1.2025e-05 | NAPA ID:18994 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018994 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2339 | NONE | To install a 400V Fuse Disconnector. Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0004625 | 5.5 | 2017 | 2016-06-08 | B | 4 | 0.000925 | 1.2025e-05
1 | 10927110 | 2016-06-01 09:50 | 2016-06-01 16:08 | 378 | 6 | 2268 | 0.0068191 | 0.006765 | 1.804e-05 | NAPA ID:18191 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | 018191 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P20254 | NONE | Replace H pole P20254 with L50 on it with new poles and ABS and xarms between temp fuses. Works location: Kawakawa Rd. WO 10157896 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.0033825 | 5.5 | 2017 | 2016-06-01 | B | 6 | 0.006765 | 1.804e-05
1 | 10927299 | 2016-06-09 09:45 | 2016-06-09 10:10 | 25 | 9 | 225 | 0.00067642 | 0.000595 | 2.7057e-05 | NAPA ID:18998 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018998 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2039 | NONE | To install a 400V Fuse Disconnector. Works location: Waharoa East Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0002975 | 5.5 | 2017 | 2016-06-09 | B | 9 | 0.000595 | 2.7057e-05
1 | 10927326 | 2016-06-09 11:30 | 2016-06-09 11:50 | 20 | 8 | 160 | 0.00048101 | 0.000408 | 2.4051e-05 | NAPA ID:18999 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 018999 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2038 | NONE | To install a 400V Fuse Disconnector. Works location: Waharoa East Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000204 | 5.5 | 2017 | 2016-06-09 | B | 8 | 0.000408 | 2.4051e-05
1 | 10927342 | 2016-06-09 13:30 | 2016-06-09 14:00 | 30 | 12 | 360 | 0.0010823 | 0.000974 | 3.6076e-05 | NAPA ID:19000 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 019000 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2324 | NONE | To install a 400V Fuse Disconnector. Work location: Waharoa East Rd, Matamata. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000487 | 5.5 | 2017 | 2016-06-09 | B | 12 | 0.000974 | 3.6076e-05
1 | 10927401 | 2016-06-07 09:25 | 2016-06-07 14:41 | 316 | 6 | 1896 | 0.0057001 | 0.005646 | 1.8038e-05 | NAPA ID:18194 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | 018194 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P20254 | NONE | Replace H pole P20254 with L50 on it with new poles and ABS and xarms between temp fuses. Works location: Kawakawa Rd. WO 10157896 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.002823 | 5.5 | 2017 | 2016-06-07 | B | 6 | 0.005646 | 1.8038e-05
1 | 10934256 | 2016-06-10 09:10 | 2016-06-10 12:26 | 195 | 2 | 391.8 | 0.0011779 | 0.001159 | 6.0125e-06 | NAPA ID:20563 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 020563 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP580 | NONE | To replace 11kV arms & Install 400V Fuse Disconnector. Works location: Piakoiti Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0005795 | 5.5 | 2017 | 2016-06-10 | B | 2 | 0.001159 | 6.0125e-06
1 | 10934477 | 2016-06-14 14:23 | 2016-06-14 15:20 | 57 | 3 | 171 | 0.00051404 | 0.000486 | 9.0183e-06 | NAPA ID:20565 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 020565 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2317 | NONE | To install a 400V Fuse Disconnector. Works location: Hutchinson Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000243 | 5.5 | 2017 | 2016-06-14 | B | 3 | 0.000486 | 9.0183e-06
1 | 10934701 | 2016-05-12 16:15 | 2016-05-12 17:23 | 68 | 43 | 2924 | 0.0087942 | 0.008406 | 0.00012933 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 739254 | CROSSARM - ARM ONLY | *RED DEFECT* Rotten crossarm and strain disc floating 11kv single phase line. Will require shutdown - HV - transferred to Control. Replace 1 x cross arm, 2 x I bolts | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.008406 | 11 | 2017 | 2016-05-12 | C | 43 | 0.008406 | 0.00012933
1 | 10934789 | 2016-06-01 08:59 | 2016-06-01 09:41 | 42 | 98 | 1134 | 0.0034096 | 0.002525 | 0.00029465 | NAPA ID:20646 TP_KINLEITH GXP > MARAETAI ROAD SUB > ARAWA ST | 11 | Planned | 020646 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw 13072 | NONE | Isolate remote end of switches 13072/1,2 & 3 One at a time to allow both local & remote operation for SCADA commissioning. Works location: Tainui St, Tokoroa. WO 30002496 | F3 | ARAWA ST | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.0012625 | 5.5 | 2017 | 2016-06-01 | B | 98 | 0.002525 | 0.00029465
1 | 10934801 | 2016-05-12 11:23 | 2016-05-12 14:54 | 211 | 296 | 26903 | 0.080913 | 0.078242 | 0.00089025 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 360625 | CONDUCTOR - REPAIR/REHANG | CB C945 Trip found span wrapped into a tree at pole 360625 isolated at 1342 no backfeed. 2r line patrol 1256 no repair removed by hotstick | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.078242 | 11 | 2017 | 2016-05-12 | C | 296 | 0.078242 | 0.00089025
1 | 10935757 | 2016-06-03 09:15 | 2016-06-03 12:15 | 180 | 10 | 1800 | 0.0054118 | 0.005321 | 3.0066e-05 | NAPA ID:17783 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 017783 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7742 | NONE | Transformer structure and hardware needs replacing. Works location: Hwy 2, Masterton. WO 30019523 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0026605 | 5.5 | 2017 | 2016-06-03 | B | 10 | 0.005321 | 3.0066e-05
1 | 10935782 | 2016-06-02 09:45 | 2016-06-02 11:50 | 125 | 9 | 1125 | 0.0033825 | 0.003301 | 2.706e-05 | NAPA ID:18868 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 018868 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1608 | NONE | Replace HV & LV Xrms at pole C651. Works location; Stanley Rd, Te Aroha. WO 30012336 | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0016505 | 5.5 | 2017 | 2016-06-02 | B | 9 | 0.003301 | 2.706e-05
1 | 10935819 | 2016-06-07 09:30 | 2016-06-07 11:00 | 90 | 6 | 540 | 0.0016235 | 0.001569 | 1.8038e-05 | NAPA ID:18848 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | 018848 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2212 | NONE | replace rusty transformer TC2212. Works location: Morrinsville Walton Rd. WO 30019928 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0007845 | 5.5 | 2017 | 2016-06-07 | B | 6 | 0.001569 | 1.8038e-05
1 | 10935824 | 2016-05-12 11:50 | 2016-05-12 17:39 | 349 | 23 | 3157.1 | 0.0094953 | 0.009287 | 6.9175e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7722555 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, NOT ALL PHASES | Reports of no power found a line down beyond fuses o52. Line repaired OK but Fuses 052 found to be in a poor condition / broken. Outage required from Fuses 806 where all 3 were replaced. Relivened OK. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.009287 | 11 | 2017 | 2016-05-12 | C | 23 | 0.009287 | 6.9175e-05
1 | 10936762 | 2016-05-12 12:13 | 2016-05-12 13:30 | 77 | 868 | 44668.35 | 0.13434 | 0.12651 | 0.0044573 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P00162 | CROSSARM - WHOLE ASSEMBLY | CB 6 TRIPPED CB 6 AND 8 LINKED TOGETHER found twisted crossarm at pole P00162 Isolated at H103 2r line patrol 1324 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.12651 | 11 | 2017 | 2016-05-12 | C | 868 | 0.12651 | 0.0044573
1 | 10939926 | 2016-05-12 13:48 | 2016-05-12 15:36 | 107 | 110 | 11839.6667 | 0.035609 | 0.034616 | 0.00033084 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 817982 | JUMPER | Reports of part power found a blown midspan jumper at Pole 817982. Outage required from ABS S306 to carryout work (2 jumpers repaired). Relivened OK. High winds. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.034616 | 11 | 2017 | 2016-05-12 | C | 110 | 0.034616 | 0.00033084
1 | 10941878 | 2016-05-12 13:31 | 2016-05-12 15:03 | 92 | 46 | 4242.7333 | 0.01276 | 0.012345 | 0.00013835 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB I23 | UNKNOWN | Feeder CBI23 found to have tripped. No fault found, reclosed OK | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.012345 | 11 | 2017 | 2016-05-12 | C | 46 | 0.012345 | 0.00013835
1 | 10943109 | 2016-06-08 08:53 | 2016-06-08 14:40 | 347 | 66 | 22924.7333 | 0.06892 | 0.068324 | 0.00019842 | NAPA ID:18872 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 018872 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole C3339 | NONE | Change all arms and ABS 614 on pole C3339. Change arms on pole C2737. Works location: Stanley Rd, Te Aroha. WO 30012336 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.034162 | 5.5 | 2017 | 2016-06-08 | B | 66 | 0.068324 | 0.00019842
1 | 10943138 | 2016-06-09 09:30 | 2016-06-09 13:28 | 238 | 22 | 5236 | 0.015741 | 0.015542 | 6.6139e-05 | NAPA ID:19411 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 019411 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC1478 | NONE | Replace HT fuses FC1478 and Xarms at various sites. Works location: Hwy 27, Waharoa. WO 30026345 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.007771 | 5.5 | 2017 | 2016-06-09 | B | 22 | 0.015542 | 6.6139e-05
1 | 10943182 | 2016-06-15 09:15 | 2016-06-15 13:45 | 270 | 94 | 25380 | 0.076294 | 0.075446 | 0.00028257 | NAPA ID:20625 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | 020625 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 550 | NONE | Replace crossarms unable to be done live line. Works location: Rawhiti Rd, Station Rd, Te Aroha. WO 30002440 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.037723 | 5.5 | 2017 | 2016-06-15 | B | 94 | 0.075446 | 0.00028257
1 | 10943221 | 2016-06-16 09:30 | 2016-06-16 14:47 | 317 | 16 | 5072 | 0.015247 | 0.015102 | 4.8096e-05 | NAPA ID:19208 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 019208 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw 1333 | NONE | To replace poles Beyond Sw 1333. Works location: Livingstone Rd. WO 30017838 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.007551 | 5.5 | 2017 | 2016-06-16 | B | 16 | 0.015102 | 4.8096e-05
1 | 10943424 | 2016-06-24 09:33 | 2016-06-24 14:45 | 312 | 16 | 4993.6 | 0.015009 | 0.014864 | 4.809e-05 | NAPA ID:19209 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 019209 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | F1368 | NONE | To replace poles Beyond ABS 1333. Works location: Livingstone Rd. WO 30017838 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.007432 | 5.5 | 2017 | 2016-06-24 | B | 16 | 0.014864 | 4.809e-05
1 | 10943444 | 2016-06-03 10:30 | 2016-06-03 14:26 | 236 | 16 | 3776 | 0.011353 | 0.011208 | 4.8105e-05 | NAPA ID:18629 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 2 | 11 | Planned | 018629 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 8454 | NONE | To replace transformer structure with new pole,and new 15kVA transformer plus upgrade earth. Works location: Kelly Rd. W/O 30024634 | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.005604 | 5.5 | 2017 | 2016-06-03 | B | 16 | 0.011208 | 4.8105e-05
1 | 10943475 | 2016-06-05 08:33 | 2016-06-05 10:31 | 118 | 227 | 26786 | 0.080532 | 0.078484 | 0.00068247 | NAPA ID:18401 TP_HAWERA GXP > CAMBRIA SUB > ARGYLE ST | 11 | Planned | 018401 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 703275 | NONE | Replace rotten HV cross arm on pole 703275. Works location: South Rd, Hawera. WO 30015998 | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.039242 | 5.5 | 2017 | 2016-06-05 | B | 227 | 0.078484 | 0.00068247
1 | 10943565 | 2016-06-08 09:38 | 2016-06-08 12:49 | 191 | 90 | 17190 | 0.05168 | 0.050867 | 0.00027057 | NAPA ID:19066 TP_OPUNAKE GXP > NGARIKI SUB > SOUTH RD NGARIKI | 11 | Planned | 019066 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 712595 | NONE | Replace defected pole 712595 & structure with new 11m Busck pole fitted with transformer structure reinstate existing 30kva N3315. Works location: Kina Rd. WO 30019380 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.025434 | 5.5 | 2017 | 2016-06-08 | B | 90 | 0.050867 | 0.00027057
1 | 10943709 | 2016-06-02 09:22 | 2016-06-02 12:56 | 214 | 66 | 14124 | 0.042466 | 0.04187 | 0.00019844 | NAPA ID:19160 TP_MANGAMAIRE GXP > ALFREDTON SUB > RONGOMAI | 11 | Planned | 019160 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS I39 | NONE | Install new road crossing pole and run new 11kv conductor. Works location: Hamua Rongomai Rd. WO 10158162 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.020935 | 5.5 | 2017 | 2016-06-02 | B | 66 | 0.04187 | 0.00019844
1 | 10944195 | 2016-06-08 10:00 | 2016-06-08 15:05 | 305 | 19 | 5795 | 0.017422 | 0.01725 | 5.7121e-05 | NAPA ID:19360 TP_OPUNAKE GXP > PUNGAREHU SUB > PARIHAKA | 11 | Planned | 019360 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses PU421 | NONE | Install new pole several metres in front of pole 710498 and reterminate HV line. Remove 50kVA pole mounted tx and pole 710498. On new pole install and connect new HV cable to supply new 100kVA GM tx with same number (P2045). All LV sevices to be reterminated into new LV pillar supplied from new tx. Fuses PU421 to be upgraded in size. Works location: Parihaka Pa. WO 30018768 | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.008625 | 5.5 | 2017 | 2016-06-08 | B | 19 | 0.01725 | 5.7121e-05
1 | 10944211 | 2016-06-01 09:30 | 2016-06-01 14:26 | 296 | 5 | 1480 | 0.0044499 | 0.004404 | 1.5033e-05 | NAPA ID:19122 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | 019122 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 804663 | NONE | Replace six 11kv railway iron poles 804663, 804672, 804679, 805680, 804681, 804684. Works location: Aldworth Rd, Hunterville. WO 10161847 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.002202 | 5.5 | 2017 | 2016-06-01 | B | 5 | 0.004404 | 1.5033e-05
1 | 10944255 | 2016-05-12 15:41 | 2016-05-12 17:42 | 120 | 110 | 9306.5333 | 0.02799 | 0.026997 | 0.00033084 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T42 | UNKNOWN | Recloser t42 Tripping on B Phase E/F. Feeder sectionalised / patrolled but nothing found. High winds in area. All restored OK. 2r line patrol 1649 no repair | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.026997 | 11 | 2017 | 2016-05-12 | C | 110 | 0.026997 | 0.00033084
1 | 10945436 | 2016-05-12 20:41 | 2016-05-12 20:55 | 14 | 46 | 681.5667 | 0.0020499 | 0.001634 | 0.00013835 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | AR C625. Severe winds | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.001634 | 11 | 2017 | 2016-05-12 | C | 46 | 0.001634 | 0.00013835
1 | 10946481 | 2016-05-13 00:26 | 2016-05-13 05:33 | 307 | 1 | 307.45 | 0.00092467 | 0.000915 | 3.0075e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 7298 | CONDUCTOR - REPAIR/REHANG | Was informed by Service hub that faultmen on Emergency Only Calls. Will go first thing in morning. Tree in Line at Pole 798859 removed with Sticks. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000915 | 11 | 2017 | 2016-05-13 | C | 1 | 0.000915 | 3.0075e-06
1 | 10946493 | 2016-05-13 01:38 | 2016-05-13 14:16 | 758 | 90 | 42950.7667 | 0.12918 | 0.12836 | 0.00039098 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 844889 | CONDUCTOR - REPAIR/REHANG | CB 926 Trip, O/C E/F lines down at pole 844889 isolated at ABS S571. Lines down at pole 844889. 4 tension joints, 5m gopher, 2 ali connectors 2R line patrol 02.53am 2R repair 12.49pm. 2r line patrol 0253. 2r reopair 1248 | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.12836 | 11 | 2017 | 2016-05-13 | C | 90 | 0.12836 | 0.00039098
1 | 10951162 | 2016-05-13 02:40 | 2016-05-13 08:36 | 356 | 604 | 62864.8 | 0.18907 | 0.18362 | 0.0022316 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB C928 trip found tree in lines at pole 81104. 2r line patrol 0343. 2r repair N/A | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.18362 | 11 | 2017 | 2016-05-13 | C | 604 | 0.18362 | 0.0022316
1 | 10952637 | 2016-05-13 01:42 | 2016-05-13 03:00 | 78 | 3 | 234.15 | 0.00070422 | 0.000677 | 9.0226e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5896 | FUSE - ELEMENT/LINK (HV) | Links To Job 10946588 | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.000677 | 11 | 2017 | 2016-05-13 | C | 3 | 0.000677 | 9.0226e-06
1 | 10953108 | 2016-05-13 03:31 | 2016-05-13 07:04 | 213 | 112 | 23691.7333 | 0.071254 | 0.070243 | 0.00067369 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1213 | CONDUCTOR - REPAIR/REHANG | CB828 trip, line patrol found tree at T1213 brought lines down, isolated at ABS S157 and 193 also CB 828. 1 x joint and 1 x jumper. 2r line patrol NA. 2R repair 0611 | F4 | TAUWERU | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.070243 | 11 | 2017 | 2016-05-13 | C | 112 | 0.070243 | 0.00067369
1 | 10954731 | 2016-05-13 03:17 | 2016-05-13 11:30 | 492 | 65 | 32003.8333 | 0.096253 | 0.095666 | 0.00039098 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p31369 | CONDUCTOR - REPAIR/REHANG | SVS hub advised Guy and Phil have finished this and have called through to clear, have completed from site as needing to be onsite at another job. FM will call control to clear. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.095666 | 11 | 2017 | 2016-05-13 | C | 65 | 0.095666 | 0.00039098
1 | 10954795 | 2016-05-13 04:25 | 2016-05-13 07:16 | 171 | 256 | 8509.4667 | 0.025593 | 0.023282 | 0.00079098 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 7300 | FUSE - ELEMENT/LINK (HV) | Reports of no powers found tree over lines, beyond fuses 7300 replaced 3 x 10amp fuses and 1 holder | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.023282 | 11 | 2017 | 2016-05-13 | C | 256 | 0.023282 | 0.00079098
1 | 10954813 | 2016-05-13 06:35 | 2016-05-13 11:55 | 320 | 3 | 960 | 0.0028872 | 0.00286 | 9.0226e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 725160 | CROSSARM - WHOLE ASSEMBLY | Trees found not to be the cause of the fault. Rehung lines, replace 1 x cross arm, 8 x sleeves, 4m conductor, binder & 1 x 3A Fuse | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.00286 | 11 | 2017 | 2016-05-13 | C | 3 | 0.00286 | 9.0226e-06
1 | 10956154 | 2016-05-13 07:37 | 2016-05-13 09:50 | 133 | 6 | 798 | 0.0024 | 0.002345 | 1.8045e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 803253 | CONDUCTOR - REPAIR/REHANG | Resag lines, and rebind conductor. Replace 2 x 8A Fuse. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.002345 | 11 | 2017 | 2016-05-13 | C | 6 | 0.002345 | 1.8045e-05
1 | 10956473 | 2016-05-13 06:39 | 2016-05-13 09:35 | 175 | 238 | 18062.3 | 0.054323 | 0.052175 | 0.0013775 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 735681 | CROSSARM - WHOLE ASSEMBLY | Replace 1 x crossarm & 6m x binder. rec 6497 trip broken crossarm at pole 735681. 2r line patrol 0728 2r repair 0843 | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.052175 | 11 | 2017 | 2016-05-13 | C | 238 | 0.052175 | 0.0013775
1 | 10956764 | 2016-05-13 06:53 | 2016-05-13 08:41 | 108 | 254 | 21221.05 | 0.063823 | 0.061531 | 0.00076392 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB H131 trip, earth fault, patrolled nothing found. 2r line patrol 0750 no repair | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.061531 | 11 | 2017 | 2016-05-13 | C | 254 | 0.061531 | 0.00076392
1 | 10958733 | 2016-05-13 14:30 | 2016-05-13 17:18 | 168 | 7 | 1176.4667 | 0.0035383 | 0.003475 | 2.1053e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 818878 | POLE | Pole reported broken - Isolated at Fuses 7217. Pole 818878 replaced. Used 1 x pole and complete cross arm. | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.003475 | 11 | 2017 | 2016-05-13 | C | 7 | 0.003475 | 2.1053e-05
1 | 10958769 | 2016-05-13 10:19 | 2016-05-13 11:10 | 51 | 47 | 2397 | 0.0072091 | 0.006785 | 0.00014135 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD5-069 | JOINT - CONDUCTOR JOINT | Reterminate burnt up connection at fuse SD5-069. Isolation at Fuses SD5-069. No Back feeds available. Pole 219866. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.006785 | 11 | 2017 | 2016-05-13 | C | 47 | 0.006785 | 0.00014135
1 | 10958780 | 2016-05-13 08:50 | 2016-05-13 09:58 | 68 | 69 | 3540 | 0.010647 | 0.010024 | 0.00020752 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 7752 | FUSE - ELEMENT/LINK (HV) | plz check if oms 10959033 & 10959241 related Line patrol suspect line clash - 4x 10amp | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.010024 | 11 | 2017 | 2016-05-13 | C | 69 | 0.010024 | 0.00020752
1 | 10958790 | 2016-05-13 07:20 | 2016-05-13 10:30 | 190 | 66 | 12559.8 | 0.037774 | 0.037178 | 0.0001985 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Check C637. Found C637 tripped, reclosed. Nothing found. | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.037178 | 11 | 2017 | 2016-05-13 | C | 66 | 0.037178 | 0.0001985
1 | 10959266 | 2016-05-13 07:50 | 2016-05-13 18:40 | 649 | 23 | 13506.1167 | 0.04062 | 0.040412 | 6.9174e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 827882 | NONE | Reports of part power found Sectionaliser CB C213 tripped. Area sectionalised / patrolled with a tree branch found sitting across a 3 phases. Removed safely with fuse stick and relivened. 2r line patrol 1820. 2r repair no branch on line. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.040412 | 11 | 2017 | 2016-05-13 | C | 23 | 0.040412 | 6.9174e-05
1 | 10959529 | 2016-05-13 11:27 | 2016-05-13 13:08 | 101 | 101 | 10201 | 0.03068 | 0.029768 | 0.00030376 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | S342 | JUMPER | Repair jumper @ abs S342 using 2x connectors 1m conductor - several no powers found to be jumper ABS S342 Isolated sectionaliser 421 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.029768 | 11 | 2017 | 2016-05-13 | C | 101 | 0.029768 | 0.00030376
1 | 10960205 | 2016-05-13 10:37 | 2016-05-13 13:35 | 178 | 5 | 891.3333 | 0.0026807 | 0.002635 | 1.5038e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 799470 | FUSE - ELEMENT/LINK (HV) | Power lines are hanging too loose and need to be tightened - these are causing faults and potential threat to property and health and safety risk - customer is extremely concerned has been attended before but has not been resolved please confirm with the customer about what is going to be done about this before more damage is caused called in by George Richie. 9.52am advised Shan at svs hub. **check oms 10961427 no power. 2x 11kV 10 amp line clash high winds spur line 799470 / Fuses 7228. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.002635 | 11 | 2017 | 2016-05-13 | C | 5 | 0.002635 | 1.5038e-05
1 | 10960348 | 2016-05-15 09:01 | 2016-05-15 15:18 | 377 | 58 | 21873.7333 | 0.065784 | 0.065261 | 0.00017443 | NAPA ID:20768 TP_BUNNYTHORPE GXP > FEILDING SUB > KAWAKAWA | 11 | Planned | 020768 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P32760 | NONE | 1. Replace pole P32670 2. Replace sleel xarms on P32665. 3. Install temp fuses temp 90 on pole P32665. 4. Install temp fuses 91 on P32636. 5. Remove ABS TEMP 54. Note: This Napa is a rewrite of switching 17601 - Engineering modification after test switching . THIS OUTAGE HAS BEEN ADVERTISED AS 17601 . | F1 | KAWAKAWA | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.03263 | 5.5 | 2017 | 2016-05-15 | B | 58 | 0.065261 | 0.00017443
1 | 10960578 | 2016-05-17 08:30 | 2016-05-17 15:11 | 401 | 34 | 13634 | 0.041003 | 0.040695 | 0.00010225 | NAPA ID:20772 TP_BUNNYTHORPE GXP > FEILDING SUB > KAWAKAWA | 11 | Planned | 020772 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace xarms beteen temp 90 to L50. This NAPA is a rewrite of NAPA 17602 , due to engineering modification after test outage . THIS OUTAGE IS ADVERTISED UNDER NAPA 17602 | F1 | KAWAKAWA | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.020348 | 5.5 | 2017 | 2016-05-17 | B | 34 | 0.040695 | 0.00010225
1 | 10960651 | 2016-06-07 09:55 | 2016-06-07 14:03 | 248 | 51 | 12648 | 0.038025 | 0.037565 | 0.00015333 | NAPA ID:18804 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | 018804 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P48076 | NONE | To replace 11kv pole P48075. North Road, Mauriceville, Parkville. W/O 30003339. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.018783 | 5.5 | 2017 | 2016-06-07 | B | 51 | 0.037565 | 0.00015333
1 | 10961374 | 2016-05-19 09:05 | 2016-05-19 13:06 | 241 | 34 | 8194 | 0.024642 | 0.024334 | 0.00010225 | NAPA ID:20779 TP_BUNNYTHORPE GXP > FEILDING SUB > KAWAKAWA | 11 | Planned | 020779 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P32665 | CROSSARM - ARM ONLY | Replace cross arms. Works Location: Kawakawa Road, Feilding. Works Order 10157896. This NAPA is a rewrite of NAPA 17603 , due to engineering modifications after test outage. This outage has been advertised under NAPA17603. | F1 | KAWAKAWA | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.012167 | 5.5 | 2017 | 2016-05-19 | B | 34 | 0.024334 | 0.00010225
1 | 10961387 | 2016-06-03 09:45 | 2016-06-03 14:14 | 269 | 22 | 5918 | 0.017793 | 0.017594 | 6.6145e-05 | NAPA ID:20706 TP_HAWERA GXP > LIVINGSTONE SUB > OTAUTU | 11 | Planned | 020706 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | LI122 | NONE | Replace DNO ABS LI180. Works Location: Otauto Rd,Livingston. W/O 30026848. | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.008797 | 5.5 | 2017 | 2016-06-03 | B | 22 | 0.017594 | 6.6145e-05
1 | 10961515 | 2016-05-13 12:04 | 2016-05-13 16:48 | 284 | 1 | 284 | 0.00085414 | 0.000845 | 3.0075e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 799856 | POLE | 10.53am advised Shan at svs hub Adrian is onsite and fire are also on site putting the fire out. Advised Fire as there was conflicting information. Isolated at Fuses 7196 Pole 799856 Replaced Used 1 x pole complete 2x joiners, 2x line gaurds 2 x binders 5 mtrs of conductor | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000845 | 11 | 2017 | 2016-05-13 | C | 1 | 0.000845 | 3.0075e-06
1 | 10962155 | 2016-06-01 21:00 | 2016-06-01 22:55 | 115 | 16 | 1840 | 0.0055323 | 0.005387 | 4.8107e-05 | NAPA ID:18780 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 7 | 11 | Planned | 018780 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Earth switch 438/2 | NONE | Systematic replacement of Magnefix 1264 with new Safelink unit. This will be done in four(4) stages due to switching requirements and work to be done. This is Stage 2. AP is to reterminate HV cable from tx 304 to new Temp 60/2. Liven Safelink from 438/2 and liven tx 304 with phase rotation. Stage 3 NAPA 18783 to follow. Currently the new location new tx 1264 is already connected to Temp 60/4 (Stage 3 it will be 1264/4). Parklands Avenue, Bell Block. W/O 30002196. | F3 | MANGATI RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.0026935 | 5.5 | 2017 | 2016-06-01 | B | 16 | 0.005387 | 4.8107e-05
1 | 10962253 | 2016-05-30 09:20 | 2016-05-30 15:45 | 385 | 6 | 2310 | 0.0069456 | 0.006891 | 1.8041e-05 | NAPA ID:20792 TP_BUNNYTHORPE GXP > SANSON SUB > MT STEWART | 11 | Planned | 020792 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P20254 | POLE | Replace H pole P20254 with new poles, ABS and xarms between temp fuses 89 and 91. Temp fuses 89 will be install on 23/5/16 under NAPA 17605. This NAPA is a rewrite of NA{A 17612 , due to engineering modification after test outage . This outage has been advertised as 17612 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.0034455 | 5.5 | 2017 | 2016-05-30 | B | 6 | 0.006891 | 1.8041e-05
1 | 10962475 | 2016-05-13 12:00 | 2016-05-13 20:59 | 539 | 117 | 54804.8833 | 0.16483 | 0.16377 | 0.00059249 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837191, 837197 | CONDUCTOR - REPAIR/REHANG | Initial tripping on Recloser C217 on C Phase, EF. Fedder patrolled and 2 faults were found. (Both isolations at ABS S147. A Floating conductor was repaired at Pole 837197. Further patrol found a broken conductor at Pole 837191. (Large Gully, difficult location). Full conductor replaced (Temp fix). Relivened OK .2r line patrol 1304 2r repair 1451 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.16377 | 11 | 2017 | 2016-05-13 | C | 117 | 0.16377 | 0.00059249
1 | 10963706 | 2016-06-07 09:47 | 2016-06-07 16:00 | 373 | 3 | 1119 | 0.0033642 | 0.003337 | 9.0192e-06 | NAPA ID:19461 TP_MASTERTON GXP > CLAREVILLE SUB > BELVEDERE | 11 | Planned | 019461 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | Poles 817563 and 817566 | NONE | tree removal between poles 817563 and 817566 11kv isolated fuses 7569 to end of line ( dead end line ). 118 Coden Road, Carterton, Clareville. W/O 30026281. | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.0016685 | 5.5 | 2017 | 2016-06-07 | B | 3 | 0.003337 | 9.0192e-06
1 | 10964152 | 2016-05-13 13:58 | 2016-05-13 17:00 | 182 | 1 | 182.4333 | 0.00054868 | 0.000539 | 3.0075e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SE6-152 | FUSE - ELEMENT/LINK (HV) | 1x Blown HV fuses at fuse/Sw SE6-152. Isolated & Earthed at SE6-152 to replace all 3 fuses. Line patrolled no fault found. 3x 6amp HRC fuses used. | F4 | MANGOREWA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000539 | 11 | 2017 | 2016-05-13 | C | 1 | 0.000539 | 3.0075e-06
1 | 10964213 | 2016-06-02 09:29 | 2016-06-02 16:02 | 392 | 17 | 6565.7667 | 0.019741 | 0.019587 | 5.1113e-05 | NAPA ID:18162 TP_BUNNYTHORPE GXP > MILSON SUB | 11 | Planned | 018162 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P38180 | NONE | 33kV cross arm replacement for BPE-MIL line from Z35 to Z36. 11kV cross arms and 400V underneath 33kV also needed to be replaced. Line is between P39685 - P39691.Palmerston North, Milson. W/O 30019577. | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.0097935 | 5.5 | 2017 | 2016-06-02 | B | 17 | 0.019587 | 5.1113e-05
1 | 10964255 | 2016-05-13 14:17 | 2016-05-13 14:42 | 25 | 4 | 102 | 0.00030677 | 0.00027 | 1.203e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7288 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Reload 2 x 6amp Fuses. Cause unknown. | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.00027 | 11 | 2017 | 2016-05-13 | C | 4 | 0.00027 | 1.203e-05
1 | 10964732 | 2016-06-08 10:02 | 2016-06-08 12:20 | 138 | 23 | 3174 | 0.0095422 | 0.009334 | 6.9146e-05 | NAPA ID:19096 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 019096 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 1492 | NONE | Replace old hardwood pole 786945 napier taihape rd. Napier Taihape Road, Taihape. W/O 30013315. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.004667 | 5.5 | 2017 | 2016-06-08 | B | 23 | 0.009334 | 6.9146e-05
1 | 10964796 | 2016-06-08 09:00 | 2016-06-08 14:44 | 344 | 20 | 6880 | 0.020684 | 0.020503 | 6.0127e-05 | NAPA ID:19304 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 019304 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Fuses 7466 | NONE | Replacing 11kv poles and hardware. Donovans Road, Masterton, Akura. W/O 30019523. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.010252 | 5.5 | 2017 | 2016-06-08 | B | 20 | 0.020503 | 6.0127e-05
1 | 10965036 | 2016-05-13 15:39 | 2016-05-13 19:00 | 200 | 31 | 6227.3833 | 0.018729 | 0.018449 | 9.3234e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | C269 | RECLOSER (HV) | have requested smc send the FM to recloser C269 as we have 3 no power jobs past this point. Please also ask FM about 10965808 and 10966083 (317 NGATAHUNA ROAD and 2096 MASTERTON-STRONVAR ROAD). Recloser C269 was found tripped after reeceiving "no power" calls. Reclosed OK. High winds. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.018449 | 11 | 2017 | 2016-05-13 | C | 31 | 0.018449 | 9.3234e-05
1 | 10965191 | 2016-05-13 16:11 | 2016-05-14 11:13 | 1142 | 10 | 11421.8333 | 0.034352 | 0.034261 | 3.0075e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P27919 | JUMPER | 5:36pm - called Cindy at SMNC to advise cust has had no power all day as per fax from Retailer. SCADA dress at 18:55 13/05/16 , Faultman advised this was not what had happened last night. Jumper found broken at pole P27919 - Isolated at Fuses I26. Used 1 mtr of conductor 4 x connectors. | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.034261 | 11 | 2017 | 2016-05-13 | C | 10 | 0.034261 | 3.0075e-05
1 | 10965710 | 2016-05-13 16:17 | 2016-05-13 19:47 | 210 | 6 | 1260.6 | 0.0037913 | 0.003737 | 1.8045e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 7101 | FUSE - ELEMENT/LINK (HV) | 2 HT fuses tripped at Fuses 7101. Reloaded OK. High winds. | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.003737 | 11 | 2017 | 2016-05-13 | C | 6 | 0.003737 | 1.8045e-05
1 | 10965946 | 2016-05-13 17:45 | 2016-05-13 19:55 | 130 | 240 | 11187 | 0.033645 | 0.031479 | 0.00072181 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H3260 | CONDUCTOR - REPAIR/REHANG | 2r request to be decided at invoicing. Advised HV line on the ground, opened CB 2 for safety due to DNO160314 on ABD 764. Outage required between ABS IC3132 & ABS 2668. Backfeed from FRM4 via ABS 999. Repaired 1 x line down at pole H3260 . All service restored. Materials used:10 Meters conductor, 4 x H/V sleeves. | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.031479 | 11 | 2017 | 2016-05-13 | C | 240 | 0.031479 | 0.00072181
1 | 10966269 | 2016-05-12 22:18 | 2016-05-13 11:50 | 812 | 1 | 812.0167 | 0.0024422 | 0.002433 | 3.0075e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Transformer found faulty during night, Isolated at Transformer T2924 fuses Transformer replaced under own AP Used 1 x 10 kVA single ph transformer | F5 | MANGAPAKEHA | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.002433 | 11 | 2017 | 2016-05-12 | C | 1 | 0.002433 | 3.0075e-06
1 | 10971977 | 2016-05-14 09:20 | 2016-05-14 12:14 | 173 | 1 | 173.7 | 0.0005224 | 0.000513 | 3.0075e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7291 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at 7291 - Caused by Weather. Used 2 x 10 amp fuses. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000513 | 11 | 2017 | 2016-05-14 | C | 1 | 0.000513 | 3.0075e-06
1 | 10971983 | 2016-05-14 15:40 | 2016-05-14 16:18 | 37 | 353 | 13302.2167 | 0.040007 | 0.036821 | 0.0010617 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Z210 | CABLE - REPAIR | Check CB Z190 at Keith St sub and CB Z210 at Main St lost 33kV #2 feeder between subs. Isolation carried out between the 2 CBs and Tests carried out (Confirm 11kV Cable fault). Offloads also carried out on Main St due to Cable loss. Ongoing. Cable terminations to be repaired under DNO 160529. | F3 | MAIN ST 21 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 0.036821 | 11 | 2017 | 2016-05-14 | C | 353 | 0.036821 | 0.0010617
1 | 10972215 | 2016-05-14 14:45 | 2016-05-14 15:30 | 45 | 64 | 2880 | 0.0086616 | 0.008084 | 0.00019248 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5603 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | at 14:45 Coromandel Sub, CB 5 Manaia Feeder. Found broken HV Fuses at Transformer TC5603. These had blown when truck hit low-hanging lines. Isolated lines at ABS IC359. Permit Issued & repairs carried out. All Power Restored on Completion. 4x 3A HV Fuses & 2x HV Fuse Carriers replaced. Ben Edwards Attended. NDR: 31023 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.008084 | 11 | 2017 | 2016-05-14 | C | 64 | 0.008084 | 0.00019248
1 | 10973055 | 2016-05-16 09:30 | 2016-05-16 10:42 | 71 | 13 | 934.9167 | 0.0028117 | 0.002694 | 3.9096e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2395 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | High Voltage as advised by Electrician called through to SMC - Glo Readings: A - 250v B - 251v C - 254v A+B 437v B+C 437v A+C 435v Replaced 3/15kVA/11 Transformer X2395 & 3x HV Fusesholders complete with 2 Amp Links. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.002694 | 11 | 2017 | 2016-05-16 | C | 13 | 0.002694 | 3.9096e-05
1 | 10973670 | 2016-05-14 14:45 | 2016-05-14 15:44 | 59 | 6 | 354 | 0.0010647 | 0.00101 | 1.8045e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 2112T | CONDUCTOR - REPAIR/REHANG | 6x sleeves, 5m conductor. NDR 22909. Nothing else repaired or replaced. Adjacent assets up to Powerco standards. | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.00101 | 11 | 2017 | 2016-05-14 | C | 6 | 0.00101 | 1.8045e-05
1 | 10973765 | 2016-05-14 16:21 | 2016-05-15 14:35 | 1333 | 63 | 18498.75 | 0.055635 | 0.055066 | 0.00018947 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764913 | CROSSARM - WHOLE ASSEMBLY | RS 12131/2 A/R, L/O, E/F. Sectionalised & Patrolled to a point where it was unsafe to carry on in the dark. Fuses 5360 Left open overnight. Patrol commenced again in the morning and found a broken HV Crossarm. Replaced & Relivened. Materials used: Crossarm, 2x HV Pin & Insulator, 2x Ali Binders 2r line patrol 1854 2r repair 1945 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.055066 | 11 | 2017 | 2016-05-14 | C | 63 | 0.055066 | 0.00018947
1 | 10973930 | 2016-05-14 17:01 | 2016-05-14 18:23 | 82 | 1 | 82 | 0.00024662 | 0.000237 | 3.0075e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nn | UNKNOWN | check oms 10973984 no fault on network, possibly related to earlier HV fault, delay possibly related to system issues | F3 | TETLEY ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 0.000237 | 11 | 2017 | 2016-05-14 | C | 1 | 0.000237 | 3.0075e-06
1 | 10974093 | 2016-05-14 18:18 | 2016-05-14 18:28 | 10 | 8 | 80 | 0.0002406 | 0.000168 | 2.406e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 826928 | FUSE - LV ELEMENT/LINK - HRC (LV) | LV Lead broken off, required HT isolation. Isolated on HV to carryout repairs. Relivened OK. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000168 | 11 | 2017 | 2016-05-14 | C | 8 | 0.000168 | 2.406e-05
1 | 10974648 | 2016-05-14 19:17 | 2016-05-14 21:00 | 102 | 10 | 750.6833 | 0.0022577 | 0.002167 | 3.0075e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 826205 | CONDUCTOR - REPAIR/REHANG | Isolation required from Fuses 7156 to repair a broken Conductor. (Wind blown branch). Line had also caused a fire underneath and the Fire Services were in attendence. Conductor repaired / rehung and livened OK. NDR 23393. High winds in area. (NOTE: Problem with OMS, this is the incorrect feeder - OMS Linked to 110974264). | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.002167 | 11 | 2017 | 2016-05-14 | C | 10 | 0.002167 | 3.0075e-05
1 | 10974900 | 2016-05-15 10:02 | 2016-05-15 10:36 | 33 | 26 | 856.75 | 0.0025766 | 0.002342 | 7.8194e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P15323 | JUMPER | Repaired broken 11kV jumper at Pole P15323. Work area Isolated at I27. Materials used: 1x Bi metal connector. | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.002342 | 11 | 2017 | 2016-05-15 | C | 26 | 0.002342 | 7.8194e-05
1 | 10976919 | 2016-05-15 14:38 | 2016-05-15 14:39 | 1 | 284 | 284 | 0.00085412 | 0 | 0.00085412 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Mike Cornelius Attended. Found recloser controller was OFF when he arrived on site. Turned controller ON. Found that when NOC did a manual comms poll of the recloser, the controller would turn OFF. Recloser bypassed & DNO'd. Needs further investigation from Technician. DNO 160528. Recloser RC01 is giving all false indications - suspect controller has malfunctioned. need faultman to attend to confirm controller has malfunctioned and may need to bypass the recloser. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-05-15 | C | 284 | 0 | 0.00085412
1 | 10978116 | 2016-06-03 09:02 | 2016-06-03 16:20 | 438 | 8 | 3504 | 0.010535 | 0.010462 | 2.4053e-05 | NAPA ID:18163 TP_BUNNYTHORPE GXP > MILSON SUB | 11 | Planned | 018163 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | 33kV Crossarm replacement for BPE-MIL line from Z35 to Z36. 400V crossarms underneath 33kV also needed to be replaced. Line is between P39694-P41945. Replace pole at P41945 | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.005231 | 5.5 | 2017 | 2016-06-03 | B | 8 | 0.010462 | 2.4053e-05
1 | 10978517 | 2016-05-16 09:35 | 2016-05-16 12:50 | 195 | 9 | 1755 | 0.005278 | 0.005196 | 2.7067e-05 |  | 22 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1488 | FUSE - ELEMENT/LINK (HV) | 2 x 15amp fuses bird strike | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.005196 | 22 | 2017 | 2016-05-16 | C | 9 | 0.005196 | 2.7067e-05
1 | 10978617 | 2016-06-08 08:31 | 2016-06-08 16:10 | 459 | 5 | 2297.0833 | 0.0069059 | 0.00686 | 1.5032e-05 | NAPA ID:19459 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 019459 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Poles 831788, 831792 | NONE | Removal of trees between poles 831788 and 831792 11kv lines isolated from fuses 7724 to end of line ,dead end line. Paierua Road, Masterton, Akura. W/O 30026281. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.00343 | 5.5 | 2017 | 2016-06-08 | B | 5 | 0.00686 | 1.5032e-05
1 | 10978863 | 2016-06-09 08:45 | 2016-06-09 13:48 | 303 | 36 | 10908 | 0.032793 | 0.032468 | 0.00010823 | NAPA ID:18933 TP_LINTON GXP > KAIRANGA SUB > TAIKOREA | 11 | Planned | 018933 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/214 | NONE | Remove 2 pole structure install new pole use existing TX. Pyke Road, Palmerston North, Kairanga. W/O 30011780. | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.016234 | 5.5 | 2017 | 2016-06-09 | B | 36 | 0.032468 | 0.00010823
1 | 10979162 | 2016-06-02 10:00 | 2016-06-02 12:16 | 136 | 28 | 3808 | 0.011449 | 0.011196 | 8.4185e-05 | NAPA ID:20775 TP_LINTON GXP > KAIRANGA SUB > BAINESSE | 11 | Planned | 020775 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P34805 | NONE | Install extra 11KV pole mid span to gain height across drive ways. Bainesse Road, Palmerston North, Kairanga. W/O 30026163. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.005598 | 5.5 | 2017 | 2016-06-02 | B | 28 | 0.011196 | 8.4185e-05
1 | 10979219 | 2016-06-01 09:00 | 2016-06-01 14:37 | 337 | 25 | 8425 | 0.025331 | 0.025105 | 7.5167e-05 | NAPA ID:17761 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 017761 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC 482 | NONE | Replace XArms at various sites. Kaihere Road, Kerepehi. W/O 30002467. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.012552 | 5.5 | 2017 | 2016-06-01 | B | 25 | 0.025105 | 7.5167e-05
1 | 10979458 | 2016-06-01 09:30 | 2016-06-01 13:16 | 226 | 128 | 28928 | 0.086977 | 0.085822 | 0.00038485 | NAPA ID:18287 TP_HUIRANGI GXP > WAITARA EAST SUB > TIKORANGI | 11 | Planned | 018287 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 764348 | NONE | DOWNERS: Replace 11KV xarms @ Pole 764309 &764348. NPETECH: Upgrade 11kV TX 2935T to a 30kVa from 15kVa. (Was NAPA 19435). DOWNERS to hold the AP with NPE tech signing on as secondary works party. 483 & 577 Inland North Road, Waitara. W/O 30017469. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.042911 | 5.5 | 2017 | 2016-06-01 | B | 128 | 0.085822 | 0.00038485
1 | 10979659 | 2016-06-01 09:35 | 2016-06-01 11:55 | 140 | 64 | 8075 | 0.024279 | 0.023701 | 0.00019243 | NAPA ID:18300 TP_KOPU GXP > WHITIANGA SUB > PURANGI | 11 | Planned | 018300 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC 2375 | NONE | Replace SP010 Electronic DDOs with standard DDOs. Replace XARM. 83 Oyster Drive, Whitianga. W/O 30018713. | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.01185 | 5.5 | 2017 | 2016-06-01 | B | 64 | 0.023701 | 0.00019243
1 | 10979674 | 2016-06-01 08:47 | 2016-06-01 15:26 | 399 | 40 | 15960 | 0.047986 | 0.047625 | 0.00012027 | NAPA ID:19383 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | 019383 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | Poles P29098, P15298, P12836 | NONE | Tree removal. Whangaehu Valley Road, Parkville. W/O 30026290. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.023813 | 5.5 | 2017 | 2016-06-01 | B | 40 | 0.047625 | 0.00012027
1 | 10979701 | 2016-06-02 08:48 | 2016-06-02 13:43 | 295 | 40 | 11800 | 0.035478 | 0.035117 | 0.00012026 | NAPA ID:19386 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | 019386 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | na | NONE | Shutdown for tree removal | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.017559 | 5.5 | 2017 | 2016-06-02 | B | 40 | 0.035117 | 0.00012026
1 | 10979903 | 2016-06-02 10:00 | 2016-06-02 14:45 | 285 | 125 | 35625 | 0.10711 | 0.10598 | 0.00037583 | NAPA ID:18783 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 7 | 11 | Planned | 018783 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Earth switch 126/4 | NONE | Systematic replacement of Magnefix 1264 with new Safelink unit. This will be done in four(4) stages due to switching requirements and work to be done. This is Stage 3. AP to cut HV cable from 233/1 at magnefix ready for stage 4 (NAPA 18787) work. Remove old tx 1264 and magnefix gear. AP is to reterminate HV cable from tx 1279 to new tx 1264 HV bushings (creating existing piggy back system). Tx 1264 extend all LV circuits to new location. Stage 4 (NAPA 18787) to follow. Parklands Avenue, Bell Block. W/O 30002196. | F3 | MANGATI RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.052991 | 5.5 | 2017 | 2016-06-02 | B | 125 | 0.10598 | 0.00037583
1 | 10980349 | 2016-05-16 16:38 | 2016-05-16 17:24 | 46 | 957 | 38670.9 | 0.1163 | 0.10766 | 0.0028781 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 701532 | NONE | High Winds and Lightning in the area. Tree branch found blown onto lines at pole 701532. Removed with Fuse Stick and feeder restored. CB 7 trip O/C | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.10766 | 11 | 2017 | 2016-05-16 | C | 957 | 0.10766 | 0.0028781
1 | 10982225 | 2016-05-16 16:57 | 2016-05-17 06:39 | 822 | 1134 | 170331.9667 | 0.51226 | 0.50203 | 0.0034104 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | W0179 | JOINT - CONDUCTOR JOINT | CB7 tripped - no flags found broken pot head at pole W0179. Isolated at IC1195, 2041, 2046, 2044. NDR18137. 2r line patrol 1729 / 2r repair.1800 | F3 | JOAN GASKELL DR | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.50203 | 11 | 2017 | 2016-05-16 | C | 1134 | 0.50203 | 0.0034104
1 | 10983369 | 2016-05-16 16:58 | 2016-05-16 18:55 | 116 | 18 | 2105.7 | 0.0063327 | 0.00617 | 5.4133e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 628 | FUSE - ELEMENT/LINK (HV) | 2 fuses blown at 628. Suspect wind.Replaced 2x10amp Fuse links. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.00617 | 11 | 2017 | 2016-05-16 | C | 18 | 0.00617 | 5.4133e-05
1 | 10983721 | 2016-05-16 17:01 | 2016-05-16 18:19 | 77 | 21 | 1636.95 | 0.004923 | 0.004733 | 6.3156e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3401 | INSULATOR | Customer called to advise that there was an explosion from the pole then no power. 5.05pm advised Sammy & emailed. Broken Insulator. 1 x HV Insulator & 1 x 10A HV Fuse Replaced | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.004733 | 11 | 2017 | 2016-05-16 | C | 21 | 0.004733 | 6.3156e-05
1 | 10983990 | 2016-05-16 17:41 | 2016-05-16 19:10 | 88 | 4 | 355.9333 | 0.0010704 | 0.001034 | 1.203e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TF4-018 | FUSE - ELEMENT/LINK (HV) | Dave Ngatai Attended. Reloaded, Relivened 2x 2A HV Fuses. Lightning in area. | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.001034 | 11 | 2017 | 2016-05-16 | C | 4 | 0.001034 | 1.203e-05
1 | 10985494 | 2016-05-16 18:36 | 2016-05-16 23:28 | 291 | 261 | 31708.5 | 0.095361 | 0.093005 | 0.0016902 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13819 | CONDUCTOR - REPAIR/REHANG | Floating conductor at pole P13819. Rebound in. Recloser 10002 tripped E/F. 2r line patrol 2008 / 2r repair 2252. | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.093005 | 11 | 2017 | 2016-05-16 | C | 261 | 0.093005 | 0.0016902
1 | 10986420 | 2016-05-16 19:04 | 2016-05-16 20:54 | 110 | 2 | 220.7333 | 0.00066384 | 0.000645 | 6.0148e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1359 | FUSE - ELEMENT/LINK (HV) | 2x3amp fuses blown at transformer 1359. due to lightning | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.000645 | 11 | 2017 | 2016-05-16 | C | 2 | 0.000645 | 6.0148e-06
1 | 10986424 | 2016-05-16 19:04 | 2016-05-16 19:32 | 28 | 205 | 5743.4167 | 0.017273 | 0.015423 | 0.00061652 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | 9198 | UNKNOWN | Job Cancelled by NOC. Lightning probable cause.Job has been created to do line patrol. | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.015423 | 11 | 2017 | 2016-05-16 | C | 205 | 0.015423 | 0.00061652
1 | 10986667 | 2016-05-16 19:14 | 2016-05-16 23:57 | 283 | 329 | 43973.8 | 0.13225 | 0.12928 | 0.00098944 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4955 | CONDUCTOR - REPAIR/REHANG | Recloser 9121 tripped. Line patrolled. Found line down at pole TC4955. NDR 55710. 2r line patrol 2002 / 2r repair 2307. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.12928 | 11 | 2017 | 2016-05-16 | C | 329 | 0.12928 | 0.00098944
1 | 10987800 | 2016-05-16 19:48 | 2016-05-16 23:40 | 232 | 5 | 1160.1667 | 0.0034891 | 0.003443 | 1.5037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC4527 | FUSE - ELEMENT/LINK (HV) | Mike Jefferies Attended. Reloaded relivened 2x HV Fuses. Lightning in area | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.003443 | 11 | 2017 | 2016-05-16 | C | 5 | 0.003443 | 1.5037e-05
1 | 10988372 | 2016-05-16 19:53 | 2016-05-16 23:44 | 230 | 727 | 106586.25 | 0.32055 | 0.31399 | 0.0031127 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 390919 | CONDUCTOR - REPAIR/REHANG | at 19:53, Tauranga Sub, CB 11 Kaimai Drive Feeder, Tripped, O/C, L/O. At the same time Sectionaliser 9698 Flagged with A + B Ph O/C. Recloser 9275 Also flagged with O/C due to 9275 Auto Reclosing After CB 11 had tripped to L/O. Faultmen dispatched and feeder sectionalising began. Found tree branch on line between Transformer TE3-005 & Pole 390919. Backfeed supplied from TGA 12: Closed IP183, fed up to Sectionaliser 9270 (Sectionaliser wouldn't close due to flat batteries) and ABS SE3-004. Removed branch with hot stick. All Power Restored on Completion. No Materials Used. Sam Jones Attended. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.31399 | 11 | 2017 | 2016-05-16 | C | 727 | 0.31399 | 0.0031127
1 | 10991727 | 2016-05-16 19:54 | 2016-05-17 15:52 | 1197 | 2723 | 48132 | 0.14475 | 0.12019 | 0.0073862 |  | 33 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | WKOROT040 | CONDUCTOR - REPAIR/REHANG | Waikino CB242 tripped on Inst O/C resulting in LOS to Paeroa Substation. Lines down at WKOROT040 and surrounding poles caused by tree. Extensive damage. Uploaded from LOS 624973: There was significant damage located at 33kV Pole WKOROT040 on the Waikino 242 - Paeroa line. This line runs over the Waikino 312 - Paeroa line at this structure. Due to this, the ring feed was deenergised for approximately 1 hour to allow repairs to be complete. During this time the 11kV feed was taken from Kerepehi to supply Paeroa. There was a tripping during the time that Kerepehi 11kV was supporting Paeroa. | S2 | WAIKINO242-PAEROA 33KV | WAIKINO | Valley | TP_WAIKINO | Eastern Electricity | POWERCO | 0.12019 | 33 | 2017 | 2016-05-16 | C | 2723 | 0.12019 | 0.0073862
1 | 10991852 | 2016-05-16 20:13 | 2016-05-16 22:32 | 138 | 5 | 694.3333 | 0.0020882 | 0.002043 | 1.5037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC622 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 3x 3A HV Fuses. Lightning in the area. Mike Jefferies Attended. | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.002043 | 11 | 2017 | 2016-05-16 | C | 5 | 0.002043 | 1.5037e-05
1 | 10991922 | 2016-05-16 20:31 | 2016-05-17 01:13 | 282 | 4 | 1129.6667 | 0.0033974 | 0.003361 | 1.203e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2500 | FUSE - ELEMENT/LINK (HV) | Reloaded Relivened 3x HV Fuses at TC2500. Lightning in area. Mike Jefferies attended. | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.003361 | 11 | 2017 | 2016-05-16 | C | 4 | 0.003361 | 1.203e-05
1 | 10992087 | 2016-05-16 21:03 | 2016-05-16 22:41 | 97 | 1 | 97.6333 | 0.00029362 | 0.000284 | 3.0074e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4195T | FUSE - ELEMENT/LINK (HV) | replaced 2x3amp fuses at tranformer 4195T, also replace 1x3amp fuse at transformer 3675T, all due to lightning. fuse barrel used at transformer 3675T. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000284 | 6.6 | 2017 | 2016-05-16 | C | 1 | 0.000284 | 3.0074e-06
1 | 10992261 | 2016-05-16 21:40 | 2016-05-17 03:00 | 320 | 1 | 320.3 | 0.00096328 | 0.000954 | 3.0074e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC4892 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x HV Fuses at Transformer TC4892. Marty Keenan Attended. Lightning in area. | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000954 | 11 | 2017 | 2016-05-16 | C | 1 | 0.000954 | 3.0074e-06
1 | 10996071 | 2016-05-16 22:02 | 2016-05-16 23:48 | 105 | 1 | 105.6667 | 0.00031778 | 0.000308 | 3.0074e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2515T | FUSE - ELEMENT/LINK (HV) | 2x3amp hv fuses blown at 2515T due to lightning | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.000308 | 6.6 | 2017 | 2016-05-16 | C | 1 | 0.000308 | 3.0074e-06
1 | 10996099 | 2016-05-16 22:20 | 2016-05-17 01:01 | 161 | 14 | 2254 | 0.0067787 | 0.006652 | 4.2104e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 801629 | CONDUCTOR - REPAIR/REHANG | Line down at pole 801629. Line repaired. Isolation at ABS 1075 & 959. Materials 5meters of dog conductor, 2 sleeves, 1 preformed binder 2r line patrol n/a - 2r repair 2245 | F4 | BULLS | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.006652 | 11 | 2017 | 2016-05-16 | C | 14 | 0.006652 | 4.2104e-05
1 | 10996136 | 2016-05-16 22:12 | 2016-05-16 23:58 | 105 | 6 | 634.8 | 0.0019091 | 0.001854 | 1.8044e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1298 | FUSE - ELEMENT/LINK (HV) | 3x3amp fuses blown at transformer 1298 due to lightning | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.001854 | 11 | 2017 | 2016-05-16 | C | 6 | 0.001854 | 1.8044e-05
1 | 10996865 | 2016-05-16 22:30 | 2016-05-17 00:36 | 126 | 8 | 1009.3333 | 0.0030355 | 0.002963 | 2.4059e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8480 | FUSE - ELEMENT/LINK (HV) | 2x10amp fuses blown at 8480 due to lightning | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.002963 | 11 | 2017 | 2016-05-16 | C | 8 | 0.002963 | 2.4059e-05
1 | 10996882 | 2016-05-16 22:35 | 2016-05-16 23:35 | 59 | 1 | 59.8167 | 0.00017989 | 0.00017 | 3.0074e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 453 | FUSE - ELEMENT/LINK (HV) | 2x3amp HV fuses blown due to lightning. reoplace 1 fuse barrel also | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.00017 | 11 | 2017 | 2016-05-16 | C | 1 | 0.00017 | 3.0074e-06
1 | 10998099 | 2016-05-16 23:02 | 2016-05-17 01:12 | 129 | 1 | 129.6167 | 0.00038981 | 0.00038 | 3.0074e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1584 | FUSE - ELEMENT/LINK (HV) | 2x3amp HV fuses blown at Transformer 1584. 1x3amp fuse blown at transformer 790 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.00038 | 11 | 2017 | 2016-05-16 | C | 1 | 0.00038 | 3.0074e-06
1 | 10998245 | 2016-05-16 23:42 | 2016-05-17 02:50 | 187 | 3 | 562.75 | 0.0016924 | 0.001665 | 9.0222e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | FC2151 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened, 2x Fuses at FC2151 6A. Lightning in area. Mike Cornelius attended. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.001665 | 11 | 2017 | 2016-05-16 | C | 3 | 0.001665 | 9.0222e-06
1 | 10998311 | 2016-05-16 23:59 | 2016-05-17 02:07 | 127 | 39 | 4989.4 | 0.015005 | 0.014653 | 0.00011729 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N57 | UNKNOWN | Non SCADA sectionaliser N57 Opened, possibly opened from feeder fault earlier in the evening. N57 closed | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.014653 | 11 | 2017 | 2016-05-16 | C | 39 | 0.014653 | 0.00011729
1 | 10998323 | 2016-05-17 00:01 | 2016-05-17 12:40 | 758 | 631 | 263988.95 | 0.79391 | 0.78822 | 0.0018977 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P47409 | CROSSARM - WHOLE ASSEMBLY | CB 1332 and CB XT30 tripped on E/F flags, line was patrolled and sectionalised and a broken x-arm was found at pole P47409, line was isolated at ABS,s XT 33 & XT36, at the same time insulators on ABS XT51 was also replaced to remove DNO Tag 160501. 1 X double cross & all hardware replaced. 1 X ground stake. 2r line patrol 0125. 2r repair 0956 | S3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 0.78822 | 33 | 2017 | 2016-05-17 | C | 631 | 0.78822 | 0.0018977
1 | 11001154 | 2016-05-17 03:07 | 2016-05-17 11:05 | 477 | 3 | 1432.85 | 0.0043091 | 0.004282 | 9.0221e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2424 | FUSE - ELEMENT/LINK (HV) | 3 x 3A HV Fuses due to lightning | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.004282 | 11 | 2017 | 2016-05-17 | C | 3 | 0.004282 | 9.0221e-06
1 | 11003925 | 2016-05-17 04:53 | 2016-05-17 08:46 | 232 | 18 | 676.5333 | 0.0020346 | 0.001872 | 5.4133e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T639 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Faultman found LV line down at transformer T639, on isolating transformer found the fuse holder to be broken, line was isolated at Fuses 7715 to replace the fuse holders. 1 x full set of fuse holders replaced with the fuses. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.001872 | 11 | 2017 | 2016-05-17 | C | 18 | 0.001872 | 5.4133e-05
1 | 11003980 | 2016-05-17 07:30 | 2016-05-17 07:57 | 27 | 49 | 1332.8 | 0.0040082 | 0.003566 | 0.00014736 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 9512 | NONE | Suspect Feeder Fault. AC Fail alarms to Reclosers / Sectionalisers beyond 9512. Comms lost to 9512. Sectionalised from recloser 9512. Found bamboo on line at pole W1506. Removed and relivened. Bad comms to RP17 had to get faultman to operate. | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.003566 | 11 | 2017 | 2016-05-17 | C | 49 | 0.003566 | 0.00014736
1 | 11004638 | 2016-05-17 05:46 | 2016-05-17 07:32 | 105 | 3 | 317.1 | 0.00095364 | 0.000926 | 9.0221e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | CA445 | FUSE - ELEMENT/LINK (HV) | 3 x 15A HV Fuses. Lightning | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.000926 | 11 | 2017 | 2016-05-17 | C | 3 | 0.000926 | 9.0221e-06
1 | 11004654 | 2016-05-17 05:54 | 2016-05-17 05:55 | 1 | 45 | 78.75 | 0.00023683 | 0 | 0.00013533 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Relates to 11003980 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-05-17 | C | 45 | 0 | 0.00013533
1 | 11004819 | 2016-05-17 06:12 | 2016-05-17 11:34 | 321 | 117 | 23887.9167 | 0.07184 | 0.070784 | 0.00035186 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M1924 | POLE | Fire called in Car V Pole. Event No. F2078929 Pole M1924. 195 Whites Rd, Putaruru. 7.12am Police called for eta - Tallia advised eta - FM is on Whites Road stationary. 2r line patrol 0747. 2r repair 0812 | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.070784 | 11 | 2017 | 2016-05-17 | C | 117 | 0.070784 | 0.00035186
1 | 11005466 | 2016-05-17 06:50 | 2016-05-17 09:00 | 129 | 93 | 9084.5667 | 0.027321 | 0.026481 | 0.00028871 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1154 | FUSE - ELEMENT/LINK (HV) | Reload reliven At FP1154. 2 x 8 A. Lightning | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.026481 | 11 | 2017 | 2016-05-17 | C | 93 | 0.026481 | 0.00028871
1 | 11005521 | 2016-05-17 07:02 | 2016-05-17 08:26 | 83 | 956 | 39835.9833 | 0.1198 | 0.11118 | 0.002875 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7396 | FUSE - ELEMENT/LINK (HV) | CB C894 tripped on O/C flags, line was patrolled and sectionalised and blown fuses was found at Fuses 7396, line was check and no fault was found suspect duck strike as lots of ducks flying around the area. 2 X 6 amp HV fuses replaced. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.11118 | 11 | 2017 | 2016-05-17 | C | 956 | 0.11118 | 0.002875
1 | 11006487 | 2016-05-17 07:03 | 2016-05-17 08:50 | 106 | 4 | 427.8667 | 0.0012868 | 0.00125 | 1.2029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 614 | FUSE - ELEMENT/LINK (HV) | 3 x 3A HV Fuses | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.00125 | 11 | 2017 | 2016-05-17 | C | 4 | 0.00125 | 1.2029e-05
1 | 11006633 | 2016-05-17 07:18 | 2016-05-17 08:41 | 82 | 3 | 248.4 | 0.00074703 | 0.000719 | 9.0221e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5125 | FUSE - ELEMENT/LINK (HV) | 2 x 2A HV Fuses due to lightning | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000719 | 11 | 2017 | 2016-05-17 | C | 3 | 0.000719 | 9.0221e-06
1 | 11006645 | 2016-05-17 07:18 | 2016-05-17 09:00 | 101 | 1 | 101.6 | 0.00030555 | 0.000296 | 3.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC4322 | FUSE - ELEMENT/LINK (HV) | 7.29am advsied Joanne at svs hub & emailed 2 x 6A HV Fuses | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.000296 | 11 | 2017 | 2016-05-17 | C | 1 | 0.000296 | 3.0073e-06
1 | 11006713 | 2016-05-17 07:22 | 2016-05-17 12:04 | 282 | 2 | 564 | 0.0016962 | 0.001678 | 6.0147e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC3414 | FUSE - ELEMENT/LINK (HV) | 3 x 3A HV Fuses | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.001678 | 11 | 2017 | 2016-05-17 | C | 2 | 0.001678 | 6.0147e-06
1 | 11006737 | 2016-05-17 07:24 | 2016-05-17 10:18 | 173 | 5 | 867.75 | 0.0026096 | 0.002564 | 1.5037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 797 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses due to lightning | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.002564 | 11 | 2017 | 2016-05-17 | C | 5 | 0.002564 | 1.5037e-05
1 | 11006957 | 2016-05-17 07:35 | 2016-05-17 09:13 | 97 | 5 | 488.4167 | 0.0014689 | 0.001423 | 1.5037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TA806 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001423 | 11 | 2017 | 2016-05-17 | C | 5 | 0.001423 | 1.5037e-05
1 | 11008068 | 2016-05-17 07:41 | 2016-05-17 15:10 | 449 | 1 | 449.3333 | 0.0013513 | 0.001342 | 3.0073e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3492 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer TC3492 Faulty. Transformer replaced. Livened at 1510 | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.001342 | 11 | 2017 | 2016-05-17 | C | 1 | 0.001342 | 3.0073e-06
1 | 11008179 | 2016-05-17 07:52 | 2016-05-17 09:44 | 112 | 3 | 336.9 | 0.0010132 | 0.000986 | 9.0221e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T7290 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000986 | 11 | 2017 | 2016-05-17 | C | 3 | 0.000986 | 9.0221e-06
1 | 11008798 | 2016-05-17 08:26 | 2016-05-17 11:00 | 153 | 2 | 307.5 | 0.00092477 | 0.000906 | 6.0147e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 461 | FUSE - ELEMENT/LINK (HV) | 3 x 3A HV Fuses due to lightning | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000906 | 11 | 2017 | 2016-05-17 | C | 2 | 0.000906 | 6.0147e-06
1 | 11009119 | 2016-06-03 12:10 | 2016-06-03 15:00 | 170 | 1 | 170 | 0.00051112 | 0.000502 | 3.0065e-06 | NAPA ID:18909 TP_WAIKINO GXP > WHANGAMATA SUB > WHIRITOA | 11 | Planned | 018909 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4095 | NONE | Replace transformer at TC4095. Works location: Waihi Whangamata Rd. WO 30010300 | F4 | WHIRITOA | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.000251 | 5.5 | 2017 | 2016-06-03 | B | 1 | 0.000502 | 3.0065e-06
1 | 11009138 | 2016-05-17 08:52 | 2016-05-17 10:15 | 83 | 1 | 83.0667 | 0.00024981 | 0.00024 | 3.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1275 | FUSE - ELEMENT/LINK (HV) | Reload reliven 3 x 2A Fuses. Caused by Burnt out LV Mains Entry Box. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.00024 | 11 | 2017 | 2016-05-17 | C | 1 | 0.00024 | 3.0073e-06
1 | 11009637 | 2016-06-02 09:00 | 2016-06-02 14:38 | 338 | 27 | 9126 | 0.027438 | 0.027194 | 8.1179e-05 | NAPA ID:18675 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018675 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1 | NONE | Replace poles ,hardware and conductor between TEMP34 & TEMP's 35-36. Works location: Minden Rd. WO 30002520 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.013597 | 5.5 | 2017 | 2016-06-02 | B | 27 | 0.027194 | 8.1179e-05
1 | 11010003 | 2016-06-02 08:49 | 2016-06-02 14:19 | 330 | 26 | 8580 | 0.025797 | 0.025562 | 7.8172e-05 | NAPA ID:20546 TP_KAITIMAKO GXP > WELCOME BAY SUB > POIKE | 11 | Planned | 020546 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 210742 | NONE | REPLACE HV POLE. Works location: Ohauiti Rd. WO 30018948 | F3/F4 | POIKE | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.012781 | 5.5 | 2017 | 2016-06-02 | B | 26 | 0.025562 | 7.8172e-05
1 | 11010043 | 2016-06-13 08:46 | 2016-06-21 13:30 | 11804 | 370 | 18322.4333 | 0.05508 | 0.051743 | 0.0016534 | NAPA ID:16158 TP_LINTON GXP > KAIRANGA SUB > TAKARO | 11 | Planned | 016158 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T6/171 | NONE | Carry out line gaps in the network to isolate switchgear 438/439/440. Change old switch to a new safelink CCC new number 10290. Return all gaps to normal, test, commission and put new switch into service. Works location: Amberly Ave. WO 10159894 | F3 | PIONEER | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.025871 | 5.5 | 2017 | 2016-06-13 | B | 370 | 0.051743 | 0.0016534
1 | 11010571 | 2016-06-07 09:12 | 2016-06-07 15:23 | 371 | 8 | 2968 | 0.008923 | 0.00885 | 2.4051e-05 | NAPA ID:18874 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018874 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 213090 | NONE | Replace poles ,hardware and conductor between TEMP70 & TEMP's 35-36. Works location: Minden Rd. WO 30002520 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.004425 | 5.5 | 2017 | 2016-06-07 | B | 8 | 0.00885 | 2.4051e-05
1 | 11011335 | 2016-06-02 09:54 | 2016-06-02 11:46 | 112 | 74 | 8288.1 | 0.024919 | 0.024251 | 0.00022249 | NAPA ID:19423 TP_WAIKINO GXP > WAIHI SUB > VICTORIA ST | 11 | Planned | 019423 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP179 | NONE | Work 1: Disconnect TP179 from network. Work 2: Re-Level TP179. Work 3: Re-Connect TP179 onto network. Works location: Colebrook Rd, Waihi. WO 30002257. Works unable to be completed due to incident. See Safety Report no. 625872. | F3 | VICTORIA ST | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.012126 | 5.5 | 2017 | 2016-06-02 | B | 74 | 0.024251 | 0.00022249
1 | 11011383 | 2016-06-09 08:49 | 2016-06-09 14:52 | 363 | 8 | 2904 | 0.0087304 | 0.008658 | 2.4051e-05 | NAPA ID:18882 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018882 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 213090 | NONE | Replace poles ,hardware and conductor between TEMP70 & TEMP's 35-36. Works location: Minden Rd. WO 30002520 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.004329 | 5.5 | 2017 | 2016-06-09 | B | 8 | 0.008658 | 2.4051e-05
1 | 11011482 | 2016-06-03 08:30 | 2016-06-03 14:26 | 356 | 19 | 6326 | 0.01902 | 0.018848 | 5.7125e-05 | NAPA ID:20648 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | 020648 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 615 | NONE | Carryout out maintenance: replace DNO160427 615 replace ABS + crossarm install insulator in stay wire. Works location: Motumaoho Rd, Morrinsville. WO 30026902 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.009424 | 5.5 | 2017 | 2016-06-03 | B | 19 | 0.018848 | 5.7125e-05
1 | 11011530 | 2016-06-13 09:16 | 2016-06-13 14:43 | 327 | 42 | 13734 | 0.041287 | 0.040907 | 0.00012626 | NAPA ID:18989 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018989 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 213108 | NONE | Replace poles ,hardware and conductor between TEMP70 & TEMP's 71-72. Works location: Minden Rd. WO 30002520 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.020453 | 5.5 | 2017 | 2016-06-13 | B | 42 | 0.040907 | 0.00012626
1 | 11011616 | 2016-05-17 11:42 | 2016-05-17 11:49 | 7 | 868 | 6076 | 0.018273 | 0.010441 | 0.0026104 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | CB 6 | NONE | Created during SIS 17957 - Switching. Loss of supply to CB 6 and CB 8, this happened CB 6 was closed and CB 8 was opened but CB 6 was showing closed but had a scan inhibit on it so CB 6 was not actually closed that caused loss of supply, this also caused CB 4 at Linton Army Camp to trip, supply was restored via the Auto Backfeed Scheme with Recloser 10055 closing. Scan inhibit was removed from CB 6 and CB 6 was closed, this restored the supply to CB 6 and CB 8 (CB 6 backfeeding CB 8). CB 4 was restored to normal config when supply was restored to CB 6. Scan inhibit was put on by Paul Douglas and was not removed when CB 6 was restored to the service position, the scan inhibit may have been remove after the switch but may have been put back on to stop causing alarm because CB 6 has faulty indication on it by Paul. | F2 | LINTON EXPRESSWAY | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.010441 | 11 | 2017 | 2016-05-17 | C | 868 | 0.010441 | 0.0026104
1 | 11012596 | 2016-06-15 09:09 | 2016-06-15 15:43 | 394 | 42 | 16548 | 0.049744 | 0.049365 | 0.00012625 | NAPA ID:18990 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018990 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Temp 70 | NONE | Replace poles ,hardware and conductor between TEMP70 & TEMP's 71-72. Works location: Minden Rd. WO 30002520 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.024682 | 5.5 | 2017 | 2016-06-15 | B | 42 | 0.049365 | 0.00012625
1 | 11015293 | 2016-06-17 09:08 | 2016-06-17 15:30 | 382 | 39 | 14898 | 0.044783 | 0.044431 | 0.00011723 | NAPA ID:18995 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018995 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-141 | NONE | Replace poles ,hardware and conductor between SD3-141 & TEMP's 71-72. Works location: Minden Rd. WO 30002520 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.022215 | 5.5 | 2017 | 2016-06-17 | B | 39 | 0.044431 | 0.00011723
1 | 11015583 | 2016-06-11 10:00 | 2016-06-11 11:07 | 67 | 2 | 134 | 0.00040284 | 0.000384 | 6.0124e-06 | NAPA ID:19378 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | 019378 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links R40 | NONE | To replace 11kv x arm. Works location: Bridge Rd. WO 30025837 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000192 | 5.5 | 2017 | 2016-06-11 | B | 2 | 0.000384 | 6.0124e-06
1 | 11015871 | 2016-05-17 11:15 | 2016-05-17 13:05 | 110 | 19 | 2090 | 0.0062854 | 0.006113 | 5.714e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3948T | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | 2 x HV Fuses and Bases replaced. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.006113 | 11 | 2017 | 2016-05-17 | C | 19 | 0.006113 | 5.714e-05
1 | 11016253 | 2016-05-17 17:15 | 2016-05-17 18:30 | 75 | 5 | 375 | 0.0011278 | 0.001082 | 1.5037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771400 | CROSSARM - WHOLE ASSEMBLY | This pole has a rotten HV Xarm that is about to fall off. Urgent. Garry leaving site and 2x FM to replace him and replace crossarm. Faultman found rotten cross arm on pole 771400, line was isolated at Fuses 2888 to replace the cross arm. 1 X 11KV cross arm & all hardware | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001082 | 11 | 2017 | 2016-05-17 | C | 5 | 0.001082 | 1.5037e-05
1 | 11016324 | 2016-06-07 10:36 | 2016-06-07 15:15 | 279 | 7 | 1953 | 0.0058715 | 0.005808 | 2.1045e-05 | NAPA ID:19319 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 019319 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3033 | NONE | Upgrade TC3033 change Xarms Re-tension LV conductor. Works location: Canal West Rd. WO 30017312 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002904 | 5.5 | 2017 | 2016-06-07 | B | 7 | 0.005808 | 2.1045e-05
1 | 11016415 | 2016-05-17 15:14 | 2016-05-17 17:16 | 121 | 1 | 121.5333 | 0.0003655 | 0.000356 | 3.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5883 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses due to lightning | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000356 | 11 | 2017 | 2016-05-17 | C | 1 | 0.000356 | 3.0073e-06
1 | 11018884 | 2016-05-18 06:13 | 2016-05-18 19:45 | 812 | 1 | 812.25 | 0.0024427 | 0.002433 | 3.0073e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5338E | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer 5338E replaced 15kVA / 3 Phase Transformer | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.002433 | 11 | 2017 | 2016-05-18 | C | 1 | 0.002433 | 3.0073e-06
1 | 11019197 | 2016-05-18 08:58 | 2016-05-18 12:06 | 188 | 14 | 2632 | 0.0079153 | 0.007788 | 4.2103e-05 |  | 22 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 805424 | CONDUCTOR - REPAIR/REHANG | plz check oms 11019543 related? part power nxt tx z30 232 Porewa Road, Marton - advised James about this at 8.53am he advised he has found fault and just getting in contact with control. Faultman found fuse blown at Fuses 538 and line down at pole 805424,line was isolated at Fuses 538 repair the line. 40 meters x 100mm copper conductor used. 4 x sleeves used & 2 meters of binder wire. | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.007788 | 22 | 2017 | 2016-05-18 | C | 14 | 0.007788 | 4.2103e-05
1 | 11019636 | 2016-05-18 10:15 | 2016-05-18 12:36 | 141 | 30 | 4230 | 0.012721 | 0.01245 | 9.022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | MA233 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, NOT ALL PHASES | Caller on site advise 2 lines down on the road. Advised control - 9am advised Tallia at svs hub & emailed. Outage needed past Fuses MA233. Replaced 5m conductor, 3 x 10 A fuses, 4 x sleeves. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.01245 | 11 | 2017 | 2016-05-18 | C | 30 | 0.01245 | 9.022e-05
1 | 11019644 | 2016-05-18 07:00 | 2016-05-18 08:52 | 111 | 6 | 669.8 | 0.0020143 | 0.00196 | 1.8044e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8300 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.00196 | 11 | 2017 | 2016-05-18 | C | 6 | 0.00196 | 1.8044e-05
1 | 11019739 | 2016-05-18 09:05 | 2016-05-18 10:00 | 55 | 363 | 20134.4 | 0.060551 | 0.057275 | 0.0010917 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | CB LI2 | UNKNOWN | Line patrolled, no fault found. Feeder manually reclosed, OK. 1r line patrol only | F4 | PATEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.057275 | 11 | 2017 | 2016-05-18 | C | 363 | 0.057275 | 0.0010917
1 | 11020274 | 2016-05-18 09:15 | 2016-05-18 13:29 | 253 | 4 | 1015.0667 | 0.0030526 | 0.003016 | 1.2029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TA113 | FUSE - ELEMENT/LINK (HV) | Please check if OMS 11020444 1398 Ihaia Road, Part power & OMS 11020814 1331 Ihaia Road, Opunake. 2 x 3A HV Fuses due to lightning. | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.003016 | 11 | 2017 | 2016-05-18 | C | 4 | 0.003016 | 1.2029e-05
1 | 11020844 | 2016-05-18 10:17 | 2016-05-18 11:17 | 60 | 23 | 1380 | 0.0041501 | 0.003942 | 6.9168e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 717505 | CONDUCTOR - REPAIR/REHANG | 9.31am advised Shannon at svs hub & emailed & taken to control. Line down at Pole 717505. Joined and re hung 1 x 8A Fuse 1mtr conductor and 2 sleeves | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.003942 | 11 | 2017 | 2016-05-18 | C | 23 | 0.003942 | 6.9168e-05
1 | 11020865 | 2016-05-18 09:30 | 2016-05-18 18:50 | 559 | 362 | 12352.4333 | 0.037148 | 0.033881 | 0.0010887 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4677T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 9.35am advised Tans at svs hub & emailed & advised Control. Transformer 4677T Faulty. To be Replaced. Replaced 10kVA Transformer with 15kVA / 1 Phase transformer. | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.033881 | 11 | 2017 | 2016-05-18 | C | 362 | 0.033881 | 0.0010887
1 | 11020956 | 2016-05-18 09:34 | 2016-05-18 12:15 | 160 | 2 | 321.5667 | 0.00096706 | 0.000949 | 6.0146e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2213 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse due to lightning | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000949 | 11 | 2017 | 2016-05-18 | C | 2 | 0.000949 | 6.0146e-06
1 | 11021319 | 2016-05-18 09:49 | 2016-05-18 13:20 | 211 | 77 | 15713.1333 | 0.047255 | 0.046559 | 0.00023156 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | 4832 | UNKNOWN | Line patrol needed due to 3 A/R events in the last half hour. Line Patrolled but nothing could be found. Suspect Lightning or High Winds | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.046559 | 11 | 2017 | 2016-05-18 | C | 77 | 0.046559 | 0.00023156
1 | 11021919 | 2016-05-18 10:12 | 2016-05-18 11:16 | 63 | 15 | 956.5 | 0.0028765 | 0.002741 | 4.511e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 8421 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses at 8421 and 3 x 3A at 8471 - reflected under this outage. All transformers within this job are beyond Fuses 8421. | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.002741 | 11 | 2017 | 2016-05-18 | C | 15 | 0.002741 | 4.511e-05
1 | 11022512 | 2016-05-18 10:26 | 2016-05-18 11:14 | 47 | 2 | 95.9667 | 0.0002886 | 0.00027 | 6.0146e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4192T | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.00027 | 6.6 | 2017 | 2016-05-18 | C | 2 | 0.00027 | 6.0146e-06
1 | 11022678 | 2016-05-18 10:40 | 2016-05-19 14:04 | 1643 | 1 | 1643.6 | 0.0049428 | 0.004933 | 3.0073e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4252T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | FM advised that this tx 4252T is faulty and needs replacing 3:20pm Sammy from hub advised Dennis has left site and is enroute to another job. 5.08pm, Sammy from hub called to say customer is happy to be off overnight, so tx can be replaced tomorrow. 5.12pm, called customer (Helen 027 685 0212) to ask if they are happy to have the power off overnight - customer said happy for the house to be off as it is vacant but still needs power to the farm 19:57 - Confirmed with the customer that they are happy to be without power over night until repairs are made tomorrow Transformer replaced with 15kVA 3ph. | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.004933 | 11 | 2017 | 2016-05-18 | C | 1 | 0.004933 | 3.0073e-06
1 | 11023140 | 2016-05-18 11:11 | 2016-05-18 12:42 | 90 | 1 | 90.8667 | 0.00027327 | 0.000264 | 3.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4752T | FUSE - ELEMENT/LINK (HV) | Transformer 4752T replaced 2 x 6A HV Fuses. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000264 | 11 | 2017 | 2016-05-18 | C | 1 | 0.000264 | 3.0073e-06
1 | 11023194 | 2016-05-18 11:15 | 2016-05-18 13:20 | 124 | 4 | 498.2667 | 0.0014985 | 0.001462 | 1.2029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4872T | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.001462 | 11 | 2017 | 2016-05-18 | C | 4 | 0.001462 | 1.2029e-05
1 | 11023984 | 2016-05-18 11:46 | 2016-05-18 13:23 | 97 | 65 | 6305 | 0.018961 | 0.018374 | 0.00019548 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 745705 | CONDUCTOR - REPAIR/REHANG | Line down lying on the timber. insulator has come off and sparking and the top the timber is burning. 11.15am advised Joanne at svs hub & sent email. & advised control. ETA is 15 mins. 11.30am advised Fire Service eta 15mins. While trying to move the job to the correct device number the system cancelled the job and completed the crew. I have placed another crew request to get Neil back on the job but he did not leave site.1 x 11kV Pin insulator and Binder | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.018374 | 11 | 2017 | 2016-05-18 | C | 65 | 0.018374 | 0.00019548
1 | 11024128 | 2016-05-18 11:55 | 2016-05-18 19:55 | 480 | 1 | 480.15 | 0.001444 | 0.001434 | 3.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3360T | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6Amp HV Fuses | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.001434 | 11 | 2017 | 2016-05-18 | C | 1 | 0.001434 | 3.0073e-06
1 | 11024169 | 2016-05-18 09:59 | 2016-05-18 12:01 | 122 | 3 | 367 | 0.0011037 | 0.001076 | 9.0219e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T1380 | FUSE - ELEMENT/LINK (HV) | 3 x 3A HV Fuses | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001076 | 11 | 2017 | 2016-05-18 | C | 3 | 0.001076 | 9.0219e-06
1 | 11024320 | 2016-05-18 15:28 | 2016-05-18 15:54 | 26 | 41 | 1066 | 0.0032058 | 0.002835 | 0.0001233 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4388 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Outage needed past ABS 413. Replace 1 x Fuse & Base. Relivened OK | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002835 | 11 | 2017 | 2016-05-18 | C | 41 | 0.002835 | 0.0001233
1 | 11024458 | 2016-05-18 12:39 | 2016-05-18 14:25 | 106 | 349 | 7440.4667 | 0.022376 | 0.019227 | 0.00027968 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | TP272 | CIRCUIT BREAKER (HV) | ( POA 5 ) Rec RC17 tripped, A/R, Sectionaliser 9380 tripped L/O Possible tree contact at transformer TP272 faultman to defect | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.019227 | 11 | 2017 | 2016-05-18 | C | 349 | 0.019227 | 0.00027968
1 | 11024826 | 2016-05-18 12:41 | 2016-05-18 15:46 | 184 | 2 | 369.4667 | 0.0011111 | 0.001093 | 6.0146e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3030T | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.001093 | 6.6 | 2017 | 2016-05-18 | C | 2 | 0.001093 | 6.0146e-06
1 | 11024837 | 2016-05-18 15:10 | 2016-05-18 16:02 | 52 | 199 | 10348 | 0.03112 | 0.029324 | 0.00059846 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4-028 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replace fault fuses at Tx TC4-028. 1 x base and 1 x 15a fuse. Isolate at SC4653 | F3 | BELLEVUE RD | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 0.029324 | 11 | 2017 | 2016-05-18 | C | 199 | 0.029324 | 0.00059846
1 | 11025502 | 2016-05-20 09:49 | 2016-05-20 12:15 | 146 | 11 | 1606 | 0.0048296 | 0.00473 | 3.308e-05 | NAPA ID:20878 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 020878 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole C1278 | NONE | Replacevery rotten X Arms at pole C1278 and TC2610. Works location: Factory Rd, Waihou. WO 30007220 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.002365 | 5.5 | 2017 | 2016-05-20 | B | 11 | 0.00473 | 3.308e-05
1 | 11025579 | 2016-05-18 10:34 | 2016-05-18 13:09 | 154 | 10 | 1547.3333 | 0.0046533 | 0.004563 | 3.0073e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | M9 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuse due to lightning | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.004563 | 11 | 2017 | 2016-05-18 | C | 10 | 0.004563 | 3.0073e-05
1 | 11025666 | 2016-05-18 13:14 | 2016-05-18 15:40 | 146 | 1 | 146.2333 | 0.00043977 | 0.00043 | 3.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4862W | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuse | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.00043 | 11 | 2017 | 2016-05-18 | C | 1 | 0.00043 | 3.0073e-06
1 | 11025896 | 2016-05-18 13:33 | 2016-05-18 15:49 | 136 | 351 | 26963.8667 | 0.081089 | 0.077922 | 0.0010556 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761139 | INSULATOR | Line down at Pole 761139. High Winds 1 x 11kV Pin Insulator replaced.and Binder | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.077922 | 6.6 | 2017 | 2016-05-18 | C | 351 | 0.077922 | 0.0010556
1 | 11026379 | 2016-05-18 13:46 | 2016-05-18 13:48 | 2 | 1 | 2.3833 | 7.1674e-06 | 0 | 3.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/12 | FUSE - ELEMENT/LINK (HV) | Robin was passing and noticed 2x fuses out. Site checked and relivened OK. Replaced 2 x 20A fuse. Cause unknown. | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-05-18 | C | 1 | 0 | 3.0073e-06
1 | 11027502 | 2016-06-13 09:45 | 2016-06-13 15:30 | 345 | 30 | 10350 | 0.031114 | 0.030843 | 9.0185e-05 | NAPA ID:20827 TP_OPUNAKE GXP > TASMAN SUB | 11 | Planned | 020827 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 713864 | NONE | Replace Pole713864 & ABS 6681 Replace 11KV cable to Transformer T2330. Live Line break created to minimise SAIDI impact. NOTE there is only ONE line break and that is on the TA2 circuit. SAFETY measures on the TA8 feeder for the live line only. Works location: Lanyard St, Opunake. WO 30017990 | F3 | OPUNAKE | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.015421 | 5.5 | 2017 | 2016-06-13 | B | 30 | 0.030843 | 9.0185e-05
1 | 11027582 | 2016-05-18 14:05 | 2016-05-18 18:13 | 248 | 178 | 44253.7667 | 0.13309 | 0.13148 | 0.0005353 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 810493 | CONDUCTOR - REPAIR/REHANG | Faultman found CB C642/2 open and on a patrol faultman found logging contractor had brought down a tree through the lines, line was isolated at ABS C642/1 & Links C642/6 to repair the lines from pole 810493. NDR:21953. Materials Used: 20 meters Goffer conductor, 4 X tension sleeves & 6 non tension sleeves. 2r repair 1559. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.13148 | 11 | 2017 | 2016-05-18 | C | 178 | 0.13148 | 0.0005353
1 | 11027788 | 2016-05-18 14:55 | 2016-05-18 18:50 | 234 | 2 | 469.6667 | 0.0014124 | 0.001394 | 6.0146e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T1405 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001394 | 11 | 2017 | 2016-05-18 | C | 2 | 0.001394 | 6.0146e-06
1 | 11028296 | 2016-05-18 13:54 | 2016-05-18 14:58 | 64 | 4 | 257.8 | 0.00077529 | 0.000739 | 1.2029e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3761T | FUSE - ELEMENT/LINK (HV) | 3 x 3A HV Fuses | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000739 | 6.6 | 2017 | 2016-05-18 | C | 4 | 0.000739 | 1.2029e-05
1 | 11030261 | 2016-05-18 18:05 | 2016-05-18 22:38 | 273 | 617 | 53705.7167 | 0.16151 | 0.15594 | 0.0018555 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 209661 | CONDUCTOR - REPAIR/REHANG | OMO CB2 tripped C Ph O/C, A/R. Sectionalised and found line down at pole 209661. Isolated between ABS SC2-024 & SD2-004. Repaired line & relivened. 2r line patrol 1951. 2r repair 2129 | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.15594 | 11 | 2017 | 2016-05-18 | C | 617 | 0.15594 | 0.0018555
1 | 11031598 | 2016-05-18 18:43 | 2016-05-18 19:50 | 66 | 1578 | 71470.7167 | 0.21494 | 0.2007 | 0.0047456 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB 10306/2 tripped contact NOC. Sectionalised & partial patrol of O/H. No fault found 2r line patrol 1915 no repair | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.2007 | 11 | 2017 | 2016-05-18 | C | 1578 | 0.2007 | 0.0047456
1 | 11035525 | 2016-05-18 19:17 | 2016-05-18 22:35 | 198 | 92 | 18223.6667 | 0.054805 | 0.053974 | 0.00027667 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C642 | UNKNOWN | C642 Tripped. Non Telemetered. Lee Wilton attended this fault. Job that Adam Whale was attending at Te Awaiti Rd and this one rolled up together? Partial patrol carried out with no cause found. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.053974 | 11 | 2017 | 2016-05-18 | C | 92 | 0.053974 | 0.00027667
1 | 11035602 | 2016-05-18 19:23 | 2016-05-18 21:06 | 102 | 1 | 102.55 | 0.0003084 | 0.000299 | 3.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1541 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2Amp HV Links | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000299 | 11 | 2017 | 2016-05-18 | C | 1 | 0.000299 | 3.0073e-06
1 | 11039955 | 2016-05-18 21:05 | 2016-05-18 21:28 | 22 | 870 | 19662 | 0.05913 | 0.05128 | 0.0026164 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | N/A - NOT APPLICABLE | UNKNOWN | CB 5 L/O. Recloser 9225 opened & 9405 Closed via back feed scheme. Reclosed CB 5. Very windy in area | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.05128 | 11 | 2017 | 2016-05-18 | C | 870 | 0.05128 | 0.0026164
1 | 11040947 | 2016-05-18 21:29 | 2016-05-18 23:26 | 117 | 7 | 820.8667 | 0.0024686 | 0.002405 | 2.1051e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W2305 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer W2305 Two HV fuses blown. Attempted reliven but failed due to blown transformer. Work area isolated at Fuses WH267 to enable transformer to be replaced. Replaced 15kVA, 3 Phase transformer. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.002405 | 11 | 2017 | 2016-05-18 | C | 7 | 0.002405 | 2.1051e-05
1 | 11045345 | 2016-05-19 04:39 | 2016-05-19 06:03 | 84 | 495 | 26604.0333 | 0.080006 | 0.07554 | 0.0016841 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB 23 A/R, L/O, E/F. Also was backfeeding part of Sanson CB8 via ABS B8. Sectionalised & partially patrolled. No fault found 2r line patrol 0522 no repair | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.07554 | 11 | 2017 | 2016-05-19 | C | 495 | 0.07554 | 0.0016841
1 | 11047157 | 2016-05-19 06:06 | 2016-05-19 07:50 | 104 | 44 | 4576.7333 | 0.013764 | 0.013366 | 0.00013232 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | SC2-017 | FUSE - ELEMENT/LINK (HV) | advised 6.42am Joanne at svs hub to send FM to Fuses SC2 017 as we have 2 other no power jobs that have come in. - OMS 11047229 & OMS 11047242. Reload Reliven at Fuses SC2-017 2 x 25A due to line clash. | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.013366 | 11 | 2017 | 2016-05-19 | C | 44 | 0.013366 | 0.00013232
1 | 11047273 | 2016-05-19 06:47 | 2016-05-19 08:48 | 121 | 254 | 11176.3667 | 0.033611 | 0.031318 | 0.00076385 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P03919 | CONDUCTOR - REPLACE LESS THAN 1 SPAN, NOT ALL PHASES | Recloser H131 - Trip A B & C OC. Lines down 62 Linton Station Rd. Fire service Awaiting ETA. Isolation required drom ABS H139 with remainder of feeder relivened. 2 Conductors were down caused by a bird strike (Duck). Required 3m conductor and 4 sleeves. Relivened OK. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.031318 | 11 | 2017 | 2016-05-19 | C | 254 | 0.031318 | 0.00076385
1 | 11048532 | 2016-06-01 08:30 | 2016-06-01 14:42 | 372 | 114 | 42408 | 0.12751 | 0.12648 | 0.00034276 | NAPA ID:20871 TP_MASTERTON GXP > CLAREVILLE SUB > TAVERNER ST | 11 | Planned | 020871 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 820020 | NONE | replace c409/1, c409/6 & c409/4 and poles 820252 and 820254. Matarawa Road, Carterton, Clareville. W/O 30026093. | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.063239 | 5.5 | 2017 | 2016-06-01 | B | 114 | 0.12648 | 0.00034276
1 | 11048614 | 2016-06-07 10:46 | 2016-06-07 12:28 | 101 | 45 | 4554.75 | 0.013693 | 0.013287 | 0.00013529 | NAPA ID:20859 TP_OHAKUNE GXP > TP_OHAKUNE > PARAPARA | 11 | Planned | 020859 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 903 | NONE | Replace cracked insulator & fit new arm & pins. Works Location: Parapara Road, TP Ohakune. W/O 30009559. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.0066435 | 5.5 | 2017 | 2016-06-07 | B | 45 | 0.013287 | 0.00013529
1 | 11048704 | 2016-06-15 08:20 | 2016-06-15 15:10 | 410 | 22 | 9020 | 0.027115 | 0.026916 | 6.6133e-05 | NAPA ID:20554 TP_MASTERTON GXP > TINUI SUB > ANNEDALE | 11 | Planned | 020554 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | DDO's 7893 | NONE | Change 2 x existing transformer. Waitawhiti Station, Tinui. W/O 30024868. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.013458 | 5.5 | 2017 | 2016-06-15 | B | 22 | 0.026916 | 6.6133e-05
1 | 11048768 | 2016-06-16 09:45 | 2016-06-16 16:00 | 375 | 22 | 8250 | 0.0248 | 0.024601 | 6.6132e-05 | NAPA ID:20556 TP_MASTERTON GXP > TINUI SUB > ANNEDALE | 11 | Planned | 020556 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | DDO's 7893 | NONE | Change 2 x existing transformer. Waitawhiti Station, Tinui. W/O 30024868. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.012301 | 5.5 | 2017 | 2016-06-16 | B | 22 | 0.024601 | 6.6132e-05
1 | 11048960 | 2016-06-15 09:27 | 2016-06-15 15:09 | 342 | 10 | 3423.1667 | 0.01029 | 0.0102 | 3.0061e-05 | NAPA ID:18814 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 018814 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S69 | NONE | To replace multiple poles, crossarms and new fuse sites. Work Location: Bruces Road and Fenemore Road, Masterton, Akura. W/O 30019523. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0051 | 5.5 | 2017 | 2016-06-15 | B | 10 | 0.0102 | 3.0061e-05
1 | 11049005 | 2016-05-19 10:50 | 2016-05-19 11:32 | 42 | 4 | 168 | 0.00050522 | 0.000469 | 1.2029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 851359 | CROSSARM - COMPONENT(S) ONLY | 9.40am advised at SVS hub & emailed & advised Control. Replaced 1x centre bolt in cross arm on pole 851359 | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000469 | 11 | 2017 | 2016-05-19 | C | 4 | 0.000469 | 1.2029e-05
1 | 11049776 | 2016-05-19 14:14 | 2016-05-19 14:51 | 37 | 17 | 629 | 0.0018916 | 0.001738 | 5.1124e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 723955 - Need fuse LI 107 to be opened | JUMPER | 11.25am advised Tallia at svs hub & emailed. advised control Please also check OMS 11050187 - 473 Main South Road Section of line from fuses LI107 isolated to repair jumper on transformer L4060 | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.001738 | 11 | 2017 | 2016-05-19 | C | 17 | 0.001738 | 5.1124e-05
1 | 11050022 | 2016-06-14 09:00 | 2016-06-14 14:47 | 347 | 52 | 18044 | 0.054242 | 0.053773 | 0.00015632 | NAPA ID:20833 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 020833 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | H136 | NONE | Cut trees away from 11KV line rebind poles as required. Scotts road, Linton, Turieta. W/O 30017468. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.026887 | 5.5 | 2017 | 2016-06-14 | B | 52 | 0.053773 | 0.00015632
1 | 11050093 | 2016-05-19 11:56 | 2016-05-19 12:09 | 12 | 39 | 494 | 0.0014856 | 0.001133 | 0.00011728 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | S530 | NONE | Urgent outage to remove trees from lines. Isolation required between ABS S530, S509 and S501 with backfeeds at ABS S570 and S556. Vegetation had grown up through 11kV and only required short outage to clear. Relivened OK. (Work carried out by J.Hall and Treescape). | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.001133 | 11 | 2017 | 2016-05-19 | C | 39 | 0.001133 | 0.00011728
1 | 11050207 | 2016-06-08 09:00 | 2016-06-08 15:12 | 372 | 35 | 13020 | 0.039143 | 0.038827 | 0.00010522 | NAPA ID:20579 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 020579 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC379 | NONE | Puriri Pole Renewals Shut 1. Between IC379 and IC545. Work on Poles S0049, S0234, S0486, S0487, S0209, S0211,S0216, S12884, S0246, S12878. Works location: Paeroa Kopu Rd. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.019414 | 5.5 | 2017 | 2016-06-08 | B | 35 | 0.038827 | 0.00010522
1 | 11050904 | 2016-06-10 09:15 | 2016-06-10 13:05 | 230 | 2 | 460 | 0.0013829 | 0.001364 | 6.0125e-06 | NAPA ID:20583 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 020583 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S0249 | NONE | Puriri Pole Renewals Shut 4. Live Line Cut jumpers on S0249. Work From Cut jumpers on 0249, Poles S0466, S0467, S12744, S12748, S0473, S0475, S0249. Works location: Neavesville Rd. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.000682 | 5.5 | 2017 | 2016-06-10 | B | 2 | 0.001364 | 6.0125e-06
1 | 11054941 | 2016-05-19 14:07 | 2016-05-19 17:19 | 192 | 1 | 192.45 | 0.00057875 | 0.000569 | 3.0072e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3762T | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a HV Fuses @ transformer 3762T | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000569 | 6.6 | 2017 | 2016-05-19 | C | 1 | 0.000569 | 3.0072e-06
1 | 11055001 | 2016-06-14 09:30 | 2016-06-14 14:59 | 329 | 43 | 14147 | 0.042527 | 0.042139 | 0.00012926 | NAPA ID:20585 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 020585 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S0308 | NONE | Puriri Pole Renewals Shut 5. Beyond IC2612. Work on Poles S0308, S0309, S0313, S12762, S0318, S12758, S0305, S12773, S12774, S12777, S12784, S12789, S0441, S0450, S12798, S12799. Works location: Neavesville Rd. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.02107 | 5.5 | 2017 | 2016-06-14 | B | 43 | 0.042139 | 0.00012926
1 | 11055063 | 2016-05-19 14:29 | 2016-05-19 16:29 | 119 | 90 | 10205.4667 | 0.030691 | 0.029878 | 0.00027066 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C926 | UNKNOWN | 1R - Patrol please, Tuhitarata CB C926 tripping. Area sectionalised / patrolled but all restored OK. 2r line patrol 1602 no repair | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.029878 | 11 | 2017 | 2016-05-19 | C | 90 | 0.029878 | 0.00027066
1 | 11055110 | 2016-06-16 09:02 | 2016-06-16 15:45 | 403 | 41 | 16539.4 | 0.049718 | 0.049347 | 0.00012325 | NAPA ID:20591 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 020591 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC526 | NONE | Puriri Pole Renewals Shut 7. Work Area 9688 to IC526. Work on Poles S0328, S12821, S0343, S12822, S0347, S0349, S0350, S12825, S0351, S12827, S0372, S0353, S12843, S12845. Works location: Hwy 26, Paeroa Kopu Rd. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.024674 | 5.5 | 2017 | 2016-06-16 | B | 41 | 0.049347 | 0.00012325
1 | 11055692 | 2016-06-21 09:15 | 2016-06-21 14:53 | 338 | 19 | 6422 | 0.019303 | 0.019131 | 5.711e-05 | NAPA ID:20592 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 020592 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FC1450 | NONE | Puriri Pole Renewals Shut 10. Work Area beyond Fc1450. Work on Poles N2043,N13133, N2046, N13112, N13119, N2048, N13105, N2058, N2071, N13110, N2077, N2253, N2255, N2083, N2256. Works location: Omahu Valley, Thames. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.0095655 | 5.5 | 2017 | 2016-06-21 | B | 19 | 0.019131 | 5.711e-05
1 | 11055696 | 2016-06-17 09:35 | 2016-06-17 15:35 | 360 | 5 | 1776 | 0.0053386 | 0.005293 | 1.503e-05 | NAPA ID:19310 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | 019310 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P11059 | NONE | to replace 11kv poles and run new 11kv conductor. Works location: Doughertys Rd. WO 10162324 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.0026465 | 5.5 | 2017 | 2016-06-17 | B | 5 | 0.005293 | 1.503e-05
1 | 11064009 | 2016-05-20 00:54 | 2016-05-20 10:38 | 584 | 8 | 4675.7333 | 0.014061 | 0.013988 | 2.4058e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 737927 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, ALL PHASES | Recloser 6551 tripped on B phase O/C flags, line was patrolled and faultman found a Big tree had come done and broken the lines and is laying across the road at pole 737927, line was isolated at ABS 6547 & Links 6540. Outage required past Recloser 6551 to remove trees from the lines and make repairs, relivened OK. Replaced 50m conductor, 10 x sleeves. NDR: 43371 | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.013988 | 6.6 | 2017 | 2016-05-20 | C | 8 | 0.013988 | 2.4058e-05
1 | 11072114 | 2016-06-15 09:26 | 2016-06-15 13:35 | 249 | 51 | 12699 | 0.038174 | 0.037714 | 0.00015331 | NAPA ID:20542 TP_KOPU GXP > THAMES SUB > TOTARA | 11 | Planned | 020542 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 9930 | NONE | Install new SWER Recloser 9930/2 and Pole. Works location: Kaueranga Valley Rd, Thames. WO 10148359 | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.018857 | 5.5 | 2017 | 2016-06-15 | B | 51 | 0.037714 | 0.00015331
1 | 11072694 | 2016-05-20 09:35 | 2016-05-20 14:00 | 265 | 1 | 265.3667 | 0.00079802 | 0.000788 | 3.0072e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4116T | FUSE - ELEMENT/LINK (HV) | Reload Reliven 2 x 2A Lightening | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.000788 | 11 | 2017 | 2016-05-20 | C | 1 | 0.000788 | 3.0072e-06
1 | 11073706 | 2016-05-20 09:37 | 2016-05-20 12:17 | 159 | 495 | 33001.75 | 0.099244 | 0.094778 | 0.0027576 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36227 | INSULATOR | Tripping on Kairanga CB23 on EF IDMT. Feeder sectionalised and patrolled with a cracked insulator found. Isolation required from ABS B11. 1 Insulator replaced and jointer. Crossarm defected. Relivened OK. NOTE: This feeder also backfeeding part of Sanson CB8 due to Sanson backfeed switching. | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.094778 | 11 | 2017 | 2016-05-20 | C | 495 | 0.094778 | 0.0027576
1 | 11077484 | 2016-05-20 11:02 | 2016-05-20 12:20 | 78 | 3 | 234.9 | 0.0007064 | 0.000679 | 9.0217e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 762 | FUSE - ELEMENT/LINK (HV) | Reload. 2 x 2A. Lightning | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000679 | 11 | 2017 | 2016-05-20 | C | 3 | 0.000679 | 9.0217e-06
1 | 11089331 | 2016-05-18 10:29 | 2016-05-18 17:30 | 421 | 2 | 842 | 0.0025322 | 0.002514 | 6.0146e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3186 | FUSE - ELEMENT/LINK (HV) | 2 x3amp fuses weather | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.002514 | 6.6 | 2017 | 2016-05-18 | C | 2 | 0.002514 | 6.0146e-06
1 | 11089343 | 2016-05-18 10:29 | 2016-05-18 17:30 | 421 | 1 | 421 | 0.0012661 | 0.001257 | 3.0073e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6365 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp fuses weather | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001257 | 6.6 | 2017 | 2016-05-18 | C | 1 | 0.001257 | 3.0073e-06
1 | 11089347 | 2016-05-18 10:29 | 2016-05-18 17:30 | 421 | 1 | 421 | 0.0012661 | 0.001257 | 3.0073e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6104 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp fuses weather | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001257 | 6.6 | 2017 | 2016-05-18 | C | 1 | 0.001257 | 3.0073e-06
1 | 11089351 | 2016-06-13 09:24 | 2016-06-13 11:41 | 137 | 71 | 9727 | 0.029241 | 0.0286 | 0.00021344 | NAPA ID:19320 TP_BUNNYTHORPE GXP > TP_BUNNYTHORPE > TWP-KEITH ST 33KV | 11 | Planned | 019320 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P44139 | NONE | Isolate 11kV and 33kV lines to change contacts at ABS 3214, remove ABS Z222 and jumper through, change insulators at pole P44139 and replace a transformer on the windfarm T7. Works location: FItzherbit East Rd. WO 30015890 | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.0143 | 5.5 | 2017 | 2016-06-13 | B | 71 | 0.0286 | 0.00021344
1 | 11090222 | 2016-05-16 22:18 | 2016-05-17 01:22 | 184 | 6 | 1104 | 0.0033202 | 0.003266 | 1.8044e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8159 | FUSE - ELEMENT/LINK (HV) | 3 x 2amp fuses weather | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.003266 | 11 | 2017 | 2016-05-16 | C | 6 | 0.003266 | 1.8044e-05
1 | 11090951 | 2016-06-16 09:39 | 2016-06-16 15:22 | 343 | 5 | 1715 | 0.0051553 | 0.00511 | 1.503e-05 | NAPA ID:20922 TP_GREYTOWN GXP > FEATHERSTON SUB > DAIRY FACTORY | 11 | Planned | 020922 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Fuses 7228 | NONE | drop 11kv and lv lines at t961 so trees can be cut,re hang 11kv line after trees cleared and correct up sag as it is very uneven,re hang new lv ferret conductor. Works location: Te Marie Rd, Featherston. WO 30026936 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.002555 | 5.5 | 2017 | 2016-06-16 | B | 5 | 0.00511 | 1.503e-05
1 | 11091106 | 2016-06-09 09:05 | 2016-06-09 15:02 | 357 | 9 | 3213 | 0.0096593 | 0.009578 | 2.7057e-05 | NAPA ID:19444 TP_WAIKINO GXP > PAEROA SUB > BENNETT ST | 11 | Planned | 019444 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV TP2963 | NONE | Install new P/M TransformerTP2963 at Pole 858391. Replace Links TEMP72 at pole N0860 with Fuses FP1801. Works location: Vedders Rd, Paeroa. WO 30018371 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.004789 | 5.5 | 2017 | 2016-06-09 | B | 9 | 0.009578 | 2.7057e-05
1 | 11091605 | 2016-05-20 15:03 | 2016-05-20 16:10 | 66 | 4 | 267.1333 | 0.00080333 | 0.000767 | 1.2029e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4681T | FUSE - ELEMENT/LINK (HV) | Replace 3 x 2A fuse | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000767 | 6.6 | 2017 | 2016-05-20 | C | 4 | 0.000767 | 1.2029e-05
1 | 11093276 | 2016-05-20 20:30 | 2016-05-20 22:45 | 135 | 3 | 405.8 | 0.0012203 | 0.001193 | 9.0217e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4030T | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses on transformer 4030T, lightning strike 3 x 3 amp hv fuses | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.001193 | 11 | 2017 | 2016-05-20 | C | 3 | 0.001193 | 9.0217e-06
1 | 11093556 | 2016-05-20 20:44 | 2016-05-20 21:45 | 60 | 4 | 242.7333 | 0.00072996 | 0.000693 | 1.2029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 917 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuse at transformer 917 fuses, lightning strike | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000693 | 11 | 2017 | 2016-05-20 | C | 4 | 0.000693 | 1.2029e-05
1 | 11093820 | 2016-05-20 21:11 | 2016-05-21 02:18 | 306 | 296 | 27278.4333 | 0.082033 | 0.079362 | 0.0018976 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 358008 | BINDER | CB C945 tripped on E/F flags, line was patrolled and sectionalised and faultman found a floating wire at pole 358008, line was isolated at Fuses 7103 to rebind in the conductor. 2r line patrol 2204. 2r repair 0145 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.079362 | 11 | 2017 | 2016-05-20 | C | 296 | 0.079362 | 0.0018976
1 | 11094264 | 2016-05-21 04:06 | 2016-05-21 19:01 | 895 | 166 | 4284 | 0.012883 | 0.011385 | 0.00010224 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 765217 | CONDUCTOR - REPAIR/REHANG | Faultman found blown fuse at Fuses 5214, line was patrolled but not all of line could be patrolled due bad visibility and some flooding in some areas, faultman also cut away lightning arrestor on pole 765196, but the A phase still blown causing Recloser 6286 to auto reclose. Conductor found down with 2 metres jointed in. (Tree through Line). Relivened OK (Stormy weather). This was the repair job related to 11112884. Delay in getting back to do line repairs as fault crews were busy with other faults. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.011385 | 11 | 2017 | 2016-05-21 | C | 166 | 0.011385 | 0.00010224
1 | 11102588 | 2016-05-20 22:57 | 2016-05-21 04:05 | 308 | 470 | 117851.95 | 0.35441 | 0.35017 | 0.0014134 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | F12598 | CIRCUIT BREAKER (HV) | WAH CB1 tripped E/F, C Ph O/C, L/O. Feeder sectionalised with magpie found at base of pole F12598. All service restored. 2r line patrol 0225 2r repair. No repair - magpie removed by hotstick. | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.35017 | 11 | 2017 | 2016-05-20 | C | 470 | 0.35017 | 0.0014134
1 | 11107777 | 2016-05-20 23:34 | 2016-05-21 09:36 | 601 | 170 | 36355.5 | 0.10933 | 0.1078 | 0.00071272 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | M0921 | CONDUCTOR - REPAIR/REHANG | REC 9320 trip no flags. Lines down at pole M0921 due to tree through them. 2r line patrol 0127 no repair | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.1078 | 11 | 2017 | 2016-05-20 | C | 170 | 0.1078 | 0.00071272
1 | 11108648 | 2016-05-21 00:39 | 2016-05-21 02:37 | 118 | 115 | 7850.7333 | 0.023609 | 0.022571 | 0.00034583 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1022 | UNKNOWN | Recloser 1022 tripped on B & C phase O/C & E/F flags, line was patrolled and sectionalised and no fault was found. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.022571 | 6.6 | 2017 | 2016-05-21 | C | 115 | 0.022571 | 0.00034583
1 | 11112884 | 2016-05-20 03:20 | 2016-05-20 04:05 | 45 | 35 | 1575 | 0.0047364 | 0.00442 | 0.00010525 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 765217 | CONDUCTOR - REPAIR/REHANG | Call came in of part power. This was thought to be caused by L/A and this was cut away but fault continued. Line was left with single phase to be patrolled and repaired in the morning. See OMS 11094264. Bulls in the field where the pole is, this job can wait till the morning. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.00442 | 11 | 2017 | 2016-05-20 | C | 35 | 0.00442 | 0.00010525
1 | 11113145 | 2016-05-21 05:26 | 2016-05-21 09:05 | 219 | 3398 | 476436.1 | 1.4327 | 1.4021 | 0.010218 |  | 33 | Unplanned |  | ZONE SUB EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 2212 | TRANSFORMER - ZONE TRANSFORMER (HV) | CB 212 Trip T1 Diff, B & C Ph O/C E/F . 33kV line patrolled LFI's flashing. Chris Malony checked flags & relays at Baird Rd sub. Protection for T1 showed Tripped to Lock out, Display show CB 22 fail. Secondary protection tripped CB 2212. Transformer T1 Isolated CB 2212 relivened, Feeder CBs relivened. DNO 160535 Created to get transformer checked & Tested. 2r line patrol 0548. 2r repair not complete been dno'd | S4 | KINLEITH2212-BAIRD RD 33KV | KINLEITH 33 | Valley | TP_KINLEITH | Eastern Electricity | POWERCO | 1.4021 | 33 | 2017 | 2016-05-21 | C | 3398 | 1.4021 | 0.010218
1 | 11116597 | 2016-05-21 06:16 | 2016-05-21 07:31 | 75 | 115 | 8596.0167 | 0.02585 | 0.024812 | 0.00034583 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 1022 | UNKNOWN | Recloser tripped C ph O/C E/F - no fault found during sectionlising. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.024812 | 6.6 | 2017 | 2016-05-21 | C | 115 | 0.024812 | 0.00034583
1 | 11116740 | 2016-05-21 09:24 | 2016-05-21 22:21 | 777 | 2 | 1052.4833 | 0.003165 | 0.003146 | 6.0143e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2487T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer found to be faulty over night, needs to be replaced during today, talk to Phil Webby about size etc. Line power are on site fixing this job, Paul is no longer onsite, no down crew on this. This job was completed by Linepower (Subcontracted to Downer). Refer Paul Fitzpatrick for more Info. Transformer 2487 was replaced. | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.003146 | 11 | 2017 | 2016-05-21 | C | 2 | 0.003146 | 6.0143e-06
1 | 11116747 | 2016-05-21 05:26 | 2016-05-21 08:09 | 162 | 2 | 246.65 | 0.00074172 | 0.000723 | 6.0143e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC1256 | FUSE - ELEMENT/LINK (HV) | 2x3amp HV fuses blown at transformer TC1256 due to lightning 1 fuse barrel used also. | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000723 | 11 | 2017 | 2016-05-21 | C | 2 | 0.000723 | 6.0143e-06
1 | 11117227 | 2016-05-21 05:22 | 2016-05-21 07:11 | 108 | 7 | 762.3 | 0.0022924 | 0.002229 | 2.105e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T3/7 | FUSE - ELEMENT/LINK (HV) | Fuses found Blown at Transformer T3/7. Cause: Lightning. Used 3 x 3 amp Fuses. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.002229 | 11 | 2017 | 2016-05-21 | C | 7 | 0.002229 | 2.105e-05
1 | 11117409 | 2016-05-21 07:05 | 2016-05-21 08:35 | 90 | 29 | 2611.9333 | 0.0078546 | 0.007592 | 8.7209e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I 43 | FUSE - ELEMENT/LINK (HV) | Fuse found blown at fuses I 43 - cause Lightening Used 1 x 10 amp Also fuses found blown at Fuses I44 - cause lightening Used 2 x 10 amp | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.007592 | 11 | 2017 | 2016-05-21 | C | 29 | 0.007592 | 8.7209e-05
1 | 11117459 | 2016-05-21 07:23 | 2016-05-21 12:27 | 304 | 3 | 914.2 | 0.0027492 | 0.002722 | 9.0215e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC2352 | FUSE - ELEMENT/LINK (HV) | 2x6amp HV fuses blown at Transformer TC2352 blown due to lightning, reloaded & livened | F4 | THOMAS ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.002722 | 11 | 2017 | 2016-05-21 | C | 3 | 0.002722 | 9.0215e-06
1 | 11117528 | 2016-05-21 07:43 | 2016-05-21 10:58 | 195 | 4 | 781.4667 | 0.00235 | 0.002313 | 1.2029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SD5-070 | FUSE - ELEMENT/LINK (HV) | 2x 2amp HV fuse blown at transformer TD5-301 2x 8amp Fuses at SD5-070 Blown due to lightning. 1 fuse barrel used also. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.002313 | 11 | 2017 | 2016-05-21 | C | 4 | 0.002313 | 1.2029e-05
1 | 11117560 | 2016-05-21 07:45 | 2016-05-21 08:32 | 46 | 1 | 46.7 | 0.00014044 | 0.000131 | 3.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T3/165 | FUSE - ELEMENT/LINK (HV) | Fuse found blown at Transformer T3/165 - Cause Lightning. Used 3 x 3amp fuses | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000131 | 11 | 2017 | 2016-05-21 | C | 1 | 0.000131 | 3.0071e-06
1 | 11117575 | 2016-05-21 07:48 | 2016-05-21 09:45 | 116 | 1 | 116.6 | 0.00035064 | 0.000341 | 3.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2457 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer X2457 - cause lightning. Used 2 x 2 amp. | F4 | CROFTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000341 | 11 | 2017 | 2016-05-21 | C | 1 | 0.000341 | 3.0071e-06
1 | 11117580 | 2016-05-21 07:48 | 2016-05-21 09:21 | 92 | 1 | 92.6 | 0.00027847 | 0.000269 | 3.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2040 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer X2040 - Cause weather. Used 3 x 3 amp fuses. | F4 | CROFTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000269 | 11 | 2017 | 2016-05-21 | C | 1 | 0.000269 | 3.0071e-06
1 | 11117814 | 2016-05-21 13:58 | 2016-05-21 14:44 | 46 | 55 | 2530 | 0.0076082 | 0.007112 | 0.0001654 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD2-027 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Fuse blown at transformer TD2-027. reloaded fuse, fuse holder broke on restoration. isolation at Fuses SD2-023 to replace 2 11kV Drop out fuse holders at transformer TD2-027. Isolation of 400V to resagg lines | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.007112 | 11 | 2017 | 2016-05-21 | C | 55 | 0.007112 | 0.0001654
1 | 11118103 | 2016-05-21 09:02 | 2016-05-21 10:44 | 101 | 1 | 101.6167 | 0.00030558 | 0.000296 | 3.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X4206 | FUSE - ELEMENT/LINK (HV) | Fuses found Blown at Transformer X4206 - cause lightning. Used 2 x 3 amp fuses and 1 x carrier. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.000296 | 11 | 2017 | 2016-05-21 | C | 1 | 0.000296 | 3.0071e-06
1 | 11118420 | 2016-05-21 13:00 | 2016-05-21 14:34 | 94 | 5 | 470 | 0.0014134 | 0.001368 | 1.5036e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7138P | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer 7138 found to be faulty, lost one phase, faultman sorting replacement transformer. Transformer replaced Off time 13:00 On time 14:34 - cause lightning. Used 1 x 100 kVA 3 phase transformer | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.001368 | 11 | 2017 | 2016-05-21 | C | 5 | 0.001368 | 1.5036e-05
1 | 11119584 | 2016-05-21 07:44 | 2016-05-21 11:35 | 230 | 101 | 19742.1667 | 0.059369 | 0.058457 | 0.00030373 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | FC4170 | FUSE - ELEMENT/LINK (HV) | 2x 15amp HV Fuses blown at FC1474, also fuse blown upstream at fuse FC4170. 1x15amp reloaded & livened. Blown due to lightning. Still no power to Port Jackson. FM going to check Recloser 9927/2. Fuses TC680 Blown. Recloser 9927/2 Open Fuses TC680 reloaded with 2x15amp HV fuses. Recloser 9927 closed all power restored. Need to look at grading between fuses FC4170 loaded with 15amp fuses & TC680 loaded with 15amp fuses. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.058457 | 11 | 2017 | 2016-05-21 | C | 101 | 0.058457 | 0.00030373
1 | 11120361 | 2016-05-21 12:00 | 2016-05-21 18:38 | 398 | 4 | 1592 | 0.0047875 | 0.004751 | 1.2029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3256T | FUSE - ELEMENT/LINK (HV) | 3 HT fuses tripped due to lightning. Reloaded / relivened OK. (Transformer in OMS incorrect, should be 3256T). OMS to be completed. Tx corrected in QA | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.004751 | 11 | 2017 | 2016-05-21 | C | 4 | 0.004751 | 1.2029e-05
1 | 11121651 | 2016-05-21 14:43 | 2016-05-21 19:34 | 290 | 2 | 581.6333 | 0.0017491 | 0.001731 | 6.0143e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | I13203 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 12:16 Transformer found blown during line patrol. Cause: Lightning. Transformer replaced all service restored. | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.001731 | 11 | 2017 | 2016-05-21 | C | 2 | 0.001731 | 6.0143e-06
1 | 11121778 | 2016-05-21 15:12 | 2016-05-22 09:48 | 1116 | 1 | 1116.1167 | 0.0033564 | 0.003347 | 3.0071e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1947 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer X1947 found to be faulty still supplying power on two phases, Glen Most to sort out replacement as no 100 kVA transformers at Raetihi. Transformer replaced - isolated at transformer fuses used 1 x 100 kVA 3 ph transformer. Glen called to advised that this has been replaced, power restored at 9.48am, Glen confirms Jeremy has also left site. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.003347 | 11 | 2017 | 2016-05-21 | C | 1 | 0.003347 | 3.0071e-06
1 | 11122277 | 2016-05-21 09:15 | 2016-05-21 09:35 | 20 | 1 | 20 | 6.0144e-05 | 5.1e-05 | 3.0071e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7290 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Broken insulator (Top com off - cannot be fixed), requires transformer change. Transformer T7290 replaced - isolated at transformer fuses. Used 1 x 30 kVA transformer & 1 x 3 amp fuse. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 5.1e-05 | 11 | 2017 | 2016-05-21 | C | 1 | 5.1e-05 | 3.0071e-06
1 | 11123380 | 2016-05-22 06:55 | 2016-05-22 09:40 | 164 | 2 | 329.0667 | 0.00098955 | 0.000971 | 6.0142e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1776N | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer 1776N found to be faulty. Isolated at fuses 6542. Transformer replaced, used 1 x 15kVA 3 phase transformer. | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.000971 | 11 | 2017 | 2016-05-22 | C | 2 | 0.000971 | 6.0142e-06
1 | 11123527 | 2016-05-22 12:08 | 2016-05-22 15:07 | 179 | 1 | 179 | 0.00053828 | 0.000529 | 3.0071e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C6105 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer C6105 faulty. Isolated transformer being replaced C6105, Bruce leaving site, Paul replacing transformer. Transformer C1605 replaced - damaged caused by lightning. Used 1 x 50 kVA transformer, 3 x fuse carriers & 3x 6amp fuses. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.000529 | 11 | 2017 | 2016-05-22 | C | 1 | 0.000529 | 3.0071e-06
1 | 11125579 | 2016-05-22 11:28 | 2016-05-22 12:45 | 77 | 1 | 77.1833 | 0.0002321 | 0.000223 | 3.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2484T | FUSE - ELEMENT/LINK (HV) | Transformer actually 2484T feeds woolshed on farm Fuses for transformer 2484T found blown - cause lightning Used 2 x 2amp fuses | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.000223 | 11 | 2017 | 2016-05-22 | C | 1 | 0.000223 | 3.0071e-06
1 | 11125628 | 2016-05-22 12:00 | 2016-05-22 15:42 | 221 | 1 | 221.5333 | 0.00066618 | 0.000657 | 3.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2946 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer X2946 - cause lightening Used 2 x 2 amp | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.000657 | 11 | 2017 | 2016-05-22 | C | 1 | 0.000657 | 3.0071e-06
1 | 11125703 | 2016-05-22 12:33 | 2016-05-22 13:16 | 43 | 115 | 4558.3667 | 0.013708 | 0.01267 | 0.00034582 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1022 | UNKNOWN | Recloser 1022 Tripped E/F L/O. No fault found during sectionlising, lines not patrolled due to faultman required else where. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.01267 | 6.6 | 2017 | 2016-05-22 | C | 115 | 0.01267 | 0.00034582
1 | 11125826 | 2016-05-22 12:36 | 2016-05-22 13:35 | 59 | 1 | 59.3833 | 0.00017857 | 0.000169 | 3.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 6623 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses 6623 - cause lightning Used 3 x 2amp | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.000169 | 11 | 2017 | 2016-05-22 | C | 1 | 0.000169 | 3.0071e-06
1 | 11125837 | 2016-05-22 12:38 | 2016-05-22 14:32 | 114 | 1 | 114.2333 | 0.00034352 | 0.000334 | 3.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4238 | FUSE - ELEMENT/LINK (HV) | Dean Brett Attended. Reloaded, Relivened 3x HV Fuses, 3A. All Power Restored on Completion. High winds in the area at the time these blew. | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000334 | 11 | 2017 | 2016-05-22 | C | 1 | 0.000334 | 3.0071e-06
1 | 11126616 | 2016-05-22 18:19 | 2016-05-22 21:29 | 190 | 15 | 2857.5 | 0.0085929 | 0.008457 | 4.5107e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 1126616 | NONE | Fuses M8 found tripped due to tree branches on line. Outage required from Fuses M8 where tree contractors were called in to clear vegetation. Relivened OK. (Heavy rain). | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.008457 | 11 | 2017 | 2016-05-22 | C | 15 | 0.008457 | 4.5107e-05
1 | 11126688 | 2016-05-22 18:48 | 2016-05-22 20:27 | 99 | 115 | 7001.1833 | 0.021054 | 0.020016 | 0.00034582 |  | 6.6 | Unplanned |  | ZONE SUB EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | 1022 | NONE | 1R crew request - Feeder was sectionalised and power restored. 2R - The Protection circuitry of another breaker at the same sub was damaged by lightning , which then exhibited similar tripping patterns as 1022. A tech went to the sub and tested the protection circuits. they were not damaged but it was discovered that the Protection settings were incorrect. The correct settings were loaded and the CB tested for correct operation. Glen Most did not do a feeder patrol but Phil McQuiod did. Protection Work. 2r line patrol 1926. 2r repair no | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.020016 | 6.6 | 2017 | 2016-05-22 | C | 115 | 0.020016 | 0.00034582
1 | 11127300 | 2016-05-22 22:57 | 2016-05-23 15:57 | 1020 | 6 | 6120 | 0.018404 | 0.018349 | 1.8043e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 790654 | POLE | 11kV pole broken on Makirikiri Valley Rd.(Pole rotten).Isolation required from Fuses 1135. Will require pole change during daylight hours. (NOTE: planned switching had been arranged for this pole change on the 8th June, NAPA 20652 ). | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.018349 | 11 | 2017 | 2016-05-22 | C | 6 | 0.018349 | 1.8043e-05
1 | 11127520 | 2016-05-22 22:40 | 2016-05-23 01:09 | 149 | 752 | 29289.1833 | 0.088077 | 0.081292 | 0.0022614 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 396704 | CONDUCTOR - REPAIR/REHANG | CB 1 Trip A,B O/C E/F Line down at Pole 396704 Isolation at ABS SD3-112, ABS SD3-009,SD3-010 ABS 9678/1 & Links 9678/4. Back feed from Sectionaliser 9805/2 & ABS SD3-148. Line Repaired. 4 sleeves, 3m conductor | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.081292 | 11 | 2017 | 2016-05-22 | C | 752 | 0.081292 | 0.0022614
1 | 11131287 | 2016-05-23 02:35 | 2016-05-23 06:38 | 242 | 254 | 13669.1833 | 0.041105 | 0.038813 | 0.00086003 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03911 | CONDUCTOR - REPAIR/REHANG | After inital restoration received calls of part powers and on investigation found a line down @ P03911 . Repaired and restored . Materials used 2 Sleeves conductor and jumper. 2r line patrol 0308 / 2r repair 0547. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.038813 | 11 | 2017 | 2016-05-23 | C | 254 | 0.038813 | 0.00086003
1 | 11132867 | 2016-06-16 08:36 | 2016-06-16 12:37 | 241 | 32 | 7712 | 0.023182 | 0.022893 | 9.6192e-05 | NAPA ID:19203 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ASHHURST | 11 | Planned | 019203 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV poel P3444718 | NONE | Replace 11KV pole P3444718. Works location: Harrisons Line, Palmerston North. WO 10152068 | F3 | ASHHURST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.011447 | 5.5 | 2017 | 2016-06-16 | B | 32 | 0.022893 | 9.6192e-05
1 | 11133446 | 2016-05-23 09:30 | 2016-05-23 14:10 | 279 | 4 | 1118.9333 | 0.0033647 | 0.003328 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2986 | FUSE - ELEMENT/LINK (HV) | Reload Reliven 2 x 6A Fuses due to Bird Strike | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.003328 | 11 | 2017 | 2016-05-23 | C | 4 | 0.003328 | 1.2028e-05
1 | 11134244 | 2016-05-23 10:20 | 2016-05-23 14:52 | 272 | 1 | 272 | 0.00081793 | 0.000808 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | K1981 | POLE | Advised svs hub 8:49am. 1 11kV Pole. 1 x Complete x-arm assembly. Isolation at Fuses FC4030. Tied to OMS 11134244. Old Pole just fell over. Original Job for this is OMS 11133078. (wrong transformer allocated to that job) | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.000808 | 11 | 2017 | 2016-05-23 | C | 1 | 0.000808 | 3.007e-06
1 | 11135196 | 2016-06-17 08:40 | 2016-06-17 15:05 | 385 | 48 | 18480 | 0.05555 | 0.055117 | 0.00014429 | NAPA ID:20562 TP_MASTERTON GXP > TINUI SUB > ANNEDALE | 11 | Planned | 020562 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S198 | NONE | Change 1 x pole and run 700 mtrs of new conductor. Works location: Annadale Rd. WO 30024868 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.027558 | 5.5 | 2017 | 2016-06-17 | B | 48 | 0.055117 | 0.00014429
1 | 11135476 | 2016-05-23 12:44 | 2016-05-23 15:55 | 191 | 1001 | 38190.05 | 0.11484 | 0.10581 | 0.0030101 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 735878 | POLE | Report of truck hitting Pole on Hills Rd. 1 x 2mtr cross arm. 3 x Pin Insulators. 10 mtrs #8 wire. Binders. 15 x sleeves. NDR 100157. 2r line patrol 1312 / 2r repair 1428. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.10581 | 11 | 2017 | 2016-05-23 | C | 1001 | 0.10581 | 0.0030101
1 | 11137780 | 2016-05-23 07:55 | 2016-05-23 11:38 | 222 | 1 | 222.7833 | 0.00066993 | 0.00066 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E90 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a HV Fuses @ E90 | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.00066 | 11 | 2017 | 2016-05-23 | C | 1 | 0.00066 | 3.007e-06
1 | 11138427 | 2016-05-24 13:20 | 2016-05-24 14:38 | 78 | 35 | 2730 | 0.0082092 | 0.007893 | 0.00010525 | NAPA ID:21009 TP_STRATFORD GXP | 11 | Planned | 021009 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 526 | NONE | DNO 160410 URGENT REPAIR of 33kV ABS 526. ABS is being held on by 1 rusty bolt the other 2 bolts have dissolved and fallen off. Review to undertake the works live line is a safety issue. Works location: East Rd, Stratford. WO 30007226 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.0039465 | 5.5 | 2017 | 2016-05-24 | B | 35 | 0.007893 | 0.00010525
1 | 11139989 | 2016-05-23 23:49 | 2016-05-24 04:19 | 269 | 112 | 29801.8 | 0.089617 | 0.088606 | 0.0010044 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 833700 | INSULATOR | Broken dead end and Pulley at Pole 833700 - Isolated at ABS's S157 & S193 plus CB C828. used 1 x pulley Insulator 1 x dead end. 2r line patrol no. 2r repair 0333. Initial trip. CB C828 found open and so system time taken. | F4 | TAUWERU | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.088606 | 11 | 2017 | 2016-05-23 | C | 112 | 0.088606 | 0.0010044
1 | 11140990 | 2016-05-24 07:14 | 2016-05-24 09:12 | 118 | 1 | 118.05 | 0.00035498 | 0.000345 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T1/350 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a HV fuses @ T1/350 suspect due to lightning | F1 | SKYHAWK | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000345 | 11 | 2017 | 2016-05-24 | C | 1 | 0.000345 | 3.007e-06
1 | 11141348 | 2016-05-24 08:44 | 2016-05-24 13:00 | 256 | 4 | 1025.0667 | 0.0030824 | 0.003046 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4116T | FUSE - ELEMENT/LINK (HV) | Previous job 11072694 - 20/05/2016 2x fuses replaced (cause: lightning). 2 x 2A HV Fuses | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.003046 | 11 | 2017 | 2016-05-24 | C | 4 | 0.003046 | 1.2028e-05
1 | 11141938 | 2016-05-24 07:11 | 2016-05-24 09:27 | 135 | 51 | 6931.75 | 0.020844 | 0.020384 | 0.00015336 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2635 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 15a HV Fuses @ 2635 | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.020384 | 11 | 2017 | 2016-05-24 | C | 51 | 0.020384 | 0.00015336
1 | 11143344 | 2016-06-10 08:50 | 2016-06-10 16:43 | 473 | 69 | 32637 | 0.098116 | 0.097493 | 0.00020743 | NAPA ID:20552 TP_WAIKINO GXP > PAEROA SUB > SHAW AVE | 11 | Planned | 020552 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4846 | NONE | Replace TC4846 with a new 200kVA unit. Works location: Ainslie Rd, Paeroa. WO 30019243 | F3 | SHAW AVE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.048746 | 5.5 | 2017 | 2016-06-10 | B | 69 | 0.097493 | 0.00020743
1 | 11144273 | 2016-05-24 14:32 | 2016-05-25 10:11 | 1179 | 149 | 37377.7167 | 0.1124 | 0.11105 | 0.0013051 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 783788 | UNKNOWN | Recloser 284 Trip flags Ph B OC & PH C OC. Due to lack of resources, weather and ground conditions as well as terrain which needs to be traversed all contributing to unsafe conditions for 1 man alone section of line between ABS 596 & ABS 509 is being left off till daylight. Twisted conductor found at pole 783788. 2r line patrol 1504. 2r repair none | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.11105 | 11 | 2017 | 2016-05-24 | C | 149 | 0.11105 | 0.0013051
1 | 11144773 | 2016-05-24 11:58 | 2016-05-24 12:53 | 55 | 1 | 55 | 0.00016539 | 0.000156 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1/162 | NONE | Start time taken from history log on 11139334 | F1 | SKYHAWK | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000156 | 11 | 2017 | 2016-05-24 | C | 1 | 0.000156 | 3.007e-06
1 | 11144835 | 2016-06-09 10:05 | 2016-06-09 14:00 | 235 | 9 | 2115 | 0.0063584 | 0.006277 | 2.7057e-05 | NAPA ID:21002 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 021002 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2882 | NONE | Open DDO Test and apply Earths Isolated side TX TC2882 remove TC2882 replace LV Xarms and Hardware Re Install TC2882. Terminate New UG LV Remove OH to IC487 Pole. Works location: Kaihere Rd. WO 30011923 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0031385 | 5.5 | 2017 | 2016-06-09 | B | 9 | 0.006277 | 2.7057e-05
1 | 11148287 | 2016-05-24 19:15 | 2016-05-24 21:10 | 115 | 11 | 1265 | 0.0038039 | 0.003704 | 3.3078e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 476 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Part power job off same tx OMS 11148432. Transformer 476 Faulty - caused by lightning. Used 1 x 50 kVA transformer off 19:15 and on 21:10 | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.003704 | 11 | 2017 | 2016-05-24 | C | 11 | 0.003704 | 3.3078e-05
1 | 11149715 | 2016-05-24 16:41 | 2016-05-24 19:24 | 163 | 13 | 2120.3 | 0.0063758 | 0.006258 | 3.9092e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 5721 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses 5721 - used 2 x 15 amp Fuses. Also 2 x fuses found blown at Transformer 4466T - used 2 x 2 amp fuses. All caused by lightning. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.006258 | 11 | 2017 | 2016-05-24 | C | 13 | 0.006258 | 3.9092e-05
1 | 11149973 | 2016-05-24 16:54 | 2016-05-24 21:19 | 265 | 1 | 265.35 | 0.00079792 | 0.000788 | 3.007e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3168T | FUSE - ELEMENT/LINK (HV) | Transformer wrong fuses found blown at transformer 3168T - cause lightning Used 3 x 2 amp fuses | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.000788 | 6.6 | 2017 | 2016-05-24 | C | 1 | 0.000788 | 3.007e-06
1 | 11150058 | 2016-05-24 17:04 | 2016-05-24 19:00 | 115 | 3 | 346.65 | 0.0010424 | 0.001015 | 9.0211e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | WH277 | FUSE - ELEMENT/LINK (HV) | Tree Branch across lines. 2 x 15A HV Fuses NDR N100158 | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.001015 | 11 | 2017 | 2016-05-24 | C | 3 | 0.001015 | 9.0211e-06
1 | 11150284 | 2016-05-24 17:31 | 2016-05-24 18:47 | 76 | 3 | 228.55 | 0.00068726 | 0.00066 | 9.0211e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1399 | FUSE - ELEMENT/LINK (HV) | 3 x 3A HV Fuses | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.00066 | 11 | 2017 | 2016-05-24 | C | 3 | 0.00066 | 9.0211e-06
1 | 11150321 | 2016-05-24 17:32 | 2016-05-24 19:09 | 96 | 1 | 96.9667 | 0.00029158 | 0.000282 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2734 | FUSE - ELEMENT/LINK (HV) | replaced 2x 6a hV fuses @ transformer T2734 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000282 | 11 | 2017 | 2016-05-24 | C | 1 | 0.000282 | 3.007e-06
1 | 11150743 | 2016-05-24 21:55 | 2016-05-24 22:30 | 35 | 1 | 35 | 0.00010525 | 9.6e-05 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 612 | FUSE - ELEMENT/LINK (HV) | Fuse found blown at fuse 612 - Cause Lightning. Also found fuse blown at Transformer 1876. Used 1 x 8 amp Fuse & 1 x 3 amp. Jumper required repair at transformer 1876 - nothing used. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 9.6e-05 | 11 | 2017 | 2016-05-24 | C | 1 | 9.6e-05 | 3.007e-06
1 | 11150847 | 2016-05-25 10:28 | 2016-05-25 12:12 | 104 | 51 | 5304 | 0.015949 | 0.015489 | 0.00015336 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M0856 | CROSSARM - WHOLE ASSEMBLY | 1R to re-position cross arm tomorrow (25/05). Has Access issues. Safer to be done in daylight.Faultman found broken 11kV cross arm on pole M0856, line was isolated at ABS's 876, 1102 & 1271 to replace cross arm. 1 x 11kV cross arm & all hardware replaced. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.015489 | 11 | 2017 | 2016-05-25 | C | 51 | 0.015489 | 0.00015336
1 | 11150972 | 2016-05-24 19:35 | 2016-05-24 22:02 | 147 | 7 | 1029 | 0.0030943 | 0.003031 | 2.1049e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TA787 | CONDUCTOR - REPAIR/REHANG | Crossarm hanging on pole and lines hanging and swinging around. Owners of the property are away, Allen is looking after the place,pole is located down tanker track driveway. Please call Allen if privately owned. 6.53pm advised Sammy at svs hub of job and emailed. Lines down past Fuses TA787 - Isolated at Fuses TA787. Lines repaired. Materials used: 3 mtrs conductor & 4 sleeves. | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.003031 | 11 | 2017 | 2016-05-24 | C | 7 | 0.003031 | 2.1049e-05
1 | 11151171 | 2016-05-24 19:06 | 2016-05-25 12:40 | 1053 | 3 | 3161 | 0.0095053 | 0.009478 | 9.0211e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TG7-004 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | transformer TG7-004 needs replacing. Has been left off overnight and will be replaced tomorrow. 1 x transformer 2x 2 amp fuses, 6 x lugs. | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.009478 | 11 | 2017 | 2016-05-24 | C | 3 | 0.009478 | 9.0211e-06
1 | 11151257 | 2016-05-24 19:22 | 2016-05-24 21:00 | 98 | 4 | 392.0667 | 0.001179 | 0.001142 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 6269 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at fuses 6269 - cause lightning. Used 2 x 6 amp Fuses. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.001142 | 11 | 2017 | 2016-05-24 | C | 4 | 0.001142 | 1.2028e-05
1 | 11151273 | 2016-05-24 19:24 | 2016-05-24 21:07 | 103 | 4 | 413.6 | 0.0012437 | 0.001207 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8407 | FUSE - ELEMENT/LINK (HV) | Fuse found blown at 8407 - cause lightning. Used 3 x 3 amp fuses. | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.001207 | 11 | 2017 | 2016-05-24 | C | 4 | 0.001207 | 1.2028e-05
1 | 11151527 | 2016-05-24 20:08 | 2016-05-24 22:17 | 129 | 279 | 36004.95 | 0.10827 | 0.10575 | 0.00083897 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC6232 | CONDUCTOR - REPAIR/REHANG | at 20:08, Whitianga Sub, CB 3 Kuaotunu Feeder. Fautlman had been called to part power/no power jobs. Found that at Regulator TC6232 an HV Line had come down and was still alive on the ground sparking. Faultman contacted NOC to Request Opening of Sectionaliser 9632 to De-energise line. NOC Opened at 20:08. Line Isolated at ABS 9632/1, Links 9632/4 & Fuses FC898. Permit Issued & Repairs carried out. All Power Restored on Completion. Replaced 8m of Conductor (1 span 1 phase) 2x HV Connectors used. Andrew King Attended. | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.10575 | 11 | 2017 | 2016-05-24 | C | 279 | 0.10575 | 0.00083897
1 | 11152118 | 2016-05-24 20:41 | 2016-05-25 11:20 | 878 | 3 | 2636.8167 | 0.007929 | 0.007901 | 9.0211e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4030T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | TX replaced this morning - OMS 11151943. Signed of with the codes | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.007901 | 11 | 2017 | 2016-05-24 | C | 3 | 0.007901 | 9.0211e-06
1 | 11162251 | 2016-05-25 02:57 | 2016-05-25 04:49 | 112 | 5 | 560.25 | 0.0016847 | 0.001639 | 1.5035e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | CA 465 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses CA 465. Cause lightning. Used 2 x 6 amp fuses. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.001639 | 11 | 2017 | 2016-05-25 | C | 5 | 0.001639 | 1.5035e-05
1 | 11162264 | 2016-05-25 03:15 | 2016-05-25 06:35 | 199 | 243 | 19887.7833 | 0.059803 | 0.05761 | 0.0007307 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 747075 | SURGE ARRESTOR (HV) | Recloser 499/2 tripped on B & C phase O/C flags, line was patrolled and sectionalised and a blown lightning arrestor was found at Pole 747075, lione was isolated at ABS's 229 & 548. cut away lightning arrestor. 2R line patrol 0417 2r repair 0617 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.05761 | 11 | 2017 | 2016-05-25 | C | 243 | 0.05761 | 0.0007307
1 | 11162608 | 2016-05-25 04:18 | 2016-05-25 07:10 | 172 | 1 | 172.3 | 0.00051811 | 0.000509 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T2556 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at transformer T2556 - Cause lightning. Used 3 x 2 amp Fuses. Faultman advised so much lightning in area not safe to replace fuses, going to contact customer and advise. Rstoration complered at 07.10am | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000509 | 11 | 2017 | 2016-05-25 | C | 1 | 0.000509 | 3.007e-06
1 | 11162613 | 2016-05-25 04:21 | 2016-05-25 04:47 | 26 | 115 | 2997.6667 | 0.009014 | 0.007976 | 0.00034581 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N/A - NOT APPLICABLE | UNKNOWN | Recloser 1022 tripped. No Flags. Line not patrolled. Cause of fault unknown however the Faultman lives in area and saw lightning | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.007976 | 6.6 | 2017 | 2016-05-25 | C | 115 | 0.007976 | 0.00034581
1 | 11163569 | 2016-05-25 05:30 | 2016-05-25 07:05 | 95 | 2 | 190.9667 | 0.00057424 | 0.000556 | 6.014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4682T | FUSE - ELEMENT/LINK (HV) | 2 x 3amp fuse due to weather. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000556 | 11 | 2017 | 2016-05-25 | C | 2 | 0.000556 | 6.014e-06
1 | 11163582 | 2016-05-25 05:37 | 2016-05-25 08:35 | 177 | 2 | 355.6 | 0.0010693 | 0.001051 | 6.014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/85 | FUSE - ELEMENT/LINK (HV) | 2 x 6 amp Fuse due to weather. | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001051 | 11 | 2017 | 2016-05-25 | C | 2 | 0.001051 | 6.014e-06
1 | 11163604 | 2016-05-25 05:44 | 2016-05-25 11:15 | 331 | 115 | 8471.0833 | 0.025473 | 0.024435 | 0.00069161 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 775964 | CROSSARM - WHOLE ASSEMBLY | Rec 1022 tripped Line patrolled found broken crossarm at pole 775964 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.024435 | 6.6 | 2017 | 2016-05-25 | C | 115 | 0.024435 | 0.00069161
1 | 11164519 | 2016-05-25 06:06 | 2016-05-25 09:40 | 214 | 1 | 214.2167 | 0.00064415 | 0.000635 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/77 | FUSE - ELEMENT/LINK (HV) | 3 x 2amp due to weather | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000635 | 11 | 2017 | 2016-05-25 | C | 1 | 0.000635 | 3.007e-06
1 | 11164970 | 2016-05-25 11:43 | 2016-05-25 13:55 | 132 | 1 | 132 | 0.00039692 | 0.000387 | 3.007e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4928T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found blown transformer 4928T, transformer was isolated at the transformer and it was replaced. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000387 | 11 | 2017 | 2016-05-25 | C | 1 | 0.000387 | 3.007e-06
1 | 11165035 | 2016-05-25 06:44 | 2016-05-25 15:00 | 495 | 3 | 1125.2833 | 0.0033837 | 0.003356 | 9.021e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2946T | CONDUCTOR - REPAIR/REHANG | Check OMS: 11167377 - 826 Mokau Road FM has confirmed 2 spans are down in the trees, 2R requested to Repair/Rehang 20-30m of new conductor once the trees are cut out of the way. 2 X FUSES 2 LV FUSES AND 20 JOINS 50M, CONDUCTOR NDRN100159 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.003356 | 11 | 2017 | 2016-05-25 | C | 3 | 0.003356 | 9.021e-06
1 | 11165056 | 2016-05-25 06:49 | 2016-05-25 07:48 | 58 | 1 | 58.8833 | 0.00017706 | 0.000168 | 3.007e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2506 | FUSE - ELEMENT/LINK (HV) | 2 x 3 amp Fuse due to weather. | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.000168 | 6.6 | 2017 | 2016-05-25 | C | 1 | 0.000168 | 3.007e-06
1 | 11165261 | 2016-05-25 07:09 | 2016-05-25 09:02 | 113 | 5 | 565.9167 | 0.0017017 | 0.001656 | 1.5035e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1353 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp fuses | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.001656 | 11 | 2017 | 2016-05-25 | C | 5 | 0.001656 | 1.5035e-05
1 | 11165564 | 2016-05-25 07:40 | 2016-05-25 13:10 | 329 | 5 | 1649.9167 | 0.0049613 | 0.004916 | 1.5035e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/217 | FUSE - ELEMENT/LINK (HV) | 2X 2A Amp Fuses due to weather. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.004916 | 11 | 2017 | 2016-05-25 | C | 5 | 0.004916 | 1.5035e-05
1 | 11165589 | 2016-05-25 07:42 | 2016-05-25 10:00 | 137 | 1 | 137.8667 | 0.00041457 | 0.000405 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1253 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp fuses due to weather | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.000405 | 11 | 2017 | 2016-05-25 | C | 1 | 0.000405 | 3.007e-06
1 | 11165606 | 2016-05-25 07:43 | 2016-05-25 08:21 | 38 | 2 | 76.5667 | 0.00023024 | 0.000212 | 6.014e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2252T | FUSE - ELEMENT/LINK (HV) | 7:54am Paul will dispatch on this - Chris Vivier is in the area. Mercury are contacting the police to do traffic management as this is a railway crossing. 3 x 2amp fuses due to weather. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000212 | 6.6 | 2017 | 2016-05-25 | C | 2 | 0.000212 | 6.014e-06
1 | 11165686 | 2016-06-17 09:00 | 2016-06-17 11:45 | 165 | 78 | 12870 | 0.038687 | 0.037983 | 0.00023447 | NAPA ID:18614 TP_GREYTOWN GXP > MARTINBOROUGH SUB > TAWAHA | 11 | Planned | 018614 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 376628 | NONE | replace 11kv pole 376628 with new 11.5m strain pole and relocate pole site 25m north. Works location: Hwy 53, Martinborough. WO 30024394 | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.018992 | 5.5 | 2017 | 2016-06-17 | B | 78 | 0.037983 | 0.00023447
1 | 11165909 | 2016-05-25 08:02 | 2016-05-25 09:47 | 105 | 3 | 315.15 | 0.00094766 | 0.00092 | 9.021e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2814 | FUSE - ELEMENT/LINK (HV) | 3 x 3amp fuses due to weather | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.00092 | 11 | 2017 | 2016-05-25 | C | 3 | 0.00092 | 9.021e-06
1 | 11166057 | 2016-05-25 08:07 | 2016-05-25 09:43 | 96 | 2 | 192.2333 | 0.00057805 | 0.00056 | 6.014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/77 | FUSE - ELEMENT/LINK (HV) | 2 x 2 amp fuseas | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.00056 | 11 | 2017 | 2016-05-25 | C | 2 | 0.00056 | 6.014e-06
1 | 11166079 | 2016-05-25 08:07 | 2016-05-25 12:55 | 288 | 4 | 1153.1333 | 0.0034675 | 0.003431 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8403 | FUSE - ELEMENT/LINK (HV) | 2 x 2 Amp Fuses due to weather. | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.003431 | 11 | 2017 | 2016-05-25 | C | 4 | 0.003431 | 1.2028e-05
1 | 11166103 | 2016-05-25 08:10 | 2016-05-25 12:00 | 230 | 2 | 460.6333 | 0.0013851 | 0.001367 | 6.014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4239 | FUSE - ELEMENT/LINK (HV) | Check OMS: 11166151 - 334 Moki Road and 11166123 - 19 RIMUPUTA ROAD 12 00 2X 2AMP FUSE LIGHTNING | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001367 | 11 | 2017 | 2016-05-25 | C | 2 | 0.001367 | 6.014e-06
1 | 11166123 | 2016-05-26 13:48 | 2016-05-26 15:00 | 72 | 34 | 2448 | 0.007361 | 0.007054 | 0.00010224 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4144T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found transformer 4144T faulty, transformer needs to be replaced in morning. OMS 11166103 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.007054 | 11 | 2017 | 2016-05-26 | C | 34 | 0.007054 | 0.00010224
1 | 11166166 | 2016-06-14 10:39 | 2016-06-14 12:35 | 116 | 6 | 696 | 0.0020923 | 0.002038 | 1.8037e-05 | NAPA ID:20564 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 020564 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4867 | FUSE - DROP OUT - REPLACE FULL SET OF FUSES (HV) | To replace the 11kV Fuse Arm & install a 400V Fuse Disconnector. Works Location: Landsdown Road, Walton. Work Order 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.001019 | 5.5 | 2017 | 2016-06-14 | B | 6 | 0.002038 | 1.8037e-05
1 | 11166237 | 2016-06-14 08:46 | 2016-06-14 15:00 | 373 | 71 | 26523.2333 | 0.079732 | 0.079091 | 0.00021343 | NAPA ID:18972 TP_KINLEITH GXP > BAIRD ROAD SUB > KAURI ST | 11 | Planned | 018972 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole B0055 | NONE | Install temp ABS # 10 at pole B0055,replace ABS 1327, replace poles & x arms at various locations. Works location: Paraonui Rd, Tokoroa. WO 30017824 | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.039545 | 5.5 | 2017 | 2016-06-14 | B | 71 | 0.079091 | 0.00021343
1 | 11166248 | 2016-05-25 08:29 | 2016-05-25 12:13 | 224 | 3 | 672.05 | 0.0020209 | 0.001993 | 9.021e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t8/352 | FUSE - ELEMENT/LINK (HV) | 2x 2amp. 26/5 - sent to ONC for follow up | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001993 | 11 | 2017 | 2016-05-25 | C | 3 | 0.001993 | 9.021e-06
1 | 11166347 | 2016-05-25 08:39 | 2016-05-25 10:22 | 102 | 4 | 411.5333 | 0.0012375 | 0.001201 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/75 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp fuse and holder due to weather. | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001201 | 11 | 2017 | 2016-05-25 | C | 4 | 0.001201 | 1.2028e-05
1 | 11167083 | 2016-05-25 11:23 | 2016-05-25 12:09 | 46 | 61 | 2794.2 | 0.0084022 | 0.007851 | 0.00018343 |  | 6.6 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2104T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found blown fuse at transformer 2104T when faultman went to liven he noticed the bushings on the transformer were broken line was isolated at ABS 5537, Links 6281 & Fuses 5489 to replace the bushings. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.007851 | 6.6 | 2017 | 2016-05-25 | C | 61 | 0.007851 | 0.00018343
1 | 11167178 | 2016-05-25 09:25 | 2016-05-25 11:13 | 108 | 1 | 108.2167 | 0.00032541 | 0.000316 | 3.007e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3527T | FUSE - ELEMENT/LINK (HV) | 2 x 2amp due to weather. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.000316 | 6.6 | 2017 | 2016-05-25 | C | 1 | 0.000316 | 3.007e-06
1 | 11167237 | 2016-05-25 09:30 | 2016-05-25 17:30 | 480 | 1 | 480.1833 | 0.0014439 | 0.001434 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4422T | FUSE - ELEMENT/LINK (HV) | Reload Reliven. 2 x 2A. Lightning | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001434 | 11 | 2017 | 2016-05-25 | C | 1 | 0.001434 | 3.007e-06
1 | 11167275 | 2016-05-25 09:36 | 2016-05-25 14:55 | 319 | 6 | 1916.3 | 0.0057623 | 0.005708 | 1.8042e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N48 | FUSE - ELEMENT/LINK (HV) | Check OMS: 11168250 - 120 Halls Road | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.005708 | 11 | 2017 | 2016-05-25 | C | 6 | 0.005708 | 1.8042e-05
1 | 11167698 | 2016-05-25 10:13 | 2016-05-25 16:35 | 382 | 2 | 764.8667 | 0.0023 | 0.002281 | 6.014e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7095 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | T7095 replaced tx - spoke to Todd and he advised just to complete fm from site - Todd advised the ONC will complete tomorrow. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.002281 | 11 | 2017 | 2016-05-25 | C | 2 | 0.002281 | 6.014e-06
1 | 11167767 | 2016-05-25 10:17 | 2016-05-25 17:00 | 402 | 1 | 402.9833 | 0.0012118 | 0.001202 | 3.007e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W2440 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 15:12 - Retailer called for an ETA on the FM heading back to replace TX. Spoke to the SMC and Jared was currently at the depot picking up the gear he needed before heading back to replace.1 X transformer replaced W2440 | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.001202 | 11 | 2017 | 2016-05-25 | C | 1 | 0.001202 | 3.007e-06
1 | 11168221 | 2016-05-25 10:52 | 2016-05-25 12:59 | 126 | 1 | 126.8 | 0.00038129 | 0.000372 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2987 | FUSE - ELEMENT/LINK (HV) | 2 X 6AMP WEATHER | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000372 | 11 | 2017 | 2016-05-25 | C | 1 | 0.000372 | 3.007e-06
1 | 11168353 | 2016-05-25 11:04 | 2016-05-25 16:00 | 295 | 1 | 295.7333 | 0.00088927 | 0.00088 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 4872T | FUSE - ELEMENT/LINK (HV) | 2 x 3A.. Weather | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.00088 | 11 | 2017 | 2016-05-25 | C | 1 | 0.00088 | 3.007e-06
1 | 11168391 | 2016-05-25 11:11 | 2016-05-25 15:47 | 276 | 4 | 1104.8 | 0.0033221 | 0.003286 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2425 | FUSE - ELEMENT/LINK (HV) | 2 X 3AMP | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.003286 | 11 | 2017 | 2016-05-25 | C | 4 | 0.003286 | 1.2028e-05
1 | 11168406 | 2016-05-25 11:14 | 2016-05-25 14:56 | 222 | 405 | 31275.5833 | 0.094046 | 0.090392 | 0.0012178 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | F12716 | SURGE ARRESTOR (HV) | CB 1 tripped on E/F flags, received a call from North Power contractor that at pole F12716 saw a flash on the pole, faultman found lightning arrestors were blown line was isolated at ABS IC1066 to replace all 3 lightning arrestors. 3 X 11KV lightning arrestors replaced. 2r line patrol 1220 2r repair 1304 | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.090392 | 11 | 2017 | 2016-05-25 | C | 405 | 0.090392 | 0.0012178
1 | 11171294 | 2016-05-25 11:21 | 2016-05-25 14:25 | 183 | 1 | 183.6833 | 0.00055234 | 0.000543 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X1552 | FUSE - ELEMENT/LINK (HV) | FM has advised 2x HV fuses blown - This job will be attended after 11166488,. FM will provide onsite off site times as he is working he way down the road repairing faults from lightning. onsite 12.15. replaced 2x 3a HV fuse link at X1552, pole#780443, OH due to lightning, nothing else repaired or replaced, adjacent assets up to powerco standard. could not work through control as had no comms, will advise them now | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000543 | 11 | 2017 | 2016-05-25 | C | 1 | 0.000543 | 3.007e-06
1 | 11171350 | 2016-05-25 11:26 | 2016-05-25 12:38 | 72 | 4 | 289 | 0.00086902 | 0.000832 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t8261 | FUSE - ELEMENT/LINK (HV) | 2 X 6Amp Fuses due to weather. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.000832 | 11 | 2017 | 2016-05-25 | C | 4 | 0.000832 | 1.2028e-05
1 | 11171597 | 2016-05-25 11:44 | 2016-05-25 13:18 | 94 | 4 | 377.4667 | 0.001135 | 0.001098 | 1.2028e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3130T | FUSE - ELEMENT/LINK (HV) | 3 X 2 Amp Fuses due to weather | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.001098 | 6.6 | 2017 | 2016-05-25 | C | 4 | 0.001098 | 1.2028e-05
1 | 11172587 | 2016-06-22 09:20 | 2016-06-22 13:00 | 220 | 3 | 660 | 0.0019838 | 0.001956 | 9.0172e-06 | NAPA ID:19288 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > STONEY CREEK | 11 | Planned | 019288 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | t2/541 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace 11KV Trani T2/541 & Trani arms | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.000978 | 5.5 | 2017 | 2016-06-22 | B | 3 | 0.001956 | 9.0172e-06
1 | 11175631 | 2016-05-25 14:19 | 2016-05-25 15:40 | 81 | 60 | 4860 | 0.014614 | 0.014072 | 0.00018042 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758744 | CROSSARM - WHOLE ASSEMBLY | Faultman found broken cross arm & insulator at pole 758744, line was isolated at Fused ABS 5400 to replace cross arm. 1 X 11KV cross arm & all hardware replaced. | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.014072 | 6.6 | 2017 | 2016-05-25 | C | 60 | 0.014072 | 0.00018042
1 | 11175637 | 2016-05-25 12:23 | 2016-05-25 13:35 | 71 | 139 | 9980.2 | 0.03001 | 0.028756 | 0.00041797 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Q31 | UNKNOWN | CB Q31 tripped on A, B & C phase O/C & E/F flags, faultman found the lightning arrestors on ABS 5919 all blown and also the cable termination are all burnt between ABS 5919 & Links Q32 & ABS Q35, this is been DNO'd. DNO Tag 160538 | F5 | CLIMIE RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.028756 | 11 | 2017 | 2016-05-25 | C | 139 | 0.028756 | 0.00041797
1 | 11175778 | 2016-05-25 12:23 | 2016-05-25 15:47 | 204 | 119 | 9150.5833 | 0.027516 | 0.026442 | 0.00071266 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC5667 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | tx TC5667 needs to be replaced tomorrow 26/5 customer happy having no power to shed tonight. FM to attend and replace tx -spoke to David Horn and he advised to put 2R request through for tx to be replaced 26/5 NOTE : Access to Transformer TC5667 Site is resticted due to weather/Ground conditions. FM Reports that it only feeds a shed. To be replasced when access is possible.Line was isolated at Fuses FC4193 to replace transformer TC5667. 1 X transformer replaced | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.026442 | 11 | 2017 | 2016-05-25 | C | 119 | 0.026442 | 0.00071266
1 | 11176698 | 2016-05-25 12:53 | 2016-05-25 15:54 | 181 | 2 | 362.9333 | 0.0010913 | 0.001073 | 6.014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1971 | FUSE - ELEMENT/LINK (HV) | 3 X 2AMP | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.001073 | 11 | 2017 | 2016-05-25 | C | 2 | 0.001073 | 6.014e-06
1 | 11177551 | 2016-05-25 14:23 | 2016-05-25 15:50 | 87 | 2 | 174.3333 | 0.00052422 | 0.000506 | 6.014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1034 | FUSE - ELEMENT/LINK (HV) | 3 x 6 AMP FUSE | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000506 | 11 | 2017 | 2016-05-25 | C | 2 | 0.000506 | 6.014e-06
1 | 11177809 | 2016-05-25 14:51 | 2016-05-25 15:39 | 48 | 52 | 2496 | 0.0075055 | 0.007036 | 0.00015636 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 742536 | INSULATOR | Faultman found broken strain insulator and broken dead ends, line was isolated at ABS's 305, 327 & 344, to replace the strain insulator and the dead ends. 1 X 11KV Strain insulator. 2 X dead ends replaced. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.007036 | 11 | 2017 | 2016-05-25 | C | 52 | 0.007036 | 0.00015636
1 | 11178131 | 2016-05-25 15:02 | 2016-05-25 15:09 | 6 | 1 | 6.5667 | 1.9746e-05 | 1e-05 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2553 | FUSE - ELEMENT/LINK (HV) | 2 X 2AMP FUSES | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 1e-05 | 11 | 2017 | 2016-05-25 | C | 1 | 1e-05 | 3.007e-06
1 | 11178166 | 2016-06-23 08:45 | 2016-06-23 13:25 | 280 | 5 | 1400 | 0.004208 | 0.004162 | 1.5028e-05 | NAPA ID:19173 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 019173 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 786506 | NONE | Replace defect pole behind line fuses 280 Pole no 786506 786505 786497. Works location: Napier Taihape Rd. WO 30018074 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.002081 | 5.5 | 2017 | 2016-06-23 | B | 5 | 0.004162 | 1.5028e-05
1 | 11178236 | 2016-06-18 11:00 | 2016-06-18 12:02 | 62 | 46 | 2852 | 0.0085729 | 0.008158 | 0.00013827 | NAPA ID:20485 TP_LINTON GXP > TURITEA SUB | 11 | Planned | 020485 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | H101 | NONE | Liven Linton Express feeder from new CB6 to ABS 10116. Disconnect Linton and Linton Express Feeders at Pole P00184 (temp jumpers) | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.004079 | 5.5 | 2017 | 2016-06-18 | B | 46 | 0.008158 | 0.00013827
1 | 11178272 | 2016-06-22 09:00 | 2016-06-22 16:16 | 435 | 65 | 28333.5 | 0.085163 | 0.084576 | 0.00019537 | NAPA ID:20589 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | 020589 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Transformer T9/27 | NONE | Tree removal. Works location: Waihi Valley Rd. WO 30026290 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.042288 | 5.5 | 2017 | 2016-06-22 | B | 65 | 0.084576 | 0.00019537
1 | 11178280 | 2016-05-25 15:17 | 2016-05-25 16:07 | 50 | 3 | 151 | 0.00045406 | 0.000426 | 9.021e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T734 | FUSE - ELEMENT/LINK (HV) | 2 X 2AMP | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000426 | 11 | 2017 | 2016-05-25 | C | 3 | 0.000426 | 9.021e-06
1 | 11178288 | 2016-05-25 15:17 | 2016-05-25 16:25 | 68 | 134 | 9147.7333 | 0.027507 | 0.026298 | 0.00040294 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 6533 | FUSE - ELEMENT/LINK (HV) | Car has hit a pole and driven out. House has no power. 3.23pm advised at svs hub & emailed & adv control 3 x 40 amp fuses caused by car pole ndr # N100160 | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.026298 | 11 | 2017 | 2016-05-25 | C | 134 | 0.026298 | 0.00040294
1 | 11178347 | 2016-06-23 09:00 | 2016-06-23 15:32 | 392 | 65 | 25480 | 0.076585 | 0.075998 | 0.00019537 | NAPA ID:20590 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | 020590 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Transformer T9/27 | NONE | Tree Removal. Works location: Waihi Valley Rd. WO 30026290 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.037999 | 5.5 | 2017 | 2016-06-23 | B | 65 | 0.075998 | 0.00019537
1 | 11178947 | 2016-05-25 16:08 | 2016-05-25 20:10 | 242 | 362 | 35646.05 | 0.10719 | 0.10392 | 0.0019756 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 732209 | CROSSARM - WHOLE ASSEMBLY | Replace crossarm complete. CB r41 trip e/f found broken crossarm at pole 732209. 2r line patrol 1706 2r repair 1812 | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.10392 | 11 | 2017 | 2016-05-25 | C | 362 | 0.10392 | 0.0019756
1 | 11180283 | 2016-05-25 15:45 | 2016-05-25 19:00 | 194 | 1042 | 73108.2 | 0.21984 | 0.21044 | 0.0031333 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB U30 | UNKNOWN | CB U30 tripped no flags, line was patrolled and sectionalised and no fault was found. 2r line patrol 1735 no repair | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.21044 | 11 | 2017 | 2016-05-25 | C | 1042 | 0.21044 | 0.0031333
1 | 11181429 | 2016-05-25 17:07 | 2016-05-25 17:34 | 26 | 1 | 26.6833 | 8.0237e-05 | 7.1e-05 | 3.007e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | duplicate job | F2 | MALEME EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 7.1e-05 | 11 | 2017 | 2016-05-25 | C | 1 | 7.1e-05 | 3.007e-06
1 | 11182951 | 2016-05-25 17:13 | 2016-05-25 21:18 | 245 | 4 | 981.8667 | 0.0029525 | 0.002916 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC514 | FUSE - ELEMENT/LINK (HV) | James Brier attended. Reloaded, relivened 2x 3A HV Fuses. Lightning in the area at the time. 7.28pm called customer at 58 old Netherton road to confirm if their power restored? customer not home advised fm replaced hv fuse so they should have power. customer will check when she gets home 7.31pm tried calling customer on home phone 66 old netherton road ph engaged | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002916 | 11 | 2017 | 2016-05-25 | C | 4 | 0.002916 | 1.2028e-05
1 | 11182965 | 2016-05-25 17:14 | 2016-05-25 21:28 | 253 | 4 | 1014.1333 | 0.0030495 | 0.003013 | 1.2028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1954 | FUSE - ELEMENT/LINK (HV) | 2 x 2A HV Fuses | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.003013 | 11 | 2017 | 2016-05-25 | C | 4 | 0.003013 | 1.2028e-05
1 | 11185098 | 2016-05-26 04:49 | 2016-05-26 09:45 | 296 | 355 | 70505.0333 | 0.21201 | 0.2088 | 0.0010675 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | K0910 | NONE | CB 1 tripped on A & B phase O/C flags, a car had hit the trees causing the trees to fall over onto the lines, lines were not broken, trees came to rest against the lines. Line was isolated at ABS's IC531 & 573 so tree contractor could cut away the trees at pole K0910. NDR: 38708. | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.2088 | 11 | 2017 | 2016-05-26 | C | 355 | 0.2088 | 0.0010675
1 | 11186441 | 2016-05-28 09:30 | 2016-05-28 12:30 | 180 | 19 | 3420 | 0.010283 | 0.010112 | 5.713e-05 | NAPA ID:21127 TP_MANGAMAIRE GXP > MANGAMUTU SUB > FONTERRA WWTP | 11 | Planned | 021127 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T7/153 | NONE | To change badly leaking TX Plus old H/W pole. Works location: Bridge Rd. WO 30006776 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.005056 | 5.5 | 2017 | 2016-05-28 | B | 19 | 0.010112 | 5.713e-05
1 | 11186651 | 2016-06-22 08:30 | 2016-06-22 13:55 | 325 | 9 | 2925 | 0.0087918 | 0.00871 | 2.7052e-05 | NAPA ID:20522 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 020522 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7054 | NONE | 11kv pole and xarm replacements. Works location: Palmers Rd, Masterton. WO 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.004355 | 5.5 | 2017 | 2016-06-22 | B | 9 | 0.00871 | 2.7052e-05
1 | 11405663 | 2016-05-25 08:53 | 2016-05-25 10:35 | 102 | 2 | 204 | 0.00061343 | 0.000595 | 6.014e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | T2254 | FUSE - ELEMENT/LINK (HV) | Is outgage Job for 11166536 | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000595 | 11 | 2017 | 2016-05-25 | C | 2 | 0.000595 | 6.014e-06
1 | 11405812 | 2016-05-26 09:33 | 2016-05-26 12:20 | 167 | 1 | 167.3 | 0.00050306 | 0.000494 | 3.0069e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T2914 | FUSE - ELEMENT/LINK (HV) | Reload 2 x 3A Lightening | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000494 | 11 | 2017 | 2016-05-26 | C | 1 | 0.000494 | 3.0069e-06
1 | 11406191 | 2016-05-26 10:14 | 2016-05-26 13:30 | 195 | 182 | 3885 | 0.011682 | 0.01004 | 6.3146e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - FIRE | 808709 | POLE | 1R - Pole on fire. Powerco pole. Will most likely need replacing. Called in by Kyle while on routine inspections (RT 592). Advised svs hub 10:07am. Pole 808709 - Te Muna Road - Martinborough. Materials Used 1 x Pole, 1 x HT Cross arm, 1 x LV Cross arm, 3 x HT Insulators and 2 x LV Insulators. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.01004 | 11 | 2017 | 2016-05-26 | C | 182 | 0.01004 | 6.3146e-05
1 | 11494036 | 2016-06-23 08:30 | 2016-06-23 14:30 | 360 | 20 | 7200 | 0.021641 | 0.02146 | 6.0114e-05 | NAPA ID:20529 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 020529 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7466 | NONE | replace 11kv poles and hardware. Works location: Donovans Rd, Masterton. WO 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.01073 | 5.5 | 2017 | 2016-06-23 | B | 20 | 0.02146 | 6.0114e-05
1 | 11494043 | 2016-06-14 09:00 | 2016-06-14 11:17 | 137 | 65 | 8905 | 0.026769 | 0.026183 | 0.0001954 | NAPA ID:20549 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 020549 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 367420 | NONE | Install RL15 at pole 367420. ABS 304 stays. Run new conductor from pole 248910 2 spans. Commission new RL15 9997. Works location: Rangihau Coroglen, Whitianga. WO 30002507 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.013092 | 5.5 | 2017 | 2016-06-14 | B | 65 | 0.026183 | 0.0001954
1 | 11494540 | 2016-05-26 10:53 | 2016-05-26 16:46 | 352 | 249 | 26220.4667 | 0.078844 | 0.076597 | 0.00074873 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C218 | CROSSARM - WHOLE ASSEMBLY | FRM CB 4 tripped Flags EF , PH C, Ground Fault. Line was patrolled by and sectionalised and a broken cross arm was found at pole C218. Line was isolated at ABS's 607 & IC1266. 1 X 11kV cross arm & all hardware replaced. | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.076597 | 11 | 2017 | 2016-05-26 | C | 249 | 0.076597 | 0.00074873
1 | 11495357 | 2016-05-26 11:01 | 2016-05-26 14:20 | 198 | 1 | 198.7 | 0.00059748 | 0.000588 | 3.0069e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 3577T | FUSE - ELEMENT/LINK (HV) | Reload 2 x 2A Lightening | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.000588 | 11 | 2017 | 2016-05-26 | C | 1 | 0.000588 | 3.0069e-06
1 | 11495373 | 2016-06-29 08:30 | 2016-06-29 14:14 | 344 | 9 | 3096 | 0.0093047 | 0.009223 | 2.7049e-05 | NAPA ID:20524 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 020524 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7054 | NONE | Replace 11kv poles and hardware. Works location: Palmers Rd, Masterton. WO 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0046115 | 5.5 | 2017 | 2016-06-29 | B | 9 | 0.009223 | 2.7049e-05
1 | 11495622 | 2016-06-30 08:30 | 2016-06-30 14:09 | 339 | 6 | 2034 | 0.0061129 | 0.006058 | 1.8032e-05 | NAPA ID:20535 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 020535 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11069 | NONE | Replace 11kV poles and hardware. Works location: Knights Rd, Masterton. WO 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.003029 | 5.5 | 2017 | 2016-06-30 | B | 6 | 0.006058 | 1.8032e-05
1 | 11495673 | 2016-06-17 08:39 | 2016-06-17 15:29 | 410 | 10 | 3886 | 0.011681 | 0.011591 | 3.006e-05 | NAPA ID:20609 TP_PIAKO GXP > WALTON SUB > CAMPBELL RD | 11 | Planned | 020609 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole H0933 | NONE | Carryout out maintenance: replace DNO160314 764 to DDO structure and complete varying tasks of crossarm, inline conductor joints, staywire, pole replacements. Works location: Curr Rd, Walton. WO 30026168 | F4 | CAMPBELL RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0057955 | 5.5 | 2017 | 2016-06-17 | B | 10 | 0.011591 | 3.006e-05
1 | 11541891 | 2016-05-26 14:08 | 2016-05-26 14:10 | 1 | 1 | 1.1167 | 3.3577e-06 | 0 | 3.0069e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3587T | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer 3587T. Cause: lightning. Used 3 x 2 amp Fuses. See 11117767 | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0 | 6.6 | 2017 | 2016-05-26 | C | 1 | 0 | 3.0069e-06
1 | 11542065 | 2016-05-26 20:30 | 2016-05-26 22:12 | 102 | 100 | 10200 | 0.030671 | 0.029768 | 0.0003007 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP543 | JOINT - CONDUCTOR JOINT | Fault man has requested a 2R for an additional fault man as he is not qualified to make off an 11kV cable. To be decided at invoicing level if meets criteria of 2R work after scope of work. Repaired jumper on cable & tested OK | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.029768 | 11 | 2017 | 2016-05-26 | C | 100 | 0.029768 | 0.0003007
1 | 11542118 | 2016-05-26 14:42 | 2016-05-26 15:20 | 38 | 1 | 38.2167 | 0.00011492 | 0.000105 | 3.0069e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | M83 | FUSE - ELEMENT/LINK (HV) | Reload 2 x 3A Lightening | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000105 | 11 | 2017 | 2016-05-26 | C | 1 | 0.000105 | 3.0069e-06
1 | 11543260 | 2016-06-20 09:00 | 2016-06-20 11:20 | 140 | 22 | 3080 | 0.009258 | 0.009059 | 6.6128e-05 | NAPA ID:19420 TP_WAIHOU GXP > TAHUNA SUB > TE PUNINGA | 11 | Planned | 019420 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole K0165 | NONE | Replace termination arms at pole K0165 and reposition Staywire. Works location: Whakahoro Rd, Te Puninga. WO 30026350 | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.0045295 | 5.5 | 2017 | 2016-06-20 | B | 22 | 0.009059 | 6.6128e-05
1 | 11543454 | 2016-05-26 17:23 | 2016-05-26 19:00 | 97 | 21 | 2037 | 0.0061252 | 0.005935 | 6.3146e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771610 | BINDER | Line down at Pole 771610. 6 mtrs Squirrel 2 sleeves and binder | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.005935 | 11 | 2017 | 2016-05-26 | C | 21 | 0.005935 | 6.3146e-05
1 | 11545920 | 2016-05-26 20:43 | 2016-05-26 21:40 | 57 | 111 | 6354.75 | 0.019108 | 0.018107 | 0.00033377 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | G181T | FUSE - ELEMENT/LINK (HV) | 3 x 25A HV Fuses | F2 | MAIN ST 12 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 0.018107 | 11 | 2017 | 2016-05-26 | C | 111 | 0.018107 | 0.00033377
1 | 11545969 | 2016-05-26 20:43 | 2016-05-26 22:23 | 99 | 24 | 2389.6 | 0.0071854 | 0.006968 | 7.2167e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 495 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.006968 | 11 | 2017 | 2016-05-26 | C | 24 | 0.006968 | 7.2167e-05
1 | 11550594 | 2016-05-27 07:09 | 2016-05-27 08:40 | 91 | 16 | 1458.1333 | 0.0043845 | 0.00424 | 4.811e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2951 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 15A fuses | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.00424 | 11 | 2017 | 2016-05-27 | C | 16 | 0.00424 | 4.811e-05
1 | 11550841 | 2016-05-27 07:54 | 2016-05-27 12:03 | 249 | 422 | 9674.0333 | 0.029089 | 0.025282 | 0.001759 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 2742 | UNKNOWN | CB 2742 tripped on O/C neutral time flags, line was patrolled and sectionalised and no fault was found, suspect a bird strike, the line will be flown by helicopter with thermal camera on Monday 30/05/16. 2r line patrol 0910 2r repair nil | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.025282 | 33 | 2017 | 2016-05-27 | C | 422 | 0.025282 | 0.001759
1 | 11551733 | 2016-05-27 08:52 | 2016-05-27 10:40 | 107 | 1 | 107.85 | 0.00032429 | 0.000315 | 3.0069e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T1033 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000315 | 11 | 2017 | 2016-05-27 | C | 1 | 0.000315 | 3.0069e-06
1 | 11551904 | 2016-06-02 23:24 | 2016-06-03 05:20 | 356 | 205 | 73041.5 | 0.21961 | 0.21776 | 0.00061636 | NAPA ID:21164 TP_WAIKINO GXP | 33 | Planned | 021164 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N2210 | NONE | Reinstate 33kV line after fault repairs. Works location: Paeroa. WO 30007220 | S2 | WAIKINO242-PAEROA 33KV | WAIKINO | Valley | TP_WAIKINO | Eastern Electricity | POWERCO | 0.10888 | 16.5 | 2017 | 2016-06-02 | B | 205 | 0.21776 | 0.00061636
1 | 11552386 | 2016-05-27 09:42 | 2016-05-27 11:58 | 136 | 1 | 136.1833 | 0.00040949 | 0.0004 | 3.0069e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | x1319 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuses | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.0004 | 11 | 2017 | 2016-05-27 | C | 1 | 0.0004 | 3.0069e-06
1 | 11553093 | 2016-06-15 02:00 | 2016-06-15 02:03 | 2 | 1363 | 0 | 0 | 0 | 0 | NAPA ID:20573 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | 020573 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SA2-010 | NONE | Change HV Poles and Xarms Between SA2 010 and Temp ABS 42. Backfeed required from KPT2 via 9405/2. 2x HV cable terminations At Poles 207532 & 20763601. Replace condemned Pole 207519. Works location: Seaforth Rd, Athenree. WO 30017825. Job did not proceed due to car vs pole in the same area. New application will be done to continue the work. | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0 | 5.5 | 2017 | 2016-06-15 | B | 1363 | 0 | 0
1 | 11553154 | 2016-06-15 12:40 | 2016-06-15 13:12 | 32 | 2 | 64 | 0.00019239 | 0.000174 | 6.0121e-06 | NAPA ID:20979 TP_PIAKO GXP > TATUA SUB | 11.00000000 | Planned | 020979 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB 17 | NONE | Maintain 11kV CB's at Tatua Substation, Each CB opened in turn for service. Note:- Either CB2 or CB17 must be closed at all times to supply factory site without a break. Works location: Tatua Sub. WO 30022827 | F1 | TATUA B | PIAKO | Valley | TATUA SUB | Eastern Electricity | POWERCO | 8.7e-05 | 5.5 | 2017 | 2016-06-15 | B | 2 | 0.000174 | 6.0121e-06
1 | 11554399 | 2016-05-27 15:04 | 2016-05-27 15:29 | 25 | 11505 | 152361.0333 | 0.45813 | 0.35435 | 0.034594 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | 60 | CIRCUIT BREAKER (HV) | Kopu GXP Tairua CB60 tripped on A, B and C phase O/C during planned switching on NAPA 20544 causing LOS to Whitianga and Coromandel Substations.Safety Manager 623708 | F3 | BUFFALO BEACH | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.35435 | 11 | 2017 | 2016-05-27 | C | 11505 | 0.35435 | 0.034594
1 | 11568185 | 2016-05-29 09:15 | 2016-05-29 14:33 | 317 | 12 | 3815.4 | 0.011472 | 0.011363 | 3.6082e-05 | Referral | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 770866 | POLE | Truck Hit Pole 770866 27.05.2016. This job is to replace the pole. Need to talk to business to work out time | F1 | BRYCE ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.011363 | 11 | 2017 | 2016-05-29 | C | 12 | 0.011363 | 3.6082e-05
1 | 11569903 | 2016-05-28 01:13 | 2016-05-28 03:57 | 163 | 283 | 23703.6167 | 0.071273 | 0.06872 | 0.0016087 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715096 | BINDER | Replaced Blinder at Pole 715096. 2r line patrol 0210. 2r repair 0332 | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.06872 | 11 | 2017 | 2016-05-28 | C | 283 | 0.06872 | 0.0016087
1 | 11570721 | 2016-05-28 01:04 | 2016-05-28 01:10 | 6 | 1 | 6.0667 | 1.8242e-05 | 9e-06 | 3.0068e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | KA7 - will need to recreate | UNKNOWN | Whole Feeder was out No job For Feeder fault. The connectivity is broken in emap. This will have to be created when error fixed. | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 9e-06 | 11 | 2017 | 2016-05-28 | C | 1 | 9e-06 | 3.0068e-06
1 | 11571331 | 2016-05-28 05:26 | 2016-05-28 06:41 | 75 | 5 | 375 | 0.0011276 | 0.001082 | 1.5034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | CA465 | NONE | Fuses CA465 found tripped after reports of no power. Tree branches found over line and removed OK with fuse stick. No damage, relivened. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.001082 | 11 | 2017 | 2016-05-28 | C | 5 | 0.001082 | 1.5034e-05
1 | 11572423 | 2016-05-28 05:48 | 2016-05-28 12:00 | 371 | 1043 | 89072.1667 | 0.26783 | 0.25842 | 0.0031362 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 763469 | JOINT - CONDUCTOR JOINT | Tripping on Waitara East CBU30, no flags. Feeder sectionalised / patrolled with 2 Faults found. FAULT 1 - a large tree found across conductors at Pole763469. (NDR N100163). Isolation ABS 5121, 5262, 5166, 5140 and 5136 with backfeed at ABS 5310 and Sw/Gear 5010/3. Damage to conductor required 15m to repair along with 12 X 35mm sleeves. A further fault was found when recloser 5329 was closed and then tripped on EF, Phase A O/C. Pine Tree found down on conductors at Pole 763916. Isolation from fuses 5193. Repairs required 5m of No.8 wire and sleeves. All Relivened OK. 2r line patrol 0646. 2r repair 0845 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.25842 | 11 | 2017 | 2016-05-28 | C | 1043 | 0.25842 | 0.0031362
1 | 11575504 | 2016-05-28 06:31 | 2016-05-28 07:40 | 68 | 11505 | 603506.9167 | 1.8147 | 1.7109 | 0.034594 |  | 66 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1092 | UNKNOWN | Changed to 2R in consultation with ASW due to length of time required to be on line patrol. Helicopter Line Patrol authorised by Dean. No DTF Flags R O/C E/F Zone 1. Line flown by helicopter twice, no fault found. A couple of sites Identified for trees. James Kennerley going to let Colin Winch know. | S3 | KOPU1092-KAUAERANGA 66KV | KOPU | Valley | TP_KOPU | Eastern Electricity | POWERCO | 1.7109 | 66 | 2017 | 2016-05-28 | C | 11505 | 1.7109 | 0.034594
1 | 11611413 | 2016-05-28 06:39 | 2016-05-28 08:07 | 88 | 240 | 20553.1667 | 0.0618 | 0.059635 | 0.00072165 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 842760 | NONE | Tripping on CB Q11 Cardiff (No flags). Patrol found wind blown bark across the conductors at Pole 842760. Removed safely with fuse stick with no damage. Relivened OK. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.059635 | 11 | 2017 | 2016-05-28 | C | 240 | 0.059635 | 0.00072165
1 | 11612262 | 2016-05-28 08:31 | 2016-05-28 11:15 | 164 | 6 | 984.6 | 0.0029606 | 0.002906 | 1.8041e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 858 | FUSE - ELEMENT/LINK (HV) | 2 HT Fuses found tripped at 858. Reloadsed OK.8A Rating | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.002906 | 11 | 2017 | 2016-05-28 | C | 6 | 0.002906 | 1.8041e-05
1 | 11613060 | 2016-05-28 10:24 | 2016-05-28 14:37 | 253 | 862 | 108601.4833 | 0.32655 | 0.31877 | 0.0025919 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Q12391 | CONDUCTOR - REPAIR/REHANG | Report of pole down outside 19 The Crescent. Fault was 1x 11kV line down at pole Q12391. 11kV has contacted the 400V an Inspector is required to inspect some houses. Isolation at ABS IP627 & IP50. Back feed from ABS IP406. Repaired Line down. Materials Squirrel conductor & 2 full tension sleeves. Sean advised that all the LV inspections have been liven and everyone is back on from this HV fault, can you please add this to the job , he is just leaving site now @ 4:15pm. 2r line patrol 1158. 2r repair 1319 | F3 | WILSON RD | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.31877 | 11 | 2017 | 2016-05-28 | C | 862 | 0.31877 | 0.0025919
1 | 11615373 | 2016-05-28 13:20 | 2016-05-28 15:17 | 117 | 4 | 468 | 0.0014072 | 0.001371 | 1.2027e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M2258 | CONDUCTOR - REPAIR/REHANG | Line down at Pole M2258, Isolation at Fuses FC2168 no Back feeds available. Material 15m squirrel conductor, 2 full tension sleeves, 1 pin & insulator. Faultman attended to a part power at these fuses in the morning OMS 11612774 | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.001371 | 11 | 2017 | 2016-05-28 | C | 4 | 0.001371 | 1.2027e-05
1 | 11616342 | 2016-05-28 12:25 | 2016-05-28 15:56 | 210 | 287 | 29417.5 | 0.088454 | 0.085865 | 0.0034519 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TA9 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Tripping on Tasman CB9 on Deft. EF. Reports of direct lightning strike in area. A Number of transformers had tripped fuses and 4 were found to be destroyed. Faulty Transformers include T7040 (OMS 11621023), T7042 (OMS 11621041), T7047 (OMS 11621049), T7055 (OMS 11621056). All to be replaced. Remainder of feeder restored OK. 2r line patrol 1335 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.085865 | 11 | 2017 | 2016-05-28 | C | 287 | 0.085865 | 0.0034519
1 | 11618694 | 2016-05-28 13:22 | 2016-05-28 15:31 | 129 | 772 | 58205.3667 | 0.17502 | 0.16805 | 0.0021589 |  | 22 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 4138 | NONE | Tripping on CB4138 on Phase B O/C, EF. Feeder patrolled / sectionalised but nothing found. Restored OK. Reports of lightning in area. 2r line patrol 1447 2r repair nope | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.16805 | 22 | 2017 | 2016-05-28 | C | 772 | 0.16805 | 0.0021589
1 | 11619805 | 2016-05-28 13:37 | 2016-05-28 17:13 | 215 | 5 | 1077.5833 | 0.0032401 | 0.003195 | 1.5034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T4/108 | FUSE - ELEMENT/LINK (HV) | 4pm called cust they still have no power. @ HT fuses tripped, reloaded OK (2A Rating). Lightning | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.003195 | 11 | 2017 | 2016-05-28 | C | 5 | 0.003195 | 1.5034e-05
1 | 11620634 | 2016-05-28 13:33 | 2016-05-28 15:27 | 114 | 2 | 228.5667 | 0.00068727 | 0.000669 | 6.0137e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T4/326 | FUSE - ELEMENT/LINK (HV) | 3 Fuses tripped, relivened OK Lightning (2A) | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.000669 | 11 | 2017 | 2016-05-28 | C | 2 | 0.000669 | 6.0137e-06
1 | 11620663 | 2016-05-28 13:27 | 2016-05-28 18:30 | 302 | 4 | 1211.5333 | 0.0036429 | 0.003606 | 1.2027e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | C4148 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Defective transformer replaced after lightning strike. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.003606 | 11 | 2017 | 2016-05-28 | C | 4 | 0.003606 | 1.2027e-05
1 | 11621023 | 2016-05-28 15:57 | 2016-05-29 00:25 | 507 | 3 | 1523.8 | 0.0045819 | 0.004554 | 9.0205e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7040 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace TX T7040. This is associated with OMS 11616342. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.004554 | 11 | 2017 | 2016-05-28 | C | 3 | 0.004554 | 9.0205e-06
1 | 11621041 | 2016-05-28 15:59 | 2016-05-29 00:25 | 505 | 18 | 2506.3 | 0.0075361 | 0.007373 | 5.4123e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7042 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Changed transformer T7042 due to lightning strike. Associated with OMS 11616342 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.007373 | 11 | 2017 | 2016-05-28 | C | 18 | 0.007373 | 5.4123e-05
1 | 11621049 | 2016-05-28 16:00 | 2016-05-28 21:50 | 349 | 2 | 699.3 | 0.0021027 | 0.002084 | 6.0137e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7047 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace tx T7047 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.002084 | 11 | 2017 | 2016-05-28 | C | 2 | 0.002084 | 6.0137e-06
1 | 11621056 | 2016-05-28 16:02 | 2016-05-28 21:16 | 314 | 15 | 2249.1667 | 0.0067629 | 0.006627 | 4.5103e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7055 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace Transformer T7040 , lightning strike | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.006627 | 11 | 2017 | 2016-05-28 | C | 15 | 0.006627 | 4.5103e-05
1 | 11621661 | 2016-05-28 17:44 | 2016-05-28 19:12 | 88 | 2 | 176.0333 | 0.00052931 | 0.000511 | 6.0137e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C4118 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Tripping on 1 HT fuse at 413. reloaded OK but further fault downstream. Transformer C4118 found to be destroyed by lightning. Separate OMS No. raised for replacement. | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.000511 | 11 | 2017 | 2016-05-28 | C | 2 | 0.000511 | 6.0137e-06
1 | 11627371 | 2016-05-28 19:24 | 2016-05-28 20:32 | 67 | 1 | 67.6333 | 0.00020336 | 0.000194 | 3.0068e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7043 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6 amp fuses at T1162 | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000194 | 11 | 2017 | 2016-05-28 | C | 1 | 0.000194 | 3.0068e-06
1 | 11627454 | 2016-05-28 17:38 | 2016-05-28 19:36 | 118 | 1 | 118.1167 | 0.00035516 | 0.000346 | 3.0068e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7442 | FUSE - ELEMENT/LINK (HV) | 1 R no power. T1154 - 36 WARRENS RD - PIRINOA | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000346 | 11 | 2017 | 2016-05-28 | C | 1 | 0.000346 | 3.0068e-06
1 | 11627853 | 2016-05-28 23:37 | 2016-05-30 20:34 | 2697 | 44 | 109201.6333 | 0.32835 | 0.32796 | 0.00028264 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 364659 | CONDUCTOR - REPAIR/REHANG | Tripping on recloser 6413 on B, C Phase O/C, EF. Patrol found very large conductor broken across gully caused by downed tree. Impractical to repair during the night. Isolation from recloser to end to carryout repairs. Helicopter required during the day with 600m conductor replaced and 10 sleeves. When relivening, the Recloser tripped again. Further patrol found another conductor down (Fault No.2) with a tree causing the problem. (Isolation for this fault at Fuses 12006 - Refer new OMS 11659585 for fault No.2 Closeout). NDR fault 1: 2016M100168. 2r line patrol power restored in one | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.32796 | 11 | 2017 | 2016-05-28 | C | 44 | 0.32796 | 0.00028264
1 | 11628048 | 2016-05-28 23:49 | 2016-05-29 01:05 | 76 | 1 | 76.3333 | 0.00022952 | 0.00022 | 3.0068e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5371 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 3amp fuses at 5371 | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.00022 | 6.6 | 2017 | 2016-05-28 | C | 1 | 0.00022 | 3.0068e-06
1 | 11628202 | 2016-05-29 00:39 | 2016-05-29 06:02 | 322 | 366 | 63736.8333 | 0.19164 | 0.18834 | 0.0011005 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 764349 | CONDUCTOR - REPAIR/REHANG | Reclosed 6224 Tripped C Phase Over current, Tree found through lines. Isolated at ABS 5207, 5128 &, 5192 Due to dual lines on Poles also isolated at ABS's 5228 & 5121. Lines repaired used 300 meters 16mm conductor & 20 16mm sleeves, 50 meters 25mm conductor & 16 meters of 25 mm conductor, plus 2 x 100amp LV fuses Faultman still to supply NDR. 2r line patrol 0140. 2r repair 0408 | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.18834 | 11 | 2017 | 2016-05-29 | C | 366 | 0.18834 | 0.0011005
1 | 11629293 | 2016-05-29 02:06 | 2016-05-29 03:42 | 96 | 1061 | 102209.6667 | 0.30733 | 0.29775 | 0.0031902 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | SD3 145 | CIRCUIT BREAKER (HV) | GRE 142, BHM 82 & TGA19 tripped E/F, O/C L/O. CB 19 patrolled & twisted H/V lines found at Fuses SD3 145. (high wind & tree branches all along road ) Lines untwisted all service restored. 33kV line patrolled & livened, small section of 11/33 run in parallel no obvious fault found. Further reports of damage to customer appliances came in and these are being investigated. | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.29775 | 11 | 2017 | 2016-05-29 | C | 1061 | 0.29775 | 0.0031902
1 | 11642297 | 2016-05-29 03:36 | 2016-05-29 14:22 | 645 | 308 | 29752.2667 | 0.08946 | 0.086681 | 0.00036082 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | M2077 | POLE | P03 Car versus pole. CB 4 Trip. E/F Isolation at ABS 2527 & 2561 Back feed from Recloser RP03. Materials. 1x11metre concrete pole, 1xHV crossarm, 2xLV crossarms, 3 drop out fuses complete 2r line poatrol 0521 2r reoair 0608 | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.086681 | 11 | 2017 | 2016-05-29 | C | 308 | 0.086681 | 0.00036082
1 | 11642732 | 2016-05-29 04:27 | 2016-05-29 12:17 | 470 | 256 | 42136.8333 | 0.1267 | 0.12439 | 0.001302 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 249325 | CONDUCTOR - REPAIR/REHANG | Second 1 R applied for as Recloser S6031 has failed & needs to be switched on site. To save F/M running backwards & forwards with the switching A second F/M can be based at the recloser S6031. Tree through the line past fuses FP1752. Isolation at Fuses FP1752. Feeder Restored. Batteries in recloser were only 4 years old, a 1kVA transformer needs to be fitted to the supply side of this recloser to keep power on when there is a fault past this device. Material 3 Squirrel full tension sleeves, 10 meters of conductor. Asplundh on site to cut trees. NDR to follow. 2r line patrol 0540. 2r repair 0936 | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.12439 | 11 | 2017 | 2016-05-29 | C | 256 | 0.12439 | 0.001302
1 | 11643787 | 2016-05-29 04:46 | 2016-05-29 05:02 | 16 | 59 | 948.9167 | 0.0028532 | 0.002321 | 0.0001774 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4230 | UNKNOWN | Recloser 4230 trip reclosed after 15 mins o/c e/f | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.002321 | 11 | 2017 | 2016-05-29 | C | 59 | 0.002321 | 0.0001774
1 | 11644622 | 2016-05-29 08:05 | 2016-05-29 11:50 | 225 | 1 | 225.3167 | 0.00067749 | 0.000668 | 3.0068e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5234 | FUSE - ELEMENT/LINK (HV) | The actual location was at Fuse 5234, 2 x 3 amp HV fuses were replaced. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000668 | 11 | 2017 | 2016-05-29 | C | 1 | 0.000668 | 3.0068e-06
1 | 11644822 | 2016-05-29 10:57 | 2016-05-29 15:11 | 254 | 3 | 762 | 0.0022912 | 0.002264 | 9.0204e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3518T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | pls check 11645170 and 11645235 are related Fuses found blown at Fuses 5134, line patroled with no fault found. Fuses blew again on closing, 2 transformers hard wired to lines, transformer 3517T disconnected and fuses closed again and blew. Transformer 3518T replaced Used 1 x 30 kVA transformer 7 4 x 3 amp fuses | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.002264 | 11 | 2017 | 2016-05-29 | C | 3 | 0.002264 | 9.0204e-06
1 | 11645654 | 2016-05-29 10:10 | 2016-05-29 12:28 | 138 | 4 | 553.8667 | 0.0016654 | 0.001629 | 1.2027e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | se3-072 | FUSE - ELEMENT/LINK (HV) | 2x3amp HV fuses blown past SE3-072. Line patrolled, reloaded & livened. Possible trees | F2 | LAKES EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001629 | 11 | 2017 | 2016-05-29 | C | 4 | 0.001629 | 1.2027e-05
1 | 11645768 | 2016-05-29 13:48 | 2016-05-30 18:28 | 1720 | 59 | 15491.7167 | 0.046581 | 0.046048 | 0.0001774 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 441705 | CONDUCTOR - REPAIR/REHANG | Check to see if OMS 11647373 (1957 MANGOHANE ROAD) is related Paul checking status of this job with SMC as 1R has been completed and 2R has been rejected with notes saying 1st responder doing 2nd response work 30/05 15:30 - Retailer called to advise 5 properties at 1957 Mangohane Road are still without power. SMC have been advised and sending out an FM Temporary repairs have been made to downed conductor and will need further work. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.046048 | 11 | 2017 | 2016-05-29 | C | 59 | 0.046048 | 0.0001774
1 | 11646238 | 2016-05-29 11:12 | 2016-05-29 16:22 | 310 | 296 | 44968 | 0.13521 | 0.13254 | 0.00043899 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 823616 | CONDUCTOR - REPAIR/REHANG | CB C945 tripped x3 then A/R load dropped by ten amps. Lines down - 1590 Longbush Road, Gladstone. Tree down. ETA required by fire comms F2086889 (048010812) 40 min eta. Tree out side notice zone nearest Pole 823616. Work site Isolated at ABS C423/1 and Links C423/6. Lines repaired. Used 2 x HV insulators, 1 Fuse base and carrier, 3 x sleeves. 2r line patrol 1211. 2r repair 1256 NDR 54452 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.13254 | 11 | 2017 | 2016-05-29 | C | 296 | 0.13254 | 0.00043899
1 | 11646601 | 2016-05-29 11:27 | 2016-05-30 14:10 | 1602 | 1 | 1602.7667 | 0.0048192 | 0.00481 | 3.0068e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 41 WESTRIDGE DRIVE | UNKNOWN | FM advised full power upon arrival. Electrical inspector has already attended after the Bethlehem Fault | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.00481 | 11 | 2017 | 2016-05-29 | C | 1 | 0.00481 | 3.0068e-06
1 | 11648355 | 2016-05-29 16:35 | 2016-05-30 14:00 | 1285 | 8 | 10280 | 0.03091 | 0.030837 | 2.4055e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 230086 | POLE | Pole over on top of ridge. Will need to be straighten up during day light hours. Isolated past fuses SF6-008 Pole straightened, backfill reinstated & supply restored 14:00. Problem caused by land owner excavating around bottom of pole(s) Josh Reid to send info on this. Alicia to create Safety Manager incident. NDR 52351 | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.030837 | 11 | 2017 | 2016-05-29 | C | 8 | 0.030837 | 2.4055e-05
1 | 11648410 | 2016-05-29 15:14 | 2016-05-29 16:23 | 69 | 4 | 277.2 | 0.00083349 | 0.000797 | 1.2027e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC5303 | FUSE - ELEMENT/LINK (HV) | 2x2amp fuses blown at transforrmer TC5303 due to lightning. reloaded & livened | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.000797 | 11 | 2017 | 2016-05-29 | C | 4 | 0.000797 | 1.2027e-05
1 | 11650267 | 2016-05-29 17:27 | 2016-05-29 18:10 | 43 | 4 | 173.9333 | 0.00052299 | 0.000486 | 1.2027e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 8095 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses 8095 - cause Bird Strike Used 2 x 10amp fuses | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000486 | 11 | 2017 | 2016-05-29 | C | 4 | 0.000486 | 1.2027e-05
1 | 11650682 | 2016-05-29 18:51 | 2016-05-30 11:32 | 1000 | 1 | 1000.6333 | 0.0030087 | 0.002999 | 3.0068e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 8 NORWICH PLACE | NONE | **Please call Shelley on 027 388 8846 to advise when power has been restored and next steps (if required)** NNF - Full power upon arrival. Due to the Bethlehem outage, contractor had already attended. | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.002999 | 11 | 2017 | 2016-05-29 | C | 1 | 0.002999 | 3.0068e-06
1 | 11651510 | 2016-05-29 21:24 | 2016-05-29 23:26 | 122 | 3 | 366.8 | 0.0011029 | 0.001075 | 9.0204e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1105 | FUSE - ELEMENT/LINK (HV) | 2 HT Fuses found tripped at T1105 after LV conductor clash. Reloaded OK with 3A. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.001075 | 11 | 2017 | 2016-05-29 | C | 3 | 0.001075 | 9.0204e-06
1 | 11651677 | 2016-05-29 22:07 | 2016-05-30 00:14 | 126 | 684 | 13109.6667 | 0.039418 | 0.033248 | 0.00036683 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 4236 | UNKNOWN | Tripping on Recloser CB4236 on O/C B- C Phase, EF. Feeder patrolled / sectionalised but nothing found. Livened OK. 2r line patrol 2304 no repair | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.033248 | 11 | 2017 | 2016-05-29 | C | 684 | 0.033248 | 0.00036683
1 | 11652597 | 2016-05-30 07:15 | 2016-05-30 09:15 | 119 | 9 | 1079.7 | 0.0032464 | 0.003165 | 2.7061e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | FC2372 | FUSE - ELEMENT/LINK (HV) | Reload Reliven. 2 x 8A Fuses. Patrolled - Cause Unknown | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.003165 | 11 | 2017 | 2016-05-30 | C | 9 | 0.003165 | 2.7061e-05
1 | 11652676 | 2016-05-30 07:27 | 2016-05-30 11:28 | 241 | 6 | 1447.9 | 0.0043535 | 0.004299 | 1.8041e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 858 | FUSE - ELEMENT/LINK (HV) | 2 X 8A HV Fuses | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.004299 | 11 | 2017 | 2016-05-30 | C | 6 | 0.004299 | 1.8041e-05
1 | 11653641 | 2016-05-30 09:07 | 2016-05-30 10:09 | 62 | 1 | 62.3167 | 0.00018737 | 0.000178 | 3.0067e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E90 | FUSE - ELEMENT/LINK (HV) | 2 x 15A HV Fuses | F3 | ROBERTS LINE | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.000178 | 11 | 2017 | 2016-05-30 | C | 1 | 0.000178 | 3.0067e-06
1 | 11656141 | 2016-05-30 11:48 | 2016-05-30 13:50 | 121 | 1 | 121.7 | 0.00036592 | 0.000356 | 3.0067e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X4150 | FUSE - ELEMENT/LINK (HV) | 2 x2A HV Fuses | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000356 | 11 | 2017 | 2016-05-30 | C | 1 | 0.000356 | 3.0067e-06
1 | 11657802 | 2016-06-02 09:50 | 2016-06-02 10:48 | 58 | 6 | 348 | 0.0010463 | 0.000992 | 1.804e-05 | NAPA ID:21251 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MCCABE ROAD | 11 | Planned | 021251 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC629 | AIR BREAK SWITCH - ABS (HV) | Repair replace Handle at ABS IC629 and replace pole C2894. Stage 1: Requires additional safety measures isolation of Cable from 11kV Fuse FC1041 to repair ABS Handle and replace pole C2894. Stage 2: Complete pole replacement C2894. Stage 1: Supplies effluent pumps to silver fern farms. Silver fern farms request that the pumps are only off for max 1hr. | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000496 | 5.5 | 2017 | 2016-06-02 | B | 6 | 0.000992 | 1.804e-05
1 | 11658649 | 2016-05-30 17:41 | 2016-05-30 19:15 | 94 | 23 | 2167.75 | 0.0065179 | 0.00631 | 6.9156e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 997 | FUSE - ELEMENT/LINK (HV) | Check OMS: 11658804 - 463 MANGAHOE ROAD. 2 HT Fuses reloaded at 997. (20A) | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.00631 | 11 | 2017 | 2016-05-30 | C | 23 | 0.00631 | 6.9156e-05
1 | 11658769 | 2016-05-30 17:45 | 2016-05-30 20:26 | 160 | 3 | 482.2 | 0.0014499 | 0.001422 | 9.0203e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | R18 | FUSE - ELEMENT/LINK (HV) | Bird strike on spur line past Fuses R18 caused 3 fuses to trip. Conductors twisted by strike, untwisted OK with fuse stick. 2A Rating. | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001422 | 11 | 2017 | 2016-05-30 | C | 3 | 0.001422 | 9.0203e-06
1 | 11660152 | 2016-05-31 | 2016-05-31 15:46 | 946 | 186 | 88956.9667 | 0.26747 | 0.2658 | 0.00055926 |  | 22 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 850049 | POLE | Tripping on Pukepapa CB1133 on Phase B O/C. Fault caused by Truck / Pole on Corner of Wings Line & SH1. 22kV Conductors broken. Isolation between ABS 800 and 796 with backfeed at ABS 539. Extensive damage to pole. 1 x Pole. 1 x 22kV x-arm and insulators. LV pin Insulator. 160mtrs Squirrel Conductor. NDR to follow 2r line patrol 0120. 2r repair 1103. NDR 30367 | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.2658 | 22 | 2017 | 2016-05-30 | C | 186 | 0.2658 | 0.00055926
1 | 11660366 | 2016-05-31 01:26 | 2016-05-31 10:35 | 549 | 873 | 29598.8 | 0.088995 | 0.08112 | 0.00043597 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Recloser 575 | UNKNOWN | Recloser 575 Trip. E/F. Feeder sectionalised but no fault found. Cause Unknown. 2r line patrol 0403 no repair | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.08112 | 11 | 2017 | 2016-05-31 | C | 873 | 0.08112 | 0.00043597
1 | 11661632 | 2016-05-31 10:08 | 2016-05-31 10:38 | 30 | 1 | 30 | 9.0202e-05 | 8.1e-05 | 3.0067e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 765348 | CONDUCTOR - REPAIR/REHANG | Report from Radar, Poletec that a tree is leaning up against the 11kV Lines. Radars Ph 0212544596. Line isolated at Fuses 4044 and tree removed between Poles 765348 and 765349 | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 8.1e-05 | 11 | 2017 | 2016-05-31 | C | 1 | 8.1e-05 | 3.0067e-06
1 | 11662651 | 2016-05-31 08:24 | 2016-05-31 10:20 | 115 | 482 | 24205.2333 | 0.072778 | 0.06843 | 0.0021077 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H2948 | INSULATOR | This Job needs a protection review as fault was beyond RC26 but tripped CB 3 at 08:25, Walton Sub, CB 3 Piakoiti Feeder Tripped, E/F, L/O. At the same time, Recloser RC26 Tripped, Ph C O/C, E/F, L/O. Was backfeeding part of Piako CB 6 Kereone Feeder at the time: Sectionaliser 9720 was closed & ABS IC765 Open. Faultmen dispatched & investigation began. Checked Walton School and Recloser RC26. Believed protection had operated incorrectly and fault was most likely beyond RC26. CB 3 Closed. Remainder of feeder beyond RC26 sectionalised. Found broken insulator at Pole H2948. Isolated Lines at ABS IC749 & Links 9720/6. Permit issued & repairs carried out. All Power Restored on Completion. Marty Keenan Attended. Replaced 1x Insulator & 1x Binder. Old Brown Insulator - Aged Equipment cause, was cracked. 2r line patrol 0905 2r repair 1003 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.06843 | 11 | 2017 | 2016-05-31 | C | 482 | 0.06843 | 0.0021077
1 | 11663783 | 2016-06-21 10:43 | 2016-06-21 15:10 | 267 | 109 | 29103 | 0.087478 | 0.086494 | 0.00032763 | NAPA ID:20659 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11 | Planned | 020659 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2066T | NONE | Replace leaking transformer 2066T with new transformer of same size. Works location: Seyton St. WO 30019686 FABS 5572 Failed during switching, additional shutdown required to bridge out OMS 11977527. Generator installed about 16:00 hours | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.043247 | 5.5 | 2017 | 2016-06-21 | B | 109 | 0.086494 | 0.00032763
1 | 11664460 | 2016-06-08 08:45 | 2016-06-09 09:02 | 1457 | 410 | 33605 | 0.10103 | 0.097331 | 0.0014581 | NAPA ID:18772 TP_CARRINGTON GXP > KATERE SUB > KATERE 12 | 11 | Planned | 018772 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Magnefix 1407 | NONE | Systematic replacement of Magnefix 1407 with new Safelink unit. This will be done in three(3) stages due to switching requirements and work to be done. This is Stage 1. First request is for switching only with lots power off for LESS THAN 5 MINUTES. This is for putting the isolations in place at magnefix for the stage 1 work. AP is to cut HV cable from 204/2 at TEMP69/1 and joint to new cable from 1407/1. Isolations kept for Stage 2 NAPA 18774. WORKS LOCATION: Culzean St. WO 30002196 | F2 | KATERE 12 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.048666 | 5.5 | 2017 | 2016-06-08 | B | 410 | 0.097331 | 0.0014581
1 | 11664775 | 2016-06-09 14:19 | 2016-06-09 14:58 | 39 | 595 | 14495 | 0.043577 | 0.03821 | 0.0017888 | NAPA ID:18775 TP_CARRINGTON GXP > KATERE SUB > KATERE 12 | 11 | Planned | 018775 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Magnefix 1407 | NONE | Systematic replacement of Magnefix 1407 with new Safelink unit. This will be done in three(3) stages due to switching requirements and work to be done. This application follows Stage 2 works NAPA 18774. This is to isolate magnefix gear to restore magnefix links at 204/2. This will only require LESS THAN 5 MINUTE outage to do switching. After supply restored, tx 1407 can be livened. HV cable from 6968/3 to remain isolated for stage 3 (NAPA 18776) works. WORKS LOCATION: Culzean St. WO 30002196 | F2 | KATERE 12 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.019105 | 5.5 | 2017 | 2016-06-09 | B | 595 | 0.03821 | 0.0017888
1 | 11665093 | 2016-05-31 14:49 | 2016-05-31 17:40 | 171 | 145 | 24795 | 0.074552 | 0.073243 | 0.00043597 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 440 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | 1 phase out on HV, not sure of cause so will patrol line to try and locate fault. HV Fuse 440 has a broken Fuse Holder. Isolation at Recloser 575 to repair. Replace Complete set Fuse Holder Bases and crossarm | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.073243 | 11 | 2017 | 2016-05-31 | C | 145 | 0.073243 | 0.00043597
1 | 11665997 | 2016-05-31 11:49 | 2016-05-31 14:20 | 150 | 5 | 754.6667 | 0.0022691 | 0.002223 | 1.5034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N4 | FUSE - ELEMENT/LINK (HV) | 2 x 6A HV Fuses | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.002223 | 11 | 2017 | 2016-05-31 | C | 5 | 0.002223 | 1.5034e-05
1 | 11666750 | 2016-05-31 15:07 | 2016-05-31 17:06 | 119 | 829 | 25314.4667 | 0.076114 | 0.068635 | 0.0024926 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 9512 | NONE | Recloser 9512 tripped to L/O. . Line sectionalised & patrolled. No fault found. All supply restored. No comms to site due to flat batteries at 9512. Sectionalising carried out via sectionaliser RP17 & 9721/2. Discussion with Downer techs identified historical battery & protection problem with this site. Recloser left open with backfeeds in place. Downer techs to address problem tomorrow under OMS 11668261. 2r line patrol 1624. 2r repair no | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.068635 | 11 | 2017 | 2016-05-31 | C | 829 | 0.068635 | 0.0024926
1 | 11670080 | 2016-06-01 07:57 | 2016-06-01 10:45 | 167 | 11 | 1843.05 | 0.0055414 | 0.005442 | 3.3073e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | sf8-002 | FUSE - ELEMENT/LINK (HV) | check oms 11670228. 307 Campbell road also affected, advised svshub to give info to FM attending to check if related. 2 x15 amp fuse and barrels SF8002 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.005442 | 11 | 2017 | 2016-06-01 | C | 11 | 0.005442 | 3.3073e-05
1 | 11671367 | 2016-06-01 11:02 | 2016-06-01 12:00 | 57 | 3 | 173.1 | 0.00052045 | 0.000493 | 9.02e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | T7/310 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000493 | 11 | 2017 | 2016-06-01 | C | 3 | 0.000493 | 9.02e-06
1 | 11671851 | 2016-06-21 09:30 | 2016-06-21 14:35 | 305 | 11 | 3355 | 0.010084 | 0.009985 | 3.3064e-05 | NAPA ID:19220 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 019220 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 800 | NONE | To replace arms and hardware. Works location: Te Poi South Rd. WO 30017838 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0049925 | 5.5 | 2017 | 2016-06-21 | B | 11 | 0.009985 | 3.3064e-05
1 | 11673245 | 2016-06-01 16:07 | 2016-06-01 17:10 | 62 | 1 | 62.7 | 0.00018852 | 0.000179 | 3.0066e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7598 | FUSE - ELEMENT/LINK (HV) | 2 x 6A HV Fuses | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000179 | 11 | 2017 | 2016-06-01 | C | 1 | 0.000179 | 3.0066e-06
1 | 11673452 | 2016-06-01 17:50 | 2016-06-01 19:41 | 111 | 7 | 777 | 0.0023362 | 0.002273 | 2.1047e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P12708 | CONDUCTOR - REPAIR/REHANG | Have advised SMC and Control Job actually past Fuses U43, Lines down caused by possible bird strike Isolated at Fuses U43. used 20 mtrs of conductor, 2 HT sleevs, 2 connectors and 2 6 amp HV fuses | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.002273 | 11 | 2017 | 2016-06-01 | C | 7 | 0.002273 | 2.1047e-05
1 | 11674631 | 2016-06-01 22:30 | 2016-06-02 15:55 | 1044 | 1411 | 100080.0333 | 0.30091 | 0.28818 | 0.0037884 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC6147 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Recloser 9607/2 tripped to L/O. E/F flag. Recloser was backfeeding part of WHT CB 4 at time of tripping due to faulty recloser 9512 being left in open position (Flat batteries). Network configuration at time - ABS IC399 was open, Sectionaliser 9721 closed & Sectionaliser RP17 closed. Line was sectionalised with 2 x A/R trips on RC20 during Sectionalising. Fault was bypassing recloser 9278 and tripping RC 20. Possibly caused by network reconfiguration during sectionalising and grading of relevant Reclosers & Sectionalisers. Review of switching sequence etc may be required by protection engineer. Fault isolated beyond beyond fuses FC2736. Fuses left open overnight due to history of terrain collapsing and damaging cable. Downer staff unable to check condition due to darkness & terrain etc. Further 1 r requested to have it checked thoroughly in morning. All other supply restored. Replaced transformer TC6147. 2r line Patrol 2342 / 2r repair 0109. | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.28818 | 11 | 2017 | 2016-06-01 | C | 1411 | 0.28818 | 0.0037884
1 | 11677431 | 2016-06-02 05:41 | 2016-06-02 07:32 | 111 | 1214 | 98920.5167 | 0.29742 | 0.28647 | 0.00365 |  | 33 | Unplanned |  | ZONE SUB EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Sanson Sub | UNKNOWN | Sanson Area has no Power cause under investigation. Empty Oil out of Tap Changer as test Showed Tap in Process staying on for more than 40 Sec which made Relay think that there was a Fault Cleaned up Contacts Tested it and Filled back up With Oil and Put back in service This was not Human Element But Had to Pick Something and this was the closet | S4 | FEILDING-SANSON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.28647 | 33 | 2017 | 2016-06-02 | C | 1214 | 0.28647 | 0.00365
1 | 11679213 | 2016-06-16 09:45 | 2016-06-16 14:46 | 301 | 10 | 3010 | 0.0090481 | 0.008957 | 3.006e-05 | NAPA ID:18793 TP_CARRINGTON GXP > CITY SUB > CITY 9 | 11.00000000 | Planned | 018793 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11klV Magnefix 388 | NONE | Systematic replacement of Magnefix 388 with new Safelink unit. This will be done in three(3) stages due to switching requirements and work to be done. This is Stage 2. (LV backfeed in place, see attached) AP is to cut HV cable from 8871/3 at magnefix ready for stage 3. Remove/cut HV cable between magnefix and tx 388 and remove magnefix gear from tx enclosure. Connect new HV cable form new 388/2 to tx 388 HV bushings. Liven switchgear from CB 9 (arc flash sub). Stage 3 (NAPA 18799). WORK LOCATION: Vivian St. WO 30018772 NO Outage - LV Backfeeds in Place | F3 | CITY 9 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.0044785 | 5.5 | 2017 | 2016-06-16 | B | 10 | 0.008957 | 3.006e-05
1 | 11679526 | 2016-06-21 08:54 | 2016-06-21 17:05 | 491 | 137 | 23632 | 0.071033 | 0.069797 | 0.00069434 | NAPA ID:20604 TP_KOPU GXP > WHITIANGA SUB > BUFFALO BEACH | 11 | Planned | 020604 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole W14302 | NONE | Change poles, xarms and reconductor between W14302 and W14305. Works location: Centennial Dr, Whitianga. WO 30019260. 15:35 Job running late due to obstructions found in the ground while trying to install poles. | F3 | BUFFALO BEACH | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.034898 | 5.5 | 2017 | 2016-06-21 | B | 137 | 0.069797 | 0.00069434
1 | 11679642 | 2016-06-02 09:41 | 2016-06-02 15:33 | 352 | 1 | 352.4667 | 0.0010597 | 0.00105 | 3.0066e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 5553E | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer 5553E blown, will be replaced today, being organised by Germaine,115 125 Puniho Road affected. Neil leaving site. Transformer 5553E was replaced. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.00105 | 11 | 2017 | 2016-06-02 | C | 1 | 0.00105 | 3.0066e-06
1 | 11679796 | 2016-06-02 09:52 | 2016-06-02 12:05 | 133 | 21 | 2794.05 | 0.0084007 | 0.008211 | 6.3139e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 7220 | FUSE - ELEMENT/LINK (HV) | HV fuses replaced. Reload reliven 2 x 10A and barrels. Cause unknown. | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.008211 | 11 | 2017 | 2016-06-02 | C | 21 | 0.008211 | 6.3139e-05
1 | 11679846 | 2016-06-23 08:46 | 2016-06-23 13:44 | 298 | 160 | 47680 | 0.14331 | 0.14187 | 0.00048091 | NAPA ID:20606 TP_KOPU GXP > WHITIANGA SUB > BUFFALO BEACH | 11 | Planned | 020606 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole W14307 | NONE | Replace Xarms and Reconductor between Poles W14307 and W14305. Works location: Centennial Dr, Whitianga. WO 30019260 | F3 | BUFFALO BEACH | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.070934 | 5.5 | 2017 | 2016-06-23 | B | 160 | 0.14187 | 0.00048091
1 | 11679953 | 2016-06-02 10:03 | 2016-06-02 12:05 | 122 | 1 | 122.25 | 0.00036756 | 0.000358 | 3.0066e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | oms 11679796 | UNKNOWN | Retailer has called to say power has been restored confirmed related to OMS 11679796 -HV fuses replaced. Reload reliven 2 x 10A and barrels. Cause unknown. | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.000358 | 11 | 2017 | 2016-06-02 | C | 1 | 0.000358 | 3.0066e-06
1 | 11682886 | 2016-06-23 09:15 | 2016-06-23 11:15 | 120 | 2 | 240 | 0.00072137 | 0.000703 | 6.0113e-06 | NAPA ID:19399 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | 019399 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P20469 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace 11KV trani T1/358 Replace LV trani arms | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.0003515 | 5.5 | 2017 | 2016-06-23 | B | 2 | 0.000703 | 6.0113e-06
1 | 11683311 | 2016-06-17 10:00 | 2016-06-17 11:03 | 63 | 108 | 6804 | 0.020453 | 0.019478 | 0.00032464 | NAPA ID:21093 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD NORTH | 11 | Planned | 021093 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5702 | NONE | Replace ABS 5702 & xarms. Works location: Broadway, Stratford. WO 30017990 | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.009739 | 5.5 | 2017 | 2016-06-17 | B | 108 | 0.019478 | 0.00032464
1 | 11683320 | 2016-06-02 12:55 | 2016-06-02 13:50 | 55 | 5 | 277.75 | 0.00083509 | 0.000789 | 1.5033e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V12573 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp plus barrels replaced due to old age. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.000789 | 11 | 2017 | 2016-06-02 | C | 5 | 0.000789 | 1.5033e-05
1 | 11683598 | 2016-06-02 13:00 | 2016-06-02 15:10 | 130 | 217 | 13664 | 0.041083 | 0.039125 | 0.0011545 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | td4-507 | JUMPER | Found LV jumper broken & vines overgrowen on transformer TD4-507, Isolated between ABS SD4-108, SD4-168, 9356/3 & 9028/1 due to Long & Crawford switch unit SD4-146 making funny noises. Isolated transformer TD4-507 at link box SD4-158, re-livened rest of area. Job complete re-isolated area to close fuses at link box, re-livened | F3 | WELCOME BAY | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.039125 | 11 | 2017 | 2016-06-02 | C | 217 | 0.039125 | 0.0011545
1 | 11684256 | 2016-07-01 09:00 | 2016-07-01 14:54 | 354 | 16 | 5664 | 0.017022 | 0.016877 | 4.8085e-05 | NAPA ID:19210 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 019210 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 278814 | NONE | LLP 1: To Br the 11kv jumpers on pole 248814 Supplying lines on Livingstone Rd. AP: To replace the lines From pole 278814 to IC1333 and from IC1333 to the end of Livingstone Rd. LLP 2: To replace the 11kv jumpers on pole 248814 Supplying lines on Livingstone Rd. Works location: Livingstone Rd. WO 30017838 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0084385 | 5.5 | 2017 | 2016-07-01 | B | 16 | 0.016877 | 4.8085e-05
1 | 11687188 | 2016-06-02 22:01 | 2016-06-03 06:51 | 529 | 348 | 32710.8167 | 0.098349 | 0.09521 | 0.0030878 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | A0373 | UNKNOWN | CB 3 tripped to L/O. B & C Ph O/C & E/F flags. Line sectionalised & patrolled. Lines down located & repaired at pole A0373. Line was isolated at ABS's 1338,1108 & 1351 and Sw/Gear 9085/3 repair line down. 1 meter 25mm copper conductor & 3 X 25mm sleeves used. | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.09521 | 11 | 2017 | 2016-06-02 | C | 348 | 0.09521 | 0.0030878
1 | 11688999 | 2016-06-03 05:03 | 2016-06-03 10:48 | 345 | 57 | 19668.8 | 0.059136 | 0.058621 | 0.00017137 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | D1520 | CONDUCTOR - REPAIR/REHANG | Faultman found lines down at pole D1520 while on way to customer fault, line was isolated at ABS 821to repair the lines down, suspect duck strike was cause as lots of ducks fling around. 30 meters of Squirrel conductor used. 4 X compression sleeves used & 2 X binders. NDR 38709. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.058621 | 11 | 2017 | 2016-06-03 | C | 57 | 0.058621 | 0.00017137
1 | 11690138 | 2016-06-03 07:41 | 2016-06-03 13:30 | 349 | 846 | 81760.3833 | 0.24582 | 0.23819 | 0.0040859 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SE6 230 | CABLE - REPAIR | Fire Event F2089716. Confirmed with control that a generator has now been put on at TE6-288 for customers affected by this outage. CB6 tripped C Ph O/C, E/F, L/O. Feeder sectionalised with cable fault located at link box SE6 230 Isolation between ABS SE6 080 & ABS SE6 222 for line break at pole 222458. Cable requires further repairs breaks still in place at pole 222458 & link box SE6 230. Transformer TE6 288 fed via ABS SE6 222 ( TPV3 ) Downer to submit application to complete repairs next week. 2r line Patrol 0831. 2r repair 1125 | F3 | CENTRAL RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.23819 | 11 | 2017 | 2016-06-03 | C | 846 | 0.23819 | 0.0040859
1 | 11691289 | 2016-06-03 08:08 | 2016-06-03 09:34 | 86 | 5703 | 109743.25 | 0.32995 | 0.27851 | 0.021984 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | cb7 | UNKNOWN | 11KV loud buzzing noise emergency shut to identify noise. PMA RH bus isolated to identify source of noise. Feeders 5 through 9 offloaded & restored in turn. Noise identified coming from CB 7 (feeding CB2 at time). CB7 isolated & backfeed for CB7 & CB2 fed via Sw/G 9024/1 (TMA 2) CB7 tested out all ok noise thought to be station intruder alarm (faulty) intruder klaxton disabled. CB 7 returned to service. | F3 | PAPAMOA BEACH WEST | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.27851 | 11 | 2017 | 2016-06-03 | C | 5703 | 0.27851 | 0.021984
1 | 11695772 | 2016-06-03 08:35 | 2016-06-03 10:42 | 126 | 1 | 126.6833 | 0.00038088 | 0.000371 | 3.0065e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 778 PAPAMOA BEACH ROAD | UNKNOWN | Full power upon arrival. FM confirmed this was due to the feeder fault earlier this morning | F2 | GRAVATT RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.000371 | 11 | 2017 | 2016-06-03 | C | 1 | 0.000371 | 3.0065e-06
1 | 11700009 | 2016-06-03 10:05 | 2016-06-03 10:18 | 13 | 1 | 13.7333 | 4.129e-05 | 3.2e-05 | 3.0065e-06 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Outage to wind farm only | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 3.2e-05 | 33 | 2017 | 2016-06-03 | C | 1 | 3.2e-05 | 3.0065e-06
1 | 11700143 | 2016-06-03 10:30 | 2016-06-03 10:39 | 8 | 2 | 17.4667 | 5.2515e-05 | 3.4e-05 | 6.0131e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 6942 | UNKNOWN | Recloser 6942 tripped on A & B phase O/C & E/F flags, suspect tripping was caused when ABS 6067 was closed under NAPA 20492, faultman suspects not all contacts closed at same time as this ABS is a very old one, faultman has put in an amber defect on so a live line crew can go and investigate. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 3.4e-05 | 11 | 2017 | 2016-06-03 | C | 2 | 3.4e-05 | 6.0131e-06
1 | 11716320 | 2016-06-04 00:36 | 2016-06-04 02:58 | 142 | 2062 | 151090.6 | 0.45426 | 0.43566 | 0.020051 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P17768 | INSULATOR | CB 24 Tripped with No Flags Cable disconnected at Pole 366281 during sectionlising, as believed to be faulty. After livening feeder tripped again and possum found on pole P17768 and cleared using hot sticks, faultman still thinks cable maybe faulty so line break left in place. 2r line patrol 0117. 2r repair 0217 | F3 | DENBIGH | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.43566 | 11 | 2017 | 2016-06-04 | C | 2062 | 0.43566 | 0.020051
1 | 11724835 | 2016-06-04 06:51 | 2016-06-04 09:00 | 128 | 24 | 3089.6 | 0.009289 | 0.009072 | 7.2157e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 805606 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses. Ducks struck lines between Poles 805606 & 805607, 805633 & 805634. Dead ducks found below lines. | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.009072 | 11 | 2017 | 2016-06-04 | C | 24 | 0.009072 | 7.2157e-05
1 | 11724967 | 2016-06-04 08:27 | 2016-06-04 11:45 | 197 | 2017 | 171307.1333 | 0.51504 | 0.49685 | 0.0060642 |  | 33 | Unplanned |  | ZONE SUB EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | T1 Featherston Sub | TRANSFORMER - ZONE TRANSFORMER (HV) | Trip 33kV CB's C903 and C905. Could not put backfeed in on Dairy Factory feeder as Comms failed to RS S548 11kV Incomer C913 Opened at time of fault but showing Still Closed on SCADA. Checked Open on site by Adam Whale. 11:45 All Power restored. 12:15 N Pope on site. Confirms a Buckholz Trip. Low oil in conservator. 12:39 Transformer T1 Isolated. DNO 160606 | S2 | FEATHERSTON 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0.49685 | 33 | 2017 | 2016-06-04 | C | 2017 | 0.49685 | 0.0060642
1 | 11727216 | 2016-06-04 09:56 | 2016-06-04 13:03 | 187 | 5 | 938.4167 | 0.0028214 | 0.002776 | 1.5033e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 243 | FUSE - ELEMENT/LINK (HV) | 2 x 5A HV Fuses | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.002776 | 11 | 2017 | 2016-06-04 | C | 5 | 0.002776 | 1.5033e-05
1 | 11727221 | 2016-06-04 09:56 | 2016-06-04 10:57 | 61 | 432 | 26395.2 | 0.079358 | 0.075461 | 0.0012988 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Trip 33kV CB's C903 and C905. Could not put backfeed in on Dairy Factory feeder as Comms failed to RS S548 11kV Incomer C913 Opened at time of fault but showing Still Closed on SCADA. Checked Open on site by Adam Whale. 11:45 All Power restored. 12:15 N Pope on site. Confirms a Buckholz Trip. Low oil in conservator. 12:39 Transformer T1 Isolated. DNO 160606 | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.075461 | 11 | 2017 | 2016-06-04 | C | 432 | 0.075461 | 0.0012988
1 | 11727655 | 2016-06-04 09:53 | 2016-06-04 10:30 | 37 | 1032 | 38184 | 0.1148 | 0.10549 | 0.0031027 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Trip 33kV CB's C903 and C905. Could not put backfeed in on Dairy Factory feeder as Comms failed to RS S548 11kV Incomer C913 Opened at time of fault but showing Still Closed on SCADA. Checked Open on site by Adam Whale. 11:45 All Power restored. 12:15 N Pope on site. Confirms a Buckholz Trip. Low oil in conservator. 12:39 Transformer T1 Isolated. DNO 160606 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.10549 | 11 | 2017 | 2016-06-04 | C | 1032 | 0.10549 | 0.0031027
1 | 11728689 | 2016-06-04 09:59 | 2016-06-04 10:30 | 31 | 1 | 31 | 9.3203e-05 | 8.4e-05 | 3.0065e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Trip 33kV CB's C903 and C905. Could not put backfeed in on Dairy Factory feeder as Comms failed to RS S548 11kV Incomer C913 Opened at time of fault but showing Still Closed on SCADA. Checked Open on site by Adam Whale. 11:45 All Power restored. 12:15 N Pope on site. Confirms a Buckholz Trip. Low oil in conservator. 12:39 Transformer T1 Isolated. DNO 160606 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 8.4e-05 | 11 | 2017 | 2016-06-04 | C | 1 | 8.4e-05 | 3.0065e-06
1 | 11730069 | 2016-06-04 11:18 | 2016-06-04 14:50 | 212 | 37 | 3974 | 0.011948 | 0.011614 | 0.00011124 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1/217 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | part of Jeffs job Transformer T1/217 Faulty To be replaced. Full set HV Fuse Holders and 3 x 3A HV Fuses 1 x Transformer | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.011614 | 11 | 2017 | 2016-06-04 | C | 37 | 0.011614 | 0.00011124
1 | 11730128 | 2016-06-09 11:29 | 2016-06-09 12:45 | 76 | 1 | 76 | 0.00022848 | 0.000219 | 3.0063e-06 | Referral | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L4379 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Bruce Kerr Attended. Replaced Transformer under emergency shutdown. Isolated Lines at Fuses LI743. Permit Issued & Repairs Carried Out. All Power Restored on Completion. 1x Transformer Replaced, 3x 100A HRC Fuses Replaced, 9x Conductor joints used, 3m of Red 16mm2 Cu Cable. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000219 | 11 | 2017 | 2016-06-09 | C | 1 | 0.000219 | 3.0063e-06
1 | 11730758 | 2016-06-04 15:11 | 2016-06-04 20:03 | 291 | 369 | 18186.1 | 0.054677 | 0.051348 | 0.0011094 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 826281 | POLE | Clareville CB C8234 (Chester Road) tripped O/C. Car vs Pole. Adam will send NDR & what was used on the 05/06/16. 2r line patrol 1544. 2r repair 1620. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.051348 | 11 | 2017 | 2016-06-04 | C | 369 | 0.051348 | 0.0011094
1 | 11732071 | 2016-06-04 16:52 | 2016-06-04 18:37 | 104 | 980 | 36991.9333 | 0.11122 | 0.10238 | 0.0058928 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | RC20 | UNKNOWN | RC 20 O/L, reconfigured network | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.10238 | 11 | 2017 | 2016-06-04 | C | 980 | 0.10238 | 0.0058928
1 | 11736567 | 2016-06-04 17:39 | 2016-06-04 23:20 | 340 | 302 | 73887.0667 | 0.22214 | 0.21942 | 0.0020865 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 225 | UNKNOWN | Tinui RS C225 trippled on O/C and L/O A & B phase. Line patrolled and nothing found. 2 r line patrol 1901 no repair | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.21942 | 11 | 2017 | 2016-06-04 | C | 302 | 0.21942 | 0.0020865
1 | 11737794 | 2016-06-05 00:10 | 2016-06-05 09:35 | 565 | 22 | 12430 | 0.037371 | 0.037172 | 6.6143e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 231054 | CONDUCTOR - REPAIR/REHANG | Lines down at pole 231054. No 8 conductor is in a bad state & really needs to be replaced. Isolated at Fuses SG7-001. No Back Feeds available. 10 meters of 16mm copper, 2 sleeves. | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.037172 | 11 | 2017 | 2016-06-05 | C | 22 | 0.037172 | 6.6143e-05
1 | 11739581 | 2016-06-05 10:00 | 2016-06-05 10:26 | 26 | 22 | 572 | 0.0017197 | 0.001521 | 6.6143e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P44025 | JUMPER | check to see if oms 11739610 is related (672 GORGE ROAD) check to see if oms 11739658 is related as feed from same TX 7285P (648A GORGE ROAD) 8:45am tried to call Phil on RT to advise him of other faults in area was related close off the same as oms 11740044 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001521 | 11 | 2017 | 2016-06-05 | C | 22 | 0.001521 | 6.6143e-05
1 | 11740528 | 2016-06-05 11:58 | 2016-06-05 14:00 | 121 | 424 | 37760.1333 | 0.11353 | 0.1097 | 0.0012748 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | CC5 | CAPACITOR BANK (HV) | CB 6 Trip A & C O/C E/F. Feeder Patrolled & sectionalised. Fault found to be fault Capacitors CC5. DNO 160605. Back feeds from PKO CB 3 via ABS IC611 & ABS IC2116. 2 r line patrol 1308 / no 2r repair. | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.1097 | 11 | 2017 | 2016-06-05 | C | 424 | 0.1097 | 0.0012748
1 | 11742487 | 2016-06-05 19:13 | 2016-06-06 14:42 | 1168 | 11 | 12855.3333 | 0.038649 | 0.03855 | 3.3071e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC823 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer TC5987 blown, customers advised have generator & happy to remain off until replacement transformer in morning. Shan called from hub to advise Sean is on stand down until 11am. Customers off transformer have a generator. Called customer to see if ok with timing, she said she can't milk with the generator that they have but will wait for the transormer to be fixed. Advised we could get a different faultman earlier to replace transformer, customer said she would like Sean as he was a great help last night so happy to wait until 11am. OMS 11747492 is also related. 2 HV fuses blown at FC823. Noticed after transformer TC5987 replaced. Possibly blew when transformer TC5987 faulted. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.03855 | 11 | 2017 | 2016-06-05 | C | 11 | 0.03855 | 3.3071e-05
1 | 11743104 | 2016-06-05 22:44 | 2016-06-06 12:30 | 826 | 138 | 114082.3 | 0.34299 | 0.34174 | 0.0004149 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 854408 | INSULATOR | ( BRD 2 ) recloser 9402/2 tripped E/F, L/O feeder patrolled ( few isolation points for sectionalising ) Line Patrolled, Line mostly cross country so FM had to travel up numerious roads trying to inspect lines. No ABS's installed past recloser 9402/2. Line Patrol during th enight abandoned & restarted after daylight. Fault found at pole 854408 where 3 insulators were broken. Pole 856015 is a termination point so an ABS could be fitted before the line goes cross country & is beside road for easy access. 2r line patrol no line patrol 2r repair 1115 | F3/F4 | ASHWORTH ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.34174 | 11 | 2017 | 2016-06-05 | C | 138 | 0.34174 | 0.0004149
1 | 11748500 | 2016-06-07 10:04 | 2016-06-07 11:25 | 81 | 3 | 243 | 0.00073056 | 0.000703 | 9.0192e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2045 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Customer is happy to leave this until tomorrow as there will need to be a complete shutdown of the transformer to replace HV fuse Holders. Replace DDOs at transformer X2045. Materials Used: 3 x Fuse Bases and Carrier and 3 x 2 Amp Fuse. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.000703 | 11 | 2017 | 2016-06-07 | C | 3 | 0.000703 | 9.0192e-06
1 | 11749040 | 2016-06-06 23:48 | 2016-06-07 02:37 | 168 | 320 | 13526.8 | 0.040668 | 0.037781 | 0.00050809 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | unknown | UNKNOWN | Rec RC20 tripped A/R, Sec 9721 tripped E/F, B Ph O/C, L/O ( at time of tripping Sec 9721 back feeding back end of WHT 4 because Rec 9512 faulty ) Feeder sectionalised. No fault found , all service restored. 2r line patrol 0053 no repair | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.037781 | 11 | 2017 | 2016-06-06 | C | 320 | 0.037781 | 0.00050809
1 | 11751058 | 2016-06-07 10:07 | 2016-06-07 13:06 | 178 | 1 | 178.5333 | 0.00053674 | 0.000527 | 3.0064e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7043 | FUSE - ELEMENT/LINK (HV) | Fuses found Blown at Fuses 7043 - Bird Strike. Used 2 x 10amp fuses. Job for wool shed fed of different transformer than Customer | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.000527 | 11 | 2017 | 2016-06-07 | C | 1 | 0.000527 | 3.0064e-06
1 | 11751519 | 2016-06-28 09:15 | 2016-06-28 14:08 | 293 | 37 | 10841 | 0.032582 | 0.032248 | 0.0001112 | NAPA ID:20547 TP_LINTON GXP > KAIRANGA SUB > TREMAINE AVE | 11 | Planned | 020547 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T6/158 | NONE | Replace Transformer Pole T6/158. Works location: Cloverlea Rd, Palmerston North. WO 30018909 | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.016124 | 5.5 | 2017 | 2016-06-28 | B | 37 | 0.032248 | 0.0001112
1 | 11751642 | 2016-06-28 09:00 | 2016-06-28 15:30 | 390 | 66 | 25740 | 0.07736 | 0.076765 | 0.00019836 | NAPA ID:20663 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 020663 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | S137 | NONE | Replace No 8 conductor with new Squirrel conductor and replace glass strains with new polymers. Works location: Skeets Rd, Masterton. WO 30027229 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.038382 | 5.5 | 2017 | 2016-06-28 | B | 66 | 0.076765 | 0.00019836
1 | 11752189 | 2016-06-07 16:50 | 2016-06-07 17:45 | 54 | 6 | 328.3 | 0.000987 | 0.000932 | 1.8038e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TD6-041 | JUMPER | Fault man is requesting a 2R to repair a HT jumper on the 11 kv. Advised him to call through to control. Will call back once hes spoken to the customers as there will need to be a shutdown of the transformer to repair the jumper. Dave has spoken to Maurice in control - shutdown will be later on today as customers are milking at the moment. shutdown will be at approx 4.30pm. Sammy called to advise that Josh has advised that this needs to be 2R as he needs to earth, and use bucket truck. Advised Sammy that because replacing a jumper (when line is isolated) then this is only 1R work. This is to be discussed at invoicing level. Line isolated at 16:50. All 3 jumpers replaced due to corrosion. Materials used - 3 x Namu compression sleeves & 3 metres 25mm Cu conductor. All supply restored | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.000932 | 11 | 2017 | 2016-06-07 | C | 6 | 0.000932 | 1.8038e-05
1 | 11752295 | 2016-06-24 05:50 | 2016-06-24 17:49 | 719 | 225 | 29345 | 0.0882 | 0.086171 | 0.0013525 | NAPA ID:19184 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > BETHLEHEM | 11 | Planned | 019184 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-563 | NONE | Replace series 1 fuse-switch (SD4-370) with new CFC Safelink (13035) and terminate existing cables plus a new 185mm cable. Install new CFCF Safelink (13036) adjacent TD4-602 and terminate other end of new 185mm cable. Change over transformer supplies as indicated in drawing attached. WORKS LOCATION: Cambridge Rd, Townhead Cres. WO 30010524 | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.043085 | 5.5 | 2017 | 2016-06-24 | B | 225 | 0.086171 | 0.0013525
1 | 11765425 | 2016-06-08 05:29 | 2016-06-08 07:10 | 101 | 1 | 101.4 | 0.00030485 | 0.000295 | 3.0063e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P1821 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp at pole p1821 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.000295 | 11 | 2017 | 2016-06-08 | C | 1 | 0.000295 | 3.0063e-06
1 | 11765436 | 2016-06-08 06:08 | 2016-06-08 07:55 | 107 | 49 | 4052.3 | 0.012183 | 0.01174 | 0.00014731 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | V13680 | CONDUCTOR - REPAIR/REHANG | Branch removed from line at pole V13680 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.01174 | 11 | 2017 | 2016-06-08 | C | 49 | 0.01174 | 0.00014731
1 | 11765758 | 2016-07-04 10:04 | 2016-07-04 14:48 | 284 | 42 | 11928 | 0.035847 | 0.035468 | 0.00012622 | NAPA ID:21354 TP_HAWERA GXP > KAPUNI SUB > MATAPU | 11 | Planned | 021354 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | KA743 | NONE | Install cross arms replace ABS KA743 (DNO160407). Replace 6772/2 11kV Recloser solid links 6772/4/6. Works location: Katotauru Rd, Okaiawa. WO 30026227 | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.017734 | 5.5 | 2017 | 2016-07-04 | B | 42 | 0.035468 | 0.00012622
1 | 11765921 | 2016-06-08 10:07 | 2016-06-08 11:05 | 58 | 28 | 1624 | 0.0048823 | 0.004629 | 8.4178e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TA2-116 | FUSE - ELEMENT/LINK (HV) | Replace 1 x 10A Fuse at Transformer TA2-116. Required Isolation past Fuses SA2-035 to access the Transformer safely | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.004629 | 11 | 2017 | 2016-06-08 | C | 28 | 0.004629 | 8.4178e-05
1 | 11765960 | 2016-06-08 08:15 | 2016-06-08 08:26 | 11 | 629 | 6737.15 | 0.020254 | 0.014581 | 0.001891 |  | 33 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | CB XT30 | UNKNOWN | CB 1332 auto reclosed at Transpower & CB XT 30 tripped on A & C phase O/C & E/F flags, line was patrolled by Robin Smith and Phil Barnes and no fault was found, faultman suspect bird strike as there are a lot of magpies flying around the lines. | S3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 0.014581 | 33 | 2017 | 2016-06-08 | C | 629 | 0.014581 | 0.001891
1 | 11772301 | 2016-06-29 08:40 | 2016-06-29 13:26 | 286 | 9 | 2574 | 0.0077359 | 0.007654 | 2.7049e-05 | NAPA ID:19178 TP_MATAROA GXP > TAIHAPE SUB > MOAWHANGO | 11 | Planned | 019178 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 510 | POLE | Replace 7 defect poles Wherewhere rd Taihape pole no 786348 to 786356 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.003827 | 5.5 | 2017 | 2016-06-29 | B | 9 | 0.007654 | 2.7049e-05
1 | 11773393 | 2016-06-29 10:00 | 2016-06-29 14:15 | 255 | 7 | 1785 | 0.0053646 | 0.005301 | 2.1038e-05 | NAPA ID:21339 TP_HAWERA GXP > KAPUNI SUB > MATAPU | 11 | Planned | 021339 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | KA704 | NONE | Install cross arms replace ABS KA704 (DNO 160408). W orks location: Skeet Rd, Kapuni. WO 30026231 | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.0026505 | 5.5 | 2017 | 2016-06-29 | B | 7 | 0.005301 | 2.1038e-05
1 | 11782840 | 2016-06-10 09:30 | 2016-06-10 15:15 | 345 | 1 | 345 | 0.0010372 | 0.001028 | 3.0062e-06 | NAPA ID:21452 TP_WANGANUI GXP > BLINK BONNIE SUB > FORDELL | 11 | Planned | 021452 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Fuses 2676 | NONE | trim trees on the 11kv line feeding Powerco radio site (Takahi). Works location: Mangamahu Valley Rd. WO 30026260 | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.000514 | 5.5 | 2017 | 2016-06-10 | B | 1 | 0.001028 | 3.0062e-06
1 | 11794826 | 2016-06-08 17:24 | 2016-06-08 18:25 | 61 | 3 | 183.55 | 0.00055182 | 0.000524 | 9.0191e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | T3781 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer T3781 - Cause Bird Strike Used 2 x 2 amp fuses | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000524 | 11 | 2017 | 2016-06-08 | C | 3 | 0.000524 | 9.0191e-06
1 | 11803176 | 2016-06-24 09:30 | 2016-06-24 12:07 | 157 | 21 | 3297 | 0.0099096 | 0.00972 | 6.3118e-05 | NAPA ID:21481 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | 021481 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P13340 | NONE | Replace Crossarms at P13340. Works location: Dickey Flat Rd, Waitawheta. WO 30010303 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.00486 | 5.5 | 2017 | 2016-06-24 | B | 21 | 0.00972 | 6.3118e-05
1 | 11804224 | 2016-06-20 09:00 | 2016-06-20 16:44 | 464 | 399 | 11687 | 0.035129 | 0.031531 | 0.0018005 | NAPA ID:20613 TP_KOPU GXP > WHITIANGA SUB | 11 | Planned | 020613 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | ic3221 | CABLE - REPLACE LESS THAN 5 METRES | AP1 - Remove cable from end box of SDAF3 unit at IC3240/FC5061/IC3221 and TC4620 AP2 - Joint in new HV cable and remove 2 spans of OH lines plus pole AP3 - Reconnect new section of U/G cable to end box of SDAF3 unit Phasing to be across ABS IC1348 | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.015766 | 5.5 | 2017 | 2016-06-20 | B | 399 | 0.031531 | 0.0018005
1 | 11804417 | 2016-06-09 12:38 | 2016-06-09 16:15 | 217 | 10 | 2170 | 0.0065237 | 0.006433 | 3.0063e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole P45468 | INSULATOR | FM Ben Taylor an NPE Tech to Isolate & Earth for Urgent Insulator Replacements as per instruction from Gavin Paget. Line was isolated at Fuses I13 to replace damaged insulator on pole P45468. 1 X 11KV insulator was replaced. | F4 | IHURAUA | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.006433 | 11 | 2017 | 2016-06-09 | C | 10 | 0.006433 | 3.0063e-05
1 | 11805553 | 2016-06-24 09:44 | 2016-06-24 14:30 | 286 | 3 | 858.55 | 0.0025805 | 0.002553 | 9.0169e-06 | NAPA ID:19259 TP_CARRINGTON GXP > CITY SUB > CITY 7 | 11 | Planned | 019259 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 691/1 | NONE | Systematic replacement of 2 old oil switchgears (inside buildings) with 1 new Safelink unit. This will be done in four(4) stages due to switching requirements and work to be done. This is Shut 2. AP is to cut and remove HV cable from Tx 42 and connect new cable from 585/2. Old oil switchgear will be drained and left inside building as redundant. HV cable from TEMP 58 to 42 also redundant. Next shut 3 to follow on NAPA 19260. WORKS LOCATION: Courtenay St. WO 30018772 | F2 | CITY 7 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.0012765 | 5.5 | 2017 | 2016-06-24 | B | 3 | 0.002553 | 9.0169e-06
1 | 11805640 | 2016-07-04 10:30 | 2016-07-04 11:28 | 58 | 5 | 290 | 0.00087153 | 0.000826 | 1.5026e-05 | NAPA ID:18551 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018551 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4158 | NONE | To install a 400V Fuse Disconnector. Works location: Hutchinson Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000413 | 5.5 | 2017 | 2016-07-04 | B | 5 | 0.000826 | 1.5026e-05
1 | 11805654 | 2016-07-04 12:25 | 2016-07-04 15:26 | 181 | 32 | 5792 | 0.017406 | 0.017117 | 9.6168e-05 | NAPA ID:18552 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 018552 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4160 | NONE | To install a 400V Fuse Disconnector. Works location: Hutchinson Rd, Walton. WO 30019182. Outage went for longer than advertised and affected more people after transformer fuses fell apart and had to take isolation back to ABS IC755 to replace. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0085585 | 5.5 | 2017 | 2016-07-04 | B | 32 | 0.017117 | 9.6168e-05
1 | 11805667 | 2016-06-30 09:37 | 2016-06-30 15:30 | 353 | 80 | 7225.2333 | 0.021714 | 0.020993 | 0.00046283 | NAPA ID:21341 TP_WAIKINO GXP > WAIHI SUB > VICTORIA ST | 11 | Planned | 021341 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP179 | NONE | Work 1: Disconnect TP179 from network. Work 2: Re-Level TP179. Work 3: Re-Connect TP179 onto network. Works location: Colebrooke Rd, Waihi. WO 30002257 | F3 | VICTORIA ST | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.010497 | 5.5 | 2017 | 2016-06-30 | B | 80 | 0.020993 | 0.00046283
1 | 11805721 | 2016-07-04 12:45 | 2016-07-04 14:45 | 120 | 3 | 360 | 0.0010819 | 0.001054 | 9.0157e-06 | NAPA ID:21105 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 021105 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1920 | NONE | To replace the 400V Arm & Install a 400V Fuse Disconnector on TC1920. Works location: Troughton Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000527 | 5.5 | 2017 | 2016-07-04 | B | 3 | 0.001054 | 9.0157e-06
1 | 11805729 | 2016-07-04 09:30 | 2016-07-04 11:45 | 135 | 6 | 810 | 0.0024343 | 0.00238 | 1.8031e-05 | NAPA ID:21104 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 021104 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC360 | NONE | To replace the 400V arm & install a 400V fuse Disconnector on TC360. Works location: Troughton Rd. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.00119 | 5.5 | 2017 | 2016-07-04 | B | 6 | 0.00238 | 1.8031e-05
1 | 11805739 | 2016-07-06 09:45 | 2016-07-06 12:35 | 170 | 3 | 510 | 0.0015327 | 0.001505 | 9.0156e-06 | NAPA ID:21204 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 021204 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3047 | NONE | To replace the 11kV and 400V arms on TC3047. Works location: Troughton Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0007525 | 5.5 | 2017 | 2016-07-06 | B | 3 | 0.001505 | 9.0156e-06
1 | 11806161 | 2016-07-06 12:50 | 2016-07-06 14:00 | 70 | 2 | 140 | 0.00042073 | 0.000402 | 6.0104e-06 | NAPA ID:21205 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 021205 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP828 | NONE | To install a 400V fuse Disconnector (TP828). Work slocation: Mowbray Rd, Walton. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000201 | 5.5 | 2017 | 2016-07-06 | B | 2 | 0.000402 | 6.0104e-06
1 | 11806184 | 2016-07-06 13:45 | 2016-07-06 14:40 | 55 | 4 | 220 | 0.00066115 | 0.000625 | 1.2021e-05 | NAPA ID:21206 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 021206 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4970 | NONE | To install a 400V Fuse Disconnector. Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0003125 | 5.5 | 2017 | 2016-07-06 | B | 4 | 0.000625 | 1.2021e-05
1 | 11806906 | 2016-07-08 10:04 | 2016-07-08 14:35 | 271 | 5 | 1355 | 0.004072 | 0.004026 | 1.5026e-05 | NAPA ID:21106 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 021106 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3124 | NONE | To replace 11kV Fuse arm, 400V service arm & Fuses. Works location: Pohlen Rd, Matamata. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.002013 | 5.5 | 2017 | 2016-07-08 | B | 5 | 0.004026 | 1.5026e-05
1 | 11806911 | 2016-07-01 09:03 | 2016-07-01 14:08 | 305 | 72 | 21961.2 | 0.066001 | 0.065351 | 0.00021638 | NAPA ID:20723 TP_MANGAMAIRE GXP > MANGAMUTU SUB > RUAWHATA | 11 | Planned | 020723 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P15489 | NONE | 11kv pole changes @ P15489 & P15450. Works location: Cambridge St, Pahiatua. WO 30024426 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.032676 | 5.5 | 2017 | 2016-07-01 | B | 72 | 0.065351 | 0.00021638
1 | 11806989 | 2016-06-09 16:45 | 2016-06-09 18:10 | 85 | 1 | 85 | 0.00025554 | 0.000246 | 3.0063e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC3126 | JUMPER | Found jumper broken at TC3126. Isolated at fuses FC2153. Repaired jumper & relivened | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000246 | 11 | 2017 | 2016-06-09 | C | 1 | 0.000246 | 3.0063e-06
1 | 11806999 | 2016-07-01 08:55 | 2016-07-01 12:25 | 210 | 23 | 4830 | 0.014516 | 0.014308 | 6.9123e-05 | NAPA ID:21101 TP_MANGAMAIRE GXP > PARKVILLE SUB > HUKANUI | 11 | Planned | 021101 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses S8 | NONE | To replace 11kv x arms and conductor. Works location: Mangaruapiu Rd. WO 30001378 | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.007154 | 5.5 | 2017 | 2016-07-01 | B | 23 | 0.014308 | 6.9123e-05
1 | 11808453 | 2016-06-10 06:46 | 2016-06-10 08:55 | 129 | 1409 | 122414 | 0.36801 | 0.3553 | 0.0042358 |  | 33 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X75 | INSULATOR | Kimbolton RC 10002 and CB X20 tripped on C ph, O/C and E/F. 2 faulty insulators found at ABS X75. OUTAGE RESTORED. Planned outage NAPA 19320 was cancelled so we could fix the ABS X75 Due to Voltage & Bad weather etc .With weekend near also so could get sub back to normal . ABS X75 is being replaced on Tuesday. Replaced 2x H/T Insulators at ABS X75. 2r line patrol n/a. 2r repair 1012 | S4 | FEILDING-KIMBOLTON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.3553 | 33 | 2017 | 2016-06-10 | C | 1409 | 0.3553 | 0.0042358
1 | 11811556 | 2016-06-10 07:26 | 2016-06-10 08:50 | 84 | 7 | 590.2167 | 0.0017744 | 0.001711 | 2.1044e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 795109 | FUSE - ELEMENT/LINK (HV) | pole 795109 2x 8 cause turkey | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.001711 | 11 | 2017 | 2016-06-10 | C | 7 | 0.001711 | 2.1044e-05
1 | 11811610 | 2016-07-01 09:45 | 2016-07-01 13:11 | 206 | 2 | 412 | 0.0012382 | 0.00122 | 6.0106e-06 | NAPA ID:21031 TP_STRATFORD GXP > MOTUKAWA SUB > KOHETE RD | 6.6 | Planned | 021031 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 5321 | NONE | To replace 6.6kV crossarms and re-sag conductors. Works location: Tarata Rd. WO 30027078 | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.00061 | 3.3 | 2017 | 2016-07-01 | B | 2 | 0.00122 | 6.0106e-06
1 | 11811735 | 2016-06-10 10:44 | 2016-06-10 11:30 | 46 | 302 | 13892 | 0.041763 | 0.039039 | 0.0009079 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4-004 | FUSE - ELEMENT/LINK (HV) | Found loose connections burning on DDO's for transformer tc4-004. Isolated between ABS sc4-011 & sc4-017. Replaced 3 x DDO units & relivened | F3 | PILLANS POINT | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 0.039039 | 11 | 2017 | 2016-06-10 | C | 302 | 0.039039 | 0.0009079
1 | 11812014 | 2016-06-10 08:56 | 2016-06-10 09:25 | 29 | 1 | 29.3667 | 8.8284e-05 | 7.9e-05 | 3.0062e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | - | UNKNOWN | No fault found - moisture from the insulators on the 33kv line was causing buzzing, this does not pose threat to safety or network. Farmer advised. Nothing else repaired or replaced. Adjacent assets up to Powerco standards. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 7.9e-05 | 11 | 2017 | 2016-06-10 | C | 1 | 7.9e-05 | 3.0062e-06
1 | 11812172 | 2016-07-13 08:46 | 2016-07-13 14:30 | 344 | 46 | 15824 | 0.047551 | 0.047136 | 0.00013823 | NAPA ID:21097 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 021097 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 839124 | NONE | replacing 11kv poles and hardware. Works location: Opaki Kaipororo Rd, Masterton. WO 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.023568 | 5.5 | 2017 | 2016-07-13 | B | 46 | 0.047136 | 0.00013823
1 | 11812980 | 2016-06-10 14:28 | 2016-06-10 14:50 | 22 | 55 | 1214.5833 | 0.0036514 | 0.003155 | 0.00016535 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P25887 | JUMPER | Repaired 2 x Jumpers at Pole P25887. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.003155 | 11 | 2017 | 2016-06-10 | C | 55 | 0.003155 | 0.00016535
1 | 11812998 | 2016-07-02 09:32 | 2016-07-02 14:06 | 274 | 28 | 7672 | 0.023057 | 0.022804 | 8.4149e-05 | NAPA ID:21366 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 021366 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/363 | NONE | To replace 11kV pole and TX T7/363. Works location: Pahiatua Pongaroa Rd. WO 30017098 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.011402 | 5.5 | 2017 | 2016-07-02 | B | 28 | 0.022804 | 8.4149e-05
1 | 11813293 | 2016-07-06 09:30 | 2016-07-06 14:49 | 318 | 61 | 19415.2833 | 0.058347 | 0.057797 | 0.00018332 | NAPA ID:21371 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11 | Planned | 021371 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 363608 | NONE | Install new HV double termination arm, reduce tension between poles 363608-803194-803195. fix audit issues. Works location: Santoft Rd. WO 30029087 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.028899 | 5.5 | 2017 | 2016-07-06 | B | 61 | 0.057797 | 0.00018332
1 | 11813318 | 2016-06-10 12:07 | 2016-06-10 13:39 | 92 | 3398 | 224544.15 | 0.67504 | 0.6444 | 0.010215 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2212 | UNKNOWN | CB 2212 tripped on N/time O/C flags, line was isolated and sub was partially backfed on the 11kV. Line patrolled and no fault was found. Fault man did report that there was a bit of wet bark laying around under the lines, suspect branch may have come in contact with the lines. 2r line patrol 1335 - no repair. | S4 | KINLEITH2212-BAIRD RD 33KV | KINLEITH 33 | Valley | TP_KINLEITH | Eastern Electricity | POWERCO | 0.6444 | 33 | 2017 | 2016-06-10 | C | 3398 | 0.6444 | 0.010215
1 | 11819480 | 2016-07-05 13:00 | 2016-07-05 16:14 | 194 | 29 | 5626 | 0.016907 | 0.016645 | 8.7152e-05 | NAPA ID:21383 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11 | Planned | 021383 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1104 | NONE | Various worksites between the isolation area for completion of outstanding audit issues. Works location: Santoft Rd. WO 30029087 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.0083225 | 5.5 | 2017 | 2016-07-05 | B | 29 | 0.016645 | 8.7152e-05
1 | 11820527 | 2016-07-05 09:15 | 2016-07-05 16:20 | 425 | 6 | 2550 | 0.0076633 | 0.007609 | 1.8031e-05 | NAPA ID:20729 TP_GREYTOWN GXP > TUHITARATA SUB > BURNSIDE | 11 | Planned | 020729 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2482 | NONE | REPLACE 811000 WITH NEW 11.0M BUSCK AND 15KVA SINGLE PHASE TRANSFORMER. REPLACE 11KV OVER HEAD WIRE BETWEEN 7435 AND T2482. REMOVE TREES AROUND LINE. Works location: Lake Ferry Rd, Tuhitarata Featherston. WO 30027277 | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.0038045 | 5.5 | 2017 | 2016-07-05 | B | 6 | 0.007609 | 1.8031e-05
1 | 11820632 | 2016-07-05 09:30 | 2016-07-05 12:27 | 177 | 60 | 10620 | 0.031916 | 0.031374 | 0.00018031 | NAPA ID:21331 TP_BRUNSWICK GXP > PEAT ST SUB > WESTMERE PEAT ST | 11 | Planned | 021331 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X4081 | NONE | Drop 11kv lines both sides of transformer X4081 and remove the Fargo sleeves. Works location: Cameron Rd East. WO 30002392 | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.015687 | 5.5 | 2017 | 2016-07-05 | B | 60 | 0.031374 | 0.00018031
1 | 11821292 | 2016-06-10 14:43 | 2016-06-10 18:05 | 202 | 132 | 14044.55 | 0.042222 | 0.041031 | 0.00039683 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P0439 | NONE | Cb 4 trip O/C E/F found broken bolt at pole Po439. 1 x King Bolt Replaced. 2r line patrol 1553. 2r repair 1705 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.041031 | 11 | 2017 | 2016-06-10 | C | 132 | 0.041031 | 0.00039683
1 | 11821809 | 2016-06-10 15:10 | 2016-06-10 17:30 | 139 | 500 | 35001.7 | 0.10522 | 0.10071 | 0.0015031 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 835300 | CONDUCTOR - REPAIR/REHANG | CB C850 Tripped O/C found Tree in lines at Pole 835300. NDR Number 37936 | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.10071 | 11 | 2017 | 2016-06-10 | C | 500 | 0.10071 | 0.0015031
1 | 11822329 | 2016-07-06 09:46 | 2016-07-06 13:57 | 251 | 58 | 14576.3667 | 0.043805 | 0.043282 | 0.0001743 | NAPA ID:21368 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | 021368 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS U22 | NONE | Replace 11kv conductor jionts and 11kv pole. Works location: Opaki Kaparoro Rd. WO 30000998 | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.021641 | 5.5 | 2017 | 2016-07-06 | B | 58 | 0.043282 | 0.0001743
1 | 11824542 | 2016-06-10 16:21 | 2016-06-10 18:28 | 127 | 1 | 127.0667 | 0.000382 | 0.000372 | 3.0062e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N3270 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Repaired Jumper at transformer N3270 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.000372 | 11 | 2017 | 2016-06-10 | C | 1 | 0.000372 | 3.0062e-06
1 | 11825639 | 2016-06-10 22:59 | 2016-06-11 01:00 | 121 | 6 | 728.7 | 0.0021907 | 0.002136 | 1.8038e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7101 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses. Wind. Line Clash | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.002136 | 11 | 2017 | 2016-06-10 | C | 6 | 0.002136 | 1.8038e-05
1 | 11825760 | 2016-06-11 08:58 | 2016-06-11 11:00 | 122 | 5 | 610 | 0.0018338 | 0.001788 | 1.5031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | T129 | CONDUCTOR - REPAIR/REHANG | Faultman found lines down at transformer T129 caused by tree through the line, line was isolated at Fuses 7082. 30 metres of No: 8 wire used. 8 x Sleeves. 2 X 6 amp hv fuses. 2 x No:8 terminations. NDR: 23394 | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.001788 | 11 | 2017 | 2016-06-11 | C | 5 | 0.001788 | 1.5031e-05
1 | 11825786 | 2016-06-11 07:24 | 2016-06-11 09:10 | 105 | 10 | 1056.8333 | 0.0031771 | 0.003086 | 3.0062e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | SB2 069 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A H/V, O/H fuses at fuses SB2 069 ( bird strike ) | F3/F4 | WILLS RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.003086 | 11 | 2017 | 2016-06-11 | C | 10 | 0.003086 | 3.0062e-05
1 | 11825834 | 2016-06-11 08:04 | 2016-06-11 14:37 | 392 | 132 | 28639.6833 | 0.086098 | 0.084907 | 0.00039682 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole P03224 | CONDUCTOR - REPAIR/REHANG | CB 4 tripped on B & C phase O/C & E/F flags, line was sectionalised and patrolled and faultman found lines down at pole P03224, line was isolated at ABS V81 & ABS V85.When ABS I29 was closed it tripped the donnor feeder CB I23 out of Alfreton, suspected there mite be a second fault passed ABS V85, but on completion of lines down, line was patrolled between ABS V85 & ABS I29 and fault was found ABS V85 was closed supply stayed in. REF.to OMS 11826580. 100 meters of Ferrett conductor used. 6 X insulators replaced. 5 X sleeves. 6 X dead-end used. 4 X non tension sleeves. 2r line patrol 0938 2r reopair 1048 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.084907 | 11 | 2017 | 2016-06-11 | C | 132 | 0.084907 | 0.00039682
1 | 11826465 | 2016-06-11 10:05 | 2016-06-11 14:30 | 265 | 3 | 795 | 0.00239 | 0.002362 | 9.0187e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T3271 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace transformer T3271 follow up from OMS: 11825324. | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.002362 | 11 | 2017 | 2016-06-11 | C | 3 | 0.002362 | 9.0187e-06
1 | 11826580 | 2016-06-11 10:51 | 2016-06-11 13:55 | 184 | 45 | 7991.25 | 0.024024 | 0.023617 | 0.00013528 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB I23 | UNKNOWN | Faultman found CB I23 open when attending no power calls, at time of tripping CB I23 was back feeding a section of CB 4 from Pongaroa Sub as there was a feeder fault, suspect a second fault on CB 4 which caused CB I23 to trip, when open point ABS I29 was opened CB I23 was restored. Customer were checked all supply is restored. REF to OMS: 11825834. 2r line patrol 1340. | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.023617 | 11 | 2017 | 2016-06-11 | C | 45 | 0.023617 | 0.00013528
1 | 11826754 | 2016-06-11 13:05 | 2016-06-11 16:04 | 179 | 422 | 5061.65 | 0.015217 | 0.01141 | 0.0012746 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 2742 | UNKNOWN | CB 2742 tripped on N/T O/C & E/F flags, line was patrolled and sectionalised and no fault was found. This feeder has been tripping a lot in the last few weeks with no faults found, every time this trips we have to shut Motukawa Generation down to restore the network back into the normal configuration, maybe it's time to carry out pole to pole checks to locate the problem. | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.01141 | 33 | 2017 | 2016-06-11 | C | 422 | 0.01141 | 0.0012746
1 | 11827871 | 2016-06-11 14:04 | 2016-06-11 18:54 | 290 | 46 | 2439.3833 | 0.0073334 | 0.006918 | 0.00014129 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 740068 | JUMPER | Jumper at Fuses 5675 re-joined | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.006918 | 11 | 2017 | 2016-06-11 | C | 46 | 0.006918 | 0.00014129
1 | 11827957 | 2016-06-11 15:10 | 2016-06-11 15:54 | 44 | 13 | 576.1167 | 0.0017319 | 0.001614 | 3.9081e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | E93 | FUSE - ELEMENT/LINK (HV) | Check for safety - pole arcing and on fire. Advised SMC. ETA required: 25 minutes. F2094688 Faultman found 2 fuse burnt up at Fuses E93, line was isolated at Fuses E93 and line was patrolled and found ducks had flown into lines, Fuses reloaded supply restored. 2 X 15 amp hv fuses & 2 X fuse holders replaced. | F3 | ASHHURST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.001614 | 11 | 2017 | 2016-06-11 | C | 13 | 0.001614 | 3.9081e-05
1 | 11828087 | 2016-06-11 15:48 | 2016-06-11 18:30 | 162 | 132 | 11868.3333 | 0.035679 | 0.034488 | 0.0010943 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 4 | UNKNOWN | CB 4 tripped on B & C phase O/C line was patrolled and sectionalised but no fault was found. Very windy at the time. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.034488 | 11 | 2017 | 2016-06-11 | C | 132 | 0.034488 | 0.0010943
1 | 11829424 | 2016-06-11 21:01 | 2016-06-11 21:18 | 17 | 132 | 2307.8 | 0.0069378 | 0.005747 | 0.00039682 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 4 | UNKNOWN | CB 4 Trip. E/F. O/C. Reclosed OK after 18 Mins | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.005747 | 11 | 2017 | 2016-06-11 | C | 132 | 0.005747 | 0.00039682
1 | 11829574 | 2016-06-11 21:28 | 2016-06-12 11:08 | 820 | 132 | 19628.3333 | 0.059007 | 0.057816 | 0.00039682 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole P02591 | INSULATOR | ABS V85 Opened and CB 4 reclosed. Between ABS V85 and I29 to be left off until daylight to patrol lines for fault.Faultman found a floating wire at pole P02591.Faultman replaced the 11KV insulators with clamp top ones as old insulators are very old and degraded. 3 X 11KV clamp top insulators replaced. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.057816 | 11 | 2017 | 2016-06-11 | C | 132 | 0.057816 | 0.00039682
1 | 11830663 | 2016-06-12 08:29 | 2016-06-12 12:20 | 230 | 422 | 2849.85 | 0.0085672 | 0.004761 | 0.0012746 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 2742 | UNKNOWN | CB 2742 tripped on N/T & O/C flags on T/Power side & E/F flags on our side, line was patrolled and sectionalised and no fault was found. | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.004761 | 33 | 2017 | 2016-06-12 | C | 422 | 0.004761 | 0.0012746
1 | 11831089 | 2016-06-12 08:34 | 2016-06-12 10:49 | 135 | 3445 | 288117.6 | 0.86614 | 0.83507 | 0.010356 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | KINMAR076 | CIRCUIT BREAKER (HV) | TP KIN 2242 tripped neut time O/C, L/O. ( loss of MAR sub ) ( no flags from MAR sub ). MAR CB's 5, 7 & 2 backfeed via Sw/Gear 9083/3 ( BRD6 ) 33kV line patrolled with report of explosion at pole KINMAR076, burn marks evident possible bird strike. Patrol found no other obvious faults on O/H line. TP CB 2232 closed & all supply to MAR restored. 2r line patrol n/a line energised by powerco | S4 | KINLEITH2242-MARAETAI 33KV | KINLEITH 33 | Valley | TP_KINLEITH | Eastern Electricity | POWERCO | 0.83507 | 33 | 2017 | 2016-06-12 | C | 3445 | 0.83507 | 0.010356
1 | 11835164 | 2016-06-12 13:35 | 2016-06-12 14:32 | 56 | 177 | 10080.15 | 0.030303 | 0.028706 | 0.0005321 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 824933 | INSULATOR | Broken insulator - Neville Pope attending. Faultman found broken insulator on pole 824933, line was isolated at ABS's S31, S792, an assurance from Kourarau's CB C406 & C407 was needed also to replace the insulator with clamp top insulator. 1 X 11kV clamp top insulator used. 2r line patrol n/a. | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.028706 | 11 | 2017 | 2016-06-12 | C | 177 | 0.028706 | 0.0005321
1 | 11835312 | 2016-06-12 15:13 | 2016-06-12 15:57 | 44 | 33 | 1452 | 0.004365 | 0.004067 | 9.9205e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 6320 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuse and broken fuse holder at Fuses 6320, line was isolated at ABS 5558 to replace fuse holder & fuse. 1 X 10 amp HV fuse replaced. 1 X fuse holder replaced. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.004067 | 11 | 2017 | 2016-06-12 | C | 33 | 0.004067 | 9.9205e-05
1 | 11836083 | 2016-06-12 16:06 | 2016-06-12 16:48 | 42 | 282 | 11844 | 0.035605 | 0.033062 | 0.00084775 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Pole 801476 | CROSSARM - WHOLE ASSEMBLY | Ken Pattie has advised of rotten crossarm that needs urgent attention. Line was isolated at ABS's 1409, 4086 & 4213/1 to replace damaged x- arm and broken LV insulator on pole 801476. 1 X cross arm and all its hardware replaced. 1 X LV insulator replaced. | F3 | NGATAWA | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.033062 | 11 | 2017 | 2016-06-12 | C | 282 | 0.033062 | 0.00084775
1 | 11836457 | 2016-06-12 15:15 | 2016-06-12 21:57 | 402 | 17 | 6834 | 0.020544 | 0.020391 | 5.1105e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | T4136 | POLE | at 15:15, Clareville Sub, CB C831 Sommerset St Feeder. Fire comms called in Car V Pole. Faultman dispatched. Isolated Lines at Fuses 7627. Permit Issued & Repairs carried out. All Power Restored on completion. Fault was at Transformer Pole T4136. Materials Used: 1x Pole, 1x Transformer, 2 Hv Fuses, 4x Crossarms Whole Assemblies. Multiple other equipment used. NDR 34827 F2095157 - Fire comms Car vs pole, pole down a,d lines down in the paddock Advised control and SMC of 999 | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.020391 | 11 | 2017 | 2016-06-12 | C | 17 | 0.020391 | 5.1105e-05
1 | 11838827 | 2016-06-12 17:31 | 2016-06-13 02:25 | 534 | 208 | 2767 | 0.0083182 | 0.006442 | 3.3068e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5210E | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | at 20:18, Ngariki Sub, CB NG3 South Rd Feeder. Found blown HV Fuse at Fuses NG384. Reloaded, Relivened Unsuccessfully. This also caused CB NG3 to Trip, E/F, A + C Fault, & Auto Reclosed. Fuse at NG384 blew again. Isolated all transformers & spur lines and relivened 1 at a time. Found that transformer 5210E had faulted. Isolated lines at Fuses 6627. remainder of area relivened beyond NG384. Permit issued & repairs carried out. All Power Restored on completion. Replaced 1x Transformer & 3x HV Fuses & Fuse Holders. Brett Bensley Attended. 2r line patrol ? | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.006442 | 11 | 2017 | 2016-06-12 | C | 208 | 0.006442 | 3.3068e-05
1 | 11839288 | 2016-06-12 18:11 | 2016-06-12 20:38 | 147 | 432 | 44555.2333 | 0.13394 | 0.13004 | 0.0012987 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 818798 | NONE | at 18:11, Featherston Sub, CB C911 Tripped, Ph C O/C. Faultmen dispatched & investigation began. Feeder Sectionalised. Found branch on lines at Pole 818798 caused by trees inside zone. Knocked branch off with hotstick. All Power restored on completion. No Materials Used. NDR: 23395. No repair | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.13004 | 11 | 2017 | 2016-06-12 | C | 432 | 0.13004 | 0.0012987
1 | 11839966 | 2016-06-12 21:55 | 2016-06-12 23:30 | 95 | 6 | 570 | 0.0017135 | 0.001659 | 1.8037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 848319 | BINDER | at 21:15, Hau Nui Sub, CB C642 Tuturumuri Feeder. Found Fuse blown at Fuses 7318. Patrolled line & Found floating conductor at Pole 848319. Isolated lines at Fuses 7318. Permit issued & repairs carried out. All Power Restored on completion. 1x Binder Used. Aged Equipment. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.001659 | 11 | 2017 | 2016-06-12 | C | 6 | 0.001659 | 1.8037e-05
1 | 11840014 | 2016-06-12 21:36 | 2016-06-12 22:38 | 62 | 3 | 186 | 0.00055915 | 0.000532 | 9.0185e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5069E | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | at 20:40, Tasman Sub, CB TA8 Pihama Feeder. Found Fuses at Transformer 5069E had blown. Reloaded, Relivened & Found transformer faulty. Own Isolation & AP. Transformer Replaced, All Power Restored on Completion. 1x Transformer. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000532 | 11 | 2017 | 2016-06-12 | C | 3 | 0.000532 | 9.0185e-06
1 | 11840625 | 2016-06-12 20:28 | 2016-06-13 11:39 | 911 | 8 | 7289.4667 | 0.021914 | 0.021841 | 2.405e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 782827 | BINDER | Fuses 686 left open overnight. Very bad weather in the area - not safe to patrol tonight. will be done tomorrow morning. Further inspection found broken binder at Pole 782827. All 3 binders replaced, conductors re-sagged & livened OK. | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.021841 | 11 | 2017 | 2016-06-12 | C | 8 | 0.021841 | 2.405e-05
1 | 11841066 | 2016-06-13 00:18 | 2016-06-13 00:33 | 14 | 170 | 2541.5 | 0.0076401 | 0.006107 | 0.00051105 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9320 | UNKNOWN | Recloser 9320 L/O No flags, reclosed | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.006107 | 11 | 2017 | 2016-06-13 | C | 170 | 0.006107 | 0.00051105
1 | 11841670 | 2016-06-13 04:31 | 2016-06-13 08:43 | 251 | 137 | 22616.35 | 0.067988 | 0.066752 | 0.00041184 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B12373 | CONDUCTOR - REPAIR/REHANG | recloser 13024 L/O, E/F. Repair Line Down at Pole B12373 Isolation at ABS 1025 & 2634. Back feed from BRD CB 3 Via ABS 2621. Isolation at ABS 2634 as pole B12373 is the ABS 2631, so could not work safely with it live on one side. 4 meters of copper conductor & 4 sleeves. 2r line patrol 0632. 2r repair 0752 | F4 | PAPANUI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.066752 | 11 | 2017 | 2016-06-13 | C | 137 | 0.066752 | 0.00041184
1 | 11842171 | 2016-06-13 05:35 | 2016-06-13 10:45 | 310 | 3 | 930.45 | 0.0027971 | 0.00277 | 9.0184e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/732 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 2 Fuses found tripped at T2/732. Transformer to be replaced, defective. Replaced OK and relivened. | F3 | ASHHURST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.00277 | 11 | 2017 | 2016-06-13 | C | 3 | 0.00277 | 9.0184e-06
1 | 11842199 | 2016-06-13 06:38 | 2016-06-13 08:25 | 107 | 156 | 16762.2 | 0.05039 | 0.048982 | 0.00046896 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P01001 | FUSE - ELEMENT/LINK (HV) | No power to woolshed. Location: Approximately 2km up Marainga Road. 2 x 10 amp fuses replaced - cause unknown. | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.048982 | 11 | 2017 | 2016-06-13 | C | 156 | 0.048982 | 0.00046896
1 | 11844896 | 2016-06-13 07:49 | 2016-06-13 10:10 | 140 | 6 | 845 | 0.0025402 | 0.002486 | 1.8037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773123 | FUSE - ELEMENT/LINK (HV) | 858 - 2 x 8amp fuses. Cause unknown. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.002486 | 11 | 2017 | 2016-06-13 | C | 6 | 0.002486 | 1.8037e-05
1 | 11844979 | 2016-07-05 08:45 | 2016-07-05 11:23 | 158 | 78 | 12324 | 0.037036 | 0.036333 | 0.00023441 | NAPA ID:20780 TP_BUNNYTHORPE GXP > SANSON SUB > OHAKEA | 11 | Planned | 020780 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P30855 | NONE | Replace 11KV pole hit by lightning. Works location: Speedy Rd, Sanson. WO 30015963 | F1 | SKYHAWK | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.018166 | 5.5 | 2017 | 2016-07-05 | B | 78 | 0.036333 | 0.00023441
1 | 11845047 | 2016-07-05 09:00 | 2016-07-05 13:20 | 260 | 104 | 27069.4667 | 0.08135 | 0.080412 | 0.00031254 | NAPA ID:20868 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11 | Planned | 020868 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Q4 | NONE | 11kV pole changes. Works location: Mangahao Rd, Pahitua. WO 30024426 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.040206 | 5.5 | 2017 | 2016-07-05 | B | 104 | 0.080412 | 0.00031254
1 | 11845380 | 2016-06-28 09:15 | 2016-06-28 15:35 | 380 | 7 | 2660 | 0.0079945 | 0.007931 | 2.1038e-05 | NAPA ID:20621 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > SANDHURST | 11 | Planned | 020621 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 215116 | NONE | RECONDUCTOR OH LINES AND RE-POLE. Works location: Tip Lane. WO 30019227 | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.0039655 | 5.5 | 2017 | 2016-06-28 | B | 7 | 0.007931 | 2.1038e-05
1 | 11846289 | 2016-06-29 09:15 | 2016-06-29 14:03 | 288 | 7 | 2016 | 0.0060589 | 0.005995 | 2.1038e-05 | NAPA ID:20622 TP_MT MAUNGANUI 33 GXP > TE MAUNGA SUB > SANDHURST | 11 | Planned | 020622 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD5-056 | NONE | RECONDUCTOR OH LINES AND RE-POLE. Works location: Tip Lane. WO 30019227 | F3 | SANDHURST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.0029975 | 5.5 | 2017 | 2016-06-29 | B | 7 | 0.005995 | 2.1038e-05
1 | 11846555 | 2016-06-13 09:45 | 2016-06-13 11:15 | 90 | 18 | 1186.1 | 0.0035656 | 0.003403 | 5.4111e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 358876 | FUSE - ELEMENT/LINK (HV) | Faultman directed to check fuses at 122 On Owhakura Road. 2 x 6 amp fuses replaced due to goose at Fuses 113. | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.003403 | 11 | 2017 | 2016-06-13 | C | 18 | 0.003403 | 5.4111e-05
1 | 11846660 | 2016-06-13 09:58 | 2016-06-13 11:00 | 62 | 14 | 872.4333 | 0.0026227 | 0.002496 | 4.2086e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 815023 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp at Fuses7203 (pole 815023) due to hawk. | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.002496 | 11 | 2017 | 2016-06-13 | C | 14 | 0.002496 | 4.2086e-05
1 | 11846799 | 2016-06-12 05:36 | 2016-06-12 11:29 | 353 | 200 | 52914 | 0.15907 | 0.15727 | 0.00060124 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Car vs pole. Police P025558026. Line was isolated at ABS S312 to replace the pole 841251 this pole also had Fuses 7368 on them. 1 x pole & all hardware & full set of HV fuses. 2R LINE PATROL 0730. 2r repair 0752 | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.15727 | 11 | 2017 | 2016-06-12 | C | 200 | 0.15727 | 0.00060124
1 | 11848146 | 2016-06-28 09:02 | 2016-06-28 16:56 | 473 | 246 | 105534 | 0.31718 | 0.31496 | 0.00073934 | NAPA ID:19252 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | 019252 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 202215 | NONE | This job ran overtime. No specific details except that the work for the day did not flow as planned. Possibly too much work to try and complete within the outage time. Also when relivening, fuses SC3-082 blew. Believe this was due to the incorrect fuse size for the transformer (were 10A but needed to be 20A. Tx TC3-059 is 200kVA.). Also pulled 1x HV Fuse at FP1766 due to concern of these also being incorrect size fuses. Checked fuse and it was okay. OFF: 16:47, ON: 16:50. Levers Rd Conductor Upgrade Area 2 Poles and Hardware, remove temp 38. Replace Poles 202214, 202215, 202216, 202217, 202218, 202220, 202221, 202226. Remedial Works on 395882, Equipment Number on 202225, 202223. Works location: Levers Rd, Tauranga. WO 30015220 | F3 | MATUA POINT | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 0.15748 | 5.5 | 2017 | 2016-06-28 | B | 246 | 0.31496 | 0.00073934
1 | 11848365 | 2016-07-01 08:45 | 2016-07-01 12:50 | 245 | 2 | 490 | 0.0014726 | 0.001454 | 6.0106e-06 | NAPA ID:21352 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | 021352 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5067 | NONE | Replace Transformer TC5067 & Lengthen LV/HV cables as required. Works location: Horrell Rd. WO 30019459 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.000727 | 5.5 | 2017 | 2016-07-01 | B | 2 | 0.001454 | 6.0106e-06
1 | 11848402 | 2016-06-30 09:00 | 2016-06-30 14:50 | 350 | 256 | 89600 | 0.26928 | 0.26697 | 0.00076937 | NAPA ID:19257 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | 019257 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 382795 | NONE | Levers Rd Conductor Upgrade. Shut 6: Area 2 between SC4007 - SC4315 and Temp 28. Replace ABS with DDO's Pole 382795, Replace Pole 202232. Replace conductor between 382795 and 395970(202233) with Fluorine (4 Spans). Replace conductor between 395476 (202203) and 395575 (202213 / Temp 28) with iodine (10 Spans). WORKS LOCATION: Levers Rd, Tauranga. WO 30015220. | F3 | MATUA POINT | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 0.13349 | 5.5 | 2017 | 2016-06-30 | B | 256 | 0.26697 | 0.00076937
1 | 11848456 | 2016-07-06 09:03 | 2016-07-06 15:11 | 368 | 82 | 30232.0333 | 0.090854 | 0.090114 | 0.00024643 | NAPA ID:20771 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11 | Planned | 020771 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2832 | NONE | Replace 33KV pole with DBL 12.5 replace 100KV Trani T2832. Replace 11KV pole P39634. Works location: Maple St, Bunnythorpe. WO 30001048 | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.045057 | 5.5 | 2017 | 2016-07-06 | B | 82 | 0.090114 | 0.00024643
1 | 11848811 | 2016-06-30 08:56 | 2016-06-30 16:28 | 452 | 32 | 14464 | 0.04347 | 0.04318 | 9.6171e-05 | NAPA ID:18977 TP_KINLEITH GXP > BAIRD ROAD SUB > KAURI ST | 11 | Planned | 018977 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole B0089 | NONE | Reconductor between poles B0089 & B0072. Works location: Paraonui Rd, Tokoroa. WO 30017824 | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.02159 | 5.5 | 2017 | 2016-06-30 | B | 32 | 0.04318 | 9.6171e-05
1 | 11849137 | 2016-07-06 08:30 | 2016-07-06 14:50 | 379 | 2 | 759.8667 | 0.0022836 | 0.002265 | 6.0104e-06 | NAPA ID:20525 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 020525 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7467 | NONE | replace 11kv poles and hardware. Works location: Kaiparoro Rd, Masterton. WO 30019523 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0011325 | 5.5 | 2017 | 2016-07-06 | B | 2 | 0.002265 | 6.0104e-06
1 | 11849253 | 2016-07-06 08:45 | 2016-07-06 14:52 | 367 | 19 | 6975.5333 | 0.020963 | 0.020791 | 5.7099e-05 | NAPA ID:21323 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | 021323 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Fuses 772 | NONE | Tree trimming and felling between poles 773513 and 773506. Works location: Pakaraka Rd, Waitotara. WO 30026260 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.010396 | 5.5 | 2017 | 2016-07-06 | B | 19 | 0.020791 | 5.7099e-05
1 | 11849510 | 2016-06-13 14:25 | 2016-06-13 17:04 | 158 | 13 | 2062.6667 | 0.0062007 | 0.006083 | 3.908e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 5708 | FUSE - ELEMENT/LINK (HV) | Advised Dennis that customer advised digger taking out trees - touched the lines - which has blown pole fuse that has taken out the whole road - lines not damaged at all - Tx 3736T also affected - ** check with FM extent of this outage and either force up or link 11850054 **. 2 HT fuses tripped at 5708, reloaded OK and livened (10A Rating). | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.006083 | 11 | 2017 | 2016-06-13 | C | 13 | 0.006083 | 3.908e-05
1 | 11851697 | 2016-06-13 22:17 | 2016-06-13 23:45 | 87 | 13 | 1142.4833 | 0.0034345 | 0.003317 | 3.908e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 757079 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 8457, line was patrolled no cause was found. 2 X 15 amp HV fuses replaced | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.003317 | 11 | 2017 | 2016-06-13 | C | 13 | 0.003317 | 3.908e-05
1 | 11851851 | 2016-06-14 07:05 | 2016-06-14 08:05 | 59 | 9 | 537 | 0.0016143 | 0.001533 | 2.7055e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 747792 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp fuses at Fuses 8295 due to goose. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.001533 | 11 | 2017 | 2016-06-14 | C | 9 | 0.001533 | 2.7055e-05
1 | 11851905 | 2016-06-14 10:11 | 2016-06-14 11:38 | 87 | 285 | 24795 | 0.074536 | 0.071966 | 0.00085674 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 210329 | CONDUCTOR - REPAIR/REHANG | HV lines hanging almost touching the LV line. Looks like crossarm is on an angle. Lines isolated between Sw/gear 9461/1, ABS's SD3-095, SD3-003 & SD3-009. Backfeed from RS9805. Line reassessed and cross arm secured. This is a temp fix and a job will be applied for to replace complete structure. | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.071966 | 11 | 2017 | 2016-06-14 | C | 285 | 0.071966 | 0.00085674
1 | 11851942 | 2016-07-04 09:36 | 2016-07-04 14:51 | 315 | 20 | 6300 | 0.018933 | 0.018752 | 6.0105e-05 | NAPA ID:21028 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 021028 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 12109 | NONE | We are replacing HV cross arms and LV cross arms on Ngaro road. Works location: Ngaro Rd, Tariki. WO 30027078 | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.009376 | 3.3 | 2017 | 2016-07-04 | B | 20 | 0.018752 | 6.0105e-05
1 | 11851948 | 2016-07-06 09:16 | 2016-07-06 13:16 | 240 | 94 | 22569.4 | 0.067826 | 0.066978 | 0.00028249 | NAPA ID:21360 TP_GREYTOWN GXP > MARTINBOROUGH SUB > COLOGNE ST | 11 | Planned | 021360 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole 816690 | NONE | Tree works around over head power lines. Works location: Hinakura Rd. WO 30026281 | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.033489 | 5.5 | 2017 | 2016-07-06 | B | 94 | 0.066978 | 0.00028249
1 | 11852216 | 2016-06-14 09:50 | 2016-06-14 10:20 | 30 | 2 | 60 | 0.00018037 | 0.000162 | 6.0122e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | N/A - NOT APPLICABLE | TERMINATION (CABLE TERMINATION) | LV lead from 200kVA transformer - need to isolate transformer to repair lead. Request 2r to do this work - working through control to isolate transformer. To be decided at invoicing level whether 2R is the correct allocation. All works is complete. ASW Replaced a LV cable onto back of transformer (one phase only). | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000162 | 11 | 2017 | 2016-06-14 | C | 2 | 0.000162 | 6.0122e-06
1 | 11853593 | 2016-07-04 09:12 | 2016-07-04 16:31 | 439 | 1 | 439 | 0.0013193 | 0.00131 | 3.0052e-06 | NAPA ID:21276 TP_HINUERA GXP > TIRAU SUB > NZDG TIRAU 1 | 11 | Planned | 021276 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3777 | NONE | Replace existing T blade transformer TC3777 & 11kV cable from TC3777 to ABS 2632. Both cable CB3777-TC3777 & ABS2632-TC3777 to be connected onto TC3777 HV bushings. Works location: Patetere St, Tirau. WO 10148293 | F1 | NZDG TIRAU 3 | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000655 | 5.5 | 2017 | 2016-07-04 | B | 1 | 0.00131 | 3.0052e-06
1 | 11853964 | 2016-07-05 08:48 | 2016-07-05 14:00 | 312 | 56 | 17472 | 0.052507 | 0.052002 | 0.00016829 | NAPA ID:19414 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 12 | 11 | Planned | 019414 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 113 | NONE | Replace and upgrade transformer 113 to 200kVA. Works location: Branch Rd. WO 30018769 | F3 | BROOKLANDS 12 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.026001 | 5.5 | 2017 | 2016-07-05 | B | 56 | 0.052002 | 0.00016829
1 | 11854350 | 2016-07-05 09:19 | 2016-07-05 15:16 | 357 | 32 | 11424 | 0.034332 | 0.034043 | 9.6167e-05 | NAPA ID:18979 TP_KINLEITH GXP > BAIRD ROAD SUB > KAURI ST | 11 | Planned | 018979 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | B0068 | NONE | Reconductor between poles B0068 & B0072. Works location: Paraonui Rd, Tokoroa. WO 30017824 | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.017021 | 5.5 | 2017 | 2016-07-05 | B | 32 | 0.034043 | 9.6167e-05
1 | 11854782 | 2016-07-06 08:45 | 2016-07-06 13:16 | 271 | 22 | 5962 | 0.017917 | 0.017718 | 6.6115e-05 | NAPA ID:21294 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | 021294 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC640 | NONE | Carryout out maintenance: Replace crossarms and ABS IC640 DNO160512. Works location: Brown St, Tatuanui. WO 30027307 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.008859 | 5.5 | 2017 | 2016-07-06 | B | 22 | 0.017718 | 6.6115e-05
1 | 11855291 | 2016-07-07 08:33 | 2016-07-07 11:43 | 190 | 7 | 1333.9667 | 0.0040088 | 0.003945 | 2.1036e-05 | NAPA ID:20829 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > WAITUNA | 11 | Planned | 020829 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T3/163 | NONE | Remove 1 pole of 2 pole structure T3/163. Works location: McKays Rd, Feilding. WO 30012868 | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.0019725 | 5.5 | 2017 | 2016-07-07 | B | 7 | 0.003945 | 2.1036e-05
1 | 11855312 | 2016-07-06 08:31 | 2016-07-06 15:26 | 415 | 12 | 4985.2 | 0.014982 | 0.014873 | 3.6063e-05 | NAPA ID:21284 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | 021284 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC1309 | NONE | Carryout out maintenance: replace ABS IC1309 and convert to DDO structure. Carry out maintenance on spur line. Works location: Bell & Waikuku Rd, Morrinsville. WO 30027395 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0074365 | 5.5 | 2017 | 2016-07-06 | B | 12 | 0.014873 | 3.6063e-05
1 | 11855336 | 2016-07-07 09:20 | 2016-07-07 12:56 | 216 | 170 | 36656.5333 | 0.11016 | 0.10863 | 0.00051088 | NAPA ID:20876 TP_BUNNYTHORPE GXP > FEILDING SUB > MAKINO | 11 | Planned | 020876 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV O13 | NONE | Replace pole hit by motorbike. Works location: Makino Rd, Feilding. WO 30019017 | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.054313 | 5.5 | 2017 | 2016-07-07 | B | 170 | 0.10863 | 0.00051088
1 | 11855767 | 2016-07-07 08:45 | 2016-07-07 15:50 | 424 | 3 | 1273.9 | 0.0038283 | 0.003801 | 9.0155e-06 | NAPA ID:21318 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 021318 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 836409 | NONE | Tree removal from around 11kv over head lines between poles 836409 836406. Works location: Matahiwi Rd. WO 30026281 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0019005 | 5.5 | 2017 | 2016-07-07 | B | 3 | 0.003801 | 9.0155e-06
1 | 11855820 | 2016-06-14 11:39 | 2016-06-14 17:29 | 349 | 65 | 16527.6833 | 0.049684 | 0.049097 | 0.0001954 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04228 | BINDER | Recloser V5 Tripped A/R a number of times before locking out - Line was being patrolled before it locked out Feeder sectionlised while feeder being patrolled. Broken binder found at Pole P04228 - Isolated at ABS V7 and Links V6. Used 2 x binders | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.049097 | 11 | 2017 | 2016-06-14 | C | 65 | 0.049097 | 0.0001954
1 | 11855888 | 2016-06-21 09:13 | 2016-06-21 16:40 | 447 | 39 | 17433 | 0.0524 | 0.052048 | 0.00011723 | NAPA ID:18997 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 018997 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 213108 | POLE | Replace poles ,hardware and conductor between SD3-141 & TEMP's 71-72, Applicant is also going to install LINKS TEMP63 between Pole 213117 & 213118 during this shutdown. 15:00 Ken Langman called to say they would be about an Hour late as they had some gear failure when running conductor. | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.026024 | 5.5 | 2017 | 2016-06-21 | B | 39 | 0.052048 | 0.00011723
1 | 11857125 | 2016-07-06 09:21 | 2016-07-06 11:20 | 118 | 3 | 355.7 | 0.001069 | 0.001041 | 9.0156e-06 | NAPA ID:21203 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 021203 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4736 | NONE | To replace the 11kV Fuse arm & Install a 400V Fuse Disconnector (TC4736). Works location: Mowbray Rd, Waharoa. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0005205 | 5.5 | 2017 | 2016-07-06 | B | 3 | 0.001041 | 9.0156e-06
1 | 11857306 | 2016-07-06 09:37 | 2016-07-06 12:43 | 186 | 3 | 558 | 0.0016769 | 0.001649 | 9.0156e-06 | NAPA ID:20980 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020980 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1271 | NONE | To replace the 11kV Fuse arm, Replace 400V Spreader Arm & Relocate, Relocate the transformer to New Steel Arm & Install a 400V Fuse Disconnector. Works location: Hwy 29, Te Poi. WO 30018182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0008245 | 5.5 | 2017 | 2016-07-06 | B | 3 | 0.001649 | 9.0156e-06
1 | 11858658 | 2016-07-06 14:40 | 2016-07-06 14:50 | 10 | 3 | 30 | 9.0156e-05 | 6.3e-05 | 9.0156e-06 | NAPA ID:21052 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 021052 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2684 | NONE | To install a 3 phase fuse/disconnector on TC2684. Works location: Hwy 29, Te Poi. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 3.15e-05 | 5.5 | 2017 | 2016-07-06 | B | 3 | 6.3e-05 | 9.0156e-06
1 | 11858689 | 2016-07-07 09:15 | 2016-07-07 14:40 | 325 | 6 | 1950 | 0.0058601 | 0.005806 | 1.8031e-05 | NAPA ID:19221 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 019221 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP872 | NONE | To replace arms and hardware on Stopford Rd. Works location: Stopford Rd, Te Poi. WO 30017838 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.002903 | 5.5 | 2017 | 2016-07-07 | B | 6 | 0.005806 | 1.8031e-05
1 | 11859054 | 2016-07-08 09:45 | 2016-07-08 12:10 | 145 | 5 | 725 | 0.0021787 | 0.002133 | 1.5026e-05 | NAPA ID:20920 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020920 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1963 | NONE | To replace the 400V Spreader arm, relocate the transformer & install a 400V Fuse Disconnector. Works location: Hwy 24, Matamata. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0010665 | 5.5 | 2017 | 2016-07-08 | B | 5 | 0.002133 | 1.5026e-05
1 | 11860165 | 2016-06-14 18:44 | 2016-06-14 20:24 | 100 | 2 | 200.1 | 0.00060152 | 0.000583 | 6.0122e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1177 | FUSE - ELEMENT/LINK (HV) | 2 HT Fuses at 1177 reloaded OK (NOTE: this is incorrect transformer - unable to force up). OMS linked | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000583 | 11 | 2017 | 2016-06-14 | C | 2 | 0.000583 | 6.0122e-06
1 | 11862913 | 2016-06-15 06:37 | 2016-06-15 08:49 | 131 | 2 | 263.3333 | 0.0007916 | 0.000773 | 6.0121e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2323 | FUSE - ELEMENT/LINK (HV) | 3x3amp HV Fuses blown at Fuses 2323 Blown possibly due to ducks. | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000773 | 11 | 2017 | 2016-06-15 | C | 2 | 0.000773 | 6.0121e-06
1 | 11862923 | 2016-06-15 06:51 | 2016-06-15 14:32 | 461 | 356 | 41286.4 | 0.12411 | 0.1209 | 0.0010702 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | K2350 | POLE | CB 1 Tripped B & C Fault, E/F Ground Fault. Car vs pole at K2350. Isolation at ABS 2534. No back feeds available. Feeder relivened 11m pole, 1 HV crossam, 1 Double LV crossarm, 1 tap off crossarm, HV & LV Insulators & Conductor & Sleeves. | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.1209 | 11 | 2017 | 2016-06-15 | C | 356 | 0.1209 | 0.0010702
1 | 11863982 | 2016-06-15 08:00 | 2016-06-15 11:01 | 180 | 948 | 10129.2833 | 0.030449 | 0.0219 | 0.0026694 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | F2097235 | POLE | fire comms reporting car vs pole ETA required. F2097235 fire comms advised 20min ETA | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.0219 | 11 | 2017 | 2016-06-15 | C | 948 | 0.0219 | 0.0026694
1 | 11867067 | 2016-06-15 09:21 | 2016-06-15 11:31 | 130 | 1 | 130.2 | 0.00039139 | 0.000382 | 3.006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P48861 | JUMPER | Line hanging down near tx - customer has no power. 9.22am advised Tallia at svs hub. TX isolated under own ap replaced jumper from ddo to tx | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.000382 | 11 | 2017 | 2016-06-15 | C | 1 | 0.000382 | 3.006e-06
1 | 11867281 | 2016-06-16 10:15 | 2016-06-16 14:37 | 262 | 41 | 10742 | 0.032291 | 0.03192 | 0.00012325 | NAPA ID:21652 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD INDUSTRIAL | 11 | Planned | 021652 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 734729 | NONE | Install Temp Recloser 12153 on pole 734729 | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.01596 | 5.5 | 2017 | 2016-06-16 | B | 41 | 0.03192 | 0.00012325
1 | 11867445 | 2016-06-20 08:50 | 2016-06-20 15:00 | 369 | 92 | 19581 | 0.058857 | 0.058027 | 0.00018336 | NAPA ID:21656 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | 021656 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 207532 | NONE | Change HV Poles and cross arms between SA2 010 and Temp ABS 42. Backfeed required from KPT2 via 9405/2. 2x HV cable terminations at Poles 207532 & 20763601. Replace condemned Pole 207519. WORKS LOCATION: Seaforth Rd, Athenree. WO 30017825 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.029014 | 5.5 | 2017 | 2016-06-20 | B | 92 | 0.058027 | 0.00018336
1 | 11867510 | 2016-06-15 10:55 | 2016-06-15 13:01 | 126 | 27 | 3402 | 0.010227 | 0.009983 | 8.1164e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 847844 | DEAD-ENDS | Check for safety - Dead-end has broken and HV line has dropped about 2 meters - Pole 847844 Advised control and SMC of 999. All 3 dead-ends replaced at pole 847844. Isolation at ABS MA451, 6757 & MA 411. Back feed from Cam 5 via ABS MA408. Justin 027 445 9162. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.009983 | 11 | 2017 | 2016-06-15 | C | 27 | 0.009983 | 8.1164e-05
1 | 11867997 | 2016-07-06 09:30 | 2016-07-06 10:33 | 63 | 22 | 1394.4333 | 0.0041906 | 0.003992 | 6.6115e-05 | NAPA ID:21415 TP_HAWERA GXP > KAPUNI SUB > MATAPU | 11 | Planned | 021415 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 721262 | NONE | Replace rotten Xarm at pole 721262. Works location: Hastings Rd, Hawera. WO: 10160665 | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.001996 | 5.5 | 2017 | 2016-07-06 | B | 22 | 0.003992 | 6.6115e-05
1 | 11871139 | 2016-06-15 15:50 | 2016-06-15 18:05 | 135 | 12 | 1620 | 0.0048698 | 0.004761 | 3.6073e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 725839 | CONDUCTOR - REPAIR/REHANG | Fuses blown at fuses 6863, tree through the line. Isolation at fuses 6863. line repaired & relivened. Used 6mtrs conductor, 8 sleeves and 2 x binders | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.004761 | 11 | 2017 | 2016-06-15 | C | 12 | 0.004761 | 3.6073e-05
1 | 11871215 | 2016-06-15 16:31 | 2016-06-15 20:00 | 209 | 4 | 836 | 0.0025131 | 0.002476 | 1.2024e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K12776 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 2x HV Fuses Blown at Transformer TC4246. Transformer blown & needs replacing. Transformer replaced. | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.002476 | 11 | 2017 | 2016-06-15 | C | 4 | 0.002476 | 1.2024e-05
1 | 11871280 | 2016-07-07 09:30 | 2016-07-07 14:00 | 270 | 27 | 7290 | 0.021908 | 0.021664 | 8.114e-05 | NAPA ID:21327 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 7 | 11 | Planned | 021327 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 454 | NONE | Replace existing industrial type tx with new dogbone type, incl. pad. Existing tx has severe rust. Works location: Wanaka Terrace. WO 30027510 | F3 | MANGATI RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.010832 | 5.5 | 2017 | 2016-07-07 | B | 27 | 0.021664 | 8.114e-05
1 | 11872299 | 2016-06-15 17:15 | 2016-06-15 19:40 | 145 | 1 | 145.5 | 0.00043738 | 0.000428 | 3.006e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | T4544 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 5.16pm advised Sammy at svs hub Have checked transformer to leak appears to be something spilled on outside of transformer | F3 | MOFFAT RD | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.000428 | 11 | 2017 | 2016-06-15 | C | 1 | 0.000428 | 3.006e-06
1 | 11877106 | 2016-06-21 09:01 | 2016-06-21 15:33 | 391 | 363 | 141936.6333 | 0.42663 | 0.42336 | 0.0010911 | NAPA ID:21651 TP_GREYTOWN GXP | 11 | Planned | 021651 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C640/2 | CROSSARM - WHOLE ASSEMBLY | Replace broken 33kv crossarms | S5 | HAU NUI 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0.21168 | 5.5 | 2017 | 2016-06-21 | B | 363 | 0.42336 | 0.0010911
1 | 11877112 | 2016-06-17 11:00 | 2016-06-17 12:19 | 79 | 234 | 18486 | 0.055568 | 0.053458 | 0.0007034 | NAPA ID:21680 TP_WAIHOU GXP > MIKKELSEN ROAD SUB | 11 | Planned | 021680 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1185 | NONE | To install jumpers across ABS 1185 to facilitate Transpower switching. Works location: Bailey Rd, Te Aroha. WO 30025209 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.026729 | 5.5 | 2017 | 2016-06-17 | B | 234 | 0.053458 | 0.0007034
1 | 11877126 | 2016-07-05 10:16 | 2016-07-05 13:30 | 194 | 3 | 582 | 0.001749 | 0.001721 | 9.0156e-06 | NAPA ID:20790 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 020790 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | O487 | NONE | Cut trees between poles O487-O14264. Works location: Ohinewai Rd, Kaihere. WO 30026193 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0008605 | 5.5 | 2017 | 2016-07-05 | B | 3 | 0.001721 | 9.0156e-06
1 | 11877729 | 2016-07-07 10:00 | 2016-07-07 11:31 | 91 | 12 | 1092 | 0.0032817 | 0.003173 | 3.6062e-05 | NAPA ID:21240 TP_HINUERA GXP > PUTARURU SUB > LICHFIELD | 11 | Planned | 021240 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2012 | NONE | Replace Tx arms at TC 2012. Works location: Hwy 1, Lichfield. WO 30027658 | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.0015865 | 5.5 | 2017 | 2016-07-07 | B | 12 | 0.003173 | 3.6062e-05
1 | 11877734 | 2016-06-19 08:54 | 2016-06-19 11:26 | 152 | 1 | 152 | 0.00045689 | 0.000447 | 3.0058e-06 | NAPA ID:21598 TP_BUNNYTHORPE GXP > FEILDING SUB > CROWN | 11 | Planned | 021598 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/276 | NONE | Replacing T3/276 | F2 | CROWN | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.0002235 | 5.5 | 2017 | 2016-06-19 | B | 1 | 0.000447 | 3.0058e-06
1 | 11878298 | 2016-06-16 09:37 | 2016-06-16 10:06 | 29 | 208 | 0 | 0 | 0 | 0 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 712557 | UNKNOWN | Auto reclose NG3 trip flags PH B & EF Trip flags. Magpies found on lines at Pole 712557 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-06-16 | C | 208 | 0 | 0
1 | 11879385 | 2016-07-05 09:10 | 2016-07-05 12:00 | 170 | 20 | 3400 | 0.010218 | 0.010037 | 6.0105e-05 | NAPA ID:21211 TP_KOPU GXP > KEREPEHI SUB > NGATEA | 11 | Planned | 021211 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC906 | NONE | Isolate TC906 and change Xarms. Works location: Pipiroa Rd. WO 30027313 | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.0050185 | 5.5 | 2017 | 2016-07-05 | B | 20 | 0.010037 | 6.0105e-05
1 | 11879858 | 2016-07-07 09:07 | 2016-07-07 12:00 | 173 | 27 | 4680.9 | 0.014067 | 0.013823 | 8.114e-05 | NAPA ID:21223 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021223 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2640 | NONE | Replace 11kV x arm & DDO's & 50kVa Tx at pole G12614(TC2640). AP1: Replace TX DDO's for TX TC2640. AP2: To complete TX TC2640 replacement. Works location: Peria Rd, Matamata. WO 30027656 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0069115 | 5.5 | 2017 | 2016-07-07 | B | 27 | 0.013823 | 8.114e-05
1 | 11880011 | 2016-07-05 09:00 | 2016-07-05 14:53 | 353 | 246 | 86838 | 0.26097 | 0.25875 | 0.00073929 | NAPA ID:19258 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | 019258 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 395575 | NONE | Levers Rd Conductor Upgrade Area 2. Shut 7: Area 2 between Temp 28 and 9801/3. Replace conductor between 395575 (202213/Temp 28) and 395882 (202227) 14 Spans. Works location: Levers Rd, Tauranga. WO 30015220 | F3 | MATUA POINT | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 0.12937 | 5.5 | 2017 | 2016-07-05 | B | 246 | 0.25875 | 0.00073929
1 | 11882481 | 2016-07-08 09:51 | 2016-07-08 10:51 | 60 | 21 | 1260 | 0.0037865 | 0.003597 | 6.3108e-05 | NAPA ID:21420 TP_OPUNAKE GXP > TASMAN SUB > TE KIRI | 11 | Planned | 021420 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 714098 | NONE | Replace rotten Hv Xarm. Works location: ELtham Rd, Opunake. WO 30015341 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.0017985 | 5.5 | 2017 | 2016-07-08 | B | 21 | 0.003597 | 6.3108e-05
1 | 11882603 | 2016-07-12 09:00 | 2016-07-12 13:02 | 242 | 6 | 1452 | 0.0043633 | 0.004309 | 1.803e-05 | NAPA ID:21363 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 021363 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole P27889 | NONE | Cutting trees around the 11Kv on Finnis rd. Works location: Finnis Rd. WO 30026290 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.0021545 | 5.5 | 2017 | 2016-07-12 | B | 6 | 0.004309 | 1.803e-05
1 | 11882614 | 2016-07-13 09:00 | 2016-07-13 15:25 | 385 | 8 | 3080 | 0.0092554 | 0.009183 | 2.404e-05 | NAPA ID:21370 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 021370 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole P14381 | NONE | Cutting trees around the 11kV. Works location: Finnis Rd. WO 30026290 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.0045915 | 5.5 | 2017 | 2016-07-13 | B | 8 | 0.009183 | 2.404e-05
1 | 11882633 | 2016-07-14 11:25 | 2016-07-14 14:45 | 200 | 55 | 11017.4167 | 0.033107 | 0.032611 | 0.00016527 | NAPA ID:21376 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 021376 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole P44644 | NONE | Cutting tree away from 11kV. Works location: Valley Rd, Colyton. WO 30026290 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.016306 | 5.5 | 2017 | 2016-07-14 | B | 55 | 0.032611 | 0.00016527
1 | 11882656 | 2016-06-17 10:15 | 2016-06-17 13:30 | 195 | 2 | 390 | 0.0011723 | 0.001154 | 6.0119e-06 | NAPA ID:21708 TP_HUIRANGI GXP > INGLEWOOD SUB > KAIMATA | 6.6 | Planned | 021708 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 758994 | INSULATOR | Urgent replacement of 33kV insulators. | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000577 | 3.3 | 2017 | 2016-06-17 | B | 2 | 0.001154 | 6.0119e-06
1 | 11882660 | 2016-07-12 12:18 | 2016-07-12 14:15 | 117 | 17 | 1989 | 0.005977 | 0.005823 | 5.1086e-05 | NAPA ID:21427 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 021427 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P47151 | NONE | Install new connections on pole p47139, Install earth spigot on pole p47151. Work location: Pongaroa Rd. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.0029115 | 5.5 | 2017 | 2016-07-12 | B | 17 | 0.005823 | 5.1086e-05
1 | 11882752 | 2016-07-08 13:45 | 2016-07-08 14:39 | 54 | 2 | 108 | 0.00032456 | 0.000306 | 6.0103e-06 | NAPA ID:20923 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020923 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1424 | NONE | To install a 400V Fuse Disconnector. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000153 | 5.5 | 2017 | 2016-07-08 | B | 2 | 0.000306 | 6.0103e-06
1 | 11883103 | 2016-06-16 15:14 | 2016-06-16 20:43 | 328 | 314 | 23025.4667 | 0.069215 | 0.066383 | 0.00094389 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T5358 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | CB TA 8 - tripped on EF flags, received a call from customer of a big flash on south rd, faultman found at transformer T5358 it had blown 2 11KV fuses and had burnt fuse holders, line was isolated at ABS's TA815 & TA836 to replace the 3 fuse holders and fuses. Transformer also found to be faulty. Used 1 x 30 kVA 3 phase transformer, 3 x fuse bases and carriers and, 3 x 3 amp fuses. Cause unknown | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.066383 | 11 | 2017 | 2016-06-16 | C | 314 | 0.066383 | 0.00094389
1 | 11886536 | 2016-06-16 17:10 | 2016-06-16 19:50 | 160 | 1 | 160 | 0.00048096 | 0.000471 | 3.006e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 760299 | CONDUCTOR - REPAIR/REHANG | Re-created outage for 11886536 | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000471 | 6.6 | 2017 | 2016-06-16 | C | 1 | 0.000471 | 3.006e-06
1 | 11886569 | 2016-06-17 08:52 | 2016-06-17 09:44 | 52 | 4 | 208 | 0.00062524 | 0.000589 | 1.2024e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D12756 | CONDUCTOR - REPAIR/REHANG | Transformer TC335 11kV Fuses opened to Repair LV Conductor. Used 3 x 25mm Sleeves. 2m of 25mm conductor | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000589 | 11 | 2017 | 2016-06-17 | C | 4 | 0.000589 | 1.2024e-05
1 | 11887141 | 2016-06-17 07:48 | 2016-06-17 09:09 | 81 | 728 | 18603.0333 | 0.05592 | 0.049355 | 0.0025431 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | 1 | UNKNOWN | Tauranga Sub CB 11 Kaimai Drive tripped after Backfeed area from sectionaliser 9698 via sectionaliser 13017 Sectionalised feeder and found no fault. Suspect trees in line, to be defected by faultman. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.049355 | 11 | 2017 | 2016-06-17 | C | 728 | 0.049355 | 0.0025431
1 | 11888134 | 2016-07-08 10:10 | 2016-07-08 14:05 | 235 | 5 | 1175 | 0.0035311 | 0.003485 | 1.5026e-05 | NAPA ID:21054 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 021054 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC317 | NONE | To replace the 11kV Pin arm, 11kV Fuse arm, 400V fuse arm, Install fuse disconnector & relocate transformer on TC317. Works location: Hwy 29, Te Poi. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0017425 | 5.5 | 2017 | 2016-07-08 | B | 5 | 0.003485 | 1.5026e-05
1 | 11888142 | 2016-07-04 14:32 | 2016-07-04 16:50 | 138 | 69 | 9522 | 0.028616 | 0.027993 | 0.00020736 | NAPA ID:21319 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > KOROMIKO ST | 11 | Planned | 021319 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 203077 | NONE | 1. LLB cable at pole 203077 (from SK5-135) and drop to ground (LLP) 2. Joint existing cable from SK5-135 to new cable from new switchgear 13028-3 (AP) 3. Test cables / joint between switchgear SK5-135 & 13028-3 (TP) 4. Liven new switchgear 13028-3 from SK5-135 5. Change-over trans TJ5-007 from DDO fuses S4649 to new fuse-switch 13028-2 & liven (AP) Works location: Edgecumbe Rd, Tauranga. WO 30015128 | F2 | KOROMIKO ST | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 0.013997 | 5.5 | 2017 | 2016-07-04 | B | 69 | 0.027993 | 0.00020736
1 | 11892519 | 2016-06-17 13:51 | 2016-06-17 13:55 | 4 | 5 | 20 | 6.0119e-05 | 1.5e-05 | 1.503e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | C13926 | NONE | Wilf Martin reported test results of transformer TC505 as R - 263V , W - 255V , B - 259v, R-W 449v, R-B 452v, W-B 442v. Customer has reported damaged equipment. PQI 1333, 432 Taititi rd. 1R - FM required to Tap down Transformer and notify NOC of Test results when restored Marty Keenan attended. Transformer tapped to lowest tap - Voltages measured with no load A ph 245v B ph 245v C ph 245v | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 1.5e-05 | 11 | 2017 | 2016-06-17 | C | 5 | 1.5e-05 | 1.503e-05
1 | 11893488 | 2016-06-17 15:56 | 2016-06-17 16:40 | 44 | 3 | 132 | 0.00039679 | 0.000369 | 9.0179e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 2836T | CONDUCTOR - REPAIR/REHANG | Advised hub of 999 and emailed. Faultman repaired LV line hit by digger at transformer 2836T. 70 meter conductor used & 12 X sleeves used. NDR: N100176 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000369 | 11 | 2017 | 2016-06-17 | C | 3 | 0.000369 | 9.0179e-06
1 | 11893550 | 2016-06-27 11:21 | 2016-06-27 14:22 | 181 | 4 | 724 | 0.002176 | 0.002139 | 1.2022e-05 | NAPA ID:21734 TP_TAURANGA 33 GXP > KAURI POINT > BOWENTOWN | 11 | Planned | 021734 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TA2-135 | NONE | Replace leaking TX TA2-135 with New 30kVA 3 Phase. Works location: Waiau Rd. WO 30007223 | F4 | BOWENTOWN | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.0010695 | 5.5 | 2017 | 2016-06-27 | B | 4 | 0.002139 | 1.2022e-05
1 | 11893950 | 2016-06-17 20:00 | 2016-06-17 21:30 | 90 | 3 | 270 | 0.00081161 | 0.000784 | 9.0179e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 821714 | JUMPER | Box up pole sparking, first white building, Toni Freeman 027 275 3099. Repaired burnt up connections on fuse at transformer T2479. Isolation at HV Fuses 7585. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000784 | 11 | 2017 | 2016-06-17 | C | 3 | 0.000784 | 9.0179e-06
1 | 11894095 | 2016-06-17 19:35 | 2016-06-17 21:08 | 92 | 24 | 2221.2 | 0.0066769 | 0.00646 | 7.2143e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 807109 | FUSE - ELEMENT/LINK (HV) | 2x20amp HV fuses blown at Fuses 997. Reloaded & Livened. Unknown Cause | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.00646 | 11 | 2017 | 2016-06-17 | C | 24 | 0.00646 | 7.2143e-05
1 | 11894402 | 2016-06-17 21:41 | 2016-06-18 01:03 | 201 | 254 | 16082.9333 | 0.048345 | 0.046054 | 0.00076352 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03920 | CONDUCTOR - REPAIR/REHANG | Recloser H131 Trip. Reverse E/F. Lines down past ABS H139. Lines down at Poles P03920 & P03925. Isolation at ABS H139 No back feeds avalable. Materials needed to be bought out to site by a third person. Materials 10 meters squirrell, 6 full tension sleeves | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.046054 | 11 | 2017 | 2016-06-17 | C | 254 | 0.046054 | 0.00076352
1 | 11895243 | 2016-06-18 06:58 | 2016-06-18 08:20 | 82 | 42 | 3303 | 0.0099286 | 0.009549 | 0.00012625 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7600 | FUSE - ELEMENT/LINK (HV) | 2 X 15 Amp | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.009549 | 11 | 2017 | 2016-06-18 | C | 42 | 0.009549 | 0.00012625
1 | 11895545 | 2016-06-18 09:20 | 2016-06-18 10:06 | 46 | 35 | 1610 | 0.0048395 | 0.004523 | 0.00010521 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P44316 | JUMPER | Repair Jumper at Transformer T7/183 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.004523 | 11 | 2017 | 2016-06-18 | C | 35 | 0.004523 | 0.00010521
1 | 11896072 | 2016-06-18 08:05 | 2016-06-18 10:30 | 144 | 1 | 144.5833 | 0.00043461 | 0.000425 | 3.0059e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 10027 | FUSE - ELEMENT/LINK (HV) | 2 X 10 Amp | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.000425 | 11 | 2017 | 2016-06-18 | C | 1 | 0.000425 | 3.0059e-06
1 | 11937724 | 2016-06-19 03:40 | 2016-06-19 12:35 | 535 | 8 | 4280 | 0.012865 | 0.012793 | 2.4047e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VANDALISM | 715776 | POLE | Lines Down on Corner of Oeo Rd & Opunake Rd. Police called it in. P025637046. Trafic management required. Isolated at fuses TA139 for repairs | F4 | IHAIA RD | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.012793 | 11 | 2017 | 2016-06-19 | C | 8 | 0.012793 | 2.4047e-05
1 | 11938261 | 2016-06-19 09:58 | 2016-06-19 11:00 | 62 | 6 | 368.4167 | 0.0011074 | 0.001053 | 1.8035e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 372582 | CROSSARM - WHOLE ASSEMBLY | Bolts at Crossarm Broken at pole 372582. Isolated at fuses V18 for repairs. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.001053 | 11 | 2017 | 2016-06-19 | C | 6 | 0.001053 | 1.8035e-05
1 | 11938269 | 2016-06-19 07:40 | 2016-06-19 07:43 | 2 | 270 | 715.5 | 0.0021507 | 0 | 0.00081159 |  | 11 | Unplanned |  | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Hamilton St Sub | CIRCUIT BREAKER (HV) | HST CB 6 tripped during planned switching Napa 21027 item 3. closing ring at Sw/Gear 9394/4 tripped CB6, to be investigated. | F1 | CHAPEL ST | TAURANGA 31 | Tauranga | HAMILTON STREET SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-06-19 | C | 270 | 0 | 0.00081159
1 | 11940064 | 2016-06-19 13:24 | 2016-06-19 15:33 | 129 | 674 | 78490.8667 | 0.23593 | 0.22986 | 0.002026 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | Omokoroa Sub | UNKNOWN | OMO CB 1 tripped B & C Ph, O/C, L/O feeder sectionalised with no fault found. strong wind at time of tripping with wind blown branches evident. Feeder returned to service all service restored | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.22986 | 11 | 2017 | 2016-06-19 | C | 674 | 0.22986 | 0.002026
1 | 11944551 | 2016-06-19 16:30 | 2016-06-19 20:14 | 223 | 1761 | 317190.8833 | 0.95344 | 0.93756 | 0.0095828 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | HUMAN ELEMENT | HUMAN ELEMENT - EQUIPMENT OPERATING ERROR | 732961 | JUMPER | * Part of planned works 19199 for the Cloton Rd Sub 11kV BUS replacement. All works went to plan. * On the final planned isolation and earthing of the 11kV BUS at day end a switching error occurred. * This error is covered in Safety manager report 629852. * Downer were notified, as per usual process the personnel involved were stood down. * The error resulted in a large loss of supply to a considerable area of the Stratford township. * Damage was done at a four pole structure with a blown jumper. * Difficult repair to effect due to four pole structure, four take off's and four ABS's requiring a large isolation and earthing area to effect safe repair. Pole numbers 732961 to 732964. * Due to the complexity and feeder loading's (due to the CLO BUS works and considerable back feeding in place) it was not viable to back feed to re-instate supply in a timely manner (or if even possible) * Based on discussion with Field and NCTL it was decided to get in and replace the blown jumper and then re-instate supply. * Initial evaluation of the repair work (from the ground in failing light conditions) was estimated to take approx 30mins for the repair. However, once the network was accessed the repair was more technical and onerous than first thought. Attn Fiona Hudson (NOC): Fiona we have a few issues to resolve here please. Being that we had Downer onsite as part of the planned works, no crew requests were done for this fault aspect. Basically this aspect was over looked by us managing the incident. This will result in Downers to being unable to bill correctly. I've notified Stacey at SMC of this issue and a copy of this report for reference We should have requested a 2R Straight up due to the complexity of the fault situation and the number of fault staff required to ascertain cause, repair and reinstatement of the network in a timely manner. Downers applied three staff (Jade W, Alan R, and Bruce K) as well a two fault ute's and a bucket truck. Required considerable mileage and time. The repair was a replacement jumper, however not the usual line type as connected via a solid BUS to ABS on top of a four Pole structure, so 'may' not fall between usual 1R requirements. Last query, being that the fault and subsequent damage was the result of a switching error, this aspect may need to be discussed further in regards to billing. ASW-nctl | F4 | CLOTON RD WEST | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.93756 | 11 | 2017 | 2016-06-19 | C | 1761 | 0.93756 | 0.0095828
1 | 11947387 | 2016-06-19 21:14 | 2016-06-19 22:56 | 102 | 6 | 614.9 | 0.0018483 | 0.001794 | 1.8035e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1401 | FUSE - ELEMENT/LINK (HV) | replaced 2x5a HV Fuses @ 1401 | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.001794 | 11 | 2017 | 2016-06-19 | C | 6 | 0.001794 | 1.8035e-05
1 | 11947446 | 2016-06-19 22:25 | 2016-06-20 00:15 | 109 | 4 | 439.6 | 0.0013214 | 0.001285 | 1.2023e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | sd5-086 | FUSE - ELEMENT/LINK (HV) | replaced 2 x 6amp HT fuses | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.001285 | 11 | 2017 | 2016-06-19 | C | 4 | 0.001285 | 1.2023e-05
1 | 11947616 | 2016-06-20 08:50 | 2016-06-20 09:36 | 46 | 4 | 184 | 0.00055307 | 0.000517 | 1.2023e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 212560 | FUSE - ELEMENT/LINK (HV) | Emergency switching to repair cable holder at pole 212560. Isolation at Fuses SE4 004 - cable secured - all service restored. Materials Used: 1 x 3A H/V, O/H fuse. | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.000517 | 11 | 2017 | 2016-06-20 | C | 4 | 0.000517 | 1.2023e-05
1 | 11947806 | 2016-07-11 12:14 | 2016-07-11 12:33 | 19 | 3 | 57.4 | 0.00017249 | 0.000145 | 9.0152e-06 | NAPA ID:21061 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 021061 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC703 | NONE | To install a 400V Fuse Disconnector on TC703. Works location: Hwy 24 Tauranga Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 7.25e-05 | 5.5 | 2017 | 2016-07-11 | B | 3 | 0.000145 | 9.0152e-06
1 | 11948050 | 2016-07-11 13:50 | 2016-07-11 14:45 | 55 | 8 | 440 | 0.0013222 | 0.00125 | 2.4041e-05 | NAPA ID:21064 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 021064 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3295 | NONE | To install a 400V Fuse Disconnector. Works location: Hwy 24, Tauranga Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000625 | 5.5 | 2017 | 2016-07-11 | B | 8 | 0.00125 | 2.4041e-05
1 | 11948282 | 2016-07-11 14:15 | 2016-07-11 14:48 | 33 | 8 | 264 | 0.00079334 | 0.000721 | 2.4041e-05 | NAPA ID:20928 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020928 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5537 | NONE | To install a 400V Fuse Disconnector. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0003605 | 5.5 | 2017 | 2016-07-11 | B | 8 | 0.000721 | 2.4041e-05
1 | 11948635 | 2016-07-13 09:54 | 2016-07-13 11:44 | 110 | 6 | 660 | 0.0019833 | 0.001929 | 1.803e-05 | NAPA ID:21065 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 021065 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transforemr TC3165 | NONE | To replace the 11kV Fuse arm and install a 400V Fuse Disconnector on TC3165. Works location: Taihoa North Rd, Matamata. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0009645 | 5.5 | 2017 | 2016-07-13 | B | 6 | 0.001929 | 1.803e-05
1 | 11948678 | 2016-07-13 09:45 | 2016-07-13 10:45 | 60 | 1 | 60 | 0.0001803 | 0.000171 | 3.005e-06 | NAPA ID:20929 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020929 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1496 | NONE | To install a 400V Fuse Disconnector. Works location: Taihoa North Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 8.55e-05 | 5.5 | 2017 | 2016-07-13 | B | 1 | 0.000171 | 3.005e-06
1 | 11948716 | 2016-07-25 11:00 | 2016-07-25 11:33 | 33 | 7 | 231 | 0.00069407 | 0.00063 | 2.1032e-05 | NAPA ID:20931 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020931 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5539 | NONE | To install a 400V Fuse Disconnector. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000315 | 5.5 | 2017 | 2016-07-25 | B | 7 | 0.00063 | 2.1032e-05
1 | 11948883 | 2016-07-15 10:00 | 2016-07-15 10:34 | 34 | 107 | 3638 | 0.010932 | 0.009967 | 0.00032153 | NAPA ID:21430 TP_HINUERA GXP > PUTARURU SUB > BENT ST | 11 | Planned | 021430 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3761 | NONE | Put Switch Unit IC3003 Into Earth Position & Replace Test Cover. Works location: Buckland St, Putaruru. WO 30026378 | F2 | BENT ST | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.0049835 | 5.5 | 2017 | 2016-07-15 | B | 107 | 0.009967 | 0.00032153
1 | 11951638 | 2016-07-13 13:40 | 2016-07-13 14:45 | 65 | 7 | 455 | 0.0013673 | 0.001304 | 2.1035e-05 | NAPA ID:21066 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 021066 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1956 | NONE | To replace the 400V Pin arm & Install a 400V Fuse Disconnector on TC1956. Works location: Taihoa North Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000652 | 5.5 | 2017 | 2016-07-13 | B | 7 | 0.001304 | 2.1035e-05
1 | 11951663 | 2016-07-13 13:45 | 2016-07-13 14:30 | 45 | 7 | 315 | 0.00094658 | 0.000883 | 2.1035e-05 | NAPA ID:20932 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020932 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2282 | NONE | To install a 400V Fuse Disconnector. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0004415 | 5.5 | 2017 | 2016-07-13 | B | 7 | 0.000883 | 2.1035e-05
1 | 11951672 | 2016-07-11 09:38 | 2016-07-11 12:37 | 179 | 99 | 17721 | 0.053253 | 0.05236 | 0.0002975 | NAPA ID:19436 TP_OPUNAKE GXP > TASMAN SUB > OPUNAKE | 11 | Planned | 019436 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TA207 | NONE | Install cross arms sleeve through remove ABS TA207. Works location: Gisborne Tce. WO 30025736 | F3 | OPUNAKE | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.02618 | 5.5 | 2017 | 2016-07-11 | B | 99 | 0.05236 | 0.0002975
1 | 11956900 | 2016-07-12 10:00 | 2016-07-12 11:31 | 91 | 3 | 273 | 0.00082038 | 0.000793 | 9.0151e-06 | NAPA ID:21423 TP_HAWERA GXP > LIVINGSTONE SUB > KAKARAMEA | 11 | Planned | 021423 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses LI706 | NONE | Replace spalling pole and rotten Xarm. Works location: Clifford Rd, Hurleyville. WO 30007226 | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.0003965 | 5.5 | 2017 | 2016-07-12 | B | 3 | 0.000793 | 9.0151e-06
1 | 11957169 | 2016-07-12 08:49 | 2016-07-12 14:16 | 327 | 33 | 10791 | 0.032427 | 0.032129 | 9.9166e-05 | NAPA ID:21509 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 021509 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 589 | NONE | We are installing a new 50kva Transformer 2310N to take some load off transformer 589. Works location: Lepper Rd. WO 30027626 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.016064 | 5.5 | 2017 | 2016-07-12 | B | 33 | 0.032129 | 9.9166e-05
1 | 11957429 | 2016-07-13 09:00 | 2016-07-13 12:45 | 225 | 36 | 5186.4667 | 0.015585 | 0.01526 | 0.00010818 | NAPA ID:21424 TP_HAWERA GXP > KAPUNI SUB > MATAPU | 11 | Planned | 021424 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 720338 | NONE | Replace rotten Hv Xarm at pole 720338. Note Powerco WO;10160665. Works location: Inuawai Rd, Hawera. NOTE: Fuses KA703 found to be damaged. After planned switching finished, further isolation carried out to ABS 6701 and 6684. (OMS 12361498 generated and linked). Required 3 HT Fuses and holder. | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.00763 | 5.5 | 2017 | 2016-07-13 | B | 36 | 0.01526 | 0.00010818
1 | 11957984 | 2016-07-18 13:00 | 2016-07-18 15:00 | 120 | 64 | 7680 | 0.023077 | 0.0225 | 0.00019231 | NAPA ID:21570 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 10 | 11 | Planned | 021570 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 417 | NONE | DNO 160104, Magnefix 362 has leaking cable termination. Shut is to clean and repair termination and grease fill. Works location: Coronation Ave. WO 30018960 | F3 | BROOKLANDS 10 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.01125 | 5.5 | 2017 | 2016-07-18 | B | 64 | 0.0225 | 0.00019231
1 | 11958624 | 2016-06-20 17:45 | 2016-06-20 23:06 | 320 | 6 | 1925 | 0.0057862 | 0.005732 | 1.8035e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | tc1487 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced fuse which blew. Isolated transformer & replaced. Own SIS & AP | F1/F4 | MCCABE ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.005732 | 11 | 2017 | 2016-06-20 | C | 6 | 0.005732 | 1.8035e-05
1 | 11961821 | 2016-06-21 06:14 | 2016-06-21 07:30 | 76 | 2 | 152.0333 | 0.00045698 | 0.000438 | 6.0115e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P33111 | FUSE - ELEMENT/LINK (HV) | Reload at O68. 2 x 15A due to Bird Strike. | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000438 | 11 | 2017 | 2016-06-21 | C | 2 | 0.000438 | 6.0115e-06
1 | 11962028 | 2016-06-27 09:30 | 2016-06-27 11:07 | 97 | 48 | 4656 | 0.013994 | 0.01356 | 0.00014426 | NAPA ID:21775 TP_WAIHOU GXP > TAHUNA SUB > HOE-O-TAINUI | 11 | Planned | 021775 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | K1849 | NONE | Replace badly rotten X-Arms at poles K1849, k1884, K12889. Works location: Tainui Rd, Tahuna. WO 30007220 | F4 | HOE-O-TAINUI | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.00678 | 5.5 | 2017 | 2016-06-27 | B | 48 | 0.01356 | 0.00014426
1 | 11962086 | 2016-06-20 19:50 | 2016-06-20 20:58 | 68 | 5 | 340 | 0.001022 | 0.000976 | 1.5029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 386145 | FUSE - ELEMENT/LINK (HV) | Reload at SE4-062 2 x 6A Unknown Cause | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.000976 | 11 | 2017 | 2016-06-20 | C | 5 | 0.000976 | 1.5029e-05
1 | 11962302 | 2016-07-10 07:47 | 2016-07-10 13:21 | 333 | 1 | 333.6 | 0.0010025 | 0.000993 | 3.005e-06 | NAPA ID:21268 TP_MT MAUNGANUI 33 GXP > TRITON SUB > FERT WORKS | 11 | Planned | 021268 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB 6 | NONE | Isolate Cable between TRI_T6 and OCB_2 Fert Works. Receive Access permit on CB's/Cable, remove cable from rear of CB's. Return Access Permit and Recive Test Permit On cable. Carry out testing of Cable. return Test permit. Take out access permit on Cable between TRI_T6 and OCB_2 Fert Works and return cables to rear of CB's . return Access permit and restore feed. WORKS LOCATION: Fert Works, Mt Maunganui. WO 30028939 | F1 | FERT WORKS | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.0004965 | 5.5 | 2017 | 2016-07-10 | B | 1 | 0.000993 | 3.005e-06
1 | 11962913 | 2016-06-21 09:25 | 2016-06-21 10:25 | 60 | 17 | 1020 | 0.0030659 | 0.002912 | 5.1098e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 820009 | CONDUCTOR - REPAIR/REHANG | Repair Floating 11kV Conductor. Outage required from Fuses 7198 with a conductor rebound at Pole 820009. 1 Binder required, relivened OK. | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.002912 | 11 | 2017 | 2016-06-21 | C | 17 | 0.002912 | 5.1098e-05
1 | 11963306 | 2016-06-21 09:19 | 2016-06-21 09:24 | 5 | 23 | 115 | 0.00034567 | 0.000138 | 6.9133e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B0055 | NONE | Replace pin in Kidney strain insulator at Pole B0055 before planned outage 18975. The pin was about to fall out, noticed by workers onsite. Pin Replaced de energised using live line Techniques | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.000138 | 11 | 2017 | 2016-06-21 | C | 23 | 0.000138 | 6.9133e-05
1 | 11964020 | 2016-06-21 13:35 | 2016-06-21 14:00 | 25 | 4 | 100 | 0.00030058 | 0.000264 | 1.2023e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715542 | FUSE - ELEMENT/LINK (HV) | Fence standard has been thrown up into pole 715542 and has charred crossarm is in 11kV. Line isolated at Fuses TA922. Standard removed by Hotstick. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.000264 | 11 | 2017 | 2016-06-21 | C | 4 | 0.000264 | 1.2023e-05
1 | 11964252 | 2016-06-21 13:00 | 2016-06-21 14:30 | 90 | 11 | 990 | 0.0029757 | 0.002876 | 3.3064e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 739335 | FUSE - ELEMENT/LINK (HV) | Please check for safety, crossed power lines, touching. FM has confirmed that this job has caused other customers to have no power on this road. Fuses 5453 Blown when F/M arrived on site. Isolated line at fuses 5453 untangled lines, line relivened. Lines tangled due to tree falling through them. NDR 43214. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.002876 | 11 | 2017 | 2016-06-21 | C | 11 | 0.002876 | 3.3064e-05
1 | 11976087 | 2016-07-12 00:16 | 2016-07-13 00:19 | 1443 | 1365 | 88188.7667 | 0.26501 | 0.25271 | 0.010268 | NAPA ID:21026 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | 021026 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 9405 | NONE | Pre-switching by Downer to shift load from CB5 to KPT2 back to TEMP42. Sync on HV Gen back to TEMP52. AP -Change HV poles and associated hardware between TEMP42, 44 & 52. Restore HV Gen to Network. Restore KPT2 to CB5. Works location: Seaforth Rd, Waihi. WO 30017825 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.12635 | 5.5 | 2017 | 2016-07-12 | B | 1365 | 0.25271 | 0.010268
1 | 11976354 | 2016-06-21 16:38 | 2016-06-21 18:51 | 132 | 1 | 132.95 | 0.00039962 | 0.00039 | 3.0057e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4709 | FUSE - ELEMENT/LINK (HV) | FM arrived at customers wool shed and there was full power upon arrival. He called the customer who advised it was his pump that's not working at another address a few kms up the road. Replaced 2 x 3 AMP Fuses. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.00039 | 6.6 | 2017 | 2016-06-21 | C | 1 | 0.00039 | 3.0057e-06
1 | 11977618 | 2016-06-22 05:58 | 2016-06-22 13:00 | 422 | 39 | 16467.75 | 0.049498 | 0.049146 | 0.00011722 |  | 6.6 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 4135 | FUSE - ELEMENT/LINK (HV) | No Power Transformer Y317W. Faultman found blown fuses at Fuses 4135, suspect branches as very windy. 2 X 10 amp fuses replaced. | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.049146 | 6.6 | 2017 | 2016-06-22 | C | 39 | 0.049146 | 0.00011722
1 | 11980802 | 2016-07-12 09:09 | 2016-07-12 15:41 | 392 | 26 | 10192 | 0.030627 | 0.030392 | 7.8131e-05 | NAPA ID:19375 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 019375 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 321053 | NONE | Replace poles, hardware and conductors between TEMP64 & TEMP65. Works location: Poripori Rd. WO 30017844 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.015196 | 5.5 | 2017 | 2016-07-12 | B | 26 | 0.030392 | 7.8131e-05
1 | 11980828 | 2016-06-22 09:27 | 2016-06-22 11:18 | 110 | 1 | 110.7167 | 0.00033279 | 0.000323 | 3.0057e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 706071 | UNKNOWN | 9.29am called hub to advise 999 unable to see from ground, 33kv feeder so wants to check up on the lines with a bucket truck, FM requesting 2R for this work. inspected 33kv and 11kv arms, nothing obvious up there | F3 | PITT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.000323 | 11 | 2017 | 2016-06-22 | C | 1 | 0.000323 | 3.0057e-06
1 | 11981017 | 2016-07-19 09:05 | 2016-07-19 15:06 | 361 | 18 | 6498 | 0.019525 | 0.019363 | 5.4087e-05 | NAPA ID:19377 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 019377 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-002 | NONE | Replace poles, hardware and conductors between SE3-002 & TEMP65. Works location: Poripori Rd. WO 30017844 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0096815 | 5.5 | 2017 | 2016-07-19 | B | 18 | 0.019363 | 5.4087e-05
1 | 11981131 | 2016-06-22 12:40 | 2016-06-22 13:34 | 54 | 8 | 432 | 0.0012985 | 0.001226 | 2.4046e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208458 | JUMPER | Earth Screen had loose connection. Isolated at Fuses SB1-037 and repaired. | F4 | WHARAWHARA ROAD | TAURANGA 31 | Tauranga | KATIKATI SUB | Eastern Electricity | POWERCO | 0.001226 | 11 | 2017 | 2016-06-22 | C | 8 | 0.001226 | 2.4046e-05
1 | 11981351 | 2016-07-17 09:00 | 2016-07-17 13:06 | 246 | 37 | 9102 | 0.02735 | 0.027016 | 0.00011118 | NAPA ID:21770 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | 021770 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC592 | NONE | Replace DNO 160514 ABS IC592 & replace 32 x HV x-arms. Works location: Morrinsville Walton Rd, Morrinsville. WO 30027354 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.013508 | 5.5 | 2017 | 2016-07-17 | B | 37 | 0.027016 | 0.00011118
1 | 11982091 | 2016-07-12 10:31 | 2016-07-12 11:00 | 29 | 19 | 556.0667 | 0.001671 | 0.001499 | 5.7096e-05 | NAPA ID:21743 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 021743 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T7/294 | NONE | Complete works on TX pole 7/294 for audit. Note* Have spoke with Mike Reid in regards to this outage, has been looked over and looks ok for July. Works location; Mangarama Rd. WO 10151698 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.0007495 | 5.5 | 2017 | 2016-07-12 | B | 19 | 0.001499 | 5.7096e-05
1 | 11982099 | 2016-07-19 08:30 | 2016-07-19 10:19 | 109 | 90 | 9810 | 0.029477 | 0.028666 | 0.00027043 | NAPA ID:21663 TP_CARRINGTON GXP > CITY SUB > CITY 4 | 11 | Planned | 021663 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Magnefix 380 | NONE | DNO 160113, Magnefix 380 has leaking cable termination. Shut is to clean and repair termination and grease fill. Works location: Elliot St. WO 30019575 | F3 | CITY 4 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.014333 | 5.5 | 2017 | 2016-07-19 | B | 90 | 0.028666 | 0.00027043
1 | 11982114 | 2016-07-19 08:48 | 2016-07-19 14:17 | 329 | 16 | 5264 | 0.015817 | 0.015673 | 4.8077e-05 | NAPA ID:19211 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 019211 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1333 | NONE | To Rewire lines Beyond Sw 1333. Works location: Livingstone Rd. WO 30017838 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0078365 | 5.5 | 2017 | 2016-07-19 | B | 16 | 0.015673 | 4.8077e-05
1 | 11982229 | 2016-07-19 10:08 | 2016-07-19 12:27 | 139 | 58 | 8062 | 0.024225 | 0.023702 | 0.00017428 | NAPA ID:21425 TP_STRATFORD GXP > STRATHMORE | 11 | Planned | 021425 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 708538 | NONE | Replace pole 708538 Tahora rd (old wooden pole). Works location: Tahora Rd, Strathmore. WO 30026874 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.011851 | 5.5 | 2017 | 2016-07-19 | B | 58 | 0.023702 | 0.00017428
1 | 11982242 | 2016-07-18 10:00 | 2016-07-18 10:50 | 50 | 7 | 350 | 0.0010517 | 0.000988 | 2.1034e-05 | NAPA ID:20934 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020934 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1934 | NONE | To install a 400V Fuse Disconnector. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000494 | 5.5 | 2017 | 2016-07-18 | B | 7 | 0.000988 | 2.1034e-05
1 | 11982295 | 2016-07-13 09:24 | 2016-07-13 14:30 | 306 | 51 | 15606 | 0.046896 | 0.046436 | 0.00015326 | NAPA ID:21700 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 021700 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC487 | NONE | Install new recloser at pole O437. Remove ABS IC487. Replace cross ams at pole P438. Works location: Kaihere Rd, Ngatea. WO 30011923. Note Outage went over by half an hour as the crew had issues with the strain arm on the pole. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.023218 | 5.5 | 2017 | 2016-07-13 | B | 51 | 0.046436 | 0.00015326
1 | 11982338 | 2016-07-18 11:30 | 2016-07-18 12:20 | 50 | 2 | 100 | 0.00030049 | 0.000282 | 6.0097e-06 | NAPA ID:20935 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020935 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1924 | NONE | To install a 400V Fuse Disconnector. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000141 | 5.5 | 2017 | 2016-07-18 | B | 2 | 0.000282 | 6.0097e-06
1 | 11982341 | 2016-07-18 14:00 | 2016-07-18 15:03 | 63 | 7 | 441 | 0.0013251 | 0.001262 | 2.1034e-05 | NAPA ID:20936 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020936 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5359 | NONE | To install a 400V Fuse Disconnector. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000631 | 5.5 | 2017 | 2016-07-18 | B | 7 | 0.001262 | 2.1034e-05
1 | 11982351 | 2016-07-20 10:00 | 2016-07-20 10:35 | 35 | 2 | 70 | 0.00021034 | 0.000192 | 6.0095e-06 | NAPA ID:20937 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020937 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP283 | NONE | To install a 400V Fuse Disconnector. Works location; Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 9.6e-05 | 5.5 | 2017 | 2016-07-20 | B | 2 | 0.000192 | 6.0095e-06
1 | 11982388 | 2016-07-07 09:14 | 2016-07-07 12:48 | 213 | 11 | 2350.8833 | 0.0070648 | 0.006965 | 3.3057e-05 | NAPA ID:21310 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 021310 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N2025 | NONE | Puriri Pole Renewals Shut 12. Work Area beyond FC2409. Work on Poles N13096, N2021, N2022, N2023, N2024, N2025, N2026, N2027, N2029, N2031, N607953, N2035, N2037. Works location; Onetai Rd, Thames. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.0034825 | 5.5 | 2017 | 2016-07-07 | B | 11 | 0.006965 | 3.3057e-05
1 | 11982393 | 2016-07-20 11:30 | 2016-07-20 12:15 | 45 | 5 | 225 | 0.00067608 | 0.000631 | 1.5024e-05 | NAPA ID:20938 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020938 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5175 | NONE | To install a 400V Fuse Disconnector. Works location: Davidson Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0003155 | 5.5 | 2017 | 2016-07-20 | B | 5 | 0.000631 | 1.5024e-05
1 | 11982417 | 2016-07-20 14:00 | 2016-07-20 15:02 | 62 | 1 | 62 | 0.0001863 | 0.000177 | 3.0047e-06 | NAPA ID:20939 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020939 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4326 | NONE | Install a 400V Fuse Disconnector. Works location: Davidson Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 8.85e-05 | 5.5 | 2017 | 2016-07-20 | B | 1 | 0.000177 | 3.0047e-06
1 | 11982438 | 2016-07-22 09:30 | 2016-07-22 11:40 | 130 | 4 | 520 | 0.0015625 | 0.001526 | 1.2019e-05 | NAPA ID:20940 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020940 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1883 | NONE | To replace the 400V Spreader Arm. Install a 400V Fuse Disconnector. To relocate the transformer. Works location: Hwy 29. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000763 | 5.5 | 2017 | 2016-07-22 | B | 4 | 0.001526 | 1.2019e-05
1 | 11982445 | 2016-07-12 08:30 | 2016-07-12 13:00 | 270 | 70 | 18900 | 0.056795 | 0.056164 | 0.00021035 | NAPA ID:18878 TP_GREYTOWN GXP > KEMPTON SUB > MOROA | 11 | Planned | 018878 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 816319 | NONE | Replace tx structure t959 and 11kv pole 816319. Works location: Fenwicks Line, Greytown. WO 30025083 | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.028082 | 5.5 | 2017 | 2016-07-12 | B | 70 | 0.056164 | 0.00021035
1 | 11982454 | 2016-07-22 14:00 | 2016-07-22 14:22 | 22 | 5 | 110 | 0.00033052 | 0.000285 | 1.5024e-05 | NAPA ID:20941 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020941 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2279 | NONE | To install a 3 phase fuse disconnector. Works location: Tauranga Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0001425 | 5.5 | 2017 | 2016-07-22 | B | 5 | 0.000285 | 1.5024e-05
1 | 11983846 | 2016-06-23 04:13 | 2016-06-23 12:27 | 493 | 240 | 33820.9667 | 0.10166 | 0.099491 | 0.00094379 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | K0482 | CONDUCTOR - REPAIR/REHANG | (TAH4 ) recloser RC27 tripped E/F, A, B C Ph O/C, L/O. Feeder sectionalised with tree through line at pole K0482. Isolation at ABS IC590 ( spur no back feed). Rest of feeder returned to service. NDR 51011. Marty advised he is leaving site | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.099491 | 11 | 2017 | 2016-06-23 | C | 240 | 0.099491 | 0.00094379
1 | 11984632 | 2016-06-23 04:25 | 2016-06-23 08:16 | 230 | 264 | 26145.4 | 0.078585 | 0.076204 | 0.0010159 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228680 | CONDUCTOR - REPAIR/REHANG | PGA CB5 tripped E/F, C Ph O/C, L/O. Report of slip at 220 Roydon Downs Rd. Isolation between Links 9987/6, ABS 9987/1 & ABS SF6 018 with back feed via ABS SF6 039. remainder of feeder returned to service. Lines down due to tree through lines at pole 228680. 18meters of 25 aluninium 7 sleeves. | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.076204 | 33 | 2017 | 2016-06-23 | C | 264 | 0.076204 | 0.0010159
1 | 11986628 | 2016-06-23 06:55 | 2016-06-23 09:20 | 145 | 5 | 725.9167 | 0.0021819 | 0.002136 | 1.5028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | D12543 | FUSE - ELEMENT/LINK (HV) | Reload. 3 x 3A. Cause Unknown | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.002136 | 11 | 2017 | 2016-06-23 | C | 5 | 0.002136 | 1.5028e-05
1 | 11987169 | 2016-06-23 07:34 | 2016-06-23 14:12 | 397 | 367 | 61819.2667 | 0.18581 | 0.1825 | 0.0011031 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - TORNADO | 764306 | CONDUCTOR - REPAIR/REHANG | O/H Line Repaired between pole 764306 & 764309. Used 1 x HV Pin. 300m Conductor. 14 x 16mm Sleeves | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.1825 | 11 | 2017 | 2016-06-23 | C | 367 | 0.1825 | 0.0011031
1 | 11988593 | 2016-06-23 09:28 | 2016-06-23 10:22 | 54 | 3 | 162 | 0.00048692 | 0.000459 | 9.017e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | M2383 | NONE | Isolated at fuses FP1495 and Earthed for tree removal from lines at Pole M2383. NDR 17991. called hub to advise 999 and emailed . | F4 | TAUMANGI RD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000459 | 11 | 2017 | 2016-06-23 | C | 3 | 0.000459 | 9.017e-06
1 | 11989318 | 2016-06-23 06:23 | 2016-06-23 09:39 | 196 | 575 | 65928.6667 | 0.19816 | 0.19298 | 0.0017283 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S12576 | JUMPER | jumper blown off at ABS 358. Isolation at ABS 2607, 9922/1, Links 9922/4, ABS IC936. Fuses FC2460 & FC2340 Open & tagged due to Imbedded Generation. | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.19298 | 11 | 2017 | 2016-06-23 | C | 575 | 0.19298 | 0.0017283
1 | 11991010 | 2016-06-23 10:14 | 2016-06-23 11:25 | 70 | 179 | 11233.7 | 0.033765 | 0.03215 | 0.00053802 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 746610 | AIR BREAK SWITCH - ABS (HV) | ABS 268 - Isolator fell off. DNO'd. | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.03215 | 11 | 2017 | 2016-06-23 | C | 179 | 0.03215 | 0.00053802
1 | 11991962 | 2016-06-23 08:30 | 2016-06-23 10:55 | 144 | 13 | 1880.45 | 0.0056521 | 0.005534 | 3.9074e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 384521 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses SB3-007. 2 x 15A & Barrels. Bird Strike (See OMS 11983710) | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.005534 | 11 | 2017 | 2016-06-23 | C | 13 | 0.005534 | 3.9074e-05
1 | 11992127 | 2016-07-01 09:01 | 2016-07-01 14:36 | 335 | 7 | 2345 | 0.0070475 | 0.006984 | 2.1037e-05 | NAPA ID:21861 TP_KINLEITH GXP > BAIRD ROAD SUB > KAURI ST | 11 | Planned | 021861 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole B12386 | NONE | Reconductor 11kV between polesB12386 - B12391. Works location: Paraonui Rd, Tokoroa. WO 30017824 | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.003492 | 5.5 | 2017 | 2016-07-01 | B | 7 | 0.006984 | 2.1037e-05
1 | 11993106 | 2016-06-23 15:01 | 2016-06-23 15:48 | 47 | 3 | 142.95 | 0.00042966 | 0.000402 | 9.017e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I13372 | CROSSARM - WHOLE ASSEMBLY | 2R - Inspect / Replace Crossarm at Pole I13372. Contractor reports that King bolt pulled away from rotten crossarm. Materials Used: Whole crossarm assembly and 3 x Binders. | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.000402 | 11 | 2017 | 2016-06-23 | C | 3 | 0.000402 | 9.017e-06
1 | 11993145 | 2016-07-15 08:50 | 2016-07-15 13:03 | 253 | 8 | 2024 | 0.006082 | 0.006009 | 2.404e-05 | NAPA ID:21829 TP_WAIHOU GXP > TAHUNA SUB > MANGATEPARU | 11 | Planned | 021829 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IC4005 | NONE | Replace DNO ABS IC4005 under LLP and AP. Works location: Tauhei Rd, Tauhei. WO 30025210 | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.0030045 | 5.5 | 2017 | 2016-07-15 | B | 8 | 0.006009 | 2.404e-05
1 | 11993275 | 2016-06-23 14:25 | 2016-06-23 15:42 | 76 | 372 | 6447.4333 | 0.019379 | 0.016024 | 0.0011181 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 754764 | INSULATOR | Have advised Control of sparking pole at 250 ngatimaru road. Insulator Replaced at Pole 754764 - This could be a 2R ***NOTE: Dianne from the HUB has advised that Brent moratti also attended this fault and would like that recorded in the notes please. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.016024 | 11 | 2017 | 2016-06-23 | C | 372 | 0.016024 | 0.0011181
1 | 11994128 | 2016-06-23 16:37 | 2016-06-23 17:02 | 24 | 199 | 4822.4333 | 0.014495 | 0.0127 | 0.00059813 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 750300 | CONDUCTOR - REPAIR/REHANG | Tree fell onto lines while public felling trees. Isolated at ABS's 329 and 317 - Tree cleared using hot sticks. NDR 100179. | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.0127 | 11 | 2017 | 2016-06-23 | C | 199 | 0.0127 | 0.00059813
1 | 11994558 | 2016-06-23 17:17 | 2016-06-23 20:25 | 187 | 427 | 16712.3333 | 0.050232 | 0.046381 | 0.0012834 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | KO702 | CONDUCTOR - REPAIR/REHANG | 172 Quine Road, lines down. Reported by fire comms F2102275 ETA required. Materials Used: 8 mtrs Conductor 2 x sleeves, 1 11kV Pin and Insulator. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.046381 | 11 | 2017 | 2016-06-23 | C | 427 | 0.046381 | 0.0012834
1 | 11997418 | 2016-06-23 20:31 | 2016-06-23 23:11 | 159 | 1 | 159.7333 | 0.00048011 | 0.000471 | 3.0056e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1216 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses. at FP1216. Customer allocated to wrong Transformer Should be TP2392 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000471 | 11 | 2017 | 2016-06-23 | C | 1 | 0.000471 | 3.0056e-06
1 | 11997879 | 2016-06-24 07:03 | 2016-06-24 12:00 | 296 | 2 | 593.6333 | 0.0017842 | 0.001766 | 6.0112e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P30520 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 8.50am onsite - hub oms down so putting FM onsite - 1R - FM Completed. 2R - Les to replace Transformer T3/165. | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.001766 | 11 | 2017 | 2016-06-24 | C | 2 | 0.001766 | 6.0112e-06
1 | 11998007 | 2016-06-24 08:19 | 2016-06-24 09:18 | 59 | 629 | 36951.8333 | 0.11106 | 0.10539 | 0.0018905 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | XT30 | UNKNOWN | Pongaroa CB XT30 Tripped on E/F, Ph A Fault, Ph C Fault, & Ground Fault. Robin Smith advises that Northpower may be onsite doing sub upgrade work. Robin has confirmed the sub is clear and safe to liven. Relivened OK | S3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 0.10539 | 33 | 2017 | 2016-06-24 | C | 629 | 0.10539 | 0.0018905
1 | 11999015 | 2016-06-27 09:40 | 2016-06-27 13:00 | 200 | 4 | 800 | 0.0024044 | 0.002368 | 1.2022e-05 | NAPA ID:21903 TP_HINUERA GXP > WAHAROA SUB (T1 Bus) > MOWBRAY RD | 11 | Planned | 021903 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2503 | NONE | Upgrade Hardware at 11kV TX TC2503 structure. Works location: Hwy 27, Matamata. WO 30019182 | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.001184 | 5.5 | 2017 | 2016-06-27 | B | 4 | 0.002368 | 1.2022e-05
1 | 11999095 | 2016-06-24 10:06 | 2016-06-24 12:47 | 160 | 69 | 7125.85 | 0.021418 | 0.020795 | 0.00020739 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 266 | UNKNOWN | Recloser 266 tripped open on EF & OC pick up.Line patrolled past recloser 266 but no fault found | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.020795 | 11 | 2017 | 2016-06-24 | C | 69 | 0.020795 | 0.00020739
1 | 12000637 | 2016-06-24 17:38 | 2016-06-24 19:20 | 102 | 8 | 808.5833 | 0.0024303 | 0.002358 | 2.4045e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | MA445 | FUSE - ELEMENT/LINK (HV) | Faultman found 2 blown fuses at Fuses MA445. 2 X 10 amp HV fuses replaced. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.002358 | 11 | 2017 | 2016-06-24 | C | 8 | 0.002358 | 2.4045e-05
1 | 12000845 | 2016-06-25 10:15 | 2016-06-25 10:54 | 39 | 1 | 39 | 0.00011722 | 0.000108 | 3.0055e-06 | Referral | 11.00000000 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 777907 | JUMPER | CR - Floating wire - to be attended to in daylight. Original job OMS 12000362. Replaced 3 insulators and rebound on pole 777907. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.000108 | 11 | 2017 | 2016-06-25 | C | 1 | 0.000108 | 3.0055e-06
1 | 12000878 | 2016-06-24 21:50 | 2016-06-24 22:46 | 56 | 20 | 1120 | 0.0033663 | 0.003185 | 6.0113e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P31636 | JUMPER | Faultman found a burnt off jumper on pole P31636, line was isolated at Fuses L37 to repair the jumper. 1 X Clamp used. | F4 | OROUA DOWNS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.003185 | 11 | 2017 | 2016-06-24 | C | 20 | 0.003185 | 6.0113e-05
1 | 12002498 | 2016-06-24 23:42 | 2016-06-25 08:02 | 499 | 291 | 10671.7 | 0.032075 | 0.029451 | 0.00087464 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Faultman found a blown fuse at Fuses 1161 no reloading and closing the it tripped recloser 1087, Fuses 1161 were isolated and faultman tried to carry out a line patrol but there is a section of line that goes through a gully and it was to dangerous to carry on with the patrol, faultman will return at first light. During daylight patrol found an opossum on crossarm on pole 791812 and removed with sticks. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.029451 | 11 | 2017 | 2016-06-24 | C | 291 | 0.029451 | 0.00087464
1 | 12002561 | 2016-06-25 07:59 | 2016-06-25 16:34 | 515 | 24 | 12360 | 0.037149 | 0.036932 | 7.2134e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | TC814 | POLE | Car v Pole. Pole is broken and lines are hanging approx 2 mtrs above ground. Accident site is 3 to 4 km's up Waitawheta Rd from the Gorge end. Pole will need replacing. Isolated between ABS IC 244 & IC 291. Replaced pole & transformer & re-livened. 9:45am svs hub confirmed Nick leaving site to attend to 12002713, will return to complete job. | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.036932 | 11 | 2017 | 2016-06-25 | C | 24 | 0.036932 | 7.2134e-05
1 | 12003359 | 2016-06-25 13:46 | 2016-06-25 13:48 | 1 | 145 | 268.25 | 0.00080625 | 0 | 0.00043581 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 9148/2 | NONE | Found regulator stuck on a high tap. NOC de-energised area via reloser S6029 so regulator could be isolated & bypassed. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-06-25 | C | 145 | 0 | 0.00043581
1 | 12003741 | 2016-06-25 14:22 | 2016-06-25 17:51 | 209 | 131 | 27403.0167 | 0.082362 | 0.081181 | 0.00039373 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 772788 | CONDUCTOR - REPAIR/REHANG | Car vs Pole 772788 NDR 47302 . Materials used so far 15x 16mm sleves & 30 M 16mm Coper conductor . (Pole still to be replaced) | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.081181 | 11 | 2017 | 2016-06-25 | C | 131 | 0.081181 | 0.00039373
1 | 12004020 | 2016-06-25 15:11 | 2016-06-25 17:07 | 115 | 786 | 68378.7833 | 0.20552 | 0.19843 | 0.0023624 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 856164 | LIGHTNING ARRESTOR (HV) | CB 1 L/O on E/F. Transformer is smoking and sparking - 200 Papamoa Beach Road. Found faulty surge arrestor at pole 856164. Isolated between ABS SD5-060, SD5-054, SD5-035, SD5-118, S4536 & 9137/1. Cut away 1 faulty arrestor and relivened. | F3 | EVANS RD | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.19843 | 11 | 2017 | 2016-06-25 | C | 786 | 0.19843 | 0.0023624
1 | 12005644 | 2016-06-25 20:48 | 2016-06-25 23:08 | 140 | 201 | 28140 | 0.084577 | 0.082765 | 0.00060412 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 367069 | JUMPER | Received a number of part & no power jobs, on inspection by faultman found a blown jumper at pole 367069, suspect this happened when car vs pole incident at Fuses 090 earlier in the afternoon on OMS 12003741.This job was also done under NDR: 47302. 2 meters - 25mm copper conductor used & 2 X sleeves used. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.082765 | 11 | 2017 | 2016-06-25 | C | 201 | 0.082765 | 0.00060412
1 | 12005868 | 2016-06-25 21:48 | 2016-06-25 23:06 | 78 | 144 | 11256 | 0.033831 | 0.032532 | 0.00043281 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V0139 | JUMPER | at 21:48, Coromandel Sub, CB 3 Wyuna Bay Feeder. Faultman called to flickering power. Found a broken jumper that had burnt off at Pole V0139. Isolated Lines at ABS IC313, Sw/gear 9429/1. Permit issued & repairs carried out. All Power Restored on Completion. Dean Brett Attended. 1x Jumper & 2x Connectors Replaced. Rotted / aged equipment was the cause. | F3 | WYUNA BAY | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.032532 | 11 | 2017 | 2016-06-25 | C | 144 | 0.032532 | 0.00043281
1 | 12006688 | 2016-06-26 06:15 | 2016-06-26 08:05 | 109 | 4 | 350.9 | 0.0010546 | 0.001018 | 1.2022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 6477 | FUSE - ELEMENT/LINK (HV) | Oakura CB6. 2 x 20amp fuses at 6477 due to lightning. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.001018 | 11 | 2017 | 2016-06-26 | C | 4 | 0.001018 | 1.2022e-05
1 | 12006695 | 2016-06-26 06:20 | 2016-06-26 07:56 | 96 | 1 | 96.4 | 0.00028973 | 0.00028 | 3.0055e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7919 | FUSE - ELEMENT/LINK (HV) | 2 X 10 Amp | F3 | BELVEDERE | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.00028 | 11 | 2017 | 2016-06-26 | C | 1 | 0.00028 | 3.0055e-06
1 | 12006753 | 2016-06-26 07:47 | 2016-06-26 08:25 | 38 | 1 | 38.3833 | 0.00011536 | 0.000106 | 3.0055e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 631 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 3Amp Fuses at transformer 631 due to lightning. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.000106 | 11 | 2017 | 2016-06-26 | C | 1 | 0.000106 | 3.0055e-06
1 | 12006825 | 2016-06-26 08:05 | 2016-06-26 10:50 | 164 | 1 | 164.6 | 0.00049471 | 0.000485 | 3.0055e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 858 | FUSE - ELEMENT/LINK (HV) | 2 x 8Amp Fuses. Cause Unknown. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000485 | 11 | 2017 | 2016-06-26 | C | 1 | 0.000485 | 3.0055e-06
1 | 12006860 | 2016-06-26 08:08 | 2016-06-26 10:00 | 112 | 5 | 561.75 | 0.0016884 | 0.001643 | 1.5028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1472 | FUSE - ELEMENT/LINK (HV) | Customer reporting whole house is without power, customer advises that he heard a heard loud bang come from outside but doesn't know the exact place it had come from. 8.09am advised Dianne at svs hub. 9.45am left message Nick Hyland cellphone advising another job OMS 12008769 has come in at next transformer down TC4395 - poss needs to go to fuses FP1472? Replaced 2 x 15 Amps fuses at FP1472. | F4 | WAIHI BEACH RD | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.001643 | 11 | 2017 | 2016-06-26 | C | 5 | 0.001643 | 1.5028e-05
1 | 12006882 | 2016-06-26 10:00 | 2016-06-26 11:05 | 65 | 2 | 130 | 0.00039072 | 0.000372 | 6.011e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE7-062 | JUMPER | Found jumper broken at TE7-062. Isolated at FP891 to repair jumper. re-livened | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000372 | 11 | 2017 | 2016-06-26 | C | 2 | 0.000372 | 6.011e-06
1 | 12006939 | 2016-06-26 15:15 | 2016-06-27 21:45 | 1830 | 144 | 8159.6 | 0.024524 | 0.023225 | 0.0004328 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TP1903 | SWITCH (HV) | 26/06/16: at 15:15, Coromandel Sub, CB 3 Wyuna Bay Feeder. Found that fuses at Fuse/Sw 9429/2 had blown. Could not get Fuse/Sw to operate to gain access to fuses. Generator installed as per details below. 27/06/16: Crew attended - Isolated Switch Unit 9429 at Temp Line Break at Pole V12682 (Live Line Crew). Investigated switch unit. Found that there was an interlocking pin that was not lining up correctly. Pin adjusted and Switch Unit functioning correctly after this repair. All Power Restored on Completion. There was a brief outage to close the line break as weather became bad so could not close the line break using live line techniques. Colin Pepper Attended. Can not open fuse/Sw. Generators install at 21:45. DNO 160623 created | F3 | WYUNA BAY | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.023225 | 11 | 2017 | 2016-06-26 | C | 144 | 0.023225 | 0.0004328
1 | 12007989 | 2016-06-26 09:14 | 2016-06-26 11:38 | 144 | 235 | 19227.2667 | 0.057788 | 0.055669 | 0.00088363 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737730 | INSULATOR | CB Q11 tripped on A phase, O/C and E/F. 1 X HT Pin & Insulator at Pole 737730. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.055669 | 11 | 2017 | 2016-06-26 | C | 235 | 0.055669 | 0.00088363
1 | 12008782 | 2016-06-26 09:47 | 2016-06-26 12:25 | 157 | 1 | 157.85 | 0.00047443 | 0.000465 | 3.0055e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2495T | FUSE - ELEMENT/LINK (HV) | Replaced 2 x 2Amp Fuses. Cause: Lightning. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.000465 | 11 | 2017 | 2016-06-26 | C | 1 | 0.000465 | 3.0055e-06
1 | 12010220 | 2016-06-26 14:12 | 2016-06-26 16:03 | 110 | 1929 | 157755.8167 | 0.47414 | 0.45675 | 0.0057977 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 2862 | UNKNOWN | Stratford CB2862 tripped O/C IN (Kaponga-Cardiff Feeder). Patrolled 33kV Line after Back feed put in. Found nothing and all went back in. | S4 | CARDIFF NORTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.45675 | 33 | 2017 | 2016-06-26 | C | 1929 | 0.45675 | 0.0057977
1 | 12012366 | 2016-06-26 16:38 | 2016-06-27 01:54 | 556 | 43 | 23908 | 0.071857 | 0.071468 | 0.00012924 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | W12480 | POLE | Car vs pole. Isolated at ABS 1202. NDR 31026. Materials, 1x11m pole, 2 HV crossarms, 6xHV insulators. | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.071468 | 11 | 2017 | 2016-06-26 | C | 43 | 0.071468 | 0.00012924
1 | 12012529 | 2016-06-26 17:28 | 2016-06-26 21:09 | 221 | 482 | 48193.3167 | 0.14485 | 0.1405 | 0.0025938 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | H1513 | CONDUCTOR - REPAIR/REHANG | CB 3 L/O on E/F & O/C. Branch removed form lines at pole by hot stick. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.1405 | 11 | 2017 | 2016-06-26 | C | 482 | 0.1405 | 0.0025938
1 | 12013854 | 2016-06-26 22:34 | 2016-06-27 04:40 | 366 | 71 | 10710 | 0.032189 | 0.031549 | 0.00021339 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H3418 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer TC2293 Faulty. Needs to be replaced. No truck access to site. Transformer needed to be hand winched up the pole. Isolation of the O/Head line needed to be done. Isolation at ABS 2575 & 746. Back fed from WAH CB 3 via ABS IC1275. 3 phase 30kVA transformer used. | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.031549 | 11 | 2017 | 2016-06-26 | C | 71 | 0.031549 | 0.00021339
1 | 12013896 | 2016-06-26 22:54 | 2016-06-27 15:22 | 988 | 273 | 237805.4833 | 0.71474 | 0.71227 | 0.00082051 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 709108 | POLE | Large tree down over road and lines several poles down (police advised ). ( STM 7131 ) sectionaliser 12085 tripped E/F, A & B Ph O/C, returned to service. L/O. Trees through line at pole 709111. Isolation at ABS 5619 ( no back feeds ) sectionaliser 12085 returned to service, remainder of feeder off until repairs completed next day. All repairs completed all service restored. Materials 6 x H/V arms, 9 x H/V insulators, 1 x pole, 2 x spans conductor all phases, NDR No N100181 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.71227 | 11 | 2017 | 2016-06-26 | C | 273 | 0.71227 | 0.00082051
1 | 12014432 | 2016-06-26 23:56 | 2016-06-27 01:35 | 99 | 587 | 49120.3833 | 0.14763 | 0.14234 | 0.0017643 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | V13613 | UNKNOWN | Recloser RP15 Trip B O/C. Line Patrolled 7 sectionalised No Fault found. | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.14234 | 11 | 2017 | 2016-06-26 | C | 587 | 0.14234 | 0.0017643
1 | 12016723 | 2016-06-27 08:46 | 2016-06-27 09:50 | 64 | 3 | 193.3 | 0.00058096 | 0.000553 | 9.0165e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 757313 | FUSE - ELEMENT/LINK (HV) | Reload at fuses 8429. 2 x 8A. Cause - Lightning | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.000553 | 11 | 2017 | 2016-06-27 | C | 3 | 0.000553 | 9.0165e-06
1 | 12016883 | 2016-06-27 10:21 | 2016-06-27 11:40 | 79 | 24 | 1918 | 0.0057646 | 0.005548 | 7.2132e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844080 | CROSSARM - WHOLE ASSEMBLY | Replace Crossarm & 3 X HT Insulators at Pole 844080 | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.005548 | 11 | 2017 | 2016-06-27 | C | 24 | 0.005548 | 7.2132e-05
1 | 12016890 | 2016-07-14 09:25 | 2016-07-14 14:40 | 315 | 6 | 1890 | 0.0056794 | 0.005625 | 1.803e-05 | NAPA ID:21322 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11.00000000 | Planned | 021322 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP1803 | NONE | Puriri Pole Renewals Shut 11 Work Area beyond FP1803. Work on Poles N1930, N1941, N13091, N13092, N1931 to N1933, N1932, N1933, N1934, N1936, N1937, N1938, N1939, N1940, N1942, N1944, N1946, N1947, N2702. Works location: Elliot Rd, Thames. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.0028125 | 5.5 | 2017 | 2016-07-14 | B | 6 | 0.005625 | 1.803e-05
1 | 12017117 | 2016-07-19 08:53 | 2016-07-19 14:57 | 364 | 21 | 7644 | 0.022969 | 0.022779 | 6.3101e-05 | NAPA ID:21315 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 021315 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC4044 | NONE | Puriri Pole Renewals Shut 15a Work Area beyond FC4044. Work on Poles N2302, N2303, N2304, N2305, N13057, N13058, N2307, N2308, N2309, N2311, N2313, N2315, N2316, N2317, N2319, N13061, N2321, N2323, N2324, N2325, N2326, N2327, N2328, N2329, N2330. Works location: Factory Rd North, Thames. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.01139 | 5.5 | 2017 | 2016-07-19 | B | 21 | 0.022779 | 6.3101e-05
1 | 12017421 | 2016-06-27 07:12 | 2016-06-27 09:36 | 143 | 2 | 287.2667 | 0.00086338 | 0.000845 | 6.011e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208149 | FUSE - ELEMENT/LINK (HV) | reload at TC1/035. 3 x 3A. Caused by lv Line Clash | F4 | KATIKATI | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.000845 | 11 | 2017 | 2016-06-27 | C | 2 | 0.000845 | 6.011e-06
1 | 12018094 | 2016-07-21 09:11 | 2016-07-21 13:35 | 264 | 88 | 23270.1333 | 0.069921 | 0.069127 | 0.00026442 | NAPA ID:20774 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 020774 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T4/158 | NONE | Remove 2 pole Trani structure install 11m Pole & new Trani T4/158. Works location: Taonui Rd, Feilding. WO 10162791 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.034563 | 5.5 | 2017 | 2016-07-21 | B | 88 | 0.069127 | 0.00026442
1 | 12018136 | 2016-07-21 09:30 | 2016-07-21 15:14 | 344 | 1 | 344 | 0.0010336 | 0.001024 | 3.0047e-06 | NAPA ID:19402 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 019402 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 217743 | NONE | Replace poles, hardware and conductors between TEMP65 & TEMP66. Works location: Poripori Rd. WO 30017844 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000512 | 5.5 | 2017 | 2016-07-21 | B | 1 | 0.001024 | 3.0047e-06
1 | 12021380 | 2016-06-27 12:27 | 2016-06-27 14:30 | 122 | 341 | 23939.45 | 0.07195 | 0.068875 | 0.0010249 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 380527 | LIGHTNING ARRESTOR (HV) | at 12:27, Papamoa Sub, CB 8 Reid Rd Feeder, Recloser RP09, Tripped, E/F, O/C, L/O. Faultmen dispatched and investigation began. Feeder sectionalised. Backfed supplied from ATU 6: Opened ABS 9876/1, Closed Sectionaliser 9954/2. Found blown lightning arrestor between Open Point Recloser 9462/2 & associated links 9462/4. Left Recloser 9462/2 Open & Open & Tagged Links 9462/4 to isolate fault. DNO'd lightning arrestor as faultman believed it could be fixed on a fine day using live line techniques. DNO 160624. No Materials Used. Haden Beddgood & Dave Ngatai Attended. All Power Restored on Completion. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.068875 | 11 | 2017 | 2016-06-27 | C | 341 | 0.068875 | 0.0010249
1 | 12021984 | 2016-06-27 13:08 | 2016-06-27 19:14 | 366 | 72 | 26352 | 0.079201 | 0.078551 | 0.0002164 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 771429 | POLE | Have advised control lines down at Intersection of State Highway 3 and Kohi Street, Waverly. Have advised police of 30-40mins. P025728943. Confirmed car v pole. 2r to replace pole 771429 . NDR Number N200041 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.078551 | 11 | 2017 | 2016-06-27 | C | 72 | 0.078551 | 0.0002164
1 | 12023586 | 2016-06-27 13:45 | 2016-06-27 14:02 | 17 | 4 | 68 | 0.00020437 | 0.000168 | 1.2022e-05 | Referral | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | D12771 | CROSSARM - ARM ONLY | 2R required to replace kicker arm at Transformer TC4-182 pole#213310. This will be done on Thursday. Replace 1 x crossarm | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000168 | 11 | 2017 | 2016-06-27 | C | 4 | 0.000168 | 1.2022e-05
1 | 12023746 | 2016-06-27 15:01 | 2016-06-27 18:06 | 185 | 2 | 370 | 0.001112 | 0.001094 | 6.011e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 220657 | POLE | at 15:01, Papamoa Sub, CB 3 Black Stump Feeder. Call came in of 11kV Pole Down at Pole 220657. Faultman dispatched. Isolated lines at Fuses SD6-007. Permit issued and repairs carried out. All Power Restored on completion. 1x Pole, 1x Crossarm whole assembly & 1x HV Fuse & Carrier. | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.001094 | 11 | 2017 | 2016-06-27 | C | 2 | 0.001094 | 6.011e-06
1 | 12024174 | 2016-06-27 19:51 | 2016-06-28 00:50 | 299 | 4 | 1196 | 0.0035946 | 0.003558 | 1.2022e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | te5-008 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Found transformer TE5-008 faulty. Replaced transformer & 2 DDO fuse units. Check OMS 12024704. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.003558 | 11 | 2017 | 2016-06-27 | C | 4 | 0.003558 | 1.2022e-05
1 | 12025009 | 2016-06-27 18:01 | 2016-06-27 19:55 | 114 | 1 | 114.4167 | 0.00034388 | 0.000334 | 3.0055e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1061 | FUSE - ELEMENT/LINK (HV) | Replaced 2 x 3amp fuse at TC1061. Suspect over loaded. To be defected | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.000334 | 11 | 2017 | 2016-06-27 | C | 1 | 0.000334 | 3.0055e-06
1 | 12025396 | 2016-06-27 22:50 | 2016-06-27 23:25 | 35 | 1 | 35 | 0.00010519 | 9.6e-05 | 3.0055e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | te7-062 | JUMPER | Found burnt out jumper at transformer TE7-062. Isolated at fuses FP891, replaced jumper & re-livened. Called hub to advise 999 and emailed | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 9.6e-05 | 11 | 2017 | 2016-06-27 | C | 1 | 9.6e-05 | 3.0055e-06
1 | 12025499 | 2016-06-27 21:55 | 2016-06-28 02:12 | 256 | 31 | 7953.5667 | 0.023904 | 0.023624 | 9.317e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 726471 | CABLE - REPLACE LESS THAN 5 METRES | Check for safety - TX on fire also lines on fire. Fire comms F2104406 ETA required please - advised fire comms eta is 30 mins temporary repais made to HV cable on pole 726471 and faultman creating an amber defect for replacement of cable | F4 | PATEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.023624 | 11 | 2017 | 2016-06-27 | C | 31 | 0.023624 | 9.317e-05
1 | 12025713 | 2016-06-28 07:16 | 2016-06-28 12:51 | 334 | 51 | 17063.75 | 0.051284 | 0.050824 | 0.00015328 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 755602 | FUSE - DROP OUT - REPLACE FULL SET OF FUSES (HV) | FM cannot complete repairs until bucket truck is available. FM is to attend a close approach while waiting for the bucket truck. Emergency switching to repair fuse holders at pole 755602. Isolation at ABS 412 (spur no back feed). Fuse holders replaced - all service restored. Materials used: 1 x set fuse holders cpmplete with 3 x 2A fuses (old age). | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.050824 | 11 | 2017 | 2016-06-28 | C | 51 | 0.050824 | 0.00015328
1 | 12025883 | 2016-07-25 09:31 | 2016-07-25 14:31 | 300 | 2 | 600 | 0.0018028 | 0.001784 | 6.0092e-06 | NAPA ID:20942 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 020942 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3316 | NONE | To replace the Arms & Hardware on TC3316 Plus the 11kV Arm Between TC3316 & FC2137. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000892 | 5.5 | 2017 | 2016-07-25 | B | 2 | 0.001784 | 6.0092e-06
1 | 12025892 | 2016-07-22 08:32 | 2016-07-22 12:20 | 227 | 11 | 2503.7833 | 0.0075232 | 0.007424 | 3.3052e-05 | NAPA ID:21429 TP_MASTERTON GXP > TE ORE ORE SUB > TAUWERU | 11 | Planned | 021429 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T172 | NONE | Replace 11kV transformer structure T172 and LV strain pole. Works location: Abbotsford Rd, Masterton. WO 30017449 | F4 | TAUWERU | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.003712 | 5.5 | 2017 | 2016-07-22 | B | 11 | 0.007424 | 3.3052e-05
1 | 12027313 | 2016-06-28 07:23 | 2016-06-28 08:45 | 81 | 34 | 2779.5 | 0.0083536 | 0.008047 | 0.00010219 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P45243 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses B48. 2 x 15A due to bird strike. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.008047 | 11 | 2017 | 2016-06-28 | C | 34 | 0.008047 | 0.00010219
1 | 12028405 | 2016-07-14 08:46 | 2016-07-14 10:30 | 104 | 15 | 1560 | 0.0046878 | 0.004552 | 4.5075e-05 | NAPA ID:21990 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 5 | 11 | Planned | 021990 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB25 | NONE | We are installing Temp 11kv Links 75 from CB5 to the overhead line at pole 743615. | F2 | DE HAVILAND NORTH | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.002276 | 5.5 | 2017 | 2016-07-14 | B | 15 | 0.004552 | 4.5075e-05
1 | 12028552 | 2016-07-12 09:13 | 2016-07-12 12:06 | 173 | 127 | 22019.6833 | 0.06617 | 0.065025 | 0.00038164 | NAPA ID:21987 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | 021987 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 772788 | NONE | Replace 11kv pole 772788 damaged by vehicle. Works location: Karahaki Rd, Waverley. WO 30007436 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.032512 | 5.5 | 2017 | 2016-07-12 | B | 127 | 0.065025 | 0.00038164
1 | 12028648 | 2016-07-14 12:00 | 2016-07-14 12:50 | 50 | 7 | 350 | 0.0010517 | 0.000988 | 2.1035e-05 | NAPA ID:21992 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 7 | 11 | Planned | 021992 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB27 | NONE | Disconnect 11kV cable from OH lines on CB7 Bell Block at pole 743616 for Bell Block switchboard project . | F3 | MANGATI RD | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000494 | 5.5 | 2017 | 2016-07-14 | B | 7 | 0.000988 | 2.1035e-05
1 | 12029064 | 2016-07-19 10:11 | 2016-07-19 14:30 | 259 | 7 | 1813 | 0.0054477 | 0.005384 | 2.1034e-05 | NAPA ID:22012 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 6.6 | Planned | 022012 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 579 | NONE | Replace rotten 6.6kv cross arm and all hardware. Works location: Hwy 3, Marton. WO 30029847 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.002692 | 3.3 | 2017 | 2016-07-19 | B | 7 | 0.005384 | 2.1034e-05
1 | 12029281 | 2016-07-15 09:34 | 2016-07-15 13:50 | 255 | 139 | 35563.15 | 0.10687 | 0.10561 | 0.00041769 | NAPA ID:21218 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 021218 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | At pole P39426, install new ABS, isolating links /4 and /6, change xarms, install new tavrida recloser/controller and comms. Liven test and commission. Remove ABS F16 and jumper through | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.052806 | 5.5 | 2017 | 2016-07-15 | B | 139 | 0.10561 | 0.00041769
1 | 12029625 | 2016-07-27 09:31 | 2016-07-27 13:14 | 223 | 8 | 1784 | 0.0053602 | 0.005288 | 2.4036e-05 | NAPA ID:21070 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 021070 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3535 | NONE | To replace the 11kV Fuse arm, 400V Pin arm & Install a 400V Fuse Disconnector on TC3535. Works location: Taihoa North Rd, Matamata. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.002644 | 5.5 | 2017 | 2016-07-27 | B | 8 | 0.005288 | 2.4036e-05
1 | 12030712 | 2016-06-28 14:02 | 2016-06-29 11:15 | 1273 | 1 | 1273.1333 | 0.0038263 | 0.003817 | 3.0054e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | UNDER INVESTIGATION | UNDER INVESTIGATION | 1794N | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | *Advise DataManager after sign off if confirmed Kaihihi Road Lower* Neil is testing LV on transformer 1794N - to determine if it needs replacing after Fuse blew at Fuses 6622. Neil confirmed 1749N needs replacing 2R Request for replacement 29/06/16 - Feeds pump shed - Farmer happy for restore tomorrow. Transformer 1794N replaced all service restored. Materials 1 x transformer | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.003817 | 11 | 2017 | 2016-06-28 | C | 1 | 0.003817 | 3.0054e-06
1 | 12032098 | 2016-06-28 13:35 | 2016-06-28 17:28 | 232 | 880 | 2890 | 0.0086857 | 0 | 0.00025546 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V1165 | JUMPER | at 13:35, Coromandel Sub, CB 5 Manaia Feeder, Tripped, A + C O/C, Auto Reclosed. Faultman dispatched for line patrol. During line patrol jobs came through from customers on Te Kouma Rd of No Powers. Faultman attended and found blown jumper on 11kV Line at Pole V1165. Isolated lines at ABS 1389. Permit Issued & Repairs carried out. Found that insulators and other jumper were also Blown. Replaced these also. All Power Restored on completion. Shane Walker Attended. Replaced 2x Insulators, 2x Jumpers & 2x Binders. Old Deteriorated. | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-06-28 | C | 880 | 0 | 0.00025546
1 | 12033098 | 2016-06-29 00:54 | 2016-06-29 01:21 | 26 | 134 | 3588.9667 | 0.010786 | 0.009578 | 0.00040272 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC3745 | FUSE - LV ELEMENT/LINK - HRC (LV) | Isolated transformer on T blade to replace LV fuse holder & 200amp fuse. Sw/gear 9655/2 opened when LV tuned off. Reclosed 9655/2 to restore power. | F3 | PAUANUI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.009578 | 11 | 2017 | 2016-06-29 | C | 134 | 0.009578 | 0.00040272
1 | 12033469 | 2016-06-29 05:43 | 2016-06-29 07:39 | 116 | 227 | 12431.5 | 0.037362 | 0.035314 | 0.00068223 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | Tower Rd Sub | CIRCUIT BREAKER (HV) | TWR CB2 tripped O/C, L/O. Feeder sectionalised with no fault found, possible bird strike | F4 | BANKS ST | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.035314 | 11 | 2017 | 2016-06-29 | C | 227 | 0.035314 | 0.00068223
1 | 12033980 | 2016-07-12 09:30 | 2016-07-12 13:45 | 255 | 6 | 1530 | 0.0045977 | 0.004543 | 1.803e-05 | NAPA ID:22071 TP_HUIRANGI GXP > BELL BLOCK SUB > BELL BLOCK 8 | 11 | Planned | 022071 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 268 | NONE | We are replacing DNO 160620 ABS 268 and as we are changing all the LV cross arms we have to off load Transformer 626. Works location: Hursthouse Rd, New Plymouth. WO 30029934 | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.0022715 | 5.5 | 2017 | 2016-07-12 | B | 6 | 0.004543 | 1.803e-05
1 | 12034016 | 2016-06-29 08:25 | 2016-06-29 16:17 | 472 | 143 | 26602 | 0.07995 | 0.07866 | 0.00056802 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | S0772 | CONDUCTOR - REPAIR/REHANG | Have advised Control report of truck hitting lines 100m from DOC - 995 Kauaeranga Valley Rd. Line down beyond Pole S0772. Temp Break made at Pole S0772 and rest of feeder restored. 76 mtrs 16mm conductor. 4 x Poly' insulators. 4 dead ends. binders. NDR# | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.07866 | 11 | 2017 | 2016-06-29 | C | 143 | 0.07866 | 0.00056802
1 | 12034711 | 2016-07-12 08:25 | 2016-07-12 15:13 | 408 | 57 | 10172 | 0.030567 | 0.030053 | 0.00017129 | NAPA ID:22000 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 022000 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole F1665 | NONE | To replace 1 pole & Hardware between poles F1665 & F1635. Works location: Te Poi Rd, Matamata. WO 30017838 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.015026 | 5.5 | 2017 | 2016-07-12 | B | 57 | 0.030053 | 0.00017129
1 | 12035028 | 2016-06-29 11:16 | 2016-06-29 15:30 | 254 | 3 | 763.35 | 0.0022942 | 0.002267 | 9.0162e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1703 | FUSE - ELEMENT/LINK (HV) | 2 x 15A HV Fuses | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002267 | 11 | 2017 | 2016-06-29 | C | 3 | 0.002267 | 9.0162e-06
1 | 12035049 | 2016-06-29 12:46 | 2016-06-29 13:15 | 29 | 54 | 1516.5333 | 0.0045578 | 0.00407 | 0.00016229 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C14433 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Emergency switching to repair floating H/V fuse at pole C14433. Isolation between ABS IC667 & ABS IC1225 with back feed via ABS IP624. Fuse repaired all service restored. Materials 1 x Fuses holder & 1 x 3A fuse. | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.00407 | 11 | 2017 | 2016-06-29 | C | 54 | 0.00407 | 0.00016229
1 | 12035076 | 2016-07-13 09:14 | 2016-07-13 14:02 | 288 | 76 | 21689.2833 | 0.065176 | 0.064491 | 0.00022838 | NAPA ID:21995 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 021995 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1041 | NONE | Replace ABS 1041 and rotten X-Arms. DNO 160610. Works location: Hwy 26, Te Aroha. WO 30029250 | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.032246 | 5.5 | 2017 | 2016-07-13 | B | 76 | 0.064491 | 0.00022838
1 | 12039337 | 2016-07-21 09:00 | 2016-07-21 13:22 | 262 | 25 | 6550 | 0.019681 | 0.019455 | 7.5119e-05 | NAPA ID:21837 TP_WAIHOU GXP > TAHUNA SUB > PATETONGA | 11 | Planned | 021837 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC548 | NONE | Replace DNO ABS IC548 in Shutdown. Works location: Hwy 27, Tahuna. WO 30025340 | F4 | PATETONGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.0097275 | 5.5 | 2017 | 2016-07-21 | B | 25 | 0.019455 | 7.5119e-05
1 | 12040680 | 2016-07-20 08:50 | 2016-07-20 14:58 | 368 | 48 | 17664 | 0.053077 | 0.052644 | 0.00014423 | NAPA ID:21257 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MOUNTAIN | 11 | Planned | 021257 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2877 | NONE | Replace transformer TC2877 & LV panel. Works location: Tui Rd, Te Aroha. WO 30026433 | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.026322 | 5.5 | 2017 | 2016-07-20 | B | 48 | 0.052644 | 0.00014423
1 | 12041600 | 2016-06-29 16:14 | 2016-06-29 18:00 | 105 | 4 | 422.9333 | 0.0012711 | 0.001235 | 1.2022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | D12741 | FUSE - ELEMENT/LINK (HV) | Replace 2 x H/V, O/H 3 A fuses at fuses FC1482 ( line clash ) | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.001235 | 11 | 2017 | 2016-06-29 | C | 4 | 0.001235 | 1.2022e-05
1 | 12042271 | 2016-06-29 19:26 | 2016-06-30 08:17 | 771 | 120 | 43498.8833 | 0.13073 | 0.12965 | 0.00090763 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P04909 | UNKNOWN | Recloser V27 and Sectionaliser V41/2 tripped on B & C phase O/C flags, line was sectionalised and patrolled, faultman had to return in morning as parts of the line goes cross country and it was to dangerous to carry on at night. Faultman found a branch across the lines at pole P04909, branch was removed with hot line sticks. | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.12965 | 11 | 2017 | 2016-06-29 | C | 120 | 0.12965 | 0.00090763
1 | 12043157 | 2016-06-29 21:54 | 2016-06-29 22:15 | 21 | 2 | 42 | 0.00012623 | 0.000108 | 6.0108e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T58 | FUSE - LV ELEMENT/LINK - HRC (LV) | Had to Tap Transformer down 2 Taps to get 230V at supply also replaced 1 X 60 Amp HRC as It had 1 X 40 amp which was to small Sran power up graded in this area the other day | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.000108 | 11 | 2017 | 2016-06-29 | C | 2 | 0.000108 | 6.0108e-06
1 | 12043660 | 2016-06-30 01:02 | 2016-06-30 05:02 | 240 | 122 | 16984.0167 | 0.051043 | 0.049943 | 0.00057703 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 837612 | CONDUCTOR - REPAIR/REHANG | Branch on Lines at Pole 837612 Remove with Hot Sticks | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.049943 | 11 | 2017 | 2016-06-30 | C | 122 | 0.049943 | 0.00057703
1 | 12044198 | 2016-06-30 07:22 | 2016-06-30 08:57 | 94 | 1089 | 28626.4167 | 0.086033 | 0.076214 | 0.0027138 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 3086 | UNKNOWN | Arahina CB 3086 tripped A phase O/C & E/F & Rata CB 3035 tripped on E/F flags, line was patrolled and no fault was found suspect bird strike as lines have magpies sitting all over them. | S4 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 0.076214 | 33 | 2017 | 2016-06-30 | C | 1089 | 0.076214 | 0.0027138
1 | 12045273 | 2016-06-30 10:42 | 2016-06-30 17:19 | 397 | 21 | 1287 | 0.0038679 | 0.003678 | 6.3112e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7029 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer T7029 found to be faulty, Faultman unable to install Operator earths safely at transformer fuses so Isolated at Fuses TA959. On Operating Fuses TA959 jumper damaged so further isolations required once transformer replaced. Isolated at ABS's 6437 and TA985 - jumper repaired. Used 1 x 15kVA 3phase transformer, 1 x sleeve, 1mtrs conductors | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.003678 | 11 | 2017 | 2016-06-30 | C | 21 | 0.003678 | 6.3112e-05
1 | 12045521 | 2016-06-30 11:57 | 2016-06-30 13:30 | 93 | 51 | 4713.8333 | 0.014167 | 0.013706 | 0.00015327 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4070 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Broken HV Fuse Holder, barrel and fuse replaced at Fuses FC4070 | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.013706 | 11 | 2017 | 2016-06-30 | C | 51 | 0.013706 | 0.00015327
1 | 12046755 | 2016-07-01 09:04 | 2016-07-01 12:36 | 212 | 262 | 55544 | 0.16693 | 0.16456 | 0.0007874 | NAPA ID:22166 TP_KOPU GXP > THAMES SUB > ROLLESTON ST | 11 | Planned | 022166 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV ABS IP600 | NONE | Drop lines for urgent tree cutting. Works location: Tararu Rd. WO 30021693 | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.082282 | 5.5 | 2017 | 2016-07-01 | B | 262 | 0.16456 | 0.0007874
1 | 12046785 | 2016-07-20 09:45 | 2016-07-20 14:10 | 265 | 42 | 11130 | 0.033443 | 0.033064 | 0.0001262 | NAPA ID:22147 TP_HUIRANGI GXP > MCKEE SUB > OTARAOA RD | 11 | Planned | 022147 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 760923 | NONE | to replace trany pole 760923 with new 11m busck pole plus upgrade trany to new 100kva plus upgrade earths etc. customer complaint pcid 7012. Works location: Otaraoa Rd. WO 30029775 | F5 | OTARAOA RD | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 0.016532 | 5.5 | 2017 | 2016-07-20 | B | 42 | 0.033064 | 0.0001262
1 | 12046845 | 2016-06-30 12:52 | 2016-06-30 13:56 | 64 | 7 | 448 | 0.0013464 | 0.001283 | 2.1037e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 726067 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer W5090 found to be faulty. Tramsformer replaced. Materials used: 1 x 50kVA 3 Phase transformer and 1 backing plate. | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.001283 | 11 | 2017 | 2016-06-30 | C | 7 | 0.001283 | 2.1037e-05
1 | 12047181 | 2016-06-30 14:30 | 2016-06-30 17:15 | 165 | 6 | 990 | 0.0029753 | 0.002921 | 1.8032e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | T9/188 | UNKNOWN | Faultman found blown fuse at Fuses V56, line was patrolled and a tree was found touching the line at transformer T9/188, line was isolated at Fuses V56 to cut away the tree.This job is a 2 R job to remove the tree. | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.002921 | 11 | 2017 | 2016-06-30 | C | 6 | 0.002921 | 1.8032e-05
1 | 12047977 | 2016-06-30 10:59 | 2016-06-30 15:15 | 256 | 1 | 256.2833 | 0.00077022 | 0.000761 | 3.0053e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2027N | FUSE - ELEMENT/LINK (HV) | FM advised that every time he tries to put a new fuse in, the fuse blows because the lines clash due to the trees. FM is to call vegetation contractors for urgent cut of trees. FM to attend another fault and return once trees are cut. Fuses blown at Transformer 2077N - used 2 x 3amp fuses. NDR # 38770 | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000761 | 11 | 2017 | 2016-06-30 | C | 1 | 0.000761 | 3.0053e-06
1 | 12048554 | 2016-07-19 09:15 | 2016-07-19 14:24 | 309 | 2 | 618 | 0.001857 | 0.001838 | 6.0096e-06 | NAPA ID:21305 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | 021305 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC843 | NONE | Replace cross arms and line hardware on spur line. Works location: Matarangi, Whitianga. WO 30002514 | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000919 | 5.5 | 2017 | 2016-07-19 | B | 2 | 0.001838 | 6.0096e-06
1 | 12050794 | 2016-06-30 12:52 | 2016-06-30 19:13 | 381 | 254 | 18051.3333 | 0.054251 | 0.05196 | 0.00076336 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | P03937 | FUSE - DROP OUT - REPLACE PARTIAL SET OF FUSES (HV) | H131 tripped on reverse earth fault. 1R - Patrol required. Job now 2 R need tree contractors to remove tree from T2/391. Feeder sectionalised & patrolled with a large tree found resting up against Transformer T2/391. The Tree had become uprooted due to excessive rain. (Positioned alongside a stream). Isolation required from fuses H137 where the Tree was cut away and area relivened. No damage - 2 HT fuses replaced at T2/391 (3A Rating). | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.05196 | 11 | 2017 | 2016-06-30 | C | 254 | 0.05196 | 0.00076336
1 | 12052072 | 2016-06-30 16:05 | 2016-06-30 17:15 | 70 | 45 | 3150 | 0.0094669 | 0.009061 | 0.00013524 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701808 | JUMPER | Blown Jumper found at fuses for Transformer 1022. Isolated at ABS 376 and Fuses 8279. Jumper Repaired and replaced all DDO's. Used 3 x fuse bases and Carriers, 3 x 3amp fuses, 1 mtrs conductor, 3 x sleeves | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.009061 | 11 | 2017 | 2016-06-30 | C | 45 | 0.009061 | 0.00013524
1 | 12052142 | 2016-07-01 13:00 | 2016-07-01 14:32 | 92 | 2 | 184 | 0.00055298 | 0.000534 | 6.0106e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - CABLE STRIKE | Fonterra Tirau Plant | CABLE - REPAIR | Had a call from Mark Barnett at Fonterra Tirau (021 633 317). A drainage contractor has nicked a HV underground cable on site. Require a fault man onsite to assess damage asap. Have advised staff to keep clear of site and meet Downers on arrival. ASW rung and advised SMC of high priority of Job (Talia). * Cable checked by fault man, damage only to the outer sheath. NO cable jointing, replacement required. * Left over night and continued on the 01/07/16.* required HV shut down of cables, done with Fonterra approval, isolated via IC937, IC906, 3777 and ABS 2632. * Only requires clean up of the affected cables and install a sheath set *(zip on, heat shrink type covers) over the affected area. Note trenches over 2 metres deep and required mechanical stabilizing to allow safe access to cables, considerable time involved to set this up. All three cables confirmed by GIS as Powerco owned. NDR number 11972.Used 1x heat shrink kit and 2x length of black shrink. | F1 | NZDG TIRAU 3 | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000534 | 11 | 2017 | 2016-07-01 | C | 2 | 0.000534 | 6.0106e-06
1 | 12053526 | 2016-07-01 09:00 | 2016-07-01 12:07 | 187 | 182 | 34034 | 0.10228 | 0.10064 | 0.00054697 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 833224 | POLE | check for safety - car vs pole pole has snapped at ground, hanging mid air. P025766435 ETA:5-10 mins P025766435 - Ph 043812000 no loss of power - will hold with crane truck for tonight (safely) Needing to replace pole tomorrow (01/07) NDR: 37524. 01/07/16, line was isolated at ABS's S79 & S80 to replace pole 833224. 1 x pole and all hardware. | F2 | COLOMBO RD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.10064 | 11 | 2017 | 2016-07-01 | C | 182 | 0.10064 | 0.00054697
1 | 12053705 | 2016-06-30 22:03 | 2016-06-30 22:52 | 48 | 708 | 25908.45 | 0.077864 | 0.07148 | 0.0021278 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 9 | UNKNOWN | Tripping on City CB9 on O/C. Feeder patrolled / sectionalised but nothing found. All restored OK. Suspect wind blown debri - Conditions windy / Gusty. | F3 | CITY 9 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.07148 | 11 | 2017 | 2016-06-30 | C | 708 | 0.07148 | 0.0021278
1 | 12054571 | 2016-07-01 06:09 | 2016-07-01 08:23 | 133 | 10 | 1339.8333 | 0.0040266 | 0.003936 | 3.0053e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | SB2-069 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuse | F3/F4 | WILLS RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.003936 | 11 | 2017 | 2016-07-01 | C | 10 | 0.003936 | 3.0053e-05
1 | 12055211 | 2016-07-01 09:55 | 2016-07-01 17:58 | 483 | 25 | 11003 | 0.033068 | 0.032842 | 8.7155e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T6/555 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | FM will advise Tracey (FM replacing TX) that 847 Tremaine Ave will still need to be checked to make sure they have full supply. Unable to check the part power fault as the LV has been isolated. Transformer T6/555 had to be replaced due to oil loss, line was isolated at Sw/Gear's 157 & OS134 to replace the transformer. | F1 | RUAHINE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.032842 | 11 | 2017 | 2016-07-01 | C | 25 | 0.032842 | 8.7155e-05
1 | 12056734 | 2016-07-01 11:08 | 2016-07-01 12:14 | 66 | 112 | 4026.2 | 0.0121 | 0.01109 | 0.0003366 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C634 | UNKNOWN | Recloser C634 tripped on B & C phase O/C flags, line was patrolled and sectionalised and no fault was found. | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.01109 | 11 | 2017 | 2016-07-01 | C | 112 | 0.01109 | 0.0003366
1 | 12057146 | 2016-07-01 11:50 | 2016-07-01 12:15 | 25 | 3 | 75 | 0.0002254 | 0.000198 | 9.0159e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 742673 | STAY WIRE | Broken stay wire needs repair / replace at Pole 742673. 1 x insulator. 7 x stay wire. 4m x ducting | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000198 | 11 | 2017 | 2016-07-01 | C | 3 | 0.000198 | 9.0159e-06
1 | 12057310 | 2016-07-01 14:35 | 2016-07-01 16:41 | 126 | 20 | 2520 | 0.0075734 | 0.007393 | 6.0107e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 811751 | CROSSARM - COMPONENT(S) ONLY | 1km before you can see the sea down White Rock Road, after the Kaiwaka Rd turn off near airstrip. 11kv crossarm is hanging loose on pole is Paul Cutfield 06 307 8818. Faultman found a broken kingpin bolt on a cross arm on pole 811751, line waqs isolated at ABS 1203 to replace the kingpin bolt and nut. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.007393 | 11 | 2017 | 2016-07-01 | C | 20 | 0.007393 | 6.0107e-05
1 | 12060451 | 2016-07-02 05:17 | 2016-07-02 08:00 | 163 | 440 | 35010.65 | 0.10522 | 0.10125 | 0.0013223 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 211604 | CONDUCTOR - REPAIR/REHANG | 2 x 1R's 462 ICP's. Recloser 9275 tripped to L/O. E/F & O/C flags. Line sectionalised & patrolled. Lines down located at pole 211604. Isolations at ABS 9275/1, SE3-027, SE3-001, SE3-002 & Links 9275/6. Material required - 5 metres Namu conductor & 2 x Namu sleeves. All supply restored following repairs. 2r line patrol 0604. 2r repair 0712 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.10125 | 11 | 2017 | 2016-07-02 | C | 440 | 0.10125 | 0.0013223
1 | 12062297 | 2016-07-02 06:19 | 2016-07-02 10:53 | 274 | 361 | 46318.35 | 0.1392 | 0.13595 | 0.0010849 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | I1792 | CONDUCTOR - REPAIR/REHANG | 2 x 1R's 360ICP's and Balance Agri. CB 5 Piako sub tripped to L/O. O/C & E/F flags. Line sectionalised & patrolled. Lines down located at pole I1790. Isolation for repairs at ABS IC779. 40 metres squirrel conductor & 3 x squirrell compression sleeves materials required. Possibly caused by bird strike. Inadvertant outage on PKO CB 6 feeder was created during sectionalising on this fault due to faultman opening incorrect recloser (Recloser 9121/2 was opened instead of recloser 9561/2) Manual opening was requested by NOC due to SCADA indication & control failure on 9561/2. DNO has been created to have this inspected/repaired. Safety manager to be created by Andrew W re mistaken opening of incorrect recloser. Safety manager 634449 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.13595 | 11 | 2017 | 2016-07-02 | C | 361 | 0.13595 | 0.0010849
1 | 12063299 | 2016-07-02 07:34 | 2016-07-02 07:39 | 5 | 330 | 1705 | 0.0051241 | 0.002148 | 0.00099175 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - SWITCHING ERROR | 9121/2 | NONE | 11kV Recloser 9121 operated in error by field resource, closed again once error found. Safety Manager 634449 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.002148 | 11 | 2017 | 2016-07-02 | C | 330 | 0.002148 | 0.00099175
1 | 12063670 | 2016-07-02 10:00 | 2016-07-02 11:32 | 92 | 22 | 2024 | 0.0060828 | 0.005884 | 6.6117e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 385945 | CONDUCTOR - REPAIR/REHANG | 1 x broken conductor located at pole 385945. Line isolated at fuses SG7-001. 8 metres Namu conductor and 3 x Namu sleeves material required. All supply restore following repairs.No obvious reason for conductor breaking. | F4 | OLD COACH RD | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.005884 | 11 | 2017 | 2016-07-02 | C | 22 | 0.005884 | 6.6117e-05
1 | 12064449 | 2016-07-02 13:56 | 2016-07-02 15:47 | 110 | 171 | 13428.15 | 0.040356 | 0.038814 | 0.00051391 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9320/2 | UNKNOWN | Recloser 9320/2 on Tahuna CB 2 feeder tripped to L/O. Line sectionalised & patrolled. No apparent fault found. All supply restored. 2r line patrol 1429. 2r repair no fault | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.038814 | 11 | 2017 | 2016-07-02 | C | 171 | 0.038814 | 0.00051391
1 | 12068138 | 2016-07-02 20:37 | 2016-07-02 23:35 | 177 | 1 | 177.9833 | 0.0005349 | 0.000525 | 3.0053e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | TC4383 | UNKNOWN | Power had come back on before faultman arrived. Faultman checked things out but could not find anything wrong. Customer said that this had happened before. | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.000525 | 11 | 2017 | 2016-07-02 | C | 1 | 0.000525 | 3.0053e-06
1 | 12069800 | 2016-07-03 07:53 | 2016-07-03 11:06 | 192 | 238 | 16177.8833 | 0.048619 | 0.046473 | 0.00071526 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 804996 | CONDUCTOR - REPAIR/REHANG | Repaired conductors @ pole 804996 materials used +/- 6m 16 mm copper conductor & 8 sleves | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.046473 | 11 | 2017 | 2016-07-03 | C | 238 | 0.046473 | 0.00071526
1 | 12070386 | 2016-07-03 08:08 | 2016-07-03 11:00 | 172 | 1 | 172.3333 | 0.00051791 | 0.000508 | 3.0052e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 362224 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Mark onsite 09.59. Replaced blown transformer 1105 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000508 | 11 | 2017 | 2016-07-03 | C | 1 | 0.000508 | 3.0052e-06
1 | 12070735 | 2016-07-03 09:47 | 2016-07-03 14:50 | 303 | 228 | 14505.8833 | 0.043594 | 0.041538 | 0.0013253 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 9423 | SWITCH (HV) | CB 2 L/O on O/C. Sectionalised and found Sw/Gear 9423/1 faulty. Isolated between Sw/Gear 9935/3, ABS IC 1035 & ABS 577. Found flash over on cable termination at Sw/gear 9423/1 . Cleaned & tested OK Relivened 2r line patrol 1021. 2r repair 1231 | F4 | BANKS ST | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.041538 | 11 | 2017 | 2016-07-03 | C | 228 | 0.041538 | 0.0013253
1 | 12072946 | 2016-07-03 16:05 | 2016-07-03 18:07 | 122 | 4 | 488 | 0.0014666 | 0.00143 | 1.2021e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP315 | CONDUCTOR - REPAIR/REHANG | Found 2 lines down. Isolated at fuses FP315. Repaired lines & relivened | F1/F3 | TE PUKE NORTH | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.00143 | 11 | 2017 | 2016-07-03 | C | 4 | 0.00143 | 1.2021e-05
1 | 12073131 | 2016-07-03 17:31 | 2016-07-03 19:59 | 148 | 190 | 27676.9 | 0.083177 | 0.081463 | 0.000571 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758932 | INSULATOR | CB H11 tripped no flags, line was patrolled and sectionalised and broken insulator was found at ABS 5399 on pole 758932, line was isolated at ABS's 5410, 4807 & 5357 to cut away the jumper to broken insulator and ABS 5399 was opened and tag with DNO Tag attached. ABS has been DNO'd No: 160703. 2r repair 1331 | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.081463 | 6.6 | 2017 | 2016-07-03 | C | 190 | 0.081463 | 0.000571
1 | 12075394 | 2016-07-04 09:18 | 2016-07-04 10:45 | 87 | 28 | 2436 | 0.0073208 | 0.007068 | 8.4147e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D12413 | CONDUCTOR - REPAIR/REHANG | Repair 1 x lines down. Materials used: 2m x conductor, 2 x sleeves. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.007068 | 11 | 2017 | 2016-07-04 | C | 28 | 0.007068 | 8.4147e-05
1 | 12075848 | 2016-07-04 09:38 | 2016-07-04 11:34 | 115 | 1 | 115.8 | 0.00034801 | 0.000338 | 3.0052e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 7341P | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace Transformer 7341P ( marked as T2/495 in SCADA). | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000338 | 11 | 2017 | 2016-07-04 | C | 1 | 0.000338 | 3.0052e-06
1 | 12075889 | 2016-07-11 09:36 | 2016-07-11 18:08 | 512 | 113 | 34820 | 0.10464 | 0.10362 | 0.00049584 | NAPA ID:21702 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > KARAMEA | 11 | Planned | 021702 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 10304 | NONE | Install a new CFCF RMU, Run new cables from new RMU 10304 to T6/629 and T6/640 also to switch 97 There will be a short outage via 11kV isolation 11kv switch 97 and 532, we will make an 11kv break at T6/630. then close switch 532 and liven back to T6/630. Which will make the isolation area from T6/630 to switch 97. This will be reversed at the end of the day. Please Note: Milsons building has its own generator (large), which will supply all customers from T6/640. | F3 | KARAMEA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.051809 | 5.5 | 2017 | 2016-07-11 | B | 113 | 0.10362 | 0.00049584
1 | 12076247 | 2016-07-14 08:50 | 2016-07-14 14:47 | 357 | 94 | 33558 | 0.10084 | 0.099993 | 0.00028247 | NAPA ID:21034 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | 021034 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/Gear 9868 | NONE | Sync on HV Gen back to TEMP52. AP -Change HV poles and associated hardware between TEMP52 & 9868. Restore HV Gen to Network. Works location: Seaforth Rd, Waihi Beach. WO 30017825 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.049996 | 5.5 | 2017 | 2016-07-14 | B | 94 | 0.099993 | 0.00028247
1 | 12076975 | 2016-07-04 10:43 | 2016-07-04 11:05 | 22 | 89 | 1975.8 | 0.0059378 | 0.005135 | 0.00026747 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701226 | AIR BREAK SWITCH - ABS (HV) | During planned switching 21207 11kV ABS 29 failed. An insulator and section of the ABS came apart. DNO 160704. The failed parts were removed and a temp line break was done on the ABS 222 side of 29 for safety. Required a number of crew to effect fault management. Two safety observers as around the corner from school and needed to keep the public out of the zone due to flash over and falling hazard from the ABS 29 structure. Hazard managed via a live line crew process. | F3 | BROOKLANDS 9 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.005135 | 11 | 2017 | 2016-07-04 | C | 89 | 0.005135 | 0.00026747
1 | 12078387 | 2016-07-17 15:01 | 2016-07-17 15:05 | 4 | 1 | 4.4 | 1.3222e-05 | 4e-06 | 3.0048e-06 | NAPA ID:20728 TP_PIAKO GXP > FARMER ROAD SUB | 11 | Planned | 020728 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Farmer Rd Sub CB 2 | NONE | Maintain Farmer Road 11kV CB's. CB2 can be opened at 15.00hours and exchanged with either CB4 or CB6 to get Wallace Corp Power back on asap. Refer David Wright 021-890287 (Wallace Corp.). Works location: Farmers Rd Sub. WO 30022860 | F1 | WOODS RD | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 2e-06 | 5.5 | 2017 | 2016-07-17 | B | 1 | 4e-06 | 3.0048e-06
1 | 12078914 | 2016-07-05 10:15 | 2016-07-05 12:27 | 132 | 7 | 924 | 0.0027768 | 0.002713 | 2.1037e-05 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 229158 | NONE | ###RED DEFECT ### Replace broken kidney Strain insulator. Note other equipment to be replaced in a later shut as other poles etc need doing, being followed up by Michael Vickers. ASW Switching being written up over night for crew to conduct temp repair (replace strainer) outage from 0900 to 1200. Retailers advised by NOC dispatch. Isolation point via Fuses SF7-024, Earthing at TF7-055. ASW advsied SMC via phone of issues etc (Sammie) | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.002713 | 11 | 2017 | 2016-07-05 | C | 7 | 0.002713 | 2.1037e-05
1 | 12079819 | 2016-07-04 18:38 | 2016-07-04 20:34 | 116 | 1 | 116.3 | 0.00034951 | 0.00034 | 3.0052e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1020 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 20a hv fuses @FP1020 suspect caused by a logging opperation in the area | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.00034 | 11 | 2017 | 2016-07-04 | C | 1 | 0.00034 | 3.0052e-06
1 | 12083552 | 2016-07-05 02:22 | 2016-07-05 05:55 | 212 | 362 | 29429.8 | 0.088443 | 0.085179 | 0.0028309 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P358578 | INSULATOR | Replaced 3x pin insulators with clamp top pin insulators on pole P358578 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.085179 | 11 | 2017 | 2016-07-05 | C | 362 | 0.085179 | 0.0028309
1 | 12084805 | 2016-07-25 21:17 | 2016-07-26 02:47 | 329 | 63 | 20785.8 | 0.062454 | 0.061885 | 0.00018929 | NAPA ID:21508 TP_CARRINGTON GXP > OAKURA SUB > OAKURA | 11 | Planned | 021508 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1575 | NONE | Replace and upgrade transformer 1575 due to overloading from 200 - 300kVA. Works Location: South Road. Work Order 30026811. | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.030943 | 5.5 | 2017 | 2016-07-25 | B | 63 | 0.061885 | 0.00018929
1 | 12085634 | 2016-07-05 11:25 | 2016-07-05 16:44 | 319 | 2 | 638 | 0.0019173 | 0.001899 | 6.0104e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X120 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer X120 found to be faulty, requires replacement. 1x blown 15A Fuse to spur line at Fuses 1138, replaced at 10:55am. Replaced Transformer 15kVA | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.001899 | 11 | 2017 | 2016-07-05 | C | 2 | 0.001899 | 6.0104e-06
1 | 12086607 | 2016-07-05 07:59 | 2016-07-05 10:55 | 175 | 1 | 175.8833 | 0.00052857 | 0.000519 | 3.0052e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 843854 | FUSE - ELEMENT/LINK (HV) | 2x HV fuses blown at 8642. Cause: Duck. | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.000519 | 11 | 2017 | 2016-07-05 | C | 1 | 0.000519 | 3.0052e-06
1 | 12087704 | 2016-07-05 17:00 | 2016-07-05 20:30 | 210 | 3 | 630 | 0.0018933 | 0.001866 | 9.0156e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2/88 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer T2/88 Found to Be Faulty . Replaced transformer | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.001866 | 11 | 2017 | 2016-07-05 | C | 3 | 0.001866 | 9.0156e-06
1 | 12088418 | 2016-07-05 19:46 | 2016-07-05 23:57 | 251 | 254 | 21792 | 0.06549 | 0.0632 | 0.0014305 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03920 | CONDUCTOR - REPAIR/REHANG | During sectionalising and patrol found 1line down @ pole P03920 Line isolated from ABS H 139 for repairs on restoration H131 tripped again further patrol found 2 lines down @ pole P04048 same isolation point and lines repaired Materials used +/- 10m copper and several joints | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0632 | 11 | 2017 | 2016-07-05 | C | 254 | 0.0632 | 0.0014305
1 | 12089052 | 2016-07-05 21:13 | 2016-07-05 23:46 | 153 | 6 | 726.8333 | 0.0021843 | 0.00213 | 1.8031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 426 & 1269 | FUSE - ELEMENT/LINK (HV) | Advised Alan to go to check fuses at 426 as another couple of jobs came in. Replaced 3x 15a hv fuses @ 426 and 2x 6a hv fuses @ 1269 . Suspect caused by bird strike | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.00213 | 11 | 2017 | 2016-07-05 | C | 6 | 0.00213 | 1.8031e-05
1 | 12090090 | 2016-07-06 07:28 | 2016-07-06 09:30 | 121 | 10 | 1215.1667 | 0.0036518 | 0.003561 | 3.0052e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 747607 | FUSE - ELEMENT/LINK (HV) | 2 x fuses 10amp due to bird | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.003561 | 11 | 2017 | 2016-07-06 | C | 10 | 0.003561 | 3.0052e-05
1 | 12090376 | 2016-07-21 09:19 | 2016-07-21 14:10 | 291 | 21 | 6111 | 0.018362 | 0.018172 | 6.31e-05 | NAPA ID:21317 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 021317 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC4044 | NONE | Puriri Pole Renewals Shut 15a Work Area beyond FC4044 Work on Poles N2302, N2303, N2304, N2305, N13057, N13058, N2307, N2308, N2309, N2311, N2313, N2315, N2316, N2317, N2319, N13061, N2321, N2323, N2324, N2325, N2326, N2327, N2328, N2329, N2330. Factory jRoad North, Puriri, Thames. W/O 30017847. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.009086 | 5.5 | 2017 | 2016-07-21 | B | 21 | 0.018172 | 6.31e-05
1 | 12090735 | 2016-07-26 09:56 | 2016-07-26 16:15 | 379 | 67 | 25393 | 0.076296 | 0.075692 | 0.00020131 | NAPA ID:21324 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 021324 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC391 | NONE | Puriri Pole Renewals Shut 14a Work Area beyond IC391. Work on Poles N13077, N13083, N1958, N1960, N1960, N1961, N1962, N1963, N1966, N1973, N1974, N1975, N1977, N1978, N1979, N607951, N2002, N2003, N2004, N2005, N2007, N2008, N2009, N2010. Works Location: Wharepoa and Puna Roads, Puriri, Thames. W/O 30017847. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.037846 | 5.5 | 2017 | 2016-07-26 | B | 67 | 0.075692 | 0.00020131
1 | 12090897 | 2016-07-28 09:16 | 2016-07-28 11:43 | 147 | 67 | 9849 | 0.029592 | 0.028987 | 0.0002013 | NAPA ID:21326 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 021326 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC391 | NONE | Puriri Pole Renewals Shut 14b Work Area beyond IC391. Work on Poles N13077, N13083, N1958, N1960, N1960, N1961, N1962, N1963, N1966, N1973, N1974, N1975, N1977, N1978, N1979, N607951, N2002, N2003, N2004, N2005, N2007, N2008, N2009, N2010. Work Location: Wharepoa and Puna Roads, Puriri, Thames. W/O 30017847. | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.014493 | 5.5 | 2017 | 2016-07-28 | B | 67 | 0.028987 | 0.0002013
1 | 12091138 | 2016-07-06 10:43 | 2016-07-06 11:35 | 52 | 178 | 8113.0667 | 0.024382 | 0.022776 | 0.00053493 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 067 | UNKNOWN | Recloser O67 tripped e/f o/c. Sectionalised & Patrolled with no fault found. A customer reported a loud bang outside his property at 1124 Kellow Rd. When faultman arrived evidence of recent tree cutting around Pole P33241 was found and he suspects, and as noted by the customer that someone trimming trees may have caused a tree contact. No one had consent to work near the lines and they had left site. Faultman is to follow this up with his manager for reporting to HSEQ | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.022776 | 11 | 2017 | 2016-07-06 | C | 178 | 0.022776 | 0.00053493
1 | 12101334 | 2016-07-15 09:15 | 2016-07-15 13:32 | 256 | 20 | 5135.6667 | 0.015432 | 0.015252 | 6.0099e-05 | NAPA ID:22390 TP_MANGAMAIRE GXP > ALFREDTON SUB > BROOKLANDS | 11 | Planned | 022390 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole P08280 | NONE | Replace broken 11kv xarm. Defect 148297.Route 52, Alferdton. W/O 30008319. | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.007626 | 5.5 | 2017 | 2016-07-15 | B | 20 | 0.015252 | 6.0099e-05
1 | 12103410 | 2016-07-09 10:24 | 2016-07-09 13:38 | 194 | 32 | 6213.3333 | 0.018672 | 0.018383 | 9.6164e-05 | NAPA ID:22432 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 022432 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P03918 | NONE | Replace 11kV wire between P03919, P03918 and P04048, P03926 due to bird strike wire is badly damage. Works location: Linton Station Rd. WO 30030464 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0091915 | 5.5 | 2017 | 2016-07-09 | B | 32 | 0.018383 | 9.6164e-05
1 | 12103587 | 2016-07-26 09:45 | 2016-07-26 13:30 | 225 | 5 | 1125 | 0.0033802 | 0.003335 | 1.5023e-05 | NAPA ID:21307 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | 021307 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC4260 | NONE | Replace cross arms and line hardware on Spur Line. Works location: Matarangi, Whitianga. WO 30002514 | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.0016675 | 5.5 | 2017 | 2016-07-26 | B | 5 | 0.003335 | 1.5023e-05
1 | 12103636 | 2016-07-22 09:46 | 2016-07-22 14:15 | 269 | 76 | 20479.4667 | 0.061535 | 0.06085 | 0.00022836 | NAPA ID:22288 TP_STRATFORD GXP > MOTUKAWA SUB > RATAPIKO | 6.6 | Planned | 022288 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 5399 | NONE | Replace ABS 5399 & cross arms & upgrade Earths @ Pole 758932. DNO160703. Works location: Tariki Rd, Ratapiko. WO 30030329 | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.030425 | 3.3 | 2017 | 2016-07-22 | B | 76 | 0.06085 | 0.00022836
1 | 12103674 | 2016-07-07 12:09 | 2016-07-07 16:45 | 276 | 324 | 24421.8 | 0.073392 | 0.07047 | 0.00097368 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 769292 | POLE | Car vs pole Pole taken out, lines on the road and over car. Occupants still inside vehicle, safety instructions given by Fire Comms. ETA REQD - 10 mins, Fire Comms advised. Control advised 12:23pm Replaced pole with 11M Busck & all associated hardware & 25mm Cu. conductor NDR# N200042 2r line patrol 1234 2r repair 1259 | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.07047 | 11 | 2017 | 2016-07-07 | C | 324 | 0.07047 | 0.00097368
1 | 12104001 | 2016-07-24 08:49 | 2016-07-24 08:55 | 6 | 47 | 288.25 | 0.0008661 | 0.000442 | 0.00014122 | NAPA ID:22400 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 022400 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P15912 | NONE | To make line brake at pole P15912,then reliven from T15 to line brake .then isolate 11kv from CB10 to T2 , then change ABS T1,and T11 DNO #'s 160625 and 160626. Works location: Halls Rd. WO 30030174. Job cancelled after it had started due to feeder faults from severe weather. Applicant will reapply. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000221 | 5.5 | 2017 | 2016-07-24 | B | 47 | 0.000442 | 0.00014122
1 | 12139859 | 2016-07-26 09:00 | 2016-07-26 14:36 | 336 | 3 | 1008 | 0.0030286 | 0.003001 | 9.0138e-06 | NAPA ID:19404 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 019404 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 217743 | NONE | Replace poles, hardware and conductors between TEMP65 & TEMP66. Works location: Poripori Rd. WO 30017844 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0015005 | 5.5 | 2017 | 2016-07-26 | B | 3 | 0.003001 | 9.0138e-06
1 | 12141179 | 2016-07-08 09:11 | 2016-07-08 12:07 | 176 | 183 | 32208 | 0.09679 | 0.09514 | 0.00054994 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P43410 | POLE | Erin Police called Car vs Pole in. No lines down but wanting site safety check. Pole will need replacing in morning Pole number P93410. Isolation Points ABS A37 & A47 CB 13 Kairanga. 1 X 11kV pole & all hardware replaced. NDR: 30792 | F3 | TAKARO | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.09514 | 11 | 2017 | 2016-07-08 | C | 183 | 0.09514 | 0.00054994
1 | 12141187 | 2016-07-07 22:53 | 2016-07-08 03:52 | 299 | 288 | 17722.4833 | 0.053259 | 0.050662 | 0.00086549 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 842666 | POLE | Car V Pole replaced 1 X 11m Pole 1X H/T Crossarm 3X H/T Insulators 30m Conductor NDR Number N100183 pole Number 842666 2r line patrol 2349 2r repair 0020 | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.050662 | 11 | 2017 | 2016-07-07 | C | 288 | 0.050662 | 0.00086549
1 | 12141503 | 2016-07-07 23:49 | 2016-07-08 03:54 | 244 | 97 | 8946.65 | 0.026886 | 0.026011 | 0.00053492 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 851396 | BINDER | at 23:49, Walton Sub, CB 4 Wardville Feeder, Recloser RC25, Tripped, Ph A + B O/C, E/F O/C, L/O. Faultmen dispatched & investigation began. Feeder sectionalised. Found Broken Jumper & Insulator at Pole 851396. Isolated Lines at ABS IC1330, IC963, 9705/1 & Links 9705/4. Permit Issued and repairs carried out. All Power Restored on completion. Mike Cornelius Attended. Replaced 1x Insulator, 1x Connector, 1x Binder. | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.026011 | 11 | 2017 | 2016-07-07 | C | 97 | 0.026011 | 0.00053492
1 | 12141994 | 2016-07-08 02:43 | 2016-07-08 03:48 | 65 | 2524 | 70416.1333 | 0.21161 | 0.18886 | 0.007585 |  | 11 | Unplanned |  | ZONE SUB EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | T7 | COMMUNICATIONS EQUIPMENT | T7 Bucholz Trip. All feeders backfed from KPT and AON. T7 Protection outdoor relay box leaking and filled up with water. Water drained and box dried out. T7 re-instated and feeders restored to normal configuration. | S4 | KATIKATI 33KV | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.18886 | 11 | 2017 | 2016-07-08 | C | 2524 | 0.18886 | 0.007585
1 | 12144587 | 2016-07-08 04:34 | 2016-07-08 07:25 | 171 | 6 | 1027.3 | 0.0030872 | 0.003033 | 1.8031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D12706 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp fuse. Cause unknown. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.003033 | 11 | 2017 | 2016-07-08 | C | 6 | 0.003033 | 1.8031e-05
1 | 12144701 | 2016-07-08 09:44 | 2016-07-08 17:06 | 442 | 33 | 14581.7333 | 0.04382 | 0.043522 | 9.917e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O12446 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer TC2550 fell off pole O12446. Cross arms rotten. Replaced Transformer TC2550. HV Crossarms Fuse Arm. 2 x LV arms. HV Fuse Holders. HV Fuses. LV Fusing. | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.043522 | 11 | 2017 | 2016-07-08 | C | 33 | 0.043522 | 9.917e-05
1 | 12144918 | 2016-07-07 13:54 | 2016-07-07 17:36 | 222 | 1 | 222 | 0.00066715 | 0.000658 | 3.0051e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227809 | FUSE - ELEMENT/LINK (HV) | FP 1366 - 2 x 3A fuses and 1 x 2A HV Fuse at Transformer TF8-043 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000658 | 11 | 2017 | 2016-07-07 | C | 1 | 0.000658 | 3.0051e-06
1 | 12145273 | 2016-07-11 14:16 | 2016-07-11 14:57 | 40 | 59 | 2389.5 | 0.0071806 | 0.006648 | 0.0001773 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 372415 | JOINT - CONDUCTOR JOINT | Check out insulator in question, Bruce has checked insulator from the ground using binoculars to check for damage not faulting at the moment. 2R will be required to get thermal imaging camera to site to check insulator. This will be done on Monday. Glowing Cable reported during weekend by Public at Pole 372415. Isolated at ABS's 5455, 5848, & 5907 with backfeed installed via ABS 5665. Loose connection found on 1 phase that had no washers on bolts for the joints. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.006648 | 11 | 2017 | 2016-07-11 | C | 59 | 0.006648 | 0.0001773
1 | 12146096 | 2016-07-08 09:53 | 2016-07-08 11:10 | 77 | 86 | 6656.4 | 0.020003 | 0.019228 | 0.00025844 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI106 | FUSE - ELEMENT/LINK (HV) | Multiple properties on Kahuterawa Road, Linton. FM needs to check fuses H106. H106 2 x 15amp fuses. Unknown cause. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.019228 | 11 | 2017 | 2016-07-08 | C | 86 | 0.019228 | 0.00025844
1 | 12147478 | 2016-07-08 11:15 | 2016-07-08 17:45 | 389 | 2 | 779.7 | 0.0023431 | 0.002325 | 6.0103e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1482 | FUSE - ELEMENT/LINK (HV) | Advised FM (voicemail left) that neighbour at 177 Hicks Road is also experiencing no power (OMS 12167058) - unlocked to roll up. 17:45 2 x 3A HV Fuses replaced at Fuses 1482. Cannot force this job up to fuses to close job off | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.002325 | 11 | 2017 | 2016-07-08 | C | 2 | 0.002325 | 6.0103e-06
1 | 12148150 | 2016-07-08 10:43 | 2016-07-08 11:29 | 46 | 50 | 2316.6667 | 0.0069619 | 0.006511 | 0.00015026 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C218/2 | UNKNOWN | Faultman found Sectionaliser C218/2 after an auto reclose on Recloser C217/2 (OMS 12146997), line was patrolled and no fault was found suspect weather as heavy rain & windy in the area. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.006511 | 11 | 2017 | 2016-07-08 | C | 50 | 0.006511 | 0.00015026
1 | 12149099 | 2016-07-08 11:40 | 2016-07-08 14:11 | 151 | 79 | 6692.4167 | 0.020112 | 0.019399 | 0.00023741 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P05299 | CONDUCTOR - REPAIR/REHANG | Recloser 10300/2 tripped on B phase O/C & E/F flags, line was patrolled and a line was found down at pole P05299, line was isolated at ABS M67 & links 10300/6, on the way to close backfeed in faultman found a branch across the line at transformer 7054P, faultman removed branch from the line with hot line sticks, suspect this could have been the cause for the line down. 1 X Squirrel Sleeve & clamp used. 2r line patrol 1255 2r repair 1341 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.019399 | 11 | 2017 | 2016-07-08 | C | 79 | 0.019399 | 0.00023741
1 | 12149348 | 2016-07-08 11:54 | 2016-07-08 12:40 | 46 | 792 | 23270.9167 | 0.069933 | 0.062792 | 0.0023801 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB3 | UNKNOWN | CB3 Tripped on O/C. Feeder patrolled / sectionalised but restored OK. Loose span found between Poles 444576 and 756658 causing possible clash in high winds. Defected by DOWNERS - No. 10157289. 2r line patrol 1219 / no repair. | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.062792 | 11 | 2017 | 2016-07-08 | C | 792 | 0.062792 | 0.0023801
1 | 12150862 | 2016-07-09 09:17 | 2016-07-09 11:04 | 107 | 41 | 4387 | 0.013183 | 0.012813 | 0.00012321 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P00903 | CONDUCTOR - REPAIR/REHANG | Fuses found at H34. outage recorded on child job FM to go back out in daylight hours to find fault. Unable to find fault in night, big gates barring access to a lot of properties. Faultman found line down across gully between poles P00903 & P00904 caused by a tree branch that had broken off, line was isolated at Fuses H34 to make repairs. 10 meters of 25mm copper cunductor used. 3 X 25mm sleeves used. | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.012813 | 11 | 2017 | 2016-07-09 | C | 41 | 0.012813 | 0.00012321
1 | 12150868 | 2016-07-08 12:36 | 2016-07-08 15:44 | 187 | 115 | 3508.8333 | 0.010545 | 0.009507 | 0.00015026 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C217/2 | UNKNOWN | Recloser C217/2 auto reclosed, line was patrolled and sectionalised and no fault could be found. 2r line patrol 1343 / 2r repair none. | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.009507 | 11 | 2017 | 2016-07-08 | C | 115 | 0.009507 | 0.00015026
1 | 12151023 | 2016-08-01 09:54 | 2016-08-01 16:05 | 371 | 9 | 3339 | 0.010032 | 0.00995 | 2.704e-05 | NAPA ID:21194 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 021194 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2844 | NONE | To Replace Defective Arms. To Remove TC2844. To install 2 new transformers. To extend the 11kV Lines 2 spans. Works location; Paeroa Tahuna Rd. WO 30027927 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.004975 | 5.5 | 2017 | 2016-08-01 | B | 9 | 0.00995 | 2.704e-05
1 | 12155674 | 2016-07-08 15:43 | 2016-07-08 16:15 | 32 | 14 | 448 | 0.0013463 | 0.00122 | 4.2072e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04332 | JUMPER | Faultman found a broken 11kV jumper at transformer T9/166 on pole P04332, line was isolated at Fuses V52 to repair the jumper. 1 X Squirrel jumper replaced. 2 X line taps used. | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.00122 | 11 | 2017 | 2016-07-08 | C | 14 | 0.00122 | 4.2072e-05
1 | 12155888 | 2016-08-05 12:15 | 2016-08-05 13:15 | 60 | 4 | 240 | 0.00072103 | 0.000684 | 1.2017e-05 | NAPA ID:21935 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021935 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2484 | NONE | To install a 400V Disconnector on TC2484. Works location: Gunn Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000342 | 5.5 | 2017 | 2016-08-05 | B | 4 | 0.000684 | 1.2017e-05
1 | 12156033 | 2016-08-05 14:00 | 2016-08-05 15:00 | 60 | 2 | 120 | 0.00036051 | 0.000342 | 6.0085e-06 | NAPA ID:21936 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021936 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4655 | NONE | To install a 400V Disconnector. Works location: Gunn Rd, Waharoa. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000171 | 5.5 | 2017 | 2016-08-05 | B | 2 | 0.000342 | 6.0085e-06
1 | 12157415 | 2016-07-25 09:50 | 2016-07-25 11:24 | 94 | 3 | 282 | 0.00084731 | 0.00082 | 9.0139e-06 | NAPA ID:22242 TP_KOPU GXP > TAIRUA SUB > TAIRUA NORTH | 11 | Planned | 022242 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 249849 | NONE | Replace blown up lightning arrestors on pole 249849 (load side of Fuses FC1115) Break load with ABS IC2142 prior to applying work area Isolation's. | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.00041 | 5.5 | 2017 | 2016-07-25 | B | 3 | 0.00082 | 9.0139e-06
1 | 12158565 | 2016-07-08 14:09 | 2016-07-08 19:23 | 313 | 1139 | 116955.4167 | 0.35147 | 0.3412 | 0.0037504 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 798617 | POLE | Car Vs Pole 91 Western Lake Road. Fire Comms require ETA F21107774 - 45 mins 04 801 0812 2.44pm job has rolled up for 810 Western Lake Road, Featherston advising that wires have come out of the insulator outside this address - advised Paul control- This was a LV fault. CB C916 tripped on C phase O/C flags, received a call from fire comms of car vs pole, line was isolated at ABS's S575, 8176, C634/1, Fuses 7198, Links C634/4, Links C634/6 and transformer T1619 400V fuses to replace the pole. Replace pole & hardware NDR 54307 2r line patrol 1421 2r repair 1601 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.3412 | 11 | 2017 | 2016-07-08 | C | 1139 | 0.3412 | 0.0037504
1 | 12161155 | 2016-07-27 08:30 | 2016-07-27 15:26 | 416 | 113 | 27177.5667 | 0.081657 | 0.080638 | 0.00067903 | NAPA ID:21165 TP_MASTERTON GXP > TE ORE ORE SUB > TAUWERU | 11 | Planned | 021165 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 833633 | NONE | 1. Switching to isolate feeder to do line breaks 2. Create line breaks at pole 833633 & 833779 do under live line permit with line isolated 3. Switching to restore power between CB C828 & pole 833633, and between ABS S157 & 833779 4. Access permit to replace 4 defective 11kv poles 833656,833672,833773, and 833755. 5. Switching to isolate feeder to close line breaks under LLP, and restore feeder to normal. WORKS LOCATION: Te Ore Ore Area in Rural Masterton. WO 30017455 | F4 | TAUWERU | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.040319 | 5.5 | 2017 | 2016-07-27 | B | 113 | 0.080638 | 0.00067903
1 | 12161546 | 2016-07-08 15:32 | 2016-07-08 17:27 | 115 | 1015 | 67826.8667 | 0.20383 | 0.19468 | 0.0034349 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P13687 | UNKNOWN | Sparking lines outside 2389 Pohangina Valley East Road TX T4/199 - caller (027) 286 371 - ONC advised. Phone not going through. CB 8 tripped no flags,line was patrolled and sectionalised and a branch was found on the lines at pole P13687,ABS F44 was opened and the branch was removed with hot line sticks. 2r line patrol 1610 2r repair no | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.19468 | 11 | 2017 | 2016-07-08 | C | 1015 | 0.19468 | 0.0034349
1 | 12162938 | 2016-07-08 15:38 | 2016-07-08 20:33 | 295 | 86 | 18934.4833 | 0.056901 | 0.056125 | 0.00025844 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H106 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuses at FABS H106. Line patrolled, no fault found | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.056125 | 11 | 2017 | 2016-07-08 | C | 86 | 0.056125 | 0.00025844
1 | 12164689 | 2016-07-08 15:52 | 2016-07-09 02:20 | 628 | 196 | 46571.55 | 0.13995 | 0.13819 | 0.0007002 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 712928 | POLE | * 15:52, Tasman Sub, CB TA7 Oaonui Feeder, Tripped, O/C, L/O. Lines/poles down Between (& isolated between) ABS's 6416 & 6438. *Permit issued & as many repairs as possible made to restore power. *Created 2x Line Breaks to help restore all power at Poles 712928 & 889250. Will be left in place until permanent repairs completed. *All Power Restored on Completion. *Closed ABS 6416 to re-liven to Transformer T3330. Closed ABS 6438 to re-liven to Transformer 3340. *Transformer 5593E Fuses are Open & Tagged to replace transformer tomorrow. Unsure of materials used. Replaced 15kVA Transformer, Back Plate, Associated bolts, & HV Fuse Links *529 arawhata Rod (fed off Tfmr 55933) is on a temporary generator for the meantime. A temp supply is to be installed O/H via the telecom poles and will be in place until all permanent repairs are completed on road. Cause is due to a ground anchor breaking in high winds at one pole. This pole lent over with the prevailing winds and pulled the five poles over with it. *Requires engineering design solution as the pole sites are compromised due to ten foot drain down road side and solid rock under ground. Additional network assets at risks. Powerco assets and design teams advised. Unknown how long until repairs are carried out as re-engineering of the assets may be required. *due to length of time to effect permanent repair/replacement the OMS closed out and entered as a residual 100111. *at this stage not suspected top be NDR applicable Have advised Control lines down between 400-590 Arawhata Road 16:07 Mark (027) 608 3538 from 520 Arawhata Road has reported 5-7 poles down outside this address Tx T3330 - ONC informed 16:15 Dianne - closest pole 712913 - chris (Infamax) advised he is a contractor in the area and has cones so will close the road to make it safer - advised hub of this. 16:15 Lines down 75-82 Arawhata Road Tx TC3300 - Controller informed. | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.13819 | 11 | 2017 | 2016-07-08 | C | 196 | 0.13819 | 0.0007002
1 | 12165245 | 2016-07-08 16:22 | 2016-07-08 21:12 | 289 | 316 | 52034.7667 | 0.15637 | 0.15352 | 0.00094963 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P35635 | NONE | 270 Paranui Road - tree on line outside this address, passed info to control. Advised faultman. RS 10227 Trip, Sectionalised & Patrolled. Tree had fallen over from outside notice zone & had contacted lines. Tree branch did not appear to be contacting HV but must have been contacting during strong gusts. Tree branch removed from lines using hot stick and relivened ok. Materials used: 1x 10Amp HV Fuse Link. 2r line patrol 1815 no 2r repair. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.15352 | 11 | 2017 | 2016-07-08 | C | 316 | 0.15352 | 0.00094963
1 | 12165352 | 2016-07-08 16:13 | 2016-07-09 16:48 | 1475 | 154 | 35035.8333 | 0.10529 | 0.1039 | 0.00088952 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 711787 | CONDUCTOR - REPAIR/REHANG | Tripping on Ngariki CB NG4 on O/C. Feeder patrolled and a line found off insulator across to centre conductor. Isolation beyond fuses with Feeder relivened. Extreme winds meant unsafe to carryout repairs. 4 Transformers off. Line was isolated at Fuses NG406 to repair lines at pole 711787. NDR: 15813. 40 meters - 35mm Aluminium conductor used. 20 X 35mm sleves used. 1 X cross arm + 3 x insulators. 6 X binders. 2r line patrol 1749 / 2r repair 1508. | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.1039 | 11 | 2017 | 2016-07-08 | C | 154 | 0.1039 | 0.00088952
1 | 12167273 | 2016-07-08 17:05 | 2016-07-08 17:44 | 38 | 324 | 8029.6833 | 0.02413 | 0.021209 | 0.00097367 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | P19290 | NONE | CB 4 tripped on A & B phase O/C flags, line was sectionalised and patrolled and a branch was found on the lines at pole P 19290, line was isolated at ABS M34 and branch was removed with hot line sticks. 2r line patrol 1716 / no 2r repair. | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.021209 | 11 | 2017 | 2016-07-08 | C | 324 | 0.021209 | 0.00097367
1 | 12167608 | 2016-07-08 18:30 | 2016-07-08 19:11 | 41 | 72 | 2952 | 0.0088712 | 0.008222 | 0.00021637 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | X2191 | CONDUCTOR - REPAIR/REHANG | Tree has gone through the LV lines which resulted in one line flicking over the HV which has been cleared by the FM. The HV through the LV affected two properties which have been isolated at the TX (X2191) along with 3 lines that are still down. These will be repaired tomorrow 09/07. Electrical inspector (Summet Electrical) is attending tomorrow morning to inspect the properties (both properties are at 2024 Main Road North) Property owner has generator and the other house is unoccupied. He has been advised of the situation. All repairs to be charged under NDR 22700. Advised properties still without lines power as the tree had put 11kV through their system. Electrical inspector not happy to reliven until more tests ? likely to be Monday. Property owner has 3x generators so has own power, other property unoccupied. Customer informed of process, but network side is fixed. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.008222 | 11 | 2017 | 2016-07-08 | C | 72 | 0.008222 | 0.00021637
1 | 12167621 | 2016-07-08 17:07 | 2016-07-09 15:29 | 1341 | 792 | 46109.0333 | 0.13856 | 0.13142 | 0.0024823 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 756227 | CONDUCTOR - REPAIR/REHANG | Tripping on MRA3 on OC. Feeder patrolled with palm tree branches found over lines on South Rd. Isolation required between ABS 6748 and 484. Backfeed via CB2 at Oakura. Gale winds to dangerous to repair. Line was isolated at ABS's 484, 6748 to repair damaged conductors between poles 756227 & 756228. 10meters - 70mm copper used. 6 X 70mm sleeves used. 2r line patrol 1709 2r repair 1415 | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.13142 | 11 | 2017 | 2016-07-08 | C | 792 | 0.13142 | 0.0024823
1 | 12170104 | 2016-07-08 17:15 | 2016-07-09 14:46 | 1291 | 1 | 1291.7333 | 0.0038819 | 0.003872 | 3.0051e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Tried calling customers cell phone which i received from Genesis but it goes straight to voice mail - 021 4055 48 - will try again soon phone is still going straight to voice mail. 11.21am 9/7 called customer again but cellphone is going to voice mail. Landline number is wrong 11.23am advised Maree at svs hub if we can check this property Recloser going off and on all night due to weather. FM has attended and found full power, explained to customers the situation re. weather and reclosers, advised should settle down with the weather - surveyed and found no network fault. Advised customers if the power fluctuations continue for a length of time to call retailer and log another job. | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.003872 | 11 | 2017 | 2016-07-08 | C | 1 | 0.003872 | 3.0051e-06
1 | 12170264 | 2016-07-08 17:14 | 2016-07-08 20:18 | 183 | 15 | 2754.5 | 0.0082777 | 0.008142 | 4.5077e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8471 | FUSE - ELEMENT/LINK (HV) | Arthur Botha attended this job under 12170093. Replaced 1 x 10A fuse at Fuses 8421 & 2 x 3A fuse at Fuses 8471 | F3 | OAKURA | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.008142 | 11 | 2017 | 2016-07-08 | C | 15 | 0.008142 | 4.5077e-05
1 | 12294140 | 2016-07-10 11:03 | 2016-07-10 12:08 | 65 | 49 | 3204.4 | 0.0096295 | 0.009187 | 0.00014725 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P1405 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Tony Julian has repaired/replaced 1x HV Fuse & Carrier. There is also a blown jumper on 1 of the DDO's at this transformer though. Can not do repairs tonight as needs bucket truck and it is too windy. Will come back tomorrow. 6.25 Customer advised they have lost a phase through the house and out to the implement shed. OMS 12312631 is related. 10/07 0810 Phoned HUB, Glo to phone Tony re this. Replaced 3x HV Drop out fuses and holders at transformer P1405. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.009187 | 11 | 2017 | 2016-07-10 | C | 49 | 0.009187 | 0.00014725
1 | 12294501 | 2016-07-08 18:20 | 2016-07-08 21:05 | 164 | 22 | 3625.9667 | 0.010897 | 0.010698 | 6.6113e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T39 | FUSE - ELEMENT/LINK (HV) | **Please confirm whether related to 2113 Waitahora Road, Dannevirke (OMS 12294387) Replaced 2x 6Amp HV Fuse Links | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.010698 | 11 | 2017 | 2016-07-08 | C | 22 | 0.010698 | 6.6113e-05
1 | 12294780 | 2016-07-08 18:52 | 2016-07-09 12:37 | 1065 | 208 | 34128.8 | 0.10256 | 0.10069 | 0.00062507 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 712392 | CONDUCTOR - REPAIR/REHANG | There is a tree that has come down on the HV lines between ABS 6768, NG302 & NG245. Will be repaired tomorrow. Tree contractors removed trees between ABS's NG 245, NG302 & 6768. 2r line patrol 2005 2r repair 1145 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.10069 | 11 | 2017 | 2016-07-08 | C | 208 | 0.10069 | 0.00062507
1 | 12295967 | 2016-07-08 19:46 | 2016-07-08 22:20 | 153 | 7 | 1077.65 | 0.0032385 | 0.003175 | 2.1036e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8178 | FUSE - ELEMENT/LINK (HV) | Reloaded relivened 2x 8A HV Fuses at 8178. Bad weather in the area at the time. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.003175 | 11 | 2017 | 2016-07-08 | C | 7 | 0.003175 | 2.1036e-05
1 | 12296007 | 2016-07-08 19:53 | 2016-07-09 13:45 | 1071 | 2 | 2143.9 | 0.0064427 | 0.006424 | 6.0103e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | li774 | FUSE - ELEMENT/LINK (HV) | LI774 2 x 10 amp fuses | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.006424 | 11 | 2017 | 2016-07-08 | C | 2 | 0.006424 | 6.0103e-06
1 | 12296832 | 2016-07-08 20:11 | 2016-07-08 22:49 | 157 | 7 | 1104.4833 | 0.0033191 | 0.003256 | 2.1036e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP116 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x HV Fuses at FP116 1x 6A. Bad weather in area at the time. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.003256 | 11 | 2017 | 2016-07-08 | C | 7 | 0.003256 | 2.1036e-05
1 | 12296899 | 2016-07-08 20:17 | 2016-07-09 01:30 | 312 | 1 | 312.7833 | 0.00093996 | 0.00093 | 3.0051e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X310 | CUSTOMER INSTALLATION (ICP) - E.G. METER BOARD | Replaced 2x HV fuse links on same phase at Transformer due to LV fault on service line. Property disconnected by faultman & Transformer & main LV relivened. | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.00093 | 11 | 2017 | 2016-07-08 | C | 1 | 0.00093 | 3.0051e-06
1 | 12297103 | 2016-07-08 20:35 | 2016-07-09 13:08 | 993 | 4 | 3972.9333 | 0.011939 | 0.011903 | 1.2021e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712097 | CONDUCTOR - REPAIR/REHANG | Lines down across road. Pulled up ,lines , due to wind 3 x fuses and holders Paul Fitzpatrick attended initially. Isolated transformer N2160 on HV - will repair lines down tomorrow. LV Lines down. | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.011903 | 11 | 2017 | 2016-07-08 | C | 4 | 0.011903 | 1.2021e-05
1 | 12297625 | 2016-07-08 21:02 | 2016-07-09 20:05 | 1382 | 1 | 1382.7667 | 0.0041554 | 0.004146 | 3.0051e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 8333 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3Amp HV Links | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.004146 | 11 | 2017 | 2016-07-08 | C | 1 | 0.004146 | 3.0051e-06
1 | 12298602 | 2016-07-08 21:21 | 2016-07-08 23:12 | 111 | 6 | 97.85 | 0.00029405 | 0.000239 | 3.0051e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC5330 | FUSE - ELEMENT/LINK (HV) | Wayne Seath Attended. Reloaded, Relivened 2x 2A HV Fuses at Transformer TC5330. Bad weather in the area at the time. See child job for outage. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.000239 | 11 | 2017 | 2016-07-08 | C | 6 | 0.000239 | 3.0051e-06
1 | 12298961 | 2016-07-08 21:31 | 2016-07-09 11:15 | 824 | 1 | 824 | 0.0024762 | 0.002467 | 3.0051e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711491 | CONDUCTOR - REPAIR/REHANG | Floating conductors past Fuses NG271. Paul Fitzpatrick attended initially. Needs repairs tomorrow. Job completed and signed off under unknown OMS No. This job was a follow up to OMS 12295903 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.002467 | 11 | 2017 | 2016-07-08 | C | 1 | 0.002467 | 3.0051e-06
1 | 12299296 | 2016-07-08 21:38 | 2016-07-08 22:36 | 58 | 103 | 3033.7667 | 0.0091169 | 0.008188 | 0.00030953 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 264/2 | CONDUCTOR - REPAIR/REHANG | at 21:37, Oakura Sub, CB 2 Moturoa 3 Feeder, Tripped, Ph A B C O/C, L/O. Known fault in this area from palm tree branches falling onto lines. OAK 2 was partially backfeeding MRA 3 due to this issue. NOC Opened Sw/gear 264/2 & Closed OAK 2 at 21:53. Line checked by faultman - All OK. Closed Sw/gear 264/2 at 22:36. No Materials - ongoing issue to be fixed tomorrow. | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.008188 | 11 | 2017 | 2016-07-08 | C | 103 | 0.008188 | 0.00030953
1 | 12299418 | 2016-07-08 21:41 | 2016-07-08 23:30 | 108 | 2 | 217.2333 | 0.00065282 | 0.000634 | 6.0103e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | O97 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 5Amp HV Fuse Links | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000634 | 11 | 2017 | 2016-07-08 | C | 2 | 0.000634 | 6.0103e-06
1 | 12300063 | 2016-07-08 21:23 | 2016-07-09 13:23 | 960 | 295 | 43640.9167 | 0.13115 | 0.12849 | 0.0016498 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Cause of auto reclosing was from fault on OMS 12298617 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.12849 | 11 | 2017 | 2016-07-08 | C | 295 | 0.12849 | 0.0016498
1 | 12301379 | 2016-07-08 21:54 | 2016-07-08 23:42 | 108 | 258 | 192.7167 | 0.00057914 | 0 | 9.0154e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC2379 | JUMPER | at 21:53, Tairua Sub, CB 3 Hikuai Feeder, Recloser 9643, Tripped, A + B O/C, Auto Reclosed. Calls came in of Part Power/No Powers beyond Recloser 9643. Faultman dispatched, investigation began. Duty NC advised Faultman that he believed the fault was probably HV due to the Auto Reclose & due to Sectionaliser 9787 & 9860 having AC Mains Fail Alarms up. Faultman found a blown jumper between Recloser 9643 & Links 9643/6. Bypassed Recloser and Opened links to isolate blown jumper. Full Power Restored on Completion. Steve Johnson Attended. DNO: 160709. 2r line patrol 2335 / no repair. | F4 | HIKUAI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-07-08 | C | 258 | 0 | 9.0154e-06
1 | 12302455 | 2016-07-09 01:31 | 2016-07-09 04:26 | 174 | 784 | 50312.3 | 0.15119 | 0.14413 | 0.00528 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701649 | CONDUCTOR - REPAIR/REHANG | at 01:31, Brooklands Sub, CB 7, Tripped, Ph C E/F, L/O. Faultmen dispatched & investigation began. Feeder patrolled & sectionalised. Backfeed supplied from MRA 9: Opened ABS 400, Closed ABS 393. Also backfed from MRA 3: Opened ABS 496, Closed VS 12001. Found lines down beyond Pole 701649. Isolated lines at ABS 370, 353, 496 & 351. Permit issued to create line break to isolate lines down. All Power Restored on completion. No materials used. 2r line patrol 0210 2r repair 0405 | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.14413 | 11 | 2017 | 2016-07-09 | C | 784 | 0.14413 | 0.00528
1 | 12305135 | 2016-07-09 07:01 | 2016-07-09 07:16 | 15 | 891 | 14003.55 | 0.042082 | 0.034049 | 0.0026776 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | V1063 | NONE | CB 7 tripped to L/O - E/F flag. Report from public received of tree branch over line at 475 Albert St Coromandel. Branch removed at pole V1063 via live line hot stick. All supply restored. No line patrol or repair. | F3 | KAPANGA ROAD | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.034049 | 11 | 2017 | 2016-07-09 | C | 891 | 0.034049 | 0.0026776
1 | 12306257 | 2016-07-09 08:01 | 2016-07-09 09:45 | 103 | 2 | 207.9333 | 0.00062487 | 0.000606 | 6.0102e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 850222 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 097 on pole 850222, line was patrolled and faultman found a tree branch touching the line when the wind was blowing from the east, faultman advised customer needs to get tree cut as soon as possible. | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000606 | 11 | 2017 | 2016-07-09 | C | 2 | 0.000606 | 6.0102e-06
1 | 12306296 | 2016-07-09 16:00 | 2016-07-09 16:55 | 55 | 9 | 495 | 0.0014875 | 0.001406 | 2.7046e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 704912 | CONDUCTOR - REPAIR/REHANG | Faultman found line down past Fuses 6803 at pole 704912, line was isolated at Fuses 6803. 1 meter Conductor used & 2 X sleeves used. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.001406 | 11 | 2017 | 2016-07-09 | C | 9 | 0.001406 | 2.7046e-05
1 | 12312807 | 2016-07-09 12:56 | 2016-07-09 13:40 | 44 | 6 | 264 | 0.00079335 | 0.000739 | 1.8031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP964 | JUMPER | Line isolated at fuses FC2407 to replace blown jumper at fuses FP964 1 x HV jumper repaired. 1 x connector only material required. All supply restored on completion of repairs. | F4 | WAOTU | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000739 | 11 | 2017 | 2016-07-09 | C | 6 | 0.000739 | 1.8031e-05
1 | 12313647 | 2016-07-09 11:12 | 2016-07-09 20:45 | 573 | 1 | 573.4833 | 0.0017234 | 0.001714 | 3.0051e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | LI741 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6Amp HV Fuse Links | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.001714 | 11 | 2017 | 2016-07-09 | C | 1 | 0.001714 | 3.0051e-06
1 | 12314444 | 2016-07-09 13:06 | 2016-07-09 18:24 | 317 | 1 | 317.7 | 0.00095473 | 0.000945 | 3.0051e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 8178 | FUSE - ELEMENT/LINK (HV) | Check 505 MAUDE ROAD - 12318290 is related Replaced 2x 8Amp HV Fuse Links | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000945 | 11 | 2017 | 2016-07-09 | C | 1 | 0.000945 | 3.0051e-06
1 | 12316442 | 2016-07-09 08:54 | 2016-07-09 16:18 | 444 | 19 | 8442.0167 | 0.025369 | 0.025198 | 5.7097e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 850647 | JUMPER | Faultman found a broken jumper at Fuses 6950 at pole 850647, line was isolated at ABS's MA415, MA579 to repair the jumper. Materials Used: 1 X 16mm Jumper replaced. 1 X non tension joint used. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.025198 | 11 | 2017 | 2016-07-09 | C | 19 | 0.025198 | 5.7097e-05
1 | 12317862 | 2016-07-09 17:15 | 2016-07-09 17:44 | 28 | 280 | 8054.6667 | 0.024205 | 0.02168 | 0.00084143 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 203673 | FUSE - ELEMENT/LINK (HV) | 12315859 linked. 3:45pm HV cutout needs to be replaced. Have talked to Control. requested 2R - but only 1 fuse to be replaced. Advised will be tidied up at invoicing if 2R work | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.02168 | 11 | 2017 | 2016-07-09 | C | 280 | 0.02168 | 0.00084143
1 | 12318722 | 2016-07-09 19:15 | 2016-07-09 23:30 | 254 | 9 | 2292.3 | 0.0068886 | 0.006807 | 2.7046e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TE6-053 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Blown fuses at Transformer TE6-053 and Fuses SE6-002. 1 x New Transformer. 4 x 3A HV Fuses | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.006807 | 11 | 2017 | 2016-07-09 | C | 9 | 0.006807 | 2.7046e-05
1 | 12318854 | 2016-07-09 19:50 | 2016-07-10 16:57 | 1266 | 4 | 5066.6667 | 0.015226 | 0.015189 | 1.202e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P59 | CROSSARM - ARM ONLY | See OMS 12316048 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.015189 | 11 | 2017 | 2016-07-09 | C | 4 | 0.015189 | 1.202e-05
1 | 12319479 | 2016-07-09 21:07 | 2016-07-10 01:15 | 247 | 367 | 22128.4167 | 0.066499 | 0.063189 | 0.0011029 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 842518 | BINDER | CB WH2 A/R, L/O, No Flags. Sectionalised & Patrolled with backfeeds installed via ABS LI704 & ABS 6567. Conductor sitting on crossarm found due to broken binder. Materials used: 1x ali binder 2r Line patrol 2142 2r repair 2356 | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.063189 | 11 | 2017 | 2016-07-09 | C | 367 | 0.063189 | 0.0011029
1 | 12321668 | 2016-07-10 03:16 | 2016-07-10 11:04 | 467 | 427 | 68285.6667 | 0.20521 | 0.20136 | 0.0036692 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC3-110 | CABLE - REPAIR | at 03:16, Omokoroa Sub, CB 4 Omokoroa Rd Feeder, Recloser 9674 Tripped, E/F, L/O. Faultmen dispatched & investigation began. Feeder sectionalised. Found cable between Fused ABS SC3-029 and Transformer TC3-110 had faulted. Isolated Cable at Fused ABS SC3-029. Generator connected to supply TC3-110. Multiple permits issued to test and carry out repairs on cable. 13/07/16 All repairs completed and Supply Restored. 1x ABS, 3x HV Fuses & Holders Replaced, 1x 11kV Jointing Kit Used. Ongoing backfed via generator atTC3110 | F3 | OMOKOROA RD | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.20136 | 11 | 2017 | 2016-07-10 | C | 427 | 0.20136 | 0.0036692
1 | 12324099 | 2016-07-10 13:08 | 2016-07-10 16:19 | 191 | 1 | 191.25 | 0.00057472 | 0.000565 | 3.005e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E49 | FUSE - ELEMENT/LINK (HV) | Replaed 2x 2a HV fuses @E49 NDR 300212 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.000565 | 11 | 2017 | 2016-07-10 | C | 1 | 0.000565 | 3.005e-06
1 | 12324448 | 2016-07-10 16:20 | 2016-07-10 16:25 | 4 | 507 | 2286.7 | 0.0068718 | 0.002301 | 0.0015236 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | PC100 | NONE | PC 100 at Walton sub tripped. Supply lost to T1 side of Waharoa bus. Restored via T2. Line patrolled as much as visible from road. Nothing found. PC100 reclosed sucessfully. T1 at Waharoa left off load until later in night in case of further tripping. No 2r line patrol all power restored in one go | S3 | WALTON-WAHAROA 33KV | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.002301 | 33 | 2017 | 2016-07-10 | C | 507 | 0.002301 | 0.0015236
1 | 12325514 | 2016-07-12 09:26 | 2016-07-12 14:20 | 294 | 4 | 1176 | 0.0035339 | 0.003497 | 1.202e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/356 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman advised transformer T8/356 needs to be replaced in morning. | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.003497 | 11 | 2017 | 2016-07-12 | C | 4 | 0.003497 | 1.202e-05
1 | 12326582 | 2016-08-05 10:00 | 2016-08-05 11:00 | 60 | 2 | 120 | 0.00036051 | 0.000342 | 6.0085e-06 | NAPA ID:21934 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11.00000000 | Planned | 021934 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1948 | NONE | To install 400V Fuses on TP1948. Works location: Matai Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000171 | 5.5 | 2017 | 2016-08-05 | B | 2 | 0.000342 | 6.0085e-06
1 | 12331983 | 2016-08-02 10:10 | 2016-08-02 15:24 | 314 | 34 | 10676 | 0.032075 | 0.031768 | 0.00010215 | NAPA ID:21614 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | 021614 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | NG201 | NONE | Pole replacement project Opourapa Road. Works location: Opourapa Rd. WO 30027682 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.015884 | 5.5 | 2017 | 2016-08-02 | B | 34 | 0.031768 | 0.00010215
1 | 12332187 | 2016-07-19 08:30 | 2016-07-19 16:25 | 475 | 178 | 48238 | 0.14495 | 0.14334 | 0.00053486 | NAPA ID:21029 TP_MT MAUNGANUI 33 GXP > OMANU SUB | 11 | Planned | 021029 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ple 214203 | NONE | 1/ INSTALL LL GAP AT POLE # 214203. 2/ RE-POLE AND RECON FEEDER CONNECT GEN SET UP AT TX TC4-307 [ LV SIDE FUSES ONLY ]. 3/ REMOVE LL GAP AT POLE #214203. Works location: Links Ave, Mt Maunganui. WO 30019228 | F3 | GOLF RD | MT MAUNGANUI 31 | Tauranga | OMANU SUB | Eastern Electricity | POWERCO | 0.071671 | 5.5 | 2017 | 2016-07-19 | B | 178 | 0.14334 | 0.00053486
1 | 12332249 | 2016-08-09 09:26 | 2016-08-09 15:45 | 379 | 22 | 8338 | 0.025049 | 0.02485 | 6.6091e-05 | NAPA ID:21621 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | 021621 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | NG201 | NONE | Pole replacement project Opourapa Road. Works location: Opourapa Rd. WO 30027682 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.012425 | 5.5 | 2017 | 2016-08-09 | B | 22 | 0.02485 | 6.6091e-05
1 | 12332455 | 2016-08-16 09:15 | 2016-08-16 14:24 | 309 | 22 | 6798 | 0.020421 | 0.020222 | 6.6086e-05 | NAPA ID:21625 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | 021625 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS NG201 | NONE | Pole replacement project Opourapa Road. Works location: Opourapa Rd. WO 30027682 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.010111 | 5.5 | 2017 | 2016-08-16 | B | 22 | 0.020222 | 6.6086e-05
1 | 12332694 | 2016-08-23 09:15 | 2016-08-23 15:33 | 378 | 12 | 4536 | 0.013625 | 0.013516 | 3.6044e-05 | NAPA ID:21628 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | 021628 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS NG479 | NONE | Pole replacement project Opourapa Road. Works location: Opourapa Rd. WO 30027682 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.006758 | 5.5 | 2017 | 2016-08-23 | B | 12 | 0.013516 | 3.6044e-05
1 | 12333003 | 2016-08-25 09:15 | 2016-08-25 14:40 | 325 | 12 | 3900 | 0.011714 | 0.011606 | 3.6044e-05 | NAPA ID:21630 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | 021630 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | NG479 | NONE | Pole replacement project Opourapa Road. Works location: Opourapa Rd. WO 30027682 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.005803 | 5.5 | 2017 | 2016-08-25 | B | 12 | 0.011606 | 3.6044e-05
1 | 12333152 | 2016-08-01 08:30 | 2016-08-01 16:30 | 480 | 8 | 3840 | 0.011537 | 0.011464 | 2.4035e-05 | NAPA ID:21653 TP_MASTERTON GXP > GLADSTONE SUB > LONGBUSH | 11 | Planned | 021653 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 823550 | NONE | Tree removal between poles 823550 823552. Works location: Longbush Rd. WO 30026281 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.005732 | 5.5 | 2017 | 2016-08-01 | B | 8 | 0.011464 | 2.4035e-05
1 | 12334125 | 2016-07-11 11:47 | 2016-07-11 12:59 | 72 | 53 | 3816 | 0.011467 | 0.010989 | 0.00015927 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1276 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Following fault during the weekend, Lucas Grant upgraded 100kVA transformer T1276 to 200kVA and upgrade 400V fusing to 200A | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.010989 | 11 | 2017 | 2016-07-11 | C | 53 | 0.010989 | 0.00015927
1 | 12334329 | 2016-07-28 09:34 | 2016-07-28 16:03 | 389 | 21 | 8169 | 0.024544 | 0.024354 | 6.3095e-05 | NAPA ID:19405 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 019405 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-002 | NONE | Replace poles, hardware and conductors between SE3-002 & TEMP65 Install TEMP85 DOF's with solid links on pole 217685. Works location: Poripori Rd. WO 30017844. OMS 12659152 created due to no scada key to ABS temp 65, so was open when parallel ABS opened. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.012177 | 5.5 | 2017 | 2016-07-28 | B | 21 | 0.024354 | 6.3095e-05
1 | 12334341 | 2016-08-01 10:20 | 2016-08-01 15:05 | 285 | 16 | 4560 | 0.0137 | 0.013555 | 4.807e-05 | NAPA ID:21789 TP_MANGAMAIRE GXP > PARKVILLE SUB > RONGOKOKAKO | 11 | Planned | 021789 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T8/385 | NONE | To change 11kV poles change transformer cross arms at T8/385 and run new LV conductor. Works location: Morgans Rd. WO 30029304 | F4 | RONGOKOKAKO | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.0067775 | 5.5 | 2017 | 2016-08-01 | B | 16 | 0.013555 | 4.807e-05
1 | 12334701 | 2016-07-09 18:00 | 2016-07-09 19:20 | 80 | 3 | 146 | 0.00043875 | 0.000411 | 9.0153e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | plz check if oms 12313563 is related Replaced 2x 6Amp Links & 2x 3Amp Links | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.000411 | 11 | 2017 | 2016-07-09 | C | 3 | 0.000411 | 9.0153e-06
1 | 12335977 | 2016-08-01 09:46 | 2016-08-01 14:45 | 299 | 18 | 5382.9 | 0.016172 | 0.01601 | 5.4079e-05 | NAPA ID:22227 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 022227 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11081 | NONE | Renew 11kV strain arms and add new 11kV Fuses 11081 on pole 831980 to network. Works location: Hwy 2, Masterton. WO 30027447 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.008005 | 5.5 | 2017 | 2016-08-01 | B | 18 | 0.01601 | 5.4079e-05
1 | 12336062 | 2016-08-01 09:30 | 2016-08-01 11:45 | 134 | 336 | 25914.65 | 0.077858 | 0.074829 | 0.0015593 | NAPA ID:21667 TP_CARRINGTON GXP > KATERE SUB > KATERE 12 | 11 | Planned | 021667 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 204 | NONE | Replace Magnefix 204/3 fuse caps and clean cable terms. Switching (-01) is to remotely isolate supply to ISOLATE @ magnefix 385/1. Switching (-01) is to remotely isolate supply to RESTORE @ magnefix 385/1. Works location: Erica Place. WO 30015277 | F2 | KATERE 12 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.037415 | 5.5 | 2017 | 2016-08-01 | B | 336 | 0.074829 | 0.0015593
1 | 12336839 | 2016-08-02 09:00 | 2016-08-02 15:03 | 363 | 61 | 22143 | 0.066526 | 0.065976 | 0.00018327 | NAPA ID:21660 TP_BUNNYTHORPE GXP > FEILDING SUB > COLYTON | 11 | Planned | 021660 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | E22 | NONE | Replace 11kV crossarms. Works location: Reids Line East. WO 30025498 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.032988 | 5.5 | 2017 | 2016-08-02 | B | 61 | 0.065976 | 0.00018327
1 | 12336844 | 2016-08-04 09:29 | 2016-08-04 15:19 | 350 | 22 | 7700 | 0.023133 | 0.022934 | 6.6095e-05 | NAPA ID:21618 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | 021618 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | NG201 | NONE | Pole replacement project Opourapa Road. Works location: Orourapa Rd. WO 30027682 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.011467 | 5.5 | 2017 | 2016-08-04 | B | 22 | 0.022934 | 6.6095e-05
1 | 12336858 | 2016-08-04 09:00 | 2016-08-04 15:02 | 362 | 61 | 22082 | 0.066341 | 0.065791 | 0.00018326 | NAPA ID:21661 TP_BUNNYTHORPE GXP > FEILDING SUB > COLYTON | 11 | Planned | 021661 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | E22 | NONE | Replace 11kV crossarms. Works location: Reids Line East. WO 30025498 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.032896 | 5.5 | 2017 | 2016-08-04 | B | 61 | 0.065791 | 0.00018326
1 | 12338819 | 2016-08-02 09:15 | 2016-08-02 14:58 | 343 | 4 | 1372 | 0.004122 | 0.004085 | 1.2017e-05 | NAPA ID:22160 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | 022160 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P30081 | NONE | Straighten leaning poles and re-sag conductors on poles P30081,P30080,P00798. Works location: McLeod Rd, Akitio. WO 30026320 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.0020425 | 5.5 | 2017 | 2016-08-02 | B | 4 | 0.004085 | 1.2017e-05
1 | 12338838 | 2016-08-11 09:23 | 2016-08-11 15:08 | 345 | 22 | 7590 | 0.022801 | 0.022602 | 6.609e-05 | NAPA ID:21623 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | 021623 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS NG201 | NONE | Pole replacement project Opourapa Road. Works location: Opourapa Rd. WO 30027682 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.011301 | 5.5 | 2017 | 2016-08-11 | B | 22 | 0.022602 | 6.609e-05
1 | 12338962 | 2016-08-02 08:30 | 2016-08-02 11:45 | 195 | 1 | 195 | 0.00058585 | 0.000576 | 3.0043e-06 | NAPA ID:21654 TP_MASTERTON GXP > GLADSTONE SUB > LONGBUSH | 11 | Planned | 021654 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 7418 | NONE | Tree removal longbush road. Works location: Longbush Rd. WO 30026281 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000288 | 5.5 | 2017 | 2016-08-02 | B | 1 | 0.000576 | 3.0043e-06
1 | 12339359 | 2016-08-03 09:03 | 2016-08-03 14:31 | 328 | 29 | 9512 | 0.028577 | 0.028315 | 8.7126e-05 | NAPA ID:21615 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | 021615 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 785919 | NONE | Isolation of 11kV line for Treescape, work area between poles 785919 , 785926 , 785921. Works location: Ruanui Rd, Taihape. WO 30026260 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.014157 | 5.5 | 2017 | 2016-08-03 | B | 29 | 0.028315 | 8.7126e-05
1 | 12339424 | 2016-08-03 09:30 | 2016-08-03 11:30 | 120 | 1 | 120 | 0.00036052 | 0.000351 | 3.0043e-06 | NAPA ID:21867 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | 021867 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T1/477 | NONE | Replace 11KV Transformer & Transformer arms T1/477. Works location: Tangimoana Rd. WO 10162827 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.0001755 | 5.5 | 2017 | 2016-08-03 | B | 1 | 0.000351 | 3.0043e-06
1 | 12339452 | 2016-08-03 11:01 | 2016-08-03 14:34 | 213 | 5 | 1065.4167 | 0.0032009 | 0.003155 | 1.5022e-05 | NAPA ID:21904 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | 021904 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2888 | NONE | Replace all cross arms on transformer pole X2191. Works location: Hwy 3, Waverley. WO 30027340 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.0015775 | 5.5 | 2017 | 2016-08-03 | B | 5 | 0.003155 | 1.5022e-05
1 | 12340646 | 2016-07-11 22:22 | 2016-07-12 09:39 | 676 | 158 | 35717.3167 | 0.10733 | 0.10591 | 0.00057998 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 229121 | CONDUCTOR - REPAIR/REHANG | Recloser 9556/2 on Pongakawa CB 3 feeder tripped to L/O. E/F & O/C flags. Line patrolled & sectionalised. Fault is between ABS SF7-025 & fuses SG7-003. Further patrolling unpracticle due to terrain, bush and darkness. Further patrolling to resume at daybreak. Lines down at pole 229121. Isolation at ABS SF7-025. Repaired lines. 18maters namu conductor 6xtension sleeves | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.10591 | 11 | 2017 | 2016-07-11 | C | 158 | 0.10591 | 0.00057998
1 | 12342542 | 2016-07-12 06:03 | 2016-07-12 07:36 | 93 | 2669 | 174356 | 0.52395 | 0.49989 | 0.0080205 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | t2 tapchanger | TRANSFORMER - POWER TRANSFORMER (HV) | Check OMS: 12347158 - 71 HEDGES STREET Caused by T2 Tap Changer ( 2nd time ) Ken Pattie was informed Tech ( Steve Morris ) has pushed the Trip times out to 25 sec from 20 secs | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.49989 | 11 | 2017 | 2016-07-12 | C | 2669 | 0.49989 | 0.0080205
1 | 12347192 | 2016-08-18 09:15 | 2016-08-18 15:12 | 357 | 12 | 4284 | 0.012869 | 0.01276 | 3.6046e-05 | NAPA ID:21626 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | 021626 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | NG479 | NONE | Pole replacement project Opourapa Road. Works location: Opourapa Rd. WO 30027682 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.00638 | 5.5 | 2017 | 2016-08-18 | B | 12 | 0.01276 | 3.6046e-05
1 | 12347538 | 2016-07-12 11:25 | 2016-07-12 11:28 | 3 | 86 | 258 | 0.0007753 | 0 | 0.00025843 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | H106 | FUSE - DROP OUT - REPLACE FULL SET OF FUSES (HV) | Replace 11kV Fuses H106 with 20 Amp fuses. Currently 10's fitted and too small. Also to conduct another line patrol of this line for any faults/issues etc.Planned outage for 11am. ASW - NCTL | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-07-12 | C | 86 | 0 | 0.00025843
1 | 12348939 | 2016-08-01 08:40 | 2016-08-01 14:55 | 375 | 25 | 9375 | 0.028166 | 0.027941 | 7.511e-05 | NAPA ID:22130 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | 022130 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2562 | NONE | Replace cross arms and line hardware. Works location: Te Reinga Owera Rd. WO 30002514 | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.013971 | 5.5 | 2017 | 2016-08-01 | B | 25 | 0.027941 | 7.511e-05
1 | 12349026 | 2016-08-04 08:36 | 2016-08-04 15:25 | 409 | 2 | 818 | 0.0024575 | 0.002439 | 6.0086e-06 | NAPA ID:21609 TP_MASTERTON GXP > GLADSTONE SUB > LONGBUSH | 11 | Planned | 021609 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 823849 | NONE | Tree removal between poles 823849 823850. Works location: Longbush Rd. WO 30026281 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.0012195 | 5.5 | 2017 | 2016-08-04 | B | 2 | 0.002439 | 6.0086e-06
1 | 12349335 | 2016-08-10 09:44 | 2016-08-10 12:42 | 178 | 39 | 6942 | 0.020855 | 0.020503 | 0.00011716 | NAPA ID:22188 TP_BUNNYTHORPE GXP > KIMBOLTON SUB > APITI | 11 | Planned | 022188 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N57 | NONE | Carry out maintenance on sectionaliser test and liven. Works location: Rangiwahia Rd. WO 30021274 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.010252 | 5.5 | 2017 | 2016-08-10 | B | 39 | 0.020503 | 0.00011716
1 | 12349568 | 2016-08-08 09:07 | 2016-08-08 16:07 | 419 | 2 | 839.2333 | 0.0025212 | 0.002503 | 6.0083e-06 | NAPA ID:21786 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | 021786 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | P15165 | NONE | Tree removal. Works location: Clelands Rd. WO 30026290 | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.0012515 | 5.5 | 2017 | 2016-08-08 | B | 2 | 0.002503 | 6.0083e-06
1 | 12349586 | 2016-08-09 09:21 | 2016-08-09 15:47 | 385 | 2 | 771.2 | 0.0023168 | 0.002298 | 6.0083e-06 | NAPA ID:21787 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | 021787 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | P15165 | NONE | Remove trees between pole P15165 & P28641. Works location: Celalands Road, Whangaehu Valley. Work Order: 30026290. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.001149 | 5.5 | 2017 | 2016-08-09 | B | 2 | 0.002298 | 6.0083e-06
1 | 12349806 | 2016-07-12 14:10 | 2016-07-12 15:02 | 52 | 15 | 780 | 0.0023439 | 0.002208 | 4.5076e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781315 | CONDUCTOR - REPAIR/REHANG | Advised SMC and Control. Check if 46 Lower Herengawe Road - OMS 12349815 - is related. 2m conductor | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.002208 | 11 | 2017 | 2016-07-12 | C | 15 | 0.002208 | 4.5076e-05
1 | 12349878 | 2016-07-12 13:33 | 2016-07-12 14:40 | 66 | 2 | 133.9333 | 0.00040248 | 0.000384 | 6.01e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F12773 | FUSE - ELEMENT/LINK (HV) | 2X HV FUSES, FC2149, 3Amps. Caused due to Weather (Been out since last week as only runs electric fence. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000384 | 11 | 2017 | 2016-07-12 | C | 2 | 0.000384 | 6.01e-06
1 | 12349932 | 2016-07-26 10:45 | 2016-07-26 15:30 | 285 | 61 | 17324.9 | 0.052055 | 0.051504 | 0.00018328 | NAPA ID:22495 TP_MARTON GXP > PUKEPAPA SUB > LAKE ALICE | 11 | Planned | 022495 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1104 | NONE | Complete remedial action required for audit issues. Works location: Santoft Rd. WO 30029087 | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.025752 | 5.5 | 2017 | 2016-07-26 | B | 61 | 0.051504 | 0.00018328
1 | 12350102 | 2016-08-09 09:00 | 2016-08-09 14:16 | 316 | 61 | 19276 | 0.057908 | 0.057358 | 0.00018325 | NAPA ID:21662 TP_BUNNYTHORPE GXP > FEILDING SUB > COLYTON | 11 | Planned | 021662 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | E22 | NONE | Replace 11KV crossarms. Works location: Reids Line East. WO 30025498 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.028679 | 5.5 | 2017 | 2016-08-09 | B | 61 | 0.057358 | 0.00018325
1 | 12350412 | 2016-07-13 09:36 | 2016-07-13 13:50 | 254 | 86 | 21844 | 0.065641 | 0.064866 | 0.00025843 | NAPA ID:22577 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 022577 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - ISOLATION FOR SAFETY | H106 | NONE | Cut trees out of 11KV line | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.032433 | 5.5 | 2017 | 2016-07-13 | B | 86 | 0.064866 | 0.00025843
1 | 12350437 | 2016-08-01 09:50 | 2016-08-01 12:40 | 170 | 34 | 5780 | 0.017365 | 0.017059 | 0.00010215 | NAPA ID:21707 TP_PIAKO GXP > PIAKO SUB > MOTUMAOHO | 11 | Planned | 021707 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I0735 | NONE | Pole I10735 - Open ABS 600, and cut jumpers at pole I10735 towards ABS 600 and change top arm at pole I10735. Pole I10735 re-instate cut jumpers. Works location: Hwy 26, Morrinsville. WO 30026849 | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0085295 | 5.5 | 2017 | 2016-08-01 | B | 34 | 0.017059 | 0.00010215
1 | 12350943 | 2016-07-12 18:46 | 2016-07-12 19:55 | 69 | 4 | 276.1333 | 0.00082979 | 0.000793 | 1.202e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1666 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp HV fuses replaced at fuses FP1666. Suspected goose strike | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.000793 | 11 | 2017 | 2016-07-12 | C | 4 | 0.000793 | 1.202e-05
1 | 12351962 | 2016-07-12 21:38 | 2016-07-13 00:28 | 169 | 301 | 51104.7833 | 0.15357 | 0.15086 | 0.00090452 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 209957 | CONDUCTOR - REPAIR/REHANG | Line down located at pole 209957. Had not made contact with ground but suspended on hedge on side of road. Line isolated at ABS 9560 & links 9560/6 to carry out repairs. All supply restored following repairs. 10 metres Al conductor & 2 compression sleeves material required. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.15086 | 11 | 2017 | 2016-07-12 | C | 301 | 0.15086 | 0.00090452
1 | 12354733 | 2016-07-13 08:44 | 2016-07-13 11:46 | 182 | 33 | 6006 | 0.018048 | 0.01775 | 9.9165e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781598 | CONDUCTOR - REPAIR/REHANG | 7.39am Advised James that we have received a no power job at OMS 12354748 670 Ihupuku Road Waverley tx X864 - so there could be a fault at fuses 2719? - also OMS 12357472 part power. Lines down found. Lines repaired 30mtr conductor, 3 x sleeves, 3 x 30 amp fuses. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.01775 | 11 | 2017 | 2016-07-13 | C | 33 | 0.01775 | 9.9165e-05
1 | 12355097 | 2016-07-13 08:00 | 2016-07-13 10:26 | 145 | 287 | 28372.8167 | 0.08526 | 0.082673 | 0.0019623 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715591 | BINDER | CB TA9 a/r e/f. Multiple auto recloses line patrol.CB9 tripped on Deft. Time EF. Feeder patrolled / sectionalised with a conductor found off an insulator beyond fuses TA994. Repairs carried out with only one binder required. Relivened OK. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.082673 | 11 | 2017 | 2016-07-13 | C | 287 | 0.082673 | 0.0019623
1 | 12359267 | 2016-07-13 10:14 | 2016-07-13 13:00 | 165 | 2061 | 68979.75 | 0.20728 | 0.1887 | 0.0061933 |  | 11 | Unplanned |  | UNDERGROUND CABLE | HUMAN ELEMENT | HUMAN ELEMENT - WORKMANSHIP | N/A - NOT APPLICABLE | CABLE - REPAIR | 11kV CB 24 tripped to lock out at 1014hrs. Cause was due to 11kV cable spiking as part of planned switching 21916 to install Sw/gear 10286. 11kV cable to be spiked should have been the isolated and earthed cable on the FEI CB 22 Makino feeder. Somehow the incorrect cable was identified and then spiked as part of final ID process. Covered Safety manager report 640313. Affected area was isolated and Earthed via Sw/gear G363 and ABS J52. Temp breaks installed at Tfmr's T4/437 and T3/424 to alow these assets to be relivened at 1247hrs. Mutually agreed between Downer and Powerco CIW team to install Sw/gear 10286 on the spiked cable. Urgent SCADA change sent through to NOC and duly carried out. Section of Makino feeder originally shut down was returned to service. Switch gear install completed, Downer to lodge another NAPA to liven and commission new sw/gear 10286. | F3 | DENBIGH | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.1887 | 11 | 2017 | 2016-07-13 | C | 2061 | 0.1887 | 0.0061933
1 | 12361338 | 2016-08-04 08:50 | 2016-08-04 10:42 | 112 | 81 | 8942.3667 | 0.026866 | 0.026135 | 0.00024335 | NAPA ID:22190 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > PAPAMOA BEACH WEST | 11 | Planned | 022190 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TD5-253 | NONE | Isolate transformer so as to investigate leaking bushing. Works location: Cornith Ave. WO 30026220 | F2 | GRAVATT RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.013067 | 5.5 | 2017 | 2016-08-04 | B | 81 | 0.026135 | 0.00024335
1 | 12361592 | 2016-07-13 11:03 | 2016-07-13 11:47 | 44 | 3 | 132 | 0.00039666 | 0.000369 | 9.015e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 710065 | BINDER | Isolation required from Fuses PU250 to repair a broken binder (Conductor off insulator). 2 binders replaced and relivened OK. | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000369 | 11 | 2017 | 2016-07-13 | C | 3 | 0.000369 | 9.015e-06
1 | 12361664 | 2016-07-13 11:13 | 2016-07-13 12:25 | 72 | 4 | 291.1333 | 0.00087486 | 0.000838 | 1.202e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 203606 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses SD4-047 3 x 15A Birds | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000838 | 11 | 2017 | 2016-07-13 | C | 4 | 0.000838 | 1.202e-05
1 | 12362529 | 2016-08-01 10:00 | 2016-08-01 14:05 | 245 | 16 | 3920 | 0.011777 | 0.011633 | 4.807e-05 | NAPA ID:22579 TP_OPUNAKE GXP > PUNGAREHU SUB > PUNGAREHU | 11 | Planned | 022579 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P2150 | NONE | Change transformer P2150 with new transformer plus upgrade low and high tension cross arms as all rotten plus transformer is rusting very badly and we also need to take road off as we will get within our 1 metre with crane. Works location: Cape Rd, Pungarehu. WO 30030429 | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.0058165 | 5.5 | 2017 | 2016-08-01 | B | 16 | 0.011633 | 4.807e-05
1 | 12362559 | 2016-07-28 10:15 | 2016-07-28 12:48 | 153 | 4 | 612 | 0.0018388 | 0.001802 | 1.2018e-05 | NAPA ID:22262 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022262 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2591 | NONE | Replace transformer hanger arms and fit LV fusing. Works location: Glenrowan Rd, Hinuera. WO 30027891 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000901 | 5.5 | 2017 | 2016-07-28 | B | 4 | 0.001802 | 1.2018e-05
1 | 12362793 | 2016-07-28 10:00 | 2016-07-28 11:45 | 105 | 6 | 630 | 0.0018929 | 0.001838 | 1.8027e-05 | NAPA ID:22264 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022264 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC635 | NONE | Replace rotten cross arms at poles E1195,E1773 and fit LV fusing to TC635. Works location: Highway 29, Hinuera. WO 30027891 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000919 | 5.5 | 2017 | 2016-07-28 | B | 6 | 0.001838 | 1.8027e-05
1 | 12362822 | 2016-08-01 08:45 | 2016-08-01 09:47 | 62 | 28 | 1741.6 | 0.0052325 | 0.00498 | 8.4123e-05 | NAPA ID:22356 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 022356 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G0041 | NONE | Replace rotten crossarm at pole G0041. Works location: Matai Rd, Matamata. WO 30027891 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.00249 | 5.5 | 2017 | 2016-08-01 | B | 28 | 0.00498 | 8.4123e-05
1 | 12363012 | 2016-07-13 16:02 | 2016-07-13 16:11 | 9 | 1647 | 12999.6333 | 0.039064 | 0.024216 | 0.0049492 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CST GXP 33kV CB 1092 - Oakura line | UNKNOWN | * 33kV CB 1092 tripped on Earth fault, over current and Neutral overtime to lock out at 16:02hrs. * Resulted in total LOS to Oakura Substation load (1647 ICP's). (Jo/Alicia will need to go to SM please, ASW) * No auto changeover on OKA sub disabled as per note details below. * MRA sub at time well below 14MW limit (approx 8.7MW). * NOC opted to change over OKA manually to MRA (via CB 3) alternative supply. * Final OKA load restored at 16:11hrs. * Ran into loading issues on MRA sub exceeding 14MW and issues with BKL 9 loading's, NOC mitigated with various offloads until 33kV returned to service. * 33kV CST - OKA Line patrolled, no fault found. * Line re-livened at 17:55hrs. OKA load restored to 33kV line at 18:17hrs. * At this stage the line fault cause is unknown. Suggest a full line patrol is carried out. Note: auto changeover disabled due to Moturoa Sub transformer Diff scheme upgrade. MRA sub has offloads in place to deal with load restriction of 14 MVA. As a result the OKA auto changeover scheme had to be disabled for the duration of the project as per engineering advice. MRA diff project to be completed on 14th July. | S1 | CARRINGTON ST1092 OAKURA4162 33KV | CARRINGTON ST 33 | Taranaki | TP_CARRINGTON | Western Electricity | POWERCO | 0.024216 | 33 | 2017 | 2016-07-13 | C | 1647 | 0.024216 | 0.0049492
1 | 12365967 | 2016-07-13 21:24 | 2016-07-14 18:10 | 1245 | 76 | 21435.8 | 0.064415 | 0.063729 | 0.00023139 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 780547 | CONDUCTOR - REPAIR/REHANG | James called to advised unable to get to this location as there are large pine trees fallen across the road. No traffic in or out. Have called customer to advise we will not be able to attend tonight due to this and will contact the council to get tree moved and FM to reattend tomorrow. Customer is happy to be off overnight and understands the situation. Advised the Wanganui Council re tree and address (is approx 10-15kms up the road) - they will attend asap. Tree branch had fallen through lines and bought a wire down on large span. NDR# 41484 Materials used: 140metres of squirrel conductor & 6x conductor joints | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.063729 | 11 | 2017 | 2016-07-13 | C | 76 | 0.063729 | 0.00023139
1 | 12365976 | 2016-07-13 21:26 | 2016-07-13 23:46 | 139 | 1 | 139.8333 | 0.0004202 | 0.000411 | 3.005e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1433 | FUSE - ELEMENT/LINK (HV) | Replaced 2x HV 10a fuses @ 1433 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000411 | 11 | 2017 | 2016-07-13 | C | 1 | 0.000411 | 3.005e-06
1 | 12366266 | 2016-07-13 21:58 | 2016-07-13 22:39 | 41 | 249 | 10271.25 | 0.030865 | 0.02862 | 0.00074825 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | KA7 | UNKNOWN | O/C Waited extra time and due to weather & no faultman being assigned yet . Executed a sucssesful reclose | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.02862 | 11 | 2017 | 2016-07-13 | C | 249 | 0.02862 | 0.00074825
1 | 12366544 | 2016-07-13 22:08 | 2016-07-14 02:06 | 238 | 274 | 46814.5167 | 0.14068 | 0.13821 | 0.00082337 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 831738 | CONDUCTOR - REPAIR/REHANG | Line sectionalised and patrolled found trees down on lines beyond pole 831739 line cutaway and repairs to be carried out in daylight. Tree branches cleared using Hot Stick. Line break at Pole 831739 closed Live Line. Materials used 3x 10mm Cu sleeves. DNO: 21863 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.13821 | 11 | 2017 | 2016-07-13 | C | 274 | 0.13821 | 0.00082337
1 | 12368267 | 2016-07-13 23:12 | 2016-07-14 00:15 | 63 | 1 | 63.1667 | 0.00018982 | 0.00018 | 3.005e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C429 | UNKNOWN | on arrival found CB C429 open . Closed on load | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.00018 | 11 | 2017 | 2016-07-13 | C | 1 | 0.00018 | 3.005e-06
1 | 12368777 | 2016-07-14 00:51 | 2016-07-14 15:51 | 899 | 77 | 35174.2333 | 0.1057 | 0.105 | 0.00044474 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 776395 | BINDER | Update 14/07/ @ 0950hrs. Still off past 6.6kV fuses 6103, very remote country side, may be several hours before the issue located, hence ETR pushed out to 1500. ASW Update @ 1420hrs. Fault crew onsite and advanced power to 6.6kV fuses 6029. ASW. Further patrol carried out morning of Friday 15th. Floating conductor found in remote area. Repaired OK with one binder needed. Fuses 6029 reclosed. (High winds at time). 2R line patrol 0324 / 2R repair 1200. | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.105 | 11 | 2017 | 2016-07-14 | C | 77 | 0.105 | 0.00044474
1 | 12368857 | 2016-07-14 00:52 | 2016-07-14 11:20 | 627 | 256 | 30554.25 | 0.091815 | 0.089507 | 0.00086243 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 742699 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, ALL PHASES | Tripping on recloser 6610 on ABC O/C, E/F. Fault tracked to Lincoln Rd where a large pine tree branch had come down midspan and caused some damage. Isolation initially required between ABS 344 and 350 where a span was removed to allow all feeder to be restored except Transformer 312 (During night) . During the day, another outage was carried out between those 2 ABSs to initiate repairs. This included straightening 2 poles and replacing 1 span of 3 phase conductors. Relivened OK. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.089507 | 11 | 2017 | 2016-07-14 | C | 256 | 0.089507 | 0.00086243
1 | 12371166 | 2016-07-14 02:08 | 2016-07-14 12:32 | 624 | 238 | 15115.5333 | 0.045422 | 0.043276 | 0.00073021 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 790818 | CROSSARM - WHOLE ASSEMBLY | Fallen tree broke end off of crossarm. Temp repairs made and relivened. Materials used 1x HV Pin & Insulator. 1x Binder. NDR# 47303 | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.043276 | 11 | 2017 | 2016-07-14 | C | 238 | 0.043276 | 0.00073021
1 | 12371419 | 2016-07-14 02:40 | 2016-07-14 04:52 | 132 | 17 | 2244 | 0.0067432 | 0.006589 | 5.1085e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 723168 | CONDUCTOR - REPAIR/REHANG | Lines in trees Reported by fire comms REF:- F2114018 Rebound conductor on pole 723168 | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.006589 | 11 | 2017 | 2016-07-14 | C | 17 | 0.006589 | 5.1085e-05
1 | 12371576 | 2016-07-14 04:00 | 2016-07-14 07:18 | 198 | 125 | 20930.5 | 0.062896 | 0.061768 | 0.00075124 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 821115 | CONDUCTOR - REPAIR/REHANG | Cb C 429 found open Removed trees from lines at pole 821115. NDR 37768 | F3 | TAVERNER ST | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.061768 | 11 | 2017 | 2016-07-14 | C | 125 | 0.061768 | 0.00075124
1 | 12371589 | 2016-07-14 04:20 | 2016-07-14 06:55 | 155 | 340 | 36973.3333 | 0.1111 | 0.10804 | 0.0010217 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | cb6 | UNKNOWN | CB 6 Trip B & C Phase O/C | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.10804 | 11 | 2017 | 2016-07-14 | C | 340 | 0.10804 | 0.0010217
1 | 12373143 | 2016-07-14 06:00 | 2016-07-14 08:01 | 120 | 903 | 30658.3 | 0.092128 | 0.083987 | 0.0027135 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 3086 | UNKNOWN | Backfed Rata Sub. Delays due to Scada controls not working & excessive workload. 33kV patrolled with no fault found. Relivened ok. Suspect wind blown debris. Feeders restored to normal configuration. | S4 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 0.083987 | 33 | 2017 | 2016-07-14 | C | 903 | 0.083987 | 0.0027135
1 | 12374699 | 2016-07-14 06:29 | 2016-07-14 09:44 | 194 | 226 | 25966.1167 | 0.078028 | 0.07599 | 0.00067913 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T21 | UNKNOWN | CB T21 tripped E/F patrolled nothing found. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.07599 | 11 | 2017 | 2016-07-14 | C | 226 | 0.07599 | 0.00067913
1 | 12374930 | 2016-07-14 09:40 | 2016-07-14 11:30 | 110 | 27 | 2970 | 0.0089248 | 0.008681 | 8.1134e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 734469 | CONDUCTOR - REPAIR/REHANG | Outage required from fuses 5621 to repair a broken conductor, Repair / rehang carried out with 2 sleeves needed. Relivened OK. Windy during night, conductor in poor condition. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.008681 | 11 | 2017 | 2016-07-14 | C | 27 | 0.008681 | 8.1134e-05
1 | 12374940 | 2016-07-14 06:32 | 2016-07-14 19:06 | 754 | 145 | 32955.5333 | 0.099031 | 0.097723 | 0.00086543 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 227725 | POLE | at 06:31, Pongakawa Sub, CB 2 Otamarakau Feeder, Recloser S6029 Tripped, A B C O/C, E/F, L/O. Faultmen dispatched & investigation began. Customer called in of lines down on Otamarakau Rd. Faultman found lines down & poles down on Otamarakau Rd. Isolated Lines at ABS SE8-013, ABS 9679/1 & Links 9679/4. Permit issued & repairs carried out. Relivened, tripped, line patrolled & sectionalised past first site, Fuses FP1136 Opened. Fault past fuses left off over night due to lines through forestry. Material 3x1mm poles, 3 crossarms, 100meters kutu conductor, numerious sleeves NDR 048483 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.097723 | 11 | 2017 | 2016-07-14 | C | 145 | 0.097723 | 0.00086543
1 | 12375431 | 2016-07-14 07:11 | 2016-07-14 10:00 | 168 | 17 | 2732.2833 | 0.0082105 | 0.008057 | 5.1085e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 373136 | FUSE - ELEMENT/LINK (HV) | Plz check oms 12376941 and OMS: 12379624 - 115 PAKIHI ROAD Gum Bark sitting on lines. Removed with Hot Stick. Replaced 2x 8Amp HV Links | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.008057 | 11 | 2017 | 2016-07-14 | C | 17 | 0.008057 | 5.1085e-05
1 | 12375630 | 2016-07-14 07:30 | 2016-07-14 11:22 | 232 | 39 | 9052.55 | 0.027203 | 0.026851 | 0.00011719 |  | 6.6 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 782618 | FUSE - ELEMENT/LINK (HV) | Removed branch from lines using hot stick at pole 782618. Replaced 2x 10Amp Links | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.026851 | 6.6 | 2017 | 2016-07-14 | C | 39 | 0.026851 | 0.00011719
1 | 12375647 | 2016-07-14 07:30 | 2016-07-14 08:47 | 76 | 22 | 1687.7667 | 0.0050717 | 0.004873 | 6.6109e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 569 | CONDUCTOR - REPAIR/REHANG | Tree down through lines. Lines down. Materials used: 6x 16mm Cu sleeves, 20m of 16mm Cu. 2x 10 Amp HV Links NDR# 22328 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.004873 | 11 | 2017 | 2016-07-14 | C | 22 | 0.004873 | 6.6109e-05
1 | 12375664 | 2016-07-14 07:33 | 2016-07-14 10:00 | 147 | 6 | 883.7 | 0.0026555 | 0.002601 | 1.803e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13184 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp fuse bird strike | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.002601 | 11 | 2017 | 2016-07-14 | C | 6 | 0.002601 | 1.803e-05
1 | 12376662 | 2016-07-14 09:15 | 2016-07-14 12:46 | 211 | 66 | 13926 | 0.041847 | 0.041252 | 0.00019833 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771842 | CONDUCTOR - REPAIR/REHANG | 7.49am advised at svs hub & emailed & advised control. Repaired 1x Line Down. Materials used: 2x Squirrel sleeves, 1x Ali conductor joint, 4mtrs of squirrel conductor, 1x Heli Tie. Outage from Fuses 1257. | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.041252 | 11 | 2017 | 2016-07-14 | C | 66 | 0.041252 | 0.00019833
1 | 12376941 | 2016-07-14 08:04 | 2016-07-14 12:02 | 238 | 1 | 238.1333 | 0.00071559 | 0.000706 | 3.0049e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 373136 | FUSE - ELEMENT/LINK (HV) | OMS 12375431 has been completed a fm replaced 2x 8amp hv fuses - called customer to confirm if customers power restored? customer has full power completed job the same | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.000706 | 11 | 2017 | 2016-07-14 | C | 1 | 0.000706 | 3.0049e-06
1 | 12377077 | 2016-07-14 14:40 | 2016-07-14 22:27 | 467 | 3 | 1401 | 0.00421 | 0.004182 | 9.0149e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 716035 | CROSSARM - WHOLE ASSEMBLY | Floating conductor and broken cross arm. Have spoken to the SMC and advised we need to go back to the property and confirm whether the cross arm is the cause of no power and if so what can we do to restore power until the cross arm is replaced tomorrow. Materials used: 1 X Cross arm 3 X HT Insulators. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.004182 | 11 | 2017 | 2016-07-14 | C | 3 | 0.004182 | 9.0149e-06
1 | 12377120 | 2016-07-14 15:20 | 2016-07-14 16:55 | 95 | 1 | 95 | 0.00028547 | 0.000276 | 3.0049e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | M3270 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer M3270 replaced (OMS No. at wrong Transformer 5576E). Also replaced LV Pins and insulators at Pole 718844. Transformer M3270 also has 1 * 3A HV fuse replaced and 1 * 100A HRC LV fuse. | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.000276 | 11 | 2017 | 2016-07-14 | C | 1 | 0.000276 | 3.0049e-06
1 | 12377795 | 2016-07-14 08:41 | 2016-07-14 15:02 | 380 | 2 | 761.4 | 0.002288 | 0.002269 | 6.0099e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 2704 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6Amp HV Links | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.002269 | 11 | 2017 | 2016-07-14 | C | 2 | 0.002269 | 6.0099e-06
1 | 12378010 | 2016-07-14 08:44 | 2016-07-14 10:05 | 81 | 168 | 13700.4 | 0.041169 | 0.039654 | 0.00050484 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 224101 | CONDUCTOR - REPAIR/REHANG | at 08:43, Paengaroa Sub, CB 1 Gulliver Rd Feeder, Recloser 9460 Tripped, E/F, L/O. Faultmen dispatched and investigation began. Customer called in of sparking lines on Otamarakau Rd. NOC Advised faultman. Faultman found tree branch on lines at Pole 224101. Knocked branch off lines with hot stick. All Power Restored on Completion. Shay Deegan Attended. No Materials Used. | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.039654 | 11 | 2017 | 2016-07-14 | C | 168 | 0.039654 | 0.00050484
1 | 12378901 | 2016-07-14 18:22 | 2016-07-14 19:24 | 62 | 35 | 2170 | 0.0065208 | 0.006205 | 0.00010517 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711448 | CROSSARM - WHOLE ASSEMBLY | 1R Please carryout repairs on twisted cross arm Pole 711448 (Noted by Contractor)South Rd just past Rahotu Rd Rebolted Cross arm. | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.006205 | 11 | 2017 | 2016-07-14 | C | 35 | 0.006205 | 0.00010517
1 | 12378977 | 2016-08-04 09:20 | 2016-08-04 12:10 | 170 | 40 | 6800 | 0.020429 | 0.020068 | 0.00012017 | NAPA ID:22076 TP_BRUNSWICK GXP > ROBERTS AVE SUB > BRUNSWICK | 11 | Planned | 022076 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 706870 | NONE | Drop 11kV lines between poles 706870 and 782740 for tree felling. Works location: Brunswick Rd, Wanganui. WO 30026260 | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.010034 | 5.5 | 2017 | 2016-08-04 | B | 40 | 0.020068 | 0.00012017
1 | 12380207 | 2016-07-14 09:50 | 2016-07-14 11:20 | 90 | 5 | 450 | 0.0013522 | 0.001307 | 1.5025e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | A21 | UNKNOWN | Tripping on Cb A21 on Phase ABC OC and EF. Feeder patrolled but nothing found. Lightning reported in area before tripping. Reclosed OK. | F1 | MCKEE 1 | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 0.001307 | 11 | 2017 | 2016-07-14 | C | 5 | 0.001307 | 1.5025e-05
1 | 12380279 | 2016-07-14 09:54 | 2016-07-14 10:16 | 22 | 42 | 924 | 0.0027766 | 0.002397 | 0.00012621 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 215957 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | at 09:35, Papamoa Sub, CB 1 Tara Rd Feeder. Found a broken DDO holder at Fuses FP1213. Backfeed supplied from PMA 9: Sw/gear 13002/4 Closed, 13002/1 Opened. Isolated Lines at Sw/gear 13002/1 & ABS IP489. Permit issued & repairs carried out. All Power Restored on Completion. Ted Glasgow Attended. Replaced 1x Jumper & 1x HV Fuse & Holder 20A at Pole 215957. | F3 | TARA RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.002397 | 11 | 2017 | 2016-07-14 | C | 42 | 0.002397 | 0.00012621
1 | 12380631 | 2016-07-14 10:28 | 2016-07-14 16:25 | 356 | 1 | 356.9833 | 0.0010727 | 0.001063 | 3.0049e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 12382795 | UNKNOWN | 12.07pm spoke with Bernie control and he confirmed that Chris Vivier spoke to this customer and confirmed that they had full power restored after he attended OMS 12380207.dispatch has tried to contact customer twice with no response/answer.called Nova to see if they have another contact number for customer? Nova advised another phone number for customer is 06 754 9038..no answer on this number either. MCKEE Sub has tripped again, another job has been put thru again- control restoring power now, confirmed related to OMS 12382795 | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.001063 | 11 | 2017 | 2016-07-14 | C | 1 | 0.001063 | 3.0049e-06
1 | 12381837 | 2016-07-14 07:05 | 2016-07-14 12:08 | 302 | 40 | 12111.3333 | 0.036394 | 0.036033 | 0.0001202 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 775829 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replaced both HV fuse holders & 2x 2Amp Links after one was found broken. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.036033 | 6.6 | 2017 | 2016-07-14 | C | 40 | 0.036033 | 0.0001202
1 | 12382795 | 2016-07-14 12:08 | 2016-07-14 16:26 | 258 | 5 | 1290.5 | 0.0038779 | 0.003832 | 1.5025e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - JOINT FAILURE | 362895 | BINDER | Tripping on CB A21 on C Phase OC, EF. Feeder patrolled and floating conductor found. Isolation required from Sub to Sw/Gear 12125/1. Conductor rebound and insulator also replaced (Found broken). Relivened OK. | F1 | MCKEE 1 | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 0.003832 | 11 | 2017 | 2016-07-14 | C | 5 | 0.003832 | 1.5025e-05
1 | 12384749 | 2016-07-14 13:22 | 2016-07-14 14:31 | 69 | 23 | 1587 | 0.0047689 | 0.004561 | 6.9114e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | K4155 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Outage required between ABS KA774, 6690 and KA743 (Backfeed at ABS MA482) to replace full set of fuse units at Transformer K4155. Relivened OK. | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.004561 | 11 | 2017 | 2016-07-14 | C | 23 | 0.004561 | 6.9114e-05
1 | 12385737 | 2016-07-14 13:40 | 2016-07-14 14:04 | 23 | 408 | 9520 | 0.028607 | 0.024929 | 0.001226 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 726816 | NONE | Tripping on CB LI7 on OC. Tree branch found hanging in lines on South Rd at Pole 726816. Removed safely with fuse stick and relivened. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.024929 | 11 | 2017 | 2016-07-14 | C | 408 | 0.024929 | 0.001226
1 | 12387023 | 2016-07-14 15:26 | 2016-07-14 16:03 | 37 | 10 | 370 | 0.0011118 | 0.001021 | 3.005e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 755103 | BINDER | Outage required from fuses 8402 to repair a floating conductor. 1 binder needed. | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.001021 | 11 | 2017 | 2016-07-14 | C | 10 | 0.001021 | 3.005e-05
1 | 12387190 | 2016-08-02 08:58 | 2016-08-02 13:17 | 259 | 29 | 7511 | 0.022566 | 0.022304 | 8.7127e-05 | NAPA ID:22169 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 022169 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1185 | NONE | To replace strain cross arms and DNO ABS 1185. Works location: Bailey Rd, Te Aroha. WO 30025209 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.011152 | 5.5 | 2017 | 2016-08-02 | B | 29 | 0.022304 | 8.7127e-05
1 | 12387992 | 2016-07-14 15:10 | 2016-07-14 16:37 | 87 | 780 | 33997.5833 | 0.10216 | 0.09513 | 0.0023439 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | K13 | UNKNOWN | Feeder sectionalised & patrolled with no fault found. Once feeder was totally relivened faultman requested by NOC controller to carry out cursory patrol on the total feeder from RS K13 to the end. Note: Lines down as per report from customer was a red herring as it was telecom twisted together | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.09513 | 11 | 2017 | 2016-07-14 | C | 780 | 0.09513 | 0.0023439
1 | 12389888 | 2016-07-14 15:20 | 2016-07-14 21:17 | 356 | 155 | 11322.9667 | 0.034025 | 0.032627 | 0.00046577 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P1529 | CONDUCTOR - REPAIR/REHANG | Recloser 9604 Trip E/F L/O. Feeder Patrolled & sectionalised. Line down at Pole P1529. Isolation at ABS 232. Back Feed from WGM CB 1 via sectionaliser 9712. Materials 5 meters 16mm copper 2 sleeves | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.032627 | 11 | 2017 | 2016-07-14 | C | 155 | 0.032627 | 0.00046577
1 | 12390746 | 2016-07-14 19:49 | 2016-07-14 20:28 | 38 | 8 | 228.5 | 0.00068664 | 0.000614 | 2.404e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 720360 | BINDER | Fuses KA703 opened and rebind conductor at Pole 720360 | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.000614 | 11 | 2017 | 2016-07-14 | C | 8 | 0.000614 | 2.404e-05
1 | 12390944 | 2016-07-14 15:57 | 2016-07-14 21:44 | 346 | 1 | 346.8167 | 0.0010422 | 0.001033 | 3.0049e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8834 | FUSE - ELEMENT/LINK (HV) | 2 X 6 Amp | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001033 | 11 | 2017 | 2016-07-14 | C | 1 | 0.001033 | 3.0049e-06
1 | 12391010 | 2016-07-14 12:40 | 2016-07-15 12:40 | 1440 | 7 | 6715.9 | 0.020181 | 0.020118 | 2.1035e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764907 | BINDER | Tripping beyond fuses 5360 feeding Kiwi Rd. Impractical to patrol during the night. Next morning a patrol found a floating conductor at Pole 764907. Rebound OK and relivened. (1 Binder required). | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.020118 | 11 | 2017 | 2016-07-14 | C | 7 | 0.020118 | 2.1035e-05
1 | 12391456 | 2016-07-14 16:29 | 2016-07-14 17:28 | 59 | 20 | 1187.6667 | 0.0035689 | 0.003388 | 6.01e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R15 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10Amp HV Fuse Links | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.003388 | 11 | 2017 | 2016-07-14 | C | 20 | 0.003388 | 6.01e-05
1 | 12392107 | 2016-07-14 17:28 | 2016-07-14 18:42 | 74 | 18 | 1335.9 | 0.0040144 | 0.003852 | 5.409e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 731171 | CONDUCTOR - REPAIR/REHANG | Outage required from ABS LI 771 to repair a line down. Repaired / rehung OK. Suspect caused by high winds. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.003852 | 11 | 2017 | 2016-07-14 | C | 18 | 0.003852 | 5.409e-05
1 | 12392242 | 2016-07-14 17:39 | 2016-07-14 19:43 | 124 | 1 | 124.1667 | 0.00037312 | 0.000364 | 3.0049e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7776 | FUSE - ELEMENT/LINK (HV) | 2 X 6 amp | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000364 | 11 | 2017 | 2016-07-14 | C | 1 | 0.000364 | 3.0049e-06
1 | 12392248 | 2016-07-14 16:37 | 2016-07-14 18:11 | 93 | 33 | 3095.95 | 0.0093033 | 0.009005 | 9.9164e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 12391420 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10Amp HV Links | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.009005 | 11 | 2017 | 2016-07-14 | C | 33 | 0.009005 | 9.9164e-05
1 | 12392977 | 2016-07-14 19:08 | 2016-07-15 00:52 | 344 | 780 | 173395.3333 | 0.52105 | 0.51402 | 0.0023439 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P38033 | CONDUCTOR - REPAIR/REHANG | Temp Line Break at pole P38033 Lines down After this only feeds pump shed Les will apply to fix later when owner has been told about it. | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.51402 | 11 | 2017 | 2016-07-14 | C | 780 | 0.51402 | 0.0023439
1 | 12395740 | 2016-07-14 20:08 | 2016-07-15 10:15 | 847 | 33 | 10689 | 0.03212 | 0.031822 | 9.9164e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 831144 | CONDUCTOR - REPAIR/REHANG | Line down. Temp line break cut at pole W12635 due to weather conditions. Will repair in the day time tomorrow. Isolation at ABS 330. to cut line break. Line down at pole 831144. Line repaired. 15mtrs Squirrel conductor. 2 x Sleeves. | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.031822 | 11 | 2017 | 2016-07-14 | C | 33 | 0.031822 | 9.9164e-05
1 | 12397723 | 2016-07-14 23:03 | 2016-07-15 05:36 | 393 | 4044 | 61973.3667 | 0.18623 | 0.14977 | 0.012152 |  | 33 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 774175 | POLE | CB 2232 Tripped on B & C ph O/C, E/F on A ph. Car vs Pole (Stud pole on corner) 1 X 11m Pole ( Stud) NDR 41485 | S3 | TAUPO QUAY 33KV | WANGANUI | Wanganui | TP_WANGANUI | Western Electricity | POWERCO | 0.14977 | 33 | 2017 | 2016-07-14 | C | 4044 | 0.14977 | 0.012152
1 | 12401917 | 2016-07-15 08:47 | 2016-07-15 11:20 | 152 | 6 | 917.5 | 0.002757 | 0.002702 | 1.803e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 837463 | INSULATOR | Fuses 7776 opened to isolate to repair broken insulator at pole 837463 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.002702 | 11 | 2017 | 2016-07-15 | C | 6 | 0.002702 | 1.803e-05
1 | 12402211 | 2016-08-08 14:20 | 2016-08-08 15:25 | 65 | 3 | 195 | 0.00058582 | 0.000558 | 9.0125e-06 | NAPA ID:21959 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021959 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2300 | NONE | To install a 400V Fuse Disconnector. Works location: Gunn Rd, Waharoa. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000279 | 5.5 | 2017 | 2016-08-08 | B | 3 | 0.000558 | 9.0125e-06
1 | 12402231 | 2016-08-08 09:30 | 2016-08-08 12:00 | 150 | 7 | 1050 | 0.0031544 | 0.003091 | 2.1029e-05 | NAPA ID:21940 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021940 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5089 | NONE | To replace the 400V spreader arm & Install a 400V fuse disconnector. Works location: Peria Rd. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0015455 | 5.5 | 2017 | 2016-08-08 | B | 7 | 0.003091 | 2.1029e-05
1 | 12402246 | 2016-08-08 13:30 | 2016-08-08 14:30 | 60 | 6 | 360 | 0.0010815 | 0.001027 | 1.8025e-05 | NAPA ID:21941 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021941 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1869 | NONE | To install a 400V Fuse Disconnector. Works location: Peria Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0005135 | 5.5 | 2017 | 2016-08-08 | B | 6 | 0.001027 | 1.8025e-05
1 | 12402302 | 2016-08-09 12:00 | 2016-08-09 13:00 | 60 | 4 | 240 | 0.000721 | 0.000684 | 1.2017e-05 | NAPA ID:21943 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021943 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5092 | NONE | To install a 400V fuse Disconnector. Works location: Peria Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000342 | 5.5 | 2017 | 2016-08-09 | B | 4 | 0.000684 | 1.2017e-05
1 | 12402320 | 2016-08-09 14:00 | 2016-08-09 14:20 | 20 | 4 | 80 | 0.00024033 | 0.000204 | 1.2017e-05 | NAPA ID:21944 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021944 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1074 | NONE | To install a 400V Fuse Disconnector. Works location: Peria Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000102 | 5.5 | 2017 | 2016-08-09 | B | 4 | 0.000204 | 1.2017e-05
1 | 12402475 | 2016-08-11 10:00 | 2016-08-11 10:30 | 30 | 3 | 90 | 0.00027037 | 0.000243 | 9.0122e-06 | NAPA ID:21945 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021945 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2323 | NONE | To install a 400V Fuse Disconnector. Works location: Morgan Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0001215 | 5.5 | 2017 | 2016-08-11 | B | 3 | 0.000243 | 9.0122e-06
1 | 12402520 | 2016-08-12 12:00 | 2016-08-12 13:45 | 105 | 3 | 315 | 0.00094628 | 0.000919 | 9.0122e-06 | NAPA ID:21946 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021946 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4403 | NONE | To install a 400V Fuse Disconnector. Works location: Morgan Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0004595 | 5.5 | 2017 | 2016-08-12 | B | 3 | 0.000919 | 9.0122e-06
1 | 12402538 | 2016-08-11 14:00 | 2016-08-11 14:30 | 30 | 4 | 120 | 0.00036049 | 0.000324 | 1.2016e-05 | NAPA ID:21947 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021947 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4453 | NONE | To install a 400V Disconnector. Works location: Matai Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000162 | 5.5 | 2017 | 2016-08-11 | B | 4 | 0.000324 | 1.2016e-05
1 | 12402597 | 2016-08-12 12:00 | 2016-08-12 12:25 | 25 | 7 | 175 | 0.00052571 | 0.000462 | 2.1028e-05 | NAPA ID:21949 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021949 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2276 | NONE | To install a 400V Fuse Disconnector. Works location: Matai Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000231 | 5.5 | 2017 | 2016-08-12 | B | 7 | 0.000462 | 2.1028e-05
1 | 12402621 | 2016-08-12 14:00 | 2016-08-12 14:30 | 30 | 7 | 210 | 0.00063085 | 0.000567 | 2.1028e-05 | NAPA ID:21950 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021950 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC356 | NONE | To install a 400V Fuse Disconnector. Works location: Matai Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0002835 | 5.5 | 2017 | 2016-08-12 | B | 7 | 0.000567 | 2.1028e-05
1 | 12402660 | 2016-08-15 09:30 | 2016-08-15 13:30 | 240 | 7 | 1680 | 0.0050467 | 0.004983 | 2.1028e-05 | NAPA ID:21951 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021951 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2286 | NONE | To replace the 400V Spreader arm & install a 400V Disconnector. Works location: Matai Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0024915 | 5.5 | 2017 | 2016-08-15 | B | 7 | 0.004983 | 2.1028e-05
1 | 12402682 | 2016-08-15 14:00 | 2016-08-15 15:15 | 75 | 1 | 75 | 0.0002253 | 0.000216 | 3.0039e-06 | NAPA ID:21952 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021952 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP1514 | NONE | To install a 400V Disconnector. Works location: Henry Watson Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000108 | 5.5 | 2017 | 2016-08-15 | B | 1 | 0.000216 | 3.0039e-06
1 | 12402735 | 2016-08-17 09:45 | 2016-08-17 15:15 | 329 | 3 | 989.1 | 0.0029712 | 0.002944 | 9.0117e-06 | NAPA ID:21953 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021953 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2765 | NONE | To rebuild the transformer structure. Works location: Bowlers Rd, Matamata. WO 30019182 Job was late going back in due to old transformer did not fit on new structure, new transformer had to be installed. | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.001472 | 5.5 | 2017 | 2016-08-17 | B | 3 | 0.002944 | 9.0117e-06
1 | 12403144 | 2016-08-17 14:00 | 2016-08-17 15:00 | 60 | 1 | 60 | 0.00018023 | 0.000171 | 3.0039e-06 | NAPA ID:21954 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021954 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5564 | NONE | To install a 400V Fuse Disconnector. Works location: Station Rd< matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 8.55e-05 | 5.5 | 2017 | 2016-08-17 | B | 1 | 0.000171 | 3.0039e-06
1 | 12403794 | 2016-07-15 09:25 | 2016-07-15 09:48 | 23 | 257 | 6018.0833 | 0.018084 | 0.015767 | 0.00077227 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 370035 | CROSSARM - WHOLE ASSEMBLY | CB XT40 A/R, L/O, E/F, A Phase. Feeder sectionalised to restore power to Alfredton Sub. Fault is due to a tipped over crossarm at Pole 370035 & Isolated via ABS XT55 & XT56. This will require a new crossarm before relivening & a new pole at a later date. Due to the windy & wet weather access cannot be gained at this stage. Due to the importance of this line Downer need to repair this as soon as weather allows. 1 X King bolt & 1 X brace bolt replaced Also REf to OMS 12424347 | S3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.015767 | 33 | 2017 | 2016-07-15 | C | 257 | 0.015767 | 0.00077227
1 | 12405112 | 2016-07-15 11:02 | 2016-07-15 12:28 | 85 | 35 | 3005.3333 | 0.0090309 | 0.008715 | 0.00010517 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p44314 | FUSE - ELEMENT/LINK (HV) | replaced broken insulator crossarm isolated at fuses r54 | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.008715 | 11 | 2017 | 2016-07-15 | C | 35 | 0.008715 | 0.00010517
1 | 12405159 | 2016-07-15 10:06 | 2016-07-15 10:55 | 48 | 163 | 6214.2667 | 0.018674 | 0.017204 | 0.00048981 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9320 | UNKNOWN | Tripping on recloser CB9320. This CB was on "single shot" for liveline work at the time, staff all checked OK, advise not related to their switching. (NAPA 21829). Feeder patrolled / sectionalised and all restored OK .2r line patrol 1029 no repair | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.017204 | 11 | 2017 | 2016-07-15 | C | 163 | 0.017204 | 0.00048981
1 | 12405820 | 2016-07-15 13:30 | 2016-07-15 15:13 | 103 | 2 | 206 | 0.00061902 | 0.0006 | 6.0099e-06 | Referral | 11.00000000 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P38033 | CONDUCTOR - REPAIR/REHANG | 2r to repair line down. Treescape called to cut trees that had bought down lines across the river. Trees cleared & lines repaired. Temp Line break closed Live Line. NDR# 52551 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.0006 | 11 | 2017 | 2016-07-15 | C | 2 | 0.0006 | 6.0099e-06
1 | 12406457 | 2016-07-15 11:19 | 2016-07-15 15:32 | 253 | 120 | 23032.3333 | 0.069211 | 0.068129 | 0.00036059 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 837612 | CONDUCTOR - REPAIR/REHANG | cb936 a/r o/c. Line patrolled & tree branches found to be contacting HV Lines around Pole 837612. Tree branches cut away from lines and damage to line repaired Materials used: 3x conductor joints, 2mtrs of mink conductor NDR# 23282 2r line patrol 1201 2r repair 1229 Previous A/R on 12406064 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.068129 | 11 | 2017 | 2016-07-15 | C | 120 | 0.068129 | 0.00036059
1 | 12406603 | 2016-08-18 12:00 | 2016-08-18 13:20 | 80 | 5 | 400 | 0.0012015 | 0.001156 | 1.5019e-05 | NAPA ID:21938 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021938 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2640 | NONE | To install a 400V Disconnector. Works location: Peria Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000578 | 5.5 | 2017 | 2016-08-18 | B | 5 | 0.001156 | 1.5019e-05
1 | 12406692 | 2016-08-18 14:00 | 2016-08-18 15:07 | 67 | 2 | 134 | 0.00040252 | 0.000384 | 6.0077e-06 | NAPA ID:21939 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021939 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5460 | NONE | To install a 400V Disconnector. Works location: Station Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000192 | 5.5 | 2017 | 2016-08-18 | B | 2 | 0.000384 | 6.0077e-06
1 | 12406725 | 2016-07-15 11:35 | 2016-07-15 13:15 | 99 | 3 | 299.75 | 0.00090073 | 0.000873 | 9.0148e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 701426 | FUSE - ELEMENT/LINK (HV) | 11.37am advised Shannon at svs hub & emailed & control. Have advised FM, customer called advising strike was at Pole: 752550 - 380 Junction Road. Reload reliven at Transformer 1276. 3 x 8A Fuses. Cause: Lightning. | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000873 | 11 | 2017 | 2016-07-15 | C | 3 | 0.000873 | 9.0148e-06
1 | 12406767 | 2016-08-18 10:00 | 2016-08-18 10:36 | 36 | 6 | 216 | 0.00064884 | 0.000594 | 1.8023e-05 | NAPA ID:21937 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021937 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5365 | NONE | To install a 400V Fuse Disconnector. Works location: Peria Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000297 | 5.5 | 2017 | 2016-08-18 | B | 6 | 0.000594 | 1.8023e-05
1 | 12406868 | 2016-07-15 11:48 | 2016-07-15 14:43 | 175 | 1 | 175.2167 | 0.00052652 | 0.000517 | 3.0049e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 370924 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp fuses due to weather. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000517 | 11 | 2017 | 2016-07-15 | C | 1 | 0.000517 | 3.0049e-06
1 | 12406903 | 2016-08-29 14:20 | 2016-08-29 14:55 | 35 | 6 | 210 | 0.00063073 | 0.000576 | 1.8021e-05 | NAPA ID:21962 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021962 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1486 | NONE | To install a 400V Disconnector. Works location: Morgan Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000288 | 5.5 | 2017 | 2016-08-29 | B | 6 | 0.000576 | 1.8021e-05
1 | 12407160 | 2016-07-15 11:53 | 2016-07-15 13:50 | 116 | 243 | 16851.9333 | 0.050639 | 0.048448 | 0.00092252 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 745171 | BINDER | Tripping on Lepper Rd Recloser CB499 on O/C A-C and EF. Feeder patrolled / sectionalised with a floating conductor found at pole 745171. Isolation between ABS 349 and 483. One binder needed, relivened OK. 2r line patrol 1226 / 2r repair 1325. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.048448 | 11 | 2017 | 2016-07-15 | C | 243 | 0.048448 | 0.00092252
1 | 12407585 | 2016-08-09 09:00 | 2016-08-09 14:57 | 357 | 50 | 17850 | 0.053624 | 0.053173 | 0.00015021 | NAPA ID:22139 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > NGARUA | 11 | Planned | 022139 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 263000 | NONE | Ngarua Feeder Step 3. Specified renewal works completed between ABS 660 and IP18 including installation of FP1814. Works location: Seddon Rd, Waihou. WO 30017830 | F4 | NGARUA | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.026586 | 5.5 | 2017 | 2016-08-09 | B | 50 | 0.053173 | 0.00015021
1 | 12407587 | 2016-08-07 08:20 | 2016-08-07 13:37 | 317 | 1 | 317.2167 | 0.00095299 | 0.000943 | 3.0042e-06 | NAPA ID:22637 TP_WANGANUI GXP > BEACH RD SUB > GILBERD ST | 11 | Planned | 022637 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X3227 | NONE | Replace FABS 2850 that feeds Tasman Tanning. Open 2850 to isolate X3227. Works location: Tasman Tanning. WO 10159909 | F2 | GILBERD ST | WANGANUI | Wanganui | BEACH RD SUB | Western Electricity | POWERCO | 0.0004715 | 5.5 | 2017 | 2016-08-07 | B | 1 | 0.000943 | 3.0042e-06
1 | 12407631 | 2016-07-15 12:31 | 2016-07-15 16:38 | 247 | 422 | 35921.5333 | 0.10794 | 0.10414 | 0.0012681 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 205425 | CONDUCTOR - REPAIR/REHANG | Aongatete CB3 tripped and L/O. No Flags. Line down at Pole 205425. High Winds. Tree through Lines NDR51862 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.10414 | 11 | 2017 | 2016-07-15 | C | 422 | 0.10414 | 0.0012681
1 | 12409039 | 2016-07-15 11:44 | 2016-07-15 12:25 | 41 | 12 | 493.6 | 0.0014832 | 0.001375 | 3.6059e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752550 | FUSE - ELEMENT/LINK (HV) | 2 x 3A Fuses due to lightnin. Refer to 12406725 | F3 | BROOKLANDS 12 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.001375 | 11 | 2017 | 2016-07-15 | C | 12 | 0.001375 | 3.6059e-05
1 | 12409765 | 2016-08-07 08:32 | 2016-08-07 10:12 | 100 | 1 | 100.3833 | 0.00030157 | 0.000292 | 3.0042e-06 | NAPA ID:22605 TP_WANGANUI GXP > TAUPO QUAY SUB > GONVILLE | 11 | Planned | 022605 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | X2381 | NONE | Isolate transformer X2381 to install data loggers. Works location: Heads Rd. WO 10141920 | F1 | GONVILLE | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 0.000146 | 5.5 | 2017 | 2016-08-07 | B | 1 | 0.000292 | 3.0042e-06
1 | 12411126 | 2016-07-15 15:17 | 2016-07-15 18:53 | 216 | 414 | 36080.2833 | 0.10842 | 0.10469 | 0.0012441 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 389426 | CONDUCTOR - REPAIR/REHANG | Lines down at pole 389426 due to tornado. Isolated at fuses SD6-006 to be repaired under planned switching | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.10469 | 11 | 2017 | 2016-07-15 | C | 414 | 0.10469 | 0.0012441
1 | 12412132 | 2016-07-15 15:30 | 2016-07-15 16:07 | 37 | 674 | 24039.2167 | 0.072237 | 0.06616 | 0.0020253 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | WHUPKO177 | CONDUCTOR - REPAIR/REHANG | Tripping on PKO 33kV CBs 3252 and 3142. (Circuits paralleld via ABS PC141 at PKO. (Loss of supply to Farmers Rd and Tatua Sub). Farmers Sub supplied via Waihou CB402 and Tatua supplied via Farmers Rd CB6. Patrol carried out and Floating conductor found at Pole WHUPKO177. PKO-FMR CCt (CB 3142) put in service with injection plant supplied. ABS PC113 closed at PKO for Morrinnsville Injection signals. Repairs to be carried out Saturday 16th. Floating Conductor found at Pole WHUPKO177. Lines isolated and Conductor rebound. 1 x Binder | S2 | PIAKO3142-FARMER ROAD42 33kV | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.06616 | 33 | 2017 | 2016-07-15 | C | 674 | 0.06616 | 0.0020253
1 | 12417738 | 2016-07-15 16:18 | 2016-07-15 20:20 | 241 | 13 | 3140.15 | 0.009436 | 0.009318 | 3.9064e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC846 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 3x 6A HV Fuses at Transformer TC846. Lightning cause. Control to close | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.009318 | 11 | 2017 | 2016-07-15 | C | 13 | 0.009318 | 3.9064e-05
1 | 12417748 | 2016-07-15 16:19 | 2016-07-15 17:38 | 79 | 6 | 475.5 | 0.0014289 | 0.001374 | 1.803e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4074 | FUSE - ELEMENT/LINK (HV) | Check OMS 12417940 - 434 D WAIHI BEACH ROAD 2 x 8A HV Fuses at FC4074 2 x 2A HV Fuses at FC 5299 | F3 | BEACH RD WAIHI BEACH | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.001374 | 11 | 2017 | 2016-07-15 | C | 6 | 0.001374 | 1.803e-05
1 | 12418123 | 2016-07-15 17:08 | 2016-07-15 23:20 | 372 | 1 | 372.2167 | 0.0011185 | 0.001109 | 3.0049e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC6475 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | at 20:37, Paeroa Sub, CB 5 Bennett St Feeder. Faultman dispatched to No Power Job. Found Transformer TC6475 had been blown up by lightning. Own Isolation & AP Issued to replace transformer. All Power Restored on completion. Pieter Diedericks Attended. Replaced 1x Transformer & 4x HV Fuses 3A. Transformer TC6475 Blown due to Lightning. | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.001109 | 11 | 2017 | 2016-07-15 | C | 1 | 0.001109 | 3.0049e-06
1 | 12418484 | 2016-07-15 17:49 | 2016-07-15 19:47 | 118 | 2 | 225.1 | 0.00067641 | 0.000658 | 6.0099e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 803 | FUSE - ELEMENT/LINK (HV) | Check OMS 12418563 - 921 KOHI ROAD | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000658 | 11 | 2017 | 2016-07-15 | C | 2 | 0.000658 | 6.0099e-06
1 | 12418534 | 2016-07-15 17:20 | 2016-07-15 18:04 | 44 | 7 | 308 | 0.00092553 | 0.000862 | 2.1035e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3861T | FUSE - ELEMENT/LINK (HV) | Outage required between ABS 4951, 6159 and 6136 to repair a broken centre DDO at Transformer 3861T. (Backfeed at ABS 4956.). 1 * 3A Fuse reolaced. | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000862 | 11 | 2017 | 2016-07-15 | C | 7 | 0.000862 | 2.1035e-05
1 | 12422326 | 2016-07-16 00:19 | 2016-07-16 03:10 | 171 | 674 | 74267.6 | 0.22317 | 0.21709 | 0.0020253 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 210283 | CONDUCTOR - REPAIR/REHANG | at 00:19, Omokoroa Sub, CB 1 Te Puna Feeder, Tripped, A B C O/C, L/O. Faultmen dispatched & investigation began. Found a tree that had fallen through lines at pole 210283. Isolated lines at Sw/gear 9461/1, ABS SD3-095 & SD3-002. Backfeed supplied from BHM 1: Closed ABS SD3-009. Tree removed. All Power restored on completion. no damage done to the lines. No materials used. TJ Tanoa Attended. 2r line patrol 0154 2r repair no repair removed by hot stick | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.21709 | 11 | 2017 | 2016-07-16 | C | 674 | 0.21709 | 0.0020253
1 | 12424941 | 2016-07-16 10:46 | 2016-07-16 12:00 | 74 | 7 | 518.1167 | 0.0015569 | 0.001493 | 2.1034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7260 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuse on transformer T7260. 2 X 6 amp HV fuses replaced | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001493 | 11 | 2017 | 2016-07-16 | C | 7 | 0.001493 | 2.1034e-05
1 | 12425458 | 2016-07-16 13:35 | 2016-07-16 15:30 | 114 | 1 | 114.7667 | 0.00034486 | 0.000335 | 3.0049e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 381945 | FUSE - ELEMENT/LINK (HV) | 2 x 2A HV Fuses Pole 381945 | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000335 | 11 | 2017 | 2016-07-16 | C | 1 | 0.000335 | 3.0049e-06
1 | 12425629 | 2016-07-16 16:15 | 2016-07-16 16:25 | 10 | 27 | 272.25 | 0.00081809 | 0.000574 | 8.1133e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 4482W | FUSE - ELEMENT/LINK (HV) | Pole 842927 - Electrician can see 2x DDO fuses hanging and bark wrapped around the wires. Low voltage at premises. Alister Stewart (027) 295 2480 - may not be onsite but can meet FM if required - please call and he can come back. Has turned off the power to the alarms to save power. Faultman removed bark from line with hot line sticks at transformer 4482W, Fuses 458 where opened to remove the bark safely. | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.000574 | 11 | 2017 | 2016-07-16 | C | 27 | 0.000574 | 8.1133e-05
1 | 12426871 | 2016-07-16 21:03 | 2016-07-16 22:07 | 63 | 522 | 33242.7 | 0.099892 | 0.095185 | 0.0015686 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | C856 | UNKNOWN | CB C856 Trip, O/C A & B Phase. Patrolled, No fault found. Relivened okay. No 2R. | F3 | CORNWALL ST | MASTERTON | Wairarapa | CHAPEL SUB | Western Electricity | POWERCO | 0.095185 | 11 | 2017 | 2016-07-16 | C | 522 | 0.095185 | 0.0015686
1 | 12427569 | 2016-07-16 23:01 | 2016-07-17 02:41 | 220 | 3 | 660 | 0.0019832 | 0.001956 | 9.0147e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P33285 | POLE | Replaced broken pole P33285 hit by milk tanker. NDR# 046981 | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.001956 | 11 | 2017 | 2016-07-16 | C | 3 | 0.001956 | 9.0147e-06
1 | 12427596 | 2016-07-16 22:03 | 2016-07-17 01:12 | 188 | 120 | 22658 | 0.068085 | 0.067003 | 0.00036059 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 837618 | NONE | CB C936 A/R, L/O, O/C A & B Phase. Sectionalised & Patrolled with tree branch contacting lines at Pole 837618. Access Permit issued to cut branch clear of lines. NDR# 37769. 2r line patrol 2324 / 2r repair 0006. | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.067003 | 11 | 2017 | 2016-07-16 | C | 120 | 0.067003 | 0.00036059
1 | 12428717 | 2016-07-17 09:58 | 2016-07-17 12:46 | 168 | 1 | 168.05 | 0.00050497 | 0.000495 | 3.0048e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP2275 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A H/V , O/H fuses . Lines may need re sagging line clash in strong wind | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.000495 | 11 | 2017 | 2016-07-17 | C | 1 | 0.000495 | 3.0048e-06
1 | 12429183 | 2016-07-17 14:00 | 2016-07-17 19:00 | 300 | 155 | 18952.4667 | 0.05695 | 0.055552 | 0.00046576 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13387 | CONDUCTOR - REPAIR/REHANG | ( WHI 1 ) recloser 9604 tripped O/C, E/F, L/O. Report of line down at pole 13387. Isolation at ABS 232 ( spur no back feed ) Remainder of feeder returned to service Line repaired all service restored 7m of 16mm2 Cu Conductor Used. 4x Links, 3x Binders. 2r line patrol 1545 2r repair 1635 | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.055552 | 11 | 2017 | 2016-07-17 | C | 155 | 0.055552 | 0.00046576
1 | 12429900 | 2016-07-17 15:50 | 2016-07-17 18:10 | 140 | 25 | 1466 | 0.0044052 | 0.004179 | 7.5122e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3361T | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Faultman found transformer 3361T, line was isolated at ABS's 5972 & 6008 to replace transformer. | F4 | DUTHIE RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.004179 | 11 | 2017 | 2016-07-17 | C | 25 | 0.004179 | 7.5122e-05
1 | 12430008 | 2016-07-17 19:37 | 2016-07-17 20:25 | 48 | 16 | 746.25 | 0.0022424 | 0.002098 | 4.8078e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 714719 | JUMPER | Faultman found broken HV jumper while looking for cause of part powers.1 x conductor joint and 1 mtr 16mm Cu. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.002098 | 11 | 2017 | 2016-07-17 | C | 16 | 0.002098 | 4.8078e-05
1 | 12430480 | 2016-07-17 17:19 | 2016-07-18 10:03 | 1004 | 17 | 17073.3833 | 0.051304 | 0.05115 | 5.1083e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | P06855 | FUSE - ELEMENT/LINK (HV) | 6.30am spoke with Paul and checked to see if this job could be related to oms 12430534 - Paul has advised 2amp fuse was replaced at tx T9/24 - Erin to call customer's after 8am to check if their power is restored before requesting 8.09am Customer still has no power - 4074 Pahiatua Pongoroa Road 8.11am called customer to check if power restored? 4469 Pahiatua Road no answer | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.05115 | 11 | 2017 | 2016-07-17 | C | 17 | 0.05115 | 5.1083e-05
1 | 12430841 | 2016-07-17 18:02 | 2016-07-17 18:09 | 7 | 2347 | 13754.2167 | 0.04133 | 0.020172 | 0.0070525 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE |  | NONE | Katere CB 12 tripped due to over current, over run of NAPA 22648, ABB had problem with wiring to restore T1 to service. | F2 | KATERE 12 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.020172 | 11 | 2017 | 2016-07-17 | C | 2347 | 0.020172 | 0.0070525
1 | 12432267 | 2016-07-17 19:38 | 2016-07-18 04:52 | 554 | 195 | 40346.3833 | 0.12124 | 0.11948 | 0.0011629 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | 205759 | NONE | at 19:38, Aongatete Sub, CB 3 Apata Feeder, Recloser 9489 Tripped, E/F O/C, L/O. Faultmen dispatched & investigation began. Feeder sectionalised. Backfeed supplied from OMO 3: ABS SC2-124 Opened, Sectionaliser 9702 Closed. Found fault was beyond Fuses SC2-017. Line patrolled multiple times. All Spur Line Fuses & Transformer Fuses Isolated as part of sectionalising. Isolated line at Fuses SC2-017 & Permits issued to create line breaks, first at Pole 205784 & second at 205767. Found fault was between Pole 202767 & Fuses SC2-017. Found Possum on Centre Phase at Pole 205759. Removed with Hot Stick Permits issued to Close Line Breaks and Repair broken fuse carrier at transformer TC2-215 (found broken while sectionalising). All Power Restored on Completion. 1x HV Fuse & Carrier replaced. 6x Connectors Used. Difficult terrain to patrol. Also, fuses at SC2-017 never blew while fault finding.2r line patrol 2100. 2r repair 0105 | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.11948 | 11 | 2017 | 2016-07-17 | C | 195 | 0.11948 | 0.0011629
1 | 12433202 | 2016-07-17 20:48 | 2016-07-17 22:17 | 88 | 3 | 266.8 | 0.0008017 | 0.000774 | 9.0146e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2151 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x 3A HV Fuses at FC2151. High winds in the area. | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000774 | 11 | 2017 | 2016-07-17 | C | 3 | 0.000774 | 9.0146e-06
1 | 12433811 | 2016-07-18 01:05 | 2016-07-19 14:14 | 2229 | 5 | 4698 | 0.014117 | 0.014071 | 1.5024e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773140 & 359384 | CROSSARM - WHOLE ASSEMBLY | Faultman found one of two HV links blown at Fuses 858. Attempted reliven but fuse blew. Open & Tagged Fuses 696. Successfully relivened Fuses 858. Left Fuses 698 open for the night. Patrol required beyond Fuses 696 after daybreak today. Broken insulator & badly scuffed wire links 696 have been pulled, found fault approx. 30mins away. Customer has generator going only 1 customer - customer has his own generator. Replaced crossarm @ pole 773140 and repaired conductor @ pole 359384 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.014071 | 11 | 2017 | 2016-07-18 | C | 5 | 0.014071 | 1.5024e-05
1 | 12435727 | 2016-07-18 03:45 | 2016-07-18 06:13 | 148 | 289 | 28377.9 | 0.085272 | 0.082666 | 0.00086841 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB C917 A/R, L/O, E/F. Sectionalised & Patrolled with no fault found. 2R line patrol 0444 no repair. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.082666 | 11 | 2017 | 2016-07-18 | C | 289 | 0.082666 | 0.00086841
1 | 12437090 | 2016-07-18 04:28 | 2016-07-19 12:08 | 1899 | 107 | 26538.6667 | 0.079745 | 0.07878 | 0.00048378 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 815321 | CONDUCTOR - REPAIR/REHANG | During patrol found 33kV line down at pole 815321 and across the 11kV Line was isolated from ABS 8039 and repaired fault men then investigated at several properties to establish whether any damage to the 400v system also several HV fuses were replaced at various points along the line. | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.07878 | 11 | 2017 | 2016-07-18 | C | 107 | 0.07878 | 0.00048378
1 | 12437202 | 2016-07-18 03:14 | 2016-07-18 06:47 | 212 | 143 | 19739.8 | 0.059315 | 0.058026 | 0.0004297 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P17883 | CONDUCTOR - REPAIR/REHANG | Rec M81 trip found lines down at pole P17883. e/f o/c. 2r line patrol 0452. 2r repair 0601 | F4 | MT STEWART | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.058026 | 11 | 2017 | 2016-07-18 | C | 143 | 0.058026 | 0.0004297
1 | 12437984 | 2016-07-18 09:30 | 2016-07-18 14:00 | 270 | 2 | 540 | 0.0016226 | 0.001604 | 6.0097e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3421T transformer LV arms | CROSSARM - WHOLE ASSEMBLY | Replace LV arms and associated equipment. Isolated via own HV fuses. Found as part of HV on Friday 15th, liaise with NCTL to sort for today. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.001604 | 11 | 2017 | 2016-07-18 | C | 2 | 0.001604 | 6.0097e-06
1 | 12438302 | 2016-08-10 08:41 | 2016-08-10 15:20 | 399 | 99 | 39501 | 0.11867 | 0.11777 | 0.00029741 | NAPA ID:22252 TP_MASTERTON GXP > TE ORE ORE SUB > BIDEFORD | 11 | Planned | 022252 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 837195 | NONE | Cut trees (by Treescape). Run replacement conductor (by Downer). Works location: Bideford Rd, Masterton. WO 30026281 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.058887 | 5.5 | 2017 | 2016-08-10 | B | 99 | 0.11777 | 0.00029741
1 | 12446618 | 2016-07-20 09:00 | 2016-07-20 15:11 | 371 | 11 | 4081 | 0.012263 | 0.012163 | 3.3053e-05 | NAPA ID:22670 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 022670 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Remove existing regulator structure TC6103. Replace existing pole numbers W1564 and W13649 with a new double pole structure and a new ABS to replace IC2112 NOTE: Regulator not fully re-commissioned until 26/07/2016 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.0060815 | 5.5 | 2017 | 2016-07-20 | B | 11 | 0.012163 | 3.3053e-05
1 | 12447683 | 2016-07-18 11:30 | 2016-07-18 12:20 | 50 | 82 | 4100 | 0.01232 | 0.01158 | 0.0002464 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | O3627 | CROSSARM - WHOLE ASSEMBLY | ( KPE 5 ) Emergency switching to replace arm at pole O3627, Was to be replaced under Napa 21756 live line No access to site due to rain ( ground conditions ) Arm in state due to fail Isolation between ABS's IC465, IC501, IP620 & IC454. Arm & hardware replaced all service restored Materials 1x H/V arm complete James Kennerly attended | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.01158 | 11 | 2017 | 2016-07-18 | C | 82 | 0.01158 | 0.0002464
1 | 12448782 | 2016-07-16 15:15 | 2016-07-16 16:11 | 56 | 2 | 112 | 0.00033655 | 0.000318 | 6.0098e-06 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN |  | S2 | 3163-FARMER ROAD52 33kV | PIAKO | Valley | TATUA SUB | Eastern Electricity | POWERCO | 0.000318 | 33 | 2017 | 2016-07-16 | C | 2 | 0.000318 | 6.0098e-06
1 | 12448995 | 2016-07-18 17:59 | 2016-07-18 18:03 | 4 | 96 | 384 | 0.0011539 | 0.000288 | 0.00028847 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 381063 | JUMPER | ( TGA 12 ) Emergency switching to repair blown jumper at FABS IP486 Isolations between ABS IP582 & Links 9806/4, with back feed via Sec 9807 Jumper repaired all service restored . Materials 1 x H/V lug | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000288 | 11 | 2017 | 2016-07-18 | C | 96 | 0.000288 | 0.00028847
1 | 12449192 | 2016-08-12 09:31 | 2016-08-12 13:29 | 238 | 5 | 1192.25 | 0.0035816 | 0.003536 | 1.502e-05 | NAPA ID:21963 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021963 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2671 | NONE | To replace the 11kV Pin arm, 11kV Fuse arm, 400V Spreader Arm & install 400V Disconnector | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.001768 | 5.5 | 2017 | 2016-08-12 | B | 5 | 0.003536 | 1.502e-05
1 | 12449208 | 2016-07-18 15:18 | 2016-07-18 15:28 | 10 | 9 | 90.9 | 0.00027314 | 0.000192 | 2.7044e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - PROTECTION SETTINGS - INCORRECT/ERROR |  | RECLOSER (HV) | (KPE 1) recloser RC22 tripped U/V ABR scheme operated via Sec 9668 ( TAH 4 ) RC22 just commissioned to service after faulting during GFN testing. Recloser RC 22 closed & back feed removed. Recloser RC22 tripped U/V, back feed restored. Scada techs disable U/V Rec RC22 returned to service back feed removed. Scada techs to re check setting in morning. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000192 | 11 | 2017 | 2016-07-18 | C | 9 | 0.000192 | 2.7044e-05
1 | 12450003 | 2016-07-19 09:49 | 2016-07-19 11:11 | 82 | 6 | 492 | 0.0014784 | 0.001424 | 1.8029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 848532 | CROSSARM - WHOLE ASSEMBLY | Faultman found floating conductor and cross arm end burnt on pole 848532 temporary repairs carried out and crossarm replaced on 19/07/16 | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.001424 | 11 | 2017 | 2016-07-19 | C | 6 | 0.001424 | 1.8029e-05
1 | 12450306 | 2016-07-19 10:05 | 2016-07-19 11:15 | 70 | 14 | 980 | 0.0029447 | 0.002818 | 4.2068e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P48307 | CROSSARM - WHOLE ASSEMBLY | Faultman found a tipped up cross arm on pole P48307, faultman reported it is safe for the night will return in morning to replace the cross arm and all it's hardware. | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.002818 | 11 | 2017 | 2016-07-19 | C | 14 | 0.002818 | 4.2068e-05
1 | 12453889 | 2016-07-19 07:50 | 2016-07-19 10:47 | 177 | 408 | 18728.0667 | 0.056275 | 0.052596 | 0.001226 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 728842 | CROSSARM - WHOLE ASSEMBLY | By 100 km sign power pole on fire. NZ Fire 04 801 0182 ETA please. Event number F2116719 Between Kakarema Hotel and Hooper Engineering. Found cross arm burnt & line down at pole 728842. Isolated between ABS LI773 & LI795, made repairs & re-livened. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.052596 | 11 | 2017 | 2016-07-19 | C | 408 | 0.052596 | 0.001226
1 | 12455095 | 2016-08-15 09:50 | 2016-08-15 14:00 | 250 | 16 | 4000 | 0.012016 | 0.011871 | 4.8063e-05 | NAPA ID:21964 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021964 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2288 | NONE | To replace the 11kV pin arm, 11kV fuse arm, 400V spreader arm & install a 400V Disconnector. Works location: Station Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0059355 | 5.5 | 2017 | 2016-08-15 | B | 16 | 0.011871 | 4.8063e-05
1 | 12455177 | 2016-08-17 10:12 | 2016-08-17 12:57 | 165 | 11 | 1815 | 0.0054521 | 0.005352 | 3.3043e-05 | NAPA ID:21965 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11.00000000 | Planned | 021965 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2749 | NONE | To replace the 11kV Fuse arm, 400V Spreader arm & install a 400V Disconnector. Works location: Station Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.002676 | 5.5 | 2017 | 2016-08-17 | B | 11 | 0.005352 | 3.3043e-05
1 | 12455943 | 2016-08-09 09:25 | 2016-08-09 13:42 | 257 | 4 | 1028 | 0.0030883 | 0.003052 | 1.2017e-05 | NAPA ID:22191 TP_TE MATAI GXP > PONGAKAWA SUB > ROTOEHU | 11 | Planned | 022191 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TF7-063 | NONE | Isolate and Replace transformer. Works location: Hereford Park Rd. WO 30019529 | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.001526 | 5.5 | 2017 | 2016-08-09 | B | 4 | 0.003052 | 1.2017e-05
1 | 12456500 | 2016-08-22 09:52 | 2016-08-22 11:08 | 76 | 8 | 608 | 0.0018263 | 0.001754 | 2.403e-05 | NAPA ID:22216 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11.00000000 | Planned | 022216 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2783 | NONE | To replace the 11kV Fuse arm, 400V Pin Arm & Install a 400V Disconnector. Works location: Buckland Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000877 | 5.5 | 2017 | 2016-08-22 | B | 8 | 0.001754 | 2.403e-05
1 | 12456697 | 2016-07-19 13:29 | 2016-07-19 17:58 | 269 | 3 | 807 | 0.0024249 | 0.002397 | 9.0144e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R13101 | CONDUCTOR - REPAIR/REHANG | Advised svs hub & control. Pole top broken off & line down. Isolated at fuses FP1606. Removed crossarm & repaired wire. pole is in Estuary. Due to tide coming in unable to completely fixed. R13101 had top break out (may have caught on fire) access permit to repair but on getting to site they've found connector also needs repairing. Will unbind conductor from broken part of pole to raise lines to approx 6m. TC1583 - no customer at moment, FM will check mains switches. What do Powerco want us to do? Generators Steve McKinney 021395047 Temp rpairs carried out to line. pole will need replacing and line repaired/replaced due to spragging of conductor at a later date. Clearance of the line over the water at high tide is approximately 4.5meters. Line relivened. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.002397 | 11 | 2017 | 2016-07-19 | C | 3 | 0.002397 | 9.0144e-06
1 | 12456920 | 2016-07-19 15:27 | 2016-07-19 17:12 | 105 | 17 | 1785 | 0.0053636 | 0.00521 | 5.1082e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P04266 | INSULATOR | Repaired 2 x floating conductors At pole Po4223 & P04266 . Materials used 2x clamptop insulators and 2 binders | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.00521 | 11 | 2017 | 2016-07-19 | C | 17 | 0.00521 | 5.1082e-05
1 | 12456967 | 2016-07-20 13:58 | 2016-07-20 14:38 | 40 | 6 | 240 | 0.00072115 | 0.000667 | 1.8029e-05 | NAPA ID:22725 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > BLACK STUMP | 11 | Planned | 022725 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 220892 | POLE | Restand two poles. Repair broken line and remove GenSet from cowshed. Remove line gap and restore supply to TD6-049. | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.0003335 | 5.5 | 2017 | 2016-07-20 | B | 6 | 0.000667 | 1.8029e-05
1 | 12457204 | 2016-07-20 09:40 | 2016-07-20 13:04 | 204 | 4 | 369 | 0.0011088 | 0.001072 | 1.2019e-05 | NAPA ID:22730 TP_TE MATAI GXP > TE PUKE SUB > KAITUNA | 11 | Planned | 022730 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 222545 | NONE | Repair broken HV wires between pole 222544 and 222545. Remake line gap at TD6-324. Restore supply and feeder to normal. | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000536 | 5.5 | 2017 | 2016-07-20 | B | 4 | 0.001072 | 1.2019e-05
1 | 12458219 | 2016-07-19 15:07 | 2016-07-19 18:09 | 182 | 110 | 10350.7667 | 0.031102 | 0.03011 | 0.00051383 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T42/2 | UNKNOWN | Section of line from ABS T38 to ABS V19 to be patrolled in daylight. Recloser T42 tripped again this line patrol will now be done under new OMS 12460451. 2r line patrol 1541 2r repair no | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.03011 | 11 | 2017 | 2016-07-19 | C | 110 | 0.03011 | 0.00051383
1 | 12459226 | 2016-07-19 16:53 | 2016-07-19 20:47 | 234 | 51 | 9682.3667 | 0.029094 | 0.028634 | 0.00015325 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 4443/2 | UNKNOWN | Recloser 4443/2 tripped on E/F flags, line was sectionalised and patrolled and no fault was found, faultman reported that most of line was hard to access at night.Also reported weather was very bad, high winds and heavy rain. 2r line patrol 1840 2r repair no fault | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.028634 | 11 | 2017 | 2016-07-19 | C | 51 | 0.028634 | 0.00015325
1 | 12459935 | 2016-07-19 18:52 | 2016-07-19 21:45 | 173 | 3 | 519 | 0.0015595 | 0.001532 | 9.0144e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P2150 | FUSE - ELEMENT/LINK (HV) | Faultman found a blown fuse at transformer P2150. 2 X 2 amp HV fuses replaced | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.001532 | 11 | 2017 | 2016-07-19 | C | 3 | 0.001532 | 9.0144e-06
1 | 12460274 | 2016-07-19 20:47 | 2016-07-20 19:07 | 1339 | 41 | 12206.8167 | 0.036679 | 0.036309 | 0.00019832 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC1685 | POLE | ( LAK 5 ) recloser 9779/2 tripped E/F, A Ph O/C, L/O. Feeder patrolled and found transformer TC1685 & pole on the ground Temp line break cut at pole E1102, rest of feeder returned to service Repairs to be carried out in morning | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.036309 | 11 | 2017 | 2016-07-19 | C | 41 | 0.036309 | 0.00019832
1 | 12460451 | 2016-07-19 20:50 | 2016-07-22 15:17 | 3986 | 110 | 52389.4667 | 0.15742 | 0.15643 | 0.0010908 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE |  | JUMPER | Recloser T42 tripped on C phase fault & E/F flags,line was partly sectionalised and patrolled, faultman will return in morning to carry out patrol in day light as to unsafe due to the bad weather, repair line break and cut trees on 22/7 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.15643 | 11 | 2017 | 2016-07-19 | C | 110 | 0.15643 | 0.0010908
1 | 12461292 | 2016-07-19 21:03 | 2016-07-20 04:46 | 463 | 429 | 22559.8 | 0.067788 | 0.063921 | 0.0012891 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | K0599 | CIRCUIT BREAKER (HV) | ( TAH 2 ) CB2 tripped A, B & C Ph O/C, L/O. Recloser 9320 opened & back feed closed via sectionaliser 9778. Tree through line at pole K0599 Isolation between CB2, ABS 541 & ABS 558 further back feed via ABS 602. Pole replaced all service restored NDR No 55716 Materials 1 x pole, 2 x H/V arms complete 2r line patrol 2105 2r repair 2255 | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.063921 | 11 | 2017 | 2016-07-19 | C | 429 | 0.063921 | 0.0012891
1 | 12463163 | 2016-07-19 21:30 | 2016-07-19 23:50 | 140 | 42 | 5875.6 | 0.017655 | 0.017276 | 0.0001262 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217325 | FUSE - ELEMENT/LINK (HV) | ** CHECK 160 SOLDIERS ROAD is related - OMS 12463182 ** Replaced 2 x 25A H/V O/H fuses ( line clash ) | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.017276 | 11 | 2017 | 2016-07-19 | C | 42 | 0.017276 | 0.0001262
1 | 12463200 | 2016-07-19 22:50 | 2016-07-19 23:40 | 50 | 5 | 250 | 0.00075121 | 0.000706 | 1.5024e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W13472 | BINDER | Em switching to replace faulty insulator & re bind conductor. Isolation at Fuses FC4144 ( spur ) Conductor re bound insulator replaced all service restored. | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000706 | 11 | 2017 | 2016-07-19 | C | 5 | 0.000706 | 1.5024e-05
1 | 12463384 | 2016-07-19 22:05 | 2016-07-20 13:16 | 910 | 51 | 11610.7 | 0.034888 | 0.034428 | 0.00017728 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P11946 | INSULATOR | Recloser 4443/2 tripped on E/F flag, line was sectionalised and patrolled and a section of line past Fuses P65 was left off due to the terrain needs to be patrolled in day light. 8 customers affected, retailer has called to ask for ETR...at the moment 2.30pm. Damaged Insulator found at Pole P11946 - Isolated at ABS K41 and ABS 4443/1 and Links 4443/6. Faultman didn't have keys to open ABS K40 Insulator removed as two cross arm pole 2r line patrol 0002 2r repair 1152 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.034428 | 11 | 2017 | 2016-07-19 | C | 51 | 0.034428 | 0.00017728
1 | 12463704 | 2016-07-19 22:26 | 2016-07-20 11:51 | 804 | 43 | 15359.2 | 0.046152 | 0.045764 | 0.00012921 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 12003 | BINDER | Fault located between ABS's P51 & E45 during sectionlising. Faultmen unable to locate cause of fault in the dark. Area left Isolated until morning. Broken binder found at pole 12003 - cause age all binders replaced as other to close to failing Used 3 x binders 2r line patrol 0116 2r repair 1052 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.045764 | 11 | 2017 | 2016-07-19 | C | 43 | 0.045764 | 0.00012921
1 | 12463895 | 2016-07-19 22:37 | 2016-07-21 12:00 | 2242 | 1 | 1022.9833 | 0.0030739 | 0.003064 | 6.0096e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | w127901 | NONE | NDR: 047815 Fuses blown at fuses TC4408, line patrolled , possible line down in gully will need to be repaired in morning High wind & rain | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.003064 | 11 | 2017 | 2016-07-19 | C | 1 | 0.003064 | 6.0096e-06
1 | 12464916 | 2016-07-19 23:28 | 2016-07-20 01:59 | 150 | 1425 | 44235.6833 | 0.13292 | 0.12007 | 0.0033864 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 200674 | CIRCUIT BREAKER (HV) | ( BHM 1 ) CB1, Recloser 9803/2 tripped A, B & C Ph O/C, L/O. Feeder sectionalised & found tree/ branch on line at pole 200674. Isolations between recloser links 9803/4, ABS SD3 058 & ABS SD3 073 with back feed via sectionaliser 9805. Tree/ branch removed all service restored Materials Nil NDR No 44160 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.12007 | 11 | 2017 | 2016-07-19 | C | 1425 | 0.12007 | 0.0033864
1 | 12467689 | 2016-07-19 23:58 | 2016-07-20 13:58 | 839 | 383 | 35501.7667 | 0.10668 | 0.10322 | 0.0011508 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 740152 | CONDUCTOR - REPAIR/REHANG | Recloser 4812/2 tripped on E/F flags, line was sectionalised and patrolled and the faultman found lines down at pole 740152, due to trees from forest plantation, faultman isolated lines at Fuses 5698 and will return in morning with tree contractor to cut away trees and then repair lines down, it is to dangerous to repair at night very windy and trees do not look stable. 2r line patrol 0041 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.10322 | 11 | 2017 | 2016-07-19 | C | 383 | 0.10322 | 0.0011508
1 | 12469074 | 2016-07-20 01:40 | 2016-07-20 02:24 | 44 | 122 | 4889.0667 | 0.014691 | 0.01359 | 0.00036659 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | 2822 | UNKNOWN | CB 2822 tripped on E/F flags, Recloser 4848 tripped on A phase O/C & E/F flags & Recloser 6942 tripped on C phase O/C & E/F flags , line was patrolled no fault found but at time of tripping there was a big lightning storm that went over the area, suspect tripping due to lightning. 2r line patrol 0206 2r repair no | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.01359 | 11 | 2017 | 2016-07-20 | C | 122 | 0.01359 | 0.00036659
1 | 12469215 | 2016-07-20 01:53 | 2016-07-20 02:43 | 50 | 256 | 12812.8 | 0.0385 | 0.036192 | 0.00076923 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | 6610 | UNKNOWN | Recloser 6610 tripped on A & B phase O/C flags, line was checked no found found suspect lightning strike as a big lightning storm went over the area. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.036192 | 11 | 2017 | 2016-07-20 | C | 256 | 0.036192 | 0.00076923
1 | 12470026 | 2016-07-20 02:06 | 2016-07-20 04:20 | 134 | 3 | 402.1 | 0.0012082 | 0.001181 | 9.0143e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 772362 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 2629 & transformer X242, customer reported a big lightning storm past over when all supply went out. 3 X 5 amp HV fuses replaced ( Fuses 2629) Pole 772362 3 X 2 amp HV fuses replaced ( X242) Pole 772381 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001181 | 11 | 2017 | 2016-07-20 | C | 3 | 0.001181 | 9.0143e-06
1 | 12470525 | 2016-07-20 02:14 | 2016-07-20 05:10 | 176 | 1 | 176.4 | 0.00053005 | 0.000521 | 3.0047e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 772538 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at transformer X4188 at pole 772538 3 X 2 amp HV fuses replaced | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000521 | 11 | 2017 | 2016-07-20 | C | 1 | 0.000521 | 3.0047e-06
1 | 12473220 | 2016-07-20 06:10 | 2016-07-20 11:10 | 300 | 9 | 2700 | 0.008113 | 0.008031 | 2.7043e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 776415 | POLE | Derek Fraser 021 754 935, No Power Tree found through lines at Pole 776415 - Isolated at Fuses 4205 Used 1 x Pole, 1 X HV crossarm complete, 2x 8amp fuses, 10 mtrs of conductor NDR # O47112 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.008031 | 11 | 2017 | 2016-07-20 | C | 9 | 0.008031 | 2.7043e-05
1 | 12473874 | 2016-07-20 07:08 | 2016-07-20 15:31 | 503 | 3 | 1509.95 | 0.0045371 | 0.00451 | 9.0143e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 772366 | FUSE - ELEMENT/LINK (HV) | 3 x 2amp at transformer and 3 x 3amp at fuses due to lightning. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.00451 | 11 | 2017 | 2016-07-20 | C | 3 | 0.00451 | 9.0143e-06
1 | 12473895 | 2016-07-20 07:13 | 2016-07-20 14:30 | 436 | 4 | 1746.8 | 0.0052488 | 0.005212 | 1.2019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781075 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp Fuses due to weather. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.005212 | 11 | 2017 | 2016-07-20 | C | 4 | 0.005212 | 1.2019e-05
1 | 12474041 | 2016-07-20 07:21 | 2016-07-20 16:10 | 528 | 4 | 2114.9333 | 0.0063549 | 0.006318 | 1.2019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 772344 | FUSE - ELEMENT/LINK (HV) | 3 x 2amp fuses due to lightning. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.006318 | 11 | 2017 | 2016-07-20 | C | 4 | 0.006318 | 1.2019e-05
1 | 12474065 | 2016-07-20 03:23 | 2016-07-20 08:14 | 291 | 41 | 11936.4667 | 0.035867 | 0.035497 | 0.0001232 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | wkogco22 | UNKNOWN | Recloser 9454/2 Tripped. Non SCADA Recloser. Line Patrolled no fault found. Possible wind blown Derbis. Tree branches across the raod | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.035497 | 11 | 2017 | 2016-07-20 | C | 41 | 0.035497 | 0.0001232
1 | 12474075 | 2016-07-20 07:27 | 2016-07-20 10:00 | 153 | 2 | 306.8 | 0.00092187 | 0.000903 | 6.0095e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 738431 | FUSE - ELEMENT/LINK (HV) | 3 x 3amp due to lightning | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000903 | 11 | 2017 | 2016-07-20 | C | 2 | 0.000903 | 6.0095e-06
1 | 12474086 | 2016-07-20 07:28 | 2016-07-20 16:00 | 511 | 1 | 511.8333 | 0.001538 | 0.001528 | 3.0047e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 772370 | FUSE - ELEMENT/LINK (HV) | 3 x 2 amp fuse @ transformer. 3 x 3amp fuses @ 4164 due to lightning. 13/10/2016: On Site time amended to reflect the ERoad data provided by Downer. Crew Times do not appear to have been done as times do not align with the ERoad data activity in the area for this faultman. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001528 | 11 | 2017 | 2016-07-20 | C | 1 | 0.001528 | 3.0047e-06
1 | 12474347 | 2016-07-20 07:55 | 2016-07-20 09:55 | 119 | 7 | 838.4833 | 0.0025195 | 0.002456 | 2.1034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 800936 | JUMPER | Customer heard sparking noises from meter box, has switched power off. 7.56am advised Tallia at svs hub & emailed because meterboard has been switched off and isolated I have changed to Priority back to 83 not 999. Replaced blown jumper at transformer - isolated for ap. | F4 | CROFTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.002456 | 11 | 2017 | 2016-07-20 | C | 7 | 0.002456 | 2.1034e-05
1 | 12474803 | 2016-08-02 08:55 | 2016-08-02 10:50 | 115 | 66 | 7590 | 0.022803 | 0.022208 | 0.00019829 | NAPA ID:21525 TP_TE MATAI GXP > PAENGAROA SUB > MAKETU | 11 | Planned | 021525 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 218615 | NONE | Replace double cross arms. Works location: Lyndhurst Ave. WO 30026215 | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.011104 | 5.5 | 2017 | 2016-08-02 | B | 66 | 0.022208 | 0.00019829
1 | 12475326 | 2016-07-20 08:35 | 2016-07-20 13:50 | 315 | 4 | 1261.2667 | 0.0037899 | 0.003753 | 1.2019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 781103 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp fuse due to weather | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.003753 | 11 | 2017 | 2016-07-20 | C | 4 | 0.003753 | 1.2019e-05
1 | 12475378 | 2016-07-20 08:40 | 2016-07-20 08:42 | 1 | 767 | 1124.9333 | 0.0033802 | 0 | 0.0023047 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Tripping due to 2 phase regulator during planned switching 22670 | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0 | 11 | 2017 | 2016-07-20 | C | 767 | 0 | 0.0023047
1 | 12476301 | 2016-08-02 09:15 | 2016-08-02 15:25 | 370 | 129 | 47730 | 0.1434 | 0.14224 | 0.00038756 | NAPA ID:21864 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 021864 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N13098 | NONE | Puriri Pole Renewals Shut 9, Work area between IC526 and IC377. Work on Poles N13123, N2040, N2705, N13098, N2706, N13131/N13132, N2695, N2677, N12826, N13020, N2344. Works location: Paeroa kopu Rd, Thames. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.071118 | 5.5 | 2017 | 2016-08-02 | B | 129 | 0.14224 | 0.00038756
1 | 12476342 | 2016-08-04 09:10 | 2016-08-04 13:40 | 270 | 26 | 7020 | 0.02109 | 0.020855 | 7.8112e-05 | NAPA ID:21865 TP_KOPU GXP > MATATOKI SUB > PURIRI | 11 | Planned | 021865 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N13035 | NONE | Puriri Pole Renewals Shut 16, Work area beyond IC1136. Work on Poles N0960, N712294, N0968, N0974, N0975, N0982, N13026, N0938, N0940, N13041, N0925, N0928, N0937, N13033, N13035. Works location: Townsend Rd, Thames. WO 30017847 | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.010427 | 5.5 | 2017 | 2016-08-04 | B | 26 | 0.020855 | 7.8112e-05
1 | 12476466 | 2016-08-02 08:15 | 2016-08-02 15:35 | 440 | 170 | 74800 | 0.22473 | 0.22319 | 0.00051074 | NAPA ID:19267 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > CAMBRIDGE RD TAURANGA | 11 | Planned | 019267 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 203783 | NONE | 1 / Install Live Line Gap at pole 203783. 2 / Replace poles and reconductor feeder. 3/ LLWP Jumoer gap out. Works location: Bongard St. WO 30019275 | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.1116 | 5.5 | 2017 | 2016-08-02 | B | 170 | 0.22319 | 0.00051074
1 | 12476602 | 2016-07-20 16:31 | 2016-07-20 18:04 | 93 | 58 | 5394 | 0.016208 | 0.015685 | 0.00017428 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/107 & P46224 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 12.27pm blown tx T8/107 will need to be replaced today Transformer found to be faulty and replaced Line down after same fault occurred after transformer replaced under own AP Isolated at ASB's U22 & U31 with backfeed via ABS 10169 and replaced +/- 10m No8 wire | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.015685 | 11 | 2017 | 2016-07-20 | C | 58 | 0.015685 | 0.00017428
1 | 12476621 | 2016-08-04 08:25 | 2016-08-04 13:55 | 330 | 170 | 55403 | 0.16645 | 0.16492 | 0.00051073 | NAPA ID:19269 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > CAMBRIDGE RD TAURANGA | 11 | Planned | 019269 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 203783 | NONE | 1 / LLWP TO RE OPEN LL GAP AT POLE 203783. 2 / REPLACE POLES AND RECON FEEDER. 3/ LLWP TO REMOVE GAP AT POLE 203783. Works location: Bongard St. WO 30019275 | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.082458 | 5.5 | 2017 | 2016-08-04 | B | 170 | 0.16492 | 0.00051073
1 | 12477942 | 2016-07-20 11:34 | 2016-07-20 13:27 | 113 | 127 | 10630.2667 | 0.031942 | 0.030796 | 0.00038161 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 448006 | NONE | Branch found on lines at Pole 448006 during sectionlising, Cleared using hot sticks 2r line patrol 1251 | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.030796 | 11 | 2017 | 2016-07-20 | C | 127 | 0.030796 | 0.00038161
1 | 12478223 | 2016-07-20 11:42 | 2016-07-20 15:50 | 247 | 2 | 495.0667 | 0.0014876 | 0.001469 | 6.0095e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 772292 | FUSE - ELEMENT/LINK (HV) | 3 x 2amp fuses due to lightning | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001469 | 11 | 2017 | 2016-07-20 | C | 2 | 0.001469 | 6.0095e-06
1 | 12478224 | 2016-08-09 08:15 | 2016-08-09 14:52 | 397 | 2 | 794 | 0.0023853 | 0.002367 | 6.0083e-06 | NAPA ID:19273 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > CAMBRIDGE RD TAURANGA | 11 | Planned | 019273 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9612/2 | NONE | Replace poles and reconductor feeder wire. Works location: Chadwich Rd. WO 30019275 | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0011835 | 5.5 | 2017 | 2016-08-09 | B | 2 | 0.002367 | 6.0083e-06
1 | 12478309 | 2016-07-20 15:11 | 2016-07-20 16:20 | 69 | 1 | 69 | 0.00020733 | 0.000198 | 3.0047e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13729 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Damaged DDO Found at Transformer T4/42. Isolated at ABS F63 - Used 1 x DDO Carrier ansd Base 2 x 2amp fuses | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.000198 | 11 | 2017 | 2016-07-20 | C | 1 | 0.000198 | 3.0047e-06
1 | 12478532 | 2016-08-03 09:30 | 2016-08-03 13:10 | 220 | 23 | 5060 | 0.015202 | 0.014994 | 6.91e-05 | NAPA ID:22153 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | 022153 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FC1488 | NONE | Install DDOs and Lightning Arrestors at various sites on SWER Line. Works location: Port Jackson, Colville Coromandel. WO 30017206 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.007497 | 5.5 | 2017 | 2016-08-03 | B | 23 | 0.014994 | 6.91e-05
1 | 12478536 | 2016-07-20 12:26 | 2016-07-21 14:55 | 1589 | 28 | 8852 | 0.026598 | 0.026346 | 8.4134e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | C13106 | POLE | Car vs Pole. 11m Pole, 3 pin HT Xarm, 1 DDO xarm, 3 DDOs. FM has confirmed School will not be back on till tomorrow due to a damaged UG cable that Powerco have asked them to replace. FM spoke with customer re this. Message has been left on 02040078934. | F4 | TOWNSHIP & LS | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.026346 | 11 | 2017 | 2016-07-20 | C | 28 | 0.026346 | 8.4134e-05
1 | 12478762 | 2016-08-03 10:00 | 2016-08-03 11:40 | 100 | 2 | 200 | 0.00060087 | 0.000582 | 6.0086e-06 | NAPA ID:22026 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | 022026 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5337 | NONE | To replace the existing 15kVA transformer with a 30kVA. Works location: Pukekauri Rd, Waihi. WO 30029958 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.000291 | 5.5 | 2017 | 2016-08-03 | B | 2 | 0.000582 | 6.0086e-06
1 | 12478851 | 2016-08-04 09:37 | 2016-08-04 14:40 | 303 | 4 | 1212 | 0.0036412 | 0.003605 | 1.2017e-05 | NAPA ID:21526 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 021526 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2-137 | NONE | Replace transformer and structure. Works location: Pahoia Rd, Tauranga. WO 30025021 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.0018025 | 5.5 | 2017 | 2016-08-04 | B | 4 | 0.003605 | 1.2017e-05
1 | 12480028 | 2016-08-15 22:30 | 2016-08-16 00:24 | 114 | 35 | 3990 | 0.011986 | 0.01167 | 0.00010514 | NAPA ID:22042 TP_BUNNYTHORPE GXP > KEITH ST SUB > KEITH ST 14 | 11 | Planned | 022042 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | G213 | NONE | Clean up earths on Magnafix G213, clean down bushings on transformer, move breather away from live equipment. Works location: Featherston St. WO 30006945 | F3 | KEITH ST 22 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 0.005835 | 5.5 | 2017 | 2016-08-15 | B | 35 | 0.01167 | 0.00010514
1 | 12480070 | 2016-07-20 19:05 | 2016-07-20 20:14 | 69 | 70 | 4830 | 0.014513 | 0.013882 | 0.00021034 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC4833 | FUSE - HOLDER/BASE (LV) | Isolated at Sw/Gaer IC3018 to replace burnt out 1 x 200amp and elect fuse & Base | F3 | PAUANUI | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.013882 | 11 | 2017 | 2016-07-20 | C | 70 | 0.013882 | 0.00021034
1 | 12480114 | 2016-08-15 09:21 | 2016-08-15 11:55 | 154 | 52 | 8008 | 0.024056 | 0.023587 | 0.00015621 | NAPA ID:21933 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 021933 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | P13059 | NONE | Isolate lines for tree work to be carried out by Treescape. Works location: Pohangina Rd. WO 30026290 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.011794 | 5.5 | 2017 | 2016-08-15 | B | 52 | 0.023587 | 0.00015621
1 | 12480465 | 2016-08-10 08:34 | 2016-08-10 12:41 | 247 | 1 | 247 | 0.00074202 | 0.000733 | 3.0041e-06 | NAPA ID:21523 TP_TE MATAI GXP > TE PUKE SUB > KAITUNA | 11 | Planned | 021523 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | FP895 | NONE | Replace HV & LV cross arms + DDO's. Also Replace Transformer TE6-192 which currently has a defect on it. Works location: Kaituna Rd, Te Puke. WO 30025522 | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.0003665 | 5.5 | 2017 | 2016-08-10 | B | 1 | 0.000733 | 3.0041e-06
1 | 12480678 | 2016-07-20 11:45 | 2016-07-20 16:00 | 255 | 3 | 765 | 0.0022987 | 0.002271 | 9.0143e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | S12636 | CONDUCTOR - REPAIR/REHANG | Retailer called to advised that there is a line down at customers shed. have advised SMC Lines repaired. Isolation at fuses FC2735. 10m Squirrel conductor, 6x squirrel sleeves | F3 | TOTARA | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.002271 | 11 | 2017 | 2016-07-20 | C | 3 | 0.002271 | 9.0143e-06
1 | 12480878 | 2016-07-20 19:00 | 2016-07-21 18:17 | 1397 | 2 | 294 | 0.00088341 | 0.000865 | 1.2019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 288639 | CONDUCTOR - REPAIR/REHANG | 20/07/16 at 19:00, Pongakawa Sub, CB 2 Otamarakau Feeder. Found tree through lines at Pole 288639. Isolated Lines at Fuses FP1136. Generator connected: 2100 - 1750. Permit issued & repairs carried out. All Power Restored on completion. 160m of Conductor used & 5x Connectors. Waiting on NDR Number for this job. Check for safety - line down in the forest one pole down from the look out. pole number 268844 and just up the road where the pole was replaced a couple of days ago. Advised control and smc of 999. To be attended today 21/7 | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000865 | 11 | 2017 | 2016-07-20 | C | 2 | 0.000865 | 1.2019e-05
1 | 12481012 | 2016-07-20 18:54 | 2016-07-20 19:13 | 18 | 83 | 1546.5667 | 0.0046471 | 0.003898 | 0.0002494 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 200851 | CONDUCTOR - REPAIR/REHANG | Polymer strain has come adrift, HV is hanging down low, very close to 400V. Pole 200851 9 Rarapua Place, Tauranga. Second 1 R to keep outage to a Minimium. Replaced nut on Polymer strain resecured to cross arm. Isolated at Fuses FP1092 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.003898 | 11 | 2017 | 2016-07-20 | C | 83 | 0.003898 | 0.0002494
1 | 12482338 | 2016-07-21 01:17 | 2016-07-21 04:05 | 168 | 41 | 5717.4333 | 0.01718 | 0.016809 | 0.0001232 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | R28 & R29 | FUSE - ELEMENT/LINK (HV) | Line from fuses R28 sectionalised and patrolled with nothing obvious found replaced HV fuses3x 8a @ R28 and 3x 6a @ R29 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.016809 | 11 | 2017 | 2016-07-21 | C | 41 | 0.016809 | 0.0001232
1 | 12484472 | 2016-07-21 03:49 | 2016-07-21 06:58 | 189 | 498 | 46773.8333 | 0.14054 | 0.13606 | 0.0016286 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 757544 | CONDUCTOR - REPAIR/REHANG | Report received of lines down @ 775 Upper pitone road and replaced insulator | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.13606 | 11 | 2017 | 2016-07-21 | C | 498 | 0.13606 | 0.0016286
1 | 12487358 | 2016-08-09 09:17 | 2016-08-09 14:13 | 296 | 4 | 1184.6667 | 0.0035589 | 0.003522 | 1.2017e-05 | NAPA ID:21848 TP_WAIKINO GXP > WAIHI SUB > WAITAWHETA | 11 | Planned | 021848 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P13194 | NONE | To replace cross arms at poles P13192 & P13194. Works location: Frankton Rd. WO 30012299 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.001761 | 5.5 | 2017 | 2016-08-09 | B | 4 | 0.003522 | 1.2017e-05
1 | 12487501 | 2016-08-09 08:49 | 2016-08-09 14:55 | 365 | 25 | 9142.9167 | 0.027467 | 0.027241 | 7.5104e-05 | NAPA ID:22142 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | 022142 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9980 | NONE | Replace cross arms and line hardware. Works location: Te Reinga Owera Rd. WO 30002514 | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.013621 | 5.5 | 2017 | 2016-08-09 | B | 25 | 0.027241 | 7.5104e-05
1 | 12496580 | 2016-08-16 08:31 | 2016-08-16 15:03 | 391 | 25 | 9790.8333 | 0.029411 | 0.029185 | 7.5098e-05 | NAPA ID:22144 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | 022144 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Recloser 9980 | NONE | Replace XARMS and Line Hardware. Works location: Te Reinga Owera Rd. WO 30002514 | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.014592 | 5.5 | 2017 | 2016-08-16 | B | 25 | 0.029185 | 7.5098e-05
1 | 12496619 | 2016-08-23 08:36 | 2016-08-23 14:44 | 368 | 25 | 9200.4167 | 0.027635 | 0.027409 | 7.5092e-05 | NAPA ID:22149 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | 022149 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9980 | NONE | Replace cross arms and line hardware. Works location: Te Reinga Owera Rd. WO 30002514 | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.013704 | 5.5 | 2017 | 2016-08-23 | B | 25 | 0.027409 | 7.5092e-05
1 | 12496718 | 2016-08-11 09:15 | 2016-08-11 15:40 | 385 | 40 | 15400 | 0.046263 | 0.045902 | 0.00012016 | NAPA ID:22154 TP_WAIHOU GXP | 11 | Planned | 022154 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC690 | NONE | Ngarua Feeder Step 4, Shut 2. Specified renewal works completed between IC690 and IP 17, (note isolation area is larger to allow safe earthing). Works location: Waiheku & Chudleigh Rds, Waihou. WO 30017830 | F4 | NGARUA | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.022951 | 5.5 | 2017 | 2016-08-11 | B | 40 | 0.045902 | 0.00012016
1 | 12496996 | 2016-07-21 11:23 | 2016-07-21 13:12 | 109 | 5 | 545 | 0.0016376 | 0.001592 | 1.5024e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 217237 | CONDUCTOR - REPAIR/REHANG | at 09:33, Tauranga GXP, CB 11 Kaimai Drive Feeder, Recloser 9275 Tripped, E/F, Auto Reclosed. Sectionaliser 9270 Flagged with Ph A E/F O/C. Call came in of lines down. Found fuses at SE2-012 had blown due to tree falling through lines. Lines down at Pole 217237. Isolated lines at Fuses SE2-012. Permit issued & repairs carried out. All Power restored on completion. 1x HV Fuse 10A Replaced, 2x Condcutor Links Replaced. NDR N400149 Customer has now found tree on the driveway and live wires hanging. This driveway is for 6 ppties. 10.26am advised Shannon at svs hub - advised control | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001592 | 11 | 2017 | 2016-07-21 | C | 5 | 0.001592 | 1.5024e-05
1 | 12497399 | 2016-08-15 09:00 | 2016-08-15 14:48 | 348 | 11 | 3828 | 0.011499 | 0.0114 | 3.3044e-05 | NAPA ID:22157 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > NGARUA | 11 | Planned | 022157 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1052 | NONE | Ngarua Feeder Step 5, Shut 23. Specified renewal works completed between beyond Temp 78. Works location: Chudleigh Rd, Waihou. WO 30017830 | F4 | NGARUA | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0057 | 5.5 | 2017 | 2016-08-15 | B | 11 | 0.0114 | 3.3044e-05
1 | 12497509 | 2016-07-21 19:15 | 2016-07-21 19:49 | 34 | 95 | 3230 | 0.0097054 | 0.008849 | 0.00028545 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36440 | BINDER | Floating Conductor Reported By Darrell Wrothery at Pole P36440. 1R - Fm Required to Re-Bind conductors All three phases rebound @ pole P36440 | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.008849 | 11 | 2017 | 2016-07-21 | C | 95 | 0.008849 | 0.00028545
1 | 12497845 | 2016-08-17 09:04 | 2016-08-17 14:51 | 346 | 6 | 2081.1 | 0.0062514 | 0.006197 | 1.8023e-05 | NAPA ID:22158 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > NGARUA | 11 | Planned | 022158 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP350 | NONE | Ngarua Feeder Step 6, Shut 4. Specified renewal works completed between beyond FP350. Works location: Seddon Rd, Waihou. WO 30017830 | F4 | NGARUA | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0030985 | 5.5 | 2017 | 2016-08-17 | B | 6 | 0.006197 | 1.8023e-05
1 | 12499922 | 2016-08-17 09:45 | 2016-08-17 13:20 | 215 | 10 | 2150 | 0.0064584 | 0.006368 | 3.0039e-05 | NAPA ID:22127 TP_BUNNYTHORPE GXP > MILSON SUB > BUNNYTHORPE | 11.00000000 | Planned | 022127 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2/289 | NONE | Remove 1pole of 2pole structure, install new 11kV fuses on remaining pole, replace Transformer T2/289 onto remaining single pole | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.003184 | 5.5 | 2017 | 2016-08-17 | B | 10 | 0.006368 | 3.0039e-05
1 | 12500378 | 2016-07-21 17:57 | 2016-07-21 18:46 | 49 | 12 | 588 | 0.0017668 | 0.001658 | 3.6057e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T9/425 | JUMPER | Broken Jumper found at Transformer T9/425 Isolated at ABS's I36 & I 35, backfeed via ABS S26 Repaired jumper @ T9/425 | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.001658 | 11 | 2017 | 2016-07-21 | C | 12 | 0.001658 | 3.6057e-05
1 | 12500486 | 2016-07-21 17:34 | 2016-07-21 19:35 | 120 | 1 | 120.8 | 0.00036298 | 0.000353 | 3.0047e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | LI747 | FUSE - ELEMENT/LINK (HV) | Found 2 fuses @ transformer L1057 blown and removed all due to transformer being faulty . Closed 2x 6a fuses @ LI747 and supply restored . Transformer L1057 has no lv connected and is being reffered to GTL for further investigation | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000353 | 11 | 2017 | 2016-07-21 | C | 1 | 0.000353 | 3.0047e-06
1 | 12500686 | 2016-07-21 18:57 | 2016-07-21 20:00 | 62 | 1 | 62.55 | 0.00018795 | 0.000178 | 3.0047e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4664W | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a HV fuses @ transformer 4664W | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000178 | 11 | 2017 | 2016-07-21 | C | 1 | 0.000178 | 3.0047e-06
1 | 12502851 | 2016-07-22 02:12 | 2016-07-22 03:34 | 82 | 661 | 49002.65 | 0.14724 | 0.14128 | 0.0019861 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | UNKNOWN | Recloser 9228 Trip No Flags.Line patrolled & sectionalised no fault found. 2r line patrol 0316 no repair | F3/F4 | THAMES COAST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.14128 | 11 | 2017 | 2016-07-22 | C | 661 | 0.14128 | 0.0019861
1 | 12505270 | 2016-07-22 13:53 | 2016-07-22 15:00 | 67 | 103 | 6901 | 0.020736 | 0.019807 | 0.00030949 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771335 | CROSSARM - WHOLE ASSEMBLY | Replaced rotten crossarm. Materials Used: Complete crossarm and accessories. | F3 | WESTMERE PEAT ST | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.019807 | 11 | 2017 | 2016-07-22 | C | 103 | 0.019807 | 0.00030949
1 | 12505277 | 2016-07-22 12:30 | 2016-07-22 14:22 | 111 | 37 | 4129.8167 | 0.012409 | 0.012075 | 0.00011118 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10 | CROSSARM - WHOLE ASSEMBLY | 11.58am spoke to control and they advised to send FM to HV fuses P10. Materials used cross arm complete 2 dead ends conductor. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.012075 | 11 | 2017 | 2016-07-22 | C | 37 | 0.012075 | 0.00011118
1 | 12505403 | 2016-08-03 08:45 | 2016-08-03 16:45 | 480 | 148 | 7696 | 0.023121 | 0.021787 | 0.00088929 | NAPA ID:22038 TP_KAITIMAKO GXP > WELCOME BAY SUB > VICTORY STREET | 11 | Planned | 022038 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 268154 | NONE | Isolate work Area, remove jumpers from LV Bushings of each TX and connect Generators. The Generation is being provided for the Outage under NAPA 22054. The Live Line Break is being made under NAPA 22034. | F3 | VICTORY STREET | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.010894 | 5.5 | 2017 | 2016-08-03 | B | 148 | 0.021787 | 0.00088929
1 | 12505491 | 2016-08-07 13:30 | 2016-08-07 15:49 | 138 | 1 | 138.9667 | 0.00041749 | 0.000408 | 3.0042e-06 | NAPA ID:22844 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | 022844 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | M38 | NONE | Calibration of 11kV metering unit to bring into test. Works location: Kakariki Proteins, Halcombe. WO 30027191 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000204 | 5.5 | 2017 | 2016-08-07 | B | 1 | 0.000408 | 3.0042e-06
1 | 12506992 | 2016-07-22 18:15 | 2016-07-22 23:00 | 285 | 1 | 285 | 0.00085635 | 0.000847 | 3.0047e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 710880 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Fuses found blown at Transformer P4055. Transformer found to be faulty - Isolated at transformer fuses. Used 1 x 30 kVA 3 ph Transformer, 2 x 3 amp fuses. | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000847 | 11 | 2017 | 2016-07-22 | C | 1 | 0.000847 | 3.0047e-06
1 | 12507368 | 2016-07-22 18:29 | 2016-07-22 21:02 | 153 | 345 | 2345 | 0.0070461 | 0.003936 | 0.00020132 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P37576 | INSULATOR | Damaged Insolater found at Pole P37576 during line patrol after a number of A/R on RS 4258 Isolated at ABS E3 - cause unknown. Used 1 x insulator 1 x pin 2 x binders | F4 | BUNNYTHORPE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.003936 | 11 | 2017 | 2016-07-22 | C | 345 | 0.003936 | 0.00020132
1 | 12508110 | 2016-07-23 05:18 | 2016-07-23 06:18 | 59 | 15 | 895 | 0.0026892 | 0.002553 | 4.507e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 760542 | INSULATOR | Line Patrol required after CB 220 Tripped and Locked out Line Patrolled with no fault found CB 220 tripped on closing, Fault found at pole 760542 Isolated at ABS 159 & CB I01, 6.6 kV lines below also Isolated at ABS's 5502 and 5496 with backfeed via ABS 5316. All 3 33kV insulators replaced | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.002553 | 6.6 | 2017 | 2016-07-23 | C | 15 | 0.002553 | 4.507e-05
1 | 12508180 | 2016-07-22 22:34 | 2016-07-22 23:35 | 60 | 24 | 1462.4 | 0.0043941 | 0.004177 | 7.2114e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P27404 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses T7 - line patrolled with no fault found. Used 2 x 10 amp fuses - possible cause bird strike | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.004177 | 11 | 2017 | 2016-07-22 | C | 24 | 0.004177 | 7.2114e-05
1 | 12508528 | 2016-07-23 07:41 | 2016-07-23 12:54 | 313 | 111 | 12543.4167 | 0.037689 | 0.036688 | 0.00033352 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 228005 | POLE | Pole 228005 fallen over in soft ground. A line break has been cut either side at Poles 228004 and 228006 and Power restored. Pole to be replaced at a later date. | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.036688 | 11 | 2017 | 2016-07-23 | C | 111 | 0.036688 | 0.00033352
1 | 12508750 | 2016-07-23 08:14 | 2016-07-23 15:15 | 421 | 433 | 80942.6 | 0.24321 | 0.2393 | 0.0015895 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | IC1457 | SWITCH (HV) | Switch Gear IC1457 Faulty. Cable has been disconnected from Switch. Switch isolated and power restored. Switch to be replaced at a later date. | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.2393 | 11 | 2017 | 2016-07-23 | C | 433 | 0.2393 | 0.0015895
1 | 12510069 | 2016-07-23 16:26 | 2016-07-23 19:25 | 179 | 32 | 5740.2667 | 0.017248 | 0.016959 | 9.615e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | D12741 | CONDUCTOR - REPAIR/REHANG | Maurice Doig Attended. Found tree branch on lines at Pole D12741 - removed with hot stick. Reloaded, Relivened at Fuses FP1313. All Power Restored on completion. 2x 10A HV Fuses replaced. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.016959 | 11 | 2017 | 2016-07-23 | C | 32 | 0.016959 | 9.615e-05
1 | 12510358 | 2016-07-23 19:20 | 2016-07-23 19:59 | 39 | 5 | 195 | 0.00058592 | 0.00054 | 1.5023e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718387 | JUMPER | Blown Jumper found at Transformer M4123. Isolated at Fuses 6549 . Materials Used: 1 mtr of conductor 2 x sleeves. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.00054 | 11 | 2017 | 2016-07-23 | C | 5 | 0.00054 | 1.5023e-05
1 | 12510574 | 2016-07-23 18:59 | 2016-07-23 21:14 | 134 | 43 | 4365.1667 | 0.013116 | 0.012728 | 0.0001292 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Recloser 4251/2 Tripped B Ph O/C E/F L/O. Line Patrolled - No fault found during sectionlising. | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.012728 | 11 | 2017 | 2016-07-23 | C | 43 | 0.012728 | 0.0001292
1 | 12511854 | 2016-07-23 22:22 | 2016-07-24 03:40 | 318 | 22 | 6362.7833 | 0.019118 | 0.018919 | 6.6103e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 836386 | CONDUCTOR - REPAIR/REHANG | Lines down found at Pole 836386 fuses 7715 found blown. Fuses Tagged, Transformer T637 offloaded due to bear LV under only earthing point. Lines repaired. Materials Used 3 x 15 amp Hv fuses, 1 x 3 amp HV Fuse 1 x HV Insulator, 8 crimp sleeves &, 6 x binders. NDR 54454 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.018919 | 11 | 2017 | 2016-07-23 | C | 22 | 0.018919 | 6.6103e-05
1 | 12512133 | 2016-07-23 22:44 | 2016-07-24 03:44 | 299 | 314 | 29144.7 | 0.087571 | 0.08474 | 0.00094348 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 847755 | CONDUCTOR - REPAIR/REHANG | Line found down at Pole 847755 Isolated at ABS's TA875 & TA851 with backfeed via ABS TA876 Used 2 mtrs of conductor and 2 Sleeves | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.08474 | 11 | 2017 | 2016-07-23 | C | 314 | 0.08474 | 0.00094348
1 | 12512460 | 2016-07-23 22:53 | 2016-07-24 01:20 | 147 | 1 | 147.0833 | 0.00044194 | 0.000432 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4297T | FUSE - ELEMENT/LINK (HV) | 2 fuses found blown at Transformer 4297T. Used 2 x 3 amp fuse | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000432 | 11 | 2017 | 2016-07-23 | C | 1 | 0.000432 | 3.0046e-06
1 | 12512533 | 2016-07-23 23:34 | 2016-07-24 03:08 | 214 | 274 | 54175.95 | 0.16278 | 0.16031 | 0.00082329 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C1024 | UNKNOWN | Recloser C1024 Tripped A,B,C Ph O/C E/F. Line patrolled with no fault found. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.16031 | 11 | 2017 | 2016-07-23 | C | 274 | 0.16031 | 0.00082329
1 | 12512832 | 2016-07-23 23:56 | 2016-07-24 10:39 | 643 | 3402 | 653946.4667 | 1.9649 | 1.9342 | 0.010222 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | KINBRD030 | BINDER | at 23:58, Kinleith GXP, CB 2212 Tripped, Neutral Time O/C, L/O. Loss of Supply to Baird Rd Sub. Faultmen dispatched & investigation began. 33kV Line fault indicators checked - none flashing. While faultman was enroute to Kinleith Injection Plant to carryout switching, found Arm Strap had broken/rusted away at Pole KINBRD030. Substation Backfeed switching then commenced. Supply fully restored at 02:43. Don Masters Attended. Arm Replaced All backfeeds removed by 1045 | S4 | KINLEITH2212-BAIRD RD 33KV | KINLEITH 33 | Valley | TP_KINLEITH | Eastern Electricity | POWERCO | 1.9342 | 33 | 2017 | 2016-07-23 | C | 3402 | 1.9342 | 0.010222
1 | 12518425 | 2016-07-24 07:08 | 2016-07-25 14:39 | 1890 | 58 | 69716.3 | 0.20947 | 0.20895 | 0.00017427 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | 708645 | CONDUCTOR - REPAIR/REHANG | 1 x broken binder located at pole 708645. Isolation at ABS 5230. All supply restored following re-tieing of binder. 1 x binder only material required. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.20895 | 11 | 2017 | 2016-07-24 | C | 58 | 0.20895 | 0.00017427
1 | 12518849 | 2016-07-24 02:04 | 2016-07-24 05:33 | 209 | 411 | 33761.5333 | 0.10144 | 0.097737 | 0.0012349 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | C13432 | CONDUCTOR - REPAIR/REHANG | at 02:04, Mikkelsen Rd Sub, CB 5 Maungakawa Feeder, Tripped, B + C O/C, L/O. Faultman dispatched & investigation began. Feeder sectionalised to find fault. Found tree branches tangled in lines between ABS 722 & Sectionaliser 9715. Isolated Lines at ABS 722 and branches removed with Hot Stick. All Power Restored on Completion. Sean Malloy Attended. No Materials Used. NDR: 53802 | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.097737 | 11 | 2017 | 2016-07-24 | C | 411 | 0.097737 | 0.0012349
1 | 12520329 | 2016-07-24 03:42 | 2016-07-24 15:40 | 718 | 63 | 15851.25 | 0.047628 | 0.047059 | 0.00028244 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 374570 | CONDUCTOR - REPAIR/REHANG | Trees Through Lines at Pole 374870. Trees removed and lines restrung | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.047059 | 11 | 2017 | 2016-07-24 | C | 63 | 0.047059 | 0.00028244
1 | 12521243 | 2016-07-24 04:35 | 2016-07-24 07:34 | 179 | 227 | 24657.45 | 0.074088 | 0.072041 | 0.00093746 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 845156 | CROSSARM - ARM ONLY | CB C956 tripped on A & B phase O/C flags, line was patrolled and sectionalised and a tipped over cross arm was found at pole 845156, line was isolated at ABS's S502 & S596 to repair the cross arm. 1 X king pin Nut replaced. 2 X insulator nuts replaced | F4 | MOROA | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.072041 | 11 | 2017 | 2016-07-24 | C | 227 | 0.072041 | 0.00093746
1 | 12522262 | 2016-07-24 05:44 | 2016-07-24 08:46 | 182 | 679 | 36600.6333 | 0.10997 | 0.10385 | 0.0036116 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P09793 | INSULATOR | CB & Tripped A Ph O/C E/F, Line was patrolled and sectionalised and a floating wire was found at pole P09793, line was isolated at ABS's K33, K38 & K43 to repair floater. 1X 11KV insulator & binder replaced | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.10385 | 11 | 2017 | 2016-07-24 | C | 679 | 0.10385 | 0.0036116
1 | 12524335 | 2016-07-24 08:17 | 2016-07-24 10:13 | 115 | 2 | 231.1 | 0.00069438 | 0.000676 | 6.0093e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FP23 | FUSE - ELEMENT/LINK (HV) | 2 x 10A HV Fuses Replaced. Line Clash | F1/F4 | KOPU | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.000676 | 11 | 2017 | 2016-07-24 | C | 2 | 0.000676 | 6.0093e-06
1 | 12524474 | 2016-07-24 11:55 | 2016-07-24 14:45 | 170 | 2 | 340 | 0.0010216 | 0.001003 | 6.0093e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M3335 | INSULATOR | 2 x 2 amp fuses, M3335 Untangled lv conductors between 721389 and 721390 replaced 3 x pin and insulators | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001003 | 11 | 2017 | 2016-07-24 | C | 2 | 0.001003 | 6.0093e-06
1 | 12525917 | 2016-07-24 08:48 | 2016-07-24 12:15 | 206 | 631 | 365.6 | 0.0010985 | 0 | 1.2019e-05 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1332 | UNKNOWN | CB 1332 tripped on O/C & E/F flags & CB XT 30 tripped on A, B & C phase O/C & E/F flags, line was patrolled and sectionalised no fault was found, suspect line clashes in high winds. | S3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 0 | 33 | 2017 | 2016-07-24 | C | 631 | 0 | 1.2019e-05
1 | 12526202 | 2016-07-24 09:18 | 2016-07-24 10:06 | 47 | 780 | 36751 | 0.11042 | 0.10339 | 0.0023436 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P38618 | CONDUCTOR - REPAIR/REHANG | control advised of line down Colyton road 402 Colyton road, has had disconnect done tag#A12643 as trees brought down lines. ndr#046983, pulled up 3x 25mm copper wires, and used 3 meters of conductor re connected, pole#P38616 | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.10339 | 11 | 2017 | 2016-07-24 | C | 780 | 0.10339 | 0.0023436
1 | 12528289 | 2016-07-24 09:32 | 2016-07-24 23:46 | 853 | 105 | 21801.6667 | 0.065507 | 0.06456 | 0.00031549 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | P14736 | CONDUCTOR - REPAIR/REHANG | at 09:31, Kelvin Grove Sub, CB 8 Pohangina Feeder, Recloser E33 Tripped, Ph B O/C, E/F, L/O. Faultman dispatched & investigation began. Found tree through lines at Pole P14736. Isolated lines at ABS E36. Permit issued & repairs carried out. All Power Restored on Completion. 10m of conductor replaced, less than 1 span, 1 phase. 3x sleeves. NDR: 37479. Treescape brought in to remove trees. advised control of lines down, 202 forlong road | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.06456 | 11 | 2017 | 2016-07-24 | C | 105 | 0.06456 | 0.00031549
1 | 12528598 | 2016-07-24 09:36 | 2016-07-24 11:40 | 123 | 19 | 2351.25 | 0.0070647 | 0.006893 | 5.7089e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 772 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 772 line was patrolled no fault found suspect line clashes as high winds in area. 2 X 20 amp HV fuses replaced. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.006893 | 11 | 2017 | 2016-07-24 | C | 19 | 0.006893 | 5.7089e-05
1 | 12529033 | 2016-07-24 10:01 | 2016-07-24 13:55 | 233 | 101 | 14174.9167 | 0.042591 | 0.04168 | 0.00030347 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 360625 | CONDUCTOR - REPAIR/REHANG | Recloser C421 tripped on A & C phase fault, line was patrolled & sectionalised and the faultman found one of the phases had got court on a tree branch at pole 360625, line was isolated at ABS S67 so faultman could remove phase, tree branch was also cut down, faultman reported that the line span gaps are a distance apart so that what caused the phase getting caught on the branch. | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.04168 | 11 | 2017 | 2016-07-24 | C | 101 | 0.04168 | 0.00030347
1 | 12529400 | 2016-07-24 09:57 | 2016-07-24 11:08 | 70 | 2 | 138.7167 | 0.0004168 | 0.000398 | 6.0093e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | UNKNOWN | cb C817 tripped no flags nothing found | F3 | OXFORD ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000398 | 11 | 2017 | 2016-07-24 | C | 2 | 0.000398 | 6.0093e-06
1 | 12530905 | 2016-07-24 12:47 | 2016-07-24 13:30 | 43 | 7 | 301 | 0.00090441 | 0.000841 | 2.1033e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761424 | CROSSARM - WHOLE ASSEMBLY | Isolated at Fuses 5439. Repair crossarm. 1 x kingpin bolt. | F3 | KAIMATA | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000841 | 6.6 | 2017 | 2016-07-24 | C | 7 | 0.000841 | 2.1033e-05
1 | 12530987 | 2016-07-25 10:10 | 2016-07-25 10:40 | 30 | 32 | 960 | 0.0028845 | 0.002596 | 9.6148e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 824833 | CROSSARM - WHOLE ASSEMBLY | check fuses 7639 **26/7 FAX ADVISED CUST HAS PART POWER AS WELL*** Faultman found a tipped over cross arm at pole 824833, line was isolated at Fuses 7639 to repair the cross arm. 1 X bras bolt & nut used | F4 | PUKETIRO | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.002596 | 11 | 2017 | 2016-07-25 | C | 32 | 0.002596 | 9.6148e-05
1 | 12531851 | 2016-07-24 10:35 | 2016-07-24 11:38 | 63 | 18 | 1134 | 0.0034073 | 0.003245 | 5.4084e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 741852 | CONDUCTOR - REPAIR/REHANG | Faultman found a line down at pole 741852, line was isolated at ABS's 445 & 12114 to repair the line. 1 metre ngamu conductor used & 2 X sleeves used | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.003245 | 11 | 2017 | 2016-07-24 | C | 18 | 0.003245 | 5.4084e-05
1 | 12532257 | 2016-07-25 09:34 | 2016-07-25 10:31 | 56 | 17 | 966.1667 | 0.002903 | 0.002749 | 5.1079e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 812878 | POLE | broken HV pole, holding up pole using crane over night and power is restored for now. Line was isolated at ABS S514 to replace broken pole 812878. 1 X 11KV pole and all hardware replaced. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.002749 | 11 | 2017 | 2016-07-25 | C | 17 | 0.002749 | 5.1079e-05
1 | 12532610 | 2016-07-24 11:24 | 2016-07-24 16:06 | 281 | 117 | 32990.1 | 0.099124 | 0.098069 | 0.00035155 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P26824 | INSULATOR | V61. Ph A & B OC. Faultman found a floating wires at pole P26824. 6 x 11 KV insulators replaced | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.098069 | 11 | 2017 | 2016-07-24 | C | 117 | 0.098069 | 0.00035155
1 | 12534110 | 2016-07-24 11:46 | 2016-07-24 19:25 | 458 | 9 | 4128.45 | 0.012405 | 0.012323 | 2.7042e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 441706 | FUSE - ELEMENT/LINK (HV) | 2 x 8amp 4036 | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.012323 | 11 | 2017 | 2016-07-24 | C | 9 | 0.012323 | 2.7042e-05
1 | 12534306 | 2016-07-24 17:09 | 2016-07-24 19:28 | 139 | 37 | 5143 | 0.015453 | 0.015119 | 0.00011117 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P40953 | JUMPER | check oms 12537089, 12561490, 12561795 , 12554154,12555790, 12555803, blown jumper on hv side. Blown jumper at ABS A22 | F4 | TREMAINE AVE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.015119 | 11 | 2017 | 2016-07-24 | C | 37 | 0.015119 | 0.00011117
1 | 12534313 | 2016-07-25 10:30 | 2016-07-25 12:41 | 131 | 1 | 131 | 0.00039361 | 0.000384 | 3.0046e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC3463 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Advised SMC Clashing LV Lines. HV Fuse blown on Transformer Faulty Transformer Follow up job entered 12558381 - To replace tranformer and fix LV Line Spacings. 2 Customer affected. One has been spoken to by the contractor and is okay with having no power. The second is not home and no contact came through. 4wd drive vehicles required to access customer property to reach pole (this pole is on the customer who isn't homes property) approx 3 man job. 128 Stokes Valley Road 0000055192UNCD4 - rung customer who has got somewhere else they can stay. | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.000384 | 11 | 2017 | 2016-07-25 | C | 1 | 0.000384 | 3.0046e-06
1 | 12534356 | 2016-07-24 11:53 | 2016-07-24 13:42 | 108 | 1033 | 104981.35 | 0.31543 | 0.30612 | 0.0031038 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB X20 | UNKNOWN | CB X20 tripped on B & C phase O/C flags, line was patrolled and sectionalised and no fault was found faultman did inform of bark flying around | S4 | FEILDING-KIMBOLTON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.30612 | 33 | 2017 | 2016-07-24 | C | 1033 | 0.30612 | 0.0031038
1 | 12534455 | 2016-07-24 12:03 | 2016-07-24 15:40 | 216 | 26 | 5625.1 | 0.016902 | 0.016667 | 7.8121e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36131 | FUSE - ELEMENT/LINK (HV) | Check OMS: 12554125 and 12549390, 12534584 - 660 HIMATANGI BLOCK ROAD , KAIRANGA Reload at B20 2 x 10 A Wind | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.016667 | 11 | 2017 | 2016-07-24 | C | 26 | 0.016667 | 7.8121e-05
1 | 12535047 | 2016-07-24 12:14 | 2016-07-24 17:50 | 336 | 8 | 2690.1333 | 0.008083 | 0.00801 | 2.4037e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 793028 | FUSE - ELEMENT/LINK (HV) | Check OMS: 12562222 - 159 WARRENGATE ROAD , KAITOKE 2 x 15 amp fuse wind | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.00801 | 11 | 2017 | 2016-07-24 | C | 8 | 0.00801 | 2.4037e-05
1 | 12535059 | 2016-07-24 12:15 | 2016-07-24 22:59 | 644 | 10 | 6185.1667 | 0.018584 | 0.018494 | 3.0047e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 827399 | CROSSARM - WHOLE ASSEMBLY | at 20:33, Te Ore Ore Sub, CB C830 Weraiti Feeder. Found trees had come through lines at Pole 827399 & Conductor Broken at Pole 443395. Isolated lines at Fuses 7779. Permit issued & repairs carried out. All Power Restored on Completion. Brad Keating Attended. Replaced 1x Crossarm & Conductor. NDR: 37938 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.018494 | 11 | 2017 | 2016-07-24 | C | 10 | 0.018494 | 3.0047e-05
1 | 12536693 | 2016-07-24 12:23 | 2016-07-24 17:20 | 296 | 92 | 17113.5833 | 0.051421 | 0.050591 | 0.00055286 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 380741 | CONDUCTOR - REPAIR/REHANG | Fire comms have called in F2120128 - 2466 Te Matai Road power box on fire Have advised Control and SMC -require eta Lines down at Pole 380741 Lines repaired. 8mtrs conductor 6 x sleeves. 3 x 25A HV Line fuses. 2 x Fuse Barrels | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.050591 | 11 | 2017 | 2016-07-24 | C | 92 | 0.050591 | 0.00055286
1 | 12536885 | 2016-07-24 12:42 | 2016-07-25 00:35 | 713 | 51 | 36371.5 | 0.10928 | 0.10882 | 0.00015324 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 216655 | FUSE - ELEMENT/LINK (HV) | Reloaded, relivened 2x 15A HV Fuses at Fuses SE3-017. Found a few branches on the ground below lines. 12537069, 12546336, 12536896, 12572339, 12572436 | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.10882 | 11 | 2017 | 2016-07-24 | C | 51 | 0.10882 | 0.00015324
1 | 12537094 | 2016-07-24 12:52 | 2016-07-25 15:47 | 1615 | 145 | 23429.1833 | 0.070397 | 0.069089 | 0.00079323 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 480999 | CONDUCTOR - REPAIR/REHANG | Lines down beyond Pole 480999 Temp Line Break made at Pole 480999 and feeder restored. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.069089 | 11 | 2017 | 2016-07-24 | C | 145 | 0.069089 | 0.00079323
1 | 12537503 | 2016-07-24 12:53 | 2016-07-24 20:26 | 452 | 3000 | 342044.9667 | 1.0277 | 1.0007 | 0.009014 |  | 33 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 790912 | CROSSARM - WHOLE ASSEMBLY | at 12:53, Wanganui GXP, CB 2182 Wanganui East Feeder, Tripped, No Flags. Also, Wanganui East Sub, CB 10 No. 3 Line Feeder, Auto Reclosed. Loss of Supply to Wanganui East Sub. Found trees through lines at Pole 790912 on 11kV Lines. Isolated lines at ABS 229, 789, 128 & CB 10. Supply restored to Wanganui East Sub. Permit issued & repairs carred out. All Power Restored on Completion. Replaced 3x Crossarms & Straightened Pole. Ben Wilson Attended. NDR: 41486 NDR#41486, jeremy hill onsite and also roger bland , Hv cross arms being replaced onsite | S4 | WANGANUI EAST 33KV | WANGANUI | Wanganui | TP_WANGANUI | Western Electricity | POWERCO | 1.0007 | 33 | 2017 | 2016-07-24 | C | 3000 | 1.0007 | 0.009014
1 | 12546343 | 2016-07-24 13:00 | 2016-07-24 17:45 | 285 | 109 | 27653.4667 | 0.08309 | 0.082107 | 0.00032751 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 845444 | CROSSARM - WHOLE ASSEMBLY | Recloser C224/2 tripped on C phase O/C & E/F flags, line was patrolled and sectionalised and a floating wire and broken peace of cross broke off, lined was isolated at Fuses 7664 to make temp repairs to insulator, will return in morning to replace the cross arm on pole 845444. | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.082107 | 11 | 2017 | 2016-07-24 | C | 109 | 0.082107 | 0.00032751
1 | 12547348 | 2016-07-24 13:02 | 2016-07-24 20:12 | 430 | 873 | 129891.8 | 0.39028 | 0.38241 | 0.0052462 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 372912 | CONDUCTOR - REPAIR/REHANG | Have advised Control lines down due to trees - 57 Papaiti Road. Advised SMC fire comms require eta F2120168 - have advised fire comms eta of 20mins also branch on line | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.38241 | 11 | 2017 | 2016-07-24 | C | 873 | 0.38241 | 0.0052462
1 | 12549529 | 2016-07-24 13:15 | 2016-07-25 21:25 | 1930 | 9 | 17370.6 | 0.052193 | 0.052111 | 2.7042e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 774820 | FUSE - ELEMENT/LINK (HV) | 2x 10Amp HV Links | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.052111 | 11 | 2017 | 2016-07-24 | C | 9 | 0.052111 | 2.7042e-05
1 | 12550668 | 2016-07-24 13:18 | 2016-07-24 15:40 | 142 | 918 | 106588.8333 | 0.32026 | 0.31199 | 0.0027583 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 8 | UNKNOWN | CB 8 tripped no flags, line was patrolled and sectionalised and no fault was found suspect line clashes due to high winds in area. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.31199 | 11 | 2017 | 2016-07-24 | C | 918 | 0.31199 | 0.0027583
1 | 12551995 | 2016-07-24 14:48 | 2016-07-24 17:27 | 158 | 5 | 794.6667 | 0.0023877 | 0.002342 | 1.5023e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 210672 | CONDUCTOR - REPAIR/REHANG | Line down at Pole 210672. Line repaired. 5 mtrs Namu. 2 x Sleeves | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.002342 | 11 | 2017 | 2016-07-24 | C | 5 | 0.002342 | 1.5023e-05
1 | 12552143 | 2016-07-24 13:06 | 2016-07-24 15:39 | 153 | 1093 | 99036 | 0.29757 | 0.28772 | 0.0065682 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB5 | UNKNOWN | Feeder sectionalised but no fault found. Suspect Lightning | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.28772 | 11 | 2017 | 2016-07-24 | C | 1093 | 0.28772 | 0.0065682
1 | 12553798 | 2016-07-24 13:54 | 2016-07-25 15:00 | 1506 | 40 | 60244.6667 | 0.18102 | 0.18065 | 0.00012019 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 774 | FUSE - ELEMENT/LINK (HV) | Check recloser 554. 25/7 11:33am advised FM to check recloser. He is on Rata Sub fault and when finished will go here and check fuses first. Faultman found blown fuses at Fuses 744 and Recloser 554 open, Fuses 744 reloaded and Recloser 554 closed all supply ok. 2 X 8 amp HV fuses replaced ( Fuses 774). | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.18065 | 6.6 | 2017 | 2016-07-24 | C | 40 | 0.18065 | 0.00012019
1 | 12554212 | 2016-07-24 14:24 | 2016-07-24 22:28 | 484 | 1 | 484.4 | 0.0014555 | 0.001446 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P21616 | FUSE - ELEMENT/LINK (HV) | Reload, Reliven 2x 6A HV Fuses at Fuses M48. Bad weather at the time | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.001446 | 11 | 2017 | 2016-07-24 | C | 1 | 0.001446 | 3.0046e-06
1 | 12556049 | 2016-07-24 14:57 | 2016-07-24 15:48 | 50 | 2 | 101.3 | 0.00030437 | 0.000286 | 6.0093e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 843850 | UNKNOWN | 6942 Ph A & B & C OC & EF | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000286 | 11 | 2017 | 2016-07-24 | C | 2 | 0.000286 | 6.0093e-06
1 | 12557820 | 2016-07-24 15:24 | 2016-07-24 18:06 | 162 | 514 | 3140.8 | 0.0094371 | 0.004803 | 0.0015444 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1332 | UNKNOWN | CB 1332 tripped on O/C N/Time & E/F 7 CB XT30 auto reclosed on A, B & C phase O/C & E/F flags, line was sectionalised and patrolled and no fault was found suspect line clashes in high winds. | S3 | MANGAMAIRE-PONGAROA 33KV | MANGAMAIRE | Manawatu | TP_MANGAMAIRE | Western Electricity | POWERCO | 0.004803 | 33 | 2017 | 2016-07-24 | C | 514 | 0.004803 | 0.0015444
1 | 12559544 | 2016-07-24 15:43 | 2016-07-25 00:11 | 507 | 324 | 94533.1667 | 0.28404 | 0.28112 | 0.0028604 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P34869 | BINDER | Call from Chris on 0278456566. Pole next to Pole P28028 the cable has come out of insulator and is slowly buring through the crossarm. Small fire can be seen from road. RS 10227 A/R, L/O, O/C, E/F. Floating conductor found at Pole P34869 which had almost burnt through crossarm. Temp repais made & feeder relivened ok. Crossarm will be defected for replacement. Before NOC control had closed off job in OMS Recloser 10227 Tripped again. Feeder sectionalised & patrolled with backfeed installed via VS 4278. Floating conductor found at Pole P34855. Repaired using 1x binder. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.28112 | 11 | 2017 | 2016-07-24 | C | 324 | 0.28112 | 0.0028604
1 | 12559941 | 2016-07-24 15:45 | 2016-07-24 18:30 | 164 | 186 | 17467.35 | 0.052484 | 0.050807 | 0.00055887 |  | 22 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 804873 | CONDUCTOR - REPAIR/REHANG | CB 1133 tripped on A phase O/C & E/F flags, line was sectionalised and faultman found a tree touching the line at pole 804873, line was isolated at ABS's 796, 4614/4, 4614/1 to remove the tree and resag line across the road. NDR: 047604 3 x sleeves used | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.050807 | 22 | 2017 | 2016-07-24 | C | 186 | 0.050807 | 0.00055887
1 | 12561071 | 2016-07-24 10:59 | 2016-07-24 22:13 | 674 | 41 | 16537.6833 | 0.04969 | 0.04932 | 0.00012319 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217325 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Dennis Ngatai Attended. Did a patrol of line - nothing found. Reloaded, Relivened 3x HV 20A HV Fuses at Fuses SE2-001. Fuses were old. Also replaced a fuse holder. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.04932 | 11 | 2017 | 2016-07-24 | C | 41 | 0.04932 | 0.00012319
1 | 12561383 | 2016-07-24 15:45 | 2016-07-24 18:30 | 165 | 20 | 3304.6667 | 0.0099294 | 0.009749 | 6.0093e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P22897 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp fuses wind | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.009749 | 11 | 2017 | 2016-07-24 | C | 20 | 0.009749 | 6.0093e-05
1 | 12561428 | 2016-07-24 16:16 | 2016-07-24 18:15 | 119 | 12 | 1432.8 | 0.0043051 | 0.004196 | 3.6056e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P012628 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp fuses wind | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.004196 | 11 | 2017 | 2016-07-24 | C | 12 | 0.004196 | 3.6056e-05
1 | 12561549 | 2016-07-24 16:26 | 2016-07-24 20:52 | 265 | 235 | 15428.05 | 0.046356 | 0.044237 | 0.00084732 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P02073 | BINDER | at 16:27. Kimbolton Sub, CB 6 Rangiwahia Feeder, Tripped, Ph A O/C, E/F, L/O. Faultman dispatched & investigation began. Feeder sectionalised. Found floating conductor at Pole P02073. Isolated lines between ABS N7 and N58. Permit issued & repairs carried out. All Power Restored on Completion. 2x Binders Replaced. Nick Brown Attended. Backfeeds: Opened N21, Closed N34 Opened N8, Closed N16 315 Peka Road, Kimbolton Line has fallen into property and is lying on dog kennels. Advised control | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.044237 | 11 | 2017 | 2016-07-24 | C | 235 | 0.044237 | 0.00084732
1 | 12562498 | 2016-07-24 16:50 | 2016-07-24 21:17 | 267 | 6 | 1604.4 | 0.0048207 | 0.004766 | 1.8028e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | T1528 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x 5A HV Fuses at Transformer T1528. Bad weather in area at the time. | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.004766 | 11 | 2017 | 2016-07-24 | C | 6 | 0.004766 | 1.8028e-05
1 | 12562732 | 2016-07-24 15:08 | 2016-07-24 18:19 | 191 | 92 | 17605.7333 | 0.052899 | 0.05207 | 0.00027643 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 799104 | JUMPER | Faultman found burnt off jumper at pole 799104, line was isolated at ABS's S512 & S525 to repair jumper. 1 X unerversal joint replaced | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.05207 | 11 | 2017 | 2016-07-24 | C | 92 | 0.05207 | 0.00027643
1 | 12564371 | 2016-07-24 19:23 | 2016-07-25 13:15 | 1072 | 211 | 44651.0333 | 0.13416 | 0.13226 | 0.00067004 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T9/72 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | CB 2 tripped on E/F flags, line was patrolled and sectionalised and blown fuse was found at Fuses V25 and a blown transformer T9/72, transformer was isolated to be replaced in morning and line patrol from Fuses V25 to to be carried out in morning. No fault was found past Fuses V25. 1 X transformer replaced. 1 X 6 amp HV fuse replaced (Fuses V25) | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.13226 | 11 | 2017 | 2016-07-24 | C | 211 | 0.13226 | 0.00067004
1 | 12565702 | 2016-07-24 19:32 | 2016-07-25 11:45 | 973 | 11 | 10703 | 0.032159 | 0.032059 | 3.3051e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P05637 | CONDUCTOR - REPAIR/REHANG | Faultman found fuses blown at Fuses I8, line was left isolated over night as due to the bad weather till morning, in morning the faultman found a tree on the lines at pole P05637, tree was removed with hot line sticks. 2 X 6 amp HV fuses replaced. NDR: 19466 | F4 | IHURAUA | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.032059 | 11 | 2017 | 2016-07-24 | C | 11 | 0.032059 | 3.3051e-05
1 | 12566790 | 2016-07-24 19:59 | 2016-07-25 01:16 | 317 | 132 | 33995.2 | 0.10214 | 0.10095 | 0.00039662 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 782248 | CROSSARM - WHOLE ASSEMBLY | Rec 711 E/F O/C. Patrol carried out with Broken crossarm found burnt through due to faulty insulator. Work area isolated & backfeed via ABS 1472. Materials used: 1x 2m Pin Arm, 3x Pins & Insulators, 2x Arm Braces, 3x Heli Ties, & Misc Nuts & Bolts | F4 | BRUNSWICK | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.10095 | 6.6 | 2017 | 2016-07-24 | C | 132 | 0.10095 | 0.00039662
1 | 12569869 | 2016-07-24 21:09 | 2016-07-25 20:36 | 1406 | 1 | 1406.5167 | 0.0042261 | 0.004217 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X345 | FUSE - ELEMENT/LINK (HV) | 10.34 PP to ppty. Wire hanging down from TX. Replaced 3X 3Amp HV Links | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.004217 | 11 | 2017 | 2016-07-24 | C | 1 | 0.004217 | 3.0046e-06
1 | 12570339 | 2016-07-25 15:45 | 2016-07-25 16:00 | 15 | 37 | 555 | 0.0016676 | 0.001334 | 0.00011117 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X743 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Check OMS: 12576522, 12577412 09.17 3 Fookes and 30 Bear Street. Confirmed power affected. Check OMS 12577030 5A Fookes Street phone 027 681 9991 Backfed on the LV. Job closed out and residual follow up job created (100123) | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001334 | 11 | 2017 | 2016-07-25 | C | 37 | 0.001334 | 0.00011117
1 | 12570654 | 2016-07-24 21:53 | 2016-07-24 23:14 | 81 | 902 | 19731.8833 | 0.059288 | 0.051157 | 0.0027102 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | N/A - NOT APPLICABLE | UNKNOWN | Arahina CB 3086 A/R, L/O, E/F, O/C B & C Phase. Caused total loss of supply to Rata Sub. Backfed Hunterville 22kv via MABS 848. 33kV Patrolled with no fault found. Relivened Sub & Restored to normal. Suspect Lightning | S4 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 0.051157 | 33 | 2017 | 2016-07-24 | C | 902 | 0.051157 | 0.0027102
1 | 12571573 | 2016-07-25 12:30 | 2016-07-25 14:10 | 100 | 68 | 6800 | 0.020432 | 0.019818 | 0.00020432 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764517 | INSULATOR | check fuses 5308 08.58 left message to call back regarding power. 09.12 Power off Line isolated at fuses 5308 to replace faulty pin, insulator & binder at pole 764517 | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.019818 | 11 | 2017 | 2016-07-25 | C | 68 | 0.019818 | 0.00020432
1 | 12572693 | 2016-07-24 13:20 | 2016-07-25 11:51 | 1351 | 17 | 3242.8667 | 0.0097438 | 0.00959 | 5.1079e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7776 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Transformer T498 is blown and requires replacement. Faultman found burnt fuses and fuse holders at Fuses 7776, line was isolated at ABS S149 to replace the fuses and fuses holders. 3 X 10 amp HV fuses replaced. Full set (3) fuse holders replaced | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.00959 | 11 | 2017 | 2016-07-24 | C | 17 | 0.00959 | 5.1079e-05
1 | 12573155 | 2016-07-24 21:27 | 2016-07-25 14:00 | 992 | 33 | 31818.05 | 0.095603 | 0.095305 | 9.9154e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 847051 | CONDUCTOR - REPAIR/REHANG | Fault man requesting a 2R to replace 2 x dead ends. To be decided at invoicing level if meets criteria of 2R work after scope of work. **Check OMS 12585406 when closing off** | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.095305 | 11 | 2017 | 2016-07-24 | C | 33 | 0.095305 | 9.9154e-05
1 | 12573184 | 2016-07-25 01:26 | 2016-07-25 13:10 | 703 | 26 | 18299.6667 | 0.054984 | 0.054749 | 7.812e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 850553 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp Fuse due to wind. | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.054749 | 11 | 2017 | 2016-07-25 | C | 26 | 0.054749 | 7.812e-05
1 | 12575200 | 2016-07-25 04:26 | 2016-07-25 05:56 | 89 | 498 | 27622.05 | 0.082994 | 0.078505 | 0.0014963 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB 6 A/R, L/O, E/F, O/C B & C Phase. Sectionalised & Cursory Patrol carried out beyond ABS 412 to the end. Report of flashing on the pole outside 18 Saunders Rd but no fault found. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.078505 | 11 | 2017 | 2016-07-25 | C | 498 | 0.078505 | 0.0014963
1 | 12576278 | 2016-07-25 06:47 | 2016-07-25 11:00 | 253 | 5 | 1266.25 | 0.0038046 | 0.003759 | 1.5023e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762643 | FUSE - ELEMENT/LINK (HV) | Check OMS: 12577106 | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.003759 | 11 | 2017 | 2016-07-25 | C | 5 | 0.003759 | 1.5023e-05
1 | 12576376 | 2016-07-25 07:10 | 2016-07-25 11:00 | 230 | 4 | 921.4667 | 0.0027687 | 0.002732 | 1.2019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T8/317 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.002732 | 11 | 2017 | 2016-07-25 | C | 4 | 0.002732 | 1.2019e-05
1 | 12576394 | 2016-07-25 07:11 | 2016-07-25 11:18 | 246 | 3 | 740 | 0.0022234 | 0.002196 | 9.0139e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D12776 | CONDUCTOR - REPAIR/REHANG | Retailer has given customer safety instructions and has advised customer line so Powerco can only TSD. Advised svs hub 7:15am isolated HV side of TX for LV lines charge to customer | F4 | CAMBRIDGE RD TIRAU | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.002196 | 11 | 2017 | 2016-07-25 | C | 3 | 0.002196 | 9.0139e-06
1 | 12576692 | 2016-07-25 07:38 | 2016-07-25 14:00 | 381 | 1 | 381.6333 | 0.0011467 | 0.001137 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p21616 | FUSE - ELEMENT/LINK (HV) | 2 x 3 Amp Fuses at N83 due to wind. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.001137 | 11 | 2017 | 2016-07-25 | C | 1 | 0.001137 | 3.0046e-06
1 | 12577015 | 2016-07-25 08:08 | 2016-07-25 20:00 | 711 | 1 | 711.65 | 0.0021382 | 0.002129 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X68 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2Amp HV Links due to lightning. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.002129 | 11 | 2017 | 2016-07-25 | C | 1 | 0.002129 | 3.0046e-06
1 | 12577106 | 2016-07-25 08:17 | 2016-07-25 11:25 | 187 | 1 | 187.6333 | 0.00056377 | 0.000554 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 12576278 | FUSE - ELEMENT/LINK (HV) | child job | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.000554 | 11 | 2017 | 2016-07-25 | C | 1 | 0.000554 | 3.0046e-06
1 | 12577148 | 2016-08-02 10:43 | 2016-08-02 16:12 | 329 | 136 | 44707.75 | 0.13432 | 0.13309 | 0.00040859 | NAPA ID:22043 TP_HAWERA GXP > CAMBRIA SUB > ARGYLE ST | 11 | Planned | 022043 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 702708 | NONE | Install LLB at pole 702708. Replace 11m pole with 12.5 m pole with new DAS RL15 switch & links on it remove Abs 6824 new sw/link no's 12150/2/4/6. Close LLB at pole 702708. Works location: Waihi Rd, Hawera. WO 30018032 | F3 | ARGYLE ST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.066546 | 5.5 | 2017 | 2016-08-02 | B | 136 | 0.13309 | 0.00040859
1 | 12579811 | 2016-07-25 16:05 | 2016-07-25 19:15 | 190 | 5 | 950 | 0.0028544 | 0.002809 | 1.5023e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P00907 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | T2/120 - blown transformer - needs replacing. 5 customers - 516, 518, 562, 584 Turitea Road and 22 Pineland Drive. Transformer replaced. | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.002809 | 11 | 2017 | 2016-07-25 | C | 5 | 0.002809 | 1.5023e-05
1 | 12580084 | 2016-07-25 11:01 | 2016-07-25 13:57 | 176 | 902 | 23433.9667 | 0.070411 | 0.062279 | 0.0027102 |  | 33 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 802749 | NONE | CB 3086 tripped on C phase O/C & E/F flags, Rata sub was back feed via Pukepapa, line was patrolled and bark was found on the lines at 33KV pole 802749, bark was removed with hot line stick. | S4 | ARAHINA 33KV | MARTON | Wanganui | TP_MARTON | Western Electricity | POWERCO | 0.062279 | 33 | 2017 | 2016-07-25 | C | 902 | 0.062279 | 0.0027102
1 | 12581103 | 2016-08-10 08:48 | 2016-08-10 13:44 | 296 | 9 | 2664 | 0.008003 | 0.007921 | 2.7037e-05 | NAPA ID:21712 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 021712 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | D12799 | NONE | DNO 10519. Pole D12799 - Replace ABS with DDO links, replace all arms and upgrade surge arrestors. Works location: Okoroire Rd, Tirau. WO 30027358 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0039605 | 5.5 | 2017 | 2016-08-10 | B | 9 | 0.007921 | 2.7037e-05
1 | 12581464 | 2016-07-25 11:31 | 2016-07-25 12:55 | 84 | 13 | 1098.35 | 0.0033001 | 0.003182 | 3.906e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 707898 | CROSSARM - WHOLE ASSEMBLY | 1 x broken crossarm located by faultman while driving through area. Line isolated between ABS 5436, 5499 and 5427 to replace. 1 x crossarm and 3ph 6.6kV assembly materials required. All supply restored. | F3 | RATA ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.003182 | 6.6 | 2017 | 2016-07-25 | C | 13 | 0.003182 | 3.906e-05
1 | 12581487 | 2016-08-02 09:27 | 2016-08-02 15:20 | 353 | 3 | 1059 | 0.0031816 | 0.003154 | 9.0131e-06 | NAPA ID:22898 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 022898 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 9378/2 | NONE | Replace poles, hardware and conductors between TEMP65 & TEMP62 Install TEMP35 & 36 on pole 217743 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001577 | 5.5 | 2017 | 2016-08-02 | B | 3 | 0.003154 | 9.0131e-06
1 | 12581624 | 2016-07-25 11:42 | 2016-07-25 12:57 | 74 | 4 | 298.6 | 0.00089718 | 0.000861 | 1.2019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P1824 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp wind sp1666 | F4 | WAITAWHETA | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.000861 | 11 | 2017 | 2016-07-25 | C | 4 | 0.000861 | 1.2019e-05
1 | 12583744 | 2016-08-03 09:22 | 2016-08-03 16:46 | 444 | 81 | 2754 | 0.008274 | 0.007543 | 0.0004867 | NAPA ID:21655 TP_KINLEITH GXP > MARAETAI ROAD SUB > BALMORAL DR | 11 | Planned | 021655 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | IC1556 | NONE | Replace cable IC1556 - IC1567 with new 3/185 Al XLPE. | F3 | BALMORAL DR | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.0037715 | 5.5 | 2017 | 2016-08-03 | B | 81 | 0.007543 | 0.0004867
1 | 12583901 | 2016-07-25 12:02 | 2016-07-25 13:40 | 98 | 498 | 41469.1833 | 0.1246 | 0.12011 | 0.0014963 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Oakura CB 6 | UNKNOWN | CB 6 tripped to L/O. No flags. HLT was still applied to CB following CAC that was issued on line earlier in day but had been cancelled. Line patrolled & sectionalised. No fault found. All supply restored. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.12011 | 11 | 2017 | 2016-07-25 | C | 498 | 0.12011 | 0.0014963
1 | 12585143 | 2016-07-25 12:49 | 2016-07-25 14:32 | 103 | 2 | 206.0333 | 0.00061906 | 0.000601 | 6.0092e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 725375 | FUSE - ELEMENT/LINK (HV) | Reload 1 x 6A & barrell due to wind. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.000601 | 11 | 2017 | 2016-07-25 | C | 2 | 0.000601 | 6.0092e-06
1 | 12586379 | 2016-07-24 21:42 | 2016-07-25 15:40 | 1077 | 13 | 14011.8333 | 0.042101 | 0.041983 | 3.9061e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 780873 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp fuses due to wind. | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.041983 | 11 | 2017 | 2016-07-24 | C | 13 | 0.041983 | 3.9061e-05
1 | 12587258 | 2016-07-25 14:30 | 2016-07-25 21:20 | 410 | 1 | 410 | 0.0012319 | 0.001222 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 840877 | FUSE - ELEMENT/LINK (HV) | TX 4090 has 2 DDO fuses hanging out of it. Contractor from Alf Downs rung fault in. Replced 2x 8Amp HV Links & attempted reliven but they blew. Found branch on lines at Pole 840877. Removed using Hot Stick. Relivened ok. Total of 4x 8Amp HV Links used. | F2 | MARTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.001222 | 11 | 2017 | 2016-07-25 | C | 1 | 0.001222 | 3.0046e-06
1 | 12587314 | 2016-07-24 15:49 | 2016-07-25 14:15 | 1346 | 7 | 9422.7 | 0.028312 | 0.028249 | 2.1033e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 379306 | FUSE - ELEMENT/LINK (HV) | Reload 3 x 3A Lightening | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.028249 | 11 | 2017 | 2016-07-24 | C | 7 | 0.028249 | 2.1033e-05
1 | 12588548 | 2016-07-25 11:20 | 2016-07-25 18:00 | 400 | 2 | 800.3 | 0.0024046 | 0.002386 | 6.0092e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T9/457 | FUSE - ELEMENT/LINK (HV) | Replace 2 X 2A Fuse | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.002386 | 11 | 2017 | 2016-07-25 | C | 2 | 0.002386 | 6.0092e-06
1 | 12589199 | 2016-07-25 16:30 | 2016-07-25 18:20 | 110 | 4 | 441.2667 | 0.0013258 | 0.001289 | 1.2019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 228469 | FUSE - ELEMENT/LINK (HV) | Glo has confirmed that as 5:50pm not onsite. Glo confirmed 5:51pm was onsite - wrong FM. HV fuse and 1 x barrel 2 x 6 amp hv fuse at pole 228469. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.001289 | 11 | 2017 | 2016-07-25 | C | 4 | 0.001289 | 1.2019e-05
1 | 12589796 | 2016-07-25 08:18 | 2016-07-25 17:23 | 544 | 2 | 1089.3667 | 0.0032732 | 0.003255 | 6.0092e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X78 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.003255 | 11 | 2017 | 2016-07-25 | C | 2 | 0.003255 | 6.0092e-06
1 | 12590078 | 2016-07-25 17:58 | 2016-07-25 18:01 | 3 | 1 | 3.6 | 1.0817e-05 | 0 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2478 | FUSE - ELEMENT/LINK (HV) | Paul found the fuses blown on his way to another job. Replace 3 x 2A fuse. | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-07-25 | C | 1 | 0 | 3.0046e-06
1 | 12590181 | 2016-07-25 08:52 | 2016-07-25 17:15 | 503 | 2 | 1006.8667 | 0.0030253 | 0.003007 | 6.0092e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T9/459 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuses | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.003007 | 11 | 2017 | 2016-07-25 | C | 2 | 0.003007 | 6.0092e-06
1 | 12590903 | 2016-07-25 19:19 | 2016-07-26 12:20 | 1020 | 1 | 1020.5167 | 0.0030663 | 0.003057 | 3.0046e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P12884 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 9.09pm called customer to check if their power is restored? Customer advised that they still have low power - transfromer by the cowshed is making bubbling noise. checked approx 15mins ago.Advised lucy about bubbling tx noise Blown 15kva 3 Phase transformer. Requires replacement tomorrow. Appears to be overloaded. 9.59pm 26/7 emailed svs hub for update | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.003057 | 11 | 2017 | 2016-07-25 | C | 1 | 0.003057 | 3.0046e-06
1 | 12591682 | 2016-07-26 | 2016-07-26 02:01 | 121 | 51 | 6171.8333 | 0.018544 | 0.018084 | 0.00015323 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 755680 | INSULATOR | 10.17pm FM has driven down customers drive and cannot find any pole down. I called customer to confirm where the pole is down but no ans on celphone. Called Energy Direct to check if there was an another phone number for the customer but they don't have any other number. FM has found the customer. FM advised cracked insulator and it has burnt arm brace off (was cause of feeder fault last night) FM will need bucket truck and traffic management to fix tonight. Replaced 3 x Pin Insulators, 2x Arm Braces, 2x Jumpers. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.018084 | 11 | 2017 | 2016-07-26 | C | 51 | 0.018084 | 0.00015323
1 | 12591928 | 2016-07-25 22:54 | 2016-07-26 11:56 | 782 | 9 | 7038 | 0.021147 | 0.021065 | 2.7042e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - RAIN | 772447 | POLE | Replaced broken pole 772447. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.021065 | 11 | 2017 | 2016-07-25 | C | 9 | 0.021065 | 2.7042e-05
1 | 12593429 | 2016-07-26 07:00 | 2016-07-26 08:21 | 80 | 430 | 31554.0833 | 0.094808 | 0.090931 | 0.001292 |  | 11 | Unplanned |  | OVERHEAD LINE | OUTAGE RESTORED | OUTAGE RESTORED | CB 24 | UNKNOWN | Note Two jobs in one. This is the HV record for reporting purposes LV job. Advised SMC Has TSD 1263 Devon Road - Sparking service line. Safety discon notice A13005. Spoke to customer and advised him of PAC's in area who can make repairs to his service line. HV Job. 11kV CB 24 tripped O/C to lock out. Due to BBK Project this also took out approx half of BBK CB 22 fdr as well. 1R request was made for the HV feeder patrol. Neil Wood head conducted patrol and sectionalised. No fault found on the HV, all power restored. Fiona, this is two jobs in one here. This OMS Job was originally a sparking LV Lines Job which Germaine was assigned to. However, Bell Block CB 24 Tripped, the LV job inferenced up to this HV job up. This may affect invoicing.ASW | F1 | AIRPORT DRIVE | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.090931 | 11 | 2017 | 2016-07-26 | C | 430 | 0.090931 | 0.001292
1 | 12594049 | 2016-07-25 18:00 | 2016-07-25 22:05 | 245 | 2 | 490 | 0.0014723 | 0.001454 | 6.0092e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 796573 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp due to wind | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.001454 | 11 | 2017 | 2016-07-25 | C | 2 | 0.001454 | 6.0092e-06
1 | 12594265 | 2016-07-26 07:55 | 2016-07-26 10:10 | 134 | 1 | 134.5167 | 0.00040417 | 0.000395 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 792036 | FUSE - ELEMENT/LINK (HV) | Reload at X4311 2 x 2A due to Weather. | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.000395 | 11 | 2017 | 2016-07-26 | C | 1 | 0.000395 | 3.0046e-06
1 | 12594383 | 2016-08-12 10:00 | 2016-08-12 10:25 | 25 | 5 | 125 | 0.00037551 | 0.00033 | 1.502e-05 | NAPA ID:21948 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 021948 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC2287 | NONE | To install a 400V Fuse Disconnector. Works location: Matai Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000165 | 5.5 | 2017 | 2016-08-12 | B | 5 | 0.00033 | 1.502e-05
1 | 12594392 | 2016-07-26 11:35 | 2016-07-26 12:08 | 33 | 74 | 2442 | 0.0073373 | 0.00667 | 0.00022234 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 844714 | JUMPER | 1R - Please Assign Garry Fisher for Jumper Repairs and Dead End Replacements. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.00667 | 11 | 2017 | 2016-07-26 | C | 74 | 0.00667 | 0.00022234
1 | 12595028 | 2016-07-26 05:26 | 2016-07-26 09:25 | 239 | 99 | 23672.55 | 0.071127 | 0.070234 | 0.00029746 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 757687 | FUSE - ELEMENT/LINK (HV) | Reload fuses with correct rating at fuses 8418 | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.070234 | 11 | 2017 | 2016-07-26 | C | 99 | 0.070234 | 0.00029746
1 | 12595190 | 2016-08-10 08:30 | 2016-08-10 16:00 | 450 | 232 | 13920 | 0.041817 | 0.039726 | 0.0013939 | NAPA ID:22183 TP_MT MAUNGANUI 33 GXP > TRITON SUB > TOTARA ST NORTH | 11 | Planned | 022183 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC4-230 | NONE | Replace 9673 with CFCC and move old CFC to new site (New No. 13046) also move TC4 230 & TC4-200 onto CFC. Works location: Pacific Ave, Tauranga. WO 30019004 | F3 | TOTARA ST NORTH | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.019863 | 5.5 | 2017 | 2016-08-10 | B | 232 | 0.039726 | 0.0013939
1 | 12595533 | 2016-07-26 09:24 | 2016-07-26 13:05 | 220 | 1 | 220.7667 | 0.00066332 | 0.000654 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 843144 | FUSE - ELEMENT/LINK (HV) | Reload at X4186 (see 12600241) 3 x 2A due to Weather - Outage reflected under OMS 12600241 | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.000654 | 11 | 2017 | 2016-07-26 | C | 1 | 0.000654 | 3.0046e-06
1 | 12596244 | 2016-08-22 09:10 | 2016-08-22 14:00 | 290 | 9 | 2610 | 0.0078397 | 0.007758 | 2.7034e-05 | NAPA ID:21819 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 021819 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole P13226 | NONE | Triming tree between P13226 and P13221. Works location: Zig Zag Rd. WO 30026290 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.003879 | 5.5 | 2017 | 2016-08-22 | B | 9 | 0.007758 | 2.7034e-05
1 | 12598220 | 2016-07-26 12:22 | 2016-07-26 14:30 | 128 | 1 | 128.1 | 0.00038489 | 0.000375 | 3.0046e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7372 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a HV fuses @ 7372 | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.000375 | 11 | 2017 | 2016-07-26 | C | 1 | 0.000375 | 3.0046e-06
1 | 12599354 | 2016-08-11 09:00 | 2016-08-11 14:37 | 337 | 74 | 24938 | 0.074916 | 0.074249 | 0.0002223 | NAPA ID:19274 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > MALEME EXPRESS | 11 | Planned | 019274 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 321009 | NONE | Replace poles & reconductor. Works location: Maitland St. WO 30019275 | F2 | MALEME EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.037124 | 5.5 | 2017 | 2016-08-11 | B | 74 | 0.074249 | 0.0002223
1 | 12599363 | 2016-07-26 14:53 | 2016-07-26 15:54 | 60 | 43 | 2612.9667 | 0.0078509 | 0.007463 | 0.0001292 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | P11403 | POLE | 2R - Replace Broken Crossarm and DNO Pole P11403 Reported by Robin Smith. Pole P11403 - 760 Kakariki Rd, Ekatahuna | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.007463 | 11 | 2017 | 2016-07-26 | C | 43 | 0.007463 | 0.0001292
1 | 12599450 | 2016-08-20 08:46 | 2016-08-20 15:23 | 396 | 47 | 1061.5 | 0.0031885 | 0.002765 | 0.00028236 | NAPA ID:22901 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 022901 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P15912 | NONE | To make line brake at pole P15912,then reliven from T15 to line break. Then isolate 11kv from CB10 to T2 , then change ABS T1,and T11 DNO #'s 160625 and 160626. Works location: Halls Rd. WO 30030174 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.0013825 | 5.5 | 2017 | 2016-08-20 | B | 47 | 0.002765 | 0.00028236
1 | 12599993 | 2016-08-22 10:53 | 2016-08-22 15:01 | 248 | 7 | 1736 | 0.0052145 | 0.005151 | 2.1026e-05 | NAPA ID:22266 TP_LINTON GXP > KAIRANGA SUB > KOPANE | 11.00000000 | Planned | 022266 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2/417 | NONE | Replace 11KV fusearm & fuses Transformer T2/417. Works location: Aranui Rd, Palmerston North. WO 30018765 | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.0025755 | 5.5 | 2017 | 2016-08-22 | B | 7 | 0.005151 | 2.1026e-05
1 | 12600096 | 2016-07-26 10:20 | 2016-07-26 14:15 | 234 | 4 | 939.6 | 0.0028231 | 0.002787 | 1.2018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 771440 | FUSE - ELEMENT/LINK (HV) | Replaced 2 x 3Amp Fuses at X419 due to lightning strike. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.002787 | 11 | 2017 | 2016-07-26 | C | 4 | 0.002787 | 1.2018e-05
1 | 12600143 | 2016-07-26 14:30 | 2016-07-27 12:40 | 1330 | 1 | 1330.3333 | 0.0039971 | 0.003988 | 3.0046e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P49806 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | GIS Error the transformer affected is T8/102 and not T8/151. Faultman found a broken 11kV bushing on transformer T8/102 and the transformer will be replaced in the morning. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.003988 | 11 | 2017 | 2016-07-26 | C | 1 | 0.003988 | 3.0046e-06
1 | 12600453 | 2016-08-12 14:54 | 2016-08-12 15:36 | 42 | 30 | 1260 | 0.0037851 | 0.003514 | 9.0122e-05 | NAPA ID:22908 TP_KOPU GXP > WHITIANGA SUB > PURANGI | 11 | Planned | 022908 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Sw/Gear IC1482 | NONE | Replace defective ringmain unit IC1482/IC1457/IC1470 with a new Safelink Unit. Works location: Oyster Dr, Cooks Beach. WO 30031161 | F3/F4 | PURANGI | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.001757 | 5.5 | 2017 | 2016-08-12 | B | 30 | 0.003514 | 9.0122e-05
1 | 12601776 | 2016-07-26 18:26 | 2016-07-26 20:08 | 102 | 2014 | 201225.7667 | 0.6046 | 0.58645 | 0.0062886 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | G267/B | CABLE - REPAIR | CB 9 tripped on E/F flags, feeder was sectionalised and a cable fault between Magnefix G183/C & Sw/Gear G267/B. Cable has been DNO'd DNO Tag 160714. | F3 | PASCAL ST 9 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 0.58645 | 11 | 2017 | 2016-07-26 | C | 2014 | 0.58645 | 0.0062886
1 | 12606491 | 2016-07-27 06:18 | 2016-07-27 08:55 | 156 | 403 | 25653.2833 | 0.077077 | 0.073444 | 0.0012108 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 222529 | CONDUCTOR - REPAIR/REHANG | Sparking transformer at 47 Seddon St - have advised Control. Line down at pole 222529 bought down by a swan. Isolation at ABS SD6-011 & SE5-221. No back feeds available. Line repaired. 2 namu sleeves, 5 meters namu conductor. | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.073444 | 11 | 2017 | 2016-07-27 | C | 403 | 0.073444 | 0.0012108
1 | 12607347 | 2016-08-16 09:00 | 2016-08-16 14:38 | 338 | 49 | 16562 | 0.049751 | 0.049309 | 0.00014719 | NAPA ID:22371 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 022371 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6402 | NONE | Replace various arms and poles within work area. Works location; South Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.024654 | 5.5 | 2017 | 2016-08-16 | B | 49 | 0.049309 | 0.00014719
1 | 12607358 | 2016-08-18 09:00 | 2016-08-18 10:10 | 70 | 11 | 770 | 0.002313 | 0.002213 | 3.3043e-05 | NAPA ID:22372 TP_OPUNAKE GXP > PUNGAREHU SUB > WAREA | 11 | Planned | 022372 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 6415 | NONE | Replace various arms and poles within work area. Works location: Mirikau Rd, Warea. WO 30024615 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.0011065 | 5.5 | 2017 | 2016-08-18 | B | 11 | 0.002213 | 3.3043e-05
1 | 12607376 | 2016-07-27 07:30 | 2016-07-27 11:39 | 249 | 1253 | 53811.6667 | 0.16168 | 0.15039 | 0.0039781 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P02111 | POLE | P026076569 - Police event number - ute v pole. Lines down, pole P02111 down. Pole Replaced. NDR - N300218 | F3 | KEITH ST 12 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 0.15039 | 11 | 2017 | 2016-07-27 | C | 1253 | 0.15039 | 0.0039781
1 | 12608954 | 2016-07-27 07:37 | 2016-07-27 10:49 | 192 | 26 | 4992.4333 | 0.015 | 0.014765 | 7.8119e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11356 | FUSE - ELEMENT/LINK (HV) | Replace 1 x insulator, 1 x 10A fuse | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.014765 | 11 | 2017 | 2016-07-27 | C | 26 | 0.014765 | 7.8119e-05
1 | 12609030 | 2016-08-18 09:03 | 2016-08-18 14:50 | 347 | 37 | 12839 | 0.038567 | 0.038233 | 0.00011114 | NAPA ID:22167 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > STONEY CREEK | 11 | Planned | 022167 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P37978 | NONE | Replace 11kV Pole P37978 with DBL 11M replace Trani T2/536. Works location: Stoney Creek Rd, Bunnythorpe. WO 10162471 | F4 | STONEY CREEK | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.019117 | 5.5 | 2017 | 2016-08-18 | B | 37 | 0.038233 | 0.00011114
1 | 12609079 | 2016-08-14 09:06 | 2016-08-14 10:12 | 66 | 7 | 462 | 0.0013878 | 0.001324 | 2.1028e-05 | NAPA ID:22968 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > 13TH AVE | 11 | Planned | 022968 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TK6-002 | NONE | Isolate transformer TK6-002 so that the lid can be opened and the transformer can be topped up with oil. Works location: Burrows St, Tauranga. WO 30026219 | F3 | 13TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 0.000662 | 5.5 | 2017 | 2016-08-14 | B | 7 | 0.001324 | 2.1028e-05
1 | 12611592 | 2016-07-27 12:03 | 2016-07-29 14:48 | 3045 | 17 | 51765 | 0.15553 | 0.15538 | 5.1078e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 5 MURDOCH STREET | CABLE - REPLACE LESS THAN 5 METRES | Possible HV cable fault on HV cable to transformer C5260. Blown HV fuse on pole 700111 blew when reloaded (Fuses not labelled on SCADA or on site) Other fuses opened, 2 r created to have cable and transformer etc tested. | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.15538 | 11 | 2017 | 2016-07-27 | C | 17 | 0.15538 | 5.1078e-05
1 | 12612698 | 2016-07-27 10:13 | 2016-07-27 11:15 | 61 | 2 | 123.6 | 0.00037137 | 0.000353 | 6.0091e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | H3194 | FUSE - ELEMENT/LINK (HV) | 2 x 3 Amp Fuses due to bird strike. | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000353 | 11 | 2017 | 2016-07-27 | C | 2 | 0.000353 | 6.0091e-06
1 | 12619879 | 2016-08-31 09:15 | 2016-08-31 14:31 | 315 | 4 | 1263.4667 | 0.0037947 | 0.003758 | 1.2014e-05 | NAPA ID:22220 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > NGARUA | 11 | Planned | 022220 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FP1814 | NONE | Ngarua Feeder Step 16, Shut 9. Specified renewal works on Seddon Rd, beyond FP1814. Works location: Seddon Rd, Waitoa. WO 30017830 | F4 | NGARUA | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.001879 | 5.5 | 2017 | 2016-08-31 | B | 4 | 0.003758 | 1.2014e-05
1 | 12637492 | 2016-07-27 17:15 | 2016-07-27 17:44 | 29 | 1 | 29 | 8.7133e-05 | 7.8e-05 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | X442 | CONDUCTOR - REPAIR/REHANG | Leighton called job through advising Higgins have hit power lines and brought them down at X442. Replaced 10m x 10mm cable, 2 x sleeves. 1 x 2amp fuse at X442. Cause: third party damage. Nothing else repaired or replaced. Adjacent assets up to Powerco standards. NDR # 047057 | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 7.8e-05 | 11 | 2017 | 2016-07-27 | C | 1 | 7.8e-05 | 3.0045e-06
1 | 12638700 | 2016-07-27 21:21 | 2016-07-27 22:28 | 67 | 1 | 67.35 | 0.00020236 | 0.000193 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7105 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses 7105, suspect bird strike. 2 X 10 amp HV fuses replaced | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000193 | 11 | 2017 | 2016-07-27 | C | 1 | 0.000193 | 3.0045e-06
1 | 12638901 | 2016-07-28 23:17 | 2016-07-29 01:02 | 105 | 29 | 3045 | 0.0091488 | 0.008887 | 8.7132e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | C633/2 | UNKNOWN | No Power. Faultman found Sectionaliser C633/2 open on arrival, suspect cause of fault was line clash as very windy in area. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.008887 | 11 | 2017 | 2016-07-28 | C | 29 | 0.008887 | 8.7132e-05
1 | 12638923 | 2016-07-28 02:57 | 2016-07-28 13:52 | 654 | 168 | 75248.1 | 0.22609 | 0.22457 | 0.00091338 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Line patrol after second tripping, CB C642 auto reclosed on A & C phase O/C flags.link to psrent | S5 | HAU NUI 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0.22457 | 11 | 2017 | 2016-07-28 | C | 168 | 0.22457 | 0.00091338
1 | 12640702 | 2016-07-28 03:27 | 2016-07-28 11:38 | 490 | 1026 | 98343.15 | 0.29548 | 0.28623 | 0.0030827 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P17000 | CROSSARM - WHOLE ASSEMBLY | Line on cross arm @ pole P17000 / Lines Down. Materials Used: 1 x binder, 3 metres conductor, 1 x sleeve, 1 x connector. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.28623 | 11 | 2017 | 2016-07-28 | C | 1026 | 0.28623 | 0.0030827
1 | 12643285 | 2016-07-28 04:07 | 2016-07-28 11:15 | 428 | 680 | 54314.3167 | 0.16319 | 0.15706 | 0.0023886 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P34606 | INSULATOR | Recloser 10183/2 tripped on C phase E/F flags line was patrolled and sectionalised, faultman suspect fault is at Pole P34606, this pole has burnt cross arm and damaged insulators on it, fault crew to return in day light to replace cross arm & insulators under emergency shut down. Isolated at ABS's C14, C17 & O57 with backfeeds via ABS's C19 and O58. Damaged Insulator removed and burnt section of crossarm cut of (double crossarm on pole). | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.15706 | 11 | 2017 | 2016-07-28 | C | 680 | 0.15706 | 0.0023886
1 | 12650082 | 2016-07-28 04:53 | 2016-07-28 06:23 | 89 | 178 | 11826.65 | 0.035534 | 0.033929 | 0.00053481 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 067 | UNKNOWN | Recloser 067 Tripped. Line patrolled - nothing found. | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.033929 | 11 | 2017 | 2016-07-28 | C | 178 | 0.033929 | 0.00053481
1 | 12654663 | 2016-07-28 06:47 | 2016-07-28 11:09 | 262 | 46 | 11894 | 0.035736 | 0.035321 | 0.00013821 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 748975 | JUMPER | **Check whether 12 Davies Road would have been affected/restored Phone 067535886 OMS 12655719 - May need to be a GIS change as different Tx ** Broken jumper at 1m conductor 1 epo 2 sleeves | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.035321 | 11 | 2017 | 2016-07-28 | C | 46 | 0.035321 | 0.00013821
1 | 12655210 | 2016-07-28 08:44 | 2016-07-28 10:45 | 120 | 7 | 843.5 | 0.0025343 | 0.002471 | 2.1032e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 763520 | FUSE - ELEMENT/LINK (HV) | 3 x 3amp due to lightning | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.002471 | 11 | 2017 | 2016-07-28 | C | 7 | 0.002471 | 2.1032e-05
1 | 12655246 | 2016-07-28 08:51 | 2016-07-28 18:18 | 567 | 53 | 13051.1 | 0.039213 | 0.038734 | 0.00015924 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 741228 | CONDUCTOR - REPAIR/REHANG | NDR 15815. 200m Conductor/20 Sleeves used over 3 spans. Pole Numbers 741228, 741229,741230. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.038734 | 11 | 2017 | 2016-07-28 | C | 53 | 0.038734 | 0.00015924
1 | 12655688 | 2016-08-22 14:00 | 2016-08-22 14:15 | 15 | 10 | 150 | 0.00045056 | 0.00036 | 3.0037e-05 | NAPA ID:22217 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022217 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV fuses TC634 | NONE | To install a 400V Disconnector. Matherson Road, Matamata, Hinuera. W/O 30019182. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.00018 | 5.5 | 2017 | 2016-08-22 | B | 10 | 0.00036 | 3.0037e-05
1 | 12656034 | 2016-07-28 10:29 | 2016-07-28 16:06 | 337 | 1 | 337.1833 | 0.0010131 | 0.001004 | 3.0045e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 771831 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 2R - For transformer replacemant X2341. 1 x Transformer 15/11/3 1 x 2A Livened at 15:50 | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001004 | 11 | 2017 | 2016-07-28 | C | 1 | 0.001004 | 3.0045e-06
1 | 12656351 | 2016-08-24 09:30 | 2016-08-24 10:45 | 75 | 3 | 225 | 0.00067582 | 0.000648 | 9.0109e-06 | NAPA ID:22199 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022199 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV fuses TC385 | NONE | To replace the 400V arm and install a 400V Disconnector on TC385. Buckland Road, Matamata, Hinuera. W/O 30019182. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000324 | 5.5 | 2017 | 2016-08-24 | B | 3 | 0.000648 | 9.0109e-06
1 | 12656629 | 2016-08-26 10:00 | 2016-08-26 10:30 | 30 | 3 | 90 | 0.00027032 | 0.000243 | 9.0107e-06 | NAPA ID:22205 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022205 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1375 | NONE | To install a 400V Disconnector on TC1375. Buckland Road, Matamata, Hinuera. W/O 30019182. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0001215 | 5.5 | 2017 | 2016-08-26 | B | 3 | 0.000243 | 9.0107e-06
1 | 12657257 | 2016-07-28 12:52 | 2016-07-29 15:25 | 1593 | 42 | 22128.5 | 0.066486 | 0.066107 | 0.00015924 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 357339 | CONDUCTOR - REPAIR/REHANG | Lines down found while sectionlising and Pole 357339 - long spane unable to reapair in remaining day light isolated a fuses 2650 - Temp line break installed at Pole 357339 - repair to be carried out on following day Lines repaired Isolated again at fuses 2650 to close line break Used 30 mtrs of conductor and 12 sleeves | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.066107 | 11 | 2017 | 2016-07-28 | C | 42 | 0.066107 | 0.00015924
1 | 12657841 | 2016-08-29 09:50 | 2016-08-29 12:10 | 140 | 4 | 560 | 0.0016819 | 0.001645 | 1.2014e-05 | NAPA ID:22208 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022208 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV fuses Prep TC5711 | NONE | To install a 400V Fuse Disconnector. Buckland Road, Matamata, Hinuera. W/O 30019182. | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0008225 | 5.5 | 2017 | 2016-08-29 | B | 4 | 0.001645 | 1.2014e-05
1 | 12658019 | 2016-07-28 07:44 | 2016-07-29 15:00 | 1875 | 6 | 2700.7 | 0.0081144 | 0.00806 | 1.8027e-05 |  | 6.6 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 775989 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Link to 12654526 tx feeds wool shed needs replacing Isolated at Fuses 473 - Cause weather Used 1 x 15 kVA 1 phase transformer | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.00806 | 6.6 | 2017 | 2016-07-28 | C | 6 | 0.00806 | 1.8027e-05
1 | 12658261 | 2016-08-16 09:00 | 2016-08-16 15:05 | 365 | 17 | 6205 | 0.018639 | 0.018486 | 5.1067e-05 | NAPA ID:21742 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 021742 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Pole 217685 | NONE | Shut down 1. Kumikumi Road Pole and Hardware replacement. Kumikumi Road, Kaimai Drive, Tauranga. W/O 30017842. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.009243 | 5.5 | 2017 | 2016-08-16 | B | 17 | 0.018486 | 5.1067e-05
1 | 12658652 | 2016-07-28 15:47 | 2016-07-29 17:55 | 1568 | 167 | 173347.85 | 0.52083 | 0.51933 | 0.00050176 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708084 | CONDUCTOR - REPAIR/REHANG | Strathmore Sub Recloser 4987- Tripped sectionaliser 12087 tripped line patrolled and found @ pole 708368 trees through lines , broken cross arm and lines down . Faultman arranging for tree crew to remove trees from lines to facilitate repairs in the morning due to dangerous terrain . NDR No:- N100199 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.51933 | 11 | 2017 | 2016-07-28 | C | 167 | 0.51933 | 0.00050176
1 | 12659339 | 2016-07-28 16:43 | 2016-07-28 17:42 | 58 | 195 | 10635 | 0.031953 | 0.030195 | 0.00058589 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 829571 | CONDUCTOR - REPAIR/REHANG | RS 279 found tripped - Branch found on lines at pole 829571 during sectionalising. Cleared using hot sticks. | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.030195 | 11 | 2017 | 2016-07-28 | C | 195 | 0.030195 | 0.00058589
1 | 12664579 | 2016-07-28 21:45 | 2016-07-29 01:45 | 240 | 5 | 1200 | 0.0036055 | 0.00356 | 1.5023e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | TP154 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Car has hit a transformer. Event # P026095820. Isolation at Fused/Sw 9482/2 to replace damaged transformer TP154. Transformer replaced all service restored. Materials used:1 x transformer. NDR No 51604 | F2 | MALEME EXPRESS | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.00356 | 11 | 2017 | 2016-07-28 | C | 5 | 0.00356 | 1.5023e-05
1 | 12665033 | 2016-07-28 19:40 | 2016-07-28 23:57 | 256 | 324 | 37862.7 | 0.11376 | 0.11084 | 0.00097347 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36508 | CONDUCTOR - REPAIR/REHANG | Report received of trees tangled in lines @ 410 Paranui road between poles P36508 & P36520 section of line from fuses B28 isolated for repairs and supply restored to balance of feeder. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.11084 | 11 | 2017 | 2016-07-28 | C | 324 | 0.11084 | 0.00097347
1 | 12666956 | 2016-07-28 19:57 | 2016-07-28 22:18 | 140 | 1 | 140.6833 | 0.00042269 | 0.000413 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | C6005 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3a HV fuses @ C6005 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.000413 | 11 | 2017 | 2016-07-28 | C | 1 | 0.000413 | 3.0045e-06
1 | 12666984 | 2016-07-28 23:07 | 2016-07-29 00:15 | 68 | 11 | 748 | 0.0022474 | 0.002148 | 3.305e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 709710 | CONDUCTOR - REPAIR/REHANG | Please check oms 12667581 3216 Coast road part power 1 phase out found line down @ pole 709710 and isolated from fuses Pu355 for repairs Replaced +/- 40m 16mm Copper conductor | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.002148 | 11 | 2017 | 2016-07-28 | C | 11 | 0.002148 | 3.305e-05
1 | 12667021 | 2016-07-28 20:18 | 2016-07-29 13:30 | 1032 | 82 | 51913.1667 | 0.15598 | 0.15524 | 0.00024637 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 794431 | CONDUCTOR - REPAIR/REHANG | Report received of lines down onTurakina Valley road just before Taurimu road line isolated from fuses 058 and to be attended in the morning. Lines down due to trees. Materials Used: 1 cross arm (complete), 50 metres of conductor and 6 x sleeves. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.15524 | 11 | 2017 | 2016-07-28 | C | 82 | 0.15524 | 0.00024637
1 | 12667137 | 2016-07-28 21:21 | 2016-07-29 03:58 | 397 | 1 | 397 | 0.0011928 | 0.001183 | 3.0045e-06 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | 823661 | CABLE - REPAIR | Transformer between Carters Line & Tiffin Road arcing and sparking =- arcing once every 45 seconds 8.26pm advised Maree at svs hub & emailed. 8.41pm Customer called to advise pole is now on fire 3rd pole down from Carters Line - advised Svs hub of update. Reterminated LV cable on pole 823661. | F3 | SOMERSET RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.001183 | 11 | 2017 | 2016-07-28 | C | 1 | 0.001183 | 3.0045e-06
1 | 12667421 | 2016-07-28 20:46 | 2016-07-28 23:04 | 137 | 1 | 137.65 | 0.00041358 | 0.000404 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | T1795 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a HV fuses @ T1795 | F4 | LONGBUSH | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000404 | 11 | 2017 | 2016-07-28 | C | 1 | 0.000404 | 3.0045e-06
1 | 12667547 | 2016-07-28 20:48 | 2016-07-28 23:11 | 142 | 3 | 399.8833 | 0.0012015 | 0.001174 | 9.0136e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | R15 | FUSE - ELEMENT/LINK (HV) | 229 Pahiatua Mangahoe Road - Damian heard loud bang, possibly transformer blown (down the hill from him). No power in other houses. Replaced 2x 10a HV fuses @ R15 | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001174 | 11 | 2017 | 2016-07-28 | C | 3 | 0.001174 | 9.0136e-06
1 | 12667556 | 2016-07-29 00:29 | 2016-07-29 02:05 | 96 | 152 | 14521.5333 | 0.04363 | 0.04226 | 0.00045669 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 209561 | BINDER | Line patrol required tonight. GRE 122, AON 92 & BHM 82 tripped A, B Ph O/C, E/F L/O . BHM 82 returned to service. Report of line down at pole 209561, turns out to be 33kV floater at pole. 33kV isolation between ABS 3183 & AON ABS 96. GRE 122 to service with OMO dual bank. OMO 2 11kV isolation between ABS SC2 024 & ABS SD2 004. 33kV conductor re bound all service restored. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.04226 | 11 | 2017 | 2016-07-29 | C | 152 | 0.04226 | 0.00045669
1 | 12667767 | 2016-07-28 21:52 | 2016-07-28 23:42 | 109 | 1347 | 147096.0333 | 0.44196 | 0.42982 | 0.0040471 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Livingstone sub | UNKNOWN | Hawera CB 352 TRipped on Inv Time O/C , Livingstone CB 3812 tripped on O/C and Whareroa CB 3722 Tripped on O/C . Livingstone substation visualy checked (due to severe lightning in area at time of tripping) and all clear and supply restored | S2 | WHAREROA 33KV | HAWERA | Taranaki | TP_HAWERA | Western Electricity | POWERCO | 0.42982 | 33 | 2017 | 2016-07-28 | C | 1347 | 0.42982 | 0.0040471
1 | 12669153 | 2016-07-28 22:05 | 2016-07-29 00:36 | 151 | 2 | 302.3 | 0.00090827 | 0.00089 | 6.009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 412 | FUSE - ELEMENT/LINK (HV) | turn right of Kohi Road 100m up karahaki Road. advisexcd Karl Replaced 1x 10a HV fuse @ 412 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.00089 | 11 | 2017 | 2016-07-28 | C | 2 | 0.00089 | 6.009e-06
1 | 12669205 | 2016-07-29 09:45 | 2016-07-29 10:10 | 25 | 1 | 25 | 7.5113e-05 | 6.6e-05 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 772538 | FUSE - ELEMENT/LINK (HV) | 2x 2amp | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 6.6e-05 | 11 | 2017 | 2016-07-29 | C | 1 | 6.6e-05 | 3.0045e-06
1 | 12669304 | 2016-07-28 22:34 | 2016-07-29 02:36 | 242 | 195 | 25679.2333 | 0.077154 | 0.075396 | 0.00058589 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 845260 | CONDUCTOR - REPAIR/REHANG | Line sectionalised and patrolled found lines down @ pole 845260 and isolated from ABS S95 for repairs | F3 | CHURCH ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.075396 | 11 | 2017 | 2016-07-28 | C | 195 | 0.075396 | 0.00058589
1 | 12669362 | 2016-07-28 22:51 | 2016-07-29 00:57 | 126 | 1 | 126.45 | 0.00037992 | 0.00037 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5134 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6a HV fuses @ 5134 | F5 | PRINCESS ST | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.00037 | 11 | 2017 | 2016-07-28 | C | 1 | 0.00037 | 3.0045e-06
1 | 12669547 | 2016-07-28 18:37 | 2016-07-28 21:50 | 193 | 10 | 1248.65 | 0.0037516 | 0.003661 | 3.0045e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8094 | JUMPER | Check Tora Rd, OMS 12664654 & 12664698 found jumper blown @ ABS 8094 line opened from CB C624 and isolated @ ABS 8094 for repairs (Related to OMS12664637 ) | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.003661 | 11 | 2017 | 2016-07-28 | C | 10 | 0.003661 | 3.0045e-05
1 | 12669646 | 2016-07-28 23:23 | 2016-07-29 05:06 | 343 | 788 | 69304.5 | 0.20823 | 0.20112 | 0.0023676 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701726 | CONDUCTOR - REPAIR/REHANG | 11.45pm advised Fire service eta 15-20mins - fire service advised address is closer to 610-620 Mangorei Road advised Lianne at SVS hub. CB 7 tripped A & B Phase O/C Section of line between ABS 295 & Fuses 8279 Isolated to repair lines @ pole 701726 & 701763 balance of line backfed via ABS 351 for duration of repairs. | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.20112 | 11 | 2017 | 2016-07-28 | C | 788 | 0.20112 | 0.0023676
1 | 12671849 | 2016-07-29 00:06 | 2016-07-29 04:19 | 252 | 154 | 38838.8 | 0.11669 | 0.1153 | 0.00046269 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712221 | BINDER | ( NGA 4 ) CB4 tripped O/C, E/F, L/O line patrolled and isolation for repairs of floating conductors @ poles 712221 & 71223 | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.1153 | 11 | 2017 | 2016-07-29 | C | 154 | 0.1153 | 0.00046269
1 | 12672612 | 2016-07-29 01:00 | 2016-07-29 16:56 | 955 | 320 | 61440.8333 | 0.1846 | 0.18171 | 0.00096144 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M2050 | POLE | Notified Kiwirail of very low hanging lines on track crossing that Les is working on. Vospers Road. Kiwirail control have Les' number and will liaise directly. Replaced 2 x 11m poles. Lots of cross arms (complete - not sure how many). 1 X ABS Complete. | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.18171 | 11 | 2017 | 2016-07-29 | C | 320 | 0.18171 | 0.00096144
1 | 12672934 | 2016-07-29 01:01 | 2016-07-29 17:55 | 1014 | 228 | 108524.6167 | 0.32606 | 0.32401 | 0.00068503 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M0786 | CROSSARM - WHOLE ASSEMBLY | ( PUT 4 ) CB4 tripped A, B & C Ph O/C L/O. Tree through lines at pole M2047. Isolation between ABS 2520, ABS 2527 & ABS 975 with back feeds via Sectionaliser 9595, Recloser RP03 & CB4 returned to service. Materials Used: 2 X 2M cross arms (complete), 6 X Polymas, 6 X Dead ends, 2 XHT Cross arms (complet), 1X Full Tension Joint, 4 x cross arms in total. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.32401 | 11 | 2017 | 2016-07-29 | C | 228 | 0.32401 | 0.00068503
1 | 12676232 | 2016-07-29 03:54 | 2016-07-29 12:30 | 515 | 1 | 515.5833 | 0.0015491 | 0.00154 | 3.0045e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W5180 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | FM called to say he was onsite and needed a 2R to replace TX. However found FM to be on OMS job 12612760 which was a site inspection to replace a pole label at the same address. Have asked him to call the SMC and get put onsite on the correct job. Replaced single Phase Transformer W5180 Off at 04:00 Back on at 12:30 Glenn Barnfield has confirmed that the customer has been isolated for safety (unsure whether there was a tag or not as it was done by Alan) but Glenn has tested and confirmed customer cable is isolated. Water had got into the customer's cable via the meterbox that had no window and caused the cable to fault. Alan explained this to the customer's wife/partner and advised her to contact an electrician. Customer has been contacting Genesis and is irate that the faultmen have left site and not given him an update. I have left a message on the customer's voicemail and spoken to Lyndon at Genesis so a note can be put on the job file too. Glenn has confirmed that the job is finished on the Powerco side and all faultmen have left. | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.00154 | 11 | 2017 | 2016-07-29 | C | 1 | 0.00154 | 3.0045e-06
1 | 12676996 | 2016-07-29 05:29 | 2016-07-29 10:52 | 322 | 50 | 16110 | 0.048403 | 0.047951 | 0.00015023 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762210 | FUSE - ELEMENT/LINK (HV) | Reload Fuses 6376 isolated at ABS 5291. (3 x 20 Amp) | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.047951 | 6.6 | 2017 | 2016-07-29 | C | 50 | 0.047951 | 0.00015023
1 | 12677001 | 2016-07-29 05:31 | 2016-07-29 07:44 | 132 | 337 | 42790.3833 | 0.12856 | 0.12553 | 0.0010125 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21489 | CONDUCTOR - REPAIR/REHANG | RS L10 Tripped E/F - During sectionlising lines down found at Pole P21489. Isolated at ABS L13. Used 1 x sleeve, 1 x Binder | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.12553 | 11 | 2017 | 2016-07-29 | C | 337 | 0.12553 | 0.0010125
1 | 12677351 | 2016-07-29 05:43 | 2016-07-29 06:35 | 51 | 1646 | 84113.7 | 0.25272 | 0.23788 | 0.0049454 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CST GXP 33kV CB 1092 tripped diff time O/C and locked out. Loss of Oakurua Sub. Suspect outage was due to severe lightning at the time. Note auto change over did not operate so complete loss of supply to all ICP's. Due to the scheme not operating the sub was inspected prior to re-Livening to ensure no damage. No damage found, sub re-livened via 33kV successfully. Auto change over issue to be investigated. | S1 | CARRINGTON ST1092 OAKURA4162 33KV | CARRINGTON ST 33 | Taranaki | TP_CARRINGTON | Western Electricity | POWERCO | 0.23788 | 33 | 2017 | 2016-07-29 | C | 1646 | 0.23788 | 0.0049454
1 | 12679183 | 2016-07-29 05:54 | 2016-07-29 09:18 | 204 | 243 | 26823.3 | 0.080591 | 0.0784 | 0.0007301 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND |  | UNKNOWN | Rec 499 tripped line patrolled nothing found lightening in area | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.0784 | 11 | 2017 | 2016-07-29 | C | 243 | 0.0784 | 0.0007301
1 | 12679860 | 2016-07-29 06:34 | 2016-07-29 09:52 | 198 | 7 | 1386.2333 | 0.004165 | 0.004101 | 2.1032e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784047 | FUSE - ELEMENT/LINK (HV) | 3 x 2 amp weather | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.004101 | 11 | 2017 | 2016-07-29 | C | 7 | 0.004101 | 2.1032e-05
1 | 12680007 | 2016-07-30 10:25 | 2016-07-30 11:30 | 65 | 1 | 65 | 0.00019529 | 0.000186 | 3.0044e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5357E | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Check OMS: 12700181 - 432 Kaharoa. Found DDO fuse blown in transformer, replaced and fuse blew straight away. 50kVA transformer will need to be replaced. 847543 5357E. Replaced 1x 50/3/11 Transformer & 2x 6Amp HV Links. | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000186 | 11 | 2017 | 2016-07-30 | C | 1 | 0.000186 | 3.0044e-06
1 | 12681405 | 2016-07-29 12:15 | 2016-07-29 13:34 | 79 | 84 | 6636 | 0.019938 | 0.01918 | 0.00025238 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 855621 | JUMPER | Jumper Broken @ 8061. Replaced connector and checked others. | F5 | TUTURUMURI | GREYTOWN | Wairarapa | HAU NUI SUB | Western Electricity | POWERCO | 0.01918 | 11 | 2017 | 2016-07-29 | C | 84 | 0.01918 | 0.00025238
1 | 12681430 | 2016-07-29 07:22 | 2016-07-29 16:50 | 568 | 2 | 1136.9333 | 0.0034159 | 0.003397 | 6.009e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 806363 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuse | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.003397 | 6.6 | 2017 | 2016-07-29 | C | 2 | 0.003397 | 6.009e-06
1 | 12681574 | 2016-07-29 07:37 | 2016-07-29 12:00 | 263 | 5 | 1315.25 | 0.0039517 | 0.003906 | 1.5023e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 1479 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Repalce transformer 1479 | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.003906 | 11 | 2017 | 2016-07-29 | C | 5 | 0.003906 | 1.5023e-05
1 | 12681690 | 2016-07-29 07:47 | 2016-08-01 17:22 | 4895 | 8 | 32545.8667 | 0.097784 | 0.097712 | 4.8072e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 803996 | POLE | Pole 803996 found blown over - Isolated at Fuses 698. 1 customer effected, customer has own generator. Car vs pole. Faultman made a temp line break at pole 803990 to replace pole 803996, Fuses 698 were isolated to close the temp line break. 1 X pole & all hardware replaced. 30 meters 16mm copper conductor replaced. 12 sleeves used. | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.097712 | 11 | 2017 | 2016-07-29 | C | 8 | 0.097712 | 4.8072e-05
1 | 12681725 | 2016-07-29 07:52 | 2016-07-29 09:50 | 118 | 4 | 472.7333 | 0.0014203 | 0.001384 | 1.2018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | B12447 | FUSE - ELEMENT/LINK (HV) | 2 x 6amp at 1422 | F3/F4 | KAURI ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.001384 | 11 | 2017 | 2016-07-29 | C | 4 | 0.001384 | 1.2018e-05
1 | 12681775 | 2016-07-29 07:57 | 2016-07-29 10:45 | 168 | 2 | 336.7333 | 0.0010117 | 0.000993 | 6.009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 4045 | FUSE - ELEMENT/LINK (HV) | 2x 3amp Fuses at FC4045 due to weather | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.000993 | 11 | 2017 | 2016-07-29 | C | 2 | 0.000993 | 6.009e-06
1 | 12681781 | 2016-07-29 14:41 | 2016-07-29 15:27 | 46 | 1 | 46 | 0.00013821 | 0.000129 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711396 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replaced all 3 DDOs and 3 x 3 Amp Fuses. | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.000129 | 11 | 2017 | 2016-07-29 | C | 1 | 0.000129 | 3.0045e-06
1 | 12681810 | 2016-07-29 07:59 | 2016-07-29 17:35 | 575 | 3 | 1726.85 | 0.0051883 | 0.005161 | 9.0135e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 806083 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F4 | CROFTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.005161 | 11 | 2017 | 2016-07-29 | C | 3 | 0.005161 | 9.0135e-06
1 | 12681881 | 2016-07-29 08:04 | 2016-07-29 10:30 | 146 | 3 | 439.1 | 0.0013193 | 0.001292 | 9.0135e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1587 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuse | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.001292 | 11 | 2017 | 2016-07-29 | C | 3 | 0.001292 | 9.0135e-06
1 | 12681940 | 2016-07-29 08:09 | 2016-07-29 13:15 | 306 | 1 | 306.3667 | 0.00092048 | 0.000911 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X4261 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F4 | BULLS | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000911 | 11 | 2017 | 2016-07-29 | C | 1 | 0.000911 | 3.0045e-06
1 | 12682009 | 2016-07-29 08:17 | 2016-07-29 13:00 | 283 | 4 | 1133.6 | 0.0034059 | 0.003369 | 1.2018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X344 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 2A fuses, & 2 x holders. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.003369 | 11 | 2017 | 2016-07-29 | C | 4 | 0.003369 | 1.2018e-05
1 | 12682076 | 2016-07-29 08:20 | 2016-07-29 19:20 | 659 | 4 | 2639.2667 | 0.0079297 | 0.007893 | 1.2018e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | L4230 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced transformer L4230 damaged by lightning. | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.007893 | 11 | 2017 | 2016-07-29 | C | 4 | 0.007893 | 1.2018e-05
1 | 12682127 | 2016-07-29 08:23 | 2016-07-29 12:30 | 246 | 1 | 246.8333 | 0.00074161 | 0.000732 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1458 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 2A fuse | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000732 | 11 | 2017 | 2016-07-29 | C | 1 | 0.000732 | 3.0045e-06
1 | 12682139 | 2016-07-29 08:24 | 2016-07-29 13:30 | 306 | 8 | 2451.0667 | 0.0073643 | 0.007292 | 2.4036e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 843771 | FUSE - ELEMENT/LINK (HV) | Retailer called to advise customer said since they logged their job another fuse fell out which caused a fire at the ppyt and now all (5 pptys) the ppty's around them have no power. 11:54am advised SMC. Replace 2 x 3A fuse. | F4 | RAETIHI | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.007292 | 11 | 2017 | 2016-07-29 | C | 8 | 0.007292 | 2.4036e-05
1 | 12682253 | 2016-07-29 08:32 | 2016-07-29 15:30 | 418 | 3 | 1254 | 0.0037677 | 0.00374 | 9.0135e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2523 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 2A & 1 x holder | F4 | BULLS | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.00374 | 11 | 2017 | 2016-07-29 | C | 3 | 0.00374 | 9.0135e-06
1 | 12682360 | 2016-07-29 08:37 | 2016-07-29 15:36 | 419 | 1 | 419.3333 | 0.0012599 | 0.00125 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | M83 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuse | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.00125 | 11 | 2017 | 2016-07-29 | C | 1 | 0.00125 | 3.0045e-06
1 | 12682377 | 2016-07-29 08:38 | 2016-07-29 11:20 | 161 | 4 | 647.6667 | 0.0019459 | 0.001909 | 1.2018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 781075 | FUSE - ELEMENT/LINK (HV) | 3 x 3amp | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001909 | 11 | 2017 | 2016-07-29 | C | 4 | 0.001909 | 1.2018e-05
1 | 12682641 | 2016-07-29 09:02 | 2016-07-30 09:55 | 1492 | 1 | 1492.9833 | 0.0044857 | 0.004476 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | L1080 | FUSE - ELEMENT/LINK (HV) | FM advised that weather is too windy to attend tonight - faultman has spoken to customer and they are not home tonight so they are ok to not have power tonight. Replaced 3x 2Amp HV Links & 2x Fuse Carriers. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.004476 | 11 | 2017 | 2016-07-29 | C | 1 | 0.004476 | 3.0045e-06
1 | 12682673 | 2016-07-29 11:00 | 2016-07-29 11:57 | 57 | 64 | 3648 | 0.01096 | 0.010383 | 0.00019229 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 845444 | CROSSARM - WHOLE ASSEMBLY | Replace 11kV broken cross arm and associated equipment at pole 845444 past fuses 7364. To be done Friday as red defect due to imminent failure. As discussed with ASW | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.010383 | 11 | 2017 | 2016-07-29 | C | 64 | 0.010383 | 0.00019229
1 | 12682767 | 2016-07-29 09:10 | 2016-07-29 17:47 | 516 | 2 | 1033.4 | 0.0031049 | 0.003086 | 6.009e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 803891 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.003086 | 11 | 2017 | 2016-07-29 | C | 2 | 0.003086 | 6.009e-06
1 | 12683062 | 2016-07-29 15:55 | 2016-07-29 17:20 | 85 | 1 | 85 | 0.00025538 | 0.000246 | 3.0045e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T1405 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace transformer. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000246 | 11 | 2017 | 2016-07-29 | C | 1 | 0.000246 | 3.0045e-06
1 | 12683580 | 2016-07-29 10:00 | 2016-07-29 12:05 | 125 | 1 | 125.3833 | 0.00037672 | 0.000367 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC1420 | JUMPER | Connect Jumper back on Fuses FC1420 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.000367 | 11 | 2017 | 2016-07-29 | C | 1 | 0.000367 | 3.0045e-06
1 | 12683667 | 2016-07-29 10:45 | 2016-07-29 13:37 | 172 | 9 | 1548 | 0.004651 | 0.004569 | 2.704e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4036 | CONDUCTOR - REPAIR/REHANG | Fuse found blown at Fuses 4036 - Cause believed to be line clash. Isolated at Fuses 4036 - Lines Rehung. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.004569 | 11 | 2017 | 2016-07-29 | C | 9 | 0.004569 | 2.704e-05
1 | 12684730 | 2016-07-29 10:27 | 2016-07-29 11:07 | 39 | 744 | 29388 | 0.088297 | 0.08159 | 0.0022354 |  | 33 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 381993 | CONDUCTOR - REPAIR/REHANG | at 10:27, Paengaroa Sub, CB 3 Maketu Feeder, Tripped, A B C O/C, L/O. Faultmen dispatched & investigation began. Faultman requested to do cursory patrol on the way to first ABS for sectionalising. On the way, found tree branch on the lines over all 3 phases at Pole 381993. Removed tree branch with hot stick while line was de-energised. All Power Restored on Completion. Ted Glasgow Attended. No Materials Used. This is an NDR but couldn't give NDR number as Ted did it on his Canvas software | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.08159 | 33 | 2017 | 2016-07-29 | C | 744 | 0.08159 | 0.0022354
1 | 12685484 | 2016-07-29 11:41 | 2016-07-29 12:16 | 35 | 68 | 2380 | 0.0071507 | 0.006537 | 0.00020431 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 208525 | CONDUCTOR - REPAIR/REHANG | at 11:41, Aongatete Sub, CB 2 Katikati Feeder. Call of Part Power/No Powers came in. Faultman dispatched. Found tree on lines at pole 208252. Had caused 1 of 3 Fuses at SB1-005 to blow. Advised Control that he would be able to safely remove tree with hot stick if fuses were Open. Control gave permission to complete this, tree removed. All Power Restored on Completion. Shae Deegan Attended. No Materials Used. This is an NDR Job but was done on faultman's canvas and did not supply him with NDR Number at the time. | F4 | KATIKATI | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.006537 | 11 | 2017 | 2016-07-29 | C | 68 | 0.006537 | 0.00020431
1 | 12685495 | 2016-08-30 08:32 | 2016-08-30 13:46 | 314 | 26 | 8164 | 0.02452 | 0.024285 | 7.8089e-05 | NAPA ID:22151 TP_KOPU GXP > WHITIANGA SUB > OWERA RD | 11 | Planned | 022151 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | Earth Switch 9457/1r | NONE | Replace Xarms and Hardware. Matarangi Road, Matarangi, Kopu. W/O 30002514. | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.012143 | 5.5 | 2017 | 2016-08-30 | B | 26 | 0.024285 | 7.8089e-05
1 | 12685505 | 2016-07-29 10:30 | 2016-07-29 16:50 | 379 | 4 | 1519.8 | 0.0045663 | 0.00453 | 1.2018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 784403 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 3A fuse | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.00453 | 11 | 2017 | 2016-07-29 | C | 4 | 0.00453 | 1.2018e-05
1 | 12689331 | 2016-07-29 10:05 | 2016-07-29 19:42 | 577 | 342 | 1860 | 0.0055884 | 0.002505 | 0.00024036 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 220112 | BINDER | Recloser RP 09 Auto Reclose. Fault found to be a floating conductor at Pole 220112. Isolation at ABS IP598 & Links SE5-030. Back feed from UATU6 Via sectionaliser 9954/2. Repairs completed under OMS 12689331 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.002505 | 11 | 2017 | 2016-07-29 | C | 342 | 0.002505 | 0.00024036
1 | 12689706 | 2016-07-29 10:59 | 2016-07-29 13:19 | 139 | 4 | 558.8 | 0.0016789 | 0.001642 | 1.2018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X343 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 2A fuse. Fuses replaced and the ICPs were included in feeder fault under OMS 12699853 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001642 | 11 | 2017 | 2016-07-29 | C | 4 | 0.001642 | 1.2018e-05
1 | 12689794 | 2016-07-29 11:05 | 2016-07-29 16:37 | 332 | 12 | 3985 | 0.011973 | 0.011864 | 3.6054e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE |  | CONDUCTOR - REPAIR/REHANG | Refer OMS 12672612 | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.011864 | 11 | 2017 | 2016-07-29 | C | 12 | 0.011864 | 3.6054e-05
1 | 12690650 | 2016-07-29 12:51 | 2016-07-29 13:24 | 33 | 47 | 1551 | 0.00466 | 0.004236 | 0.00014121 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4548 | JUMPER | Reconnected jumper at Transformer TC4548 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.004236 | 11 | 2017 | 2016-07-29 | C | 47 | 0.004236 | 0.00014121
1 | 12690679 | 2016-07-29 11:25 | 2016-07-29 13:59 | 154 | 403 | 19340 | 0.058107 | 0.054474 | 0.0012108 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 222537 | CONDUCTOR - REPAIR/REHANG | at 11:25, Te Puke Sub, CB 3 Tripped, A B C Fault, E/F, L/O. Faultmen dispatched & investigation began. Began sectionalising feeder. A short time later call came in of lines down at Pole 222537. Isolated Lines at ABS SD6-011 & SE5-221. Remainder of feeder relivened. Permit issued & repairs carried out. All Power Restored on completion. Ted Glasgow Attended. 6x Links & 25m of Conductor Replaced (1 Span 1 Phase). Was high winds in the area at the time. Feeder fault | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.054474 | 11 | 2017 | 2016-07-29 | C | 403 | 0.054474 | 0.0012108
1 | 12691098 | 2016-07-29 11:42 | 2016-07-30 00:15 | 753 | 1 | 753.0333 | 0.0022625 | 0.002253 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | X697 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a HV fuses @ X697 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.002253 | 11 | 2017 | 2016-07-29 | C | 1 | 0.002253 | 3.0045e-06
1 | 12691105 | 2016-07-29 13:00 | 2016-07-29 13:47 | 47 | 34 | 1614.4333 | 0.0048506 | 0.004544 | 0.00010215 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 211434 | CONDUCTOR - REPAIR/REHANG | at 13:00, Tauranga GXP, 11kV CB 19 Bethlehem Feeder. Call came in of trees touching lines at Pole 211434. Isolated lines at Fuses SD3-046. Permit issued & repairs carried out. All Power Restored on Completion. Dave Ngatai Attended. No Materials Used. NDR 51219 - trees within shelter belt. Advised SMC. Police event number P026104998. | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.004544 | 11 | 2017 | 2016-07-29 | C | 34 | 0.004544 | 0.00010215
1 | 12696367 | 2016-07-29 11:50 | 2016-07-29 13:40 | 110 | 1 | 110.4667 | 0.0003319 | 0.000322 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1118 | LIGHTNING ARRESTOR (HV) | Replace 2 x 3A fuse at transformer 1118. May need investigation as to what transformer these ICP's are fed from. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000322 | 11 | 2017 | 2016-07-29 | C | 1 | 0.000322 | 3.0045e-06
1 | 12697082 | 2016-07-29 12:37 | 2016-07-29 14:20 | 103 | 1 | 103.3667 | 0.00031057 | 0.000301 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N/A - NOT APPLICABLE | UNKNOWN | Replace 2 x 5A HV fuse | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.000301 | 11 | 2017 | 2016-07-29 | C | 1 | 0.000301 | 3.0045e-06
1 | 12698134 | 2016-07-29 13:07 | 2016-07-29 13:52 | 45 | 1412 | 10945.0167 | 0.032884 | 0.020157 | 0.0042424 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | 33kV CB X20 at FEI sub tripped to lock out at 1306hrs. LOS to KIM Sub. Sub back fed on the 11kV and all completed by 1321Hrs. Line patrolled, branches on line at pole P19361 (or P19561??) due to high winds in area. Branches cleared by wind, 33kV re-livened, all power restored. Note: on restoration of back feed KIM CB 7 tripped to lock out at 1406hrs. On discussion with NCTL it was agreed the cause was due to vegetation. NCTL advised duty NC to re-close CB at 1407hrs. NO further issues encountered. | S4 | FEILDING-KIMBOLTON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.020157 | 33 | 2017 | 2016-07-29 | C | 1412 | 0.020157 | 0.0042424
1 | 12699853 | 2016-07-29 13:19 | 2016-07-29 19:40 | 380 | 312 | 82701.5 | 0.24848 | 0.24566 | 0.00093741 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 367048 | CONDUCTOR - REPAIR/REHANG | Repaired 3 spans of lone beyond Pole 367048 used +/- 30m 25mm copper and 20 sleves | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.24566 | 11 | 2017 | 2016-07-29 | C | 312 | 0.24566 | 0.00093741
1 | 12700356 | 2016-07-29 08:00 | 2016-07-29 10:05 | 125 | 1 | 125 | 0.00037556 | 0.000366 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 745570 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000366 | 11 | 2017 | 2016-07-29 | C | 1 | 0.000366 | 3.0045e-06
1 | 12700563 | 2016-07-29 13:40 | 2016-07-29 16:11 | 150 | 183 | 13456.6 | 0.04043 | 0.038781 | 0.0010997 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 561 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | RS C216 Tripped B,C Ph E/F L/O at 1340hrs. Report from public of pole hit and lines down. Found LV lines down, fuses pulled to transformer T2561 for repairs. Recloser C216 re-closed at 1426hrs. At 1543hrs, recloser C216 trip to lock out for second time at 1543hrs. NOC unable to contact repair crew at T2561 site. NOC requested SMC dispatch fault man to site to check crew safety. Fault man confirmed crew all safe, advised transformer T2561 was faulty, requiring replacement. NOC advised that repairs on LV were still underway. Fault man confirmed repairs had been completed, however the repair crew had re livened T2561 without NOC authorisation. This aspect was discussed in detail between fault man and repair crew this was not correct operational protocol. Recloser C216 re-closed at 1611hrs, Transformer T2561 replacement then duly completed. Safety Manager 647329 completed by NOC. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.038781 | 11 | 2017 | 2016-07-29 | C | 183 | 0.038781 | 0.0010997
1 | 12700783 | 2016-07-29 08:00 | 2016-07-29 10:29 | 149 | 71 | 10579 | 0.031785 | 0.031144 | 0.00021332 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 751948 | FUSE - ELEMENT/LINK (HV) | 3 x 2amp | F3 | CITY 3 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.031144 | 11 | 2017 | 2016-07-29 | C | 71 | 0.031144 | 0.00021332
1 | 12700879 | 2016-07-29 08:00 | 2016-07-29 10:15 | 135 | 5 | 675 | 0.002028 | 0.001982 | 1.5023e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 742956 | FUSE - ELEMENT/LINK (HV) | 2 x 3amp | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.001982 | 11 | 2017 | 2016-07-29 | C | 5 | 0.001982 | 1.5023e-05
1 | 12700906 | 2016-07-29 08:00 | 2016-07-29 11:00 | 180 | 8 | 1440 | 0.0043265 | 0.004254 | 2.4036e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 746383 | FUSE - ELEMENT/LINK (HV) | 3 x 3amp | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.004254 | 11 | 2017 | 2016-07-29 | C | 8 | 0.004254 | 2.4036e-05
1 | 12703117 | 2016-07-29 08:00 | 2016-07-29 09:00 | 60 | 5 | 300 | 0.00090135 | 0.000856 | 1.5023e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 745240 | FUSE - ELEMENT/LINK (HV) | 3 x 3amp | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000856 | 11 | 2017 | 2016-07-29 | C | 5 | 0.000856 | 1.5023e-05
1 | 12704868 | 2016-07-29 14:59 | 2016-07-29 17:40 | 161 | 23 | 3711.05 | 0.01115 | 0.010942 | 6.9104e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 851809 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 15A fuse | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.010942 | 11 | 2017 | 2016-07-29 | C | 23 | 0.010942 | 6.9104e-05
1 | 12707202 | 2016-07-29 15:51 | 2016-07-29 23:39 | 468 | 5 | 2341.1667 | 0.0070341 | 0.006988 | 1.5023e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 390337 | FUSE - ELEMENT/LINK (HV) | Also affecting 120 OLIVER ROAD OMS 12707305 - next Tx down - check fuses FC4000. 2 fuses blown at FC4000. Possibly weather related. | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.006988 | 11 | 2017 | 2016-07-29 | C | 5 | 0.006988 | 1.5023e-05
1 | 12707326 | 2016-07-29 16:04 | 2016-07-29 21:43 | 338 | 10 | 3389.6667 | 0.010184 | 0.010094 | 3.0045e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | I12389 | CONDUCTOR - REPAIR/REHANG | repaired 4 lines ( 3 phases on 1 span) that were down due to tree through lines (farmers Trees) used 40 meters of conductor - repaired and rehung lines Les is going to call back with NDR and pole number that he will get from marty NDR # 55719 then lines were down on Scottsman Valley Road No other assets repaired or replaced. Adjacent assets were checked and confirmed as being ok FULL POWER RESTORE Part of OMS 12704450 | F4 | KIWITAHI | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.010094 | 11 | 2017 | 2016-07-29 | C | 10 | 0.010094 | 3.0045e-05
1 | 12708907 | 2016-07-29 17:35 | 2016-07-29 20:27 | 171 | 1 | 171.9167 | 0.00051653 | 0.000507 | 3.0045e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4193T | FUSE - ELEMENT/LINK (HV) | Replaced 3x 3A HV fuses @ 4193T | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000507 | 6.6 | 2017 | 2016-07-29 | C | 1 | 0.000507 | 3.0045e-06
1 | 12710367 | 2016-07-29 18:25 | 2016-07-29 21:19 | 173 | 10 | 1736.1667 | 0.0052163 | 0.005126 | 3.0045e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P00752 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6a HVfuses @ V44 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.005126 | 11 | 2017 | 2016-07-29 | C | 10 | 0.005126 | 3.0045e-05
1 | 12710483 | 2016-07-29 18:37 | 2016-07-29 22:59 | 262 | 112 | 15632.3167 | 0.046967 | 0.045957 | 0.00048974 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 735041 | POLE | Reported Car v pole from Alistar from NPE tech 027 298 2989. He reports that a pole has been hit by a car on the Stratford-Opunake Road between Ronald & Hastings Roads. The pole is gone and the lines are less than 2 meters from the ground but in the air. NC dropped the feeder for safety. Alistar has agreed to remain on site to prevent public accessing the site until field switchers arrive. Section of line between ABS 5930 , 5746 , 5848 and 5940 isolated to replace pole 735041 after car vs pole balance of line backfed via ABS 5975 for the duration of repairs. NDR: N100200. | F4 | MAHOE | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.045957 | 11 | 2017 | 2016-07-29 | C | 112 | 0.045957 | 0.00048974
1 | 12711035 | 2016-07-29 19:12 | 2016-07-29 21:18 | 126 | 1 | 126 | 0.00037857 | 0.000369 | 3.0045e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 1619 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a fuses @ 1619 | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000369 | 11 | 2017 | 2016-07-29 | C | 1 | 0.000369 | 3.0045e-06
1 | 12712663 | 2016-07-29 22:42 | 2016-07-30 00:19 | 97 | 4 | 388.8 | 0.0011682 | 0.001132 | 1.2018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 220489 | FUSE - ELEMENT/LINK (HV) | 10:52pm called through to SMC (Glo) -HEARD A HUGE EXPLOSION THEN NO POWER. 2x8 amp HV fuses blown at Fuses SD5-086. Line patrolled fuses reloaded & livened. | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.001132 | 11 | 2017 | 2016-07-29 | C | 4 | 0.001132 | 1.2018e-05
1 | 12712702 | 2016-07-29 06:51 | 2016-07-30 11:54 | 1742 | 11 | 19073.9667 | 0.057308 | 0.057208 | 3.305e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 7121 | FUSE - ELEMENT/LINK (HV) | On arrival found fuse holder burnt in half and removed other fuse. Due to terrain and access will return in daylight to patrol to locate fault. Patrolled, No fault found. Replaced 1x 6Amp HV Link & 1x Fuse Carrier | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.057208 | 11 | 2017 | 2016-07-29 | C | 11 | 0.057208 | 3.305e-05
1 | 12713201 | 2016-07-30 06:59 | 2016-07-30 09:06 | 127 | 2 | 254.3667 | 0.00076424 | 0.000746 | 6.0089e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FC2348 | FUSE - ELEMENT/LINK (HV) | Reloaded, Relivened 2x 2A HV Fuses at Fuses FC2348. High winds at the time. | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.000746 | 11 | 2017 | 2016-07-30 | C | 2 | 0.000746 | 6.0089e-06
1 | 12713259 | 2016-07-30 07:58 | 2016-07-30 10:08 | 129 | 109 | 8981.8333 | 0.026986 | 0.026003 | 0.00057986 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 798184 | CONDUCTOR - REPAIR/REHANG | RS C634/2 A/R, L/O. O/C A & B Phase. Feeder sectionalised with branch found sitting on lines after tree had fallen. Branch removed using hot stick. Also attended by Adam Whale. NDR# 23283. | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.026003 | 11 | 2017 | 2016-07-30 | C | 109 | 0.026003 | 0.00057986
1 | 12714309 | 2016-07-30 10:18 | 2016-07-30 15:35 | 317 | 1 | 317.0333 | 0.00095252 | 0.000943 | 3.0044e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X520 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced 30/11/3 Transformer, 1 Arm Brace & 3x3A HV Links | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000943 | 11 | 2017 | 2016-07-30 | C | 1 | 0.000943 | 3.0044e-06
1 | 12715483 | 2016-07-30 13:58 | 2016-07-30 15:50 | 112 | 1 | 112.3167 | 0.00033745 | 0.000328 | 3.0044e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X2326 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 3Amp HV Links due to lightning. | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.000328 | 6.6 | 2017 | 2016-07-30 | C | 1 | 0.000328 | 3.0044e-06
1 | 12716620 | 2016-07-30 15:58 | 2016-07-30 17:36 | 98 | 680 | 41524.7333 | 0.12476 | 0.11863 | 0.002043 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | P35759 | UNKNOWN | Line is arcing and sparking at 656 Taikorea Road, Rongatea - advised control. Line LV, line separated at Pole P35759. RS 10183 Tripped C Ph E/F. Line Patrolled and sectionlised with no fault found. | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.11863 | 11 | 2017 | 2016-07-30 | C | 680 | 0.11863 | 0.002043
1 | 12718071 | 2016-07-30 16:30 | 2016-07-30 17:48 | 77 | 423 | 31480.35 | 0.094582 | 0.090769 | 0.0012709 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Line had come off crossarm link to 12717879 | S4 | MOTUKAWA SOUTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.090769 | 33 | 2017 | 2016-07-30 | C | 423 | 0.090769 | 0.0012709
1 | 12718322 | 2016-07-30 16:50 | 2016-07-30 22:13 | 322 | 46 | 14805.35 | 0.044482 | 0.044067 | 0.00013821 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 12720101 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses 803 lines down found on patrol at Pole 781091. Isolated at Fuses 803. Used 8 mtrs of conductor, 3 x sleeves, 2 x 15 amp HV fuses. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.044067 | 11 | 2017 | 2016-07-30 | C | 46 | 0.044067 | 0.00013821
1 | 12718438 | 2016-07-30 17:27 | 2016-07-30 17:37 | 10 | 1646 | 14977.9 | 0.045001 | 0.030164 | 0.0049454 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT LIGHTNING STRIKE | 1092 | UNKNOWN | CST GXP 33kV CB 1092 neutral time E/F and A/R. However 11kV CB 1 at OKA sub tripped and locked out resulting in loss of supply to ICPs. Suspect A/R event was due to severe lightning at the time. Note auto change over did not operate either. As 33kV was still live, Re-Livened sub successfully. Auto change over issue to be investigated as second time issue has occurred in three days. | S1 | CARRINGTON ST1092 OAKURA4162 33KV | CARRINGTON ST 33 | Taranaki | TP_CARRINGTON | Western Electricity | POWERCO | 0.030164 | 33 | 2017 | 2016-07-30 | C | 1646 | 0.030164 | 0.0049454
1 | 12720110 | 2016-07-30 17:42 | 2016-07-31 11:00 | 1038 | 22 | 22844.4333 | 0.068635 | 0.068437 | 6.6098e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 728030 | CONDUCTOR - REPAIR/REHANG | Fuses found blown at Fuses LI732 line down found on patrol. Isolated at fuses LI732. Unable to get lines back up in wind (refer OMS 12718412). Repaired using 4x conductor joints, 2x metres of Poco conductor, 2x 20Amp HV Links | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.068437 | 11 | 2017 | 2016-07-30 | C | 22 | 0.068437 | 6.6098e-05
1 | 12720380 | 2016-07-30 17:51 | 2016-07-30 23:16 | 324 | 4 | 1298.8 | 0.0039022 | 0.003866 | 1.2018e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752500 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer replaced 3/11/30kVA transformer | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.003866 | 11 | 2017 | 2016-07-30 | C | 4 | 0.003866 | 1.2018e-05
1 | 12720447 | 2016-07-30 18:01 | 2016-07-30 23:45 | 343 | 1 | 343.9167 | 0.0010333 | 0.001024 | 3.0044e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 939 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Fuses found blown at Transformer 939 Transformer found to be faulty used 1 x 50 kVA transformer 3 x 6 amp fuses, set of LV binders | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.001024 | 11 | 2017 | 2016-07-30 | C | 1 | 0.001024 | 3.0044e-06
1 | 12720504 | 2016-07-30 20:16 | 2016-07-30 21:07 | 51 | 1 | 51 | 0.00015323 | 0.000144 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10029 | FUSE - ELEMENT/LINK (HV) | Fuse found blown at Transformer T5/80 also insulator damaged below DDO's - cause Lightning Isulator removed under own AP. Used 2 x 3 amp fuse. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.000144 | 11 | 2017 | 2016-07-30 | C | 1 | 0.000144 | 3.0044e-06
1 | 12720871 | 2016-07-30 19:47 | 2016-07-30 22:41 | 174 | 468 | 39426.3 | 0.11846 | 0.11424 | 0.0014061 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F0593 | CROSSARM - WHOLE ASSEMBLY | CB 1 Trip . A,B,C O/C Def T E/F Ground. Report of sparking lines at Tower Rd Mowbray Rd intersection. Broken Crossarm at pole F0593. Isolation at ABS IC1311 & IC766. Back feed from TWR CB 1 via ABS IC759. Materials Used: 1xcrossarm 3x insulators. | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.11424 | 11 | 2017 | 2016-07-30 | C | 468 | 0.11424 | 0.0014061
1 | 12722670 | 2016-07-30 21:34 | 2016-07-30 23:17 | 102 | 108 | 4100.1833 | 0.012319 | 0.011345 | 0.00012318 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | N/A - NOT APPLICABLE | UNKNOWN | Sectionliser 2917 tripped A,B Ph O/C No Fault found while sectionlising | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.011345 | 11 | 2017 | 2016-07-30 | C | 108 | 0.011345 | 0.00012318
1 | 12722968 | 2016-07-30 21:56 | 2016-07-31 00:14 | 138 | 288 | 8553 | 0.025697 | 0.023101 | 0.00086529 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 747125 | POLE | Fire services called Car V Pole Lines down on Car Event Number F2124125. Feeder dropped off Faultman advised lines LV fuses opened at transformer 731 - feeder livened. LV line break made at pole 391478 all power restored except to hall. Pole 747125 hit by car - pole to be replaced at later date. 1/08: Safety tag A13048, applied Henwood Hall , line has been dropped and made safe as is road crossing. As a result of accident, line has been pulled away from barge board, Mark has made contact with hall owner. | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.023101 | 11 | 2017 | 2016-07-30 | C | 288 | 0.023101 | 0.00086529
1 | 12765352 | 2016-07-30 21:51 | 2016-07-30 23:08 | 76 | 1 | 76.5167 | 0.00022989 | 0.00022 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | M83 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at fuses M83 - cause weather. Used 2 x 6 amp fuses. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.00022 | 11 | 2017 | 2016-07-30 | C | 1 | 0.00022 | 3.0044e-06
1 | 12765712 | 2016-07-30 23:51 | 2016-07-31 19:10 | 1159 | 108 | 45999.5 | 0.1382 | 0.13723 | 0.0010065 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 842169 | CONDUCTOR - REPAIR/REHANG | Sec 2917 tripped O/C E/F. Found pole 842169 leaning contacting trees due to land slip. Isolated at Links 2873. Materials Used: 3m conductor 2 joints. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.13723 | 11 | 2017 | 2016-07-30 | C | 108 | 0.13723 | 0.0010065
1 | 12768182 | 2016-07-31 05:26 | 2016-07-31 06:17 | 51 | 2 | 102.5333 | 0.00030805 | 0.00029 | 6.0088e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 6942 | UNKNOWN | RS 6942 Tripped B ph O/C E/F RS would not operate remotely - Battery fault reset on site. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.00029 | 11 | 2017 | 2016-07-31 | C | 2 | 0.00029 | 6.0088e-06
1 | 12768190 | 2016-07-31 05:37 | 2016-07-31 07:09 | 91 | 430 | 38966.05 | 0.11707 | 0.1132 | 0.0012919 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | N/A - NOT APPLICABLE | UNKNOWN | CB 24 Trip, O/C, E/F. Sectionalised after lightning strike. No fault found | F1 | AIRPORT DRIVE | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.1132 | 11 | 2017 | 2016-07-31 | C | 430 | 0.1132 | 0.0012919
1 | 12768624 | 2016-07-31 05:38 | 2016-07-31 09:15 | 217 | 8 | 1737.7333 | 0.0052209 | 0.005148 | 2.4036e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 726738 | CROSSARM - COMPONENT(S) ONLY | Crossarm Tipped over. Isolated at Fuses LI715 & repaired. Materials used: 1x HV Fuse Carrier, 2x 6Amp HV Links, 1x 300mm Bolt | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.005148 | 11 | 2017 | 2016-07-31 | C | 8 | 0.005148 | 2.4036e-05
1 | 12769485 | 2016-07-31 08:17 | 2016-07-31 14:47 | 389 | 222 | 61528.1 | 0.18486 | 0.18286 | 0.00066699 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 389049 | CONDUCTOR - REPAIR/REHANG | Recloser 4222 trip E/F O/C found line down at pole 389049. Isolated at ABS 2733. Materials Used: 40 metres 16mmCu conductor 6 and 6 x 16mm sleeves | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.18286 | 11 | 2017 | 2016-07-31 | C | 222 | 0.18286 | 0.00066699
1 | 12770323 | 2016-07-31 08:43 | 2016-07-31 12:20 | 217 | 1 | 217.0333 | 0.00065206 | 0.000643 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | p21616 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp at M83 | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000643 | 11 | 2017 | 2016-07-31 | C | 1 | 0.000643 | 3.0044e-06
1 | 12770360 | 2016-07-31 09:07 | 2016-07-31 11:39 | 152 | 32 | 4873.6 | 0.014642 | 0.014354 | 9.6142e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711181 | CROSSARM - WHOLE ASSEMBLY | Crossarm tipped over Isolated at fuses PU 364 materials 10m conductor 4 sleeve 1 x 15 fuse and sundries | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.014354 | 11 | 2017 | 2016-07-31 | C | 32 | 0.014354 | 9.6142e-05
1 | 12770491 | 2016-07-31 13:00 | 2016-07-31 14:58 | 118 | 42 | 4956 | 0.01489 | 0.014511 | 0.00012619 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P16866 | JUMPER | Jumper at pole P16866 blown isolated at ABS' U13, U15 & U12. | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.014511 | 11 | 2017 | 2016-07-31 | C | 42 | 0.014511 | 0.00012619
1 | 12771146 | 2016-07-31 09:50 | 2016-07-31 13:00 | 189 | 2 | 379.6667 | 0.0011407 | 0.001122 | 6.0088e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784626 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp fuse 282 and 1 holder | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.001122 | 11 | 2017 | 2016-07-31 | C | 2 | 0.001122 | 6.0088e-06
1 | 12771154 | 2016-07-31 09:53 | 2016-07-31 12:50 | 176 | 1 | 176.9667 | 0.00053169 | 0.000522 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC5192 | FUSE - ELEMENT/LINK (HV) | 3 x 8A HV Fuses. Bottom of Fuse Holder needed cleaning. | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.000522 | 11 | 2017 | 2016-07-31 | C | 1 | 0.000522 | 3.0044e-06
1 | 12771251 | 2016-07-31 10:24 | 2016-07-31 13:40 | 195 | 373 | 21480.9 | 0.064538 | 0.061176 | 0.0011207 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 774389 | CROSSARM - WHOLE ASSEMBLY | CB 8 tripped E/F. Broken cross arm located. Isolated at Fuses 2546. Materials Used: 1 cross arm complete. | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.061176 | 11 | 2017 | 2016-07-31 | C | 373 | 0.061176 | 0.0011207
1 | 12772393 | 2016-07-31 11:22 | 2016-07-31 12:12 | 50 | 1412 | 42435.1667 | 0.12749 | 0.11477 | 0.0042423 |  | 33 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P19561 | NONE | CB x20 O/C E/F Trees have fallen and brushed through lines at Pole P19561 Trees are approx 30mtrs away from lines but slid down a hillside into the lines. Chris has contacted Treecsape to see what can be done about the remaining trees as there is a possibility that they may also give problems. After checking site line was re-livened. Trees to be removed tomorrow 01/08/16. OMS 12779815 | S4 | FEILDING-KIMBOLTON 33KV | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.11477 | 33 | 2017 | 2016-07-31 | C | 1412 | 0.11477 | 0.0042423
1 | 12778854 | 2016-07-31 16:28 | 2016-08-02 12:42 | 2653 | 1 | 2653.9167 | 0.0079735 | 0.007964 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 394325 | BINDER | Fuses 1177 Opened & Tagged as not safe to continue with job due to weather Created OMS 12782090 but this job will not force up to fuses. Floating conductor to be rebound 02/08/16 Faultman repaired floating coductor at pole 394325, line was isolated at Fuses 1177 to make the repairs. 2 X Binders used | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.007964 | 11 | 2017 | 2016-07-31 | C | 1 | 0.007964 | 3.0044e-06
1 | 12778954 | 2016-07-31 11:17 | 2016-07-31 12:14 | 57 | 3 | 171.2 | 0.00051436 | 0.000487 | 9.0133e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 774434 | FUSE - ELEMENT/LINK (HV) | Following Feeder 2 x 2Amp Fuses were replaced at X2400. | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000487 | 11 | 2017 | 2016-07-31 | C | 3 | 0.000487 | 9.0133e-06
1 | 12779121 | 2016-07-31 12:42 | 2016-07-31 15:52 | 189 | 1 | 189.65 | 0.00056979 | 0.00056 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | x4040 | FUSE - ELEMENT/LINK (HV) | 2 x 8A HV Fuses | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.00056 | 11 | 2017 | 2016-07-31 | C | 1 | 0.00056 | 3.0044e-06
1 | 12779445 | 2016-07-31 13:36 | 2016-07-31 15:20 | 103 | 1 | 103.55 | 0.00031111 | 0.000302 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | M83 | FUSE - ELEMENT/LINK (HV) | Contractor arrived 10:34am and worked till 12:00pm for a previous job tgf0612168, said problem be with transformer if the fuses blow again. Both pole fuses blew again at 12:55pm. Please investigate transformer,Dog Restrained, Alternate Descr of Location: Job Type Code: NPN Emergency Services: No Emergency Details: Life Threatening? No Main Switch Off Phone Number Other: 0274433737 Customer Responsibility Advised? No 2x 6Amp fuses | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000302 | 11 | 2017 | 2016-07-31 | C | 1 | 0.000302 | 3.0044e-06
1 | 12779508 | 2016-07-31 13:38 | 2016-07-31 15:00 | 81 | 1 | 81.7667 | 0.00024566 | 0.000236 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | PU231 | FUSE - ELEMENT/LINK (HV) | Replaced 1x3A Transformer fuse at P1440 & & 1x 8Amp at PU231 | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.000236 | 11 | 2017 | 2016-07-31 | C | 1 | 0.000236 | 3.0044e-06
1 | 12780254 | 2016-07-31 08:55 | 2016-07-31 16:30 | 454 | 4 | 1819.9333 | 0.0054679 | 0.005431 | 1.2018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 6933 | FUSE - ELEMENT/LINK (HV) | Nick Patton found these 2x 10Amp HV Fuses | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.005431 | 11 | 2017 | 2016-07-31 | C | 4 | 0.005431 | 1.2018e-05
1 | 12780703 | 2016-07-31 15:23 | 2016-07-31 23:15 | 471 | 379 | 43710.85 | 0.13133 | 0.12791 | 0.0021332 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 703920 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer 1440 found to be faulty during sectionlising Hub to organise crew faultman logged off job to continue with other faults Work site Isolated at Fuses PU231 used 1 x 30kVA 3 Ph transformer, 3 x 3amp fuses, 2 x carriers, 6 x sleeves, 16 mtrs conductor | F4 | WAREA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.12791 | 11 | 2017 | 2016-07-31 | C | 379 | 0.12791 | 0.0021332
1 | 12781095 | 2016-07-31 15:14 | 2016-07-31 16:52 | 97 | 122 | 8450.0333 | 0.025388 | 0.024287 | 0.00064295 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M2245 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer M2245 found to be faulty during sectionlising Replaced under own AP - cause lightning Used 1 x 30 kVA transformer 3 Ph and 2 x 3 amp fuses | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.024287 | 11 | 2017 | 2016-07-31 | C | 122 | 0.024287 | 0.00064295
1 | 12781162 | 2016-07-31 15:30 | 2016-07-31 17:20 | 110 | 1 | 110.4167 | 0.00033174 | 0.000322 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 1166 | FUSE - ELEMENT/LINK (HV) | 3x 6Amp | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.000322 | 11 | 2017 | 2016-07-31 | C | 1 | 0.000322 | 3.0044e-06
1 | 12781873 | 2016-07-31 16:06 | 2016-07-31 18:34 | 147 | 1 | 147.65 | 0.00044361 | 0.000434 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 2934 | FUSE - ELEMENT/LINK (HV) | 2x 6Amp HV Links | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000434 | 11 | 2017 | 2016-07-31 | C | 1 | 0.000434 | 3.0044e-06
1 | 12782043 | 2016-07-31 16:14 | 2016-07-31 17:20 | 65 | 1 | 65.4667 | 0.00019669 | 0.000187 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | X4202 | FUSE - ELEMENT/LINK (HV) | 3 x 2A HV Fuse | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.000187 | 11 | 2017 | 2016-07-31 | C | 1 | 0.000187 | 3.0044e-06
1 | 12782744 | 2016-07-31 18:17 | 2016-07-31 19:48 | 91 | 4 | 365 | 0.0010966 | 0.00106 | 1.2018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 4056 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses 4056 - cause wind. Used 2 x 6 amp | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.00106 | 11 | 2017 | 2016-07-31 | C | 4 | 0.00106 | 1.2018e-05
1 | 12782767 | 2016-07-31 17:32 | 2016-07-31 17:59 | 27 | 6 | 162.25 | 0.00048747 | 0.000433 | 1.8027e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 233 | FUSE - ELEMENT/LINK (HV) | Faultman Leighton Harris replaced 2x 50Amp HV Fuses at Sw/Gear 233. Unknown cause. Army camp will need a planned shut down at some stage. | F3/F4 | RUAPEHU | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.000433 | 11 | 2017 | 2016-07-31 | C | 6 | 0.000433 | 1.8027e-05
1 | 12782796 | 2016-07-31 15:22 | 2016-08-01 13:41 | 1338 | 4 | 5354.9333 | 0.016089 | 0.016052 | 1.2018e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | LI762 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformers L1053 & L1055 are blown and requires replacement. Isolate at Fuses L!762 to replace transformers. Replace 1 x 15kVA 7 1 x 30kVA & 3 x 10-A fuses at Fuses 8804. Transformer L1055 has been left disconnected for safety due to a blown customer service line. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.016052 | 11 | 2017 | 2016-07-31 | C | 4 | 0.016052 | 1.2018e-05
1 | 12823599 | 2016-07-31 20:23 | 2016-07-31 21:24 | 61 | 45 | 2745 | 0.0082472 | 0.007841 | 0.0001352 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 782781 | FUSE - ELEMENT/LINK (HV) | 3 fuses found blown at Transformer X2067 - Cause lightning. DDO damaged and had to be replaced. Isolated at ABS's 1073 and 815 with back feed via ABS 068. Used 3 x 2 amp fuses and 1 x carrier and base. | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.007841 | 11 | 2017 | 2016-07-31 | C | 45 | 0.007841 | 0.0001352
1 | 12823918 | 2016-07-31 20:10 | 2016-08-01 11:59 | 949 | 108 | 38921.9833 | 0.11694 | 0.11596 | 0.00012318 |  | 11 | Unplanned |  | OVERHEAD LINE | OUTAGE RESTORED | OUTAGE RESTORED | 842169 | POLE | Slip causing trees to contact lines referral job already in system sectionaliser to be left off over night refer OMS 12781768. Faultman straightened pole 842169 that had moved in the slip, pole will be moved at later in a planned shut down. NDR 17521 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.11596 | 11 | 2017 | 2016-07-31 | C | 108 | 0.11596 | 0.00012318
1 | 12824056 | 2016-07-31 20:28 | 2016-07-31 21:59 | 90 | 171 | 5290.4167 | 0.015895 | 0.014353 | 0.00051376 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | K12720 | POLE | at 20:28, Tahuna Sub, CB 2 Mangateparu Feeder. Call came in from Callcare of a report of a Powerco Pole that was badly leaning over into some trees on Valentine Rd and was causing the trees to smoulder. WEL Networks had originally advised Callcare as this area is on the border of WEL & Powerco's Networks. Callcare advised of Pole Number K12720. NOC located affected Pole & Feeder on GIS. NOC Controller Opened Recloser 9320 to de-energise affected Pole at 20:28. Faultmen dispatched. Isolated affected area at Fuses FC2147. Remainder of feeder relivened. Faultmen carried out temp repairs to Pole K12720. All Power Restored on Completion. Marty Keenan Attended. There are a number of poles on this road that are badly affected. Sean Malloy from Downer will take photos tomorrow & advise Bernard Dale of the issue to get repairs carried out in this area on other affected poles. No Materials Used Mel from Callcare advised that someone has contacted WEL Networks and advised of Pole Leaning badly into trees/bushes and is smoldering. Is in Powerco network. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.014353 | 11 | 2017 | 2016-07-31 | C | 171 | 0.014353 | 0.00051376
1 | 12825241 | 2016-08-01 09:17 | 2016-08-01 10:23 | 65 | 19 | 1249.8833 | 0.0037552 | 0.003583 | 5.7084e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 718742 | CROSSARM - WHOLE ASSEMBLY | Car v pole at 718742. Pole ok but line isolated at fuses MA550 to replace broken crossarm. 1 x HV crossarm & assembly materials required. All supply restored following repairs. NDR number 38866. | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.003583 | 11 | 2017 | 2016-08-01 | C | 19 | 0.003583 | 5.7084e-05
1 | 12825368 | 2016-08-01 07:22 | 2016-08-01 09:15 | 112 | 38 | 4283.2333 | 0.012869 | 0.012526 | 0.00011417 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 790995 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses 1138. 2 x 15 amp. Possible bird strike. | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.012526 | 11 | 2017 | 2016-08-01 | C | 38 | 0.012526 | 0.00011417
1 | 12825443 | 2016-08-01 10:35 | 2016-08-01 11:45 | 70 | 172 | 12040 | 0.036173 | 0.034622 | 0.00051676 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227184 | CONDUCTOR - REPAIR/REHANG | Emergency isolation to repair broken conductor at pole 227184. Replace 3mtrs Namu Conductor. 2 x HV Fuses. | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.034622 | 11 | 2017 | 2016-08-01 | C | 172 | 0.034622 | 0.00051676
1 | 12825725 | 2016-08-01 08:14 | 2016-08-01 12:20 | 246 | 1 | 246.4833 | 0.00074054 | 0.000731 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P21616 | FUSE - ELEMENT/LINK (HV) | Reload at fuses M83 due to Weather | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000731 | 11 | 2017 | 2016-08-01 | C | 1 | 0.000731 | 3.0044e-06
1 | 12825792 | 2016-08-01 09:17 | 2016-08-01 09:23 | 5 | 198 | 1115.4 | 0.0033511 | 0.001566 | 0.00059487 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Tripped when switching being carried out NAPA 23005. HLT was on recloser in rediness for LLP | F3 | OMOKOROA RD | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.001566 | 11 | 2017 | 2016-08-01 | C | 198 | 0.001566 | 0.00059487
1 | 12825927 | 2016-08-16 08:58 | 2016-08-16 14:47 | 349 | 30 | 10470 | 0.031451 | 0.03118 | 9.0118e-05 | NAPA ID:21792 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 021792 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 200520 | NONE | Replace poles, hardware and conductors between Poles 200520 & 217767 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.01559 | 5.5 | 2017 | 2016-08-16 | B | 30 | 0.03118 | 9.0118e-05
1 | 12825971 | 2016-08-01 11:22 | 2016-08-01 22:30 | 668 | 1 | 668 | 0.0020069 | 0.001997 | 3.0044e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X63 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | This transformer is not the one with the fault on it, it is transformer X63 and is faulty and will be replaced. Materials used: 3/11/15kVA transformer, 1x LV fuseholder complete, 1x 63A HRC Fuse. Outage reflected under OMS 12832079 | F4 | MISSION RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.001997 | 11 | 2017 | 2016-08-01 | C | 1 | 0.001997 | 3.0044e-06
1 | 12826039 | 2016-08-23 09:27 | 2016-08-23 15:01 | 334 | 11 | 3682.6167 | 0.011061 | 0.010962 | 3.3041e-05 | NAPA ID:21795 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 021795 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 217752 | NONE | Replace poles, hardware and conductors between Poles 217752 & 217767. Work location: Porr Pori Road. Work Order 30017844 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.005481 | 5.5 | 2017 | 2016-08-23 | B | 11 | 0.010962 | 3.3041e-05
1 | 12826201 | 2016-08-25 08:50 | 2016-08-25 13:55 | 305 | 11 | 3355 | 0.010077 | 0.009978 | 3.304e-05 | NAPA ID:21797 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 021797 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 217752 | NONE | Replace poles, hardware and conductors between poles 217752 & 217767. Works Location: Pori Pori Road. Work Order 30017844 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.004989 | 5.5 | 2017 | 2016-08-25 | B | 11 | 0.009978 | 3.304e-05
1 | 12826475 | 2016-08-01 09:18 | 2016-08-01 10:18 | 59 | 70 | 4197.6667 | 0.012612 | 0.01198 | 0.00021031 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P37958 | FUSE - ELEMENT/LINK (HV) | Reload at fuses E67 / 2 x 10A due to Birds. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.01198 | 11 | 2017 | 2016-08-01 | C | 70 | 0.01198 | 0.00021031
1 | 12827195 | 2016-08-24 13:30 | 2016-08-24 14:30 | 60 | 3 | 180 | 0.00054066 | 0.000513 | 9.0109e-06 | NAPA ID:22201 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022201 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3325 | NONE | To install a 400V Disconnector on TC3325. Works location: Buckland Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0002565 | 5.5 | 2017 | 2016-08-24 | B | 3 | 0.000513 | 9.0109e-06
1 | 12827553 | 2016-08-01 13:47 | 2016-08-01 14:39 | 51 | 42 | 2165.1 | 0.0065048 | 0.006126 | 0.00012619 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M0768 | CROSSARM - WHOLE ASSEMBLY | Line isolated at ABS 1187 & 1271 to replace broken crossarm at pole M0768. All supply restored following repairs. Material used - 1 x HV crossarm and assemblies | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.006126 | 11 | 2017 | 2016-08-01 | C | 42 | 0.006126 | 0.00012619
1 | 12831959 | 2016-08-01 11:55 | 2016-08-01 13:15 | 80 | 62 | 4960 | 0.014902 | 0.014343 | 0.00018627 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 793442 | INSULATOR | Aprox 2 poles past Turakina School going south, there is a broken insulator and the cable is on the cross arm. Called in by a fault man heading south on a course. Line was isolated at ABS's 434 & 709 to replace insulators on pole 793442, cross arm will replaced at a later planned shut down. | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.014343 | 11 | 2017 | 2016-08-01 | C | 62 | 0.014343 | 0.00018627
1 | 12832030 | 2016-08-01 11:27 | 2016-08-01 15:00 | 213 | 2 | 426.1333 | 0.0012803 | 0.001262 | 6.0088e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 780559 | FUSE - ELEMENT/LINK (HV) | Outage recorded on the child job. Replace 2 x 2A fuse due to line clash. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001262 | 11 | 2017 | 2016-08-01 | C | 2 | 0.001262 | 6.0088e-06
1 | 12832127 | 2016-08-01 13:20 | 2016-08-01 13:40 | 20 | 2 | 40 | 0.00012018 | 0.000102 | 6.0088e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | C14017 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Tap transformer TC2137 down 1 tap, 238V on both phases. Also replace the neutral crimp lug as it was nearly burnt off. | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000102 | 11 | 2017 | 2016-08-01 | C | 2 | 0.000102 | 6.0088e-06
1 | 12832468 | 2016-08-16 09:15 | 2016-08-16 11:45 | 150 | 260 | 39034.6667 | 0.11726 | 0.11491 | 0.00078102 | NAPA ID:21556 TP_KAITIMAKO GXP > WELCOME BAY SUB > MAUNGATAPU | 11 | Planned | 021556 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD4-700 | NONE | Replace arms and 3 poles. Works location: Hairini St, Haukori St. WO 30017841 | F3 | MAUNGATAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.057457 | 5.5 | 2017 | 2016-08-16 | B | 260 | 0.11491 | 0.00078102
1 | 12833095 | 2016-08-23 09:38 | 2016-08-23 14:10 | 271 | 7 | 1903.1833 | 0.0057166 | 0.005653 | 2.1026e-05 | NAPA ID:22271 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | 022271 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T3/350 | NONE | Replace 11kV transformer fuses & transformer T3/350. Works location: James Rd, Halcombe. WO 30018765 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.0028265 | 5.5 | 2017 | 2016-08-23 | B | 7 | 0.005653 | 2.1026e-05
1 | 12833306 | 2016-08-23 08:39 | 2016-08-23 14:56 | 377 | 24 | 9056.4 | 0.027203 | 0.026986 | 7.2089e-05 | NAPA ID:21996 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 021996 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7148 | NONE | Replace defective poles past Links 7148. Works location: Cameron Rd, Carterton. WO 30018283 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.013493 | 5.5 | 2017 | 2016-08-23 | B | 24 | 0.026986 | 7.2089e-05
1 | 12833322 | 2016-08-26 08:30 | 2016-08-26 14:26 | 356 | 24 | 8544 | 0.025663 | 0.025446 | 7.2086e-05 | NAPA ID:22004 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 022004 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7148 | NONE | replace defective poles past links 7148. Works location: Cameron Rd, Carterton. WO 30018283 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.012723 | 5.5 | 2017 | 2016-08-26 | B | 24 | 0.025446 | 7.2086e-05
1 | 12833342 | 2016-08-29 08:30 | 2016-08-29 15:40 | 430 | 24 | 10320 | 0.030996 | 0.030779 | 7.2084e-05 | NAPA ID:22006 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 022006 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7148 | NONE | replace defective poles past links 7148. Works location; Cameron Rd, Carterton. WO 30018283 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.01539 | 5.5 | 2017 | 2016-08-29 | B | 24 | 0.030779 | 7.2084e-05
1 | 12833374 | 2016-08-31 08:30 | 2016-08-31 15:17 | 407 | 24 | 9768 | 0.029337 | 0.029121 | 7.2082e-05 | NAPA ID:22010 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 022010 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7148 | NONE | replace defective poles past links 7148. Works location; Cameron Rd, Carterton. WO 30018283 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.014561 | 5.5 | 2017 | 2016-08-31 | B | 24 | 0.029121 | 7.2082e-05
1 | 12835109 | 2016-08-01 15:12 | 2016-08-01 17:00 | 107 | 2 | 215.1667 | 0.00064645 | 0.000628 | 6.0088e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 729279 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.000628 | 11 | 2017 | 2016-08-01 | C | 2 | 0.000628 | 6.0088e-06
1 | 12835152 | 2016-08-03 12:45 | 2016-08-03 14:33 | 108 | 29 | 3132 | 0.0094096 | 0.009148 | 8.7126e-05 | NAPA ID:23129 TP_TE MATAI GXP > TE PUKE SUB > KAITUNA | 11 | Planned | 023129 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 228004 | NONE | Repair pole down in wet lands and two spans of wire. | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.004574 | 5.5 | 2017 | 2016-08-03 | B | 29 | 0.009148 | 8.7126e-05
1 | 12835781 | 2016-08-01 19:22 | 2016-08-01 21:30 | 128 | 3 | 384 | 0.0011537 | 0.001126 | 9.0132e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | L1060 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace Transformer L1060 after it was hit by lightning. Materials used: 3/11/30kVA transformer, 5x 3Amp HV Fuses, 4x 6Amp HV Fuses, Misc Nuts & Bolts. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.001126 | 11 | 2017 | 2016-08-01 | C | 3 | 0.001126 | 9.0132e-06
1 | 12837740 | 2016-08-02 00:32 | 2016-08-02 02:37 | 125 | 942 | 83558.65 | 0.25104 | 0.24255 | 0.0035992 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | CB 23 | CABLE - REPAIR | CB 23 Trip, E/F. Sectionalised with fault found to be on cable between Magnefix G166B & G235B. | F3 | KEITH ST 23 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 0.24255 | 11 | 2017 | 2016-08-02 | C | 942 | 0.24255 | 0.0035992
1 | 12840984 | 2016-08-02 03:01 | 2016-08-02 11:33 | 511 | 953 | 146922.0667 | 0.44141 | 0.43282 | 0.0028632 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC4007 | CABLE - REPAIR | CB 6 tripped on A phase OC & EF. Feeder sectionalised and fault isolated between Sw/Gear IC3139 & IC3142. Backfeeds put in place from MIK1 via Sw/Gear 9455/3. DNO 160805 | F3 | STANLEY AVE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.43282 | 11 | 2017 | 2016-08-02 | C | 953 | 0.43282 | 0.0028632
1 | 12842333 | 2016-08-02 07:04 | 2016-08-02 09:00 | 116 | 253 | 11463.3333 | 0.03444 | 0.032159 | 0.00076011 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P03912 | CONDUCTOR - REPAIR/REHANG | Recloser H131 - Report lines down 142 Linton Station Road, due to bird strike Mark Craw. 0727 Further call from Mark Craw said he checked were he saw bird strike , can see no lines down. Faultman found line down at pole P03912 due to bird strike, line was isolated at ABS H139 to make repairs. 5 meters Squirrel conductor used. 11 X sleeves used | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.032159 | 11 | 2017 | 2016-08-02 | C | 253 | 0.032159 | 0.00076011
1 | 12842933 | 2016-08-02 07:14 | 2016-08-02 08:30 | 75 | 127 | 9643.5333 | 0.028973 | 0.027828 | 0.00038156 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 803671 | FUSE - ELEMENT/LINK (HV) | Reload reliven at fuses 462. 3 x 30A Fuses due to Bird Strike. | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.027828 | 11 | 2017 | 2016-08-02 | C | 127 | 0.027828 | 0.00038156
1 | 12843195 | 2016-08-02 07:22 | 2016-08-02 09:06 | 104 | 1 | 104.4 | 0.00031366 | 0.000304 | 3.0043e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | W12551 | FUSE - ELEMENT/LINK (HV) | Reload at TC5748 2 x 5 A & barrel Aged burnt out barrel | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000304 | 11 | 2017 | 2016-08-02 | C | 1 | 0.000304 | 3.0043e-06
1 | 12843433 | 2016-07-30 20:49 | 2016-07-30 21:07 | 18 | 1 | 18 | 5.408e-05 | 4.5e-05 | 3.0044e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P10029 | INSULATOR | Created as outage for OMS 12720504 | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 4.5e-05 | 11 | 2017 | 2016-07-30 | C | 1 | 4.5e-05 | 3.0044e-06
1 | 12843761 | 2016-08-02 08:36 | 2016-08-02 10:00 | 84 | 2 | 126.1 | 0.00037885 | 0.00036 | 6.0087e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 790840 | FUSE - ELEMENT/LINK (HV) | Reload at X2829. 2 x 3A. Cause: Unknown. | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.00036 | 11 | 2017 | 2016-08-02 | C | 2 | 0.00036 | 6.0087e-06
1 | 12844637 | 2016-08-02 11:18 | 2016-08-02 12:55 | 96 | 7 | 677.4833 | 0.0020354 | 0.001972 | 2.1031e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P39424 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Faultman found a damaged 11kV fuse holder on transformer T4/22, line was isolated at Fuses F18 to replace the 11kV fuse holder and repair jumper on pole P39424. 1 X 3 amp HV fuse replaced. 1 X 11kV fuse holder replaced. 300 millimeters of 25 mm conductor used. | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.001972 | 11 | 2017 | 2016-08-02 | C | 7 | 0.001972 | 2.1031e-05
1 | 12846684 | 2016-08-02 10:51 | 2016-08-02 12:20 | 89 | 2 | 178.8 | 0.00053718 | 0.000519 | 6.0087e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 781942 | FUSE - ELEMENT/LINK (HV) | Reload at X2636. Paul checked other HV Lines to Pump Sheds. 2 x 2A due to lightning. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000519 | 11 | 2017 | 2016-08-02 | C | 2 | 0.000519 | 6.0087e-06
1 | 12847442 | 2016-08-02 12:30 | 2016-08-02 13:00 | 30 | 3 | 90 | 0.00027039 | 0.000243 | 9.0131e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N/A - NOT APPLICABLE | UNKNOWN | Check for safety - pole outside gate of property is arcing. TX 419 - Pole 756865. Isolated and earthed for LV Works at transformer. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.000243 | 11 | 2017 | 2016-08-02 | C | 3 | 0.000243 | 9.0131e-06
1 | 12848727 | 2016-08-24 09:16 | 2016-08-24 13:45 | 269 | 322 | 86757.5333 | 0.26059 | 0.25769 | 0.00096718 | NAPA ID:20770 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > ASHHURST | 11 | Planned | 020770 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | F77 | NONE | Replace 4 spalling 11kV poles. Works location: Salisbury St, Ashhurst. WO 30020880 | F3 | ASHHURST | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.12884 | 5.5 | 2017 | 2016-08-24 | B | 322 | 0.25769 | 0.00096718
1 | 12848979 | 2016-08-24 08:53 | 2016-08-24 11:27 | 153 | 212 | 10769.45 | 0.032348 | 0.030437 | 0.00063678 | NAPA ID:22040 TP_BUNNYTHORPE GXP > MILSON SUB | 11 | Planned | 022040 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB4 | NONE | Milson Substation CB CT ratio and setting changes to mitigate arc flash. Works location: Milson Sub. WO 30027397 | F1 | RUAHINE | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.015218 | 5.5 | 2017 | 2016-08-24 | B | 212 | 0.030437 | 0.00063678
1 | 12849058 | 2016-08-25 09:04 | 2016-08-25 09:41 | 36 | 10 | 366 | 0.0010993 | 0.001009 | 3.0036e-05 | NAPA ID:22046 TP_BUNNYTHORPE GXP > MILSON SUB | 11 | Planned | 022046 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CB 9 | NONE | Milson Substation CB CT ratio and setting changes to mitigate arc flash. Works location: Milson Sub. WO 30027397 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.0005045 | 5.5 | 2017 | 2016-08-25 | B | 10 | 0.001009 | 3.0036e-05
1 | 12849741 | 2016-08-24 09:04 | 2016-08-24 16:19 | 434 | 9 | 3914.4 | 0.011758 | 0.011676 | 2.7033e-05 | NAPA ID:23192 TP_WAIHOU GXP | 11 | Planned | 023192 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | FUSE - ELEMENT/LINK (HV) | Ngarua Feeder Step 11, Shut 7 Specified renewal works on SH26 Specified distribution renewal works completed between poles C1826 and WHUWTO061. | F4 | THOMAS ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.005838 | 5.5 | 2017 | 2016-08-24 | B | 9 | 0.011676 | 2.7033e-05
1 | 12851128 | 2016-08-02 21:50 | 2016-08-02 22:40 | 50 | 28 | 1400 | 0.0042061 | 0.003953 | 8.4122e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K13555 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replace HV Fuse Holder and Base 1 x HV Fuse. Lines isolated between ABS 554 and 437 to carry out job. | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.003953 | 11 | 2017 | 2016-08-02 | C | 28 | 0.003953 | 8.4122e-05
1 | 12852092 | 2016-08-03 08:09 | 2016-08-03 08:35 | 25 | 59 | 1504.5 | 0.00452 | 0.003988 | 0.00017726 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 710183 | JUMPER | Section of line from ABS 5555 isolated to repair jumper on load side of ABS | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.003988 | 11 | 2017 | 2016-08-03 | C | 59 | 0.003988 | 0.00017726
1 | 12852147 | 2016-08-02 13:47 | 2016-08-02 18:34 | 286 | 62 | 17764.0333 | 0.05337 | 0.05281 | 0.00018627 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | t3220 | FUSE - ELEMENT/LINK (HV) | Line isolated at ABS 6661, TA709 & temp line break at transformer T3330 and broken HV fuse base and 6 amp HV fuse replaced at transformer T3220. | F4 | OAONUI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.05281 | 11 | 2017 | 2016-08-02 | C | 62 | 0.05281 | 0.00018627
1 | 12853266 | 2016-08-03 09:29 | 2016-08-03 10:21 | 51 | 57 | 2960.2 | 0.0088935 | 0.008379 | 0.00017125 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | F13015 | INSULATOR | Contact control for emergency switching. section of line between ABS IC2611 and ABS IC813 isolated to repair eye bolt @ pole F13015 balance of line backfed via ABS 720 for duration of repairs | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.008379 | 11 | 2017 | 2016-08-03 | C | 57 | 0.008379 | 0.00017125
1 | 12855463 | 2016-08-03 09:28 | 2016-08-03 14:08 | 280 | 32 | 8965.8667 | 0.026937 | 0.026648 | 9.6139e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 715561 | CONDUCTOR - REPAIR/REHANG | Repair 2 spans of conductor @ pole 715561. Used 2m conductor 2x sleeves and one HV fuse element. | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.026648 | 11 | 2017 | 2016-08-03 | C | 32 | 0.026648 | 9.6139e-05
1 | 12855778 | 2016-08-18 09:06 | 2016-08-18 13:48 | 282 | 73 | 19611 | 0.058909 | 0.058251 | 0.00021928 | NAPA ID:22654 TP_TAURANGA 33 GXP | 11 | Planned | 022654 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SD3-003 | NONE | REMOVE FROM THE NETWORK, ABS SD3-003 (DNO #160701). REPLACE ARMS ONLY, AS PER POWERCO REQUEST PETER APPERLEY. REPLACE ABS SD3-002 AND POLE DFT #101-56595. INSTALL 2 X LL GAPS AT POLES 391821 & 210526. Works location: Snodgrass Rd. WO 30029353 | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.029125 | 5.5 | 2017 | 2016-08-18 | B | 73 | 0.058251 | 0.00021928
1 | 12856682 | 2016-08-03 13:01 | 2016-08-03 14:08 | 66 | 680 | 22239.9333 | 0.066816 | 0.060687 | 0.0026378 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB C10183/2 | UNKNOWN | Recloser 10183/2 tripped on C phase. Area patrolled / sectionalised but nothing found. Ongoing fault, proving difficult to locate. Feeder split into 3 sections to reduce faulted area. | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.060687 | 11 | 2017 | 2016-08-03 | C | 680 | 0.060687 | 0.0026378
1 | 12859087 | 2016-08-28 01:01 | 2016-08-29 01:01 | 1439 | 206 | 0 | 0 | 0 | 0 | NAPA ID:20710 TP_KINLEITH GXP | 11 | Planned | 020710 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Service Baird Road Sub ABS's 27, 24, 48 and T1 Transformer and CB22. Kinleith Ripple Sub PC5 Only. Plus test SEL Protection Relays on CB22 and CB17 by Mark Tucker Tech. | F4 | LICHFIELD | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0 | 5.5 | 2017 | 2016-08-28 | B | 206 | 0 | 0
1 | 12859426 | 2016-07-28 22:05 | 2016-07-29 01:29 | 204 | 3 | 612.45 | 0.0018401 | 0.001813 | 9.0136e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 772828 | FUSE - ELEMENT/LINK (HV) | 3x 2a HV fuses @ X345 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.001813 | 11 | 2017 | 2016-07-28 | C | 3 | 0.001813 | 9.0136e-06
1 | 12859704 | 2016-08-26 12:00 | 2016-08-26 12:40 | 40 | 2 | 80 | 0.00024029 | 0.000222 | 6.0071e-06 | NAPA ID:22206 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022206 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC6528 | NONE | To install a 400V Fuse Disconnector on TC6528. Works location: Buckland Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000111 | 5.5 | 2017 | 2016-08-26 | B | 2 | 0.000222 | 6.0071e-06
1 | 12860037 | 2016-08-03 15:35 | 2016-08-03 16:35 | 60 | 2 | 120.5 | 0.00036202 | 0.000343 | 6.0086e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P49044 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2a fuse | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.000343 | 11 | 2017 | 2016-08-03 | C | 2 | 0.000343 | 6.0086e-06
1 | 12860531 | 2016-08-03 18:04 | 2016-08-04 15:50 | 1305 | 573 | 45376.1167 | 0.13633 | 0.13116 | 0.0021121 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | TC3299 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | POA CB9 tripped E/F, L/O. Recloser RC33 Opened & back feed via Sectionaliser 9953. Feeder sectionalised 2nd backfeed via ABS IC373 up to ABS 552 Transformers TC3299 & TC3575 Blown by Lightning. Transformers replaced | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.13116 | 11 | 2017 | 2016-08-03 | C | 573 | 0.13116 | 0.0021121
1 | 12863972 | 2016-08-04 06:30 | 2016-08-04 08:28 | 118 | 499 | 14541.7667 | 0.043688 | 0.03919 | 0.0012438 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P32290 | INSULATOR | Initial Auto-reclose on Recloser D79 (Milson CB9 feeder) followed by tripping on Sectionaliser CB 10249 (C phase, EF, OC). NOTE: There has been an ongoing fault proving difficult to locate beyond Recloser 10183/2 (Kairanga CB22 feeder). This area has been split into 3 sections to reduce faulted area with the Sectionaliser 10249 backfeeding up to ABS C20 and O58. A Patrol was carried out and a blown insulator found on Fairfield Rd. (Isolation beyond ABS O59). 1 Insulator and binder replaced with power restored and feede returned to normal configuration. (Crossarm also burnt, defected by DOWNER). | F4 | KOPANE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.03919 | 11 | 2017 | 2016-08-04 | C | 499 | 0.03919 | 0.0012438
1 | 12864328 | 2016-08-04 06:41 | 2016-08-04 11:50 | 309 | 56 | 17324.5333 | 0.052048 | 0.051543 | 0.00016824 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | X2316 | FUSE - HOLDER/BASE (LV) | Waiting on Control to advise when power is off to HV fuses and will update ETR and send to retailers James advised leaving site now. HV Fuses open at 10:55 to carryout LV work. 3 * 400V Isolators replaced and 3 8 400V Fuses. | F3 | ST JOHNS | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.051543 | 11 | 2017 | 2016-08-04 | C | 56 | 0.051543 | 0.00016824
1 | 12864477 | 2016-08-04 06:56 | 2016-08-04 08:15 | 79 | 20 | 1584 | 0.0047588 | 0.004578 | 6.0086e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 795596 | FUSE - ELEMENT/LINK (HV) | 2 x 15amp unknown | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.004578 | 11 | 2017 | 2016-08-04 | C | 20 | 0.004578 | 6.0086e-05
1 | 12864486 | 2016-08-04 07:19 | 2016-08-04 08:33 | 73 | 1 | 73.9833 | 0.00022227 | 0.000213 | 3.0043e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TC2487 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | TX has been isolated for change. Crew are currently on site with TX isolated | F4/F5 | MOUNTAIN | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000213 | 11 | 2017 | 2016-08-04 | C | 1 | 0.000213 | 3.0043e-06
1 | 12866170 | 2016-08-23 09:07 | 2016-08-23 15:24 | 376 | 15 | 5651.75 | 0.016976 | 0.01684 | 4.5055e-05 | NAPA ID:21753 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 021753 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-059 | NONE | Shutdown number 2. Continuation of the Pole and Hardware replacement on Kumikumi Road. Works location: KUmikumi Rd. WO 30017842 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.00842 | 5.5 | 2017 | 2016-08-23 | B | 15 | 0.01684 | 4.5055e-05
1 | 12868367 | 2016-08-04 13:58 | 2016-08-04 16:22 | 144 | 1 | 144.55 | 0.00043427 | 0.000425 | 3.0043e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P15640 | POLE | check for safety - stay pole hit by vehicle and has cracked up the middle. Opposite pole P15640 Advised control and SMC of 999. Pole safe but will need to be replaced. | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.000425 | 11 | 2017 | 2016-08-04 | C | 1 | 0.000425 | 3.0043e-06
1 | 12868511 | 2016-08-04 14:29 | 2016-08-04 21:22 | 413 | 44 | 14844.7333 | 0.044598 | 0.044201 | 0.00013219 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | P08275 | CONDUCTOR - REPAIR/REHANG | Please check 12868620 - 13559 Route 52. & OMS 12868843 13920 Route 52 No power & OMS 12869033 13573 ROUTE 52 No power Faultman found a branch on the line at pole P08275, branch was removed with hot line sticks. | F4 | BROOKLANDS | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.044201 | 11 | 2017 | 2016-08-04 | C | 44 | 0.044201 | 0.00013219
1 | 12869232 | 2016-08-04 17:58 | 2016-08-04 18:50 | 52 | 5 | 70.2167 | 0.00021095 | 0.000165 | 1.5022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N13028 | FUSE - ELEMENT/LINK (HV) | Transformer T2917 2x 3A HV O/H fuses blown. Old age | F4 | PURIRI | KOPU | Valley | MATATOKI SUB | Eastern Electricity | POWERCO | 0.000165 | 11 | 2017 | 2016-08-04 | C | 5 | 0.000165 | 1.5022e-05
1 | 12869447 | 2016-08-04 19:09 | 2016-08-04 20:40 | 90 | 4 | 363.9333 | 0.0010934 | 0.001057 | 1.2017e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 204048 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A H/V, O/H fuses at Fuses SB2 020 ( bird strike ). | F4 | LINDERMANN RD | TAURANGA 31 | Tauranga | KAURI POINT | Eastern Electricity | POWERCO | 0.001057 | 11 | 2017 | 2016-08-04 | C | 4 | 0.001057 | 1.2017e-05
1 | 12869716 | 2016-08-04 20:46 | 2016-08-04 21:00 | 13 | 4 | 54.5333 | 0.00016384 | 0.000127 | 1.2017e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | G250/A | FAULT INDICATOR | Faultman to investigate noisy and reset stuck fault indicators on Sw/Gear G250/A, feeder was isolated At Magnefix G193/B & G250/A. | F3 | KEITH ST 23 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 0.000127 | 11 | 2017 | 2016-08-04 | C | 4 | 0.000127 | 1.2017e-05
1 | 12871346 | 2016-08-05 15:59 | 2016-08-05 16:57 | 58 | 17 | 986 | 0.0029622 | 0.002809 | 5.1073e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P06286 | JUMPER | Blown Jumper found at Transformer T9/9. Isolated at fuses V17 - Jumper repaired. No materials used. | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.002809 | 11 | 2017 | 2016-08-05 | C | 17 | 0.002809 | 5.1073e-05
1 | 12872481 | 2016-08-05 12:24 | 2016-08-05 13:41 | 76 | 109 | 7327.0333 | 0.022012 | 0.02103 | 0.00032747 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 798605 | NONE | R/S C634/2 Tripped A,B Ph O/C L/O During sectionlising dead swans found at Pole 798318 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.02103 | 11 | 2017 | 2016-08-05 | C | 109 | 0.02103 | 0.00032747
1 | 12873011 | 2016-08-05 14:15 | 2016-08-05 14:36 | 21 | 19 | 399 | 0.0011987 | 0.001027 | 5.7081e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718790 | BINDER | 1R Floating HV conductor pole no 718790 , suggest replace HV insulator. Advised control and SMC. Replaced 1 binder on pole 718790 | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.001027 | 11 | 2017 | 2016-08-05 | C | 19 | 0.001027 | 5.7081e-05
1 | 12873434 | 2016-08-29 13:30 | 2016-08-29 14:00 | 30 | 7 | 210 | 0.00063073 | 0.000567 | 2.1024e-05 | NAPA ID:22209 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022209 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1536 | NONE | To install a 400V Disconnector on TC1536. Works location: Buckland Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0002835 | 5.5 | 2017 | 2016-08-29 | B | 7 | 0.000567 | 2.1024e-05
1 | 12873450 | 2016-08-15 08:30 | 2016-08-15 13:31 | 301 | 3 | 903 | 0.0027126 | 0.002685 | 9.0119e-06 | NAPA ID:23277 TP_WAIKINO GXP > WHANGAMATA SUB > OPOUTERE | 11 | Planned | 023277 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | R13101 | NONE | To install risers to raise height of 11kV lines. Works location: Opoutere. WO 30024974 | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.0013425 | 5.5 | 2017 | 2016-08-15 | B | 3 | 0.002685 | 9.0119e-06
1 | 12873479 | 2016-08-29 10:00 | 2016-08-29 11:00 | 60 | 2 | 120 | 0.00036042 | 0.000342 | 6.0069e-06 | NAPA ID:23219 TP_HUIRANGI GXP > INGLEWOOD SUB > MOUNTAIN RD | 6.6 | Planned | 023219 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV | NONE | to replace 11kv fuses 2435 on trany 2435t ,are going to do them live line but require the fuses to be opened first. Works location: Norfolk Rd, Inglewood. WO 30025365 | F4 | MOUNTAIN RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000171 | 3.3 | 2017 | 2016-08-29 | B | 2 | 0.000342 | 6.0069e-06
1 | 12873788 | 2016-08-05 13:58 | 2016-08-05 15:30 | 92 | 1 | 92.1667 | 0.00027689 | 0.000267 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 849434 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses 2972. 2 x 6A due to Bird strike. | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000267 | 11 | 2017 | 2016-08-05 | C | 1 | 0.000267 | 3.0042e-06
1 | 12874201 | 2016-08-05 16:11 | 2016-08-05 17:33 | 82 | 11 | 905.1833 | 0.0027194 | 0.00262 | 3.3047e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | TD4-264 | SERVICE BOX - GYRO/PILLAR/POD (LV) | check 334 Ohauiti road, also has no power. 2 R issued as investigation is needed in to smoke coming from tranformer cubicle or Gyro box. Isolation of Transformers TD4-111 & TD4-264 to investigate. Fault found to be in LV gyro. Replaced 3 phase 160 amp jean muller fuse unit C/W 100amp fuses. Also a gyro EP2000 Box. | F3/F4 | OHAUITI RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.00262 | 11 | 2017 | 2016-08-05 | C | 11 | 0.00262 | 3.3047e-05
1 | 12875939 | 2016-08-05 19:27 | 2016-08-05 23:47 | 260 | 220 | 25669.75 | 0.077119 | 0.075136 | 0.0016824 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 730399 | CONDUCTOR - REPAIR/REHANG | Tripping on Kaponga CB T31 on EF, OC Phase A. Feeder Sectionalised / Patrolled with a conductor found down. Rejointed OK and relivened. (5 M conductor, 2 sleeves). | F4 | RIVERLEA | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.075136 | 11 | 2017 | 2016-08-05 | C | 220 | 0.075136 | 0.0016824
1 | 12876385 | 2016-08-05 20:12 | 2016-08-07 16:02 | 2630 | 8 | 21030.5333 | 0.063182 | 0.063109 | 2.4034e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737942 | CONDUCTOR - REPAIR/REHANG | CB 6561 Trip O/C. Have advised SMC and Control on 998 Pembroke Road - Mountain House has no power - powerlines sparking due to snowfall on tree branch which is weighing it onto the power lines. Patrol found heavy snow on tree branches causing lots of problems. Impractical to repair during night. Will proceed in morning. Line Patrolled lines down in 7 locations unsafe to repair as snow still falling and road not safe. To be repaired at later date. Lines repaired & branches cleared from lines at multiple points. Leaning pole righted. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.063109 | 6.6 | 2017 | 2016-08-05 | C | 8 | 0.063109 | 2.4034e-05
1 | 12876477 | 2016-08-05 20:21 | 2016-08-06 11:35 | 914 | 8 | 7315.3333 | 0.021977 | 0.021905 | 2.4034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | L1035 | FUSE - ELEMENT/LINK (HV) | Fire comms - F2127298. 2 HT Fuses found tripped at Transformer L1035. Reloaded / Relivened unsuccessful. Transformer requires replacement.. Impractical to complete during night. Will proceed in morning. Transformer replaced - Used 1 x 50 kVA 3 phase transformer 1 x transformer backing plate, 2 x 5 amp fuses. | F4 | KAKARAMEA | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.021905 | 11 | 2017 | 2016-08-05 | C | 8 | 0.021905 | 2.4034e-05
1 | 12877333 | 2016-08-05 22:38 | 2016-08-13 17:28 | 11209 | 59 | 295487.7667 | 0.88773 | 0.8872 | 0.00030944 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 442143 | UNKNOWN | Tripping on recloser CB 4230 on OC, EF Phase A. Feeder sectionalised with spur line beyong fuses 2835 left off for the night. Heavy snow, becoming dangerous to drive. However, Recloser tripped 23 minutes later. - faultman advised. Will investigate first light. Job checked Sun morning but still no access. Will have to be attended as soon as the snow clears. Have entered site inspection for 1957 MANGOHANE ROAD, TAIHAPE | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.8872 | 11 | 2017 | 2016-08-05 | C | 59 | 0.8872 | 0.00030944
1 | 12877738 | 2016-08-06 01:45 | 2016-08-17 12:18 | 16473 | 163 | 138275.15 | 0.41541 | 0.41394 | 0.00057982 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | N/A - NOT APPLICABLE | UNKNOWN | Multiple lines down found starting Pole 389049 Faultman unable to get to lines due to Snow feeder Isolated at ABS 2733 Fault attended again on Sunday morning but access still not possible due to snow. Will need to wait until snow clears. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.41394 | 11 | 2017 | 2016-08-06 | C | 163 | 0.41394 | 0.00057982
1 | 12878111 | 2016-08-06 06:22 | 2016-08-06 09:52 | 209 | 1 | 209.6667 | 0.00062989 | 0.00062 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | N1030 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer N1030 - Cause Wind. Used 2 x 3 amp HV fuse and 1 x 80 amp LV fuse. | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.00062 | 11 | 2017 | 2016-08-06 | C | 1 | 0.00062 | 3.0042e-06
1 | 12878486 | 2016-08-06 06:59 | 2016-08-06 12:36 | 336 | 115 | 17347.3333 | 0.052116 | 0.051079 | 0.00034549 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 839405 | UNKNOWN | sec 218 found open found Branck on lines removed by hotstick at pole 839405 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.051079 | 11 | 2017 | 2016-08-06 | C | 115 | 0.051079 | 0.00034549
1 | 12879856 | 2016-08-06 08:41 | 2016-08-06 14:29 | 347 | 1 | 347.7333 | 0.0010447 | 0.001035 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 840128 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at fuses 6635 - Cause weather. Used 2 x 8. Also fuses to cow shed (not labelled) Pole 840128 blown. Used 2 x 6. | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.001035 | 11 | 2017 | 2016-08-06 | C | 1 | 0.001035 | 3.0042e-06
1 | 12880111 | 2016-08-06 09:05 | 2016-08-06 16:40 | 455 | 161 | 73174.5 | 0.21983 | 0.21838 | 0.00048368 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762073 | CONDUCTOR - REPAIR/REHANG | at 09:05, Motukawa Sub, CB H41 Tarata Feeder Tripped, A B C O/C, L/O. Faultmen dispatched & investigation began. Feeder sectionalised. Found tree through lines at Pole 762073. Isolated Lines at Links H42 & ABS H43. Permit issued & repairs carried out. All Power Restored on completion. 1m of Conductor replaced, all 3 phases. 6x Sleeves used. Job is an NDR - number to come. | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.21838 | 6.6 | 2017 | 2016-08-06 | C | 161 | 0.21838 | 0.00048368
1 | 12880631 | 2016-08-06 12:41 | 2016-08-06 13:59 | 78 | 5 | 390 | 0.0011717 | 0.001126 | 1.5021e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717066 | CONDUCTOR - REPAIR/REHANG | Lines are hanging low and had been disconnected from the pole - pole is in the paddock - advised Glo 2R request as HV strain insulator broken and HV line down. Require bucket and another person to assist. (to be decided at invoicing level if meets criteria of 2R work after scope of work). Isolated at Fuses TA806 - Strains repaired and lines lifted. Used 2 x pol strainers, 2x Dead Ends, 2 x 3 amp fuses 6x sleeves. | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001126 | 11 | 2017 | 2016-08-06 | C | 5 | 0.001126 | 1.5021e-05
1 | 12880666 | 2016-08-06 09:30 | 2016-08-06 17:59 | 508 | 1 | 508.4333 | 0.0015275 | 0.001518 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | NNF | UNKNOWN | Full power on arrival, part of feeder fault earlier today | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.001518 | 11 | 2017 | 2016-08-06 | C | 1 | 0.001518 | 3.0042e-06
1 | 12880740 | 2016-08-06 09:52 | 2016-08-06 13:26 | 213 | 1 | 213.8167 | 0.00064236 | 0.000633 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T33 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at fuses T33 - cause unknown. Used 2 x 6 amp fuses. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000633 | 11 | 2017 | 2016-08-06 | C | 1 | 0.000633 | 3.0042e-06
1 | 12880769 | 2016-08-06 10:01 | 2016-08-06 14:08 | 247 | 163 | 17136.1 | 0.051481 | 0.050012 | 0.00043261 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 784167 | CONDUCTOR - REPAIR/REHANG | CB7 Trip O/C E/. Lines down found while sectionalising. Isolated at ABS 1026 line break made at pole 784165 to isolate unused spur line. No materials used. | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.050012 | 11 | 2017 | 2016-08-06 | C | 163 | 0.050012 | 0.00043261
1 | 12881808 | 2016-08-06 11:02 | 2016-08-06 15:55 | 292 | 147 | 15219.35 | 0.045723 | 0.044397 | 0.00088325 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 786537 | CROSSARM - ARM ONLY | at 11:03, Taihape Sub, CB 8 Moawhango Feeder, Tripped, B Ph O/C, E/F, L/O. Faulman dispatched & investigation began. Found broken crossarm at Pole 786537. Isolated Lines at Fuses 2618. Permit issued & a temp repair was carried out on the affected crossarm. All Power restored on completion. Neville Ashton Attended. No Materials Used. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.044397 | 11 | 2017 | 2016-08-06 | C | 147 | 0.044397 | 0.00088325
1 | 12883242 | 2016-08-06 13:19 | 2016-08-06 15:53 | 154 | 39 | 6006 | 0.018044 | 0.017692 | 0.00011717 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 752380 | CONDUCTOR - REPAIR/REHANG | at 13:19, Mangorei Sub, CB 5 Junction Rd Feeder. Faultman attended Lines down job. Found Lines down at Pole 752380. 2x DDO's had blown at Fuses 8235. Isolated Lines at Fuses 8235. Permit issued & repairs carried out. All Power Restored on Completion. 1x Jumper Replaced, 2x Sleeves, 1x Binder. Check to see if OMS 12883296 (432 Korito rd is related) | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.017692 | 11 | 2017 | 2016-08-06 | C | 39 | 0.017692 | 0.00011717
1 | 12883482 | 2016-08-06 12:48 | 2016-08-07 13:58 | 1509 | 2 | 3019.8 | 0.0090722 | 0.009054 | 6.0084e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | PU363 | FUSE - ELEMENT/LINK (HV) | Fuse PU363 Open and Tagged Lines clashing unsafe to work up lines. Faultman to return when wind decreases Replaced 3x #amp HV Fuses | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.009054 | 11 | 2017 | 2016-08-06 | C | 2 | 0.009054 | 6.0084e-06
1 | 12883499 | 2016-08-06 12:51 | 2016-08-06 15:45 | 173 | 1 | 173.6167 | 0.00052159 | 0.000512 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 858 | FUSE - ELEMENT/LINK (HV) | Fuses 858 found blown - cause wind. Used 2 x 8 amp fuses. | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000512 | 11 | 2017 | 2016-08-06 | C | 1 | 0.000512 | 3.0042e-06
1 | 12883652 | 2016-08-06 13:13 | 2016-08-06 19:08 | 354 | 132 | 37478.5833 | 0.11259 | 0.11141 | 0.00039656 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 377045 | CONDUCTOR - REPAIR/REHANG | Initial tripping on CB4 on E/F. Patrol found large span of conductor down. (Possibly 1000m). Isolation made from ABS V81 and V76 with temp Line breaks installed (Poles 377045, 377219, 377182). All power restored via ABS V81 and V76. To be repaired during daylight hours after storm has passed. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.11141 | 11 | 2017 | 2016-08-06 | C | 132 | 0.11141 | 0.00039656
1 | 12883881 | 2016-08-06 13:24 | 2016-08-06 18:03 | 278 | 1 | 278.8 | 0.00083758 | 0.000828 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | Recloser 575 | UNKNOWN | Part of feeder fault which is ongoing but the part of the network affecting this customer has been relivened - OMS 12885874 | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.000828 | 11 | 2017 | 2016-08-06 | C | 1 | 0.000828 | 3.0042e-06
1 | 12884100 | 2016-08-06 14:38 | 2016-08-06 16:40 | 122 | 66 | 3102 | 0.0093192 | 0.008724 | 0.00019828 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758174 | CONDUCTOR - REPAIR/REHANG | Lines down found at pole 758174. Isolated at ABS 169 as quick isolation point (lines still live) faultman at ABS when called. Isolation installed at Fuses 8459 for repairs, ABS 169 closed. Used 3 mtrs of conductor and 4 sleeves. | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.008724 | 11 | 2017 | 2016-08-06 | C | 66 | 0.008724 | 0.00019828
1 | 12885184 | 2016-08-06 15:52 | 2016-08-06 18:06 | 134 | 18 | 2412 | 0.0072462 | 0.007084 | 5.4076e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 842129 | CONDUCTOR - REPAIR/REHANG | FM advised he has signed this off with control but was left onsite. LV lines down at pole 842129 Isolated at fuses 1336 | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.007084 | 11 | 2017 | 2016-08-06 | C | 18 | 0.007084 | 5.4076e-05
1 | 12885487 | 2016-08-06 14:43 | 2016-08-06 16:24 | 100 | 1 | 100.7 | 0.00030253 | 0.000293 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2849 | FUSE - ELEMENT/LINK (HV) | Fire service called in lines down fire called for ETA - 5-10mins Fuses found blown at fuses 2849 - cause wind Used 2 x 3amp fuses and 1 x carrier | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.000293 | 11 | 2017 | 2016-08-06 | C | 1 | 0.000293 | 3.0042e-06
1 | 12885874 | 2016-08-06 14:59 | 2016-08-06 21:28 | 389 | 872 | 18144.6 | 0.054511 | 0.046651 | 0.0004957 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 78944 | CONDUCTOR - REPAIR/REHANG | Initial tripping on recloser CB575 on C Phase, EF. Line patrolled with 3 lines down beyond fuses 2650. (Caused by tree falling, wet ground / high wind). Condcutors repaired, relivened OK. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.046651 | 11 | 2017 | 2016-08-06 | C | 872 | 0.046651 | 0.0004957
1 | 12888235 | 2016-08-06 16:18 | 2016-08-06 18:35 | 136 | 7 | 958.65 | 0.00288 | 0.002816 | 2.103e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 8178 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses 8178 - cause wind. Used 2 x 10 amp fuses. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.002816 | 11 | 2017 | 2016-08-06 | C | 7 | 0.002816 | 2.103e-05
1 | 12888328 | 2016-08-06 16:39 | 2016-08-06 21:19 | 279 | 1 | 279.3833 | 0.00083934 | 0.00083 | 3.0042e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 33 DERBY ROAD SOUTH | UNKNOWN | NNF - part of feeder fault earlier on today | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.00083 | 6.6 | 2017 | 2016-08-06 | C | 1 | 0.00083 | 3.0042e-06
1 | 12888727 | 2016-08-06 17:24 | 2016-08-06 19:20 | 116 | 826 | 55498.85 | 0.16673 | 0.15929 | 0.0024815 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | S5249 | SWITCH (HV) | CB4 Trip C Ph Fault, INVT O/C, E/F. Feeder sectionalised & restored. Fault found to be bus coupler unit feeding Sw/Gear S5249. This has damaged the SD 3 switch unit S5247 which is starting to weap oil and will need to be replaced as well. Isolation at Sw/Gears S5253, IP376 S5450, S4542. DNO 160809 raised to carryout repairs. | F3 | GRENADA ST | MT MAUNGANUI 31 | Tauranga | TE MAUNGA SUB | Eastern Electricity | POWERCO | 0.15929 | 11 | 2017 | 2016-08-06 | C | 826 | 0.15929 | 0.0024815
1 | 12891146 | 2016-08-06 18:54 | 2016-08-06 22:31 | 217 | 121 | 19110.9 | 0.057414 | 0.056323 | 0.00036351 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | E0959 | CONDUCTOR - REPAIR/REHANG | Line down at Pole E0959. Isolation at ABS 1145 no back feeds available. 7 meters 16mm Copper conductor 3x sleeves | F4 | RANGITANUKU RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.056323 | 11 | 2017 | 2016-08-06 | C | 121 | 0.056323 | 0.00036351
1 | 12891412 | 2016-08-06 19:19 | 2016-08-06 20:25 | 65 | 176 | 3313.9167 | 0.0099558 | 0.008369 | 0.00046566 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Patrol found 1 HT fuses tripped at 8729. (Broken binder found with conductor on crossarm. Isolation required between Fuses 8729 and ABS 376 with backfeed at 351). Repaired / relivened OK with 1 binder used. Customer jobs came through under OMS 12888601 also but have now been included within this outage. | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.008369 | 11 | 2017 | 2016-08-06 | C | 176 | 0.008369 | 0.00046566
1 | 12891839 | 2016-08-06 18:21 | 2016-08-06 21:36 | 195 | 46 | 8993.7667 | 0.02702 | 0.026604 | 0.0001382 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13373 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | HV Fuse holder at FC2159 burnt up. Isolations at ABS IC278, ABS 9604/1, Links 9604/4. Back feed from WGM 1 Via sectionaliser 9712/2. Fuse holder replaced. Hayden Taunoa & Wayne seath on site. 1x 11kV Drop Out fuse assembly used. | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.026604 | 11 | 2017 | 2016-08-06 | C | 46 | 0.026604 | 0.0001382
1 | 12892342 | 2016-08-06 20:27 | 2016-08-06 20:52 | 25 | 71 | 1775 | 0.0053325 | 0.004692 | 0.0002133 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5182 | FUSE - ELEMENT/LINK (HV) | Initial reports of part power beyond Recloser 12131/2. CB closed but burnt up link found at 5182. ABS 6872 open (Safety) with the link replaced using a 40A fuse (Temp fix). Relivened OK. Referral job put in to replace Temp fuse with Link. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.004692 | 11 | 2017 | 2016-08-06 | C | 71 | 0.004692 | 0.0002133
1 | 12892572 | 2016-08-06 20:45 | 2016-08-06 22:25 | 100 | 1 | 100.2 | 0.00030103 | 0.000292 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 2626 | FUSE - ELEMENT/LINK (HV) | 2 HT Fuses replaced at 6A. | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000292 | 11 | 2017 | 2016-08-06 | C | 1 | 0.000292 | 3.0042e-06
1 | 12892748 | 2016-08-06 20:49 | 2016-08-07 14:40 | 1070 | 144 | 43734.4 | 0.13139 | 0.13009 | 0.00043261 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 847613 | CONDUCTOR - REPAIR/REHANG | Tripping on recloser CB2032 on O/C Phase A, EF. Feeder sectionalised / patrolled with broken conductors found near links 728. (Isolation at fuses 828). Damage appeared extensive, unable to carryout repairs at night, will continue daylight hours. Repaired lines down caused by fallen tree from outside notice zone. Materials used: 20mtrs squirrel conductor, 4 sleeves, 1x conductor joint, 1x 20Amp HV Fuse | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.13009 | 11 | 2017 | 2016-08-06 | C | 144 | 0.13009 | 0.00043261
1 | 12893263 | 2016-08-06 22:31 | 2016-08-07 10:26 | 714 | 156 | 34044 | 0.10228 | 0.10087 | 0.00046866 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 701827 | CONDUCTOR - REPAIR/REHANG | Line down. Left off overnight due to extreme winds & dark. Faultmen returned next day to repair. Traffic Management required. Used 2metres of ngamu conductor & 2 conductor joints | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.10087 | 11 | 2017 | 2016-08-06 | C | 156 | 0.10087 | 0.00046866
1 | 12893627 | 2016-08-06 21:26 | 2016-08-07 03:06 | 339 | 747 | 109893.6833 | 0.33015 | 0.32342 | 0.0040467 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 220096 | CONDUCTOR - REPAIR/REHANG | Recloser RP09 Trip C O/C E/F. CB 2182 Trip Kaitimako GXP. Multiple faults on this feeder. 11kV Line down at pole 220096, Sectionaliser 9462 Faulty Pole 380527. 33kV lines down at Pole312477. Isolations for 11kV line down ABS 9876/1 & IP598. Back feed from ATU CB 6 via Sectionaliser 9954/2. Isolation for 33kV line required the back feed of Aturoa Sub Station to achieve isolation of 33kV. No visible break at 3227. Isolation for faulty sectionaliser 9462/2 ABS SD4-066 on PMA CB 8 & Sw/Gear SD4-773 ABS SD4-075 for WBY CB 3. While this shut down was occuring Recloser RP09 batteries went flat, no comms couldn't close. F/M tied up sorting out downed lines so a delay in restoring power. | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.32342 | 11 | 2017 | 2016-08-06 | C | 747 | 0.32342 | 0.0040467
1 | 12895343 | 2016-08-06 19:53 | 2016-08-06 23:34 | 220 | 6 | 1323.3 | 0.0039755 | 0.003921 | 1.8025e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - SNOW/ICE | 233 | FUSE - ELEMENT/LINK (HV) | 2 HT fuses found tripped at Fuse/Sw 233. Isolation carried out at ABS 2541 due to Oil immersed Sw/Gear. 3 Fuses replaced and relivened OK. Patrol found no cause. (Heavy snow in area). | F3/F4 | RUAPEHU | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.003921 | 11 | 2017 | 2016-08-06 | C | 6 | 0.003921 | 1.8025e-05
1 | 12895743 | 2016-08-06 23:17 | 2016-08-07 07:30 | 492 | 161 | 20125.6833 | 0.060463 | 0.059011 | 0.00027639 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 267719 | POLE | Sectionaliser 9781/2 Trip A,B,C O/C. Car VS Pole Isolation at Fuses SG5-00. NDR 52306 1x 11m concrete pole 1x double arm, 6x11kV insulators. | F4 | TE MATAI RD | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.059011 | 11 | 2017 | 2016-08-06 | C | 161 | 0.059011 | 0.00027639
1 | 12896817 | 2016-08-07 04:20 | 2016-08-07 05:37 | 77 | 29 | 2257.65 | 0.0067825 | 0.006521 | 8.7122e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | O14229 | FUSE - ELEMENT/LINK (HV) | 2x20amp HV fuses blown at FP1438. Line Patrolled & reloaded & Livened. Possible lightning | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.006521 | 11 | 2017 | 2016-08-07 | C | 29 | 0.006521 | 8.7122e-05
1 | 12896898 | 2016-08-07 05:29 | 2016-08-07 06:48 | 78 | 11 | 866.6167 | 0.0026035 | 0.002504 | 3.3046e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 957 | FUSE - ELEMENT/LINK (HV) | 2 HT fuses tripped at 957. Suspect bird strike. Reloaded / relivened O)K Replaced 2 * 6A Fuses | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.002504 | 11 | 2017 | 2016-08-07 | C | 11 | 0.002504 | 3.3046e-05
1 | 12897224 | 2016-08-07 07:04 | 2016-08-07 09:52 | 168 | 342 | 22482.55 | 0.067543 | 0.06446 | 0.0010274 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | n/a | UNKNOWN | at 07:17, Papamoa Sub, CB 8 Reid Rd Feeder. Report came in of lines down. Duty NC checked GIS for HV or LV conformation. Recloser RP09 was Opened to de-energise lines. Faultman was dispatched & confirmed there were lines down. There was confusion around this job, as it was initially thought that this was an 11kV Line Down, however on further inspection, faultman confirmed it was in fact the 33kV Line down (part of the 11kV Lines for this feeder are built on an old 50kV Line). There was already a follow up job in OMS to repair the 33kV Lines down which had been isolated the night before. Power all restored after confirmation of no fault on 33kV Lines. For repairs to 33kV Lines see OMS 12896958. NDR for this is 56001 | F4 | REID RD | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.06446 | 11 | 2017 | 2016-08-07 | C | 342 | 0.06446 | 0.0010274
1 | 12898443 | 2016-08-07 08:05 | 2016-08-07 10:40 | 155 | 10 | 1551 | 0.0046595 | 0.004569 | 3.0042e-05 |  | 22 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 136 COOKS ROAD | FUSE - ELEMENT/LINK (HV) | 2x 10Amp HV Fuses | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.004569 | 22 | 2017 | 2016-08-07 | C | 10 | 0.004569 | 3.0042e-05
1 | 12898582 | 2016-08-07 08:44 | 2016-08-07 11:30 | 166 | 8 | 1328 | 0.0039896 | 0.003917 | 2.4034e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 601 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced 30kvA /11kV / 3 Phase transformer. Fitted 3x LV fuseholders & 3x 100Amp LV Links | F4 | LEPPERTON | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.003917 | 11 | 2017 | 2016-08-07 | C | 8 | 0.003917 | 2.4034e-05
1 | 12898798 | 2016-08-07 07:06 | 2016-08-07 08:58 | 112 | 1 | 112.0167 | 0.00033652 | 0.000327 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | See OMS 12897233 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000327 | 11 | 2017 | 2016-08-07 | C | 1 | 0.000327 | 3.0042e-06
1 | 12899794 | 2016-08-07 12:40 | 2016-08-07 14:10 | 90 | 2 | 180 | 0.00054076 | 0.000522 | 6.0084e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - WORKMANSHIP | T4530 | JUMPER | at 12:40, Papamoa Sub, CB 7 Roads Feeder. Found badly burnt up neutral connection. Own 11kV Isolation & AP Issued for Transformer T4530 to carryout repairs on neutral connection. All Power Restored on Completion. Faultman advised that this transformer was not very old, and this fault was the result of bad workmanship. The neutral connection was not tight, and the transformer was also missing the Transformer Tank Earth Connection. Clint Johnstone Attended. Replaced 1x Neutral Jumper & Installed New Transformer Tank Earth. | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000522 | 11 | 2017 | 2016-08-07 | C | 2 | 0.000522 | 6.0084e-06
1 | 12901384 | 2016-08-07 16:59 | 2016-08-07 18:17 | 77 | 8 | 622.8 | 0.001871 | 0.001798 | 2.4034e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 6551 | CONDUCTOR - REPAIR/REHANG | RS 6551 A/R, E/F B Phase. Faultman dispatched to patrol found tree branches contacting lines. No pole number. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.001798 | 6.6 | 2017 | 2016-08-07 | C | 8 | 0.001798 | 2.4034e-05
1 | 12901763 | 2016-08-07 18:36 | 2016-08-07 21:40 | 183 | 9 | 1655.25 | 0.0049727 | 0.004891 | 2.7038e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TE6-053 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Fuses blown at at SE6-002. Possible Cable fault or transformer change. Transformer was changed last week. Transformer Replaced Damaged due to Overload F/M to organise PQM | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.004891 | 11 | 2017 | 2016-08-07 | C | 9 | 0.004891 | 2.7038e-05
1 | 12902335 | 2016-08-07 21:30 | 2016-08-07 23:26 | 115 | 8 | 883.3 | 0.0026536 | 0.002581 | 2.4034e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 211205 | JUMPER | Bolt rusted off bushing on Transformer TE4-112 causing jumper to float. Jumper repaired. Isolated transformer on HV to carry out repairs | F3/F4 | WAIMAPU | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.002581 | 11 | 2017 | 2016-08-07 | C | 8 | 0.002581 | 2.4034e-05
1 | 12902861 | 2016-08-08 04:48 | 2016-08-08 07:25 | 156 | 23 | 3602.95 | 0.010824 | 0.010616 | 6.9096e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | O13232 | FUSE - ELEMENT/LINK (HV) | 2 x 15 amp FC803 due to ducks. | F3/F4 | NGATEA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.010616 | 11 | 2017 | 2016-08-08 | C | 23 | 0.010616 | 6.9096e-05
1 | 12902878 | 2016-08-08 05:45 | 2016-08-08 15:00 | 554 | 214 | 32809.55 | 0.098566 | 0.096637 | 0.0010665 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 787657 | CROSSARM - WHOLE ASSEMBLY | CB 7 trip O/C repair tipped crossarm at pole 787657 | F4 | PAPAKAI | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.096637 | 11 | 2017 | 2016-08-08 | C | 214 | 0.096637 | 0.0010665
1 | 12903309 | 2016-08-08 07:34 | 2016-08-08 10:00 | 146 | 2 | 292.7 | 0.00087932 | 0.000861 | 6.0083e-06 |  | 22 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 805319 | FUSE - ELEMENT/LINK (HV) | 2 x 25amp fuses birds | F4 | LEEDSTOWN 22KV | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000861 | 22 | 2017 | 2016-08-08 | C | 2 | 0.000861 | 6.0083e-06
1 | 12903891 | 2016-08-08 11:18 | 2016-08-08 12:06 | 48 | 1 | 48.1333 | 0.0001446 | 0.000135 | 3.0041e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P45681 | CONDUCTOR - REPAIR/REHANG | Fire comms also reported this F2128584. ETA required 04 801 0812 called and emailed hub to advise 999 isolated at fuses R59 Temp Line Break At Pole P19961 due to trees in lines. No repairs notified as at 17.08.2016 and Referral 13077847 created. Outage for T7/201 will be assigned to referral job. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000135 | 11 | 2017 | 2016-08-08 | C | 1 | 0.000135 | 3.0041e-06
1 | 12903965 | 2016-08-08 09:17 | 2016-08-08 13:10 | 233 | 2 | 466.8 | 0.0014024 | 0.001384 | 6.0083e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 784885 | FUSE - ELEMENT/LINK (HV) | 12.22pm Fm advised fuses for transformer are across river. Will need to drive back into town, cross the river then drive up the other side to access the transformer - suspect a couple of HV fuses have blown. Reload at 1433 2 x 10A due to trees. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.001384 | 11 | 2017 | 2016-08-08 | C | 2 | 0.001384 | 6.0083e-06
1 | 12905189 | 2016-08-08 13:01 | 2016-08-08 14:11 | 70 | 51 | 3615.05 | 0.01086 | 0.0104 | 0.00015321 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P46992 | CONDUCTOR - REPAIR/REHANG | Repaired floating 11kV conductor. Used 1x Clamptop insulator | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.0104 | 11 | 2017 | 2016-08-08 | C | 51 | 0.0104 | 0.00015321
1 | 12905779 | 2016-08-25 09:50 | 2016-08-25 12:30 | 160 | 16 | 2560 | 0.0076893 | 0.007545 | 4.8058e-05 | NAPA ID:23143 TP_WAIKINO GXP > WAIHI SUB > WAIHI NORTH | 11 | Planned | 023143 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | WHIWGM048 | NONE | Install TEMP Live Line Break at pole WHIWGM048 on 11kV. Access Permit from TEMP break WHIWGM048 to replace Drop Out Fuses at FC2159. Close TEMP break on 11kV at WHIWGM048 Live Line. Works location: Waihi Whangamata Rd. WO 3002668. | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.0037725 | 5.5 | 2017 | 2016-08-25 | B | 16 | 0.007545 | 4.8058e-05
1 | 12905810 | 2016-08-08 11:29 | 2016-08-08 12:55 | 86 | 1 | 86.3167 | 0.00025931 | 0.00025 | 3.0041e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P34010 | FUSE - ELEMENT/LINK (HV) | Advised hub and emailed re 999. Reload at Fuses J83 2 x 10A due to trees. | F2 | WORKS | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.00025 | 11 | 2017 | 2016-08-08 | C | 1 | 0.00025 | 3.0041e-06
1 | 12906052 | 2016-08-07 07:20 | 2016-08-07 09:20 | 119 | 1 | 119.5667 | 0.0003592 | 0.00035 | 3.0042e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Replaced 2x 8Amp HV Fuses at 12019. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.00035 | 11 | 2017 | 2016-08-07 | C | 1 | 0.00035 | 3.0042e-06
1 | 12906061 | 2016-08-07 07:20 | 2016-08-07 09:40 | 139 | 19 | 2651.7667 | 0.0079665 | 0.007795 | 5.708e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Replaced 2x 20Amp Fuses At NG 384. | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.007795 | 11 | 2017 | 2016-08-07 | C | 19 | 0.007795 | 5.708e-05
1 | 12907168 | 2016-08-30 08:45 | 2016-08-30 11:50 | 185 | 33 | 2640 | 0.0079291 | 0.007631 | 0.00019823 | NAPA ID:23295 TP_MASTERTON GXP > CLAREVILLE SUB > PARK RD | 11 | Planned | 023295 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 845895 | NONE | replace 11kv pole. Works location: Woodlands Rd, Carterton. WO 30000801 | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.0038155 | 5.5 | 2017 | 2016-08-30 | B | 33 | 0.007631 | 0.00019823
1 | 12907285 | 2016-09-01 10:25 | 2016-09-01 15:03 | 278 | 6 | 1668 | 0.0050097 | 0.004955 | 1.802e-05 | NAPA ID:22487 TP_MANGAMAIRE GXP > PARKVILLE SUB > EKETAHUNA | 11 | Planned | 022487 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T8/35 | NONE | To replace transformer cross arms on transformer T8/35 replace LV poles and run new LV conductor. Works location: Hwy 2. WO 30018774 | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.0024775 | 5.5 | 2017 | 2016-09-01 | B | 6 | 0.004955 | 1.802e-05
1 | 12907419 | 2016-08-08 15:18 | 2016-08-08 16:25 | 67 | 3 | 201 | 0.00060384 | 0.000576 | 9.0125e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP1287 | CONDUCTOR - REPAIR/REHANG | Steve Johnson is on way to site. Pole W1189 - will be an NDR. Customer was felling trees and tree fell on line. Advised by Colin at Downer depot in Coromandel. Advised SMC and control. Found 1 HT fuse blown. Isolated transformer via HT fuse to repair LT. | F3/F4 | TAIRUA NORTH | KOPU | Valley | TAIRUA SUB | Eastern Electricity | POWERCO | 0.000576 | 11 | 2017 | 2016-08-08 | C | 3 | 0.000576 | 9.0125e-06
1 | 12907436 | 2016-09-01 08:45 | 2016-09-01 12:00 | 195 | 5 | 975 | 0.0029283 | 0.002883 | 1.5017e-05 | NAPA ID:22793 TP_MASTERTON GXP > TE ORE ORE SUB > BIDEFORD | 11 | Planned | 022793 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 7775 | NONE | Replace 11kV defected cross arm (twisted). Works location: Coopers Rd, Masterton. WO 30018914 | F5 | BIDEFORD | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.0014415 | 5.5 | 2017 | 2016-09-01 | B | 5 | 0.002883 | 1.5017e-05
1 | 12908450 | 2016-08-08 17:21 | 2016-08-08 19:30 | 129 | 16 | 2064 | 0.0062006 | 0.006056 | 4.8067e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13922 | CROSSARM - WHOLE ASSEMBLY | Contractor Zane Marshall has seen a broken 11kV insulator and badly burnt HV cross arm that requires urgent replacement. Replaced HV crossarm complete & 1x HV Fuse holder & 5Amp Fuse Link. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.006056 | 11 | 2017 | 2016-08-08 | C | 16 | 0.006056 | 4.8067e-05
1 | 12911545 | 2016-09-01 09:17 | 2016-09-01 14:16 | 298 | 38 | 11339.2 | 0.034056 | 0.033713 | 0.00011413 | NAPA ID:21851 TP_PIAKO GXP > PIAKO SUB > HORRELLS RD | 11 | Planned | 021851 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC5555 | NONE | Replace 11kV cross arms at various locations. Works location: Taukoro Rd, Morrinsville. WO 30007220 | F4 | HORRELLS RD | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.016856 | 5.5 | 2017 | 2016-09-01 | B | 38 | 0.033713 | 0.00011413
1 | 12911608 | 2016-09-02 09:40 | 2016-09-02 10:40 | 60 | 3 | 180 | 0.00054061 | 0.000513 | 9.01e-06 | NAPA ID:22453 TP_PIAKO GXP > WALTON SUB > PIAKOITI RD | 11 | Planned | 022453 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3080 | NONE | To install a 400V Fuse Disconnector. Works location: Hutchingson Rd, Walton. WO 30019182 | F4 | PIAKOITI RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.0002565 | 5.5 | 2017 | 2016-09-02 | B | 3 | 0.000513 | 9.01e-06
1 | 12911911 | 2016-08-24 09:54 | 2016-08-24 11:22 | 88 | 1 | 88 | 0.00026432 | 0.000255 | 3.0036e-06 | NAPA ID:23288 TP_KAITIMAKO GXP > WELCOME BAY SUB > KAITEMAKO RD | 11 | Planned | 023288 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TP2542 | NONE | Replace temporary transformer TP2542 installed under fault. Works location: Estates Terrace, Tauranga. WO 30026108 | F4 | KAITEMAKO RD | KAITIMAKO | Tauranga | WELCOME BAY SUB | Eastern Electricity | POWERCO | 0.0001275 | 5.5 | 2017 | 2016-08-24 | B | 1 | 0.000255 | 3.0036e-06
1 | 12972300 | 2016-08-09 13:40 | 2016-08-09 15:25 | 105 | 1 | 105.25 | 0.00031619 | 0.000307 | 3.0041e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | FC2149 | FUSE - ELEMENT/LINK (HV) | 2 x 3A HV Fuses at FC2149. OMS job has wrong Transformer. Outage reflected under OMS 12974033. | F4 | GORDON | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000307 | 11 | 2017 | 2016-08-09 | C | 1 | 0.000307 | 3.0041e-06
1 | 12972417 | 2016-09-03 09:45 | 2016-09-03 14:50 | 305 | 13 | 3965 | 0.011908 | 0.011791 | 3.9043e-05 | NAPA ID:22294 TP_LINTON GXP > KAIRANGA SUB > AWAPUNI | 11 | Planned | 022294 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T6/77 | NONE | Replace 2pole Trani structure with DBL 11Mpoles & new 100KVA Trani. Works location: Highway 56, Longburn. WO 30018765 | F3 | AWAPUNI | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.0058955 | 5.5 | 2017 | 2016-09-03 | B | 13 | 0.011791 | 3.9043e-05
1 | 12972579 | 2016-09-05 08:35 | 2016-09-05 12:50 | 255 | 32 | 8160 | 0.024507 | 0.024218 | 9.6105e-05 | NAPA ID:23184 TP_MASTERTON GXP > TE ORE ORE SUB > GORDON ST | 11 | Planned | 023184 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1381 | NONE | Replace Lv fuse rack at T1381. Works location: Puriri Crescent, Masterton. WO 30019932 | F3/F4 | GORDON ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.012109 | 5.5 | 2017 | 2016-09-05 | B | 32 | 0.024218 | 9.6105e-05
1 | 12975944 | 2016-08-10 07:18 | 2016-08-10 11:41 | 263 | 18 | 4738.2 | 0.014234 | 0.014071 | 5.4074e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 5327 | FUSE - ELEMENT/LINK (HV) | Check OMS 12975978 and OMS 12975962 (30 and 42 Lower Kaipaikari Road) Check OMS 53 WHAKAPAKI STREET , URENUI phone 06 752 3351 OMS 12976228 - This may be a GIS one as on different sub and feeder 2 x 3A HV Fuses Replaced. Bird Strike | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.014071 | 11 | 2017 | 2016-08-10 | C | 18 | 0.014071 | 5.4074e-05
1 | 12976128 | 2016-08-10 07:50 | 2016-08-10 13:50 | 359 | 2 | 719.1333 | 0.0021604 | 0.002142 | 6.0082e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 992 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer 992 Faulty. To be replaced. 12:19 Contractor to issue own AP, Replace transformer and re-liven. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.002142 | 11 | 2017 | 2016-08-10 | C | 2 | 0.002142 | 6.0082e-06
1 | 12977433 | 2016-08-10 15:40 | 2016-08-10 16:00 | 20 | 12 | 240 | 0.00072099 | 0.000612 | 3.605e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 759767 | NONE | Pleas check 3 spans north - wind blown pine tree in lines. Tahlia called to advise that Neil is leaving site to attend to another job while traffic management is set up, will be returning. Line isolated at Fuses 5294 and line pulled out of trees with fuse stick. ASPLUNDH have been notified to schedule a job to cut back trees although they are not in the notice zone. | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.000612 | 6.6 | 2017 | 2016-08-10 | C | 12 | 0.000612 | 3.605e-05
1 | 12977510 | 2016-08-10 11:50 | 2016-08-10 12:36 | 46 | 1 | 46 | 0.00013819 | 0.000129 | 3.0041e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 827236 | CONDUCTOR - REPAIR/REHANG | Isolate transformer for LV work. Stripped back neutral screen, FM repaired crutch and repaired neutral screen. Water had come through ducting - shorted out and burned through - deterioration. Nothing else repaired or replaced. All adjacent assets up to Powerco standard. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.000129 | 11 | 2017 | 2016-08-10 | C | 1 | 0.000129 | 3.0041e-06
1 | 12978793 | 2016-08-23 09:16 | 2016-08-23 13:30 | 254 | 119 | 30277.5667 | 0.090945 | 0.089872 | 0.00035744 | NAPA ID:22272 TP_LINTON GXP > TURITEA SUB > AOKAUTERE | 11 | Planned | 022272 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Replace 11kV double arms, Fuse arm & transformer T2/91. Repair & paint Transformer T2/56. Works location: Pahiatua Track, Palmerston North. | F2 | AOKAUTERE | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.044936 | 5.5 | 2017 | 2016-08-23 | B | 119 | 0.089872 | 0.00035744
1 | 12979095 | 2016-08-10 16:22 | 2016-08-10 22:00 | 337 | 2 | 675.5 | 0.0020293 | 0.002011 | 6.0082e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 794072 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, NOT ALL PHASES | Faultman found LV line down transformer X858 also had 2 blown HV fuses, transformer was offloaded to make repairs to LV line. NDR 56101. Replaced 1 x 3 amp transformer fuse. Materials Used: 3 x HD12 connectors, 3 x 10 mm copper sleeves, 9 x 15 mm copper sleeves, 10 m copper conductor 10mm, 40 m copper conductor 16mm. | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.002011 | 11 | 2017 | 2016-08-10 | C | 2 | 0.002011 | 6.0082e-06
1 | 12979780 | 2016-08-10 18:35 | 2016-08-10 20:25 | 109 | 1 | 109.7 | 0.00032955 | 0.00032 | 3.0041e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | 5667 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 20Amp HV Fuses | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.00032 | 6.6 | 2017 | 2016-08-10 | C | 1 | 0.00032 | 3.0041e-06
1 | 12981733 | 2016-09-05 08:45 | 2016-09-05 16:24 | 459 | 98 | 44982 | 0.13509 | 0.13421 | 0.00029432 | NAPA ID:23150 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11 | Planned | 023150 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P37405 | NONE | Replace pole P37405 with double pole. Remove 11kV overhead between pole numbers P37405 and 366927. Replace transformer structure P35046. Reconfigure crossarm at pole P37490. Works location: Paterston St, Pahiatua. WO 30019582 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.067105 | 5.5 | 2017 | 2016-09-05 | B | 98 | 0.13421 | 0.00029432
1 | 12982276 | 2016-09-07 08:30 | 2016-09-07 15:15 | 405 | 51 | 20655 | 0.062032 | 0.061572 | 0.00015316 | NAPA ID:22007 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 022007 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV S323 | NONE | replace defective poles past s323. Works location: Cameron Rd, Carterton. WO 30018283 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.030786 | 5.5 | 2017 | 2016-09-07 | B | 51 | 0.061572 | 0.00015316
1 | 12982548 | 2016-08-14 08:30 | 2016-08-14 16:28 | 478 | 280 | 55167 | 0.16572 | 0.1632 | 0.00084112 | NAPA ID:23450 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > CAMBRIDGE RD TAURANGA | 11 | Planned | 023450 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 203662 | NONE | 1 / LLWPS FOR LL GAP AT POLES 203662 & 203674 2 / REPLACE POLES AND RECON FEEDER & REPLACE ABS SD4-026 ( DNO ) 3/ LLWP TO REMOVE GAPS AT POLE 203662 & 203674 This NAPA is a rewrite of 19271 Advertising still under 19271 | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.081599 | 5.5 | 2017 | 2016-08-14 | B | 280 | 0.1632 | 0.00084112
1 | 12983261 | 2016-08-11 20:24 | 2016-08-11 21:30 | 66 | 17 | 1122 | 0.0033706 | 0.003217 | 5.107e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 743048 | CONDUCTOR - REPAIR/REHANG | Faultman found line down at pole 743048, line was isolated at Fuses 5265 to repair line down. 5m 16mm copper conductor. Used: 2 X sleeves & 1 X binder used. 1 X 10 amp HV fuse replaced. | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.003217 | 11 | 2017 | 2016-08-11 | C | 17 | 0.003217 | 5.107e-05
1 | 12983457 | 2016-08-11 20:59 | 2016-08-11 23:15 | 135 | 171 | 10732.1833 | 0.03224 | 0.030699 | 0.0005137 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9320 | UNKNOWN | Recloser 9320 L/O no flags. Sectionalised and & found no fault. Centre phase LFI indicator flashing beyound ABS IC2565. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.030699 | 11 | 2017 | 2016-08-11 | C | 171 | 0.030699 | 0.0005137
1 | 12984267 | 2016-08-12 02:10 | 2016-08-12 05:24 | 193 | 120 | 21826.9167 | 0.06557 | 0.064488 | 0.00067592 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 837616 | NONE | CB C936 tripped on A & B phase O/C flags, line was sectionalised and patrolled and a branch was found on the line at pole 837616, branch was removed with hot line sticks. NDR: 34828 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.064488 | 11 | 2017 | 2016-08-12 | C | 120 | 0.064488 | 0.00067592
1 | 12986056 | 2016-08-12 07:25 | 2016-08-12 10:10 | 165 | 1 | 165.2333 | 0.00049637 | 0.000487 | 3.004e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 849456 | FUSE - ELEMENT/LINK (HV) | 3 x2amp fuses due to lightning | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.000487 | 11 | 2017 | 2016-08-12 | C | 1 | 0.000487 | 3.004e-06
1 | 12988215 | 2016-09-07 09:02 | 2016-09-07 09:58 | 56 | 65 | 3679 | 0.011049 | 0.010463 | 0.00019521 | NAPA ID:21920 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | 021920 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV ABS V | NONE | Tree removal. Works location: Waihi Valley Rd. WO 30026290 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.0052315 | 5.5 | 2017 | 2016-09-07 | B | 65 | 0.010463 | 0.00019521
1 | 12988717 | 2016-08-24 10:08 | 2016-08-24 14:48 | 280 | 29 | 8120 | 0.02439 | 0.024128 | 8.7106e-05 | NAPA ID:22156 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 022156 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 1 | NONE | Reconductor and Pole Change | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.012064 | 5.5 | 2017 | 2016-08-24 | B | 29 | 0.024128 | 8.7106e-05
1 | 12988944 | 2016-08-12 15:44 | 2016-08-12 15:45 | 1 | 48 | 48 | 0.0001442 | 0 | 0.0001442 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 2018T | FUSE - LV ELEMENT/LINK - HRC (LV) | Isolate at ABS 5815 to replace 1 x 150A Fuse at Transformer 2018T. There is a saftey notice on the LV switchboard at this transformer. It must be de energised before any fuses are replaced | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-08-12 | C | 48 | 0 | 0.0001442
1 | 12989458 | 2016-08-12 16:30 | 2016-08-12 18:47 | 137 | 3 | 411 | 0.0012347 | 0.001207 | 9.0122e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761324 | CROSSARM - WHOLE ASSEMBLY | Isolated at Fuses 5471 for safety due to the fire on Pole 761324. 1 X cross arm & all hardware replaced. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.001207 | 6.6 | 2017 | 2016-08-12 | C | 3 | 0.001207 | 9.0122e-06
1 | 12989834 | 2016-08-12 19:15 | 2016-08-13 10:02 | 886 | 1 | 886.8333 | 0.0026641 | 0.002655 | 3.004e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | T4047 | UNKNOWN | Faultman found transformer T4047 to be faulty transformer was isolated at Fuses 8015 to replace the transformer. Faultman contacted customer and customer is happy for the transformer to be replaced in the morning as he is not at the property. Transformer replaced. Used 1 x 15 kVA 3 phase transformer, 3 x 3 amp fuses. Property to be inspected before livening. FM called to advise property has been inspected and has been re-livened. | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.002655 | 11 | 2017 | 2016-08-12 | C | 1 | 0.002655 | 3.004e-06
1 | 12990261 | 2016-08-12 23:02 | 2016-08-12 23:34 | 32 | 4 | 128 | 0.00038452 | 0.000348 | 1.2016e-05 | hris | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - INSIDE ZONE | 756086 | NONE | Sparking line, reported by Police event no p026282235 eta please 06 759 5500 Police advise this is 100m Sth of intersection heading towards Okato Chris advised Faultman found a palm tree branch hanging over the lines and is touching them when its windy or when it rains, line was isolated at ABS's 149, 245 & 8958 to cut them away from the lines at pole 756086 NDR:100206 | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.000348 | 11 | 2017 | 2016-08-12 | C | 4 | 0.000348 | 1.2016e-05
1 | 12991689 | 2016-08-13 05:11 | 2016-08-13 07:06 | 115 | 716 | 42196.5167 | 0.12676 | 0.12031 | 0.0021509 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 767196 | INSULATOR | CB6 O/C E/F fire service report arcing lines at 104 Ikitara Rd. After receiving call from fire services CB 6 auto reclosed, CB 6 was then opened by NOC, faultman found a damaged 11KV insulator on pole 767196, line was isolated at ABS's 111 & 730 & 998, transformer X1271 and CB 6 to replace damaged insulator. Used 2 x 11kV insulators, 1 x line gaurd, 4 mtrs binder | F3 | IKITARA RD | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.12031 | 11 | 2017 | 2016-08-13 | C | 716 | 0.12031 | 0.0021509
1 | 12993285 | 2016-08-13 05:47 | 2016-08-13 07:48 | 120 | 61 | 7367.7833 | 0.022133 | 0.021583 | 0.00018325 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Sectionliser C641/2 found open, closed and held. Cursory line patrol done with no fault found. All contacts called to check power restored | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.021583 | 11 | 2017 | 2016-08-13 | C | 61 | 0.021583 | 0.00018325
1 | 12996648 | 2016-08-13 09:50 | 2016-08-13 12:41 | 171 | 486 | 15403.5667 | 0.046273 | 0.041892 | 0.00035748 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | A0249 | CONDUCTOR - REPAIR/REHANG | Rec 9539 E/F. Repair lines down at Pole A0249 caused by branch across the line further down the line. Isolation at ABS 987. | F4 | OLD CAMBRIDGE RD | KINLEITH 33 | Valley | MARAETAI ROAD SUB | Eastern Electricity | POWERCO | 0.041892 | 11 | 2017 | 2016-08-13 | C | 486 | 0.041892 | 0.00035748
1 | 12997641 | 2016-08-13 12:58 | 2016-08-13 19:40 | 402 | 4 | 402.4833 | 0.0012091 | 0.001173 | 3.004e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T102 - request for paperwork | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Customer wants power to stay on until new transformer on site. Isolated at transformer fuses and replaced under own AP. Used 1 x 50 kVA 3 phase transformer 1x 11kV insulator | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.001173 | 11 | 2017 | 2016-08-13 | C | 4 | 0.001173 | 3.004e-06
1 | 12997750 | 2016-08-13 13:52 | 2016-08-13 15:55 | 123 | 39 | 4816.5 | 0.014469 | 0.014117 | 0.00011716 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7268 | FUSE - ELEMENT/LINK (HV) | FM has spoken to the customer and his address is 858 Ponatahi Road. Customer tried to explain this to his retailer but the information was not passed on in the job notes. Fuses found blown at Fuses 7268 which are on KEM C955 - Cause Bird Strike. Used 2 x 8amp Fuses. | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.014117 | 11 | 2017 | 2016-08-13 | C | 39 | 0.014117 | 0.00011716
1 | 12998494 | 2016-08-14 06:10 | 2016-08-14 07:33 | 83 | 18 | 1500 | 0.004506 | 0.004343 | 5.4072e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | V83 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses V83 - Cause Bird Strike. Used 2 x 10 amp. | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.004343 | 11 | 2017 | 2016-08-14 | C | 18 | 0.004343 | 5.4072e-05
1 | 12998738 | 2016-08-14 07:27 | 2016-08-14 08:43 | 75 | 6 | 453.5 | 0.0013623 | 0.001308 | 1.8024e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | U8 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses U8 - Cause Bird strike. Used 2 x 6 amp fuses. | F3 | EKETAHUNA | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.001308 | 11 | 2017 | 2016-08-14 | C | 6 | 0.001308 | 1.8024e-05
1 | 12999877 | 2016-08-14 08:14 | 2016-08-14 10:55 | 160 | 218 | 18190.1167 | 0.054643 | 0.052678 | 0.0010003 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB R11 | UNKNOWN | Feeder sectionlised with no fault found | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.052678 | 11 | 2017 | 2016-08-14 | C | 218 | 0.052678 | 0.0010003
1 | 13042151 | 2016-08-14 14:50 | 2016-08-14 21:05 | 375 | 46 | 4443.6333 | 0.013349 | 0.012934 | 0.00013818 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 810707 | POLE | CB C929 Tripped A, C Ph E/F L/O. Car V Pole Reported. Isolated at ABS's S564 & S388, plus Links 7178. Emergency services removed people and car. Pole 810707 replaced. Used 1 x Pole, 2 x HV Crossarms Complete, 15 mtrs of Conductor, 2 x Sleeves. | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.012934 | 11 | 2017 | 2016-08-14 | C | 46 | 0.012934 | 0.00013818
1 | 13042425 | 2016-08-14 15:35 | 2016-08-14 17:20 | 104 | 5 | 524 | 0.0015741 | 0.001529 | 1.502e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 7655 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at fuses 7655 - cause bird strike. Used 2 x 10amp. | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.001529 | 11 | 2017 | 2016-08-14 | C | 5 | 0.001529 | 1.502e-05
1 | 13042551 | 2016-08-15 11:35 | 2016-08-15 12:55 | 80 | 1 | 80 | 0.00024032 | 0.000231 | 3.0039e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P46893 | JUMPER | NO POWER TO RADIO SITE Between Coonoor and Horoeka - Chorus Radio Site past Quarry on left heading towards Horoeka. DDO's all ok. Not safe to access site in dark. Faultman to return in morning. Faultman returned & found broken jumper at Pole P46893. Power isolated at Fuses T40 & jumper replaced. Materials used: 1mtr of gopher conductor & 3x conductor joints. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000231 | 11 | 2017 | 2016-08-15 | C | 1 | 0.000231 | 3.0039e-06
1 | 13043578 | 2016-08-14 22:08 | 2016-08-14 23:01 | 53 | 581 | 14548.6833 | 0.043704 | 0.038468 | 0.00084713 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9208 | UNKNOWN | Sectionaliser 9208 Trip A& B O/C Flags from Rec 13004 which A/R. Line LFI's checked - none flashing. Sectionaliser closed. | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.038468 | 11 | 2017 | 2016-08-14 | C | 581 | 0.038468 | 0.00084713
1 | 13045831 | 2016-09-01 10:00 | 2016-09-01 11:33 | 93 | 15 | 1396.75 | 0.004195 | 0.004059 | 4.5051e-05 | NAPA ID:22913 TP_HUIRANGI GXP > WAITARA EAST SUB > MAIN RD MOTONUI | 11 | Planned | 022913 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 5091 | NONE | Replace 11Kv Lightning Arrestors @ Links 5091. Works location: Tikorangi Rd West, Waitara. WO 30030106. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.0020295 | 5.5 | 2017 | 2016-09-01 | B | 15 | 0.004059 | 4.5051e-05
1 | 13045852 | 2016-09-01 12:30 | 2016-09-01 14:13 | 103 | 17 | 1751 | 0.0052589 | 0.005105 | 5.1058e-05 | NAPA ID:22912 TP_HUIRANGI GXP > WAITARA EAST SUB > TIKORANGI | 11 | Planned | 022912 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 5127 | NONE | Replace 11KV Lightning Arrestors @Links5127. Works location: Tikorangi Rd West, Waitara. WO 30030106 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.0025525 | 5.5 | 2017 | 2016-09-01 | B | 17 | 0.005105 | 5.1058e-05
1 | 13045910 | 2016-09-01 09:02 | 2016-09-01 14:02 | 300 | 34 | 10200 | 0.030635 | 0.030328 | 0.00010212 | NAPA ID:21634 TP_OPUNAKE GXP > NGARIKI SUB > RAHOTU | 11 | Planned | 021634 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS NG201 | NONE | Pole replacement project Opourapa Road. Works location: Opourapa Rd. WO 30027682 | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.015164 | 5.5 | 2017 | 2016-09-01 | B | 34 | 0.030328 | 0.00010212
1 | 13046357 | 2016-09-01 10:04 | 2016-09-01 10:57 | 53 | 104 | 5522.4 | 0.016586 | 0.015648 | 0.00031235 | NAPA ID:23190 TP_PIAKO GXP > PIAKO SUB > MVILLE NORTH | 11 | Planned | 023190 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3763 | NONE | Replace lug on red phase LV incomer cable in TC3763, which has been heating up. Works location: George St, Morrinsville. WO 30031466 | F3 | MVILLE NORTH | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.007824 | 5.5 | 2017 | 2016-09-01 | B | 104 | 0.015648 | 0.00031235
1 | 13047819 | 2016-09-02 09:19 | 2016-09-02 11:20 | 120 | 52 | 6249.5333 | 0.01877 | 0.018301 | 0.00015617 | NAPA ID:22399 TP_STRATFORD GXP > ELTHAM SUB > TE ROTI | 11 | Planned | 022399 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5998 | NONE | Replace Hv Xarm (has had end of arm burnt off ). Works location: Fraser Rd, Hawera. WO 30026974 | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.0091505 | 5.5 | 2017 | 2016-09-02 | B | 52 | 0.018301 | 0.00015617
1 | 13047841 | 2016-09-08 09:36 | 2016-09-08 15:31 | 355 | 33 | 11715 | 0.035183 | 0.034885 | 9.9106e-05 | NAPA ID:23037 TP_WAVERLEY GXP > TP_WAVERLEY > WAITOTARA | 11 | Planned | 023037 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 780560 | NONE | Trim trees around the 11kv lines between poles 780560, and 850966. Works location: Makakaho Valley Rd, Waitotara. WO 30026260 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.017442 | 5.5 | 2017 | 2016-09-08 | B | 33 | 0.034885 | 9.9106e-05
1 | 13048279 | 2016-09-01 09:30 | 2016-09-01 12:05 | 154 | 23 | 3563.4667 | 0.010702 | 0.010495 | 6.9078e-05 | NAPA ID:22394 TP_STRATFORD GXP > ELTHAM SUB > TE ROTI | 11 | Planned | 022394 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 2268T | NONE | Replace transformer 2268T (has severe rust in lid) and transformer hanger arms. Works location: Mountain Rd, Eltham. WO 30027863 | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.0052475 | 5.5 | 2017 | 2016-09-01 | B | 23 | 0.010495 | 6.9078e-05
1 | 13048389 | 2016-09-01 09:05 | 2016-09-01 15:24 | 379 | 17 | 6431 | 0.019315 | 0.019161 | 5.1058e-05 | NAPA ID:21764 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 021764 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses SE3-059 | NONE | Re-conductor the first 1.5ks of Kumikumi Road. Works location; Kumikumi Rd. WO 30017842 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0095805 | 5.5 | 2017 | 2016-09-01 | B | 17 | 0.019161 | 5.1058e-05
1 | 13048430 | 2016-09-06 14:10 | 2016-09-06 15:00 | 50 | 7 | 350 | 0.0010511 | 0.000988 | 2.1023e-05 | NAPA ID:22783 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 022783 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1933 | NONE | To install a 400V Fuse Disconnector on TC1933. Works location: Hwy 29, Te Poi. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000494 | 5.5 | 2017 | 2016-09-06 | B | 7 | 0.000988 | 2.1023e-05
1 | 13048442 | 2016-08-31 09:10 | 2016-08-31 12:19 | 189 | 118 | 22319.7 | 0.067035 | 0.065972 | 0.0003544 | NAPA ID:23370 TP_STRATFORD GXP > CLOTON RD SUB > CLOTON RD SOUTH | 11 | Planned | 023370 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 741683 | NONE | Tricky Trees are to cut trees at poles 741683-741686. Works location: Stanley Rd, Stratford. WO 30007226 | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.032986 | 5.5 | 2017 | 2016-08-31 | B | 118 | 0.065972 | 0.0003544
1 | 13048462 | 2016-09-06 09:45 | 2016-09-06 11:25 | 100 | 10 | 1000 | 0.0030033 | 0.002913 | 3.0033e-05 | NAPA ID:22797 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022797 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2334 | NONE | To replace the 400V Spreader arm, Relocate transformer to new arm, Install 400V Disconector. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0014565 | 5.5 | 2017 | 2016-09-06 | B | 10 | 0.002913 | 3.0033e-05
1 | 13048493 | 2016-09-06 14:00 | 2016-09-06 14:30 | 30 | 4 | 120 | 0.00036039 | 0.000324 | 1.2013e-05 | NAPA ID:22798 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022798 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4522 | NONE | To install a 400V Fuse Disconnector on TC4522. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000162 | 5.5 | 2017 | 2016-09-06 | B | 4 | 0.000324 | 1.2013e-05
1 | 13048546 | 2016-09-07 09:50 | 2016-09-07 10:05 | 15 | 4 | 60 | 0.00018019 | 0.000144 | 1.2013e-05 | NAPA ID:22799 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022799 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4523 | NONE | To install a 400V Fuse Disconnector on TC4523. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 7.2e-05 | 5.5 | 2017 | 2016-09-07 | B | 4 | 0.000144 | 1.2013e-05
1 | 13048567 | 2016-09-07 11:45 | 2016-09-07 13:30 | 105 | 9 | 945 | 0.0028381 | 0.002756 | 2.7029e-05 | NAPA ID:22800 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022800 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2698 | NONE | To install a 400V Fuse Disconnector. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.001378 | 5.5 | 2017 | 2016-09-07 | B | 9 | 0.002756 | 2.7029e-05
1 | 13048647 | 2016-10-03 12:00 | 2016-10-03 12:21 | 21 | 4 | 84 | 0.0002522 | 0.000216 | 1.2009e-05 | NAPA ID:22803 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022803 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3913 | NONE | To install a 400V Fuse Disconnector on TC3913. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000108 | 5.5 | 2017 | 2016-10-03 | B | 4 | 0.000216 | 1.2009e-05
1 | 13048675 | 2016-10-03 14:00 | 2016-10-03 14:45 | 45 | 12 | 540 | 0.0016213 | 0.001513 | 3.6028e-05 | NAPA ID:22804 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022804 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2854 | NONE | To install a 400V Fuse Disconnector on TC2854. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0007565 | 5.5 | 2017 | 2016-10-03 | B | 12 | 0.001513 | 3.6028e-05
1 | 13048717 | 2016-09-09 10:00 | 2016-09-09 10:30 | 30 | 4 | 120 | 0.00036038 | 0.000324 | 1.2013e-05 | NAPA ID:22805 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022805 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4387 | NONE | To install a 400V Fuse Disconnector on TC4387. Works location: Pont Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000162 | 5.5 | 2017 | 2016-09-09 | B | 4 | 0.000324 | 1.2013e-05
1 | 13048740 | 2016-09-09 12:00 | 2016-09-09 13:20 | 80 | 5 | 400 | 0.0012013 | 0.001156 | 1.5016e-05 | NAPA ID:22806 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022806 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC1885 | NONE | To install a 400V Fuse disconnector on TC1885. Works location: Gore Rd. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000578 | 5.5 | 2017 | 2016-09-09 | B | 5 | 0.001156 | 1.5016e-05
1 | 13048742 | 2016-09-09 14:00 | 2016-09-09 14:35 | 35 | 4 | 140 | 0.00042044 | 0.000384 | 1.2013e-05 | NAPA ID:22807 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022807 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2275 | NONE | To install a 400V Fuse Disconnector on TC2275. Works location: Hwy 27, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000192 | 5.5 | 2017 | 2016-09-09 | B | 4 | 0.000384 | 1.2013e-05
1 | 13048761 | 2016-09-12 13:50 | 2016-09-12 15:20 | 90 | 5 | 450 | 0.0013514 | 0.001306 | 1.5015e-05 | NAPA ID:23048 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 023048 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5536 | NONE | To install a 400V Fuse Disconnector on TC5536. Works location: Taihoa South Rd. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000653 | 5.5 | 2017 | 2016-09-12 | B | 5 | 0.001306 | 1.5015e-05
1 | 13048798 | 2016-09-12 10:00 | 2016-09-12 10:15 | 15 | 3 | 45 | 0.00013514 | 0.000108 | 9.0092e-06 | NAPA ID:22808 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022808 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2337 | NONE | To install a 400V Fuse disconnector on TC2337. Works location: Hwy 27, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 5.4e-05 | 5.5 | 2017 | 2016-09-12 | B | 3 | 0.000108 | 9.0092e-06
1 | 13048819 | 2016-09-12 12:00 | 2016-09-12 12:45 | 45 | 3 | 135 | 0.00040542 | 0.000378 | 9.0092e-06 | NAPA ID:22809 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022809 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP905 | NONE | To install a 400V Disconnector on TP905. Works location: Hwy 27, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000189 | 5.5 | 2017 | 2016-09-12 | B | 3 | 0.000378 | 9.0092e-06
1 | 13048891 | 2016-09-12 14:00 | 2016-09-12 14:15 | 15 | 7 | 105 | 0.00031532 | 0.000252 | 2.1021e-05 | NAPA ID:22810 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022810 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1859 | NONE | To install a 400V Fuse disconnector on TC1859. Works location: Hwy 27, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000126 | 5.5 | 2017 | 2016-09-12 | B | 7 | 0.000252 | 2.1021e-05
1 | 13049062 | 2016-08-15 19:00 | 2016-08-15 19:30 | 30 | 28 | 840 | 0.0025233 | 0.00227 | 8.4111e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737085 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Burnt DDo's found at Transformer 3314T Isolated at Fuses 6051 DDO's replaced - used 3 x DDO Fuse carriers and bases Transformer failed at livening, Replaced under own AP Used 3 HV carriers and bases, 3 X 15 amp fuses 1 x 15 kVA transformer | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.00227 | 11 | 2017 | 2016-08-15 | C | 28 | 0.00227 | 8.4111e-05
1 | 13050410 | 2016-08-16 08:25 | 2016-08-16 08:33 | 8 | 1442 | 11944.5667 | 0.035881 | 0.022885 | 0.0043317 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | rec 9503 tripped while doing planned switching under napa 21556 | F3 | MATAPIHI RD | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 0.022885 | 11 | 2017 | 2016-08-16 | C | 1442 | 0.022885 | 0.0043317
1 | 13051941 | 2016-08-16 13:10 | 2016-08-17 17:45 | 1715 | 3 | 832 | 0.0024993 | 0.002472 | 1.2016e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | See Referral - 13072384 | CABLE - REPLACE LESS THAN 5 METRES | Found Fuse blown at FC4251, disconnect cable to transformer TC4895, Replaced fuse & relivened. Transformer TC4895 to have a generator installed until fault located and fixed. 11kv cable fault on network to be repaired 17/08/16. Referral Created - 13072384. Repaired cable & re-livened | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.002472 | 11 | 2017 | 2016-08-16 | C | 3 | 0.002472 | 1.2016e-05
1 | 13052076 | 2016-09-13 09:38 | 2016-09-13 13:45 | 247 | 6 | 1482 | 0.0044505 | 0.004396 | 1.8018e-05 | NAPA ID:22464 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | 022464 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3042 | NONE | To replace arms & hardware. To install a 400V Fuse Disconnector. Works location: Puketutu Rd, Matamata. WO 30019182 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.002198 | 5.5 | 2017 | 2016-09-13 | B | 6 | 0.004396 | 1.8018e-05
1 | 13053793 | 2016-09-06 08:15 | 2016-09-06 15:12 | 417 | 48 | 20016 | 0.060113 | 0.05968 | 0.00014416 | NAPA ID:22785 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 022785 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 216810 | NONE | Replace poles,hardware and conductor. Works location: Belk Rd South. WO 30019862 | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.02984 | 5.5 | 2017 | 2016-09-06 | B | 48 | 0.05968 | 0.00014416
1 | 13054103 | 2016-09-13 13:40 | 2016-09-13 14:00 | 20 | 3 | 60 | 0.00018018 | 0.000153 | 9.0091e-06 | NAPA ID:22812 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022812 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2704 | NONE | To install a 400V Disconnector on TC2704. Works location: Hwy 27, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 7.65e-05 | 5.5 | 2017 | 2016-09-13 | B | 3 | 0.000153 | 9.0091e-06
1 | 13054193 | 2016-09-14 09:00 | 2016-09-14 14:16 | 316 | 2 | 632 | 0.0018979 | 0.001879 | 6.006e-06 | NAPA ID:22813 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022813 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3389 | NONE | To replace 11kV arms & Hardware beyond FP1488. Works location: Hwy 27, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0009395 | 5.5 | 2017 | 2016-09-14 | B | 2 | 0.001879 | 6.006e-06
1 | 13054195 | 2016-08-21 08:00 | 2016-08-21 11:16 | 196 | 17 | 3316 | 0.0099605 | 0.009807 | 5.1064e-05 | NAPA ID:23525 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV | 11 | Planned | 023525 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS SD4-026 | NONE | OPEN ABS SD4-026 ONCE PARALLEL MADE. INSTALL 2 LINE GAPS. REPLACE DNO 160813. ABS SWITCH. REMOVE 2 LINE GAPS. Works location: Sherson St, Greerton. WO 30031715 | F3 | CAMBRIDGE RD TAURANGA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0049035 | 5.5 | 2017 | 2016-08-21 | B | 17 | 0.009807 | 5.1064e-05
1 | 13054217 | 2016-09-01 23:30 | 2016-09-02 00:13 | 43 | 40 | 1720 | 0.0051658 | 0.004805 | 0.00012014 | NAPA ID:23194 TP_PIAKO GXP > MORRINSVILLE SUB > LORNE ST | 11 | Planned | 023194 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC713 | NONE | Low oil identified in transformer TC713 during routing inspection. To top up oil and inspect transformer for source of leak. Works location: Thames St, Morrinsville. WO 30031467 | F1/F3 | LORNE ST | PIAKO | Valley | MORRINSVILLE SUB | Eastern Electricity | POWERCO | 0.0024025 | 5.5 | 2017 | 2016-09-01 | B | 40 | 0.004805 | 0.00012014
1 | 13054247 | 2016-09-06 10:19 | 2016-09-06 12:49 | 150 | 3 | 450 | 0.0013515 | 0.001324 | 9.0097e-06 | NAPA ID:22743 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 022743 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1442 | NONE | To Replace the existing 11kV Fuses TC1442 & install a 400V Fuse Disconnector on TC1442. Works location: Hwy 29, Matamata. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.000662 | 5.5 | 2017 | 2016-09-06 | B | 3 | 0.001324 | 9.0097e-06
1 | 13054404 | 2016-09-07 09:34 | 2016-09-07 15:17 | 343 | 4 | 1372 | 0.0041204 | 0.004084 | 1.2013e-05 | NAPA ID:23094 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023094 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1055 | NONE | To replace the 11kV Fuse arm, 400V Spreader arm, 400V Service arm, Relocate the transformer. TC1055. Works location: Taotaoroa Rd, Matamata. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.002042 | 5.5 | 2017 | 2016-09-07 | B | 4 | 0.004084 | 1.2013e-05
1 | 13054560 | 2016-09-12 09:15 | 2016-09-12 11:57 | 161 | 6 | 969.4 | 0.0029112 | 0.002857 | 1.8019e-05 | NAPA ID:23056 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 023056 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC366 | NONE | To replace the 11kV Fuse arm & Fuses & install a 400V Fuse Disconnector. Works location: Taihoa North Rd, Matamata. WO 30019182 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0014285 | 5.5 | 2017 | 2016-09-12 | B | 6 | 0.002857 | 1.8019e-05
1 | 13054564 | 2016-09-06 09:35 | 2016-09-06 12:36 | 180 | 11 | 1987.7 | 0.0059696 | 0.00587 | 3.3036e-05 | NAPA ID:22516 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 022516 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2700 | NONE | Replace Tx TC2700 structure. Works location: North Rd, Mangatarata. WO 30019417 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002935 | 5.5 | 2017 | 2016-09-06 | B | 11 | 0.00587 | 3.3036e-05
1 | 13056691 | 2016-09-19 09:46 | 2016-09-19 15:00 | 314 | 10 | 3140 | 0.0094289 | 0.009338 | 3.0028e-05 | NAPA ID:22814 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022814 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP1047 | NONE | LLP1: To break the jumpers supplying service line to TP1047. AP: To complete line Maint. Between pole HINTWR045 & TP1047. LLP2: To Restore the jumpers supplying service line to TP1047. Works location: Hwy 27, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.004669 | 5.5 | 2017 | 2016-09-19 | B | 10 | 0.009338 | 3.0028e-05
1 | 13056750 | 2016-09-06 10:06 | 2016-09-06 13:37 | 211 | 52 | 10972 | 0.032952 | 0.032483 | 0.00015617 | NAPA ID:22518 TP_KOPU GXP > KEREPEHI SUB > MANGATARATA | 11 | Planned | 022518 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1362 | NONE | Replace 11kv & 400v x arms including fuses FC4009. Works location: Miranda Rd, Mangatarata. WO 30026354 | F4 | MANGATARATA | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.016241 | 5.5 | 2017 | 2016-09-06 | B | 52 | 0.032483 | 0.00015617
1 | 13056817 | 2016-08-16 12:22 | 2016-08-16 16:54 | 271 | 191 | 23988.65 | 0.07206 | 0.070339 | 0.00085312 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 779863 | CONDUCTOR - REPAIR/REHANG | RS 142 Tripped. No comms to site. Sectionalised & patrolled with floating HV conductor found at Pole 779863. Replaced 3x Ali Binders | F5 | IRIRANGI | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.070339 | 11 | 2017 | 2016-08-16 | C | 191 | 0.070339 | 0.00085312
1 | 13063253 | 2016-09-05 10:02 | 2016-09-05 13:50 | 228 | 6 | 1368 | 0.0041085 | 0.004054 | 1.802e-05 | NAPA ID:22816 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 022816 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2262 | NONE | To replace the 11kV arm, 11kV fuse arm, 400V Pin arm and install a 400V Disconnector. Works location: Hwy 27, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.002027 | 5.5 | 2017 | 2016-09-05 | B | 6 | 0.004054 | 1.802e-05
1 | 13070902 | 2016-08-30 09:45 | 2016-08-30 15:41 | 356 | 67 | 23887.7333 | 0.071745 | 0.071141 | 0.00020123 | NAPA ID:23561 TP_TAURANGA 33 GXP > MATUA SUB > MATUA POINT | 11 | Planned | 023561 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SC4-007 | NONE | Install Live Line Gap. Replace Switch SC4-007 (DNO 160717). Works location: Levers Rd, Tauranga. WO 30031377 | F3 | WARATAH ST | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 0.03557 | 5.5 | 2017 | 2016-08-30 | B | 67 | 0.071141 | 0.00020123
1 | 13070998 | 2016-08-16 14:09 | 2016-08-16 14:26 | 16 | 4 | 67.7333 | 0.00020347 | 0.000167 | 1.2016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 804191 | CONDUCTOR - REPAIR/REHANG | Bark seen sitting on HV lines by faultman. Isolated at Fuses 133 & bark removed using hot stick. Relivened ok. Nil materials used. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000167 | 11 | 2017 | 2016-08-16 | C | 4 | 0.000167 | 1.2016e-05
1 | 13071050 | 2016-08-30 09:25 | 2016-08-30 13:17 | 232 | 1 | 232 | 0.0006968 | 0.000687 | 3.0034e-06 | NAPA ID:23519 TP_BRUNSWICK GXP > ROBERTS AVE SUB > MAKIRIKIRI | 11 | Planned | 023519 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | x606 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Create line break on spur line at pole 783491. Upgrade all hardware & Transformer X606. On completion reinstate line break. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.0003435 | 5.5 | 2017 | 2016-08-30 | B | 1 | 0.000687 | 3.0034e-06
1 | 13071389 | 2016-09-02 09:59 | 2016-09-02 13:51 | 231 | 97 | 6909.2333 | 0.020751 | 0.019876 | 0.00029133 | NAPA ID:22549 TP_HINUERA GXP > TOWER ROAD SUB > TE POI | 11 | Planned | 022549 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5538 | NONE | AP 1: To replace 2 x 11kV pin arms On TC343 & Pole F1419. LLP: To replace the 11kV Fuse arm and 400V Pin arm on TC343. AP 2: To install a 400V Fuse Disconnector on TC5538. Works location: Taihoa South Rd, Matamata. WO 30030695 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.009938 | 5.5 | 2017 | 2016-09-02 | B | 97 | 0.019876 | 0.00029133
1 | 13073895 | 2016-08-16 16:37 | 2016-08-16 20:54 | 257 | 603 | 27898.9 | 0.083806 | 0.078372 | 0.0018114 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 831317 | POLE | 4.28pm called police comms to advise eta 5mins CB C818 opened for safety to isolate between ABS S61, ABS S185 & ABS S141 to replace pole 831317 damaged by vehicle. No backfeeds available. Used 1 x Pole, 1 x Donut block, 2 x blocks 1 x HV crossarm complete, 1 x LV crossarm complete, 3 x LV fuse bases and carriers, 3 x 63 amp HRC fuses, 3 x shackles, 3 x bobbins Power still off to 62 Lincoln Rd due to damage to mains entry point to house and customers cable. disconnected for safety. Tag # A1090 | F3 | CORADINE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.078372 | 11 | 2017 | 2016-08-16 | C | 603 | 0.078372 | 0.0018114
1 | 13075313 | 2016-08-16 18:53 | 2016-08-16 20:53 | 119 | 120 | 14302 | 0.042962 | 0.04188 | 0.00036047 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 837616 - request for paperwork | CONDUCTOR - REPAIR/REHANG | cb C936 Tripped O/C a&b Phase Branch found on lines while sectionlising at Pole 837616. Cleared using hot sticks | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.04188 | 11 | 2017 | 2016-08-16 | C | 120 | 0.04188 | 0.00036047
1 | 13077723 | 2016-09-06 09:24 | 2016-09-06 14:35 | 311 | 9 | 2799 | 0.0084061 | 0.008325 | 2.7029e-05 | NAPA ID:23494 TP_TE MATAI GXP > PAENGAROA SUB > GULLIVER RD | 11 | Planned | 023494 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TE6-053 | NONE | upgrade transformer te6-053 from a 50 kva to a 100 kva to remedy PQI job. Works location: Hwy 2, Te Puke. WO 30025651 | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.0041625 | 5.5 | 2017 | 2016-09-06 | B | 9 | 0.008325 | 2.7029e-05
1 | 13078009 | 2016-08-26 08:54 | 2016-08-26 13:20 | 265 | 6 | 1595.7 | 0.0047928 | 0.004738 | 1.8022e-05 | NAPA ID:23602 TP_PIAKO GXP > PIAKO SUB > KIWITAHI | 11 | Planned | 023602 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | I2107 | NONE | LLP1: To cut away the lines between pole I2107 and FC1420 AP: To work on the lines beyond FC1420. LLP2: To replace the arms on pole I2107. LLP3: To replace the lines from FC1420 to pole I2107 after AP is cancelled. Works location: Paratu West St, Walton. WO 30031981 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.002369 | 5.5 | 2017 | 2016-08-26 | B | 6 | 0.004738 | 1.8022e-05
1 | 13078539 | 2016-09-06 10:11 | 2016-09-06 14:15 | 244 | 29 | 7076 | 0.021251 | 0.020989 | 8.7094e-05 | NAPA ID:22171 TP_KOPU GXP > COROMANDEL SUB > MANAIA COROMANDEL | 11 | Planned | 022171 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2609 | NONE | Reconductor. Works location: Tiki Rd, Coromandel. WO 30029959 | F4 | MANAIA COROMANDEL | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.010495 | 5.5 | 2017 | 2016-09-06 | B | 29 | 0.020989 | 8.7094e-05
1 | 13078743 | 2016-09-07 08:45 | 2016-09-07 15:18 | 393 | 46 | 18078 | 0.054292 | 0.053877 | 0.00013815 | NAPA ID:23218 TP_MARTON GXP > ARAHINA SUB > TUTAENUI | 11 | Planned | 023218 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole 794431 | NONE | Drop 11kv lines between poles 794431 and 794432 so that a number of pine trees that are threatning the 11kv lines can be dropped. Works location: Turakina Valley Rd, Wanganui. WO 30007436 | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.026939 | 5.5 | 2017 | 2016-09-07 | B | 46 | 0.053877 | 0.00013815
1 | 13079738 | 2016-08-18 00:17 | 2016-08-18 01:17 | 59 | 27 | 1589.9667 | 0.0047761 | 0.004532 | 8.1104e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3932T | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Replace Transformer 3932T. 15kVA 3 Phase. Fault found to be a poor connection at the fuseholder at Txfmr 3932. Transformer replacement not required but shutdown via fuses 5193 & 1x HV fuseholder & 2Amp link replaced | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.004532 | 11 | 2017 | 2016-08-18 | C | 27 | 0.004532 | 8.1104e-05
1 | 13081675 | 2016-08-18 06:39 | 2016-08-18 08:51 | 132 | 12 | 1592 | 0.0047822 | 0.004674 | 3.6046e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H12458 | FUSE - ELEMENT/LINK (HV) | When closing check OMS 13081722 - 114 Jagger Road. 2 x 20 fp1338 unknown poss bird | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.004674 | 11 | 2017 | 2016-08-18 | C | 12 | 0.004674 | 3.6046e-05
1 | 13081830 | 2016-09-07 10:00 | 2016-09-07 11:47 | 107 | 5 | 535 | 0.0016067 | 0.001561 | 1.5016e-05 | NAPA ID:23134 TP_OPUNAKE GXP > TASMAN SUB > PIHAMA | 11 | Planned | 023134 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 5023E | NONE | Tx HV fuses are loose and burning Xarm. Works location: South Rd, Pihama. WO 30015984 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.0007805 | 5.5 | 2017 | 2016-09-07 | B | 5 | 0.001561 | 1.5016e-05
1 | 13082861 | 2016-08-18 09:06 | 2016-08-18 13:21 | 254 | 242 | 61637.4 | 0.18515 | 0.18297 | 0.00072694 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 248572 | JUMPER | When closing check OMS 13082988, 13082918, 13082875. Emergency switching to repair blown jumper at pole 248572 Isolation at ABS 986 ( spur no back feed ) Jumper repaired all service restored NOTE SD unit 9016 is in bad state may req replacement | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.18297 | 11 | 2017 | 2016-08-18 | C | 242 | 0.18297 | 0.00072694
1 | 13083669 | 2016-09-07 09:37 | 2016-09-07 09:51 | 14 | 7 | 98 | 0.00029432 | 0.000231 | 2.1023e-05 | NAPA ID:22745 TP_PIAKO GXP > FARMER ROAD SUB > TATUANUI | 11 | Planned | 022745 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP2982 | NONE | To complete Audit Defects as per Northpower Audit. Works location: No. 1 Rd, Waihou. WO 30027279 | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.0001155 | 5.5 | 2017 | 2016-09-07 | B | 7 | 0.000231 | 2.1023e-05
1 | 13084312 | 2016-09-01 08:48 | 2016-09-01 15:17 | 389 | 40 | 15560 | 0.046733 | 0.046372 | 0.00012014 | NAPA ID:23639 TP_WAIKINO GXP > WAIHI BEACH SUB > ATHENREE | 11 | Planned | 023639 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TA2-061 | NONE | Replace Transformer TA2-061. Relocate SL CCTs into new adjacent Gyro Pillar. Works location: Hanlen Ave, Waihi Beach. WO 30013538 | F3 | ATHENREE | WAIKINO | Valley | WAIHI BEACH SUB | Eastern Electricity | POWERCO | 0.023186 | 5.5 | 2017 | 2016-09-01 | B | 40 | 0.046372 | 0.00012014
1 | 13084405 | 2016-09-12 09:30 | 2016-09-12 14:30 | 300 | 81 | 24300 | 0.072975 | 0.072245 | 0.00024325 | NAPA ID:23000 TP_CARRINGTON GXP > KATERE SUB > KATERE 8 | 11 | Planned | 023000 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 8373 | NONE | replace two pole tx structure with new fused underground cable to new groundmount tx. Works location: Alberta Rd. WO 30018773 | F3 | KATERE 8 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.036123 | 5.5 | 2017 | 2016-09-12 | B | 81 | 0.072245 | 0.00024325
1 | 13084421 | 2016-09-12 09:00 | 2016-09-12 16:48 | 468 | 130 | 60840 | 0.18271 | 0.18154 | 0.0003904 | NAPA ID:23074 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11 | Planned | 023074 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P18137 | NONE | Replace poles P18141, P18142, P35000, P35001, P18137 & P18138. Works location: Huxley St, Pahiatua. WO 30019582 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.090768 | 5.5 | 2017 | 2016-09-12 | B | 130 | 0.18154 | 0.0003904
1 | 13084550 | 2016-09-07 09:19 | 2016-09-07 10:30 | 71 | 32 | 2272 | 0.0068233 | 0.006535 | 9.6103e-05 | NAPA ID:22412 TP_OPUNAKE GXP > TASMAN SUB > TE KIRI | 11 | Planned | 022412 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 716413 | NONE | Replace Faulty Hv insulators on pole 716413. Works location: Oeo Rd, Opunake. WO 30015290 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.0032675 | 5.5 | 2017 | 2016-09-07 | B | 32 | 0.006535 | 9.6103e-05
1 | 13084568 | 2016-09-06 08:45 | 2016-09-06 14:01 | 316 | 82 | 25912 | 0.07782 | 0.077081 | 0.00024627 | NAPA ID:22575 TP_KOPU GXP > THAMES SUB > THAMES COAST | 11 | Planned | 022575 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1256 | NONE | TO MAKE A TEMP BREAK LIVE LINE AT POLE T1256 & REPLACE ABS 1354 & XARMS UNDER ACCESS PERMIT THEN CLOSE TEMP BREAK LIVE LINE. Works location: Waiomu Valley Rd. WO 30027650 | F3 | ROLLESTON ST | KOPU | Valley | THAMES SUB | Eastern Electricity | POWERCO | 0.03854 | 5.5 | 2017 | 2016-09-06 | B | 82 | 0.077081 | 0.00024627
1 | 13084622 | 2016-09-06 13:08 | 2016-09-06 14:15 | 67 | 90 | 6030 | 0.01811 | 0.017298 | 0.00027029 | NAPA ID:22419 TP_OPUNAKE GXP > NGARIKI SUB > SOUTH RD NGARIKI | 11 | Planned | 022419 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 712719 | NONE | Replace faulty HV insulators at pole 712719. Works location: Kina Rd, Opunake. WO 30015290 | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.008649 | 5.5 | 2017 | 2016-09-06 | B | 90 | 0.017298 | 0.00027029
1 | 13085585 | 2016-08-18 18:14 | 2016-08-18 20:39 | 145 | 149 | 10582.2167 | 0.031788 | 0.030444 | 0.00044758 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 376434 | NONE | RS 284 A/R, L/O, E/F B Phase. Sectionalised with backfeed installed via MABS 688. Fault due to a wire dropped by bird onto HV making nest on HV cross arm. Removed using hot stick | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.030444 | 11 | 2017 | 2016-08-18 | C | 149 | 0.030444 | 0.00044758
1 | 13086632 | 2016-08-19 03:56 | 2016-08-19 07:54 | 237 | 253 | 14328.6333 | 0.043041 | 0.040761 | 0.00075997 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB C955 Trip. Sectionalised & patrolled. No fault found. Flags checked at Sub, Phase R-B. Possibly birds, CB also auto-reclosed at 06:30 and 07:53. | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.040761 | 11 | 2017 | 2016-08-19 | C | 253 | 0.040761 | 0.00075997
1 | 13087737 | 2016-08-19 06:49 | 2016-08-19 08:22 | 93 | 26 | 2420.1667 | 0.0072698 | 0.007035 | 7.81e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 747941 | FUSE - ELEMENT/LINK (HV) | When closing check OMS 13087748 - 548 ALFRED ROAD and 13087774 - 115 ALFRED ROAD | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.007035 | 11 | 2017 | 2016-08-19 | C | 26 | 0.007035 | 7.81e-05
1 | 13088195 | 2016-08-19 09:00 | 2016-08-19 10:05 | 65 | 4 | 260 | 0.000781 | 0.000744 | 1.2015e-05 | NAPA ID:23668 TP_GREYTOWN GXP > KEMPTON SUB > PONATAHI | 11 | Planned | 023668 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T2495 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Upgrade transformer T2495 from 15kVA to 30kvaVA. Works Location: Papawai Road, Greytown. Work Order: 30032026 | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.000372 | 5.5 | 2017 | 2016-08-19 | B | 4 | 0.000744 | 1.2015e-05
1 | 13088439 | 2016-09-09 09:05 | 2016-09-09 15:00 | 355 | 2 | 710 | 0.0021322 | 0.002114 | 6.0063e-06 | NAPA ID:23095 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023095 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5069 | NONE | To replace arms, Hardware, Relocate transformer & install a 400V Disconnector on TC5069. Works location: Taotaoroa Rd, Matamata. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.001057 | 5.5 | 2017 | 2016-09-09 | B | 2 | 0.002114 | 6.0063e-06
1 | 13089578 | 2016-09-12 23:01 | 2016-09-13 01:14 | 132 | 1 | 132.4167 | 0.00039766 | 0.000388 | 3.003e-06 | NAPA ID:23571 TP_CARRINGTON GXP > CITY SUB > CITY 9 | 11 | Planned | 023571 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV Sw/Gear 6682 | NONE | 10 Yearly 11kV metering at CCSC. Outage negotiated with consumer. Isolations as per request with the two incomers at CCSC closed for earthing purposes. Fuse switches 1,2,3 will be opened under the AP for testing and the incomers 5,6 will also be opened when testing under the isolations of the AP. Works location: St Aubyn St. WO 30027195 | F3 | CITY 9 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.000194 | 5.5 | 2017 | 2016-09-12 | B | 1 | 0.000388 | 3.003e-06
1 | 13089665 | 2016-08-23 09:07 | 2016-08-23 14:18 | 310 | 5 | 1552.0833 | 0.004662 | 0.004616 | 1.5018e-05 | NAPA ID:23666 TP_WAIHOU GXP > TP_WAIHOU > WAIHOU392-KEREONE 33KV | 11 | Planned | 023666 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS |  | NONE | Ngarua Feeder Step 10b, Shut 6b Specified renewal works on Waihekau Rd. Replace 33kV Termination arms on WHUKER088 under AP. Combined to rewrite switching from 22175. | F4 | NGARUA | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.002308 | 5.5 | 2017 | 2016-08-23 | B | 5 | 0.004616 | 1.5018e-05
1 | 13091289 | 2016-08-20 07:34 | 2016-08-20 08:49 | 75 | 120 | 9000 | 0.027034 | 0.025952 | 0.00036046 | NAPA ID:23710 TP_MASTERTON GXP > TINUI SUB > ANNEDALE | 11 | Planned | 023710 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 936 | NONE | Cut tree causing feeder outages. Works location: Manawa Road, Tinui. Work Order 30024973 | F5 | ANNEDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.012976 | 5.5 | 2017 | 2016-08-20 | B | 120 | 0.025952 | 0.00036046
1 | 13091388 | 2016-09-13 09:15 | 2016-09-13 12:11 | 176 | 11 | 1936 | 0.0058139 | 0.005714 | 3.3034e-05 | NAPA ID:23097 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 023097 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2609 | NONE | Replace 11kV crossarms and install and LV disconnector on TC2609. Works location: Factory Rd, Waihou. WO 30017829 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.002857 | 5.5 | 2017 | 2016-09-13 | B | 11 | 0.005714 | 3.3034e-05
1 | 13091868 | 2016-08-19 16:49 | 2016-08-19 20:15 | 206 | 20 | 4129.6667 | 0.012405 | 0.012224 | 6.0077e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 218336 | JUMPER | ( PGA 3 ) Emergency switching to repair blown jumper @ pole 218336 ( TE7 010 ). Isolation at fuses SE7 032 ( spur no back feed ). Jumper repaired all service restored. | F4 | MAKETU | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.012224 | 11 | 2017 | 2016-08-19 | C | 20 | 0.012224 | 6.0077e-05
1 | 13093053 | 2016-08-20 04:58 | 2016-08-20 08:00 | 182 | 38 | 6929.3 | 0.020814 | 0.020471 | 0.00011414 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 201998 | FUSE - ELEMENT/LINK (HV) | 2x15amp fuses blown at SC3-071. Possible bird strike. Line patrolled with no faults found. Reloaded & livened. | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.020471 | 11 | 2017 | 2016-08-20 | C | 38 | 0.020471 | 0.00011414
1 | 13093060 | 2016-08-20 07:55 | 2016-08-20 08:19 | 24 | 68 | 1632 | 0.0049022 | 0.004289 | 0.00020426 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208087 | FUSE - ELEMENT/LINK (HV) | 1x20amp Fuse blown at SB1-005. Had to open other fuses to determine correct fuse size for replacement. Line patrolled & no cause found. Reloaded & livened. | F4 | KATIKATI | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.004289 | 11 | 2017 | 2016-08-20 | C | 68 | 0.004289 | 0.00020426
1 | 13093738 | 2016-08-20 07:08 | 2016-08-20 07:53 | 45 | 3403 | 140736.2 | 0.42274 | 0.39208 | 0.010222 |  | 33 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | KINBRD074 | INSULATOR | CB 2212 tripped. O/C Time. Magpie at Pole KINBRD074. Blown clear. Feeder Relivened after pole inspected. 11kV feeders restored. 1 back feed used. Sectionaliser 9595 Closed. | S4 | KINLEITH2212-BAIRD RD 33KV | KINLEITH 33 | Valley | TP_KINLEITH | Eastern Electricity | POWERCO | 0.39208 | 33 | 2017 | 2016-08-20 | C | 3403 | 0.39208 | 0.010222
1 | 13097808 | 2016-08-20 08:29 | 2016-08-20 09:40 | 70 | 8 | 565.2 | 0.0016978 | 0.001625 | 2.403e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7602 | FUSE - ELEMENT/LINK (HV) | 2 HV Fuses tripped at both Fuses 7603 and 7602. Reloaded / relivened OK. Suspect bird strike. All 4 fuses 10A rating. | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.001625 | 11 | 2017 | 2016-08-20 | C | 8 | 0.001625 | 2.403e-05
1 | 13098685 | 2016-08-20 14:36 | 2016-08-20 14:56 | 19 | 48 | 924.8 | 0.0027779 | 0.002345 | 0.00014418 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 819142 | BINDER | Broken binder repaired at Pole 819412. Fault found while carrying out operational patrol on feeder after auto-recloses (Not considered to be the fault). | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.002345 | 11 | 2017 | 2016-08-20 | C | 48 | 0.002345 | 0.00014418
1 | 13099028 | 2016-08-20 17:52 | 2016-08-20 19:58 | 125 | 4 | 420.9167 | 0.0012644 | 0.001228 | 1.2015e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 070 | FUSE - ELEMENT/LINK (HV) | Replaced 2x HV fuses | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.001228 | 11 | 2017 | 2016-08-20 | C | 4 | 0.001228 | 1.2015e-05
1 | 13100128 | 2016-08-21 03:32 | 2016-08-21 20:32 | 1019 | 415 | 33259.4833 | 0.099904 | 0.096164 | 0.0023159 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | T6/432 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Initial Tripping on Milson 11kV CB8 and 33kV CB Z70 on A Phase O/C. Feeder sectionalised and fault traced to defective transformer T6/432. Heavy fault had also caised a joint to blow in the 11kV Cable feeding transformers T6/432 and T6/433 plus 33kV above (Flygers) line tripped due to 11kV movement underneath. 33kV CB70 closed OK. Earthing the 11kV Cable for repairs required a Temp Line Break in Place on 11kV Cables between Sw/Gear 158 and T6/434. 11kV Earths were then applied and Sw/Gear158 closed for earthing continuity. Transformer T6/432 replaced and 11kV Cable rejointed. 2 transition joints used and 6 metres of 95mm Cable. | F2 | RANGITIKEI | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.096164 | 11 | 2017 | 2016-08-21 | C | 415 | 0.096164 | 0.0023159
1 | 13100862 | 2016-08-21 07:08 | 2016-08-21 13:16 | 367 | 469 | 87728.5333 | 0.26352 | 0.25929 | 0.0014088 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 803804 | POLE | CB 7 TRIPPED O/C, E/F. Car vs pole outside Criterion street. Police notified Powerco P026386753. Isolated at ABS's 1384 and 4466 with backfeed via ABS 1318. Pole 803804 replaced. NDR # 30370. Faultman to fax materials list on Monday. | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.25929 | 11 | 2017 | 2016-08-21 | C | 469 | 0.25929 | 0.0014088
1 | 13105525 | 2016-08-22 06:35 | 2016-08-22 10:38 | 242 | 197 | 24770.9833 | 0.074405 | 0.07263 | 0.00059174 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 267392 | CONDUCTOR - REPAIR/REHANG | RC 28 tripped to L/O. E/F flag. Line sectionalised & patrolled. Lines down located at pole 267392. Isolation at ABS 286. All supply restored following repairs. | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.07263 | 11 | 2017 | 2016-08-22 | C | 197 | 0.07263 | 0.00059174
1 | 13106407 | 2016-08-22 08:34 | 2016-08-22 08:35 | 1 | 496 | 412.1333 | 0.0012379 | 0 | 0.00095218 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | P28597 | NONE | CB 1332 tripped O/C time at Mangamaire GXP Pongaroa sub transferred onto alternative feeder Cursory line patrol carried out on 33 kV lines with Magpie found on lines at Pole P28597 Bird cleared using hot sticks | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-08-22 | C | 496 | 0 | 0.00095218
1 | 13106866 | 2016-09-01 10:43 | 2016-09-01 15:17 | 274 | 235 | 64390 | 0.19339 | 0.19127 | 0.0007058 | NAPA ID:23140 TP_BUNNYTHORPE GXP > SANSON SUB > RONGOTEA | 11 | Planned | 023140 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P34159 | NONE | Poles need to be changed, LL not an option conductor condition not good | F4 | RONGOTEA | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.095635 | 5.5 | 2017 | 2016-09-01 | B | 235 | 0.19127 | 0.0007058
1 | 13107025 | 2016-09-08 08:19 | 2016-09-08 13:42 | 323 | 48 | 15504 | 0.046562 | 0.046129 | 0.00014415 | NAPA ID:22787 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 022787 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 263493 | NONE | Replace poles,hardware and conductor. Install DOF's TEMP's 54&56 on pole 263493. Works Location: Belk Rd South. WO 30019862 | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.023065 | 5.5 | 2017 | 2016-09-08 | B | 48 | 0.046129 | 0.00014415
1 | 13107333 | 2016-08-27 09:57 | 2016-08-27 12:16 | 139 | 39 | 5421 | 0.016282 | 0.01593 | 0.00011714 | NAPA ID:23701 TP_MANGAMAIRE GXP > PONGAROA SUB > TIRAUMEA | 11 | Planned | 023701 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 377045 | NONE | To Close temp gaps at poles 377219&377182 and at pole 377045 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.007965 | 5.5 | 2017 | 2016-08-27 | B | 39 | 0.01593 | 0.00011714
1 | 13107523 | 2016-08-22 13:01 | 2016-08-22 14:08 | 67 | 5 | 335 | 0.0010063 | 0.000961 | 1.5019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | H3116 | CONDUCTOR - REPAIR/REHANG | at 13:01, Walton Sub, CB 4 Wardville Feeder. Faultman was called to LV Lines down. Found lines down at Pole H3116 caused by digger. Isolated Lines at Transformer TC507. Own isolation & AP, all repairs carried. All Power Restored on completion. 1x 3A HV Fuse Replaced & 2x Connectors Used. NDR: 55720 Check for safety - Line down hit by digger , in paddock, all precautions read out (OMS 13109930) Advised Control and SMC of 999 NDR or SRC? | F4 | WARDVILLE | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.000961 | 11 | 2017 | 2016-08-22 | C | 5 | 0.000961 | 1.5019e-05
1 | 13107893 | 2016-08-22 12:35 | 2016-08-22 13:26 | 51 | 420 | 16000.8333 | 0.048062 | 0.044277 | 0.0012616 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 228306 | CONDUCTOR - REPAIR/REHANG | CB 3 tripped to L/O. E/F flag. Back feed established via recloser 9679/2 to recloser 9556/2 following 15min down time. Line sectionalised & patrolled. Member of public advised Downer faultman on site of vehicle (truck with deck raised) contacting HV line at pole 228306 that would have caused tripping. Site checked out and all appeared ok. Supply successfully restored. Driver of vehicle has been asked why he hadn't reported the line contact, his response was he had reported it to Trustpower.?? NDR has been created. | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.044277 | 11 | 2017 | 2016-08-22 | C | 420 | 0.044277 | 0.0012616
1 | 13110143 | 2016-09-08 10:11 | 2016-09-08 11:08 | 57 | 714 | 23239 | 0.069791 | 0.063358 | 0.0021443 | NAPA ID:23003 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11 | Planned | 023003 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 12164 | NONE | Replace two pole tx structure with new groundmount tx and install new fuses 12164. Works location: Barrett Rd, New Plymouth. WO 30018773 | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.031679 | 5.5 | 2017 | 2016-09-08 | B | 714 | 0.063358 | 0.0021443
1 | 13110419 | 2016-09-18 08:11 | 2016-09-19 08:15 | 1444 | 462 | 1848 | 0.0055493 | 0.001387 | 0.0013873 | NAPA ID:21472 TP_HAWERA GXP > WHAREROA SUB > MANUTAHI | 11 | Planned | 021472 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS WH108 | NONE | Replace Faulty Hv Xarm. Works location: South Rd, Mokoia. WO 30002019. Switching occurred for the outage but crew were not planning to do the job and job was cancelled. Safety Manager 661555 | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.0006935 | 5.5 | 2017 | 2016-09-18 | B | 462 | 0.001387 | 0.0013873
1 | 13110659 | 2016-09-12 09:40 | 2016-09-12 11:55 | 135 | 1 | 135 | 0.00040542 | 0.000396 | 3.003e-06 | NAPA ID:23614 TP_WANGANUI GXP > HATRICKS WHARF SUB > MARANGAI | 11 | Planned | 023614 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 4284 | NONE | Isolate 11kv metering unit 4285 for calibration testing. Works location: Airport Rd, Wanganui. WO 30027200 | F2 | TAUPO 2 | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 0.000198 | 5.5 | 2017 | 2016-09-12 | B | 1 | 0.000396 | 3.003e-06
1 | 13111053 | 2016-08-22 20:45 | 2016-08-22 22:40 | 115 | 8 | 920 | 0.0027634 | 0.002691 | 2.403e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X4320 | INSULATOR | When closing check OMS 13111120 - 170 TE HUE ROAD R D 3 , WANGANUI. Outage required from Fuses 478 to replace a broken insulator at Transformer X4320. Also replaced one binder and 5A HV Fuse at 478. Assistance called from Raetihi faultman. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.002691 | 11 | 2017 | 2016-08-22 | C | 8 | 0.002691 | 2.403e-05
1 | 13111171 | 2016-08-22 18:27 | 2016-08-22 18:50 | 23 | 861 | 19803 | 0.059483 | 0.051724 | 0.0025862 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1072 | FUSE - ELEMENT/LINK (HV) | Fire on tranny up pole, fire services responding now. F2137347 - ETA 15mins (18:32) SMC and control advised. CB7 open via SCADA from NOC. Fault turned out to be a burnt up DDO fuse at Transformer X1072. CB7 then failed to close either locally or via SCADA. (Backfed via ABS 111 - DNO 160827 applied to CB). 1 HT fuse replaced (25A) and fuse holder at Transformer X1072 | F2/F3 | WANGANUI EAST | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.051724 | 11 | 2017 | 2016-08-22 | C | 861 | 0.051724 | 0.0025862
1 | 13114616 | 2016-08-23 07:47 | 2016-08-23 10:47 | 179 | 2 | 359.8 | 0.0010807 | 0.001062 | 6.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 735093 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp fuse unknown | F4 | MAHOE | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.001062 | 11 | 2017 | 2016-08-23 | C | 2 | 0.001062 | 6.0073e-06
1 | 13114676 | 2016-09-07 08:45 | 2016-09-07 17:55 | 550 | 27 | 14850 | 0.044598 | 0.044354 | 8.1087e-05 | NAPA ID:23155 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11.00000000 | Planned | 023155 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/442 | POLE | Replace poles between P35567 and P35571 Replace transformer structure P35572 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.022177 | 5.5 | 2017 | 2016-09-07 | B | 27 | 0.044354 | 8.1087e-05
1 | 13114678 | 2016-09-13 08:30 | 2016-09-13 09:24 | 53 | 365 | 19576.1667 | 0.058788 | 0.055499 | 0.0010961 | NAPA ID:22685 TP_MT MAUNGANUI 33 GXP > MATAPIHI SUB > TE MAUNGA | 11 | Planned | 022685 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-290 | NONE | 1. Make permanent cable break at HV link-box TD4-290 (AP1) 2. Remove and abandon old 25mm cable from switchgear 13053-3 and install new 185mm cable connected to switchgear 13057 & 13058 (AP2) 3. Test new cable (TP) 4. Liven new cable and switchgear 13057 & 13058 (Bus only). Works location: Bayfair Dr, Mt Maunganui. WO 30019186 | F3 | TE MAUNGA | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 0.027749 | 5.5 | 2017 | 2016-09-13 | B | 365 | 0.055499 | 0.0010961
1 | 13114845 | 2016-09-01 08:33 | 2016-09-01 15:40 | 426 | 14 | 5972.6333 | 0.017938 | 0.017812 | 4.2047e-05 | NAPA ID:22742 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > MAUNGAKAWA ROAD | 11 | Planned | 022742 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | C13340 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | DNO160616 ABS 664 - AP: Replace ABS with DDO links (FP1824), replace 16mm conductor from C13339 and C13340. LLP: Replace all arms on pole C13340. Works Location: 384 Mamawaru Road, Te Aroha. | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.008906 | 5.5 | 2017 | 2016-09-01 | B | 14 | 0.017812 | 4.2047e-05
1 | 13117518 | 2016-08-23 14:17 | 2016-08-23 16:30 | 132 | 16 | 2124.5333 | 0.0063815 | 0.006237 | 4.8059e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T825 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replace transformer T825. Access Permit self issued. | F3 | NAPLES ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.006237 | 11 | 2017 | 2016-08-23 | C | 16 | 0.006237 | 4.8059e-05
1 | 13117706 | 2016-08-23 11:51 | 2016-08-23 12:35 | 44 | 3001 | 118363.6833 | 0.35553 | 0.32849 | 0.0090141 |  | 33 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 366923 | UNKNOWN | CB 2182 Trip, O/C Instanteous. Wanganui East Sub backfed. 33kV line patrol carried out. Dead magpie found at base of Pole 366923 | S4 | WANGANUI EAST 33KV | WANGANUI | Wanganui | TP_WANGANUI | Western Electricity | POWERCO | 0.32849 | 33 | 2017 | 2016-08-23 | C | 3001 | 0.32849 | 0.0090141
1 | 13121758 | 2016-09-23 10:28 | 2016-09-23 10:59 | 31 | 3 | 94.45 | 0.00028361 | 0.000256 | 9.0081e-06 | NAPA ID:23086 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023086 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP542 | NONE | To install a 400V Disconnector at TP542. Works location: Hwy 27, Hinuera. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000128 | 5.5 | 2017 | 2016-09-23 | B | 3 | 0.000256 | 9.0081e-06
1 | 13121781 | 2016-09-23 11:45 | 2016-09-23 12:20 | 35 | 1 | 35 | 0.00010509 | 9.6e-05 | 3.0027e-06 | NAPA ID:23087 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023087 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4609 | NONE | To install a 400V Disconnector. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 4.8e-05 | 5.5 | 2017 | 2016-09-23 | B | 1 | 9.6e-05 | 3.0027e-06
1 | 13121804 | 2016-09-23 14:05 | 2016-09-23 14:30 | 25 | 4 | 100 | 0.00030027 | 0.000264 | 1.2011e-05 | NAPA ID:23088 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023088 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4496 | NONE | To install a 400V Disconnector on TC4496. Works location: Taotaoroa Rd, Matamata. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000132 | 5.5 | 2017 | 2016-09-23 | B | 4 | 0.000264 | 1.2011e-05
1 | 13121837 | 2016-09-26 10:03 | 2016-09-26 10:40 | 37 | 2 | 74 | 0.00022219 | 0.000204 | 6.0052e-06 | NAPA ID:23089 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023089 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1056 | NONE | To install a 400V Disconnector On TC1056. Works location: Taotaoroa Rd. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000102 | 5.5 | 2017 | 2016-09-26 | B | 2 | 0.000204 | 6.0052e-06
1 | 13121856 | 2016-09-26 12:00 | 2016-09-26 12:35 | 35 | 4 | 140 | 0.00042036 | 0.000384 | 1.201e-05 | NAPA ID:23090 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023090 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2254 | NONE | To install a 400V Disconnector on TC2254. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000192 | 5.5 | 2017 | 2016-09-26 | B | 4 | 0.000384 | 1.201e-05
1 | 13121874 | 2016-09-26 14:00 | 2016-09-26 14:20 | 20 | 4 | 80 | 0.00024021 | 0.000204 | 1.201e-05 | NAPA ID:23091 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023091 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2252 | NONE | To install a 400V disconnector on TC2252. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000102 | 5.5 | 2017 | 2016-09-26 | B | 4 | 0.000204 | 1.201e-05
1 | 13121883 | 2016-09-15 10:00 | 2016-09-15 10:13 | 13 | 365 | 4745 | 0.014249 | 0.01096 | 0.0010961 | NAPA ID:22690 TP_MT MAUNGANUI 33 GXP > MATAPIHI SUB > TE MAUNGA | 11 | Planned | 022690 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-289 | NONE | AP1. Make permanent cable break at HV link-box TD4-289 to TD4-290. Remove jumpers and fuses (L1) from HV link-box TD4-289 and connect new cable from new fuse-switch 13058/2 to transformer TD4-289. Liven HV link-box TD4-289 to HV link-box TD4-715 from fuse-switch SD4-693. Liven transformer TD4-289 from fuse-switch 13058-2. AP2. Remove HV link-box TD4-290 and connect new cable to transformer TD4-290 from fuse-switch 13057/2 and liven. Works location: Bayfair Dr, Mt Maunganui. WO 30019186 | F3 | TE MAUNGA | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 0.00548 | 5.5 | 2017 | 2016-09-15 | B | 365 | 0.01096 | 0.0010961
1 | 13121904 | 2016-09-28 10:05 | 2016-09-28 10:45 | 40 | 5 | 200 | 0.00060051 | 0.000555 | 1.5013e-05 | NAPA ID:23092 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023092 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2253 | NONE | To install a 400V Disconnector on TC2253. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0002775 | 5.5 | 2017 | 2016-09-28 | B | 5 | 0.000555 | 1.5013e-05
1 | 13121913 | 2016-09-28 12:40 | 2016-09-28 13:05 | 25 | 5 | 125 | 0.00037532 | 0.00033 | 1.5013e-05 | NAPA ID:23093 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023093 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4527 | NONE | To install a 400V Disconnector on TC4527. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000165 | 5.5 | 2017 | 2016-09-28 | B | 5 | 0.00033 | 1.5013e-05
1 | 13121917 | 2016-09-26 08:31 | 2016-09-26 09:40 | 68 | 64 | 4404.2667 | 0.013224 | 0.012647 | 0.00019217 | NAPA ID:22451 TP_HINUERA GXP > BROWNE STREET SUB > TAINUI ST | 11 | Planned | 022451 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1758 | NONE | Replace Ceramic fuse carrier base on LV cct 3 at TC1758. Works location: Farmers Rd, Matamata. WO 30029354 | F4 | TE POI | HINUERA | Valley | TOWER ROAD SUB | Eastern Electricity | POWERCO | 0.0063235 | 5.5 | 2017 | 2016-09-26 | B | 64 | 0.012647 | 0.00019217
1 | 13121968 | 2016-09-13 09:15 | 2016-09-13 13:30 | 255 | 2 | 510 | 0.0015316 | 0.001513 | 6.006e-06 | NAPA ID:23078 TP_BRUNSWICK GXP > KAI IWI SUB > MAXWELL | 11 | Planned | 023078 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X1417 | NONE | Replace transformer pole X1417 damaged by falling tree. Works location: Hgarino Rd. WO 30007436 | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.0007565 | 5.5 | 2017 | 2016-09-13 | B | 2 | 0.001513 | 6.006e-06
1 | 13122016 | 2016-08-23 15:12 | 2016-08-23 15:25 | 13 | 622 | 1040 | 0.0031238 | 0 | 0.0002403 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 703771 | JUMPER | at 15:11, Cambria Sub, CB 9 Glover Rd West Feeder. Fautlman called to sparking/arcing lines and part/flickering power calls. Found blown jumper at ABS 6716. Sectionaliser 12083 opened initially to de-energise lines at 15:11. Sectionalising commenced and all power restored at 15:25. ABS has been DNO'd: 160831. Phil Webby will attempt to do live line tomorrow. No Materials Used. Check for safety - Sparking / arcing power lines outside the cafe Advised control and SMC of 999 Onsite contact had left site. Spoke to another onsite who said he had not seen the sparking. Advised of safety process | F3 | GLOVER RD WEST | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-08-23 | C | 622 | 0 | 0.0002403
1 | 13123887 | 2016-08-23 18:13 | 2016-08-23 20:01 | 107 | 2 | 215.2667 | 0.0006466 | 0.000628 | 6.0073e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 356454 | FUSE - ELEMENT/LINK (HV) | 2x6amp HV fuse blown at 2630. Line checked no fault found. Reloaded & Livened. | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.000628 | 11 | 2017 | 2016-08-23 | C | 2 | 0.000628 | 6.0073e-06
1 | 13124426 | 2016-08-23 20:19 | 2016-08-23 21:30 | 71 | 170 | 9639.8333 | 0.028955 | 0.027423 | 0.00051063 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P17219 | NONE | RS 010 tripped O/C E/F. Possum found on lines during sectionlising at Pole P17219 Cleared using hot sticks | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.027423 | 11 | 2017 | 2016-08-23 | C | 170 | 0.027423 | 0.00051063
1 | 13126059 | 2016-08-24 09:01 | 2016-08-24 09:30 | 28 | 6 | 168.9 | 0.00050732 | 0.000453 | 1.8022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 776549 | INSULATOR | Faultman found floating HV conductor due to rusted through pin on insulator. Replaced and pin & Insulator & Ali binder. | F5 | PARAPARA | OHAKUNE | Wanganui | TP_OHAKUNE | Western Electricity | POWERCO | 0.000453 | 11 | 2017 | 2016-08-24 | C | 6 | 0.000453 | 1.8022e-05
1 | 13126954 | 2016-09-20 08:30 | 2016-09-20 13:10 | 280 | 187 | 52360 | 0.15723 | 0.15554 | 0.00056153 | NAPA ID:22702 TP_MT MAUNGANUI 33 GXP > MATAPIHI SUB > TE MAUNGA | 11 | Planned | 022702 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-289 | NONE | Remove cables and HV link-box TD4-289. Re-connect cables to switch gear 13058-1 (SD4-693) and 13058-4 (TD4-715), test, liven & phase check. Works location: Russley Dr, Mt Maunganui. WO 30019186 | F3 | TE MAUNGA | MT MAUNGANUI 31 | Tauranga | MATAPIHI SUB | Eastern Electricity | POWERCO | 0.077771 | 5.5 | 2017 | 2016-09-20 | B | 187 | 0.15554 | 0.00056153
1 | 13127208 | 2016-08-24 11:22 | 2016-08-24 13:27 | 124 | 4 | 498.7333 | 0.001498 | 0.001461 | 1.2015e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 805586 | FUSE - ELEMENT/LINK (HV) | called hub re 999 and emailed Called customer re Hazard Process. Reload at Fused ABS 4171 2 x 10A Cause Birds | F4 | PUTORINO | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.001461 | 11 | 2017 | 2016-08-24 | C | 4 | 0.001461 | 1.2015e-05
1 | 13128153 | 2016-09-09 09:32 | 2016-09-09 12:10 | 157 | 40 | 6306.6667 | 0.01894 | 0.018579 | 0.00012013 | NAPA ID:23788 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | 023788 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2498 | NONE | Install new Tx at pole I2858 ,reposition existing Tx TC2498 on pole. Works location: Te Miro Rd, Te Miro. WO 30031644 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.0092895 | 5.5 | 2017 | 2016-09-09 | B | 40 | 0.018579 | 0.00012013
1 | 13129680 | 2016-08-24 18:34 | 2016-08-24 20:59 | 145 | 294 | 25159 | 0.075569 | 0.072919 | 0.00088308 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1011 | UNKNOWN | R/S 1011 Tripped A Ph E/F L/O No Fault found during sectionlising | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.072919 | 11 | 2017 | 2016-08-24 | C | 294 | 0.072919 | 0.00088308
1 | 13130965 | 2016-08-24 20:26 | 2016-08-24 22:52 | 146 | 1 | 146.0167 | 0.00043858 | 0.000429 | 3.0036e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 786342 | FUSE - ELEMENT/LINK (HV) | HV fuses found blown at Transformer X1181 - Cause Unknown Used 2 x 2 amp fuses LV jumper cut away at Pole 849140 due to privite line down | F4 | MOAWHANGO | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000429 | 11 | 2017 | 2016-08-24 | C | 1 | 0.000429 | 3.0036e-06
1 | 13131636 | 2016-08-25 00:46 | 2016-08-25 06:32 | 346 | 265 | 27418.6167 | 0.082355 | 0.079967 | 0.00079596 |  | 33 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 228680 | CONDUCTOR - REPAIR/REHANG | CB 5 Paengaroa sub tripped to L/O simultaneously with trip to L/O on Recloser 9987/2. Flags - CB 5 A & B Ph O/C & E/F - Recloser 9987/2 E/F. Line sectionalised & patrolled up to 9987/2 in 1st instance with no fault found. Supply restored to that point by closing CB 5. Patrol continued beyond 9987 with tree through line located at pole 228680. Isolations for line repair repairs were ABS 9987/1, Links 9987/6 & ABS SF6-018. Remainder of feeder backfed via ABS SF6-039. Materials required - 10 x Namu sleeves, 80 metres Namu conductor. All supply restored following repairs. Comment from Downer contractor that this is an historical site for tree problems. Some action required to have problem rectified?? Also may need to have protection discrimination between CB 5 & Recloser 9987/2 as both tripped to L/O simultaneously. Will need protection review as both Recloser and CB tripped. NDR N400175. | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.079967 | 33 | 2017 | 2016-08-25 | C | 265 | 0.079967 | 0.00079596
1 | 13133083 | 2016-08-25 07:43 | 2016-08-25 11:18 | 215 | 622 | 64738.9167 | 0.19445 | 0.18885 | 0.0018683 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 209900 | POLE | Car vs pole at 45 Whakamarama Rd. ETA required: 40 mins. Called fire comms to advise ETA Event # F2138857. Fire service called to advise power pole is down and lying across the road towards centre of road, powerlines still live - passed onto Tallia at svs hub. CB 2 L/O on O/C. Isolated between ABS SD3-043 & SD2-007. Backfeed rest of area. Replaced pole & relivened. NDR to come. Materials Used: 1 x pole and 1 x HT crossarm. | F4 | WHAKAMARAMA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.18885 | 11 | 2017 | 2016-08-25 | C | 622 | 0.18885 | 0.0018683
1 | 13140251 | 2016-09-16 09:07 | 2016-09-16 15:16 | 369 | 5 | 1845 | 0.0055404 | 0.005495 | 1.5015e-05 | NAPA ID:22008 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 022008 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-026 | NONE | First shutdown on spur line down into McLarens Falls Park. Replacing old poles and hardware. Works location: McLarens Falls Rd. WO 30017842 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0027475 | 5.5 | 2017 | 2016-09-16 | B | 5 | 0.005495 | 1.5015e-05
1 | 13150352 | 2016-08-25 10:35 | 2016-08-25 13:40 | 185 | 7 | 1295 | 0.0038897 | 0.003826 | 2.1025e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | UNKNOWN | UNKNOWN - NO FAULT FOUND | te5-097 | UNKNOWN | Found 1 HT fuse blown. Isolated at HT fuses to check HT bushing of transformer. Found OK. Removed dirt & walnuts from LT side. Tested cables OK. No cause of fault found. | F3 | NO 3 ROAD | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.003826 | 11 | 2017 | 2016-08-25 | C | 7 | 0.003826 | 2.1025e-05
1 | 13150382 | 2016-09-19 09:32 | 2016-09-19 12:28 | 175 | 188 | 32994 | 0.099076 | 0.097382 | 0.00056454 | NAPA ID:23014 TP_TE MATAI GXP > PONGAKAWA SUB | 11 | Planned | 023014 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 387543 | NONE | Replace crossarms and conductor between poles 387543 - 316911. Works location: Pukehina Parade, Te Puke. WO 30019859 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.048691 | 5.5 | 2017 | 2016-09-19 | B | 188 | 0.097382 | 0.00056454
1 | 13150420 | 2016-08-25 09:07 | 2016-08-25 11:15 | 127 | 1 | 127.9833 | 0.00038441 | 0.000375 | 3.0036e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 248642 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp fuse poss ducks | F3 | RAILWAY ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.000375 | 11 | 2017 | 2016-08-25 | C | 1 | 0.000375 | 3.0036e-06
1 | 13150614 | 2016-09-13 10:00 | 2016-09-13 10:45 | 45 | 4 | 180 | 0.00054055 | 0.000504 | 1.2012e-05 | NAPA ID:23809 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 023809 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1773 | NONE | To install a 400V Fuse/Disconnector on TC1773. Works location: Hwy 29, Hinuera. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000252 | 5.5 | 2017 | 2016-09-13 | B | 4 | 0.000504 | 1.2012e-05
1 | 13161125 | 2016-08-25 14:22 | 2016-08-25 15:11 | 49 | 56 | 2744 | 0.0082419 | 0.007737 | 0.0001682 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | te5-042 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Found DDO at TE5-042 broken. Isolated between ABS 9146/1, Links 9146/6 & ABS SE5-225. Replaced 2 x DDO's & relivened | F4 | ROADS | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.007737 | 11 | 2017 | 2016-08-25 | C | 56 | 0.007737 | 0.0001682
1 | 13161134 | 2016-08-25 12:29 | 2016-08-25 14:20 | 111 | 4 | 445.8 | 0.001339 | 0.001302 | 1.2014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 389572 | FUSE - ELEMENT/LINK (HV) | called and emailed hub re 999. ETA required 20 mins called customer re Hazard process - spoke to electrician who advised the meter board has blown up, not the incoming line. advised hub of updated information. 2 x 6amp fuse blown up main switch | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.001302 | 11 | 2017 | 2016-08-25 | C | 4 | 0.001302 | 1.2014e-05
1 | 13217131 | 2016-08-25 14:31 | 2016-08-25 16:22 | 111 | 294 | 25690.75 | 0.077165 | 0.074516 | 0.00088307 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1011 | UNKNOWN | Line sectionalised and supply restored with no apparent fault found | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.074516 | 11 | 2017 | 2016-08-25 | C | 294 | 0.074516 | 0.00088307
1 | 13218543 | 2016-08-25 14:53 | 2016-08-25 20:29 | 335 | 392 | 15925.5 | 0.047834 | 0.044301 | 0.0011774 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 756706 | INSULATOR | CB 8 tripped on A & B phase O/c & E/F flags, line was patrolled at sectionalised. Temp line break made as fault cause could not be determined and 3x backfeeds installed. Pin hole found in insulator. Insulator replaced & temp break closed. All restored to normal. | F4 | SEAWARD COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.044301 | 11 | 2017 | 2016-08-25 | C | 392 | 0.044301 | 0.0011774
1 | 13219962 | 2016-08-25 19:44 | 2016-08-25 20:37 | 53 | 1 | 53 | 0.00015919 | 0.00015 | 3.0036e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M83 | CONDUCTOR - REPAIR/REHANG | FM has noted HV pole is on a slight lean - will Amber 2 defect this. Also noted there is a sparking/arcing joint which will be causing the power issues. FM believes this is on the customer side (un-numbered pole, furthermore, pole not safe for him to climb) - I spoke to customer (Mary) to explain SRC may be required, Mary said the pole has three service lines coming off of it, and is further out on the road than their customer service line, spoke to CST earlier in the day and is under the impression line is HV/POCO. - Zane has remained onsite - undone to Onsite. - NOC Viewer showing POCO pole and Tx at the end of the line. Explained to Zane it is the service provider's responsibility to confirm ownership of an asset before commencing repair work on it. Zane not HV qualified to disconnect/repair on HV side. Suggested he contact a senior linesman. - Peter Marshall has attended to assist Zane to identify whether customer or network - Peter also believes customer side. It has crossed boundary and the pole has no asset ID. Near the road. Zane confirmed Peter will be working through Control for an HV outage. - Called back customer (Ossie) to confirm that it is customer side, and SRC will be required. Ossie noted at this point the line is sparking "like a Christmas tree". He questioned what the criteria are for determining whether it is network or customer - he understood it had to be done, but before signing up to SRC he wanted the confirmation on how we could determine that it was definitely his responsibility. - I explained the contractor had determined it was customer side - the customer challenged this as he was unaware of ever being responsible for it. I advised I will contact my manager. At this point I called Kris to explain and seek assistance. Peter confirmed the joint was affecting a spur line - 11kV near fuse M83. Kris advised to advise FM to go ahead and fix it. - Tx T3/49 has two ICPs off it - customer (Ossie) says it feeds three properties but they are the only customers who would be affected by an outage. Advised Ossie the power will be isolated while the fault is fixed. Replaced 1x deteriorated fargo with 2x ferret sleeves and 1mtr of ferret conductor. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.00015 | 11 | 2017 | 2016-08-25 | C | 1 | 0.00015 | 3.0036e-06
1 | 13224350 | 2016-08-25 18:10 | 2016-08-25 23:45 | 334 | 801 | 41923.0333 | 0.12592 | 0.1187 | 0.0024059 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 756368 | POLE | cb3 trip o/c F2139218 - ETA required Car vs Pole at 726 South road CB 3 tripped on O/C flags, line was isolated at ABS's 202, 374 & 8717, fuses 8406 and transformer 1489 fuses NDR #N100210 Replaced 11m pole, crossarm, 3x pins & insulators, 8mtrs of 70mm wire, 6x binders | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.1187 | 11 | 2017 | 2016-08-25 | C | 801 | 0.1187 | 0.0024059
1 | 13227900 | 2016-08-25 19:14 | 2016-08-25 21:43 | 148 | 294 | 21914.8333 | 0.065824 | 0.063174 | 0.00088307 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | RS1011 A/R, L/O, E/F A Phase. Sectionalised & Patrolled with no fault found | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.063174 | 11 | 2017 | 2016-08-25 | C | 294 | 0.063174 | 0.00088307
1 | 13229505 | 2016-08-26 01:02 | 2016-08-26 12:18 | 676 | 144 | 20507.2833 | 0.061595 | 0.060297 | 0.00076592 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 268839 | JUMPER | Recloser S6029 tripped to L/O. E/F flag. Line sectionalised & patrolled. Fault is beyond fuses FP1136 but unable to continue patrol due to weather & terrain issues (Thick fog and through bush) Line patrol to continue at daylight. Line patrolled in morning & found at pole 268839 jumper resting on eyebolt ( report of tree in lines near this site last week ) Jumper re set all service restored Materials Nil | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.060297 | 11 | 2017 | 2016-08-26 | C | 144 | 0.060297 | 0.00076592
1 | 13230137 | 2016-08-26 01:53 | 2016-08-26 06:06 | 253 | 2 | 506.4 | 0.001521 | 0.001502 | 6.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | RS 6942 Trip, E/F, O/C A Phase. Cheal Control room notified they will stay in island mode until they check their site. Closed. No fault found. Suspect picked up spike & tripped when RS4182 tripped. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.001502 | 11 | 2017 | 2016-08-26 | C | 2 | 0.001502 | 6.0071e-06
1 | 13231296 | 2016-08-26 01:53 | 2016-08-26 04:30 | 156 | 382 | 30104.7833 | 0.090422 | 0.08698 | 0.0013456 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 740157 | INSULATOR | RS 4182 A/R, L/O E/F, O/C A Phase. Found a broken insulator had burnt end of crossarm. Replaced HV pin & Insulator & Binder. Moved insulator inwards on the crossarm. Crossarm to be defected for replacement. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.08698 | 11 | 2017 | 2016-08-26 | C | 382 | 0.08698 | 0.0013456
1 | 13233055 | 2016-08-26 05:34 | 2016-08-26 07:56 | 141 | 260 | 28181.35 | 0.084645 | 0.082302 | 0.00078093 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 208193 | BINDER | CB 2 tripped to L/O ( no flags ) Feeder sectionalised with floating conductor found at pole 208193 Isolation at ABS SB1 008 ( spur no back feed ) Binder repaired all service restored | F4 | KATIKATI | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.082302 | 11 | 2017 | 2016-08-26 | C | 260 | 0.082302 | 0.00078093
1 | 13235642 | 2016-08-26 07:22 | 2016-08-26 12:19 | 297 | 34 | 9504.4333 | 0.028547 | 0.028241 | 0.00010212 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 783865 | INSULATOR | called customer - left msg for her to call back, will try again in 5 mins to go through Hazard Process called hub and emailed re 999 - ETA:45 mins advised customer of Hazard Process and advised ETA REC 083 trip Isolated between ABS 1299 & Links 4614/4 to replace insulator at pole 783865. no backfeeds available. Replace 3 x strain insulators. | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.028241 | 11 | 2017 | 2016-08-26 | C | 34 | 0.028241 | 0.00010212
1 | 13235728 | 2016-08-26 07:47 | 2016-08-26 11:21 | 213 | 1 | 213.5833 | 0.00064152 | 0.000632 | 3.0035e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 707512 | UNKNOWN | This property is currently being back feed due to a car vs pole last night. Tried to call the FM but was unable to get through related to back from feeder fault, this was rectified on OMS 13236025 when LV jumpers were installed. | F3 | BRASSEY ROAD | BRUNSWICK | Wanganui | TP_BRUNSWICK | Western Electricity | POWERCO | 0.000632 | 11 | 2017 | 2016-08-26 | C | 1 | 0.000632 | 3.0035e-06
1 | 13235929 | 2016-08-26 08:33 | 2016-08-26 11:15 | 161 | 2 | 323.4667 | 0.00097156 | 0.000953 | 6.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C3178 | FUSE - ELEMENT/LINK (HV) | 2x 15 amp @ FC 2129 1 x 2amp 3197 uknown poss weather | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000953 | 11 | 2017 | 2016-08-26 | C | 2 | 0.000953 | 6.0071e-06
1 | 13236025 | 2016-08-26 08:55 | 2016-08-26 10:19 | 83 | 2 | 167.1667 | 0.0005021 | 0.000484 | 6.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 707512 | UNKNOWN | back feed for pole hit by truck which was causing voltage issues, These have now been corrected, a new back feed has been put in place to rectify this issue at pole#7075112 | F3 | ST JOHNS | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.000484 | 11 | 2017 | 2016-08-26 | C | 2 | 0.000484 | 6.0071e-06
1 | 13236123 | 2016-09-15 09:15 | 2016-09-15 14:42 | 327 | 3 | 981 | 0.0029459 | 0.002918 | 9.0089e-06 | NAPA ID:23769 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 023769 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV H139 | NONE | Change 1 x pole and 23 x 11kv xarms, Xarms to be fitted as Delta construction. Works location: Scotts Rd. WO 30031038 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.001459 | 5.5 | 2017 | 2016-09-15 | B | 3 | 0.002918 | 9.0089e-06
1 | 13236134 | 2016-09-19 09:00 | 2016-09-19 15:58 | 418 | 3 | 1254 | 0.0037656 | 0.003738 | 9.0085e-06 | NAPA ID:23770 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 023770 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV H139 | NONE | Run approximately 2kms of new Ferret conductor. Works location: Scotts Rd. WO 30031038. This job ran over because fargo sleeves kept breaking while conductor was being pulled through. | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.001869 | 5.5 | 2017 | 2016-09-19 | B | 3 | 0.003738 | 9.0085e-06
1 | 13241688 | 2016-09-22 09:15 | 2016-09-22 14:37 | 322 | 16 | 5152 | 0.01547 | 0.015326 | 4.8044e-05 | NAPA ID:23781 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 023781 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P01672 | NONE | Change 18 x new cross arms, and fit 11kV Links TEMP 82 on pole P01672. Works location: Lochmoigh Rd. WO 30031038 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.007663 | 5.5 | 2017 | 2016-09-22 | B | 16 | 0.015326 | 4.8044e-05
1 | 13241813 | 2016-08-26 10:21 | 2016-08-26 11:33 | 71 | 415 | 24065.5667 | 0.072283 | 0.068543 | 0.0012465 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 6 | UNKNOWN | CB 6 tripped on A, B & C phase O/C flags, line was patrolled and sectionalised and no fault was found, suspect line clash as is windy. | F1 | TATUANUI | PIAKO | Valley | FARMER ROAD SUB | Eastern Electricity | POWERCO | 0.068543 | 11 | 2017 | 2016-08-26 | C | 415 | 0.068543 | 0.0012465
1 | 13243408 | 2016-09-23 10:00 | 2016-09-23 12:30 | 150 | 1 | 150 | 0.00045041 | 0.000441 | 3.0027e-06 | NAPA ID:23792 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 023792 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2/13 | NONE | Isolate TX t2/13, remove transformer from pole, and change 400v hanger xarm. Works location: Te Puna South. WO 30031038 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0002205 | 5.5 | 2017 | 2016-09-23 | B | 1 | 0.000441 | 3.0027e-06
1 | 13257391 | 2016-09-26 09:25 | 2016-09-26 13:28 | 243 | 6 | 1458 | 0.0043778 | 0.004323 | 1.8016e-05 | NAPA ID:23786 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 023786 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T2/13 | NONE | Change 19 x new cross arms, and fit 3 x transformers and install 1 x pole. Works location: Te Puna Rd. WO 30031038 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0021615 | 5.5 | 2017 | 2016-09-26 | B | 6 | 0.004323 | 1.8016e-05
1 | 13257409 | 2016-09-27 09:18 | 2016-09-27 12:02 | 164 | 14 | 2296 | 0.0068939 | 0.006767 | 4.2036e-05 | NAPA ID:23793 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 023793 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV H128 | NONE | Change 7 x 11kv xarms, and trim trees. Works location: Kendalls Line. WO 30031038 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0033835 | 5.5 | 2017 | 2016-09-27 | B | 14 | 0.006767 | 4.2036e-05
1 | 13257878 | 2016-08-26 14:02 | 2016-08-26 15:05 | 62 | 3 | 188.6 | 0.00056648 | 0.000539 | 9.0107e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P18229 | FUSE - ELEMENT/LINK (HV) | Disconnection for safety - the meter to the water pump is smoking. Known outage in area Advised SMC of 999 ETA required... 5 mins 2 x 3amp fuses main sw fire | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000539 | 11 | 2017 | 2016-08-26 | C | 3 | 0.000539 | 9.0107e-06
1 | 13258000 | 2016-08-26 14:34 | 2016-08-26 15:03 | 29 | 1 | 29.2167 | 8.7755e-05 | 7.8e-05 | 3.0035e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | T3/307 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Have advised customer of the safety precautions. Schools are close and customer is concerned when the children finish school. Customer advised she is at location and to make she herself and others are 10m away from hazard. re latched door on transformer and re secured with screws | F3/F4 | COLYTON | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 7.8e-05 | 11 | 2017 | 2016-08-26 | C | 1 | 7.8e-05 | 3.0035e-06
1 | 13259334 | 2016-08-26 16:23 | 2016-08-27 00:28 | 484 | 401 | 79299.95 | 0.23818 | 0.23457 | 0.0021356 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | t#/304 need paperwork | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | When closing please check OMS 13259403 - 105 Fraser Drive Jeff report the transformer has blown up and will require replacement Replaced 3/300kVa/11 Transformer | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.23457 | 11 | 2017 | 2016-08-26 | C | 401 | 0.23457 | 0.0021356
1 | 13259359 | 2016-08-26 16:29 | 2016-08-26 17:45 | 76 | 2 | 152.2333 | 0.00045725 | 0.000439 | 6.0071e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC2420 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses FC2420. 2 X 3 amp HV fuses replaced | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.000439 | 11 | 2017 | 2016-08-26 | C | 2 | 0.000439 | 6.0071e-06
1 | 13259658 | 2016-08-26 16:39 | 2016-08-26 18:08 | 89 | 236 | 11636.1667 | 0.03495 | 0.032823 | 0.00070885 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 6 | UNKNOWN | CB 6 A/R B & C phase OC Protection analysed and back feed put in place via MABS N34 up to Recloser N21. Remianing feeder sectionalised, no fault found. Relivened OK | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.032823 | 11 | 2017 | 2016-08-26 | C | 236 | 0.032823 | 0.00070885
1 | 13260870 | 2016-08-26 18:36 | 2016-08-26 21:40 | 184 | 17 | 664.7833 | 0.0019967 | 0.001843 | 5.1061e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B30 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 6Amp HV Fuses - cause unknown. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.001843 | 11 | 2017 | 2016-08-26 | C | 17 | 0.001843 | 5.1061e-05
1 | 13262212 | 2016-08-26 20:07 | 2016-08-27 04:16 | 489 | 277 | 122814.7333 | 0.36889 | 0.36639 | 0.00083199 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 1 | NONE | Rec 9549 trip O/C ETA 20:45 Found car verse pole. Isolated between ABS SE7-020, 9760/1 & 9760/4 Replaced pole & relivened Please check OMS: 13262282 2 x poles 2 x HT arms complete 2 x LT arms complete 3 x 63amp fuse units etc NDR to come | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.36639 | 11 | 2017 | 2016-08-26 | C | 277 | 0.36639 | 0.00083199
1 | 13262450 | 2016-08-26 21:36 | 2016-08-27 01:53 | 256 | 171 | 24457.75 | 0.073461 | 0.07192 | 0.00051361 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | K1032 | CONDUCTOR - REPAIR/REHANG | Recloser 9320 L/O. Sectionalised & found fault beyound ABS IC2565. Repaired conductor & binder on pole K1032 & relivened | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.07192 | 11 | 2017 | 2016-08-26 | C | 171 | 0.07192 | 0.00051361
1 | 13263414 | 2016-08-26 22:19 | 2016-08-27 01:54 | 214 | 788 | 45183.0667 | 0.13571 | 0.12861 | 0.0023668 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 702145 | CONDUCTOR - REPAIR/REHANG | CB 6969/7 A/R, L/O. Sectionalised & Patrolled, All 3 wires in one span bought down by large pine branch. NDR# N100211 Materials used: 150mtrs of 16mm Bare CU conductor, 10x 16mm cu sleeves | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.12861 | 11 | 2017 | 2016-08-26 | C | 788 | 0.12861 | 0.0023668
1 | 13264238 | 2016-08-26 22:30 | 2016-08-27 04:55 | 384 | 1 | 384.5667 | 0.0011551 | 0.001146 | 3.0035e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | SE2-001 | FUSE - ELEMENT/LINK (HV) | 2 x 15amp HT fuse. Cause unknown. | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001146 | 11 | 2017 | 2016-08-26 | C | 1 | 0.001146 | 3.0035e-06
1 | 13266914 | 2016-08-26 22:59 | 2016-08-27 00:21 | 82 | 1235 | 50980.8 | 0.15313 | 0.142 | 0.0037094 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB 42 at Aongatete L/O Backfeed CB 1 at Kauri Point Patrolled line on way to sub, Found no fault. Reclosed CB 42. Relived Kauri Point & CB 2 High wind in area | S5 | AONGATETE42-KAURI POINT 33KV | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.142 | 33 | 2017 | 2016-08-26 | C | 1235 | 0.142 | 0.0037094
1 | 13268822 | 2016-08-26 23:30 | 2016-08-27 03:18 | 228 | 581 | 105941.6333 | 0.31821 | 0.31297 | 0.0017451 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1 | UNKNOWN | Sectionaliser 9208 L/O at 23:30 Recloser 13004 L/O at 23:45 B Phase O/C. Comms to reclose lost at 23:45 Sectionalised No fault Found | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.31297 | 11 | 2017 | 2016-08-26 | C | 581 | 0.31297 | 0.0017451
1 | 13269459 | 2016-08-26 23:48 | 2016-08-27 02:24 | 156 | 1 | 156.2 | 0.00046916 | 0.00046 | 3.0035e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 0994 | FUSE - ELEMENT/LINK (HV) | 2 x 2amp HT fuses replaced | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.00046 | 11 | 2017 | 2016-08-26 | C | 1 | 0.00046 | 3.0035e-06
1 | 13269478 | 2016-08-27 02:35 | 2016-08-27 04:34 | 119 | 35 | 4165 | 0.01251 | 0.012194 | 0.00010512 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 205430 | CONDUCTOR - REPAIR/REHANG | Found lines down beyound Fuse SC2-042. Isolated at fuses. Repaired lines & relivened | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.012194 | 11 | 2017 | 2016-08-27 | C | 35 | 0.012194 | 0.00010512
1 | 13281114 | 2016-08-27 00:24 | 2016-08-27 10:50 | 625 | 236 | 16711.6333 | 0.050194 | 0.048067 | 0.0013906 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P03773 | INSULATOR | CB 6 Trip, O/C A & B Phase. Sectionalised & Patrolled. Fault located between ABS N13 & N15 but Faultman cant get access in the dark. Suspect fault may be floating conductor at Pole P03773. Three transformers left off overnight. Isolation required between ABS N13 and N15 with backfeeds at ABS N16 and N34. Replaced a double pin insulator, rebound and relivened OK. High winds in area. | F4 | RANGIWAHIA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.048067 | 11 | 2017 | 2016-08-27 | C | 236 | 0.048067 | 0.0013906
1 | 13293886 | 2016-08-27 00:40 | 2016-08-27 04:50 | 250 | 144 | 34881.65 | 0.10477 | 0.10347 | 0.00043251 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 784044 | CONDUCTOR - REPAIR/REHANG | RS 2032 A/R, L/O, O/C A & B Phase. Sectionalised & Patrolled. Line down due to fallen tree branch. NDR# 56102 Materials used: 10mtrs conductor, 3x Tension sleeves | F2 | WATERWORKS RD | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.10347 | 11 | 2017 | 2016-08-27 | C | 144 | 0.10347 | 0.00043251
1 | 13294646 | 2016-08-27 01:19 | 2016-08-27 01:56 | 36 | 194 | 7081 | 0.021268 | 0.01952 | 0.00058269 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1 | UNKNOWN | Recloser RS9489 L/O. Patrolled No fault found | F4/F1 | APATA | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.01952 | 11 | 2017 | 2016-08-27 | C | 194 | 0.01952 | 0.00058269
1 | 13298349 | 2016-08-27 04:32 | 2016-08-27 06:43 | 131 | 873 | 97350.15 | 0.2924 | 0.28453 | 0.003364 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 784436 | UNKNOWN | CB 4 A/R, L/O. Sectionalised & Patrolled. Branch found sitting on lines. Removed with hot stick | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.28453 | 11 | 2017 | 2016-08-27 | C | 873 | 0.28453 | 0.003364
1 | 13299779 | 2016-08-27 11:33 | 2016-08-27 19:47 | 494 | 5 | 493 | 0.0014808 | 0.001435 | 3.0035e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 201282 | CONDUCTOR - REPAIR/REHANG | ( KTK2 ) Faultman report H/V line down at pole 201282 ( no danger to public ) ABS SB1 011 opened & back feed in place by closing Sectionaliser 9515 Line break cut at pole 201282 to isolate work area. ( L/V to transformer TB1 040 offloaded ) | F4 | KATIKATI | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.001435 | 11 | 2017 | 2016-08-27 | C | 5 | 0.001435 | 3.0035e-06
1 | 13299794 | 2016-08-27 05:14 | 2016-08-27 06:06 | 52 | 7 | 364 | 0.0010933 | 0.00103 | 2.1025e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | Veale Rd, McGiven Dr, Ridgewood Dr | FUSE - ELEMENT/LINK (HV) | Reload/Reliven all blown HV Fuses due to lightning strikes. Multiple Sites. Reloaded Relivened 1504 1x 8Amp HV Link, 1508 3x3Amp HV Links, See OMS 13300332: 1512 3x 3Amp HV Links | F4 | BROOKLANDS 6 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.00103 | 11 | 2017 | 2016-08-27 | C | 7 | 0.00103 | 2.1025e-05
1 | 13300332 | 2016-08-27 05:25 | 2016-08-27 06:46 | 81 | 27 | 2187.9 | 0.0065715 | 0.006328 | 8.1096e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 8430 | FUSE - ELEMENT/LINK (HV) | 3 HV fuses tripped at 1840 - Reloaded OK (6A) Lightning in area | F4 | BROOKLANDS 6 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.006328 | 11 | 2017 | 2016-08-27 | C | 27 | 0.006328 | 8.1096e-05
1 | 13301219 | 2016-08-27 07:06 | 2016-08-27 11:52 | 286 | 442 | 106593.0167 | 0.32016 | 0.31617 | 0.0013276 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | nil | UNKNOWN | ( TGA11 ) recloser 9275 tripped A, B & C Ph O/c, L/O. feeder sectionalied with no fault found, all service restored Windy conditions & rain NOTE slow response from Downers due to faultmen on stand down A Wilson advised 08:13 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.31617 | 11 | 2017 | 2016-08-27 | C | 442 | 0.31617 | 0.0013276
1 | 13302941 | 2016-08-27 07:18 | 2016-08-27 11:06 | 227 | 4 | 911.2 | 0.0027368 | 0.0027 | 1.2014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 222699 | JUMPER | Emergency switching to repair jumper at pole 222699. Isolation at fuses FP315 ( spur no back feed ). Jumper repaired all service restored. | F1/F3 | TE PUKE NORTH | TE MATAI | Tauranga | ATUAROA AVE SUB | Eastern Electricity | POWERCO | 0.0027 | 11 | 2017 | 2016-08-27 | C | 4 | 0.0027 | 1.2014e-05
1 | 13302997 | 2016-08-27 06:30 | 2016-08-27 09:23 | 173 | 122 | 21146.6667 | 0.063515 | 0.062415 | 0.00036643 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT TREE CONTACT | I32 | UNKNOWN | 8.02am advised Cindy at svs hub about poss feeder fault. CB reclosed OK on site. Suspect line clashes with trees due to gale force winds. Delays in restoration due to HUB workload - P.Barnes attending a plan fault - requested to attend feeder fault directly from NOC. | F4 | RONGOMAI | MANGAMAIRE | Manawatu | ALFREDTON SUB | Western Electricity | POWERCO | 0.062415 | 11 | 2017 | 2016-08-27 | C | 122 | 0.062415 | 0.00036643
1 | 13303434 | 2016-08-27 07:57 | 2016-08-27 14:40 | 402 | 4 | 1610.8 | 0.0048381 | 0.004802 | 1.2014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 224349 | FUSE - ELEMENT/LINK (HV) | Replaced 2 x 6 A H/V, O/H fuses at transformer TE6 048 ( trees / wind ). NDR No to follow. Repairs to L/V lines. | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.004802 | 11 | 2017 | 2016-08-27 | C | 4 | 0.004802 | 1.2014e-05
1 | 13304639 | 2016-08-27 12:20 | 2016-08-27 16:19 | 239 | 3 | 717 | 0.0021535 | 0.002126 | 9.0106e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 794665 | INSULATOR | tripping on fuses 2919 caused by a bird strike (Magpie) that had shorted out the line and caused the top of the pole to become badly burnt. Top of pole cut off with the crossarm lowered. New insulator fitted. Relivened OK. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.002126 | 11 | 2017 | 2016-08-27 | C | 3 | 0.002126 | 9.0106e-06
1 | 13304889 | 2016-08-27 08:34 | 2016-08-27 10:55 | 140 | 241 | 33884.6 | 0.10177 | 0.099602 | 0.00072386 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 4141 | UNKNOWN | Tripping on recloser CB4141 on Phase A-B-C OC. Cursory patrol carried out and CB reclosed OK. High winds, suspect clash. Some delay in restoration due to HUB workload. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.099602 | 11 | 2017 | 2016-08-27 | C | 241 | 0.099602 | 0.00072386
1 | 13305558 | 2016-08-27 08:44 | 2016-08-27 14:05 | 321 | 181 | 32807.6167 | 0.098539 | 0.096908 | 0.0010212 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13722 | BINDER | Tripping on recloser F55 on EF, OC. Feeder sectionalised / patrolled with a floating conductor found at Pole P13722. Isolation required from ABS F63. Repairs carried out with 1 binder required. Relivened OK, Super user - Unable to close job off | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.096908 | 11 | 2017 | 2016-08-27 | C | 181 | 0.096908 | 0.0010212
1 | 13306551 | 2016-08-27 10:06 | 2016-08-27 12:11 | 124 | 10 | 1245.3333 | 0.0037404 | 0.00365 | 3.0036e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | N47 | FUSE - ELEMENT/LINK (HV) | 2 HV fuses tripped at N47, Relivened OK. 10A Rating - High winds | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.00365 | 11 | 2017 | 2016-08-27 | C | 10 | 0.00365 | 3.0036e-05
1 | 13308708 | 2016-08-27 13:13 | 2016-08-27 15:56 | 163 | 239 | 20011.1833 | 0.060105 | 0.057951 | 0.00072986 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5359 | INSULATOR | Tripping on recloser 6497 on Phase A O/C, EF. Feeder sectionalised sectionalised at ABS 6151 and reclose attempted. CB Auto-reclosed successfully and brought up original flaggings. ABS 6151 closed and patrol carried out on upper / lower Stuart Rd. One HV Fuse found tripped at 6357 and 2 fuses tripped at 5859. 6357 reloaded (10A) with isolation beyond 5859 to replace a blown insulator (Conductor had also come over causing extra fuse trip. Relivened OK. 2 HT fuses replaced at 5359. | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.057951 | 11 | 2017 | 2016-08-27 | C | 239 | 0.057951 | 0.00072986
1 | 13310394 | 2016-08-27 14:57 | 2016-08-27 20:06 | 309 | 1 | 309.0167 | 0.00092815 | 0.000919 | 3.0035e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M83 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 2a HV fuses. Cause unknown. | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000919 | 11 | 2017 | 2016-08-27 | C | 1 | 0.000919 | 3.0035e-06
1 | 13315423 | 2016-08-28 06:23 | 2016-08-28 08:10 | 106 | 212 | 16775.4167 | 0.050385 | 0.048475 | 0.00063675 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - SUSPECT BIRD STRIKE | CB3 | UNKNOWN | Tripping on CB3 on Phase B-C OC. Feeder patrolled / sectionalised but all restored OK. Possible bird strike. | F4 | UNION LINE | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.048475 | 11 | 2017 | 2016-08-28 | C | 212 | 0.048475 | 0.00063675
1 | 13317516 | 2016-08-28 16:07 | 2016-08-28 21:54 | 347 | 114 | 39558 | 0.11881 | 0.11779 | 0.0003424 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | A0402 | POLE | 3.27pm advised Liane at svs hub & emailed ETA not required, Police onsite. Pole A0402 broken. Isolation at Sw/Gear IC3223 & 9899/3. Back feed via 9652/2 Mar CB 7. Pole replaced all service restored. NDR No 048269. Materials 1 x pole, 1 x L/V arm, 5 x L/V insulators, 5 X L/V fuses & bases. | F3 | CAMPBELL ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.11779 | 11 | 2017 | 2016-08-28 | C | 114 | 0.11779 | 0.0003424
1 | 13318648 | 2016-08-28 18:08 | 2016-08-28 23:40 | 331 | 208 | 25086.1333 | 0.075347 | 0.073472 | 0.00062473 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 713234 | POLE | Fire car Vs Pole 165 Tai Rd, Opunake F2140649 pole 713234 replaced with all hardware | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.073472 | 11 | 2017 | 2016-08-28 | C | 208 | 0.073472 | 0.00062473
1 | 13319174 | 2016-08-28 22:38 | 2016-08-29 01:05 | 146 | 429 | 38414.8 | 0.11538 | 0.11151 | 0.0013155 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC4901 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | ( BRD 2 ) tripped E/F, A Ph O/C, L/O Feeder sectionalised. Fault isolated to beyond recloser 9402. Patrol found trees growing through lines ( noted & defected ) & transformer TC4901 with blown H/V fuses ( likely cause ) Transformer isolated with remainder of feeder returned to service Transformer TC4901 to be tested in morning | F3/F4 | ASHWORTH ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.11151 | 11 | 2017 | 2016-08-28 | C | 429 | 0.11151 | 0.0013155
1 | 13321275 | 2016-08-29 07:50 | 2016-08-29 17:19 | 568 | 429 | 69434.2167 | 0.20854 | 0.20468 | 0.002577 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | TC4047 | SWITCH (HV) | at 07:50, Baird Rd Sub, CB 2 Ashworth St Feeder, Tripped, Ph A O/C, E/F, L/O. Feeder sectionaliser, patrols commenced. All Power Restored. at 10:46, Baird Rd Sub, CB 2 Ashworth St Feeder, Tripped, Ph A O/C, E/F, L/O. Feeder sectionalising commenced again as tripping occured while fault staff were still patrolling from original fault. Checked through 11kV Sw/gear on BRD 2 feeder. Faultmen noticed signs of burning & smell of burning at Sw/gear 9597. Sw/gear isolated at Temp Cable Break at TC3767 Source B, Sw/gear 9143/1 & 9044/3. Found that there had been a cable/cable box blow up at Sw/gear 9597/4. Backfeeds supplied from MAR3 & MAR 2: Sw/gear 9063/3 Closed, Sw/gear 9597/3 Closed. All Power Restored on Completion. DNO 160837. Please Note: Fault indicators not on SCADA but were confirmed at Sw/gear 9597 & 9594 by faultmen and were flashing. These were found when fault staff were asked to check each piece of switchgear on BRD 2. | F3/F4 | ASHWORTH ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.20468 | 11 | 2017 | 2016-08-29 | C | 429 | 0.20468 | 0.002577
1 | 13322565 | 2016-09-20 09:00 | 2016-09-20 16:02 | 422 | 90 | 37880 | 0.11375 | 0.11294 | 0.00027025 | NAPA ID:22126 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 022126 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 213160 | NONE | Replace poles ,hardware and conductor between TEMP63 & TEMP09. Install TEMP73 DOF's with solid links on pole 213160. Works location: Minden Rd. WO 30002520 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.056468 | 5.5 | 2017 | 2016-09-20 | B | 90 | 0.11294 | 0.00027025
1 | 13322665 | 2016-08-29 13:01 | 2016-08-29 14:49 | 107 | 107 | 11513.2 | 0.03458 | 0.033615 | 0.00032137 | Referral | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P38821 | POLE | Replace 11kV Pole P38821 on NDR 30796, as urgent Red Defect fault. Pole is standing but not stable. Power to go off at 1300hrs. | F2 | WORKS | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.033615 | 11 | 2017 | 2016-08-29 | C | 107 | 0.033615 | 0.00032137
1 | 13324033 | 2016-08-29 10:46 | 2016-08-29 14:55 | 249 | 64 | 15936 | 0.047863 | 0.047286 | 0.00019222 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M0408 | CROSSARM - WHOLE ASSEMBLY | at 10:46, Putaruru Sub, CB 6 Horahora Feeder. Found broken HV crossarm at Pole M0408. Isolated Lines at ABS 860 & 1314. Permit Issued & Repairs carried out. All Power restored on completion. Dandy Trimidal Attended. 9x insulators, 2x HV Crossarms & 3x Binders Replaced. Crossarm was rotten. | F2 | HORAHORA | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.047286 | 11 | 2017 | 2016-08-29 | C | 64 | 0.047286 | 0.00019222
1 | 13324244 | 2016-09-12 10:06 | 2016-09-12 15:23 | 317 | 10 | 3170 | 0.0095198 | 0.009429 | 3.0031e-05 | NAPA ID:23073 TP_LINTON GXP > TURITEA SUB > LINTON | 11 | Planned | 023073 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV H108 | NONE | Cutting trees around the 11kv. Works location: Kahuterawa Rd, Palmerston North. WO 30026291 | F2 | LINTON | LINTON | Manawatu | TURITEA SUB | Western Electricity | POWERCO | 0.0047145 | 5.5 | 2017 | 2016-09-12 | B | 10 | 0.009429 | 3.0031e-05
1 | 13324399 | 2016-09-14 09:30 | 2016-09-14 13:16 | 226 | 21 | 4746 | 0.014252 | 0.014063 | 6.3063e-05 | NAPA ID:22857 TP_MASTERTON GXP > AKURA SUB > CORADINE ST | 11 | Planned | 022857 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 1827 | NONE | Replace tx pole 1827 and hardware. Works location: Perry St, Masterton. WO 30018777 | F3 | CORADINE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0070315 | 5.5 | 2017 | 2016-09-14 | B | 21 | 0.014063 | 6.3063e-05
1 | 13324491 | 2016-09-13 08:30 | 2016-09-13 15:43 | 433 | 108 | 46782 | 0.14049 | 0.13952 | 0.00032433 | NAPA ID:23827 TP_GREYTOWN GXP > KEMPTON SUB > PONATAHI | 11 | Planned | 023827 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV CB C955 | NONE | Tree removal at multiple sites fabians road glenmorven road kempton line area. Works location: Kempton Line. WO 30026281 | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.069758 | 5.5 | 2017 | 2016-09-13 | B | 108 | 0.13952 | 0.00032433
1 | 13324941 | 2016-09-13 09:00 | 2016-09-13 15:03 | 363 | 44 | 15972 | 0.047965 | 0.047568 | 0.00013213 | NAPA ID:22954 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | 022954 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 2463 | NONE | Change single structure pole# 2463 to a two pole structure regulator site 13075. Works location: Kiwitahi Railway Rd, Morrinsville. WO 30019249 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.023784 | 5.5 | 2017 | 2016-09-13 | B | 44 | 0.047568 | 0.00013213
1 | 13324954 | 2016-08-29 16:46 | 2016-08-29 17:37 | 51 | 3 | 153 | 0.00045953 | 0.000432 | 9.0104e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 4575W - need paperwork | INSULATOR | Faultman found a blown fuse at Fuses 522 and at Fused ABS 4269, after investigation the faultman found a broken stand-off insulator on transformer 4575W, line was isolated at Fused ABS 4269 to replace stand-off insulator. 1 X 25 amp HV fuse replaced (Fused ABS 4269) 1 X 25 amp HV fuse replaced (Fuses 522) | F4 | RACECOURSE | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.000432 | 11 | 2017 | 2016-08-29 | C | 3 | 0.000432 | 9.0104e-06
1 | 13325006 | 2016-09-14 09:23 | 2016-09-14 15:30 | 367 | 44 | 16148 | 0.048493 | 0.048096 | 0.00013213 | NAPA ID:22955 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | 022955 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 2463 | NONE | Change single structure pole# 2463 to a two pole structure regulator site 13075. Works location: Kiwitahi Railway Rd, Morrinsville. WO 30019249 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.024048 | 5.5 | 2017 | 2016-09-14 | B | 44 | 0.048096 | 0.00013213
1 | 13325014 | 2016-09-14 08:45 | 2016-09-14 15:30 | 405 | 67 | 27135 | 0.081487 | 0.080883 | 0.0002012 | NAPA ID:23833 TP_GREYTOWN GXP > KEMPTON SUB > PONATAHI | 11 | Planned | 023833 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV ABS S518 | NONE | Urgent tree removal at multiple sites between S518 S521 along Ponatahi road. Works location: Ponatahi Rd. WO 30026281 | F4 | PONATAHI | GREYTOWN | Wairarapa | KEMPTON SUB | Western Electricity | POWERCO | 0.040441 | 5.5 | 2017 | 2016-09-14 | B | 67 | 0.080883 | 0.0002012
1 | 13325087 | 2016-09-11 08:31 | 2016-09-11 13:45 | 314 | 21 | 6599.95 | 0.01982 | 0.019631 | 6.3065e-05 | NAPA ID:22858 TP_MASTERTON GXP > AKURA SUB > CORADINE ST | 11 | Planned | 022858 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 1531 | NONE | replace tx pole 1531 and hardware. Works location: Lincoln Rd, Masterton. WO 30018777 | F3 | CORADINE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0098155 | 5.5 | 2017 | 2016-09-11 | B | 21 | 0.019631 | 6.3065e-05
1 | 13325634 | 2016-09-16 08:45 | 2016-09-16 14:51 | 366 | 14 | 5124 | 0.015387 | 0.01526 | 4.2041e-05 | NAPA ID:23853 TP_TE MATAI GXP > PAENGAROA SUB > ROYDEN DOWNS RD | 11 | Planned | 023853 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 228703 | NONE | Replace poles and arms. Install TEMP ABS 23 for remaining shutdowns to reconductor feeder. Works location: Royden Downs Rd. WO 30017837. | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.00763 | 5.5 | 2017 | 2016-09-16 | B | 14 | 0.01526 | 4.2041e-05
1 | 13327578 | 2016-09-19 09:15 | 2016-09-19 14:56 | 341 | 53 | 18073 | 0.054271 | 0.053793 | 0.00015915 | NAPA ID:23948 TP_WANGANUI GXP > WANGANUI EAST SUB > NO 3 LINE | 11 | Planned | 023948 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 790818 | NONE | Replace broken X arms on pole Structure 790818, also replace lightning arrestors at pole 970912 and transformer X2927. Works location: Longacre Valley Rd, Wanganui. WO 30030920 | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.026897 | 5.5 | 2017 | 2016-09-19 | B | 53 | 0.053793 | 0.00015915
1 | 13327731 | 2016-09-20 08:45 | 2016-09-20 14:22 | 337 | 6 | 2022 | 0.0060717 | 0.006017 | 1.8017e-05 | NAPA ID:23856 TP_TE MATAI GXP > PAENGAROA SUB > ROYDEN DOWNS RD | 11 | Planned | 023856 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole 269007 | NONE | REPLACE POLES AND ARMS RECON FEEDER. Works location: Royden Downs Rd. WO 30017837 | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.0030085 | 5.5 | 2017 | 2016-09-20 | B | 6 | 0.006017 | 1.8017e-05
1 | 13327767 | 2016-08-30 08:49 | 2016-08-30 09:02 | 13 | 2046 | 22672.5667 | 0.068096 | 0.04966 | 0.006145 |  | 33 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE |  | CABLE - REPLACE LESS THAN 5 METRES | 30/06/16 * 0848hrs. 33kV tripping of the following 33kV CB's MAI Z130, PAS W130 and KAR Z40 (one circuit) * Also tripped BPE CB 2232 (currently open ended due to cable fault past ABS Z25, DNO 160835) * Also tripped BPE 2242 and MIL Z70. * Various protection flags across CB's. Combination of differential and O/C notifications. * Resulted in MIL sub going to N security * Loss of supply to MAI T2 side of BUS MAI (currently reconfigured due to oil cable issue) to feeders 21, 23, 24, 26, approx. 2160 ICP's on F2/F3 feeder types. * LOS to Injection plant (on BPE 2232) * Ken Pattie, Downers, NOC management and Chris Norman notified immediately. * 0902hrs, NOC reconfigured network to re-liven feeders 21, 23, 24, 26 back via usual network configuration, taking approx. 14 minutes to reinstate all load to affected (ICP's) customers. * Downers dispatched to strategic parts of network to investigate network assets. * A dead Magpie was located on four pole structure P42292, 93, 94, 99. (adjacent to Z64) * Inspection confirmed this to be the cause of the outage from a visual aspect. * Powerco engineering requested Cables to be tested prior to re-livening. * Downer notify Powerco, unable to test BPE 2232 due to size of cables on terminations, matter discussed in detail as to correct actions required. * 1630hrs, NOC carried out contingency plan to utilise Linton GXP injection plant if BPE plant unable to be brought back online prior to night fall. Transpower advised of urgent GXP tie via LTN 1182 to BPE 2252. Powerco advise Trustpower to place all TWP turbines into standby mode with the expectation of an hour long outage to allow Powerco to manage network and injection signals, Kathy Thomas advised due to commercial impact on Trustpower. Note: TWP total load approx 100 Amps at time. * 1742hrs this contingency was not required, NOC advised Trustpower to re-commence generation. * 1741hrs, BPE 2232 re-closed successfully, in turn, BPE injection plant brought back online successfully. * 1802hrs, PAS to MAI oil cable tested clear and brought back online successfully. * 1842hrs, Keith St sub 33kV Cable fault (from last week) between KST Z150 to ABS Z25 repairs complete, tested clear and restored to service. Thus Restored KST and MAI Sub's to N-1 security level. * BPE 2242 to MIL Z70 circuit left offline for night, leaves MIL Sub on N security. * 33kV PAS to KAR section of circuit from ABS W99 to Z64 to KAR Z40 circuit left offline for night, leaves KAR Sub on N security for the night. * Day end. 31/08/16. * 1230hrs BPE 2242 re-livened, MIL Z70 closed, MIL Sub restored to N-1 security. * 1404hrs KAR CB Z40 re-closed to overhead line successfully. ABS W99 and ABS Z37 still open& tagged and undergoing testing. * 1533hrs Oil cable between Z99 and Z37 testing complete, confirmed fault clear and returned to service successfully. * Downers to provide Powerco with all test results as per Mike Whaley?s request. All work complete. Safety Manager Number 655030 to cover event. End NOC Note: Fiona, please expect a considerable amount of data from Downers for this event, please let me know if any assistance is required to clarify, AW | F2 | MAIN ST 24 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 0.04966 | 33 | 2017 | 2016-08-30 | C | 2046 | 0.04966 | 0.006145
1 | 13330218 | 2016-09-21 09:30 | 2016-09-21 11:53 | 143 | 8 | 1144 | 0.0034352 | 0.003363 | 2.4022e-05 | NAPA ID:23860 TP_TE MATAI GXP > PAENGAROA SUB > ROYDEN DOWNS RD | 11 | Planned | 023860 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 228703 | NONE | REPLACE POLES AND ARMS RECON FEEDER. Works location: Royden Downs Rd. WO 30017837 | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.0016815 | 5.5 | 2017 | 2016-09-21 | B | 8 | 0.003363 | 2.4022e-05
1 | 13330349 | 2016-08-30 09:59 | 2016-08-30 12:02 | 122 | 431 | 21020.9 | 0.063135 | 0.059251 | 0.0005226 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB XT40 A/R & ALF CB I23 Tripped HLT applied to CB I23 due to PON Sub upgrade. 33kv & 11kv Lines patrolled with no fault found | S3 | PARKVILLE-ALFREDTON 33KV | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.059251 | 33 | 2017 | 2016-08-30 | C | 431 | 0.059251 | 0.0005226
1 | 13331453 | 2016-09-22 09:15 | 2016-09-22 14:54 | 339 | 6 | 2034 | 0.0061076 | 0.006053 | 1.8016e-05 | NAPA ID:23861 TP_TE MATAI GXP > PAENGAROA SUB > ROYDEN DOWNS RD | 11 | Planned | 023861 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 228703 | NONE | REPLACE POLES AND ARMS RECON FEEDER. Works location: Royden Downs Rd. WO 30017837 | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.0030265 | 5.5 | 2017 | 2016-09-22 | B | 6 | 0.006053 | 1.8016e-05
1 | 13331576 | 2016-09-28 09:30 | 2016-09-28 14:34 | 304 | 8 | 2432 | 0.0073022 | 0.00723 | 2.402e-05 | NAPA ID:23863 TP_TE MATAI GXP > PAENGAROA SUB > ROYDEN DOWNS RD | 11 | Planned | 023863 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 228703 | NONE | REPLACE POLES AND ARMS RECON FEEDER. Works location: Royden Downs Rd. WO 30017837 | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.003615 | 5.5 | 2017 | 2016-09-28 | B | 8 | 0.00723 | 2.402e-05
1 | 13332502 | 2016-09-20 08:30 | 2016-09-20 15:40 | 429 | 70 | 29889.5 | 0.089753 | 0.089122 | 0.0002102 | NAPA ID:22817 TP_MASTERTON GXP > AKURA SUB > CORADINE ST | 11 | Planned | 022817 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 831049 | NONE | cut 11kv jumpers at pole 831049 live line to limit outage area for replacement of tx pole t880 and hardware,on completion re-instatement of 11kv jumpers live line. Works location: Bentley St, Masterton. WO 30018777 | F3 | CORADINE ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.044561 | 5.5 | 2017 | 2016-09-20 | B | 70 | 0.089122 | 0.0002102
1 | 13332710 | 2016-08-30 09:00 | 2016-08-30 13:01 | 241 | 2 | 482 | 0.0014477 | 0.001429 | 6.0068e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | ADVERSE ENVIRONMENT | ADVERSE ENVIRONMENT - LAND SLIPPAGE | 832302 | POLE | Fuses 7851 were opened as transformer T2127 is falling into the sea, this was isolated under the request from Gavin Paget ( Powerco Project Manager 027 230 3514).Transformer will have to be moved, Gavin is in contact with the customer as to what will happen next. Fuses will remain open until transformer is moved. Inquires contact Gavin. Pole and transformer have been relocated and service restored. | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.001429 | 11 | 2017 | 2016-08-30 | C | 2 | 0.001429 | 6.0068e-06
1 | 13332793 | 2016-09-13 09:16 | 2016-09-13 12:24 | 188 | 50 | 9400 | 0.028229 | 0.027778 | 0.00015015 | NAPA ID:23976 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > 18TH AVE | 11 | Planned | 023976 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TD4-511 | NONE | change transformer SD4-345. Works location: Baycroft Ave, Tauranga. WO 30019815 | F2 | 18TH AVE | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 0.013889 | 5.5 | 2017 | 2016-09-13 | B | 50 | 0.027778 | 0.00015015
1 | 13332881 | 2016-09-20 09:00 | 2016-09-20 12:30 | 210 | 91 | 19110 | 0.057384 | 0.056564 | 0.00027326 | NAPA ID:22352 TP_BUNNYTHORPE GXP > MILSON SUB > TE ARAKURA | 11 | Planned | 022352 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | P36746 | NONE | Replace 11KV pole hit by Vehicle. Works location: Hwy 3, Palmerston North. WO 30015151 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.028282 | 5.5 | 2017 | 2016-09-20 | B | 91 | 0.056564 | 0.00027326
1 | 13332909 | 2016-09-23 09:55 | 2016-09-23 13:50 | 235 | 2 | 470 | 0.0014113 | 0.001393 | 6.0054e-06 | NAPA ID:23523 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 023523 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses TC2137 | NONE | LLP: To install a third 11kV D.O.Fuse. AP: To upgrade TC2137 to a 3 phase 30kVA. Works location: Endowment Rd, Te Aroha. WO 30031570 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.0006965 | 5.5 | 2017 | 2016-09-23 | B | 2 | 0.001393 | 6.0054e-06
1 | 13332918 | 2016-08-30 14:37 | 2016-08-30 14:55 | 18 | 38 | 684 | 0.0020544 | 0.001711 | 0.00011413 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P26267 | CROSSARM - WHOLE ASSEMBLY | During line Patrol Pole Tech found faulty Crossarm at pole P26267. 2R- Repair/Replace King Bolt & Crossarm- Please Assign Phil Barnes Line was isolated at ABS's S27 & S44 to repair kingpin on pole P26267. 2 x nuts used | F4 | KONINI | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.001711 | 11 | 2017 | 2016-08-30 | C | 38 | 0.001711 | 0.00011413
1 | 13333307 | 2016-09-21 09:11 | 2016-09-21 13:40 | 268 | 2 | 537.8333 | 0.001615 | 0.001596 | 6.0055e-06 | NAPA ID:23130 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 023130 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7454 | NONE | Replace 11kv poles. Works location: WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000798 | 5.5 | 2017 | 2016-09-21 | B | 2 | 0.001596 | 6.0055e-06
1 | 13333536 | 2016-08-30 16:18 | 2016-08-30 21:21 | 303 | 40 | 12093.4 | 0.036322 | 0.035961 | 0.00012014 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | N12528 | FUSE - ELEMENT/LINK (HV) | Called through to SMC - Tallia Generator on, all power restored Will return tomorrow (31/08) to sort cable fault. Cable past fuses FC796 faulted Bloue phase down to Earth. Generator connected to Transformer TC3432 @ 2121 hours. DNO 160839 Created for cable repairs Need confirmation from fault man of which transformer this customer is fed from... Dean called and advised he has an Emergency LV shutdown as they need to get through the LV to access the HV and repair a cable. Emergency LV notice done for an hour, Dean will call when it is complete. 1.15 FM called and advised needs another Emergency LV shutdown as they need to get through the LV to access the HV and repair a cable. Emergency LV notice done for an hour, FM will call when it is complete. | F3 | SHAW AVE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.035961 | 11 | 2017 | 2016-08-30 | C | 40 | 0.035961 | 0.00012014
1 | 13335509 | 2016-08-30 21:00 | 2016-08-30 23:15 | 135 | 1 | 135.4667 | 0.00040687 | 0.000397 | 3.0034e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 853921 | FUSE - ELEMENT/LINK (HV) | 2x6amp Fuses at FP892 blown, line patrolled no fault found reloaded & livened. | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000397 | 11 | 2017 | 2016-08-30 | C | 1 | 0.000397 | 3.0034e-06
1 | 13335725 | 2016-08-31 05:31 | 2016-08-31 12:30 | 419 | 1065 | 45565.2667 | 0.13685 | 0.12726 | 0.00080191 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 384023 | POLE | Car vs Pole opposite 237 Ngatai Rd, Reported Brian Sperling from Downers CB 4 A/R No Flags Brian called he is going to isolate at TX tc4-026 pull LV fuses for 5 hours Email sent out with list of ICPs to retailer Pole in and HV reconnected, just installing a crossarm that was also damaged on an adjacent pole then will close. ETR approx 2.00pm | F3 | BURETA RD | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 0.12726 | 11 | 2017 | 2016-08-31 | C | 1065 | 0.12726 | 0.00080191
1 | 13337057 | 2016-08-31 07:42 | 2016-08-31 09:18 | 96 | 1 | 96.3333 | 0.00028933 | 0.00028 | 3.0034e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8164 | FUSE - ELEMENT/LINK (HV) | Replaced 2x 10a HV fuses | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.00028 | 11 | 2017 | 2016-08-31 | C | 1 | 0.00028 | 3.0034e-06
1 | 13337197 | 2016-09-22 09:00 | 2016-09-22 15:40 | 400 | 32 | 12800 | 0.038435 | 0.038146 | 9.6088e-05 | NAPA ID:23126 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 023126 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7457 | NONE | Replace 11kv poles and crossarms. Works location: Lennies Rd, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.019073 | 5.5 | 2017 | 2016-09-22 | B | 32 | 0.038146 | 9.6088e-05
1 | 13352097 | 2016-08-31 14:30 | 2016-08-31 18:11 | 221 | 5 | 1105 | 0.0033188 | 0.003273 | 1.5017e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TC1438 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Check 3385 State Highway 1 is related, OMS 13352533 Replacement Transformer Required. 50kVA/3 Ph/11kV Transformer replaced along with seismic bracket & associated hardware. | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.003273 | 11 | 2017 | 2016-08-31 | C | 5 | 0.003273 | 1.5017e-05
1 | 13352624 | 2016-09-26 09:00 | 2016-09-26 14:15 | 315 | 13 | 4095 | 0.012296 | 0.012178 | 3.9034e-05 | NAPA ID:23125 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 023125 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 8084 | NONE | Replace 11kv poles. Works location: Loopline Rd, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.006089 | 5.5 | 2017 | 2016-09-26 | B | 13 | 0.012178 | 3.9034e-05
1 | 13357443 | 2016-09-15 09:30 | 2016-09-15 14:33 | 303 | 244 | 73932 | 0.22202 | 0.21982 | 0.00073273 | NAPA ID:23985 TP_KOPU GXP > WHITIANGA SUB > KUAOTUNU | 11 | Planned | 023985 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV CFC SDAF3 | NONE | Replace SDAF3 Switch with CFC Safelink, and reterminate pothead at pole 248572 concurrently for DNO160819. Works location: Black Jack Rd, Whitianga. WO 30032127 | F3 | KUAOTUNU | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.10991 | 5.5 | 2017 | 2016-09-15 | B | 244 | 0.21982 | 0.00073273
1 | 13362793 | 2016-09-01 09:47 | 2016-09-01 09:59 | 11 | 171 | 2014.95 | 0.0060517 | 0.00451 | 0.00051358 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - PROTECTION SETTINGS - INCORRECT/ERROR | 9320 | UNKNOWN | RS 9320 Trip, No flags. This occured whilst the Recloser was being bypassed under Live Line Permit. E/F Protection disabled & Recloser 9320 closed on site. Live Line work then recommenced. | F4 | MANGATEPARU | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.00451 | 11 | 2017 | 2016-09-01 | C | 171 | 0.00451 | 0.00051358
1 | 13367341 | 2016-09-01 20:00 | 2016-09-02 06:04 | 604 | 8 | 4832 | 0.014512 | 0.01444 | 2.4027e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | SB2-034 | CABLE - REPAIR | Cable fault located & repaired between fuses SB2-034 & transformer TB2-081. Materials required 1 x 25mm repair kit, 1 x zip sleeve, 2 x 6amp HV fuses. All supply restored. | F3/F4 | WILLS RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.01444 | 11 | 2017 | 2016-09-01 | C | 8 | 0.01444 | 2.4027e-05
1 | 13371199 | 2016-09-01 23:31 | 2016-09-02 00:53 | 81 | 241 | 15533.45 | 0.046653 | 0.044481 | 0.00072382 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 807423 | UNKNOWN | Recloser 4141 Trip on Ph A & B OC. Lines patrolled but nothing found. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.044481 | 11 | 2017 | 2016-09-01 | C | 241 | 0.044481 | 0.00072382
1 | 13372141 | 2016-09-02 06:09 | 2016-09-02 07:22 | 73 | 1 | 73.4167 | 0.0002205 | 0.000211 | 3.0033e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | C14095 | FUSE - ELEMENT/LINK (HV) | Reload at Fuses FC4233 - Fuses will not operate on e-MAP - TC5780 has no ICP's 2 x 6A Bird strike | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000211 | 11 | 2017 | 2016-09-02 | C | 1 | 0.000211 | 3.0033e-06
1 | 13372815 | 2016-09-02 09:50 | 2016-09-02 11:10 | 80 | 1 | 80 | 0.00024027 | 0.000231 | 3.0033e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TP2144 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer leaking oil Replaced transformer TP2144, Own SIS & AP | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.000231 | 11 | 2017 | 2016-09-02 | C | 1 | 0.000231 | 3.0033e-06
1 | 13374150 | 2016-09-02 12:18 | 2016-09-02 12:30 | 12 | 2 | 24.5 | 7.3582e-05 | 5.5e-05 | 6.0067e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 217757 | FUSE - ELEMENT/LINK (HV) | Farmer reported direct to John Peters Northpower, advises 2 x DDOs down on spur line on this property John was working on property 029 771 0302 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 5.5e-05 | 11 | 2017 | 2016-09-02 | C | 2 | 5.5e-05 | 6.0067e-06
1 | 13374599 | 2016-09-22 09:00 | 2016-09-22 16:23 | 443 | 14 | 6202 | 0.018623 | 0.018496 | 4.2039e-05 | NAPA ID:22664 TP_TAURANGA 33 GXP > BETHLEHEM SUB > WAIPUNA | 11 | Planned | 022664 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-141 | NONE | Replace poles ,hardware and conductor between SD3-141 & TEMP 73. Works location: Minden Rd. WO 30002520 | F4 | WAIPUNA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.009248 | 5.5 | 2017 | 2016-09-22 | B | 14 | 0.018496 | 4.2039e-05
1 | 13375036 | 2016-09-22 09:02 | 2016-09-22 14:22 | 320 | 5 | 1600 | 0.0048044 | 0.004759 | 1.5014e-05 | NAPA ID:22011 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 022011 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE3-026 | NONE | First shutdown on spurline down into McClarens falls park. Re-conductoring first section 817mtrs. Works location: McClarens Falls Rd. WO 30017842 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0023795 | 5.5 | 2017 | 2016-09-22 | B | 5 | 0.004759 | 1.5014e-05
1 | 13375059 | 2016-09-27 09:05 | 2016-09-27 15:46 | 401 | 2 | 802 | 0.0024081 | 0.00239 | 6.0051e-06 | NAPA ID:22014 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 022014 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE3-066 | NONE | Shutdown on spurline down into McClarens falls park. Second phase of pole and Hardware replacement. Works location: McClarens Falls Rd. WO 30017842 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001195 | 5.5 | 2017 | 2016-09-27 | B | 2 | 0.00239 | 6.0051e-06
1 | 13375072 | 2016-09-29 09:06 | 2016-09-29 11:58 | 172 | 2 | 344 | 0.0010329 | 0.001014 | 6.0049e-06 | NAPA ID:22016 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 022016 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | SE3-066 | NONE | Last Shutdown on spur line down into McClarens falls park. Re-conductor 721mtrs on last section. Works location: McClarens Falls Rd. WO 30017842 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000507 | 5.5 | 2017 | 2016-09-29 | B | 2 | 0.001014 | 6.0049e-06
1 | 13375359 | 2016-09-02 16:45 | 2016-09-02 20:04 | 199 | 8 | 1592 | 0.0047814 | 0.004709 | 2.4027e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 929 OLD COACH ROAD | POLE | Car vs Pole. Tried calling customer who is onsite to advise safety precaution - no answer. Pete 0278105125 3:07pm ETA 20 mins Isolated between Sw/Gear SE7-049, ABS SE7-011, SE7-013, CB1 & CB2. Backfeed rest or area Replaced broken pole & re-livened Materials required - 1 x 11m busck pole, 3 x HV crossarms & associated hardware, 1 x LV crossarm and hardware | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.004709 | 11 | 2017 | 2016-09-02 | C | 8 | 0.004709 | 2.4027e-05
1 | 13376238 | 2016-09-02 17:38 | 2016-09-02 22:22 | 284 | 59 | 16756 | 0.050324 | 0.049792 | 0.0001772 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 710275 | POLE | Car vs Pole. Pole requires replacement. Work area isolated at Fuses 5555. Replaced pole 710275 and hardware NDR to follow in the morning nDR n100217 | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.049792 | 11 | 2017 | 2016-09-02 | C | 59 | 0.049792 | 0.0001772
1 | 13376362 | 2016-09-02 17:57 | 2016-09-02 21:01 | 184 | 17 | 3132.8167 | 0.009409 | 0.009255 | 5.1057e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | D4 | FUSE - ELEMENT/LINK (HV) | (pls check OMS13376345) 422 Kairanga Bunnythorpe Road also has part power - and is flickering as well) replaced 2x 10 a HV fuses @ D4 | F4 | TE ARAKURA | BUNNYTHORPE | Manawatu | MILSON SUB | Western Electricity | POWERCO | 0.009255 | 11 | 2017 | 2016-09-02 | C | 17 | 0.009255 | 5.1057e-05
1 | 13376778 | 2016-09-02 20:53 | 2016-09-02 22:36 | 103 | 219 | 17308.2667 | 0.051983 | 0.050009 | 0.00065774 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | R11 | UNKNOWN | CB R11 Eltham sub tripped to L/O E/F line sectionalised and cursorary patrol caried out with nothing obvious found. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.050009 | 11 | 2017 | 2016-09-02 | C | 219 | 0.050009 | 0.00065774
1 | 13377447 | 2016-09-03 16:45 | 2016-09-03 18:05 | 80 | 6 | 480 | 0.0014416 | 0.001387 | 1.802e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | X2014 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Replaced 1x 5a fuse @ 637 and found faulty bushing on transformer X2014 after repairs found transformer faulty and will replace in daylight. 1 X 15 kVA transformer replaced. | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.001387 | 11 | 2017 | 2016-09-03 | C | 6 | 0.001387 | 1.802e-05
1 | 13377611 | 2016-09-03 02:22 | 2016-09-03 16:31 | 849 | 697 | 64020.2667 | 0.19227 | 0.18599 | 0.0020933 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | P19915 | POLE | Car vs pole section between ABS Q52 , Q53 , Q54 & Q78 isolated and supply restored to balance of feeder. Repairs to be carried out in the morning due to extent of damage and location also suspect some damage to customers equipment. No 81366 SH 2 safety disconnected - A10468. No. 81284 SH 2 safety disconnected - A10467. 5/09: pillar box replaced today, tx T7-491. All work as consequence of NDR 35343 - line clash affecting 8 properties, 6 which sustained damage. Only 81366 SH 2 remains off now waiting on electrical work to be completed. | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.18599 | 11 | 2017 | 2016-09-03 | C | 697 | 0.18599 | 0.0020933
1 | 13379164 | 2016-09-03 09:10 | 2016-09-03 10:25 | 75 | 26 | 1950 | 0.0058565 | 0.005622 | 7.8087e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36131 | JUMPER | Faultman found a burnt 11KV jumper at Fuses B20 on pole P36131, line was isolated at Fuses B20 to repair the jumper, transformer T1/420, 400V fuses were also isolated as it's 400V was alive in the work area where faultman need to access trhe Fuses B20. 1 x 1meter of 25mm copper jumper used | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.005622 | 11 | 2017 | 2016-09-03 | C | 26 | 0.005622 | 7.8087e-05
1 | 13379238 | 2016-09-03 07:26 | 2016-09-03 09:02 | 96 | 967 | 92161.1667 | 0.27679 | 0.26808 | 0.0029042 |  | 33 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 3139/2 | UNKNOWN | CB C885 auto reclosed on B phase O/C flags, Reclosers 3139/2 & 3141/2 both tripped on B phase O/C & E/F flags, line was sectionalised and supply restored, NOC requested faultman carry out rapid patrol of the rest of the line. Line was patrolled and no fault was found. | S2 | FEATHERSTON 33KV | GREYTOWN | Wairarapa | TP_GREYTOWN | Western Electricity | POWERCO | 0.26808 | 33 | 2017 | 2016-09-03 | C | 967 | 0.26808 | 0.0029042
1 | 13383142 | 2016-09-03 13:25 | 2016-09-03 19:44 | 379 | 525 | 103025.8167 | 0.30942 | 0.30469 | 0.0015768 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | IC3160 | CABLE - REPLACE LESS THAN 5 METRES | CB 8 L/O E/F & O/C. Sectionalised and found fault between IC 3160 & transformer TC4874 Isolated cable & restored power | F1/F3 | KENNEDY DRIVE | HINUERA | Valley | PUTARURU SUB | Eastern Electricity | POWERCO | 0.30469 | 11 | 2017 | 2016-09-03 | C | 525 | 0.30469 | 0.0015768
1 | 13385718 | 2016-09-04 10:39 | 2016-09-04 17:18 | 398 | 219 | 27111.7167 | 0.081425 | 0.079451 | 0.0016338 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738106 | INSULATOR | Tripping on Eltham CB R11 on EF. Feeder patrolled aqnd sectionalised with fault proving very difficult to locate. A dead Magpie was removed from ABS 12044 but proved not to be he fault. Similar result when 2 damaged insulators were replaced on Pukengahu Rd (Pole 738098). A further broken insulator was replaced at Pole 739430 and feeder restored OK. Part backfeed at ABS 6034 with isolation required from Fuses 6114 to carryout repairs. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.079451 | 11 | 2017 | 2016-09-04 | C | 219 | 0.079451 | 0.0016338
1 | 13385963 | 2016-09-04 10:51 | 2016-09-04 13:00 | 128 | 2 | 257.1667 | 0.00077235 | 0.000754 | 6.0066e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 217312 | FUSE - ELEMENT/LINK (HV) | Replace 3 x 6A H/V O/H fuses at fuses SE2 014 ( unknown ) | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.000754 | 11 | 2017 | 2016-09-04 | C | 2 | 0.000754 | 6.0066e-06
1 | 13386612 | 2016-09-04 16:51 | 2016-09-04 18:17 | 85 | 19 | 1627.35 | 0.0048874 | 0.004716 | 5.7063e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 739430 | JUMPER | Isolation required from Fuses 4973 to replace a broken binder. (Caused some burning on crossarm). Relivened OK. | F4 | HUIROA | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.004716 | 11 | 2017 | 2016-09-04 | C | 19 | 0.004716 | 5.7063e-05
1 | 13387581 | 2016-09-05 07:30 | 2016-09-05 12:45 | 315 | 3 | 945 | 0.0028381 | 0.002811 | 9.0098e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X2199 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | 1 HT fuses 6A replaced at 957. Defective Transformer at X2199 to be changed. Transformer Changed during day with off time 07:30, On 12:45- | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.002811 | 11 | 2017 | 2016-09-05 | C | 3 | 0.002811 | 9.0098e-06
1 | 13387610 | 2016-09-05 06:03 | 2016-09-05 12:49 | 406 | 155 | 36324.3333 | 0.10909 | 0.10769 | 0.00053458 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 760840 | INSULATOR | at 06:02, McKee Sub, CB A11 Tripped, Ph A O/C, E/F, L/O. Faultmen dispatched & investigation began. Found blown lightning arrestor at Pole 760698. Isolated lines at ABS 12037 & 5130. Permit issued & repairs carried out - lightning arrestor cut away. Attempted to reliven and feeder tripped again. Backfeed supplied from Waitara East CB U30: ABS 12037 Open, ABS 5166 Closed. Sectionalised/Patrolled feeder. Found blown insulator at Pole 760840. Isolated Lines at ABS 5129. Permit issued & repairs carried out. All Power Restored on Completion. 1x Insulator & 1x Binder Replaced at Pole 760840. No Materials Used at Pole 760698. Unsure if this is 2R work. | F5 | OTARAOA RD | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 0.10769 | 11 | 2017 | 2016-09-05 | C | 155 | 0.10769 | 0.00053458
1 | 13388730 | 2016-09-05 07:40 | 2016-09-05 10:15 | 154 | 4 | 618.2 | 0.0018566 | 0.00182 | 1.2013e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 759746 | FUSE - ELEMENT/LINK (HV) | 3 x 6amp unklmown | F4 | BRISTOL RD | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.00182 | 6.6 | 2017 | 2016-09-05 | C | 4 | 0.00182 | 1.2013e-05
1 | 13389041 | 2016-09-05 08:39 | 2016-09-05 10:00 | 80 | 28 | 2257.2667 | 0.0067792 | 0.006526 | 8.4092e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 211421 | FUSE - ELEMENT/LINK (HV) | Check 386 CAMBRIDGE ROAD OMS 13389936 is related, and 390 Cambridge OMS 13390348 2 x 8amp fuses incorrect fuse size | F3 | BETHLEHEM | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.006526 | 11 | 2017 | 2016-09-05 | C | 28 | 0.006526 | 8.4092e-05
1 | 13390075 | 2016-09-28 09:24 | 2016-09-28 14:54 | 329 | 9 | 2965.95 | 0.0089054 | 0.008824 | 2.7023e-05 | NAPA ID:23136 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 023136 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FC2162 | NONE | AP: To complete line maintenance between FC2162 and end of line. LLP: to replace 11kV fuses FC2162. Works location: Campbell Rd. WO 30017829 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.004412 | 5.5 | 2017 | 2016-09-28 | B | 9 | 0.008824 | 2.7023e-05
1 | 13390721 | 2016-09-05 10:20 | 2016-09-05 13:08 | 168 | 1 | 168 | 0.00050455 | 0.000495 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T2597 | CROSSARM - WHOLE ASSEMBLY | An outage was required (Isolate Transformer T2597) on Cameron Rd to replace a broken double crossarm. This was to be part of a planned outage on 6/9/16 but considered urgent. (ELECTRIX Contractors) | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.000495 | 11 | 2017 | 2016-09-05 | C | 1 | 0.000495 | 3.0032e-06
1 | 13390987 | 2016-09-05 10:55 | 2016-09-05 14:11 | 195 | 185 | 14106.45 | 0.042366 | 0.040698 | 0.0010481 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P13722 | BINDER | Tripping on Recloser F55 on Phase A-B OC. Feeder patrolled / sectionalised with a floating conductor found at Pole P13722 (Isolation at ABS F63). All 3 binders replaced and livened OK. (Insulators all good). | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.040698 | 11 | 2017 | 2016-09-05 | C | 185 | 0.040698 | 0.0010481
1 | 13391405 | 2016-09-05 11:50 | 2016-09-05 15:51 | 240 | 1 | 240.9333 | 0.00072359 | 0.000714 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21616 | FUSE - ELEMENT/LINK (HV) | 3 x3 amp fuse m83 high winds | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000714 | 11 | 2017 | 2016-09-05 | C | 1 | 0.000714 | 3.0032e-06
1 | 13391421 | 2016-09-05 11:54 | 2016-09-05 13:00 | 66 | 23 | 1520.6833 | 0.004567 | 0.004359 | 6.9075e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P44069 | FUSE - ELEMENT/LINK (HV) | Please check 13391605 - 634 Hall Block Road 2x 15 amp unknown | F4 | MANGATAINOKA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.004359 | 11 | 2017 | 2016-09-05 | C | 23 | 0.004359 | 6.9075e-05
1 | 13391658 | 2016-09-05 22:03 | 2016-09-06 00:46 | 162 | 112 | 17231.2 | 0.05175 | 0.050741 | 0.00067274 | NAPA ID:24246 TP_HINUERA GXP > BROWNE STREET SUB > ELIZABETH ST | 11 | Planned | 024246 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | TC3806 | CABLE - REPAIR | Investigate and repair cable terminations to 11kV SwGear 9591/2. Inspectes 11kV cable terms, cleaned , replaced earths, tested & returned to service | F3 | ELIZABETH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.025371 | 5.5 | 2017 | 2016-09-05 | B | 112 | 0.050741 | 0.00067274
1 | 13392022 | 2016-09-05 15:52 | 2016-09-05 16:10 | 18 | 4 | 72 | 0.00021624 | 0.00018 | 1.2013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H12584 | JUMPER | at 15:52, Waharoa Sub, CB 3 Factory Rd Feeder. Faultman attended part power/flickering power job. Found blown jumper at ABS 1224. Decision was made to complete work using live line techniques due to heavy industrial area and also due to live line crew working closing by. Isolated Lines at ABS 1224. Jumper repaired and all power restored on completion. Malcolm Shields Attended. 1x Conductor Joint replaced. Pole H12584 Marty left site 16:12, glove & barrier crew still onsite | F3 | FACTORY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.00018 | 11 | 2017 | 2016-09-05 | C | 4 | 0.00018 | 1.2013e-05
1 | 13392058 | 2016-09-27 09:00 | 2016-09-27 09:57 | 56 | 41 | 2306.9333 | 0.0069267 | 0.006557 | 0.00012311 | NAPA ID:21612 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | 021612 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole 367388 | NONE | isolation of 11 kv line for treecape , work area between pole 367388 to 842169. Works location: Turakina Valley Rd, Papanui Junction. WO 30026271 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0032785 | 5.5 | 2017 | 2016-09-27 | B | 41 | 0.006557 | 0.00012311
1 | 13392423 | 2016-09-05 15:09 | 2016-09-05 15:21 | 12 | 362 | 4591.3667 | 0.013789 | 0.010527 | 0.0010872 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 732204 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, NOT ALL PHASES | 1R Check for safety - Lines down across driveway, fire services not attending. F2144915 Attempted hazard process but went straight to voicemail Advised control and SMC of 999 network line down, pulled neutral up and re secured using 2x sleeves and 2 meters of conductor, OH due to age. | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.010527 | 11 | 2017 | 2016-09-05 | C | 362 | 0.010527 | 0.0010872
1 | 13396275 | 2016-09-06 00:29 | 2016-09-06 04:39 | 249 | 451 | 41928.4667 | 0.12592 | 0.12186 | 0.0013545 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 200498 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, NOT ALL PHASES | BHM CB2 tripped E/F, L/O feeder sectionalised with line down found at pole 200498 Isolation between ABS IP610 & Sw/Gear 13034-3 ( end of line no back feed ) Line repaired all service restored except transformer TD3 064 L/V fuses open & tagged H/V contacted L/V require inspector before livening Materials 6 x H/V comp sleeves, 10 Meters conductor, 1 x 10A H/V fuse Referral job:13397499 | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.12186 | 11 | 2017 | 2016-09-06 | C | 451 | 0.12186 | 0.0013545
1 | 13397452 | 2016-09-06 02:55 | 2016-09-06 12:25 | 570 | 9 | 5130 | 0.015407 | 0.015325 | 2.7029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 774888 | POLE | Fire service report lines down No 2145211 Faultman found a burnt pole 774888, line was isolated at Fuses 119 to replace pole in morning. Have put an Emergency Outage out to retailers to advise timing from 4am - 2pm (as per Jeremy Hill) | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.015325 | 11 | 2017 | 2016-09-06 | C | 9 | 0.015325 | 2.7029e-05
1 | 13397499 | 2016-09-06 12:15 | 2016-09-06 13:02 | 47 | 66 | 3102 | 0.0093161 | 0.008721 | 0.00019821 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 200498 | JUMPER | Transformer TD3 064 L/V left isolated after H/V contacted L/V require inspecttion & faultman to attend in morning BHM2 Crawford Rd HV line isolated between ABS SD3-118 & IP610 to repair jumper. All supply restored | F4 | WAIROA | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.008721 | 11 | 2017 | 2016-09-06 | C | 66 | 0.008721 | 0.00019821
1 | 13398626 | 2016-09-27 08:15 | 2016-09-27 16:30 | 495 | 42 | 20790 | 0.062423 | 0.062045 | 0.00012611 | NAPA ID:24250 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11 | Planned | 024250 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Pole P18129 | NONE | Replace poles P18129 & P35551. Works location: Sedcole St, Pahiatua. WO 30019582. Job ran 1 1/4 hours over time. | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.031023 | 5.5 | 2017 | 2016-09-27 | B | 42 | 0.062045 | 0.00012611
1 | 13398699 | 2016-09-06 08:43 | 2016-09-06 15:48 | 425 | 2 | 850.9 | 0.0025555 | 0.002537 | 6.0065e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 227781 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | replaced Tx tf8-006 with new unknown failure | F4 | OTAMARAKAU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.002537 | 11 | 2017 | 2016-09-06 | C | 2 | 0.002537 | 6.0065e-06
1 | 13401027 | 2016-09-06 12:34 | 2016-09-06 14:42 | 128 | 109 | 6655 | 0.019987 | 0.019004 | 0.00032735 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 798318 | CONDUCTOR - REPAIR/REHANG | CB C634 A/R O/C E/F Line down found at Pole 798318 - caused by Swan Isolated at ABS's S505 and S526 with back feed via VS11035 Conductor replaced, temp repair using larger conduct Used 305 mtrs of conductor, 4 x 12A connectors, 1 x Bullet joint | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.019004 | 11 | 2017 | 2016-09-06 | C | 109 | 0.019004 | 0.00032735
1 | 13403478 | 2016-09-09 10:15 | 2016-09-09 13:05 | 170 | 8 | 1360 | 0.0040843 | 0.004012 | 2.4025e-05 | NAPA ID:24273 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > KAIMAI DRIVE | 11 | Planned | 024273 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 217765 | CABLE - REPLACE LESS THAN 5 METRES | Replace cable up pole and joint at base of pole on cable supplying TD3-221 | F4 | KAIMAI DRIVE | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.002006 | 5.5 | 2017 | 2016-09-09 | B | 8 | 0.004012 | 2.4025e-05
1 | 13403550 | 2016-09-06 15:50 | 2016-09-06 17:54 | 124 | 1 | 124.0333 | 0.0003725 | 0.000363 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 795604 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at fuses 1500 - cause Possible bird strike Used 2 x 6amp HV fuses replaced. .All supply restored. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000363 | 11 | 2017 | 2016-09-06 | C | 1 | 0.000363 | 3.0032e-06
1 | 13405434 | 2016-09-28 09:30 | 2016-09-28 12:39 | 189 | 28 | 5292 | 0.015889 | 0.015637 | 8.4071e-05 | NAPA ID:24258 TP_HAWERA GXP > MANAIA SUB > OKAIAWA | 11 | Planned | 024258 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS MA405 | NONE | Replace DNO 160710 Abs MA405. Works location: Normanby Rd. WO 30030838 | F4 | OKAIAWA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.0078185 | 5.5 | 2017 | 2016-09-28 | B | 28 | 0.015637 | 8.4071e-05
1 | 13407703 | 2016-09-07 11:18 | 2016-09-07 14:24 | 185 | 1412 | 18406.3833 | 0.055279 | 0.042556 | 0.0042406 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P19561 | CONDUCTOR - REPAIR/REHANG | CB X20 Tripped at Feilding Sub (Kimbolton 33kV Feeder) Tree through lines Rob 0274455038 Through Information provided location where 33kV line separate from 11 kV lines 11kV back feeds installed to restore all supply NDR 300232 | F4 | APITI | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.042556 | 11 | 2017 | 2016-09-07 | C | 1412 | 0.042556 | 0.0042406
1 | 13411012 | 2016-09-07 12:55 | 2016-09-07 18:55 | 359 | 82 | 14855.8833 | 0.044616 | 0.043876 | 0.0005616 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 845884 | CONDUCTOR - REPAIR/REHANG | Tripping on CB C935 on C Phase O/C, EF. 2 faults found beyond fuses 7889. One burnt crossarm and associated hardware replaced (Pole 845884), and one floating conductor rebound plus insulator at Pole 358072. Relivened OK. | F5 | LANGDALE | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.043876 | 11 | 2017 | 2016-09-07 | C | 82 | 0.043876 | 0.0005616
1 | 13413419 | 2016-09-07 14:03 | 2016-09-07 16:14 | 131 | 501 | 20231.9167 | 0.060761 | 0.056247 | 0.0023996 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 742750 | INSULATOR | at 14:02, Bell Block Sub, CB 22, Recloser 6610, Tripped, Ph C O/C, E/F, L/O. Faultmen dispatched & investigation began. Feeder sectionalised. Attempted to close in backfeed from MAN 5 as from feeder sectionalising believed fault was between ABS 327 & ABS 45. Backfeed tripped: Recloser 499 Tripped, Ph A O/C, E/F. (MAN 5 CB flagged with Ph C O/C - believe it was Ph C Fault). Investigated further and found that ABS 344 had a blown insulator. Isolated Lines at ABS 327, 305 & 350. Permit issued & repairs carried out. All Power Restored on Completion. Warren Wright Attended. 1x Insulator, 2x Connectors, 1x Dead End & 1x Jumper Replaced. Pole 742750. The fault indicators were not flashing past ABS 45 even though fault was past this point. | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.056247 | 11 | 2017 | 2016-09-07 | C | 501 | 0.056247 | 0.0023996
1 | 13414640 | 2016-09-07 14:11 | 2016-09-07 16:38 | 147 | 931 | 96819.1167 | 0.29077 | 0.28238 | 0.002796 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 770344 | CONDUCTOR - REPAIR/REHANG | CB 7 Tripped B Ph O/C, N < E/F Lines down reported outside 3 and 5 Karewa Street on the Crn of Karaka Street, Castlecliff Rebecca took the call and has advised customer of safety procedure Control have been advised of address of fault Isolated at ABS 488 and due to enbedded generation also ABS 151 and Fuses for Transformer X2246 Lines repaired Used 6 mtrs of conductor, 3 x sleeves | F3 | CORNFOOT ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.28238 | 11 | 2017 | 2016-09-07 | C | 931 | 0.28238 | 0.002796
1 | 13415794 | 2016-09-07 14:16 | 2016-09-07 15:30 | 74 | 1 | 74.2333 | 0.00022294 | 0.000213 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21616 | FUSE - ELEMENT/LINK (HV) | 2 x 10amp fuse wind | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000213 | 11 | 2017 | 2016-09-07 | C | 1 | 0.000213 | 3.0032e-06
1 | 13415878 | 2016-09-07 14:31 | 2016-09-07 15:55 | 83 | 44 | 3686.4667 | 0.011071 | 0.010674 | 0.00013214 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | o12693 | FUSE - ELEMENT/LINK (HV) | Check 270 Orongo Road OMS 13417659 is related 2 x15 fp 1458 unknown poss bird | F4 | HAURAKI RD | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.010674 | 11 | 2017 | 2016-09-07 | C | 44 | 0.010674 | 0.00013214
1 | 13416046 | 2016-09-07 14:33 | 2016-09-08 14:26 | 1432 | 1 | 1432.6667 | 0.0043026 | 0.004293 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | Feeder Fault | INSULATOR | Part of oms 13413419 but was not linked when the job was completed. closed off with the same fault details | F3 | BELL BLOCK 2 | HUIRANGI | Taranaki | BELL BLOCK SUB | Western Electricity | POWERCO | 0.004293 | 11 | 2017 | 2016-09-07 | C | 1 | 0.004293 | 3.0032e-06
1 | 13416294 | 2016-09-07 15:30 | 2016-09-07 16:41 | 71 | 296 | 9009.0667 | 0.027056 | 0.024389 | 0.00088896 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 762573 | FUSE - ELEMENT/LINK (HV) | at 15:30, Waitara East Sub, CB U40 Tikorangi Feeder, Recloser 6224. Report from dispatch came in of lines down. Duty NC assessed and made decision to Open Recloser 6224 as believed there was HV Lines Down. Faultman advised and dispatched to location. On arrival faultman advised NOC that 2x HV Fuses were blown at Fuses 5308. Isolated all fuses at 5308 and patrolled line. NOC then reclosed 6224 successfully at 15:48. Did not find any lines down anywhere near the reported area - believes someone reported a broken stay wire as lines down. No Fault Found. Reloaded, Relivened 2x 20A HV Fuses 5308 at 16:40 and All Power Restored. Unknown cause. Were very high winds in the area at the time so could have been line clash. Brent Moratti Attended. 2x 20A HV Fuses Replaced. | F4 | TIKORANGI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.024389 | 11 | 2017 | 2016-09-07 | C | 296 | 0.024389 | 0.00088896
1 | 13416810 | 2016-09-07 14:53 | 2016-09-07 22:49 | 476 | 9 | 4287.9 | 0.012878 | 0.012796 | 2.7029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2567 | FUSE - ELEMENT/LINK (HV) | Tried to call customers to see if power back on, but could not contact them. 10pm Retailer Calling for ETA - 487 Breamore Rd - cow shed 15 - 20mins. Tripping on 2 Fuses at 2567. Reloaded OK. (8A Rating). | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.012796 | 11 | 2017 | 2016-09-07 | C | 9 | 0.012796 | 2.7029e-05
1 | 13416880 | 2016-09-07 15:00 | 2016-09-07 18:15 | 194 | 22 | 4288.9 | 0.012881 | 0.012682 | 6.6071e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 792760 | FUSE - ELEMENT/LINK (HV) | check OMS 13418599 794 Waikupa Road (no power) fuses found blown at fuses 2691 - cause debris on lines Used 2 x 15 | F4 | FORDELL | WANGANUI | Wanganui | BLINK BONNIE SUB | Western Electricity | POWERCO | 0.012682 | 11 | 2017 | 2016-09-07 | C | 22 | 0.012682 | 6.6071e-05
1 | 13418839 | 2016-09-07 16:52 | 2016-09-07 18:50 | 117 | 3 | 353 | 0.0010601 | 0.001033 | 9.0096e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP894 | FUSE - ELEMENT/LINK (HV) | Faultman found blown fuses at Fuses FP894, supect duck strike. 2 X 10 amp HV fuses replaced | F4 | GULLIVER RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.001033 | 11 | 2017 | 2016-09-07 | C | 3 | 0.001033 | 9.0096e-06
1 | 13419850 | 2016-09-07 18:14 | 2016-09-07 19:08 | 54 | 155 | 6972.9833 | 0.020941 | 0.019544 | 0.0004655 |  | 11 | Unplanned |  | OVERHEAD LINE | UNDER INVESTIGATION | UNDER INVESTIGATION | Recloser 9604/2 | UNKNOWN | 1 x A/R on recloser 9604/2. E/F flag. 2nd in 6 minutes. A/R disabled. 1 r created for line patrol. Line was patrolled as best as possible but to dark to see, faultman will return in morning to complete line patrol. Line patrol recommenced 07:30. All of line visible patrolled again with no apparent cause identified. Network left in reconfigured state in case of further trippings. Will be restored this afternoon if none. | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.019544 | 11 | 2017 | 2016-09-07 | C | 155 | 0.019544 | 0.0004655
1 | 13420656 | 2016-09-07 18:45 | 2016-09-07 19:50 | 65 | 1 | 65.05 | 0.00019536 | 0.000186 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 722089 | FUSE - ELEMENT/LINK (HV) | 2 Fuses tripped at W5180. (2A) Reloaded OK. Suspect internal fault earlier. Single phase Transformer | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.000186 | 11 | 2017 | 2016-09-07 | C | 1 | 0.000186 | 3.0032e-06
1 | 13421815 | 2016-09-07 21:17 | 2016-09-07 23:33 | 136 | 496 | 30335.0167 | 0.091103 | 0.086634 | 0.0016998 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 759067 | INSULATOR | just past the 100k sign on the RHside of the road about 1k past the sign was the sparking pole - Janet Richards called this in 027 7106 535. Tripping on CB6 on EF. Feeder patrolled / sectionalised with a blown Insulator found at Pole 759067. Isolation required between ABS 511, 514, 41 and CB6 with backfeed at ABS 185. Insulator replaced and relivened OK. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.086634 | 11 | 2017 | 2016-09-07 | C | 496 | 0.086634 | 0.0016998
1 | 13422371 | 2016-09-07 21:39 | 2016-09-08 12:00 | 861 | 23 | 19808.3667 | 0.059489 | 0.059281 | 6.9074e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 781024 | INSULATOR | Reports of part / no power found 2 HT fuses tripped at 778. Difficult to patrol during night / stormy conditions. Fuses tripped on reload attempt. To be patrolled during daylight hours. 11.00am Tans from SMC advised that Ben wilson and one other are patrolling the line trying to locate cause of fault at the moment. Outage required past Fuses 778 to replace insulator and rebind in conductors. | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.059281 | 11 | 2017 | 2016-09-07 | C | 23 | 0.059281 | 6.9074e-05
1 | 13424054 | 2016-09-07 23:29 | 2016-09-08 15:16 | 946 | 173 | 26118.2333 | 0.078439 | 0.07688 | 0.0011412 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 812724 | BINDER | Tripping on CB C926 on Phase A-B O/C. Feeder patrolled / sectionalised with the faulted area somewhere between ABS 7952 and Safety Manager 658613. Fault restoration was hindered by incorrect SCADA indication at TUH Sub Outage required between CB C926 & ABS 7952. Back feeds put in place from TUHC927 via ABS S544. Rebound conductors at Poles 812724 & 812725 Restored OK | F4 | PIRINOA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.07688 | 11 | 2017 | 2016-09-07 | C | 173 | 0.07688 | 0.0011412
1 | 13424165 | 2016-09-07 23:35 | 2016-09-08 14:19 | 883 | 237 | 58101.2833 | 0.17449 | 0.17236 | 0.00071177 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | P12951 | CROSSARM - WHOLE ASSEMBLY | Tripping on CB3 on EF. Feeder patrolled with large tree found down through all 3 conductors. (Storm conditions). Isolation from fuses U24 (Pole P12951). To be repaired during daylight hours. Trees removed and lines repaired Replaces 2 x crossarms and insulators | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.17236 | 11 | 2017 | 2016-09-07 | C | 237 | 0.17236 | 0.00071177
1 | 13424653 | 2016-09-08 00:44 | 2016-09-08 10:48 | 604 | 3767 | 262956.2 | 0.78971 | 0.75577 | 0.019124 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | multiple | CABLE - REPAIR | 11kV CB 14 tripped to lockout. A/B/C Over current and Earth fault. During fault finding process and testing it was thought the fault had been isolated, however a second cable caused the back feed via MAI CB 26 to trip to lock out too. On further testing found to be two 11kV cable faults on the MAI CB 14 feeder as per DNO data below. During fault finding, also caused outage to PAS-MAI-KAR 33kV circuit. MAI to PAS oil cable is faulted and lost all oil pressure. DNO, Powerco Management to discuss direction of repair/replace. Issue escalated to NCTL at 0245hrs. In turn escalated to Chris Norman at 0305Hrs as per contingency process. All works to 2R, multiple crews mobilised, including tech team from Wanganui. 33kV cable Fault between PAS to MAI, DNO 160905 11kV cable Fault between Sw/gear G97/C to G124/B, DNO 160906. 11kV Cable Fault between Sw/gear 10018/B to G252/A, DNO 160907 | F3 | MAIN ST 14 | BUNNYTHORPE | Manawatu | MAIN ST SUB | Western Electricity | POWERCO | 0.75577 | 11 | 2017 | 2016-09-08 | C | 3767 | 0.75577 | 0.019124
1 | 13425713 | 2016-09-08 00:49 | 2016-09-08 14:23 | 813 | 171 | 54474.4667 | 0.1636 | 0.16206 | 0.00051355 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 811438 | CONDUCTOR - REPLACE 1 SPAN OR GREATER, ALL PHASES | Recloser C604 tripped A - B O/C Outage required to remove trees and repair lines past Fuses 8179 to remove trees and repair lines. No backfeeds available. Replace 500m conductor, 6 joints NDR 54357 | F3 | DYERVILLE | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.16206 | 11 | 2017 | 2016-09-08 | C | 171 | 0.16206 | 0.00051355
1 | 13427009 | 2016-09-08 01:16 | 2016-09-08 02:35 | 78 | 12 | 943.2 | 0.0028326 | 0.002724 | 3.6038e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 799260 | NONE | Tripping on Recloser CB C640 on Phase B O/C. Branch found sitting across conductors at Pole 799260. Removed OK with fuse stick and relivened. Stormy conditions. | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.002724 | 11 | 2017 | 2016-09-08 | C | 12 | 0.002724 | 3.6038e-05
1 | 13432890 | 2016-09-08 03:49 | 2016-09-08 03:51 | 1 | 1016 | 1524 | 0.0045769 | 0 | 0.0030513 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | multiple | CABLE - REPAIR | This job and 13433910 relates to 13424653. Part of Main st Cable issue | F3 | PASCAL ST 12 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-09-08 | C | 1016 | 0 | 0.0030513
1 | 13433910 | 2016-09-08 03:53 | 2016-09-08 03:55 | 1 | 1016 | 2015.0667 | 0.0060517 | 0 | 0.0030513 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | multiple | CABLE - REPAIR | This job and 13432890 relates to 13424653. Part of Main st Cable issue | F3 | PASCAL ST 12 | LINTON | Manawatu | PASCAL ST SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-09-08 | C | 1016 | 0 | 0.0030513
1 | 13435689 | 2016-09-08 04:02 | 2016-09-08 08:56 | 294 | 248 | 25001.2667 | 0.075084 | 0.072849 | 0.0013454 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | wh212 | CONDUCTOR - REPAIR/REHANG | Whareroa CB 12080/2 tripped on E/F, Phase A. Lines down with tree through line. Transformer W2230 on generator until lines could be repaired. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.072849 | 11 | 2017 | 2016-09-08 | C | 248 | 0.072849 | 0.0013454
1 | 13436119 | 2016-09-08 04:41 | 2016-09-08 08:50 | 249 | 8 | 1993.8667 | 0.005988 | 0.005915 | 2.4026e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 819919 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 10A fuses at Fuses 7602, 2 x 2A fuses at Fuses 7603 | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.005915 | 11 | 2017 | 2016-09-08 | C | 8 | 0.005915 | 2.4026e-05
1 | 13436127 | 2016-09-08 10:02 | 2016-09-08 10:49 | 47 | 19 | 893 | 0.0026819 | 0.00251 | 5.7061e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773385 | JUMPER | Jumper blown at Fuses 772. Jeremy Hill will repair live line due to large isolation. Outage required from Fuses 772 to repair jumper using live line. Jumper replaced, relivened OK | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.00251 | 11 | 2017 | 2016-09-08 | C | 19 | 0.00251 | 5.7061e-05
1 | 13436149 | 2016-09-08 05:08 | 2016-09-08 12:00 | 412 | 2 | 824.4333 | 0.0024759 | 0.002457 | 6.0064e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733693 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Check 5381 MOUNTAIN ROAD OMS 13439692 and 5200A MOUNTAIN ROAD OMS 13438314 is related Transformer confirmed to be faulted, requires replacement, three phase 50KVA Please confirm if 5381 Mountain Road would have been affected. If no please call customer to see if they have power - OMS 13439692 Tx was replaced. Gone through control. Replace 1 x 50kVA Transformer | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.002457 | 11 | 2017 | 2016-09-08 | C | 2 | 0.002457 | 6.0064e-06
1 | 13436156 | 2016-09-08 05:15 | 2016-09-08 12:03 | 407 | 75 | 30586.25 | 0.091857 | 0.09118 | 0.00022524 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 832119 | CONDUCTOR - REPAIR/REHANG | Outage required past Recloser 7417 to repair lines bought down by trees. No backfeeds available. Replace 6 x joints, 20m conductor & 3 x terminations NDR 37940 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.09118 | 11 | 2017 | 2016-09-08 | C | 75 | 0.09118 | 0.00022524
1 | 13438190 | 2016-09-08 06:00 | 2016-09-08 14:29 | 508 | 77 | 17172.55 | 0.051573 | 0.050878 | 0.00023125 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 736369 | BINDER | RS 4832 A/R, L/O, E/F. Sectionalised & Patrolled. Found floating HV Conductor. Repaired using 2x Ali Binders. Bruce Kerr also attended in bucket truck. | F5 | RAWHITIROA | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.050878 | 11 | 2017 | 2016-09-08 | C | 77 | 0.050878 | 0.00023125
1 | 13439084 | 2016-09-08 06:26 | 2016-09-08 11:06 | 280 | 242 | 37060.9 | 0.1113 | 0.10912 | 0.0010151 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 727131 | CONDUCTOR - REPAIR/REHANG | Livingstone CB1 tripped on O/c. Floating HV conductor at pole 727131. HV insulator, and pin and set of binders. | F4 | OTAUTU | HAWERA | Taranaki | LIVINGSTONE SUB | Western Electricity | POWERCO | 0.10912 | 11 | 2017 | 2016-09-08 | C | 242 | 0.10912 | 0.0010151
1 | 13439345 | 2016-09-08 06:33 | 2016-09-08 14:22 | 469 | 2 | 938.6333 | 0.0028189 | 0.0028 | 6.0064e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764766 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6A fuses | F4 | MAKIRIKIRI | BRUNSWICK | Wanganui | ROBERTS AVE SUB | Western Electricity | POWERCO | 0.0028 | 11 | 2017 | 2016-09-08 | C | 2 | 0.0028 | 6.0064e-06
1 | 13439679 | 2016-09-08 07:52 | 2016-09-08 10:59 | 187 | 82 | 15334 | 0.046051 | 0.045312 | 0.00024626 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | N/A - NOT APPLICABLE | FUSE - DROP OUT - REPLACE FULL SET OF FUSES (HV) | Line down. Replace 3 x DDOs at Tx 690. | F4 | MOTUROA 3 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.045312 | 11 | 2017 | 2016-09-08 | C | 82 | 0.045312 | 0.00024626
1 | 13440024 | 2016-09-08 07:46 | 2016-09-08 18:09 | 623 | 1 | 623.3167 | 0.0018719 | 0.001862 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | LIGHTNING | LIGHTNING - LIGHTNING STRIKE | 6150 | FUSE - ELEMENT/LINK (HV) | 4.38pm update from retailer. Customer has advised them this is a waste water treatment and only has a few hours left till it overflows. Asked SMC if we can prioritize - originally requested at 8.08am Replaced 3x 15Amp HV fuses | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.001862 | 11 | 2017 | 2016-09-08 | C | 1 | 0.001862 | 3.0032e-06
1 | 13440523 | 2016-09-08 07:51 | 2016-09-08 10:36 | 165 | 1 | 165.1833 | 0.00049608 | 0.000487 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P21616 | FUSE - ELEMENT/LINK (HV) | 2 x 10 amp fuses wind | F3/F4 | MAKINO | BUNNYTHORPE | Manawatu | FEILDING SUB | Western Electricity | POWERCO | 0.000487 | 11 | 2017 | 2016-09-08 | C | 1 | 0.000487 | 3.0032e-06
1 | 13440693 | 2016-09-08 08:05 | 2016-09-08 08:34 | 28 | 2137 | 52844.2667 | 0.1587 | 0.13945 | 0.0064178 |  | 11 | Unplanned |  | OVERHEAD LINE | HUMAN ELEMENT | HUMAN ELEMENT - LOADING ERROR - NETWORK LOAD | N/A - NOT APPLICABLE | NONE | Loss of KST 23 due to overload situation. Due to earlier large fault off MAI Sub (OMS 13424653) MAI 21 load was back fed off KST 23. NOC opened Sw/gear 10165/1. Relivened both MAI 21 (As T2 BUS was now live) and KST 23. Had to get Staff to Hospital to check state of changeover scheme to ensure was in right configuration. 2x staff went, Jeff Roberts and Mick Salter | F3 | KEITH ST 23 | BUNNYTHORPE | Manawatu | KEITH ST SUB | Western Electricity | POWERCO | 0.13945 | 11 | 2017 | 2016-09-08 | C | 2137 | 0.13945 | 0.0064178
1 | 13442961 | 2016-09-08 11:22 | 2016-09-08 11:28 | 6 | 22 | 132 | 0.00039642 | 0.000198 | 6.607e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8 Sangster Road | FUSE - ELEMENT/LINK (HV) | Replaced 1x 80Amp HV Fuse Link. Backfed via ABS 5643 and opened ABS 5557.Isolated at RS 4812 to carry out the reliven of fuse. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000198 | 11 | 2017 | 2016-09-08 | C | 22 | 0.000198 | 6.607e-05
1 | 13443757 | 2016-09-08 09:04 | 2016-09-08 11:44 | 159 | 474 | 38582.3167 | 0.11587 | 0.1116 | 0.002817 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | W0952 | NONE | Recloser RC 15 tripped to L/O. E/F flag. Line sectionalised & patrolled. Branch removed from line at pole W0952. All supply restored. | F4 | OWERA RD | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.1116 | 11 | 2017 | 2016-09-08 | C | 474 | 0.1116 | 0.002817
1 | 13444665 | 2016-09-09 00:02 | 2016-09-09 01:15 | 72 | 6 | 437.7 | 0.0013145 | 0.00126 | 1.8019e-05 | NAPA ID:24316 TP_KINLEITH GXP > BAIRD ROAD SUB > ASHWORTH ST | 11 | Planned | 024316 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | TC3767 | NONE | Close 11kV Cable break between 11kV SwGear 9597/3 & 11kV T/Blade switch B TC3767. | F3/F4 | ASHWORTH ST | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.00063 | 5.5 | 2017 | 2016-09-09 | B | 6 | 0.00126 | 1.8019e-05
1 | 13448070 | 2016-09-08 14:05 | 2016-09-08 15:13 | 67 | 13 | 876.4 | 0.002632 | 0.002514 | 3.9042e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 758591 | BINDER | Faultman found floating HV conductor. Isolated at Fuses 5552. Repaired using 2mtrs of Ali Binder | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.002514 | 11 | 2017 | 2016-09-08 | C | 13 | 0.002514 | 3.9042e-05
1 | 13451680 | 2016-09-08 10:11 | 2016-09-08 10:45 | 34 | 145 | 4930 | 0.014806 | 0.013499 | 0.00043546 |  | 11 | Planned | 023003 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | N/A - NOT APPLICABLE | UNKNOWN | Created during Supplementary Switching for NAPA 2303 | F3 | MOTUROA 8 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.0067495 | 5.5 | 2017 | 2016-09-08 | B | 145 | 0.013499 | 0.00043546
1 | 13452249 | 2016-09-08 10:28 | 2016-09-08 21:05 | 637 | 3 | 1912.35 | 0.0057432 | 0.005716 | 9.0096e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810795 | FUSE - ELEMENT/LINK (HV) | 5:30pm sent email for an update Fuses found blown at Fuses 7352 - Cause Wind Used 2 x 10 amp fuses | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.005716 | 11 | 2017 | 2016-09-08 | C | 3 | 0.005716 | 9.0096e-06
1 | 13454030 | 2016-09-08 10:54 | 2016-09-08 20:10 | 556 | 87 | 27351.15 | 0.082141 | 0.081357 | 0.00026128 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 763924 | POLE | Lines and poles down , due to trees Fulton Hogan, on site , advised to stay 10 m away, Jai Anderson 027 334 2596 , Asplundh on way ETA 1230 Has been told lines are deenergised by local farmer, advised Jai not to take this for granted until arrival of Downer Representitve REF to OMS 13454030 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.081357 | 11 | 2017 | 2016-09-08 | C | 87 | 0.081357 | 0.00026128
1 | 13454692 | 2016-09-08 11:22 | 2016-09-08 11:28 | 5 | 42 | 249.9 | 0.0007505 | 0.000372 | 0.00012613 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | 740535 | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.000372 | 11 | 2017 | 2016-09-08 | C | 42 | 0.000372 | 0.00012613
1 | 13454757 | 2016-09-08 15:20 | 2016-09-08 16:57 | 97 | 17 | 1649 | 0.0049523 | 0.004799 | 5.1054e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 816627 | FUSE - DROP OUT - REPLACE PARTIAL SET OF FUSES (HV) | Replace 1 x Fuse holder & 2 x 3A fuses at Transformer T2620 Frank not sure as to if this is a 2R, to be decided at invoicing | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.004799 | 11 | 2017 | 2016-09-08 | C | 17 | 0.004799 | 5.1054e-05
1 | 13454855 | 2016-09-08 11:39 | 2016-09-08 17:26 | 346 | 411 | 114040.2 | 0.34249 | 0.33878 | 0.0012343 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 741252 | CONDUCTOR - REPAIR/REHANG | CB D11 A/R, L/O, O/C, E/F. Patrolled with lines down found at Pole 741252 Repaired using 30mtrs of 16mm cu wire, 8x sleeves, 3x cu binders | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.33878 | 11 | 2017 | 2016-09-08 | C | 411 | 0.33878 | 0.0012343
1 | 13455295 | 2016-09-08 11:43 | 2016-09-08 14:07 | 143 | 108 | 15526.8 | 0.04663 | 0.045657 | 0.00032435 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 842422 | INSULATOR | Outage required past Recloser 2680 due to floating conductor that is iminent danger of causing an unplanned outage. No backfeeds available. Replace 1 x pin and insulator Restored OK | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.045657 | 11 | 2017 | 2016-09-08 | C | 108 | 0.045657 | 0.00032435
1 | 13457126 | 2016-09-08 12:04 | 2016-09-08 15:08 | 184 | 161 | 23421.8667 | 0.070341 | 0.06889 | 0.00048352 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 762376 | CONDUCTOR - REPAIR/REHANG | CB H41 A/R, L/O, E/F, O/C B Phase. Sectionalised & Patrolled. Lines down. Repaired using 100mtrs of 16mm cu wire & 10x 16mm sleeves | F3 | TARATA | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.06889 | 6.6 | 2017 | 2016-09-08 | C | 161 | 0.06889 | 0.00048352
1 | 13457339 | 2016-09-08 15:38 | 2016-09-08 16:50 | 72 | 118 | 8486.25 | 0.025486 | 0.024422 | 0.00035438 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 741688 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Faultman found broken HV fuse at Transformer 2304T. Shutdown via Recloser 8763/2 Repaired using 1x HV fuse complete with 3Amp Link. 2mtrs of 16mm cu wire, & 2x sleeves | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.024422 | 11 | 2017 | 2016-09-08 | C | 118 | 0.024422 | 0.00035438
1 | 13458402 | 2016-09-08 13:11 | 2016-09-08 18:45 | 334 | 421 | 32304.2667 | 0.097016 | 0.093223 | 0.0012643 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 013690 | CROSSARM - WHOLE ASSEMBLY | CB 2 tripped to L/O. E/F flag. Police advised 3 power poles affected, "2 bays" of powerlines on the road event #P026602782. 5773 Pekapeka Road. **Please advise Police Comms on (0800) 115 019 when job is complete, thank you ** Lines down confirmed. Isolation's at ABS IC398 & IC414. All other supply restored at 14:21 1 X cross arm & all hardware replaced. 5 X sleeves used. 6 X binders replaced. 10 m of Iodine conductor used. | F4 | AWAITI | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.093223 | 11 | 2017 | 2016-09-08 | C | 421 | 0.093223 | 0.0012643
1 | 13459516 | 2016-09-08 14:46 | 2016-09-08 20:00 | 313 | 3 | 941.5 | 0.0028275 | 0.0028 | 9.0096e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 702237 | CONDUCTOR - REPAIR/REHANG | Hazards process complete ETA 3.05pm Holly Genesis CSR spoke to neighbours at 63 they are happy to have power off for night if we cannot restore power tonight, line was isolated at Fuses 8485 to repair line down at pole 702237. 3 X sleeves used. 2 X binders used. 10 m of conductor replaced. 2 X 2 amp HV fuses replace. | F2 | MOTUROA 5 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.0028 | 11 | 2017 | 2016-09-08 | C | 3 | 0.0028 | 9.0096e-06
1 | 13459550 | 2016-09-08 14:47 | 2016-09-08 15:40 | 52 | 120 | 6342 | 0.019046 | 0.017965 | 0.00036038 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | V27 | UNKNOWN | Recloser V27 Tripped on B Phase EF Feeder patrolled, no fault found. Relivened OK | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.017965 | 11 | 2017 | 2016-09-08 | C | 120 | 0.017965 | 0.00036038
1 | 13460324 | 2016-09-08 15:34 | 2016-09-08 17:55 | 141 | 1 | 141.35 | 0.0004245 | 0.000415 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | WH105 | FUSE - ELEMENT/LINK (HV) | check to see if OMS 13460492 (66 Old South Rd ) is related - no power and OMS 13462607 Mokoia School 969 South rd - no power ans OMS 13462648 36 Mokoia Rd - no power and OMS 13462892 126 Mokoia Rd - no power Replaced 2x 25Amp Links | F4 | MANUTAHI | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.000415 | 11 | 2017 | 2016-09-08 | C | 1 | 0.000415 | 3.0032e-06
1 | 13460518 | 2016-09-08 15:49 | 2016-09-08 18:55 | 186 | 2 | 372.8 | 0.0011196 | 0.001101 | 6.0064e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND-BLOWN DEBRIS (NOT TREES) | 828337 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Transformer T2830 - cause wind Used 2 x 2 amp fuses | F3/F4 | GORDON ST | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.001101 | 11 | 2017 | 2016-09-08 | C | 2 | 0.001101 | 6.0064e-06
1 | 13460882 | 2016-09-08 15:58 | 2016-09-08 17:12 | 74 | 206 | 11506.8833 | 0.034557 | 0.032701 | 0.00061866 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 9198/2 | NONE | Recloser 9198/2 tripped to L/O. No flags. Line sectionalised & patrolled. No apparent fault found. All supply restored. | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.032701 | 11 | 2017 | 2016-09-08 | C | 206 | 0.032701 | 0.00061866
1 | 13461385 | 2016-09-08 15:58 | 2016-09-08 18:15 | 137 | 289 | 22580.15 | 0.067813 | 0.065208 | 0.00085291 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 747210 | CONDUCTOR - REPAIR/REHANG | CB 5 A/R, L/O, E/F. Sectionalised & patrolled. Fault due to a HV line down. Repaired using 10mtrs of 16mm cu wire & 4 sleeves | F4 | KATERE 5 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.065208 | 11 | 2017 | 2016-09-08 | C | 289 | 0.065208 | 0.00085291
1 | 13462947 | 2016-09-08 17:23 | 2016-09-08 21:40 | 256 | 6 | 1540 | 0.0046249 | 0.00457 | 1.8019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 7201 | FUSE - ELEMENT/LINK (HV) | check OMS 13463001 (1579B STATE HIGHWAY 53) -Power has gone out, all 3 houses around it also have no power. Power went out around 5pm Fuse found blown at Fuses 7201 - cause Wind Used 2 x 10amp fuses | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.00457 | 11 | 2017 | 2016-09-08 | C | 6 | 0.00457 | 1.8019e-05
1 | 13463106 | 2016-09-08 18:03 | 2016-09-09 00:47 | 403 | 5 | 734.0167 | 0.0022044 | 0.002159 | 1.5016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - WIND-BLOWN DEBRIS - TREES | 797494 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at fuses 7443 blow again on reload Branch found on lines at pole 797494 cleared using hot sticks Fuses closed Used 4 x 10 amp fuses | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.002159 | 11 | 2017 | 2016-09-08 | C | 5 | 0.002159 | 1.5016e-05
1 | 13464056 | 2016-09-08 19:18 | 2016-09-09 00:18 | 300 | 219 | 63661.4333 | 0.19119 | 0.18921 | 0.0006577 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 734855 | INSULATOR | CB R11 Tripped E/F. Replace insulator at Pole 734855. Replaced 3 x Pin Insulators. 3 x Ali Binders. | F4 | NGAERE | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.18921 | 11 | 2017 | 2016-09-08 | C | 219 | 0.18921 | 0.0006577
1 | 13464306 | 2016-09-08 19:22 | 2016-09-09 14:06 | 1123 | 316 | 78038.8333 | 0.23437 | 0.23152 | 0.0011562 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 725409 | CONDUCTOR - REPAIR/REHANG | CB WH2 Trip, No flags, Sectionalised & Patrolled. Section that could not be patrolled between ABS WH284 & WH 203 left off overnight. Returned next day to find trees in lines through large gully. Span of wire removed between Poles 725409 & 725421. Relivened from both ends. Ongoing work required to clear faults & restore line break. | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.23152 | 11 | 2017 | 2016-09-08 | C | 316 | 0.23152 | 0.0011562
1 | 13466056 | 2016-09-08 20:05 | 2016-09-09 16:00 | 1195 | 1 | 1195.6333 | 0.0035907 | 0.003581 | 3.0032e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737052 | FUSE - ELEMENT/LINK (HV) | reloaded 2x 2a HV fuse at transformer 2135T Restore time 3.51pm. Replaced 2x2Amp HV Fuses. SR 107633 forwarded to OSI as 'Restore' Time is picking up an inaccurate time for KPI Reporting.. | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.003581 | 11 | 2017 | 2016-09-08 | C | 1 | 0.003581 | 3.0032e-06
1 | 13466064 | 2016-09-08 20:05 | 2016-09-09 09:30 | 804 | 13 | 10462.4 | 0.031421 | 0.031303 | 3.9042e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 370783 | FUSE - ELEMENT/LINK (HV) | Have advised svs hub of Priority customer. Please check if OMS 13474769 is related 252 Fairfield Road. Reload at fuses WH841. 2 x 15A due to Weather. | F4 | MANAWAPOU RD | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.031303 | 11 | 2017 | 2016-09-08 | C | 13 | 0.031303 | 3.9042e-05
1 | 13466697 | 2016-09-08 20:07 | 2016-09-09 00:46 | 278 | 115 | 18099.6167 | 0.054357 | 0.05332 | 0.00034537 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 738444 | JUMPER | Transformer pole is sparking/arcing, embers are coming down from pole. Affecting power @ 415B WAIHAPA ROAD, STRATFORD Faultman found a broken 11KV jumper on pole 738444 going to transformer line was isolated at ABS's 5687 & 5807 to repair the jumper. | F4 | CLOTON RD INDUSTRIAL | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.05332 | 11 | 2017 | 2016-09-08 | C | 115 | 0.05332 | 0.00034537
1 | 13468033 | 2016-09-09 15:01 | 2016-09-09 16:49 | 107 | 5 | 535.5 | 0.0016082 | 0.001563 | 1.5016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 739353 | CONDUCTOR - REPAIR/REHANG | Replaced 1x 6Amp HV fuse at 5453. Replaced 2x 3Amp HV Fuses at 8834. Repaired line down beyond Fuses 8834 using 4x sleeves. | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001563 | 11 | 2017 | 2016-09-09 | C | 5 | 0.001563 | 1.5016e-05
1 | 13468246 | 2016-09-08 20:30 | 2016-09-09 11:06 | 875 | 120 | 74714.0667 | 0.22438 | 0.2233 | 0.00036038 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | P04909 | NONE | Bailing plastic found on hte lines, removed with hot sticks. Relivened OK | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.2233 | 11 | 2017 | 2016-09-08 | C | 120 | 0.2233 | 0.00036038
1 | 13469295 | 2016-09-08 20:05 | 2016-09-08 21:44 | 99 | 868 | 85730.5167 | 0.25747 | 0.24965 | 0.0026068 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 734507 | STREET LIGHT (LV) | Recloser 12154 tripped on E/F flags, received a call of line down on Fint Rd, faultman found that it was a lighting circuit lv had burnt through and flick into 11KV line at pole 734507, faultman cut away the lighting circuit. | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.24965 | 11 | 2017 | 2016-09-08 | C | 868 | 0.24965 | 0.0026068
1 | 13469338 | 2016-09-08 20:26 | 2016-09-09 14:04 | 1058 | 493 | 107305 | 0.32226 | 0.31782 | 0.0015947 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 835677 | POLE | CB C850 tripped Feeder sectionalised and outage required past ABS S384 to open line break at pole 835679. Feeder restored with 2 transformers left off overnight. Trees removed & pole 835677 replaced. Additional outage required past ABS S384 to close line break. Relivened OK NDR 21822 | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.31782 | 11 | 2017 | 2016-09-08 | C | 493 | 0.31782 | 0.0015947
1 | 13472034 | 2016-09-08 22:15 | 2016-09-09 11:20 | 784 | 180 | 92549.3667 | 0.27794 | 0.27632 | 0.00035438 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P26884 | INSULATOR | CB 3 AR A Phase EF Recloser V61 tripped B & C phase EF Outage required past Recloser V41 to repair. No back feeds available. Replace 2 x insulators Relivened OK | F5 | COAST ROAD | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.27632 | 11 | 2017 | 2016-09-08 | C | 180 | 0.27632 | 0.00035438
1 | 13473951 | 2016-09-09 00:06 | 2016-09-09 10:10 | 603 | 7 | 4225.6667 | 0.01269 | 0.012627 | 2.1022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 752195 | FUSE - ELEMENT/LINK (HV) | Reload at 8178. 2 x 15A due to Weather. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.012627 | 11 | 2017 | 2016-09-09 | C | 7 | 0.012627 | 2.1022e-05
1 | 13474281 | 2016-09-09 01:46 | 2016-09-09 12:37 | 651 | 1 | 651.35 | 0.0019561 | 0.001947 | 3.0031e-06 |  | 6.6 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 761114 | CONDUCTOR - REPAIR/REHANG | Multi properties affected past fuses 6313 Cloton Road Floating conductor 1 x Ali binder 2 x 20A Fuses | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.001947 | 6.6 | 2017 | 2016-09-09 | C | 1 | 0.001947 | 3.0031e-06
1 | 13474347 | 2016-09-09 03:40 | 2016-09-09 17:28 | 827 | 1 | 827.7167 | 0.0024858 | 0.002476 | 3.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 725204 | FUSE - ELEMENT/LINK (HV) | Reload reliven Replaced 2x 6Amp HV Links Weather | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.002476 | 11 | 2017 | 2016-09-09 | C | 1 | 0.002476 | 3.0031e-06
1 | 13474376 | 2016-09-09 04:40 | 2016-09-09 07:30 | 169 | 1 | 169.55 | 0.00050919 | 0.0005 | 3.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 846361 | FUSE - ELEMENT/LINK (HV) | Full power restored Replaced 1x 2A HV fuse and 1x 100A LV fuse Duse to line clash Advised FM he needs to speak to control before job can be closed | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0005 | 11 | 2017 | 2016-09-09 | C | 1 | 0.0005 | 3.0031e-06
1 | 13474500 | 2016-09-09 06:00 | 2016-09-09 12:30 | 390 | 3 | 1170.75 | 0.003516 | 0.003488 | 9.0094e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737698 | FUSE - ELEMENT/LINK (HV) | Check for safety - THE ROOF FOR A SHED IS ON THE ROAD AND IT KNOCKED DOWN THE OH SERVICE LINES AS WELL AS THE NETWORK LINES DOWN THE RD. Service lines cut away and will need replacing. Reload at Transformer 3706T 2 x 6A Fuses due to Weather. | F4 | CARDIFF RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.003488 | 11 | 2017 | 2016-09-09 | C | 3 | 0.003488 | 9.0094e-06
1 | 13474813 | 2016-09-09 07:21 | 2016-09-09 11:54 | 272 | 104 | 15324.5 | 0.046022 | 0.045085 | 0.00031233 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 815173 | POLE | Check for safety - Lines down due to Car vs Pole. ETA required Awaiting on exact location from fire comms Advised control and SMC of 999 Replace pole, relivened OK NDR 54310 | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.045085 | 11 | 2017 | 2016-09-09 | C | 104 | 0.045085 | 0.00031233
1 | 13475722 | 2016-09-09 08:17 | 2016-09-09 14:04 | 347 | 29 | 10067.8333 | 0.030235 | 0.029974 | 8.7092e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 745760 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Reload at 8292. 2 x 15 A due to Weather. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.029974 | 11 | 2017 | 2016-09-09 | C | 29 | 0.029974 | 8.7092e-05
1 | 13475810 | 2016-09-09 12:28 | 2016-09-09 14:53 | 145 | 14 | 2030 | 0.0060964 | 0.00597 | 4.2044e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 713213 | CONDUCTOR - REPAIR/REHANG | Upgraded to lines down - Check for safety - Lines down on the side of the road Advised smc of 999 upgrade hazard process completed by Tara Lines repaired at pole 713213 1 x Ali Binder 1 x Namu Sleeve | F4/F1 | SOUTH RD NGARIKI | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.00597 | 11 | 2017 | 2016-09-09 | C | 14 | 0.00597 | 4.2044e-05
1 | 13476143 | 2016-09-09 11:41 | 2016-09-09 17:07 | 326 | 7 | 2282 | 0.0068532 | 0.00679 | 2.1022e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 720330 | CROSSARM - WHOLE ASSEMBLY | Check for safety -Part power, advised line outside pole to pole is down. One side still attached, the other side snapped Advised SMC of 999 chris has made safe and leaving site, crew to attend on 2R and repair fault. Replaced 1x 10Amp HV Fuse Link, HV crossarm with 3 pins & insulators & all associated hardware | F1/F4 | MATAPU | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.00679 | 11 | 2017 | 2016-09-09 | C | 7 | 0.00679 | 2.1022e-05
1 | 13476171 | 2016-09-09 08:56 | 2016-09-09 17:10 | 494 | 2 | 593.6667 | 0.0017829 | 0.001764 | 6.0063e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 2194T | FUSE - ELEMENT/LINK (HV) | Replaced 3x 2Amp HV Links | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.001764 | 11 | 2017 | 2016-09-09 | C | 2 | 0.001764 | 6.0063e-06
1 | 13476988 | 2016-09-09 10:50 | 2016-09-09 12:55 | 125 | 47 | 5875 | 0.017644 | 0.01722 | 0.00014115 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 735813 | POLE | Pole 735813 - 180 Opanake Rd found out of ground and leaning by FM attending another Fault. This OMS created for Jade to carry out pole relocation and re-stand the pole. 2R - Please Assign Jade Williams to Relocate/Repair Pole 735813. | F5 | CLIMIE RD | STRATFORD | Taranaki | CARDIFF SUB | Western Electricity | POWERCO | 0.01722 | 11 | 2017 | 2016-09-09 | C | 47 | 0.01722 | 0.00014115
1 | 13477638 | 2016-09-09 09:33 | 2016-09-09 13:45 | 251 | 281 | 27475.6167 | 0.082514 | 0.079982 | 0.00084389 |  | 11 | Unplanned |  | OVERHEAD LINE | ADVERSE WEATHER | ADVERSE WEATHER - WIND | 217075 | CONDUCTOR - REPAIR/REHANG | Sectionaliser 9208 trip open, no flags. Sectionalised and found fault beyond fuses FP1534. Repaired lines down & re-livened. | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.079982 | 11 | 2017 | 2016-09-09 | C | 281 | 0.079982 | 0.00084389
1 | 13477966 | 2016-09-11 13:08 | 2016-09-11 13:21 | 13 | 3 | 39 | 0.00011712 | 9e-05 | 9.0093e-06 | NAPA ID:24337 TP_MARTON GXP > BULLS SUB > PAREWANUI | 11 | Planned | 024337 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 4449/1 | NONE | Isolate 11kv metering unit 44491 for calibration | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 4.5e-05 | 5.5 | 2017 | 2016-09-11 | B | 3 | 9e-05 | 9.0093e-06
1 | 13478892 | 2016-09-09 09:59 | 2016-09-09 12:43 | 164 | 493 | 46524.3833 | 0.13972 | 0.13528 | 0.0019881 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758075 | CONDUCTOR - REPAIR/REHANG | CB 6 A/R, L/O, E/F. Floating Conductor at pole 758075. Used 2 x Binders. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.13528 | 11 | 2017 | 2016-09-09 | C | 493 | 0.13528 | 0.0019881
1 | 13480241 | 2016-09-09 13:30 | 2016-09-09 14:00 | 30 | 4 | 120 | 0.00036038 | 0.000324 | 1.2013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 826322 | FUSE - DROP OUT - REPLACE PARTIAL SET OF FUSES (HV) | 2R - Require FM to Repair DDO fuse, Replace Missing Bolt in Insulator and Repair Jumper on Crossarm as Reported by Rodger Castle at Pole Tech Transformer T3439 @ Pole 826322 - 30 Tea Creek Rd - Clareville CB C834 Repair Transformer T3439 fusess | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.000324 | 11 | 2017 | 2016-09-09 | C | 4 | 0.000324 | 1.2013e-05
1 | 13480261 | 2016-09-09 14:49 | 2016-09-09 15:37 | 48 | 2 | 96 | 0.0002883 | 0.00027 | 6.0063e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 794744 | JUMPER | Repair jumper on load side of Transformer X861 fuses | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.00027 | 11 | 2017 | 2016-09-09 | C | 2 | 0.00027 | 6.0063e-06
1 | 13480318 | 2016-09-30 08:48 | 2016-09-30 14:47 | 359 | 8 | 2872 | 0.0086231 | 0.008551 | 2.402e-05 | NAPA ID:24342 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 024342 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 263493 | NONE | Replace poles, hardware and conductor. Works location: Belk Rd South. WO 30019862 | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0042755 | 5.5 | 2017 | 2016-09-30 | B | 8 | 0.008551 | 2.402e-05
1 | 13480369 | 2016-09-08 21:47 | 2016-09-09 19:19 | 1291 | 4 | 3365.6333 | 0.010108 | 0.010071 | 1.2013e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718260 | FUSE - ELEMENT/LINK (HV) | 2:46 - Spoke to SMC (Tarn) and advised customer is still without power. Check OMS 13484108, 44 THOMAS ROAD and 13475392, 37 THOMAS RD are related. Replaced 2x 8Amp HV Fuses | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.010071 | 11 | 2017 | 2016-09-08 | C | 4 | 0.010071 | 1.2013e-05
1 | 13481553 | 2016-09-09 11:01 | 2016-09-09 15:22 | 261 | 206 | 20950.4333 | 0.062918 | 0.061061 | 0.00086191 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 858183 | INSULATOR | Floating conductor at pole 858183. Used 1 x Insulator & Pine 5 x Binders | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.061061 | 11 | 2017 | 2016-09-09 | C | 206 | 0.061061 | 0.00086191
1 | 13482766 | 2016-09-09 11:33 | 2016-09-09 19:54 | 500 | 256 | 34476.3833 | 0.10354 | 0.10123 | 0.00090395 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 221755 | UNKNOWN | Recloser S6031 L/O E/F & O/C. Sectionalised 7 found lines down in two seperate areas. Isolated between ABS S6011 & SF6-039. Repaired & Relivened | F4 | MAUNGARANGI RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.10123 | 11 | 2017 | 2016-09-09 | C | 256 | 0.10123 | 0.00090395
1 | 13483174 | 2016-09-27 08:47 | 2016-09-27 12:41 | 234 | 26 | 6084 | 0.018268 | 0.018033 | 7.8067e-05 | NAPA ID:24341 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 024341 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 263493 | NONE | Replace poles, hardware and conductor. Works location: Belk Rd South. WO 30019862 | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0090165 | 5.5 | 2017 | 2016-09-27 | B | 26 | 0.018033 | 7.8067e-05
1 | 13484416 | 2016-09-09 12:19 | 2016-09-09 16:08 | 229 | 1 | 229.35 | 0.00068878 | 0.000679 | 3.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 3144T | FUSE - ELEMENT/LINK (HV) | Replaced 3x 10Amp Links | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000679 | 11 | 2017 | 2016-09-09 | C | 1 | 0.000679 | 3.0031e-06
1 | 13484721 | 2016-09-09 12:47 | 2016-09-09 15:00 | 133 | 967 | 80110.55 | 0.24059 | 0.23187 | 0.0029041 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | CB C928 A/R on A Phase E/F. Also CB C930 Tripped on EF Suspect that feeder fault may have taken out CB C930. Possible protection review. Feeder sectionalised, relivened OK 2r line patrol 14:16 2r repai NA | F4 | BURNSIDE | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.23187 | 11 | 2017 | 2016-09-09 | C | 967 | 0.23187 | 0.0029041
1 | 13487774 | 2016-09-09 12:57 | 2016-09-09 13:21 | 24 | 47 | 1144.45 | 0.003437 | 0.003013 | 0.00014115 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 9987 | CONDUCTOR - REPAIR/REHANG | Recloser 9987 tripped on E/F. Sectionalised and found tree down on line. Isolated between Temp 26 & ABS SF6-039. No backfeed due to fault on other side of ABS SF6-039. Repaired line and relivened. NDR 51606 | F4 | ROYDEN DOWNS RD | TE MATAI | Tauranga | PAENGAROA SUB | Eastern Electricity | POWERCO | 0.003013 | 11 | 2017 | 2016-09-09 | C | 47 | 0.003013 | 0.00014115
1 | 13488395 | 2016-10-03 11:00 | 2016-10-03 12:25 | 85 | 4 | 340 | 0.0010208 | 0.000984 | 1.2009e-05 | NAPA ID:23527 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 023527 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC636 | NONE | To install a 400V Fuse Disconnector. Works location: Buckland Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000492 | 5.5 | 2017 | 2016-10-03 | B | 4 | 0.000984 | 1.2009e-05
1 | 13488432 | 2016-10-03 10:00 | 2016-10-03 12:30 | 150 | 2 | 300 | 0.0009007 | 0.000882 | 6.0046e-06 | NAPA ID:24142 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024142 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4065 | NONE | To install an LV Isolator on TC4065. Works location: Ngutumanga Rd, Te Aroha. WO 30017829 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000441 | 5.5 | 2017 | 2016-10-03 | B | 2 | 0.000882 | 6.0046e-06
1 | 13489345 | 2016-09-08 13:13 | 2016-09-09 16:00 | 1607 | 20 | 32149.6667 | 0.096552 | 0.096371 | 6.0064e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733414 | BINDER | broken HV insulator onsite, Chris requires help to replaced HV insulator (isolated lines) and pull up wires down Isolate at ABS 6092 and Erth to Repair Floating Conductor at Pole 733414 Used 1 x 15A HV Fuse 1 x 10A HV Fuse 1 X Ali Binder | F1/F4 | MANGATOKI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.096371 | 11 | 2017 | 2016-09-08 | C | 20 | 0.096371 | 6.0064e-05
1 | 13489641 | 2016-10-03 13:31 | 2016-10-03 14:40 | 69 | 3 | 207 | 0.00062149 | 0.000594 | 9.007e-06 | NAPA ID:23528 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 023528 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1921 | NONE | To install a 400V Disconnector on TC1921. Works location: Buckland Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.000297 | 5.5 | 2017 | 2016-10-03 | B | 3 | 0.000594 | 9.007e-06
1 | 13489683 | 2016-10-03 14:06 | 2016-10-03 15:15 | 69 | 7 | 483 | 0.0014501 | 0.001387 | 2.1016e-05 | NAPA ID:24097 TP_HINUERA GXP > TIRAU SUB > OKOROIRE | 11 | Planned | 024097 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4687 | NONE | To install a 400V Disconnector on TC4687. Works location: Hwy 5, Tirau. WO 30019182 | F4 | OKOROIRE | HINUERA | Valley | TIRAU SUB | Eastern Electricity | POWERCO | 0.0006935 | 5.5 | 2017 | 2016-10-03 | B | 7 | 0.001387 | 2.1016e-05
1 | 13489909 | 2016-10-04 10:05 | 2016-10-04 14:25 | 260 | 7 | 1820 | 0.0054642 | 0.005401 | 2.1016e-05 | NAPA ID:23572 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023572 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5641 | NONE | Replace transformer pole TC5641. Works location: Rangipai Rd, Tirau. WO 30031671 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.0027005 | 5.5 | 2017 | 2016-10-04 | B | 7 | 0.005401 | 2.1016e-05
1 | 13490190 | 2016-09-12 09:55 | 2016-09-12 11:00 | 65 | 38 | 2470 | 0.0074176 | 0.007075 | 0.00011412 | NAPA ID:24335 TP_TAURANGA 11 GXP > TP_TAURANGA 11kV > PYES PA | 11 | Planned | 024335 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | CB12 | NONE | repair o/h 11kv line | F4 | PYES PA | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.0035375 | 5.5 | 2017 | 2016-09-12 | B | 38 | 0.007075 | 0.00011412
1 | 13490192 | 2016-09-09 14:12 | 2016-09-09 15:29 | 76 | 1 | 76.9 | 0.00023094 | 0.000221 | 3.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 843542 | FUSE - ELEMENT/LINK (HV) | Fuses 6411. Reload reliven | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.000221 | 11 | 2017 | 2016-09-09 | C | 1 | 0.000221 | 3.0031e-06
1 | 13506899 | 2016-10-05 10:00 | 2016-10-05 10:25 | 25 | 5 | 125 | 0.00037528 | 0.00033 | 1.5011e-05 | NAPA ID:23428 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 023428 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5090 | NONE | To install a 400V Fuse Disconnector on TC5090. Works location: Peria Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000165 | 5.5 | 2017 | 2016-10-05 | B | 5 | 0.00033 | 1.5011e-05
1 | 13506976 | 2016-10-05 12:35 | 2016-10-05 14:12 | 97 | 3 | 291 | 0.00087366 | 0.000846 | 9.0068e-06 | NAPA ID:23429 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 023429 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC5655 | NONE | To install a 400V Disconnector. Works location: Station Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000423 | 5.5 | 2017 | 2016-10-05 | B | 3 | 0.000846 | 9.0068e-06
1 | 13507036 | 2016-10-05 09:15 | 2016-10-05 13:40 | 265 | 6 | 1590 | 0.0047736 | 0.004719 | 1.8014e-05 | NAPA ID:23610 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 023610 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC206 | NONE | To replace the 11kV Fuse arm, 400V Spreader arm & install a 400V fuse disconnector. Works location: Peria Rd, Matamata. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.0023595 | 5.5 | 2017 | 2016-10-05 | B | 6 | 0.004719 | 1.8014e-05
1 | 13507055 | 2016-09-09 18:02 | 2016-09-09 18:32 | 30 | 72 | 2160 | 0.0064868 | 0.005838 | 0.00021623 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 9376/2 | FUSE - ELEMENT/LINK (HV) | Found Sw/Gear 9376/2 tripped. Patrolled O/H line, cut branches from line, Isolated Sw/Gear 9376 between SE6-223 & SE6-009. Changed fuse and relivened. 2 x fuses were blown. All 3 fuses replaced | F4 | KAITUNA | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.005838 | 11 | 2017 | 2016-09-09 | C | 72 | 0.005838 | 0.00021623
1 | 13507458 | 2016-10-09 08:15 | 2016-10-09 14:36 | 381 | 1 | 381 | 0.0011438 | 0.001134 | 3.0021e-06 | NAPA ID:23753 TP_TE MATAI GXP > TE PUKE SUB > RANGIURU | 11.00000000 | Planned | 023753 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SE6-076 | NONE | Replace Long & Crawford RMU with ABB Safe Link CFC and 2 sets of cross arms. Works location: Rangiuru Rd, Te Puke. WO 30027170 | F1 | RANGIURU | TE MATAI | Tauranga | TE PUKE SUB | Eastern Electricity | POWERCO | 0.000567 | 5.5 | 2017 | 2016-10-09 | B | 1 | 0.001134 | 3.0021e-06
1 | 13508309 | 2016-09-09 20:28 | 2016-09-09 21:21 | 53 | 5 | 265 | 0.00079584 | 0.00075 | 1.5016e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 709795 | CONDUCTOR - REPAIR/REHANG | Lines down across the road. Caller no longer on site Tureene advised it's an HV line - no permission to touch. 1 span is down. will try to make it safe. Called hub to advise. told control. Isolated at fuses PU446 Lines repaired Used 1 x 3amp fuse, 2mtrs conductor, 2 x sleeves | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.00075 | 11 | 2017 | 2016-09-09 | C | 5 | 0.00075 | 1.5016e-05
1 | 13508548 | 2016-09-09 21:33 | 2016-09-09 23:17 | 104 | 26 | 2704 | 0.0081206 | 0.007886 | 7.8082e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711685 | CONDUCTOR - REPAIR/REHANG | Fuses found blown at Fuses NG404 Lines Down found at Pole 711685 Isolated at Fuses NG404 Used 15 mtrs conductor, 4 x sleeves | F4 | NGARIKI RD | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.007886 | 11 | 2017 | 2016-09-09 | C | 26 | 0.007886 | 7.8082e-05
1 | 13509127 | 2016-09-09 21:13 | 2016-09-09 22:57 | 104 | 1 | 104 | 0.00031233 | 0.000303 | 3.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 702026 | CONDUCTOR - REPAIR/REHANG | Fuse found blown at Fuses 8425 also conductor broken at Pole 702026. Isolated at Fuses 8425 used 4 mtrs conductor, 4 x sleeves 1 x 3amp fuse | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000303 | 11 | 2017 | 2016-09-09 | C | 1 | 0.000303 | 3.0031e-06
1 | 13509683 | 2016-09-09 20:30 | 2016-09-09 23:05 | 155 | 6 | 931 | 0.0027959 | 0.002741 | 1.8019e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 813902 | FUSE - ELEMENT/LINK (HV) | When closing please check OMS 13463658 and 13509910 - both SH 53 Fuses found blown at Fuses 7201- cause unknown Used 3 x 15 amp fuses | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.002741 | 11 | 2017 | 2016-09-09 | C | 6 | 0.002741 | 1.8019e-05
1 | 13509867 | 2016-09-09 21:16 | 2016-09-09 23:01 | 105 | 3 | 315.1 | 0.0009463 | 0.000919 | 9.0094e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8425 | FUSE - ELEMENT/LINK (HV) | Fuses 8425 replaced. Storm related. | F4 | BROOKLANDS 7 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.000919 | 11 | 2017 | 2016-09-09 | C | 3 | 0.000919 | 9.0094e-06
1 | 13510346 | 2016-09-09 22:04 | 2016-09-10 00:57 | 173 | 665 | 49618.3333 | 0.14901 | 0.14302 | 0.0016127 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | P11729 | UNKNOWN | RS 10303 Tripped A, B Ph E/F Recloser not on map Links 6 dressed open to make job Oppossum found during sectionlising at Pole P11729 - cleared using hot sticks | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.14302 | 11 | 2017 | 2016-09-09 | C | 665 | 0.14302 | 0.0016127
1 | 13512209 | 2016-09-09 23:54 | 2016-09-10 05:06 | 311 | 172 | 11483.4 | 0.034487 | 0.032936 | 0.00051654 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | I13280 | NONE | Recloser RC34 on CB 4 feeder tripped to L/O. E/F flag. Line sectionalised & patrolled. Possum located & removed from pole I13280. Pole had no possum guard. Will be addressed by f/man. Some delays in restoration due to f/man becoming stuck in a paddock while patrolling line over very difficult terrain. All supply restored. | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.032936 | 11 | 2017 | 2016-09-09 | C | 172 | 0.032936 | 0.00051654
1 | 13512899 | 2016-09-10 01:47 | 2016-09-10 04:29 | 161 | 1 | 161.6333 | 0.00048541 | 0.000476 | 3.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 366545 | FUSE - ELEMENT/LINK (HV) | fuses found blown at transfotmer 2615W - Cause Unknown Used 2 x 2 amp fuses | F4 | LAKE ALICE | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.000476 | 11 | 2017 | 2016-09-10 | C | 1 | 0.000476 | 3.0031e-06
1 | 13513147 | 2016-09-10 04:56 | 2016-09-10 11:49 | 413 | 122 | 30244.0667 | 0.090827 | 0.089727 | 0.00036638 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VANDALISM | ABS 709 | POLE | Car V Pole reported by Fire services Event # F2148122. Recloser 4236 open. ndr 047263. 11.5 Pole, 1 x HT xarm, 3 x HT insulators, top and bottom blocks. | F4 | TURAKINA | MARTON | Wanganui | PUKEPAPA SUB | Western Electricity | POWERCO | 0.089727 | 11 | 2017 | 2016-09-10 | C | 122 | 0.089727 | 0.00036638
1 | 13513492 | 2016-09-10 08:49 | 2016-09-10 11:09 | 139 | 1 | 139.5833 | 0.00041919 | 0.00041 | 3.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | M9 | FUSE - ELEMENT/LINK (HV) | 13513509 linked 2 X 10 Amp | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.00041 | 11 | 2017 | 2016-09-10 | C | 1 | 0.00041 | 3.0031e-06
1 | 13514325 | 2016-09-10 10:32 | 2016-09-10 13:23 | 170 | 496 | 30974.1333 | 0.09302 | 0.08855 | 0.0014896 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 6 | UNKNOWN | Oakura CB6 tripped on E/F. Lines patrolled and no fault found. Severe weather conditions at the time. | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.08855 | 11 | 2017 | 2016-09-10 | C | 496 | 0.08855 | 0.0014896
1 | 13517716 | 2016-09-10 11:29 | 2016-09-10 14:40 | 190 | 1 | 190.6 | 0.0005724 | 0.000563 | 3.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FP1647 | FUSE - ELEMENT/LINK (HV) | Replaced 3 x 5amp HT fuses at FP1647 | F4 | HARRIS BLOCK | KINLEITH 33 | Valley | BAIRD ROAD SUB | Eastern Electricity | POWERCO | 0.000563 | 11 | 2017 | 2016-09-10 | C | 1 | 0.000563 | 3.0031e-06
1 | 13517980 | 2016-09-10 12:59 | 2016-09-10 14:30 | 91 | 342 | 30222 | 0.090761 | 0.087679 | 0.0010271 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | TD3-123 | CONDUCTOR - REPAIR/REHANG | Feeder fault Started sectionalising Public reported tree in line to faultman . Found wattle tree in line, removed and relivened | F3 | STERLING GATE | TAURANGA 31 | Tauranga | BETHLEHEM SUB | Eastern Electricity | POWERCO | 0.087679 | 11 | 2017 | 2016-09-10 | C | 342 | 0.087679 | 0.0010271
1 | 13519059 | 2016-09-10 15:41 | 2016-09-10 16:17 | 36 | 32 | 1152 | 0.0034596 | 0.003171 | 9.61e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 719408 | CONDUCTOR - REPAIR/REHANG | Lines down at Pole 719408. 3M x 16mm Copper | F1 | MANAIA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.003171 | 11 | 2017 | 2016-09-10 | C | 32 | 0.003171 | 9.61e-05
1 | 13519171 | 2016-09-10 16:27 | 2016-09-10 17:30 | 63 | 24 | 1512 | 0.0045407 | 0.004324 | 7.2075e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 758033 | INSULATOR | Lines down at pole 758033. 1 X Ht Insulator 2 X Armor Rods | F4 | INLAND COAST | CARRINGTON ST 33 | Taranaki | OAKURA SUB | Western Electricity | POWERCO | 0.004324 | 11 | 2017 | 2016-09-10 | C | 24 | 0.004324 | 7.2075e-05
1 | 13519584 | 2016-09-10 19:04 | 2016-09-10 20:45 | 101 | 25 | 2507.9 | 0.0075316 | 0.007306 | 7.5078e-05 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5348 and 12109 | FUSE - ELEMENT/LINK (HV) | Replaced 1x 10a fuse @ 5348 and 2x 8a fuses @ 12109 | F4 | RATAPIKO | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.007306 | 6.6 | 2017 | 2016-09-10 | C | 25 | 0.007306 | 7.5078e-05
1 | 13522518 | 2016-09-11 18:46 | 2016-09-12 10:31 | 945 | 84 | 7015.1333 | 0.021067 | 0.02031 | 0.00025226 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | T7/173 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | Found 2x HV fuses blown and on closing the holder broke replaced holder on OMS 13522518 . On returning to replace fuses found transformer blown and faultman discussed with the customer who is happy for the transformer to be replaced in the morning . Followup job created .Section of line from ASB R52 isolated to replace broken drop out holder @ trransformer T7/173. | F4 | FONTERRA WWTP | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.02031 | 11 | 2017 | 2016-09-11 | C | 84 | 0.02031 | 0.00025226
1 | 13524824 | 2016-09-12 12:03 | 2016-09-12 13:12 | 69 | 34 | 2346 | 0.0070452 | 0.006738 | 0.0001021 | Referral | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 5607 | FUSE - HOLDER/BASE - REPLACE FULL SET (HV) | Require urgent shut from fuses 5612 to replace fuses 5607. All 3 Drop out fuses 5607 replaced. | F5 | CLOTON RD SOUTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.006738 | 11 | 2017 | 2016-09-12 | C | 34 | 0.006738 | 0.0001021
1 | 13525085 | 2016-09-12 07:20 | 2016-09-12 08:28 | 68 | 48 | 3264 | 0.0098021 | 0.009369 | 0.00014415 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 712061 | CONDUCTOR - REPAIR/REHANG | Line down at pole 712061. Isolated at ABS NG237 & NG248. Line repaired. Materials, 3x binders, 2 Namu sleeves | F4 | RAHOTU | OPUNAKE | Taranaki | NGARIKI SUB | Western Electricity | POWERCO | 0.009369 | 11 | 2017 | 2016-09-12 | C | 48 | 0.009369 | 0.00014415
1 | 13533146 | 2016-09-12 07:31 | 2016-09-12 08:08 | 37 | 7965 | 203771.0333 | 0.61194 | 0.54018 | 0.02392 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 829192 | CONDUCTOR - REPAIR/REHANG | MST GXP CB2132 tripped on Neutral Time OC. NOTE: This circuit was supplying TeOreOre, Akura, Awatoitoi and Tinui Subs due to a planned outage on Akura T2 Bank. (Loss of supply to the 4 Subs). Switching was reversed at Akura and supplied via CB2212 at MST GXP. Remaining Subs supplied from 33kV Bus with ABS S190 Closed. Patrol carried out with a broken conductor found at Pole 829192. (Isolation carried out between TeOreOre and MST GXP). Conductor rehung with 2 Insulators replaced including10m Conductor. Relivened OK. | S1 | TE ORE ORE 33KV | MASTERTON | Wairarapa | TP_MASTERTON | Western Electricity | POWERCO | 0.54018 | 33 | 2017 | 2016-09-12 | C | 7965 | 0.54018 | 0.02392
1 | 13549723 | 2016-10-03 10:12 | 2016-10-03 12:10 | 118 | 25 | 2950 | 0.0088569 | 0.008631 | 7.5059e-05 | NAPA ID:23830 TP_TAURANGA 33 GXP > OMOKOROA SUB > TE PUNA | 11 | Planned | 023830 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3-042 | NONE | Change transformer. Works location: Wallace Rd, Omokoroa. WO 30026812 | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.0043155 | 5.5 | 2017 | 2016-10-03 | B | 25 | 0.008631 | 7.5059e-05
1 | 13549854 | 2016-10-07 09:51 | 2016-10-07 10:51 | 60 | 4 | 240 | 0.00072053 | 0.000684 | 1.2009e-05 | NAPA ID:23703 TP_HINUERA GXP > BROWNE STREET SUB > STATION RD | 11 | Planned | 023703 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3288 | NONE | To replace the 11kV Fuse arm, 400V Spreader arm & install a 400V Disconnector. Works location: Gunn Rd, Waharoa. WO 30019182 | F4 | STATION RD | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000342 | 5.5 | 2017 | 2016-10-07 | B | 4 | 0.000684 | 1.2009e-05
1 | 13550345 | 2016-10-03 09:30 | 2016-10-03 13:37 | 247 | 4 | 988 | 0.0029663 | 0.00293 | 1.2009e-05 | NAPA ID:24013 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 024013 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2-082 | NONE | Off-load Transformer TC2-084 to replace X-arms and install new Spur line Fuses FP1836 at pole 207990. Works location: Pahoia Rd, Tauranga. WO 30032224 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.001465 | 5.5 | 2017 | 2016-10-03 | B | 4 | 0.00293 | 1.2009e-05
1 | 13550360 | 2016-10-03 09:45 | 2016-10-03 12:42 | 177 | 338 | 1720.5833 | 0.0051658 | 0.002121 | 0.0010148 | NAPA ID:24144 TP_CARRINGTON GXP > KATERE SUB > KATERE 12 | 11 | Planned | 024144 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Magnefix 204 | NONE | DNO 160802 Magnefix 204/3 fuse caps and clean cable terms. Switching (-01) is to remotely isolate supply to ISOLATE @ magnefix 385/1. Switching (-03) is to remotely isolate supply to RESTORE @ magnefix 385/1. Works location: Erica place. WO 30031438 | F2 | KATERE 12 | CARRINGTON ST 33 | Taranaki | KATERE SUB | Western Electricity | POWERCO | 0.0010605 | 5.5 | 2017 | 2016-10-03 | B | 338 | 0.002121 | 0.0010148
1 | 13550414 | 2016-10-11 09:00 | 2016-10-11 13:31 | 271 | 81 | 21967.2 | 0.065947 | 0.065217 | 0.00024317 | NAPA ID:23212 TP_PIAKO GXP > PIAKO SUB > KEREONE | 11 | Planned | 023212 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 781 | NONE | Replace ABS 781. Works location: Morrinsville Walton Rd, Walton. WO 30008220 | F4 | KEREONE | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.032608 | 5.5 | 2017 | 2016-10-11 | B | 81 | 0.065217 | 0.00024317
1 | 13551433 | 2016-10-03 09:15 | 2016-10-03 11:40 | 145 | 3 | 435 | 0.001306 | 0.001278 | 9.007e-06 | NAPA ID:24020 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 024020 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC2-084 | NONE | Worksite 1 - Off-load Transformer TC2-084 to replace X-arms and install new Spur line Fuses FP1835 at pole 209000. Worksite 2 - Change pin X-arm at poles 207974, 207973. Works location: Pahoia Rd, Tauranga. WO 30032224 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.000639 | 5.5 | 2017 | 2016-10-03 | B | 3 | 0.001278 | 9.007e-06
1 | 13551474 | 2016-10-04 09:05 | 2016-10-04 11:09 | 124 | 11 | 1364 | 0.0040951 | 0.003996 | 3.3025e-05 | NAPA ID:23203 TP_HINUERA GXP > LAKE ROAD SUB > TOTMANS RD | 11 | Planned | 023203 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole E12591 | NONE | Replace X arms at poles E12591,E12589, E12588, E12579. Works location: Nicholson Rd, Hinuera. WO 30027292 | F4 | TOTMANS RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 0.001998 | 5.5 | 2017 | 2016-10-04 | B | 11 | 0.003996 | 3.3025e-05
1 | 13551535 | 2016-10-04 08:40 | 2016-10-04 13:17 | 277 | 9 | 2493 | 0.0074848 | 0.007403 | 2.7021e-05 | NAPA ID:23354 TP_STRATFORD GXP > ELTHAM SUB > ELTHAM TOWN NORTH | 11 | Planned | 023354 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 6078 | NONE | Replace Transformer Structure. Works location: Hill St. WO 30017305 | F1 | ELTHAM TOWN NORTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.0037015 | 5.5 | 2017 | 2016-10-04 | B | 9 | 0.007403 | 2.7021e-05
1 | 13551625 | 2016-09-12 11:55 | 2016-09-12 16:20 | 265 | 1 | 265.3167 | 0.00079677 | 0.000787 | 3.003e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 794238 | FUSE - ELEMENT/LINK (HV) | Reload at fuses 1028 2 x 10A Bird Strike | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000787 | 11 | 2017 | 2016-09-12 | C | 1 | 0.000787 | 3.003e-06
1 | 13551957 | 2016-09-12 14:32 | 2016-09-12 16:15 | 103 | 26 | 2678 | 0.0080423 | 0.007808 | 7.808e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P11390 | CONDUCTOR - REPAIR/REHANG | 2 HT fuses found tripped at S!!. Patrol found 2 floating conductors found at poles P11390 and P10342. 3 Insulators replaced along with binders and 2 HT fuses (10A). Relivened OK. | F4 | HUKANUI | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.007808 | 11 | 2017 | 2016-09-12 | C | 26 | 0.007808 | 7.808e-05
1 | 13552735 | 2016-10-05 09:00 | 2016-10-05 11:25 | 145 | 12 | 1740 | 0.005224 | 0.005115 | 3.6027e-05 | NAPA ID:23685 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 12 | 11 | Planned | 023685 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 2314N | NONE | 1: Off loading Transformer 1071 to work on the LV. 2: Install new 11kV TX 2314N at pole 752555 and connect to previously installed 11kV Fuses 8142. (At completion of livening new TX 2314N the fuse number 8142 will be removed). Works location: Junction Rd, New Plymouth. WO 30020618 | F3 | BROOKLANDS 12 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.0025575 | 5.5 | 2017 | 2016-10-05 | B | 12 | 0.005115 | 3.6027e-05
1 | 13552877 | 2016-09-12 14:23 | 2016-09-12 15:48 | 84 | 5 | 84.1333 | 0.00025266 | 0.000207 | 3.003e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - OTHER | 804129 | FUSE - ELEMENT/LINK (HV) | 1R DIGGER PULLED LINES DOWN under CAC 42871 Lines untangled NDR 41489 Reload at Transformer X1433 used 2 x 2A HV Fuses 1 x 61A HRC Fuse | F4 | TUTAENUI | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.000207 | 11 | 2017 | 2016-09-12 | C | 5 | 0.000207 | 3.003e-06
1 | 13553039 | 2016-10-06 09:30 | 2016-10-06 14:31 | 301 | 4 | 1204 | 0.0036147 | 0.003578 | 1.2009e-05 | NAPA ID:24044 TP_TAURANGA 33 GXP > OMOKOROA SUB > PAHOIA | 11 | Planned | 024044 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses FP1836 | NONE | Change 11kV Xarms beyond Fuses FP1836 (pole 207990). Works location: Pahoia Rd, Tauranga. WO 30032224 | F4 | PAHOIA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.001789 | 5.5 | 2017 | 2016-10-06 | B | 4 | 0.003578 | 1.2009e-05
1 | 13553082 | 2016-09-12 18:37 | 2016-09-12 20:46 | 129 | 3 | 387 | 0.0011622 | 0.001135 | 9.0092e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 810797 | BINDER | Floating conductor at pole 810797. Fuses 7352 opened and tagged for repairs. | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.001135 | 11 | 2017 | 2016-09-12 | C | 3 | 0.001135 | 9.0092e-06
1 | 13553284 | 2016-09-09 13:18 | 2016-09-09 15:13 | 115 | 53 | 6095 | 0.018304 | 0.017826 | 0.00015917 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 760075 | BINDER | Outage created for 13478355 | F4 | KOHETE RD | STRATFORD | Taranaki | MOTUKAWA SUB | Western Electricity | POWERCO | 0.017826 | 6.6 | 2017 | 2016-09-09 | C | 53 | 0.017826 | 0.00015917
1 | 13553377 | 2016-09-09 14:12 | 2016-09-09 15:29 | 77 | 1 | 77 | 0.00023124 | 0.000222 | 3.0031e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 843544 | CONDUCTOR - REPAIR/REHANG | Outage created for OMS Fault 13484674 | F4 | AUROA | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.000222 | 11 | 2017 | 2016-09-09 | C | 1 | 0.000222 | 3.0031e-06
1 | 13553531 | 2016-10-04 08:45 | 2016-10-04 15:03 | 378 | 12 | 4536 | 0.013618 | 0.01351 | 3.6028e-05 | NAPA ID:23289 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023289 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 8433 | NONE | change 11kv poles and xarms. Works location: Lincoln Rd. WO 30030730 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.006755 | 5.5 | 2017 | 2016-10-04 | B | 12 | 0.01351 | 3.6028e-05
1 | 13553621 | 2016-09-12 15:21 | 2016-09-13 14:20 | 1379 | 178 | 48326.1333 | 0.14513 | 0.14352 | 0.0014775 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | Cable Fault | CABLE - REPLACE 5 METRES OR MORE | Recloser S6040 tripped to L/O. B Ph O/C flag. Sectionalised and found Marine cable faulty. Isolated at links SC3-090. Left off until Tuesday to supply generators to customers & decide what to do with faulty cable. Downers to follow up on Tuesday 13/09/16 Testing of Marine Cable shows cable is faulted. 14/09/16 DNO 160914 16/09/16 | F4/F5 | MATAKANA RD | TAURANGA 31 | Tauranga | AONGATETE SUB | Eastern Electricity | POWERCO | 0.14352 | 11 | 2017 | 2016-09-12 | C | 178 | 0.14352 | 0.0014775
1 | 13553851 | 2016-10-01 09:00 | 2016-10-01 10:53 | 113 | 61 | 6893 | 0.020696 | 0.020146 | 0.00018315 | NAPA ID:23745 TP_MANGAMAIRE GXP > MANGAMUTU SUB > RUAWHATA | 11 | Planned | 023745 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 10318 | NONE | To install 11kv fuses 10318 on pole p23398. Works location: Ruawhata West Rd. WO 30025077 | F4 | RUAWHATA | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.010073 | 5.5 | 2017 | 2016-10-01 | B | 61 | 0.020146 | 0.00018315
1 | 13554495 | 2016-09-28 09:22 | 2016-09-28 10:48 | 86 | 129 | 11117.65 | 0.033381 | 0.032219 | 0.00038733 | NAPA ID:24301 TP_KOPU GXP > KEREPEHI SUB > KAIHERE | 11 | Planned | 024301 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3221 | NONE | Create break on de-energised Line at pole O019. Replace 11kV P/M Transformer TC3221 with G/M 200kVA. Close break at pole O019 (Line de-energised). Works location: Kerepehi Town Rd, Paeroa. WO 30031355. This job was cancelled half way through switching due to customer complaining that they were not advertised. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.016109 | 5.5 | 2017 | 2016-09-28 | B | 129 | 0.032219 | 0.00038733
1 | 13555518 | 2016-09-13 09:35 | 2016-09-13 13:09 | 214 | 49 | 10486 | 0.03149 | 0.031048 | 0.00014715 | Referral | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 732626 | POLE | Replace pole after Car accident on 13/09/16. Pole 732626 Replaced, Isolation at ABS's 6155 & 5958. Materials 1x11m concrete Pole, 1x9m concrete pole, 1x double LV termination arm, 1x 11kV pin insulator, 1x LV pin insulator. NDR N100225 | F3 | ELTHAM TOWN SOUTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.031048 | 11 | 2017 | 2016-09-13 | C | 49 | 0.031048 | 0.00014715
1 | 13556165 | 2016-09-13 06:04 | 2016-09-13 07:41 | 96 | 25 | 2407.0833 | 0.0072286 | 0.007003 | 7.5076e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 739665 | FUSE - ELEMENT/LINK (HV) | 2x8 amp HV fuse blown at 4957, Line patrolled, reloaded & relivened. Unknown cause | F3 | TOKO | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.007003 | 11 | 2017 | 2016-09-13 | C | 25 | 0.007003 | 7.5076e-05
1 | 13558473 | 2016-09-13 07:03 | 2016-09-13 09:38 | 154 | 9 | 1392.3 | 0.0041811 | 0.0041 | 2.7027e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 819797 | FUSE - ELEMENT/LINK (HV) | Reload at fuses 7609 2 x 10A Fusese and 1 x Candle cause unknown | F3/F4 | PARK RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.0041 | 11 | 2017 | 2016-09-13 | C | 9 | 0.0041 | 2.7027e-05
1 | 13558713 | 2016-09-15 11:15 | 2016-09-15 12:55 | 100 | 5 | 500 | 0.0015015 | 0.001456 | 1.5015e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 708114 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer 4120T Isolated as it is Faulty & will need replaceing. HV needed to be Isolated to be able to replace transformer Isolated at fuses 5333 Used 1 x 15 kVA 3 ph transformer | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001456 | 11 | 2017 | 2016-09-15 | C | 5 | 0.001456 | 1.5015e-05
1 | 13558741 | 2016-10-04 09:45 | 2016-10-04 14:00 | 255 | 149 | 37995 | 0.11407 | 0.11273 | 0.00044734 | NAPA ID:23940 TP_WAIKINO GXP > PAEROA SUB > BENNETT ST | 11 | Planned | 023940 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 859981 | NONE | Change pole# 859981. Works location: Alley Memorial Rd, Paeroa. WO 30010389 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.056365 | 5.5 | 2017 | 2016-10-04 | B | 149 | 0.11273 | 0.00044734
1 | 13560121 | 2016-09-29 09:15 | 2016-09-29 16:08 | 412 | 65 | 26817.9167 | 0.080521 | 0.079935 | 0.00019516 | NAPA ID:24375 TP_MANGAMAIRE GXP > PONGAROA SUB > HOROEKA | 11 | Planned | 024375 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV ABS V7 | NONE | Tree removal. Works location: Waihi Valley Rd. WO 30026290 | F4 | HOROEKA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.039968 | 5.5 | 2017 | 2016-09-29 | B | 65 | 0.079935 | 0.00019516
1 | 13560605 | 2016-10-03 08:59 | 2016-10-03 14:38 | 339 | 3 | 1017 | 0.0030534 | 0.003026 | 9.007e-06 | NAPA ID:23122 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 023122 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole836458 | NONE | Change 11kv pole 836458 and TX T632. Works location: Matahiwi Rd, Masterton. WO 30031325 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.001513 | 5.5 | 2017 | 2016-10-03 | B | 3 | 0.003026 | 9.007e-06
1 | 13560831 | 2016-10-03 09:37 | 2016-10-03 11:56 | 139 | 1 | 139 | 0.00041733 | 0.000408 | 3.0023e-06 | NAPA ID:23185 TP_MATAROA GXP > TAIHAPE SUB > MANGAWEKA | 11 | Planned | 023185 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2953 | NONE | Isolation of 11 kv line to remove recloser 4199/2 for new upgrade on settings and control box, same recloser to be reinstalled once work is completed, no change to scada required, but the Scada team will be informed of the work for comms reasons. Works location: Kawhatau Valley Rd, Taihape. WO 30024630 | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000204 | 5.5 | 2017 | 2016-10-03 | B | 1 | 0.000408 | 3.0023e-06
1 | 13560835 | 2016-10-04 10:00 | 2016-10-04 12:35 | 155 | 10 | 1550 | 0.0046536 | 0.004563 | 3.0023e-05 | NAPA ID:24087 TP_KOPU GXP > COROMANDEL SUB > COLVILLE | 11 | Planned | 024087 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole V2126 | NONE | Replace Defected XARMS. Works location: Captain Amodeo Rd, Coromandel. WO 30014048 | F4/F5 | COLVILLE | KOPU | Valley | COROMANDEL SUB | Eastern Electricity | POWERCO | 0.0022815 | 5.5 | 2017 | 2016-10-04 | B | 10 | 0.004563 | 3.0023e-05
1 | 13561053 | 2016-10-03 08:34 | 2016-10-03 09:27 | 53 | 3 | 159 | 0.00047737 | 0.00045 | 9.007e-06 | NAPA ID:23272 TP_MASTERTON GXP > AKURA SUB > MOUNT BRUCE | 11 | Planned | 023272 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T653 | NONE | Replace faulty 11kv fuses at t653. Works location: Upper plain Rd, Masterton. WO 30025246 | F4 | MOUNT BRUCE | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.000225 | 5.5 | 2017 | 2016-10-03 | B | 3 | 0.00045 | 9.007e-06
1 | 13561208 | 2016-10-03 09:55 | 2016-10-03 15:07 | 312 | 38 | 11856 | 0.035596 | 0.035253 | 0.00011409 | NAPA ID:24046 TP_BRUNSWICK GXP > KAI IWI SUB > MAXWELL | 11 | Planned | 024046 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 773972 | NONE | Replace all X arms on pole 773972 including rotten 11kv X arms. Works location: Hwy 3, Maxwell. WO 30027866 | F4 | MAXWELL | BRUNSWICK | Wanganui | KAI IWI SUB | Western Electricity | POWERCO | 0.017626 | 5.5 | 2017 | 2016-10-03 | B | 38 | 0.035253 | 0.00011409
1 | 13561751 | 2016-10-04 20:07 | 2016-10-05 03:50 | 463 | 14 | 6482 | 0.019461 | 0.019334 | 4.2032e-05 | NAPA ID:23563 TP_TAURANGA 33 GXP > WAIHI ROAD SUB > TAKITIMU DR | 11 | Planned | 023563 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TL4-010 | NONE | Replace TX TL4-010 and LV Frame. Works location: Second Ave, Tauranga. WO 30024668 | F2 | TAKITIMU DR | TAURANGA 31 | Tauranga | WAIHI ROAD SUB | Eastern Electricity | POWERCO | 0.009667 | 5.5 | 2017 | 2016-10-04 | B | 14 | 0.019334 | 4.2032e-05
1 | 13563832 | 2016-09-13 13:08 | 2016-09-13 13:09 | 1 | 1569 | 1569 | 0.0047118 | 0 | 0.0047118 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 8056 | AIR BREAK SWITCH - ABS (HV) | Initial Reports of Part Power / No Power in Featherston Township - Patrol carried out with a blown Jumper found at ABS 8056. CB C911 Tripped on EF when backfeed ABS S587 was closed. A 1 minute outage was required on both CB C911 and CB C916 to Open Defective ABS 8056. Power then restored via CB 911 OK. Liveline work was carried out to cut away the jumpers from ABS 8056 - ABS has DNO 160192 applied. (Flashed over, may need replacement). | F3/F4 | WAITE ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0 | 11 | 2017 | 2016-09-13 | C | 1569 | 0 | 0.0047118
1 | 13567009 | 2016-09-27 09:00 | 2016-09-27 11:31 | 151 | 16 | 2416 | 0.0072542 | 0.00711 | 4.8041e-05 | NAPA ID:23937 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023937 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 848052 | NONE | Replace & repair Rusting 70mm Cu Deadends @ 499/2 Pole848052. Works location: Lepper Rd, Inglewood. WO 30032254 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.003555 | 5.5 | 2017 | 2016-09-27 | B | 16 | 0.00711 | 4.8041e-05
1 | 13567043 | 2016-10-04 10:30 | 2016-10-04 16:12 | 342 | 88 | 30166.4 | 0.090569 | 0.089776 | 0.0002642 | NAPA ID:21822 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 021822 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV E34 | NONE | Cutting trees - two crews at different sites working at the same time. Works location: Taonui Rd. WO 30026290 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.044888 | 5.5 | 2017 | 2016-10-04 | B | 88 | 0.089776 | 0.0002642
1 | 13567345 | 2016-09-13 15:54 | 2016-09-13 18:38 | 164 | 244 | 18257.2167 | 0.054827 | 0.052629 | 0.00083785 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 747013 | INSULATOR | recloser 499 Trip, A,B,C O/C E/F. Line patrolled & sectionalised. 1 insulator blown at pole 747013. insulator replaced. Isolation at ABS's 229 & 548. | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.052629 | 11 | 2017 | 2016-09-13 | C | 244 | 0.052629 | 0.00083785
1 | 13567670 | 2016-09-13 16:45 | 2016-09-13 20:41 | 236 | 155 | 19841.45 | 0.059585 | 0.058188 | 0.0011201 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 760838 | BINDER | Cb a11 trip O/C E/F found broken binder at pole 760838 | F5 | OTARAOA RD | HUIRANGI | Taranaki | MCKEE SUB | Western Electricity | POWERCO | 0.058188 | 11 | 2017 | 2016-09-13 | C | 155 | 0.058188 | 0.0011201
1 | 13570802 | 2016-09-13 23:41 | 2016-09-14 05:07 | 326 | 297 | 33305.2167 | 0.10002 | 0.097341 | 0.0012222 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X1374 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | recloser 717 trip line patrolled and found blown fuse 1 X DDO at Transformer X1374 | F3/F4 | PAREWANUI | MARTON | Wanganui | BULLS SUB | Western Electricity | POWERCO | 0.097341 | 11 | 2017 | 2016-09-13 | C | 297 | 0.097341 | 0.0012222
1 | 13575036 | 2016-09-14 03:07 | 2016-09-14 04:18 | 70 | 317 | 15623.8 | 0.046919 | 0.044062 | 0.0012703 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Karinaga CB23 tripped E/F Flag. Line patrolled and nothing found. | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.044062 | 11 | 2017 | 2016-09-14 | C | 317 | 0.044062 | 0.0012703
1 | 13576713 | 2016-09-14 04:43 | 2016-09-14 09:27 | 284 | 714 | 92426.1167 | 0.27756 | 0.27113 | 0.0035946 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 757825 | INSULATOR | CB 10 Tripped O/C E/F Faulty Insulator found during sectionlising at Pole 757825 Isolated at ABS 343 & Sw/Gear 196/3 with backfeed via Sw/Gear 30/3 Insulator replaced - Used 1 x HV Insultor, 1 x binder | F3 | CITY 10 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.27113 | 11 | 2017 | 2016-09-14 | C | 714 | 0.27113 | 0.0035946
1 | 13577785 | 2016-09-14 04:42 | 2016-09-14 06:14 | 91 | 353 | 21105.7167 | 0.063381 | 0.0602 | 0.0010601 |  | 6.6 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN |  | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.0602 | 6.6 | 2017 | 2016-09-14 | C | 353 | 0.0602 | 0.0010601
1 | 13579239 | 2016-09-14 04:59 | 2016-09-14 05:17 | 18 | 317 | 5563.35 | 0.016707 | 0.01385 | 0.00095196 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | Kairanga CB23 tripped on E/F. Line patrolled and no fault found. Pole P34988 has insulator that may be cause | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.01385 | 11 | 2017 | 2016-09-14 | C | 317 | 0.01385 | 0.00095196
1 | 13580774 | 2016-10-04 08:30 | 2016-10-04 15:33 | 423 | 4 | 1692 | 0.0050799 | 0.005043 | 1.2009e-05 | NAPA ID:23304 TP_MASTERTON GXP > CLAREVILLE SUB > CHESTER RD | 11 | Planned | 023304 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV Fuses 11014 | NONE | tree works to restrain 11kv and LV conductors. Works location: Chester Rd. WO 30026281 | F4 | CHESTER RD | MASTERTON | Wairarapa | CLAREVILLE SUB | Western Electricity | POWERCO | 0.0025215 | 5.5 | 2017 | 2016-10-04 | B | 4 | 0.005043 | 1.2009e-05
1 | 13580873 | 2016-09-29 09:04 | 2016-09-29 12:48 | 223 | 3 | 670.3 | 0.0020126 | 0.001985 | 9.0074e-06 | NAPA ID:23119 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 023119 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 834636 | NONE | 1. First AP to disconnect and remove span between pole 834635 & 834636 to create gap. 2. Second AP for replacement of cross arms and conductor from pole 834636 to end of line. 3. LLP at same time as second AP to replace fuses 7463 and cross arms on pole 834635. 4. Third AP to reconnect 11kV lines at pole 834635. Works Location: State Highway 2, Masterton. Work Order 30030270. | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.0009925 | 5.5 | 2017 | 2016-09-29 | B | 3 | 0.001985 | 9.0074e-06
1 | 13581058 | 2016-09-14 06:16 | 2016-09-14 08:10 | 113 | 18 | 2043.9 | 0.0061379 | 0.005975 | 5.4054e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | V83 | FUSE - ELEMENT/LINK (HV) | This is the outage job for 13580505 | F4 | TIRAUMEA | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.005975 | 11 | 2017 | 2016-09-14 | C | 18 | 0.005975 | 5.4054e-05
1 | 13581096 | 2016-10-04 10:20 | 2016-10-04 15:43 | 323 | 19 | 6144.6 | 0.018448 | 0.018276 | 5.7044e-05 | NAPA ID:23812 TP_MASTERTON GXP > TE ORE ORE SUB > WERAITI | 11 | Planned | 023812 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - VEGETATION CLEARANCE | 11kV pole 845860 | NONE | tree removal between poles 845860 841849. Works location: Ngahapi Rd. WO 30026281 | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.009138 | 5.5 | 2017 | 2016-10-04 | B | 19 | 0.018276 | 5.7044e-05
1 | 13581453 | 2016-10-04 09:38 | 2016-10-04 14:31 | 293 | 4 | 1173.3333 | 0.0035227 | 0.003486 | 1.2009e-05 | NAPA ID:23532 TP_MANGAMAIRE GXP > PONGAROA SUB > WAIONE | 11 | Planned | 023532 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P00693 | NONE | Replace softwood poles that have burnt at the top with new concrete poles. Works location: McLeod Rd. WO 30026320 | F5 | WAIONE | MANGAMAIRE | Manawatu | PONGAROA SUB | Western Electricity | POWERCO | 0.001743 | 5.5 | 2017 | 2016-10-04 | B | 4 | 0.003486 | 1.2009e-05
1 | 13581538 | 2016-10-04 09:25 | 2016-10-04 12:40 | 195 | 9 | 1755 | 0.0052691 | 0.005187 | 2.7021e-05 | NAPA ID:23739 TP_MATAROA GXP > TAIHAPE SUB > MATAROA A | 11 | Planned | 023739 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 795394 | NONE | replace 11 hardwood pole to gain extra height over the loading race. Works location: Pukanaua Rd, Taihape. WO 30030980 | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0025935 | 5.5 | 2017 | 2016-10-04 | B | 9 | 0.005187 | 2.7021e-05
1 | 13581702 | 2016-10-04 10:54 | 2016-10-04 13:38 | 164 | 20 | 3282.3167 | 0.0098545 | 0.009674 | 6.0046e-05 | NAPA ID:22956 TP_GREYTOWN GXP > TUHITARATA SUB | 11 | Planned | 022956 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 11kV ABS S702 | NONE | Maintenance on ABS S702, S701, S703, S704, S37, S38, S39, S40, S41, S42, S43, S44. Works location: Tuhitarata Zone Substation. WO 30020948 | F4 | KUMENGA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.004837 | 5.5 | 2017 | 2016-10-04 | B | 20 | 0.009674 | 6.0046e-05
1 | 13581738 | 2016-09-14 13:30 | 2016-09-14 14:28 | 58 | 1 | 58 | 0.00017418 | 0.000165 | 3.003e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 733832 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Single fuse found blown at Transformer 2108T - fuse blow on reload Transformer found to be faulty, isolated at fuses for transformer Transformer changed under own AP Used 1 x 30 kVA 3 ph transformer, 1 x 3 amp fuse | F4 | MANAIA RD | STRATFORD | Taranaki | KAPONGA SUB | Western Electricity | POWERCO | 0.000165 | 11 | 2017 | 2016-09-14 | C | 1 | 0.000165 | 3.003e-06
1 | 13581782 | 2016-10-04 09:00 | 2016-10-04 12:10 | 190 | 61 | 11590 | 0.034797 | 0.034247 | 0.00018314 | NAPA ID:23299 TP_GREYTOWN GXP > FEATHERSTON SUB > DAIRY FACTORY | 11 | Planned | 023299 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T991 | NONE | replace tx pole t991 and hardware. Works location: Kahutara Rd. WO 30030362 | F4 | DAIRY FACTORY | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.017123 | 5.5 | 2017 | 2016-10-04 | B | 61 | 0.034247 | 0.00018314
1 | 13581838 | 2016-09-14 10:03 | 2016-09-14 16:51 | 408 | 2 | 816.5667 | 0.0024522 | 0.002434 | 6.006e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 718390 | JUMPER | FM advised faulty tx needs to replace TX M4125 advised that this could take approx 1hr-2hrs called service hub and asked Tallia to get FM to advise all 3 customers of this outage 220,227,4 Sutherland Road what is happening. TRansformer Isolated at fuses at Transformer M4125, Transformer replace under own AP uSED 1 X 50 kVA 3 Ph transformer FM advised TX did not have to be replaced after all. They ended up finding a burnt up jumper on the neutral. This has been repaired and full power is restored. | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.002434 | 11 | 2017 | 2016-09-14 | C | 2 | 0.002434 | 6.006e-06
1 | 13581917 | 2016-09-15 11:45 | 2016-09-15 13:42 | 117 | 1 | 117 | 0.00035135 | 0.000342 | 3.0029e-06 | Referral | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | T1/18 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer T1/18 is suspected to be causing numerous trippings on tap fuses M9. The transformer is in very bad state with rust holes in the lid and requires replacement. Comprehensive before pictures of the existing transformer required. To be forwarded to Alicia Keirnan to assess for public safety Transformer T1/18 was replaced. | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000342 | 11 | 2017 | 2016-09-15 | C | 1 | 0.000342 | 3.0029e-06
1 | 13581989 | 2016-10-04 08:20 | 2016-10-04 15:06 | 406 | 18 | 7308 | 0.021941 | 0.021778 | 5.4042e-05 | NAPA ID:24003 TP_TAURANGA 33 GXP > OMOKOROA SUB > TE PUNA | 11 | Planned | 024003 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-058 | NONE | Replace Poles, hardware and conductors. Works location: Armstrong Rd. WO 30019163 | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.010889 | 5.5 | 2017 | 2016-10-04 | B | 18 | 0.021778 | 5.4042e-05
1 | 13581996 | 2016-10-05 08:30 | 2016-10-05 14:22 | 352 | 220 | 77440 | 0.2325 | 0.23051 | 0.0006605 | NAPA ID:23274 TP_GREYTOWN GXP > FEATHERSTON SUB > REVANS ST | 11 | Planned | 023274 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV 8056 | NONE | replace defective poles in south featherston. Works location: Reavans St, Featherston. WO 30030519 | F3/F4 | REVANS ST | GREYTOWN | Wairarapa | FEATHERSTON SUB | Western Electricity | POWERCO | 0.11526 | 5.5 | 2017 | 2016-10-05 | B | 220 | 0.23051 | 0.0006605
1 | 13582021 | 2016-10-05 10:00 | 2016-10-05 14:50 | 290 | 34 | 9860 | 0.029602 | 0.029296 | 0.00010208 | NAPA ID:24377 TP_BRUNSWICK GXP > PEAT ST SUB | 11 | Planned | 024377 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X3156 | NONE | Replace 400V switchgear for X3156.All 400V cables from X3156 will be shut down. Works location: Downes Ave, Wanganui. WO 30027670 | F3 | BRASSEY ROAD | BRUNSWICK | Wanganui | TP_BRUNSWICK | Western Electricity | POWERCO | 0.014648 | 5.5 | 2017 | 2016-10-05 | B | 34 | 0.029296 | 0.00010208
1 | 13582044 | 2016-09-14 13:35 | 2016-09-14 13:40 | 5 | 1 | 5 | 1.5015e-05 | 6e-06 | 3.003e-06 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | X4171 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Tap Transformer X4171 down from tap 3 to tap 1. Relivened OK | F4 | WAVERLEY | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 6e-06 | 11 | 2017 | 2016-09-14 | C | 1 | 6e-06 | 3.003e-06
1 | 13582123 | 2016-10-12 10:15 | 2016-10-12 15:42 | 327 | 18 | 5886 | 0.01767 | 0.017507 | 5.4036e-05 | NAPA ID:24004 TP_TAURANGA 33 GXP > OMOKOROA SUB > TE PUNA | 11 | Planned | 024004 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD3-058 | NONE | Replace Poles, hardware and conductors. Install TEMP65 Pole 210387. Works location: Armstrong Rd. WO 30019163 | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.0087535 | 5.5 | 2017 | 2016-10-12 | B | 18 | 0.017507 | 5.4036e-05
1 | 13582168 | 2016-10-05 09:47 | 2016-10-05 16:30 | 403 | 5 | 2014.1833 | 0.0060471 | 0.006002 | 1.5011e-05 | NAPA ID:23566 TP_WAVERLEY GXP > TP_WAVERLEY > RANGIKURA | 11 | Planned | 023566 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer X717 | NONE | Cut line breaks to access transformer X717 replace all X arms. Works location: Wybourne Rd, Waverley. WO 30027080 | F4 | RANGIKURA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.003001 | 5.5 | 2017 | 2016-10-05 | B | 5 | 0.006002 | 1.5011e-05
1 | 13582377 | 2016-10-05 09:00 | 2016-10-05 11:10 | 130 | 3 | 390 | 0.0011709 | 0.001143 | 9.0068e-06 | NAPA ID:23281 TP_GREYTOWN GXP > MARTINBOROUGH SUB > COLOGNE ST | 11 | Planned | 023281 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T1884 | NONE | Replace defective T/X. Works location: Longbush Rd, Martinborough. WO 30031331 | F3/F5 | COLOGNE ST | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.0005715 | 5.5 | 2017 | 2016-10-05 | B | 3 | 0.001143 | 9.0068e-06
1 | 13582506 | 2016-10-05 09:45 | 2016-10-05 12:15 | 150 | 5 | 750 | 0.0022517 | 0.002206 | 1.5011e-05 | NAPA ID:23877 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | 023877 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T3/20 | NONE | Replace 11KV trani & trani arms T3/20. Works location: Halcombe Mt Stewart Rd. WO 30027943 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.001103 | 5.5 | 2017 | 2016-10-05 | B | 5 | 0.002206 | 1.5011e-05
1 | 13583339 | 2016-09-14 12:55 | 2016-09-14 14:44 | 109 | 317 | 21609.0333 | 0.064892 | 0.062036 | 0.00095196 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | CB 23 | UNKNOWN | CB 23 tripped on E/F flags, line was patrolled and sectionalised and no fault was found. | F4 | TAIKOREA | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.062036 | 11 | 2017 | 2016-09-14 | C | 317 | 0.062036 | 0.00095196
1 | 13585463 | 2016-10-31 09:00 | 2016-10-31 15:25 | 385 | 23 | 8855 | 0.026577 | 0.026369 | 6.903e-05 | NAPA ID:24005 TP_TAURANGA 33 GXP > OMOKOROA SUB > TE PUNA | 11 | Planned | 024005 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 324810 | NONE | Replace Poles, hardware and conductors. Works location: Armstrong Rd. WO 30019163 | F4 | TE PUNA | TAURANGA 31 | Tauranga | OMOKOROA SUB | Eastern Electricity | POWERCO | 0.013185 | 5.5 | 2017 | 2016-10-31 | B | 23 | 0.026369 | 6.903e-05
1 | 13585587 | 2016-10-06 09:35 | 2016-10-06 12:45 | 190 | 2 | 380 | 0.0011408 | 0.001122 | 6.0044e-06 | NAPA ID:23760 TP_MARTON GXP > RATA SUB > HUNTERVILLE 22KV | 11 | Planned | 023760 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 4162 | NONE | Replace 11kv Transformer X2154 replace low voltage X arms and upgrade earthing. Works location: Pukekoa Rd, Hunterville. WO 30000401 | F3 | HUNTERVILLE 22KV | MARTON | Wanganui | RATA SUB | Western Electricity | POWERCO | 0.000561 | 5.5 | 2017 | 2016-10-06 | B | 2 | 0.001122 | 6.0044e-06
1 | 13585935 | 2016-10-05 08:48 | 2016-10-05 09:17 | 28 | 11 | 316.8 | 0.00095112 | 0.000852 | 3.3025e-05 | NAPA ID:23434 TP_WANGANUI GXP > HATRICKS WHARF SUB > MARANGAI | 11 | Planned | 023434 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 4182 | NONE | Ground mount switchgear maintenance on Sw/gear 4457. Works location: Kaitoke Rd. WO 30021058 | F2 | TAUPO 2 | WANGANUI | Wanganui | TAUPO QUAY SUB | Western Electricity | POWERCO | 0.000426 | 5.5 | 2017 | 2016-10-05 | B | 11 | 0.000852 | 3.3025e-05
1 | 13588279 | 2016-09-14 22:02 | 2016-09-14 23:08 | 65 | 1 | 65.6333 | 0.0001971 | 0.000188 | 3.003e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 444053 | FUSE - ELEMENT/LINK (HV) | 2 blown fuses at pole 444053. these fuses were Temp fuses installed by Connectics about a year ago for work on this feeder. the fuses have never been removed, have no network number. they are loaded with 15amp fuse now. Safety Manager Incident 661057 raised. | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.000188 | 11 | 2017 | 2016-09-14 | C | 1 | 0.000188 | 3.003e-06
1 | 13588416 | 2016-09-14 22:35 | 2016-09-14 23:08 | 33 | 1 | 33.4 | 0.0001003 | 9.1e-05 | 3.003e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 444053 | FUSE - HOLDER/BASE - REPLACE PARTIAL SET (HV) | tried to call customer when job came in, need to ring in the morning possibly power restored with another job as line fuse had blown. Restored under 13588279 - See link | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 9.1e-05 | 11 | 2017 | 2016-09-14 | C | 1 | 9.1e-05 | 3.003e-06
1 | 13593148 | 2016-09-15 07:49 | 2016-09-15 11:52 | 242 | 76 | 18445.2 | 0.055391 | 0.054705 | 0.00022823 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - TREES | 835828 | CONDUCTOR - REPAIR/REHANG | Recloser C281 tripped on B phase OC, and E/F. Received a call from a customer of a tree that has gone through the lines, Faultman isolated the lines at Links C281/6 & ABS C281/1, faultman found that a loggers had cut down trees and one had fallen through the lines at pole 835828. 20 meters of Gofer conductor was used. 5 X tension joints used. NDR: 34890 | F5 | BLAIRLOGIE | MASTERTON | Wairarapa | AWATOITOI SUB | Western Electricity | POWERCO | 0.054705 | 11 | 2017 | 2016-09-15 | C | 76 | 0.054705 | 0.00022823
1 | 13593509 | 2016-09-15 08:11 | 2016-09-15 10:10 | 119 | 714 | 49685.5333 | 0.1492 | 0.14277 | 0.0021441 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 751816 | INSULATOR | CB 10 Tripped O/C E/F Fault reported by public while sectionlising Isolated at ABS 343 & Sw/Gear 196/3 with back feed installed Via Sw/Gear 30/3 HV Insulator Replaced at Pole 751816 Used 1 x HV Insulator, 1 x Binder | F3 | CITY 10 | CARRINGTON ST 33 | Taranaki | CITY SUB | Western Electricity | POWERCO | 0.14277 | 11 | 2017 | 2016-09-15 | C | 714 | 0.14277 | 0.0021441
1 | 13594394 | 2016-09-15 15:00 | 2016-09-15 17:01 | 121 | 1 | 121 | 0.00036336 | 0.000354 | 3.0029e-06 | NAPA ID:24498 TP_MT MAUNGANUI 33 GXP > TRITON SUB > HULL RD | 11 | Planned | 024498 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - MAINTENANCE | 9271 | NONE | Calibration of Metering Unit 9271 | F2 | HULL RD | MT MAUNGANUI 31 | Tauranga | TRITON SUB | Eastern Electricity | POWERCO | 0.000177 | 5.5 | 2017 | 2016-09-15 | B | 1 | 0.000354 | 3.0029e-06
1 | 13594917 | 2016-10-13 11:00 | 2016-10-13 12:55 | 115 | 267 | 30705 | 0.092176 | 0.089771 | 0.00080153 | NAPA ID:24125 TP_KOPU GXP > WHITIANGA SUB > JOAN GASKELL DR | 11 | Planned | 024125 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2706 | NONE | Relevel SD Unit. Clean up HV cabels to stop ionisation. Works location: Cook Drive, Whitianga. WO 30025885 | F3 | JOAN GASKELL DR | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.044886 | 5.5 | 2017 | 2016-10-13 | B | 267 | 0.089771 | 0.00080153
1 | 13595607 | 2016-10-06 09:25 | 2016-10-06 12:35 | 190 | 3 | 570 | 0.0017113 | 0.001684 | 9.0067e-06 | NAPA ID:23998 TP_BUNNYTHORPE GXP > SANSON SUB > KAKARIKI | 11 | Planned | 023998 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T3/542 | NONE | Upgrading existing 30 kVA Tx to 50kVA due to load issues. Works location: Tokorangi Rd, Feilding. WO 30029172 | F4 | KAKARIKI | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.000842 | 5.5 | 2017 | 2016-10-06 | B | 3 | 0.001684 | 9.0067e-06
1 | 13595641 | 2016-10-06 09:11 | 2016-10-06 10:43 | 92 | 67 | 6164 | 0.018506 | 0.017902 | 0.00020115 | NAPA ID:23353 TP_WAIKINO GXP > WHANGAMATA SUB > HETHERINGTON RD | 11 | Planned | 023353 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC4077 | NONE | OFF-LOAD TRANSFORMER TC4077 AND REPLACE 3 X DROPOUT FUSES LIVE LINE. Works location: Harbour View Rd, Whangamata. WO 30019411 | F3 | HETHERINGTON RD | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.008951 | 5.5 | 2017 | 2016-10-06 | B | 67 | 0.017902 | 0.00020115
1 | 13595651 | 2016-10-05 09:37 | 2016-10-05 11:25 | 108 | 301 | 32508 | 0.097598 | 0.094886 | 0.00090368 | NAPA ID:23831 TP_TAURANGA 33 GXP > OTUMOETAI SUB > BROOKFIELD TCE | 11 | Planned | 023831 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS SD4-163 | NONE | change over temp o/h line to new underground cable 11kv. Works location: Kingswood Rd. WO 30018901 | F3 | BROOKFIELD TCE | TAURANGA 31 | Tauranga | OTUMOETAI SUB | Eastern Electricity | POWERCO | 0.047443 | 5.5 | 2017 | 2016-10-05 | B | 301 | 0.094886 | 0.00090368
1 | 13595716 | 2016-10-06 09:15 | 2016-10-06 14:15 | 300 | 17 | 5100 | 0.015311 | 0.015158 | 5.1038e-05 | NAPA ID:24103 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 024103 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T7/337 | NONE | To change Tx pole and TX | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.007579 | 5.5 | 2017 | 2016-10-06 | B | 17 | 0.015158 | 5.1038e-05
1 | 13596275 | 2016-10-06 09:50 | 2016-10-06 15:30 | 340 | 14 | 4760 | 0.014291 | 0.014164 | 4.2031e-05 | NAPA ID:23631 TP_BRUNSWICK GXP > PEAT ST SUB > ST JOHNS | 11 | Planned | 023631 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1462 | NONE | Replace 400V switchgear for X2219 .All 400V lines will be isolated,advertising required. Works location: Great North Rd. WO 30027670 | F3 | ST JOHNS | BRUNSWICK | Wanganui | PEAT ST SUB | Western Electricity | POWERCO | 0.007082 | 5.5 | 2017 | 2016-10-06 | B | 14 | 0.014164 | 4.2031e-05
1 | 13596727 | 2016-09-15 14:32 | 2016-09-15 15:15 | 43 | 2 | 86 | 0.00025826 | 0.00024 | 6.0059e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711032 | CONDUCTOR - REPAIR/REHANG | Conductor need replacing Floating conduct found at Pole 711032 Isolated at fuses PU363 Used 1 x binder | F4 | PUNGAREHU | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.00024 | 11 | 2017 | 2016-09-15 | C | 2 | 0.00024 | 6.0059e-06
1 | 13599180 | 2016-09-16 06:40 | 2016-09-16 12:00 | 320 | 238 | 22494.6667 | 0.06755 | 0.065406 | 0.0007147 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 790583 | CABLE - REPLACE 5 METRES OR MORE | Outage required between ABS 177 & Links 1173. Backfeed from ROB4 via ABS 1487. Replaced 20m x conductor & 4 x sleeves | F4 | NO 3 LINE | WANGANUI | Wanganui | WANGANUI EAST SUB | Western Electricity | POWERCO | 0.065406 | 11 | 2017 | 2016-09-16 | C | 238 | 0.065406 | 0.0007147
1 | 13599512 | 2016-10-05 07:35 | 2016-10-05 16:45 | 550 | 55 | 30250 | 0.090819 | 0.090323 | 0.00016512 | NAPA ID:24427 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > TE AROHA BOROUGH | 11 | Planned | 024427 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV TC3-742 | NONE | Isolate Tx disconnect LV & connect LV generation, Replace Tx. disconnect LV generation & re-terminate LV onto new LV board. Works location: Rewi St, Te Aroha. WO 30026836 | F2/F4 | TE AROHA BOROUGH | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.045162 | 5.5 | 2017 | 2016-10-05 | B | 55 | 0.090323 | 0.00016512
1 | 13600810 | 2016-09-16 08:55 | 2016-09-16 11:45 | 170 | 10 | 1704 | 0.005117 | 0.005026 | 3.0029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | M9 | UNKNOWN | Replace 3 x 20A fuses. Cause Unknown. | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.005026 | 11 | 2017 | 2016-09-16 | C | 10 | 0.005026 | 3.0029e-05
1 | 13601401 | 2016-10-05 09:15 | 2016-10-05 14:25 | 310 | 26 | 8060 | 0.024198 | 0.023964 | 7.8059e-05 | NAPA ID:23991 TP_WAIKINO GXP > PAEROA SUB > TIROHIA-KARANGAHAKE | 11 | Planned | 023991 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 1162 | NONE | TO REPLACE EXISTING POLE WITH NEW 11M BUSCK, GROUND CLEARANCE ISSUES. Works location: Gerrand Rd, Paeroa. WO 30010090 | F4 | TIROHIA-KARANGAHAKE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.011982 | 5.5 | 2017 | 2016-10-05 | B | 26 | 0.023964 | 7.8059e-05
1 | 13601567 | 2016-09-16 22:15 | 2016-09-16 23:19 | 64 | 32 | 2063.4667 | 0.0061965 | 0.005908 | 9.6094e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737105 | JUMPER | Faultman found a burnt 11KV jumper on pole 737105, line was isolated at Fuses 6051 to repair the jumper. | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.005908 | 11 | 2017 | 2016-09-16 | C | 32 | 0.005908 | 9.6094e-05
1 | 13603446 | 2016-10-07 09:45 | 2016-10-07 12:35 | 170 | 66 | 10914 | 0.032766 | 0.032171 | 0.00019815 | NAPA ID:23672 TP_CARRINGTON GXP > KATERE SUB > KATERE 5 | 11 | Planned | 023672 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 365 | NONE | We are replacing the 11kv pole and ABS as it is faulty and is a main open point between 2 feeders. Works location: Egmont Rd, New Plymouth. WO 30030490 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.016085 | 5.5 | 2017 | 2016-10-07 | B | 66 | 0.032171 | 0.00019815
1 | 13603513 | 2016-10-06 08:45 | 2016-10-06 14:50 | 365 | 119 | 43435 | 0.1304 | 0.12933 | 0.00035727 | NAPA ID:24152 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024152 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV IC641 | NONE | To replace arms and hardware between switches IC641 & 1185. Works location: Ngutumanga Rd, Te Aroha. WO 30017829 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.064665 | 5.5 | 2017 | 2016-10-06 | B | 119 | 0.12933 | 0.00035727
1 | 13603733 | 2016-09-16 13:16 | 2016-09-17 11:45 | 1349 | 161 | 178432.7833 | 0.53582 | 0.53437 | 0.001069 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 709054 | INSULATOR | Faultman found lines broken off insulators caused by fallen trees at pole 709054, faultman will return in morning to repair lines and remove trees as access is to dangerous at night, as have to go in on foot to do the repairs. Isolated at ABS 5619 Trees cleared and lines repaired Used 1 x insulator 1 x binder Faultman still to proved NDR # | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.53437 | 11 | 2017 | 2016-09-16 | C | 161 | 0.53437 | 0.001069
1 | 13604008 | 2016-09-16 14:45 | 2016-09-16 17:42 | 177 | 3 | 531 | 0.0015946 | 0.001567 | 9.0088e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717238 | CONDUCTOR - REPAIR/REHANG | Hazard process complete. 14:23 ETA 2Ominutes. Lines damaged by hedge trimmer. NDR - 11.18am 17/9 customer calling for update - Dianne advised will be today unable to give eta. Fuses at Transformer T5300 Damaged removed and road side fuses down rated Used 6 mtrs of conductor, 6 sleeves &, 3 3 amp fuses. repairs also down on privately owned pole 717238 | F4 | PIHAMA | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.001567 | 11 | 2017 | 2016-09-16 | C | 3 | 0.001567 | 9.0088e-06
1 | 13604132 | 2016-09-16 13:52 | 2016-09-16 15:35 | 102 | 606 | 51651.35 | 0.15511 | 0.14965 | 0.0018198 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NOT PATROLLED - CAUSE UNKNOWN | CB R21 | UNKNOWN | CB R21 Tripped E/FPatrolled no fault found | F1 | ELTHAM TOWN NORTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.14965 | 11 | 2017 | 2016-09-16 | C | 606 | 0.14965 | 0.0018198
1 | 13605116 | 2016-10-06 08:15 | 2016-10-06 13:55 | 340 | 99 | 33660 | 0.10106 | 0.10016 | 0.00029722 | NAPA ID:24184 TP_MANGAMAIRE GXP > MANGAMUTU SUB > PAHIATUA 1 | 11 | Planned | 024184 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS Q23 | NONE | Replace crossarm and install crucifix at pole P37490. Works location: Paterson St, Pahiatua. WO 30019582 | F2 | PAHIATUA 1 | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.050082 | 5.5 | 2017 | 2016-10-06 | B | 99 | 0.10016 | 0.00029722
1 | 13605144 | 2016-10-07 09:00 | 2016-10-07 12:30 | 210 | 61 | 12810 | 0.038458 | 0.037908 | 0.00018313 | NAPA ID:23824 TP_MASTERTON GXP > TINUI SUB > CASTLEPOINT | 11 | Planned | 023824 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 7366 | NONE | replace defected tx structure and hardware (t1691). Works location: Mataikona Rd, Castlepoint. WO 30007343 | F5 | CASTLEPOINT | MASTERTON | Wairarapa | TINUI SUB | Western Electricity | POWERCO | 0.018954 | 5.5 | 2017 | 2016-10-07 | B | 61 | 0.037908 | 0.00018313
1 | 13605346 | 2016-09-16 14:40 | 2016-09-16 18:31 | 230 | 10 | 2309 | 0.0069338 | 0.006843 | 3.0029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | M9 | FUSE - ELEMENT/LINK (HV) | Fuses found to be mismatched. Replaced all fuses with 20A. | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.006843 | 11 | 2017 | 2016-09-16 | C | 10 | 0.006843 | 3.0029e-05
1 | 13606230 | 2016-09-16 14:41 | 2016-09-16 20:58 | 377 | 430 | 44292.2167 | 0.13301 | 0.12913 | 0.0023843 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | 10227 | UNKNOWN | 1r - Cursory Feeder Patrol after Recloser 10227 tripped on B phase E/F flags, at time of tripping a part of Kairanga CB 23 is been backfed from Kairanga CB 11 to look for a on going fault, line was sectionalised and patrolled and no fault was found, tripping only happens when raining heaverly. Suspect pin hole in an insulator past ABS B16. | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.12913 | 11 | 2017 | 2016-09-16 | C | 430 | 0.12913 | 0.0023843
1 | 13606662 | 2016-10-07 09:04 | 2016-10-07 15:31 | 387 | 70 | 27090 | 0.08133 | 0.080699 | 0.00021015 | NAPA ID:23291 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023291 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 349 | NONE | change poles and xarms on Lincoln and install temporary links on wortley rd. Works location: Wortley Rd. WO 30030730 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.04035 | 5.5 | 2017 | 2016-10-07 | B | 70 | 0.080699 | 0.00021015
1 | 13607384 | 2016-09-16 14:55 | 2016-09-16 16:29 | 94 | 6 | 564 | 0.0016937 | 0.001639 | 1.8018e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 813902 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 15A fuses. Cause Unknown. | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.001639 | 11 | 2017 | 2016-09-16 | C | 6 | 0.001639 | 1.8018e-05
1 | 13607392 | 2016-10-11 09:15 | 2016-10-11 15:00 | 345 | 7 | 2415 | 0.00725 | 0.007186 | 2.1014e-05 | NAPA ID:23292 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023292 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 352 | NONE | change poles 742987, 742988, 742989, 742991, 742992, 742997 and xarms 742990 742994 742995 742996. Works location: Wortley Rd. WO 30030730 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.003593 | 5.5 | 2017 | 2016-10-11 | B | 7 | 0.007186 | 2.1014e-05
1 | 13607480 | 2016-10-13 09:00 | 2016-10-13 13:55 | 295 | 7 | 2065 | 0.0061991 | 0.006136 | 2.1014e-05 | NAPA ID:23293 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023293 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 352 | NONE | change ppoles 742999, 745107, 745109, 745110, 745111 and change xarms 742998 and 745108. Works location: Wortley Rd. WO 30030730 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.003068 | 5.5 | 2017 | 2016-10-13 | B | 7 | 0.006136 | 2.1014e-05
1 | 13607553 | 2016-10-20 09:00 | 2016-10-20 15:14 | 374 | 24 | 8976 | 0.026943 | 0.026727 | 7.2041e-05 | NAPA ID:23311 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023311 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 140 | NONE | change 11kv poles and xarms. Works location: Mountain Rd. WO 30030730 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.013364 | 5.5 | 2017 | 2016-10-20 | B | 24 | 0.026727 | 7.2041e-05
1 | 13607560 | 2016-09-16 15:18 | 2016-09-16 17:29 | 130 | 155 | 13488.6333 | 0.040506 | 0.039109 | 0.00046546 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | P13371 | UNKNOWN | Recloser 9604 - Tripped open on E/F line sectionalised and cursory patrol carried out with nothing found. Referal created for a full line patrol on Monday | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.039109 | 11 | 2017 | 2016-09-16 | C | 155 | 0.039109 | 0.00046546
1 | 13608189 | 2016-09-16 18:30 | 2016-09-16 18:37 | 7 | 83 | 477 | 0.0014324 | 0.000684 | 0.00024924 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 732055 | INSULATOR | Pole fuse has fallen from the pole and taken into the Eltham library - Not part of feeder fault Entered as a site inspection as there is a verified feeder fault in the area Centre Insulator found broken on ASB 6192 De-energised at ABS's 6044 & 6180 ABS 6192 Opened & Tagged ABS's 6044 & 6180 closed to restore all power DNO 160916 | F1 | ELTHAM TOWN NORTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.000684 | 11 | 2017 | 2016-09-16 | C | 83 | 0.000684 | 0.00024924
1 | 13608584 | 2016-10-26 09:00 | 2016-10-26 15:30 | 390 | 57 | 22230 | 0.066723 | 0.06621 | 0.00017109 | NAPA ID:23315 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023315 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 349 | NONE | change xarms on ABS pole 349, reconductor between ABS352 and ABS349 and change xarms on Davies rd. Works location: Wortley & Davies Rd. WO 30030730 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.033105 | 5.5 | 2017 | 2016-10-26 | B | 57 | 0.06621 | 0.00017109
1 | 13608617 | 2016-10-28 09:00 | 2016-10-28 15:07 | 367 | 55 | 19558 | 0.058702 | 0.058206 | 0.00016508 | NAPA ID:23318 TP_CARRINGTON GXP > BROOKLANDS SUB > BROOKLANDS 5 | 11 | Planned | 023318 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 483 | NONE | Change ABS pole 483 and change 11 kv poles and xarms. Works location: Wortley Rd. WO 30030730 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.029103 | 5.5 | 2017 | 2016-10-28 | B | 55 | 0.058206 | 0.00016508
1 | 13609109 | 2016-09-16 22:41 | 2016-09-17 00:20 | 99 | 18 | 1782 | 0.0053513 | 0.005189 | 5.4053e-05 |  | 11 | Unplanned |  | DISTRIBUTION EQUIPMENT | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 711610 | TRANSFORMER - DISTRIBUTION TRANSFORMER (HV) | Transformer P4095 found to be faulty - Isolated at fuses for transformer , line was isolated at ABS's NG408, 6394 & 6434 to replace transformer P4095. | F4 | PARIHAKA | OPUNAKE | Taranaki | PUNGAREHU SUB | Western Electricity | POWERCO | 0.005189 | 11 | 2017 | 2016-09-16 | C | 18 | 0.005189 | 5.4053e-05
1 | 13609197 | 2016-09-17 00:56 | 2016-09-17 02:37 | 101 | 9 | 909 | 0.0027297 | 0.002648 | 2.7026e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P07635 | INSULATOR | Faultman found a damaged insulator on pole P07635, line was isolated at Fuses K76 to replace the insulator. 1 X 11KV insulator replaced. | F4 | WAITUNA | BUNNYTHORPE | Manawatu | KIMBOLTON SUB | Western Electricity | POWERCO | 0.002648 | 11 | 2017 | 2016-09-17 | C | 9 | 0.002648 | 2.7026e-05
1 | 13611286 | 2016-09-16 22:03 | 2016-09-17 00:58 | 175 | 352 | 26259.05 | 0.078855 | 0.075683 | 0.0019279 |  | 6.6 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 761659 | INSULATOR | Recloser 6616 tripped on Bphase O/C & E/F flags, line was patrolled and sectionalised and a broken insulator was found on pole 761659, line was isolated at Fuses 5516 to replace the insulators. 2 X insulators replaced. 2 X binders used | F4 | CLOTON RD NORTH | STRATFORD | Taranaki | CLOTON RD SUB | Western Electricity | POWERCO | 0.075683 | 6.6 | 2017 | 2016-09-16 | C | 352 | 0.075683 | 0.0019279
1 | 13612833 | 2016-09-16 22:13 | 2016-09-16 23:50 | 97 | 316 | 24010.0667 | 0.072101 | 0.069254 | 0.00094893 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB C830 | UNKNOWN | CB C830 tripped on C phase E/F flags, line was patrolled and sectionalised and no fault was found. | F5 | WERAITI | MASTERTON | Wairarapa | TE ORE ORE SUB | Western Electricity | POWERCO | 0.069254 | 11 | 2017 | 2016-09-16 | C | 316 | 0.069254 | 0.00094893
1 | 13614742 | 2016-09-17 00:52 | 2016-09-17 12:00 | 668 | 27 | 18036 | 0.054161 | 0.053917 | 8.1079e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 480764 | CONDUCTOR - REPAIR/REHANG | Faultman found a pine tree that had fallen through and broken the lines, line was isolated at Fuses 5193 to remove the tree and make the lines safe, will turn at day light to repair the lines. Lines need to repaired and pole straightened. Lines repaired after tree completely removed Lines down from Pole 480764 to 763930 Used 10 sleeves, 28 mtrs of conductor, 6 mtrs of binder, 1 cubic mtrs shingle Faultman still to supply NDR # NDR N00227 | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.053917 | 11 | 2017 | 2016-09-17 | C | 27 | 0.053917 | 8.1079e-05
1 | 13615747 | 2016-09-17 04:11 | 2016-09-18 17:00 | 2208 | 6396 | 71729.0167 | 0.2154 | 0.15778 | 0.0017567 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P1567 | CONDUCTOR - REPAIR/REHANG | Recloser 9604 L/O on E/F line Sectionalised and patrolled trees removed from lines @ pole P13742 on attempted restoration breaker tripped again (fresh crew attended) Line break created @ pole P13610 and fed from CB 9712 . Further line break made @ pole P1550 and supply restored from ABS IC 278 . New crew to return in the morning. Found floating wire on pole P1567, Repaired, Closed temp line breaks & restored power | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.15778 | 11 | 2017 | 2016-09-17 | C | 6396 | 0.15778 | 0.0017567
1 | 13617397 | 2016-09-17 09:23 | 2016-09-17 12:54 | 210 | 329 | 2907 | 0.0087295 | 0.005765 | 0.00017117 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 732055 | JUMPER | Faulty ABS 6192 may be causing trips. Isolated at ABS 6180 and jumpers cut | F1 | ELTHAM TOWN NORTH | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.005765 | 11 | 2017 | 2016-09-17 | C | 329 | 0.005765 | 0.00017117
1 | 13618334 | 2016-09-17 12:33 | 2016-09-17 13:35 | 62 | 1 | 62 | 0.00018618 | 0.000177 | 3.0029e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 813902 | FUSE - ELEMENT/LINK (HV) | please check if oms 13618374 is related Fuse found blown at fuses 7201- cause loading Used 1 x 20amp fuse | F4 | TAWAHA | GREYTOWN | Wairarapa | MARTINBOROUGH SUB | Western Electricity | POWERCO | 0.000177 | 11 | 2017 | 2016-09-17 | C | 1 | 0.000177 | 3.0029e-06
1 | 13619592 | 2016-09-17 12:27 | 2016-09-17 15:58 | 210 | 430 | 56211.75 | 0.1688 | 0.16492 | 0.0023843 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P36231 | INSULATOR | Recloser 10227 Tripped A,B Ph E/F Faulty Insulator found at Pole P36231 while sectionlising Isolated at ABS B16 Insulator replaced | F4/F5 | BAINESSE | LINTON | Manawatu | KAIRANGA SUB | Western Electricity | POWERCO | 0.16492 | 11 | 2017 | 2016-09-17 | C | 430 | 0.16492 | 0.0023843
1 | 13622767 | 2016-09-17 14:25 | 2016-09-17 19:46 | 321 | 570 | 103314 | 0.31024 | 0.30511 | 0.0017117 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P12543 & P12521 | POLE | CB 1 L/O on E/F. Reported pole on fire at 34 Mataura Rd. Isolated between IC204 & IC3176 Replaced jumper, installed 1 carrier pin & 1 LV insulator DDO at pole P12521 Broken when closed. Same isolation points and Drop out replaced | F4 | WAIHI NORTH | WAIKINO | Valley | WAIHI SUB | Eastern Electricity | POWERCO | 0.30511 | 11 | 2017 | 2016-09-17 | C | 570 | 0.30511 | 0.0017117
1 | 13624647 | 2016-09-17 16:32 | 2016-09-17 18:30 | 118 | 10 | 1184.6667 | 0.0035575 | 0.003467 | 3.0029e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | P18604 | FUSE - ELEMENT/LINK (HV) | Fuses found blown at Fuses M9 - Cause unknown. Used 2 X 20 amp fuses. | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.003467 | 11 | 2017 | 2016-09-17 | C | 10 | 0.003467 | 3.0029e-05
1 | 13632764 | 2016-09-18 07:15 | 2016-09-18 11:15 | 240 | 1 | 240 | 0.00072069 | 0.000711 | 3.0028e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | TF8-014 | CABLE - REPLACE LESS THAN 5 METRES | Main earth broken for transformer. LT cable from bushings to LT O/H line faulty, needs repairing. Isolated single phase transformer at HT fuses for repairs to be done | F4 | ROTOEHU | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.000711 | 11 | 2017 | 2016-09-18 | C | 1 | 0.000711 | 3.0028e-06
1 | 13632772 | 2016-09-18 08:30 | 2016-09-18 09:43 | 73 | 11 | 803 | 0.0024113 | 0.002312 | 3.3032e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 734940 | INSULATOR | 1 X HT Insulator at Pole 734940 | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.002312 | 11 | 2017 | 2016-09-18 | C | 11 | 0.002312 | 3.3032e-05
1 | 13632817 | 2016-09-18 06:31 | 2016-09-18 10:12 | 221 | 2 | 336.0833 | 0.0010092 | 0.000991 | 6.0057e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC4069 | FUSE - ELEMENT/LINK (HV) | Also check if 13633856 related - 402 Old Maratoto Replaced 2 x 10 amp HT fuses at FC4069 | F4 | BENNETT ST | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.000991 | 11 | 2017 | 2016-09-18 | C | 2 | 0.000991 | 6.0057e-06
1 | 13632835 | 2016-09-18 06:50 | 2016-09-18 08:14 | 83 | 202 | 12499.5333 | 0.037535 | 0.035714 | 0.00060658 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | 1 | UNKNOWN | CB 1 L/O on E/F. Sectionalised and found NO fault. CB indication faulty showed invalid. To be defected. | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.035714 | 11 | 2017 | 2016-09-18 | C | 202 | 0.035714 | 0.00060658
1 | 13633427 | 2016-09-18 06:59 | 2016-09-18 09:24 | 145 | 2 | 209.7333 | 0.00062981 | 0.000611 | 6.0057e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 2554 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 6 Amp Fuses at 2554 due to birds. | F4 | MANGAWEKA | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.000611 | 11 | 2017 | 2016-09-18 | C | 2 | 0.000611 | 6.0057e-06
1 | 13633843 | 2016-09-18 14:28 | 2016-09-18 15:00 | 32 | 76 | 2432 | 0.007303 | 0.006618 | 0.00022822 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE |  | FUSE - HOLDER/BASE (LV) | Isolated at 9455/2 to repair LT fuse bushing. | F3 | STANLEY AVE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.006618 | 11 | 2017 | 2016-09-18 | C | 76 | 0.006618 | 0.00022822
1 | 13634355 | 2016-09-18 11:01 | 2016-09-18 11:48 | 46 | 135 | 6275.25 | 0.018844 | 0.017627 | 0.00040539 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 724877 | JUMPER | Used Hot sticks to push jumper off crossarm at Pole 724877 | F4 | TAWHITI RD | HAWERA | Taranaki | CAMBRIA SUB | Western Electricity | POWERCO | 0.017627 | 11 | 2017 | 2016-09-18 | C | 135 | 0.017627 | 0.00040539
1 | 13634621 | 2016-09-18 14:24 | 2016-09-18 16:44 | 140 | 79 | 11060 | 0.033212 | 0.0325 | 0.00023723 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | H2186 | CROSSARM - WHOLE ASSEMBLY | Broken crossarm on pole H2186. IsolaTed between ABS 884, IC1192 & 852. Replaced broken crossarm & relivened 2 crossarms & 6 insulators. | F3/F4 | MOWBRAY RD | HINUERA | Valley | WAHAROA SUB (T1 Bus) | Eastern Electricity | POWERCO | 0.0325 | 11 | 2017 | 2016-09-18 | C | 79 | 0.0325 | 0.00023723
1 | 13634850 | 2016-09-18 13:51 | 2016-09-18 16:19 | 148 | 3 | 428.7167 | 0.0012874 | 0.00126 | 9.0086e-06 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | M9 | UNKNOWN | Replaced 2 x 15amp Fuses at M9 due to birds. | F2 | SANSON LS | BUNNYTHORPE | Manawatu | SANSON SUB | Western Electricity | POWERCO | 0.00126 | 11 | 2017 | 2016-09-18 | C | 3 | 0.00126 | 9.0086e-06
1 | 13634970 | 2016-09-18 14:31 | 2016-09-18 19:32 | 300 | 20 | 2416.9333 | 0.0072578 | 0.007077 | 6.0058e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 773123 | INSULATOR | Replaced broken strain insulator @ Pole 773123 | F4 | WAITOTARA | WAVERLEY | Wanganui | TP_WAVERLEY | Western Electricity | POWERCO | 0.007077 | 11 | 2017 | 2016-09-18 | C | 20 | 0.007077 | 6.0058e-05
1 | 13637086 | 2016-09-18 13:42 | 2016-09-18 15:53 | 131 | 7 | 491.15 | 0.0014749 | 0.001411 | 2.102e-05 |  | 11 | Unplanned |  | UNDERGROUND CABLE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - UG EQUIPMENT FAILURE | sf3-007 | CABLE - REPAIR | Isolated at fuses SF3-007, reconnected earths on 11kV cables & relivened | F4 | KEENAN RD | TAURANGA 11 | Tauranga | TP_TAURANGA 11kV | Eastern Electricity | POWERCO | 0.001411 | 11 | 2017 | 2016-09-18 | C | 7 | 0.001411 | 2.102e-05
1 | 13644967 | 2016-09-18 23:30 | 2016-09-19 01:00 | 89 | 11 | 988.35 | 0.0029679 | 0.002868 | 3.3032e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | FC823 | FUSE - ELEMENT/LINK (HV) | 2 x 8 amp HV fuses replaced at fuses FC823. Possibly due to bird. | F4 | KAIHERE | KOPU | Valley | KEREPEHI SUB | Eastern Electricity | POWERCO | 0.002868 | 11 | 2017 | 2016-09-18 | C | 11 | 0.002868 | 3.3032e-05
1 | 13645016 | 2016-09-19 06:00 | 2016-09-19 07:08 | 67 | 26 | 1746.3333 | 0.005244 | 0.005009 | 7.8074e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 719357 | FUSE - ELEMENT/LINK (HV) | CNR skeet & manaia near kapuni store, sparks & flames from pole on corner 06 274 8175 - dianne - advised control ABS KA138 has DNO 160917 | F4 | KAPUNI | HAWERA | Taranaki | KAPUNI SUB | Western Electricity | POWERCO | 0.005009 | 11 | 2017 | 2016-09-19 | C | 26 | 0.005009 | 7.8074e-05
1 | 13645092 | 2016-09-19 06:35 | 2016-09-19 08:10 | 95 | 5 | 476.0833 | 0.0014296 | 0.001384 | 1.5014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - BIRD STRIKE | 372852 | FUSE - ELEMENT/LINK (HV) | Reload at Fuss 7349 2 x 6A Birds | F4 | OTARAIA | GREYTOWN | Wairarapa | TUHITARATA SUB | Western Electricity | POWERCO | 0.001384 | 11 | 2017 | 2016-09-19 | C | 5 | 0.001384 | 1.5014e-05
1 | 13645318 | 2016-10-16 08:32 | 2016-10-16 11:25 | 173 | 13 | 2249 | 0.0067512 | 0.006634 | 3.9024e-05 | NAPA ID:23600 TP_MASTERTON GXP > AKURA SUB > MIRO ST | 11 | Planned | 023600 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 834425 | NONE | Replace 11kv crossarms. Works location: Hwy 2, Masterton. WO 30030270 | F3/F4 | MIRO ST | MASTERTON | Wairarapa | AKURA SUB | Western Electricity | POWERCO | 0.003317 | 5.5 | 2017 | 2016-10-16 | B | 13 | 0.006634 | 3.9024e-05
1 | 13645576 | 2016-09-30 10:01 | 2016-09-30 14:20 | 259 | 15 | 3885 | 0.011665 | 0.011529 | 4.5037e-05 | NAPA ID:24578 TP_CARRINGTON GXP | 11 | Planned | 024578 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 577 | NONE | to change existing trany structure to new 11m busck pole with new 50kva trany and earths upgraded as well,because of voltage complaints at 1745 egmont rd. Works location: Egmont Rd. WO 30031882 | F3 | BROOKLANDS 5 | CARRINGTON ST 33 | Taranaki | BROOKLANDS SUB | Western Electricity | POWERCO | 0.0057645 | 5.5 | 2017 | 2016-09-30 | B | 15 | 0.011529 | 4.5037e-05
1 | 13646861 | 2016-09-19 10:07 | 2016-09-19 11:06 | 59 | 37 | 2183 | 0.0065552 | 0.006221 | 0.00011111 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 737020 | FUSE - ELEMENT/LINK (HV) | Replace Faulty Fuses at Transofmer 2117T. Isolate HV from Fuses 6082 Used 1 full set of DDO's 3 x 3A Fuses | F4 | TE ROTI | STRATFORD | Taranaki | ELTHAM SUB | Western Electricity | POWERCO | 0.006221 | 11 | 2017 | 2016-09-19 | C | 37 | 0.006221 | 0.00011111
1 | 13680155 | 2016-10-17 09:30 | 2016-10-17 11:00 | 90 | 75 | 6750 | 0.020262 | 0.019586 | 0.00022514 | NAPA ID:23401 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | 023401 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 807 | NONE | Install new LV transformer fusing on TX 807. Works location: Maratahu Rd. WO 30018569 | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.009793 | 5.5 | 2017 | 2016-10-17 | B | 75 | 0.019586 | 0.00022514
1 | 13680171 | 2016-10-12 09:22 | 2016-10-12 16:20 | 418 | 5 | 2090 | 0.0062742 | 0.006229 | 1.501e-05 | NAPA ID:23712 TP_BRUNSWICK GXP > CASTLECLIFF SUB > HEADS RD | 11 | Planned | 023712 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 765394 | NONE | Replace 11kv poles 765394, 765395 and all X arms on transformer pole X1468. Works location: Mosston Rd, Wanganui. WO 30026831 | F2 | HEADS RD | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 0.0031145 | 5.5 | 2017 | 2016-10-12 | B | 5 | 0.006229 | 1.501e-05
1 | 13680240 | 2016-10-13 10:10 | 2016-10-13 11:30 | 80 | 14 | 1120 | 0.0033622 | 0.003236 | 4.2028e-05 | NAPA ID:23826 TP_STRATFORD GXP > DOUGLAS SUB > STRATHMORE | 11 | Planned | 023826 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 708819 | NONE | Replace HV cross arm and repair stay wire at pole 708819. Works location: Domain St. WO 30027374 | F4 | STRATHMORE | STRATFORD | Taranaki | DOUGLAS SUB | Western Electricity | POWERCO | 0.001618 | 5.5 | 2017 | 2016-10-13 | B | 14 | 0.003236 | 4.2028e-05
1 | 13680825 | 2016-10-05 09:00 | 2016-10-05 15:00 | 360 | 308 | 63895 | 0.19183 | 0.18906 | 0.0012519 | NAPA ID:23285 TP_TAURANGA 33 GXP > MATUA SUB > BELLEVUE RD | 11 | Planned | 023285 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 202335 | NONE | LLWP TO OPEN LINE GAPS X 2 AT POLES 202335 & 202307. AP TO REPLACE HV POLE WITH ABS , AND INSTALL 2 X SETS LINKS AS PER POWERCO SCOPE OF WORKS AND SOILD LINKS. LLWP TO CLOSE LINE GAPS X 2 AT POLES 202335 & 202307. Works location: Ngatai Rd, Tauranga. WO 30019246 | F3 | BELLEVUE RD | TAURANGA 31 | Tauranga | MATUA SUB | Eastern Electricity | POWERCO | 0.094528 | 5.5 | 2017 | 2016-10-05 | B | 308 | 0.18906 | 0.0012519
1 | 13680864 | 2016-10-11 09:15 | 2016-10-11 17:07 | 472 | 40 | 18880 | 0.056679 | 0.056318 | 0.00012008 | NAPA ID:23839 TP_MANGAMAIRE GXP > PARKVILLE SUB > MAURICEVILLE | 11 | Planned | 023839 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole P12836 | NONE | Tree removal between poles P12836 & P15595. Works location: Whangaehu Valley Rd. WO 30026290 | F4 | MAURICEVILLE | MANGAMAIRE | Manawatu | PARKVILLE SUB | Western Electricity | POWERCO | 0.028159 | 5.5 | 2017 | 2016-10-11 | B | 40 | 0.056318 | 0.00012008
1 | 13697390 | 2016-09-19 12:40 | 2016-09-19 12:58 | 17 | 82 | 1460.9667 | 0.0043871 | 0.003648 | 0.00024623 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | I12489 | INSULATOR | Emergency Switching to unbind conductor from broken insulator at ABS IC663. | F4 | MOTUMAOHO | PIAKO | Valley | PIAKO SUB | Eastern Electricity | POWERCO | 0.003648 | 11 | 2017 | 2016-09-19 | C | 82 | 0.003648 | 0.00024623
1 | 13697612 | 2016-09-19 13:21 | 2016-09-19 14:45 | 83 | 5 | 417.6667 | 0.0012542 | 0.001209 | 1.5014e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | B0394 | FUSE - ELEMENT/LINK (HV) | Replace 2 x 2A fuse | F3/F4 | OPOUTERE | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.001209 | 11 | 2017 | 2016-09-19 | C | 5 | 0.001209 | 1.5014e-05
1 | 13697834 | 2016-10-10 09:20 | 2016-10-10 10:48 | 88 | 88 | 7744 | 0.023248 | 0.022455 | 0.00026418 | NAPA ID:23411 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | 023411 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV pole 748812 | NONE | Install new HV insulators on Network pole 748812. Works location: Breakwater Rd, New Plymouth. WO 30018569 | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.011227 | 5.5 | 2017 | 2016-10-10 | B | 88 | 0.022455 | 0.00026418
1 | 13697836 | 2016-10-18 10:41 | 2016-10-18 14:23 | 222 | 3 | 666 | 0.0019992 | 0.001972 | 9.0053e-06 | NAPA ID:24110 TP_WAIHOU GXP > MIKKELSEN ROAD SUB > SPRINGDALE | 11 | Planned | 024110 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuse FP1281 | NONE | To relocate the existing 11kV Fuses on pole 264677 to below the 11kV arms and on the supply side of the pole. To replace and lower the 400V arm. Works location: Paeroa-Tahuna Rd, Te Aroha. WO 30031668 | F4 | SPRINGDALE | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.000986 | 5.5 | 2017 | 2016-10-18 | B | 3 | 0.001972 | 9.0053e-06
1 | 13697902 | 2016-10-11 09:48 | 2016-10-11 13:25 | 217 | 11 | 2387 | 0.0071659 | 0.007066 | 3.3023e-05 | NAPA ID:24105 TP_MANGAMAIRE GXP > MANGAMUTU SUB > COONOOR | 11 | Planned | 024105 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses T26 | NONE | To replace tx and tx pole. Works location: Mangone Valley Rd. WO 30017380 | F4/F5 | COONOOR | MANGAMAIRE | Manawatu | MANGAMUTU SUB | Western Electricity | POWERCO | 0.003533 | 5.5 | 2017 | 2016-10-11 | B | 11 | 0.007066 | 3.3023e-05
1 | 13697910 | 2016-09-30 11:00 | 2016-09-30 13:16 | 136 | 28 | 3808 | 0.011433 | 0.011181 | 8.4069e-05 | NAPA ID:24587 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 8 | 11 | Planned | 024587 | UNDERGROUND CABLE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 307 | NONE | remove inline fuses 785/3. cable from sw/g 12002/3 will now go to 785/2. Works location: Poplar Grove. WO 30018773 | F3 | MOTUROA 8 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.0055905 | 5.5 | 2017 | 2016-09-30 | B | 28 | 0.011181 | 8.4069e-05
1 | 13698118 | 2016-10-05 08:30 | 2016-10-05 14:11 | 341 | 46 | 15686 | 0.047094 | 0.046679 | 0.0001381 | NAPA ID:24586 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11 | Planned | 024586 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 12164 | NONE | Replace two pole tx structure with new groundmount tx and install new fuses 12164. Works location: Barrett Rd, New Plymouth. WO 30018773 | F3 | MOTUROA 9 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.023339 | 5.5 | 2017 | 2016-10-05 | B | 46 | 0.046679 | 0.0001381
1 | 13716754 | 2016-09-20 07:34 | 2016-09-20 11:58 | 263 | 422 | 58424.0667 | 0.17544 | 0.17164 | 0.0012672 |  | 11 | Unplanned |  | OVERHEAD LINE | VEGETATION | VEGETATION - OUTSIDE ZONE | 801220 | CONDUCTOR - REPAIR/REHANG | Faultman advises of 2 HV conductors down on Goldings Line, Marton. (CB 8 open from NOC, No tripping). Isolation required from ABS 519 to end. 4 Jointers required and about 10m conductor. Relivened OK. Problem caused by farmers trees in paddock. NDR 41491 | F4 | CROFTON | MARTON | Wanganui | ARAHINA SUB | Western Electricity | POWERCO | 0.17164 | 11 | 2017 | 2016-09-20 | C | 422 | 0.17164 | 0.0012672
1 | 13717300 | 2016-10-10 13:10 | 2016-10-10 14:22 | 72 | 122 | 8784 | 0.02637 | 0.025271 | 0.00036626 | NAPA ID:23404 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 2 | 11 | Planned | 023404 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer 548 | NONE | Install new TX LV fusing on TX 548 and replace LV insulators on pole 700579. Works location: Wallace Place. WO 30018569 | F4 | MOTUROA 2 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.012635 | 5.5 | 2017 | 2016-10-10 | B | 122 | 0.025271 | 0.00036626
1 | 13718904 | 2016-10-08 08:38 | 2016-10-08 09:17 | 39 | 1 | 39 | 0.00011708 | 0.000108 | 3.0021e-06 | NAPA ID:23351 TP_BRUNSWICK GXP > CASTLECLIFF SUB > PURIRI ST | 11 | Planned | 023351 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2640 | NONE | Non Resin DGS maintenance. Works location: Hinau St, Wanganui. WO 30021135 | F3 | PURIRI ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 5.4e-05 | 5.5 | 2017 | 2016-10-08 | B | 1 | 0.000108 | 3.0021e-06
1 | 13722943 | 2016-10-11 08:35 | 2016-10-11 12:25 | 230 | 18 | 4140 | 0.012429 | 0.012266 | 5.4037e-05 | NAPA ID:23367 TP_OPUNAKE GXP > TASMAN SUB > TE KIRI | 11 | Planned | 023367 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer T7445 | NONE | Replace T7445 and T7450 arms and fuses. Works location: Eltham Rd. WO 30015292 | F4 | TE KIRI | OPUNAKE | Taranaki | TASMAN SUB | Western Electricity | POWERCO | 0.006133 | 5.5 | 2017 | 2016-10-11 | B | 18 | 0.012266 | 5.4037e-05
1 | 13722991 | 2016-10-08 09:25 | 2016-10-08 09:48 | 23 | 2 | 46 | 0.0001381 | 0.00012 | 6.0043e-06 | NAPA ID:23444 TP_BRUNSWICK GXP > CASTLECLIFF SUB > PURIRI ST | 11 | Planned | 023444 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 2942 | NONE | Ground mount switchgear 4038 maintenance. Works location: Hinau St, Wanganui. WO 30021135 | F3 | PURIRI ST | BRUNSWICK | Wanganui | CASTLECLIFF SUB | Western Electricity | POWERCO | 6e-05 | 5.5 | 2017 | 2016-10-08 | B | 2 | 0.00012 | 6.0043e-06
1 | 13723204 | 2016-10-10 08:41 | 2016-10-10 15:15 | 394 | 46 | 18124 | 0.05441 | 0.053995 | 0.0001381 | NAPA ID:24591 TP_NEW PLYMOUTH GXP > MOTUROA SUB > MOTUROA 9 | 11 | Planned | 024591 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Fuses 12164 | NONE | Replace two pole tx structure with new groundmount tx and install new fuses 12164. Works location: Barrett Rd, New Plymouth. WO 30018773 | F3 | MOTUROA 9 | NEW PLYMOUTH | Taranaki | MOTUROA SUB | Western Electricity | POWERCO | 0.026998 | 5.5 | 2017 | 2016-10-10 | B | 46 | 0.053995 | 0.0001381
1 | 13723350 | 2016-10-04 09:38 | 2016-10-04 13:54 | 256 | 71 | 18176 | 0.05457 | 0.05393 | 0.00021316 | NAPA ID:23665 TP_HUIRANGI GXP > INGLEWOOD SUB > BROOKES ST | 6.60000000 | Planned | 023665 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS 5374 | NONE | replace two pole tx structure with new 300kva groundmount tx. remove abs and install new 11kv fuses. Works location: Miro St, Inglewood. WO 30018773 | F3 | BROOKES ST | HUIRANGI | Taranaki | INGLEWOOD SUB | Western Electricity | POWERCO | 0.026965 | 3.3 | 2017 | 2016-10-04 | B | 71 | 0.05393 | 0.00021316
1 | 13723444 | 2016-10-18 10:05 | 2016-10-18 10:20 | 15 | 7 | 105 | 0.00031519 | 0.000252 | 2.1012e-05 | NAPA ID:24084 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | 024084 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC646 | NONE | To install a 400V Fuse Disconnector on TC646. Works location: Banks Rd, Matamata. WO 30019182 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 0.000126 | 5.5 | 2017 | 2016-10-18 | B | 7 | 0.000252 | 2.1012e-05
1 | 13723500 | 2016-10-18 11:30 | 2016-10-18 11:50 | 20 | 3 | 60 | 0.00018011 | 0.000153 | 9.0053e-06 | NAPA ID:24086 TP_HINUERA GXP > BROWNE STREET SUB > FIRTH ST | 11 | Planned | 024086 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TP1602 | NONE | To install a 400V Disconnector on TP1602. Works location: Banks Rd, Matamata. WO 30019182 | F3 | FIRTH ST | HINUERA | Valley | BROWNE STREET SUB | Eastern Electricity | POWERCO | 7.65e-05 | 5.5 | 2017 | 2016-10-18 | B | 3 | 0.000153 | 9.0053e-06
1 | 13723529 | 2016-09-27 10:30 | 2016-09-27 14:30 | 240 | 1 | 240 | 0.00072062 | 0.000711 | 3.0025e-06 | NAPA ID:23987 TP_BUNNYTHORPE GXP > KELVIN GROVE SUB > POHANGINA | 11 | Planned | 023987 | DISTRIBUTION EQUIPMENT | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | T4/181 | NONE | LLP to disconnect 11kV fuses and replace fuse arm and hardware at T4/181, reconnect to main Line. AP to replace TX T4/181 | F4 | POHANGINA | BUNNYTHORPE | Manawatu | KELVIN GROVE SUB | Western Electricity | POWERCO | 0.0003555 | 5.5 | 2017 | 2016-09-27 | B | 1 | 0.000711 | 3.0025e-06
1 | 13723533 | 2016-10-18 14:00 | 2016-10-18 14:15 | 15 | 3 | 45 | 0.00013508 | 0.000108 | 9.0053e-06 | NAPA ID:23531 TP_HINUERA GXP > LAKE ROAD SUB > BUCKLAND RD | 11 | Planned | 023531 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC1645 | NONE | To install a 400V Disconnector on TC1645. Works location: Pond Rd, Matamata. WO 30019182 | F4 | BUCKLAND RD | HINUERA | Valley | LAKE ROAD SUB | Eastern Electricity | POWERCO | 5.4e-05 | 5.5 | 2017 | 2016-10-18 | B | 3 | 0.000108 | 9.0053e-06
1 | 13723576 | 2016-10-11 09:35 | 2016-10-11 12:35 | 180 | 6 | 1080 | 0.0032422 | 0.003188 | 1.8012e-05 | NAPA ID:23464 TP_MT MAUNGANUI 33 GXP > PAPAMOA SUB > BLACK STUMP | 11 | Planned | 023464 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV SD5-021 | NONE | REPLACE HV HARD WOOD POLE. Works location: Bell Rd, Te Puke. WO 30018946 | F4 | BLACK STUMP | MT MAUNGANUI 31 | Tauranga | PAPAMOA SUB | Eastern Electricity | POWERCO | 0.001594 | 5.5 | 2017 | 2016-10-11 | B | 6 | 0.003188 | 1.8012e-05
1 | 13741334 | 2016-09-20 19:13 | 2016-09-20 22:30 | 197 | 169 | 25035.7167 | 0.075178 | 0.073655 | 0.00050748 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 764738 | CONDUCTOR - REPAIR/REHANG | Recloser 5475 tripped on A & B phase. O/C. Rehang conductor at pole 764738. 6 X 16mm Selvees 10M Copper 16mm | F5 | MAIN RD MOTONUI | HUIRANGI | Taranaki | WAITARA EAST SUB | Western Electricity | POWERCO | 0.073655 | 11 | 2017 | 2016-09-20 | C | 169 | 0.073655 | 0.00050748
1 | 13741543 | 2016-09-20 19:33 | 2016-09-20 22:28 | 174 | 202 | 22941.2 | 0.068888 | 0.067068 | 0.00060657 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1 | UNKNOWN | CB 1 tripped E/F L/O During sectionlising CB 1 operations were slow break came up with trips while breaker still in transit but drawing current. No Fault found during sectionlising | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.067068 | 11 | 2017 | 2016-09-20 | C | 202 | 0.067068 | 0.00060657
1 | 13742144 | 2016-09-20 23:47 | 2016-09-21 01:05 | 78 | 202 | 14747.9667 | 0.044286 | 0.042465 | 0.00060657 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - NO FAULT FOUND | CB 1 | UNKNOWN | CB 1 Tripped E/F no fault found during sectionlising Feeder split to help locate fault | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.042465 | 11 | 2017 | 2016-09-20 | C | 202 | 0.042465 | 0.00060657
1 | 13746146 | 2016-09-21 07:42 | 2016-09-21 13:18 | 335 | 186 | 25990.9333 | 0.078045 | 0.076369 | 0.00055852 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | 346482 | POLE | Car v Pole on State Highway 27, between Whakahoro Road and No 9 Road, Spingdale. Fire comms require eta - F2154902. Have advised Control and svs hub Eta: 15mins. Car v pole 346482. isolation between ABS's 583 & 1057 Recloser RP05 closed & back feed via ABS IC653. NDR No 55723 All repairs carried out all service restored ( pole ok & reused, arm replaced ) Materials 1 x H/V arm complete | F4 | TE PUNINGA | WAIHOU | Valley | TAHUNA SUB | Eastern Electricity | POWERCO | 0.076369 | 11 | 2017 | 2016-09-21 | C | 186 | 0.076369 | 0.00055852
1 | 13746823 | 2016-10-11 10:34 | 2016-10-11 12:31 | 117 | 1 | 117 | 0.00035124 | 0.000342 | 3.002e-06 | NAPA ID:24413 TP_MATAROA GXP > WAIOURU SUB > CAMP RD | 11 | Planned | 024413 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV FABS 4478 | NONE | 11Kv metering calibration checks at two sites Waiouru Army camp. Stage 1. Camp road sub.Stage 2 Tank hanger Sub. Works location: Waiouru Army Camp. WO 30033067 | F1 | CAMP RD | MATAROA | Wanganui | WAIOURU SUB | Western Electricity | POWERCO | 0.000171 | 5.5 | 2017 | 2016-10-11 | B | 1 | 0.000342 | 3.002e-06
1 | 13746931 | 2016-10-12 09:31 | 2016-10-12 15:37 | 366 | 395 | 45786 | 0.13745 | 0.13389 | 0.0011858 | NAPA ID:24451 TP_KOPU GXP > WHITIANGA SUB > COROGLEN | 11 | Planned | 024451 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Transformer TC3979 | NONE | Replace pole mount 100kVA with ground mount 300kVA. Works location: Hahei Beach Rd, Whitianga. WO 30032451 | F4 | COROGLEN | KOPU | Valley | WHITIANGA SUB | Eastern Electricity | POWERCO | 0.066947 | 5.5 | 2017 | 2016-10-12 | B | 395 | 0.13389 | 0.0011858
1 | 13748414 | 2016-09-21 10:57 | 2016-09-21 11:14 | 16 | 95 | 1605.5 | 0.004821 | 0.003965 | 0.00028526 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | C12918 | JUMPER | Outage required between ABS IC1241 & ABS IC676 to repair blown jumper at Pole C12918. No backfeeds available. 2r not needed because job needed to be completed by an outage due to bad weather making it unsafe to complete live line 1 x fuse holder, 1 x 3amp HV fuses and Jumper replaced, relivend OK | F4 | MAUNGAKAWA ROAD | WAIHOU | Valley | MIKKELSEN ROAD SUB | Eastern Electricity | POWERCO | 0.003965 | 11 | 2017 | 2016-09-21 | C | 95 | 0.003965 | 0.00028526
1 | 13749178 | 2016-09-21 11:04 | 2016-09-21 13:36 | 151 | 640 | 9154.95 | 0.02749 | 0.021725 | 0.0019218 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - ANIMAL - OPOSSUM | R12392 | UNKNOWN | CB 1 - Tripped on E/F Opossum found on Lines at pole R12392 | F4 | WHIRITOA | WAIKINO | Valley | WHANGAMATA SUB | Eastern Electricity | POWERCO | 0.021725 | 11 | 2017 | 2016-09-21 | C | 640 | 0.021725 | 0.0019218
1 | 13751691 | 2016-09-21 14:46 | 2016-09-22 03:10 | 744 | 324 | 135166.4 | 0.40588 | 0.40296 | 0.0009729 |  | 11 | Unplanned |  | OVERHEAD LINE | FOREIGN INTERFERENCE | FOREIGN INTERFERENCE - THIRD PARTY DAMAGE - VEHICLE DAMAGE | WKOPOA113 | POLE | NOC Tripped CB7. A call was received at 14:46 from a Northpower employee driving past, that a car had hit a pole just out of Paeroa and that the 33kV and 11kV lines were hanging at about head height. Police were on site directing traffic. The 11kV lines were de-energised by NOC, 33kV Lines by NGOC and a faultman dispatched. There had been an earlier Auto Reclose tripping on this feeder at 14:28. Pole Replaced NDR 52007 - | F3 | SHAW AVE | WAIKINO | Valley | PAEROA SUB | Eastern Electricity | POWERCO | 0.40296 | 11 | 2017 | 2016-09-21 | C | 324 | 0.40296 | 0.0009729
1 | 13752326 | 2016-09-21 18:00 | 2016-09-21 18:37 | 37 | 23 | 851 | 0.0025554 | 0.002348 | 6.9064e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 717515 | JUMPER | MNA 6 Emergency switching to repair burnt jumper at transformer M2052 pole 717515 Isolation at fuses MA298 ( spur no back feed ) Jumper repaired all service restored | F4 | OTAKEHO | HAWERA | Taranaki | MANAIA SUB | Western Electricity | POWERCO | 0.002348 | 11 | 2017 | 2016-09-21 | C | 23 | 0.002348 | 6.9064e-05
1 | 13752455 | 2016-09-21 16:21 | 2016-09-21 18:31 | 130 | 68 | 8889.8667 | 0.026694 | 0.026081 | 0.00020419 |  | 11 | Unplanned |  | OVERHEAD LINE | UNKNOWN | UNKNOWN - PATROLLED - CAUSE UNKNOWN | N/A - NOT APPLICABLE | UNKNOWN | WLN 1 tripped E/F, L/O Sectionalised & Patrolled, No fault found. Walton CB1 Feeder opened at ABS IC730 & from there to the end left backfed from WLN 4 via ABS 724. This to determine fault area as there seems to be a recurrent fault on the feeder that can not be found. | F4 | WAIRERE RD | PIAKO | Valley | WALTON SUB | Eastern Electricity | POWERCO | 0.026081 | 11 | 2017 | 2016-09-21 | C | 68 | 0.026081 | 0.00020419
1 | 13753476 | 2016-09-22 01:13 | 2016-09-22 02:38 | 84 | 4206 | 239623.5 | 0.71953 | 0.68164 | 0.01263 |  | 33 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - BROKEN HARDWARE | 738827 | DEAD-ENDS | 33kV CB 2842 tripped Over Current to lock out. LOS to Cloten Road Sub - Safety Manager report No. 662451 LOS to sub & protection review. 11kV CB's opened by NOC. 33kV line patrolled with a broken dead end found at pole 738827. 33kV network reconfigured with transformer re-livened by SFD 2782 circuit (ABS 359 now open) On re-livening 11kV CB's, 8 closed successfully. Attempts to close CB's 4 & 6 were unsuccessful and seen SOTF alarms initiated. Also brought up relay 2082T 787 protection trip flag. Both CB's 6 & 8 had to be sectionalised to allow relivening. NO fault found, suspect protection issues, NCTL advised, to follow up with PCO protection. Mike Allpress requested relays to be down loaded asap to allow review of events to ascertain why CB's 4 & 6 would not close. The 33kV fault will be completed in daylight via bucket truck to replace the broken 33kV dead end at pole 738827. Used 1 x 33kV Weta Deadend. | S1 | CLOTON ROAD NORTH 33KV | STRATFORD | Taranaki | TP_STRATFORD | Western Electricity | POWERCO | 0.68164 | 33 | 2017 | 2016-09-22 | C | 4206 | 0.68164 | 0.01263
1 | 13758188 | 2016-10-11 09:04 | 2016-10-11 15:26 | 382 | 172 | 65704 | 0.19725 | 0.1957 | 0.00051635 | NAPA ID:23407 TP_TE MATAI GXP > PONGAKAWA SUB > TAINUI | 11 | Planned | 023407 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV ABS IP506 | NONE | Replace poles,hardware and conductor along Pukehina Parade. Works location: Pukehina Parade, Te Puke. WO 30019859 | F4 | TAINUI | TE MATAI | Tauranga | PONGAKAWA SUB | Eastern Electricity | POWERCO | 0.097849 | 5.5 | 2017 | 2016-10-11 | B | 172 | 0.1957 | 0.00051635
1 | 13758298 | 2016-09-22 08:25 | 2016-09-22 10:00 | 95 | 17 | 1616.4167 | 0.0048537 | 0.0047 | 5.1047e-05 |  | 11 | Unplanned |  | OVERHEAD LINE | DEFECTIVE EQUIPMENT | DEFECTIVE EQUIPMENT - OH EQUIPMENT FAILURE | 366350 | FUSE - ELEMENT/LINK (HV) | 2 HV fuses blown at 840 Reload 2 x 6A Fuses 840 Unknown | F4 | MATAROA A | MATAROA | Wanganui | TAIHAPE SUB | Western Electricity | POWERCO | 0.0047 | 11 | 2017 | 2016-09-22 | C | 17 | 0.0047 | 5.1047e-05
1 | 13759793 | 2016-09-27 09:11 | 2016-09-27 10:47 | 96 | 15 | 1416 | 0.0042516 | 0.004116 | 4.5038e-05 | NAPA ID:24663 TP_HAWERA GXP > WHAREROA SUB > WHAKAMARA | 11 | Planned | 024663 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 725409 | POLE | Span between 725409 and 725421 has two phases down third is cut way at termination. Require emergancy shutdown to stay two pole structure 725409 as exess weight is putting strain on pole. (will place double stay to single deadman) and straighten poles. Require dry weather to access and run new conductor at a later date | F4 | WHAKAMARA | HAWERA | Taranaki | WHAREROA SUB | Western Electricity | POWERCO | 0.002058 | 5.5 | 2017 | 2016-09-27 | B | 15 | 0.004116 | 4.5038e-05
1 | 13759836 | 2016-10-13 08:32 | 2016-10-13 13:25 | 293 | 24 | 7032 | 0.02111 | 0.020893 | 7.2048e-05 | NAPA ID:24459 TP_MASTERTON GXP > GLADSTONE SUB > WESTMERE GLADSTONE | 11 | Planned | 024459 | OVERHEAD LINE | PLANNED SHUTDOWN | PLANNED SHUTDOWN - CAPITAL WORKS | 11kV Links 7148 | NONE | replace defective poles past links 7148. Works location: Cameron Rd, Carterton. WO 30018283 | F4 | WESTMERE GLADSTONE | MASTERTON | Wairarapa | GLADSTONE SUB | Western Electricity | POWERCO | 0.010446 | 5.5 | 2017 | 2016-10-13 | B | 24 | 0.020893 | 7.2048e-05