## Cover
QUALITY PATH UNPLANNED SAIDI/SAIFI MODEL
Profile MODEL
Final
2017-06-02
Document information
Author: | Powerco
Created:
Last updated: | 2017-06-02
Status: | Final

## Approach
Purpose
This model builds up a complete profile for the Unplanned SAIDI Forecast 2018-2028 through a combination of historical trending and planned CPP investment during the forecast period
Forecasting Approach
Summary of the approach
Component | Fault numbers | Duration |  | ICPs Impacted
Poles | Based on fault rates using cumulative retirement curves for each area and historical faults from 2008 to 2017. | Average historical duration linked to historical trend |  | ICPs escalated in accordance with the projected ICP growth by region
Crossarms
Distribution Transformers
Fuses | As above except for 2015 to 2017
Conductors | Based on forecast conductor fault rates
Subtransmission | Baselined using historical average
Remaining equipment related faults
Vegetation | Forecast based on the modelled impact of the proposed vegetation management approach.
Adverse Weather | Remainder forecast base-lines the average remainder values from 2008 to 2017. Unknown is trend adjusted for both historical presistence and vegetation management changes
Unknown
Remainder
Structure
Workbook colour coding
Input worksheets are
Calculation worksheets are
Output worksheets are
Grouping/guidance worksheets are
Worksheet structure
Direct input cells are:
Inputs from other model outputs
| Worksheet Type |  | Worksheets |  | Description
Input
Calcs
Calcs
Calcs
Calcs
Output
Output
End

## Historical Fault Information
Historical SAIDI Data
Histoical non-normalised ID input data.
| # of Faults | [9 empty] | Weighted Average Duration | [9 empty] | Weighted average # of ICPs Impacted | [9 empty] | SAIDI | [9 empty] | SAIFI
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Poles
Total | 32 | 36 | 25 | 40 | 38 | 29 | 56 | 41 | 31 | 21 | 89.6803 | 109.8632 | 126.9121 | 253.8869 | 103.0909 | 118.9194 | 254.6859 | 213.5395 | 114.2917 | 249.1835 | 61.7244 | 140.8352 | 140.6495 | 110.5178 | 102.9303 | 273.9356 | 63.2967 | 168.1264 | 180.4038 | 47.3901 | 1.2787 | 1.5166 | 1.2991 | 4.6808 | 3.5281 | 2.0677 | 4.4908 | 2.2979 | 3.6058 | 0.7913 | 0.0076381 | 0.012226 | 0.0076789 | 0.023361 | 0.016016 | 0.019236 | 0.017614 | 0.014344 | 0.019936 | 0.0048574
Non-zero Average | 4 | 3 | 2.5 | 3.6364 | 4.2222 | 3.2222 | 5.0909 | 3.7273 | 2.8182 | 2.3333 | 145.7304 | 119.0185 | 164.9857 | 300.0481 | 148.909 | 171.7725 | 300.9924 | 252.3649 | 135.072 | 359.9318 | 100.3021 | 152.5714 | 182.8443 | 130.6119 | 148.6771 | 395.6847 | 74.8052 | 198.6948 | 213.2045 | 68.4524 | 0.15984 | 0.12639 | 0.12991 | 0.42553 | 0.39201 | 0.22974 | 0.40826 | 0.2089 | 0.3278 | 0.087922 | 0.00095476 | 0.0010189 | 0.00076789 | 0.0021238 | 0.0017796 | 0.0021373 | 0.0016012 | 0.001304 | 0.0018123 | 0.00053971
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 0 | 3 | 2 | 1 | 1 | 1 | 4 | 3 | 2 | 0 | 0 | 163.8647 | 221.3597 | 148.9178 | 57.9208 | 397 | 97.3282 | 127.8634 | 356.9181 | 0 | 0 | 202 | 151.4999 | 89 | 36 | 2.9997 | 74.25 | 266 | 958 | 0 | 0 | 0.31568 | 0.21195 | 0.041627 | 0.0065164 | 0.0036969 | 0.089027 | 0.31166 | 2.0678 | 0 | 0 | 0.0019265 | 0.00095749 | 0.00027953 | 0.0001125 | 9.3121e-06 | 0.00091471 | 0.0024374 | 0.0057935 | 0
Egmont | 3 | 2 | 2 | 1 | 5 | 0 | 2 | 1 | 4 | 2 | 98.2912 | 85.8876 | 257 | 204 | 77.4126 | 0 | 39.913 | 17 | 135.0181 | 187.9913 | 121.3333 | 124.5 | 25 | 15 | 112.2 | 0 | 23 | 2 | 151.25 | 193 | 0.11506 | 0.067986 | 0.040606 | 0.0096109 | 0.13572 | 0 | 0.0056546 | 0.00010385 | 0.247 | 0.21731 | 0.0011706 | 0.00079157 | 0.000158 | 4.7112e-05 | 0.0017532 | 0 | 0.00014167 | 6.1088e-06 | 0.0018294 | 0.0011559
Kinleith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022878 | 0 | 0
Manawatu | 0 | 1 | 1 | 5 | 0 | 3 | 1 | 1 | 2 | 0 | 0 | 139.9389 | 91.4763 | 189.1024 | 0 | 89.3891 | 64 | 657 | 25.2251 | 0 | 0 | 131 | 736.9996 | 698.8 | 0 | 557.9376 | 3 | 3 | 36.5 | 0 | 0 | 0.058277 | 0.21304 | 2.0752 | 0 | 0.46448 | 0.00059133 | 0.0060203 | 0.0055681 | 0 | 0 | 0.00041645 | 0.0023289 | 0.010974 | 0 | 0.0051961 | 9.2395e-06 | 9.1633e-06 | 0.00022073 | 0
Mt Maunganui | 0 | 1 | 1 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 138 | 203.9083 | 124.1381 | 66.5356 | 239.2158 | 0 | 0 | 165 | 0 | 0 | 43 | 555.9997 | 201 | 333 | 144.9838 | 0 | 0 | 13 | 0 | 0 | 0.018864 | 0.35826 | 0.23511 | 0.069241 | 0.10767 | 0 | 0 | 0.006486 | 0 | 0 | 0.0001367 | 0.001757 | 0.0018939 | 0.0010407 | 0.00045008 | 0 | 0 | 3.9309e-05 | 0
Rangitikei | 1 | 1 | 0 | 1 | 3 | 3 | 4 | 3 | 1 | 1 | 117 | 6 | 0 | 1046.0246 | 113.6771 | 135.2102 | 272.8797 | 1152.25 | 210.3002 | 96 | 182 | 796 | 0 | 59 | 32.3333 | 52.3275 | 45.25 | 52 | 69 | 11 | 0.068482 | 0.015183 | 0 | 0.19384 | 0.03446 | 0.065892 | 0.15212 | 0.54904 | 0.043877 | 0.0031624 | 0.00058532 | 0.0025305 | 0 | 0.00018531 | 0.00030314 | 0.00048733 | 0.00055745 | 0.00047649 | 0.00020864 | 3.2942e-05
Taranaki | 3 | 4 | 2 | 1 | 9 | 4 | 2 | 6 | 2 | 2 | 91.895 | 154.8938 | 263.0588 | 145 | 367.848 | 79.5533 | 224.85 | 30.4264 | 39.6667 | 1582.6381 | 127 | 129.5 | 8.5 | 17 | 240.6667 | 179.4799 | 60 | 41 | 67.5 | 7 | 0.1126 | 0.25507 | 0.014132 | 0.0077421 | 2.49 | 0.1773 | 0.0831 | 0.022862 | 0.016192 | 0.066353 | 0.0012253 | 0.0016467 | 5.372e-05 | 5.3394e-05 | 0.006769 | 0.0022287 | 0.00036958 | 0.00075139 | 0.00040821 | 4.1926e-05
Tararua | 3 | 3 | 2 | 3 | 6 | 4 | 7 | 6 | 5 | 2 | 258.7545 | 113.507 | 83.5976 | 156.2677 | 86.1302 | 97.7363 | 115.7158 | 71.132 | 101.8354 | 56.3013 | 55.6667 | 47.3333 | 41 | 42.3333 | 90.1667 | 112.9874 | 108.8571 | 41.3333 | 13 | 26.5 | 0.13897 | 0.051239 | 0.021662 | 0.062333 | 0.14562 | 0.13713 | 0.27157 | 0.053882 | 0.020015 | 0.008936 | 0.00053708 | 0.00045142 | 0.00025912 | 0.00039888 | 0.0016907 | 0.001403 | 0.0023468 | 0.0007575 | 0.00019654 | 0.00015872
Tauranga | 3 | 2 | 2 | 4 | 0 | 1 | 1 | 1 | 3 | 1 | 215.01 | 23.8683 | 272.4792 | 658.0174 | 0 | 30.032 | 185 | 16.2405 | 40.1218 | 182 | 199.6667 | 121.5 | 215.9999 | 33.5 | 0 | 1332.851 | 6 | 817 | 834.6667 | 2 | 0.4142 | 0.018438 | 0.37197 | 0.27694 | 0 | 0.12426 | 0.0034186 | 0.040528 | 0.30378 | 0.0010901 | 0.0019264 | 0.0007725 | 0.0013651 | 0.00042087 | 0 | 0.0041377 | 1.8479e-05 | 0.0024955 | 0.0075715 | 5.9894e-06
Waikato | 2 | 1 | 1 | 3 | 1 | 1 | 2 | 1 | 3 | 2 | 102.3985 | 95 | 58 | 346.2511 | 236.7492 | 66.9217 | 176.0683 | 172.3519 | 131.8667 | 118.25 | 66.5 | 88 | 66 | 103.3333 | 167 | 1123.8744 | 80.5 | 348 | 49.3333 | 2 | 0.043799 | 0.026576 | 0.012097 | 0.33713 | 0.12356 | 0.23349 | 0.087304 | 0.1832 | 0.059013 | 0.0014165 | 0.00042773 | 0.00027975 | 0.00020856 | 0.00097365 | 0.0005219 | 0.0034889 | 0.00049585 | 0.0010629 | 0.00044752 | 1.1979e-05
Waikino | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 53 | 0 | 0 | 0 | 0 | 736.4261 | 0 | 0 | 177.6963 | 0 | 72 | 0 | 0 | 0 | 0 | 284.5 | 0 | 0 | 286.5 | 0 | 0.012131 | 0 | 0 | 0 | 0 | 1.2905 | 0 | 0 | 0.30492 | 0 | 0.00022889 | 0 | 0 | 0 | 0 | 0.0017524 | 0 | 0 | 0.001716
Wairarapa | 16 | 14 | 9 | 17 | 11 | 11 | 30 | 14 | 7 | 7 | 223.4944 | 222.0549 | 90.9108 | 177.9366 | 117.6393 | 410.8943 | 222.7354 | 275.8746 | 259.8399 | 91.5088 | 33.25 | 66.3571 | 17.4444 | 150.7647 | 89.7273 | 53.7213 | 118.5 | 55.1429 | 152 | 80.5714 | 0.38238 | 0.65579 | 0.045103 | 1.4324 | 0.36286 | 0.75378 | 2.4387 | 0.65052 | 0.83598 | 0.15456 | 0.0017109 | 0.0029533 | 0.00049612 | 0.0080499 | 0.0030845 | 0.0018345 | 0.010949 | 0.002358 | 0.0032173 | 0.001689
Whanganui | 1 | 3 | 3 | 1 | 1 | 0 | 1 | 3 | 1 | 2 | 59 | 232.2069 | 108.0667 | 104.8736 | 216.2684 | 0 | 1176 | 179.4986 | 20 | 747 | 17 | 9.6667 | 10 | 27 | 237 | 0 | 19 | 185.6667 | 1 | 7.5 | 0.0032257 | 0.021407 | 0.010245 | 0.0088935 | 0.16018 | 0 | 0.068816 | 0.30538 | 6.0475e-05 | 0.033555 | 5.4673e-05 | 9.2191e-05 | 9.4801e-05 | 8.4802e-05 | 0.00074066 | 0 | 5.8517e-05 | 0.0017013 | 3.0238e-06 | 4.492e-05
Xarms
Total | 408 | 366 | 357 | 424 | 507 | 423 | 461 | 377 | 378 | 464 | 83.5654 | 85.9145 | 78.9782 | 109.1959 | 97.8118 | 78.6012 | 88.0785 | 105.1263 | 95.1743 | 90.4271 | 255.4045 | 179.2468 | 166.3371 | 150.9657 | 148.4864 | 202.4812 | 185.5713 | 177.6257 | 184.9067 | 148.4604 | 22.0394 | 14.639 | 16.0717 | 23.0731 | 27.7836 | 17.4652 | 23.3919 | 19.8116 | 16.3802 | 17.834 | 0.27852 | 0.21265 | 0.19034 | 0.21606 | 0.23926 | 0.23207 | 0.24742 | 0.20305 | 0.20314 | 0.23919
Non-zero Average | 31.3846 | 28.1538 | 27.4615 | 32.6154 | 42.25 | 32.5385 | 35.4615 | 29 | 29.0769 | 35.6923 | 83.5654 | 85.9145 | 78.9782 | 109.1959 | 105.9628 | 78.6012 | 88.0785 | 105.1263 | 95.1743 | 90.4271 | 255.4045 | 179.2468 | 166.3371 | 150.9657 | 160.8603 | 202.4812 | 185.5713 | 177.6257 | 184.9067 | 148.4604 | 1.6953 | 1.1261 | 1.2363 | 1.7749 | 2.3153 | 1.3435 | 1.7994 | 1.524 | 1.26 | 1.3718 | 0.021424 | 0.016358 | 0.014642 | 0.01662 | 0.019938 | 0.017852 | 0.019032 | 0.015619 | 0.015626 | 0.018399
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 25 | 35 | 19 | 20 | 19 | 26 | 29 | 26 | 23 | 21 | 59.5881 | 41.5041 | 67.9183 | 104.0411 | 67.0423 | 66.7896 | 133.937 | 66.6672 | 67.1845 | 79.0282 | 367.76 | 283.6 | 175.1578 | 162.35 | 209.0526 | 167.5582 | 103.4483 | 263.4615 | 251 | 220.9524 | 1.7619 | 1.3096 | 0.71427 | 1.061 | 0.8322 | 0.90328 | 1.2375 | 1.3949 | 1.1728 | 1.0981 | 0.029568 | 0.031555 | 0.010517 | 0.010198 | 0.012413 | 0.013524 | 0.0092395 | 0.020923 | 0.017456 | 0.013895
Egmont | 30 | 37 | 46 | 42 | 73 | 40 | 90 | 66 | 43 | 71 | 84.7084 | 64.2916 | 101.8463 | 105.4639 | 230.2376 | 68.8994 | 98.4656 | 93.5536 | 59.7926 | 79.582 | 149.7333 | 91.1081 | 155.1304 | 105.4524 | 110.0959 | 113.1374 | 134.6 | 133.1364 | 141.907 | 151.2676 | 1.2237 | 0.68897 | 2.2966 | 1.4671 | 5.7828 | 0.96796 | 3.6737 | 2.5109 | 1.1032 | 2.5596 | 0.014446 | 0.010716 | 0.02255 | 0.013911 | 0.025117 | 0.014049 | 0.037309 | 0.026839 | 0.018451 | 0.032163
Kinleith | 4 | 1 | 1 | 5 | 0 | 3 | 3 | 3 | 3 | 5 | 66.2191 | 132 | 25 | 96.9223 | 0 | 88.0853 | 28.5238 | 149.7227 | 171.6662 | 269.6943 | 499.75 | 1 | 52 | 80.4 | 0 | 47.328 | 21 | 55.3333 | 67 | 115.6 | 0.42571 | 0.00041963 | 0.004108 | 0.12238 | 0 | 0.038826 | 0.0055345 | 0.075915 | 0.10433 | 0.46682 | 0.0064289 | 3.179e-06 | 0.00016432 | 0.0012626 | 0 | 0.00044077 | 0.00019403 | 0.00050703 | 0.00060778 | 0.0017309
Manawatu | 44 | 38 | 54 | 53 | 67 | 42 | 42 | 45 | 37 | 51 | 54.2278 | 71.1594 | 86.3559 | 125.2416 | 86.9549 | 63.9456 | 68.0642 | 98.4092 | 66.7534 | 50.4444 | 207.0455 | 177.1316 | 151.2221 | 229.4717 | 174.1493 | 236.4736 | 265.2857 | 270.9778 | 188.5676 | 325.0588 | 1.5888 | 1.5227 | 2.2284 | 4.7841 | 3.1707 | 1.9716 | 2.3357 | 3.6653 | 1.4083 | 2.5044 | 0.029298 | 0.021398 | 0.025805 | 0.038199 | 0.036464 | 0.030832 | 0.034316 | 0.037246 | 0.021097 | 0.049646
Mt Maunganui | 13 | 19 | 13 | 15 | 16 | 17 | 16 | 9 | 12 | 15 | 124.91 | 97.9634 | 120.3394 | 136.9234 | 40.6805 | 14.6002 | 66.3475 | 56.5845 | 77.2443 | 84.9714 | 251.1538 | 201.5263 | 240.2306 | 61.2 | 118.625 | 198.8601 | 85.9375 | 104.6667 | 173.1667 | 34.7333 | 1.3116 | 1.1924 | 1.1876 | 0.39479 | 0.2413 | 0.15323 | 0.28097 | 0.16281 | 0.48535 | 0.13258 | 0.0105 | 0.012172 | 0.0098688 | 0.0028833 | 0.0059315 | 0.010495 | 0.0042348 | 0.0028773 | 0.0062834 | 0.0015602
Rangitikei | 19 | 16 | 24 | 27 | 29 | 30 | 20 | 20 | 14 | 27 | 80.8582 | 170.9382 | 132.6724 | 169.1167 | 144.6876 | 90.2759 | 130.6984 | 134.8988 | 137.9061 | 85.5035 | 143.2632 | 62.6875 | 107.4583 | 114.7778 | 208.7241 | 178.4467 | 191.5 | 192.85 | 222.5714 | 144.3333 | 0.70784 | 0.54504 | 1.0812 | 1.6461 | 2.737 | 1.5003 | 1.5417 | 1.5892 | 1.2994 | 0.99785 | 0.0087541 | 0.0031885 | 0.0081497 | 0.0097334 | 0.018916 | 0.016619 | 0.011796 | 0.011781 | 0.009422 | 0.01167
Taranaki | 58 | 61 | 61 | 66 | 96 | 77 | 64 | 50 | 64 | 80 | 78.0601 | 65.4927 | 87.0084 | 109.5387 | 123.457 | 63.3972 | 109.22 | 110.2681 | 73.2577 | 78.7213 | 238.2241 | 255.7869 | 220.754 | 264.6212 | 185.4583 | 174.6039 | 184.5 | 220.58 | 271.0312 | 201.225 | 3.4687 | 3.2486 | 3.7025 | 6.0087 | 6.8691 | 2.646 | 3.972 | 3.7146 | 3.8424 | 3.795 | 0.044436 | 0.049602 | 0.042553 | 0.054854 | 0.05564 | 0.041737 | 0.036367 | 0.033687 | 0.05245 | 0.048208
Tararua | 47 | 38 | 22 | 40 | 59 | 37 | 48 | 42 | 43 | 49 | 137.1531 | 154.7924 | 78.1157 | 140.0982 | 132.4237 | 107.3246 | 88.462 | 69.2371 | 204.1308 | 140.6028 | 77.8085 | 64.0263 | 121.409 | 74.2 | 86.6949 | 104.7721 | 105.3958 | 108.0238 | 57.1395 | 94.3265 | 1.6131 | 1.1972 | 0.65933 | 1.306 | 2.1168 | 1.2916 | 1.3783 | 0.95948 | 1.5166 | 1.9461 | 0.011761 | 0.0077345 | 0.0084404 | 0.009322 | 0.015985 | 0.012034 | 0.015581 | 0.013858 | 0.0074294 | 0.013841
Tauranga | 26 | 18 | 16 | 25 | 33 | 20 | 23 | 19 | 25 | 28 | 84.0396 | 68.7839 | 41.301 | 82.8822 | 98.0646 | 68.6278 | 63.5179 | 59.3533 | 86.355 | 53.2026 | 315.4231 | 499.1111 | 119.8124 | 233.2 | 187.1818 | 188.7289 | 259.2174 | 370.2632 | 258.48 | 136.2143 | 2.2165 | 1.9645 | 0.25019 | 1.5177 | 1.893 | 0.80416 | 1.1663 | 1.2754 | 1.6873 | 0.60767 | 0.026375 | 0.02856 | 0.0060578 | 0.018311 | 0.019304 | 0.011718 | 0.018362 | 0.021488 | 0.01954 | 0.011422
Waikato | 44 | 35 | 35 | 44 | 41 | 53 | 29 | 15 | 44 | 25 | 83.6542 | 92.5967 | 81.6459 | 88.0293 | 75.5032 | 74.2896 | 55.109 | 94.6031 | 59.6669 | 55.5019 | 118.6364 | 121.4286 | 157.9999 | 105.5455 | 146.8049 | 196.129 | 163.4828 | 146.0667 | 156.3864 | 108.2 | 1.4044 | 1.251 | 1.4268 | 1.284 | 1.4202 | 2.3973 | 0.80468 | 0.63311 | 1.2415 | 0.4496 | 0.016788 | 0.013511 | 0.017475 | 0.014586 | 0.01881 | 0.032269 | 0.014602 | 0.0066922 | 0.020806 | 0.0081006
Waikino | 26 | 18 | 10 | 12 | 10 | 6 | 13 | 8 | 6 | 2 | 86.9393 | 42.7361 | 89.7873 | 110.4112 | 72.2353 | 111.5004 | 55.7781 | 162.9046 | 32.749 | 55.0261 | 607.9231 | 282.7222 | 249.5999 | 188.25 | 259 | 688.0898 | 368.1538 | 210.75 | 380.3333 | 18.5 | 4.4194 | 0.69138 | 0.70819 | 0.78338 | 0.58468 | 1.429 | 0.82218 | 0.83892 | 0.22598 | 0.0060971 | 0.050833 | 0.016178 | 0.0078874 | 0.0070951 | 0.0080941 | 0.012817 | 0.01474 | 0.0051498 | 0.0069002 | 0.0001108
Wairarapa | 51 | 36 | 38 | 48 | 38 | 41 | 62 | 50 | 42 | 53 | 101.5815 | 62.2724 | 40.8975 | 74.6746 | 123.5003 | 126.0907 | 140.5228 | 129.8783 | 102.8651 | 77.2442 | 63.4902 | 73.2222 | 118.0526 | 100.2708 | 72.4211 | 96.477 | 119.9516 | 61.9 | 115.4762 | 99.7358 | 1.0578 | 0.52183 | 0.57976 | 1.1288 | 1.0621 | 1.5483 | 3.2186 | 1.2278 | 1.5085 | 1.2228 | 0.010414 | 0.0083798 | 0.014176 | 0.015117 | 0.0086003 | 0.01228 | 0.022905 | 0.0094534 | 0.014665 | 0.01583
Whanganui | 21 | 14 | 18 | 27 | 26 | 31 | 22 | 24 | 22 | 37 | 44.4112 | 52.358 | 73.8289 | 76.2035 | 76.7667 | 77.989 | 106.3745 | 140.5619 | 97.6941 | 66.03 | 280.0476 | 216.8571 | 293.5554 | 242.8148 | 172.1154 | 241.6504 | 409.9545 | 171.125 | 120.7273 | 279.8378 | 0.83997 | 0.50533 | 1.2328 | 1.5691 | 1.0736 | 1.8137 | 2.9548 | 1.7633 | 0.78459 | 2.0474 | 0.018914 | 0.0096514 | 0.016698 | 0.020591 | 0.013985 | 0.023255 | 0.027777 | 0.012545 | 0.0080311 | 0.031007
Conductor
Total | 202 | 141 | 214 | 269 | 312 | 151 | 233 | 236 | 259 | 273 | 95.1167 | 115.9301 | 131.5884 | 155.862 | 182.0604 | 142.2767 | 168.7129 | 168.1292 | 127.3446 | 117.316 | 215.8725 | 218.4639 | 239.1783 | 277.7164 | 197.5402 | 243.964 | 215.9926 | 257.7051 | 269.9266 | 217.0044 | 12.299 | 9.9913 | 16.2623 | 33.1632 | 35.7275 | 11.4779 | 29.309 | 25.7811 | 21.1722 | 19.9193 | 0.13589 | 0.086659 | 0.13739 | 0.21679 | 0.17496 | 0.10372 | 0.15194 | 0.18652 | 0.19429 | 0.18056
Non-zero Average | 15.5385 | 10.8462 | 16.4615 | 20.6923 | 24 | 11.6154 | 17.9231 | 19.6667 | 19.9231 | 21 | 95.1167 | 115.9301 | 131.5884 | 155.862 | 182.0604 | 142.2767 | 168.7129 | 182.1399 | 127.3446 | 117.316 | 215.8725 | 218.4639 | 239.1783 | 277.7164 | 197.5402 | 243.964 | 215.9926 | 279.1805 | 269.9266 | 217.0044 | 0.94607 | 0.76856 | 1.2509 | 2.551 | 2.7483 | 0.88292 | 2.2545 | 2.1484 | 1.6286 | 1.5323 | 0.010453 | 0.0066661 | 0.010568 | 0.016676 | 0.013458 | 0.0079788 | 0.011688 | 0.015543 | 0.014946 | 0.013889
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 7 | 8 | 13 | 14 | 6 | 11 | 14 | 17 | 11 | 9 | 70.4669 | 106.3224 | 185.3178 | 226.7258 | 52.5302 | 213.0961 | 187.323 | 108.7966 | 59.8149 | 102.0864 | 429 | 193.875 | 277.3845 | 217.6429 | 340.6667 | 240.7913 | 314.4286 | 464.3529 | 384.9091 | 187.5556 | 0.68055 | 0.52424 | 2.1117 | 2.1698 | 0.33555 | 1.7522 | 2.5396 | 2.6233 | 0.76579 | 0.51605 | 0.0096578 | 0.0049306 | 0.011395 | 0.0095701 | 0.0063878 | 0.0082226 | 0.013557 | 0.024112 | 0.012803 | 0.005055
Egmont | 27 | 24 | 37 | 19 | 69 | 25 | 36 | 37 | 35 | 49 | 128.6032 | 71.9233 | 101.4054 | 116.7242 | 319.4939 | 63.0839 | 141.7805 | 105.9774 | 121.5982 | 131.3112 | 132.8148 | 156.5417 | 108.081 | 161.2105 | 84.7536 | 320.8441 | 79.7222 | 196.9189 | 175.5429 | 122.3878 | 1.4831 | 0.85901 | 1.2815 | 1.1229 | 5.839 | 1.5708 | 1.2532 | 2.3585 | 2.2591 | 2.3582 | 0.011533 | 0.011943 | 0.012637 | 0.0096203 | 0.018276 | 0.024901 | 0.0088391 | 0.022255 | 0.018578 | 0.017959
Kinleith | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 0 | 1 | 2 | 50.2765 | 82.9329 | 191.3792 | 83.6962 | 111.7023 | 150.3881 | 82.9228 | 0 | 185.5844 | 160.5811 | 170 | 141.5 | 250.4999 | 335 | 76.5 | 258.9711 | 72 | 0 | 346 | 70 | 0.054975 | 0.074611 | 0.30299 | 0.088063 | 0.05341 | 0.36271 | 0.036776 | 0 | 0.19416 | 0.067325 | 0.0010935 | 0.00089966 | 0.0015832 | 0.0010522 | 0.00047814 | 0.0024118 | 0.0004435 | 0 | 0.0010462 | 0.00041926
Manawatu | 25 | 13 | 23 | 24 | 28 | 11 | 21 | 21 | 18 | 25 | 66.3882 | 76.8579 | 81.1512 | 86.4623 | 90.1125 | 89.4132 | 85.9465 | 85.863 | 62.8518 | 73.2141 | 421.6 | 107.1538 | 372.2172 | 408.2917 | 451.8929 | 409.3179 | 324.9048 | 472.7143 | 339.3889 | 407.72 | 2.2504 | 0.34035 | 2.1954 | 2.661 | 3.5632 | 1.2498 | 1.8061 | 2.6035 | 1.161 | 2.2348 | 0.033897 | 0.0044283 | 0.027053 | 0.030777 | 0.039542 | 0.013977 | 0.021014 | 0.030321 | 0.018472 | 0.030525
Mt Maunganui | 12 | 13 | 17 | 29 | 18 | 12 | 7 | 20 | 22 | 18 | 81.2806 | 113.8355 | 83.6005 | 187.5211 | 123.3231 | 110.7856 | 106.9444 | 241.4513 | 102.1894 | 70.8225 | 204 | 209.5385 | 312.1763 | 297.069 | 186 | 288.9677 | 57.2857 | 101 | 294.5 | 220.5556 | 0.63991 | 0.98577 | 1.402 | 5.074 | 1.2903 | 1.1926 | 0.13208 | 1.4897 | 2.002 | 0.842 | 0.0078729 | 0.0086596 | 0.01677 | 0.027058 | 0.010463 | 0.010765 | 0.001235 | 0.0061699 | 0.019591 | 0.011889
Rangitikei | 14 | 5 | 17 | 21 | 22 | 8 | 14 | 15 | 28 | 18 | 174.8615 | 102.5426 | 87.046 | 184.3156 | 222.5268 | 140.1511 | 268.5333 | 216.0096 | 172.4671 | 127.5543 | 62.9286 | 220.4 | 165.0587 | 165.9524 | 136.4545 | 66.6176 | 147.2143 | 194.4 | 158.9286 | 108.3889 | 0.49544 | 0.35923 | 0.77184 | 2.0175 | 2.0877 | 0.23187 | 1.7045 | 1.9239 | 2.3207 | 0.74525 | 0.0028333 | 0.0035033 | 0.008867 | 0.010946 | 0.0093816 | 0.0016544 | 0.0063476 | 0.0089067 | 0.013456 | 0.0058426
Taranaki | 27 | 11 | 28 | 33 | 57 | 21 | 32 | 25 | 37 | 44 | 72.3744 | 118.1641 | 94.3894 | 271.2948 | 380.3537 | 69.0504 | 204.8939 | 123.7321 | 93.6522 | 134.5792 | 148.0741 | 209.4545 | 240.9284 | 150.697 | 141.5088 | 136.4133 | 394.4062 | 313.4 | 236.5946 | 248.1818 | 0.93057 | 0.86548 | 2.0121 | 4.2374 | 9.5877 | 0.61407 | 7.9644 | 2.9611 | 2.479 | 4.401 | 0.012858 | 0.0073244 | 0.021318 | 0.015619 | 0.025207 | 0.008893 | 0.038871 | 0.023931 | 0.02647 | 0.032702
Tararua | 11 | 15 | 18 | 17 | 25 | 13 | 16 | 21 | 15 | 7 | 105.3296 | 203.9114 | 138.5805 | 142.0554 | 208.0033 | 271.4704 | 204.6367 | 496.0435 | 293.8161 | 210.0829 | 137.0909 | 57.2 | 36.9444 | 105.6471 | 152.6 | 50.0713 | 102.8125 | 95 | 135.0667 | 105.4286 | 0.51083 | 0.55618 | 0.29122 | 0.80132 | 2.4799 | 0.54857 | 1.0368 | 3.0227 | 1.8 | 0.4643 | 0.0048498 | 0.0027276 | 0.0021014 | 0.0056409 | 0.011922 | 0.0020207 | 0.0050663 | 0.0060936 | 0.0061261 | 0.0022101
Tauranga | 17 | 9 | 7 | 35 | 21 | 9 | 16 | 19 | 18 | 18 | 137.8103 | 84.0154 | 87.8785 | 108.3303 | 116.1431 | 103.3683 | 111.1326 | 102.8155 | 107.3548 | 110.281 | 261.3529 | 555 | 196.4285 | 513.2857 | 285.4286 | 492.1672 | 355.75 | 487.2632 | 430.7778 | 352.6667 | 1.9692 | 1.3341 | 0.38184 | 6.1125 | 2.1756 | 1.4214 | 1.9482 | 2.9074 | 2.5171 | 2.0965 | 0.014289 | 0.015879 | 0.004345 | 0.056425 | 0.018732 | 0.013751 | 0.01753 | 0.028278 | 0.023446 | 0.01901
Waikato | 11 | 9 | 15 | 15 | 7 | 9 | 2 | 15 | 19 | 8 | 52.7212 | 166.4408 | 74.565 | 114.7703 | 132.0655 | 48.6288 | 62.1567 | 176.9194 | 62.3162 | 58.6226 | 226.6364 | 160.5556 | 211.3332 | 270.4667 | 154.5714 | 180.7576 | 417 | 237.2667 | 309.3158 | 341 | 0.4227 | 0.76457 | 0.74694 | 1.4624 | 0.44656 | 0.24559 | 0.15966 | 1.9232 | 1.1074 | 0.47892 | 0.0080176 | 0.0045936 | 0.010017 | 0.012742 | 0.0033814 | 0.0050503 | 0.0025686 | 0.010871 | 0.017771 | 0.0081695
Waikino | 10 | 3 | 5 | 4 | 4 | 4 | 11 | 7 | 7 | 10 | 124.0398 | 86.1464 | 283.858 | 51.7044 | 85.0888 | 182.4497 | 80.9911 | 85.6695 | 181.406 | 98.2646 | 306.2 | 464.3333 | 740.5996 | 652 | 192 | 554.1881 | 247.7273 | 551.4286 | 258.8571 | 235.8 | 1.2215 | 0.38149 | 3.3216 | 0.42352 | 0.20422 | 1.2556 | 0.67972 | 1.0101 | 0.99393 | 0.69389 | 0.0098475 | 0.0044283 | 0.011702 | 0.0081913 | 0.0024001 | 0.0068816 | 0.0083926 | 0.01179 | 0.0054791 | 0.0070615
Wairarapa | 20 | 20 | 18 | 31 | 32 | 18 | 45 | 23 | 26 | 45 | 89.7523 | 197.9249 | 152.775 | 146.9833 | 152.2649 | 262.3203 | 394.5787 | 118.9623 | 67.702 | 132.0486 | 126.75 | 197.7 | 67.6666 | 123.9355 | 139.3125 | 42.4397 | 146.7111 | 104.6087 | 152.3462 | 193.4222 | 0.73172 | 2.4879 | 0.58802 | 1.7737 | 2.1213 | 0.62209 | 8.023 | 0.87425 | 0.81088 | 3.4419 | 0.0081527 | 0.01257 | 0.0038489 | 0.012067 | 0.013932 | 0.0023715 | 0.020333 | 0.0073489 | 0.011977 | 0.026066
Whanganui | 19 | 9 | 14 | 26 | 21 | 7 | 17 | 16 | 22 | 20 | 82.6126 | 96.074 | 148.7022 | 305.6227 | 373.1769 | 145.3917 | 261.4278 | 323.4392 | 144.7267 | 115.6593 | 179.8947 | 166.7778 | 129.9999 | 209.1154 | 226.3333 | 129.9855 | 147.9412 | 131.8125 | 286.8182 | 227.95 | 0.90811 | 0.45843 | 0.85522 | 5.219 | 5.5431 | 0.41068 | 2.025 | 2.0835 | 2.7614 | 1.5791 | 0.010992 | 0.0047717 | 0.0057512 | 0.017077 | 0.014854 | 0.0028247 | 0.0077458 | 0.0064418 | 0.01908 | 0.013653
Transformers
Total | 39 | 43 | 39 | 60 | 59 | 163 | 142 | 123 | 129 | 200 | 72.4562 | 225.2825 | 96.8192 | 154.9533 | 168.5814 | 139.2909 | 86.381 | 459.4227 | 277.1069 | 161.9058 | 174.5325 | 119.3786 | 89.3589 | 116.1293 | 236.8658 | 48.0476 | 33.3412 | 40.1735 | 37.0519 | 47.2515 | 2.1034 | 3.7463 | 1.2509 | 2.3298 | 4.818 | 2.5609 | 1.159 | 4.2522 | 4.0459 | 2.3464 | 0.020052 | 0.021169 | 0.016103 | 0.0186 | 0.029526 | 0.023147 | 0.014041 | 0.018498 | 0.020175 | 0.026758
Non-zero Average | 3.9 | 3.9091 | 3.5455 | 4.6154 | 4.5385 | 12.5385 | 11.8333 | 10.25 | 9.9231 | 15.3846 | 94.193 | 266.243 | 114.4227 | 154.9533 | 168.5814 | 139.2909 | 93.5795 | 497.7079 | 277.1069 | 161.9058 | 226.8923 | 141.0838 | 105.606 | 116.1293 | 236.8658 | 48.0476 | 36.1196 | 43.5213 | 37.0519 | 47.2515 | 0.21034 | 0.34058 | 0.11372 | 0.17921 | 0.37061 | 0.19699 | 0.096586 | 0.35435 | 0.31123 | 0.18049 | 0.0020052 | 0.0019244 | 0.001464 | 0.0014308 | 0.0022712 | 0.0017805 | 0.0011701 | 0.0015415 | 0.0015519 | 0.0020583
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 1 | 2 | 4 | 4 | 4 | 9 | 11 | 11 | 15 | 10 | 237 | 75.0089 | 64.2603 | 123.0095 | 108.7647 | 199.9583 | 51.0538 | 431.6978 | 607.9792 | 104.8417 | 9 | 392.5 | 467.7498 | 78.75 | 154 | 15.9982 | 23.6364 | 13.7273 | 5.6 | 133.8 | 0.0068598 | 0.18719 | 0.37993 | 0.1217 | 0.20938 | 0.089377 | 0.040882 | 0.19911 | 0.15442 | 0.42009 | 2.8944e-05 | 0.0024955 | 0.0059124 | 0.00098936 | 0.0019251 | 0.00044698 | 0.00080076 | 0.00046122 | 0.000254 | 0.0040069
Egmont | 6 | 9 | 8 | 17 | 8 | 31 | 36 | 30 | 23 | 52 | 102.4774 | 81.0479 | 65.5311 | 64.0681 | 152.4442 | 71.2895 | 109.0277 | 69.8086 | 38.8612 | 77.6366 | 66.3333 | 261.8889 | 168.7499 | 68.6471 | 58.75 | 54.7036 | 15.4722 | 74.6333 | 82.6522 | 28.2692 | 0.13117 | 0.60728 | 0.27956 | 0.23483 | 0.22391 | 0.3753 | 0.18703 | 0.47741 | 0.22338 | 0.34177 | 0.00128 | 0.0074929 | 0.004266 | 0.0036653 | 0.0014688 | 0.0052644 | 0.0017155 | 0.0068389 | 0.0057482 | 0.0044022
Kinleith | 1 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | 3 | 5 | 69.5508 | 40.2974 | 135.5968 | 48 | 71.9951 | 156 | 0 | 0 | 150.7846 | 71.4248 | 1298 | 417 | 62 | 58 | 588 | 49.9944 | 0 | 0 | 13.3333 | 138.4 | 0.29033 | 0.10684 | 0.053133 | 0.008744 | 0.1323 | 0.024211 | 0 | 0 | 0.018237 | 0.14802 | 0.0041744 | 0.0026513 | 0.00039184 | 0.00018217 | 0.0018376 | 0.0001552 | 0 | 0 | 0.00012095 | 0.0020723
Manawatu | 0 | 1 | 0 | 6 | 7 | 19 | 14 | 9 | 6 | 20 | 0 | 217 | 0 | 66.8428 | 52.8144 | 88.512 | 138.3582 | 2124.7578 | 82.25 | 83.5696 | 0 | 10 | 0 | 72 | 324.5714 | 73.4128 | 9.5714 | 1.8889 | 84.5 | 86.15 | 0 | 0.0068984 | 0 | 0.090695 | 0.375 | 0.38327 | 0.0571 | 0.11033 | 0.12609 | 0.43121 | 0 | 3.179e-05 | 0 | 0.0013568 | 0.0071003 | 0.0043301 | 0.0004127 | 5.1925e-05 | 0.001533 | 0.0051598
Mt Maunganui | 0 | 3 | 3 | 5 | 4 | 9 | 8 | 5 | 9 | 5 | 0 | 43 | 61.0285 | 220.9904 | 165.7291 | 87.9565 | 75.2354 | 345.6648 | 860.3312 | 329.8562 | 0 | 4.3333 | 105.3333 | 20.8 | 251.75 | 2.5553 | 38.125 | 3.6 | 5.2222 | 5.4 | 0 | 0.0017771 | 0.060941 | 0.072186 | 0.52155 | 0.0062794 | 0.070673 | 0.019005 | 0.12227 | 0.026671 | 0 | 4.1327e-05 | 0.00099857 | 0.00032665 | 0.003147 | 7.1393e-05 | 0.00093935 | 5.498e-05 | 0.00014212 | 8.0856e-05
Rangitikei | 4 | 1 | 1 | 1 | 2 | 12 | 5 | 5 | 4 | 8 | 92.8182 | 1289 | 110 | 101.0501 | 350.8928 | 51.1433 | 235 | 54.0804 | 240.4743 | 209.1743 | 145.75 | 99 | 2 | 301 | 566 | 51.1609 | 1.8 | 91.6 | 12.5 | 4.375 | 0.17403 | 0.40567 | 0.00069521 | 0.095532 | 1.2413 | 0.097473 | 0.0065139 | 0.075655 | 0.036357 | 0.021924 | 0.001875 | 0.00031472 | 6.3201e-06 | 0.00094539 | 0.0035376 | 0.0019059 | 2.7719e-05 | 0.0013989 | 0.00015119 | 0.00010481
Taranaki | 3 | 8 | 3 | 5 | 15 | 29 | 19 | 16 | 15 | 42 | 51.0667 | 71.0713 | 266.35 | 117.6158 | 89.216 | 129.713 | 89.0495 | 164.3191 | 73.3598 | 70.0778 | 25 | 177 | 6.6667 | 124.4 | 63.7333 | 21.9286 | 17.4737 | 27.1875 | 81.6 | 30.5238 | 0.012317 | 0.31992 | 0.016833 | 0.22977 | 0.26654 | 0.25607 | 0.091054 | 0.21833 | 0.27151 | 0.26904 | 0.0002412 | 0.0045015 | 6.3201e-05 | 0.0019536 | 0.0029876 | 0.0019742 | 0.0010225 | 0.0013287 | 0.0037011 | 0.0038392
Tararua | 0 | 0 | 3 | 1 | 2 | 7 | 5 | 3 | 8 | 14 | 0 | 0 | 35.2222 | 82 | 45.498 | 131.7826 | 85.1768 | 308.0692 | 160.906 | 185.8453 | 0 | 0 | 18 | 14 | 57 | 60.7075 | 47 | 53 | 1.75 | 22.1429 | 0 | 0 | 0.0060104 | 0.0036057 | 0.016209 | 0.17385 | 0.061648 | 0.14961 | 0.0068116 | 0.17253 | 0 | 0 | 0.00017064 | 4.3972e-05 | 0.00035626 | 0.0013192 | 0.00072376 | 0.00048565 | 4.2333e-05 | 0.00092835
Tauranga | 7 | 5 | 4 | 8 | 2 | 10 | 10 | 13 | 13 | 13 | 97.7378 | 160.9121 | 331.8397 | 78.5988 | 138.794 | 401.8376 | 73.0551 | 1231.5046 | 113.5442 | 249.7589 | 228.8571 | 61.4 | 32.75 | 104.75 | 150.5 | 43.0952 | 186.8 | 33.7692 | 53.9231 | 6.7692 | 0.50356 | 0.15704 | 0.13737 | 0.20687 | 0.13056 | 0.53759 | 0.4203 | 1.6513 | 0.24067 | 0.06582 | 0.0051521 | 0.00097595 | 0.00041396 | 0.002632 | 0.00094066 | 0.0013378 | 0.0057531 | 0.0013409 | 0.0021197 | 0.00026353
Waikato | 8 | 10 | 6 | 4 | 5 | 15 | 11 | 5 | 18 | 8 | 153.8336 | 775.335 | 33.1538 | 467.4603 | 254.1896 | 189.6915 | 43.3154 | 636.7865 | 459.1446 | 210.5351 | 214.125 | 78.8 | 60.6666 | 126 | 137.2 | 33.063 | 11.8182 | 4.2 | 107.4444 | 14.125 | 0.84748 | 1.9423 | 0.038135 | 0.73998 | 0.54494 | 0.29205 | 0.017343 | 0.040845 | 2.6851 | 0.071245 | 0.0055091 | 0.002505 | 0.0011502 | 0.001583 | 0.0021438 | 0.0015396 | 0.00040038 | 6.4143e-05 | 0.005848 | 0.0003384
Waikino | 1 | 1 | 1 | 3 | 1 | 2 | 6 | 4 | 5 | 1 | 2 | 110 | 52 | 465.3061 | 102.5831 | 48 | 50.3211 | 72.3333 | 328.6627 | 369.2167 | 161 | 7 | 29 | 16.3333 | 535 | 6.4993 | 36.3333 | 3 | 24.4 | 1 | 0.0010356 | 0.0024478 | 0.0047653 | 0.071611 | 0.17151 | 0.0019369 | 0.033786 | 0.0026512 | 0.12124 | 0.0011057 | 0.00051778 | 2.2253e-05 | 9.1641e-05 | 0.0001539 | 0.0016719 | 4.0352e-05 | 0.00067141 | 3.6653e-05 | 0.0003689 | 2.9947e-06
Wairarapa | 7 | 1 | 4 | 3 | 4 | 12 | 14 | 13 | 6 | 15 | 131.4455 | 66 | 103.6671 | 96.2563 | 222.5179 | 198.8783 | 113.2723 | 397.0327 | 293.7034 | 66.4492 | 45.8571 | 43 | 208.7499 | 468 | 24.75 | 10.6655 | 34.0714 | 41.5385 | 6.5 | 106.6 | 0.1357 | 0.009022 | 0.27354 | 0.42446 | 0.068844 | 0.079017 | 0.16641 | 0.65486 | 0.034635 | 0.31819 | 0.0010324 | 0.0001367 | 0.0026386 | 0.0044097 | 0.00030939 | 0.00039732 | 0.0014691 | 0.0016494 | 0.00011793 | 0.0047885
Whanganui | 1 | 0 | 0 | 2 | 4 | 7 | 3 | 9 | 4 | 7 | 4 | 0 | 0 | 83.194 | 436.1196 | 56.0196 | 60.0882 | 136.4403 | 192.3889 | 76.3887 | 75 | 0 | 0 | 57 | 168 | 200.8347 | 11.3333 | 174.1111 | 2.25 | 36.7143 | 0.00096481 | 0 | 0 | 0.029788 | 0.91589 | 0.24448 | 0.0062921 | 0.65304 | 0.0052356 | 0.058791 | 0.0002412 | 0 | 0 | 0.00035805 | 0.0021001 | 0.0043643 | 0.00010471 | 0.0047863 | 2.7214e-05 | 0.00076963
Fuses
Total | 65 | 88 | 89 | 96 | 78 | 103 | 101 | 461 | 662 | 755 | 57.587 | 34.0723 | 55.034 | 63.5955 | 56.9518 | 55.5214 | 106.2104 | 188.3029 | 130.169 | 105.1315 | 140.7374 | 83.3233 | 82.7927 | 90.0016 | 123.337 | 73.8385 | 63.5098 | 30.4765 | 21.5464 | 20.3266 | 1.3304 | 1.0693 | 1.1135 | 1.9544 | 1.553 | 1.2722 | 1.4249 | 5.563 | 5.5067 | 5.3584 | 0.02303 | 0.02644 | 0.022474 | 0.030962 | 0.027939 | 0.025841 | 0.025815 | 0.042817 | 0.044235 | 0.047175
Non-zero Average | 5.4167 | 7.3333 | 6.8462 | 7.3846 | 6 | 8.5833 | 8.4167 | 35.4615 | 50.9231 | 58.0769 | 62.3859 | 36.9117 | 55.034 | 63.5955 | 56.9518 | 60.1482 | 115.0613 | 188.3029 | 130.169 | 105.1315 | 152.4655 | 90.2669 | 82.7927 | 90.0016 | 123.337 | 79.9917 | 68.8023 | 30.4765 | 21.5464 | 20.3266 | 0.11087 | 0.089106 | 0.08565 | 0.15034 | 0.11946 | 0.10602 | 0.11874 | 0.42792 | 0.42359 | 0.41219 | 0.0019192 | 0.0022033 | 0.0017288 | 0.0023817 | 0.0021491 | 0.0021534 | 0.0021513 | 0.0032936 | 0.0034027 | 0.0036289
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 4 | 4 | 6 | 3 | 2 | 5 | 8 | 32 | 45 | 49 | 37.7553 | 53.8333 | 49.8045 | 75.1197 | 13.5413 | 83.7655 | 40.6824 | 99.2147 | 274.3799 | 106.9275 | 47 | 51 | 66.5 | 47.3333 | 490.5 | 70.7921 | 82.25 | 57.5312 | 33.8444 | 18.9796 | 0.022827 | 0.034912 | 0.062796 | 0.033503 | 0.041514 | 0.092044 | 0.082444 | 0.5579 | 1.2636 | 0.2978 | 0.00060462 | 0.00064851 | 0.0012609 | 0.000446 | 0.0030657 | 0.0010988 | 0.0020265 | 0.0056232 | 0.0046052 | 0.0027851
Egmont | 5 | 8 | 15 | 18 | 10 | 17 | 20 | 66 | 64 | 86 | 45.7266 | 44.0049 | 49.1918 | 117.1601 | 58.7367 | 29.5046 | 79.0041 | 100.269 | 75.9466 | 169.6673 | 55.6 | 25.625 | 35.8 | 45.6111 | 152.2 | 140.102 | 31.6 | 28.0606 | 37.8125 | 9.6512 | 0.040882 | 0.028678 | 0.083475 | 0.30211 | 0.27938 | 0.21815 | 0.15378 | 0.5672 | 0.55574 | 0.42172 | 0.00089406 | 0.00065169 | 0.0016969 | 0.0025786 | 0.0047564 | 0.0073938 | 0.0019465 | 0.0056568 | 0.0073175 | 0.0024856
Kinleith | 0 | 0 | 1 | 4 | 3 | 3 | 0 | 5 | 3 | 5 | 0 | 0 | 57 | 51.2265 | 91.6249 | 52.7752 | 0 | 85.2877 | 54.2052 | 52.2614 | 0 | 0 | 18 | 178.75 | 133 | 42.9952 | 0 | 3.8 | 15 | 10.2 | 0 | 0 | 0.0032422 | 0.11504 | 0.11425 | 0.021132 | 0 | 0.0049496 | 0.0073757 | 0.0079818 | 0 | 0 | 5.688e-05 | 0.0022457 | 0.0012469 | 0.00040042 | 0 | 5.8034e-05 | 0.00013607 | 0.00015273
Manawatu | 7 | 5 | 7 | 18 | 11 | 12 | 6 | 38 | 42 | 64 | 60.236 | 41.661 | 54.6145 | 48.9801 | 52.4571 | 55.8541 | 49.0152 | 235.1365 | 45.1012 | 152.7386 | 81.7143 | 221.8 | 173.4285 | 122.0556 | 124.9091 | 47.4114 | 186.6667 | 32.8421 | 44.881 | 24.3438 | 0.11081 | 0.14688 | 0.20952 | 0.33798 | 0.22525 | 0.098649 | 0.16907 | 0.89632 | 0.25707 | 0.71264 | 0.0018396 | 0.0035255 | 0.0038363 | 0.0069004 | 0.0042939 | 0.0017662 | 0.0034494 | 0.0038119 | 0.0056998 | 0.0046657
Mt Maunganui | 6 | 4 | 3 | 3 | 7 | 0 | 7 | 13 | 27 | 24 | 42.4615 | 25.4074 | 50.6882 | 57.5132 | 78.5747 | 0 | 16.8797 | 29.4133 | 86.9074 | 57.0315 | 28.1667 | 20.25 | 62 | 25.3333 | 101.5714 | 0 | 19 | 8.7692 | 28.7407 | 11.5417 | 0.023078 | 0.0065424 | 0.029793 | 0.013729 | 0.17459 | 0 | 0.0069142 | 0.010242 | 0.20392 | 0.047309 | 0.00054351 | 0.0002575 | 0.00058776 | 0.0002387 | 0.002222 | 0 | 0.00040962 | 0.0003482 | 0.0023464 | 0.00082953
Rangitikei | 6 | 5 | 2 | 3 | 6 | 9 | 6 | 55 | 63 | 64 | 40.1039 | 37.9202 | 34.2358 | 117.7917 | 123.2022 | 62.9182 | 87.1338 | 133.2561 | 235.0806 | 147.9554 | 64.1667 | 47.6 | 53 | 32 | 117 | 65.2149 | 104.5 | 6.9091 | 9.4762 | 31.7812 | 0.049656 | 0.02869 | 0.011468 | 0.035516 | 0.27029 | 0.11464 | 0.16826 | 0.15467 | 0.42436 | 0.90122 | 0.0012382 | 0.0007566 | 0.00033496 | 0.00030152 | 0.0021938 | 0.0018221 | 0.0019311 | 0.0011607 | 0.0018052 | 0.0060912
Taranaki | 14 | 23 | 21 | 19 | 12 | 26 | 20 | 69 | 95 | 132 | 41.3321 | 63.2466 | 46.6167 | 99.5134 | 45.6469 | 66.2834 | 46.7883 | 205.7519 | 174.1723 | 106.2865 | 116.5714 | 85.6957 | 76.9047 | 130.7368 | 121.5833 | 58.4935 | 169.75 | 10.971 | 18.5263 | 24.6818 | 0.21694 | 0.39629 | 0.23791 | 0.77638 | 0.20813 | 0.31294 | 0.48922 | 0.47574 | 0.92691 | 1.037 | 0.0052486 | 0.0062658 | 0.0051034 | 0.0078018 | 0.0045596 | 0.0047212 | 0.010456 | 0.0023122 | 0.0053218 | 0.0097567
Tararua | 3 | 5 | 8 | 1 | 6 | 7 | 2 | 30 | 36 | 67 | 71.8871 | 30.311 | 49.5344 | 34 | 26.4846 | 35.9167 | 32.5357 | 193.371 | 191.6386 | 119.4883 | 41.3333 | 32.8 | 49.125 | 35 | 41.1667 | 104.5597 | 28 | 7.1 | 9.7222 | 20.806 | 0.028668 | 0.015803 | 0.061516 | 0.0037376 | 0.020444 | 0.081608 | 0.0056115 | 0.12581 | 0.20281 | 0.49881 | 0.00039879 | 0.00052135 | 0.0012419 | 0.00010993 | 0.00077191 | 0.0022721 | 0.00017247 | 0.00065059 | 0.0010583 | 0.0041746
Tauranga | 5 | 9 | 6 | 15 | 7 | 8 | 15 | 27 | 73 | 40 | 17.1326 | 30.4957 | 38.2249 | 19.7696 | 43.944 | 43.9951 | 46.6956 | 93.6187 | 85.6449 | 71.0696 | 229.2 | 206.6667 | 117.8333 | 136.8667 | 55 | 180.8548 | 81.4667 | 37.8148 | 30.3014 | 54.325 | 0.063144 | 0.18032 | 0.0854 | 0.12748 | 0.052872 | 0.19761 | 0.17574 | 0.29196 | 0.57284 | 0.46248 | 0.0036856 | 0.0059129 | 0.0022341 | 0.0064481 | 0.0012032 | 0.0044915 | 0.0037636 | 0.0031186 | 0.0066886 | 0.0065074
Waikato | 9 | 11 | 7 | 3 | 4 | 5 | 1 | 21 | 53 | 23 | 47.5571 | 33.541 | 46.02 | 67.7109 | 61.6319 | 70.0058 | 26 | 108.374 | 119.4951 | 55.9899 | 148 | 103.1818 | 35.7143 | 213.6667 | 92.75 | 34.5961 | 38 | 7.1905 | 10.3396 | 10.6957 | 0.20372 | 0.12102 | 0.036356 | 0.13632 | 0.071457 | 0.037593 | 0.0030429 | 0.049984 | 0.19801 | 0.041247 | 0.0042838 | 0.0036082 | 0.00079001 | 0.0020133 | 0.0011594 | 0.000537 | 0.00011703 | 0.00046122 | 0.001657 | 0.00073669
Waikino | 1 | 4 | 4 | 2 | 2 | 1 | 3 | 9 | 26 | 31 | 187.5006 | 23.609 | 43.4663 | 19 | 74.3858 | 73 | 828.8274 | 61.7663 | 125.9573 | 118.1279 | 851 | 133 | 170.4999 | 144.5 | 14.5 | 171.9808 | 10.6667 | 98.7778 | 8.1154 | 15.6452 | 0.51316 | 0.039928 | 0.093676 | 0.017246 | 0.0067415 | 0.038974 | 0.081685 | 0.16772 | 0.080362 | 0.17157 | 0.0027369 | 0.0016912 | 0.0021551 | 0.0009077 | 9.0629e-05 | 0.00053389 | 9.8555e-05 | 0.0027154 | 0.00063801 | 0.0014524
Wairarapa | 3 | 6 | 8 | 6 | 5 | 7 | 11 | 60 | 74 | 100 | 30.3925 | 23.8109 | 53.0444 | 56.9568 | 37.4031 | 73.0175 | 60.7785 | 67.485 | 127.3705 | 125.1857 | 150.3333 | 97.8333 | 112.4999 | 50.1667 | 141.2 | 32.5678 | 35.7273 | 85.9 | 20.6216 | 10.18 | 0.044082 | 0.044433 | 0.15086 | 0.053846 | 0.082524 | 0.051676 | 0.073565 | 1.0624 | 0.58772 | 0.38164 | 0.0014504 | 0.0018661 | 0.002844 | 0.00094539 | 0.0022063 | 0.00070772 | 0.0012104 | 0.015742 | 0.0046143 | 0.0030486
Whanganui | 2 | 4 | 1 | 1 | 3 | 3 | 2 | 36 | 61 | 70 | 126.5455 | 35.0996 | 143 | 62 | 32.7403 | 74.7419 | 66.3947 | 1034.9932 | 96.2977 | 83.979 | 16.5 | 57.75 | 104.9999 | 8 | 18 | 10.3322 | 38 | 10.5278 | 12.7213 | 21.4143 | 0.01343 | 0.025775 | 0.047448 | 0.0015578 | 0.0055252 | 0.007192 | 0.015541 | 1.1981 | 0.22596 | 0.37698 | 0.00010613 | 0.00073435 | 0.0003318 | 2.5127e-05 | 0.00016876 | 9.6225e-05 | 0.00023407 | 0.0011576 | 0.0023464 | 0.004489
Sub-Trans
Total | 26 | 32 | 29 | 23 | 22 | 25 | 28 | 10 | 21 | 21 | 88.0914 | 54.3278 | 124.3356 | 72.8943 | 42.9945 | 40.9787 | 79.9598 | 30.08 | 89.0464 | 81.9592 | 1669.2679 | 1662.9449 | 1368.0485 | 1931.9121 | 1544.8483 | 1421.8719 | 1443.3004 | 908.9615 | 1836.9487 | 1366.5397 | 19.8775 | 13.4269 | 23.903 | 12.7745 | 6.769 | 10.2634 | 17.4055 | 2.5378 | 11.8489 | 11.6565 | 0.15325 | 0.24777 | 0.21106 | 0.13725 | 0.11189 | 0.15451 | 0.19333 | 0.055395 | 0.10157 | 0.1258
Non-zero Average | 2.6 | 3.2 | 2.9 | 2.3 | 2.4444 | 2.5 | 2.5455 | 1.6667 | 1.9091 | 2.3333 | 114.5188 | 70.6262 | 161.6363 | 94.7626 | 62.1032 | 53.2724 | 94.498 | 65.1733 | 105.2366 | 118.3855 | 2170.0483 | 2161.8283 | 1778.4631 | 2511.4857 | 2231.4475 | 1848.4334 | 1705.7186 | 1969.4167 | 2170.9394 | 1973.8907 | 1.9878 | 1.3427 | 2.3903 | 1.2774 | 0.75211 | 1.0263 | 1.5823 | 0.42297 | 1.0772 | 1.2952 | 0.015325 | 0.024777 | 0.021106 | 0.013725 | 0.012432 | 0.015451 | 0.017576 | 0.0092325 | 0.009234 | 0.013978
GXP | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 4 | 6 | 7 | 0 | 1 | 4 | 1 | 1 | 0 | 2 | 52.2089 | 14.7966 | 131.8452 | 0 | 142.9987 | 54.281 | 339.1338 | 157 | 0 | 77.4522 | 3936.75 | 4402.3333 | 6004.854 | 0 | 2327 | 4553.9911 | 2651 | 1 | 0 | 2404 | 2.644 | 1.2425 | 17.5128 | 0 | 1.0399 | 3.0695 | 2.7689 | 0.00047954 | 0 | 1.1152 | 0.050643 | 0.08397 | 0.13283 | 0 | 0.0072722 | 0.056549 | 0.0081647 | 3.0544e-06 | 0 | 0.014398
Egmont | 1 | 1 | 2 | 0 | 1 | 1 | 2 | 0 | 2 | 1 | 25 | 171.9367 | 65.4964 | 0 | 41.3861 | 36.0583 | 121.1343 | 0 | 90.9777 | 402.9907 | 1384 | 537 | 1463.4992 | 0 | 1452 | 592.9337 | 1456.5 | 0 | 903 | 1730 | 0.11128 | 0.29352 | 0.6058 | 0 | 0.1878 | 0.066372 | 1.0868 | 0 | 0.49682 | 2.0878 | 0.004451 | 0.0017071 | 0.0092494 | 0 | 0.0045377 | 0.0018407 | 0.0089716 | 0 | 0.0054609 | 0.0051808
Kinleith | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 148.7415 | 0 | 0 | 0 | 0 | 60.0418 | 163.2327 | 0 | 0 | 0 | 2787 | 0 | 0 | 0 | 0 | 3358 | 3400 | 0 | 0 | 0 | 1.302 | 0 | 0 | 0 | 0 | 1.2193 | 3.324 | 0 | 0 | 0 | 0.0087535 | 0 | 0 | 0 | 0 | 0.020308 | 0.020364
Manawatu | 3 | 3 | 1 | 1 | 2 | 2 | 2 | 0 | 4 | 5 | 55.1657 | 12.6278 | 863 | 2 | 1.2441 | 61.8376 | 53.8718 | 0 | 96.3074 | 104.3371 | 1885.3333 | 3454 | 1 | 5781 | 2917.5 | 2950.6702 | 1205.5 | 0 | 535 | 1393.6 | 1.0035 | 0.41597 | 0.0027271 | 0.036314 | 0.022687 | 1.1329 | 0.40003 | 0 | 0.62319 | 2.1772 | 0.01819 | 0.032941 | 3.16e-06 | 0.018157 | 0.018235 | 0.01832 | 0.0074255 | 0 | 0.0064708 | 0.020867
Mt Maunganui | 1 | 0 | 4 | 7 | 0 | 0 | 2 | 1 | 1 | 1 | 32.5092 | 0 | 169.0367 | 135.2252 | 0 | 0 | 18.7863 | 49.0438 | 271.5902 | 75.0101 | 5546 | 0 | 954.7495 | 1540.8571 | 0 | 0 | 1531.5 | 3698 | 4799 | 338 | 0.57984 | 0 | 2.04 | 4.581 | 0 | 0 | 0.17722 | 0.55396 | 3.9411 | 0.075925 | 0.017836 | 0 | 0.012068 | 0.033877 | 0 | 0 | 0.0094336 | 0.011295 | 0.014511 | 0.0010122
Rangitikei | 1 | 2 | 2 | 1 | 2 | 5 | 0 | 2 | 2 | 0 | 30.8325 | 94 | 69.4451 | 4.6563 | 71.0422 | 202.7609 | 0 | 82.2373 | 16.3976 | 0 | 800 | 816 | 891.9995 | 856 | 1705 | 1148.2717 | 0 | 1563.5 | 1643.5 | 0 | 0.079327 | 0.48768 | 0.3915 | 0.012519 | 0.75707 | 3.6139 | 0 | 0.78546 | 0.16298 | 0 | 0.0025728 | 0.0051881 | 0.0056375 | 0.0026885 | 0.010657 | 0.017823 | 0 | 0.0095512 | 0.0099391 | 0
Taranaki | 1 | 0 | 3 | 2 | 9 | 4 | 6 | 3 | 2 | 2 | 18 | 0 | 25.2548 | 126.8762 | 111.84 | 10.3061 | 55.389 | 42.3933 | 122.591 | 45.5622 | 136 | 0 | 761.3329 | 505 | 804.7778 | 737.4176 | 539.6667 | 1028 | 1301 | 3322.5 | 0.0078729 | 0 | 0.18228 | 0.40248 | 2.5315 | 0.094372 | 0.55237 | 0.39934 | 0.96452 | 0.90667 | 0.00043738 | 0 | 0.0072175 | 0.0031722 | 0.022635 | 0.0091569 | 0.0099725 | 0.0094198 | 0.0078678 | 0.0199
Tararua | 5 | 3 | 3 | 2 | 1 | 1 | 1 | 1 | 3 | 4 | 40.1991 | 61.4404 | 78.6857 | 40.102 | 73.9942 | 0.99684 | 204 | 25.0669 | 19.5973 | 135.2077 | 314.4 | 464 | 630.9997 | 152 | 500 | 632.9293 | 632 | 2826 | 313.3333 | 537.25 | 0.20323 | 0.27188 | 0.47069 | 0.03829 | 0.11562 | 0.0019586 | 0.39708 | 0.21637 | 0.055702 | 0.87014 | 0.0050556 | 0.0044252 | 0.0059819 | 0.00095481 | 0.0015626 | 0.0019648 | 0.0019465 | 0.0086318 | 0.0028423 | 0.0064356
Tauranga | 0 | 5 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 60.52 | 0 | 34.3024 | 34.9827 | 49.5191 | 21.5672 | 0 | 0 | 0 | 0 | 4046.6 | 0 | 5731 | 5724 | 5683.8648 | 1212 | 0 | 0 | 0 | 0 | 3.8927 | 0 | 0.61744 | 0.62578 | 1.7475 | 0.080505 | 0 | 0 | 0 | 0 | 0.064321 | 0 | 0.018 | 0.017888 | 0.03529 | 0.0037328 | 0 | 0 | 0
Waikato | 6 | 1 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 41.5732 | 12 | 56.5054 | 0 | 0 | 19.4704 | 14.2288 | 0 | 28.101 | 32.6665 | 1568 | 1192 | 2870.9985 | 0 | 0 | 411.454 | 1328 | 0 | 2067 | 674 | 1.2579 | 0.045472 | 0.51264 | 0 | 0 | 0.049739 | 0.058196 | 0 | 0.17563 | 0.065935 | 0.030257 | 0.0037894 | 0.0090724 | 0 | 0 | 0.0025546 | 0.00409 | 0 | 0.0062501 | 0.0020184
Waikino | 1 | 2 | 0 | 2 | 0 | 0 | 7 | 0 | 1 | 0 | 761.0268 | 167.0645 | 0 | 67.4135 | 0 | 0 | 90.2558 | 0 | 210.266 | 0 | 5494 | 5547 | 0 | 4421 | 0 | 0 | 5643.5714 | 0 | 5688 | 0 | 13.4465 | 5.892 | 0 | 1.8721 | 0 | 0 | 10.9813 | 0 | 3.6164 | 0 | 0.017669 | 0.035268 | 0 | 0.027771 | 0 | 0 | 0.12167 | 0 | 0.017199 | 0
Wairarapa | 3 | 5 | 5 | 5 | 4 | 2 | 3 | 2 | 2 | 3 | 88.6724 | 65.2998 | 69.4572 | 118.6687 | 71.9574 | 41.6289 | 96.2634 | 35.2983 | 215.7995 | 29.01 | 636 | 445.6 | 1243.1993 | 1065 | 1552.75 | 1444.8385 | 693.6667 | 2700 | 274.5 | 3965.6667 | 0.54411 | 0.46251 | 1.3643 | 1.9847 | 1.3967 | 0.37344 | 0.61697 | 0.58221 | 0.35824 | 1.0336 | 0.0061362 | 0.0070828 | 0.019643 | 0.016725 | 0.01941 | 0.0089706 | 0.0064092 | 0.016494 | 0.00166 | 0.035628
Whanganui | 0 | 4 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 0 | 46.5762 | 87.6364 | 269.6401 | 9.483 | 55.8642 | 24.8473 | 0 | 25.9335 | 0 | 0 | 713.75 | 2961.9984 | 2276 | 3100 | 327.9633 | 1869.5 | 0 | 2998 | 0 | 0 | 0.42273 | 0.82028 | 1.9275 | 0.09187 | 0.11375 | 0.28613 | 0 | 0.23509 | 0 | 0 | 0.009076 | 0.00936 | 0.0071485 | 0.0096879 | 0.0020362 | 0.011516 | 0 | 0.0090652 | 0
The rest
Total | 81 | 109 | 124 | 111 | 93 | 83 | 126 | 110 | 102 | 118 | 85.1162 | 128.5941 | 66.9699 | 70.7556 | 120.6445 | 86.7437 | 87.2255 | 209.6436 | 66.0495 | 56.1633 | 333.5974 | 393.5099 | 374.484 | 648.7332 | 427.2109 | 525.9394 | 346.7214 | 396.6162 | 358.6819 | 734.1962 | 9.1498 | 15.6301 | 10.7536 | 10.0579 | 11.2957 | 9.554 | 11.0704 | 21.5421 | 7.7417 | 12.8168 | 0.10943 | 0.16928 | 0.16869 | 0.16981 | 0.13722 | 0.14464 | 0.1569 | 0.15277 | 0.11386 | 0.25289
Non-zero Average | 6.2308 | 8.3846 | 9.5385 | 8.5385 | 7.1538 | 6.3846 | 10.5 | 8.4615 | 8.5 | 9.0769 | 85.1162 | 128.5941 | 66.9699 | 70.7556 | 120.6445 | 86.7437 | 94.4943 | 209.6436 | 71.5536 | 56.1633 | 333.5974 | 393.5099 | 374.484 | 648.7332 | 427.2109 | 525.9394 | 375.6148 | 396.6162 | 388.572 | 734.1962 | 0.70383 | 1.2023 | 0.8272 | 0.77368 | 0.8689 | 0.73492 | 0.92254 | 1.6571 | 0.64514 | 0.98591 | 0.0084176 | 0.013022 | 0.012976 | 0.013062 | 0.010555 | 0.011127 | 0.013075 | 0.011752 | 0.0094883 | 0.019453
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 5 | 11 | 8 | 9 | 5 | 4 | 9 | 13 | 3 | 7 | 322.7002 | 121.8442 | 78.441 | 122.8858 | 94.184 | 29.8699 | 55.8801 | 182.9413 | 39.2152 | 66.6486 | 338.2 | 689.8182 | 327.1248 | 670.4444 | 498.8 | 2348.7375 | 108.1111 | 893.7503 | 551.2125 | 193.2857 | 1.755 | 2.9392 | 0.64869 | 2.3289 | 0.73408 | 0.87117 | 0.16746 | 6.4923 | 0.19608 | 0.27005 | 0.0054383 | 0.024122 | 0.0082698 | 0.018952 | 0.0077941 | 0.029165 | 0.0029967 | 0.035489 | 0.0050002 | 0.0040518
Egmont | 2 | 5 | 6 | 7 | 4 | 2 | 17 | 10 | 11 | 11 | 13.5203 | 53.0506 | 108.0134 | 27.359 | 54.3449 | 152.1719 | 86.9331 | 181.731 | 58.1505 | 109.524 | 148 | 474 | 173.6666 | 296.8571 | 500.5 | 843.4057 | 397.1765 | 244.5441 | 182.5575 | 277.5455 | 0.012871 | 0.39969 | 0.35566 | 0.17856 | 0.34001 | 0.79685 | 1.8078 | 1.3574 | 0.3531 | 1.0014 | 0.00095195 | 0.0075342 | 0.0032927 | 0.0065266 | 0.0062565 | 0.0052365 | 0.020795 | 0.0074694 | 0.0060721 | 0.0091428
Kinleith | 4 | 1 | 5 | 2 | 1 | 3 | 5 | 2 | 2 | 8 | 70.7323 | 57.462 | 91.599 | 146.1197 | 51.2243 | 43.5447 | 111.1768 | 136.3325 | 116.0124 | 67.0068 | 412.75 | 868 | 486.7997 | 808.5 | 541 | 171.6475 | 497.6 | 787.1627 | 412.4023 | 699.875 | 0.37557 | 0.15856 | 0.70453 | 0.7421 | 0.086605 | 0.069609 | 0.85191 | 0.65558 | 0.28934 | 1.1235 | 0.0053097 | 0.0027594 | 0.0076915 | 0.0050787 | 0.0016907 | 0.0015986 | 0.0076626 | 0.0048087 | 0.002494 | 0.016767
Manawatu | 16 | 24 | 34 | 20 | 27 | 21 | 21 | 18 | 12 | 13 | 75.9054 | 82.6892 | 71.4461 | 62.4891 | 82.8186 | 49.3789 | 57.1326 | 110.9853 | 54.6266 | 50.4719 | 583.3125 | 1005.6667 | 587.7056 | 482.75 | 586.9259 | 741.2981 | 774.1905 | 797.7838 | 820.2727 | 1582.3846 | 2.2783 | 6.3446 | 4.5114 | 1.895 | 4.1015 | 2.3863 | 2.8607 | 4.868 | 1.6259 | 3.1093 | 0.030015 | 0.076728 | 0.063144 | 0.030325 | 0.049524 | 0.048327 | 0.050072 | 0.043862 | 0.029764 | 0.061604
Mt Maunganui | 3 | 4 | 7 | 10 | 5 | 5 | 11 | 6 | 4 | 13 | 18.4917 | 769.5349 | 33.7045 | 58.6355 | 83.412 | 27.9835 | 211.4483 | 631.3924 | 104.9894 | 52.303 | 480.6667 | 10.75 | 270.2856 | 327.5 | 110.2 | 95.3893 | 50.6364 | 46.2711 | 162.6446 | 322.4615 | 0.085756 | 0.10519 | 0.20151 | 0.60314 | 0.14363 | 0.041433 | 0.36273 | 0.53541 | 0.20653 | 0.6566 | 0.0046375 | 0.0001367 | 0.0059788 | 0.010286 | 0.0017219 | 0.0014806 | 0.0017155 | 0.00084799 | 0.0019672 | 0.012554
Rangitikei | 4 | 5 | 3 | 1 | 2 | 1 | 4 | 5 | 4 | 3 | 61.0699 | 142.8149 | 54.703 | 81.7107 | 88.7633 | 204 | 92.2055 | 282.5768 | 19.7313 | 41.7819 | 275.5 | 61.6 | 329.9998 | 1114 | 666 | 201.9774 | 386 | 152.6115 | 308.9241 | 1007.3333 | 0.21644 | 0.13983 | 0.17113 | 0.2859 | 0.36949 | 0.12791 | 0.43846 | 0.6586 | 0.073725 | 0.37812 | 0.0035441 | 0.00097913 | 0.0031284 | 0.0034989 | 0.0041627 | 0.00062701 | 0.0047553 | 0.0023307 | 0.0037364 | 0.0090499
Taranaki | 13 | 11 | 17 | 6 | 8 | 9 | 13 | 12 | 21 | 14 | 64.0309 | 82.4327 | 61.1774 | 60.8481 | 68.062 | 35.7061 | 46.198 | 171.075 | 65.4063 | 38.7435 | 471.1538 | 216.8182 | 318.941 | 405.6667 | 506.375 | 355.1825 | 461.7692 | 347.1717 | 213.0709 | 355.0714 | 1.2613 | 0.625 | 1.0482 | 0.46517 | 0.86166 | 0.35433 | 0.85412 | 2.1769 | 0.88493 | 0.57676 | 0.019698 | 0.0075819 | 0.017134 | 0.0076448 | 0.01266 | 0.0099236 | 0.018488 | 0.012725 | 0.01353 | 0.014887
Tararua | 2 | 1 | 3 | 1 | 1 | 1 | 0 | 1 | 0 | 3 | 58.4505 | 30 | 44.3257 | 125 | 651.7408 | 62 | 0 | 264.6386 | 0 | 81.9022 | 111 | 25 | 174.9999 | 8 | 115 | 19.9978 | 0 | 3.3249 | 0 | 77.6667 | 0.041731 | 0.0023842 | 0.073537 | 0.0031408 | 0.23423 | 0.003849 | 0 | 0.0026876 | 0 | 0.057148 | 0.00071396 | 7.9475e-05 | 0.001659 | 2.5127e-05 | 0.00035939 | 6.2081e-05 | 0 | 1.0156e-05 | 0 | 0.00069776
Tauranga | 15 | 24 | 10 | 26 | 16 | 11 | 19 | 23 | 21 | 24 | 70.0122 | 112.3359 | 15.7467 | 70.8382 | 92.4028 | 67.2549 | 57.4334 | 98.0091 | 123.8322 | 48.6579 | 446.7333 | 465.25 | 629.2997 | 226.6538 | 519.3125 | 375.5944 | 353.7368 | 378.8182 | 259.6367 | 831.0417 | 1.5088 | 3.9875 | 0.31314 | 1.3111 | 2.3994 | 0.8626 | 1.1888 | 2.6083 | 2.0416 | 2.9063 | 0.021551 | 0.035497 | 0.019886 | 0.018509 | 0.025967 | 0.012826 | 0.0207 | 0.026613 | 0.016487 | 0.059729
Waikato | 4 | 13 | 7 | 7 | 5 | 11 | 5 | 4 | 11 | 5 | 82.0799 | 87.6336 | 77.6011 | 40.3078 | 76.9723 | 71.5583 | 48.6584 | 233.0143 | 41.5892 | 68.395 | 237.75 | 164.1538 | 124.2856 | 707.1429 | 460.6 | 477.583 | 481.8 | 11.2214 | 629.979 | 782.6 | 0.25104 | 0.5945 | 0.21334 | 0.62667 | 0.55398 | 1.167 | 0.36101 | 0.031946 | 0.87146 | 0.80147 | 0.0030585 | 0.006784 | 0.0027492 | 0.015547 | 0.0071972 | 0.016309 | 0.0074193 | 0.0001371 | 0.020954 | 0.011718
Waikino | 6 | 1 | 7 | 4 | 7 | 4 | 7 | 2 | 5 | 5 | 92.3679 | 53 | 76.2228 | 18.8268 | 115.3808 | 114.4299 | 78.4078 | 108.6573 | 116.6776 | 38.203 | 641.5 | 720 | 532.1426 | 2707.25 | 303.1429 | 189.4788 | 671.8571 | 944.2627 | 398.2024 | 2879.2 | 1.1434 | 0.12131 | 0.89723 | 0.64034 | 0.76515 | 0.26924 | 1.1357 | 0.62677 | 0.70244 | 1.647 | 0.012379 | 0.0022889 | 0.011771 | 0.034012 | 0.0066315 | 0.0023529 | 0.014484 | 0.0057684 | 0.0060203 | 0.043111
Wairarapa | 5 | 7 | 9 | 11 | 5 | 6 | 10 | 6 | 5 | 7 | 122.8577 | 58.1623 | 114.0984 | 44.9614 | 46.1938 | 69.6731 | 119.5902 | 224.7288 | 37.3125 | 10.6308 | 94.2 | 135.5714 | 284.6665 | 356.9091 | 489.6 | 306.799 | 182.7 | 115.8163 | 209.6756 | 259.2857 | 0.1861 | 0.17547 | 0.92374 | 0.55441 | 0.3534 | 0.39815 | 0.67292 | 0.47699 | 0.11828 | 0.057782 | 0.0015148 | 0.0030169 | 0.008096 | 0.012331 | 0.0076503 | 0.0057145 | 0.0056269 | 0.0021225 | 0.00317 | 0.0054354
Whanganui | 2 | 2 | 8 | 7 | 7 | 5 | 5 | 8 | 3 | 5 | 54.2917 | 20.7634 | 43.5295 | 59.8403 | 62.8791 | 200.0971 | 168.8673 | 99.284 | 81.1 | 55.8546 | 96 | 279 | 628.3747 | 321.8571 | 256.2857 | 710.1206 | 141.8 | 433.272 | 514.286 | 276.8 | 0.033524 | 0.036832 | 0.69149 | 0.42345 | 0.35253 | 2.2056 | 0.36874 | 1.0511 | 0.37835 | 0.2315 | 0.00061748 | 0.0017739 | 0.015885 | 0.0070763 | 0.0056065 | 0.011022 | 0.0021836 | 0.010587 | 0.0046652 | 0.0041446
Vegetation
Total | 146 | 157 | 157 | 296 | 358 | 181 | 320 | 292 | 185 | 286 | 79.5936 | 87.5698 | 104.2711 | 120.4205 | 273.4942 | 85.1185 | 126.112 | 168.0107 | 107.1335 | 91.6907 | 374.5329 | 299.8423 | 256.0837 | 384.0631 | 396.6754 | 310.4333 | 226.9093 | 424.2258 | 225.4319 | 291.2555 | 12.3696 | 12.4981 | 14.1164 | 39.4129 | 104.0789 | 13.4909 | 34.3336 | 60.0675 | 13.2679 | 22.9363 | 0.16358 | 0.14721 | 0.14033 | 0.30742 | 0.39861 | 0.16241 | 0.25891 | 0.3381 | 0.1231 | 0.24004
Non-zero Average | 11.2308 | 12.0769 | 13.0833 | 22.7692 | 27.5385 | 13.9231 | 24.6154 | 22.4615 | 14.2308 | 22 | 79.5936 | 87.5698 | 112.9604 | 120.4205 | 273.4942 | 85.1185 | 126.112 | 168.0107 | 107.1335 | 91.6907 | 374.5329 | 299.8423 | 277.424 | 384.0631 | 396.6754 | 310.4333 | 226.9093 | 424.2258 | 225.4319 | 291.2555 | 0.95151 | 0.96139 | 1.1764 | 3.0318 | 8.0061 | 1.0378 | 2.641 | 4.6206 | 1.0206 | 1.7643 | 0.012583 | 0.011324 | 0.011694 | 0.023648 | 0.030663 | 0.012493 | 0.019916 | 0.026008 | 0.0094695 | 0.018465
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 17 | 12 | 12 | 20 | 19 | 12 | 21 | 20 | 13 | 18 | 54.4366 | 54.0079 | 83.3278 | 221.1204 | 78.1464 | 44.821 | 127.9821 | 122.5699 | 125.1552 | 75.9157 | 746.8824 | 421.6667 | 505.4164 | 1147.8 | 493.5263 | 307.4656 | 355.1429 | 1266.684 | 283.1538 | 540.6111 | 2.2229 | 0.86876 | 1.597 | 15.9429 | 2.29 | 0.51337 | 2.9397 | 9.4844 | 1.393 | 2.2123 | 0.040834 | 0.016086 | 0.019166 | 0.072101 | 0.029304 | 0.011454 | 0.022969 | 0.07738 | 0.01113 | 0.029141
Egmont | 3 | 7 | 0 | 17 | 21 | 6 | 19 | 19 | 6 | 17 | 85.1053 | 130.0549 | 0 | 77.7938 | 941.4588 | 91.1869 | 82.8903 | 117.2199 | 84.1176 | 66.7403 | 12.6667 | 83.2857 | 0 | 435.8824 | 289.9524 | 265.3037 | 190.5789 | 135.1034 | 234.8333 | 138.5294 | 0.010401 | 0.24104 | 0 | 1.8105 | 17.9149 | 0.45061 | 0.9244 | 0.91907 | 0.35838 | 0.47068 | 0.00012221 | 0.0018534 | 0 | 0.023273 | 0.019029 | 0.0049416 | 0.011152 | 0.0078406 | 0.0042605 | 0.0070525
Kinleith | 5 | 2 | 2 | 2 | 4 | 1 | 3 | 1 | 3 | 2 | 112.2869 | 33.0786 | 77.3317 | 64.2629 | 99.1978 | 126.5729 | 234.4708 | 52.0404 | 89.5793 | 55.3458 | 272.6 | 547 | 311.9998 | 483 | 215.75 | 318.9644 | 134.6667 | 322.2703 | 104.3333 | 128.5 | 0.49221 | 0.11504 | 0.15249 | 0.19498 | 0.26753 | 0.12533 | 0.29174 | 0.051226 | 0.084781 | 0.042596 | 0.0043835 | 0.0034778 | 0.0019719 | 0.003034 | 0.002697 | 0.00099019 | 0.0012443 | 0.00098435 | 0.00094644 | 0.00076963
Manawatu | 9 | 11 | 19 | 20 | 21 | 10 | 24 | 24 | 13 | 20 | 64.9727 | 64.4298 | 54.2168 | 40.1552 | 158.2321 | 77.3853 | 67.2056 | 93.3627 | 69.913 | 59.0535 | 407.1111 | 401.9091 | 671.3681 | 536.4 | 500.6667 | 383.2572 | 483.5 | 356.9029 | 471.1538 | 365.95 | 0.76561 | 0.90552 | 2.1854 | 1.353 | 5.1991 | 0.92071 | 2.4018 | 2.4427 | 1.2948 | 1.2943 | 0.011784 | 0.014054 | 0.040309 | 0.033695 | 0.032858 | 0.011898 | 0.035738 | 0.026163 | 0.018521 | 0.021918
Mt Maunganui | 7 | 9 | 4 | 16 | 14 | 8 | 12 | 17 | 11 | 22 | 47.7024 | 96.5305 | 95.7814 | 233.5754 | 153.3078 | 91.4208 | 177.9708 | 196.1577 | 95.6091 | 69.0972 | 592.2857 | 410.3333 | 99.4999 | 197.375 | 249 | 379.0826 | 104.75 | 730.3232 | 201.0909 | 211.1364 | 0.63605 | 1.1333 | 0.12046 | 2.3168 | 1.6702 | 0.86068 | 0.68899 | 7.4387 | 0.63949 | 0.96116 | 0.013334 | 0.01174 | 0.0012577 | 0.0099187 | 0.010894 | 0.0094145 | 0.0038714 | 0.037922 | 0.0066886 | 0.01391
Rangitikei | 13 | 8 | 14 | 30 | 34 | 13 | 26 | 26 | 14 | 20 | 67.1795 | 87.6449 | 241.9804 | 123.5456 | 191.6769 | 117.509 | 111.609 | 184.2717 | 116.7888 | 120.4769 | 228.4615 | 61.25 | 178.4285 | 184.7667 | 255.7941 | 333.1166 | 171.2692 | 184.633 | 223.1429 | 121.1 | 0.64167 | 0.13653 | 1.9101 | 2.1509 | 5.2096 | 1.5797 | 1.5307 | 2.7019 | 1.1032 | 0.87383 | 0.0095517 | 0.0015577 | 0.0078937 | 0.01741 | 0.027179 | 0.013444 | 0.013715 | 0.014663 | 0.0094462 | 0.0072531
Taranaki | 18 | 20 | 30 | 54 | 59 | 19 | 32 | 25 | 25 | 42 | 147.8149 | 117.4118 | 149.3753 | 92.1801 | 220.3663 | 81.9187 | 225.3194 | 161.7533 | 122.2511 | 158.7529 | 306.3889 | 324.15 | 245.3332 | 326.5185 | 335.1864 | 340.1725 | 323.0938 | 326.9986 | 144.36 | 255.119 | 2.6217 | 2.4198 | 3.4741 | 5.1048 | 13.6192 | 1.6437 | 7.1747 | 4.0389 | 1.3341 | 5.0941 | 0.017736 | 0.020609 | 0.023258 | 0.055379 | 0.061803 | 0.020064 | 0.031842 | 0.02497 | 0.010913 | 0.032088
Tararua | 3 | 6 | 11 | 10 | 20 | 9 | 14 | 19 | 15 | 12 | 63.4371 | 92.0377 | 130.2814 | 135.3615 | 122.8964 | 65.5001 | 95.1358 | 186.4444 | 111.6954 | 154.017 | 381.3333 | 101.6667 | 87.5454 | 67.1 | 115.7 | 77.2136 | 118.9286 | 124.4287 | 62.1333 | 181.9167 | 0.23339 | 0.17848 | 0.39646 | 0.28527 | 0.88873 | 0.1413 | 0.48785 | 1.3463 | 0.31477 | 1.0069 | 0.0036792 | 0.0019392 | 0.0030431 | 0.0021075 | 0.0072315 | 0.0021573 | 0.0051279 | 0.0072211 | 0.0028181 | 0.0065374
Tauranga | 9 | 18 | 5 | 13 | 29 | 15 | 23 | 24 | 11 | 25 | 95.5553 | 65.7602 | 87.763 | 114.2986 | 83.8882 | 82.8977 | 64.3327 | 189.1898 | 128.5025 | 72.861 | 506.6667 | 713.3889 | 275.9999 | 265.0769 | 1088.7241 | 450.1497 | 292.7391 | 629.7128 | 427.5455 | 351.28 | 1.4013 | 2.6844 | 0.38272 | 1.2371 | 8.2772 | 1.7377 | 1.334 | 8.7333 | 1.8274 | 1.9162 | 0.014665 | 0.040821 | 0.0043608 | 0.010823 | 0.09867 | 0.020962 | 0.020737 | 0.046162 | 0.014221 | 0.026299
Waikato | 20 | 12 | 17 | 30 | 27 | 16 | 14 | 15 | 14 | 12 | 67.6477 | 87.4069 | 76.4416 | 101.5912 | 74.5732 | 52.7299 | 67.1139 | 141.0255 | 118.1117 | 69.9766 | 316.35 | 351.8333 | 198.3528 | 261 | 322.1852 | 373.9582 | 169.5714 | 312.1501 | 163.2143 | 383.9167 | 1.3765 | 1.1732 | 0.81453 | 2.4984 | 2.0273 | 0.97943 | 0.49071 | 2.0169 | 0.81607 | 0.96543 | 0.020348 | 0.013422 | 0.010656 | 0.024593 | 0.027185 | 0.018575 | 0.0073115 | 0.014302 | 0.0069093 | 0.013797
Waikino | 5 | 8 | 8 | 3 | 3 | 15 | 10 | 6 | 9 | 9 | 47.151 | 105.4291 | 89.0478 | 136.8469 | 108.153 | 73.6721 | 82.1351 | 299.0473 | 111.8076 | 79.7579 | 710 | 162.25 | 463.2498 | 638.3333 | 751.3333 | 260.7042 | 81.7 | 612.8113 | 103.8889 | 550.5556 | 0.53832 | 0.43504 | 1.0428 | 0.82309 | 0.76183 | 0.89437 | 0.20667 | 3.3585 | 0.3161 | 1.1835 | 0.011417 | 0.0041263 | 0.011711 | 0.0060147 | 0.007044 | 0.01214 | 0.0025162 | 0.011231 | 0.0028272 | 0.014839
Wairarapa | 29 | 37 | 19 | 62 | 78 | 40 | 99 | 79 | 34 | 58 | 117.7397 | 153.0413 | 107.8793 | 124.3489 | 205.382 | 101.3958 | 155.9159 | 277.9305 | 102.9726 | 94.178 | 84.931 | 109.2162 | 204.8946 | 164.7258 | 168.9615 | 105.5882 | 280.1414 | 225.1214 | 157.8824 | 207.3276 | 0.93263 | 1.966 | 1.3271 | 3.9888 | 8.4589 | 1.3294 | 13.3178 | 15.0977 | 1.6714 | 3.3915 | 0.0079211 | 0.012846 | 0.012302 | 0.032077 | 0.041186 | 0.013111 | 0.085416 | 0.054322 | 0.016232 | 0.036011
Whanganui | 8 | 7 | 16 | 19 | 29 | 17 | 23 | 17 | 17 | 29 | 63.6876 | 51.5735 | 162.0984 | 100.3858 | 1118.1455 | 99.5298 | 147.3744 | 163.1266 | 116.2319 | 115.8063 | 303.25 | 210 | 87 | 284.8421 | 370 | 440.6566 | 243.7391 | 287.7962 | 353.8824 | 350.3793 | 0.4969 | 0.24101 | 0.71303 | 1.7064 | 37.4943 | 2.3146 | 2.5445 | 2.4377 | 2.1144 | 3.5239 | 0.0078021 | 0.0046731 | 0.0043988 | 0.016998 | 0.033533 | 0.023255 | 0.017266 | 0.014944 | 0.018191 | 0.030429
Adverse Weather
Total | 290 | 384 | 184 | 230 | 206 | 154 | 264 | 427 | 196 | 458 | 240.4824 | 148.6128 | 86.0791 | 125.9596 | 156.484 | 71.4776 | 93.5448 | 210.518 | 176.4924 | 137.5852 | 390.0725 | 372.5206 | 395.4412 | 454.5643 | 390.6453 | 210.5186 | 333.2577 | 200.2072 | 99.1375 | 292.7451 | 159.9594 | 103.7444 | 17.039 | 36.9118 | 43.8584 | 6.527 | 24.4302 | 40.4887 | 9.4636 | 28.3485 | 0.36895 | 0.5318 | 0.24988 | 0.28569 | 0.24852 | 0.08803 | 0.28877 | 0.21972 | 0.053251 | 0.22566
Non-zero Average | 22.3077 | 32 | 15.3333 | 17.6923 | 17.1667 | 11.8462 | 20.3077 | 32.8462 | 15.0769 | 35.2308 | 240.4824 | 160.9972 | 93.2523 | 125.9596 | 169.5243 | 71.4776 | 93.5448 | 210.518 | 176.4924 | 137.5852 | 390.0725 | 403.564 | 428.3946 | 454.5643 | 423.1991 | 210.5186 | 333.2577 | 200.2072 | 99.1375 | 292.7451 | 12.3046 | 8.6454 | 1.4199 | 2.8394 | 3.6549 | 0.50208 | 1.8792 | 3.1145 | 0.72797 | 2.1807 | 0.028381 | 0.044317 | 0.020823 | 0.021976 | 0.02071 | 0.0067716 | 0.022213 | 0.016901 | 0.0040963 | 0.017359
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 43 | 29 | 3 | 16 | 7 | 1 | 19 | 34 | 17 | 15 | 973.9759 | 315.8679 | 262.9806 | 23.196 | 47.3699 | 51 | 56.848 | 142.8162 | 15.1233 | 35.23 | 873.1395 | 1311.2414 | 568.333 | 817.6875 | 1381 | 128.9856 | 886.2105 | 524.5828 | 103.0588 | 848 | 117.6041 | 38.1835 | 1.4169 | 0.95316 | 1.4311 | 0.020421 | 2.948 | 7.7804 | 0.080118 | 1.342 | 0.12075 | 0.12088 | 0.0053878 | 0.041091 | 0.030211 | 0.00040042 | 0.051858 | 0.054478 | 0.0052976 | 0.038092
Egmont | 48 | 32 | 26 | 17 | 26 | 11 | 28 | 68 | 14 | 69 | 171.0677 | 88.4027 | 90.8212 | 123.3731 | 409.6775 | 50.441 | 123.5385 | 170.7866 | 148.3682 | 139.0583 | 276.375 | 243.9688 | 302.6921 | 405.3529 | 533.1923 | 404.7729 | 100.6429 | 74.2923 | 83.5 | 106.5217 | 7.2984 | 2.194 | 2.2587 | 2.6702 | 17.7487 | 0.69721 | 1.0722 | 2.6353 | 0.52445 | 3.0608 | 0.042664 | 0.024818 | 0.024869 | 0.021643 | 0.043324 | 0.013822 | 0.008679 | 0.015431 | 0.0035348 | 0.022011
Kinleith | 3 | 0 | 3 | 3 | 0 | 3 | 8 | 3 | 2 | 4 | 60.6983 | 0 | 28.1136 | 45.1666 | 0 | 31.1592 | 26.9698 | 211.6135 | 361.9197 | 254.1183 | 362.3333 | 0 | 419.6664 | 770.6667 | 0 | 119.32 | 67.75 | 45.2167 | 5.5 | 2.5 | 0.21219 | 0 | 0.11185 | 0.32798 | 0 | 0.034625 | 0.04502 | 0.087678 | 0.012038 | 0.00761 | 0.0034958 | 0 | 0.0039785 | 0.0072616 | 0 | 0.0011112 | 0.0016693 | 0.00041433 | 3.3261e-05 | 2.9947e-05
Manawatu | 20 | 54 | 17 | 21 | 20 | 10 | 25 | 24 | 12 | 47 | 46.3845 | 161.2084 | 81.6354 | 91.6279 | 76.7164 | 64.9771 | 68.0802 | 82.455 | 216.1469 | 137.3661 | 324.15 | 477 | 404.4704 | 344.1429 | 487.9 | 104.2883 | 348.28 | 261.1358 | 136.75 | 232.8511 | 0.9671 | 13.2005 | 1.7738 | 2.0798 | 2.3395 | 0.21036 | 1.8257 | 1.5784 | 1.0725 | 4.502 | 0.02085 | 0.081885 | 0.021728 | 0.022699 | 0.030495 | 0.0032375 | 0.026816 | 0.019143 | 0.004962 | 0.032774
Mt Maunganui | 7 | 12 | 5 | 12 | 4 | 5 | 7 | 22 | 20 | 7 | 121.6219 | 164.8902 | 165.8471 | 205.2595 | 151.9853 | 70.9536 | 68.7592 | 182.6811 | 82.0275 | 68.5505 | 923.7143 | 333.3333 | 482.7997 | 284.3333 | 218.25 | 112.3874 | 70.8571 | 170.2589 | 55.4 | 157.7143 | 2.5291 | 2.0967 | 1.2651 | 2.1997 | 0.41465 | 0.12378 | 0.10504 | 2.09 | 0.27482 | 0.22664 | 0.020795 | 0.012716 | 0.0076283 | 0.010716 | 0.0027282 | 0.0017445 | 0.0015276 | 0.011441 | 0.0033503 | 0.0033061
Rangitikei | 16 | 21 | 25 | 22 | 13 | 7 | 23 | 35 | 13 | 40 | 168.4085 | 169.5955 | 75.7666 | 141.823 | 198.5991 | 70.3897 | 237.4227 | 334.2199 | 238.0871 | 291.1582 | 163.25 | 161.7619 | 370.0398 | 321.3182 | 331.2308 | 309.394 | 181.5652 | 70.7944 | 15 | 59.7 | 1.4147 | 1.8315 | 2.2149 | 3.1488 | 2.6725 | 0.47325 | 3.0536 | 2.5295 | 0.14038 | 2.0822 | 0.0084003 | 0.010799 | 0.029233 | 0.022202 | 0.013457 | 0.0067233 | 0.012861 | 0.0075683 | 0.00058963 | 0.0071513
Taranaki | 34 | 47 | 33 | 28 | 52 | 33 | 30 | 74 | 35 | 127 | 149.9835 | 60.6422 | 67.9772 | 135.0242 | 143.477 | 54.78 | 122.8825 | 87.9187 | 165.3127 | 166.2882 | 485.2941 | 331.4894 | 365.818 | 286.8214 | 342.0192 | 168.5569 | 106.9 | 107.1483 | 35.0857 | 111.1102 | 7.9588 | 3.0035 | 2.5932 | 3.4058 | 7.9745 | 0.94592 | 1.2137 | 2.1293 | 0.61384 | 7.027 | 0.053065 | 0.049529 | 0.038148 | 0.025224 | 0.05558 | 0.017268 | 0.0098771 | 0.024218 | 0.0037132 | 0.042258
Tararua | 16 | 9 | 8 | 18 | 22 | 16 | 20 | 21 | 7 | 18 | 77.2482 | 139.8972 | 120.0247 | 71.7601 | 122.7041 | 91.6123 | 140.2664 | 197.2721 | 297.5206 | 144.0684 | 77.0625 | 172.8889 | 91.125 | 152.0556 | 132.3182 | 104.0509 | 263.3 | 114.7088 | 60.4286 | 95.6111 | 0.30632 | 0.692 | 0.2765 | 0.61688 | 1.1163 | 0.47347 | 2.2749 | 1.4515 | 0.38054 | 0.74251 | 0.0039654 | 0.0049465 | 0.0023037 | 0.0085964 | 0.0090972 | 0.0051682 | 0.016218 | 0.0073578 | 0.0012791 | 0.0051539
Tauranga | 17 | 34 | 20 | 36 | 9 | 6 | 30 | 32 | 9 | 8 | 85.1257 | 125.0317 | 35.0224 | 167.2837 | 27.5707 | 56.55 | 62.8064 | 235.6005 | 60.5717 | 114.6484 | 402.8824 | 448.5882 | 1344.5993 | 507.1667 | 838.7778 | 59.66 | 766.4667 | 276.1207 | 409 | 184.125 | 1.875 | 6.0623 | 2.9762 | 9.5929 | 0.65044 | 0.062841 | 4.4478 | 6.3585 | 0.67419 | 0.50573 | 0.022027 | 0.048486 | 0.084979 | 0.057345 | 0.023592 | 0.0011112 | 0.070818 | 0.026988 | 0.01113 | 0.0044112
Waikato | 16 | 72 | 6 | 17 | 11 | 20 | 13 | 26 | 24 | 6 | 339.9318 | 246.4063 | 24.5415 | 136.4775 | 107.6681 | 122.9056 | 64.8267 | 234.112 | 46.3669 | 62.2203 | 325.375 | 334.3056 | 239.1665 | 251.5882 | 219.9091 | 177.8801 | 429.6923 | 201.8765 | 47.9167 | 227.3333 | 5.6914 | 18.8546 | 0.11129 | 1.8333 | 0.81394 | 1.3574 | 1.1153 | 3.7533 | 0.16123 | 0.25415 | 0.016743 | 0.076518 | 0.0045346 | 0.013433 | 0.0075597 | 0.011044 | 0.017204 | 0.016032 | 0.0034773 | 0.0040847
Waikino | 13 | 36 | 0 | 7 | 4 | 5 | 12 | 6 | 7 | 5 | 631.4238 | 171.3803 | 0 | 269.695 | 215.1243 | 48.1156 | 61.4294 | 488.851 | 85.2162 | 96.8084 | 267.5385 | 749.5556 | 0 | 1070.8571 | 50.5 | 708.7208 | 282.3333 | 545.5181 | 93.2857 | 1528 | 7.0627 | 14.7013 | 0 | 6.3496 | 0.1358 | 0.5293 | 0.64099 | 4.8873 | 0.16826 | 2.2149 | 0.011185 | 0.085782 | 0 | 0.023544 | 0.00063128 | 0.011001 | 0.010435 | 0.0099975 | 0.0019745 | 0.022879
Wairarapa | 41 | 32 | 30 | 21 | 21 | 26 | 33 | 49 | 16 | 46 | 240.4001 | 217.7994 | 58.8846 | 93.1556 | 134.9859 | 139.9187 | 99.8829 | 231.8287 | 102.3758 | 117.8908 | 182.3902 | 122.4688 | 188.8999 | 199.7619 | 238.7619 | 82.2985 | 381.7273 | 109.9981 | 69.3125 | 105.8261 | 5.7815 | 2.7134 | 1.0545 | 1.2274 | 2.1151 | 0.92943 | 3.8751 | 3.8166 | 0.3433 | 1.7186 | 0.02405 | 0.012458 | 0.017908 | 0.013176 | 0.015669 | 0.0066426 | 0.038797 | 0.016463 | 0.0033534 | 0.014578
Whanganui | 16 | 6 | 8 | 12 | 17 | 11 | 16 | 33 | 20 | 66 | 60.0012 | 70.8442 | 107.4131 | 133.6331 | 398.4132 | 76.4058 | 82.3701 | 136.579 | 475.3651 | 161.2019 | 407.4375 | 156.1667 | 363.1248 | 497.5833 | 304.5294 | 256.4259 | 446.625 | 101.0415 | 174.55 | 146.3939 | 1.2579 | 0.21102 | 0.98604 | 2.5061 | 6.4458 | 0.66904 | 1.8128 | 1.391 | 5.0179 | 4.6643 | 0.020965 | 0.0029787 | 0.0091799 | 0.018754 | 0.016179 | 0.0087565 | 0.022009 | 0.010185 | 0.010556 | 0.028935
Unknown
Total | 219 | 267 | 301 | 384 | 371 | 273 | 268 | 396 | 513 | 502 | 39.5118 | 53.1439 | 45.9606 | 49.4522 | 57.5489 | 61.4369 | 44.1327 | 57.4105 | 52.1545 | 61.2258 | 521.9054 | 698.8743 | 564.1356 | 416.7882 | 501.7682 | 405.6566 | 460.4706 | 482.0747 | 420.074 | 531.5383 | 11.605 | 23.4565 | 23.8883 | 26.2833 | 26.5732 | 18.5295 | 19.7671 | 29.9752 | 37.5201 | 44.7277 | 0.39983 | 0.46588 | 0.57311 | 0.51271 | 0.52312 | 0.34058 | 0.42744 | 0.57572 | 0.64939 | 0.69985
Non-zero Average | 16.8462 | 20.5385 | 23.1538 | 29.5385 | 28.5385 | 21 | 20.6154 | 30.4615 | 39.4615 | 38.6154 | 39.5118 | 53.1439 | 45.9606 | 49.4522 | 57.5489 | 61.4369 | 44.1327 | 57.4105 | 52.1545 | 61.2258 | 521.9054 | 698.8743 | 564.1356 | 416.7882 | 501.7682 | 405.6566 | 460.4706 | 482.0747 | 420.074 | 531.5383 | 0.89269 | 1.8043 | 1.8376 | 2.0218 | 2.0441 | 1.4253 | 1.5205 | 2.3058 | 2.8862 | 3.4406 | 0.030756 | 0.035837 | 0.044085 | 0.039439 | 0.04024 | 0.026198 | 0.03288 | 0.044286 | 0.049953 | 0.053835
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 17 | 19 | 23 | 28 | 17 | 13 | 13 | 34 | 22 | 22 | 25.2801 | 53.951 | 34.4505 | 58.2661 | 47.5782 | 98.8033 | 24.8963 | 35.4387 | 53.9977 | 46.4733 | 1175.4118 | 563.0526 | 1078.4342 | 556 | 969.5294 | 690.769 | 535.2308 | 1502.4536 | 343.7727 | 945.2305 | 1.6246 | 1.8348 | 2.7003 | 2.849 | 2.4507 | 2.7544 | 0.53352 | 5.5295 | 1.2349 | 2.8941 | 0.064263 | 0.034009 | 0.078381 | 0.048896 | 0.051508 | 0.027877 | 0.02143 | 0.15603 | 0.022869 | 0.062275
Egmont | 8 | 16 | 18 | 19 | 25 | 22 | 22 | 51 | 33 | 38 | 71.8791 | 32.0369 | 38.6648 | 60.3849 | 36.4663 | 46.0227 | 36.897 | 108.2182 | 40.9267 | 59.3161 | 258.375 | 633.25 | 391.1665 | 546.4737 | 738.2 | 337.8259 | 391 | 211.129 | 166.7576 | 402.1058 | 0.47782 | 1.0319 | 0.86028 | 1.9692 | 2.1032 | 1.0618 | 0.9775 | 3.5592 | 0.68101 | 2.7142 | 0.0066476 | 0.03221 | 0.02225 | 0.032611 | 0.057674 | 0.023072 | 0.026493 | 0.032889 | 0.01664 | 0.045759
Kinleith | 8 | 5 | 2 | 4 | 1 | 6 | 7 | 5 | 5 | 9 | 40.4198 | 35.2132 | 83.1217 | 54.9454 | 43.7164 | 87.5032 | 50.8515 | 42.898 | 48.609 | 68.12 | 930.5 | 535.6 | 344.9998 | 386.5 | 484 | 852.4047 | 403.8571 | 804.3011 | 235.8 | 918.3395 | 0.96766 | 0.29978 | 0.18124 | 0.2668 | 0.066124 | 1.3893 | 0.44275 | 0.52693 | 0.17329 | 1.6861 | 0.02394 | 0.0085133 | 0.0021804 | 0.0048557 | 0.0015126 | 0.015877 | 0.0087067 | 0.012283 | 0.003565 | 0.024751
Manawatu | 31 | 45 | 57 | 58 | 69 | 23 | 50 | 51 | 55 | 66 | 34.5276 | 30.0484 | 38.1074 | 58.2581 | 42.8883 | 52.4927 | 51.1675 | 57.9298 | 45.193 | 50.8014 | 391.4516 | 527.6 | 566.4032 | 437.0517 | 506.6957 | 631.1034 | 515.42 | 608.8689 | 283.6182 | 355.6795 | 1.3475 | 2.2679 | 3.8878 | 4.6383 | 4.686 | 2.3654 | 4.0612 | 5.4945 | 2.1316 | 3.5713 | 0.039027 | 0.075476 | 0.10202 | 0.079617 | 0.10926 | 0.045061 | 0.079371 | 0.094847 | 0.047168 | 0.0703
Mt Maunganui | 7 | 7 | 8 | 9 | 15 | 8 | 12 | 9 | 27 | 9 | 25.5306 | 51.0538 | 55.2762 | 55.0645 | 32.3019 | 49.0226 | 58.8897 | 77.3228 | 37.9083 | 44.8253 | 644.8571 | 1439.1429 | 321.3748 | 138.2222 | 470.4 | 262.0957 | 221.6667 | 212.403 | 652.6296 | 319.8247 | 0.37063 | 1.635 | 0.44909 | 0.21515 | 0.71229 | 0.3191 | 0.48245 | 0.45148 | 2.0198 | 0.38639 | 0.014517 | 0.032025 | 0.0081244 | 0.0039072 | 0.022051 | 0.0065091 | 0.0081924 | 0.0058389 | 0.053282 | 0.00862
Rangitikei | 10 | 18 | 16 | 27 | 46 | 15 | 15 | 29 | 51 | 48 | 44.2612 | 46.2777 | 55.8705 | 56.3692 | 34.901 | 67.487 | 30.6757 | 51.4125 | 30.5094 | 75.8711 | 295.6 | 320.8889 | 535.5622 | 327.5556 | 329.1957 | 186.7791 | 492 | 262.336 | 393.9804 | 258.1994 | 0.42077 | 0.84974 | 1.5129 | 1.5658 | 1.6516 | 0.58697 | 0.69724 | 1.1947 | 1.8536 | 2.8159 | 0.0095066 | 0.018362 | 0.027078 | 0.027777 | 0.047324 | 0.0086975 | 0.022729 | 0.023237 | 0.060756 | 0.037115
Taranaki | 44 | 27 | 41 | 56 | 64 | 41 | 51 | 50 | 75 | 97 | 27.3542 | 37.0628 | 46.3715 | 49.3454 | 63.1817 | 53.3386 | 41.3322 | 44.4221 | 45.6516 | 60.1714 | 521.7955 | 498.6296 | 474.5363 | 349.8214 | 302.0625 | 348.205 | 757.6863 | 442.9969 | 402.0533 | 424.3685 | 2.0198 | 1.5862 | 2.851 | 3.0362 | 3.8171 | 2.3639 | 4.919 | 3.0054 | 4.1624 | 7.4175 | 0.073837 | 0.042799 | 0.061481 | 0.061529 | 0.060415 | 0.044319 | 0.11901 | 0.067655 | 0.091178 | 0.12327
Tararua | 12 | 21 | 12 | 17 | 34 | 17 | 6 | 27 | 47 | 28 | 57.4145 | 73.6405 | 26.2659 | 41.6774 | 79.1455 | 72.6191 | 12.521 | 31.6464 | 44.2645 | 67.3379 | 197.8333 | 179.619 | 450.0831 | 227.4706 | 191.3235 | 103.8707 | 391.3333 | 534.4533 | 314.8723 | 216.7452 | 0.43835 | 0.88304 | 0.44829 | 0.5062 | 1.6089 | 0.39808 | 0.090545 | 1.3949 | 1.9808 | 1.2238 | 0.0076349 | 0.011991 | 0.017067 | 0.012146 | 0.020329 | 0.0054817 | 0.0072315 | 0.044076 | 0.044749 | 0.018174
Tauranga | 31 | 30 | 30 | 43 | 18 | 29 | 25 | 27 | 41 | 37 | 14.9311 | 25.9489 | 42.4561 | 49.8113 | 57.2694 | 27.8565 | 75.8485 | 37.5726 | 31.049 | 82.4986 | 1077.2581 | 932.9667 | 1400.1659 | 692.7907 | 883.3333 | 796.4972 | 640.04 | 306.4215 | 512.0732 | 1134.0908 | 1.6036 | 2.3089 | 5.6355 | 4.6606 | 2.8457 | 1.9975 | 3.7379 | 0.94947 | 1.9711 | 10.3669 | 0.1074 | 0.088977 | 0.13274 | 0.093565 | 0.04969 | 0.071706 | 0.049281 | 0.02527 | 0.063484 | 0.12566
Waikato | 15 | 28 | 40 | 48 | 20 | 23 | 17 | 11 | 39 | 30 | 37.3026 | 48.0917 | 38.2841 | 61.4489 | 31.9219 | 51.8249 | 43.121 | 34.0827 | 45.2673 | 41.8569 | 329.6 | 303.75 | 388.2748 | 285.9375 | 426.9 | 233.3652 | 183.8235 | 361.4633 | 619.359 | 316.8706 | 0.59312 | 1.3003 | 1.8789 | 2.6489 | 0.85175 | 0.86353 | 0.41502 | 0.41392 | 3.3063 | 1.1916 | 0.0159 | 0.027037 | 0.049078 | 0.043108 | 0.026682 | 0.016662 | 0.0096245 | 0.012145 | 0.073039 | 0.028468
Waikino | 7 | 6 | 10 | 9 | 7 | 3 | 4 | 9 | 10 | 11 | 62.5315 | 141.3724 | 32.3856 | 16.7016 | 139.1414 | 81.6132 | 57.3494 | 63.4488 | 59.0945 | 52.4375 | 541.5714 | 2444.3333 | 505.8997 | 509.7778 | 363.4286 | 132.3185 | 333.5 | 199.4816 | 488.7 | 700.0188 | 0.76239 | 6.5912 | 0.51774 | 0.24067 | 1.1062 | 0.10057 | 0.23562 | 0.34794 | 0.87325 | 1.2092 | 0.012192 | 0.046623 | 0.015987 | 0.01441 | 0.0079503 | 0.0012323 | 0.0041085 | 0.0054837 | 0.014777 | 0.02306
Wairarapa | 24 | 29 | 27 | 46 | 41 | 42 | 28 | 60 | 64 | 66 | 39.7856 | 74.6764 | 63.0375 | 43.3355 | 65.0479 | 43.4046 | 47.0193 | 98.8523 | 54.5273 | 87.9977 | 297.9167 | 288.3448 | 304.3332 | 366.6957 | 369.561 | 201.4537 | 296.8929 | 160.6313 | 306.6406 | 262.0092 | 0.91486 | 1.9851 | 1.6368 | 2.2959 | 3.0801 | 1.1401 | 1.2038 | 2.91 | 3.2357 | 4.557 | 0.022995 | 0.026583 | 0.025966 | 0.052979 | 0.047352 | 0.026266 | 0.025603 | 0.029438 | 0.059341 | 0.051786
Whanganui | 5 | 16 | 17 | 20 | 14 | 31 | 18 | 33 | 44 | 41 | 32.4356 | 41.4963 | 43.1968 | 37.2705 | 74.5761 | 66.6917 | 43.1563 | 63.0917 | 141.0107 | 58.2285 | 122.6 | 418.1875 | 572.5291 | 593.95 | 488.3571 | 496.8477 | 823.6667 | 660.0313 | 740.7045 | 656.5149 | 0.063945 | 0.88265 | 1.3286 | 1.3906 | 1.5934 | 3.1888 | 1.9706 | 4.1974 | 13.8962 | 4.6937 | 0.0019714 | 0.021271 | 0.030757 | 0.03731 | 0.021366 | 0.047814 | 0.045662 | 0.066529 | 0.098547 | 0.080608
The remainder
Total | 321 | 336 | 296 | 264 | 291 | 296 | 240 | 282 | 351 | 398 | 61.3838 | 79.604 | 97.7748 | 76.7 | 67.202 | 75.3129 | 69.6496 | 84.5044 | 103.5727 | 83.0407 | 609.3597 | 438.5831 | 545.4592 | 499.0828 | 563.5614 | 379.0612 | 509.6963 | 341.1485 | 430.3017 | 522.1542 | 40.5094 | 36.5469 | 58.5777 | 27.0018 | 34.9459 | 22.5603 | 23.5778 | 19.4781 | 41.3476 | 29.4602 | 0.65742 | 0.52312 | 0.55009 | 0.43537 | 0.5864 | 0.3441 | 0.35757 | 0.28835 | 0.43099 | 0.41128
Non-zero Average | 24.6923 | 25.8462 | 22.7692 | 20.3077 | 22.3846 | 22.7692 | 18.4615 | 21.6923 | 27 | 30.6154 | 61.3838 | 79.604 | 97.7748 | 76.7 | 67.202 | 75.3129 | 69.6496 | 84.5044 | 103.5727 | 83.0407 | 609.3597 | 438.5831 | 545.4592 | 499.0828 | 563.5614 | 379.0612 | 509.6963 | 341.1485 | 430.3017 | 522.1542 | 3.1161 | 2.8113 | 4.506 | 2.0771 | 2.6881 | 1.7354 | 1.8137 | 1.4983 | 3.1806 | 2.2662 | 0.050571 | 0.04024 | 0.042315 | 0.03349 | 0.045108 | 0.026469 | 0.027505 | 0.022181 | 0.033153 | 0.031637
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 28 | 16 | 20 | 9 | 18 | 20 | 18 | 17 | 17 | 14 | 75.4491 | 79.3995 | 256.7008 | 23.9755 | 29.767 | 88.7472 | 114.5474 | 93.3604 | 84.0494 | 35.4717 | 915.3214 | 474.625 | 1826.499 | 1336.0411 | 1315.6111 | 280.5686 | 318.8889 | 224.135 | 456.9412 | 1112.2857 | 6.2188 | 1.9168 | 29.6324 | 0.90547 | 2.2029 | 1.546 | 2.025 | 1.0866 | 1.9742 | 1.6542 | 0.082424 | 0.024141 | 0.11544 | 0.037766 | 0.074006 | 0.01742 | 0.017678 | 0.011638 | 0.023489 | 0.046633
Egmont | 10 | 17 | 21 | 15 | 11 | 17 | 30 | 22 | 24 | 42 | 64.8226 | 83.3872 | 51.2408 | 98.2839 | 94.4633 | 49.9847 | 61.6912 | 55.8821 | 68.0767 | 86.8156 | 244.6 | 343.5294 | 562.333 | 200.2524 | 271.6364 | 423.3056 | 307.4 | 187.4612 | 265.9583 | 218.6905 | 0.50992 | 1.5481 | 1.9121 | 0.92725 | 0.88209 | 1.1166 | 1.7522 | 0.70394 | 1.3139 | 2.388 | 0.0078664 | 0.018565 | 0.037317 | 0.0094344 | 0.0093379 | 0.02234 | 0.028402 | 0.012597 | 0.019301 | 0.027506
Kinleith | 9 | 5 | 2 | 9 | 3 | 4 | 4 | 5 | 2 | 4 | 67.8296 | 94.3654 | 89.9582 | 83.4421 | 100.5838 | 45.3969 | 54.7903 | 37.0754 | 133.82 | 45.5926 | 1166 | 156 | 179.4999 | 796.9088 | 142.3333 | 626.9299 | 960 | 855.6894 | 433 | 2624.25 | 2.2892 | 0.23399 | 0.10205 | 1.8797 | 0.13422 | 0.35341 | 0.64798 | 0.48451 | 0.35042 | 1.4332 | 0.033749 | 0.0024796 | 0.0011344 | 0.022527 | 0.0013344 | 0.0077849 | 0.011827 | 0.013068 | 0.0026186 | 0.031435
Manawatu | 40 | 41 | 43 | 39 | 19 | 29 | 20 | 27 | 32 | 43 | 56.2321 | 52.9388 | 40.4543 | 32.7058 | 45.5525 | 60.47 | 46.0799 | 26.7348 | 28.0526 | 37.1122 | 989.2 | 1016.4878 | 769.9996 | 775.2223 | 516.2632 | 424.125 | 579.95 | 823.8728 | 421 | 649.0698 | 7.1557 | 7.0137 | 4.2327 | 3.1057 | 1.3964 | 2.3089 | 1.6461 | 1.8165 | 1.1428 | 3.1019 | 0.12725 | 0.13249 | 0.10463 | 0.094959 | 0.030654 | 0.038183 | 0.035723 | 0.067944 | 0.040736 | 0.083582
Mt Maunganui | 18 | 20 | 19 | 10 | 21 | 18 | 10 | 11 | 14 | 23 | 77.0858 | 144.9946 | 86.4549 | 91.4184 | 71.5545 | 100.7338 | 88.4606 | 130.7337 | 90.8974 | 132.4006 | 843.5 | 256.95 | 481.0524 | 205.1391 | 392.2857 | 271.803 | 338.3 | 226.3466 | 159.8571 | 111.3478 | 3.764 | 2.3688 | 2.497 | 0.58901 | 1.8422 | 1.5299 | 0.92168 | 0.99422 | 0.61512 | 1.0154 | 0.048829 | 0.016337 | 0.028883 | 0.0064431 | 0.025745 | 0.015188 | 0.010419 | 0.0076049 | 0.0067672 | 0.0076694
Rangitikei | 12 | 11 | 12 | 8 | 18 | 19 | 10 | 23 | 32 | 37 | 57.9201 | 70.9334 | 242.1891 | 126.4421 | 37.8866 | 122.9662 | 47.5597 | 56.3336 | 67.0978 | 133.1388 | 339.1667 | 259.1818 | 267.9165 | 265.5224 | 505.7778 | 163.3502 | 574.8 | 156.72 | 272.1875 | 107.4595 | 0.75813 | 0.64289 | 2.4605 | 0.84358 | 1.0779 | 1.1848 | 0.84195 | 0.62023 | 1.7672 | 1.5853 | 0.013089 | 0.0090633 | 0.010159 | 0.0066717 | 0.028451 | 0.0096349 | 0.017703 | 0.01101 | 0.026337 | 0.011907
Taranaki | 49 | 48 | 32 | 32 | 44 | 46 | 42 | 52 | 53 | 52 | 40.085 | 57.805 | 54.2517 | 69.8936 | 41.6607 | 50.1067 | 46.3205 | 83.7192 | 86.3047 | 99.6858 | 668.8571 | 461.4792 | 437.2185 | 310.9187 | 587.0227 | 457.2098 | 617.4286 | 371.8853 | 407.3774 | 346.25 | 4.2251 | 4.0705 | 2.3986 | 2.1841 | 3.3628 | 3.2715 | 3.6995 | 4.945 | 5.6345 | 5.375 | 0.1054 | 0.070418 | 0.044212 | 0.031249 | 0.080719 | 0.06529 | 0.079866 | 0.059067 | 0.065286 | 0.053919
Tararua | 10 | 1 | 6 | 6 | 4 | 7 | 7 | 13 | 13 | 15 | 55.8919 | 61 | 69.9671 | 84.5241 | 11.0316 | 95.0783 | 63.0579 | 108.2094 | 31.1909 | 28.846 | 154.5 | 562 | 101.1666 | 128.1479 | 787.25 | 108.845 | 170 | 102.06 | 305.8462 | 197.8667 | 0.27772 | 0.10898 | 0.13421 | 0.20412 | 0.10856 | 0.22489 | 0.23111 | 0.43852 | 0.37499 | 0.25639 | 0.0049688 | 0.0017866 | 0.0019181 | 0.0024149 | 0.009841 | 0.0023653 | 0.003665 | 0.0040525 | 0.012022 | 0.0088882
Tauranga | 43 | 59 | 35 | 49 | 56 | 37 | 30 | 34 | 42 | 40 | 91.3844 | 76.2459 | 77.1831 | 72.2104 | 64.196 | 58.4606 | 77.0147 | 78.1063 | 58.9572 | 95.117 | 657.5581 | 693.6949 | 524.0569 | 851.8433 | 1136.5357 | 408.4408 | 596.9333 | 412.4269 | 919.3333 | 349.225 | 8.3099 | 9.9203 | 4.4736 | 9.4667 | 12.7687 | 2.7426 | 4.2477 | 3.3453 | 6.8835 | 3.979 | 0.090934 | 0.13011 | 0.057961 | 0.1311 | 0.1989 | 0.046914 | 0.055154 | 0.042831 | 0.11675 | 0.041833
Waikato | 43 | 55 | 42 | 41 | 31 | 28 | 16 | 14 | 51 | 21 | 67.2395 | 103.1777 | 81.2297 | 122.815 | 115.6233 | 92.5941 | 55.0574 | 117.1436 | 85.8169 | 76.319 | 359.7209 | 210.4182 | 235.238 | 214.9633 | 356.2903 | 180.1941 | 351.625 | 158.5749 | 233.6667 | 212.5714 | 3.3449 | 3.796 | 2.5361 | 3.3997 | 3.991 | 1.4503 | 0.95399 | 0.79435 | 3.0923 | 1.0203 | 0.049746 | 0.03679 | 0.031221 | 0.027682 | 0.034517 | 0.015663 | 0.017327 | 0.006781 | 0.036034 | 0.013368
Waikino | 13 | 7 | 18 | 3 | 10 | 13 | 8 | 15 | 14 | 19 | 39.6477 | 109.7808 | 63.6952 | 88.0884 | 119.5813 | 102.0824 | 42.6266 | 123.8389 | 154.6348 | 155.8913 | 320.3077 | 470.5714 | 650.9441 | 486.2784 | 394.3 | 555.861 | 990.125 | 124.1407 | 913.6429 | 262.2105 | 0.53095 | 1.1496 | 2.3584 | 0.40362 | 1.4735 | 2.29 | 1.0399 | 0.70436 | 5.9808 | 2.3258 | 0.013392 | 0.010472 | 0.037026 | 0.0045819 | 0.012322 | 0.022433 | 0.024395 | 0.0056877 | 0.038677 | 0.01492
Wairarapa | 28 | 42 | 21 | 26 | 27 | 40 | 24 | 32 | 43 | 57 | 76.6517 | 56.913 | 89.1801 | 46.3258 | 72.4971 | 54.8189 | 115.1141 | 124.7499 | 85.0717 | 77.2813 | 207 | 393.3571 | 249.2856 | 409.9154 | 463.8889 | 343.9616 | 252.7917 | 108.3454 | 101.3256 | 182.6491 | 1.4288 | 2.9891 | 1.4753 | 1.5507 | 2.8377 | 2.3414 | 2.151 | 1.3211 | 1.1208 | 2.4095 | 0.01864 | 0.05252 | 0.016543 | 0.033474 | 0.039142 | 0.042711 | 0.018685 | 0.01059 | 0.013175 | 0.031178
Whanganui | 18 | 14 | 25 | 17 | 29 | 18 | 21 | 17 | 14 | 31 | 27.7498 | 43.9102 | 68.5676 | 56.9752 | 69.2284 | 57.6281 | 93.1241 | 62.6698 | 372.4745 | 75.8571 | 1055.9444 | 403.2857 | 805.7596 | 506.9228 | 457.1034 | 683.2014 | 567.8095 | 683.2722 | 703.7857 | 414.129 | 1.6963 | 0.78813 | 4.3647 | 1.5421 | 2.8679 | 2.2 | 3.4199 | 2.2235 | 11.0972 | 2.9164 | 0.061127 | 0.017949 | 0.063656 | 0.027067 | 0.041427 | 0.038176 | 0.036724 | 0.035479 | 0.029793 | 0.038446
Totals
Total | 1829 | 1959 | 1815 | 2197 | 2335 | 1881 | 2239 | 2755 | 2827 | 3496 | 108.154 | 94.1671 | 80.4683 | 97.5635 | 125.7987 | 77.3517 | 88.4279 | 121.4841 | 89.3055 | 81.8155 | 420.9368 | 386.9526 | 406.8882 | 379.1454 | 348.5969 | 302.7414 | 328.788 | 274.0664 | 249.1355 | 286.8709 | 292.5216 | 236.2655 | 184.2754 | 217.6434 | 300.9311 | 115.7691 | 190.3603 | 231.7952 | 171.9007 | 196.1955 | 2.3176 | 2.4442 | 2.2671 | 2.354 | 2.4935 | 1.6383 | 2.1398 | 2.0953 | 1.954 | 2.4541
Non-zero Average | 140.6923 | 150.6923 | 139.6154 | 169 | 179.6154 | 144.6923 | 172.2308 | 211.9231 | 217.4615 | 268.9231 | 108.154 | 94.1671 | 80.4683 | 97.5635 | 125.7987 | 77.3517 | 88.4279 | 121.4841 | 89.3055 | 81.8155 | 420.9368 | 386.9526 | 406.8882 | 379.1454 | 348.5969 | 302.7414 | 328.788 | 274.0664 | 249.1355 | 286.8709 | 22.5017 | 18.1743 | 14.175 | 16.7418 | 23.1485 | 8.9053 | 14.6431 | 17.8304 | 13.2231 | 15.092 | 0.17828 | 0.18801 | 0.1744 | 0.18108 | 0.1918 | 0.12602 | 0.1646 | 0.16118 | 0.1503 | 0.18878
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 151 | 145 | 117 | 124 | 99 | 106 | 147 | 208 | 168 | 167 | 332.8516 | 143.1604 | 146.3085 | 109.8969 | 51.6691 | 69.9017 | 101.375 | 91.2578 | 94.7834 | 53.6451 | 832.351 | 747.9448 | 1053.5208 | 616.9788 | 724.0101 | 504.9719 | 334.932 | 611.62 | 213.974 | 440.5693 | 134.5415 | 49.3572 | 56.9888 | 26.4071 | 11.5739 | 11.6154 | 15.3721 | 35.4605 | 10.3027 | 11.8198 | 0.40421 | 0.34477 | 0.38951 | 0.24029 | 0.224 | 0.16617 | 0.15164 | 0.38857 | 0.1087 | 0.22033
Egmont | 143 | 158 | 181 | 172 | 253 | 172 | 302 | 370 | 259 | 438 | 124.0366 | 67.2974 | 72.1279 | 86.7102 | 268.5615 | 59.594 | 83.4873 | 109.4823 | 75.7149 | 100.7992 | 200.1049 | 235.4937 | 241.7734 | 228.2604 | 242.2411 | 230.0964 | 166.0497 | 121.9514 | 136.8731 | 133.2786 | 11.4147 | 7.9602 | 9.9743 | 10.6923 | 51.4375 | 7.3218 | 12.8942 | 15.089 | 8.1161 | 17.6215 | 0.092027 | 0.11828 | 0.13829 | 0.12331 | 0.19153 | 0.12286 | 0.15444 | 0.13782 | 0.10719 | 0.17482
Kinleith | 36 | 18 | 20 | 32 | 15 | 27 | 32 | 26 | 26 | 46 | 61.8569 | 47.5957 | 84.3544 | 89.7334 | 79.1346 | 78.6199 | 73.1317 | 59.9074 | 76.9634 | 84.3435 | 713.2222 | 363.2222 | 303.0498 | 559.6931 | 230.3333 | 367.1071 | 322.125 | 433.3153 | 405.454 | 714.9795 | 5.1078 | 0.98924 | 1.6156 | 5.0477 | 0.85444 | 2.4192 | 2.3217 | 2.0615 | 2.4533 | 8.3072 | 0.082575 | 0.020784 | 0.019153 | 0.056253 | 0.010797 | 0.03077 | 0.031747 | 0.034412 | 0.031876 | 0.098492
Manawatu | 195 | 236 | 256 | 265 | 271 | 182 | 226 | 258 | 233 | 354 | 55.9586 | 72.6779 | 54.8541 | 62.7137 | 69.9707 | 61.0158 | 59.6713 | 72.6085 | 55.7371 | 62.0383 | 497.7487 | 590.9703 | 483.156 | 441.727 | 423.2177 | 391.3793 | 422.885 | 410.3834 | 276.2716 | 359.4318 | 17.4676 | 32.2233 | 21.4401 | 23.0571 | 25.0794 | 13.4923 | 17.5641 | 23.4815 | 10.8488 | 23.6391 | 0.31215 | 0.44337 | 0.39086 | 0.36766 | 0.35843 | 0.22113 | 0.29435 | 0.3234 | 0.19464 | 0.38104
Mt Maunganui | 74 | 92 | 84 | 119 | 105 | 83 | 92 | 113 | 148 | 137 | 71.5802 | 101.2963 | 102.3378 | 151.5075 | 82.3778 | 77.2427 | 76.9146 | 162.8619 | 91.4762 | 71.1479 | 583.5 | 322.163 | 353.8331 | 287.7512 | 261.9143 | 217.7949 | 148.1522 | 244.5332 | 256.9026 | 149.733 | 9.94 | 9.5444 | 9.6118 | 16.2945 | 7.0799 | 4.3347 | 3.2287 | 13.7456 | 10.5168 | 4.3707 | 0.13887 | 0.094222 | 0.093922 | 0.10755 | 0.085944 | 0.056118 | 0.041978 | 0.084401 | 0.11497 | 0.061431
Rangitikei | 100 | 93 | 116 | 142 | 177 | 122 | 127 | 218 | 226 | 266 | 81.1368 | 96.7586 | 104.7511 | 117.1935 | 109.3782 | 120.555 | 109.6591 | 138.8181 | 67.9123 | 108.1373 | 192.63 | 190.2366 | 274.1378 | 229.5083 | 299.3107 | 209.7471 | 236.2913 | 138.2919 | 198.7907 | 120.7879 | 5.0265 | 5.442 | 10.5263 | 11.9959 | 18.109 | 9.5767 | 10.135 | 12.7829 | 9.2257 | 10.4047 | 0.061951 | 0.056243 | 0.10049 | 0.10236 | 0.16556 | 0.079438 | 0.092423 | 0.092084 | 0.13585 | 0.096218
Taranaki | 264 | 260 | 271 | 302 | 425 | 309 | 311 | 382 | 424 | 634 | 68.3322 | 64.5097 | 71.1245 | 97.7715 | 132.6261 | 56.2119 | 87.0803 | 92.6208 | 75.2398 | 94.4291 | 393.6061 | 314.9 | 304.2397 | 278.8324 | 292.8635 | 235.1582 | 371.8232 | 222.8897 | 219.0507 | 200.6037 | 22.8356 | 16.7904 | 18.5308 | 25.8586 | 51.5883 | 12.6801 | 31.0131 | 24.0875 | 21.1303 | 35.9654 | 0.33419 | 0.26028 | 0.26054 | 0.26448 | 0.38898 | 0.22558 | 0.35614 | 0.26007 | 0.28084 | 0.38087
Tararua | 112 | 102 | 96 | 116 | 180 | 119 | 126 | 184 | 192 | 219 | 87.0497 | 108.1125 | 64.2595 | 91.7358 | 111.8339 | 95.9002 | 107.3593 | 98.3072 | 84.6826 | 107.8507 | 120.9464 | 112.8824 | 145.6562 | 114.6197 | 140.7 | 98.1235 | 149.6667 | 165.8227 | 135.3229 | 102.4651 | 3.7923 | 3.9572 | 2.8394 | 3.8309 | 8.8513 | 3.4763 | 6.2354 | 9.1617 | 6.653 | 7.2476 | 0.043565 | 0.036603 | 0.044187 | 0.04176 | 0.079147 | 0.036249 | 0.05808 | 0.093195 | 0.078563 | 0.0672
Tauranga | 173 | 213 | 135 | 255 | 192 | 148 | 193 | 219 | 256 | 234 | 64.4969 | 70.6271 | 47.7442 | 84.9352 | 69.9498 | 54.5644 | 70.5314 | 125.3938 | 66.5129 | 77.6155 | 553.5896 | 679.8028 | 736.8441 | 516.3856 | 758.1146 | 488.0738 | 447.2487 | 335.7429 | 363.5796 | 421.1767 | 19.8653 | 32.5105 | 15.0079 | 35.1273 | 31.8193 | 12.2358 | 18.7507 | 28.1615 | 18.7194 | 22.9076 | 0.308 | 0.46031 | 0.31434 | 0.41358 | 0.45489 | 0.22424 | 0.26585 | 0.22458 | 0.28144 | 0.29514
Waikato | 178 | 247 | 177 | 212 | 152 | 183 | 111 | 127 | 277 | 141 | 90.233 | 158.1744 | 60.8028 | 95.7817 | 83.9643 | 73.3545 | 55.0299 | 143.5611 | 70.9855 | 58.817 | 298.8483 | 240.4939 | 244.853 | 234.6769 | 271.9013 | 217.7298 | 237.4054 | 176.7092 | 230.6562 | 215.0647 | 15.4368 | 29.8694 | 8.3271 | 14.9669 | 10.8447 | 9.0734 | 4.4662 | 9.8408 | 13.7139 | 5.3412 | 0.17108 | 0.18884 | 0.13695 | 0.15626 | 0.12916 | 0.12369 | 0.08116 | 0.068548 | 0.19319 | 0.090811
Waikino | 83 | 87 | 63 | 49 | 48 | 53 | 83 | 66 | 90 | 95 | 208.4805 | 144.938 | 90.9626 | 91.7673 | 111.2318 | 98.0685 | 84.364 | 206.4333 | 137.8722 | 75.5542 | 532.6024 | 748.8391 | 493.9204 | 823.1395 | 312.2292 | 421.9906 | 795.1566 | 287.0144 | 348.5779 | 453.9706 | 29.6394 | 30.0178 | 8.9444 | 11.6252 | 5.2097 | 6.809 | 17.1481 | 11.9442 | 13.0788 | 9.758 | 0.14217 | 0.20711 | 0.098331 | 0.12668 | 0.046836 | 0.069431 | 0.20326 | 0.05786 | 0.094861 | 0.12915
Wairarapa | 227 | 229 | 188 | 276 | 266 | 245 | 359 | 388 | 319 | 457 | 116.7097 | 99.7811 | 75.6791 | 81.5247 | 110.5036 | 79.0598 | 150.6207 | 172.7565 | 80.7882 | 82.6722 | 142.4802 | 192.8777 | 209.4999 | 232.2746 | 238.8383 | 159.1006 | 214.7159 | 140.055 | 136.3523 | 165.1633 | 12.1397 | 14.0106 | 9.4191 | 16.4151 | 21.9397 | 9.5668 | 35.7579 | 28.6744 | 10.6255 | 18.687 | 0.10402 | 0.14041 | 0.12446 | 0.20135 | 0.19854 | 0.12101 | 0.2374 | 0.16598 | 0.13152 | 0.22604
Whanganui | 93 | 79 | 111 | 133 | 152 | 132 | 130 | 196 | 209 | 308 | 43.2789 | 49.2434 | 70.7814 | 107.0538 | 354.1821 | 81.4832 | 90.3384 | 105.2852 | 182.3033 | 86.552 | 410.5484 | 290.557 | 445.0628 | 365.0428 | 336.0855 | 394.365 | 427.7923 | 274.5344 | 316.9563 | 252.0978 | 5.3143 | 3.5933 | 11.0498 | 16.3245 | 56.5442 | 13.1678 | 15.4731 | 17.3041 | 36.5164 | 20.1256 | 0.12279 | 0.072971 | 0.15611 | 0.15249 | 0.15965 | 0.1616 | 0.17128 | 0.16435 | 0.20031 | 0.23253

## CPP Fault Rate Information
CPP Fault Rate Information - Conductor and Vegetation
Conductor
Failure Rates
| FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30
Coromandel | 13.2343 | 13.3519 | 13.475 | 13.5825 | 13.718 | 13.8234 | 13.8444 | 14.0156 | 14.0418 | 14.0257 | 13.9499 | 13.9499 | 13.9499 | 13.9499
Egmont | 24.2981 | 24.2832 | 24.3786 | 23.6536 | 20.788 | 19.3717 | 19.2434 | 19.0909 | 18.9202 | 18.1645 | 17.339 | 17.339 | 17.339 | 17.339
Kinleith | 2.5212 | 2.5304 | 2.543 | 2.557 | 2.5723 | 2.5892 | 2.607 | 2.6275 | 2.6379 | 2.6158 | 2.6015 | 2.6015 | 2.6015 | 2.6015
Manawatu | 23.5253 | 23.7224 | 23.7614 | 23.9797 | 23.9947 | 24.1744 | 23.4064 | 23.6222 | 23.7684 | 23.3674 | 23.4031 | 23.4031 | 23.4031 | 23.4031
Mt Maunganui | 14.4137 | 14.4841 | 14.557 | 14.4534 | 14.3993 | 13.1231 | 12.1775 | 10.1659 | 8.2697 | 8.1016 | 7.7491 | 7.7491 | 7.7491 | 7.7491
Rangitikei | 24.8825 | 24.4402 | 24.4178 | 24.6077 | 24.7797 | 24.6011 | 24.5406 | 24.6569 | 24.9719 | 24.2051 | 23.784 | 23.784 | 23.784 | 23.784
Taranaki | 41.736 | 41.5624 | 40.5011 | 38.8817 | 37.942 | 36.4267 | 34.7538 | 33.949 | 33.0678 | 31.4755 | 29.826 | 29.826 | 29.826 | 29.826
Tararua | 12.8156 | 12.9785 | 13.1051 | 13.2938 | 13.2849 | 13.3549 | 13.4995 | 13.7181 | 13.9793 | 14.1074 | 13.8989 | 13.8989 | 13.8989 | 13.8989
Tauranga | 22.7365 | 22.8106 | 22.9049 | 22.6491 | 22.6422 | 21.4843 | 19.589 | 16.7 | 13.1225 | 12.9579 | 12.8166 | 12.8166 | 12.8166 | 12.8166
Waikato | 19.9272 | 20.0711 | 20.2469 | 20.44 | 20.6263 | 20.7863 | 20.9063 | 21.0893 | 21.286 | 20.9833 | 20.8171 | 20.8171 | 20.8171 | 20.8171
Waikino | 5.6232 | 5.6676 | 5.7409 | 5.8116 | 5.8956 | 5.9735 | 6.075 | 6.1449 | 6.2526 | 6.235 | 6.3534 | 6.3534 | 6.3534 | 6.3534
Wairarapa | 33.1853 | 32.4964 | 32.3238 | 32.3029 | 32.5587 | 32.1444 | 32.4965 | 32.1883 | 32.3954 | 32.0084 | 32.0037 | 32.0037 | 32.0037 | 32.0037
Whanganui | 21.3213 | 21.3759 | 21.3885 | 21.3396 | 20.9319 | 20.8504 | 19.5612 | 19.1565 | 19.2671 | 18.574 | 17.9004 | 17.9004 | 17.9004 | 17.9004
Total | 260.2201 | 259.7747 | 259.344 | 257.5527 | 254.1335 | 248.7035 | 242.7005 | 237.125 | 231.9807 | 226.8215 | 222.4427 | 222.4427 | 222.4427 | 222.4427
Vegetation
Moderator | FY17: 0.9
| Historic | yr1 | yr2 | yr3 | yr4 | yr5 | remainder | [5 empty] | Historic | yr1 | yr2 | yr3 | yr4 | yr5 | remainder
Number of reactive tree sites | FY17: 2615; FY18: 1743; FY19: 872; FY20: 523; FY27: Number of reactive tree sites; FY29: 2615; FY30: 1743 | 872 | 523
Coromandel | 760 | 760 | 760 | 760 | 532.3 | 303.7 | 212.8 |  |  |  | Coromandel |  | 760 | 760 | 760 | 760 | 507 | 253 | 152
Egmont | 382 | 266.8 | 152.5 | 106.6 | 106.6 | 106.6 | 106.6 |  |  |  | Egmont |  | 382 | 254 | 127 | 76 | 76 | 76 | 76
Kinleith | 760 | 760 | 760 | 760 | 532.3 | 303.7 | 212.8 |  |  |  | Kinleith |  | 760 | 760 | 760 | 760 | 507 | 253 | 152
Manawatu | 486 | 340.2 | 194.4 | 135.9 | 135.9 | 135.9 | 135.9 |  |  |  | Manawatu |  | 486 | 324 | 162 | 97 | 97 | 97 | 97
Mt Maunganui | 266 | 266 | 266 | 266 | 185.9 | 106.7 | 74.3 |  |  |  | Mt Maunganui |  | 266 | 266 | 266 | 266 | 177 | 89 | 53
Rangitikei | 486 | 340.2 | 194.4 | 135.9 | 135.9 | 135.9 | 135.9 |  |  |  | Rangitikei |  | 486 | 324 | 162 | 97 | 97 | 97 | 97
Taranaki | 382 | 266.8 | 152.5 | 106.6 | 106.6 | 106.6 | 106.6 |  |  |  | Taranaki |  | 382 | 254 | 127 | 76 | 76 | 76 | 76
Tararua | 486 | 340.2 | 194.4 | 135.9 | 135.9 | 135.9 | 135.9 |  |  |  | Tararua |  | 486 | 324 | 162 | 97 | 97 | 97 | 97
Tauranga | 266 | 266 | 266 | 266 | 185.9 | 106.7 | 74.3 |  |  |  | Tauranga |  | 266 | 266 | 266 | 266 | 177 | 89 | 53
Waikato | 760 | 760 | 760 | 760 | 532.3 | 303.7 | 212.8 |  |  |  | Waikato |  | 760 | 760 | 760 | 760 | 507 | 253 | 152
Waikino | 760 | 760 | 760 | 760 | 532.3 | 303.7 | 212.8 |  |  |  | Waikino |  | 760 | 760 | 760 | 760 | 507 | 253 | 152
Wairarapa | 401 | 280.4 | 160.7 | 112.1 | 112.1 | 112.1 | 112.1 |  |  |  | Wairarapa |  | 401 | 267 | 134 | 80 | 80 | 80 | 80
Whanganui | 320 | 223.7 | 128.3 | 89.6 | 89.6 | 89.6 | 89.6 |  |  |  | Whanganui |  | 320 | 213 | 107 | 64 | 64 | 64 | 64
Overall Profile | 6515 | 5630.3 | 4749.2 | 4394.6 | 3323.6 | 2250.8 | 1822.4 |  |  |  | Total |  | 6515 | 5532 | 4553 | 4159 | 2969 | 1777 | 1301
Baseline | FY17: 20%
Year 1 | FY17: 2019
Overview | FY18: Baseline number of reactive tree sites; FY19: Year 1 expected number of reactive tree sites; FY20: Year 2 expected number of reactive tree sites; FY21: Year 3 (and longer term) expected number of reactive tree sites; FY22: Start year; FY23: Planning area translation
| Tauranga | 266 | 177 | 89 | 53 | 4 | Mt Maunganui, Tauranga
| Valley | 760 | 507 | 253 | 152 | 4 | Waikato, Waikino, Rangitikei, Coromandel, Kinleith
| Masterton | 401 | 267 | 134 | 80 | 1
| Palmerston | 486 | 324 | 162 | 97 | 1 | Manawatu, Rangitikei
| Taranaki | 382 | 254 | 127 | 76 | 1
| Wanganui | 320 | 213 | 107 | 64 | 1
| Powerco | 2615 | 1743 | 872 | 523

## Total ICPs
ICP Forecast
ICPs - Total
Source: CIW CAPEX Forecasts by Network Region 300916-2.xlsx, via Bernie
Forecasts
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Total Customers | 310940 | 301754 | 304478 | 306759 | 307997 | 309867 | 311659 | 315569 | 318895 | 322561 | 326301 | 329708 | 333000 | 336229 | 339043 | 342060 | 344745 | 347948 | 350938 | 353660 | 356216 | 358930 | 361759 | 364002 | 366519 | 368743 | 370801 | 373244
Used for ID | 310941 | 314565 | 316453 | 318388 | 319987 | 322126 | 324692 | 327394 | 330714 | 333925
ICPs - By Region
|  | Actual | [7 empty] | FORECAST - Scaled to match historical ID ICP numbers
Total | 314565 | 314565 | 316453 | 318388 | 319987 | 322126 | 324692 | 327394 | 330714 | 333925 | 337665 | 341072 | 344364 | 347593 | 350407 | 353424 | 356109 | 359312 | 362302 | 365024 | 367580 | 370294 | 373123 | 375366 | 377883 | 380107 | 382165 | 384608
Planning Area |  | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Coromandel |  | 23549.061 | 23696.715 | 23950.7936 | 24113.5409 | 24276.8945 | 24515.0227 | 24695.9834 | 24949.6462 | 25235.815 | 25657.815 | 25970.815 | 26281.815 | 26589.815 | 26895.815 | 27199.815 | 27400.815 | 27700.815 | 27998.815 | 28294.815 | 28490.815 | 28783.815 | 29074.815 | 29267.815 | 29555.815 | 29746.815 | 29936.815 | 30125.815
Egmont |  | 12576.1785 | 12597.7142 | 12619.9384 | 12614.6753 | 12625.4821 | 12643.505 | 12669.608 | 12642.8272 | 12702.2788 | 12858.2788 | 12935.2788 | 13012.2788 | 13166.2788 | 13242.2788 | 13318.2788 | 13394.2788 | 13546.2788 | 13621.2788 | 13696.2788 | 13771.2788 | 13846.2788 | 13994.2788 | 14067.2788 | 14140.2788 | 14213.2788 | 14286.2788 | 14359.2788
Kinleith |  | 6719.6657 | 6777.4684 | 6781.699 | 6777.9725 | 6791.4594 | 6810.3652 | 6778.842 | 6837.3521 | 6825.275 | 6825.275 | 6825.275 | 6825.275 | 6901.275 | 6976.275 | 6976.275 | 7050.275 | 7124.275 | 7124.275 | 7197.275 | 7270.275 | 7270.275 | 7343.275 | 7343.275 | 7415.275 | 7415.275 | 7415.275 | 7487.275
Manawatu |  | 50408.9594 | 50619.5092 | 50800.4677 | 51026.9954 | 51235.8594 | 51500.1962 | 51808.239 | 52044.9743 | 52491.3648 | 52933.3648 | 53447.3648 | 53885.3648 | 54248.3648 | 54609.3648 | 54969.3648 | 55327.3648 | 55756.3648 | 56111.3648 | 56465.3648 | 56817.3648 | 57168.3648 | 57588.3648 | 57866.3648 | 58213.3648 | 58489.3648 | 58765.3648 | 59109.3648
Mt Maunganui |  | 29694.3339 | 29983.6198 | 30274.7746 | 30536.1997 | 30748.1688 | 31126.4006 | 31864.9149 | 32646.723 | 32988.6566 | 33371.6566 | 33751.6566 | 34129.6566 | 34429.6566 | 34802.6566 | 35099.6566 | 35468.6566 | 35761.6566 | 36125.6566 | 36415.6566 | 36703.6566 | 36989.6566 | 37274.6566 | 37558.6566 | 37840.6566 | 38121.6566 | 38331.6566 | 38610.6566
Rangitikei |  | 10569.4524 | 10514.8976 | 10492.2245 | 10311.3698 | 10285.4278 | 10321.2923 | 10399.6193 | 10390.3277 | 10445.4762 | 10587.4762 | 10657.4762 | 10726.4762 | 10795.4762 | 10864.4762 | 10933.4762 | 11002.4762 | 11139.4762 | 11207.4762 | 11275.4762 | 11343.4762 | 11411.4762 | 11479.4762 | 11546.4762 | 11613.4762 | 11679.4762 | 11745.4762 | 11811.4762
Taranaki |  | 44338.7433 | 44743.1396 | 45128.2937 | 45390.8059 | 45746.9713 | 46096.2855 | 46385.3729 | 46766.3269 | 47150.6104 | 47599.6104 | 47971.6104 | 48415.6104 | 48782.6104 | 49074.6104 | 49438.6104 | 49728.6104 | 50090.6104 | 50449.6104 | 50808.6104 | 51093.6104 | 51447.6104 | 51801.6104 | 52083.6104 | 52364.6104 | 52644.6104 | 52922.6104 | 53131.6104
Tararua |  | 4486.7268 | 4469.1173 | 4463.0097 | 4427.9152 | 4453.4842 | 4438.1453 | 4436.2303 | 4426.1821 | 4418.364 | 4418.364 | 4418.364 | 4418.364 | 4520.364 | 4520.364 | 4520.364 | 4520.364 | 4520.364 | 4620.364 | 4620.364 | 4620.364 | 4620.364 | 4620.364 | 4620.364 | 4620.364 | 4620.364 | 4620.364 | 4719.364
Tauranga |  | 45628.2603 | 46076.5995 | 46584.4803 | 47189.1919 | 47950.843 | 48710.2072 | 49224.9337 | 50365.9704 | 50936.4485 | 51568.4485 | 52124.4485 | 52677.4485 | 53226.4485 | 53703.4485 | 54246.4485 | 54718.4485 | 55254.4485 | 55786.4485 | 56249.4485 | 56710.4485 | 57169.4485 | 57625.4485 | 58014.4485 | 58466.4485 | 58851.4485 | 59235.4485 | 59682.4485
Waikato |  | 23480.259 | 23514.8324 | 23582.3358 | 23605.5047 | 23705.1354 | 23870.1372 | 24049.6383 | 24197.776 | 24560.8447 | 24871.8447 | 25178.8447 | 25484.8447 | 25787.8447 | 26013.8447 | 26313.8447 | 26536.8447 | 26832.8447 | 27052.8447 | 27344.8447 | 27561.8447 | 27778.8447 | 27994.8447 | 28208.8447 | 28421.8447 | 28634.8447 | 28845.8447 | 29055.8447
Waikino |  | 15722.308 | 15833.1472 | 15798.0165 | 15897.6908 | 15999.9008 | 16173.1848 | 16287.2728 | 16427.0677 | 16600.957 | 16794.957 | 17084.957 | 17275.957 | 17465.957 | 17653.957 | 17840.957 | 18026.957 | 18211.957 | 18394.957 | 18485.957 | 18667.957 | 18848.957 | 18938.957 | 19117.957 | 19206.957 | 19383.957 | 19471.957 | 19647.957
Wairarapa |  | 23786.7408 | 23928.4855 | 24106.48 | 24260.0299 | 24469.2135 | 24659.8354 | 24822.555 | 25013.944 | 25368.3245 | 25749.3245 | 26050.3245 | 26350.3245 | 26573.3245 | 26795.3245 | 27089.3245 | 27308.3245 | 27526.3245 | 27743.3245 | 27959.3245 | 28174.3245 | 28388.3245 | 28601.3245 | 28743.3245 | 28954.3245 | 29094.3245 | 29234.3245 | 29373.3245
Whanganui |  | 23604.3111 | 23697.7544 | 23805.4863 | 23835.108 | 23837.1597 | 23827.4227 | 23970.7904 | 24004.8824 | 24200.5845 | 24428.5845 | 24655.5845 | 24880.5845 | 25105.5845 | 25254.5845 | 25477.5845 | 25625.5845 | 25846.5845 | 26065.5845 | 26210.5845 | 26354.5845 | 26570.5845 | 26785.5845 | 26927.5845 | 27069.5845 | 27211.5845 | 27353.5845 | 27493.5845
ChkSum |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Growth Rates
Planning Area | [10 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
Coromandel | [10 empty] | 1.672% | 1.22% | 1.197% | 1.172% | 1.151% | 1.13% | 0.739% | 1.095% | 1.076% | 1.057% | 0.6927% | 1.028% | 1.011% | 0.6638% | 0.984% | 0.6462% | 0.6387% | 0.6313%
Egmont | [10 empty] | 1.228% | 0.5988% | 0.5953% | 1.183% | 0.5772% | 0.5739% | 0.5706% | 1.135% | 0.5537% | 0.5506% | 0.5476% | 0.5446% | 1.069% | 0.5216% | 0.5189% | 0.5163% | 0.5136% | 0.511%
Kinleith | [10 empty] | 0% | 0% | 0% | 1.114% | 1.087% | 0% | 1.061% | 1.05% | 0% | 1.025% | 1.014% | 0% | 1.004% | 0% | 0.9805% | 0% | 0% | 0.971%
Manawatu | [10 empty] | 0.842% | 0.971% | 0.8195% | 0.6737% | 0.6655% | 0.6592% | 0.6513% | 0.7754% | 0.6367% | 0.6309% | 0.6234% | 0.6178% | 0.7347% | 0.4827% | 0.5997% | 0.4741% | 0.4719% | 0.5854%
Mt Maunganui | [10 empty] | 1.161% | 1.139% | 1.12% | 0.879% | 1.083% | 0.8534% | 1.051% | 0.8261% | 1.018% | 0.8028% | 0.7909% | 0.7792% | 0.7705% | 0.7619% | 0.7508% | 0.7426% | 0.5509% | 0.7279%
Rangitikei | [10 empty] | 1.359% | 0.6612% | 0.6474% | 0.6433% | 0.6392% | 0.6351% | 0.6311% | 1.245% | 0.6104% | 0.6067% | 0.6031% | 0.5995% | 0.5959% | 0.5837% | 0.5803% | 0.5683% | 0.5651% | 0.5619%
Taranaki | [10 empty] | 0.9523% | 0.7815% | 0.9255% | 0.758% | 0.5986% | 0.7417% | 0.5866% | 0.728% | 0.7167% | 0.7116% | 0.5609% | 0.6928% | 0.6881% | 0.5444% | 0.5395% | 0.5347% | 0.5281% | 0.3949%
Tararua | [10 empty] | 0% | 0% | 0% | 2.309% | 0% | 0% | 0% | 0% | 2.212% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.143%
Tauranga | [10 empty] | 1.241% | 1.078% | 1.061% | 1.042% | 0.8962% | 1.011% | 0.8701% | 0.9796% | 0.9628% | 0.83% | 0.8196% | 0.8094% | 0.7976% | 0.675% | 0.7791% | 0.6585% | 0.6525% | 0.7546%
Waikato | [10 empty] | 1.266% | 1.234% | 1.215% | 1.189% | 0.8764% | 1.153% | 0.8475% | 1.115% | 0.8199% | 1.079% | 0.7936% | 0.7873% | 0.7776% | 0.7644% | 0.7551% | 0.7494% | 0.7369% | 0.728%
Waikino | [10 empty] | 1.169% | 1.727% | 1.118% | 1.1% | 1.076% | 1.059% | 1.043% | 1.026% | 1.005% | 0.4947% | 0.9845% | 0.9696% | 0.4775% | 0.9451% | 0.4655% | 0.9215% | 0.454% | 0.9039%
Wairarapa | [10 empty] | 1.502% | 1.169% | 1.152% | 0.8463% | 0.8354% | 1.097% | 0.8084% | 0.7983% | 0.7883% | 0.7786% | 0.769% | 0.7596% | 0.7503% | 0.4965% | 0.7341% | 0.4835% | 0.4812% | 0.4755%
Whanganui | [10 empty] | 0.9421% | 0.9292% | 0.9126% | 0.9043% | 0.5935% | 0.883% | 0.5809% | 0.8624% | 0.8473% | 0.5563% | 0.5494% | 0.8196% | 0.8092% | 0.5301% | 0.5273% | 0.5246% | 0.5218% | 0.5118%
[5 empty] | Historical actual number of ICPs | [5 empty] | 2027: Forecast number of ICPs
AMP Region |  | FY09 | FY10 | FY11 | FY12 | FY13 | FY14 | FY15 | FY16 | FY17 | FY18 | FY19 | FY20 | FY21 | FY22 | FY23 | FY24 | FY25 | FY26 | FY27 | FY28 | FY29 | FY30 | FY31 | FY32 | FY33 | FY34 | FY35
Coromandel |  | 22590 | 22800 | 23076 | 23210 | 23353 | 23531 | 23804 | 24058 | 24377 | 24799 | 25112 | 25423 | 25731 | 26037 | 26341 | 26542 | 26842 | 27140 | 27436 | 27632 | 27925 | 28216 | 28409 | 28697 | 28888 | 29078 | 29267
Egmont |  | 12064 | 12121 | 12159 | 12142 | 12145 | 12136 | 12212 | 12191 | 12270 | 12426 | 12503 | 12580 | 12734 | 12810 | 12886 | 12962 | 13114 | 13189 | 13264 | 13339 | 13414 | 13562 | 13635 | 13708 | 13781 | 13854 | 13927
Kinleith |  | 6446 | 6521 | 6534 | 6524 | 6533 | 6537 | 6534 | 6593 | 6593 | 6593 | 6593 | 6593 | 6669 | 6744 | 6744 | 6818 | 6892 | 6892 | 6965 | 7038 | 7038 | 7111 | 7111 | 7183 | 7183 | 7183 | 7255
Manawatu |  | 48356 | 48704 | 48945 | 49115 | 49286 | 49433 | 49937 | 50185 | 50705 | 51147 | 51661 | 52099 | 52462 | 52823 | 53183 | 53541 | 53970 | 54325 | 54679 | 55031 | 55382 | 55802 | 56080 | 56427 | 56703 | 56979 | 57323
Mt Maunganui |  | 28485 | 28849 | 29169 | 29392 | 29578 | 29877 | 30714 | 31480 | 31866 | 32249 | 32629 | 33007 | 33307 | 33680 | 33977 | 34346 | 34639 | 35003 | 35293 | 35581 | 35867 | 36152 | 36436 | 36718 | 36999 | 37209 | 37488
Rangitikei |  | 10139 | 10117 | 10109 | 9925 | 9894 | 9907 | 10024 | 10019 | 10090 | 10232 | 10302 | 10371 | 10440 | 10509 | 10578 | 10647 | 10784 | 10852 | 10920 | 10988 | 11056 | 11124 | 11191 | 11258 | 11324 | 11390 | 11456
Taranaki |  | 42533 | 43050 | 43480 | 43690 | 44006 | 44246 | 44710 | 45095 | 45546 | 45995 | 46367 | 46811 | 47178 | 47470 | 47834 | 48124 | 48486 | 48845 | 49204 | 49489 | 49843 | 50197 | 50479 | 50760 | 51040 | 51318 | 51527
Tararua |  | 4304 | 4300 | 4300 | 4262 | 4284 | 4260 | 4276 | 4268 | 4268 | 4268 | 4268 | 4268 | 4370 | 4370 | 4370 | 4370 | 4370 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4470 | 4569
Tauranga |  | 43770 | 44333 | 44883 | 45421 | 46126 | 46755 | 47447 | 48566 | 49203 | 49835 | 50391 | 50944 | 51493 | 51970 | 52513 | 52985 | 53521 | 54053 | 54516 | 54977 | 55436 | 55892 | 56281 | 56733 | 57118 | 57502 | 57949
Waikato |  | 22524 | 22625 | 22721 | 22721 | 22803 | 22912 | 23181 | 23333 | 23725 | 24036 | 24343 | 24649 | 24952 | 25178 | 25478 | 25701 | 25997 | 26217 | 26509 | 26726 | 26943 | 27159 | 27373 | 27586 | 27799 | 28010 | 28220
Waikino |  | 15082 | 15234 | 15221 | 15302 | 15391 | 15524 | 15699 | 15840 | 16036 | 16230 | 16520 | 16711 | 16901 | 17089 | 17276 | 17462 | 17647 | 17830 | 17921 | 18103 | 18284 | 18374 | 18553 | 18642 | 18819 | 18907 | 19083
Wairarapa |  | 22818 | 23023 | 23226 | 23351 | 23538 | 23670 | 23926 | 24120 | 24505 | 24886 | 25187 | 25487 | 25710 | 25932 | 26226 | 26445 | 26663 | 26880 | 27096 | 27311 | 27525 | 27738 | 27880 | 28091 | 28231 | 28371 | 28510
Whanganui |  | 22643 | 22801 | 22936 | 22942 | 22930 | 22871 | 23105 | 23147 | 23377 | 23605 | 23832 | 24057 | 24282 | 24431 | 24654 | 24802 | 25023 | 25242 | 25387 | 25531 | 25747 | 25962 | 26104 | 26246 | 26388 | 26530 | 26670
|  | 301754 | 304478 | 306759 | 307997 | 309867 | 311659 | 315569 | 318895 | 322561 | 326301 | 329708 | 333000 | 336229 | 339043 | 342060 | 344745 | 347948 | 350938 | 353660 | 356216 | 358930 | 361759 | 364002 | 366519 | 368743 | 370801 | 373244

## Analysis Fault Information
Analysis Fault Data
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Poles
Total | 32 | 36 | 25 | 40 | 38 | 29 | 56 | 41 | 31 | 21
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 0 | 3 | 2 | 1 | 1 | 1 | 4 | 3 | 2 | 0
Egmont | 3 | 2 | 2 | 1 | 5 | 0 | 2 | 1 | 4 | 2
Kinleith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0
Manawatu | 0 | 1 | 1 | 5 | 0 | 3 | 1 | 1 | 2 | 0
Mt Maunganui | 0 | 1 | 1 | 3 | 1 | 1 | 0 | 0 | 1 | 0
Rangitikei | 1 | 1 | 0 | 1 | 3 | 3 | 4 | 3 | 1 | 1
Taranaki | 3 | 4 | 2 | 1 | 9 | 4 | 2 | 6 | 2 | 2
Tararua | 3 | 3 | 2 | 3 | 6 | 4 | 7 | 6 | 5 | 2
Tauranga | 3 | 2 | 2 | 4 | 0 | 1 | 1 | 1 | 3 | 1
Waikato | 2 | 1 | 1 | 3 | 1 | 1 | 2 | 1 | 3 | 2
Waikino | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2
Wairarapa | 16 | 14 | 9 | 17 | 11 | 11 | 30 | 14 | 7 | 7
Whanganui | 1 | 3 | 3 | 1 | 1 | 0 | 1 | 3 | 1 | 2
Xarms
Total | 408 | 366 | 357 | 424 | 507 | 423 | 461 | 377 | 378 | 464
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 25 | 35 | 19 | 20 | 19 | 26 | 29 | 26 | 23 | 21
Egmont | 30 | 37 | 46 | 42 | 73 | 40 | 90 | 66 | 43 | 71
Kinleith | 4 | 1 | 1 | 5 | 0 | 3 | 3 | 3 | 3 | 5
Manawatu | 44 | 38 | 54 | 53 | 67 | 42 | 42 | 45 | 37 | 51
Mt Maunganui | 13 | 19 | 13 | 15 | 16 | 17 | 16 | 9 | 12 | 15
Rangitikei | 19 | 16 | 24 | 27 | 29 | 30 | 20 | 20 | 14 | 27
Taranaki | 58 | 61 | 61 | 66 | 96 | 77 | 64 | 50 | 64 | 80
Tararua | 47 | 38 | 22 | 40 | 59 | 37 | 48 | 42 | 43 | 49
Tauranga | 26 | 18 | 16 | 25 | 33 | 20 | 23 | 19 | 25 | 28
Waikato | 44 | 35 | 35 | 44 | 41 | 53 | 29 | 15 | 44 | 25
Waikino | 26 | 18 | 10 | 12 | 10 | 6 | 13 | 8 | 6 | 2
Wairarapa | 51 | 36 | 38 | 48 | 38 | 41 | 62 | 50 | 42 | 53
Whanganui | 21 | 14 | 18 | 27 | 26 | 31 | 22 | 24 | 22 | 37
Conductor
Total | 202 | 141 | 214 | 269 | 312 | 151 | 233 | 236 | 259 | 273
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 7 | 8 | 13 | 14 | 6 | 11 | 14 | 17 | 11 | 9
Egmont | 27 | 24 | 37 | 19 | 69 | 25 | 36 | 37 | 35 | 49
Kinleith | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 0 | 1 | 2
Manawatu | 25 | 13 | 23 | 24 | 28 | 11 | 21 | 21 | 18 | 25
Mt Maunganui | 12 | 13 | 17 | 29 | 18 | 12 | 7 | 20 | 22 | 18
Rangitikei | 14 | 5 | 17 | 21 | 22 | 8 | 14 | 15 | 28 | 18
Taranaki | 27 | 11 | 28 | 33 | 57 | 21 | 32 | 25 | 37 | 44
Tararua | 11 | 15 | 18 | 17 | 25 | 13 | 16 | 21 | 15 | 7
Tauranga | 17 | 9 | 7 | 35 | 21 | 9 | 16 | 19 | 18 | 18
Waikato | 11 | 9 | 15 | 15 | 7 | 9 | 2 | 15 | 19 | 8
Waikino | 10 | 3 | 5 | 4 | 4 | 4 | 11 | 7 | 7 | 10
Wairarapa | 20 | 20 | 18 | 31 | 32 | 18 | 45 | 23 | 26 | 45
Whanganui | 19 | 9 | 14 | 26 | 21 | 7 | 17 | 16 | 22 | 20
Transformers
Total | 39 | 43 | 39 | 60 | 59 | 163 | 142 | 123 | 129 | 200
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 1 | 2 | 4 | 4 | 4 | 9 | 11 | 11 | 15 | 10
Egmont | 6 | 9 | 8 | 17 | 8 | 31 | 36 | 30 | 23 | 52
Kinleith | 1 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | 3 | 5
Manawatu | 0 | 1 | 0 | 6 | 7 | 19 | 14 | 9 | 6 | 20
Mt Maunganui | 0 | 3 | 3 | 5 | 4 | 9 | 8 | 5 | 9 | 5
Rangitikei | 4 | 1 | 1 | 1 | 2 | 12 | 5 | 5 | 4 | 8
Taranaki | 3 | 8 | 3 | 5 | 15 | 29 | 19 | 16 | 15 | 42
Tararua | 0 | 0 | 3 | 1 | 2 | 7 | 5 | 3 | 8 | 14
Tauranga | 7 | 5 | 4 | 8 | 2 | 10 | 10 | 13 | 13 | 13
Waikato | 8 | 10 | 6 | 4 | 5 | 15 | 11 | 5 | 18 | 8
Waikino | 1 | 1 | 1 | 3 | 1 | 2 | 6 | 4 | 5 | 1
Wairarapa | 7 | 1 | 4 | 3 | 4 | 12 | 14 | 13 | 6 | 15
Whanganui | 1 | 0 | 0 | 2 | 4 | 7 | 3 | 9 | 4 | 7
Fuses
Total | 65 | 88 | 89 | 96 | 78 | 103 | 101 | 461 | 662 | 755
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 4 | 4 | 6 | 3 | 2 | 5 | 8 | 32 | 45 | 49
Egmont | 5 | 8 | 15 | 18 | 10 | 17 | 20 | 66 | 64 | 86
Kinleith | 0 | 0 | 1 | 4 | 3 | 3 | 0 | 5 | 3 | 5
Manawatu | 7 | 5 | 7 | 18 | 11 | 12 | 6 | 38 | 42 | 64
Mt Maunganui | 6 | 4 | 3 | 3 | 7 | 0 | 7 | 13 | 27 | 24
Rangitikei | 6 | 5 | 2 | 3 | 6 | 9 | 6 | 55 | 63 | 64
Taranaki | 14 | 23 | 21 | 19 | 12 | 26 | 20 | 69 | 95 | 132
Tararua | 3 | 5 | 8 | 1 | 6 | 7 | 2 | 30 | 36 | 67
Tauranga | 5 | 9 | 6 | 15 | 7 | 8 | 15 | 27 | 73 | 40
Waikato | 9 | 11 | 7 | 3 | 4 | 5 | 1 | 21 | 53 | 23
Waikino | 1 | 4 | 4 | 2 | 2 | 1 | 3 | 9 | 26 | 31
Wairarapa | 3 | 6 | 8 | 6 | 5 | 7 | 11 | 60 | 74 | 100
Whanganui | 2 | 4 | 1 | 1 | 3 | 3 | 2 | 36 | 61 | 70
Sub-Trans
Total | 26 | 32 | 29 | 23 | 22 | 25 | 28 | 10 | 21 | 21
GXP | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 4 | 6 | 7 | 0 | 1 | 4 | 1 | 1 | 0 | 2
Egmont | 1 | 1 | 2 | 0 | 1 | 1 | 2 | 0 | 2 | 1
Kinleith | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 2
Manawatu | 3 | 3 | 1 | 1 | 2 | 2 | 2 | 0 | 4 | 5
Mt Maunganui | 1 | 0 | 4 | 7 | 0 | 0 | 2 | 1 | 1 | 1
Rangitikei | 1 | 2 | 2 | 1 | 2 | 5 | 0 | 2 | 2 | 0
Taranaki | 1 | 0 | 3 | 2 | 9 | 4 | 6 | 3 | 2 | 2
Tararua | 5 | 3 | 3 | 2 | 1 | 1 | 1 | 1 | 3 | 4
Tauranga | 0 | 5 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 0
Waikato | 6 | 1 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1
Waikino | 1 | 2 | 0 | 2 | 0 | 0 | 7 | 0 | 1 | 0
Wairarapa | 3 | 5 | 5 | 5 | 4 | 2 | 3 | 2 | 2 | 3
Whanganui | 0 | 4 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0
The rest of the equipment
Total | 81 | 109 | 124 | 111 | 93 | 83 | 126 | 110 | 102 | 118
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 5 | 11 | 8 | 9 | 5 | 4 | 9 | 13 | 3 | 7
Egmont | 2 | 5 | 6 | 7 | 4 | 2 | 17 | 10 | 11 | 11
Kinleith | 4 | 1 | 5 | 2 | 1 | 3 | 5 | 2 | 2 | 8
Manawatu | 16 | 24 | 34 | 20 | 27 | 21 | 21 | 18 | 12 | 13
Mt Maunganui | 3 | 4 | 7 | 10 | 5 | 5 | 11 | 6 | 4 | 13
Rangitikei | 4 | 5 | 3 | 1 | 2 | 1 | 4 | 5 | 4 | 3
Taranaki | 13 | 11 | 17 | 6 | 8 | 9 | 13 | 12 | 21 | 14
Tararua | 2 | 1 | 3 | 1 | 1 | 1 | 0 | 1 | 0 | 3
Tauranga | 15 | 24 | 10 | 26 | 16 | 11 | 19 | 23 | 21 | 24
Waikato | 4 | 13 | 7 | 7 | 5 | 11 | 5 | 4 | 11 | 5
Waikino | 6 | 1 | 7 | 4 | 7 | 4 | 7 | 2 | 5 | 5
Wairarapa | 5 | 7 | 9 | 11 | 5 | 6 | 10 | 6 | 5 | 7
Whanganui | 2 | 2 | 8 | 7 | 7 | 5 | 5 | 8 | 3 | 5
Vegetation
Total | 146 | 157 | 157 | 296 | 358 | 181 | 320 | 292 | 185 | 286
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 17 | 12 | 12 | 20 | 19 | 12 | 21 | 20 | 13 | 18
Egmont | 3 | 7 | 0 | 17 | 21 | 6 | 19 | 19 | 6 | 17
Kinleith | 5 | 2 | 2 | 2 | 4 | 1 | 3 | 1 | 3 | 2
Manawatu | 9 | 11 | 19 | 20 | 21 | 10 | 24 | 24 | 13 | 20
Mt Maunganui | 7 | 9 | 4 | 16 | 14 | 8 | 12 | 17 | 11 | 22
Rangitikei | 13 | 8 | 14 | 30 | 34 | 13 | 26 | 26 | 14 | 20
Taranaki | 18 | 20 | 30 | 54 | 59 | 19 | 32 | 25 | 25 | 42
Tararua | 3 | 6 | 11 | 10 | 20 | 9 | 14 | 19 | 15 | 12
Tauranga | 9 | 18 | 5 | 13 | 29 | 15 | 23 | 24 | 11 | 25
Waikato | 20 | 12 | 17 | 30 | 27 | 16 | 14 | 15 | 14 | 12
Waikino | 5 | 8 | 8 | 3 | 3 | 15 | 10 | 6 | 9 | 9
Wairarapa | 29 | 37 | 19 | 62 | 78 | 40 | 99 | 79 | 34 | 58
Whanganui | 8 | 7 | 16 | 19 | 29 | 17 | 23 | 17 | 17 | 29
Adverse Weather
Total | 290 | 384 | 184 | 230 | 206 | 154 | 264 | 427 | 196 | 458
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 43 | 29 | 3 | 16 | 7 | 1 | 19 | 34 | 17 | 15
Egmont | 48 | 32 | 26 | 17 | 26 | 11 | 28 | 68 | 14 | 69
Kinleith | 3 | 0 | 3 | 3 | 0 | 3 | 8 | 3 | 2 | 4
Manawatu | 20 | 54 | 17 | 21 | 20 | 10 | 25 | 24 | 12 | 47
Mt Maunganui | 7 | 12 | 5 | 12 | 4 | 5 | 7 | 22 | 20 | 7
Rangitikei | 16 | 21 | 25 | 22 | 13 | 7 | 23 | 35 | 13 | 40
Taranaki | 34 | 47 | 33 | 28 | 52 | 33 | 30 | 74 | 35 | 127
Tararua | 16 | 9 | 8 | 18 | 22 | 16 | 20 | 21 | 7 | 18
Tauranga | 17 | 34 | 20 | 36 | 9 | 6 | 30 | 32 | 9 | 8
Waikato | 16 | 72 | 6 | 17 | 11 | 20 | 13 | 26 | 24 | 6
Waikino | 13 | 36 | 0 | 7 | 4 | 5 | 12 | 6 | 7 | 5
Wairarapa | 41 | 32 | 30 | 21 | 21 | 26 | 33 | 49 | 16 | 46
Whanganui | 16 | 6 | 8 | 12 | 17 | 11 | 16 | 33 | 20 | 66
Unknown
Total | 219 | 267 | 301 | 384 | 371 | 273 | 268 | 396 | 513 | 502
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 17 | 19 | 23 | 28 | 17 | 13 | 13 | 34 | 22 | 22
Egmont | 8 | 16 | 18 | 19 | 25 | 22 | 22 | 51 | 33 | 38
Kinleith | 8 | 5 | 2 | 4 | 1 | 6 | 7 | 5 | 5 | 9
Manawatu | 31 | 45 | 57 | 58 | 69 | 23 | 50 | 51 | 55 | 66
Mt Maunganui | 7 | 7 | 8 | 9 | 15 | 8 | 12 | 9 | 27 | 9
Rangitikei | 10 | 18 | 16 | 27 | 46 | 15 | 15 | 29 | 51 | 48
Taranaki | 44 | 27 | 41 | 56 | 64 | 41 | 51 | 50 | 75 | 97
Tararua | 12 | 21 | 12 | 17 | 34 | 17 | 6 | 27 | 47 | 28
Tauranga | 31 | 30 | 30 | 43 | 18 | 29 | 25 | 27 | 41 | 37
Waikato | 15 | 28 | 40 | 48 | 20 | 23 | 17 | 11 | 39 | 30
Waikino | 7 | 6 | 10 | 9 | 7 | 3 | 4 | 9 | 10 | 11
Wairarapa | 24 | 29 | 27 | 46 | 41 | 42 | 28 | 60 | 64 | 66
Whanganui | 5 | 16 | 17 | 20 | 14 | 31 | 18 | 33 | 44 | 41
The remainder
Total | 321 | 336 | 296 | 264 | 291 | 296 | 240 | 282 | 351 | 398
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 28 | 16 | 20 | 9 | 18 | 20 | 18 | 17 | 17 | 14
Egmont | 10 | 17 | 21 | 15 | 11 | 17 | 30 | 22 | 24 | 42
Kinleith | 9 | 5 | 2 | 9 | 3 | 4 | 4 | 5 | 2 | 4
Manawatu | 40 | 41 | 43 | 39 | 19 | 29 | 20 | 27 | 32 | 43
Mt Maunganui | 18 | 20 | 19 | 10 | 21 | 18 | 10 | 11 | 14 | 23
Rangitikei | 12 | 11 | 12 | 8 | 18 | 19 | 10 | 23 | 32 | 37
Taranaki | 49 | 48 | 32 | 32 | 44 | 46 | 42 | 52 | 53 | 52
Tararua | 10 | 1 | 6 | 6 | 4 | 7 | 7 | 13 | 13 | 15
Tauranga | 43 | 59 | 35 | 49 | 56 | 37 | 30 | 34 | 42 | 40
Waikato | 43 | 55 | 42 | 41 | 31 | 28 | 16 | 14 | 51 | 21
Waikino | 13 | 7 | 18 | 3 | 10 | 13 | 8 | 15 | 14 | 19
Wairarapa | 28 | 42 | 21 | 26 | 27 | 40 | 24 | 32 | 43 | 57
Whanganui | 18 | 14 | 25 | 17 | 29 | 18 | 21 | 17 | 14 | 31
Totals
Total | 1829 | 1959 | 1815 | 2197 | 2335 | 1881 | 2239 | 2755 | 2827 | 3496
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Coromandel | 151 | 145 | 117 | 124 | 99 | 106 | 147 | 208 | 168 | 167
Egmont | 143 | 158 | 181 | 172 | 253 | 172 | 302 | 370 | 259 | 438
Kinleith | 36 | 18 | 20 | 32 | 15 | 27 | 32 | 26 | 26 | 46
Manawatu | 195 | 236 | 256 | 265 | 271 | 182 | 226 | 258 | 233 | 354
Mt Maunganui | 74 | 92 | 84 | 119 | 105 | 83 | 92 | 113 | 148 | 137
Rangitikei | 100 | 93 | 116 | 142 | 177 | 122 | 127 | 218 | 226 | 266
Taranaki | 264 | 260 | 271 | 302 | 425 | 309 | 311 | 382 | 424 | 634
Tararua | 112 | 102 | 96 | 116 | 180 | 119 | 126 | 184 | 192 | 219
Tauranga | 173 | 213 | 135 | 255 | 192 | 148 | 193 | 219 | 256 | 234
Waikato | 178 | 247 | 177 | 212 | 152 | 183 | 111 | 127 | 277 | 141
Waikino | 83 | 87 | 63 | 49 | 48 | 53 | 83 | 66 | 90 | 95
Wairarapa | 227 | 229 | 188 | 276 | 266 | 245 | 359 | 388 | 319 | 457
Whanganui | 93 | 79 | 111 | 133 | 152 | 132 | 130 | 196 | 209 | 308

## Retirement
Retirement Rates for Poles
Inputs
History is from the backcast from 2016
Asset retirements by Area - Poles
| Totals | 22511.1436 | 22347.6482 | 22168.8174 | 22078.6617 | 22141.5981 | 21761.2831 | 21516.0009 | 21254.0601 | 21253.9019 | 20981.1582 | 20900.2903 | 20881.4049 | 20100.7486 | 19563.9578 | 18994.5724 | 18299.4025 | 17688.136 | 17116.4371 | 16789.4097 | 16610.2917 | 16141.2405
Poles
|  | History | [8 empty] | Forecast - residual retirement
|  | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Coromandel | 1167.4953 | 1130.1147 | 1118.3246 | 1094.266 | 1097.6868 | 1087.1468 | 1097.2773 | 1108.1226 | 1112.3576 | 1118.1888 | 1125.4926 | 1132.4146 | 1137.8826 | 1146.6891 | 1185.5978 | 1207.4472 | 1226.6699 | 1245.3785 | 1263.6112 | 1284.1398 | 1305.5895
| Egmont | 1187.94 | 1058.9436 | 1036.2631 | 968.7439 | 913.8721 | 758.2079 | 680.383 | 514.2362 | 369.5331 | 313.0416 | 260.407 | 165.1155 | 138.3979 | 115.2156 | 128.6748 | 135.9623 | 142.2303 | 155.4376 | 170.8023 | 184.6659 | 198.8012
| Kinleith | 339.9654 | 292.3833 | 167.5949 | 173.0025 | 177.0686 | 179.8434 | 170.8977 | 173.4524 | 169.3267 | 174.6596 | 181.1061 | 186.3077 | 193.0564 | 199.7445 | 203.5109 | 208.5136 | 215.0834 | 220.9783 | 227.0645 | 241.8062 | 252.9418
| Manawatu | 524.4596 | 509.5397 | 498.6917 | 483.7785 | 460.2989 | 431.7083 | 443.8344 | 436.1212 | 523.2834 | 730.9959 | 951.7092 | 1158.0515 | 1305.7551 | 1360.6642 | 1381.3498 | 1437.5311 | 1409.2373 | 1388.388 | 1370.8154 | 1318.5338 | 1262.1804
| Mt Maunganui | 1036.1328 | 1019.6805 | 985.6389 | 957.0399 | 963.8055 | 897.8816 | 905.9788 | 864.6863 | 798.8767 | 794.7992 | 796.0711 | 809.5154 | 821.9695 | 799.4529 | 788.3499 | 652.058 | 570.9354 | 527.4341 | 493.8879 | 469.2599 | 444.2565
| Rangitikei | 3938.3412 | 3936.8746 | 4003.81 | 3885.6302 | 3915.3819 | 3868.6267 | 3803.3786 | 3782.6537 | 3821.7551 | 3718.5169 | 3625.6134 | 3726.9209 | 3370.9218 | 3339.0485 | 3116.0305 | 2859.2899 | 2614.6618 | 2397.0243 | 2348.2629 | 2393.0949 | 2320.6145
| Taranaki | 1334.7503 | 1335.7461 | 1335.195 | 1351.1382 | 1323.8513 | 1334.945 | 1346.3745 | 1339.1615 | 1356.7986 | 1372.3858 | 1417.9721 | 1448.636 | 1467.9868 | 1436.6269 | 1448.0664 | 1420.2081 | 1425.2202 | 1389.7164 | 1358.7383 | 1399.7801 | 1436.7872
| Tararua | 1612.0958 | 1611.7343 | 1576.5989 | 1601.0666 | 1626.8692 | 1632.7765 | 1652.9371 | 1693.9824 | 1726.6655 | 1739.8213 | 1730.0085 | 1717.1227 | 1693.2605 | 1614.2896 | 1517.8949 | 1427.3964 | 1321.0174 | 1252.3833 | 1181.593 | 1178.1059 | 1130.8854
| Tauranga | 1733.6378 | 1738.3713 | 1679.169 | 1631.296 | 1595.6669 | 1526.7617 | 1538.4479 | 1479.1362 | 1440.9248 | 1298.429 | 1292.9317 | 1305.4321 | 1129.5511 | 1016.6034 | 915.4563 | 847.3299 | 786.6589 | 730.2919 | 683.38 | 649.8031 | 614.6481
| Waikato | 2143.8059 | 2117.1441 | 2149.9321 | 2161.9125 | 2191.6224 | 2202.2139 | 2227.9387 | 2202.4366 | 2213.1368 | 2290.9358 | 2369.813 | 2440.5198 | 2522.8671 | 2584.43 | 2653.37 | 2704.1966 | 2756.0306 | 2805.4926 | 2846.8864 | 2879.3632 | 2912.4418
| Waikino | 572.8864 | 580.2083 | 588.0497 | 599.2568 | 611.6216 | 617.334 | 620.8713 | 597.793 | 597.4902 | 592.7323 | 605.8208 | 605.7401 | 617.729 | 629.3371 | 641.0241 | 650.7895 | 660.9165 | 670.129 | 677.9795 | 684.5264 | 690.8822
| Wairarapa | 4937.2454 | 5017.0508 | 4998.943 | 5106.27 | 5180.5359 | 5159.105 | 5048.7753 | 5061.0026 | 5149.5571 | 4863.6182 | 4584.8367 | 4261.4849 | 3864.46 | 3546.0386 | 3246.8797 | 2963.8446 | 2712.9451 | 2495.2892 | 2336.5712 | 2179.3594 | 2034.5193
| Whanganui | 1982.3876 | 1999.8568 | 2030.6065 | 2065.2606 | 2083.3169 | 2064.7324 | 1978.9064 | 2001.2753 | 1974.1963 | 1973.0336 | 1958.5082 | 1924.1436 | 1836.9109 | 1775.8176 | 1768.3672 | 1784.8354 | 1846.5292 | 1838.494 | 1829.8173 | 1747.853 | 1536.6926
Asset retirements by Area - Xarms
| Totals | 46656.7956 | 47715.265 | 49146.0752 | 50383.6383 | 50657.5101 | 50088.5914 | 49447.6497 | 48886.5099 | 51896.8343 | 52829.0903 | 53932.4733 | 54212.1268 | 54248.7678 | 53729.205 | 52830.2015 | 51481.5768 | 50484.4764 | 50231.9853 | 49965.9409 | 49815.7778 | 49513.5578
Xarms
|  | History | [8 empty] | Forecast - residual retirement
|  | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Coromandel | 2847.809 | 2738.0362 | 2664.5002 | 2514.6223 | 2450.1254 | 2276.1953 | 2166.2914 | 2055.6957 | 2197.1599 | 2257.7259 | 2317.9145 | 2375.8062 | 2414.4879 | 2431.1884 | 2439.0784 | 2425.3812 | 2420.98 | 2424.1647 | 2404.4833 | 2385.2094 | 2371.9996
| Egmont | 3164.9117 | 3344.2604 | 3503.2277 | 3608.166 | 3702.7082 | 3808.501 | 3724.6385 | 3618.6562 | 3828.0512 | 3880.7767 | 3973.2248 | 3906.3587 | 3859.9388 | 3731.9891 | 3608.1818 | 3510.0291 | 3351.7706 | 3482.6113 | 3543.4996 | 3586.6901 | 3582.6355
| Kinleith | 722.3207 | 547.0716 | 543.0025 | 567.3867 | 571.3839 | 566.0322 | 556.4208 | 547.7549 | 576.1364 | 596.9186 | 614.165 | 627.0776 | 640.3369 | 635.9633 | 621.6894 | 601.1852 | 585.6278 | 574.0829 | 560.8192 | 543.0451 | 521.1508
| Manawatu | 5113.1257 | 5391.9983 | 5713.562 | 6019.9023 | 6207.0979 | 6354.3035 | 6438.3698 | 6222.3667 | 6563.1263 | 6701.2234 | 6842.408 | 6931.5393 | 6965.9024 | 6834.9554 | 6664.7926 | 6428.203 | 6274.2866 | 6216.1666 | 6187.325 | 6142.5543 | 6122.5802
| Mt Maunganui | 1792.2536 | 1772.4048 | 1704.5711 | 1757.7819 | 1532.0847 | 1454.2939 | 1340.4067 | 1157.4766 | 1201.685 | 1179.8866 | 1178.2965 | 1143.7554 | 1071.0177 | 1026.6909 | 930.2331 | 831.3598 | 734.3614 | 640.0371 | 550.6835 | 480.9707 | 408.9039
| Rangitikei | 4183.0332 | 4334.2717 | 4405.4612 | 4568.5246 | 4807.0025 | 4802.0824 | 4692.1419 | 4853.1245 | 5154.9284 | 5131.4616 | 5128.9661 | 5011.0469 | 4876.8161 | 4886.8245 | 5013.4169 | 5078.6421 | 5144.2384 | 5240.4783 | 5383.2763 | 5479.7876 | 5569.9296
| Taranaki | 8324.3092 | 8692.6421 | 9073.1912 | 9347.5231 | 9644.7807 | 9865.1486 | 10105.2407 | 10361.3867 | 10872.4767 | 11169.2536 | 11453.2145 | 11593.8161 | 11737.5647 | 11425.8871 | 10842.9123 | 10212.6322 | 9700.5735 | 9436.6576 | 9248.2288 | 9004.2095 | 8772.9388
| Tararua | 1818.4776 | 1833.695 | 1917.0572 | 2061.0901 | 2159.9402 | 2111.3524 | 2171.9393 | 2208.7954 | 2377.5946 | 2444.9067 | 2510.859 | 2536.8284 | 2554.2547 | 2584.9021 | 2640.6218 | 2649.1577 | 2689.1874 | 2779.3119 | 2836.6015 | 2875.7069 | 2931.8498
| Tauranga | 3070.7832 | 2909.5955 | 2924.7798 | 2860.0923 | 2573.3112 | 2317.2319 | 2074.5971 | 1823.5696 | 1992.8894 | 1886.2832 | 1807.423 | 1677.1515 | 1538.2385 | 1499.8877 | 1376.0308 | 1229.4042 | 1126.4854 | 1027.4065 | 896.7715 | 801.6409 | 712.8989
| Waikato | 6616.4088 | 6889.4571 | 7019.1128 | 7001.9165 | 6768.3284 | 6525.3035 | 6200.2197 | 5841.2783 | 6145.9153 | 6179.6293 | 6231.6635 | 6184.1352 | 6108.2364 | 6017.7909 | 5958.1557 | 5840.9069 | 5784.7049 | 5724.6913 | 5627.7964 | 5509.848 | 5387.13
| Waikino | 1697.7393 | 1643.3948 | 1679.9459 | 1714.2395 | 1693.977 | 1474.9459 | 1339.8009 | 1297.6667 | 1359.0152 | 1394.7939 | 1429.1248 | 1449.1669 | 1462.6744 | 1457.1811 | 1440.53 | 1409.8615 | 1382.2714 | 1357.1133 | 1324.2496 | 1288.4065 | 1249.2534
| Wairarapa | 4553.5556 | 4685.9637 | 4900.4097 | 5072.7243 | 5122.0185 | 5117.7608 | 5113.7311 | 5333.2903 | 5796.2536 | 6008.3233 | 6295.8198 | 6497.3537 | 6657.6148 | 6802.8414 | 6902.9192 | 6935.4634 | 7025.1543 | 7109.6627 | 7202.032 | 7527.651 | 7715.3178
| Whanganui | 2752.0682 | 2932.4741 | 3097.254 | 3289.6687 | 3424.7516 | 3415.4399 | 3523.8517 | 3565.4482 | 3831.6022 | 3997.9078 | 4149.3938 | 4278.0911 | 4361.6844 | 4393.103 | 4391.6394 | 4329.3504 | 4264.8347 | 4219.6009 | 4200.1742 | 4190.0577 | 4166.9698
Asset retirements by Area - Distribution transformers
| Totals | 4879.4036 | 4640.323 | 4490.8433 | 4371.5592 | 4223.5295 | 4096.5199 | 3881.2371 | 3642.7488 | 3584.4776 | 3579.2645 | 3618.6096 | 3648.8154 | 3701.169 | 3745.1973 | 3791.4434 | 3827.1201 | 3881.5332 | 3957.8658 | 4000.3464 | 4059.7915 | 4118.3258
Distribution Transformers
|  | History | [8 empty] | Forecast - residual retirement
|  | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Coromandel | 255.0996 | 229.5084 | 204.8304 | 201.1558 | 186.2755 | 171.8174 | 157.8107 | 132.5594 | 121.8375 | 123.1394 | 127.5717 | 133.0759 | 136.6859 | 141.9033 | 148.0612 | 152.7297 | 162.5926 | 172.6353 | 176.7493 | 181.9435 | 186.7856
| Egmont | 393.154 | 364.0339 | 349.8155 | 314.0466 | 281.3621 | 264.7654 | 221.606 | 184.1456 | 161.4861 | 153.3675 | 151.7212 | 146.5331 | 142.0674 | 136.1317 | 129.7171 | 129.6851 | 127.7609 | 130.6748 | 129.2098 | 129.9825 | 128.0809
| Kinleith | 78.9885 | 64.8278 | 54.0361 | 52.6285 | 50.7326 | 45.6844 | 42.4786 | 40.4533 | 40.9693 | 41.3236 | 42.1411 | 44.0442 | 45.4258 | 49.0906 | 51.0588 | 54.4424 | 55.8631 | 57.8761 | 59.074 | 60.2329 | 60.4114
| Manawatu | 360.0171 | 345.2361 | 353.5308 | 355.528 | 350.4883 | 341.7974 | 327.7226 | 301.898 | 303.7584 | 311.2245 | 320.3828 | 332.3041 | 345.2199 | 360.1489 | 380.0733 | 390.9891 | 403.8107 | 416.7027 | 432.6919 | 446.7337 | 455.471
| Mt Maunganui | 197.6717 | 188.3999 | 177.5425 | 164.8972 | 156.9413 | 150.6287 | 142.6266 | 133.0429 | 131.5644 | 131.4908 | 134.0047 | 137.2428 | 142.0411 | 144.6235 | 146.1607 | 149.8455 | 151.4953 | 158.2886 | 162.4706 | 168.7806 | 175.8837
| Rangitikei | 460.55 | 458.9995 | 467.6834 | 467.6979 | 464.7387 | 463.9599 | 462.3433 | 455.9201 | 469.2009 | 468.439 | 468.7644 | 467.3055 | 465.5738 | 464.6858 | 462.3517 | 458.9356 | 454.1667 | 451.5583 | 448.5178 | 447.0496 | 443.9496
| Taranaki | 712.6996 | 688.6934 | 670.6483 | 639.611 | 613.5684 | 591.0604 | 541.7651 | 503.0653 | 481.1994 | 478.9489 | 484.9421 | 483.9518 | 484.4989 | 482.1557 | 483.5543 | 480.2657 | 485.5758 | 500.351 | 514.0283 | 516.1265 | 533.228
| Tararua | 139.476 | 136.483 | 137.4725 | 138.0542 | 144.4226 | 145.3938 | 151.8411 | 162.7963 | 163.1838 | 161.415 | 160.7375 | 161.7881 | 161.5117 | 167.6882 | 174.1723 | 179.5412 | 185.0473 | 189.3083 | 191.4254 | 193.9858 | 202.3352
| Tauranga | 465.6137 | 439.8345 | 391.3536 | 374.6441 | 356.1667 | 347.3447 | 334.706 | 300.4171 | 294.3834 | 294.5431 | 303.6536 | 309.7042 | 328.0656 | 337.6915 | 338.1221 | 344.6344 | 354.7242 | 374.4188 | 384.6181 | 398.9436 | 418.2755
| Waikato | 513.147 | 459.2887 | 428.0378 | 417.2335 | 401.148 | 365.7461 | 340.4981 | 313.4433 | 308.2553 | 309.2916 | 314.8697 | 321.7753 | 331.609 | 338.8881 | 350.3446 | 359.1544 | 379.9162 | 393.6657 | 396.1371 | 410.564 | 412.2339
| Waikino | 103.8667 | 93.1611 | 81.9076 | 73.0248 | 69.1431 | 68.0785 | 59.5358 | 53.056 | 49.1961 | 49.542 | 52.0781 | 57.4739 | 62.8569 | 66.8522 | 75.2912 | 79.7176 | 84.0881 | 86.6926 | 89.7211 | 94.1877 | 97.1436
| Wairarapa | 821.7359 | 800.0432 | 795.9473 | 805.261 | 791.5167 | 785.2323 | 754.7084 | 725.5667 | 723.8296 | 719.6506 | 717.7264 | 715.6021 | 718.0682 | 718.2096 | 718.4194 | 714.2364 | 707.3202 | 698.2797 | 691.3408 | 686.8102 | 684.0813
| Whanganui | 377.3839 | 371.8136 | 378.0373 | 367.7765 | 357.0254 | 355.0109 | 343.5949 | 336.3848 | 335.6134 | 336.8885 | 340.0164 | 338.0144 | 337.5448 | 337.1283 | 334.1164 | 332.9429 | 329.1722 | 327.4139 | 324.3623 | 324.4507 | 320.4461
Asset retirements by Area - Fuses
| Totals | 6618.5064 | 6639.4512 | 6651.3148 | 6672.9034 | 6671.1869 | 6655.0277 | 6537.6043 | 6309.0895 | 6203.445 | 6251.2519 | 6332.5981 | 6415.2791 | 6445.4076 | 6495.6419 | 6517.8814 | 6529.0049 | 6550.1693 | 6666.8828 | 6784.378 | 6837.7464 | 6898.3997
Distribution Transformers
|  | History | [8 empty] | Forecast - residual retirement
|  | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Coromandel | 330.5194 | 320.8626 | 316.3662 | 323.9893 | 325.5673 | 322.9873 | 308.0899 | 302.268 | 293.4371 | 301.8661 | 317.7324 | 329.1632 | 335.1956 | 345.5976 | 353.7313 | 361.2149 | 365.4548 | 373.9056 | 382.089 | 390.4124 | 399.0615
| Egmont | 429.9551 | 426.7661 | 440.0905 | 441.3902 | 443.4681 | 431.9851 | 410.1216 | 366.2136 | 350.4597 | 354.8002 | 357.9296 | 374.2553 | 377.9896 | 384.5581 | 387.284 | 394.2469 | 398.9244 | 423.9706 | 441.5939 | 450.2176 | 459.3349
| Kinleith | 93.1884 | 83.1958 | 57.705 | 57.1382 | 56.6043 | 55.2193 | 53.4099 | 55.6829 | 53.6428 | 54.848 | 55.7567 | 56.8301 | 56.6839 | 56.685 | 56.0929 | 55.6618 | 56.1064 | 56.4978 | 57.0395 | 57.7529 | 58.4495
| Manawatu | 437.3108 | 450.7481 | 456.9287 | 451.8324 | 450.4607 | 446.6651 | 441.1353 | 388.6244 | 368.722 | 367.5974 | 367.4691 | 367.7317 | 368.7888 | 371.5529 | 371.0884 | 377.0495 | 383.0467 | 424.4869 | 435.6171 | 443.8311 | 451.9512
| Mt Maunganui | 370.1596 | 379.8661 | 383.9831 | 377.032 | 385.1183 | 373.7122 | 364.1667 | 349.497 | 316.0425 | 316.1205 | 315.8674 | 319.14 | 321.0013 | 322.8918 | 324.7015 | 322.0158 | 322.1821 | 321.73 | 322.0837 | 322.8769 | 325.5938
| Rangitikei | 721.1668 | 727.9245 | 745.7299 | 760.477 | 769.0331 | 776.2721 | 771.2114 | 759.3298 | 765.6731 | 761.8795 | 760.2079 | 756.1919 | 752.7204 | 751.5859 | 746.3059 | 740.7666 | 735.1687 | 727.3049 | 717.2773 | 708.0691 | 698.7312
| Taranaki | 944.3132 | 962.4462 | 961.378 | 962.9986 | 955.0513 | 964.1993 | 952.4708 | 917.1351 | 906.5349 | 928.0486 | 948.4485 | 966.8738 | 974.8065 | 976.7011 | 980.0508 | 980.5048 | 986.3841 | 998.4748 | 1046.5999 | 1058.4364 | 1068.1702
| Tararua | 282.838 | 277.4532 | 277.3629 | 269.6839 | 271.5675 | 266.3303 | 268.3809 | 275.3082 | 282.6732 | 263.3155 | 260.5226 | 256.3046 | 250.9798 | 248.0446 | 244.1647 | 241.427 | 239.6146 | 258.3484 | 257.5328 | 255.2499 | 251.904
| Tauranga | 737.4231 | 751.3799 | 759.4698 | 756.2584 | 753.4499 | 744.6008 | 741.1523 | 708.5705 | 687.9798 | 693.5911 | 701.4077 | 717.4903 | 722.767 | 728.6302 | 735.6118 | 737.3167 | 742.4755 | 745.7754 | 749.347 | 752.0104 | 758.8671
| Waikato | 776.8105 | 758.864 | 755.544 | 744.6427 | 723.6394 | 691.7427 | 663.8826 | 627.2263 | 598.6132 | 608.7532 | 633.9569 | 648.9134 | 654.1003 | 665.8771 | 667.4815 | 669.095 | 673.1679 | 680.0111 | 688.0496 | 695.4128 | 707.7513
| Waikino | 153.9992 | 151.9236 | 149.0389 | 147.6701 | 154.7227 | 160.9371 | 154.62 | 155.0082 | 159.1299 | 165.7684 | 170.0452 | 174.0046 | 177.3157 | 182.8979 | 185.708 | 188.2362 | 189.6636 | 192.8291 | 196.4884 | 198.1827 | 201.147
| Wairarapa | 796.1527 | 799.6945 | 788.744 | 813.2088 | 814.101 | 841.6861 | 837.6618 | 841.6062 | 857.5848 | 871.4093 | 880.9886 | 890.2564 | 896.668 | 901.5099 | 909.3793 | 910.3998 | 913.3801 | 925.3512 | 960.0943 | 984.2028 | 1002.0051
| Whanganui | 544.6695 | 548.3267 | 558.9739 | 566.5818 | 568.403 | 578.6903 | 571.3011 | 562.6193 | 562.9518 | 563.2539 | 562.2654 | 558.1238 | 556.3909 | 559.1097 | 556.2813 | 551.0697 | 544.6004 | 538.1971 | 530.5656 | 521.0915 | 515.4331

## Model parameters
Forecast parameters
|  |  |  | Trend Impact | Note: method changed for determining ICP numbers in 2009. Therefore only average from 2009 onwards
| Faults |  | Duration | 0.2 | ICP Numbers
Poles
need to update to 2017 as base year
| Faults |  | Duration |  | ICP Numbers
Approach | Fault Rate |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Fault Rate | Average | Trend Impact | Weighted average
| Coromandel | 0.0011137 | 177.9348 | 0.2 | 238.1176
| Egmont | 0.0032213 | 120.5115 | 0.2 | 100.7368
| Kinleith | 0.0011137 | 76.3765 | 0.2 | 374.5
| Manawatu | 0.0011137 | 158.3246 | 0.2 | 436.7723
| Mt Maunganui | 0.0011137 | 148.1342 | 0.2 | 211.6229
| Rangitikei | 0.0011137 | 391.368 | 0.2 | 89.7637
| Taranaki | 0.0011137 | 274.8877 | 0.2 | 123.4662
| Tararua | 0.0032213 | 98.4955 | 0.2 | 65.0513
| Tauranga | 0.0011137 | 250.5602 | 0.2 | 364.7234
| Waikato | 0.0011137 | 176.8008 | 0.2 | 161.0583
| Waikino | 0.0011137 | 376.249 | 0.2 | 242.8
| Wairarapa | 0.0032213 | 214.7459 | 0.2 | 93.1828
| Whanganui | 0.0011137 | 304.6972 | 0.2 | 61
Xarms
| Faults |  | Duration |  | ICP Numbers
Approach | Fault Rate |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Fault Rate | Average | Trend Impact | Weighted average
| Coromandel | 0.0066108 | 76.4064 | 0.2 | 206.8464
| Egmont | 0.011181 | 106.9181 | 0.2 | 128.4281
| Kinleith | 0.0066108 | 137.6699 | 0.2 | 66.8743
| Manawatu | 0.0066108 | 81.2271 | 0.2 | 222.727
| Mt Maunganui | 0.011181 | 76.9014 | 0.2 | 136.8532
| Rangitikei | 0.0066108 | 130.1485 | 0.2 | 158.3932
| Taranaki | 0.0066108 | 91.6886 | 0.2 | 216.5808
| Tararua | 0.019715 | 126.4812 | 0.2 | 89.2555
| Tauranga | 0.011181 | 71.579 | 0.2 | 241.3313
| Waikato | 0.0066108 | 74.875 | 0.2 | 147.526
| Waikino | 0.0066108 | 79.0389 | 0.2 | 298.2769
| Wairarapa | 0.0066108 | 100.1559 | 0.2 | 96.3494
| Whanganui | 0.0066108 | 85.2449 | 0.2 | 239.7202
Conductors
| Faults |  | Duration |  | ICP Numbers
Approach | Average adjusted for failure rate analysis |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Average | Average | Trend Impact | Weighted average
| Coromandel | 11.875 | 147.0089 | 0.2 | 302.0845
| Egmont | 38.375 | 154.1799 | 0.2 | 141.9489
| Kinleith | 1.625 | 131.9654 | 0.2 | 178.5942
| Manawatu | 21.375 | 81.6147 | 0.2 | 380.2201
| Mt Maunganui | 17.875 | 134.5451 | 0.2 | 232.8949
| Rangitikei | 17.875 | 175.7067 | 0.2 | 150.7158
| Taranaki | 34.625 | 191.1881 | 0.2 | 225.985
| Tararua | 16.5 | 246.7087 | 0.2 | 96.5233
| Tauranga | 17.875 | 106.4555 | 0.2 | 419.8059
| Waikato | 11.25 | 102.3354 | 0.2 | 246.2507
| Waikino | 6.5 | 121.7778 | 0.2 | 389.8864
| Wairarapa | 29.75 | 190.131 | 0.2 | 139.1818
| Whanganui | 17.875 | 229.3659 | 0.2 | 196.802
Transformers
| Faults |  | Duration |  | ICP Numbers
Approach | Fault Rate |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Fault Rate | Average | Trend Impact | Average | Weighted average
| Coromandel | 0.12311 | 196.286 | 0.2 | 79.4855
| Egmont | 0.12311 | 81.0794 | 0.2 | 61.7141
| Kinleith | 0.05609 | 74.8998 | 0.2 | 159.0663
| Manawatu | 0.05609 | 317.1228 | 0.2 | 79.1444
| Mt Maunganui | 0.05609 | 243.3102 | 0.2 | 36.4705
| Rangitikei | 0.015952 | 293.4239 | 0.2 | 69.229
| Taranaki | 0.015952 | 118.9747 | 0.2 | 45.5456
| Tararua | 0.05609 | 114.9445 | 0.2 | 30.8128
| Tauranga | 0.05609 | 308.8717 | 0.2 | 65.4353
| Waikato | 0.05609 | 341.068 | 0.2 | 61.414
| Waikino | 0.12311 | 177.6026 | 0.2 | 41.0833
| Wairarapa | 0.015952 | 173.0864 | 0.2 | 71.722
| Whanganui | 0.015952 | 115.6266 | 0.2 | 112.7456
Fuses
| Faults |  | Duration |  | ICP Numbers
Approach | Fault Rate |  | Average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Fault Rate | Average | Trend Impact | Weighted average
| Coromandel | 0.18262 | 88.5854 | 0.2 | 45.6621
| Egmont | 0.18262 | 80.3872 | 0.2 | 36.8445
| Kinleith | 0.091161 | 49.3757 | 0.2 | 57.3327
| Manawatu | 0.091161 | 81.7287 | 0.2 | 60.4627
| Mt Maunganui | 0.091161 | 44.7128 | 0.2 | 26.75
| Rangitikei | 0.091161 | 108.8327 | 0.2 | 25.1969
| Taranaki | 0.091161 | 94.9229 | 0.2 | 43.6926
| Tararua | 0.091161 | 79.2534 | 0.2 | 22.123
| Tauranga | 0.013039 | 52.6065 | 0.2 | 65.3992
| Waikato | 0.013039 | 65.4187 | 0.2 | 27.7577
| Waikino | 0.091161 | 152.0156 | 0.2 | 40.4998
| Wairarapa | 0.091161 | 69.4503 | 0.2 | 39.036
| Whanganui | 0.091161 | 181.0274 | 0.2 | 17.453
Sub-Trans
| Faults |  | Duration |  | ICP Numbers
Approach | Averaged from 2008 |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Average | Average | Trend Impact | Average | Weighted average
| Coromandel | 2.6 | 91.948 | 0.2 | 2628.0928 | 4384.1337
| Egmont | 1.1 | 120.7589 | 0.2 | 951.8933 | 1195.7932
| Kinleith | 0.5 | 119.0581 | 0.2 | 954.5 | 3260.6
| Manawatu | 2.3 | 102.1853 | 0.2 | 2012.3604 | 1969.967
| Mt Maunganui | 1.7 | 128.4962 | 0.2 | 1840.8107 | 1656.4374
| Rangitikei | 1.7 | 105.2941 | 0.2 | 942.4271 | 1239.8348
| Taranaki | 3.2 | 70.1007 | 0.2 | 913.5695 | 937.2796
| Tararua | 2.4 | 73.9086 | 0.2 | 700.2912 | 593.1015
| Tauranga | 1 | 49.2491 | 0.2 | 2239.7465 | 4426.773
| Waikato | 1.3 | 26.0632 | 0.2 | 1011.1453 | 1279.2724
| Waikino | 1.3 | 109.251 | 0.2 | 2679.3571 | 5427.4167
| Wairarapa | 3.4 | 81.1688 | 0.2 | 1402.1221 | 1380.5379
| Whanganui | 1.2 | 61.7017 | 0.2 | 1424.7212 | 1548.8271
The rest of the equipment
| Faults |  | Duration |  | ICP Numbers
Approach | Averaged from 2008 |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | co-efficent | Average | Trend Impact | Weighted average
| Coromandel | 7.4 | 103.3265 | 0.2 | 633.7151
| Egmont | 7.5 | 92.6871 | 0.2 | 321.0601
| Kinleith | 3.3 | 89.1787 | 0.2 | 567.6231
| Manawatu | 20.6 | 70.767 | 0.2 | 769.577
| Mt Maunganui | 6.8 | 179.5629 | 0.2 | 183.31
| Rangitikei | 3.2 | 118.8356 | 0.2 | 375.3832
| Taranaki | 12.4 | 69.794 | 0.2 | 334.263
| Tararua | 1.3 | 137.4603 | 0.2 | 84.4839
| Tauranga | 18.9 | 80.6166 | 0.2 | 440.3662
| Waikato | 7.2 | 75.1677 | 0.2 | 423.6333
| Waikino | 4.8 | 82.5672 | 0.2 | 979.3441
| Wairarapa | 7.1 | 81.5584 | 0.2 | 259.2586
| Whanganui | 5.2 | 88.2093 | 0.2 | 405.6927
Vegetation
Moderator: | 0.9
Area | Faults |  | Duration |  | ICP Numbers
Approach | Average adjusted for reactive tree count |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | co-efficent | Average | Trend Impact | Weighted average
| Coromandel | 16.2222 | 110.3782 | 0.2 | 635.0426
| Egmont | 10.8889 | 249.9287 | 0.2 | 228.8017
| Kinleith | 2.5556 | 100.3796 | 0.2 | 258.1117
| Manawatu | 16.7778 | 77.6682 | 0.2 | 468.3039
| Mt Maunganui | 10.8889 | 140.7872 | 0.2 | 303.5146
| Rangitikei | 19.7778 | 149.0668 | 0.2 | 196.5296
| Taranaki | 31.3333 | 154.7165 | 0.2 | 295.9223
| Tararua | 11.8889 | 127.4512 | 0.2 | 106.8713
| Tauranga | 16.3333 | 98.4041 | 0.2 | 560.266
| Waikato | 18.3333 | 87.9079 | 0.2 | 280.6024
| Waikino | 7.4444 | 108.9524 | 0.2 | 330.5272
| Wairarapa | 53 | 161.765 | 0.2 | 194.5872
| Whanganui | 17 | 290.099 | 0.2 | 305.5787
Adverse Weather
| Faults |  | Duration |  | ICP Numbers
Approach | Averaged from 2008 |  | Average 2010 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2010 to 2017 average
Co-efficents | Planning Area | Average | Average | Trend Impact | Average
| Coromandel | 18.4 | 79.3205 | 0.2 | 657.2323
| Egmont | 33.9 | 157.008 | 0.2 | 251.3709
| Kinleith | 2.9 | 119.8826 | 0.2 | 178.8275
| Manawatu | 25 | 102.3756 | 0.2 | 289.9773
| Mt Maunganui | 10.1 | 124.508 | 0.2 | 194.0001
| Rangitikei | 21.5 | 198.4333 | 0.2 | 207.3803
| Taranaki | 49.3 | 117.9576 | 0.2 | 190.4325
| Tararua | 15.5 | 148.1536 | 0.2 | 126.6998
| Tauranga | 20.1 | 95.0067 | 0.2 | 548.2395
| Waikato | 21.1 | 99.8898 | 0.2 | 224.4203
| Waikino | 9.5 | 158.155 | 0.2 | 534.9019
| Wairarapa | 31.5 | 122.3654 | 0.2 | 172.0733
| Whanganui | 20.5 | 196.4227 | 0.2 | 286.2842
Unknown
Vegetation Moderator: | 0.5
.
| Faults |  | Duration |  | ICP Numbers
Approach | linear trend with scaler | 0.8 | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Average | Average | Trend Impact | Weighted average
| Coromandel | 0.8 | 48.592 | 0.2 | 853.0444
| Egmont | 0.8 | 58.2602 | 0.2 | 383.5892
| Kinleith | 0.8 | 58.1228 | 0.2 | 609.2043
| Manawatu | 0.8 | 47.3021 | 0.2 | 478.3766
| Mt Maunganui | 0.8 | 48.0905 | 0.2 | 462.6232
| Rangitikei | 0.8 | 49.1152 | 0.2 | 334.3698
| Taranaki | 0.8 | 50.7676 | 0.2 | 434.7151
| Tararua | 0.8 | 54.5029 | 0.2 | 282.0905
| Tauranga | 0.8 | 47.3888 | 0.2 | 807.1898
| Waikato | 0.8 | 46.0429 | 0.2 | 361.0492
| Waikino | 0.8 | 65.354 | 0.2 | 622.7608
| Wairarapa | 0.8 | 66.7402 | 0.2 | 277.7383
| Whanganui | 0.8 | 71.3927 | 0.2 | 626.7411
The remainder
| Faults |  | Duration |  | ICP Numbers
Approach | Averaged from 2008 |  | Weighted average 2009 to 2017 with moderated trend | 0.2 | Regional growth rates applied to 2009 to 2017 weighted average
Co-efficents | Planning Area | Average | Average | Trend Impact | Weighted average
| Coromandel | 17.7 | 97.3514 | 0.2 | 794.1679
| Egmont | 20.9 | 71.4421 | 0.2 | 300.2569
| Kinleith | 4.7 | 72.1213 | 0.2 | 808.6144
| Manawatu | 33.3 | 40.7564 | 0.2 | 690.6274
| Mt Maunganui | 16.4 | 105.5687 | 0.2 | 274.8812
| Rangitikei | 18.2 | 97.4172 | 0.2 | 249.6258
| Taranaki | 45 | 67.1869 | 0.2 | 443.4366
| Tararua | 8.2 | 60.8878 | 0.2 | 212.6331
| Tauranga | 42.5 | 72.6262 | 0.2 | 691.8328
| Waikato | 34.2 | 96.318 | 0.2 | 236.0668
| Waikino | 12 | 112.407 | 0.2 | 515.8424
| Wairarapa | 34 | 78.3193 | 0.2 | 266.0234
| Whanganui | 20.4 | 91.0196 | 0.2 | 570.9244

## Modelled Faults
Forecast Faults
| Faults | [20 empty] | Linear trend
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Poles
| History | [9 empty] | Forecast | Fault Rate | [9 empty] | Linear trend
Total | 32 | 36 | 25 | 40 | 38 | 29 | 56 | 41 | 31 | 21
Forecast | [10 empty] | 37.135 | 36.2045 | 34.3917 | 32.9075 | 31.4681 | 29.9219 | 28.5014 | 27.2891 | 26.4736 | 25.9646 | 25.0673 | [10 empty] | 34.4 | 34.3091 | 34.2182 | 34.1273 | 34.0364 | 33.9455 | 33.8545 | 33.7636 | 33.6727 | 33.5818 | 33.4909
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0 | 3 | 2 | 1 | 1 | 1 | 4 | 3 | 2 | 0 | 1.2535 | 1.2612 | 1.2673 | 1.2771 | 1.3204 | 1.3448 | 1.3662 | 1.387 | 1.4073 | 1.4302 | 1.4541 | 0 | 3 | 2 | 1 | 1 | 1 | 4 | 3 | 2 | 0 | 1.9333 | 1.9758 | 2.0182 | 2.0606 | 2.103 | 2.1455 | 2.1879 | 2.2303 | 2.2727 | 2.3152 | 2.3576
Egmont | 3 | 2 | 2 | 1 | 5 | 0 | 2 | 1 | 4 | 2 | 0.83884 | 0.53188 | 0.44582 | 0.37114 | 0.4145 | 0.43797 | 0.45816 | 0.50071 | 0.5502 | 0.59486 | 0.64039 | 3 | 2 | 2 | 1 | 5 | 0 | 2 | 1 | 4 | 2 | 2.1333 | 2.1212 | 2.1091 | 2.097 | 2.0848 | 2.0727 | 2.0606 | 2.0485 | 2.0364 | 2.0242 | 2.0121
Kinleith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.2017 | 0.2075 | 0.21501 | 0.22246 | 0.22666 | 0.23223 | 0.23955 | 0.24611 | 0.25289 | 0.26931 | 0.28171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0.53333 | 0.59394 | 0.65455 | 0.71515 | 0.77576 | 0.83636 | 0.89697 | 0.95758 | 1.0182 | 1.0788 | 1.1394
Manawatu | 0 | 1 | 1 | 5 | 0 | 3 | 1 | 1 | 2 | 0 | 1.06 | 1.2898 | 1.4543 | 1.5154 | 1.5385 | 1.601 | 1.5695 | 1.5463 | 1.5267 | 1.4685 | 1.4057 | 0 | 1 | 1 | 5 | 0 | 3 | 1 | 1 | 2 | 0 | 1.3333 | 1.3212 | 1.3091 | 1.297 | 1.2848 | 1.2727 | 1.2606 | 1.2485 | 1.2364 | 1.2242 | 1.2121
Mt Maunganui | 0 | 1 | 1 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0.88661 | 0.90158 | 0.91545 | 0.89038 | 0.87801 | 0.72622 | 0.63587 | 0.58742 | 0.55006 | 0.52263 | 0.49478 | 0 | 1 | 1 | 3 | 1 | 1 | 0 | 0 | 1 | 0 | 0.33333 | 0.24848 | 0.16364 | 0.078788 | -0.0060606 | -0.090909 | -0.17576 | -0.26061 | -0.34545 | -0.4303 | -0.51515
Rangitikei | 1 | 1 | 0 | 1 | 3 | 3 | 4 | 3 | 1 | 1 | 4.038 | 4.1508 | 3.7543 | 3.7188 | 3.4704 | 3.1845 | 2.912 | 2.6696 | 2.6153 | 2.6653 | 2.5845 | 1 | 1 | 0 | 1 | 3 | 3 | 4 | 3 | 1 | 1 | 2.6 | 2.7455 | 2.8909 | 3.0364 | 3.1818 | 3.3273 | 3.4727 | 3.6182 | 3.7636 | 3.9091 | 4.0545
Taranaki | 3 | 4 | 2 | 1 | 9 | 4 | 2 | 6 | 2 | 2 | 1.5792 | 1.6134 | 1.6349 | 1.6 | 1.6128 | 1.5817 | 1.5873 | 1.5478 | 1.5133 | 1.559 | 1.6002 | 3 | 4 | 2 | 1 | 9 | 4 | 2 | 6 | 2 | 2 | 3.3333 | 3.303 | 3.2727 | 3.2424 | 3.2121 | 3.1818 | 3.1515 | 3.1212 | 3.0909 | 3.0606 | 3.0303
Tararua | 3 | 3 | 2 | 3 | 6 | 4 | 7 | 6 | 5 | 2 | 5.5728 | 5.5313 | 5.4545 | 5.2001 | 4.8896 | 4.598 | 4.2554 | 4.0343 | 3.8062 | 3.795 | 3.6429 | 3 | 3 | 2 | 3 | 6 | 4 | 7 | 6 | 5 | 2 | 5.2667 | 5.4788 | 5.6909 | 5.903 | 6.1152 | 6.3273 | 6.5394 | 6.7515 | 6.9636 | 7.1758 | 7.3879
Tauranga | 3 | 2 | 2 | 4 | 0 | 1 | 1 | 1 | 3 | 1 | 1.44 | 1.4539 | 1.258 | 1.1322 | 1.0196 | 0.9437 | 0.87613 | 0.81335 | 0.7611 | 0.72371 | 0.68455 | 3 | 2 | 2 | 4 | 0 | 1 | 1 | 1 | 3 | 1 | 1 | 0.85455 | 0.70909 | 0.56364 | 0.41818 | 0.27273 | 0.12727 | -0.018182 | -0.16364 | -0.30909 | -0.45455
Waikato | 2 | 1 | 1 | 3 | 1 | 1 | 2 | 1 | 3 | 2 | 2.6393 | 2.7181 | 2.8098 | 2.8784 | 2.9551 | 3.0118 | 3.0695 | 3.1246 | 3.1707 | 3.2068 | 3.2437 | 2 | 1 | 1 | 3 | 1 | 1 | 2 | 1 | 3 | 2 | 2.0667 | 2.1333 | 2.2 | 2.2667 | 2.3333 | 2.4 | 2.4667 | 2.5333 | 2.6 | 2.6667 | 2.7333
Waikino | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0.67472 | 0.67463 | 0.68799 | 0.70091 | 0.71393 | 0.72481 | 0.73608 | 0.74634 | 0.75509 | 0.76238 | 0.76946 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 1.0667 | 1.1697 | 1.2727 | 1.3758 | 1.4788 | 1.5818 | 1.6848 | 1.7879 | 1.8909 | 1.9939 | 2.097
Wairarapa | 16 | 14 | 9 | 17 | 11 | 11 | 30 | 14 | 7 | 7 | 14.769 | 13.7274 | 12.4485 | 11.4228 | 10.4591 | 9.5474 | 8.7392 | 8.038 | 7.5268 | 7.0203 | 6.5538 | 16 | 14 | 9 | 17 | 11 | 11 | 30 | 14 | 7 | 7 | 11.4 | 11 | 10.6 | 10.2 | 9.8 | 9.4 | 9 | 8.6 | 8.2 | 7.8 | 7.4
Whanganui | 1 | 3 | 3 | 1 | 1 | 0 | 1 | 3 | 1 | 2 | 2.1813 | 2.143 | 2.0458 | 1.9778 | 1.9695 | 1.9878 | 2.0565 | 2.0476 | 2.0379 | 1.9466 | 1.7115 | 1 | 3 | 3 | 1 | 1 | 0 | 1 | 3 | 1 | 2 | 1.4 | 1.3636 | 1.3273 | 1.2909 | 1.2545 | 1.2182 | 1.1818 | 1.1455 | 1.1091 | 1.0727 | 1.0364
Xarms
| History | [9 empty] | Forecast | Fault Rate | [9 empty] | Linear trend
Total | 408 | 366 | 357 | 424 | 507 | 423 | 461 | 377 | 378 | 464
Forecast | [10 empty] | 421.2453 | 422.3755 | 421.6667 | 417.6709 | 410.8852 | 400.511 | 392.8069 | 392.0329 | 390.2977 | 389.2615 | 387.2458 | [10 empty] | 440.3333 | 444.6667 | 449 | 453.3333 | 457.6667 | 462 | 466.3333 | 470.6667 | 475 | 479.3333 | 483.6667
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 25 | 35 | 19 | 20 | 19 | 26 | 29 | 26 | 23 | 21 | 15.3233 | 15.706 | 15.9617 | 16.0721 | 16.1243 | 16.0337 | 16.0046 | 16.0257 | 15.8956 | 15.7682 | 15.6808 | 25 | 35 | 19 | 20 | 19 | 26 | 29 | 26 | 23 | 21 | 22.6 | 22.2909 | 21.9818 | 21.6727 | 21.3636 | 21.0545 | 20.7455 | 20.4364 | 20.1273 | 19.8182 | 19.5091
Egmont | 30 | 37 | 46 | 42 | 73 | 40 | 90 | 66 | 43 | 71 | 44.4251 | 43.6774 | 43.1584 | 41.7278 | 40.3435 | 39.246 | 37.4765 | 38.9395 | 39.6203 | 40.1032 | 40.0579 | 30 | 37 | 46 | 42 | 73 | 40 | 90 | 66 | 43 | 71 | 74.5333 | 78.303 | 82.0727 | 85.8424 | 89.6121 | 93.3818 | 97.1515 | 100.9212 | 104.6909 | 108.4606 | 112.2303
Kinleith | 4 | 1 | 1 | 5 | 0 | 3 | 3 | 3 | 3 | 5 | 4.0601 | 4.1455 | 4.2331 | 4.2042 | 4.1099 | 3.9743 | 3.8715 | 3.7952 | 3.7075 | 3.59 | 3.4452 | 4 | 1 | 1 | 5 | 0 | 3 | 3 | 3 | 3 | 5 | 3.8 | 3.9818 | 4.1636 | 4.3455 | 4.5273 | 4.7091 | 4.8909 | 5.0727 | 5.2545 | 5.4364 | 5.6182
Manawatu | 44 | 38 | 54 | 53 | 67 | 42 | 42 | 45 | 37 | 51 | 45.2339 | 45.8231 | 46.0503 | 45.1846 | 44.0597 | 42.4956 | 41.4781 | 41.0939 | 40.9032 | 40.6073 | 40.4752 | 44 | 38 | 54 | 53 | 67 | 42 | 42 | 45 | 37 | 51 | 45.7333 | 45.4485 | 45.1636 | 44.8788 | 44.5939 | 44.3091 | 44.0242 | 43.7394 | 43.4545 | 43.1697 | 42.8848
Mt Maunganui | 13 | 19 | 13 | 15 | 16 | 17 | 16 | 9 | 12 | 15 | 13.1747 | 12.7885 | 11.9752 | 11.4795 | 10.401 | 9.2955 | 8.211 | 7.1563 | 6.1573 | 5.3778 | 4.572 | 13 | 19 | 13 | 15 | 16 | 17 | 16 | 9 | 12 | 15 | 12.9333 | 12.6485 | 12.3636 | 12.0788 | 11.7939 | 11.5091 | 11.2242 | 10.9394 | 10.6545 | 10.3697 | 10.0848
Rangitikei | 19 | 16 | 24 | 27 | 29 | 30 | 20 | 20 | 14 | 27 | 33.9066 | 33.1271 | 32.2397 | 32.3059 | 33.1427 | 33.5739 | 34.0076 | 34.6438 | 35.5878 | 36.2258 | 36.8217 | 19 | 16 | 24 | 27 | 29 | 30 | 20 | 20 | 14 | 27 | 23.2 | 23.3091 | 23.4182 | 23.5273 | 23.6364 | 23.7455 | 23.8545 | 23.9636 | 24.0727 | 24.1818 | 24.2909
Taranaki | 58 | 61 | 61 | 66 | 96 | 77 | 64 | 50 | 64 | 80 | 75.715 | 76.6445 | 77.5948 | 75.5344 | 71.6804 | 67.5138 | 64.1287 | 62.384 | 61.1383 | 59.5251 | 57.9962 | 58 | 61 | 61 | 66 | 96 | 77 | 64 | 50 | 64 | 80 | 72.3333 | 73.1758 | 74.0182 | 74.8606 | 75.703 | 76.5455 | 77.3879 | 78.2303 | 79.0727 | 79.9152 | 80.7576
Tararua | 47 | 38 | 22 | 40 | 59 | 37 | 48 | 42 | 43 | 49 | 49.5023 | 50.0143 | 50.3579 | 50.9621 | 52.0606 | 52.2289 | 53.0181 | 54.7949 | 55.9244 | 56.6954 | 57.8022 | 47 | 38 | 22 | 40 | 59 | 37 | 48 | 42 | 43 | 49 | 47.6667 | 48.6061 | 49.5455 | 50.4848 | 51.4242 | 52.3636 | 53.303 | 54.2424 | 55.1818 | 56.1212 | 57.0606
Tauranga | 26 | 18 | 16 | 25 | 33 | 20 | 23 | 19 | 25 | 28 | 20.209 | 18.7524 | 17.1992 | 16.7704 | 15.3856 | 13.7461 | 12.5954 | 11.4875 | 10.0269 | 8.9632 | 7.971 | 26 | 18 | 16 | 25 | 33 | 20 | 23 | 19 | 25 | 28 | 25.4 | 25.7818 | 26.1636 | 26.5455 | 26.9273 | 27.3091 | 27.6909 | 28.0727 | 28.4545 | 28.8364 | 29.2182
Waikato | 44 | 35 | 35 | 44 | 41 | 53 | 29 | 15 | 44 | 25 | 41.1963 | 40.8821 | 40.3804 | 39.7825 | 39.3882 | 38.6131 | 38.2416 | 37.8448 | 37.2043 | 36.4246 | 35.6133 | 44 | 35 | 35 | 44 | 41 | 53 | 29 | 15 | 44 | 25 | 28.4667 | 27.0061 | 25.5455 | 24.0848 | 22.6242 | 21.1636 | 19.703 | 18.2424 | 16.7818 | 15.3212 | 13.8606
Waikino | 26 | 18 | 10 | 12 | 10 | 6 | 13 | 8 | 6 | 2 | 9.4477 | 9.5802 | 9.6695 | 9.6331 | 9.5231 | 9.3203 | 9.1379 | 8.9716 | 8.7544 | 8.5174 | 8.2586 | 26 | 18 | 10 | 12 | 10 | 6 | 13 | 8 | 6 | 2 | 0.73333 | -1.1515 | -3.0364 | -4.9212 | -6.8061 | -8.6909 | -10.5758 | -12.4606 | -14.3455 | -16.2303 | -18.1152
Wairarapa | 51 | 36 | 38 | 48 | 38 | 41 | 62 | 50 | 42 | 53 | 41.6205 | 42.9528 | 44.0122 | 44.9723 | 45.6339 | 45.849 | 46.442 | 47.0006 | 47.6113 | 49.7639 | 51.0045 | 51 | 36 | 38 | 48 | 38 | 41 | 62 | 50 | 42 | 53 | 51.4 | 52.4 | 53.4 | 54.4 | 55.4 | 56.4 | 57.4 | 58.4 | 59.4 | 60.4 | 61.4
Whanganui | 21 | 14 | 18 | 27 | 26 | 31 | 22 | 24 | 22 | 37 | 27.4309 | 28.2816 | 28.8343 | 29.042 | 29.0323 | 28.6205 | 28.194 | 27.895 | 27.7666 | 27.6997 | 27.547 | 21 | 14 | 18 | 27 | 26 | 31 | 22 | 24 | 22 | 37 | 31.5333 | 32.8667 | 34.2 | 35.5333 | 36.8667 | 38.2 | 39.5333 | 40.8667 | 42.2 | 43.5333 | 44.8667
Conductor
| History | [9 empty] | Forecast | Average adjusted for failure rate analysis | [9 empty] | Linear trend
Total | 202 | 141 | 214 | 269 | 312 | 151 | 233 | 236 | 259 | 273
Forecast | [10 empty] | 243.375 | 243.1378 | 241.1242 | 236.0929 | 230.0666 | 224.7234 | 219.3505 | 214.4432 | 209.6744 | 205.3076 | 205.3076 | [10 empty] | 272.5333 | 280.4485 | 288.3636 | 296.2788 | 304.1939 | 312.1091 | 320.0242 | 327.9394 | 335.8545 | 343.7697 | 351.6848
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 7 | 8 | 13 | 14 | 6 | 11 | 14 | 17 | 11 | 9 | 11.875 | 11.9845 | 12.0801 | 12.2006 | 12.2943 | 12.313 | 12.4653 | 12.4886 | 12.4743 | 12.4068 | 12.4068 | 7 | 8 | 13 | 14 | 6 | 11 | 14 | 17 | 11 | 9 | 13.1333 | 13.5212 | 13.9091 | 14.297 | 14.6848 | 15.0727 | 15.4606 | 15.8485 | 16.2364 | 16.6242 | 17.0121
Egmont | 27 | 24 | 37 | 19 | 69 | 25 | 36 | 37 | 35 | 49 | 38.375 | 38.5257 | 37.38 | 32.8515 | 30.6133 | 30.4104 | 30.1695 | 29.8997 | 28.7055 | 27.4009 | 27.4009 | 27 | 24 | 37 | 19 | 69 | 25 | 36 | 37 | 35 | 49 | 45.2 | 46.9091 | 48.6182 | 50.3273 | 52.0364 | 53.7455 | 55.4545 | 57.1636 | 58.8727 | 60.5818 | 62.2909
Kinleith | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 0 | 1 | 2 | 1.625 | 1.6331 | 1.6421 | 1.6519 | 1.6628 | 1.6742 | 1.6873 | 1.6941 | 1.6799 | 1.6706 | 1.6706 | 2 | 2 | 2 | 1 | 2 | 3 | 2 | 0 | 1 | 2 | 1.2667 | 1.1879 | 1.1091 | 1.0303 | 0.95152 | 0.87273 | 0.79394 | 0.71515 | 0.63636 | 0.55758 | 0.47879
Manawatu | 25 | 13 | 23 | 24 | 28 | 11 | 21 | 21 | 18 | 25 | 21.375 | 21.4102 | 21.6069 | 21.6204 | 21.7823 | 21.0903 | 21.2847 | 21.4164 | 21.0551 | 21.0873 | 21.0873 | 25 | 13 | 23 | 24 | 28 | 11 | 21 | 21 | 18 | 25 | 20.8667 | 20.8606 | 20.8545 | 20.8485 | 20.8424 | 20.8364 | 20.8303 | 20.8242 | 20.8182 | 20.8121 | 20.8061
Mt Maunganui | 12 | 13 | 17 | 29 | 18 | 12 | 7 | 20 | 22 | 18 | 17.875 | 17.9649 | 17.8371 | 17.7703 | 16.1954 | 15.0284 | 12.5458 | 10.2057 | 9.9983 | 9.5632 | 9.5632 | 12 | 13 | 17 | 29 | 18 | 12 | 7 | 20 | 22 | 18 | 18.8 | 19.1636 | 19.5273 | 19.8909 | 20.2545 | 20.6182 | 20.9818 | 21.3455 | 21.7091 | 22.0727 | 22.4364
Rangitikei | 14 | 5 | 17 | 21 | 22 | 8 | 14 | 15 | 28 | 18 | 17.875 | 17.8586 | 17.9975 | 18.1233 | 17.9927 | 17.9484 | 18.0335 | 18.2638 | 17.703 | 17.395 | 17.395 | 14 | 5 | 17 | 21 | 22 | 8 | 14 | 15 | 28 | 18 | 21.2667 | 22.1879 | 23.1091 | 24.0303 | 24.9515 | 25.8727 | 26.7939 | 27.7152 | 28.6364 | 29.5576 | 30.4788
Taranaki | 27 | 11 | 28 | 33 | 57 | 21 | 32 | 25 | 37 | 44 | 34.625 | 33.7408 | 32.3917 | 31.6089 | 30.3465 | 28.9528 | 28.2824 | 27.5483 | 26.2218 | 24.8476 | 24.8476 | 27 | 11 | 28 | 33 | 57 | 21 | 32 | 25 | 37 | 44 | 40.8667 | 42.5697 | 44.2727 | 45.9758 | 47.6788 | 49.3818 | 51.0848 | 52.7879 | 54.4909 | 56.1939 | 57.897
Tararua | 11 | 15 | 18 | 17 | 25 | 13 | 16 | 21 | 15 | 7 | 16.5 | 16.661 | 16.9009 | 16.8896 | 16.9786 | 17.1624 | 17.4403 | 17.7724 | 17.9352 | 17.6702 | 17.6702 | 11 | 15 | 18 | 17 | 25 | 13 | 16 | 21 | 15 | 7 | 14.6 | 14.3818 | 14.1636 | 13.9455 | 13.7273 | 13.5091 | 13.2909 | 13.0727 | 12.8545 | 12.6364 | 12.4182
Tauranga | 17 | 9 | 7 | 35 | 21 | 9 | 16 | 19 | 18 | 18 | 17.875 | 17.9489 | 17.7484 | 17.743 | 16.8357 | 15.3504 | 13.0866 | 10.2832 | 10.1542 | 10.0434 | 10.0434 | 17 | 9 | 7 | 35 | 21 | 9 | 16 | 19 | 18 | 18 | 19 | 19.3818 | 19.7636 | 20.1455 | 20.5273 | 20.9091 | 21.2909 | 21.6727 | 22.0545 | 22.4364 | 22.8182
Waikato | 11 | 9 | 15 | 15 | 7 | 9 | 2 | 15 | 19 | 8 | 11.25 | 11.3485 | 11.4568 | 11.5612 | 11.6509 | 11.7182 | 11.8207 | 11.931 | 11.7613 | 11.6681 | 11.6681 | 11 | 9 | 15 | 15 | 7 | 9 | 2 | 15 | 19 | 8 | 11.2 | 11.2364 | 11.2727 | 11.3091 | 11.3455 | 11.3818 | 11.4182 | 11.4545 | 11.4909 | 11.5273 | 11.5636
Waikino | 10 | 3 | 5 | 4 | 4 | 4 | 11 | 7 | 7 | 10 | 6.5 | 6.5841 | 6.6651 | 6.7614 | 6.8508 | 6.9672 | 7.0474 | 7.171 | 7.1507 | 7.2865 | 7.2865 | 10 | 3 | 5 | 4 | 4 | 4 | 11 | 7 | 7 | 10 | 8.4667 | 8.8242 | 9.1818 | 9.5394 | 9.897 | 10.2545 | 10.6121 | 10.9697 | 11.3273 | 11.6848 | 12.0424
Wairarapa | 20 | 20 | 18 | 31 | 32 | 18 | 45 | 23 | 26 | 45 | 29.75 | 29.592 | 29.5729 | 29.8071 | 29.4278 | 29.7501 | 29.4679 | 29.6575 | 29.3032 | 29.299 | 29.299 | 20 | 20 | 18 | 31 | 32 | 18 | 45 | 23 | 26 | 45 | 38.4667 | 40.4061 | 42.3455 | 44.2848 | 46.2242 | 48.1636 | 50.103 | 52.0424 | 53.9818 | 55.9212 | 57.8606
Whanganui | 19 | 9 | 14 | 26 | 21 | 7 | 17 | 16 | 22 | 20 | 17.875 | 17.8856 | 17.8447 | 17.5037 | 17.4356 | 16.3575 | 16.0191 | 16.1116 | 15.532 | 14.9688 | 14.9688 | 19 | 9 | 14 | 26 | 21 | 7 | 17 | 16 | 22 | 20 | 19.4 | 19.8182 | 20.2364 | 20.6545 | 21.0727 | 21.4909 | 21.9091 | 22.3273 | 22.7455 | 23.1636 | 23.5818
Transformers
| History | [9 empty] | Forecast | Fault Rate | [9 empty] | Linear trend
Total | 39 | 43 | 39 | 60 | 59 | 163 | 142 | 123 | 129 | 200
Forecast | [10 empty] | 144.4425 | 146.7835 | 149.9909 | 152.8208 | 156.1132 | 159.2059 | 163.4902 | 168.7598 | 171.4972 | 175.6838 | 179.0705 | [10 empty] | 193.7333 | 210.8303 | 227.9273 | 245.0242 | 262.1212 | 279.2182 | 296.3152 | 313.4121 | 330.5091 | 347.6061 | 364.703
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 1 | 2 | 4 | 4 | 4 | 9 | 11 | 11 | 15 | 10 | 15.706 | 16.3836 | 16.8281 | 17.4704 | 18.2285 | 18.8033 | 20.0176 | 21.254 | 21.7605 | 22.3999 | 22.9961 | 1 | 2 | 4 | 4 | 4 | 9 | 11 | 11 | 15 | 10 | 14.8667 | 16.2788 | 17.6909 | 19.103 | 20.5152 | 21.9273 | 23.3394 | 24.7515 | 26.1636 | 27.5758 | 28.9879
Egmont | 6 | 9 | 8 | 17 | 8 | 31 | 36 | 30 | 23 | 52 | 18.6791 | 18.0404 | 17.4906 | 16.7598 | 15.9701 | 15.9662 | 15.7293 | 16.088 | 15.9076 | 16.0028 | 15.7687 | 6 | 9 | 8 | 17 | 8 | 31 | 36 | 30 | 23 | 52 | 45.4 | 49.6545 | 53.9091 | 58.1636 | 62.4182 | 66.6727 | 70.9273 | 75.1818 | 79.4364 | 83.6909 | 87.9455
Kinleith | 1 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | 3 | 5 | 2.3637 | 2.4705 | 2.548 | 2.7535 | 2.8639 | 3.0537 | 3.1334 | 3.2463 | 3.3135 | 3.3785 | 3.3885 | 1 | 2 | 2 | 1 | 1 | 1 | 0 | 0 | 3 | 5 | 2.6 | 2.7818 | 2.9636 | 3.1455 | 3.3273 | 3.5091 | 3.6909 | 3.8727 | 4.0545 | 4.2364 | 4.4182
Manawatu | 0 | 1 | 0 | 6 | 7 | 19 | 14 | 9 | 6 | 20 | 17.9704 | 18.6391 | 19.3635 | 20.2009 | 21.3185 | 21.9308 | 22.6499 | 23.3731 | 24.2699 | 25.0575 | 25.5476 | 0 | 1 | 0 | 6 | 7 | 19 | 14 | 9 | 6 | 20 | 18.0667 | 19.8606 | 21.6545 | 23.4485 | 25.2424 | 27.0364 | 28.8303 | 30.6242 | 32.4182 | 34.2121 | 36.0061
Mt Maunganui | 0 | 3 | 3 | 5 | 4 | 9 | 8 | 5 | 9 | 5 | 7.5164 | 7.698 | 7.9672 | 8.112 | 8.1982 | 8.4049 | 8.4974 | 8.8785 | 9.1131 | 9.467 | 9.8654 | 0 | 3 | 3 | 5 | 4 | 9 | 8 | 5 | 9 | 5 | 8.8 | 9.4727 | 10.1455 | 10.8182 | 11.4909 | 12.1636 | 12.8364 | 13.5091 | 14.1818 | 14.8545 | 15.5273
Rangitikei | 4 | 1 | 1 | 1 | 2 | 12 | 5 | 5 | 4 | 8 | 7.4776 | 7.4543 | 7.4267 | 7.4126 | 7.3753 | 7.3208 | 7.2448 | 7.2032 | 7.1547 | 7.1312 | 7.0818 | 4 | 1 | 1 | 1 | 2 | 12 | 5 | 5 | 4 | 8 | 7.6 | 8.2 | 8.8 | 9.4 | 10 | 10.6 | 11.2 | 11.8 | 12.4 | 13 | 13.6
Taranaki | 3 | 8 | 3 | 5 | 15 | 29 | 19 | 16 | 15 | 42 | 7.7357 | 7.7199 | 7.7286 | 7.6912 | 7.7135 | 7.6611 | 7.7458 | 7.9815 | 8.1997 | 8.2331 | 8.5059 | 3 | 8 | 3 | 5 | 15 | 29 | 19 | 16 | 15 | 42 | 32.8667 | 36.0242 | 39.1818 | 42.3394 | 45.497 | 48.6545 | 51.8121 | 54.9697 | 58.1273 | 61.2848 | 64.4424
Tararua | 0 | 0 | 3 | 1 | 2 | 7 | 5 | 3 | 8 | 14 | 9.0158 | 9.0748 | 9.0593 | 9.4057 | 9.7694 | 10.0706 | 10.3794 | 10.6184 | 10.7371 | 10.8808 | 11.3491 | 0 | 0 | 3 | 1 | 2 | 7 | 5 | 3 | 8 | 14 | 10.9333 | 12.1394 | 13.3455 | 14.5515 | 15.7576 | 16.9636 | 18.1697 | 19.3758 | 20.5818 | 21.7879 | 22.9939
Tauranga | 7 | 5 | 4 | 8 | 2 | 10 | 10 | 13 | 13 | 13 | 17.0321 | 17.3715 | 18.4014 | 18.9413 | 18.9654 | 19.3307 | 19.8966 | 21.0013 | 21.5734 | 22.3769 | 23.4613 | 7 | 5 | 4 | 8 | 2 | 10 | 10 | 13 | 13 | 13 | 14.1333 | 15.1576 | 16.1818 | 17.2061 | 18.2303 | 19.2545 | 20.2788 | 21.303 | 22.3273 | 23.3515 | 24.3758
Waikato | 8 | 10 | 6 | 4 | 5 | 15 | 11 | 5 | 18 | 8 | 17.6612 | 18.0485 | 18.6001 | 19.0084 | 19.651 | 20.1451 | 21.3097 | 22.0809 | 22.2195 | 23.0287 | 23.1224 | 8 | 10 | 6 | 4 | 5 | 15 | 11 | 5 | 18 | 8 | 11.7333 | 12.2303 | 12.7273 | 13.2242 | 13.7212 | 14.2182 | 14.7152 | 15.2121 | 15.7091 | 16.2061 | 16.703
Waikino | 1 | 1 | 1 | 3 | 1 | 2 | 6 | 4 | 5 | 1 | 6.4116 | 7.0759 | 7.7386 | 8.2305 | 9.2695 | 9.8144 | 10.3525 | 10.6731 | 11.046 | 11.5959 | 11.9598 | 1 | 1 | 1 | 3 | 1 | 2 | 6 | 4 | 5 | 1 | 4.2667 | 4.5879 | 4.9091 | 5.2303 | 5.5515 | 5.8727 | 6.1939 | 6.5152 | 6.8364 | 7.1576 | 7.4788
Wairarapa | 7 | 1 | 4 | 3 | 4 | 12 | 14 | 13 | 6 | 15 | 11.449 | 11.4151 | 11.4545 | 11.4567 | 11.4601 | 11.3933 | 11.283 | 11.1388 | 11.0281 | 10.9558 | 10.9123 | 7 | 1 | 4 | 3 | 4 | 12 | 14 | 13 | 6 | 15 | 14.3333 | 15.503 | 16.6727 | 17.8424 | 19.0121 | 20.1818 | 21.3515 | 22.5212 | 23.6909 | 24.8606 | 26.0303
Whanganui | 1 | 0 | 0 | 2 | 4 | 7 | 3 | 9 | 4 | 7 | 5.4239 | 5.3919 | 5.3844 | 5.3778 | 5.3297 | 5.311 | 5.2509 | 5.2228 | 5.1742 | 5.1756 | 5.1117 | 1 | 0 | 0 | 2 | 4 | 7 | 3 | 9 | 4 | 7 | 8.1333 | 8.9394 | 9.7455 | 10.5515 | 11.3576 | 12.1636 | 12.9697 | 13.7758 | 14.5818 | 15.3879 | 16.1939
Fuses
| History | [9 empty] | Forecast | Fault Rate | [9 empty] | Linear trend
Total | 65 | 88 | 89 | 96 | 78 | 103 | 101 | 461 | 662 | 755
Forecast | [10 empty] | 534.7576 | 542.4085 | 545.2309 | 549.9843 | 552.3341 | 554.4101 | 556.4338 | 569.3446 | 581.5088 | 587.1405 | 592.795 | [10 empty] | 654.0667 | 727.5697 | 801.0727 | 874.5758 | 948.0788 | 1021.5818 | 1095.0848 | 1168.5879 | 1242.0909 | 1315.5939 | 1389.097
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 4 | 4 | 6 | 3 | 2 | 5 | 8 | 32 | 45 | 49 | 58.0234 | 60.1109 | 61.2125 | 63.1121 | 64.5974 | 65.9641 | 66.7384 | 68.2816 | 69.776 | 71.296 | 72.8755 | 4 | 4 | 6 | 3 | 2 | 5 | 8 | 32 | 45 | 49 | 43.8 | 48.8909 | 53.9818 | 59.0727 | 64.1636 | 69.2545 | 74.3455 | 79.4364 | 84.5273 | 89.6182 | 94.7091
Egmont | 5 | 8 | 15 | 18 | 10 | 17 | 20 | 66 | 64 | 86 | 65.3641 | 68.3455 | 69.0274 | 70.2269 | 70.7247 | 71.9963 | 72.8505 | 77.4243 | 80.6427 | 82.2175 | 83.8825 | 5 | 8 | 15 | 18 | 10 | 17 | 20 | 66 | 64 | 86 | 77.2 | 85.6182 | 94.0364 | 102.4545 | 110.8727 | 119.2909 | 127.7091 | 136.1273 | 144.5455 | 152.9636 | 161.3818
Kinleith | 0 | 0 | 1 | 4 | 3 | 3 | 0 | 5 | 3 | 5 | 5.0828 | 5.1807 | 5.1674 | 5.1675 | 5.1135 | 5.0742 | 5.1147 | 5.1504 | 5.1998 | 5.2648 | 5.3283 | 0 | 0 | 1 | 4 | 3 | 3 | 0 | 5 | 3 | 5 | 4.8667 | 5.3152 | 5.7636 | 6.2121 | 6.6606 | 7.1091 | 7.5576 | 8.0061 | 8.4545 | 8.903 | 9.3515
Manawatu | 7 | 5 | 7 | 18 | 11 | 12 | 6 | 38 | 42 | 64 | 33.4988 | 33.5228 | 33.6191 | 33.8711 | 33.8288 | 34.3722 | 34.9189 | 38.6966 | 39.7113 | 40.46 | 41.2003 | 7 | 5 | 7 | 18 | 11 | 12 | 6 | 38 | 42 | 64 | 50.7333 | 56.1394 | 61.5455 | 66.9515 | 72.3576 | 77.7636 | 83.1697 | 88.5758 | 93.9818 | 99.3879 | 104.7939
Mt Maunganui | 6 | 4 | 3 | 3 | 7 | 0 | 7 | 13 | 27 | 24 | 28.7948 | 29.0931 | 29.2628 | 29.4351 | 29.6001 | 29.3553 | 29.3704 | 29.3292 | 29.3614 | 29.4338 | 29.6814 | 6 | 4 | 3 | 3 | 7 | 0 | 7 | 13 | 27 | 24 | 22 | 24.2909 | 26.5818 | 28.8727 | 31.1636 | 33.4545 | 35.7455 | 38.0364 | 40.3273 | 42.6182 | 44.9091
Rangitikei | 6 | 5 | 2 | 3 | 6 | 9 | 6 | 55 | 63 | 64 | 69.3012 | 68.9351 | 68.6187 | 68.5153 | 68.0339 | 67.529 | 67.0186 | 66.3018 | 65.3876 | 64.5482 | 63.697 | 6 | 5 | 2 | 3 | 6 | 9 | 6 | 55 | 63 | 64 | 62.0667 | 69.3697 | 76.6727 | 83.9758 | 91.2788 | 98.5818 | 105.8848 | 113.1879 | 120.4909 | 127.7939 | 135.097
Taranaki | 14 | 23 | 21 | 19 | 12 | 26 | 20 | 69 | 95 | 132 | 86.4614 | 88.1411 | 88.8642 | 89.037 | 89.3423 | 89.3837 | 89.9197 | 91.0219 | 95.409 | 96.488 | 97.3754 | 14 | 23 | 21 | 19 | 12 | 26 | 20 | 69 | 95 | 132 | 103.8667 | 114.9152 | 125.9636 | 137.0121 | 148.0606 | 159.1091 | 170.1576 | 181.2061 | 192.2545 | 203.303 | 214.3515
Tararua | 3 | 5 | 8 | 1 | 6 | 7 | 2 | 30 | 36 | 67 | 23.7495 | 23.365 | 22.8795 | 22.612 | 22.2583 | 22.0087 | 21.8435 | 23.5513 | 23.4769 | 23.2688 | 22.9638 | 3 | 5 | 8 | 1 | 6 | 7 | 2 | 30 | 36 | 67 | 46.7333 | 52.2303 | 57.7273 | 63.2242 | 68.7212 | 74.2182 | 79.7152 | 85.2121 | 90.7091 | 96.2061 | 101.703
Tauranga | 5 | 9 | 6 | 15 | 7 | 8 | 15 | 27 | 73 | 40 | 9.1456 | 9.3553 | 9.4241 | 9.5005 | 9.5916 | 9.6138 | 9.6811 | 9.7241 | 9.7707 | 9.8054 | 9.8948 | 5 | 9 | 6 | 15 | 7 | 8 | 15 | 27 | 73 | 40 | 49.4667 | 54.7333 | 60 | 65.2667 | 70.5333 | 75.8 | 81.0667 | 86.3333 | 91.6 | 96.8667 | 102.1333
Waikato | 9 | 11 | 7 | 3 | 4 | 5 | 1 | 21 | 53 | 23 | 8.2661 | 8.4611 | 8.5287 | 8.6823 | 8.7032 | 8.7243 | 8.7774 | 8.8666 | 8.9714 | 9.0674 | 9.2283 | 9 | 11 | 7 | 3 | 4 | 5 | 1 | 21 | 53 | 23 | 29.8667 | 32.8061 | 35.7455 | 38.6848 | 41.6242 | 44.5636 | 47.503 | 50.4424 | 53.3818 | 56.3212 | 59.2606
Waikino | 1 | 4 | 4 | 2 | 2 | 1 | 3 | 9 | 26 | 31 | 15.5015 | 15.8624 | 16.1643 | 16.6731 | 16.9293 | 17.1598 | 17.2899 | 17.5785 | 17.9121 | 18.0665 | 18.3367 | 1 | 4 | 4 | 2 | 2 | 1 | 3 | 9 | 26 | 31 | 23.3333 | 26.0667 | 28.8 | 31.5333 | 34.2667 | 37 | 39.7333 | 42.4667 | 45.2 | 47.9333 | 50.6667
Wairarapa | 3 | 6 | 8 | 6 | 5 | 7 | 11 | 60 | 74 | 100 | 80.3117 | 81.1566 | 81.7411 | 82.1825 | 82.8998 | 82.9929 | 83.2646 | 84.3559 | 87.5231 | 89.7208 | 91.3437 | 3 | 6 | 8 | 6 | 5 | 7 | 11 | 60 | 74 | 100 | 82.2 | 92.0545 | 101.9091 | 111.7636 | 121.6182 | 131.4727 | 141.3273 | 151.1818 | 161.0364 | 170.8909 | 180.7455
Whanganui | 2 | 4 | 1 | 1 | 3 | 3 | 2 | 36 | 61 | 70 | 51.2566 | 50.8791 | 50.7211 | 50.969 | 50.7111 | 50.236 | 49.6463 | 49.0625 | 48.3668 | 47.5032 | 46.9874 | 2 | 4 | 1 | 1 | 3 | 3 | 2 | 36 | 61 | 70 | 57.9333 | 65.1394 | 72.3455 | 79.5515 | 86.7576 | 93.9636 | 101.1697 | 108.3758 | 115.5818 | 122.7879 | 129.9939
Sub-Trans
| History | [9 empty] | Forecast | Averaged from 2008 | [9 empty] | Linear trend
Total | 26 | 32 | 29 | 23 | 22 | 25 | 28 | 10 | 21 | 21
Forecast | [10 empty] | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | 23.7 | [10 empty] | 17.0667 | 15.8606 | 14.6545 | 13.4485 | 12.2424 | 11.0364 | 9.8303 | 8.6242 | 7.4182 | 6.2121 | 5.0061
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 4 | 6 | 7 | 0 | 1 | 4 | 1 | 1 | 0 | 2 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 4 | 6 | 7 | 0 | 1 | 4 | 1 | 1 | 0 | 2 | -0.2 | -0.70909 | -1.2182 | -1.7273 | -2.2364 | -2.7455 | -3.2545 | -3.7636 | -4.2727 | -4.7818 | -5.2909
Egmont | 1 | 1 | 2 | 0 | 1 | 1 | 2 | 0 | 2 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1 | 1 | 2 | 0 | 1 | 1 | 2 | 0 | 2 | 1 | 1.2 | 1.2182 | 1.2364 | 1.2545 | 1.2727 | 1.2909 | 1.3091 | 1.3273 | 1.3455 | 1.3636 | 1.3818
Kinleith | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 2 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 2 | 1.4667 | 1.6424 | 1.8182 | 1.9939 | 2.1697 | 2.3455 | 2.5212 | 2.697 | 2.8727 | 3.0485 | 3.2242
Manawatu | 3 | 3 | 1 | 1 | 2 | 2 | 2 | 0 | 4 | 5 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 3 | 3 | 1 | 1 | 2 | 2 | 2 | 0 | 4 | 5 | 3.0667 | 3.2061 | 3.3455 | 3.4848 | 3.6242 | 3.7636 | 3.903 | 4.0424 | 4.1818 | 4.3212 | 4.4606
Mt Maunganui | 1 | 0 | 4 | 7 | 0 | 0 | 2 | 1 | 1 | 1 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1 | 0 | 4 | 7 | 0 | 0 | 2 | 1 | 1 | 1 | 0.93333 | 0.79394 | 0.65455 | 0.51515 | 0.37576 | 0.23636 | 0.09697 | -0.042424 | -0.18182 | -0.32121 | -0.46061
Rangitikei | 1 | 2 | 2 | 1 | 2 | 5 | 0 | 2 | 2 | 0 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1 | 2 | 2 | 1 | 2 | 5 | 0 | 2 | 2 | 0 | 1.4 | 1.3455 | 1.2909 | 1.2364 | 1.1818 | 1.1273 | 1.0727 | 1.0182 | 0.96364 | 0.90909 | 0.85455
Taranaki | 1 | 0 | 3 | 2 | 9 | 4 | 6 | 3 | 2 | 2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 1 | 0 | 3 | 2 | 9 | 4 | 6 | 3 | 2 | 2 | 4.2 | 4.3818 | 4.5636 | 4.7455 | 4.9273 | 5.1091 | 5.2909 | 5.4727 | 5.6545 | 5.8364 | 6.0182
Tararua | 5 | 3 | 3 | 2 | 1 | 1 | 1 | 1 | 3 | 4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 5 | 3 | 3 | 2 | 1 | 1 | 1 | 1 | 3 | 4 | 1.6667 | 1.5333 | 1.4 | 1.2667 | 1.1333 | 1 | 0.86667 | 0.73333 | 0.6 | 0.46667 | 0.33333
Tauranga | 0 | 5 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 5 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 0 | -0.13333 | -0.33939 | -0.54545 | -0.75152 | -0.95758 | -1.1636 | -1.3697 | -1.5758 | -1.7818 | -1.9879 | -2.1939
Waikato | 6 | 1 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 6 | 1 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 1 | -0.2 | -0.47273 | -0.74545 | -1.0182 | -1.2909 | -1.5636 | -1.8364 | -2.1091 | -2.3818 | -2.6545 | -2.9273
Waikino | 1 | 2 | 0 | 2 | 0 | 0 | 7 | 0 | 1 | 0 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1 | 2 | 0 | 2 | 0 | 0 | 7 | 0 | 1 | 0 | 1.2667 | 1.2606 | 1.2545 | 1.2485 | 1.2424 | 1.2364 | 1.2303 | 1.2242 | 1.2182 | 1.2121 | 1.2061
Wairarapa | 3 | 5 | 5 | 5 | 4 | 2 | 3 | 2 | 2 | 3 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3.4 | 3 | 5 | 5 | 5 | 4 | 2 | 3 | 2 | 2 | 3 | 1.9333 | 1.6667 | 1.4 | 1.1333 | 0.86667 | 0.6 | 0.33333 | 0.066667 | -0.2 | -0.46667 | -0.73333
Whanganui | 0 | 4 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 0 | 4 | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 0.46667 | 0.33333 | 0.2 | 0.066667 | -0.066667 | -0.2 | -0.33333 | -0.46667 | -0.6 | -0.73333 | -0.86667
The rest of the equipment
| History | [9 empty] | Forecast | Averaged from 2008 | [9 empty] | Linear trend
Total | 81 | 109 | 124 | 111 | 93 | 83 | 126 | 110 | 102 | 118
Forecast | [10 empty] | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | [10 empty] | 114 | 115.5091 | 117.0182 | 118.5273 | 120.0364 | 121.5455 | 123.0545 | 124.5636 | 126.0727 | 127.5818 | 129.0909
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 5 | 11 | 8 | 9 | 5 | 4 | 9 | 13 | 3 | 7 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 5 | 11 | 8 | 9 | 5 | 4 | 9 | 13 | 3 | 7 | 6.9333 | 6.8485 | 6.7636 | 6.6788 | 6.5939 | 6.5091 | 6.4242 | 6.3394 | 6.2545 | 6.1697 | 6.0848
Egmont | 2 | 5 | 6 | 7 | 4 | 2 | 17 | 10 | 11 | 11 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 2 | 5 | 6 | 7 | 4 | 2 | 17 | 10 | 11 | 11 | 13.2 | 14.2364 | 15.2727 | 16.3091 | 17.3455 | 18.3818 | 19.4182 | 20.4545 | 21.4909 | 22.5273 | 23.5636
Kinleith | 4 | 1 | 5 | 2 | 1 | 3 | 5 | 2 | 2 | 8 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 4 | 1 | 5 | 2 | 1 | 3 | 5 | 2 | 2 | 8 | 4.6 | 4.8364 | 5.0727 | 5.3091 | 5.5455 | 5.7818 | 6.0182 | 6.2545 | 6.4909 | 6.7273 | 6.9636
Manawatu | 16 | 24 | 34 | 20 | 27 | 21 | 21 | 18 | 12 | 13 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | 16 | 24 | 34 | 20 | 27 | 21 | 21 | 18 | 12 | 13 | 14.1333 | 12.9576 | 11.7818 | 10.6061 | 9.4303 | 8.2545 | 7.0788 | 5.903 | 4.7273 | 3.5515 | 2.3758
Mt Maunganui | 3 | 4 | 7 | 10 | 5 | 5 | 11 | 6 | 4 | 13 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 3 | 4 | 7 | 10 | 5 | 5 | 11 | 6 | 4 | 13 | 9.7333 | 10.2667 | 10.8 | 11.3333 | 11.8667 | 12.4 | 12.9333 | 13.4667 | 14 | 14.5333 | 15.0667
Rangitikei | 4 | 5 | 3 | 1 | 2 | 1 | 4 | 5 | 4 | 3 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 4 | 5 | 3 | 1 | 2 | 1 | 4 | 5 | 4 | 3 | 3.2667 | 3.2788 | 3.2909 | 3.303 | 3.3152 | 3.3273 | 3.3394 | 3.3515 | 3.3636 | 3.3758 | 3.3879
Taranaki | 13 | 11 | 17 | 6 | 8 | 9 | 13 | 12 | 21 | 14 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 13 | 11 | 17 | 6 | 8 | 9 | 13 | 12 | 21 | 14 | 14.9333 | 15.3939 | 15.8545 | 16.3152 | 16.7758 | 17.2364 | 17.697 | 18.1576 | 18.6182 | 19.0788 | 19.5394
Tararua | 2 | 1 | 3 | 1 | 1 | 1 | 0 | 1 | 0 | 3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 2 | 1 | 3 | 1 | 1 | 1 | 0 | 1 | 0 | 3 | 0.93333 | 0.86667 | 0.8 | 0.73333 | 0.66667 | 0.6 | 0.53333 | 0.46667 | 0.4 | 0.33333 | 0.26667
Tauranga | 15 | 24 | 10 | 26 | 16 | 11 | 19 | 23 | 21 | 24 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 15 | 24 | 10 | 26 | 16 | 11 | 19 | 23 | 21 | 24 | 22.2 | 22.8 | 23.4 | 24 | 24.6 | 25.2 | 25.8 | 26.4 | 27 | 27.6 | 28.2
Waikato | 4 | 13 | 7 | 7 | 5 | 11 | 5 | 4 | 11 | 5 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 4 | 13 | 7 | 7 | 5 | 11 | 5 | 4 | 11 | 5 | 6.5333 | 6.4121 | 6.2909 | 6.1697 | 6.0485 | 5.9273 | 5.8061 | 5.6848 | 5.5636 | 5.4424 | 5.3212
Waikino | 6 | 1 | 7 | 4 | 7 | 4 | 7 | 2 | 5 | 5 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 6 | 1 | 7 | 4 | 7 | 4 | 7 | 2 | 5 | 5 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
Wairarapa | 5 | 7 | 9 | 11 | 5 | 6 | 10 | 6 | 5 | 7 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 5 | 7 | 9 | 11 | 5 | 6 | 10 | 6 | 5 | 7 | 6.6667 | 6.5879 | 6.5091 | 6.4303 | 6.3515 | 6.2727 | 6.1939 | 6.1152 | 6.0364 | 5.9576 | 5.8788
Whanganui | 2 | 2 | 8 | 7 | 7 | 5 | 5 | 8 | 3 | 5 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 2 | 2 | 8 | 7 | 7 | 5 | 5 | 8 | 3 | 5 | 6.0667 | 6.2242 | 6.3818 | 6.5394 | 6.697 | 6.8545 | 7.0121 | 7.1697 | 7.3273 | 7.4848 | 7.6424
Vegetation
| History | [9 empty] | Forecast | Average adjusted for reactive tree count | [9 empty] | Linear trend
Total | 146 | 157 | 157 | 296 | 358 | 181 | 320 | 292 | 185 | 286
Forecast | [10 empty] | 232.4444 | 232.4444 | 184.1225 | 136.0669 | 116.6829 | 95.1365 | 73.6294 | 64.9845 | 64.9845 | 64.9845 | 64.9845 | [10 empty] | 305.3333 | 317.6121 | 329.8909 | 342.1697 | 354.4485 | 366.7273 | 379.0061 | 391.2848 | 403.5636 | 415.8424 | 428.1212
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 17 | 12 | 12 | 20 | 19 | 12 | 21 | 20 | 13 | 18 | 16.2222 | 16.2222 | 16.2222 | 16.2222 | 16.2222 | 11.362 | 6.4825 | 4.5422 | 4.5422 | 4.5422 | 4.5422 | 17 | 12 | 12 | 20 | 19 | 12 | 21 | 20 | 13 | 18 | 18.1333 | 18.4485 | 18.7636 | 19.0788 | 19.3939 | 19.7091 | 20.0242 | 20.3394 | 20.6545 | 20.9697 | 21.2848
Egmont | 3 | 7 | 0 | 17 | 21 | 6 | 19 | 19 | 6 | 17 | 10.8889 | 10.8889 | 7.6051 | 4.347 | 3.0386 | 3.0386 | 3.0386 | 3.0386 | 3.0386 | 3.0386 | 3.0386 | 3 | 7 | 0 | 17 | 21 | 6 | 19 | 19 | 6 | 17 | 18.3333 | 19.5758 | 20.8182 | 22.0606 | 23.303 | 24.5455 | 25.7879 | 27.0303 | 28.2727 | 29.5152 | 30.7576
Kinleith | 5 | 2 | 2 | 2 | 4 | 1 | 3 | 1 | 3 | 2 | 2.5556 | 2.5556 | 2.5556 | 2.5556 | 2.5556 | 1.7899 | 1.0212 | 0.71556 | 0.71556 | 0.71556 | 0.71556 | 5 | 2 | 2 | 2 | 4 | 1 | 3 | 1 | 3 | 2 | 1.6667 | 1.5152 | 1.3636 | 1.2121 | 1.0606 | 0.90909 | 0.75758 | 0.60606 | 0.45455 | 0.30303 | 0.15152
Manawatu | 9 | 11 | 19 | 20 | 21 | 10 | 24 | 24 | 13 | 20 | 16.7778 | 16.7778 | 11.7444 | 6.7111 | 4.6916 | 4.6916 | 4.6916 | 4.6916 | 4.6916 | 4.6916 | 4.6916 | 9 | 11 | 19 | 20 | 21 | 10 | 24 | 24 | 13 | 20 | 21.7333 | 22.5758 | 23.4182 | 24.2606 | 25.103 | 25.9455 | 26.7879 | 27.6303 | 28.4727 | 29.3152 | 30.1576
Mt Maunganui | 7 | 9 | 4 | 16 | 14 | 8 | 12 | 17 | 11 | 22 | 10.8889 | 10.8889 | 10.8889 | 10.8889 | 10.8889 | 7.6099 | 4.3678 | 3.0415 | 3.0415 | 3.0415 | 3.0415 | 7 | 9 | 4 | 16 | 14 | 8 | 12 | 17 | 11 | 22 | 18.5333 | 19.7212 | 20.9091 | 22.097 | 23.2848 | 24.4727 | 25.6606 | 26.8485 | 28.0364 | 29.2242 | 30.4121
Rangitikei | 13 | 8 | 14 | 30 | 34 | 13 | 26 | 26 | 14 | 20 | 19.7778 | 19.7778 | 13.8444 | 7.9111 | 5.5305 | 5.5305 | 5.5305 | 5.5305 | 5.5305 | 5.5305 | 5.5305 | 13 | 8 | 14 | 30 | 34 | 13 | 26 | 26 | 14 | 20 | 24.2 | 25 | 25.8 | 26.6 | 27.4 | 28.2 | 29 | 29.8 | 30.6 | 31.4 | 32.2
Taranaki | 18 | 20 | 30 | 54 | 59 | 19 | 32 | 25 | 25 | 42 | 31.3333 | 31.3333 | 21.8841 | 12.5087 | 8.7438 | 8.7438 | 8.7438 | 8.7438 | 8.7438 | 8.7438 | 8.7438 | 18 | 20 | 30 | 54 | 59 | 19 | 32 | 25 | 25 | 42 | 36.4 | 37.1273 | 37.8545 | 38.5818 | 39.3091 | 40.0364 | 40.7636 | 41.4909 | 42.2182 | 42.9455 | 43.6727
Tararua | 3 | 6 | 11 | 10 | 20 | 9 | 14 | 19 | 15 | 12 | 11.8889 | 11.8889 | 8.3222 | 4.7556 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3.3245 | 3 | 6 | 11 | 10 | 20 | 9 | 14 | 19 | 15 | 12 | 18.0667 | 19.1879 | 20.3091 | 21.4303 | 22.5515 | 23.6727 | 24.7939 | 25.9152 | 27.0364 | 28.1576 | 29.2788
Tauranga | 9 | 18 | 5 | 13 | 29 | 15 | 23 | 24 | 11 | 25 | 16.3333 | 16.3333 | 16.3333 | 16.3333 | 16.3333 | 11.4149 | 6.5518 | 4.5623 | 4.5623 | 4.5623 | 4.5623 | 9 | 18 | 5 | 13 | 29 | 15 | 23 | 24 | 11 | 25 | 24.0667 | 25.3152 | 26.5636 | 27.8121 | 29.0606 | 30.3091 | 31.5576 | 32.8061 | 34.0545 | 35.303 | 36.5515
Waikato | 20 | 12 | 17 | 30 | 27 | 16 | 14 | 15 | 14 | 12 | 18.3333 | 18.3333 | 18.3333 | 18.3333 | 18.3333 | 12.8406 | 7.3261 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 20 | 12 | 17 | 30 | 27 | 16 | 14 | 15 | 14 | 12 | 13.4667 | 12.697 | 11.9273 | 11.1576 | 10.3879 | 9.6182 | 8.8485 | 8.0788 | 7.3091 | 6.5394 | 5.7697
Waikino | 5 | 8 | 8 | 3 | 3 | 15 | 10 | 6 | 9 | 9 | 7.4444 | 7.4444 | 7.4444 | 7.4444 | 7.4444 | 5.214 | 2.9748 | 2.0844 | 2.0844 | 2.0844 | 2.0844 | 5 | 8 | 8 | 3 | 3 | 15 | 10 | 6 | 9 | 9 | 9.8 | 10.2 | 10.6 | 11 | 11.4 | 11.8 | 12.2 | 12.6 | 13 | 13.4 | 13.8
Wairarapa | 29 | 37 | 19 | 62 | 78 | 40 | 99 | 79 | 34 | 58 | 53 | 53 | 37.0603 | 21.2397 | 14.8162 | 14.8162 | 14.8162 | 14.8162 | 14.8162 | 14.8162 | 14.8162 | 29 | 37 | 19 | 62 | 78 | 40 | 99 | 79 | 34 | 58 | 73.9333 | 77.6485 | 81.3636 | 85.0788 | 88.7939 | 92.5091 | 96.2242 | 99.9394 | 103.6545 | 107.3697 | 111.0848
Whanganui | 8 | 7 | 16 | 19 | 29 | 17 | 23 | 17 | 17 | 29 | 17 | 17 | 11.8841 | 6.8159 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 4.76 | 8 | 7 | 16 | 19 | 29 | 17 | 23 | 17 | 17 | 29 | 27 | 28.6 | 30.2 | 31.8 | 33.4 | 35 | 36.6 | 38.2 | 39.8 | 41.4 | 43
Adverse Weather
| History | [9 empty] | Forecast | Averaged from 2008 | [9 empty] | Linear trend
Total | 290 | 384 | 184 | 230 | 206 | 154 | 264 | 427 | 196 | 458
Forecast | [10 empty] | 279.3 | 279.3 | 279.3 | 279.3 | 279.3 | 279.3 | 279.3 | 279.3 | 279.3 | 279.3 | 279.3 | [10 empty] | 328 | 336.8545 | 345.7091 | 354.5636 | 363.4182 | 372.2727 | 381.1273 | 389.9818 | 398.8364 | 407.6909 | 416.5455
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 43 | 29 | 3 | 16 | 7 | 1 | 19 | 34 | 17 | 15 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 43 | 29 | 3 | 16 | 7 | 1 | 19 | 34 | 17 | 15 | 12.4667 | 11.3879 | 10.3091 | 9.2303 | 8.1515 | 7.0727 | 5.9939 | 4.9152 | 3.8364 | 2.7576 | 1.6788
Egmont | 48 | 32 | 26 | 17 | 26 | 11 | 28 | 68 | 14 | 69 | 33.9 | 33.9 | 33.9 | 33.9 | 33.9 | 33.9 | 33.9 | 33.9 | 33.9 | 33.9 | 33.9 | 48 | 32 | 26 | 17 | 26 | 11 | 28 | 68 | 14 | 69 | 43.6 | 45.3636 | 47.1273 | 48.8909 | 50.6545 | 52.4182 | 54.1818 | 55.9455 | 57.7091 | 59.4727 | 61.2364
Kinleith | 3 | 0 | 3 | 3 | 0 | 3 | 8 | 3 | 2 | 4 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 2.9 | 3 | 0 | 3 | 3 | 0 | 3 | 8 | 3 | 2 | 4 | 4.2667 | 4.5152 | 4.7636 | 5.0121 | 5.2606 | 5.5091 | 5.7576 | 6.0061 | 6.2545 | 6.503 | 6.7515
Manawatu | 20 | 54 | 17 | 21 | 20 | 10 | 25 | 24 | 12 | 47 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 54 | 17 | 21 | 20 | 10 | 25 | 24 | 12 | 47 | 24.5333 | 24.4485 | 24.3636 | 24.2788 | 24.1939 | 24.1091 | 24.0242 | 23.9394 | 23.8545 | 23.7697 | 23.6848
Mt Maunganui | 7 | 12 | 5 | 12 | 4 | 5 | 7 | 22 | 20 | 7 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 7 | 12 | 5 | 12 | 4 | 5 | 7 | 22 | 20 | 7 | 14.3333 | 15.103 | 15.8727 | 16.6424 | 17.4121 | 18.1818 | 18.9515 | 19.7212 | 20.4909 | 21.2606 | 22.0303
Rangitikei | 16 | 21 | 25 | 22 | 13 | 7 | 23 | 35 | 13 | 40 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 16 | 21 | 25 | 22 | 13 | 7 | 23 | 35 | 13 | 40 | 28.4 | 29.6545 | 30.9091 | 32.1636 | 33.4182 | 34.6727 | 35.9273 | 37.1818 | 38.4364 | 39.6909 | 40.9455
Taranaki | 34 | 47 | 33 | 28 | 52 | 33 | 30 | 74 | 35 | 127 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 49.3 | 34 | 47 | 33 | 28 | 52 | 33 | 30 | 74 | 35 | 127 | 80.8 | 86.5273 | 92.2545 | 97.9818 | 103.7091 | 109.4364 | 115.1636 | 120.8909 | 126.6182 | 132.3455 | 138.0727
Tararua | 16 | 9 | 8 | 18 | 22 | 16 | 20 | 21 | 7 | 18 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 16 | 9 | 8 | 18 | 22 | 16 | 20 | 21 | 7 | 18 | 17.8 | 18.2182 | 18.6364 | 19.0545 | 19.4727 | 19.8909 | 20.3091 | 20.7273 | 21.1455 | 21.5636 | 21.9818
Tauranga | 17 | 34 | 20 | 36 | 9 | 6 | 30 | 32 | 9 | 8 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 17 | 34 | 20 | 36 | 9 | 6 | 30 | 32 | 9 | 8 | 12.8667 | 11.5515 | 10.2364 | 8.9212 | 7.6061 | 6.2909 | 4.9758 | 3.6606 | 2.3455 | 1.0303 | -0.28485
Waikato | 16 | 72 | 6 | 17 | 11 | 20 | 13 | 26 | 24 | 6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 16 | 72 | 6 | 17 | 11 | 20 | 13 | 26 | 24 | 6 | 10.1333 | 8.1394 | 6.1455 | 4.1515 | 2.1576 | 0.16364 | -1.8303 | -3.8242 | -5.8182 | -7.8121 | -9.8061
Waikino | 13 | 36 | 0 | 7 | 4 | 5 | 12 | 6 | 7 | 5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 13 | 36 | 0 | 7 | 4 | 5 | 12 | 6 | 7 | 5 | 1.8667 | 0.47879 | -0.90909 | -2.297 | -3.6848 | -5.0727 | -6.4606 | -7.8485 | -9.2364 | -10.6242 | -12.0121
Wairarapa | 41 | 32 | 30 | 21 | 21 | 26 | 33 | 49 | 16 | 46 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 31.5 | 41 | 32 | 30 | 21 | 21 | 26 | 33 | 49 | 16 | 46 | 33.8 | 34.2182 | 34.6364 | 35.0545 | 35.4727 | 35.8909 | 36.3091 | 36.7273 | 37.1455 | 37.5636 | 37.9818
Whanganui | 16 | 6 | 8 | 12 | 17 | 11 | 16 | 33 | 20 | 66 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 16 | 6 | 8 | 12 | 17 | 11 | 16 | 33 | 20 | 66 | 43.1333 | 47.2485 | 51.3636 | 55.4788 | 59.5939 | 63.7091 | 67.8242 | 71.9394 | 76.0545 | 80.1697 | 84.2848
Unknown
0.5
| History | [9 empty] | Forecast | linear trend with scaler | [9 empty] | Linear trend
Total | 219 | 267 | 301 | 384 | 371 | 273 | 268 | 396 | 513 | 502
Forecast | [10 empty] | 492.6667 | 513.5055 | 519.2421 | 541.0867 | 561.8239 | 580.4431 | 599.5848 | 618.1542 | 638.9929 | 659.8317 | 680.6705 | [10 empty] | 492.6667 | 518.7152 | 544.7636 | 570.8121 | 596.8606 | 622.9091 | 648.9576 | 675.0061 | 701.0545 | 727.103 | 753.1515
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 17 | 19 | 23 | 28 | 17 | 13 | 13 | 34 | 22 | 22 | 23.2 | 23.5491 | 23.5491 | 23.7236 | 23.8982 | 24.3342 | 24.876 | 25.3015 | 25.6506 | 25.9997 | 26.3488 | 17 | 19 | 23 | 28 | 17 | 13 | 13 | 34 | 22 | 22 | 23.2 | 23.6364 | 24.0727 | 24.5091 | 24.9455 | 25.3818 | 25.8182 | 26.2545 | 26.6909 | 27.1273 | 27.5636
Egmont | 8 | 16 | 18 | 19 | 25 | 22 | 22 | 51 | 33 | 38 | 43.8667 | 46.5818 | 47.4006 | 50.3862 | 53.2119 | 55.5482 | 57.8845 | 60.2208 | 62.936 | 65.6511 | 68.3663 | 8 | 16 | 18 | 19 | 25 | 22 | 22 | 51 | 33 | 38 | 43.8667 | 47.2606 | 50.6545 | 54.0485 | 57.4424 | 60.8364 | 64.2303 | 67.6242 | 71.0182 | 74.4121 | 77.8061
Kinleith | 8 | 5 | 2 | 4 | 1 | 6 | 7 | 5 | 5 | 9 | 6.4667 | 6.6509 | 6.6509 | 6.743 | 6.8352 | 7.0653 | 7.3512 | 7.5758 | 7.76 | 7.9443 | 8.1285 | 8 | 5 | 2 | 4 | 1 | 6 | 7 | 5 | 5 | 9 | 6.4667 | 6.697 | 6.9273 | 7.1576 | 7.3879 | 7.6182 | 7.8485 | 8.0788 | 8.3091 | 8.5394 | 8.7697
Manawatu | 31 | 45 | 57 | 58 | 69 | 23 | 50 | 51 | 55 | 66 | 60 | 61.3818 | 61.7964 | 63.3164 | 64.7545 | 65.9431 | 67.1317 | 68.3203 | 69.7022 | 71.084 | 72.4658 | 31 | 45 | 57 | 58 | 69 | 23 | 50 | 51 | 55 | 66 | 60 | 61.7273 | 63.4545 | 65.1818 | 66.9091 | 68.6364 | 70.3636 | 72.0909 | 73.8182 | 75.5455 | 77.2727
Mt Maunganui | 7 | 7 | 8 | 9 | 15 | 8 | 12 | 9 | 27 | 9 | 16.6 | 17.4 | 17.4 | 17.8 | 18.2 | 19.2023 | 20.4373 | 21.4179 | 22.2179 | 23.0179 | 23.8179 | 7 | 7 | 8 | 9 | 15 | 8 | 12 | 9 | 27 | 9 | 16.6 | 17.6 | 18.6 | 19.6 | 20.6 | 21.6 | 22.6 | 23.6 | 24.6 | 25.6 | 26.6
Rangitikei | 10 | 18 | 16 | 27 | 46 | 15 | 15 | 29 | 51 | 48 | 46.5333 | 49.3018 | 50.1324 | 53.1777 | 56.059 | 58.4404 | 60.8218 | 63.2032 | 65.9717 | 68.7402 | 71.5087 | 10 | 18 | 16 | 27 | 46 | 15 | 15 | 29 | 51 | 48 | 46.5333 | 49.9939 | 53.4545 | 56.9152 | 60.3758 | 63.8364 | 67.297 | 70.7576 | 74.2182 | 77.6788 | 81.1394
Taranaki | 44 | 27 | 41 | 56 | 64 | 41 | 51 | 50 | 75 | 97 | 81.9333 | 85.9091 | 87.1081 | 91.4798 | 95.6174 | 99.0385 | 102.4595 | 105.8805 | 109.8563 | 113.832 | 117.8078 | 44 | 27 | 41 | 56 | 64 | 41 | 51 | 50 | 75 | 97 | 81.9333 | 86.903 | 91.8727 | 96.8424 | 101.8121 | 106.7818 | 111.7515 | 116.7212 | 121.6909 | 126.6606 | 131.6303
Tararua | 12 | 21 | 12 | 17 | 34 | 17 | 6 | 27 | 47 | 28 | 33.8 | 35.5018 | 36.0124 | 37.8844 | 39.6555 | 41.1194 | 42.5833 | 44.0472 | 45.749 | 47.4508 | 49.1526 | 12 | 21 | 12 | 17 | 34 | 17 | 6 | 27 | 47 | 28 | 33.8 | 35.9273 | 38.0545 | 40.1818 | 42.3091 | 44.4364 | 46.5636 | 48.6909 | 50.8182 | 52.9455 | 55.0727
Tauranga | 31 | 30 | 30 | 43 | 18 | 29 | 25 | 27 | 41 | 37 | 33.5333 | 33.8873 | 33.8873 | 34.0642 | 34.2412 | 34.6846 | 35.231 | 35.6649 | 36.0188 | 36.3728 | 36.7267 | 31 | 30 | 30 | 43 | 18 | 29 | 25 | 27 | 41 | 37 | 33.5333 | 33.9758 | 34.4182 | 34.8606 | 35.303 | 35.7455 | 36.1879 | 36.6303 | 37.0727 | 37.5152 | 37.9576
Waikato | 15 | 28 | 40 | 48 | 20 | 23 | 17 | 11 | 39 | 30 | 26.3333 | 26.2218 | 26.2218 | 26.1661 | 26.1103 | 25.971 | 25.7979 | 25.662 | 25.5505 | 25.439 | 25.3275 | 15 | 28 | 40 | 48 | 20 | 23 | 17 | 11 | 39 | 30 | 26.3333 | 26.1939 | 26.0545 | 25.9152 | 25.7758 | 25.6364 | 25.497 | 25.3576 | 25.2182 | 25.0788 | 24.9394
Waikino | 7 | 6 | 10 | 9 | 7 | 3 | 4 | 9 | 10 | 11 | 8.9333 | 9.1273 | 9.1273 | 9.2242 | 9.3212 | 9.5634 | 9.8645 | 10.1008 | 10.2948 | 10.4887 | 10.6827 | 7 | 6 | 10 | 9 | 7 | 3 | 4 | 9 | 10 | 11 | 8.9333 | 9.1758 | 9.4182 | 9.6606 | 9.903 | 10.1455 | 10.3879 | 10.6303 | 10.8727 | 11.1152 | 11.3576
Wairarapa | 24 | 29 | 27 | 46 | 41 | 42 | 28 | 60 | 64 | 66 | 67.2 | 70.7636 | 71.8354 | 75.7487 | 79.4621 | 82.5276 | 85.5932 | 88.6587 | 92.2223 | 95.786 | 99.3496 | 24 | 29 | 27 | 46 | 41 | 42 | 28 | 60 | 64 | 66 | 67.2 | 71.6545 | 76.1091 | 80.5636 | 85.0182 | 89.4727 | 93.9273 | 98.3818 | 102.8364 | 107.2909 | 111.7455
Whanganui | 5 | 16 | 17 | 20 | 14 | 31 | 18 | 33 | 44 | 41 | 44.2667 | 47.2291 | 48.1206 | 51.3723 | 54.4574 | 57.0051 | 59.5528 | 62.1005 | 65.0629 | 68.0253 | 70.9877 | 5 | 16 | 17 | 20 | 14 | 31 | 18 | 33 | 44 | 41 | 44.2667 | 47.9697 | 51.6727 | 55.3758 | 59.0788 | 62.7818 | 66.4848 | 70.1879 | 73.8909 | 77.5939 | 81.297
The remainder
| History | [9 empty] | Forecast | Averaged from 2008 | [9 empty] | Linear trend
Total | 321 | 336 | 296 | 264 | 291 | 296 | 240 | 282 | 351 | 398
Forecast | [10 empty] | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | 307.5 | [10 empty] | 329.5333 | 333.5394 | 337.5455 | 341.5515 | 345.5576 | 349.5636 | 353.5697 | 357.5758 | 361.5818 | 365.5879 | 369.5939
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 28 | 16 | 20 | 9 | 18 | 20 | 18 | 17 | 17 | 14 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 28 | 16 | 20 | 9 | 18 | 20 | 18 | 17 | 17 | 14 | 14.2 | 13.5636 | 12.9273 | 12.2909 | 11.6545 | 11.0182 | 10.3818 | 9.7455 | 9.1091 | 8.4727 | 7.8364
Egmont | 10 | 17 | 21 | 15 | 11 | 17 | 30 | 22 | 24 | 42 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 10 | 17 | 21 | 15 | 11 | 17 | 30 | 22 | 24 | 42 | 34 | 36.3818 | 38.7636 | 41.1455 | 43.5273 | 45.9091 | 48.2909 | 50.6727 | 53.0545 | 55.4364 | 57.8182
Kinleith | 9 | 5 | 2 | 9 | 3 | 4 | 4 | 5 | 2 | 4 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 9 | 5 | 2 | 9 | 3 | 4 | 4 | 5 | 2 | 4 | 2.5333 | 2.1394 | 1.7455 | 1.3515 | 0.95758 | 0.56364 | 0.1697 | -0.22424 | -0.61818 | -1.0121 | -1.4061
Manawatu | 40 | 41 | 43 | 39 | 19 | 29 | 20 | 27 | 32 | 43 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 40 | 41 | 43 | 39 | 19 | 29 | 20 | 27 | 32 | 43 | 27.8667 | 26.8788 | 25.8909 | 24.903 | 23.9152 | 22.9273 | 21.9394 | 20.9515 | 19.9636 | 18.9758 | 17.9879
Mt Maunganui | 18 | 20 | 19 | 10 | 21 | 18 | 10 | 11 | 14 | 23 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 18 | 20 | 19 | 10 | 21 | 18 | 10 | 11 | 14 | 23 | 15.0667 | 14.8242 | 14.5818 | 14.3394 | 14.097 | 13.8545 | 13.6121 | 13.3697 | 13.1273 | 12.8848 | 12.6424
Rangitikei | 12 | 11 | 12 | 8 | 18 | 19 | 10 | 23 | 32 | 37 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 12 | 11 | 12 | 8 | 18 | 19 | 10 | 23 | 32 | 37 | 32.6667 | 35.297 | 37.9273 | 40.5576 | 43.1879 | 45.8182 | 48.4485 | 51.0788 | 53.7091 | 56.3394 | 58.9697
Taranaki | 49 | 48 | 32 | 32 | 44 | 46 | 42 | 52 | 53 | 52 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 49 | 48 | 32 | 32 | 44 | 46 | 42 | 52 | 53 | 52 | 51.4667 | 52.6424 | 53.8182 | 54.9939 | 56.1697 | 57.3455 | 58.5212 | 59.697 | 60.8727 | 62.0485 | 63.2242
Tararua | 10 | 1 | 6 | 6 | 4 | 7 | 7 | 13 | 13 | 15 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 10 | 1 | 6 | 6 | 4 | 7 | 7 | 13 | 13 | 15 | 13.8667 | 14.897 | 15.9273 | 16.9576 | 17.9879 | 19.0182 | 20.0485 | 21.0788 | 22.1091 | 23.1394 | 24.1697
Tauranga | 43 | 59 | 35 | 49 | 56 | 37 | 30 | 34 | 42 | 40 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 43 | 59 | 35 | 49 | 56 | 37 | 30 | 34 | 42 | 40 | 34.9333 | 33.5576 | 32.1818 | 30.8061 | 29.4303 | 28.0545 | 26.6788 | 25.303 | 23.9273 | 22.5515 | 21.1758
Waikato | 43 | 55 | 42 | 41 | 31 | 28 | 16 | 14 | 51 | 21 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 43 | 55 | 42 | 41 | 31 | 28 | 16 | 14 | 51 | 21 | 19.4 | 16.7091 | 14.0182 | 11.3273 | 8.6364 | 5.9455 | 3.2545 | 0.56364 | -2.1273 | -4.8182 | -7.5091
Waikino | 13 | 7 | 18 | 3 | 10 | 13 | 8 | 15 | 14 | 19 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 7 | 18 | 3 | 10 | 13 | 8 | 15 | 14 | 19 | 15.5333 | 16.1758 | 16.8182 | 17.4606 | 18.103 | 18.7455 | 19.3879 | 20.0303 | 20.6727 | 21.3152 | 21.9576
Wairarapa | 28 | 42 | 21 | 26 | 27 | 40 | 24 | 32 | 43 | 57 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 28 | 42 | 21 | 26 | 27 | 40 | 24 | 32 | 43 | 57 | 45 | 47 | 49 | 51 | 53 | 55 | 57 | 59 | 61 | 63 | 65
Whanganui | 18 | 14 | 25 | 17 | 29 | 18 | 21 | 17 | 14 | 31 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 20.4 | 18 | 14 | 25 | 17 | 29 | 18 | 21 | 17 | 14 | 31 | 23 | 23.4727 | 23.9455 | 24.4182 | 24.8909 | 25.3636 | 25.8364 | 26.3091 | 26.7818 | 27.2545 | 27.7273
Totals
| History | [9 empty] | Forecast | [10 empty] | Linear trend
Total | 1829 | 1959 | 1815 | 2197 | 2335 | 1881 | 2239 | 2755 | 2827 | 3496
Forecast | [10 empty] | 2822.2665 | 2853.0598 | 2811.969 | 2782.83 | 2775.574 | 2760.5519 | 2749.997 | 2771.2083 | 2799.6291 | 2824.3742 | 2851.3412 | [10 empty] | 3181.6667 | 3335.9152 | 3490.1636 | 3644.4121 | 3798.6606 | 3952.9091 | 4107.1576 | 4261.4061 | 4415.6545 | 4569.903 | 4724.1515
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 151 | 145 | 117 | 124 | 99 | 106 | 147 | 208 | 168 | 167 | 187.7034 | 191.3175 | 193.221 | 196.1782 | 198.7854 | 196.255 | 194.0505 | 195.3806 | 197.6065 | 199.9431 | 202.4044 | 151 | 145 | 117 | 124 | 99 | 106 | 147 | 208 | 168 | 167 | 171.0667 | 176.1333 | 181.2 | 186.2667 | 191.3333 | 196.4 | 201.4667 | 206.5333 | 211.6 | 216.6667 | 221.7333
Egmont | 143 | 158 | 181 | 172 | 253 | 172 | 302 | 370 | 259 | 438 | 285.8377 | 289.9916 | 285.908 | 280.0704 | 277.7166 | 280.0437 | 281.007 | 289.5116 | 294.8009 | 298.409 | 302.5552 | 143 | 158 | 181 | 172 | 253 | 172 | 302 | 370 | 259 | 438 | 398.6667 | 426.6424 | 454.6182 | 482.5939 | 510.5697 | 538.5455 | 566.5212 | 594.497 | 622.4727 | 650.4485 | 678.4242
Kinleith | 36 | 18 | 20 | 32 | 15 | 27 | 32 | 26 | 26 | 46 | 33.7556 | 34.2437 | 34.412 | 34.6982 | 34.7674 | 34.2638 | 33.8189 | 33.8234 | 34.0291 | 34.2331 | 34.3585 | 36 | 18 | 20 | 32 | 15 | 27 | 32 | 26 | 26 | 46 | 34.0667 | 35.2061 | 36.3455 | 37.4848 | 38.6242 | 39.7636 | 40.903 | 42.0424 | 43.1818 | 44.3212 | 45.4606
Manawatu | 195 | 236 | 256 | 265 | 271 | 182 | 226 | 258 | 233 | 354 | 277.1158 | 280.0445 | 276.8349 | 273.6199 | 273.1737 | 273.3245 | 274.9244 | 280.3382 | 283.0599 | 285.6562 | 288.0735 | 195 | 236 | 256 | 265 | 271 | 182 | 226 | 258 | 233 | 354 | 288.0667 | 295.4242 | 302.7818 | 310.1394 | 317.497 | 324.8545 | 332.2121 | 339.5697 | 346.9273 | 354.2848 | 361.6424
Mt Maunganui | 74 | 92 | 84 | 119 | 105 | 83 | 92 | 113 | 148 | 137 | 130.7363 | 131.7349 | 131.2465 | 131.3762 | 129.3616 | 124.6225 | 119.0657 | 115.6166 | 115.4395 | 115.4238 | 116.0362 | 74 | 92 | 84 | 119 | 105 | 83 | 92 | 113 | 148 | 137 | 138.0667 | 144.1333 | 150.2 | 156.2667 | 162.3333 | 168.4 | 174.4667 | 180.5333 | 186.6 | 192.6667 | 198.7333
Rangitikei | 100 | 93 | 116 | 142 | 177 | 122 | 127 | 218 | 226 | 266 | 243.5096 | 245.2055 | 238.6137 | 235.7646 | 236.2045 | 238.1275 | 240.1688 | 242.4159 | 244.5506 | 246.8362 | 249.2192 | 100 | 93 | 116 | 142 | 177 | 122 | 127 | 218 | 226 | 266 | 253.2 | 270.3818 | 287.5636 | 304.7455 | 321.9273 | 339.1091 | 356.2909 | 373.4727 | 390.6545 | 407.8364 | 425.0182
Taranaki | 264 | 260 | 271 | 302 | 425 | 309 | 311 | 382 | 424 | 634 | 429.2831 | 435.0022 | 427.1065 | 419.36 | 414.9568 | 412.7754 | 412.7671 | 415.0077 | 420.982 | 423.1287 | 426.7769 | 264 | 260 | 271 | 302 | 425 | 309 | 311 | 382 | 424 | 634 | 523 | 552.9636 | 582.9273 | 612.8909 | 642.8545 | 672.8182 | 702.7818 | 732.7455 | 762.7091 | 792.6727 | 822.6364
Tararua | 112 | 102 | 96 | 116 | 180 | 119 | 126 | 184 | 192 | 219 | 177.4293 | 179.4371 | 176.3866 | 175.1094 | 176.3364 | 177.9125 | 180.2444 | 185.5429 | 188.3534 | 190.4854 | 193.3053 | 112 | 102 | 96 | 116 | 180 | 119 | 126 | 184 | 192 | 219 | 211.3333 | 223.4667 | 235.6 | 247.7333 | 259.8667 | 272 | 284.1333 | 296.2667 | 308.4 | 320.5333 | 332.6667
Tauranga | 173 | 213 | 135 | 255 | 192 | 148 | 193 | 219 | 256 | 234 | 198.0683 | 197.6026 | 196.7517 | 196.9851 | 194.8723 | 187.5843 | 180.4186 | 176.0366 | 175.3674 | 175.3477 | 175.844 | 173 | 213 | 135 | 255 | 192 | 148 | 193 | 219 | 256 | 234 | 236.4667 | 242.7697 | 249.0727 | 255.3758 | 261.6788 | 267.9818 | 274.2848 | 280.5879 | 286.8909 | 293.1939 | 299.497
Waikato | 178 | 247 | 177 | 212 | 152 | 183 | 111 | 127 | 277 | 141 | 189.4796 | 189.8136 | 190.131 | 190.2121 | 190.5922 | 184.824 | 180.1429 | 178.4432 | 177.811 | 177.768 | 177.1366 | 178 | 247 | 177 | 212 | 152 | 183 | 111 | 127 | 277 | 141 | 159 | 155.0909 | 151.1818 | 147.2727 | 143.3636 | 139.4545 | 135.5455 | 131.6364 | 127.7273 | 123.8182 | 119.9091
Waikino | 83 | 87 | 63 | 49 | 48 | 53 | 83 | 66 | 90 | 95 | 82.5132 | 83.9489 | 85.0972 | 86.2678 | 87.6523 | 86.3641 | 85.0031 | 84.9258 | 85.5974 | 86.4019 | 86.9782 | 83 | 87 | 63 | 49 | 48 | 53 | 83 | 66 | 90 | 95 | 80.0667 | 81.5879 | 83.1091 | 84.6303 | 86.1515 | 87.6727 | 89.1939 | 90.7152 | 92.2364 | 93.7576 | 95.2788
Wairarapa | 227 | 229 | 188 | 276 | 266 | 245 | 359 | 388 | 319 | 457 | 374.1002 | 378.6076 | 364.1249 | 352.8297 | 350.159 | 352.8766 | 355.606 | 359.6657 | 366.031 | 373.362 | 379.279 | 227 | 229 | 188 | 276 | 266 | 245 | 359 | 388 | 319 | 457 | 426.3333 | 450.1394 | 473.9455 | 497.7515 | 521.5576 | 545.3636 | 569.1697 | 592.9758 | 616.7818 | 640.5879 | 664.3939
Whanganui | 93 | 79 | 111 | 133 | 152 | 132 | 130 | 196 | 209 | 308 | 212.7343 | 216.1103 | 212.135 | 210.3585 | 210.9956 | 211.578 | 212.7796 | 214.5 | 216.0004 | 217.3791 | 219.3741 | 93 | 79 | 111 | 133 | 152 | 132 | 130 | 196 | 209 | 308 | 262.3333 | 281.9758 | 301.6182 | 321.2606 | 340.903 | 360.5455 | 380.1879 | 399.8303 | 419.4727 | 439.1152 | 458.7576

## Modelled Duration
Forecast Duration
[16 empty] | Trend Influence | 0.5 | 0.4 | 0.2 | 0 | 0
| Duration | [20 empty] | Linear trend
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Poles
| History | [9 empty] | Forecast | Weighted average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 145.7304 | 119.0185 | 164.9857 | 300.0481 | 148.909 | 171.7725 | 300.9924 | 252.3649 | 135.072 | 359.9318
[11 empty] | 213.0066 | 215.3313 | 217.656 | 219.9808 | 222.3055 | 224.6302 | 225.7926 | 227.6523 | 229.0472 | 229.0472 | 229.0472 | [10 empty] | 227.335 | 238.9586 | 250.5822 | 262.2058 | 273.8294 | 285.453 | 297.0765 | 308.7001 | 320.3237 | 331.9473 | 343.5709
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0 | 163.8647 | 221.3597 | 148.9178 | 57.9208 | 397 | 97.3282 | 127.8634 | 356.9181 | 0 | 177.9348 | 179.2296 | 180.5244 | 181.8192 | 183.114 | 184.4088 | 185.0562 | 186.092 | 186.8689 | 186.8689 | 186.8689 | 0 | 163.8647 | 221.3597 | 148.9178 | 57.9208 | 397 | 97.3282 | 127.8634 | 356.9181 | 0 | 192.7241 | 199.198 | 205.672 | 212.1459 | 218.6199 | 225.0938 | 231.5678 | 238.0418 | 244.5157 | 250.9897 | 257.4636
Egmont | 98.2912 | 85.8876 | 257 | 204 | 77.4126 | 0 | 39.913 | 17 | 135.0181 | 187.9913 | 120.5115 | 119.7619 | 119.0122 | 118.2626 | 117.5129 | 116.7633 | 116.3885 | 115.7888 | 115.339 | 115.339 | 115.339 | 98.2912 | 85.8876 | 257 | 204 | 77.4126 | 0 | 39.913 | 17 | 135.0181 | 187.9913 | 89.6361 | 85.8879 | 82.1396 | 78.3914 | 74.6432 | 70.8949 | 67.1467 | 63.3985 | 59.6502 | 55.902 | 52.1538
Kinleith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3765 | 0 | 0 | 76.3765 | 76.8394 | 77.3023 | 77.7652 | 78.2281 | 78.6909 | 78.9224 | 79.2927 | 79.5704 | 79.5704 | 79.5704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.3765 | 0 | 0 | 20.3671 | 22.6815 | 24.9959 | 27.3104 | 29.6248 | 31.9393 | 34.2537 | 36.5681 | 38.8826 | 41.197 | 43.5115
Manawatu | 0 | 139.9389 | 91.4763 | 189.1024 | 0 | 89.3891 | 64 | 657 | 25.2251 | 0 | 158.3246 | 160.4321 | 162.5397 | 164.6472 | 166.7547 | 168.8622 | 169.916 | 171.602 | 172.8665 | 172.8665 | 172.8665 | 0 | 139.9389 | 91.4763 | 189.1024 | 0 | 89.3891 | 64 | 657 | 25.2251 | 0 | 183.57 | 194.1076 | 204.6452 | 215.1828 | 225.7204 | 236.258 | 246.7956 | 257.3332 | 267.8708 | 278.4084 | 288.946
Mt Maunganui | 0 | 138 | 203.9083 | 124.1381 | 66.5356 | 239.2158 | 0 | 0 | 165 | 0 | 148.1342 | 146.8854 | 145.6366 | 144.3878 | 143.139 | 141.8901 | 141.2657 | 140.2667 | 139.5174 | 139.5174 | 139.5174 | 0 | 138 | 203.9083 | 124.1381 | 66.5356 | 239.2158 | 0 | 0 | 165 | 0 | 59.3373 | 53.0932 | 46.8491 | 40.605 | 34.3609 | 28.1168 | 21.8727 | 15.6286 | 9.3845 | 3.1404 | -3.1037
Rangitikei | 117 | 6 | 0 | 1046.0246 | 113.6771 | 135.2102 | 272.8797 | 1152.25 | 210.3002 | 96 | 391.368 | 397.0703 | 402.7727 | 408.4751 | 414.1774 | 419.8798 | 422.731 | 427.2929 | 430.7143 | 430.7143 | 430.7143 | 117 | 6 | 0 | 1046.0246 | 113.6771 | 135.2102 | 272.8797 | 1152.25 | 210.3002 | 96 | 471.7492 | 500.261 | 528.7728 | 557.2846 | 585.7964 | 614.3083 | 642.8201 | 671.3319 | 699.8437 | 728.3555 | 756.8674
Taranaki | 91.895 | 154.8938 | 263.0588 | 145 | 367.848 | 79.5533 | 224.85 | 30.4264 | 39.6667 | 1582.6381 | 274.8877 | 288.7037 | 302.5197 | 316.3357 | 330.1517 | 343.9676 | 350.8756 | 361.9284 | 370.218 | 370.218 | 370.218 | 91.895 | 154.8938 | 263.0588 | 145 | 367.848 | 79.5533 | 224.85 | 30.4264 | 39.6667 | 1582.6381 | 677.9227 | 747.0027 | 816.0826 | 885.1625 | 954.2425 | 1023.3224 | 1092.4024 | 1161.4823 | 1230.5623 | 1299.6422 | 1368.7222
Tararua | 258.7545 | 113.507 | 83.5976 | 156.2677 | 86.1302 | 97.7363 | 115.7158 | 71.132 | 101.8354 | 56.3013 | 98.4955 | 95.9789 | 93.4624 | 90.9458 | 88.4292 | 85.9127 | 84.6544 | 82.6412 | 81.1312 | 81.1312 | 81.1312 | 258.7545 | 113.507 | 83.5976 | 156.2677 | 86.1302 | 97.7363 | 115.7158 | 71.132 | 101.8354 | 56.3013 | 44.8925 | 32.3097 | 19.7269 | 7.1442 | -5.4386 | -18.0214 | -30.6042 | -43.1869 | -55.7697 | -68.3525 | -80.9353
Tauranga | 215.01 | 23.8683 | 272.4792 | 658.0174 | 0 | 30.032 | 185 | 16.2405 | 40.1218 | 182 | 250.5602 | 247.1013 | 243.6425 | 240.1837 | 236.7249 | 233.266 | 231.5366 | 228.7696 | 226.6943 | 226.6943 | 226.6943 | 215.01 | 23.8683 | 272.4792 | 658.0174 | 0 | 30.032 | 185 | 16.2405 | 40.1218 | 182 | 67.1593 | 49.8652 | 32.571 | 15.2769 | -2.0172 | -19.3113 | -36.6054 | -53.8996 | -71.1937 | -88.4878 | -105.7819
Waikato | 102.3985 | 95 | 58 | 346.2511 | 236.7492 | 66.9217 | 176.0683 | 172.3519 | 131.8667 | 118.25 | 176.8008 | 177.1549 | 177.509 | 177.8631 | 178.2172 | 178.5712 | 178.7483 | 179.0315 | 179.244 | 179.244 | 179.244 | 102.3985 | 95 | 58 | 346.2511 | 236.7492 | 66.9217 | 176.0683 | 172.3519 | 131.8667 | 118.25 | 160.1229 | 161.8933 | 163.6636 | 165.434 | 167.2044 | 168.9748 | 170.7452 | 172.5156 | 174.286 | 176.0563 | 177.8267
Waikino | 0 | 53 | 0 | 0 | 0 | 0 | 736.4261 | 0 | 0 | 177.6963 | 376.249 | 380.4157 | 384.5824 | 388.7491 | 392.9158 | 397.0826 | 399.1659 | 402.4993 | 404.9993 | 404.9993 | 404.9993 | 0 | 53 | 0 | 0 | 0 | 0 | 736.4261 | 0 | 0 | 177.6963 | 211.2971 | 232.1307 | 252.9643 | 273.7979 | 294.6315 | 315.4651 | 336.2987 | 357.1323 | 377.9659 | 398.7995 | 419.6332
Wairarapa | 223.4944 | 222.0549 | 90.9108 | 177.9366 | 117.6393 | 410.8943 | 222.7354 | 275.8746 | 259.8399 | 91.5088 | 214.7459 | 215.266 | 215.7861 | 216.3063 | 216.8264 | 217.3465 | 217.6065 | 218.0226 | 218.3347 | 218.3347 | 218.3347 | 223.4944 | 222.0549 | 90.9108 | 177.9366 | 117.6393 | 410.8943 | 222.7354 | 275.8746 | 259.8399 | 91.5088 | 223.5921 | 226.1927 | 228.7933 | 231.3939 | 233.9944 | 236.595 | 239.1956 | 241.7962 | 244.3967 | 246.9973 | 249.5979
Whanganui | 59 | 232.2069 | 108.0667 | 104.8736 | 216.2684 | 0 | 1176 | 179.4986 | 20 | 747 | 304.6972 | 314.4679 | 324.2386 | 334.0093 | 343.78 | 353.5507 | 358.436 | 366.2526 | 372.115 | 372.115 | 372.115 | 59 | 232.2069 | 108.0667 | 104.8736 | 216.2684 | 0 | 1176 | 179.4986 | 20 | 747 | 552.9855 | 601.8389 | 650.6924 | 699.5459 | 748.3993 | 797.2528 | 846.1063 | 894.9597 | 943.8132 | 992.6667 | 1041.5201
Xarms
| History | [9 empty] | Forecast | Weighted average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 83.5654 | 85.9145 | 78.9782 | 109.1959 | 105.9628 | 78.6012 | 88.0785 | 105.1263 | 95.1743 | 90.4271
[11 empty] | 95.2565 | 95.4684 | 95.6802 | 95.892 | 96.1038 | 96.3156 | 96.4215 | 96.591 | 96.7181 | 96.7181 | 96.7181 | [10 empty] | 97.1124 | 98.1715 | 99.2306 | 100.2897 | 101.3488 | 102.4079 | 103.467 | 104.5261 | 105.5852 | 106.6443 | 107.7034
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 59.5881 | 41.5041 | 67.9183 | 104.0411 | 67.0423 | 66.7896 | 133.937 | 66.6672 | 67.1845 | 79.0282 | 76.4064 | 76.9372 | 77.468 | 77.9988 | 78.5296 | 79.0604 | 79.3258 | 79.7504 | 80.0689 | 80.0689 | 80.0689 | 59.5881 | 41.5041 | 67.9183 | 104.0411 | 67.0423 | 66.7896 | 133.937 | 66.6672 | 67.1845 | 79.0282 | 89.9668 | 92.6208 | 95.2747 | 97.9287 | 100.5826 | 103.2366 | 105.8906 | 108.5445 | 111.1985 | 113.8524 | 116.5064
Egmont | 84.7084 | 64.2916 | 101.8463 | 105.4639 | 230.2376 | 68.8994 | 98.4656 | 93.5536 | 59.7926 | 79.582 | 106.9181 | 106.5527 | 106.1873 | 105.822 | 105.4566 | 105.0912 | 104.9086 | 104.6163 | 104.397 | 104.397 | 104.397 | 84.7084 | 64.2916 | 101.8463 | 105.4639 | 230.2376 | 68.8994 | 98.4656 | 93.5536 | 59.7926 | 79.582 | 88.6365 | 86.8097 | 84.9829 | 83.1561 | 81.3292 | 79.5024 | 77.6756 | 75.8487 | 74.0219 | 72.1951 | 70.3683
Kinleith | 66.2191 | 132 | 25 | 96.9223 | 0 | 88.0853 | 28.5238 | 149.7227 | 171.6662 | 269.6943 | 137.6699 | 140.8401 | 144.0103 | 147.1806 | 150.3508 | 153.521 | 155.1062 | 157.6423 | 159.5445 | 159.5445 | 159.5445 | 66.2191 | 132 | 25 | 96.9223 | 0 | 88.0853 | 28.5238 | 149.7227 | 171.6662 | 269.6943 | 189.9648 | 205.816 | 221.6671 | 237.5183 | 253.3695 | 269.2207 | 285.0718 | 300.923 | 316.7742 | 332.6253 | 348.4765
Manawatu | 54.2278 | 71.1594 | 86.3559 | 125.2416 | 86.9549 | 63.9456 | 68.0642 | 98.4092 | 66.7534 | 50.4444 | 81.2271 | 80.9857 | 80.7443 | 80.5028 | 80.2614 | 80.02 | 79.8993 | 79.7062 | 79.5613 | 79.5613 | 79.5613 | 54.2278 | 71.1594 | 86.3559 | 125.2416 | 86.9549 | 63.9456 | 68.0642 | 98.4092 | 66.7534 | 50.4444 | 70.5167 | 69.3096 | 68.1026 | 66.8955 | 65.6884 | 64.4813 | 63.2743 | 62.0672 | 60.8601 | 59.653 | 58.446
Mt Maunganui | 124.91 | 97.9634 | 120.3394 | 136.9234 | 40.6805 | 14.6002 | 66.3475 | 56.5845 | 77.2443 | 84.9714 | 76.9014 | 75.6153 | 74.3291 | 73.043 | 71.7568 | 70.4707 | 69.8276 | 68.7987 | 68.0271 | 68.0271 | 68.0271 | 124.91 | 97.9634 | 120.3394 | 136.9234 | 40.6805 | 14.6002 | 66.3475 | 56.5845 | 77.2443 | 84.9714 | 46.6877 | 40.257 | 33.8263 | 27.3956 | 20.9649 | 14.5343 | 8.1036 | 1.6729 | -4.7578 | -11.1885 | -17.6192
Rangitikei | 80.8582 | 170.9382 | 132.6724 | 169.1167 | 144.6876 | 90.2759 | 130.6984 | 134.8988 | 137.9061 | 85.5035 | 130.1485 | 129.7268 | 129.305 | 128.8832 | 128.4615 | 128.0397 | 127.8288 | 127.4914 | 127.2384 | 127.2384 | 127.2384 | 80.8582 | 170.9382 | 132.6724 | 169.1167 | 144.6876 | 90.2759 | 130.6984 | 134.8988 | 137.9061 | 85.5035 | 116.1572 | 114.0484 | 111.9396 | 109.8308 | 107.722 | 105.6133 | 103.5045 | 101.3957 | 99.2869 | 97.1781 | 95.0693
Taranaki | 78.0601 | 65.4927 | 87.0084 | 109.5387 | 123.457 | 63.3972 | 109.22 | 110.2681 | 73.2577 | 78.7213 | 91.6886 | 91.8287 | 91.9689 | 92.109 | 92.2491 | 92.3892 | 92.4592 | 92.5713 | 92.6554 | 92.6554 | 92.6554 | 78.0601 | 65.4927 | 87.0084 | 109.5387 | 123.457 | 63.3972 | 109.22 | 110.2681 | 73.2577 | 78.7213 | 93.6951 | 94.3956 | 95.0962 | 95.7967 | 96.4973 | 97.1978 | 97.8983 | 98.5989 | 99.2994 | 100 | 100.7005
Tararua | 137.1531 | 154.7924 | 78.1157 | 140.0982 | 132.4237 | 107.3246 | 88.462 | 69.2371 | 204.1308 | 140.6028 | 126.4812 | 126.6655 | 126.8497 | 127.034 | 127.2182 | 127.4025 | 127.4946 | 127.642 | 127.7526 | 127.7526 | 127.7526 | 137.1531 | 154.7924 | 78.1157 | 140.0982 | 132.4237 | 107.3246 | 88.462 | 69.2371 | 204.1308 | 140.6028 | 130.3012 | 131.2225 | 132.1438 | 133.0651 | 133.9864 | 134.9077 | 135.829 | 136.7503 | 137.6716 | 138.5929 | 139.5142
Tauranga | 84.0396 | 68.7839 | 41.301 | 82.8822 | 98.0646 | 68.6278 | 63.5179 | 59.3533 | 86.355 | 53.2026 | 71.579 | 71.3949 | 71.2109 | 71.0269 | 70.8429 | 70.6589 | 70.5669 | 70.4197 | 70.3093 | 70.3093 | 70.3093 | 84.0396 | 68.7839 | 41.301 | 82.8822 | 98.0646 | 68.6278 | 63.5179 | 59.3533 | 86.355 | 53.2026 | 65.5527 | 64.6326 | 63.7126 | 62.7926 | 61.8726 | 60.9526 | 60.0325 | 59.1125 | 58.1925 | 57.2725 | 56.3524
Waikato | 83.6542 | 92.5967 | 81.6459 | 88.0293 | 75.5032 | 74.2896 | 55.109 | 94.6031 | 59.6669 | 55.5019 | 74.875 | 74.2458 | 73.6166 | 72.9874 | 72.3583 | 71.7291 | 71.4145 | 70.9112 | 70.5337 | 70.5337 | 70.5337 | 83.6542 | 92.5967 | 81.6459 | 88.0293 | 75.5032 | 74.2896 | 55.109 | 94.6031 | 59.6669 | 55.5019 | 58.7577 | 55.6119 | 52.466 | 49.3202 | 46.1743 | 43.0284 | 39.8826 | 36.7367 | 33.5908 | 30.445 | 27.2991
Waikino | 86.9393 | 42.7361 | 89.7873 | 110.4112 | 72.2353 | 111.5004 | 55.7781 | 162.9046 | 32.749 | 55.0261 | 79.0389 | 78.8981 | 78.7573 | 78.6165 | 78.4757 | 78.3349 | 78.2644 | 78.1518 | 78.0673 | 78.0673 | 78.0673 | 86.9393 | 42.7361 | 89.7873 | 110.4112 | 72.2353 | 111.5004 | 55.7781 | 162.9046 | 32.749 | 55.0261 | 78.1342 | 77.4301 | 76.726 | 76.0219 | 75.3178 | 74.6137 | 73.9096 | 73.2055 | 72.5014 | 71.7974 | 71.0933
Wairarapa | 101.5815 | 62.2724 | 40.8975 | 74.6746 | 123.5003 | 126.0907 | 140.5228 | 129.8783 | 102.8651 | 77.2442 | 100.1559 | 101.0167 | 101.8775 | 102.7383 | 103.5991 | 104.4599 | 104.8903 | 105.5789 | 106.0954 | 106.0954 | 106.0954 | 101.5815 | 62.2724 | 40.8975 | 74.6746 | 123.5003 | 126.0907 | 140.5228 | 129.8783 | 102.8651 | 77.2442 | 121.6245 | 125.9284 | 130.2324 | 134.5363 | 138.8403 | 143.1443 | 147.4482 | 151.7522 | 156.0561 | 160.3601 | 164.664
Whanganui | 44.4112 | 52.358 | 73.8289 | 76.2035 | 76.7667 | 77.989 | 106.3745 | 140.5619 | 97.6941 | 66.03 | 85.2449 | 86.381 | 87.5172 | 88.6533 | 89.7895 | 90.9256 | 91.4937 | 92.4026 | 93.0843 | 93.0843 | 93.0843 | 44.4112 | 52.358 | 73.8289 | 76.2035 | 76.7667 | 77.989 | 106.3745 | 140.5619 | 97.6941 | 66.03 | 112.4659 | 118.1466 | 123.8273 | 129.5081 | 135.1888 | 140.8696 | 146.5503 | 152.2311 | 157.9118 | 163.5925 | 169.2733
Conductor
| History | [9 empty] | Forecast | Weighted average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 95.1167 | 115.9301 | 131.5884 | 155.862 | 182.0604 | 142.2767 | 168.7129 | 182.1399 | 127.3446 | 117.316
[11 empty] | 154.8448 | 155.4038 | 155.9628 | 156.5218 | 157.0808 | 157.6398 | 157.9193 | 158.3665 | 158.7019 | 158.7019 | 158.7019 | [10 empty] | 155.806 | 158.6009 | 161.3959 | 164.1908 | 166.9858 | 169.7808 | 172.5757 | 175.3707 | 178.1656 | 180.9606 | 183.7556
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 70.4669 | 106.3224 | 185.3178 | 226.7258 | 52.5302 | 213.0961 | 187.323 | 108.7966 | 59.8149 | 102.0864 | 147.0089 | 146.5468 | 146.0847 | 145.6226 | 145.1605 | 144.6984 | 144.4674 | 144.0977 | 143.8205 | 143.8205 | 143.8205 | 70.4669 | 106.3224 | 185.3178 | 226.7258 | 52.5302 | 213.0961 | 187.323 | 108.7966 | 59.8149 | 102.0864 | 118.5405 | 116.2301 | 113.9196 | 111.6092 | 109.2987 | 106.9883 | 104.6778 | 102.3674 | 100.0569 | 97.7464 | 95.436
Egmont | 128.6032 | 71.9233 | 101.4054 | 116.7242 | 319.4939 | 63.0839 | 141.7805 | 105.9774 | 121.5982 | 131.3112 | 154.1799 | 154.4389 | 154.698 | 154.957 | 155.2161 | 155.4751 | 155.6047 | 155.8119 | 155.9673 | 155.9673 | 155.9673 | 128.6032 | 71.9233 | 101.4054 | 116.7242 | 319.4939 | 63.0839 | 141.7805 | 105.9774 | 121.5982 | 131.3112 | 137.314 | 138.6092 | 139.9045 | 141.1997 | 142.4949 | 143.7902 | 145.0854 | 146.3807 | 147.6759 | 148.9712 | 150.2664
Kinleith | 50.2765 | 82.9329 | 191.3792 | 83.6962 | 111.7023 | 150.3881 | 82.9228 | 0 | 185.5844 | 160.5811 | 131.9654 | 132.9239 | 133.8825 | 134.841 | 135.7995 | 136.758 | 137.2372 | 138.004 | 138.5792 | 138.5792 | 138.5792 | 50.2765 | 82.9329 | 191.3792 | 83.6962 | 111.7023 | 150.3881 | 82.9228 | 0 | 185.5844 | 160.5811 | 136.3054 | 141.0979 | 145.8905 | 150.683 | 155.4756 | 160.2682 | 165.0607 | 169.8533 | 174.6458 | 179.4384 | 184.2309
Manawatu | 66.3882 | 76.8579 | 81.1512 | 86.4623 | 90.1125 | 89.4132 | 85.9465 | 85.863 | 62.8518 | 73.2141 | 81.6147 | 81.5961 | 81.5776 | 81.5591 | 81.5405 | 81.522 | 81.5127 | 81.4979 | 81.4868 | 81.4868 | 81.4868 | 66.3882 | 76.8579 | 81.1512 | 86.4623 | 90.1125 | 89.4132 | 85.9465 | 85.863 | 62.8518 | 73.2141 | 79.3162 | 79.2235 | 79.1308 | 79.0381 | 78.9454 | 78.8527 | 78.7599 | 78.6672 | 78.5745 | 78.4818 | 78.3891
Mt Maunganui | 81.2806 | 113.8355 | 83.6005 | 187.5211 | 123.3231 | 110.7856 | 106.9444 | 241.4513 | 102.1894 | 70.8225 | 134.5451 | 134.9807 | 135.4162 | 135.8518 | 136.2873 | 136.7229 | 136.9407 | 137.2891 | 137.5505 | 137.5505 | 137.5505 | 81.2806 | 113.8355 | 83.6005 | 187.5211 | 123.3231 | 110.7856 | 106.9444 | 241.4513 | 102.1894 | 70.8225 | 134.1534 | 136.3313 | 138.5091 | 140.6869 | 142.8647 | 145.0425 | 147.2204 | 149.3982 | 151.576 | 153.7538 | 155.9317
Rangitikei | 174.8615 | 102.5426 | 87.046 | 184.3156 | 222.5268 | 140.1511 | 268.5333 | 216.0096 | 172.4671 | 127.5543 | 175.7067 | 176.7719 | 177.8371 | 178.9023 | 179.9675 | 181.0327 | 181.5653 | 182.4175 | 183.0566 | 183.0566 | 183.0566 | 174.8615 | 102.5426 | 87.046 | 184.3156 | 222.5268 | 140.1511 | 268.5333 | 216.0096 | 172.4671 | 127.5543 | 198.8942 | 204.2203 | 209.5463 | 214.8724 | 220.1985 | 225.5245 | 230.8506 | 236.1767 | 241.5027 | 246.8288 | 252.1549
Taranaki | 72.3744 | 118.1641 | 94.3894 | 271.2948 | 380.3537 | 69.0504 | 204.8939 | 123.7321 | 93.6522 | 134.5792 | 191.1881 | 191.2178 | 191.2474 | 191.2771 | 191.3067 | 191.3364 | 191.3512 | 191.3749 | 191.3927 | 191.3927 | 191.3927 | 72.3744 | 118.1641 | 94.3894 | 271.2948 | 380.3537 | 69.0504 | 204.8939 | 123.7321 | 93.6522 | 134.5792 | 157.064 | 157.2122 | 157.3605 | 157.5088 | 157.6571 | 157.8054 | 157.9537 | 158.1019 | 158.2502 | 158.3985 | 158.5468
Tararua | 105.3296 | 203.9114 | 138.5805 | 142.0554 | 208.0033 | 271.4704 | 204.6367 | 496.0435 | 293.8161 | 210.0829 | 246.7087 | 251.0853 | 255.4618 | 259.8383 | 264.2149 | 268.5914 | 270.7797 | 274.2809 | 276.9068 | 276.9068 | 276.9068 | 105.3296 | 203.9114 | 138.5805 | 142.0554 | 208.0033 | 271.4704 | 204.6367 | 496.0435 | 293.8161 | 210.0829 | 347.7476 | 369.6303 | 391.513 | 413.3956 | 435.2783 | 457.161 | 479.0436 | 500.9263 | 522.8089 | 544.6916 | 566.5743
Tauranga | 137.8103 | 84.0154 | 87.8785 | 108.3303 | 116.1431 | 103.3683 | 111.1326 | 102.8155 | 107.3548 | 110.281 | 106.4555 | 106.4384 | 106.4214 | 106.4043 | 106.3872 | 106.3702 | 106.3617 | 106.348 | 106.3378 | 106.3378 | 106.3378 | 137.8103 | 84.0154 | 87.8785 | 108.3303 | 116.1431 | 103.3683 | 111.1326 | 102.8155 | 107.3548 | 110.281 | 106.444 | 106.3587 | 106.2734 | 106.1881 | 106.1029 | 106.0176 | 105.9323 | 105.847 | 105.7618 | 105.6765 | 105.5912
Waikato | 52.7212 | 166.4408 | 74.565 | 114.7703 | 132.0655 | 48.6288 | 62.1567 | 176.9194 | 62.3162 | 58.6226 | 102.3354 | 101.8442 | 101.353 | 100.8617 | 100.3705 | 99.8793 | 99.6336 | 99.2407 | 98.9459 | 98.9459 | 98.9459 | 52.7212 | 166.4408 | 74.565 | 114.7703 | 132.0655 | 48.6288 | 62.1567 | 176.9194 | 62.3162 | 58.6226 | 81.4118 | 78.9556 | 76.4995 | 74.0433 | 71.5872 | 69.131 | 66.6749 | 64.2187 | 61.7626 | 59.3064 | 56.8503
Waikino | 124.0398 | 86.1464 | 283.858 | 51.7044 | 85.0888 | 182.4497 | 80.9911 | 85.6695 | 181.406 | 98.2646 | 121.7778 | 121.3282 | 120.8787 | 120.4291 | 119.9796 | 119.53 | 119.3052 | 118.9456 | 118.6759 | 118.6759 | 118.6759 | 124.0398 | 86.1464 | 283.858 | 51.7044 | 85.0888 | 182.4497 | 80.9911 | 85.6695 | 181.406 | 98.2646 | 113.5991 | 111.3514 | 109.1036 | 106.8558 | 104.6081 | 102.3603 | 100.1125 | 97.8648 | 95.617 | 93.3692 | 91.1215
Wairarapa | 89.7523 | 197.9249 | 152.775 | 146.9833 | 152.2649 | 262.3203 | 394.5787 | 118.9623 | 67.702 | 132.0486 | 190.131 | 190.3163 | 190.5016 | 190.6869 | 190.8722 | 191.0575 | 191.1502 | 191.2985 | 191.4096 | 191.4096 | 191.4096 | 89.7523 | 197.9249 | 152.775 | 146.9833 | 152.2649 | 262.3203 | 394.5787 | 118.9623 | 67.702 | 132.0486 | 176.6274 | 177.554 | 178.4806 | 179.4071 | 180.3337 | 181.2603 | 182.1869 | 183.1134 | 184.04 | 184.9666 | 185.8932
Whanganui | 82.6126 | 96.074 | 148.7022 | 305.6227 | 373.1769 | 145.3917 | 261.4278 | 323.4392 | 144.7267 | 115.6593 | 229.3659 | 230.7614 | 232.1569 | 233.5525 | 234.948 | 236.3435 | 237.0413 | 238.1577 | 238.995 | 238.995 | 238.995 | 82.6126 | 96.074 | 148.7022 | 305.6227 | 373.1769 | 145.3917 | 261.4278 | 323.4392 | 144.7267 | 115.6593 | 238.0601 | 245.0377 | 252.0153 | 258.9929 | 265.9705 | 272.9481 | 279.9257 | 286.9033 | 293.8809 | 300.8585 | 307.8361
Transformers
| History | [9 empty] | Forecast | Weighted average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 94.193 | 266.243 | 114.4227 | 154.9533 | 168.5814 | 139.2909 | 93.5795 | 497.7079 | 277.1069 | 161.9058
[11 empty] | 196.6382 | 199.9665 | 203.2947 | 206.623 | 209.9513 | 213.2796 | 214.9437 | 217.6063 | 219.6033 | 219.6033 | 219.6033 | [10 empty] | 275.7476 | 292.389 | 309.0304 | 325.6717 | 342.3131 | 358.9545 | 375.5959 | 392.2373 | 408.8786 | 425.52 | 442.1614
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 237 | 75.0089 | 64.2603 | 123.0095 | 108.7647 | 199.9583 | 51.0538 | 431.6978 | 607.9792 | 104.8417 | 196.286 | 201.4423 | 206.5985 | 211.7547 | 216.9109 | 222.0671 | 224.6452 | 228.7702 | 231.8639 | 231.8639 | 231.8639 | 237 | 75.0089 | 64.2603 | 123.0095 | 108.7647 | 199.9583 | 51.0538 | 431.6978 | 607.9792 | 104.8417 | 342.1535 | 367.9346 | 393.7157 | 419.4968 | 445.2779 | 471.059 | 496.8401 | 522.6212 | 548.4023 | 574.1834 | 599.9645
Egmont | 102.4774 | 81.0479 | 65.5311 | 64.0681 | 152.4442 | 71.2895 | 109.0277 | 69.8086 | 38.8612 | 77.6366 | 81.0794 | 80.5415 | 80.0036 | 79.4657 | 78.9278 | 78.3899 | 78.121 | 77.6907 | 77.3679 | 77.3679 | 77.3679 | 102.4774 | 81.0479 | 65.5311 | 64.0681 | 152.4442 | 71.2895 | 109.0277 | 69.8086 | 38.8612 | 77.6366 | 68.4271 | 65.7376 | 63.0482 | 60.3587 | 57.6692 | 54.9798 | 52.2903 | 49.6008 | 46.9113 | 44.2219 | 41.5324
Kinleith | 69.5508 | 40.2974 | 135.5968 | 48 | 71.9951 | 156 | 0 | 0 | 150.7846 | 71.4248 | 74.8998 | 74.9632 | 75.0266 | 75.09 | 75.1534 | 75.2168 | 75.2485 | 75.2992 | 75.3372 | 75.3372 | 75.3372 | 69.5508 | 40.2974 | 135.5968 | 48 | 71.9951 | 156 | 0 | 0 | 150.7846 | 71.4248 | 76.1082 | 76.4251 | 76.7421 | 77.059 | 77.376 | 77.693 | 78.0099 | 78.3269 | 78.6438 | 78.9608 | 79.2777
Manawatu | 0 | 217 | 0 | 66.8428 | 52.8144 | 88.512 | 138.3582 | 2124.7578 | 82.25 | 83.5696 | 317.1228 | 330.0718 | 343.0207 | 355.9697 | 368.9187 | 381.8677 | 388.3422 | 398.7014 | 406.4707 | 406.4707 | 406.4707 | 0 | 217 | 0 | 66.8428 | 52.8144 | 88.512 | 138.3582 | 2124.7578 | 82.25 | 83.5696 | 641.5075 | 706.2524 | 770.9973 | 835.7422 | 900.4871 | 965.232 | 1029.9769 | 1094.7218 | 1159.4667 | 1224.2116 | 1288.9565
Mt Maunganui | 0 | 43 | 61.0285 | 220.9904 | 165.7291 | 87.9565 | 75.2354 | 345.6648 | 860.3312 | 329.8562 | 243.3102 | 254.9444 | 266.5785 | 278.2127 | 289.8468 | 301.481 | 307.298 | 316.6053 | 323.5858 | 323.5858 | 323.5858 | 0 | 43 | 61.0285 | 220.9904 | 165.7291 | 87.9565 | 75.2354 | 345.6648 | 860.3312 | 329.8562 | 538.9182 | 597.0889 | 655.2596 | 713.4303 | 771.601 | 829.7717 | 887.9424 | 946.1132 | 1004.2839 | 1062.4546 | 1120.6253
Rangitikei | 92.8182 | 1289 | 110 | 101.0501 | 350.8928 | 51.1433 | 235 | 54.0804 | 240.4743 | 209.1743 | 293.4239 | 285.5815 | 277.7391 | 269.8967 | 262.0543 | 254.212 | 250.2908 | 244.0168 | 239.3114 | 239.3114 | 239.3114 | 92.8182 | 1289 | 110 | 101.0501 | 350.8928 | 51.1433 | 235 | 54.0804 | 240.4743 | 209.1743 | 57.6976 | 18.4856 | -20.7263 | -59.9383 | -99.1502 | -138.3622 | -177.5741 | -216.7861 | -255.998 | -295.21 | -334.422
Taranaki | 51.0667 | 71.0713 | 266.35 | 117.6158 | 89.216 | 129.713 | 89.0495 | 164.3191 | 73.3598 | 70.0778 | 118.9747 | 118.5284 | 118.082 | 117.6357 | 117.1893 | 116.743 | 116.5198 | 116.1627 | 115.8949 | 115.8949 | 115.8949 | 51.0667 | 71.0713 | 266.35 | 117.6158 | 89.216 | 129.713 | 89.0495 | 164.3191 | 73.3598 | 70.0778 | 99.9094 | 97.6776 | 95.4459 | 93.2142 | 90.9824 | 88.7507 | 86.519 | 84.2872 | 82.0555 | 79.8238 | 77.592
Tararua | 0 | 0 | 35.2222 | 82 | 45.498 | 131.7826 | 85.1768 | 308.0692 | 160.906 | 185.8453 | 114.9445 | 120.1069 | 125.2693 | 130.4317 | 135.5941 | 140.7566 | 143.3378 | 147.4677 | 150.5652 | 150.5652 | 150.5652 | 0 | 0 | 35.2222 | 82 | 45.498 | 131.7826 | 85.1768 | 308.0692 | 160.906 | 185.8453 | 245.4167 | 271.2288 | 297.0409 | 322.853 | 348.6651 | 374.4772 | 400.2894 | 426.1015 | 451.9136 | 477.7257 | 503.5378
Tauranga | 97.7378 | 160.9121 | 331.8397 | 78.5988 | 138.794 | 401.8376 | 73.0551 | 1231.5046 | 113.5442 | 249.7589 | 308.8717 | 315.8794 | 322.8871 | 329.8948 | 336.9025 | 343.9102 | 347.414 | 353.0202 | 357.2248 | 357.2248 | 357.2248 | 97.7378 | 160.9121 | 331.8397 | 78.5988 | 138.794 | 401.8376 | 73.0551 | 1231.5046 | 113.5442 | 249.7589 | 480.47 | 515.5085 | 550.547 | 585.5855 | 620.624 | 655.6625 | 690.701 | 725.7395 | 760.778 | 795.8165 | 830.855
Waikato | 153.8336 | 775.335 | 33.1538 | 467.4603 | 254.1896 | 189.6915 | 43.3154 | 636.7865 | 459.1446 | 210.5351 | 341.068 | 341.0416 | 341.0152 | 340.9888 | 340.9624 | 340.9359 | 340.9227 | 340.9016 | 340.8858 | 340.8858 | 340.8858 | 153.8336 | 775.335 | 33.1538 | 467.4603 | 254.1896 | 189.6915 | 43.3154 | 636.7865 | 459.1446 | 210.5351 | 321.6183 | 321.4862 | 321.3542 | 321.2221 | 321.09 | 320.958 | 320.8259 | 320.6939 | 320.5618 | 320.4298 | 320.2977
Waikino | 2 | 110 | 52 | 465.3061 | 102.5831 | 48 | 50.3211 | 72.3333 | 328.6627 | 369.2167 | 177.6026 | 182.0119 | 186.4213 | 190.8306 | 195.24 | 199.6493 | 201.854 | 205.3815 | 208.0271 | 208.0271 | 208.0271 | 2 | 110 | 52 | 465.3061 | 102.5831 | 48 | 50.3211 | 72.3333 | 328.6627 | 369.2167 | 281.2996 | 303.3463 | 325.3931 | 347.4399 | 369.4866 | 391.5334 | 413.5802 | 435.627 | 457.6737 | 479.7205 | 501.7673
Wairarapa | 131.4455 | 66 | 103.6671 | 96.2563 | 222.5179 | 198.8783 | 113.2723 | 397.0327 | 293.7034 | 66.4492 | 173.0864 | 176.1205 | 179.1547 | 182.1889 | 185.2231 | 188.2572 | 189.7743 | 192.2017 | 194.0222 | 194.0222 | 194.0222 | 131.4455 | 66 | 103.6671 | 96.2563 | 222.5179 | 198.8783 | 113.2723 | 397.0327 | 293.7034 | 66.4492 | 252.3621 | 267.5329 | 282.7038 | 297.8747 | 313.0456 | 328.2164 | 343.3873 | 358.5582 | 373.7291 | 388.8999 | 404.0708
Whanganui | 4 | 0 | 0 | 83.194 | 436.1196 | 56.0196 | 60.0882 | 136.4403 | 192.3889 | 76.3887 | 115.6266 | 118.3308 | 121.0351 | 123.7393 | 126.4436 | 129.1478 | 130.5 | 132.6634 | 134.2859 | 134.2859 | 134.2859 | 4 | 0 | 0 | 83.194 | 436.1196 | 56.0196 | 60.0882 | 136.4403 | 192.3889 | 76.3887 | 178.8307 | 192.352 | 205.8732 | 219.3945 | 232.9157 | 246.4369 | 259.9582 | 273.4794 | 287.0007 | 300.5219 | 314.0431
Fuses
| History | [9 empty] | Forecast | Average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 62.3859 | 36.9117 | 55.034 | 63.5955 | 56.9518 | 60.1482 | 115.0613 | 188.3029 | 130.169 | 105.1315
[11 empty] | 88.3321 | 90.627 | 92.922 | 95.2169 | 97.5119 | 99.8069 | 100.9543 | 102.7903 | 104.1673 | 104.1673 | 104.1673 | [10 empty] | 148.3688 | 159.8435 | 171.3183 | 182.7931 | 194.2678 | 205.7426 | 217.2173 | 228.6921 | 240.1669 | 251.6416 | 263.1164
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 37.7553 | 53.8333 | 49.8045 | 75.1197 | 13.5413 | 83.7655 | 40.6824 | 99.2147 | 274.3799 | 106.9275 | 88.5854 | 91.4707 | 94.356 | 97.2412 | 100.1265 | 103.0117 | 104.4544 | 106.7626 | 108.4937 | 108.4937 | 108.4937 | 37.7553 | 53.8333 | 49.8045 | 75.1197 | 13.5413 | 83.7655 | 40.6824 | 99.2147 | 274.3799 | 106.9275 | 162.8471 | 177.2734 | 191.6997 | 206.126 | 220.5523 | 234.9785 | 249.4048 | 263.8311 | 278.2574 | 292.6837 | 307.11
Egmont | 45.7266 | 44.0049 | 49.1918 | 117.1601 | 58.7367 | 29.5046 | 79.0041 | 100.269 | 75.9466 | 169.6673 | 80.3872 | 82.1457 | 83.9042 | 85.6627 | 87.4211 | 89.1796 | 90.0589 | 91.4656 | 92.5207 | 92.5207 | 92.5207 | 45.7266 | 44.0049 | 49.1918 | 117.1601 | 58.7367 | 29.5046 | 79.0041 | 100.269 | 75.9466 | 169.6673 | 125.2793 | 134.0717 | 142.8641 | 151.6565 | 160.4489 | 169.2412 | 178.0336 | 186.826 | 195.6184 | 204.4108 | 213.2032
Kinleith | 0 | 0 | 57 | 51.2265 | 91.6249 | 52.7752 | 0 | 85.2877 | 54.2052 | 52.2614 | 49.3757 | 50.3438 | 51.3119 | 52.28 | 53.2481 | 54.2163 | 54.7003 | 55.4748 | 56.0557 | 56.0557 | 56.0557 | 0 | 0 | 57 | 51.2265 | 91.6249 | 52.7752 | 0 | 85.2877 | 54.2052 | 52.2614 | 71.0614 | 75.902 | 80.7426 | 85.5832 | 90.4238 | 95.2644 | 100.105 | 104.9456 | 109.7862 | 114.6268 | 119.4674
Manawatu | 60.236 | 41.661 | 54.6145 | 48.9801 | 52.4571 | 55.8541 | 49.0152 | 235.1365 | 45.1012 | 152.7386 | 81.7287 | 83.8653 | 86.002 | 88.1386 | 90.2752 | 92.4118 | 93.4802 | 95.1895 | 96.4714 | 96.4714 | 96.4714 | 60.236 | 41.661 | 54.6145 | 48.9801 | 52.4571 | 55.8541 | 49.0152 | 235.1365 | 45.1012 | 152.7386 | 138.3367 | 149.0198 | 159.703 | 170.3861 | 181.0692 | 191.7524 | 202.4355 | 213.1186 | 223.8018 | 234.4849 | 245.168
Mt Maunganui | 42.4615 | 25.4074 | 50.6882 | 57.5132 | 78.5747 | 0 | 16.8797 | 29.4133 | 86.9074 | 57.0315 | 44.7128 | 45.0217 | 45.3305 | 45.6393 | 45.9481 | 46.257 | 46.4114 | 46.6584 | 46.8437 | 46.8437 | 46.8437 | 42.4615 | 25.4074 | 50.6882 | 57.5132 | 78.5747 | 0 | 16.8797 | 29.4133 | 86.9074 | 57.0315 | 52.9804 | 54.5245 | 56.0686 | 57.6128 | 59.1569 | 60.701 | 62.2451 | 63.7893 | 65.3334 | 66.8775 | 68.4216
Rangitikei | 40.1039 | 37.9202 | 34.2358 | 117.7917 | 123.2022 | 62.9182 | 87.1338 | 133.2561 | 235.0806 | 147.9554 | 108.8327 | 112.0977 | 115.3627 | 118.6277 | 121.8927 | 125.1577 | 126.7902 | 129.4022 | 131.3612 | 131.3612 | 131.3612 | 40.1039 | 37.9202 | 34.2358 | 117.7917 | 123.2022 | 62.9182 | 87.1338 | 133.2561 | 235.0806 | 147.9554 | 191.7475 | 208.0725 | 224.3976 | 240.7226 | 257.0477 | 273.3727 | 289.6977 | 306.0228 | 322.3478 | 338.6728 | 354.9979
Taranaki | 41.3321 | 63.2466 | 46.6167 | 99.5134 | 45.6469 | 66.2834 | 46.7883 | 205.7519 | 174.1723 | 106.2865 | 94.9229 | 97.3704 | 99.8179 | 102.2654 | 104.713 | 107.1605 | 108.3842 | 110.3423 | 111.8108 | 111.8108 | 111.8108 | 41.3321 | 63.2466 | 46.6167 | 99.5134 | 45.6469 | 66.2834 | 46.7883 | 205.7519 | 174.1723 | 106.2865 | 156.8707 | 169.1083 | 181.3459 | 193.5835 | 205.8211 | 218.0587 | 230.2963 | 242.534 | 254.7716 | 267.0092 | 279.2468
Tararua | 71.8871 | 30.311 | 49.5344 | 34 | 26.4846 | 35.9167 | 32.5357 | 193.371 | 191.6386 | 119.4883 | 79.2534 | 82.0193 | 84.7853 | 87.5513 | 90.3172 | 93.0832 | 94.4662 | 96.679 | 98.3386 | 98.3386 | 98.3386 | 71.8871 | 30.311 | 49.5344 | 34 | 26.4846 | 35.9167 | 32.5357 | 193.371 | 191.6386 | 119.4883 | 154.581 | 168.4108 | 182.2407 | 196.0705 | 209.9004 | 223.7302 | 237.5601 | 251.39 | 265.2198 | 279.0497 | 292.8795
Tauranga | 17.1326 | 30.4957 | 38.2249 | 19.7696 | 43.944 | 43.9951 | 46.6956 | 93.6187 | 85.6449 | 71.0696 | 52.6065 | 54.0965 | 55.5865 | 57.0766 | 58.5666 | 60.0566 | 60.8016 | 61.9937 | 62.8877 | 62.8877 | 62.8877 | 17.1326 | 30.4957 | 38.2249 | 19.7696 | 43.944 | 43.9951 | 46.6956 | 93.6187 | 85.6449 | 71.0696 | 90.0349 | 97.4851 | 104.9352 | 112.3854 | 119.8355 | 127.2857 | 134.7358 | 142.186 | 149.6361 | 157.0863 | 164.5364
Waikato | 47.5571 | 33.541 | 46.02 | 67.7109 | 61.6319 | 70.0058 | 26 | 108.374 | 119.4951 | 55.9899 | 65.4187 | 66.4764 | 67.5341 | 68.5918 | 69.6494 | 70.7071 | 71.236 | 72.0821 | 72.7167 | 72.7167 | 72.7167 | 47.5571 | 33.541 | 46.02 | 67.7109 | 61.6319 | 70.0058 | 26 | 108.374 | 119.4951 | 55.9899 | 92.7188 | 98.0071 | 103.2955 | 108.5839 | 113.8723 | 119.1607 | 124.4491 | 129.7375 | 135.0259 | 140.3143 | 145.6027
Waikino | 187.5006 | 23.609 | 43.4663 | 19 | 74.3858 | 73 | 828.8274 | 61.7663 | 125.9573 | 118.1279 | 152.0156 | 155.1812 | 158.3469 | 161.5126 | 164.6782 | 167.8439 | 169.4268 | 171.9593 | 173.8587 | 173.8587 | 173.8587 | 187.5006 | 23.609 | 43.4663 | 19 | 74.3858 | 73 | 828.8274 | 61.7663 | 125.9573 | 118.1279 | 242.6201 | 258.4484 | 274.2768 | 290.1052 | 305.9335 | 321.7619 | 337.5903 | 353.4186 | 369.247 | 385.0754 | 400.9037
Wairarapa | 30.3925 | 23.8109 | 53.0444 | 56.9568 | 37.4031 | 73.0175 | 60.7785 | 67.485 | 127.3705 | 125.1857 | 69.4503 | 71.5077 | 73.565 | 75.6224 | 77.6798 | 79.7372 | 80.7659 | 82.4118 | 83.6462 | 83.6462 | 83.6462 | 30.3925 | 23.8109 | 53.0444 | 56.9568 | 37.4031 | 73.0175 | 60.7785 | 67.485 | 127.3705 | 125.1857 | 122.1225 | 132.4094 | 142.6963 | 152.9832 | 163.2701 | 173.557 | 183.8439 | 194.1308 | 204.4177 | 214.7046 | 224.9915
Whanganui | 126.5455 | 35.0996 | 143 | 62 | 32.7403 | 74.7419 | 66.3947 | 1034.9932 | 96.2977 | 83.979 | 181.0274 | 186.5552 | 192.083 | 197.6108 | 203.1386 | 208.6664 | 211.4303 | 215.8526 | 219.1693 | 219.1693 | 219.1693 | 126.5455 | 35.0996 | 143 | 62 | 32.7403 | 74.7419 | 66.3947 | 1034.9932 | 96.2977 | 83.979 | 327.5939 | 355.2329 | 382.872 | 410.511 | 438.1501 | 465.7891 | 493.4281 | 521.0672 | 548.7062 | 576.3452 | 603.9843
Sub-Trans
| History | [9 empty] | Forecast | Weighted average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 114.5188 | 70.6262 | 161.6363 | 94.7626 | 62.1032 | 53.2724 | 94.498 | 65.1733 | 105.2366 | 118.3855
[11 empty] | 87.6295 | 87.3092 | 86.9889 | 86.6686 | 86.3483 | 86.028 | 85.8678 | 85.6115 | 85.4194 | 85.4194 | 85.4194 | [10 empty] | 61.6582 | 60.0566 | 58.4551 | 56.8535 | 55.2519 | 53.6504 | 52.0488 | 50.4473 | 48.8457 | 47.2441 | 45.6426
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 52.2089 | 14.7966 | 131.8452 | 0 | 142.9987 | 54.281 | 339.1338 | 157 | 0 | 77.4522 | 91.948 | 93.376 | 94.804 | 96.2319 | 97.6599 | 99.0879 | 99.8018 | 100.9442 | 101.801 | 101.801 | 101.801 | 52.2089 | 14.7966 | 131.8452 | 0 | 142.9987 | 54.281 | 339.1338 | 157 | 0 | 77.4522 | 136.2407 | 143.3805 | 150.5203 | 157.6602 | 164.8 | 171.9398 | 179.0797 | 186.2195 | 193.3593 | 200.4991 | 207.639
Egmont | 25 | 171.9367 | 65.4964 | 0 | 41.3861 | 36.0583 | 121.1343 | 0 | 90.9777 | 402.9907 | 120.7589 | 124.2325 | 127.7062 | 131.1799 | 134.6536 | 138.1273 | 139.8642 | 142.6431 | 144.7273 | 144.7273 | 144.7273 | 25 | 171.9367 | 65.4964 | 0 | 41.3861 | 36.0583 | 121.1343 | 0 | 90.9777 | 402.9907 | 191.0246 | 208.393 | 225.7615 | 243.1299 | 260.4984 | 277.8669 | 295.2353 | 312.6038 | 329.9723 | 347.3407 | 364.7092
Kinleith | 0 | 0 | 0 | 148.7415 | 0 | 0 | 0 | 0 | 60.0418 | 163.2327 | 119.0581 | 120.8074 | 122.5567 | 124.306 | 126.0553 | 127.8046 | 128.6792 | 130.0786 | 131.1282 | 131.1282 | 131.1282 | 0 | 0 | 0 | 148.7415 | 0 | 0 | 0 | 0 | 60.0418 | 163.2327 | 85.307 | 94.0535 | 102.7999 | 111.5463 | 120.2928 | 129.0392 | 137.7857 | 146.5321 | 155.2785 | 164.025 | 172.7714
Manawatu | 55.1657 | 12.6278 | 863 | 2 | 1.2441 | 61.8376 | 53.8718 | 0 | 96.3074 | 104.3371 | 102.1853 | 98.4635 | 94.7417 | 91.0199 | 87.298 | 83.5762 | 81.7153 | 78.7379 | 76.5048 | 76.5048 | 76.5048 | 55.1657 | 12.6278 | 863 | 2 | 1.2441 | 61.8376 | 53.8718 | 0 | 96.3074 | 104.3371 | 22.6895 | 4.0804 | -14.5286 | -33.1377 | -51.7467 | -70.3557 | -88.9648 | -107.5738 | -126.1828 | -144.7919 | -163.4009
Mt Maunganui | 32.5092 | 0 | 169.0367 | 135.2252 | 0 | 0 | 18.7863 | 49.0438 | 271.5902 | 75.0101 | 128.4962 | 130.1136 | 131.731 | 133.3484 | 134.9658 | 136.5832 | 137.3919 | 138.6859 | 139.6563 | 139.6563 | 139.6563 | 32.5092 | 0 | 169.0367 | 135.2252 | 0 | 0 | 18.7863 | 49.0438 | 271.5902 | 75.0101 | 119.5987 | 127.6858 | 135.7728 | 143.8598 | 151.9468 | 160.0338 | 168.1209 | 176.2079 | 184.2949 | 192.3819 | 200.4689
Rangitikei | 30.8325 | 94 | 69.4451 | 4.6563 | 71.0422 | 202.7609 | 0 | 82.2373 | 16.3976 | 0 | 105.2941 | 104.5195 | 103.745 | 102.9704 | 102.1959 | 101.4214 | 101.0341 | 100.4145 | 99.9497 | 99.9497 | 99.9497 | 30.8325 | 94 | 69.4451 | 4.6563 | 71.0422 | 202.7609 | 0 | 82.2373 | 16.3976 | 0 | 35.8372 | 31.9645 | 28.0918 | 24.2191 | 20.3464 | 16.4736 | 12.6009 | 8.7282 | 4.8555 | 0.98277 | -2.89
Taranaki | 18 | 0 | 25.2548 | 126.8762 | 111.84 | 10.3061 | 55.389 | 42.3933 | 122.591 | 45.5622 | 70.1007 | 71.1624 | 72.2241 | 73.2858 | 74.3475 | 75.4092 | 75.94 | 76.7893 | 77.4264 | 77.4264 | 77.4264 | 18 | 0 | 25.2548 | 126.8762 | 111.84 | 10.3061 | 55.389 | 42.3933 | 122.591 | 45.5622 | 85.0177 | 90.3262 | 95.6346 | 100.943 | 106.2515 | 111.5599 | 116.8684 | 122.1768 | 127.4853 | 132.7937 | 138.1022
Tararua | 40.1991 | 61.4404 | 78.6857 | 40.102 | 73.9942 | 0.99684 | 204 | 25.0669 | 19.5973 | 135.2077 | 73.9086 | 74.7725 | 75.6365 | 76.5005 | 77.3645 | 78.2284 | 78.6604 | 79.3516 | 79.87 | 79.87 | 79.87 | 40.1991 | 61.4404 | 78.6857 | 40.102 | 73.9942 | 0.99684 | 204 | 25.0669 | 19.5973 | 135.2077 | 91.6883 | 96.0081 | 100.328 | 104.6479 | 108.9677 | 113.2876 | 117.6075 | 121.9273 | 126.2472 | 130.5671 | 134.887
Tauranga | 0 | 60.52 | 0 | 34.3024 | 34.9827 | 49.5191 | 21.5672 | 0 | 0 | 0 | 49.2491 | 48.7069 | 48.1647 | 47.6225 | 47.0803 | 46.5381 | 46.267 | 45.8333 | 45.5079 | 45.5079 | 45.5079 | 0 | 60.52 | 0 | 34.3024 | 34.9827 | 49.5191 | 21.5672 | 0 | 0 | 0 | 5.1788 | 2.4679 | -0.24311 | -2.9541 | -5.665 | -8.376 | -11.087 | -13.7979 | -16.5089 | -19.2199 | -21.9308
Waikato | 41.5732 | 12 | 56.5054 | 0 | 0 | 19.4704 | 14.2288 | 0 | 28.101 | 32.6665 | 26.0632 | 25.8356 | 25.6079 | 25.3802 | 25.1526 | 24.9249 | 24.8111 | 24.6289 | 24.4923 | 24.4923 | 24.4923 | 41.5732 | 12 | 56.5054 | 0 | 0 | 19.4704 | 14.2288 | 0 | 28.101 | 32.6665 | 14.1937 | 13.0554 | 11.9171 | 10.7787 | 9.6404 | 8.5021 | 7.3638 | 6.2254 | 5.0871 | 3.9488 | 2.8105
Waikino | 761.0268 | 167.0645 | 0 | 67.4135 | 0 | 0 | 90.2558 | 0 | 210.266 | 0 | 109.251 | 101.3985 | 93.5461 | 85.6936 | 77.8411 | 69.9886 | 66.0623 | 59.7803 | 55.0689 | 55.0689 | 55.0689 | 761.0268 | 167.0645 | 0 | 67.4135 | 0 | 0 | 90.2558 | 0 | 210.266 | 0 | -86.3408 | -125.6033 | -164.8657 | -204.1282 | -243.3906 | -282.6531 | -321.9155 | -361.178 | -400.4404 | -439.7029 | -478.9653
Wairarapa | 88.6724 | 65.2998 | 69.4572 | 118.6687 | 71.9574 | 41.6289 | 96.2634 | 35.2983 | 215.7995 | 29.01 | 81.1688 | 81.4696 | 81.7705 | 82.0713 | 82.3722 | 82.673 | 82.8234 | 83.0641 | 83.2446 | 83.2446 | 83.2446 | 88.6724 | 65.2998 | 69.4572 | 118.6687 | 71.9574 | 41.6289 | 96.2634 | 35.2983 | 215.7995 | 29.01 | 91.4788 | 92.983 | 94.4872 | 95.9915 | 97.4957 | 98.9999 | 100.5041 | 102.0084 | 103.5126 | 105.0168 | 106.521
Whanganui | 0 | 46.5762 | 87.6364 | 269.6401 | 9.483 | 55.8642 | 24.8473 | 0 | 25.9335 | 0 | 61.7017 | 60.1615 | 58.6213 | 57.0811 | 55.5409 | 54.0007 | 53.2305 | 51.9984 | 51.0742 | 51.0742 | 51.0742 | 0 | 46.5762 | 87.6364 | 269.6401 | 9.483 | 55.8642 | 24.8473 | 0 | 25.9335 | 0 | 9.6421 | 1.9411 | -5.76 | -13.4611 | -21.1622 | -28.8633 | -36.5643 | -44.2654 | -51.9665 | -59.6676 | -67.3686
The rest of the equipment
| History | [9 empty] | Forecast | Weighted average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 85.1162 | 128.5941 | 66.9699 | 70.7556 | 120.6445 | 86.7437 | 94.4943 | 209.6436 | 71.5536 | 56.1633
[11 empty] | 97.6716 | 97.7086 | 97.7456 | 97.7825 | 97.8195 | 97.8564 | 97.8749 | 97.9045 | 97.9266 | 97.9266 | 97.9266 | [10 empty] | 98.8069 | 98.9917 | 99.1764 | 99.3612 | 99.546 | 99.7308 | 99.9156 | 100.1004 | 100.2851 | 100.4699 | 100.6547
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 322.7002 | 121.8442 | 78.441 | 122.8858 | 94.184 | 29.8699 | 55.8801 | 182.9413 | 39.2152 | 66.6486 | 103.3265 | 100.1438 | 96.9612 | 93.7785 | 90.5959 | 87.4132 | 85.8219 | 83.2757 | 81.3661 | 81.3661 | 81.3661 | 322.7002 | 121.8442 | 78.441 | 122.8858 | 94.184 | 29.8699 | 55.8801 | 182.9413 | 39.2152 | 66.6486 | 23.9378 | 8.0245 | -7.8888 | -23.8021 | -39.7154 | -55.6288 | -71.5421 | -87.4554 | -103.3687 | -119.282 | -135.1953
Egmont | 13.5203 | 53.0506 | 108.0134 | 27.359 | 54.3449 | 152.1719 | 86.9331 | 181.731 | 58.1505 | 109.524 | 92.6871 | 94.5597 | 96.4323 | 98.3048 | 100.1774 | 102.05 | 102.9863 | 104.4843 | 105.6079 | 105.6079 | 105.6079 | 13.5203 | 53.0506 | 108.0134 | 27.359 | 54.3449 | 152.1719 | 86.9331 | 181.731 | 58.1505 | 109.524 | 135.9755 | 145.3384 | 154.7012 | 164.064 | 173.4269 | 182.7897 | 192.1526 | 201.5154 | 210.8783 | 220.2411 | 229.604
Kinleith | 70.7323 | 57.462 | 91.599 | 146.1197 | 51.2243 | 43.5447 | 111.1768 | 136.3325 | 116.0124 | 67.0068 | 89.1787 | 89.7696 | 90.3605 | 90.9514 | 91.5423 | 92.1332 | 92.4286 | 92.9013 | 93.2559 | 93.2559 | 93.2559 | 70.7323 | 57.462 | 91.599 | 146.1197 | 51.2243 | 43.5447 | 111.1768 | 136.3325 | 116.0124 | 67.0068 | 105.3705 | 108.3249 | 111.2794 | 114.2338 | 117.1882 | 120.1427 | 123.0971 | 126.0516 | 129.006 | 131.9605 | 134.9149
Manawatu | 75.9054 | 82.6892 | 71.4461 | 62.4891 | 82.8186 | 49.3789 | 57.1326 | 110.9853 | 54.6266 | 50.4719 | 70.767 | 70.431 | 70.0951 | 69.7591 | 69.4232 | 69.0872 | 68.9193 | 68.6505 | 68.449 | 68.449 | 68.449 | 75.9054 | 82.6892 | 71.4461 | 62.4891 | 82.8186 | 49.3789 | 57.1326 | 110.9853 | 54.6266 | 50.4719 | 60.5559 | 58.8762 | 57.1965 | 55.5168 | 53.8371 | 52.1574 | 50.4777 | 48.798 | 47.1182 | 45.4385 | 43.7588
Mt Maunganui | 18.4917 | 769.5349 | 33.7045 | 58.6355 | 83.412 | 27.9835 | 211.4483 | 631.3924 | 104.9894 | 52.303 | 179.5629 | 178.404 | 177.2451 | 176.0863 | 174.9274 | 173.7685 | 173.1891 | 172.262 | 171.5667 | 171.5667 | 171.5667 | 18.4917 | 769.5349 | 33.7045 | 58.6355 | 83.412 | 27.9835 | 211.4483 | 631.3924 | 104.9894 | 52.303 | 167.3206 | 161.5262 | 155.7319 | 149.9375 | 144.1432 | 138.3488 | 132.5545 | 126.7601 | 120.9658 | 115.1714 | 109.3771
Rangitikei | 61.0699 | 142.8149 | 54.703 | 81.7107 | 88.7633 | 204 | 92.2055 | 282.5768 | 19.7313 | 41.7819 | 118.8356 | 119.1398 | 119.4439 | 119.7481 | 120.0522 | 120.3563 | 120.5084 | 120.7517 | 120.9342 | 120.9342 | 120.9342 | 61.0699 | 142.8149 | 54.703 | 81.7107 | 88.7633 | 204 | 92.2055 | 282.5768 | 19.7313 | 41.7819 | 115.2995 | 116.8202 | 118.3409 | 119.8615 | 121.3822 | 122.9029 | 124.4236 | 125.9443 | 127.465 | 128.9856 | 130.5063
Taranaki | 64.0309 | 82.4327 | 61.1774 | 60.8481 | 68.062 | 35.7061 | 46.198 | 171.075 | 65.4063 | 38.7435 | 69.794 | 69.9472 | 70.1004 | 70.2536 | 70.4069 | 70.5601 | 70.6367 | 70.7593 | 70.8512 | 70.8512 | 70.8512 | 64.0309 | 82.4327 | 61.1774 | 60.8481 | 68.062 | 35.7061 | 46.198 | 171.075 | 65.4063 | 38.7435 | 73.5817 | 74.3478 | 75.1139 | 75.88 | 76.6462 | 77.4123 | 78.1784 | 78.9445 | 79.7107 | 80.4768 | 81.2429
Tararua | 58.4505 | 30 | 44.3257 | 125 | 651.7408 | 62 | 0 | 264.6386 | 0 | 81.9022 | 137.4603 | 137.6274 | 137.7946 | 137.9617 | 138.1289 | 138.296 | 138.3796 | 138.5133 | 138.6136 | 138.6136 | 138.6136 | 58.4505 | 30 | 44.3257 | 125 | 651.7408 | 62 | 0 | 264.6386 | 0 | 81.9022 | 136.4021 | 137.2378 | 138.0735 | 138.9092 | 139.7449 | 140.5806 | 141.4163 | 142.252 | 143.0877 | 143.9234 | 144.7591
Tauranga | 70.0122 | 112.3359 | 15.7467 | 70.8382 | 92.4028 | 67.2549 | 57.4334 | 98.0091 | 123.8322 | 48.6579 | 80.6166 | 80.9005 | 81.1844 | 81.4683 | 81.7522 | 82.0362 | 82.1781 | 82.4053 | 82.5756 | 82.5756 | 82.5756 | 70.0122 | 112.3359 | 15.7467 | 70.8382 | 92.4028 | 67.2549 | 57.4334 | 98.0091 | 123.8322 | 48.6579 | 83.4602 | 84.8798 | 86.2994 | 87.719 | 89.1386 | 90.5582 | 91.9778 | 93.3974 | 94.817 | 96.2366 | 97.6562
Waikato | 82.0799 | 87.6336 | 77.6011 | 40.3078 | 76.9723 | 71.5583 | 48.6584 | 233.0143 | 41.5892 | 68.395 | 75.1677 | 75.5935 | 76.0192 | 76.4449 | 76.8707 | 77.2964 | 77.5093 | 77.8499 | 78.1053 | 78.1053 | 78.1053 | 82.0799 | 87.6336 | 77.6011 | 40.3078 | 76.9723 | 71.5583 | 48.6584 | 233.0143 | 41.5892 | 68.395 | 94.4886 | 96.6173 | 98.7459 | 100.8746 | 103.0033 | 105.1319 | 107.2606 | 109.3892 | 111.5179 | 113.6466 | 115.7752
Waikino | 92.3679 | 53 | 76.2228 | 18.8268 | 115.3808 | 114.4299 | 78.4078 | 108.6573 | 116.6776 | 38.203 | 82.5672 | 82.9287 | 83.2902 | 83.6517 | 84.0132 | 84.3746 | 84.5554 | 84.8446 | 85.0615 | 85.0615 | 85.0615 | 92.3679 | 53 | 76.2228 | 18.8268 | 115.3808 | 114.4299 | 78.4078 | 108.6573 | 116.6776 | 38.203 | 91.1582 | 92.9656 | 94.773 | 96.5804 | 98.3878 | 100.1952 | 102.0027 | 103.8101 | 105.6175 | 107.4249 | 109.2323
Wairarapa | 122.8577 | 58.1623 | 114.0984 | 44.9614 | 46.1938 | 69.6731 | 119.5902 | 224.7288 | 37.3125 | 10.6308 | 81.5584 | 81.1276 | 80.6967 | 80.2658 | 79.8349 | 79.4041 | 79.1886 | 78.8439 | 78.5854 | 78.5854 | 78.5854 | 122.8577 | 58.1623 | 114.0984 | 44.9614 | 46.1938 | 69.6731 | 119.5902 | 224.7288 | 37.3125 | 10.6308 | 72.9718 | 70.8174 | 68.663 | 66.5087 | 64.3543 | 62.1999 | 60.0455 | 57.8911 | 55.7367 | 53.5824 | 51.428
Whanganui | 54.2917 | 20.7634 | 43.5295 | 59.8403 | 62.8791 | 200.0971 | 168.8673 | 99.284 | 81.1 | 55.8546 | 88.2093 | 89.639 | 91.0687 | 92.4984 | 93.9281 | 95.3578 | 96.0726 | 97.2164 | 98.0742 | 98.0742 | 98.0742 | 54.2917 | 20.7634 | 43.5295 | 59.8403 | 62.8791 | 200.0971 | 168.8673 | 99.284 | 81.1 | 55.8546 | 123.9672 | 131.1156 | 138.2641 | 145.4125 | 152.5609 | 159.7094 | 166.8578 | 174.0063 | 181.1547 | 188.3032 | 195.4516
Vegetation
| History | [9 empty] | Forecast | Weighted average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 79.5936 | 87.5698 | 112.9604 | 120.4205 | 273.4942 | 85.1185 | 126.112 | 168.0107 | 107.1335 | 91.6907
[11 empty] | 142.885 | 143.3616 | 143.8382 | 144.3149 | 144.7915 | 145.2681 | 145.5064 | 145.8877 | 146.1737 | 146.1737 | 146.1737 | [10 empty] | 137.4487 | 139.8318 | 142.215 | 144.5981 | 146.9812 | 149.3644 | 151.7475 | 154.1306 | 156.5138 | 158.8969 | 161.28
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 54.4366 | 54.0079 | 83.3278 | 221.1204 | 78.1464 | 44.821 | 127.9821 | 122.5699 | 125.1552 | 75.9157 | 110.3782 | 111.0749 | 111.7717 | 112.4684 | 113.1651 | 113.8619 | 114.2103 | 114.7676 | 115.1857 | 115.1857 | 115.1857 | 54.4366 | 54.0079 | 83.3278 | 221.1204 | 78.1464 | 44.821 | 127.9821 | 122.5699 | 125.1552 | 75.9157 | 117.9087 | 121.3924 | 124.8761 | 128.3599 | 131.8436 | 135.3273 | 138.811 | 142.2947 | 145.7784 | 149.2621 | 152.7459
Egmont | 85.1053 | 130.0549 | 0 | 77.7938 | 941.4588 | 91.1869 | 82.8903 | 117.2199 | 84.1176 | 66.7403 | 249.9287 | 249.0369 | 248.1452 | 247.2534 | 246.3616 | 245.4698 | 245.0239 | 244.3104 | 243.7754 | 243.7754 | 243.7754 | 85.1053 | 130.0549 | 0 | 77.7938 | 941.4588 | 91.1869 | 82.8903 | 117.2199 | 84.1176 | 66.7403 | 143.1325 | 138.6735 | 134.2146 | 129.7556 | 125.2966 | 120.8377 | 116.3787 | 111.9197 | 107.4608 | 103.0018 | 98.5429
Kinleith | 112.2869 | 33.0786 | 77.3317 | 64.2629 | 99.1978 | 126.5729 | 234.4708 | 52.0404 | 89.5793 | 55.3458 | 100.3796 | 100.7367 | 101.0938 | 101.4508 | 101.8079 | 102.1649 | 102.3435 | 102.6291 | 102.8434 | 102.8434 | 102.8434 | 112.2869 | 33.0786 | 77.3317 | 64.2629 | 99.1978 | 126.5729 | 234.4708 | 52.0404 | 89.5793 | 55.3458 | 104.2359 | 106.0212 | 107.8066 | 109.5919 | 111.3772 | 113.1625 | 114.9478 | 116.7331 | 118.5184 | 120.3038 | 122.0891
Manawatu | 64.9727 | 64.4298 | 54.2168 | 40.1552 | 158.2321 | 77.3853 | 67.2056 | 93.3627 | 69.913 | 59.0535 | 77.6682 | 77.8878 | 78.1074 | 78.327 | 78.5465 | 78.7661 | 78.8759 | 79.0515 | 79.1833 | 79.1833 | 79.1833 | 64.9727 | 64.4298 | 54.2168 | 40.1552 | 158.2321 | 77.3853 | 67.2056 | 93.3627 | 69.913 | 59.0535 | 80.9308 | 82.0286 | 83.1264 | 84.2243 | 85.3221 | 86.42 | 87.5178 | 88.6156 | 89.7135 | 90.8113 | 91.9091
Mt Maunganui | 47.7024 | 96.5305 | 95.7814 | 233.5754 | 153.3078 | 91.4208 | 177.9708 | 196.1577 | 95.6091 | 69.0972 | 140.7872 | 141.3439 | 141.9006 | 142.4573 | 143.014 | 143.5707 | 143.8491 | 144.2944 | 144.6285 | 144.6285 | 144.6285 | 47.7024 | 96.5305 | 95.7814 | 233.5754 | 153.3078 | 91.4208 | 177.9708 | 196.1577 | 95.6091 | 69.0972 | 141.0248 | 143.8083 | 146.5919 | 149.3754 | 152.159 | 154.9425 | 157.726 | 160.5096 | 163.2931 | 166.0767 | 168.8602
Rangitikei | 67.1795 | 87.6449 | 241.9804 | 123.5456 | 191.6769 | 117.509 | 111.609 | 184.2717 | 116.7888 | 120.4769 | 149.0668 | 149.4125 | 149.7581 | 150.1038 | 150.4494 | 150.7951 | 150.9679 | 151.2444 | 151.4518 | 151.4518 | 151.4518 | 67.1795 | 87.6449 | 241.9804 | 123.5456 | 191.6769 | 117.509 | 111.609 | 184.2717 | 116.7888 | 120.4769 | 145.7737 | 147.502 | 149.2302 | 150.9585 | 152.6868 | 154.415 | 156.1433 | 157.8716 | 159.5998 | 161.3281 | 163.0564
Taranaki | 147.8149 | 117.4118 | 149.3753 | 92.1801 | 220.3663 | 81.9187 | 225.3194 | 161.7533 | 122.2511 | 158.7529 | 154.7165 | 155.2682 | 155.8199 | 156.3716 | 156.9234 | 157.4751 | 157.751 | 158.1924 | 158.5234 | 158.5234 | 158.5234 | 147.8149 | 117.4118 | 149.3753 | 92.1801 | 220.3663 | 81.9187 | 225.3194 | 161.7533 | 122.2511 | 158.7529 | 162.8869 | 165.6456 | 168.4042 | 171.1629 | 173.9215 | 176.6802 | 179.4388 | 182.1974 | 184.9561 | 187.7147 | 190.4734
Tararua | 63.4371 | 92.0377 | 130.2814 | 135.3615 | 122.8964 | 65.5001 | 95.1358 | 186.4444 | 111.6954 | 154.017 | 127.4512 | 128.7307 | 130.0102 | 131.2897 | 132.5691 | 133.8486 | 134.4883 | 135.5119 | 136.2796 | 136.2796 | 136.2796 | 63.4371 | 92.0377 | 130.2814 | 135.3615 | 122.8964 | 65.5001 | 95.1358 | 186.4444 | 111.6954 | 154.017 | 150.8662 | 157.2635 | 163.6609 | 170.0582 | 176.4556 | 182.853 | 189.2503 | 195.6477 | 202.0451 | 208.4424 | 214.8398
Tauranga | 95.5553 | 65.7602 | 87.763 | 114.2986 | 83.8882 | 82.8977 | 64.3327 | 189.1898 | 128.5025 | 72.861 | 98.4041 | 99.1207 | 99.8373 | 100.5539 | 101.2705 | 101.9871 | 102.3454 | 102.9187 | 103.3486 | 103.3486 | 103.3486 | 95.5553 | 65.7602 | 87.763 | 114.2986 | 83.8882 | 82.8977 | 64.3327 | 189.1898 | 128.5025 | 72.861 | 118.2114 | 121.7944 | 125.3773 | 128.9603 | 132.5433 | 136.1263 | 139.7093 | 143.2923 | 146.8753 | 150.4583 | 154.0413
Waikato | 67.6477 | 87.4069 | 76.4416 | 101.5912 | 74.5732 | 52.7299 | 67.1139 | 141.0255 | 118.1117 | 69.9766 | 87.9079 | 88.4334 | 88.9589 | 89.4844 | 90.0099 | 90.5354 | 90.7982 | 91.2186 | 91.5339 | 91.5339 | 91.5339 | 67.6477 | 87.4069 | 76.4416 | 101.5912 | 74.5732 | 52.7299 | 67.1139 | 141.0255 | 118.1117 | 69.9766 | 100.1131 | 102.7406 | 105.3681 | 107.9956 | 110.6231 | 113.2506 | 115.8782 | 118.5057 | 121.1332 | 123.7607 | 126.3882
Waikino | 47.151 | 105.4291 | 89.0478 | 136.8469 | 108.153 | 73.6721 | 82.1351 | 299.0473 | 111.8076 | 79.7579 | 108.9524 | 110.3942 | 111.836 | 113.2778 | 114.7196 | 116.1614 | 116.8823 | 118.0358 | 118.9009 | 118.9009 | 118.9009 | 47.151 | 105.4291 | 89.0478 | 136.8469 | 108.153 | 73.6721 | 82.1351 | 299.0473 | 111.8076 | 79.7579 | 152.9545 | 160.1636 | 167.3726 | 174.5817 | 181.7907 | 188.9998 | 196.2088 | 203.4178 | 210.6269 | 217.8359 | 225.045
Wairarapa | 117.7397 | 153.0413 | 107.8793 | 124.3489 | 205.382 | 101.3958 | 155.9159 | 277.9305 | 102.9726 | 94.178 | 161.765 | 162.1025 | 162.44 | 162.7774 | 163.1149 | 163.4524 | 163.6212 | 163.8912 | 164.0937 | 164.0937 | 164.0937 | 117.7397 | 153.0413 | 107.8793 | 124.3489 | 205.382 | 101.3958 | 155.9159 | 277.9305 | 102.9726 | 94.178 | 153.3595 | 155.047 | 156.7345 | 158.4219 | 160.1094 | 161.7969 | 163.4844 | 165.1719 | 166.8593 | 168.5468 | 170.2343
Whanganui | 63.6876 | 51.5735 | 162.0984 | 100.3858 | 1118.1455 | 99.5298 | 147.3744 | 163.1266 | 116.2319 | 115.8063 | 290.099 | 290.1586 | 290.2182 | 290.2778 | 290.3374 | 290.397 | 290.4268 | 290.4745 | 290.5103 | 290.5103 | 290.5103 | 63.6876 | 51.5735 | 162.0984 | 100.3858 | 1118.1455 | 99.5298 | 147.3744 | 163.1266 | 116.2319 | 115.8063 | 215.4349 | 215.7329 | 216.0309 | 216.3289 | 216.6269 | 216.9249 | 217.2229 | 217.5209 | 217.8189 | 218.1169 | 218.4149
Adverse Weather
| History | [9 empty] | Forecast | Average 2010 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 240.4824 | 160.9972 | 93.2523 | 125.9596 | 169.5243 | 71.4776 | 93.5448 | 210.518 | 176.4924 | 137.5852
[11 empty] | 132.2676 | 131.9149 | 131.5622 | 131.2095 | 130.8568 | 130.5041 | 130.3278 | 130.0456 | 129.834 | 129.834 | 129.834 | [10 empty] | 135.0245 | 133.261 | 131.4976 | 129.7341 | 127.9706 | 126.2071 | 124.4437 | 122.6802 | 120.9167 | 119.1532 | 117.3898
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 973.9759 | 315.8679 | 262.9806 | 23.196 | 47.3699 | 51 | 56.848 | 142.8162 | 15.1233 | 35.23 | 79.3205 | 65.9264 | 52.5322 | 39.1381 | 25.744 | 12.3498 | 5.6528 | -5.0626 | -13.099 | -13.099 | -13.099 | 973.9759 | 315.8679 | 262.9806 | 23.196 | 47.3699 | 51 | 56.848 | 142.8162 | 15.1233 | 35.23 | -175.8979 | -242.8686 | -309.8393 | -376.81 | -443.7806 | -510.7513 | -577.722 | -644.6927 | -711.6634 | -778.634 | -845.6047
Egmont | 171.0677 | 88.4027 | 90.8212 | 123.3731 | 409.6775 | 50.441 | 123.5385 | 170.7866 | 148.3682 | 139.0583 | 157.008 | 157.2175 | 157.4269 | 157.6363 | 157.8457 | 158.0551 | 158.1598 | 158.3273 | 158.4529 | 158.4529 | 158.4529 | 171.0677 | 88.4027 | 90.8212 | 123.3731 | 409.6775 | 50.441 | 123.5385 | 170.7866 | 148.3682 | 139.0583 | 157.3121 | 158.3592 | 159.4062 | 160.4532 | 161.5003 | 162.5473 | 163.5943 | 164.6414 | 165.6884 | 166.7354 | 167.7825
Kinleith | 60.6983 | 0 | 28.1136 | 45.1666 | 0 | 31.1592 | 26.9698 | 211.6135 | 361.9197 | 254.1183 | 119.8826 | 126.1472 | 132.4118 | 138.6764 | 144.9409 | 151.2055 | 154.3378 | 159.3495 | 163.1083 | 163.1083 | 163.1083 | 60.6983 | 0 | 28.1136 | 45.1666 | 0 | 31.1592 | 26.9698 | 211.6135 | 361.9197 | 254.1183 | 274.2521 | 305.5751 | 336.898 | 368.221 | 399.5439 | 430.8669 | 462.1898 | 493.5128 | 524.8357 | 556.1587 | 587.4816
Manawatu | 46.3845 | 161.2084 | 81.6354 | 91.6279 | 76.7164 | 64.9771 | 68.0802 | 82.455 | 216.1469 | 137.3661 | 102.3756 | 103.7394 | 105.1032 | 106.467 | 107.8308 | 109.1945 | 109.8764 | 110.9674 | 111.7857 | 111.7857 | 111.7857 | 46.3845 | 161.2084 | 81.6354 | 91.6279 | 76.7164 | 64.9771 | 68.0802 | 82.455 | 216.1469 | 137.3661 | 140.1638 | 146.9827 | 153.8016 | 160.6205 | 167.4394 | 174.2583 | 181.0772 | 187.8961 | 194.715 | 201.5339 | 208.3528
Mt Maunganui | 121.6219 | 164.8902 | 165.8471 | 205.2595 | 151.9853 | 70.9536 | 68.7592 | 182.6811 | 82.0275 | 68.5505 | 124.508 | 122.7334 | 120.9588 | 119.1842 | 117.4096 | 115.635 | 114.7477 | 113.328 | 112.2633 | 112.2633 | 112.2633 | 121.6219 | 164.8902 | 165.8471 | 205.2595 | 151.9853 | 70.9536 | 68.7592 | 182.6811 | 82.0275 | 68.5505 | 79.4561 | 70.5831 | 61.7101 | 52.8371 | 43.9641 | 35.0912 | 26.2182 | 17.3452 | 8.4722 | -0.40083 | -9.2738
Rangitikei | 168.4085 | 169.5955 | 75.7666 | 141.823 | 198.5991 | 70.3897 | 237.4227 | 334.2199 | 238.0871 | 291.1582 | 198.4333 | 202.1121 | 205.791 | 209.4698 | 213.1486 | 216.8275 | 218.6669 | 221.61 | 223.8173 | 223.8173 | 223.8173 | 168.4085 | 169.5955 | 75.7666 | 141.823 | 198.5991 | 70.3897 | 237.4227 | 334.2199 | 238.0871 | 291.1582 | 293.7152 | 312.1094 | 330.5036 | 348.8978 | 367.292 | 385.6862 | 404.0804 | 422.4746 | 440.8688 | 459.263 | 477.6572
Taranaki | 149.9835 | 60.6422 | 67.9772 | 135.0242 | 143.477 | 54.78 | 122.8825 | 87.9187 | 165.3127 | 166.2882 | 117.9576 | 118.9927 | 120.0279 | 121.0631 | 122.0983 | 123.1334 | 123.651 | 124.4792 | 125.1003 | 125.1003 | 125.1003 | 149.9835 | 60.6422 | 67.9772 | 135.0242 | 143.477 | 54.78 | 122.8825 | 87.9187 | 165.3127 | 166.2882 | 143.896 | 149.0719 | 154.2478 | 159.4237 | 164.5995 | 169.7754 | 174.9513 | 180.1272 | 185.3031 | 190.479 | 195.6549
Tararua | 77.2482 | 139.8972 | 120.0247 | 71.7601 | 122.7041 | 91.6123 | 140.2664 | 197.2721 | 297.5206 | 144.0684 | 148.1536 | 150.8995 | 153.6455 | 156.3914 | 159.1374 | 161.8833 | 163.2563 | 165.4531 | 167.1006 | 167.1006 | 167.1006 | 77.2482 | 139.8972 | 120.0247 | 71.7601 | 122.7041 | 91.6123 | 140.2664 | 197.2721 | 297.5206 | 144.0684 | 215.7511 | 229.4808 | 243.2106 | 256.9403 | 270.6701 | 284.3999 | 298.1296 | 311.8594 | 325.5891 | 339.3189 | 353.0487
Tauranga | 85.1257 | 125.0317 | 35.0224 | 167.2837 | 27.5707 | 56.55 | 62.8064 | 235.6005 | 60.5717 | 114.6484 | 95.0067 | 95.6527 | 96.2987 | 96.9446 | 97.5906 | 98.2366 | 98.5596 | 99.0763 | 99.4639 | 99.4639 | 99.4639 | 85.1257 | 125.0317 | 35.0224 | 167.2837 | 27.5707 | 56.55 | 62.8064 | 235.6005 | 60.5717 | 114.6484 | 114.7852 | 118.0151 | 121.2449 | 124.4747 | 127.7046 | 130.9344 | 134.1642 | 137.3941 | 140.6239 | 143.8537 | 147.0836
Waikato | 339.9318 | 246.4063 | 24.5415 | 136.4775 | 107.6681 | 122.9056 | 64.8267 | 234.112 | 46.3669 | 62.2203 | 99.8898 | 96.191 | 92.4921 | 88.7933 | 85.0945 | 81.3956 | 79.5462 | 76.5871 | 74.3678 | 74.3678 | 74.3678 | 339.9318 | 246.4063 | 24.5415 | 136.4775 | 107.6681 | 122.9056 | 64.8267 | 234.112 | 46.3669 | 62.2203 | 36.8276 | 18.3334 | -0.16077 | -18.655 | -37.1492 | -55.6433 | -74.1375 | -92.6317 | -111.1259 | -129.6201 | -148.1143
Waikino | 631.4238 | 171.3803 | 0 | 269.695 | 215.1243 | 48.1156 | 61.4294 | 488.851 | 85.2162 | 96.8084 | 158.155 | 153.5947 | 149.0344 | 144.4741 | 139.9138 | 135.3536 | 133.0734 | 129.4252 | 126.689 | 126.689 | 126.689 | 631.4238 | 171.3803 | 0 | 269.695 | 215.1243 | 48.1156 | 61.4294 | 488.851 | 85.2162 | 96.8084 | 81.3965 | 58.595 | 35.7936 | 12.9922 | -9.8093 | -32.6107 | -55.4121 | -78.2136 | -101.015 | -123.8165 | -146.6179
Wairarapa | 240.4001 | 217.7994 | 58.8846 | 93.1556 | 134.9859 | 139.9187 | 99.8829 | 231.8287 | 102.3758 | 117.8908 | 122.3654 | 121.1281 | 119.8909 | 118.6537 | 117.4164 | 116.1792 | 115.5606 | 114.5708 | 113.8285 | 113.8285 | 113.8285 | 240.4001 | 217.7994 | 58.8846 | 93.1556 | 134.9859 | 139.9187 | 99.8829 | 231.8287 | 102.3758 | 117.8908 | 109.6884 | 103.5023 | 97.3162 | 91.13 | 84.9439 | 78.7577 | 72.5716 | 66.3854 | 60.1993 | 54.0131 | 47.827
Whanganui | 60.0012 | 70.8442 | 107.4131 | 133.6331 | 398.4132 | 76.4058 | 82.3701 | 136.579 | 475.3651 | 161.2019 | 196.4227 | 200.559 | 204.6954 | 208.8317 | 212.9681 | 217.1044 | 219.1726 | 222.4817 | 224.9635 | 224.9635 | 224.9635 | 60.0012 | 70.8442 | 107.4131 | 133.6331 | 398.4132 | 76.4058 | 82.3701 | 136.579 | 475.3651 | 161.2019 | 283.9722 | 304.654 | 325.3357 | 346.0174 | 366.6992 | 387.3809 | 408.0626 | 428.7444 | 449.4261 | 470.1079 | 490.7896
Unknown
| History | [9 empty] | Forecast | Weighted average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 39.5118 | 53.1439 | 45.9606 | 49.4522 | 57.5489 | 61.4369 | 44.1327 | 57.4105 | 52.1545 | 61.2258
[11 empty] | 54.744 | 55.0272 | 55.3105 | 55.5937 | 55.877 | 56.1602 | 56.3019 | 56.5285 | 56.6984 | 56.6984 | 56.6984 | [10 empty] | 59.9871 | 61.4034 | 62.8196 | 64.2359 | 65.6521 | 67.0683 | 68.4846 | 69.9008 | 71.3171 | 72.7333 | 74.1496
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 25.2801 | 53.951 | 34.4505 | 58.2661 | 47.5782 | 98.8033 | 24.8963 | 35.4387 | 53.9977 | 46.4733 | 48.592 | 48.7704 | 48.9487 | 49.127 | 49.3054 | 49.4837 | 49.5729 | 49.7155 | 49.8225 | 49.8225 | 49.8225 | 25.2801 | 53.951 | 34.4505 | 58.2661 | 47.5782 | 98.8033 | 24.8963 | 35.4387 | 53.9977 | 46.4733 | 52.8176 | 53.7093 | 54.6009 | 55.4926 | 56.3842 | 57.2759 | 58.1675 | 59.0592 | 59.9508 | 60.8425 | 61.7341
Egmont | 71.8791 | 32.0369 | 38.6648 | 60.3849 | 36.4663 | 46.0227 | 36.897 | 108.2182 | 40.9267 | 59.3161 | 58.2602 | 58.5463 | 58.8324 | 59.1184 | 59.4045 | 59.6906 | 59.8337 | 60.0625 | 60.2342 | 60.2342 | 60.2342 | 71.8791 | 32.0369 | 38.6648 | 60.3849 | 36.4663 | 46.0227 | 36.897 | 108.2182 | 40.9267 | 59.3161 | 60.9487 | 62.3791 | 63.8095 | 65.24 | 66.6704 | 68.1009 | 69.5313 | 70.9617 | 72.3922 | 73.8226 | 75.253
Kinleith | 40.4198 | 35.2132 | 83.1217 | 54.9454 | 43.7164 | 87.5032 | 50.8515 | 42.898 | 48.609 | 68.12 | 58.1228 | 58.333 | 58.5433 | 58.7535 | 58.9638 | 59.1741 | 59.2792 | 59.4474 | 59.5735 | 59.5735 | 59.5735 | 40.4198 | 35.2132 | 83.1217 | 54.9454 | 43.7164 | 87.5032 | 50.8515 | 42.898 | 48.609 | 68.12 | 61.3218 | 62.3731 | 63.4243 | 64.4756 | 65.5269 | 66.5781 | 67.6294 | 68.6807 | 69.7319 | 70.7832 | 71.8345
Manawatu | 34.5276 | 30.0484 | 38.1074 | 58.2581 | 42.8883 | 52.4927 | 51.1675 | 57.9298 | 45.193 | 50.8014 | 47.3021 | 47.7141 | 48.1262 | 48.5382 | 48.9502 | 49.3622 | 49.5682 | 49.8979 | 50.1451 | 50.1451 | 50.1451 | 34.5276 | 30.0484 | 38.1074 | 58.2581 | 42.8883 | 52.4927 | 51.1675 | 57.9298 | 45.193 | 50.8014 | 57.4722 | 59.5323 | 61.5924 | 63.6526 | 65.7127 | 67.7728 | 69.833 | 71.8931 | 73.9532 | 76.0134 | 78.0735
Mt Maunganui | 25.5306 | 51.0538 | 55.2762 | 55.0645 | 32.3019 | 49.0226 | 58.8897 | 77.3228 | 37.9083 | 44.8253 | 48.0905 | 48.3572 | 48.624 | 48.8907 | 49.1574 | 49.4242 | 49.5576 | 49.771 | 49.931 | 49.931 | 49.931 | 25.5306 | 51.0538 | 55.2762 | 55.0645 | 32.3019 | 49.0226 | 58.8897 | 77.3228 | 37.9083 | 44.8253 | 56.055 | 57.3887 | 58.7224 | 60.0562 | 61.3899 | 62.7236 | 64.0573 | 65.391 | 66.7248 | 68.0585 | 69.3922
Rangitikei | 44.2612 | 46.2777 | 55.8705 | 56.3692 | 34.901 | 67.487 | 30.6757 | 51.4125 | 30.5094 | 75.8711 | 49.1152 | 49.2453 | 49.3754 | 49.5055 | 49.6356 | 49.7657 | 49.8307 | 49.9348 | 50.0129 | 50.0129 | 50.0129 | 44.2612 | 46.2777 | 55.8705 | 56.3692 | 34.901 | 67.487 | 30.6757 | 51.4125 | 30.5094 | 75.8711 | 52.9411 | 53.5915 | 54.242 | 54.8925 | 55.5429 | 56.1934 | 56.8439 | 57.4943 | 58.1448 | 58.7953 | 59.4457
Taranaki | 27.3542 | 37.0628 | 46.3715 | 49.3454 | 63.1817 | 53.3386 | 41.3322 | 44.4221 | 45.6516 | 60.1714 | 50.7676 | 51.1456 | 51.5236 | 51.9016 | 52.2796 | 52.6576 | 52.8466 | 53.149 | 53.3758 | 53.3758 | 53.3758 | 27.3542 | 37.0628 | 46.3715 | 49.3454 | 63.1817 | 53.3386 | 41.3322 | 44.4221 | 45.6516 | 60.1714 | 57.2181 | 59.108 | 60.998 | 62.888 | 64.778 | 66.668 | 68.558 | 70.4479 | 72.3379 | 74.2279 | 76.1179
Tararua | 57.4145 | 73.6405 | 26.2659 | 41.6774 | 79.1455 | 72.6191 | 12.521 | 31.6464 | 44.2645 | 67.3379 | 54.5029 | 54.2806 | 54.0582 | 53.8359 | 53.6136 | 53.3913 | 53.2801 | 53.1023 | 52.9689 | 52.9689 | 52.9689 | 57.4145 | 73.6405 | 26.2659 | 41.6774 | 79.1455 | 72.6191 | 12.521 | 31.6464 | 44.2645 | 67.3379 | 44.5395 | 43.4279 | 42.3163 | 41.2047 | 40.0931 | 38.9815 | 37.8699 | 36.7583 | 35.6467 | 34.5351 | 33.4235
Tauranga | 14.9311 | 25.9489 | 42.4561 | 49.8113 | 57.2694 | 27.8565 | 75.8485 | 37.5726 | 31.049 | 82.4986 | 47.3888 | 48.1986 | 49.0084 | 49.8182 | 50.628 | 51.4378 | 51.8427 | 52.4905 | 52.9764 | 52.9764 | 52.9764 | 14.9311 | 25.9489 | 42.4561 | 49.8113 | 57.2694 | 27.8565 | 75.8485 | 37.5726 | 31.049 | 82.4986 | 66.7938 | 70.8429 | 74.8919 | 78.9409 | 82.9899 | 87.039 | 91.088 | 95.137 | 99.1861 | 103.2351 | 107.2841
Waikato | 37.3026 | 48.0917 | 38.2841 | 61.4489 | 31.9219 | 51.8249 | 43.121 | 34.0827 | 45.2673 | 41.8569 | 46.0429 | 46.0006 | 45.9584 | 45.9161 | 45.8738 | 45.8316 | 45.8104 | 45.7766 | 45.7513 | 45.7513 | 45.7513 | 37.3026 | 48.0917 | 38.2841 | 61.4489 | 31.9219 | 51.8249 | 43.121 | 34.0827 | 45.2673 | 41.8569 | 42.1579 | 41.9465 | 41.7352 | 41.5239 | 41.3125 | 41.1012 | 40.8899 | 40.6785 | 40.4672 | 40.2559 | 40.0445
Waikino | 62.5315 | 141.3724 | 32.3856 | 16.7016 | 139.1414 | 81.6132 | 57.3494 | 63.4488 | 59.0945 | 52.4375 | 65.354 | 64.8121 | 64.2702 | 63.7284 | 63.1865 | 62.6446 | 62.3736 | 61.9401 | 61.615 | 61.615 | 61.615 | 62.5315 | 141.3724 | 32.3856 | 16.7016 | 139.1414 | 81.6132 | 57.3494 | 63.4488 | 59.0945 | 52.4375 | 55.7055 | 52.9961 | 50.2866 | 47.5772 | 44.8677 | 42.1582 | 39.4488 | 36.7393 | 34.0298 | 31.3204 | 28.6109
Wairarapa | 39.7856 | 74.6764 | 63.0375 | 43.3355 | 65.0479 | 43.4046 | 47.0193 | 98.8523 | 54.5273 | 87.9977 | 66.7402 | 67.2994 | 67.8586 | 68.4178 | 68.977 | 69.5362 | 69.8158 | 70.2632 | 70.5987 | 70.5987 | 70.5987 | 39.7856 | 74.6764 | 63.0375 | 43.3355 | 65.0479 | 43.4046 | 47.0193 | 98.8523 | 54.5273 | 87.9977 | 77.1467 | 79.9427 | 82.7387 | 85.5348 | 88.3308 | 91.1269 | 93.9229 | 96.719 | 99.515 | 102.3111 | 105.1071
Whanganui | 32.4356 | 41.4963 | 43.1968 | 37.2705 | 74.5761 | 66.6917 | 43.1563 | 63.0917 | 141.0107 | 58.2285 | 71.3927 | 72.6509 | 73.909 | 75.1672 | 76.4253 | 77.6835 | 78.3126 | 79.3191 | 80.074 | 80.074 | 80.074 | 32.4356 | 41.4963 | 43.1968 | 37.2705 | 74.5761 | 66.6917 | 43.1563 | 63.0917 | 141.0107 | 58.2285 | 94.7149 | 101.0058 | 107.2966 | 113.5874 | 119.8782 | 126.169 | 132.4599 | 138.7507 | 145.0415 | 151.3323 | 157.6231
The remainder
| History | [9 empty] | Forecast | Weighted average 2009 to 2017 with moderated trend | [9 empty] | Linear trend
Total | 61.3838 | 79.604 | 97.7748 | 76.7 | 67.202 | 75.3129 | 69.6496 | 84.5044 | 103.5727 | 83.0407
[11 empty] | 81.8017 | 82.1451 | 82.4885 | 82.8319 | 83.1753 | 83.5187 | 83.6904 | 83.9651 | 84.1711 | 84.1711 | 84.1711 | [10 empty] | 89.3178 | 91.0348 | 92.7518 | 94.4688 | 96.1857 | 97.9027 | 99.6197 | 101.3366 | 103.0536 | 104.7706 | 106.4876
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 75.4491 | 79.3995 | 256.7008 | 23.9755 | 29.767 | 88.7472 | 114.5474 | 93.3604 | 84.0494 | 35.4717 | 97.3514 | 96.3657 | 95.3799 | 94.3941 | 93.4084 | 92.4226 | 91.9297 | 91.1411 | 90.5497 | 90.5497 | 90.5497 | 75.4491 | 79.3995 | 256.7008 | 23.9755 | 29.767 | 88.7472 | 114.5474 | 93.3604 | 84.0494 | 35.4717 | 61.0384 | 56.1095 | 51.1807 | 46.2519 | 41.3231 | 36.3943 | 31.4655 | 26.5367 | 21.6079 | 16.6791 | 11.7503
Egmont | 64.8226 | 83.3872 | 51.2408 | 98.2839 | 94.4633 | 49.9847 | 61.6912 | 55.8821 | 68.0767 | 86.8156 | 71.4421 | 71.3932 | 71.3444 | 71.2956 | 71.2467 | 71.1979 | 71.1735 | 71.1344 | 71.1051 | 71.1051 | 71.1051 | 64.8226 | 83.3872 | 51.2408 | 98.2839 | 94.4633 | 49.9847 | 61.6912 | 55.8821 | 68.0767 | 86.8156 | 70.1219 | 69.8777 | 69.6336 | 69.3894 | 69.1452 | 68.9011 | 68.6569 | 68.4127 | 68.1686 | 67.9244 | 67.6803
Kinleith | 67.8296 | 94.3654 | 89.9582 | 83.4421 | 100.5838 | 45.3969 | 54.7903 | 37.0754 | 133.82 | 45.5926 | 72.1213 | 71.7219 | 71.3225 | 70.9231 | 70.5237 | 70.1243 | 69.9246 | 69.6051 | 69.3655 | 69.3655 | 69.3655 | 67.8296 | 94.3654 | 89.9582 | 83.4421 | 100.5838 | 45.3969 | 54.7903 | 37.0754 | 133.82 | 45.5926 | 64.3019 | 62.3049 | 60.3079 | 58.3108 | 56.3138 | 54.3168 | 52.3198 | 50.3228 | 48.3258 | 46.3288 | 44.3318
Manawatu | 56.2321 | 52.9388 | 40.4543 | 32.7058 | 45.5525 | 60.47 | 46.0799 | 26.7348 | 28.0526 | 37.1122 | 40.7564 | 40.3202 | 39.8841 | 39.4479 | 39.0117 | 38.5756 | 38.3575 | 38.0085 | 37.7468 | 37.7468 | 37.7468 | 56.2321 | 52.9388 | 40.4543 | 32.7058 | 45.5525 | 60.47 | 46.0799 | 26.7348 | 28.0526 | 37.1122 | 30.6386 | 28.4578 | 26.2769 | 24.0961 | 21.9152 | 19.7344 | 17.5535 | 15.3727 | 13.1918 | 11.011 | 8.8301
Mt Maunganui | 77.0858 | 144.9946 | 86.4549 | 91.4184 | 71.5545 | 100.7338 | 88.4606 | 130.7337 | 90.8974 | 132.4006 | 105.5687 | 106.0061 | 106.4435 | 106.8809 | 107.3183 | 107.7557 | 107.9744 | 108.3243 | 108.5867 | 108.5867 | 108.5867 | 77.0858 | 144.9946 | 86.4549 | 91.4184 | 71.5545 | 100.7338 | 88.4606 | 130.7337 | 90.8974 | 132.4006 | 113.5019 | 115.6888 | 117.8758 | 120.0628 | 122.2498 | 124.4368 | 126.6238 | 128.8108 | 130.9977 | 133.1847 | 135.3717
Rangitikei | 57.9201 | 70.9334 | 242.1891 | 126.4421 | 37.8866 | 122.9662 | 47.5597 | 56.3336 | 67.0978 | 133.1388 | 97.4172 | 96.8951 | 96.373 | 95.8509 | 95.3289 | 94.8068 | 94.5457 | 94.128 | 93.8148 | 93.8148 | 93.8148 | 57.9201 | 70.9334 | 242.1891 | 126.4421 | 37.8866 | 122.9662 | 47.5597 | 56.3336 | 67.0978 | 133.1388 | 81.8892 | 79.2788 | 76.6683 | 74.0579 | 71.4474 | 68.837 | 66.2265 | 63.616 | 61.0056 | 58.3951 | 55.7847
Taranaki | 40.085 | 57.805 | 54.2517 | 69.8936 | 41.6607 | 50.1067 | 46.3205 | 83.7192 | 86.3047 | 99.6858 | 67.1869 | 68.182 | 69.1771 | 70.1722 | 71.1673 | 72.1624 | 72.66 | 73.4561 | 74.0532 | 74.0532 | 74.0532 | 40.085 | 57.805 | 54.2517 | 69.8936 | 41.6607 | 50.1067 | 46.3205 | 83.7192 | 86.3047 | 99.6858 | 90.3489 | 95.3245 | 100.3 | 105.2756 | 110.2512 | 115.2267 | 120.2023 | 125.1779 | 130.1534 | 135.129 | 140.1046
Tararua | 55.8919 | 61 | 69.9671 | 84.5241 | 11.0316 | 95.0783 | 63.0579 | 108.2094 | 31.1909 | 28.846 | 60.8878 | 60.5954 | 60.303 | 60.0107 | 59.7183 | 59.4259 | 59.2797 | 59.0458 | 58.8704 | 58.8704 | 58.8704 | 55.8919 | 61 | 69.9671 | 84.5241 | 11.0316 | 95.0783 | 63.0579 | 108.2094 | 31.1909 | 28.846 | 52.8392 | 51.3773 | 49.9153 | 48.4534 | 46.9915 | 45.5296 | 44.0677 | 42.6057 | 41.1438 | 39.6819 | 38.22
Tauranga | 91.3844 | 76.2459 | 77.1831 | 72.2104 | 64.196 | 58.4606 | 77.0147 | 78.1063 | 58.9572 | 95.117 | 72.6262 | 72.5363 | 72.4464 | 72.3566 | 72.2667 | 72.1769 | 72.1319 | 72.06 | 72.0061 | 72.0061 | 72.0061 | 91.3844 | 76.2459 | 77.1831 | 72.2104 | 64.196 | 58.4606 | 77.0147 | 78.1063 | 58.9572 | 95.117 | 72.4165 | 71.9672 | 71.5179 | 71.0686 | 70.6193 | 70.17 | 69.7207 | 69.2714 | 68.8221 | 68.3728 | 67.9235
Waikato | 67.2395 | 103.1777 | 81.2297 | 122.815 | 115.6233 | 92.5941 | 55.0574 | 117.1436 | 85.8169 | 76.319 | 96.318 | 96.2131 | 96.1082 | 96.0033 | 95.8984 | 95.7935 | 95.7411 | 95.6571 | 95.5942 | 95.5942 | 95.5942 | 67.2395 | 103.1777 | 81.2297 | 122.815 | 115.6233 | 92.5941 | 55.0574 | 117.1436 | 85.8169 | 76.319 | 88.8169 | 88.2924 | 87.7679 | 87.2434 | 86.7189 | 86.1944 | 85.6699 | 85.1454 | 84.6209 | 84.0964 | 83.5719
Waikino | 39.6477 | 109.7808 | 63.6952 | 88.0884 | 119.5813 | 102.0824 | 42.6266 | 123.8389 | 154.6348 | 155.8913 | 112.407 | 114.2336 | 116.0603 | 117.887 | 119.7137 | 121.5403 | 122.4537 | 123.915 | 125.011 | 125.011 | 125.011 | 39.6477 | 109.7808 | 63.6952 | 88.0884 | 119.5813 | 102.0824 | 42.6266 | 123.8389 | 154.6348 | 155.8913 | 150.2202 | 159.3535 | 168.4869 | 177.6203 | 186.7536 | 195.887 | 205.0203 | 214.1537 | 223.287 | 232.4204 | 241.5537
Wairarapa | 76.6517 | 56.913 | 89.1801 | 46.3258 | 72.4971 | 54.8189 | 115.1141 | 124.7499 | 85.0717 | 77.2813 | 78.3193 | 79.0094 | 79.6995 | 80.3896 | 81.0796 | 81.7697 | 82.1148 | 82.6668 | 83.0809 | 83.0809 | 83.0809 | 76.6517 | 56.913 | 89.1801 | 46.3258 | 72.4971 | 54.8189 | 115.1141 | 124.7499 | 85.0717 | 77.2813 | 98.8375 | 102.2879 | 105.7383 | 109.1887 | 112.639 | 116.0894 | 119.5398 | 122.9902 | 126.4406 | 129.891 | 133.3414
Whanganui | 27.7498 | 43.9102 | 68.5676 | 56.9752 | 69.2284 | 57.6281 | 93.1241 | 62.6698 | 372.4745 | 75.8571 | 91.0196 | 94.4139 | 97.8081 | 101.2024 | 104.5967 | 107.991 | 109.6881 | 112.4035 | 114.4401 | 114.4401 | 114.4401 | 27.7498 | 43.9102 | 68.5676 | 56.9752 | 69.2284 | 57.6281 | 93.1241 | 62.6698 | 372.4745 | 75.8571 | 186.1609 | 203.1323 | 220.1036 | 237.075 | 254.0464 | 271.0177 | 287.9891 | 304.9604 | 321.9318 | 338.9031 | 355.8745
Totals
Linear trend
Total | 108.154 | 94.1671 | 80.4683 | 97.5635 | 125.7987 | 77.3517 | 88.4279 | 121.4841 | 89.3055 | 81.8155
[32 empty] | 91.7252 | 90.8655 | 90.0058 | 89.1461 | 88.2864 | 87.4267 | 86.567 | 85.7073 | 84.8476 | 83.9879 | 83.1282
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | [11 empty] | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 332.8516 | 143.1604 | 146.3085 | 109.8969 | 51.6691 | 69.9017 | 101.375 | 91.2578 | 94.7834 | 53.6451 | [11 empty] | 332.8516 | 143.1604 | 146.3085 | 109.8969 | 51.6691 | 69.9017 | 101.375 | 91.2578 | 94.7834 | 53.6451 | 15.0155 | -3.979 | -22.9734 | -41.9679 | -60.9623 | -79.9568 | -98.9512 | -117.9457 | -136.9401 | -155.9346 | -174.929
Egmont | 124.0366 | 67.2974 | 72.1279 | 86.7102 | 268.5615 | 59.594 | 83.4873 | 109.4823 | 75.7149 | 100.7992 | [11 empty] | 124.0366 | 67.2974 | 72.1279 | 86.7102 | 268.5615 | 59.594 | 83.4873 | 109.4823 | 75.7149 | 100.7992 | 98.7118 | 97.6083 | 96.5048 | 95.4013 | 94.2978 | 93.1943 | 92.0908 | 90.9872 | 89.8837 | 88.7802 | 87.6767
Kinleith | 61.8569 | 47.5957 | 84.3544 | 89.7334 | 79.1346 | 78.6199 | 73.1317 | 59.9074 | 76.9634 | 84.3435 | [11 empty] | 61.8569 | 47.5957 | 84.3544 | 89.7334 | 79.1346 | 78.6199 | 73.1317 | 59.9074 | 76.9634 | 84.3435 | 81.4107 | 82.8374 | 84.264 | 85.6907 | 87.1173 | 88.544 | 89.9706 | 91.3973 | 92.824 | 94.2506 | 95.6773
Manawatu | 55.9586 | 72.6779 | 54.8541 | 62.7137 | 69.9707 | 61.0158 | 59.6713 | 72.6085 | 55.7371 | 62.0383 | [11 empty] | 55.9586 | 72.6779 | 54.8541 | 62.7137 | 69.9707 | 61.0158 | 59.6713 | 72.6085 | 55.7371 | 62.0383 | 62.952 | 62.9933 | 63.0346 | 63.076 | 63.1173 | 63.1587 | 63.2 | 63.2413 | 63.2827 | 63.324 | 63.3654
Mt Maunganui | 71.5802 | 101.2963 | 102.3378 | 151.5075 | 82.3778 | 77.2427 | 76.9146 | 162.8619 | 91.4762 | 71.1479 | [11 empty] | 71.5802 | 101.2963 | 102.3378 | 151.5075 | 82.3778 | 77.2427 | 76.9146 | 162.8619 | 91.4762 | 71.1479 | 98.9101 | 98.9166 | 98.9232 | 98.9297 | 98.9362 | 98.9427 | 98.9492 | 98.9557 | 98.9622 | 98.9688 | 98.9753
Rangitikei | 81.1368 | 96.7586 | 104.7511 | 117.1935 | 109.3782 | 120.555 | 109.6591 | 138.8181 | 67.9123 | 108.1373 | [11 empty] | 81.1368 | 96.7586 | 104.7511 | 117.1935 | 109.3782 | 120.555 | 109.6591 | 138.8181 | 67.9123 | 108.1373 | 112.0963 | 113.3083 | 114.5204 | 115.7324 | 116.9445 | 118.1565 | 119.3686 | 120.5806 | 121.7927 | 123.0047 | 124.2168
Taranaki | 68.3322 | 64.5097 | 71.1245 | 97.7715 | 132.6261 | 56.2119 | 87.0803 | 92.6208 | 75.2398 | 94.4291 | [11 empty] | 68.3322 | 64.5097 | 71.1245 | 97.7715 | 132.6261 | 56.2119 | 87.0803 | 92.6208 | 75.2398 | 94.4291 | 94.2938 | 96.1664 | 98.039 | 99.9115 | 101.7841 | 103.6567 | 105.5293 | 107.4019 | 109.2745 | 111.147 | 113.0196
Tararua | 87.0497 | 108.1125 | 64.2595 | 91.7358 | 111.8339 | 95.9002 | 107.3593 | 98.3072 | 84.6826 | 107.8507 | [11 empty] | 87.0497 | 108.1125 | 64.2595 | 91.7358 | 111.8339 | 95.9002 | 107.3593 | 98.3072 | 84.6826 | 107.8507 | 103.1883 | 104.5482 | 105.908 | 107.2679 | 108.6277 | 109.9876 | 111.3475 | 112.7073 | 114.0672 | 115.427 | 116.7869
Tauranga | 64.4969 | 70.6271 | 47.7442 | 84.9352 | 69.9498 | 54.5644 | 70.5314 | 125.3938 | 66.5129 | 77.6155 | [11 empty] | 64.4969 | 70.6271 | 47.7442 | 84.9352 | 69.9498 | 54.5644 | 70.5314 | 125.3938 | 66.5129 | 77.6155 | 87.2011 | 89.74 | 92.2789 | 94.8178 | 97.3567 | 99.8957 | 102.4346 | 104.9735 | 107.5124 | 110.0513 | 112.5902
Waikato | 90.233 | 158.1744 | 60.8028 | 95.7817 | 83.9643 | 73.3545 | 55.0299 | 143.5611 | 70.9855 | 58.817 | [11 empty] | 90.233 | 158.1744 | 60.8028 | 95.7817 | 83.9643 | 73.3545 | 55.0299 | 143.5611 | 70.9855 | 58.817 | 68.6658 | 64.9558 | 61.2459 | 57.5359 | 53.826 | 50.1161 | 46.4061 | 42.6962 | 38.9862 | 35.2763 | 31.5664
Waikino | 208.4805 | 144.938 | 90.9626 | 91.7673 | 111.2318 | 98.0685 | 84.364 | 206.4333 | 137.8722 | 75.5542 | [11 empty] | 208.4805 | 144.938 | 90.9626 | 91.7673 | 111.2318 | 98.0685 | 84.364 | 206.4333 | 137.8722 | 75.5542 | 101.5067 | 97.2411 | 92.9756 | 88.71 | 84.4444 | 80.1789 | 75.9133 | 71.6478 | 67.3822 | 63.1166 | 58.8511
Wairarapa | 116.7097 | 99.7811 | 75.6791 | 81.5247 | 110.5036 | 79.0598 | 150.6207 | 172.7565 | 80.7882 | 82.6722 | [11 empty] | 116.7097 | 99.7811 | 75.6791 | 81.5247 | 110.5036 | 79.0598 | 150.6207 | 172.7565 | 80.7882 | 82.6722 | 112.4077 | 113.7528 | 115.0979 | 116.443 | 117.7881 | 119.1332 | 120.4783 | 121.8234 | 123.1685 | 124.5137 | 125.8588
Whanganui | 43.2789 | 49.2434 | 70.7814 | 107.0538 | 354.1821 | 81.4832 | 90.3384 | 105.2852 | 182.3033 | 86.552 | [11 empty] | 43.2789 | 49.2434 | 70.7814 | 107.0538 | 354.1821 | 81.4832 | 90.3384 | 105.2852 | 182.3033 | 86.552 | 156.0686 | 163.1628 | 170.2571 | 177.3513 | 184.4456 | 191.5398 | 198.6341 | 205.7283 | 212.8226 | 219.9168 | 227.0111

## Modelled ICPs
Forecast ICPs Impacted
| ICP | [20 empty] | Linear trend
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Poles
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 100.3021 | 152.5714 | 182.8443 | 130.6119 | 148.6771 | 395.6847 | 74.8052 | 198.6948 | 213.2045 | 68.4524
[11 empty] | 211.1315 | 213.066 | 214.8366 | 216.9947 | 218.9018 | 220.5351 | 222.3424 | 224.4275 | 226.1316 | 227.8931 | 229.626 | [10 empty] | 139.4709 | 141.3782 | 143.2855 | 145.1927 | 147.1 | 149.0073 | 150.9145 | 152.8218 | 154.7291 | 156.6363 | 158.5436
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0 | 202 | 151.4999 | 89 | 36 | 2.9997 | 74.25 | 266 | 958 | 0 | 242.0995 | 245.0529 | 247.9874 | 250.8936 | 253.7809 | 256.6493 | 258.5459 | 261.3766 | 264.1885 | 266.9814 | 268.8308 | 0 | 202 | 151.4999 | 89 | 36 | 2.9997 | 74.25 | 266 | 958 | 0 | 370.8833 | 405.9575 | 441.0318 | 476.106 | 511.1803 | 546.2545 | 581.3288 | 616.403 | 651.4772 | 686.5515 | 721.6257
Egmont | 121.3333 | 124.5 | 25 | 15 | 112.2 | 0 | 23 | 2 | 151.25 | 193 | 101.974 | 102.5847 | 103.1953 | 104.4166 | 105.0194 | 105.6221 | 106.2248 | 107.4303 | 108.0251 | 108.6199 | 109.2147 | 121.3333 | 124.5 | 25 | 15 | 112.2 | 0 | 23 | 2 | 151.25 | 193 | 97.6967 | 101.5091 | 105.3215 | 109.1339 | 112.9464 | 116.7588 | 120.5712 | 124.3836 | 128.1961 | 132.0085 | 135.8209
Kinleith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374.5 | 0 | 0 | 379.0993 | 379.0993 | 379.0993 | 383.3206 | 387.4864 | 387.4864 | 391.5966 | 395.7068 | 395.7068 | 399.7615 | 403.8162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374.5 | 0 | 0 | 99.8667 | 111.2152 | 122.5636 | 133.9121 | 145.2606 | 156.6091 | 167.9576 | 179.3061 | 190.6545 | 202.003 | 213.3515
Manawatu | 0 | 131 | 736.9996 | 698.8 | 0 | 557.9376 | 3 | 3 | 36.5 | 0 | 442.1364 | 446.4297 | 450.0882 | 453.1202 | 456.1356 | 459.1425 | 462.1328 | 465.7161 | 468.6813 | 471.6382 | 474.5783 | 0 | 131 | 736.9996 | 698.8 | 0 | 557.9376 | 3 | 3 | 36.5 | 0 | 21.3584 | -14.1626 | -49.6836 | -85.2045 | -120.7255 | -156.2465 | -191.7675 | -227.2884 | -262.8094 | -298.3304 | -333.8513
Mt Maunganui | 0 | 43 | 555.9997 | 201 | 333 | 144.9838 | 0 | 0 | 13 | 0 | 214.2219 | 216.6613 | 219.0877 | 221.0135 | 223.4079 | 225.3144 | 227.6832 | 229.564 | 231.9006 | 233.7622 | 235.611 | 0 | 43 | 555.9997 | 201 | 333 | 144.9838 | 0 | 0 | 13 | 0 | 3.0645 | -19.8507 | -42.766 | -65.6812 | -88.5964 | -111.5117 | -134.4269 | -157.3422 | -180.2574 | -203.1726 | -226.0879
Rangitikei | 182 | 796 | 0 | 59 | 32.3333 | 52.3275 | 45.25 | 52 | 69 | 11 | 90.8661 | 91.4669 | 92.059 | 92.6512 | 93.2434 | 93.8356 | 94.4278 | 95.6036 | 96.1872 | 96.7708 | 97.3544 | 182 | 796 | 0 | 59 | 32.3333 | 52.3275 | 45.25 | 52 | 69 | 11 | -83.0841 | -121.8069 | -160.5296 | -199.2524 | -237.9752 | -276.6979 | -315.4207 | -354.1435 | -392.8662 | -431.589 | -470.3117
Taranaki | 127 | 129.5 | 8.5 | 17 | 240.6667 | 179.4799 | 60 | 41 | 67.5 | 7 | 124.9826 | 125.9593 | 127.1251 | 128.0888 | 128.8555 | 129.8112 | 130.5727 | 131.5232 | 132.4658 | 133.4085 | 134.1568 | 127 | 129.5 | 8.5 | 17 | 240.6667 | 179.4799 | 60 | 41 | 67.5 | 7 | 44.9751 | 37.1952 | 29.4153 | 21.6353 | 13.8554 | 6.0755 | -1.7044 | -9.4843 | -17.2643 | -25.0442 | -32.8241
Tararua | 55.6667 | 47.3333 | 41 | 42.3333 | 90.1667 | 112.9874 | 108.8571 | 41.3333 | 13 | 26.5 | 65.8502 | 65.8502 | 65.8502 | 67.3704 | 67.3704 | 67.3704 | 67.3704 | 67.3704 | 68.8608 | 68.8608 | 68.8608 | 55.6667 | 47.3333 | 41 | 42.3333 | 90.1667 | 112.9874 | 108.8571 | 41.3333 | 13 | 26.5 | 48.6253 | 46.9358 | 45.2462 | 43.5567 | 41.8671 | 40.1776 | 38.4881 | 36.7985 | 35.109 | 33.4194 | 31.7299
Tauranga | 199.6667 | 121.5 | 215.9999 | 33.5 | 0 | 1332.851 | 6 | 817 | 834.6667 | 2 | 369.2027 | 373.1833 | 377.1425 | 381.073 | 384.4881 | 388.3757 | 391.755 | 395.5924 | 399.4013 | 402.7161 | 406.0166 | 199.6667 | 121.5 | 215.9999 | 33.5 | 0 | 1332.851 | 6 | 817 | 834.6667 | 2 | 605.269 | 650.5328 | 695.7965 | 741.0603 | 786.324 | 831.5878 | 876.8515 | 922.1153 | 967.379 | 1012.6428 | 1057.9065
Waikato | 66.5 | 88 | 66 | 103.3333 | 167 | 1123.8744 | 80.5 | 348 | 49.3333 | 2 | 163.0363 | 165.0487 | 167.0545 | 169.0407 | 170.5222 | 172.4887 | 173.9505 | 175.8908 | 177.3329 | 179.2469 | 180.6694 | 66.5 | 88 | 66 | 103.3333 | 167 | 1123.8744 | 80.5 | 348 | 49.3333 | 2 | 257.6944 | 266.4653 | 275.2363 | 284.0072 | 292.7782 | 301.5492 | 310.3201 | 319.0911 | 327.862 | 336.633 | 345.4039
Waikino | 0 | 72 | 0 | 0 | 0 | 0 | 284.5 | 0 | 0 | 286.5 | 245.7819 | 250.0258 | 252.821 | 255.6015 | 258.3527 | 261.0893 | 263.8113 | 266.5186 | 269.1967 | 270.5284 | 273.1919 | 0 | 72 | 0 | 0 | 0 | 0 | 284.5 | 0 | 0 | 286.5 | 161.9 | 179.6455 | 197.3909 | 215.1364 | 232.8818 | 250.6273 | 268.3727 | 286.1182 | 303.8636 | 321.6091 | 339.3545
Wairarapa | 33.25 | 66.3571 | 17.4444 | 150.7647 | 89.7273 | 53.7213 | 118.5 | 55.1429 | 152 | 80.5714 | 94.3272 | 95.4298 | 96.5288 | 97.3457 | 98.159 | 99.236 | 100.0382 | 100.8368 | 101.6318 | 102.4231 | 103.2107 | 33.25 | 66.3571 | 17.4444 | 150.7647 | 89.7273 | 53.7213 | 118.5 | 55.1429 | 152 | 80.5714 | 117.7841 | 124.3361 | 130.8881 | 137.4402 | 143.9922 | 150.5442 | 157.0962 | 163.6483 | 170.2003 | 176.7523 | 183.3044
Whanganui | 17 | 9.6667 | 10 | 27 | 237 | 0 | 19 | 185.6667 | 1 | 7.5 | 61.7492 | 62.323 | 62.8917 | 63.4604 | 63.8371 | 64.4008 | 64.7749 | 65.3335 | 65.8871 | 66.2536 | 66.6176 | 17 | 9.6667 | 10 | 27 | 237 | 0 | 19 | 185.6667 | 1 | 7.5 | 67.0889 | 69.9444 | 72.8 | 75.6556 | 78.5111 | 81.3667 | 84.2222 | 87.0778 | 89.9333 | 92.7889 | 95.6444
Xarms
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 255.4045 | 179.2468 | 166.3371 | 150.9657 | 160.8603 | 202.4812 | 185.5713 | 177.6257 | 184.9067 | 148.4604
[11 empty] | 169.5866 | 171.3129 | 172.8862 | 174.6469 | 176.0914 | 177.5578 | 178.9191 | 180.5844 | 182.1598 | 183.4685 | 184.7768 | [10 empty] | 156.3278 | 152.0331 | 147.7384 | 143.4437 | 139.1491 | 134.8544 | 130.5597 | 126.265 | 121.9703 | 117.6756 | 113.3809
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 367.76 | 283.6 | 175.1578 | 162.35 | 209.0526 | 167.5582 | 103.4483 | 263.4615 | 251 | 220.9524 | 210.3053 | 212.8708 | 215.42 | 217.9445 | 220.4526 | 222.9444 | 224.5919 | 227.0509 | 229.4934 | 231.9196 | 233.5261 | 367.76 | 283.6 | 175.1578 | 162.35 | 209.0526 | 167.5582 | 103.4483 | 263.4615 | 251 | 220.9524 | 176.2291 | 168.1918 | 160.1546 | 152.1173 | 144.08 | 136.0428 | 128.0055 | 119.9682 | 111.9309 | 103.8937 | 95.8564
Egmont | 149.7333 | 91.1081 | 155.1304 | 105.4524 | 110.0959 | 113.1374 | 134.6 | 133.1364 | 141.907 | 151.2676 | 130.0054 | 130.7839 | 131.5624 | 133.1195 | 133.8879 | 134.6563 | 135.4247 | 136.9615 | 137.7198 | 138.4781 | 139.2364 | 149.7333 | 91.1081 | 155.1304 | 105.4524 | 110.0959 | 113.1374 | 134.6 | 133.1364 | 141.907 | 151.2676 | 140.2207 | 142.3414 | 144.4621 | 146.5828 | 148.7035 | 150.8241 | 152.9448 | 155.0655 | 157.1862 | 159.3069 | 161.4276
Kinleith | 499.75 | 1 | 52 | 80.4 | 0 | 47.328 | 21 | 55.3333 | 67 | 115.6 | 67.6956 | 67.6956 | 67.6956 | 68.4494 | 69.1933 | 69.1933 | 69.9273 | 70.6612 | 70.6612 | 71.3853 | 72.1093 | 499.75 | 1 | 52 | 80.4 | 0 | 47.328 | 21 | 55.3333 | 67 | 115.6 | -9.7107 | -28.5565 | -47.4023 | -66.2481 | -85.0939 | -103.9396 | -122.7854 | -141.6312 | -160.477 | -179.3228 | -198.1686
Manawatu | 207.0455 | 177.1316 | 151.2221 | 229.4717 | 174.1493 | 236.4736 | 265.2857 | 270.9778 | 188.5676 | 325.0588 | 225.4624 | 227.6517 | 229.5173 | 231.0634 | 232.6011 | 234.1344 | 235.6593 | 237.4866 | 238.9986 | 240.5064 | 242.0057 | 207.0455 | 177.1316 | 151.2221 | 229.4717 | 174.1493 | 236.4736 | 265.2857 | 270.9778 | 188.5676 | 325.0588 | 286.2289 | 297.809 | 309.3891 | 320.9692 | 332.5493 | 344.1294 | 355.7095 | 367.2896 | 378.8697 | 390.4498 | 402.0299
Mt Maunganui | 251.1538 | 201.5263 | 240.2306 | 61.2 | 118.625 | 198.8601 | 85.9375 | 104.6667 | 173.1667 | 34.7333 | 138.5339 | 140.1114 | 141.6806 | 142.9259 | 144.4743 | 145.7073 | 147.2391 | 148.4554 | 149.9664 | 151.1703 | 152.3659 | 251.1538 | 201.5263 | 240.2306 | 61.2 | 118.625 | 198.8601 | 85.9375 | 104.6667 | 173.1667 | 34.7333 | 58.0209 | 41.841 | 25.6612 | 9.4813 | -6.6985 | -22.8784 | -39.0582 | -55.2381 | -71.4179 | -87.5977 | -103.7776
Rangitikei | 143.2632 | 62.6875 | 107.4583 | 114.7778 | 208.7241 | 178.4467 | 191.5 | 192.85 | 222.5714 | 144.3333 | 160.3385 | 161.3986 | 162.4435 | 163.4885 | 164.5334 | 165.5784 | 166.6233 | 168.6981 | 169.7279 | 170.7577 | 171.7875 | 143.2632 | 62.6875 | 107.4583 | 114.7778 | 208.7241 | 178.4467 | 191.5 | 192.85 | 222.5714 | 144.3333 | 215.1835 | 225.8239 | 236.4643 | 247.1047 | 257.7451 | 268.3855 | 279.0259 | 289.6663 | 300.3067 | 310.9471 | 321.5875
Taranaki | 238.2241 | 255.7869 | 220.754 | 264.6212 | 185.4583 | 174.6039 | 184.5 | 220.58 | 271.0312 | 201.225 | 219.2406 | 220.9541 | 222.9991 | 224.6895 | 226.0344 | 227.711 | 229.0467 | 230.714 | 232.3676 | 234.0211 | 235.3338 | 238.2241 | 255.7869 | 220.754 | 264.6212 | 185.4583 | 174.6039 | 184.5 | 220.58 | 271.0312 | 201.225 | 205.7328 | 202.8336 | 199.9344 | 197.0352 | 194.136 | 191.2368 | 188.3375 | 185.4383 | 182.5391 | 179.6399 | 176.7407
Tararua | 77.8085 | 64.0263 | 121.409 | 74.2 | 86.6949 | 104.7721 | 105.3958 | 108.0238 | 57.1395 | 94.3265 | 90.3516 | 90.3516 | 90.3516 | 92.4374 | 92.4374 | 92.4374 | 92.4374 | 92.4374 | 94.4824 | 94.4824 | 94.4824 | 77.8085 | 64.0263 | 121.409 | 74.2 | 86.6949 | 104.7721 | 105.3958 | 108.0238 | 57.1395 | 94.3265 | 94.2194 | 95.0994 | 95.9793 | 96.8593 | 97.7393 | 98.6192 | 99.4992 | 100.3791 | 101.2591 | 102.1391 | 103.019
Tauranga | 315.4231 | 499.1111 | 119.8124 | 233.2 | 187.1818 | 188.7289 | 259.2174 | 370.2632 | 258.48 | 136.2143 | 244.2951 | 246.9291 | 249.5488 | 252.1496 | 254.4093 | 256.9816 | 259.2176 | 261.7568 | 264.2771 | 266.4704 | 268.6543 | 315.4231 | 499.1111 | 119.8124 | 233.2 | 187.1818 | 188.7289 | 259.2174 | 370.2632 | 258.48 | 136.2143 | 191.2484 | 179.3366 | 167.4249 | 155.5131 | 143.6013 | 131.6895 | 119.7777 | 107.8659 | 95.9542 | 84.0424 | 72.1306
Waikato | 118.6364 | 121.4286 | 157.9999 | 105.5455 | 146.8049 | 196.129 | 163.4828 | 146.0667 | 156.3864 | 108.2 | 149.3378 | 151.1811 | 153.0184 | 154.8377 | 156.1947 | 157.996 | 159.3349 | 161.1122 | 162.4331 | 164.1864 | 165.4893 | 118.6364 | 121.4286 | 157.9999 | 105.5455 | 146.8049 | 196.129 | 163.4828 | 146.0667 | 156.3864 | 108.2 | 152.5429 | 154.4474 | 156.352 | 158.2565 | 160.161 | 162.0655 | 163.9701 | 165.8746 | 167.7791 | 169.6837 | 171.5882
Waikino | 607.9231 | 282.7222 | 249.5999 | 188.25 | 259 | 688.0898 | 368.1538 | 210.75 | 380.3333 | 18.5 | 301.9401 | 307.1538 | 310.5876 | 314.0034 | 317.3832 | 320.7451 | 324.0891 | 327.415 | 330.705 | 332.341 | 335.613 | 607.9231 | 282.7222 | 249.5999 | 188.25 | 259 | 688.0898 | 368.1538 | 210.75 | 380.3333 | 18.5 | 197.0996 | 173.7846 | 150.4696 | 127.1546 | 103.8395 | 80.5245 | 57.2095 | 33.8945 | 10.5795 | -12.7355 | -36.0506
Wairarapa | 63.4902 | 73.2222 | 118.0526 | 100.2708 | 72.4211 | 96.477 | 119.9516 | 61.9 | 115.4762 | 99.7358 | 97.5327 | 98.6728 | 99.8091 | 100.6538 | 101.4947 | 102.6083 | 103.4378 | 104.2636 | 105.0855 | 105.9037 | 106.7181 | 63.4902 | 73.2222 | 118.0526 | 100.2708 | 72.4211 | 96.477 | 119.9516 | 61.9 | 115.4762 | 99.7358 | 106.2439 | 108.8156 | 111.3872 | 113.9589 | 116.5305 | 119.1022 | 121.6739 | 124.2455 | 126.8172 | 129.3888 | 131.9605
Whanganui | 280.0476 | 216.8571 | 293.5554 | 242.8148 | 172.1154 | 241.6504 | 409.9545 | 171.125 | 120.7273 | 279.8378 | 242.6642 | 244.9192 | 247.1542 | 249.3893 | 250.8694 | 253.0846 | 254.5548 | 256.7501 | 258.9256 | 260.366 | 261.7964 | 280.0476 | 216.8571 | 293.5554 | 242.8148 | 172.1154 | 241.6504 | 409.9545 | 171.125 | 120.7273 | 279.8378 | 219.002 | 214.6627 | 210.3233 | 205.984 | 201.6446 | 197.3052 | 192.9659 | 188.6265 | 184.2871 | 179.9478 | 175.6084
Conductor
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 215.8725 | 218.4639 | 239.1783 | 277.7164 | 197.5402 | 243.964 | 215.9926 | 279.1805 | 269.9266 | 217.0044
[11 empty] | 245.0916 | 247.5871 | 249.8638 | 252.4004 | 254.5659 | 256.6852 | 258.7275 | 261.1506 | 263.3632 | 265.3386 | 267.296 | [10 empty] | 246.1468 | 248.1123 | 250.0779 | 252.0434 | 254.0089 | 255.9744 | 257.94 | 259.9055 | 261.871 | 263.8366 | 265.8021
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 429 | 193.875 | 277.3845 | 217.6429 | 340.6667 | 240.7913 | 314.4286 | 464.3529 | 384.9091 | 187.5556 | 307.136 | 310.8828 | 314.6056 | 318.2925 | 321.9555 | 325.5945 | 328.0005 | 331.5917 | 335.1589 | 338.7021 | 341.0484 | 429 | 193.875 | 277.3845 | 217.6429 | 340.6667 | 240.7913 | 314.4286 | 464.3529 | 384.9091 | 187.5556 | 314.7127 | 316.4677 | 318.2226 | 319.9775 | 321.7324 | 323.4874 | 325.2423 | 326.9972 | 328.7521 | 330.5071 | 332.262
Egmont | 132.8148 | 156.5417 | 108.081 | 161.2105 | 84.7536 | 320.8441 | 79.7222 | 196.9189 | 175.5429 | 122.3878 | 143.6923 | 144.5527 | 145.4132 | 147.1342 | 147.9835 | 148.8328 | 149.6821 | 151.3807 | 152.2188 | 153.057 | 153.8951 | 132.8148 | 156.5417 | 108.081 | 161.2105 | 84.7536 | 320.8441 | 79.7222 | 196.9189 | 175.5429 | 122.3878 | 169.7144 | 172.5931 | 175.4717 | 178.3504 | 181.2291 | 184.1077 | 186.9864 | 189.8651 | 192.7437 | 195.6224 | 198.5011
Kinleith | 170 | 141.5 | 250.4999 | 335 | 76.5 | 258.9711 | 72 | 0 | 346 | 70 | 180.7876 | 180.7876 | 180.7876 | 182.8006 | 184.7872 | 184.7872 | 186.7473 | 188.7075 | 188.7075 | 190.6411 | 192.5747 | 170 | 141.5 | 250.4999 | 335 | 76.5 | 258.9711 | 72 | 0 | 346 | 70 | 127.7961 | 119.7505 | 111.7049 | 103.6593 | 95.6136 | 87.568 | 79.5224 | 71.4768 | 63.4311 | 55.3855 | 47.3399
Manawatu | 421.6 | 107.1538 | 372.2172 | 408.2917 | 451.8929 | 409.3179 | 324.9048 | 472.7143 | 339.3889 | 407.72 | 384.8896 | 388.6271 | 391.8118 | 394.4513 | 397.0762 | 399.6938 | 402.2969 | 405.4163 | 407.9976 | 410.5716 | 413.131 | 421.6 | 107.1538 | 372.2172 | 408.2917 | 451.8929 | 409.3179 | 324.9048 | 472.7143 | 339.3889 | 407.72 | 428.536 | 438.9025 | 449.269 | 459.6355 | 470.002 | 480.3686 | 490.7351 | 501.1016 | 511.4681 | 521.8346 | 532.2011
Mt Maunganui | 204 | 209.5385 | 312.1763 | 297.069 | 186 | 288.9677 | 57.2857 | 101 | 294.5 | 220.5556 | 235.7552 | 238.4397 | 241.1101 | 243.2295 | 245.8645 | 247.9627 | 250.5695 | 252.6394 | 255.2109 | 257.2596 | 259.2942 | 204 | 209.5385 | 312.1763 | 297.069 | 186 | 288.9677 | 57.2857 | 101 | 294.5 | 220.5556 | 186.1582 | 180.5307 | 174.9032 | 169.2758 | 163.6483 | 158.0208 | 152.3933 | 146.7659 | 141.1384 | 135.5109 | 129.8835
Rangitikei | 62.9286 | 220.4 | 165.0587 | 165.9524 | 136.4545 | 66.6176 | 147.2143 | 194.4 | 158.9286 | 108.3889 | 152.5668 | 153.5755 | 154.5698 | 155.5641 | 156.5584 | 157.5527 | 158.547 | 160.5212 | 161.5011 | 162.4809 | 163.4608 | 62.9286 | 220.4 | 165.0587 | 165.9524 | 136.4545 | 66.6176 | 147.2143 | 194.4 | 158.9286 | 108.3889 | 142.6176 | 142.6146 | 142.6115 | 142.6085 | 142.6054 | 142.6024 | 142.5994 | 142.5963 | 142.5933 | 142.5902 | 142.5872
Taranaki | 148.0741 | 209.4545 | 240.9284 | 150.697 | 141.5088 | 136.4133 | 394.4062 | 313.4 | 236.5946 | 248.1818 | 228.7604 | 230.5482 | 232.682 | 234.4458 | 235.8491 | 237.5985 | 238.9922 | 240.7319 | 242.4573 | 244.1826 | 245.5523 | 148.0741 | 209.4545 | 240.9284 | 150.697 | 141.5088 | 136.4133 | 394.4062 | 313.4 | 236.5946 | 248.1818 | 294.6106 | 307.8187 | 321.0268 | 334.2349 | 347.443 | 360.6512 | 373.8593 | 387.0674 | 400.2755 | 413.4837 | 426.6918
Tararua | 137.0909 | 57.2 | 36.9444 | 105.6471 | 152.6 | 50.0713 | 102.8125 | 95 | 135.0667 | 105.4286 | 97.7087 | 97.7087 | 97.7087 | 99.9644 | 99.9644 | 99.9644 | 99.9644 | 99.9644 | 102.1758 | 102.1758 | 102.1758 | 137.0909 | 57.2 | 36.9444 | 105.6471 | 152.6 | 50.0713 | 102.8125 | 95 | 135.0667 | 105.4286 | 112.4312 | 115.0939 | 117.7567 | 120.4194 | 123.0821 | 125.7449 | 128.4076 | 131.0703 | 133.7331 | 136.3958 | 139.0585
Tauranga | 261.3529 | 555 | 196.4285 | 513.2857 | 285.4286 | 492.1672 | 355.75 | 487.2632 | 430.7778 | 352.6667 | 424.9617 | 429.5435 | 434.1007 | 438.6248 | 442.5557 | 447.0304 | 450.92 | 455.337 | 459.7211 | 463.5366 | 467.3355 | 261.3529 | 555 | 196.4285 | 513.2857 | 285.4286 | 492.1672 | 355.75 | 487.2632 | 430.7778 | 352.6667 | 431.0311 | 437.9437 | 444.8563 | 451.7688 | 458.6814 | 465.594 | 472.5065 | 479.4191 | 486.3317 | 493.2442 | 500.1568
Waikato | 226.6364 | 160.5556 | 211.3332 | 270.4667 | 154.5714 | 180.7576 | 417 | 237.2667 | 309.3158 | 341 | 249.2749 | 252.3518 | 255.4187 | 258.4554 | 260.7205 | 263.7272 | 265.9622 | 268.9288 | 271.1337 | 274.0603 | 276.2351 | 226.6364 | 160.5556 | 211.3332 | 270.4667 | 154.5714 | 180.7576 | 417 | 237.2667 | 309.3158 | 341 | 339.7586 | 355.9164 | 372.0743 | 388.2322 | 404.39 | 420.5479 | 436.7058 | 452.8636 | 469.0215 | 485.1794 | 501.3372
Waikino | 306.2 | 464.3333 | 740.5996 | 652 | 192 | 554.1881 | 247.7273 | 551.4286 | 258.8571 | 235.8 | 394.6747 | 401.4895 | 405.978 | 410.4429 | 414.8608 | 419.2552 | 423.6262 | 427.9736 | 432.274 | 434.4125 | 438.6894 | 306.2 | 464.3333 | 740.5996 | 652 | 192 | 554.1881 | 247.7273 | 551.4286 | 258.8571 | 235.8 | 291.3661 | 267.9212 | 244.4762 | 221.0312 | 197.5863 | 174.1413 | 150.6963 | 127.2514 | 103.8064 | 80.3615 | 56.9165
Wairarapa | 126.75 | 197.7 | 67.6666 | 123.9355 | 139.3125 | 42.4397 | 146.7111 | 104.6087 | 152.3462 | 193.4222 | 140.8912 | 142.5381 | 144.1796 | 145.3998 | 146.6145 | 148.2232 | 149.4215 | 150.6143 | 151.8016 | 152.9835 | 154.1599 | 126.75 | 197.7 | 67.6666 | 123.9355 | 139.3125 | 42.4397 | 146.7111 | 104.6087 | 152.3462 | 193.4222 | 144.1138 | 146.7728 | 149.4319 | 152.0909 | 154.7499 | 157.4089 | 160.0679 | 162.7269 | 165.386 | 168.045 | 170.704
Whanganui | 179.8947 | 166.7778 | 129.9999 | 209.1154 | 226.3333 | 129.9855 | 147.9412 | 131.8125 | 286.8182 | 227.95 | 199.2189 | 201.0702 | 202.9051 | 204.74 | 205.9551 | 207.7737 | 208.9807 | 210.7829 | 212.5689 | 213.7514 | 214.9258 | 179.8947 | 166.7778 | 129.9999 | 209.1154 | 226.3333 | 129.9855 | 147.9412 | 131.8125 | 286.8182 | 227.95 | 217.0619 | 223.1345 | 229.2071 | 235.2796 | 241.3522 | 247.4247 | 253.4973 | 259.5699 | 265.6424 | 271.715 | 277.7875
Transformers
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 226.8923 | 141.0838 | 105.606 | 116.1293 | 236.8658 | 48.0476 | 36.1196 | 43.5213 | 37.0519 | 47.2515
[11 empty] | 67.6095 | 68.1454 | 68.655 | 69.3623 | 69.9514 | 70.4305 | 70.987 | 71.6671 | 72.1708 | 72.7402 | 73.2796 | [10 empty] | 14.0489 | -0.52641 | -15.1017 | -29.677 | -44.2523 | -58.8276 | -73.4029 | -87.9782 | -102.5535 | -117.1289 | -131.7042
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 9 | 392.5 | 467.7498 | 78.75 | 154 | 15.9982 | 23.6364 | 13.7273 | 5.6 | 133.8 | 80.8146 | 81.8005 | 82.7801 | 83.7502 | 84.714 | 85.6715 | 86.3046 | 87.2495 | 88.1881 | 89.1204 | 89.7378 | 9 | 392.5 | 467.7498 | 78.75 | 154 | 15.9982 | 23.6364 | 13.7273 | 5.6 | 133.8 | -9.1423 | -34.3457 | -59.5491 | -84.7524 | -109.9558 | -135.1592 | -160.3625 | -185.5659 | -210.7693 | -235.9726 | -261.176
Egmont | 66.3333 | 261.8889 | 168.7499 | 68.6471 | 58.75 | 54.7036 | 15.4722 | 74.6333 | 82.6522 | 28.2692 | 62.472 | 62.8461 | 63.2202 | 63.9684 | 64.3377 | 64.7069 | 65.0761 | 65.8146 | 66.179 | 66.5434 | 66.9078 | 66.3333 | 261.8889 | 168.7499 | 68.6471 | 58.75 | 54.7036 | 15.4722 | 74.6333 | 82.6522 | 28.2692 | 13.6304 | 0.10682 | -13.4167 | -26.9403 | -40.4639 | -53.9874 | -67.511 | -81.0346 | -94.5581 | -108.0817 | -121.6052
Kinleith | 1298 | 417 | 62 | 58 | 588 | 49.9944 | 0 | 0 | 13.3333 | 138.4 | 161.0198 | 161.0198 | 161.0198 | 162.8128 | 164.5822 | 164.5822 | 166.328 | 168.0737 | 168.0737 | 169.7959 | 171.5181 | 1298 | 417 | 62 | 58 | 588 | 49.9944 | 0 | 0 | 13.3333 | 138.4 | -213.663 | -300.2331 | -386.8032 | -473.3734 | -559.9435 | -646.5136 | -733.0838 | -819.6539 | -906.224 | -992.7942 | -1079.3643
Manawatu | 0 | 10 | 0 | 72 | 324.5714 | 73.4128 | 9.5714 | 1.8889 | 84.5 | 86.15 | 80.1164 | 80.8944 | 81.5573 | 82.1067 | 82.6531 | 83.198 | 83.7398 | 84.3891 | 84.9264 | 85.4622 | 85.995 | 0 | 10 | 0 | 72 | 324.5714 | 73.4128 | 9.5714 | 1.8889 | 84.5 | 86.15 | 95.1378 | 100.3975 | 105.6572 | 110.9169 | 116.1766 | 121.4363 | 126.696 | 131.9557 | 137.2154 | 142.4751 | 147.7348
Mt Maunganui | 0 | 4.3333 | 105.3333 | 20.8 | 251.75 | 2.5553 | 38.125 | 3.6 | 5.2222 | 5.4 | 36.9184 | 37.3388 | 37.757 | 38.0889 | 38.5015 | 38.8301 | 39.2383 | 39.5625 | 39.9651 | 40.286 | 40.6046 | 0 | 4.3333 | 105.3333 | 20.8 | 251.75 | 2.5553 | 38.125 | 3.6 | 5.2222 | 5.4 | 22.0098 | 18.0639 | 14.1181 | 10.1723 | 6.2264 | 2.2806 | -1.6653 | -5.6111 | -9.557 | -13.5028 | -17.4486
Rangitikei | 145.75 | 99 | 2 | 301 | 566 | 51.1609 | 1.8 | 91.6 | 12.5 | 4.375 | 70.0792 | 70.5426 | 70.9993 | 71.456 | 71.9127 | 72.3694 | 72.8261 | 73.733 | 74.1831 | 74.6331 | 75.0832 | 145.75 | 99 | 2 | 301 | 566 | 51.1609 | 1.8 | 91.6 | 12.5 | 4.375 | 32.7748 | 15.5486 | -1.6775 | -18.9036 | -36.1298 | -53.3559 | -70.5821 | -87.8082 | -105.0344 | -122.2605 | -139.4867
Taranaki | 25 | 177 | 6.6667 | 124.4 | 63.7333 | 21.9286 | 17.4737 | 27.1875 | 81.6 | 30.5238 | 46.1049 | 46.4653 | 46.8953 | 47.2508 | 47.5336 | 47.8862 | 48.1671 | 48.5177 | 48.8654 | 49.2132 | 49.4892 | 25 | 177 | 6.6667 | 124.4 | 63.7333 | 21.9286 | 17.4737 | 27.1875 | 81.6 | 30.5238 | 28.2825 | 22.9609 | 17.6393 | 12.3177 | 6.9961 | 1.6745 | -3.6471 | -8.9687 | -14.2903 | -19.612 | -24.9336
Tararua | 0 | 0 | 18 | 14 | 57 | 60.7075 | 47 | 53 | 1.75 | 22.1429 | 31.1913 | 31.1913 | 31.1913 | 31.9113 | 31.9113 | 31.9113 | 31.9113 | 31.9113 | 32.6173 | 32.6173 | 32.6173 | 0 | 0 | 18 | 14 | 57 | 60.7075 | 47 | 53 | 1.75 | 22.1429 | 43.6681 | 46.6333 | 49.5984 | 52.5635 | 55.5286 | 58.4937 | 61.4588 | 64.4239 | 67.389 | 70.3541 | 73.3193
Tauranga | 228.8571 | 61.4 | 32.75 | 104.75 | 150.5 | 43.0952 | 186.8 | 33.7692 | 53.9231 | 6.7692 | 66.2389 | 66.9531 | 67.6634 | 68.3686 | 68.9813 | 69.6788 | 70.285 | 70.9735 | 71.6569 | 72.2516 | 72.8437 | 228.8571 | 61.4 | 32.75 | 104.75 | 150.5 | 43.0952 | 186.8 | 33.7692 | 53.9231 | 6.7692 | 26.6851 | 15.1258 | 3.5665 | -7.9929 | -19.5522 | -31.1115 | -42.6708 | -54.2301 | -65.7895 | -77.3488 | -88.9081
Waikato | 214.125 | 78.8 | 60.6666 | 126 | 137.2 | 33.063 | 11.8182 | 4.2 | 107.4444 | 14.125 | 62.1682 | 62.9356 | 63.7004 | 64.4578 | 65.0227 | 65.7725 | 66.3299 | 67.0698 | 67.6197 | 68.3496 | 68.892 | 214.125 | 78.8 | 60.6666 | 126 | 137.2 | 33.063 | 11.8182 | 4.2 | 107.4444 | 14.125 | 1.1274 | -12.9847 | -27.0969 | -41.209 | -55.3212 | -69.4333 | -83.5455 | -97.6576 | -111.7698 | -125.8819 | -139.9941
Waikino | 161 | 7 | 29 | 16.3333 | 535 | 6.4993 | 36.3333 | 3 | 24.4 | 1 | 41.5878 | 42.3059 | 42.7789 | 43.2494 | 43.7149 | 44.1779 | 44.6385 | 45.0966 | 45.5498 | 45.7751 | 46.2258 | 161 | 7 | 29 | 16.3333 | 535 | 6.4993 | 36.3333 | 3 | 24.4 | 1 | 18.0666 | 6.4502 | -5.1662 | -16.7825 | -28.3989 | -40.0153 | -51.6316 | -63.248 | -74.8644 | -86.4807 | -98.0971
Wairarapa | 45.8571 | 43 | 208.7499 | 468 | 24.75 | 10.6655 | 34.0714 | 41.5385 | 6.5 | 106.6 | 72.6029 | 73.4516 | 74.2974 | 74.9262 | 75.5522 | 76.3811 | 76.9986 | 77.6133 | 78.2251 | 78.8342 | 79.4404 | 45.8571 | 43 | 208.7499 | 468 | 24.75 | 10.6655 | 34.0714 | 41.5385 | 6.5 | 106.6 | 36.9485 | 25.6713 | 14.3941 | 3.1169 | -8.1604 | -19.4376 | -30.7148 | -41.992 | -53.2693 | -64.5465 | -75.8237
Whanganui | 75 | 0 | 0 | 57 | 168 | 200.8347 | 11.3333 | 174.1111 | 2.25 | 36.7143 | 114.1303 | 115.1908 | 116.242 | 117.2932 | 117.9894 | 119.0312 | 119.7227 | 120.7552 | 121.7784 | 122.4558 | 123.1286 | 75 | 0 | 0 | 57 | 168 | 200.8347 | 11.3333 | 174.1111 | 2.25 | 36.7143 | 87.11 | 89.7619 | 92.4138 | 95.0658 | 97.7177 | 100.3696 | 103.0216 | 105.6735 | 108.3254 | 110.9774 | 113.6293
Fuses
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 152.4655 | 90.2669 | 82.7927 | 90.0016 | 123.337 | 79.9917 | 68.8023 | 30.4765 | 21.5464 | 20.3266
[11 empty] | 41.4156 | 41.7853 | 42.132 | 42.5646 | 42.9177 | 43.2407 | 43.5749 | 43.9767 | 44.3248 | 44.6577 | 44.9804 | [10 empty] | 9.4326 | -2.1231 | -13.6788 | -25.2345 | -36.7902 | -48.3459 | -59.9016 | -71.4573 | -83.013 | -94.5687 | -106.1244
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 47 | 51 | 66.5 | 47.3333 | 490.5 | 70.7921 | 82.25 | 57.5312 | 33.8444 | 18.9796 | 46.4257 | 46.992 | 47.5547 | 48.112 | 48.6657 | 49.2158 | 49.5795 | 50.1223 | 50.6615 | 51.1971 | 51.5517 | 47 | 51 | 66.5 | 47.3333 | 490.5 | 70.7921 | 82.25 | 57.5312 | 33.8444 | 18.9796 | 72.1706 | 67.7338 | 63.297 | 58.8602 | 54.4233 | 49.9865 | 45.5497 | 41.1129 | 36.6761 | 32.2393 | 27.8025
Egmont | 55.6 | 25.625 | 35.8 | 45.6111 | 152.2 | 140.102 | 31.6 | 28.0606 | 37.8125 | 9.6512 | 37.297 | 37.5204 | 37.7437 | 38.1904 | 38.4109 | 38.6313 | 38.8517 | 39.2926 | 39.5102 | 39.7277 | 39.9453 | 55.6 | 25.625 | 35.8 | 45.6111 | 152.2 | 140.102 | 31.6 | 28.0606 | 37.8125 | 9.6512 | 42.1711 | 39.6192 | 37.0674 | 34.5155 | 31.9637 | 29.4118 | 26.86 | 24.3081 | 21.7563 | 19.2044 | 16.6526
Kinleith | 0 | 0 | 18 | 178.75 | 133 | 42.9952 | 0 | 3.8 | 15 | 10.2 | 58.0369 | 58.0369 | 58.0369 | 58.6831 | 59.3208 | 59.3208 | 59.9501 | 60.5793 | 60.5793 | 61.2001 | 61.8208 | 0 | 0 | 18 | 178.75 | 133 | 42.9952 | 0 | 3.8 | 15 | 10.2 | 23.4927 | 20.4596 | 17.4266 | 14.3935 | 11.3605 | 8.3274 | 5.2943 | 2.2613 | -0.77178 | -3.8048 | -6.8379
Manawatu | 81.7143 | 221.8 | 173.4285 | 122.0556 | 124.9091 | 47.4114 | 186.6667 | 32.8421 | 44.881 | 24.3438 | 61.2053 | 61.7996 | 62.3061 | 62.7258 | 63.1432 | 63.5595 | 63.9734 | 64.4694 | 64.8799 | 65.2892 | 65.6963 | 81.7143 | 221.8 | 173.4285 | 122.0556 | 124.9091 | 47.4114 | 186.6667 | 32.8421 | 44.881 | 24.3438 | 27.9597 | 13.7697 | -0.42043 | -14.6105 | -28.8006 | -42.9907 | -57.1808 | -71.3709 | -85.561 | -99.751 | -113.9411
Mt Maunganui | 28.1667 | 20.25 | 62 | 25.3333 | 101.5714 | 0 | 19 | 8.7692 | 28.7407 | 11.5417 | 27.0785 | 27.3869 | 27.6936 | 27.937 | 28.2397 | 28.4807 | 28.7801 | 29.0178 | 29.3132 | 29.5485 | 29.7822 | 28.1667 | 20.25 | 62 | 25.3333 | 101.5714 | 0 | 19 | 8.7692 | 28.7407 | 11.5417 | 14.6401 | 11.7497 | 8.8594 | 5.969 | 3.0786 | 0.18817 | -2.7022 | -5.5926 | -8.483 | -11.3734 | -14.2638
Rangitikei | 64.1667 | 47.6 | 53 | 32 | 117 | 65.2149 | 104.5 | 6.9091 | 9.4762 | 31.7812 | 25.5063 | 25.675 | 25.8412 | 26.0074 | 26.1736 | 26.3399 | 26.5061 | 26.8361 | 27 | 27.1638 | 27.3276 | 64.1667 | 47.6 | 53 | 32 | 117 | 65.2149 | 104.5 | 6.9091 | 9.4762 | 31.7812 | 32.3956 | 28.6194 | 24.8432 | 21.067 | 17.2908 | 13.5146 | 9.7384 | 5.9622 | 2.186 | -1.5903 | -5.3665
Taranaki | 116.5714 | 85.6957 | 76.9047 | 130.7368 | 121.5833 | 58.4935 | 169.75 | 10.971 | 18.5263 | 24.6818 | 44.2292 | 44.5749 | 44.9875 | 45.3285 | 45.5998 | 45.938 | 46.2075 | 46.5439 | 46.8774 | 47.211 | 47.4758 | 116.5714 | 85.6957 | 76.9047 | 130.7368 | 121.5833 | 58.4935 | 169.75 | 10.971 | 18.5263 | 24.6818 | 28.9611 | 19.4283 | 9.8955 | 0.36272 | -9.1701 | -18.7029 | -28.2357 | -37.7684 | -47.3012 | -56.834 | -66.3668
Tararua | 41.3333 | 32.8 | 49.125 | 35 | 41.1667 | 104.5597 | 28 | 7.1 | 9.7222 | 20.806 | 22.3946 | 22.3946 | 22.3946 | 22.9116 | 22.9116 | 22.9116 | 22.9116 | 22.9116 | 23.4185 | 23.4185 | 23.4185 | 41.3333 | 32.8 | 49.125 | 35 | 41.1667 | 104.5597 | 28 | 7.1 | 9.7222 | 20.806 | 19.8272 | 16.7119 | 13.5966 | 10.4813 | 7.3661 | 4.2508 | 1.1355 | -1.9798 | -5.0951 | -8.2104 | -11.3257
Tauranga | 229.2 | 206.6667 | 117.8333 | 136.8667 | 55 | 180.8548 | 81.4667 | 37.8148 | 30.3014 | 54.325 | 66.2024 | 66.9162 | 67.6261 | 68.3309 | 68.9432 | 69.6403 | 70.2463 | 70.9344 | 71.6173 | 72.2117 | 72.8036 | 229.2 | 206.6667 | 117.8333 | 136.8667 | 55 | 180.8548 | 81.4667 | 37.8148 | 30.3014 | 54.325 | 4.7373 | -14.9528 | -34.643 | -54.3331 | -74.0232 | -93.7133 | -113.4034 | -133.0936 | -152.7837 | -172.4738 | -192.1639
Waikato | 148 | 103.1818 | 35.7143 | 213.6667 | 92.75 | 34.5961 | 38 | 7.1905 | 10.3396 | 10.6957 | 28.0986 | 28.4454 | 28.7911 | 29.1334 | 29.3887 | 29.7276 | 29.9796 | 30.314 | 30.5625 | 30.8924 | 31.1375 | 148 | 103.1818 | 35.7143 | 213.6667 | 92.75 | 34.5961 | 38 | 7.1905 | 10.3396 | 10.6957 | -17.7001 | -33.5389 | -49.3778 | -65.2166 | -81.0554 | -96.8943 | -112.7331 | -128.5719 | -144.4108 | -160.2496 | -176.0884
Waikino | 851 | 133 | 170.4999 | 144.5 | 14.5 | 171.9808 | 10.6667 | 98.7778 | 8.1154 | 15.6452 | 40.9971 | 41.7051 | 42.1713 | 42.6351 | 43.094 | 43.5505 | 44.0045 | 44.4561 | 44.9028 | 45.1249 | 45.5692 | 851 | 133 | 170.4999 | 144.5 | 14.5 | 171.9808 | 10.6667 | 98.7778 | 8.1154 | 15.6452 | -137.9653 | -192.4805 | -246.9958 | -301.511 | -356.0263 | -410.5415 | -465.0568 | -519.572 | -574.0873 | -628.6025 | -683.1178
Wairarapa | 150.3333 | 97.8333 | 112.4999 | 50.1667 | 141.2 | 32.5678 | 35.7273 | 85.9 | 20.6216 | 10.18 | 39.5154 | 39.9773 | 40.4377 | 40.7799 | 41.1206 | 41.5718 | 41.9079 | 42.2424 | 42.5755 | 42.9069 | 43.2369 | 150.3333 | 97.8333 | 112.4999 | 50.1667 | 141.2 | 32.5678 | 35.7273 | 85.9 | 20.6216 | 10.18 | 4.1426 | -8.5048 | -21.1521 | -33.7994 | -46.4468 | -59.0941 | -71.7415 | -84.3888 | -97.0362 | -109.6835 | -122.3309
Whanganui | 16.5 | 57.75 | 104.9999 | 8 | 18 | 10.3322 | 38 | 10.5278 | 12.7213 | 21.4143 | 17.6674 | 17.8315 | 17.9943 | 18.157 | 18.2647 | 18.426 | 18.5331 | 18.6929 | 18.8513 | 18.9562 | 19.0603 | 16.5 | 57.75 | 104.9999 | 8 | 18 | 10.3322 | 38 | 10.5278 | 12.7213 | 21.4143 | 7.7912 | 3.7851 | -0.22095 | -4.227 | -8.2331 | -12.2391 | -16.2452 | -20.2513 | -24.2573 | -28.2634 | -32.2695
Sub-Trans
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 2170.0483 | 2161.8283 | 1778.4631 | 2511.4857 | 2231.4475 | 1848.4334 | 1705.7186 | 1969.4167 | 2170.9394 | 1973.8907
[11 empty] | 1542.7036 | 1558.8207 | 1573.425 | 1589.6243 | 1603.596 | 1617.2382 | 1630.1861 | 1645.4359 | 1659.9147 | 1672.3042 | 1684.6459 | [10 empty] | 1335.7719 | 1303.1006 | 1270.4292 | 1237.7579 | 1205.0865 | 1172.4152 | 1139.7438 | 1107.0725 | 1074.4011 | 1041.7298 | 1009.0584
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 3936.75 | 4402.3333 | 6004.854 | 0 | 2327 | 4553.9911 | 2651 | 1 | 0 | 2404 | 2672.0405 | 2704.6368 | 2737.0247 | 2769.1003 | 2800.9675 | 2832.6265 | 2853.5589 | 2884.8014 | 2915.8355 | 2946.6613 | 2967.0731 | 3936.75 | 4402.3333 | 6004.854 | 0 | 2327 | 4553.9911 | 2651 | 1 | 0 | 2404 | 479.7474 | 89.1392 | -301.4691 | -692.0773 | -1082.6856 | -1473.2938 | -1863.9021 | -2254.5104 | -2645.1186 | -3035.7269 | -3426.3351
Egmont | 1384 | 537 | 1463.4992 | 0 | 1452 | 592.9337 | 1456.5 | 0 | 903 | 1730 | 963.5837 | 969.354 | 975.1243 | 986.6649 | 992.3602 | 998.0556 | 1003.7509 | 1015.1416 | 1020.762 | 1026.3824 | 1032.0029 | 1384 | 537 | 1463.4992 | 0 | 1452 | 592.9337 | 1456.5 | 0 | 903 | 1730 | 1014.1912 | 1025.5181 | 1036.845 | 1048.1719 | 1059.4988 | 1070.8257 | 1082.1526 | 1093.4795 | 1104.8064 | 1116.1333 | 1127.4602
Kinleith | 0 | 0 | 0 | 2787 | 0 | 0 | 0 | 0 | 3358 | 3400 | 966.2225 | 966.2225 | 966.2225 | 976.9814 | 987.5988 | 987.5988 | 998.0747 | 1008.5505 | 1008.5505 | 1018.8848 | 1029.219 | 0 | 0 | 0 | 2787 | 0 | 0 | 0 | 0 | 3358 | 3400 | 2479.3333 | 2756.5758 | 3033.8182 | 3311.0606 | 3588.303 | 3865.5455 | 4142.7879 | 4420.0303 | 4697.2727 | 4974.5152 | 5251.7576
Manawatu | 1885.3333 | 3454 | 1 | 5781 | 2917.5 | 2950.6702 | 1205.5 | 0 | 535 | 1393.6 | 2037.0747 | 2056.8553 | 2073.7112 | 2087.6808 | 2101.5735 | 2115.4276 | 2129.2048 | 2145.7143 | 2159.3761 | 2172.9993 | 2186.5456 | 1885.3333 | 3454 | 1 | 5781 | 2917.5 | 2950.6702 | 1205.5 | 0 | 535 | 1393.6 | 727.1294 | 493.451 | 259.7726 | 26.0943 | -207.5841 | -441.2624 | -674.9408 | -908.6192 | -1142.2975 | -1375.9759 | -1609.6543
Mt Maunganui | 5546 | 0 | 954.7495 | 1540.8571 | 0 | 0 | 1531.5 | 3698 | 4799 | 338 | 1863.4181 | 1884.6367 | 1905.7436 | 1922.4951 | 1943.3228 | 1959.9068 | 1980.5112 | 1996.8718 | 2017.1969 | 2033.3901 | 2049.4715 | 5546 | 0 | 954.7495 | 1540.8571 | 0 | 0 | 1531.5 | 3698 | 4799 | 338 | 1854.45 | 1856.9299 | 1859.4098 | 1861.8897 | 1864.3696 | 1866.8495 | 1869.3293 | 1871.8092 | 1874.2891 | 1876.769 | 1879.2489
Rangitikei | 800 | 816 | 891.9995 | 856 | 1705 | 1148.2717 | 0 | 1563.5 | 1643.5 | 0 | 954.0013 | 960.3088 | 966.5261 | 972.7435 | 978.9608 | 985.1782 | 991.3955 | 1003.7401 | 1009.8674 | 1015.9946 | 1022.1219 | 800 | 816 | 891.9995 | 856 | 1705 | 1148.2717 | 0 | 1563.5 | 1643.5 | 0 | 903.2696 | 896.15 | 889.0305 | 881.9109 | 874.7914 | 867.6718 | 860.5523 | 853.4327 | 846.3132 | 839.1936 | 832.0741
Taranaki | 136 | 0 | 761.3329 | 505 | 804.7778 | 737.4176 | 539.6667 | 1028 | 1301 | 3322.5 | 924.7893 | 932.0167 | 940.6429 | 947.7732 | 953.4463 | 960.5183 | 966.1526 | 973.1857 | 980.1605 | 987.1354 | 992.6725 | 136 | 0 | 761.3329 | 505 | 804.7778 | 737.4176 | 539.6667 | 1028 | 1301 | 3322.5 | 2218.752 | 2456.0579 | 2693.3638 | 2930.6697 | 3167.9756 | 3405.2816 | 3642.5875 | 3879.8934 | 4117.1993 | 4354.5052 | 4591.8111
Tararua | 314.4 | 464 | 630.9997 | 152 | 500 | 632.9293 | 632 | 2826 | 313.3333 | 537.25 | 708.8917 | 708.8917 | 708.8917 | 725.2568 | 725.2568 | 725.2568 | 725.2568 | 725.2568 | 741.301 | 741.301 | 741.301 | 314.4 | 464 | 630.9997 | 152 | 500 | 632.9293 | 632 | 2826 | 313.3333 | 537.25 | 1150.255 | 1232.0666 | 1313.8782 | 1395.6898 | 1477.5014 | 1559.313 | 1641.1246 | 1722.9362 | 1804.7478 | 1886.5594 | 1968.3711
Tauranga | 0 | 4046.6 | 0 | 5731 | 5724 | 5683.8648 | 1212 | 0 | 0 | 0 | 2267.2534 | 2291.6984 | 2316.0116 | 2340.1489 | 2361.1206 | 2384.9941 | 2405.746 | 2429.3117 | 2452.7016 | 2473.0578 | 2493.3261 | 0 | 4046.6 | 0 | 5731 | 5724 | 5683.8648 | 1212 | 0 | 0 | 0 | 842.302 | 588.2212 | 334.1403 | 80.0595 | -174.0213 | -428.1021 | -682.1829 | -936.2638 | -1190.3446 | -1444.4254 | -1698.5062
Waikato | 1568 | 1192 | 2870.9985 | 0 | 0 | 411.454 | 1328 | 0 | 2067 | 674 | 1023.5634 | 1036.1975 | 1048.7905 | 1061.26 | 1070.5607 | 1082.9067 | 1092.084 | 1104.2654 | 1113.3192 | 1125.336 | 1134.2663 | 1568 | 1192 | 2870.9985 | 0 | 0 | 411.454 | 1328 | 0 | 2067 | 674 | 615.1273 | 543.124 | 471.1208 | 399.1175 | 327.1143 | 255.111 | 183.1077 | 111.1045 | 39.1012 | -32.9021 | -104.9053
Waikino | 5494 | 5547 | 0 | 4421 | 0 | 0 | 5643.5714 | 0 | 5688 | 0 | 2712.263 | 2759.0959 | 2789.941 | 2820.6246 | 2850.9853 | 2881.1844 | 2911.222 | 2941.0982 | 2970.6514 | 2985.3472 | 3014.7389 | 5494 | 5547 | 0 | 4421 | 0 | 0 | 5643.5714 | 0 | 5688 | 0 | 1186.3143 | 914.8519 | 643.3896 | 371.9273 | 100.4649 | -170.9974 | -442.4597 | -713.9221 | -985.3844 | -1256.8468 | -1528.3091
Wairarapa | 636 | 445.6 | 1243.1993 | 1065 | 1552.75 | 1444.8385 | 693.6667 | 2700 | 274.5 | 3965.6667 | 1419.3419 | 1435.9335 | 1452.47 | 1464.7621 | 1476.9991 | 1493.2048 | 1505.2764 | 1517.2929 | 1529.2543 | 1541.1605 | 1553.0116 | 636 | 445.6 | 1243.1993 | 1065 | 1552.75 | 1444.8385 | 693.6667 | 2700 | 274.5 | 3965.6667 | 2563.1685 | 2774.2679 | 2985.3672 | 3196.4665 | 3407.5659 | 3618.6652 | 3829.7646 | 4040.8639 | 4251.9633 | 4463.0626 | 4674.162
Whanganui | 0 | 713.75 | 2961.9984 | 2276 | 3100 | 327.9633 | 1869.5 | 0 | 2998 | 0 | 1442.2186 | 1455.6202 | 1468.9038 | 1482.1874 | 1490.9841 | 1504.1496 | 1512.8872 | 1525.9347 | 1538.864 | 1547.4245 | 1555.926 | 0 | 713.75 | 2961.9984 | 2276 | 3100 | 327.9633 | 1869.5 | 0 | 2998 | 0 | 1330.9952 | 1313.9541 | 1296.913 | 1279.872 | 1262.8309 | 1245.7898 | 1228.7487 | 1211.7076 | 1194.6665 | 1177.6255 | 1160.5844
The rest of the equipment
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 333.5974 | 393.5099 | 374.484 | 648.7332 | 427.2109 | 525.9394 | 375.6148 | 396.6162 | 388.572 | 734.1962
[11 empty] | 453.4006 | 457.9778 | 462.0048 | 466.6343 | 470.7375 | 474.5266 | 478.376 | 483.0358 | 486.7826 | 490.4409 | 494.1803 | [10 empty] | 542.8006 | 558.9518 | 575.103 | 591.2542 | 607.4054 | 623.5566 | 639.7078 | 655.859 | 672.0102 | 688.1614 | 704.3126
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 338.2 | 689.8182 | 327.1248 | 670.4444 | 498.8 | 2348.7375 | 108.1111 | 893.7503 | 551.2125 | 193.2857 | 644.3122 | 652.1722 | 659.9819 | 667.7164 | 675.4006 | 683.0345 | 688.082 | 695.6155 | 703.0988 | 710.5319 | 715.4538 | 338.2 | 689.8182 | 327.1248 | 670.4444 | 498.8 | 2348.7375 | 108.1111 | 893.7503 | 551.2125 | 193.2857 | 686.0017 | 690.375 | 694.7483 | 699.1216 | 703.4949 | 707.8683 | 712.2416 | 716.6149 | 720.9882 | 725.3615 | 729.7348
Egmont | 148 | 474 | 173.6666 | 296.8571 | 500.5 | 843.4057 | 397.1765 | 244.5441 | 182.5575 | 277.5455 | 325.0031 | 326.9493 | 328.8956 | 332.788 | 334.709 | 336.6299 | 338.5509 | 342.3928 | 344.2885 | 346.1842 | 348.0799 | 148 | 474 | 173.6666 | 296.8571 | 500.5 | 843.4057 | 397.1765 | 244.5441 | 182.5575 | 277.5455 | 357.9607 | 358.7126 | 359.4645 | 360.2164 | 360.9683 | 361.7202 | 362.4721 | 363.224 | 363.9759 | 364.7278 | 365.4797
Kinleith | 412.75 | 868 | 486.7997 | 808.5 | 541 | 171.6475 | 497.6 | 787.1627 | 412.4023 | 699.875 | 574.5943 | 574.5943 | 574.5943 | 580.9924 | 587.3064 | 587.3064 | 593.5362 | 599.766 | 599.766 | 605.9116 | 612.0571 | 412.75 | 868 | 486.7997 | 808.5 | 541 | 171.6475 | 497.6 | 787.1627 | 412.4023 | 699.875 | 555.0638 | 552.6075 | 550.1511 | 547.6948 | 545.2385 | 542.7821 | 540.3258 | 537.8694 | 535.4131 | 532.9567 | 530.5004
Manawatu | 583.3125 | 1005.6667 | 587.7056 | 482.75 | 586.9259 | 741.2981 | 774.1905 | 797.7838 | 820.2727 | 1582.3846 | 779.0284 | 786.593 | 793.0391 | 798.3814 | 803.6943 | 808.9925 | 814.2612 | 820.5749 | 825.7995 | 831.0094 | 836.1898 | 583.3125 | 1005.6667 | 587.7056 | 482.75 | 586.9259 | 741.2981 | 774.1905 | 797.7838 | 820.2727 | 1582.3846 | 1121.9949 | 1181.2251 | 1240.4552 | 1299.6854 | 1358.9155 | 1418.1457 | 1477.3759 | 1536.606 | 1595.8362 | 1655.0663 | 1714.2965
Mt Maunganui | 480.6667 | 10.75 | 270.2856 | 327.5 | 110.2 | 95.3893 | 50.6364 | 46.2711 | 162.6446 | 322.4615 | 185.5613 | 187.6743 | 189.7761 | 191.4442 | 193.5183 | 195.1697 | 197.2215 | 198.8508 | 200.8748 | 202.4873 | 204.0887 | 480.6667 | 10.75 | 270.2856 | 327.5 | 110.2 | 95.3893 | 50.6364 | 46.2711 | 162.6446 | 322.4615 | 110.1453 | 96.0479 | 81.9506 | 67.8533 | 53.756 | 39.6587 | 25.5613 | 11.464 | -2.6333 | -16.7306 | -30.8279
Rangitikei | 275.5 | 61.6 | 329.9998 | 1114 | 666 | 201.9774 | 386 | 152.6115 | 308.9241 | 1007.3333 | 379.9934 | 382.5058 | 384.9822 | 387.4587 | 389.9352 | 392.4116 | 394.8881 | 399.8052 | 402.2457 | 404.6863 | 407.1269 | 275.5 | 61.6 | 329.9998 | 1114 | 666 | 201.9774 | 386 | 152.6115 | 308.9241 | 1007.3333 | 609.8214 | 638.8081 | 667.7948 | 696.7815 | 725.7682 | 754.7549 | 783.7416 | 812.7283 | 841.715 | 870.7017 | 899.6883
Taranaki | 471.1538 | 216.8182 | 318.941 | 405.6667 | 506.375 | 355.1825 | 461.7692 | 347.1717 | 213.0709 | 355.0714 | 338.3681 | 341.0126 | 344.1688 | 346.7777 | 348.8534 | 351.4409 | 353.5024 | 356.0757 | 358.6277 | 361.1797 | 363.2057 | 471.1538 | 216.8182 | 318.941 | 405.6667 | 506.375 | 355.1825 | 461.7692 | 347.1717 | 213.0709 | 355.0714 | 334.6986 | 329.1671 | 323.6355 | 318.104 | 312.5724 | 307.0409 | 301.5094 | 295.9778 | 290.4463 | 284.9148 | 279.3832
Tararua | 111 | 25 | 174.9999 | 8 | 115 | 19.9978 | 0 | 3.3249 | 0 | 77.6667 | 85.5214 | 85.5214 | 85.5214 | 87.4957 | 87.4957 | 87.4957 | 87.4957 | 87.4957 | 89.4313 | 89.4313 | 89.4313 | 111 | 25 | 174.9999 | 8 | 115 | 19.9978 | 0 | 3.3249 | 0 | 77.6667 | 5.0863 | -3.7159 | -12.5182 | -21.3205 | -30.1228 | -38.9251 | -47.7274 | -56.5297 | -65.332 | -74.1342 | -82.9365
Tauranga | 446.7333 | 465.25 | 629.2997 | 226.6538 | 519.3125 | 375.5944 | 353.7368 | 378.8182 | 259.6367 | 831.0417 | 445.7745 | 450.5807 | 455.361 | 460.1068 | 464.2301 | 468.924 | 473.0041 | 477.6375 | 482.2363 | 486.2386 | 490.2236 | 446.7333 | 465.25 | 629.2997 | 226.6538 | 519.3125 | 375.5944 | 353.7368 | 378.8182 | 259.6367 | 831.0417 | 482.0946 | 488.1831 | 494.2716 | 500.3601 | 506.4486 | 512.5372 | 518.6257 | 524.7142 | 530.8027 | 536.8912 | 542.9798
Waikato | 237.75 | 164.1538 | 124.2856 | 707.1429 | 460.6 | 477.583 | 481.8 | 11.2214 | 629.979 | 782.6 | 428.8361 | 434.1293 | 439.4053 | 444.6296 | 448.5263 | 453.6988 | 457.5437 | 462.6473 | 466.4405 | 471.4751 | 475.2166 | 237.75 | 164.1538 | 124.2856 | 707.1429 | 460.6 | 477.583 | 481.8 | 11.2214 | 629.979 | 782.6 | 639.0469 | 681.1079 | 723.1688 | 765.2298 | 807.2907 | 849.3517 | 891.4127 | 933.4736 | 975.5346 | 1017.5956 | 1059.6565
Waikino | 641.5 | 720 | 532.1426 | 2707.25 | 303.1429 | 189.4788 | 671.8571 | 944.2627 | 398.2024 | 2879.2 | 991.3716 | 1008.4897 | 1019.7641 | 1030.9794 | 1042.0766 | 1053.1149 | 1064.0941 | 1075.0142 | 1085.8163 | 1091.1879 | 1101.931 | 641.5 | 720 | 532.1426 | 2707.25 | 303.1429 | 189.4788 | 671.8571 | 944.2627 | 398.2024 | 2879.2 | 1456.2861 | 1539.483 | 1622.6798 | 1705.8766 | 1789.0734 | 1872.2702 | 1955.467 | 2038.6639 | 2121.8607 | 2205.0575 | 2288.2543
Wairarapa | 94.2 | 135.5714 | 284.6665 | 356.9091 | 489.6 | 306.799 | 182.7 | 115.8163 | 209.6756 | 259.2857 | 262.4426 | 265.5105 | 268.5682 | 270.841 | 273.1037 | 276.1002 | 278.3323 | 280.5542 | 282.7659 | 284.9674 | 287.1588 | 94.2 | 135.5714 | 284.6665 | 356.9091 | 489.6 | 306.799 | 182.7 | 115.8163 | 209.6756 | 259.2857 | 258.6831 | 261.4396 | 264.1961 | 266.9525 | 269.709 | 272.4655 | 275.222 | 277.9785 | 280.735 | 283.4915 | 286.248
Whanganui | 96 | 279 | 628.3747 | 321.8571 | 256.2857 | 710.1206 | 141.8 | 433.272 | 514.286 | 276.8 | 410.6751 | 414.4913 | 418.2738 | 422.0563 | 424.5612 | 428.3101 | 430.7982 | 434.5135 | 438.1951 | 440.6328 | 443.0536 | 96 | 279 | 628.3747 | 321.8571 | 256.2857 | 710.1206 | 141.8 | 433.272 | 514.286 | 276.8 | 439.5247 | 452.9329 | 466.3411 | 479.7493 | 493.1574 | 506.5656 | 519.9738 | 533.382 | 546.7902 | 560.1984 | 573.6066
Vegetation
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 374.5329 | 299.8423 | 277.424 | 384.0631 | 396.6754 | 310.4333 | 226.9093 | 424.2258 | 225.4319 | 291.2555
[11 empty] | 325.7746 | 329.0015 | 332.0334 | 335.4117 | 338.3294 | 341.1575 | 343.8328 | 347.0945 | 350.0141 | 352.7527 | 355.317 | [10 empty] | 286.0333 | 280.0493 | 274.0652 | 268.0812 | 262.0972 | 256.1132 | 250.1292 | 244.1452 | 238.1612 | 232.1772 | 226.1932
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 746.8824 | 421.6667 | 505.4164 | 1147.8 | 493.5263 | 307.4656 | 355.1429 | 1266.684 | 283.1538 | 540.6111 | 645.662 | 653.5384 | 661.3645 | 669.1151 | 676.8154 | 684.4654 | 689.5234 | 697.0727 | 704.5717 | 712.0203 | 716.9525 | 746.8824 | 421.6667 | 505.4164 | 1147.8 | 493.5263 | 307.4656 | 355.1429 | 1266.684 | 283.1538 | 540.6111 | 554.0441 | 544.4457 | 534.8474 | 525.2491 | 515.6507 | 506.0524 | 496.4541 | 486.8557 | 477.2574 | 467.6591 | 458.0607
Egmont | 12.6667 | 83.2857 | 0 | 435.8824 | 289.9524 | 265.3037 | 190.5789 | 135.1034 | 234.8333 | 138.5294 | 231.6116 | 232.9986 | 234.3856 | 237.1595 | 238.5285 | 239.8974 | 241.2664 | 244.0043 | 245.3553 | 246.7062 | 248.0572 | 12.6667 | 83.2857 | 0 | 435.8824 | 289.9524 | 265.3037 | 190.5789 | 135.1034 | 234.8333 | 138.5294 | 248.8988 | 261.6779 | 274.457 | 287.2362 | 300.0153 | 312.7944 | 325.5735 | 338.3527 | 351.1318 | 363.9109 | 376.69
Kinleith | 272.6 | 547 | 311.9998 | 483 | 215.75 | 318.9644 | 134.6667 | 322.2703 | 104.3333 | 128.5 | 261.2817 | 261.2817 | 261.2817 | 264.191 | 267.0622 | 267.0622 | 269.895 | 272.7278 | 272.7278 | 275.5224 | 278.3169 | 272.6 | 547 | 311.9998 | 483 | 215.75 | 318.9644 | 134.6667 | 322.2703 | 104.3333 | 128.5 | 107.7084 | 75.6721 | 43.6357 | 11.5994 | -20.437 | -52.4734 | -84.5097 | -116.5461 | -148.5825 | -180.6188 | -212.6552
Manawatu | 407.1111 | 401.9091 | 671.3681 | 536.4 | 500.6667 | 383.2572 | 483.5 | 356.9029 | 471.1538 | 365.95 | 474.0553 | 478.6585 | 482.5811 | 485.832 | 489.065 | 492.2891 | 495.4952 | 499.3372 | 502.5165 | 505.6868 | 508.8392 | 407.1111 | 401.9091 | 671.3681 | 536.4 | 500.6667 | 383.2572 | 483.5 | 356.9029 | 471.1538 | 365.95 | 400.0162 | 389.506 | 378.9959 | 368.4858 | 357.9756 | 347.4655 | 336.9554 | 326.4452 | 315.9351 | 305.425 | 294.9148
Mt Maunganui | 592.2857 | 410.3333 | 99.4999 | 197.375 | 249 | 379.0826 | 104.75 | 730.3232 | 201.0909 | 211.1364 | 307.2422 | 310.7407 | 314.2209 | 316.9829 | 320.4169 | 323.1513 | 326.5486 | 329.2462 | 332.5974 | 335.2673 | 337.9188 | 592.2857 | 410.3333 | 99.4999 | 197.375 | 249 | 379.0826 | 104.75 | 730.3232 | 201.0909 | 211.1364 | 254.5305 | 243.0837 | 231.6369 | 220.1901 | 208.7434 | 197.2966 | 185.8498 | 174.4031 | 162.9563 | 151.5095 | 140.0627
Rangitikei | 228.4615 | 61.25 | 178.4285 | 184.7667 | 255.7941 | 333.1166 | 171.2692 | 184.633 | 223.1429 | 121.1 | 198.9432 | 200.2585 | 201.5551 | 202.8516 | 204.1482 | 205.4447 | 206.7412 | 209.3155 | 210.5933 | 211.871 | 213.1488 | 228.4615 | 61.25 | 178.4285 | 184.7667 | 255.7941 | 333.1166 | 171.2692 | 184.633 | 223.1429 | 121.1 | 202.0246 | 203.4479 | 204.8712 | 206.2945 | 207.7179 | 209.1412 | 210.5645 | 211.9878 | 213.4112 | 214.8345 | 216.2578
Taranaki | 306.3889 | 324.15 | 245.3332 | 326.5185 | 335.1864 | 340.1725 | 323.0938 | 326.9986 | 144.36 | 255.119 | 299.5566 | 301.8977 | 304.6919 | 307.0016 | 308.8392 | 311.1299 | 312.955 | 315.2332 | 317.4924 | 319.7517 | 321.5453 | 306.3889 | 324.15 | 245.3332 | 326.5185 | 335.1864 | 340.1725 | 323.0938 | 326.9986 | 144.36 | 255.119 | 248.8348 | 240.8534 | 232.8721 | 224.8908 | 216.9094 | 208.9281 | 200.9468 | 192.9654 | 184.9841 | 177.0028 | 169.0214
Tararua | 381.3333 | 101.6667 | 87.5454 | 67.1 | 115.7 | 77.2136 | 118.9286 | 124.4287 | 62.1333 | 181.9167 | 108.1838 | 108.1838 | 108.1838 | 110.6813 | 110.6813 | 110.6813 | 110.6813 | 110.6813 | 113.1298 | 113.1298 | 113.1298 | 381.3333 | 101.6667 | 87.5454 | 67.1 | 115.7 | 77.2136 | 118.9286 | 124.4287 | 62.1333 | 181.9167 | 72.7944 | 62.0667 | 51.339 | 40.6113 | 29.8836 | 19.156 | 8.4283 | -2.2994 | -13.0271 | -23.7548 | -34.4825
Tauranga | 506.6667 | 713.3889 | 275.9999 | 265.0769 | 1088.7241 | 450.1497 | 292.7391 | 629.7128 | 427.5455 | 351.28 | 567.1467 | 573.2616 | 579.3435 | 585.3813 | 590.6273 | 596.5992 | 601.7903 | 607.6851 | 613.5361 | 618.6281 | 623.6981 | 506.6667 | 713.3889 | 275.9999 | 265.0769 | 1088.7241 | 450.1497 | 292.7391 | 629.7128 | 427.5455 | 351.28 | 427.2481 | 413.9972 | 400.7462 | 387.4953 | 374.2443 | 360.9934 | 347.7424 | 334.4915 | 321.2405 | 307.9896 | 294.7386
Waikato | 316.35 | 351.8333 | 198.3528 | 261 | 322.1852 | 373.9582 | 169.5714 | 312.1501 | 163.2143 | 383.9167 | 284.0486 | 287.5547 | 291.0493 | 294.5097 | 297.0908 | 300.5169 | 303.0637 | 306.4442 | 308.9567 | 312.2914 | 314.7697 | 316.35 | 351.8333 | 198.3528 | 261 | 322.1852 | 373.9582 | 169.5714 | 312.1501 | 163.2143 | 383.9167 | 273.0612 | 270.8445 | 268.6278 | 266.411 | 264.1943 | 261.9776 | 259.7609 | 257.5441 | 255.3274 | 253.1107 | 250.894
Waikino | 710 | 162.25 | 463.2498 | 638.3333 | 751.3333 | 260.7042 | 81.7 | 612.8113 | 103.8889 | 550.5556 | 334.5865 | 340.3638 | 344.1689 | 347.954 | 351.6993 | 355.4247 | 359.1302 | 362.8157 | 366.4614 | 368.2743 | 371.9001 | 710 | 162.25 | 463.2498 | 638.3333 | 751.3333 | 260.7042 | 81.7 | 612.8113 | 103.8889 | 550.5556 | 324.941 | 305.2061 | 285.4713 | 265.7365 | 246.0016 | 226.2668 | 206.5319 | 186.7971 | 167.0622 | 147.3274 | 127.5925
Wairarapa | 84.931 | 109.2162 | 204.8946 | 164.7258 | 168.9615 | 105.5882 | 280.1414 | 225.1214 | 157.8824 | 207.3276 | 196.977 | 199.2796 | 201.5745 | 203.2804 | 204.9786 | 207.2277 | 208.903 | 210.5706 | 212.2306 | 213.883 | 215.5277 | 84.931 | 109.2162 | 204.8946 | 164.7258 | 168.9615 | 105.5882 | 280.1414 | 225.1214 | 157.8824 | 207.3276 | 231.7537 | 242.8218 | 253.8899 | 264.958 | 276.0261 | 287.0942 | 298.1624 | 309.2305 | 320.2986 | 331.3667 | 342.4348
Whanganui | 303.25 | 210 | 87 | 284.8421 | 370 | 440.6566 | 243.7391 | 287.7962 | 353.8824 | 350.3793 | 309.3316 | 312.206 | 315.0552 | 317.9043 | 319.791 | 322.6148 | 324.4889 | 327.2873 | 330.0604 | 331.8965 | 333.72 | 303.25 | 210 | 87 | 284.8421 | 370 | 440.6566 | 243.7391 | 287.7962 | 353.8824 | 350.3793 | 372.5769 | 387.0173 | 401.4577 | 415.8981 | 430.3386 | 444.779 | 459.2194 | 473.6598 | 488.1002 | 502.5407 | 516.9811
Adverse Weather
| History | [9 empty] | Forecast | Regional growth rates applied to 2010 to 2017 average | [9 empty] | Linear trend
Total | 390.0725 | 403.564 | 428.3946 | 454.5643 | 423.1991 | 210.5186 | 333.2577 | 200.2072 | 99.1375 | 292.7451
[11 empty] | 301.8656 | 305.0181 | 307.8828 | 311.1318 | 313.8794 | 316.5968 | 319.0964 | 322.1781 | 325.0251 | 327.4956 | 329.9072 | [10 empty] | 170.2495 | 144.1293 | 118.009 | 91.8887 | 65.7684 | 39.6482 | 13.5279 | -12.5924 | -38.7126 | -64.8329 | -90.9532
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 873.1395 | 1311.2414 | 568.333 | 817.6875 | 1381 | 128.9856 | 886.2105 | 524.5828 | 103.0588 | 848 | 668.2227 | 676.3744 | 684.4739 | 692.4954 | 700.4647 | 708.382 | 713.6168 | 721.4298 | 729.1908 | 736.8998 | 742.0043 | 873.1395 | 1311.2414 | 568.333 | 817.6875 | 1381 | 128.9856 | 886.2105 | 524.5828 | 103.0588 | 848 | 412.5996 | 352.3043 | 292.0089 | 231.7136 | 171.4183 | 111.1229 | 50.8276 | -9.4677 | -69.7631 | -130.0584 | -190.3537
Egmont | 276.375 | 243.9688 | 302.6921 | 405.3529 | 533.1923 | 404.7729 | 100.6429 | 74.2923 | 83.5 | 106.5217 | 254.4581 | 255.9818 | 257.5056 | 260.5532 | 262.0572 | 263.5612 | 265.0652 | 268.0732 | 269.5574 | 271.0416 | 272.5258 | 276.375 | 243.9688 | 302.6921 | 405.3529 | 533.1923 | 404.7729 | 100.6429 | 74.2923 | 83.5 | 106.5217 | 91.9141 | 62.6019 | 33.2898 | 3.9776 | -25.3346 | -54.6468 | -83.959 | -113.2711 | -142.5833 | -171.8955 | -201.2077
Kinleith | 362.3333 | 0 | 419.6664 | 770.6667 | 0 | 119.32 | 67.75 | 45.2167 | 5.5 | 2.5 | 181.0237 | 181.0237 | 181.0237 | 183.0394 | 185.0286 | 185.0286 | 186.9913 | 188.954 | 188.954 | 190.8901 | 192.8262 | 362.3333 | 0 | 419.6664 | 770.6667 | 0 | 119.32 | 67.75 | 45.2167 | 5.5 | 2.5 | -56.094 | -98.892 | -141.6901 | -184.4881 | -227.2862 | -270.0842 | -312.8823 | -355.6803 | -398.4784 | -441.2764 | -484.0745
Manawatu | 324.15 | 477 | 404.4704 | 344.1429 | 487.9 | 104.2883 | 348.28 | 261.1358 | 136.75 | 232.8511 | 293.5386 | 296.3889 | 298.8178 | 300.8308 | 302.8327 | 304.8291 | 306.8144 | 309.1934 | 311.162 | 313.1251 | 315.0771 | 324.15 | 477 | 404.4704 | 344.1429 | 487.9 | 104.2883 | 348.28 | 261.1358 | 136.75 | 232.8511 | 169.0531 | 143.0451 | 117.0371 | 91.0292 | 65.0212 | 39.0133 | 13.0053 | -13.0027 | -39.0106 | -65.0186 | -91.0266
Mt Maunganui | 923.7143 | 333.3333 | 482.7997 | 284.3333 | 218.25 | 112.3874 | 70.8571 | 170.2589 | 55.4 | 157.7143 | 196.3827 | 198.6189 | 200.8433 | 202.6087 | 204.8037 | 206.5515 | 208.7229 | 210.4471 | 212.5892 | 214.2957 | 215.9905 | 923.7143 | 333.3333 | 482.7997 | 284.3333 | 218.25 | 112.3874 | 70.8571 | 170.2589 | 55.4 | 157.7143 | -90.7128 | -158.2796 | -225.8464 | -293.4133 | -360.9801 | -428.547 | -496.1138 | -563.6806 | -631.2475 | -698.8143 | -766.3812
Rangitikei | 163.25 | 161.7619 | 370.0398 | 321.3182 | 331.2308 | 309.394 | 181.5652 | 70.7944 | 15 | 59.7 | 209.9272 | 211.3151 | 212.6833 | 214.0514 | 215.4195 | 216.7876 | 218.1558 | 220.8722 | 222.2205 | 223.5688 | 224.9171 | 163.25 | 161.7619 | 370.0398 | 321.3182 | 331.2308 | 309.394 | 181.5652 | 70.7944 | 15 | 59.7 | 68.5186 | 44.9028 | 21.287 | -2.3288 | -25.9446 | -49.5604 | -73.1762 | -96.792 | -120.4078 | -144.0236 | -167.6394
Taranaki | 485.2941 | 331.4894 | 365.818 | 286.8214 | 342.0192 | 168.5569 | 106.9 | 107.1483 | 35.0857 | 111.1102 | 192.7712 | 194.2778 | 196.0759 | 197.5622 | 198.7448 | 200.2189 | 201.3934 | 202.8594 | 204.3133 | 205.7672 | 206.9214 | 485.2941 | 331.4894 | 365.818 | 286.8214 | 342.0192 | 168.5569 | 106.9 | 107.1483 | 35.0857 | 111.1102 | -14.2775 | -59.4233 | -104.5691 | -149.7149 | -194.8607 | -240.0065 | -285.1523 | -330.2981 | -375.4438 | -420.5896 | -465.7354
Tararua | 77.0625 | 172.8889 | 91.125 | 152.0556 | 132.3182 | 104.0509 | 263.3 | 114.7088 | 60.4286 | 95.6111 | 128.2558 | 128.2558 | 128.2558 | 131.2166 | 131.2166 | 131.2166 | 131.2166 | 131.2166 | 134.1194 | 134.1194 | 134.1194 | 77.0625 | 172.8889 | 91.125 | 152.0556 | 132.3182 | 104.0509 | 263.3 | 114.7088 | 60.4286 | 95.6111 | 119.7916 | 118.5983 | 117.405 | 116.2116 | 115.0183 | 113.825 | 112.6317 | 111.4383 | 110.245 | 109.0517 | 107.8583
Tauranga | 402.8824 | 448.5882 | 1344.5993 | 507.1667 | 838.7778 | 59.66 | 766.4667 | 276.1207 | 409 | 184.125 | 554.9726 | 560.9562 | 566.9075 | 572.8158 | 577.9492 | 583.7929 | 588.8725 | 594.6408 | 600.3661 | 605.3489 | 610.3101 | 402.8824 | 448.5882 | 1344.5993 | 507.1667 | 838.7778 | 59.66 | 766.4667 | 276.1207 | 409 | 184.125 | 270.7538 | 224.7566 | 178.7594 | 132.7621 | 86.7649 | 40.7676 | -5.2296 | -51.2268 | -97.2241 | -143.2213 | -189.2186
Waikato | 325.375 | 334.3056 | 239.1665 | 251.5882 | 219.9091 | 177.8801 | 429.6923 | 201.8765 | 47.9167 | 227.3333 | 227.1765 | 229.9806 | 232.7756 | 235.5431 | 237.6074 | 240.3476 | 242.3844 | 245.0881 | 247.0975 | 249.7646 | 251.7467 | 325.375 | 334.3056 | 239.1665 | 251.5882 | 219.9091 | 177.8801 | 429.6923 | 201.8765 | 47.9167 | 227.3333 | 159.4622 | 143.8182 | 128.1741 | 112.5301 | 96.8861 | 81.2421 | 65.598 | 49.954 | 34.31 | 18.666 | 3.0219
Waikino | 267.5385 | 749.5556 | 0 | 1070.8571 | 50.5 | 708.7208 | 282.3333 | 545.5181 | 93.2857 | 1528 | 541.4712 | 550.8208 | 556.9786 | 563.1043 | 569.1654 | 575.1943 | 581.191 | 587.1554 | 593.0553 | 595.9892 | 601.8569 | 267.5385 | 749.5556 | 0 | 1070.8571 | 50.5 | 708.7208 | 282.3333 | 545.5181 | 93.2857 | 1528 | 788.6477 | 835.7417 | 882.8357 | 929.9296 | 977.0236 | 1024.1176 | 1071.2115 | 1118.3055 | 1165.3995 | 1212.4935 | 1259.5874
Wairarapa | 182.3902 | 122.4688 | 188.8999 | 199.7619 | 238.7619 | 82.2985 | 381.7273 | 109.9981 | 69.3125 | 105.8261 | 174.1866 | 176.2227 | 178.2521 | 179.7607 | 181.2624 | 183.2513 | 184.7327 | 186.2074 | 187.6754 | 189.1365 | 190.591 | 182.3902 | 122.4688 | 188.8999 | 199.7619 | 238.7619 | 82.2985 | 381.7273 | 109.9981 | 69.3125 | 105.8261 | 132.6029 | 126.1408 | 119.6787 | 113.2166 | 106.7545 | 100.2924 | 93.8303 | 87.3682 | 80.9061 | 74.444 | 67.9819
Whanganui | 407.4375 | 156.1667 | 363.1248 | 497.5833 | 304.5294 | 256.4259 | 446.625 | 101.0415 | 174.55 | 146.3939 | 289.8002 | 292.4931 | 295.1623 | 297.8315 | 299.5991 | 302.2446 | 304.0004 | 306.6221 | 309.2202 | 310.9403 | 312.6486 | 407.4375 | 156.1667 | 363.1248 | 497.5833 | 304.5294 | 256.4259 | 446.625 | 101.0415 | 174.55 | 146.3939 | 160.9843 | 138.3655 | 115.7467 | 93.1279 | 70.5091 | 47.8903 | 25.2715 | 2.6527 | -19.9661 | -42.5849 | -65.2038
Unknown
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 521.9054 | 698.8743 | 564.1356 | 416.7882 | 501.7682 | 405.6566 | 460.4706 | 482.0747 | 420.074 | 531.5383
[11 empty] | 498.5902 | 503.266 | 507.613 | 512.977 | 517.4118 | 521.4822 | 525.5859 | 530.5315 | 534.994 | 539.0831 | 543.0188 | [10 empty] | 425.6527 | 412.0753 | 398.4979 | 384.9204 | 371.343 | 357.7656 | 344.1881 | 330.6107 | 317.0333 | 303.4559 | 289.8784
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 1175.4118 | 563.0526 | 1078.4342 | 556 | 969.5294 | 690.769 | 535.2308 | 1502.4536 | 343.7727 | 945.2305 | 867.3092 | 877.8895 | 888.4022 | 898.8135 | 909.1572 | 919.4333 | 926.2277 | 936.3686 | 946.4419 | 956.4475 | 963.0729 | 1175.4118 | 563.0526 | 1078.4342 | 556 | 969.5294 | 690.769 | 535.2308 | 1502.4536 | 343.7727 | 945.2305 | 775.0697 | 763.9936 | 752.9175 | 741.8413 | 730.7652 | 719.6891 | 708.6129 | 697.5368 | 686.4607 | 675.3846 | 664.3084
Egmont | 258.375 | 633.25 | 391.1665 | 546.4737 | 738.2 | 337.8259 | 391 | 211.129 | 166.7576 | 402.1058 | 388.3002 | 390.6254 | 392.9507 | 397.6013 | 399.8964 | 402.1914 | 404.4865 | 409.0767 | 411.3416 | 413.6065 | 415.8713 | 258.375 | 633.25 | 391.1665 | 546.4737 | 738.2 | 337.8259 | 391 | 211.129 | 166.7576 | 402.1058 | 282.9999 | 260.3402 | 237.6805 | 215.0208 | 192.3611 | 169.7013 | 147.0416 | 124.3819 | 101.7222 | 79.0625 | 56.4028
Kinleith | 930.5 | 535.6 | 344.9998 | 386.5 | 484 | 852.4047 | 403.8571 | 804.3011 | 235.8 | 918.3395 | 616.6861 | 616.6861 | 616.6861 | 623.5529 | 630.3294 | 630.3294 | 637.0156 | 643.7017 | 643.7017 | 650.2975 | 656.8933 | 930.5 | 535.6 | 344.9998 | 386.5 | 484 | 852.4047 | 403.8571 | 804.3011 | 235.8 | 918.3395 | 606.5948 | 609.6793 | 612.7638 | 615.8483 | 618.9327 | 622.0172 | 625.1017 | 628.1861 | 631.2706 | 634.3551 | 637.4396
Manawatu | 391.4516 | 527.6 | 566.4032 | 437.0517 | 506.6957 | 631.1034 | 515.42 | 608.8689 | 283.6182 | 355.6795 | 484.2517 | 488.9539 | 492.9609 | 496.2817 | 499.5843 | 502.8777 | 506.1528 | 510.0774 | 513.3251 | 516.5636 | 519.7838 | 391.4516 | 527.6 | 566.4032 | 437.0517 | 506.6957 | 631.1034 | 515.42 | 608.8689 | 283.6182 | 355.6795 | 433.7898 | 424.9536 | 416.1173 | 407.2811 | 398.4448 | 389.6086 | 380.7723 | 371.9361 | 363.0998 | 354.2636 | 345.4274
Mt Maunganui | 644.8571 | 1439.1429 | 321.3748 | 138.2222 | 470.4 | 262.0957 | 221.6667 | 212.403 | 652.6296 | 319.8247 | 468.3048 | 473.6374 | 478.9418 | 483.1517 | 488.386 | 492.5539 | 497.732 | 501.8437 | 506.9517 | 511.0213 | 515.0628 | 644.8571 | 1439.1429 | 321.3748 | 138.2222 | 470.4 | 262.0957 | 221.6667 | 212.403 | 652.6296 | 319.8247 | 170.4712 | 116.3275 | 62.1838 | 8.04 | -46.1037 | -100.2474 | -154.3911 | -208.5349 | -262.6786 | -316.8223 | -370.966
Rangitikei | 295.6 | 320.8889 | 535.5622 | 327.5556 | 329.1957 | 186.7791 | 492 | 262.336 | 393.9804 | 258.1994 | 338.4763 | 340.7141 | 342.92 | 345.1259 | 347.3318 | 349.5377 | 351.7436 | 356.1234 | 358.2974 | 360.4713 | 362.6452 | 295.6 | 320.8889 | 535.5622 | 327.5556 | 329.1957 | 186.7791 | 492 | 262.336 | 393.9804 | 258.1994 | 312.2037 | 307.1118 | 302.0198 | 296.9278 | 291.8358 | 286.7438 | 281.6518 | 276.5598 | 271.4678 | 266.3758 | 261.2838
Taranaki | 521.7955 | 498.6296 | 474.5363 | 349.8214 | 302.0625 | 348.205 | 757.6863 | 442.9969 | 402.0533 | 424.3685 | 440.054 | 443.4931 | 447.5978 | 450.9907 | 453.6902 | 457.0553 | 459.7364 | 463.083 | 466.402 | 469.7209 | 472.3557 | 521.7955 | 498.6296 | 474.5363 | 349.8214 | 302.0625 | 348.205 | 757.6863 | 442.9969 | 402.0533 | 424.3685 | 437.521 | 434.8493 | 432.1775 | 429.5058 | 426.8341 | 424.1623 | 421.4906 | 418.8188 | 416.1471 | 413.4754 | 410.8036
Tararua | 197.8333 | 179.619 | 450.0831 | 227.4706 | 191.3235 | 103.8707 | 391.3333 | 534.4533 | 314.8723 | 216.7452 | 285.5549 | 285.5549 | 285.5549 | 292.147 | 292.147 | 292.147 | 292.147 | 292.147 | 298.61 | 298.61 | 298.61 | 197.8333 | 179.619 | 450.0831 | 227.4706 | 191.3235 | 103.8707 | 391.3333 | 534.4533 | 314.8723 | 216.7452 | 345.526 | 357.3016 | 369.0771 | 380.8527 | 392.6282 | 404.4038 | 416.1793 | 427.9549 | 439.7304 | 451.506 | 463.2815
Tauranga | 1077.2581 | 932.9667 | 1400.1659 | 692.7907 | 883.3333 | 796.4972 | 640.04 | 306.4215 | 512.0732 | 1134.0908 | 817.1031 | 825.9129 | 834.6752 | 843.3741 | 850.9322 | 859.536 | 867.0149 | 875.5078 | 883.9374 | 891.2736 | 898.5782 | 1077.2581 | 932.9667 | 1400.1659 | 692.7907 | 883.3333 | 796.4972 | 640.04 | 306.4215 | 512.0732 | 1134.0908 | 565.9447 | 516.5595 | 467.1742 | 417.7889 | 368.4036 | 319.0184 | 269.6331 | 220.2478 | 170.8625 | 121.4773 | 72.092
Waikato | 329.6 | 303.75 | 388.2748 | 285.9375 | 426.9 | 233.3652 | 183.8235 | 361.4633 | 619.359 | 316.8706 | 365.4834 | 369.9946 | 374.4912 | 378.9437 | 382.2647 | 386.6731 | 389.95 | 394.2996 | 397.5324 | 401.8233 | 405.012 | 329.6 | 303.75 | 388.2748 | 285.9375 | 426.9 | 233.3652 | 183.8235 | 361.4633 | 619.359 | 316.8706 | 393.6265 | 402.4796 | 411.3328 | 420.1859 | 429.039 | 437.8921 | 446.7452 | 455.5983 | 464.4514 | 473.3046 | 482.1577
Waikino | 541.5714 | 2444.3333 | 505.8997 | 509.7778 | 363.4286 | 132.3185 | 333.5 | 199.4816 | 488.7 | 700.0188 | 630.4091 | 641.2944 | 648.4637 | 655.5955 | 662.6522 | 669.6713 | 676.653 | 683.597 | 690.4661 | 693.8818 | 700.7133 | 541.5714 | 2444.3333 | 505.8997 | 509.7778 | 363.4286 | 132.3185 | 333.5 | 199.4816 | 488.7 | 700.0188 | 136.7216 | 48.5068 | -39.708 | -127.9228 | -216.1376 | -304.3524 | -392.5672 | -480.782 | -568.9968 | -657.2115 | -745.4263
Wairarapa | 297.9167 | 288.3448 | 304.3332 | 366.6957 | 369.561 | 201.4537 | 296.8929 | 160.6313 | 306.6406 | 262.0092 | 281.1493 | 284.4358 | 287.7114 | 290.1463 | 292.5702 | 295.7803 | 298.1715 | 300.5518 | 302.9212 | 305.2796 | 307.6271 | 297.9167 | 288.3448 | 304.3332 | 366.6957 | 369.561 | 201.4537 | 296.8929 | 160.6313 | 306.6406 | 262.0092 | 242.4105 | 234.5855 | 226.7606 | 218.9356 | 211.1106 | 203.2856 | 195.4606 | 187.6357 | 179.8107 | 171.9857 | 164.1607
Whanganui | 122.6 | 418.1875 | 572.5291 | 593.95 | 488.3571 | 496.8477 | 823.6667 | 660.0313 | 740.7045 | 656.5149 | 634.4383 | 640.3337 | 646.1772 | 652.0207 | 655.8904 | 661.682 | 665.5257 | 671.2654 | 676.953 | 680.7189 | 684.4587 | 122.6 | 418.1875 | 572.5291 | 593.95 | 488.3571 | 496.8477 | 823.6667 | 660.0313 | 740.7045 | 656.5149 | 830.6057 | 880.2906 | 929.9755 | 979.6604 | 1029.3452 | 1079.0301 | 1128.715 | 1178.3999 | 1228.0848 | 1277.7696 | 1327.4545
The remainder
| History | [9 empty] | Forecast | Regional growth rates applied to 2009 to 2017 weighted average | [9 empty] | Linear trend
Total | 609.3597 | 438.5831 | 545.4592 | 499.0828 | 563.5614 | 379.0612 | 509.6963 | 341.1485 | 430.3017 | 522.1542
[11 empty] | 462.9072 | 467.0298 | 470.8551 | 475.7239 | 479.8502 | 483.4185 | 487.2359 | 491.8073 | 495.645 | 499.4888 | 503.1813 | [10 empty] | 416.6064 | 404.382 | 392.1575 | 379.9331 | 367.7086 | 355.4842 | 343.2598 | 331.0353 | 318.8109 | 306.5864 | 294.362
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 915.3214 | 474.625 | 1826.499 | 1336.0411 | 1315.6111 | 280.5686 | 318.8889 | 224.135 | 456.9412 | 1112.2857 | 807.4482 | 817.2983 | 827.0854 | 836.7781 | 846.4079 | 855.9747 | 862.3002 | 871.7411 | 881.1192 | 890.4343 | 896.6023 | 915.3214 | 474.625 | 1826.499 | 1336.0411 | 1315.6111 | 280.5686 | 318.8889 | 224.135 | 456.9412 | 1112.2857 | 477.7775 | 414.4476 | 351.1177 | 287.7879 | 224.458 | 161.1281 | 97.7983 | 34.4684 | -28.8614 | -92.1913 | -155.5212
Egmont | 244.6 | 343.5294 | 562.333 | 200.2524 | 271.6364 | 423.3056 | 307.4 | 187.4612 | 265.9583 | 218.6905 | 303.9444 | 305.7646 | 307.5847 | 311.2249 | 313.0214 | 314.8179 | 316.6144 | 320.2074 | 321.9802 | 323.7531 | 325.5259 | 244.6 | 343.5294 | 562.333 | 200.2524 | 271.6364 | 423.3056 | 307.4 | 187.4612 | 265.9583 | 218.6905 | 229.9357 | 216.7391 | 203.5426 | 190.346 | 177.1495 | 163.9529 | 150.7564 | 137.5598 | 124.3633 | 111.1667 | 97.9702
Kinleith | 1166 | 156 | 179.4999 | 796.9088 | 142.3333 | 626.9299 | 960 | 855.6894 | 433 | 2624.25 | 818.5452 | 818.5452 | 818.5452 | 827.6597 | 836.6544 | 836.6544 | 845.5291 | 854.4038 | 854.4038 | 863.1586 | 871.9134 | 1166 | 156 | 179.4999 | 796.9088 | 142.3333 | 626.9299 | 960 | 855.6894 | 433 | 2624.25 | 1441.3301 | 1559.0153 | 1676.7006 | 1794.3858 | 1912.0711 | 2029.7564 | 2147.4416 | 2265.1269 | 2382.8121 | 2500.4974 | 2618.1827
Manawatu | 989.2 | 1016.4878 | 769.9996 | 775.2223 | 516.2632 | 424.125 | 579.95 | 823.8728 | 421 | 649.0698 | 699.1092 | 705.8978 | 711.6826 | 716.4769 | 721.2447 | 725.9994 | 730.7276 | 736.3936 | 741.0822 | 745.7576 | 750.4066 | 989.2 | 1016.4878 | 769.9996 | 775.2223 | 516.2632 | 424.125 | 579.95 | 823.8728 | 421 | 649.0698 | 441.9132 | 395.6212 | 349.3292 | 303.0373 | 256.7453 | 210.4533 | 164.1614 | 117.8694 | 71.5774 | 25.2854 | -21.0065
Mt Maunganui | 843.5 | 256.95 | 481.0524 | 205.1391 | 392.2857 | 271.803 | 338.3 | 226.3466 | 159.8571 | 111.3478 | 278.2571 | 281.4256 | 284.5774 | 287.0788 | 290.1889 | 292.6653 | 295.7421 | 298.1852 | 301.2203 | 303.6383 | 306.0397 | 843.5 | 256.95 | 481.0524 | 205.1391 | 392.2857 | 271.803 | 338.3 | 226.3466 | 159.8571 | 111.3478 | 53.2066 | 3.1244 | -46.9577 | -97.0398 | -147.1219 | -197.204 | -247.2861 | -297.3682 | -347.4503 | -397.5324 | -447.6146
Rangitikei | 339.1667 | 259.1818 | 267.9165 | 265.5224 | 505.7778 | 163.3502 | 574.8 | 156.72 | 272.1875 | 107.4595 | 252.6915 | 254.3622 | 256.0091 | 257.6559 | 259.3027 | 260.9495 | 262.5964 | 265.8661 | 267.4891 | 269.1121 | 270.735 | 339.1667 | 259.1818 | 267.9165 | 265.5224 | 505.7778 | 163.3502 | 574.8 | 156.72 | 272.1875 | 107.4595 | 225.7115 | 213.803 | 201.8945 | 189.986 | 178.0775 | 166.169 | 154.2605 | 142.352 | 130.4435 | 118.535 | 106.6265
Taranaki | 668.8571 | 461.4792 | 437.2185 | 310.9187 | 587.0227 | 457.2098 | 617.4286 | 371.8853 | 407.3774 | 346.25 | 448.8826 | 452.3907 | 456.5778 | 460.0387 | 462.7924 | 466.225 | 468.9598 | 472.3736 | 475.7592 | 479.1447 | 481.8323 | 668.8571 | 461.4792 | 437.2185 | 310.9187 | 587.0227 | 457.2098 | 617.4286 | 371.8853 | 407.3774 | 346.25 | 372.5938 | 355.5082 | 338.4226 | 321.337 | 304.2514 | 287.1658 | 270.0802 | 252.9945 | 235.9089 | 218.8233 | 201.7377
Tararua | 154.5 | 562 | 101.1666 | 128.1479 | 787.25 | 108.845 | 170 | 102.06 | 305.8462 | 197.8667 | 215.2445 | 215.2445 | 215.2445 | 220.2135 | 220.2135 | 220.2135 | 220.2135 | 220.2135 | 225.0851 | 225.0851 | 225.0851 | 154.5 | 562 | 101.1666 | 128.1479 | 787.25 | 108.845 | 170 | 102.06 | 305.8462 | 197.8667 | 196.7296 | 184.9044 | 173.0792 | 161.254 | 149.4288 | 137.6036 | 125.7784 | 113.9532 | 102.128 | 90.3028 | 78.4776
Tauranga | 657.5581 | 693.6949 | 524.0569 | 851.8433 | 1136.5357 | 408.4408 | 596.9333 | 412.4269 | 919.3333 | 349.225 | 700.3294 | 707.8802 | 715.3903 | 722.846 | 729.3239 | 736.6982 | 743.1082 | 750.3874 | 757.6123 | 763.9001 | 770.1607 | 657.5581 | 693.6949 | 524.0569 | 851.8433 | 1136.5357 | 408.4408 | 596.9333 | 412.4269 | 919.3333 | 349.225 | 546.788 | 527.1123 | 507.4365 | 487.7607 | 468.0849 | 448.4092 | 428.7334 | 409.0576 | 389.3818 | 369.706 | 350.0303
Waikato | 359.7209 | 210.4182 | 235.238 | 214.9633 | 356.2903 | 180.1941 | 351.625 | 158.5749 | 233.6667 | 212.5714 | 238.966 | 241.9156 | 244.8556 | 247.7668 | 249.9382 | 252.8206 | 254.9631 | 257.8071 | 259.9208 | 262.7263 | 264.8112 | 359.7209 | 210.4182 | 235.238 | 214.9633 | 356.2903 | 180.1941 | 351.625 | 158.5749 | 233.6667 | 212.5714 | 207.6252 | 199.6795 | 191.7339 | 183.7882 | 175.8426 | 167.8969 | 159.9513 | 152.0056 | 144.06 | 136.1143 | 128.1687
Waikino | 320.3077 | 470.5714 | 650.9441 | 486.2784 | 394.3 | 555.861 | 990.125 | 124.1407 | 913.6429 | 262.2105 | 522.1776 | 531.194 | 537.1325 | 543.0398 | 548.885 | 554.6991 | 560.4821 | 566.234 | 571.9237 | 574.753 | 580.4116 | 320.3077 | 470.5714 | 650.9441 | 486.2784 | 394.3 | 555.861 | 990.125 | 124.1407 | 913.6429 | 262.2105 | 570.7618 | 580.5661 | 590.3704 | 600.1747 | 609.979 | 619.7833 | 629.5876 | 639.3919 | 649.1962 | 659.0005 | 668.8048
Wairarapa | 207 | 393.3571 | 249.2856 | 409.9154 | 463.8889 | 343.9616 | 252.7917 | 108.3454 | 101.3256 | 182.6491 | 269.2905 | 272.4385 | 275.5759 | 277.9081 | 280.2298 | 283.3045 | 285.5948 | 287.8747 | 290.1441 | 292.4031 | 294.6516 | 207 | 393.3571 | 249.2856 | 409.9154 | 463.8889 | 343.9616 | 252.7917 | 108.3454 | 101.3256 | 182.6491 | 152.6061 | 131.0341 | 109.4621 | 87.8901 | 66.3181 | 44.7462 | 23.1742 | 1.6022 | -19.9698 | -41.5418 | -63.1138
Whanganui | 1055.9444 | 403.2857 | 805.7596 | 506.9228 | 457.1034 | 683.2014 | 567.8095 | 683.2722 | 703.7857 | 414.129 | 577.936 | 583.3064 | 588.6295 | 593.9526 | 597.4777 | 602.7535 | 606.2549 | 611.4833 | 616.6645 | 620.0949 | 623.5017 | 1055.9444 | 403.2857 | 805.7596 | 506.9228 | 457.1034 | 683.2014 | 567.8095 | 683.2722 | 703.7857 | 414.129 | 498.9041 | 475.4101 | 451.916 | 428.422 | 404.928 | 381.4339 | 357.9399 | 334.4458 | 310.9518 | 287.4577 | 263.9637
Totals
Linear trend
Total | 420.9368 | 386.9526 | 406.8882 | 379.1454 | 348.5969 | 302.7414 | 328.788 | 274.0664 | 249.1355 | 286.8709
[32 empty] | 237.3339 | 218.956 | 200.5782 | 182.2003 | 163.8224 | 145.4445 | 127.0667 | 108.6888 | 90.3109 | 71.9331 | 53.5552
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | [11 empty] | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 832.351 | 747.9448 | 1053.5208 | 616.9788 | 724.0101 | 504.9719 | 334.932 | 611.62 | 213.974 | 440.5693 | [11 empty] | 832.351 | 747.9448 | 1053.5208 | 616.9788 | 724.0101 | 504.9719 | 334.932 | 611.62 | 213.974 | 440.5693 | 256.8035 | 192.9337 | 129.0639 | 65.1942 | 1.3244 | -62.5454 | -126.4152 | -190.285 | -254.1547 | -318.0245 | -381.8943
Egmont | 200.1049 | 235.4937 | 241.7734 | 228.2604 | 242.2411 | 230.0964 | 166.0497 | 121.9514 | 136.8731 | 133.2786 | [11 empty] | 200.1049 | 235.4937 | 241.7734 | 228.2604 | 242.2411 | 230.0964 | 166.0497 | 121.9514 | 136.8731 | 133.2786 | 123.9567 | 111.292 | 98.6274 | 85.9627 | 73.2981 | 60.6334 | 47.9687 | 35.3041 | 22.6394 | 9.9748 | -2.6899
Kinleith | 713.2222 | 363.2222 | 303.0498 | 559.6931 | 230.3333 | 367.1071 | 322.125 | 433.3153 | 405.454 | 714.9795 | [11 empty] | 713.2222 | 363.2222 | 303.0498 | 559.6931 | 230.3333 | 367.1071 | 322.125 | 433.3153 | 405.454 | 714.9795 | 454.1447 | 456.4891 | 458.8336 | 461.178 | 463.5225 | 465.8669 | 468.2114 | 470.5558 | 472.9003 | 475.2447 | 477.5892
Manawatu | 497.7487 | 590.9703 | 483.156 | 441.727 | 423.2177 | 391.3793 | 422.885 | 410.3834 | 276.2716 | 359.4318 | [11 empty] | 497.7487 | 590.9703 | 483.156 | 441.727 | 423.2177 | 391.3793 | 422.885 | 410.3834 | 276.2716 | 359.4318 | 299.718 | 276.0818 | 252.4456 | 228.8095 | 205.1733 | 181.5371 | 157.9009 | 134.2647 | 110.6285 | 86.9923 | 63.3561
Mt Maunganui | 583.5 | 322.163 | 353.8331 | 287.7512 | 261.9143 | 217.7949 | 148.1522 | 244.5332 | 256.9026 | 149.733 | [11 empty] | 583.5 | 322.163 | 353.8331 | 287.7512 | 261.9143 | 217.7949 | 148.1522 | 244.5332 | 256.9026 | 149.733 | 103.623 | 71.0767 | 38.5304 | 5.9841 | -26.5622 | -59.1086 | -91.6549 | -124.2012 | -156.7475 | -189.2938 | -221.8401
Rangitikei | 192.63 | 190.2366 | 274.1378 | 229.5083 | 299.3107 | 209.7471 | 236.2913 | 138.2919 | 198.7907 | 120.7879 | [11 empty] | 192.63 | 190.2366 | 274.1378 | 229.5083 | 299.3107 | 209.7471 | 236.2913 | 138.2919 | 198.7907 | 120.7879 | 164.4684 | 156.3766 | 148.2848 | 140.193 | 132.1013 | 124.0095 | 115.9177 | 107.8259 | 99.7341 | 91.6423 | 83.5505
Taranaki | 393.6061 | 314.9 | 304.2397 | 278.8324 | 292.8635 | 235.1582 | 371.8232 | 222.8897 | 219.0507 | 200.6037 | [11 empty] | 393.6061 | 314.9 | 304.2397 | 278.8324 | 292.8635 | 235.1582 | 371.8232 | 222.8897 | 219.0507 | 200.6037 | 196.9484 | 181.2305 | 165.5127 | 149.7948 | 134.0769 | 118.359 | 102.6412 | 86.9233 | 71.2054 | 55.4875 | 39.7697
Tararua | 120.9464 | 112.8824 | 145.6562 | 114.6197 | 140.7 | 98.1235 | 149.6667 | 165.8227 | 135.3229 | 102.4651 | [11 empty] | 120.9464 | 112.8824 | 145.6562 | 114.6197 | 140.7 | 98.1235 | 149.6667 | 165.8227 | 135.3229 | 102.4651 | 133.7589 | 134.6931 | 135.6273 | 136.5616 | 137.4958 | 138.4301 | 139.3643 | 140.2985 | 141.2328 | 142.167 | 143.1012
Tauranga | 553.5896 | 679.8028 | 736.8441 | 516.3856 | 758.1146 | 488.0738 | 447.2487 | 335.7429 | 363.5796 | 421.1767 | [11 empty] | 553.5896 | 679.8028 | 736.8441 | 516.3856 | 758.1146 | 488.0738 | 447.2487 | 335.7429 | 363.5796 | 421.1767 | 333.7813 | 298.095 | 262.4088 | 226.7225 | 191.0362 | 155.3499 | 119.6637 | 83.9774 | 48.2911 | 12.6048 | -23.0815
Waikato | 298.8483 | 240.4939 | 244.853 | 234.6769 | 271.9013 | 217.7298 | 237.4054 | 176.7092 | 230.6562 | 215.0647 | [11 empty] | 298.8483 | 240.4939 | 244.853 | 234.6769 | 271.9013 | 217.7298 | 237.4054 | 176.7092 | 230.6562 | 215.0647 | 196.5131 | 189.1821 | 181.8511 | 174.52 | 167.189 | 159.8579 | 152.5269 | 145.1959 | 137.8648 | 130.5338 | 123.2027
Waikino | 532.6024 | 748.8391 | 493.9204 | 823.1395 | 312.2292 | 421.9906 | 795.1566 | 287.0144 | 348.5779 | 453.9706 | [11 empty] | 532.6024 | 748.8391 | 493.9204 | 823.1395 | 312.2292 | 421.9906 | 795.1566 | 287.0144 | 348.5779 | 453.9706 | 371.1363 | 343.7531 | 316.3699 | 288.9867 | 261.6034 | 234.2202 | 206.837 | 179.4538 | 152.0705 | 124.6873 | 97.3041
Wairarapa | 142.4802 | 192.8777 | 209.4999 | 232.2746 | 238.8383 | 159.1006 | 214.7159 | 140.055 | 136.3523 | 165.1633 | [11 empty] | 142.4802 | 192.8777 | 209.4999 | 232.2746 | 238.8383 | 159.1006 | 214.7159 | 140.055 | 136.3523 | 165.1633 | 160.7635 | 156.6958 | 152.6281 | 148.5604 | 144.4927 | 140.425 | 136.3573 | 132.2896 | 128.2219 | 124.1543 | 120.0866
Whanganui | 410.5484 | 290.557 | 445.0628 | 365.0428 | 336.0855 | 394.365 | 427.7923 | 274.5344 | 316.9563 | 252.0978 | [11 empty] | 410.5484 | 290.557 | 445.0628 | 365.0428 | 336.0855 | 394.365 | 427.7923 | 274.5344 | 316.9563 | 252.0978 | 289.7251 | 278.5289 | 267.3327 | 256.1364 | 244.9402 | 233.744 | 222.5478 | 211.3516 | 200.1554 | 188.9592 | 177.763

## SAIDI
Forecast SAIDI
| SAIDI | [20 empty] | Linear trend
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Poles
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 1.264 | 1.5166 | 1.2991 | 4.6808 | 3.5281 | 2.0677 | 4.4908 | 2.2979 | 3.6058 | 0.7913
[11 empty] | 3.0159 | 3.0349 | 2.923 | 2.85 | 2.7714 | 2.6902 | 2.5997 | 2.5239 | 2.4803 | 2.4411 | 2.3757 | [10 empty] | 2.9987 | 3.0795 | 3.1603 | 3.2411 | 3.3219 | 3.4027 | 3.4835 | 3.5643 | 3.6451 | 3.726 | 3.8068
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0 | 0.31568 | 0.21195 | 0.041627 | 0.0065164 | 0.0036969 | 0.089027 | 0.31166 | 2.0678 | 0 | 0.15992 | 0.16241 | 0.16475 | 0.1676 | 0.17512 | 0.18008 | 0.18356 | 0.18776 | 0.19177 | 0.19547 | 0.19872 | 0 | 0.31568 | 0.21195 | 0.041627 | 0.0065164 | 0.0036969 | 0.089027 | 0.31166 | 2.0678 | 0 | 0.73489 | 0.81309 | 0.89129 | 0.96949 | 1.0477 | 1.1259 | 1.2041 | 1.2823 | 1.3605 | 1.4387 | 1.5169
Egmont | 0.11374 | 0.067986 | 0.040606 | 0.0096109 | 0.13572 | 0 | 0.0056546 | 0.00010385 | 0.247 | 0.21731 | 0.030529 | 0.019159 | 0.0159 | 0.013185 | 0.014598 | 0.015283 | 0.015906 | 0.017334 | 0.018921 | 0.020416 | 0.021946 | 0.11374 | 0.067986 | 0.040606 | 0.0096109 | 0.13572 | 0 | 0.0056546 | 0.00010385 | 0.247 | 0.21731 | 0.14494 | 0.15607 | 0.16719 | 0.17831 | 0.18943 | 0.20055 | 0.21167 | 0.2228 | 0.23392 | 0.24504 | 0.25616
Kinleith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17473 | 0 | 0 | 0.017296 | 0.017722 | 0.018298 | 0.019078 | 0.019607 | 0.020036 | 0.02079 | 0.021491 | 0.021978 | 0.023468 | 0.024626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17473 | 0 | 0 | 0.046595 | 0.05189 | 0.057185 | 0.06248 | 0.067775 | 0.073069 | 0.078364 | 0.083659 | 0.088954 | 0.094249 | 0.099544
Manawatu | 0 | 0.058277 | 0.21304 | 2.0752 | 0 | 0.46448 | 0.00059133 | 0.0060203 | 0.0055681 | 0 | 0.21974 | 0.27084 | 0.30895 | 0.32526 | 0.33395 | 0.35122 | 0.34609 | 0.34393 | 0.34141 | 0.328 | 0.31374 | 0 | 0.058277 | 0.21304 | 2.0752 | 0 | 0.46448 | 0.00059133 | 0.0060203 | 0.0055681 | 0 | 0.043537 | 0.00012203 | -0.043293 | -0.086708 | -0.13012 | -0.17354 | -0.21695 | -0.26037 | -0.30378 | -0.3472 | -0.39061
Mt Maunganui | 0 | 0.018864 | 0.35826 | 0.23511 | 0.069241 | 0.10767 | 0 | 0 | 0.006486 | 0 | 0.083323 | 0.084124 | 0.084822 | 0.081743 | 0.080128 | 0.065692 | 0.057432 | 0.052642 | 0.049121 | 0.046696 | 0.044247 | 0 | 0.018864 | 0.35826 | 0.23511 | 0.069241 | 0.10767 | 0 | 0 | 0.006486 | 0 | -0.0052656 | -0.020689 | -0.036112 | -0.051536 | -0.066959 | -0.082382 | -0.097806 | -0.11323 | -0.12865 | -0.14408 | -0.1595
Rangitikei | 0.067693 | 0.015183 | 0 | 0.19384 | 0.03446 | 0.065892 | 0.15212 | 0.54904 | 0.043877 | 0.0031624 | 0.42527 | 0.44199 | 0.40424 | 0.4049 | 0.38249 | 0.35501 | 0.32642 | 0.30352 | 0.29906 | 0.30434 | 0.29483 | 0.067693 | 0.015183 | 0 | 0.19384 | 0.03446 | 0.065892 | 0.15212 | 0.54904 | 0.043877 | 0.0031624 | 0.18824 | 0.20201 | 0.21578 | 0.22954 | 0.24331 | 0.25708 | 0.27084 | 0.28461 | 0.29838 | 0.31215 | 0.32591
Taranaki | 0.1113 | 0.25507 | 0.014132 | 0.0077421 | 2.49 | 0.1773 | 0.0831 | 0.022862 | 0.016192 | 0.066353 | 0.16068 | 0.17202 | 0.18259 | 0.18651 | 0.1958 | 0.19983 | 0.20421 | 0.20505 | 0.20484 | 0.21094 | 0.21622 | 0.1113 | 0.25507 | 0.014132 | 0.0077421 | 2.49 | 0.1773 | 0.0831 | 0.022862 | 0.016192 | 0.066353 | 0.18708 | 0.16211 | 0.13715 | 0.11218 | 0.087212 | 0.062245 | 0.037278 | 0.01231 | -0.012657 | -0.037624 | -0.062592
Tararua | 0.13737 | 0.051239 | 0.021662 | 0.062333 | 0.14562 | 0.13713 | 0.27157 | 0.053882 | 0.020015 | 0.008936 | 0.10704 | 0.1025 | 0.097483 | 0.091662 | 0.083131 | 0.075301 | 0.068151 | 0.062511 | 0.058693 | 0.058083 | 0.055368 | 0.13737 | 0.051239 | 0.021662 | 0.062333 | 0.14562 | 0.13713 | 0.27157 | 0.053882 | 0.020015 | 0.008936 | 0.071169 | 0.067568 | 0.063967 | 0.060366 | 0.056765 | 0.053164 | 0.049563 | 0.045962 | 0.042361 | 0.03876 | 0.035159
Tauranga | 0.40943 | 0.018438 | 0.37197 | 0.27694 | 0 | 0.12426 | 0.0034186 | 0.040528 | 0.30378 | 0.0010901 | 0.3945 | 0.39309 | 0.33568 | 0.29814 | 0.26483 | 0.2419 | 0.22316 | 0.20486 | 0.19021 | 0.181 | 0.17141 | 0.40943 | 0.018438 | 0.37197 | 0.27694 | 0 | 0.12426 | 0.0034186 | 0.040528 | 0.30378 | 0.0010901 | 0.020615 | -0.0038165 | -0.028248 | -0.052679 | -0.07711 | -0.10154 | -0.12597 | -0.1504 | -0.17483 | -0.19927 | -0.2237
Waikato | 0.043295 | 0.026576 | 0.012097 | 0.33713 | 0.12356 | 0.23349 | 0.087304 | 0.1832 | 0.059013 | 0.0014165 | 0.22531 | 0.23301 | 0.24196 | 0.24897 | 0.25629 | 0.26248 | 0.26801 | 0.27384 | 0.27817 | 0.28226 | 0.28577 | 0.043295 | 0.026576 | 0.012097 | 0.33713 | 0.12356 | 0.23349 | 0.087304 | 0.1832 | 0.059013 | 0.0014165 | 0.11291 | 0.11331 | 0.11371 | 0.11411 | 0.11451 | 0.11491 | 0.11532 | 0.11572 | 0.11612 | 0.11652 | 0.11692
Waikino | 0 | 0.012131 | 0 | 0 | 0 | 0 | 1.2905 | 0 | 0 | 0.30492 | 0.18478 | 0.18813 | 0.19425 | 0.20037 | 0.20682 | 0.21262 | 0.21767 | 0.22282 | 0.22722 | 0.22883 | 0.23161 | 0 | 0.012131 | 0 | 0 | 0 | 0 | 1.2905 | 0 | 0 | 0.30492 | 0.37846 | 0.41804 | 0.45762 | 0.4972 | 0.53678 | 0.57636 | 0.61595 | 0.65553 | 0.69511 | 0.73469 | 0.77427
Wairarapa | 0.37798 | 0.65579 | 0.045103 | 1.4324 | 0.36286 | 0.75378 | 2.4387 | 0.65052 | 0.83598 | 0.15456 | 0.88599 | 0.82681 | 0.75297 | 0.69197 | 0.63528 | 0.58265 | 0.53423 | 0.49181 | 0.46099 | 0.43009 | 0.40178 | 0.37798 | 0.65579 | 0.045103 | 1.4324 | 0.36286 | 0.75378 | 2.4387 | 0.65052 | 0.83598 | 0.15456 | 0.96035 | 0.99481 | 1.0293 | 1.0638 | 1.0982 | 1.1327 | 1.1672 | 1.2016 | 1.2361 | 1.2706 | 1.305
Whanganui | 0.0031885 | 0.021407 | 0.010245 | 0.0088935 | 0.16018 | 0 | 0.068816 | 0.30538 | 6.0475e-05 | 0.033555 | 0.12154 | 0.12314 | 0.12115 | 0.12061 | 0.12335 | 0.12806 | 0.13408 | 0.13636 | 0.13791 | 0.13148 | 0.11542 | 0.0031885 | 0.021407 | 0.010245 | 0.0088935 | 0.16018 | 0 | 0.068816 | 0.30538 | 6.0475e-05 | 0.033555 | 0.11514 | 0.12496 | 0.13477 | 0.14458 | 0.1544 | 0.16421 | 0.17402 | 0.18384 | 0.19365 | 0.20346 | 0.21328
Xarms
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 21.7855 | 14.639 | 16.0717 | 23.0731 | 27.7836 | 17.4652 | 23.3919 | 19.8116 | 16.3802 | 17.834
[11 empty] | 19.7802 | 19.805 | 19.7584 | 19.566 | 19.1854 | 18.6475 | 18.225 | 18.1408 | 18.0585 | 17.9415 | 17.7931 | [10 empty] | 19.3557 | 19.2706 | 19.1855 | 19.1005 | 19.0154 | 18.9303 | 18.8452 | 18.7602 | 18.6751 | 18.59 | 18.5049
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 1.7416 | 1.3096 | 0.71427 | 1.061 | 0.8322 | 0.90328 | 1.2375 | 1.3949 | 1.1728 | 1.0981 | 0.7292 | 0.75418 | 0.77352 | 0.78602 | 0.79663 | 0.79964 | 0.8007 | 0.80761 | 0.80619 | 0.80216 | 0.79766 | 1.7416 | 1.3096 | 0.71427 | 1.061 | 0.8322 | 0.90328 | 1.2375 | 1.3949 | 1.1728 | 1.0981 | 1.055 | 1.0384 | 1.0217 | 1.0051 | 0.98843 | 0.97179 | 0.95514 | 0.9385 | 0.92186 | 0.90522 | 0.88857
Egmont | 1.2096 | 0.68897 | 2.2966 | 1.4671 | 5.7828 | 0.96796 | 3.6737 | 2.5109 | 1.1032 | 2.5596 | 1.8288 | 1.7846 | 1.7509 | 1.6911 | 1.6256 | 1.5714 | 1.4952 | 1.5528 | 1.5723 | 1.5883 | 1.5841 | 1.2096 | 0.68897 | 2.2966 | 1.4671 | 5.7828 | 0.96796 | 3.6737 | 2.5109 | 1.1032 | 2.5596 | 2.8236 | 2.9322 | 3.0409 | 3.1495 | 3.2581 | 3.3668 | 3.4754 | 3.5841 | 3.6927 | 3.8013 | 3.91
Kinleith | 0.42081 | 0.00041963 | 0.004108 | 0.12238 | 0 | 0.038826 | 0.0055345 | 0.075915 | 0.10433 | 0.46682 | 0.11206 | 0.11588 | 0.11984 | 0.12185 | 0.12202 | 0.11945 | 0.11791 | 0.11766 | 0.11536 | 0.11201 | 0.10783 | 0.42081 | 0.00041963 | 0.004108 | 0.12238 | 0 | 0.038826 | 0.0055345 | 0.075915 | 0.10433 | 0.46682 | 0.16354 | 0.17075 | 0.17795 | 0.18516 | 0.19236 | 0.19957 | 0.20677 | 0.21398 | 0.22118 | 0.22839 | 0.23559
Manawatu | 1.5705 | 1.5227 | 2.2284 | 4.7841 | 3.1707 | 1.9716 | 2.3357 | 3.6653 | 1.4083 | 2.5044 | 2.4533 | 2.477 | 2.4782 | 2.418 | 2.3474 | 2.2527 | 2.1931 | 2.1649 | 2.1468 | 2.1287 | 2.1201 | 1.5705 | 1.5227 | 2.2284 | 4.7841 | 3.1707 | 1.9716 | 2.3357 | 3.6653 | 1.4083 | 2.5044 | 2.7243 | 2.7622 | 2.8 | 2.8378 | 2.8757 | 2.9135 | 2.9514 | 2.9892 | 3.0271 | 3.0649 | 3.1028
Mt Maunganui | 1.2965 | 1.1924 | 1.1876 | 0.39479 | 0.2413 | 0.15323 | 0.28097 | 0.16281 | 0.48535 | 0.13258 | 0.41567 | 0.39724 | 0.36621 | 0.34478 | 0.30772 | 0.27006 | 0.23706 | 0.20342 | 0.17338 | 0.15151 | 0.12892 | 1.2965 | 1.1924 | 1.1876 | 0.39479 | 0.2413 | 0.15323 | 0.28097 | 0.16281 | 0.48535 | 0.13258 | -0.14652 | -0.27367 | -0.40081 | -0.52795 | -0.65509 | -0.78223 | -0.90937 | -1.0365 | -1.1637 | -1.2908 | -1.4179
Rangitikei | 0.69968 | 0.54504 | 1.0812 | 1.6461 | 2.737 | 1.5003 | 1.5417 | 1.5892 | 1.2994 | 0.99785 | 2.0954 | 2.0336 | 1.9665 | 1.9584 | 1.9991 | 2.014 | 2.034 | 2.0737 | 2.1213 | 2.1562 | 2.1896 | 0.69968 | 0.54504 | 1.0812 | 1.6461 | 2.737 | 1.5003 | 1.5417 | 1.5892 | 1.2994 | 0.99785 | 1.6622 | 1.7165 | 1.7707 | 1.825 | 1.8793 | 1.9335 | 1.9878 | 2.0421 | 2.0963 | 2.1506 | 2.2049
Taranaki | 3.4287 | 3.2486 | 3.7025 | 6.0087 | 6.8691 | 2.646 | 3.972 | 3.7146 | 3.8424 | 3.795 | 4.5075 | 4.5595 | 4.6212 | 4.4974 | 4.2654 | 4.0188 | 3.8137 | 3.7081 | 3.6332 | 3.5359 | 3.4404 | 3.4287 | 3.2486 | 3.7025 | 6.0087 | 6.8691 | 2.646 | 3.972 | 3.7146 | 3.8424 | 3.795 | 4.0288 | 4.0117 | 3.9946 | 3.9775 | 3.9605 | 3.9434 | 3.9263 | 3.9092 | 3.8921 | 3.875 | 3.858
Tararua | 1.5945 | 1.1972 | 0.65933 | 1.306 | 2.1168 | 1.2916 | 1.3783 | 0.95948 | 1.5166 | 1.9461 | 1.6753 | 1.6782 | 1.676 | 1.7216 | 1.7472 | 1.7404 | 1.7546 | 1.7993 | 1.8632 | 1.8748 | 1.8981 | 1.5945 | 1.1972 | 0.65933 | 1.306 | 2.1168 | 1.2916 | 1.3783 | 0.95948 | 1.5166 | 1.9461 | 1.6064 | 1.6445 | 1.6826 | 1.7208 | 1.7589 | 1.797 | 1.8352 | 1.8733 | 1.9115 | 1.9496 | 1.9877
Tauranga | 2.191 | 1.9645 | 0.25019 | 1.5177 | 1.893 | 0.80416 | 1.1663 | 1.2754 | 1.6873 | 0.60767 | 1.0465 | 0.96928 | 0.88755 | 0.86408 | 0.79135 | 0.70624 | 0.64698 | 0.58932 | 0.51424 | 0.46005 | 0.40961 | 2.191 | 1.9645 | 0.25019 | 1.5177 | 1.893 | 0.80416 | 1.1663 | 1.2754 | 1.6873 | 0.60767 | 0.89549 | 0.81545 | 0.73541 | 0.65537 | 0.57533 | 0.49528 | 0.41524 | 0.3352 | 0.25516 | 0.17512 | 0.095076
Waikato | 1.3882 | 1.251 | 1.4268 | 1.284 | 1.4202 | 2.3973 | 0.80468 | 0.63311 | 1.2415 | 0.4496 | 1.3642 | 1.3454 | 1.3209 | 1.2934 | 1.2704 | 1.2382 | 1.2219 | 1.2033 | 1.1765 | 1.1556 | 1.1309 | 1.3882 | 1.251 | 1.4268 | 1.284 | 1.4202 | 2.3973 | 0.80468 | 0.63311 | 1.2415 | 0.4496 | 0.79818 | 0.71974 | 0.64129 | 0.56285 | 0.4844 | 0.40595 | 0.32751 | 0.24906 | 0.17062 | 0.092171 | 0.013725
Waikino | 4.3685 | 0.69138 | 0.70819 | 0.78338 | 0.58468 | 1.429 | 0.82218 | 0.83892 | 0.22598 | 0.0060971 | 0.66773 | 0.68069 | 0.68685 | 0.68414 | 0.6769 | 0.6626 | 0.65087 | 0.63891 | 0.62383 | 0.6054 | 0.58866 | 4.3685 | 0.69138 | 0.70819 | 0.78338 | 0.58468 | 1.429 | 0.82218 | 0.83892 | 0.22598 | 0.0060971 | -0.31766 | -0.56557 | -0.81347 | -1.0614 | -1.3093 | -1.5572 | -1.8051 | -2.053 | -2.3009 | -2.5488 | -2.7967
Wairarapa | 1.0456 | 0.52183 | 0.57976 | 1.1288 | 1.0621 | 1.5483 | 3.2186 | 1.2278 | 1.5085 | 1.2228 | 1.2041 | 1.2553 | 1.2996 | 1.3379 | 1.3693 | 1.3905 | 1.415 | 1.4399 | 1.4651 | 1.5318 | 1.5711 | 1.0456 | 0.52183 | 0.57976 | 1.1288 | 1.0621 | 1.5483 | 3.2186 | 1.2278 | 1.5085 | 1.2228 | 1.923 | 2.0351 | 2.1472 | 2.2593 | 2.3714 | 2.4835 | 2.5956 | 2.7077 | 2.8198 | 2.9319 | 3.044
Whanganui | 0.8303 | 0.50533 | 1.2328 | 1.5691 | 1.0736 | 1.8137 | 2.9548 | 1.7633 | 0.78459 | 2.0474 | 1.6805 | 1.7543 | 1.8111 | 1.8473 | 1.8663 | 1.8635 | 1.8439 | 1.8418 | 1.8472 | 1.8391 | 1.8263 | 0.8303 | 0.50533 | 1.2328 | 1.5691 | 1.0736 | 1.8137 | 2.9548 | 1.7633 | 0.78459 | 2.0474 | 2.1394 | 2.2634 | 2.3874 | 2.5114 | 2.6354 | 2.7594 | 2.8834 | 3.0074 | 3.1313 | 3.2553 | 3.3793
Conductor
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 12.1573 | 9.9913 | 16.2623 | 33.1632 | 35.7275 | 11.4779 | 29.309 | 25.7811 | 21.1722 | 19.9193
[11 empty] | 23.919 | 23.8926 | 23.7054 | 23.3768 | 22.8243 | 22.1979 | 21.5718 | 20.9947 | 20.5481 | 20.0941 | 20.0795 | [10 empty] | 26.8263 | 27.7955 | 28.7646 | 29.7337 | 30.7028 | 31.672 | 32.6411 | 33.6102 | 34.5794 | 35.5485 | 36.5176
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.67271 | 0.52424 | 2.1117 | 2.1698 | 0.33555 | 1.7522 | 2.5396 | 2.6233 | 0.76579 | 0.51605 | 1.5879 | 1.6008 | 1.6122 | 1.6269 | 1.6397 | 1.6414 | 1.6587 | 1.6607 | 1.6596 | 1.6557 | 1.6556 | 0.67271 | 0.52424 | 2.1117 | 2.1698 | 0.33555 | 1.7522 | 2.5396 | 2.6233 | 0.76579 | 0.51605 | 1.5799 | 1.6124 | 1.6449 | 1.6775 | 1.71 | 1.7425 | 1.775 | 1.8075 | 1.84 | 1.8725 | 1.9051
Egmont | 1.4661 | 0.85901 | 1.2815 | 1.1229 | 5.839 | 1.5708 | 1.2532 | 2.3585 | 2.2591 | 2.3582 | 2.5178 | 2.5217 | 2.4418 | 2.1548 | 2.0067 | 1.9911 | 1.9732 | 1.9628 | 1.881 | 1.792 | 1.7893 | 1.4661 | 0.85901 | 1.2815 | 1.1229 | 5.839 | 1.5708 | 1.2532 | 2.3585 | 2.2591 | 2.3582 | 2.6814 | 2.7986 | 2.9158 | 3.033 | 3.1502 | 3.2674 | 3.3846 | 3.5018 | 3.619 | 3.7362 | 3.8534
Kinleith | 0.054342 | 0.074611 | 0.30299 | 0.088063 | 0.05341 | 0.36271 | 0.036776 | 0 | 0.19416 | 0.067325 | 0.11481 | 0.11506 | 0.11542 | 0.11714 | 0.11908 | 0.11971 | 0.12144 | 0.12278 | 0.12125 | 0.12091 | 0.12129 | 0.054342 | 0.074611 | 0.30299 | 0.088063 | 0.05341 | 0.36271 | 0.036776 | 0 | 0.19416 | 0.067325 | 0.10991 | 0.10745 | 0.10499 | 0.10253 | 0.10008 | 0.097616 | 0.095156 | 0.092697 | 0.090238 | 0.087778 | 0.085319
Manawatu | 2.2244 | 0.34035 | 2.1954 | 2.661 | 3.5632 | 1.2498 | 1.8061 | 2.6035 | 1.161 | 2.2348 | 1.9885 | 1.9906 | 2.0055 | 2.001 | 2.0127 | 1.9444 | 1.96 | 1.9693 | 1.9321 | 1.9328 | 1.9313 | 2.2244 | 0.34035 | 2.1954 | 2.661 | 3.5632 | 1.2498 | 1.8061 | 2.6035 | 1.161 | 2.2348 | 2.104 | 2.1222 | 2.1403 | 2.1585 | 2.1767 | 2.1949 | 2.2131 | 2.2313 | 2.2494 | 2.2676 | 2.2858
Mt Maunganui | 0.63254 | 0.98577 | 1.402 | 5.074 | 1.2903 | 1.1926 | 0.13208 | 1.4897 | 2.002 | 0.842 | 1.6791 | 1.6952 | 1.6912 | 1.6893 | 1.5487 | 1.4416 | 1.2089 | 0.98517 | 0.96876 | 0.92708 | 0.92791 | 0.63254 | 0.98577 | 1.402 | 5.074 | 1.2903 | 1.1926 | 0.13208 | 1.4897 | 2.002 | 0.842 | 1.3214 | 1.2882 | 1.2549 | 1.2217 | 1.1884 | 1.1552 | 1.1219 | 1.0887 | 1.0554 | 1.0222 | 0.98894
Rangitikei | 0.48973 | 0.35923 | 0.77184 | 2.0175 | 2.0877 | 0.23187 | 1.7045 | 1.9239 | 2.3207 | 0.74525 | 1.4191 | 1.4215 | 1.4366 | 1.4511 | 1.4467 | 1.4485 | 1.4578 | 1.4884 | 1.4446 | 1.4174 | 1.416 | 0.48973 | 0.35923 | 0.77184 | 2.0175 | 2.0877 | 0.23187 | 1.7045 | 1.9239 | 2.3207 | 0.74525 | 1.8984 | 2.0135 | 2.1287 | 2.2438 | 2.3589 | 2.474 | 2.5892 | 2.7043 | 2.8194 | 2.9345 | 3.0497
Taranaki | 0.91985 | 0.86548 | 2.0121 | 4.2374 | 9.5877 | 0.61407 | 7.9644 | 2.9611 | 2.479 | 4.401 | 4.4848 | 4.3611 | 4.1858 | 4.078 | 3.9075 | 3.7242 | 3.632 | 3.5322 | 3.3585 | 3.1813 | 3.1769 | 0.91985 | 0.86548 | 2.0121 | 4.2374 | 9.5877 | 0.61407 | 7.9644 | 2.9611 | 2.479 | 4.401 | 5.2568 | 5.5572 | 5.8577 | 6.1582 | 6.4586 | 6.7591 | 7.0596 | 7.36 | 7.6605 | 7.9609 | 8.2614
Tararua | 0.50494 | 0.55618 | 0.29122 | 0.80132 | 2.4799 | 0.54857 | 1.0368 | 3.0227 | 1.8 | 0.4643 | 1.1779 | 1.1984 | 1.225 | 1.2621 | 1.2798 | 1.3038 | 1.3257 | 1.3562 | 1.4006 | 1.3696 | 1.3601 | 0.50494 | 0.55618 | 0.29122 | 0.80132 | 2.4799 | 0.54857 | 1.0368 | 3.0227 | 1.8 | 0.4643 | 1.843 | 1.9689 | 2.0948 | 2.2207 | 2.3466 | 2.4725 | 2.5984 | 2.7243 | 2.8502 | 2.9761 | 3.102
Tauranga | 1.9465 | 1.3341 | 0.38184 | 6.1125 | 2.1756 | 1.4214 | 1.9482 | 2.9074 | 2.5171 | 2.0965 | 2.3948 | 2.406 | 2.381 | 2.3824 | 2.2621 | 2.0653 | 1.7625 | 1.3859 | 1.3701 | 1.3562 | 1.3578 | 1.9465 | 1.3341 | 0.38184 | 6.1125 | 2.1756 | 1.4214 | 1.9482 | 2.9074 | 2.5171 | 2.0965 | 2.5845 | 2.6391 | 2.6937 | 2.7483 | 2.803 | 2.8576 | 2.9122 | 2.9668 | 3.0214 | 3.076 | 3.1306
Waikato | 0.41783 | 0.76457 | 0.74694 | 1.4624 | 0.44656 | 0.24559 | 0.15966 | 1.9232 | 1.1074 | 0.47892 | 0.84991 | 0.85514 | 0.86126 | 0.86705 | 0.8701 | 0.87336 | 0.8796 | 0.8862 | 0.8709 | 0.86681 | 0.86761 | 0.41783 | 0.76457 | 0.74694 | 1.4624 | 0.44656 | 0.24559 | 0.15966 | 1.9232 | 1.1074 | 0.47892 | 0.93271 | 0.96132 | 0.98994 | 1.0186 | 1.0472 | 1.0758 | 1.1044 | 1.133 | 1.1616 | 1.1903 | 1.2189
Waikino | 1.2074 | 0.38149 | 3.3216 | 0.42352 | 0.20422 | 1.2556 | 0.67972 | 1.0101 | 0.99393 | 0.69389 | 0.9252 | 0.94034 | 0.94982 | 0.96151 | 0.97315 | 0.98792 | 1.0002 | 1.0159 | 1.0125 | 1.0291 | 1.032 | 1.2074 | 0.38149 | 3.3216 | 0.42352 | 0.20422 | 1.2556 | 0.67972 | 1.0101 | 0.99393 | 0.69389 | 0.68139 | 0.62035 | 0.55931 | 0.49826 | 0.43722 | 0.37617 | 0.31513 | 0.25408 | 0.19304 | 0.132 | 0.070952
Wairarapa | 0.72329 | 2.4879 | 0.58802 | 1.7737 | 2.1213 | 0.62209 | 8.023 | 0.87425 | 0.81088 | 3.4419 | 2.3601 | 2.3536 | 2.3587 | 2.3776 | 2.3502 | 2.3838 | 2.3635 | 2.3782 | 2.3501 | 2.3504 | 2.352 | 0.72329 | 2.4879 | 0.58802 | 1.7737 | 2.1213 | 0.62209 | 8.023 | 0.87425 | 0.81088 | 3.4419 | 3.1936 | 3.384 | 3.5743 | 3.7647 | 3.955 | 4.1454 | 4.3357 | 4.5261 | 4.7165 | 4.9068 | 5.0972
Whanganui | 0.89765 | 0.45843 | 0.85522 | 5.219 | 5.5431 | 0.41068 | 2.025 | 2.0835 | 2.7614 | 1.5791 | 2.4189 | 2.4331 | 2.441 | 2.4079 | 2.4077 | 2.2728 | 2.2284 | 2.251 | 2.1779 | 2.0949 | 2.0918 | 0.89765 | 0.45843 | 0.85522 | 5.219 | 5.5431 | 0.41068 | 2.025 | 2.0835 | 2.7614 | 1.5791 | 2.6393 | 2.7222 | 2.8051 | 2.888 | 2.971 | 3.0539 | 3.1368 | 3.2197 | 3.3026 | 3.3855 | 3.4684
Transformers
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 2.0792 | 3.7463 | 1.2509 | 2.3298 | 4.818 | 2.5609 | 1.159 | 4.2522 | 4.0459 | 2.3464
[11 empty] | 6.2506 | 6.5065 | 6.823 | 7.127 | 7.4561 | 7.7567 | 8.0796 | 8.487 | 8.7531 | 9.0057 | 9.194 | [10 empty] | 3.3168 | 3.4001 | 3.4834 | 3.5666 | 3.6499 | 3.7331 | 3.8164 | 3.8997 | 3.9829 | 4.0662 | 4.1495
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.0067808 | 0.18719 | 0.37993 | 0.1217 | 0.20938 | 0.089377 | 0.040882 | 0.19911 | 0.15442 | 0.42009 | 0.73783 | 0.79153 | 0.83574 | 0.89135 | 0.95591 | 1.0122 | 1.0898 | 1.1807 | 1.2281 | 1.268 | 1.3017 | 0.0067808 | 0.18719 | 0.37993 | 0.1217 | 0.20938 | 0.089377 | 0.040882 | 0.19911 | 0.15442 | 0.42009 | 0.25501 | 0.26849 | 0.28197 | 0.29545 | 0.30893 | 0.3224 | 0.33588 | 0.34936 | 0.36284 | 0.37632 | 0.38979
Egmont | 0.12966 | 0.60728 | 0.27956 | 0.23483 | 0.22391 | 0.3753 | 0.18703 | 0.47741 | 0.22338 | 0.34177 | 0.2802 | 0.26773 | 0.25689 | 0.2451 | 0.23144 | 0.22915 | 0.22455 | 0.22894 | 0.22481 | 0.2257 | 0.22207 | 0.12966 | 0.60728 | 0.27956 | 0.23483 | 0.22391 | 0.3753 | 0.18703 | 0.47741 | 0.22338 | 0.34177 | 0.31531 | 0.31664 | 0.31797 | 0.31929 | 0.32062 | 0.32195 | 0.32327 | 0.3246 | 0.32593 | 0.32726 | 0.32858
Kinleith | 0.28699 | 0.10684 | 0.053133 | 0.008744 | 0.1323 | 0.024211 | 0 | 0 | 0.018237 | 0.14802 | 0.084425 | 0.08743 | 0.089386 | 0.096847 | 0.10109 | 0.10696 | 0.11013 | 0.11434 | 0.1158 | 0.1184 | 0.11912 | 0.28699 | 0.10684 | 0.053133 | 0.008744 | 0.1323 | 0.024211 | 0 | 0 | 0.018237 | 0.14802 | 0.0021477 | -0.011616 | -0.025379 | -0.039143 | -0.052906 | -0.06667 | -0.080433 | -0.094196 | -0.10796 | -0.12172 | -0.13549
Manawatu | 0 | 0.0068984 | 0 | 0.090695 | 0.375 | 0.38327 | 0.0571 | 0.11033 | 0.12609 | 0.43121 | 1.3521 | 1.4592 | 1.5731 | 1.6986 | 1.8551 | 1.9714 | 2.0684 | 2.1887 | 2.3124 | 2.3846 | 2.4294 | 0 | 0.0068984 | 0 | 0.090695 | 0.375 | 0.38327 | 0.0571 | 0.11033 | 0.12609 | 0.43121 | 0.33054 | 0.3619 | 0.39326 | 0.42462 | 0.45598 | 0.48734 | 0.51869 | 0.55005 | 0.58141 | 0.61277 | 0.64413
Mt Maunganui | 0 | 0.0017771 | 0.060941 | 0.072186 | 0.52155 | 0.0062794 | 0.070673 | 0.019005 | 0.12227 | 0.026671 | 0.19995 | 0.21485 | 0.23287 | 0.2473 | 0.26109 | 0.2784 | 0.28772 | 0.30951 | 0.32528 | 0.33809 | 0.35264 | 0 | 0.0017771 | 0.060941 | 0.072186 | 0.52155 | 0.0062794 | 0.070673 | 0.019005 | 0.12227 | 0.026671 | 0.10193 | 0.10408 | 0.10622 | 0.10837 | 0.11052 | 0.11266 | 0.11481 | 0.11695 | 0.1191 | 0.12124 | 0.12339
Rangitikei | 0.17202 | 0.40567 | 0.00069521 | 0.095532 | 1.2413 | 0.097473 | 0.0065139 | 0.075655 | 0.036357 | 0.021924 | 0.45537 | 0.4403 | 0.42528 | 0.41128 | 0.39665 | 0.38108 | 0.37083 | 0.36069 | 0.35058 | 0.34893 | 0.34618 | 0.17202 | 0.40567 | 0.00069521 | 0.095532 | 1.2413 | 0.097473 | 0.0065139 | 0.075655 | 0.036357 | 0.021924 | 0.049577 | 0.019442 | -0.010693 | -0.040828 | -0.070963 | -0.1011 | -0.13123 | -0.16137 | -0.1915 | -0.22164 | -0.25177
Taranaki | 0.012176 | 0.31992 | 0.016833 | 0.22977 | 0.26654 | 0.25607 | 0.091054 | 0.21833 | 0.27151 | 0.26904 | 0.12567 | 0.12466 | 0.12428 | 0.12299 | 0.12262 | 0.12118 | 0.12208 | 0.12519 | 0.12817 | 0.12864 | 0.13272 | 0.012176 | 0.31992 | 0.016833 | 0.22977 | 0.26654 | 0.25607 | 0.091054 | 0.21833 | 0.27151 | 0.26904 | 0.28025 | 0.29573 | 0.3112 | 0.32668 | 0.34216 | 0.35764 | 0.37311 | 0.38859 | 0.40407 | 0.41955 | 0.43502
Tararua | 0 | 0 | 0.0060104 | 0.0036057 | 0.016209 | 0.17385 | 0.061648 | 0.14961 | 0.0068116 | 0.17253 | 0.095729 | 0.099676 | 0.10279 | 0.11263 | 0.12064 | 0.12799 | 0.13332 | 0.13907 | 0.14554 | 0.14639 | 0.15163 | 0 | 0 | 0.0060104 | 0.0036057 | 0.016209 | 0.17385 | 0.061648 | 0.14961 | 0.0068116 | 0.17253 | 0.14737 | 0.16343 | 0.17949 | 0.19556 | 0.21162 | 0.22768 | 0.24374 | 0.2598 | 0.27587 | 0.29193 | 0.30799
Tauranga | 0.49775 | 0.15704 | 0.13737 | 0.20687 | 0.13056 | 0.53759 | 0.4203 | 1.6513 | 0.24067 | 0.06582 | 1.032 | 1.0772 | 1.1674 | 1.2291 | 1.2578 | 1.3107 | 1.3643 | 1.4644 | 1.5242 | 1.5822 | 1.6609 | 0.49775 | 0.15704 | 0.13737 | 0.20687 | 0.13056 | 0.53759 | 0.4203 | 1.6513 | 0.24067 | 0.06582 | 0.5817 | 0.61391 | 0.64612 | 0.67834 | 0.71055 | 0.74276 | 0.77497 | 0.80718 | 0.8394 | 0.87161 | 0.90382
Waikato | 0.83772 | 1.9423 | 0.038135 | 0.73998 | 0.54494 | 0.29205 | 0.017343 | 0.040845 | 2.6851 | 0.071245 | 1.109 | 1.1358 | 1.1733 | 1.202 | 1.2433 | 1.2782 | 1.3532 | 1.4051 | 1.4137 | 1.4699 | 1.4773 | 0.83772 | 1.9423 | 0.038135 | 0.73998 | 0.54494 | 0.29205 | 0.017343 | 0.040845 | 2.6851 | 0.071245 | 0.58409 | 0.55921 | 0.53433 | 0.50944 | 0.48456 | 0.45967 | 0.43479 | 0.40991 | 0.38502 | 0.36014 | 0.33525
Waikino | 0.0010236 | 0.0024478 | 0.0047653 | 0.071611 | 0.17151 | 0.0019369 | 0.033786 | 0.0026512 | 0.12124 | 0.0011057 | 0.14025 | 0.15975 | 0.17921 | 0.19543 | 0.22578 | 0.24493 | 0.26194 | 0.27512 | 0.2889 | 0.3025 | 0.31288 | 0.0010236 | 0.0024478 | 0.0047653 | 0.071611 | 0.17151 | 0.0019369 | 0.033786 | 0.0026512 | 0.12124 | 0.0011057 | 0.059165 | 0.062429 | 0.065694 | 0.068959 | 0.072224 | 0.075488 | 0.078753 | 0.082018 | 0.085283 | 0.088547 | 0.091812
Wairarapa | 0.13413 | 0.009022 | 0.27354 | 0.42446 | 0.068844 | 0.079017 | 0.16641 | 0.65486 | 0.034635 | 0.31819 | 0.42609 | 0.43296 | 0.44275 | 0.44993 | 0.45767 | 0.46355 | 0.46298 | 0.46244 | 0.46199 | 0.45908 | 0.45757 | 0.13413 | 0.009022 | 0.27354 | 0.42446 | 0.068844 | 0.079017 | 0.16641 | 0.65486 | 0.034635 | 0.31819 | 0.31559 | 0.33364 | 0.35169 | 0.36975 | 0.3878 | 0.40585 | 0.4239 | 0.44195 | 0.46 | 0.47805 | 0.4961
Whanganui | 0.0009537 | 0 | 0 | 0.029788 | 0.91589 | 0.24448 | 0.0062921 | 0.65304 | 0.0052356 | 0.058791 | 0.21197 | 0.21548 | 0.21999 | 0.22455 | 0.22692 | 0.23101 | 0.23038 | 0.23286 | 0.23354 | 0.23316 | 0.22993 | 0.0009537 | 0 | 0 | 0.029788 | 0.91589 | 0.24448 | 0.0062921 | 0.65304 | 0.0052356 | 0.058791 | 0.29413 | 0.3128 | 0.33147 | 0.35014 | 0.36881 | 0.38748 | 0.40615 | 0.42482 | 0.44349 | 0.46216 | 0.48083
Fuses
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 1.3151 | 1.0693 | 1.1135 | 1.9544 | 1.553 | 1.2722 | 1.4249 | 5.563 | 5.5067 | 5.3584
[11 empty] | 5.263 | 5.4869 | 5.6655 | 5.8709 | 6.0472 | 6.2281 | 6.3283 | 6.6131 | 6.8622 | 6.9341 | 7.0057 | [10 empty] | 5.5407 | 6.073 | 6.6053 | 7.1376 | 7.6699 | 8.2022 | 8.7345 | 9.2668 | 9.7991 | 10.3314 | 10.8637
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.022564 | 0.034912 | 0.062796 | 0.033503 | 0.041514 | 0.092044 | 0.082444 | 0.5579 | 1.2636 | 0.2978 | 0.7067 | 0.75755 | 0.7976 | 0.84947 | 0.89829 | 0.94624 | 0.97056 | 1.0169 | 1.0586 | 1.0849 | 1.1089 | 0.022564 | 0.034912 | 0.062796 | 0.033503 | 0.041514 | 0.092044 | 0.082444 | 0.5579 | 1.2636 | 0.2978 | 0.70726 | 0.7906 | 0.87393 | 0.95727 | 1.0406 | 1.1239 | 1.2073 | 1.2906 | 1.374 | 1.4573 | 1.5406
Egmont | 0.040411 | 0.028678 | 0.083475 | 0.30211 | 0.27938 | 0.21815 | 0.15378 | 0.5672 | 0.55574 | 0.42172 | 0.58038 | 0.61761 | 0.63479 | 0.66097 | 0.67775 | 0.70181 | 0.71579 | 0.77442 | 0.81366 | 0.8279 | 0.84338 | 0.040411 | 0.028678 | 0.083475 | 0.30211 | 0.27938 | 0.21815 | 0.15378 | 0.5672 | 0.55574 | 0.42172 | 0.56619 | 0.62094 | 0.67568 | 0.73043 | 0.78518 | 0.83993 | 0.89468 | 0.94943 | 1.0042 | 1.0589 | 1.1137
Kinleith | 0 | 0 | 0.0032422 | 0.11504 | 0.11425 | 0.021132 | 0 | 0.0049496 | 0.0073757 | 0.0079818 | 0.043136 | 0.04438 | 0.044686 | 0.045609 | 0.046095 | 0.046175 | 0.0471 | 0.048171 | 0.048737 | 0.04948 | 0.050233 | 0 | 0 | 0.0032422 | 0.11504 | 0.11425 | 0.021132 | 0 | 0.0049496 | 0.0073757 | 0.0079818 | 0.017189 | 0.015333 | 0.013477 | 0.011621 | 0.0097655 | 0.0079096 | 0.0060536 | 0.0041977 | 0.0023418 | 0.00048582 | -0.0013701
Manawatu | 0.10953 | 0.14688 | 0.20952 | 0.33798 | 0.22525 | 0.098649 | 0.16907 | 0.89632 | 0.25707 | 0.71264 | 0.49626 | 0.5094 | 0.52313 | 0.53873 | 0.55031 | 0.57124 | 0.5864 | 0.66091 | 0.68604 | 0.69814 | 0.71037 | 0.10953 | 0.14688 | 0.20952 | 0.33798 | 0.22525 | 0.098649 | 0.16907 | 0.89632 | 0.25707 | 0.71264 | 0.61629 | 0.67083 | 0.72538 | 0.77993 | 0.83447 | 0.88902 | 0.94356 | 0.99811 | 1.0527 | 1.1072 | 1.1617
Mt Maunganui | 0.022812 | 0.0065424 | 0.029793 | 0.013729 | 0.17459 | 0 | 0.0069142 | 0.010242 | 0.20392 | 0.047309 | 0.10325 | 0.10517 | 0.10668 | 0.10797 | 0.10961 | 0.10943 | 0.11016 | 0.11052 | 0.11128 | 0.11161 | 0.11265 | 0.022812 | 0.0065424 | 0.029793 | 0.013729 | 0.17459 | 0 | 0.0069142 | 0.010242 | 0.20392 | 0.047309 | 0.09523 | 0.10317 | 0.1111 | 0.11904 | 0.12697 | 0.13491 | 0.14284 | 0.15078 | 0.15871 | 0.16665 | 0.17458
Rangitikei | 0.049084 | 0.02869 | 0.011468 | 0.035516 | 0.27029 | 0.11464 | 0.16826 | 0.15467 | 0.42436 | 0.90122 | 0.56972 | 0.5817 | 0.59402 | 0.60813 | 0.61943 | 0.62989 | 0.63248 | 0.64079 | 0.64011 | 0.63099 | 0.62206 | 0.049084 | 0.02869 | 0.011468 | 0.035516 | 0.27029 | 0.11464 | 0.16826 | 0.15467 | 0.42436 | 0.90122 | 0.59574 | 0.66482 | 0.73389 | 0.80297 | 0.87204 | 0.94112 | 1.0102 | 1.0793 | 1.1483 | 1.2174 | 1.2865
Taranaki | 0.21444 | 0.39629 | 0.23791 | 0.77638 | 0.20813 | 0.31294 | 0.48922 | 0.47574 | 0.92691 | 1.037 | 1.075 | 1.1216 | 1.1588 | 1.1874 | 1.2174 | 1.245 | 1.2646 | 1.301 | 1.3803 | 1.3953 | 1.4062 | 0.21444 | 0.39629 | 0.23791 | 0.77638 | 0.20813 | 0.31294 | 0.48922 | 0.47574 | 0.92691 | 1.037 | 0.89249 | 0.96249 | 1.0325 | 1.1025 | 1.1725 | 1.2425 | 1.3125 | 1.3825 | 1.4525 | 1.5225 | 1.5925
Tararua | 0.028338 | 0.015803 | 0.061516 | 0.0037376 | 0.020444 | 0.081608 | 0.0056115 | 0.12581 | 0.20281 | 0.49881 | 0.12483 | 0.12583 | 0.12615 | 0.13049 | 0.13145 | 0.13281 | 0.13276 | 0.14519 | 0.14923 | 0.1468 | 0.14387 | 0.028338 | 0.015803 | 0.061516 | 0.0037376 | 0.020444 | 0.081608 | 0.0056115 | 0.12581 | 0.20281 | 0.49881 | 0.30217 | 0.33812 | 0.37407 | 0.41002 | 0.44597 | 0.48192 | 0.51786 | 0.55381 | 0.58976 | 0.62571 | 0.66166
Tauranga | 0.062416 | 0.18032 | 0.0854 | 0.12748 | 0.052872 | 0.19761 | 0.17574 | 0.29196 | 0.57284 | 0.46248 | 0.094327 | 0.099291 | 0.10287 | 0.1066 | 0.11052 | 0.11377 | 0.11611 | 0.11901 | 0.12146 | 0.12199 | 0.12325 | 0.062416 | 0.18032 | 0.0854 | 0.12748 | 0.052872 | 0.19761 | 0.17574 | 0.29196 | 0.57284 | 0.46248 | 0.4766 | 0.52308 | 0.56957 | 0.61606 | 0.66255 | 0.70904 | 0.75553 | 0.80201 | 0.8485 | 0.89499 | 0.94148
Waikato | 0.20138 | 0.12102 | 0.036356 | 0.13632 | 0.071457 | 0.037593 | 0.0030429 | 0.049984 | 0.19801 | 0.041247 | 0.044999 | 0.04691 | 0.048156 | 0.049915 | 0.05084 | 0.051887 | 0.052639 | 0.053921 | 0.055032 | 0.055802 | 0.056844 | 0.20138 | 0.12102 | 0.036356 | 0.13632 | 0.071457 | 0.037593 | 0.0030429 | 0.049984 | 0.19801 | 0.041247 | 0.04738 | 0.039696 | 0.032012 | 0.024328 | 0.016644 | 0.0089606 | 0.0012769 | -0.0064069 | -0.014091 | -0.021775 | -0.029458
Waikino | 0.50725 | 0.039928 | 0.093676 | 0.017246 | 0.0067415 | 0.038974 | 0.081685 | 0.16772 | 0.080362 | 0.17157 | 0.28611 | 0.30099 | 0.31345 | 0.33031 | 0.34286 | 0.35491 | 0.36198 | 0.374 | 0.38596 | 0.3883 | 0.39522 | 0.50725 | 0.039928 | 0.093676 | 0.017246 | 0.0067415 | 0.038974 | 0.081685 | 0.16772 | 0.080362 | 0.17157 | 0.049105 | 0.036122 | 0.023138 | 0.010155 | -0.0028291 | -0.015813 | -0.028796 | -0.04178 | -0.054764 | -0.067747 | -0.080731
Wairarapa | 0.043574 | 0.044433 | 0.15086 | 0.053846 | 0.082524 | 0.051676 | 0.073565 | 1.0624 | 0.58772 | 0.38164 | 0.65273 | 0.68021 | 0.70612 | 0.72913 | 0.7557 | 0.7784 | 0.79141 | 0.8173 | 0.86031 | 0.88216 | 0.89873 | 0.043574 | 0.044433 | 0.15086 | 0.053846 | 0.082524 | 0.051676 | 0.073565 | 1.0624 | 0.58772 | 0.38164 | 0.63427 | 0.70355 | 0.77284 | 0.84212 | 0.9114 | 0.98068 | 1.05 | 1.1192 | 1.1885 | 1.2578 | 1.3271
Whanganui | 0.013275 | 0.025775 | 0.047448 | 0.0015578 | 0.0055252 | 0.007192 | 0.015541 | 1.1981 | 0.22596 | 0.37698 | 0.48549 | 0.49624 | 0.50909 | 0.52613 | 0.53695 | 0.54652 | 0.54628 | 0.55095 | 0.55157 | 0.54067 | 0.534 | 0.013275 | 0.025775 | 0.047448 | 0.0015578 | 0.0055252 | 0.007192 | 0.015541 | 1.1981 | 0.22596 | 0.37698 | 0.5408 | 0.60426 | 0.66773 | 0.73119 | 0.79466 | 0.85812 | 0.92159 | 0.98505 | 1.0485 | 1.112 | 1.1754
Sub-Trans
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 19.6485 | 13.4269 | 23.903 | 12.7745 | 6.769 | 10.2634 | 17.4055 | 2.5378 | 11.8489 | 11.6565
[11 empty] | 9.6075 | 9.5381 | 9.4636 | 9.3944 | 9.325 | 9.2508 | 9.2132 | 9.1535 | 9.1159 | 9.1164 | 9.1149 | [10 empty] | 7.2763 | 6.2314 | 5.1865 | 4.1416 | 3.0966 | 2.0517 | 1.0068 | -0.038146 | -1.0831 | -2.128 | -3.1729
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 2.6136 | 1.2425 | 17.5128 | 0 | 1.0399 | 3.0695 | 2.7689 | 0.00047954 | 0 | 1.1152 | 1.8918 | 1.9252 | 1.9591 | 1.9932 | 2.0297 | 2.0648 | 2.0793 | 2.1072 | 2.1302 | 2.1367 | 2.1365 | 2.6136 | 1.2425 | 17.5128 | 0 | 1.0399 | 3.0695 | 2.7689 | 0.00047954 | 0 | 1.1152 | -0.37731 | -0.97978 | -1.5822 | -2.1847 | -2.7872 | -3.3897 | -3.9921 | -4.5946 | -5.1971 | -5.7995 | -6.402
Egmont | 0.10999 | 0.29352 | 0.6058 | 0 | 0.1878 | 0.066372 | 1.0868 | 0 | 0.49682 | 2.0878 | 0.37907 | 0.38839 | 0.39778 | 0.4096 | 0.41948 | 0.42907 | 0.43365 | 0.4433 | 0.44854 | 0.44764 | 0.44696 | 0.10999 | 0.29352 | 0.6058 | 0 | 0.1878 | 0.066372 | 1.0868 | 0 | 0.49682 | 2.0878 | 1.1379 | 1.2551 | 1.3723 | 1.4895 | 1.6066 | 1.7238 | 1.841 | 1.9581 | 2.0753 | 2.1925 | 2.3097
Kinleith | 0 | 0 | 0 | 1.302 | 0 | 0 | 0 | 0 | 1.2193 | 3.324 | 0.17034 | 0.17112 | 0.17194 | 0.17469 | 0.17764 | 0.17857 | 0.18033 | 0.18256 | 0.18251 | 0.18301 | 0.18358 | 0 | 0 | 0 | 1.302 | 0 | 0 | 0 | 0 | 1.2193 | 3.324 | 1.7361 | 1.9454 | 2.1548 | 2.3642 | 2.5735 | 2.7829 | 2.9923 | 3.2016 | 3.411 | 3.6204 | 3.8297
Manawatu | 0.9919 | 0.41597 | 0.0027271 | 0.036314 | 0.022687 | 1.1329 | 0.40003 | 0 | 0.62319 | 2.1772 | 1.4179 | 1.3657 | 1.3122 | 1.2574 | 1.2042 | 1.1506 | 1.1237 | 1.0815 | 1.0488 | 1.0475 | 1.0467 | 0.9919 | 0.41597 | 0.0027271 | 0.036314 | 0.022687 | 1.1329 | 0.40003 | 0 | 0.62319 | 2.1772 | 1.0572 | 1.1439 | 1.2306 | 1.3173 | 1.404 | 1.4907 | 1.5774 | 1.6641 | 1.7508 | 1.8375 | 1.9242
Mt Maunganui | 0.57316 | 0 | 2.04 | 4.581 | 0 | 0 | 0.17722 | 0.55396 | 3.9411 | 0.075925 | 1.2055 | 1.2222 | 1.2393 | 1.2538 | 1.2725 | 1.2876 | 1.299 | 1.3103 | 1.3219 | 1.3225 | 1.3237 | 0.57316 | 0 | 2.04 | 4.581 | 0 | 0 | 0.17722 | 0.55396 | 3.9411 | 0.075925 | 1.2766 | 1.2916 | 1.3065 | 1.3215 | 1.3365 | 1.3515 | 1.3664 | 1.3814 | 1.3964 | 1.4114 | 1.4263
Rangitikei | 0.078413 | 0.48768 | 0.3915 | 0.012519 | 0.75707 | 3.6139 | 0 | 0.78546 | 0.16298 | 0 | 0.50573 | 0.50028 | 0.49501 | 0.48988 | 0.48537 | 0.48061 | 0.47817 | 0.47686 | 0.47361 | 0.47293 | 0.47248 | 0.078413 | 0.48768 | 0.3915 | 0.012519 | 0.75707 | 3.6139 | 0 | 0.78546 | 0.16298 | 0 | 0.6893 | 0.70027 | 0.71124 | 0.72221 | 0.73319 | 0.74416 | 0.75513 | 0.7661 | 0.77708 | 0.78805 | 0.79902
Taranaki | 0.0077822 | 0 | 0.18228 | 0.40248 | 2.5315 | 0.094372 | 0.55237 | 0.39934 | 0.96452 | 0.90667 | 0.61437 | 0.62227 | 0.6313 | 0.63944 | 0.64735 | 0.65582 | 0.6593 | 0.66554 | 0.67029 | 0.67003 | 0.6691 | 0.0077822 | 0 | 0.18228 | 0.40248 | 2.5315 | 0.094372 | 0.55237 | 0.39934 | 0.96452 | 0.90667 | 1.0688 | 1.1533 | 1.2377 | 1.3222 | 1.4067 | 1.4912 | 1.5757 | 1.6602 | 1.7446 | 1.8291 | 1.9136
Tararua | 0.20089 | 0.27188 | 0.47069 | 0.03829 | 0.11562 | 0.0019586 | 0.39708 | 0.21637 | 0.055702 | 0.87014 | 0.37239 | 0.37298 | 0.37368 | 0.38309 | 0.3843 | 0.38528 | 0.38448 | 0.3844 | 0.39221 | 0.38929 | 0.38658 | 0.20089 | 0.27188 | 0.47069 | 0.03829 | 0.11562 | 0.0019586 | 0.39708 | 0.21637 | 0.055702 | 0.87014 | 0.4039 | 0.42936 | 0.45482 | 0.48028 | 0.50574 | 0.5312 | 0.55667 | 0.58213 | 0.60759 | 0.63305 | 0.65851
Tauranga | 0 | 3.8927 | 0 | 0.61744 | 0.62578 | 1.7475 | 0.080505 | 0 | 0 | 0 | 0.33068 | 0.32727 | 0.32393 | 0.32062 | 0.31724 | 0.31405 | 0.31256 | 0.30988 | 0.30808 | 0.30832 | 0.30868 | 0 | 3.8927 | 0 | 0.61744 | 0.62578 | 1.7475 | 0.080505 | 0 | 0 | 0 | -0.2282 | -0.39631 | -0.56442 | -0.73253 | -0.90064 | -1.0687 | -1.2369 | -1.405 | -1.5731 | -1.7412 | -1.9093
Waikato | 1.2434 | 0.045472 | 0.51264 | 0 | 0 | 0.049739 | 0.058196 | 0 | 0.17563 | 0.065935 | 0.10271 | 0.10204 | 0.10139 | 0.10074 | 0.0999 | 0.099282 | 0.098915 | 0.098399 | 0.097841 | 0.09816 | 0.098251 | 1.2434 | 0.045472 | 0.51264 | 0 | 0 | 0.049739 | 0.058196 | 0 | 0.17563 | 0.065935 | -0.18572 | -0.2586 | -0.33148 | -0.40435 | -0.47723 | -0.55011 | -0.62298 | -0.69586 | -0.76874 | -0.84161 | -0.91449
Waikino | 13.2916 | 5.892 | 0 | 1.8721 | 0 | 0 | 10.9813 | 0 | 3.6164 | 0 | 1.1408 | 1.0663 | 0.98525 | 0.90399 | 0.82333 | 0.74173 | 0.70208 | 0.63612 | 0.58699 | 0.58549 | 0.58715 | 13.2916 | 5.892 | 0 | 1.8721 | 0 | 0 | 10.9813 | 0 | 3.6164 | 0 | -0.04219 | -0.69811 | -1.354 | -2.0099 | -2.6659 | -3.3218 | -3.9777 | -4.6336 | -5.2895 | -5.9454 | -6.6014
Wairarapa | 0.53784 | 0.46251 | 1.3643 | 1.9847 | 1.3967 | 0.37344 | 0.61697 | 0.58221 | 0.35824 | 1.0336 | 1.16 | 1.1662 | 1.1726 | 1.1759 | 1.1805 | 1.1876 | 1.1903 | 1.1926 | 1.1947 | 1.195 | 1.1958 | 0.53784 | 0.46251 | 1.3643 | 1.9847 | 1.3967 | 0.37344 | 0.61697 | 0.58221 | 0.35824 | 1.0336 | 0.6942 | 0.66204 | 0.62989 | 0.59773 | 0.56558 | 0.53342 | 0.50127 | 0.46912 | 0.43696 | 0.40481 | 0.37265
Whanganui | 0 | 0.42273 | 0.82028 | 1.9275 | 0.09187 | 0.11375 | 0.28613 | 0 | 0.23509 | 0 | 0.31624 | 0.30811 | 0.30006 | 0.29208 | 0.28359 | 0.27579 | 0.27137 | 0.26499 | 0.26032 | 0.25982 | 0.25943 | 0 | 0.42273 | 0.82028 | 1.9275 | 0.09187 | 0.11375 | 0.28613 | 0 | 0.23509 | 0 | 0.045833 | -0.016694 | -0.079222 | -0.14175 | -0.20428 | -0.26681 | -0.32933 | -0.39186 | -0.45439 | -0.51692 | -0.57945
The rest of the equipment
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 9.0444 | 15.6301 | 10.7536 | 10.0579 | 11.2957 | 9.554 | 11.0704 | 21.5421 | 7.7417 | 12.8168
[11 empty] | 12.874 | 12.8537 | 12.8268 | 12.8035 | 12.7831 | 12.7566 | 12.7462 | 12.7317 | 12.7124 | 12.7108 | 12.7134 | [10 empty] | 13.0831 | 13.289 | 13.4949 | 13.7007 | 13.9066 | 14.1125 | 14.3184 | 14.5243 | 14.7302 | 14.9361 | 15.142
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 1.7347 | 2.9392 | 0.64869 | 2.3289 | 0.73408 | 0.87117 | 0.16746 | 6.4923 | 0.19608 | 0.27005 | 1.459 | 1.417 | 1.3751 | 1.3331 | 1.2922 | 1.2501 | 1.2271 | 1.193 | 1.1685 | 1.172 | 1.1719 | 1.7347 | 2.9392 | 0.64869 | 2.3289 | 0.73408 | 0.87117 | 0.16746 | 6.4923 | 0.19608 | 0.27005 | 1.3212 | 1.2635 | 1.2059 | 1.1482 | 1.0906 | 1.0329 | 0.97526 | 0.91761 | 0.85995 | 0.8023 | 0.74465
Egmont | 0.012722 | 0.39969 | 0.35566 | 0.17856 | 0.34001 | 0.79685 | 1.8078 | 1.3574 | 0.3531 | 1.0014 | 0.66909 | 0.67983 | 0.69075 | 0.70588 | 0.71767 | 0.72901 | 0.73431 | 0.74673 | 0.75268 | 0.75118 | 0.75004 | 0.012722 | 0.39969 | 0.35566 | 0.17856 | 0.34001 | 0.79685 | 1.8078 | 1.3574 | 0.3531 | 1.0014 | 1.2911 | 1.4058 | 1.5205 | 1.6352 | 1.7499 | 1.8646 | 1.9793 | 2.094 | 2.2087 | 2.3234 | 2.4381
Kinleith | 0.37124 | 0.15856 | 0.70453 | 0.7421 | 0.086605 | 0.069609 | 0.85191 | 0.65558 | 0.28934 | 1.1235 | 0.50078 | 0.49907 | 0.49755 | 0.50168 | 0.50632 | 0.50524 | 0.50838 | 0.51174 | 0.50945 | 0.51083 | 0.51242 | 0.37124 | 0.15856 | 0.70453 | 0.7421 | 0.086605 | 0.069609 | 0.85191 | 0.65558 | 0.28934 | 1.1235 | 0.76375 | 0.81074 | 0.85774 | 0.90473 | 0.95172 | 0.99871 | 1.0457 | 1.0927 | 1.1397 | 1.1867 | 1.2337
Manawatu | 2.2521 | 6.3446 | 4.5114 | 1.895 | 4.1015 | 2.3863 | 2.8607 | 4.868 | 1.6259 | 3.1093 | 3.3633 | 3.3461 | 3.3253 | 3.3007 | 3.2801 | 3.2577 | 3.2463 | 3.2297 | 3.2139 | 3.2101 | 3.2077 | 2.2521 | 6.3446 | 4.5114 | 1.895 | 4.1015 | 2.3863 | 2.8607 | 4.868 | 1.6259 | 3.1093 | 2.6504 | 2.515 | 2.3795 | 2.2441 | 2.1086 | 1.9731 | 1.8377 | 1.7022 | 1.5668 | 1.4313 | 1.2958
Mt Maunganui | 0.084768 | 0.10519 | 0.20151 | 0.60314 | 0.14363 | 0.041433 | 0.36273 | 0.53541 | 0.20653 | 0.6566 | 0.67101 | 0.66753 | 0.66421 | 0.65949 | 0.65693 | 0.65252 | 0.65223 | 0.64827 | 0.64684 | 0.64717 | 0.64775 | 0.084768 | 0.10519 | 0.20151 | 0.60314 | 0.14363 | 0.041433 | 0.36273 | 0.53541 | 0.20653 | 0.6566 | 0.51749 | 0.55811 | 0.59873 | 0.63935 | 0.67997 | 0.72058 | 0.7612 | 0.80182 | 0.84244 | 0.88305 | 0.92367
Rangitikei | 0.21394 | 0.13983 | 0.17113 | 0.2859 | 0.36949 | 0.12791 | 0.43846 | 0.6586 | 0.073725 | 0.37812 | 0.42794 | 0.42756 | 0.4273 | 0.42714 | 0.4275 | 0.42763 | 0.42762 | 0.42995 | 0.42965 | 0.42904 | 0.42862 | 0.21394 | 0.13983 | 0.17113 | 0.2859 | 0.36949 | 0.12791 | 0.43846 | 0.6586 | 0.073725 | 0.37812 | 0.40799 | 0.43022 | 0.45245 | 0.47469 | 0.49692 | 0.51915 | 0.54138 | 0.56362 | 0.58585 | 0.60808 | 0.63031
Taranaki | 1.2468 | 0.625 | 1.0482 | 0.46517 | 0.86166 | 0.35433 | 0.85412 | 2.1769 | 0.88493 | 0.57676 | 0.86725 | 0.86719 | 0.86875 | 0.8691 | 0.86917 | 0.87004 | 0.86948 | 0.86951 | 0.86965 | 0.8693 | 0.8681 | 1.2468 | 0.625 | 1.0482 | 0.46517 | 0.86166 | 0.35433 | 0.85412 | 2.1769 | 0.88493 | 0.57676 | 0.97914 | 0.99182 | 1.0045 | 1.0172 | 1.0299 | 1.0426 | 1.0552 | 1.0679 | 1.0806 | 1.0933 | 1.106
Tararua | 0.041251 | 0.0023842 | 0.073537 | 0.0031408 | 0.23423 | 0.003849 | 0 | 0.0026876 | 0 | 0.057148 | 0.045259 | 0.044862 | 0.044487 | 0.045146 | 0.044838 | 0.044509 | 0.0442 | 0.043848 | 0.04448 | 0.044149 | 0.043842 | 0.041251 | 0.0023842 | 0.073537 | 0.0031408 | 0.23423 | 0.003849 | 0 | 0.0026876 | 0 | 0.057148 | 0.026234 | 0.0234 | 0.020565 | 0.017731 | 0.014897 | 0.012062 | 0.0092281 | 0.0063938 | 0.0035595 | 0.00072517 | -0.0021091
Tauranga | 1.4914 | 3.9875 | 0.31314 | 1.3111 | 2.3994 | 0.8626 | 1.1888 | 2.6083 | 2.0416 | 2.9063 | 2.0115 | 2.0199 | 2.029 | 2.0382 | 2.047 | 2.0572 | 2.063 | 2.0703 | 2.0773 | 2.0789 | 2.0814 | 1.4914 | 3.9875 | 0.31314 | 1.3111 | 2.3994 | 0.8626 | 1.1888 | 2.6083 | 2.0416 | 2.9063 | 2.2005 | 2.2531 | 2.3058 | 2.3584 | 2.411 | 2.4636 | 2.5163 | 2.5689 | 2.6215 | 2.6742 | 2.7268
Waikato | 0.24815 | 0.5945 | 0.21334 | 0.62667 | 0.55398 | 1.167 | 0.36101 | 0.031946 | 0.87146 | 0.80147 | 0.68734 | 0.69277 | 0.6984 | 0.70406 | 0.70845 | 0.71444 | 0.71703 | 0.72172 | 0.724 | 0.72636 | 0.72703 | 0.24815 | 0.5945 | 0.21334 | 0.62667 | 0.55398 | 1.167 | 0.36101 | 0.031946 | 0.87146 | 0.80147 | 0.74121 | 0.77653 | 0.81185 | 0.84717 | 0.88249 | 0.9178 | 0.95312 | 0.98844 | 1.0238 | 1.0591 | 1.0944
Waikino | 1.1302 | 0.12131 | 0.89723 | 0.64034 | 0.76515 | 0.26924 | 1.1357 | 0.62677 | 0.70244 | 1.647 | 1.1636 | 1.177 | 1.1839 | 1.191 | 1.1993 | 1.2068 | 1.2128 | 1.2185 | 1.2237 | 1.2205 | 1.224 | 1.1302 | 0.12131 | 0.89723 | 0.64034 | 0.76515 | 0.26924 | 1.1357 | 0.62677 | 0.70244 | 1.647 | 1.0721 | 1.1227 | 1.1734 | 1.224 | 1.2747 | 1.3253 | 1.376 | 1.4266 | 1.4773 | 1.5279 | 1.5786
Wairarapa | 0.18396 | 0.17547 | 0.92374 | 0.55441 | 0.3534 | 0.39815 | 0.67292 | 0.47699 | 0.11828 | 0.057782 | 0.45007 | 0.4484 | 0.44684 | 0.44405 | 0.44178 | 0.44042 | 0.43944 | 0.43709 | 0.43547 | 0.43559 | 0.43588 | 0.18396 | 0.17547 | 0.92374 | 0.55441 | 0.3534 | 0.39815 | 0.67292 | 0.47699 | 0.11828 | 0.057782 | 0.2792 | 0.25878 | 0.23836 | 0.21794 | 0.19752 | 0.1771 | 0.15668 | 0.13626 | 0.11584 | 0.095416 | 0.074996
Whanganui | 0.033138 | 0.036832 | 0.69149 | 0.42345 | 0.35253 | 2.2056 | 0.36874 | 1.0511 | 0.37835 | 0.2315 | 0.55787 | 0.56646 | 0.5752 | 0.58403 | 0.59179 | 0.60093 | 0.60436 | 0.61133 | 0.61681 | 0.61562 | 0.6147 | 0.033138 | 0.036832 | 0.69149 | 0.42345 | 0.35253 | 2.2056 | 0.36874 | 1.0511 | 0.37835 | 0.2315 | 0.8327 | 0.87915 | 0.92559 | 0.97203 | 1.0185 | 1.0649 | 1.1114 | 1.1578 | 1.2042 | 1.2507 | 1.2971
Vegetation
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 12.2271 | 12.4981 | 14.1164 | 39.4129 | 104.0789 | 13.4909 | 34.3336 | 60.0675 | 13.2679 | 22.9363
[11 empty] | 29.6148 | 29.7083 | 23.8619 | 18.0428 | 15.7446 | 12.7445 | 9.6758 | 8.4527 | 8.4704 | 8.4692 | 8.4665 | [10 empty] | 40.1663 | 41.5342 | 42.9021 | 44.27 | 45.6379 | 47.0058 | 48.3736 | 49.7415 | 51.1094 | 52.4773 | 53.8452
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 2.1973 | 0.86876 | 1.597 | 15.9429 | 2.29 | 0.51337 | 2.9397 | 9.4844 | 1.393 | 2.2123 | 3.4238 | 3.4526 | 3.4823 | 3.5121 | 3.5459 | 2.5055 | 1.4335 | 1.0113 | 1.0175 | 1.0206 | 1.0205 | 2.1973 | 0.86876 | 1.597 | 15.9429 | 2.29 | 0.51337 | 2.9397 | 9.4844 | 1.393 | 2.2123 | 4.0257 | 4.0406 | 4.0555 | 4.0704 | 4.0853 | 4.1002 | 4.115 | 4.1299 | 4.1448 | 4.1597 | 4.1746
Egmont | 0.010281 | 0.24104 | 0 | 1.8105 | 17.9149 | 0.45061 | 0.9244 | 0.91907 | 0.35838 | 0.47068 | 1.8667 | 1.8525 | 1.2845 | 0.73333 | 0.50959 | 0.5063 | 0.50443 | 0.50413 | 0.50164 | 0.50064 | 0.49988 | 0.010281 | 0.24104 | 0 | 1.8105 | 17.9149 | 0.45061 | 0.9244 | 0.91907 | 0.35838 | 0.47068 | 1.9579 | 1.8939 | 1.8299 | 1.7659 | 1.7019 | 1.6378 | 1.5738 | 1.5098 | 1.4458 | 1.3818 | 1.3178
Kinleith | 0.48654 | 0.11504 | 0.15249 | 0.19498 | 0.26753 | 0.12533 | 0.29174 | 0.051226 | 0.084781 | 0.042596 | 0.1985 | 0.19721 | 0.19602 | 0.19706 | 0.19829 | 0.13818 | 0.079212 | 0.055741 | 0.055396 | 0.055546 | 0.05572 | 0.48654 | 0.11504 | 0.15249 | 0.19498 | 0.26753 | 0.12533 | 0.29174 | 0.051226 | 0.084781 | 0.042596 | 0.029042 | 0.0013724 | -0.026297 | -0.053967 | -0.081636 | -0.10931 | -0.13698 | -0.16465 | -0.19231 | -0.21998 | -0.24765
Manawatu | 0.75679 | 0.90552 | 2.1854 | 1.353 | 5.1991 | 0.92071 | 2.4018 | 2.4427 | 1.2948 | 1.2943 | 1.8295 | 1.8339 | 1.2855 | 0.73472 | 0.51433 | 0.51473 | 0.51489 | 0.51541 | 0.51526 | 0.51465 | 0.51426 | 0.75679 | 0.90552 | 2.1854 | 1.353 | 5.1991 | 0.92071 | 2.4018 | 2.4427 | 1.2948 | 1.2943 | 2.1327 | 2.1794 | 2.2262 | 2.273 | 2.3198 | 2.3665 | 2.4133 | 2.4601 | 2.5068 | 2.5536 | 2.6004
Mt Maunganui | 0.62872 | 1.1333 | 0.12046 | 2.3168 | 1.6702 | 0.86068 | 0.68899 | 7.4387 | 0.63949 | 0.96116 | 1.3949 | 1.4022 | 1.4099 | 1.4146 | 1.424 | 0.99898 | 0.57615 | 0.40215 | 0.40382 | 0.40403 | 0.40439 | 0.62872 | 1.1333 | 0.12046 | 2.3168 | 1.6702 | 0.86068 | 0.68899 | 7.4387 | 0.63949 | 0.96116 | 2.6603 | 2.8448 | 3.0292 | 3.2137 | 3.3981 | 3.5826 | 3.767 | 3.9514 | 4.1359 | 4.3203 | 4.5048
Rangitikei | 0.63428 | 0.13653 | 1.9101 | 2.1509 | 5.2096 | 1.5797 | 1.5307 | 2.7019 | 1.1032 | 0.87383 | 1.737 | 1.735 | 1.2135 | 0.69301 | 0.48476 | 0.48478 | 0.48472 | 0.48727 | 0.48687 | 0.48617 | 0.4857 | 0.63428 | 0.13653 | 1.9101 | 2.1509 | 5.2096 | 1.5797 | 1.5307 | 2.7019 | 1.1032 | 0.87383 | 2.0295 | 2.0742 | 2.119 | 2.1638 | 2.2086 | 2.2534 | 2.2982 | 2.343 | 2.3878 | 2.4326 | 2.4774
Taranaki | 2.5915 | 2.4198 | 3.4741 | 5.1048 | 13.6192 | 1.6437 | 7.1747 | 4.0389 | 1.3341 | 5.0941 | 4.3007 | 4.3063 | 3.0171 | 1.7276 | 1.2093 | 1.2122 | 1.2122 | 1.2135 | 1.2147 | 1.2142 | 1.2125 | 2.5915 | 2.4198 | 3.4741 | 5.1048 | 13.6192 | 1.6437 | 7.1747 | 4.0389 | 1.3341 | 5.0941 | 5.0489 | 5.1215 | 5.1941 | 5.2667 | 5.3393 | 5.4119 | 5.4846 | 5.5572 | 5.6298 | 5.7024 | 5.775
Tararua | 0.23071 | 0.17848 | 0.39646 | 0.28527 | 0.88873 | 0.1413 | 0.48785 | 1.3463 | 0.31477 | 1.0069 | 0.48547 | 0.48544 | 0.33991 | 0.19881 | 0.13921 | 0.13935 | 0.13896 | 0.13877 | 0.14147 | 0.14041 | 0.13944 | 0.23071 | 0.17848 | 0.39646 | 0.28527 | 0.88873 | 0.1413 | 0.48785 | 1.3463 | 0.31477 | 1.0069 | 0.94599 | 1.022 | 1.0981 | 1.1742 | 1.2502 | 1.3263 | 1.4023 | 1.4784 | 1.5544 | 1.6305 | 1.7065
Tauranga | 1.3852 | 2.6844 | 0.38272 | 1.2371 | 8.2772 | 1.7377 | 1.334 | 8.7333 | 1.8274 | 1.9162 | 2.6996 | 2.7211 | 2.7434 | 2.7659 | 2.788 | 1.9652 | 1.1332 | 0.79411 | 0.79847 | 0.79909 | 0.80004 | 1.3852 | 2.6844 | 0.38272 | 1.2371 | 8.2772 | 1.7377 | 1.334 | 8.7333 | 1.8274 | 1.9162 | 4.0943 | 4.3021 | 4.5099 | 4.7177 | 4.9255 | 5.1333 | 5.341 | 5.5488 | 5.7566 | 5.9644 | 6.1722
Waikato | 1.3606 | 1.1732 | 0.81453 | 2.4984 | 2.0273 | 0.97943 | 0.49071 | 2.0169 | 0.81607 | 0.96543 | 1.3557 | 1.3669 | 1.3784 | 1.39 | 1.3991 | 0.9885 | 0.56611 | 0.39936 | 0.40069 | 0.40199 | 0.40237 | 1.3606 | 1.1732 | 0.81453 | 2.4984 | 2.0273 | 0.97943 | 0.49071 | 2.0169 | 0.81607 | 0.96543 | 1.0771 | 1.0339 | 0.99082 | 0.9477 | 0.90457 | 0.86145 | 0.81832 | 0.7752 | 0.73208 | 0.68895 | 0.64583
Waikino | 0.53212 | 0.43504 | 1.0428 | 0.82309 | 0.76183 | 0.89437 | 0.20667 | 3.3585 | 0.3161 | 1.1835 | 0.8037 | 0.82012 | 0.83209 | 0.84417 | 0.85717 | 0.6091 | 0.35066 | 0.24844 | 0.25069 | 0.25005 | 0.25076 | 0.53212 | 0.43504 | 1.0428 | 0.82309 | 0.76183 | 0.89437 | 0.20667 | 3.3585 | 0.3161 | 1.1835 | 1.4518 | 1.542 | 1.6323 | 1.7225 | 1.8128 | 1.9031 | 1.9933 | 2.0836 | 2.1738 | 2.2641 | 2.3543
Wairarapa | 0.92189 | 1.966 | 1.3271 | 3.9888 | 8.4589 | 1.3294 | 13.3178 | 15.0977 | 1.6714 | 3.3915 | 5.0014 | 5.0198 | 3.5239 | 2.0219 | 1.4137 | 1.42 | 1.4221 | 1.423 | 1.4242 | 1.4246 | 1.4255 | 0.92189 | 1.966 | 1.3271 | 3.9888 | 8.4589 | 1.3294 | 13.3178 | 15.0977 | 1.6714 | 3.3915 | 8.8095 | 9.4754 | 10.1413 | 10.8072 | 11.4731 | 12.139 | 12.8049 | 13.4708 | 14.1367 | 14.8026 | 15.4685
Whanganui | 0.49117 | 0.24101 | 0.71303 | 1.7064 | 37.4943 | 2.3146 | 2.5445 | 2.4377 | 2.1144 | 3.5239 | 4.5179 | 4.5152 | 3.1554 | 1.8095 | 1.2613 | 1.2618 | 1.2597 | 1.2594 | 1.2598 | 1.2573 | 1.2554 | 0.49117 | 0.24101 | 0.71303 | 1.7064 | 37.4943 | 2.3146 | 2.5445 | 2.4377 | 2.1144 | 3.5239 | 5.9036 | 6.0028 | 6.102 | 6.2012 | 6.3004 | 6.3996 | 6.4988 | 6.598 | 6.6971 | 6.7963 | 6.8955
Adverse Weather
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 158.1165 | 103.7444 | 17.039 | 36.9118 | 43.8584 | 6.527 | 24.4302 | 40.4887 | 9.4636 | 28.3485
[11 empty] | 29.2967 | 28.873 | 28.4424 | 28.0435 | 27.6065 | 27.1739 | 26.9458 | 26.8047 | 26.8437 | 26.815 | 26.8001 | [10 empty] | -12.6207 | -23.4413 | -34.262 | -45.0826 | -55.9032 | -66.7239 | -77.5445 | -88.3652 | -99.1858 | -110.0064 | -120.8271
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 116.2492 | 38.1835 | 1.4169 | 0.95316 | 1.4311 | 0.020421 | 2.948 | 7.7804 | 0.080118 | 1.342 | 2.8883 | 2.4056 | 1.9212 | 1.4347 | 0.94691 | 0.45546 | 0.20843 | 0 | 0 | 0 | 0 | 116.2492 | 38.1835 | 1.4169 | 0.95316 | 1.4311 | 0.020421 | 2.948 | 7.7804 | 0.080118 | 1.342 | -25.1094 | -32.773 | -40.4367 | -48.1003 | -55.7639 | -63.4275 | -71.0911 | -78.7548 | -86.4184 | -94.082 | -101.7456
Egmont | 7.2144 | 2.194 | 2.2587 | 2.6702 | 17.7487 | 0.69721 | 1.0722 | 2.6353 | 0.52445 | 3.0608 | 4.011 | 4 | 3.9907 | 4.0057 | 4.0018 | 3.9957 | 3.9909 | 4.0044 | 3.9965 | 3.9885 | 3.9825 | 7.2144 | 2.194 | 2.2587 | 2.6702 | 17.7487 | 0.69721 | 1.0722 | 2.6353 | 0.52445 | 3.0608 | 1.7066 | 1.2882 | 0.86981 | 0.45144 | 0.033072 | -0.3853 | -0.80367 | -1.222 | -1.6404 | -2.0588 | -2.4772
Kinleith | 0.20975 | 0 | 0.11185 | 0.32798 | 0 | 0.034625 | 0.04502 | 0.087678 | 0.012038 | 0.00761 | 0.18638 | 0.19416 | 0.20186 | 0.21177 | 0.22195 | 0.22957 | 0.23502 | 0.24301 | 0.24669 | 0.24736 | 0.24814 | 0.20975 | 0 | 0.11185 | 0.32798 | 0 | 0.034625 | 0.04502 | 0.087678 | 0.012038 | 0.00761 | -0.0053477 | -0.02153 | -0.037712 | -0.053894 | -0.070077 | -0.086259 | -0.10244 | -0.11862 | -0.13481 | -0.15099 | -0.16717
Manawatu | 0.95596 | 13.2005 | 1.7738 | 2.0798 | 2.3395 | 0.21036 | 1.8257 | 1.5784 | 1.0725 | 4.502 | 2.2249 | 2.2537 | 2.2801 | 2.3036 | 2.3298 | 2.3545 | 2.3667 | 2.3872 | 2.4002 | 2.3973 | 2.3955 | 0.95596 | 13.2005 | 1.7738 | 2.0798 | 2.3395 | 0.21036 | 1.8257 | 1.5784 | 1.0725 | 4.502 | 1.0589 | 0.71432 | 0.36977 | 0.025228 | -0.31932 | -0.66386 | -1.0084 | -1.3529 | -1.6975 | -2.042 | -2.3866
Mt Maunganui | 2.5 | 2.0967 | 1.2651 | 2.1997 | 0.41465 | 0.12378 | 0.10504 | 2.09 | 0.27482 | 0.22664 | 0.73137 | 0.72187 | 0.71252 | 0.70166 | 0.69309 | 0.68256 | 0.67929 | 0.67039 | 0.66532 | 0.66566 | 0.66626 | 2.5 | 2.0967 | 1.2651 | 2.1997 | 0.41465 | 0.12378 | 0.10504 | 2.09 | 0.27482 | 0.22664 | -0.059143 | -0.27529 | -0.49143 | -0.70758 | -0.92372 | -1.1399 | -1.356 | -1.5722 | -1.7883 | -2.0044 | -2.2206
Rangitikei | 1.3984 | 1.8315 | 2.2149 | 3.1488 | 2.6725 | 0.47325 | 3.0536 | 2.5295 | 0.14038 | 2.0822 | 2.6524 | 2.6922 | 2.7326 | 2.7734 | 2.8173 | 2.8595 | 2.8801 | 2.9288 | 2.9515 | 2.9473 | 2.9444 | 1.3984 | 1.8315 | 2.2149 | 3.1488 | 2.6725 | 0.47325 | 3.0536 | 2.5295 | 0.14038 | 2.0822 | 1.7346 | 1.6947 | 1.6547 | 1.6147 | 1.5747 | 1.5348 | 1.4948 | 1.4548 | 1.4148 | 1.3749 | 1.3349
Taranaki | 7.8671 | 3.0035 | 2.5932 | 3.4058 | 7.9745 | 0.94592 | 1.2137 | 2.1293 | 0.61384 | 7.027 | 3.3199 | 3.3415 | 3.3693 | 3.3923 | 3.4141 | 3.439 | 3.4475 | 3.4647 | 3.478 | 3.4766 | 3.4718 | 7.8671 | 3.0035 | 2.5932 | 3.4058 | 7.9745 | 0.94592 | 1.2137 | 2.1293 | 0.61384 | 7.027 | 2.3369 | 2.0932 | 1.8495 | 1.6058 | 1.3621 | 1.1183 | 0.87462 | 0.6309 | 0.38718 | 0.14346 | -0.10025
Tararua | 0.30279 | 0.692 | 0.2765 | 0.61688 | 1.1163 | 0.47347 | 2.2749 | 1.4515 | 0.38054 | 0.74251 | 0.87224 | 0.87953 | 0.88697 | 0.91509 | 0.92368 | 0.93159 | 0.93241 | 0.93653 | 0.95881 | 0.95166 | 0.94504 | 0.30279 | 0.692 | 0.2765 | 0.61688 | 1.1163 | 0.47347 | 2.2749 | 1.4515 | 0.38054 | 0.74251 | 1.2322 | 1.3048 | 1.3774 | 1.4501 | 1.5227 | 1.5953 | 1.6679 | 1.7406 | 1.8132 | 1.8858 | 1.9585
Tauranga | 1.8534 | 6.0623 | 2.9762 | 9.5929 | 0.65044 | 0.062841 | 4.4478 | 6.3585 | 0.67419 | 0.50573 | 3.1386 | 3.1621 | 3.1865 | 3.2112 | 3.2353 | 3.2616 | 3.2759 | 3.2957 | 3.3129 | 3.3155 | 3.3194 | 1.8534 | 6.0623 | 2.9762 | 9.5929 | 0.65044 | 0.062841 | 4.4478 | 6.3585 | 0.67419 | 0.50573 | 1.6865 | 1.3898 | 1.0931 | 0.79639 | 0.49968 | 0.20297 | -0.093741 | -0.39045 | -0.68716 | -0.98387 | -1.2806
Waikato | 5.6258 | 18.8546 | 0.11129 | 1.8333 | 0.81394 | 1.3574 | 1.1153 | 3.7533 | 0.16123 | 0.25415 | 1.418 | 1.3686 | 1.3192 | 1.2696 | 1.2175 | 1.168 | 1.1424 | 1.1023 | 1.0702 | 1.0737 | 1.0747 | 5.6258 | 18.8546 | 0.11129 | 1.8333 | 0.81394 | 1.3574 | 1.1153 | 3.7533 | 0.16123 | 0.25415 | -2.0319 | -3.0174 | -4.0028 | -4.9883 | -5.9737 | -6.9592 | -7.9446 | -8.9301 | -9.9155 | -10.901 | -11.8864
Waikino | 6.9814 | 14.7013 | 0 | 6.3496 | 0.1358 | 0.5293 | 0.64099 | 4.8873 | 0.16826 | 2.2149 | 2.4093 | 2.3565 | 2.29 | 2.2235 | 2.159 | 2.0927 | 2.0632 | 2.0092 | 1.9701 | 1.9651 | 1.9706 | 6.9814 | 14.7013 | 0 | 6.3496 | 0.1358 | 0.5293 | 0.64099 | 4.8873 | 0.16826 | 2.2149 | -0.9033 | -1.7332 | -2.563 | -3.3929 | -4.2227 | -5.0526 | -5.8824 | -6.7123 | -7.5421 | -8.372 | -9.2018
Wairarapa | 5.7149 | 2.7134 | 1.0545 | 1.2274 | 2.1151 | 0.92943 | 3.8751 | 3.8166 | 0.3433 | 1.7186 | 1.9884 | 1.9714 | 1.9549 | 1.9329 | 1.9133 | 1.8975 | 1.8883 | 1.8703 | 1.8574 | 1.8579 | 1.8591 | 5.7149 | 2.7134 | 1.0545 | 1.2274 | 2.1151 | 0.92943 | 3.8751 | 3.8166 | 0.3433 | 1.7186 | 1.2845 | 1.0907 | 0.89678 | 0.7029 | 0.50903 | 0.31515 | 0.12128 | -0.072601 | -0.26648 | -0.46035 | -0.65423
Whanganui | 1.2435 | 0.21102 | 0.98604 | 2.5061 | 6.4458 | 0.66904 | 1.8128 | 1.391 | 5.0179 | 4.6643 | 3.4559 | 3.5259 | 3.5967 | 3.6682 | 3.7328 | 3.8061 | 3.8356 | 3.8921 | 3.9361 | 3.9285 | 3.9226 | 1.2435 | 0.21102 | 0.98604 | 2.5061 | 6.4458 | 0.66904 | 1.8128 | 1.391 | 5.0179 | 4.6643 | 4.4482 | 4.8034 | 5.1586 | 5.5138 | 5.8689 | 6.2241 | 6.5793 | 6.9345 | 7.2897 | 7.6448 | 8
Unknown
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 11.4713 | 23.4565 | 23.8883 | 26.2833 | 26.5732 | 18.5295 | 19.7671 | 29.9752 | 37.5201 | 44.7277
[11 empty] | 36.888 | 38.6894 | 39.3869 | 41.3233 | 43.1557 | 44.911 | 46.5411 | 48.2675 | 50.1021 | 51.6692 | 53.2348 | [10 empty] | 39.5724 | 42.0002 | 44.4281 | 46.8559 | 49.2838 | 51.7116 | 54.1395 | 56.5673 | 58.9952 | 61.423 | 63.8509
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 1.6059 | 1.8348 | 2.7003 | 2.849 | 2.4507 | 2.7544 | 0.53352 | 5.5295 | 1.2349 | 2.8941 | 2.8956 | 2.9561 | 2.9738 | 3.0137 | 3.0572 | 3.1326 | 3.2075 | 3.278 | 3.3385 | 3.3942 | 3.4395 | 1.6059 | 1.8348 | 2.7003 | 2.849 | 2.4507 | 2.7544 | 0.53352 | 5.5295 | 1.2349 | 2.8941 | 2.9353 | 3.0256 | 3.1159 | 3.2062 | 3.2965 | 3.3868 | 3.477 | 3.5673 | 3.6576 | 3.7479 | 3.8382
Egmont | 0.47232 | 1.0319 | 0.86028 | 1.9692 | 2.1032 | 1.0618 | 0.9775 | 3.5592 | 0.68101 | 2.7142 | 2.9389 | 3.1234 | 3.1822 | 3.4073 | 3.6075 | 3.7732 | 3.934 | 4.118 | 4.304 | 4.4808 | 4.659 | 0.47232 | 1.0319 | 0.86028 | 1.9692 | 2.1032 | 1.0618 | 0.9775 | 3.5592 | 0.68101 | 2.7142 | 2.4497 | 2.6145 | 2.7794 | 2.9442 | 3.1091 | 3.2739 | 3.4388 | 3.6036 | 3.7684 | 3.9333 | 4.0981
Kinleith | 0.95651 | 0.29978 | 0.18124 | 0.2668 | 0.066124 | 1.3893 | 0.44275 | 0.52693 | 0.17329 | 1.6861 | 0.68644 | 0.70148 | 0.69728 | 0.71071 | 0.72498 | 0.74564 | 0.77953 | 0.80682 | 0.82136 | 0.84314 | 0.86538 | 0.95651 | 0.29978 | 0.18124 | 0.2668 | 0.066124 | 1.3893 | 0.44275 | 0.52693 | 0.17329 | 1.6861 | 0.90754 | 0.96366 | 1.0198 | 1.0759 | 1.132 | 1.1881 | 1.2443 | 1.3004 | 1.3565 | 1.4126 | 1.4688
Manawatu | 1.332 | 2.2679 | 3.8878 | 4.6383 | 4.686 | 2.3654 | 4.0612 | 5.4945 | 2.1316 | 3.5713 | 4.0702 | 4.1986 | 4.2573 | 4.3879 | 4.5192 | 4.6316 | 4.7297 | 4.8395 | 4.9522 | 5.0443 | 5.1385 | 1.332 | 2.2679 | 3.8878 | 4.6383 | 4.686 | 2.3654 | 4.0612 | 5.4945 | 2.1316 | 3.5713 | 4.2163 | 4.3568 | 4.4973 | 4.6378 | 4.7783 | 4.9188 | 5.0593 | 5.1998 | 5.3403 | 5.4808 | 5.6213
Mt Maunganui | 0.36636 | 1.635 | 0.44909 | 0.21515 | 0.71229 | 0.3191 | 0.48245 | 0.45148 | 2.0198 | 0.38639 | 1.1072 | 1.1685 | 1.1767 | 1.2096 | 1.247 | 1.3227 | 1.4156 | 1.4888 | 1.5523 | 1.609 | 1.6664 | 0.36636 | 1.635 | 0.44909 | 0.21515 | 0.71229 | 0.3191 | 0.48245 | 0.45148 | 2.0198 | 0.38639 | 0.81353 | 0.8335 | 0.85347 | 0.87343 | 0.8934 | 0.91337 | 0.93334 | 0.9533 | 0.97327 | 0.99324 | 1.0132
Rangitikei | 0.41593 | 0.84974 | 1.5129 | 1.5658 | 1.6516 | 0.58697 | 0.69724 | 1.1947 | 1.8536 | 2.8159 | 2.291 | 2.4253 | 2.4649 | 2.6139 | 2.7581 | 2.8763 | 2.9936 | 3.128 | 3.263 | 3.395 | 3.5283 | 0.41593 | 0.84974 | 1.5129 | 1.5658 | 1.6516 | 0.58697 | 0.69724 | 1.1947 | 1.8536 | 2.8159 | 2.0933 | 2.2349 | 2.3765 | 2.5182 | 2.6598 | 2.8014 | 2.943 | 3.0846 | 3.2262 | 3.3678 | 3.5094
Taranaki | 1.9965 | 1.5862 | 2.851 | 3.0362 | 3.8171 | 2.3639 | 4.919 | 3.0054 | 4.1624 | 7.4175 | 5.4208 | 5.7133 | 5.8336 | 6.1603 | 6.4723 | 6.7443 | 6.9903 | 7.2527 | 7.5485 | 7.8186 | 8.0804 | 1.9965 | 1.5862 | 2.851 | 3.0362 | 3.8171 | 2.3639 | 4.919 | 3.0054 | 4.1624 | 7.4175 | 5.9085 | 6.3436 | 6.7787 | 7.2138 | 7.6489 | 8.084 | 8.519 | 8.9541 | 9.3892 | 9.8243 | 10.2594
Tararua | 0.4333 | 0.88304 | 0.44829 | 0.5062 | 1.6089 | 0.39808 | 0.090545 | 1.3949 | 1.9808 | 1.2238 | 1.5579 | 1.6134 | 1.6143 | 1.7142 | 1.7726 | 1.8148 | 1.8613 | 1.9018 | 1.9973 | 2.0561 | 2.115 | 0.4333 | 0.88304 | 0.44829 | 0.5062 | 1.6089 | 0.39808 | 0.090545 | 1.3949 | 1.9808 | 1.2238 | 1.4659 | 1.5694 | 1.6729 | 1.7763 | 1.8798 | 1.9833 | 2.0868 | 2.1903 | 2.2937 | 2.3972 | 2.5007
Tauranga | 1.5851 | 2.3089 | 5.6355 | 4.6606 | 2.8457 | 1.9975 | 3.7379 | 0.94947 | 1.9711 | 10.3669 | 3.8454 | 3.9551 | 4.0254 | 4.1175 | 4.2098 | 4.339 | 4.4469 | 4.5615 | 4.6555 | 4.7049 | 4.7563 | 1.5851 | 2.3089 | 5.6355 | 4.6606 | 2.8457 | 1.9975 | 3.7379 | 0.94947 | 1.9711 | 10.3669 | 5.26 | 5.5608 | 5.8615 | 6.1623 | 6.463 | 6.7638 | 7.0646 | 7.3653 | 7.6661 | 7.9668 | 8.2676
Waikato | 0.58628 | 1.3003 | 1.8789 | 2.6489 | 0.85175 | 0.86353 | 0.41502 | 0.41392 | 3.3063 | 1.1916 | 1.3124 | 1.3085 | 1.3105 | 1.3098 | 1.3067 | 1.3023 | 1.2941 | 1.2891 | 1.2826 | 1.2812 | 1.2768 | 0.58628 | 1.3003 | 1.8789 | 2.6489 | 0.85175 | 0.86353 | 0.41502 | 0.41392 | 3.3063 | 1.1916 | 1.5281 | 1.5613 | 1.5945 | 1.6277 | 1.6609 | 1.694 | 1.7272 | 1.7604 | 1.7936 | 1.8268 | 1.8599
Waikino | 0.7536 | 6.5912 | 0.51774 | 0.24067 | 1.1062 | 0.10057 | 0.23562 | 0.34794 | 0.87325 | 1.2092 | 1.09 | 1.1123 | 1.1046 | 1.1087 | 1.1138 | 1.1352 | 1.1691 | 1.1903 | 1.2089 | 1.2285 | 1.2547 | 0.7536 | 6.5912 | 0.51774 | 0.24067 | 1.1062 | 0.10057 | 0.23562 | 0.34794 | 0.87325 | 1.2092 | -0.062243 | -0.29131 | -0.52037 | -0.74943 | -0.97849 | -1.2076 | -1.4366 | -1.6657 | -1.8947 | -2.1238 | -2.3529
Wairarapa | 0.90432 | 1.9851 | 1.6368 | 2.2959 | 3.0801 | 1.1401 | 1.2038 | 2.91 | 3.2357 | 4.557 | 3.7343 | 3.9715 | 4.0727 | 4.326 | 4.5764 | 4.8027 | 5.0035 | 5.2107 | 5.4437 | 5.6556 | 5.87 | 0.90432 | 1.9851 | 1.6368 | 2.2959 | 3.0801 | 1.1401 | 1.2038 | 2.91 | 3.2357 | 4.557 | 3.7208 | 3.9801 | 4.2394 | 4.4986 | 4.7579 | 5.0172 | 5.2764 | 5.5357 | 5.795 | 6.0542 | 6.3135
Whanganui | 0.063208 | 0.88265 | 1.3286 | 1.3906 | 1.5934 | 3.1888 | 1.9706 | 4.1974 | 13.8962 | 4.6937 | 5.9379 | 6.4418 | 6.6736 | 7.2435 | 7.7903 | 8.2908 | 8.716 | 9.2023 | 9.7345 | 10.158 | 10.5845 | 0.063208 | 0.88265 | 1.3286 | 1.3906 | 1.5934 | 3.1888 | 1.9706 | 4.1974 | 13.8962 | 4.6937 | 8.3355 | 9.2473 | 10.1591 | 11.0709 | 11.9827 | 12.8946 | 13.8064 | 14.7182 | 15.63 | 16.5418 | 17.4536
The remainder
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 40.0427 | 36.5469 | 58.5777 | 27.0018 | 34.9459 | 22.5603 | 23.5778 | 19.4781 | 41.3476 | 29.4602
[11 empty] | 32.3078 | 32.4522 | 32.5961 | 32.7481 | 32.8931 | 33.0438 | 33.1126 | 33.2355 | 33.3242 | 33.3269 | 33.3291 | [10 empty] | 24.0275 | 22.3318 | 20.6361 | 18.9403 | 17.2446 | 15.5489 | 13.8532 | 12.1575 | 10.4618 | 8.7661 | 7.0704
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 6.1472 | 1.9168 | 29.6324 | 0.90547 | 2.2029 | 1.546 | 2.025 | 1.0866 | 1.9742 | 1.6542 | 4.1204 | 4.0872 | 4.0547 | 4.0221 | 3.9936 | 3.962 | 3.9401 | 3.9138 | 3.8978 | 3.9097 | 3.9094 | 6.1472 | 1.9168 | 29.6324 | 0.90547 | 2.2029 | 1.546 | 2.025 | 1.0866 | 1.9742 | 1.6542 | -1.093 | -2.1843 | -3.2756 | -4.3669 | -5.4582 | -6.5495 | -7.6408 | -8.7321 | -9.8234 | -10.9147 | -12.006
Egmont | 0.50405 | 1.5481 | 1.9121 | 0.92725 | 0.88209 | 1.1166 | 1.7522 | 0.70394 | 1.3139 | 2.388 | 1.344 | 1.3377 | 1.3318 | 1.3342 | 1.3302 | 1.3255 | 1.3226 | 1.3249 | 1.3207 | 1.3181 | 1.3161 | 0.50405 | 1.5481 | 1.9121 | 0.92725 | 0.88209 | 1.1166 | 1.7522 | 0.70394 | 1.3139 | 2.388 | 1.7043 | 1.7769 | 1.8496 | 1.9222 | 1.9948 | 2.0675 | 2.1401 | 2.2127 | 2.2854 | 2.358 | 2.4306
Kinleith | 2.2628 | 0.23399 | 0.10205 | 1.8797 | 0.13422 | 0.35341 | 0.64798 | 0.48451 | 0.35042 | 1.4332 | 0.82171 | 0.809 | 0.7968 | 0.79372 | 0.79142 | 0.78022 | 0.78032 | 0.77791 | 0.76884 | 0.77092 | 0.77333 | 2.2628 | 0.23399 | 0.10205 | 1.8797 | 0.13422 | 0.35341 | 0.64798 | 0.48451 | 0.35042 | 1.4332 | 0.51439 | 0.46461 | 0.41482 | 0.36503 | 0.31524 | 0.26545 | 0.21567 | 0.16588 | 0.11609 | 0.066301 | 0.016513
Manawatu | 7.0732 | 7.0137 | 4.2327 | 3.1057 | 1.3964 | 2.3089 | 1.6461 | 1.8165 | 1.1428 | 3.1019 | 2.81 | 2.7788 | 2.7448 | 2.7077 | 2.6739 | 2.6387 | 2.621 | 2.594 | 2.5711 | 2.568 | 2.5661 | 7.0732 | 7.0137 | 4.2327 | 3.1057 | 1.3964 | 2.3089 | 1.6461 | 1.8165 | 1.1428 | 3.1019 | 0.20425 | -0.35566 | -0.91558 | -1.4755 | -2.0354 | -2.5953 | -3.1552 | -3.7152 | -4.2751 | -4.835 | -5.3949
Mt Maunganui | 3.7207 | 2.3688 | 2.497 | 0.58901 | 1.8422 | 1.5299 | 0.92168 | 0.99422 | 0.61512 | 1.0154 | 1.4267 | 1.4345 | 1.4426 | 1.4477 | 1.4576 | 1.4634 | 1.4706 | 1.4743 | 1.4806 | 1.4813 | 1.4827 | 3.7207 | 2.3688 | 2.497 | 0.58901 | 1.8422 | 1.5299 | 0.92168 | 0.99422 | 0.61512 | 1.0154 | 0.16104 | -0.1023 | -0.36564 | -0.62898 | -0.89232 | -1.1557 | -1.419 | -1.6823 | -1.9457 | -2.209 | -2.4724
Rangitikei | 0.7494 | 0.64289 | 2.4605 | 0.84358 | 1.0779 | 1.1848 | 0.84195 | 0.62023 | 1.7672 | 1.5853 | 1.3268 | 1.3152 | 1.304 | 1.2931 | 1.2839 | 1.274 | 1.2689 | 1.2676 | 1.2606 | 1.2588 | 1.2576 | 0.7494 | 0.64289 | 2.4605 | 0.84358 | 1.0779 | 1.1848 | 0.84195 | 0.62023 | 1.7672 | 1.5853 | 1.3871 | 1.4253 | 1.4634 | 1.5016 | 1.5397 | 1.5778 | 1.616 | 1.6541 | 1.6923 | 1.7304 | 1.7685
Taranaki | 4.1764 | 4.0705 | 2.3986 | 2.1841 | 3.3628 | 3.2715 | 3.6995 | 4.945 | 5.6345 | 5.375 | 4.0192 | 4.0696 | 4.1274 | 4.1793 | 4.2297 | 4.2837 | 4.3059 | 4.3456 | 4.376 | 4.3742 | 4.3682 | 4.1764 | 4.0705 | 2.3986 | 2.1841 | 3.3628 | 3.2715 | 3.6995 | 4.945 | 5.6345 | 5.375 | 5.2092 | 5.4451 | 5.681 | 5.9169 | 6.1527 | 6.3886 | 6.6245 | 6.8604 | 7.0963 | 7.3322 | 7.5681
Tararua | 0.27452 | 0.10898 | 0.13421 | 0.20412 | 0.10856 | 0.22489 | 0.23111 | 0.43852 | 0.37499 | 0.25639 | 0.31827 | 0.31357 | 0.30908 | 0.31176 | 0.30775 | 0.30362 | 0.30059 | 0.29674 | 0.29991 | 0.29767 | 0.2956 | 0.27452 | 0.10898 | 0.13421 | 0.20412 | 0.10856 | 0.22489 | 0.23111 | 0.43852 | 0.37499 | 0.25639 | 0.34956 | 0.37027 | 0.39098 | 0.4117 | 0.43241 | 0.45313 | 0.47384 | 0.49455 | 0.51527 | 0.53598 | 0.5567
Tauranga | 8.2142 | 9.9203 | 4.4736 | 9.4667 | 12.7687 | 2.7426 | 4.2477 | 3.3453 | 6.8835 | 3.979 | 6.4017 | 6.3982 | 6.3963 | 6.395 | 6.3926 | 6.3941 | 6.3971 | 6.3958 | 6.3993 | 6.4043 | 6.4119 | 8.2142 | 9.9203 | 4.4736 | 9.4667 | 12.7687 | 2.7426 | 4.2477 | 3.3453 | 6.8835 | 3.979 | 3.5809 | 3.0312 | 2.4815 | 1.9318 | 1.3821 | 0.83239 | 0.2827 | -0.267 | -0.81669 | -1.3664 | -1.9161
Waikato | 3.3063 | 3.796 | 2.5361 | 3.3997 | 3.991 | 1.4503 | 0.95399 | 0.79435 | 3.0923 | 1.0203 | 2.3312 | 2.3339 | 2.3371 | 2.3404 | 2.3394 | 2.3436 | 2.3443 | 2.3473 | 2.3455 | 2.3531 | 2.3553 | 3.3063 | 3.796 | 2.5361 | 3.3997 | 3.991 | 1.4503 | 0.95399 | 0.79435 | 3.0923 | 1.0203 | 0.96447 | 0.69728 | 0.43009 | 0.1629 | -0.10429 | -0.37149 | -0.63868 | -0.90587 | -1.1731 | -1.4403 | -1.7074
Waikino | 0.52483 | 1.1496 | 2.3584 | 0.40362 | 1.4735 | 2.29 | 1.0399 | 0.70436 | 5.9808 | 2.3258 | 2.086 | 2.1349 | 2.1723 | 2.2101 | 2.2503 | 2.2891 | 2.3128 | 2.3433 | 2.3681 | 2.3621 | 2.3687 | 0.52483 | 1.1496 | 2.3584 | 0.40362 | 1.4735 | 2.29 | 1.0399 | 0.70436 | 5.9808 | 2.3258 | 3.3078 | 3.5774 | 3.847 | 4.1166 | 4.3862 | 4.6558 | 4.9254 | 5.195 | 5.4646 | 5.7342 | 6.0038
Wairarapa | 1.4123 | 2.9891 | 1.4753 | 1.5507 | 2.8377 | 2.3414 | 2.151 | 1.3211 | 1.1208 | 2.4095 | 2.1237 | 2.1458 | 2.1685 | 2.1853 | 2.2046 | 2.2286 | 2.2391 | 2.2519 | 2.2622 | 2.2628 | 2.2643 | 1.4123 | 2.9891 | 1.4753 | 1.5507 | 2.8377 | 2.3414 | 2.151 | 1.3211 | 1.1208 | 2.4095 | 1.8419 | 1.8202 | 1.7986 | 1.7769 | 1.7553 | 1.7337 | 1.712 | 1.6904 | 1.6687 | 1.6471 | 1.6254
Whanganui | 1.6767 | 0.78813 | 4.3647 | 1.5421 | 2.8679 | 2.2 | 3.4199 | 2.2235 | 11.0972 | 2.9164 | 3.178 | 3.2939 | 3.4106 | 3.5278 | 3.6383 | 3.7572 | 3.8094 | 3.9023 | 3.9736 | 3.9659 | 3.96 | 1.6767 | 0.78813 | 4.3647 | 1.5421 | 2.8679 | 2.2 | 3.4199 | 2.2235 | 11.0972 | 2.9164 | 5.8956 | 6.3658 | 6.836 | 7.3062 | 7.7764 | 8.2465 | 8.7167 | 9.1869 | 9.6571 | 10.1272 | 10.5974
Totals
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 289.1515 | 236.2655 | 184.2754 | 217.6434 | 300.9311 | 115.7691 | 190.3603 | 231.7952 | 171.9007 | 196.1955
[11 empty] | 208.8175 | 210.8408 | 205.4531 | 201.1463 | 199.7925 | 197.4009 | 195.0392 | 195.4051 | 197.2708 | 198.5241 | 200.1069 | [10 empty] | 169.5431 | 161.5639 | 153.5847 | 145.6054 | 137.6262 | 129.647 | 121.6678 | 113.6886 | 105.7094 | 97.7302 | 89.751
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 132.9914 | 49.3572 | 56.9888 | 26.4071 | 11.5739 | 11.6154 | 15.3721 | 35.4605 | 10.3027 | 11.8198 | 20.6005 | 20.3103 | 19.9501 | 19.6304 | 19.3311 | 17.95 | 16.7993 | 16.3571 | 16.4967 | 16.6394 | 16.7403 | 132.9914 | 49.3572 | 56.9888 | 26.4071 | 11.5739 | 11.6154 | 15.3721 | 35.4605 | 10.3027 | 11.8198 | -13.9655 | -23.0844 | -32.2034 | -41.3224 | -50.4414 | -59.5603 | -68.6793 | -77.7983 | -86.9173 | -96.0362 | -105.1552
Egmont | 11.2832 | 7.9602 | 9.9743 | 10.6923 | 51.4375 | 7.3218 | 12.8942 | 15.089 | 8.1161 | 17.6215 | 16.4465 | 16.5925 | 15.9779 | 15.3612 | 15.1423 | 15.2675 | 15.3444 | 15.6777 | 15.8348 | 15.9411 | 16.1152 | 11.2832 | 7.9602 | 9.9743 | 10.6923 | 51.4375 | 7.3218 | 12.8942 | 15.089 | 8.1161 | 17.6215 | 16.779 | 17.059 | 17.339 | 17.619 | 17.899 | 18.1789 | 18.4589 | 18.7389 | 19.0189 | 19.2989 | 19.5789
Kinleith | 5.049 | 0.98924 | 1.6156 | 5.0477 | 0.85444 | 2.4192 | 2.3217 | 2.0615 | 2.4533 | 8.3072 | 2.9359 | 2.9525 | 2.9491 | 2.9902 | 3.0285 | 2.9898 | 2.9801 | 3.0022 | 3.0074 | 3.0351 | 3.0617 | 5.049 | 0.98924 | 1.6156 | 5.0477 | 0.85444 | 2.4192 | 2.3217 | 2.0615 | 2.4533 | 8.3072 | 4.2848 | 4.4981 | 4.7113 | 4.9246 | 5.1379 | 5.3511 | 5.5644 | 5.7776 | 5.9909 | 6.2042 | 6.4174
Manawatu | 17.2664 | 32.2233 | 21.4401 | 23.0571 | 25.0794 | 13.4923 | 17.5641 | 23.4815 | 10.8488 | 23.6391 | 22.2256 | 22.4838 | 22.0941 | 21.6736 | 21.621 | 21.6389 | 21.7563 | 21.9749 | 22.1202 | 22.2541 | 22.3736 | 17.2664 | 32.2233 | 21.4401 | 23.0571 | 25.0794 | 13.4923 | 17.5641 | 23.4815 | 10.8488 | 23.6391 | 17.1383 | 16.4709 | 15.8035 | 15.136 | 14.4686 | 13.8012 | 13.1338 | 12.4663 | 11.7989 | 11.1315 | 10.464
Mt Maunganui | 9.8255 | 9.5444 | 9.6118 | 16.2945 | 7.0799 | 4.3347 | 3.2287 | 13.7456 | 10.5168 | 4.3707 | 9.018 | 9.1134 | 9.127 | 9.158 | 9.0582 | 8.5729 | 7.9941 | 7.6555 | 7.6985 | 7.7047 | 7.7576 | 9.8255 | 9.5444 | 9.6118 | 16.2945 | 7.0799 | 4.3347 | 3.2287 | 13.7456 | 10.5168 | 4.3707 | 6.7366 | 6.3514 | 5.9662 | 5.581 | 5.1958 | 4.8106 | 4.4254 | 4.0402 | 3.655 | 3.2698 | 2.8846
Rangitikei | 4.9686 | 5.442 | 10.5263 | 11.9959 | 18.109 | 9.5767 | 10.135 | 12.7829 | 9.2257 | 10.4047 | 13.9057 | 14.0147 | 13.464 | 13.1242 | 13.1014 | 13.2313 | 13.3546 | 13.5857 | 13.7208 | 13.8471 | 13.9858 | 4.9686 | 5.442 | 10.5263 | 11.9959 | 18.109 | 9.5767 | 10.135 | 12.7829 | 9.2257 | 10.4047 | 12.736 | 13.1759 | 13.6158 | 14.0556 | 14.4955 | 14.9354 | 15.3753 | 15.8151 | 16.255 | 16.6949 | 17.1348
Taranaki | 22.5726 | 16.7904 | 18.5308 | 25.8586 | 51.5883 | 12.6801 | 31.0131 | 24.0875 | 21.1303 | 35.9654 | 28.896 | 29.2591 | 28.1201 | 27.0402 | 26.5507 | 26.5141 | 26.5212 | 26.6831 | 26.8621 | 26.8751 | 27.0426 | 22.5726 | 16.7904 | 18.5308 | 25.8586 | 51.5883 | 12.6801 | 31.0131 | 24.0875 | 21.1303 | 35.9654 | 31.1968 | 32.1377 | 33.0787 | 34.0196 | 34.9605 | 35.9015 | 36.8424 | 37.7833 | 38.7242 | 39.6652 | 40.6061
Tararua | 3.7486 | 3.9572 | 2.8394 | 3.8309 | 8.8513 | 3.4763 | 6.2354 | 9.1617 | 6.653 | 7.2476 | 6.8324 | 6.9144 | 6.7959 | 6.8866 | 6.9345 | 6.9994 | 7.0765 | 7.2043 | 7.4514 | 7.475 | 7.5346 | 3.7486 | 3.9572 | 2.8394 | 3.8309 | 8.8513 | 3.4763 | 6.2354 | 9.1617 | 6.653 | 7.2476 | 8.3938 | 8.9018 | 9.4097 | 9.9177 | 10.4256 | 10.9336 | 11.4415 | 11.9495 | 12.4574 | 12.9654 | 13.4733
Tauranga | 19.6364 | 32.5105 | 15.0079 | 35.1273 | 31.8193 | 12.2358 | 18.7507 | 28.1615 | 18.7194 | 22.9076 | 23.3897 | 23.5286 | 23.579 | 23.7287 | 23.6767 | 22.769 | 21.7417 | 21.1909 | 21.2718 | 21.3125 | 21.4007 | 19.6364 | 32.5105 | 15.0079 | 35.1273 | 31.8193 | 12.2358 | 18.7507 | 28.1615 | 18.7194 | 22.9076 | 21.1529 | 20.7284 | 20.3039 | 19.8794 | 19.4549 | 19.0304 | 18.6059 | 18.1814 | 17.7569 | 17.3324 | 16.9079
Waikato | 15.259 | 29.8694 | 8.3271 | 14.9669 | 10.8447 | 9.0734 | 4.4662 | 9.8408 | 13.7139 | 5.3412 | 10.8008 | 10.7889 | 10.7906 | 10.7759 | 10.762 | 10.3201 | 9.9383 | 9.7805 | 9.7151 | 9.7649 | 9.7528 | 15.259 | 29.8694 | 8.3271 | 14.9669 | 10.8447 | 9.0734 | 4.4662 | 9.8408 | 13.7139 | 5.3412 | 4.5685 | 3.1864 | 1.8042 | 0.42208 | -0.96006 | -2.3422 | -3.7243 | -5.1065 | -6.4886 | -7.8708 | -9.2529
Waikino | 29.2979 | 30.0178 | 8.9444 | 11.6252 | 5.2097 | 6.809 | 17.1481 | 11.9442 | 13.0788 | 9.758 | 10.8974 | 10.937 | 10.8918 | 10.8531 | 10.8283 | 10.5376 | 10.3033 | 10.1726 | 10.1468 | 10.1659 | 10.2164 | 29.2979 | 30.0178 | 8.9444 | 11.6252 | 5.2097 | 6.809 | 17.1481 | 11.9442 | 13.0788 | 9.758 | 5.6745 | 4.091 | 2.5076 | 0.92417 | -0.65926 | -2.2427 | -3.8261 | -5.4095 | -6.993 | -8.5764 | -10.1598
Wairarapa | 11.9999 | 14.0106 | 9.4191 | 16.4151 | 21.9397 | 9.5668 | 35.7579 | 28.6744 | 10.6255 | 18.687 | 19.9868 | 20.2719 | 18.8996 | 17.6727 | 17.2985 | 17.5757 | 17.7499 | 17.9752 | 18.216 | 18.4848 | 18.7318 | 11.9999 | 14.0106 | 9.4191 | 16.4151 | 21.9397 | 9.5668 | 35.7579 | 28.6744 | 10.6255 | 18.687 | 23.6569 | 24.7383 | 25.8196 | 26.901 | 27.9823 | 29.0636 | 30.145 | 31.2263 | 32.3076 | 33.389 | 34.4703
Whanganui | 5.2531 | 3.5933 | 11.0498 | 16.3245 | 56.5442 | 13.1678 | 15.4731 | 17.3041 | 36.5164 | 20.1256 | 22.8822 | 23.6737 | 22.814 | 22.2516 | 22.4593 | 23.0345 | 23.4794 | 24.1454 | 24.7292 | 25.0245 | 25.394 | 5.2531 | 3.5933 | 11.0498 | 16.3245 | 56.5442 | 13.1678 | 15.4731 | 17.3041 | 36.5164 | 20.1256 | 31.1903 | 33.3095 | 35.4286 | 37.5477 | 39.6668 | 41.7859 | 43.9051 | 46.0242 | 48.1433 | 50.2624 | 52.3815

## SAIFI
Forecast SAIFI
| SAIFI | [20 empty] | Linear trend
| 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Poles
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.0075501 | 0.012226 | 0.0076789 | 0.023361 | 0.016016 | 0.019236 | 0.017614 | 0.014344 | 0.019936 | 0.0048574
[11 empty] | 0.013951 | 0.013968 | 0.013525 | 0.013126 | 0.012722 | 0.012293 | 0.011832 | 0.011449 | 0.011199 | 0.011004 | 0.010719 | [10 empty] | 0.015916 | 0.016213 | 0.016511 | 0.016808 | 0.017105 | 0.017402 | 0.017699 | 0.017996 | 0.018293 | 0.018591 | 0.018888
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0 | 0.0019265 | 0.00095749 | 0.00027953 | 0.0001125 | 9.3121e-06 | 0.00091471 | 0.0024374 | 0.0057935 | 0 | 0.00089874 | 0.00090615 | 0.00091262 | 0.00092182 | 0.00095632 | 0.00097655 | 0.00099189 | 0.001009 | 0.0010262 | 0.0010461 | 0.0010634 | 0 | 0.0019265 | 0.00095749 | 0.00027953 | 0.0001125 | 9.3121e-06 | 0.00091471 | 0.0024374 | 0.0057935 | 0 | 0.0024521 | 0.002672 | 0.0028918 | 0.0031116 | 0.0033315 | 0.0035513 | 0.0037711 | 0.0039909 | 0.0042108 | 0.0044306 | 0.0046504
Egmont | 0.0011572 | 0.00079157 | 0.000158 | 4.7112e-05 | 0.0017532 | 0 | 0.00014167 | 6.1088e-06 | 0.0018294 | 0.0011559 | 0.00025333 | 0.00015998 | 0.0001336 | 0.00011149 | 0.00012423 | 0.00013089 | 0.00013667 | 0.00014971 | 0.00016405 | 0.00017701 | 0.00019027 | 0.0011572 | 0.00079157 | 0.000158 | 4.7112e-05 | 0.0017532 | 0 | 0.00014167 | 6.1088e-06 | 0.0018294 | 0.0011559 | 0.00087151 | 0.00090196 | 0.00093241 | 0.00096287 | 0.00099332 | 0.0010238 | 0.0010542 | 0.0010847 | 0.0011151 | 0.0011456 | 0.001176
Kinleith | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022878 | 0 | 0 | 0.00022645 | 0.00023063 | 0.0002367 | 0.00024533 | 0.00025064 | 0.00025461 | 0.00026342 | 0.00027104 | 0.00027621 | 0.00029494 | 0.00030948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022878 | 0 | 0 | 0.00061007 | 0.0006794 | 0.00074872 | 0.00081805 | 0.00088737 | 0.0009567 | 0.001026 | 0.0010954 | 0.0011647 | 0.001234 | 0.0013033
Manawatu | 0 | 0.00041645 | 0.0023289 | 0.010974 | 0 | 0.0051961 | 9.2395e-06 | 9.1633e-06 | 0.00022073 | 0 | 0.0013879 | 0.0016882 | 0.0019007 | 0.0019755 | 0.0020027 | 0.0020799 | 0.0020368 | 0.0020042 | 0.001975 | 0.0018974 | 0.0018149 | 0 | 0.00041645 | 0.0023289 | 0.010974 | 0 | 0.0051961 | 9.2395e-06 | 9.1633e-06 | 0.00022073 | 0 | 0.0005599 | 0.00031343 | 6.6965e-05 | -0.0001795 | -0.00042597 | -0.00067244 | -0.0009189 | -0.0011654 | -0.0014118 | -0.0016583 | -0.0019048
Mt Maunganui | 0 | 0.0001367 | 0.001757 | 0.0018939 | 0.0010407 | 0.00045008 | 0 | 0 | 3.9309e-05 | 0 | 0.00056248 | 0.00057272 | 0.00058242 | 0.00056614 | 0.00055979 | 0.00046298 | 0.00040655 | 0.0003753 | 0.00035208 | 0.00033469 | 0.00031715 | 0 | 0.0001367 | 0.001757 | 0.0018939 | 0.0010407 | 0.00045008 | 0 | 0 | 3.9309e-05 | 0 | 7.1342e-06 | -8.8253e-05 | -0.00018364 | -0.00027903 | -0.00037442 | -0.0004698 | -0.00056519 | -0.00066058 | -0.00075596 | -0.00085135 | -0.00094674
Rangitikei | 0.00057858 | 0.0025305 | 0 | 0.00018531 | 0.00030314 | 0.00048733 | 0.00055745 | 0.00047649 | 0.00020864 | 3.2942e-05 | 0.0010866 | 0.0011131 | 0.0010036 | 0.00099125 | 0.00092348 | 0.00084549 | 0.00077217 | 0.00071032 | 0.00069434 | 0.00070658 | 0.00068452 | 0.00057858 | 0.0025305 | 0 | 0.00018531 | 0.00030314 | 0.00048733 | 0.00055745 | 0.00047649 | 0.00020864 | 3.2942e-05 | -4.6648e-05 | -0.00015259 | -0.00025853 | -0.00036448 | -0.00047042 | -0.00057636 | -0.0006823 | -0.00078825 | -0.00089419 | -0.0010001 | -0.0011061
Taranaki | 0.0012112 | 0.0016467 | 5.372e-05 | 5.3394e-05 | 0.006769 | 0.0022287 | 0.00036958 | 0.00075139 | 0.00040821 | 4.1926e-05 | 0.00058454 | 0.00059583 | 0.00060356 | 0.00058961 | 0.00059306 | 0.00058096 | 0.00058201 | 0.00056655 | 0.00055329 | 0.00056977 | 0.00058403 | 0.0012112 | 0.0016467 | 5.372e-05 | 5.3394e-05 | 0.006769 | 0.0022287 | 0.00036958 | 0.00075139 | 0.00040821 | 4.1926e-05 | 0.00071017 | 0.00059322 | 0.00047627 | 0.00035933 | 0.00024238 | 0.00012543 | 8.4811e-06 | -0.00010847 | -0.00022542 | -0.00034236 | -0.00045931
Tararua | 0.00053089 | 0.00045142 | 0.00025912 | 0.00039888 | 0.0016907 | 0.001403 | 0.0023468 | 0.0007575 | 0.00019654 | 0.00015872 | 0.0010868 | 0.0010679 | 0.001043 | 0.0010079 | 0.00094008 | 0.00087649 | 0.00080505 | 0.00075642 | 0.00072343 | 0.00071592 | 0.00068244 | 0.00053089 | 0.00045142 | 0.00025912 | 0.00039888 | 0.0016907 | 0.001403 | 0.0023468 | 0.0007575 | 0.00019654 | 0.00015872 | 0.00091651 | 0.00093417 | 0.00095184 | 0.0009695 | 0.00098716 | 0.0010048 | 0.0010225 | 0.0010402 | 0.0010578 | 0.0010755 | 0.0010931
Tauranga | 0.0019042 | 0.0007725 | 0.0013651 | 0.00042087 | 0 | 0.0041377 | 1.8479e-05 | 0.0024955 | 0.0075715 | 5.9894e-06 | 0.0015745 | 0.0015908 | 0.0013778 | 0.0012413 | 0.0011187 | 0.001037 | 0.00096383 | 0.00089548 | 0.00083904 | 0.00079844 | 0.00075614 | 0.0019042 | 0.0007725 | 0.0013651 | 0.00042087 | 0 | 0.0041377 | 1.8479e-05 | 0.0024955 | 0.0075715 | 5.9894e-06 | 0.0031722 | 0.0034091 | 0.0036461 | 0.003883 | 0.0041199 | 0.0043568 | 0.0045937 | 0.0048306 | 0.0050675 | 0.0053045 | 0.0055414
Waikato | 0.00042281 | 0.00027975 | 0.00020856 | 0.00097365 | 0.0005219 | 0.0034889 | 0.00049585 | 0.0010629 | 0.00044752 | 1.1979e-05 | 0.0012744 | 0.0013153 | 0.0013631 | 0.0013998 | 0.0014381 | 0.0014699 | 0.0014994 | 0.0015295 | 0.0015519 | 0.0015747 | 0.0015943 | 0.00042281 | 0.00027975 | 0.00020856 | 0.00097365 | 0.0005219 | 0.0034889 | 0.00049585 | 0.0010629 | 0.00044752 | 1.1979e-05 | 0.0009008 | 0.0009207 | 0.00094059 | 0.00096048 | 0.00098038 | 0.0010003 | 0.0010202 | 0.0010401 | 0.00106 | 0.0010798 | 0.0010997
Waikino | 0 | 0.00022889 | 0 | 0 | 0 | 0 | 0.0017524 | 0 | 0 | 0.001716 | 0.00049112 | 0.00049455 | 0.0005051 | 0.00051541 | 0.00052638 | 0.00053544 | 0.0005453 | 0.0005536 | 0.00056104 | 0.00056502 | 0.00057187 | 0 | 0.00022889 | 0 | 0 | 0 | 0 | 0.0017524 | 0 | 0 | 0.001716 | 0.0010063 | 0.0011221 | 0.0012378 | 0.0013536 | 0.0014693 | 0.0015851 | 0.0017008 | 0.0018166 | 0.0019323 | 0.0020481 | 0.0021638
Wairarapa | 0.0016912 | 0.0029533 | 0.00049612 | 0.0080499 | 0.0030845 | 0.0018345 | 0.010949 | 0.002358 | 0.0032173 | 0.001689 | 0.0041258 | 0.0038409 | 0.0034894 | 0.003199 | 0.0029299 | 0.0026808 | 0.002455 | 0.0022558 | 0.0021114 | 0.0019699 | 0.0018402 | 0.0016912 | 0.0029533 | 0.00049612 | 0.0080499 | 0.0030845 | 0.0018345 | 0.010949 | 0.002358 | 0.0032173 | 0.001689 | 0.0042517 | 0.0043644 | 0.004477 | 0.0045896 | 0.0047023 | 0.0048149 | 0.0049275 | 0.0050402 | 0.0051528 | 0.0052654 | 0.0053781
Whanganui | 5.4043e-05 | 9.2191e-05 | 9.4801e-05 | 8.4802e-05 | 0.00074066 | 0 | 5.8517e-05 | 0.0017013 | 3.0238e-06 | 4.492e-05 | 0.00039889 | 0.00039158 | 0.00037363 | 0.00036109 | 0.0003588 | 0.00036222 | 0.00037408 | 0.00037231 | 0.00037061 | 0.00035332 | 0.00031017 | 5.4043e-05 | 9.2191e-05 | 9.4801e-05 | 8.4802e-05 | 0.00074066 | 0 | 5.8517e-05 | 0.0017013 | 3.0238e-06 | 4.492e-05 | 0.00050432 | 0.00054375 | 0.00058319 | 0.00062262 | 0.00066206 | 0.00070149 | 0.00074093 | 0.00078036 | 0.0008198 | 0.00085923 | 0.00089867
Xarms
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.27531 | 0.21265 | 0.19034 | 0.21606 | 0.23926 | 0.23207 | 0.24742 | 0.20305 | 0.20314 | 0.23919
[11 empty] | 0.2146 | 0.21485 | 0.21417 | 0.21167 | 0.2068 | 0.20024 | 0.19511 | 0.19334 | 0.19149 | 0.18958 | 0.18738 | [10 empty] | 0.21781 | 0.21634 | 0.21488 | 0.21342 | 0.21196 | 0.2105 | 0.20903 | 0.20757 | 0.20611 | 0.20465 | 0.20318
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.029228 | 0.031555 | 0.010517 | 0.010198 | 0.012413 | 0.013524 | 0.0092395 | 0.020923 | 0.017456 | 0.013895 | 0.0095437 | 0.0098025 | 0.009985 | 0.010077 | 0.010144 | 0.010114 | 0.010094 | 0.010127 | 0.010069 | 0.010018 | 0.0099621 | 0.029228 | 0.031555 | 0.010517 | 0.010198 | 0.012413 | 0.013524 | 0.0092395 | 0.020923 | 0.017456 | 0.013895 | 0.010681 | 0.0095512 | 0.0084214 | 0.0072917 | 0.0061619 | 0.0050321 | 0.0039023 | 0.0027725 | 0.0016427 | 0.00051296 | -0.00061682
Egmont | 0.01428 | 0.010716 | 0.02255 | 0.013911 | 0.025117 | 0.014049 | 0.037309 | 0.026839 | 0.018451 | 0.032163 | 0.017104 | 0.016748 | 0.016488 | 0.015981 | 0.015415 | 0.014953 | 0.014252 | 0.014843 | 0.015061 | 0.015214 | 0.015174 | 0.01428 | 0.010716 | 0.02255 | 0.013911 | 0.025117 | 0.014049 | 0.037309 | 0.026839 | 0.018451 | 0.032163 | 0.031394 | 0.033186 | 0.034978 | 0.03677 | 0.038561 | 0.040353 | 0.042145 | 0.043937 | 0.045729 | 0.047521 | 0.049313
Kinleith | 0.0063548 | 3.179e-06 | 0.00016432 | 0.0012626 | 0 | 0.00044077 | 0.00019403 | 0.00050703 | 0.00060778 | 0.0017309 | 0.00081398 | 0.00082279 | 0.00083216 | 0.00082791 | 0.00081156 | 0.00077809 | 0.00076022 | 0.00074634 | 0.00072308 | 0.00070207 | 0.00067586 | 0.0063548 | 3.179e-06 | 0.00016432 | 0.0012626 | 0 | 0.00044077 | 0.00019403 | 0.00050703 | 0.00060778 | 0.0017309 | -0.00015459 | -0.00038753 | -0.00062046 | -0.00085339 | -0.0010863 | -0.0013193 | -0.0015522 | -0.0017851 | -0.0020181 | -0.002251 | -0.0024839
Manawatu | 0.028961 | 0.021398 | 0.025805 | 0.038199 | 0.036464 | 0.030832 | 0.034316 | 0.037246 | 0.021097 | 0.049646 | 0.030203 | 0.030585 | 0.030692 | 0.030037 | 0.029247 | 0.028152 | 0.027449 | 0.027161 | 0.026983 | 0.026755 | 0.026648 | 0.028961 | 0.021398 | 0.025805 | 0.038199 | 0.036464 | 0.030832 | 0.034316 | 0.037246 | 0.021097 | 0.049646 | 0.039862 | 0.04122 | 0.042577 | 0.043935 | 0.045292 | 0.04665 | 0.048007 | 0.049365 | 0.050722 | 0.05208 | 0.053437
Mt Maunganui | 0.010379 | 0.012172 | 0.0098688 | 0.0028833 | 0.0059315 | 0.010495 | 0.0042348 | 0.0028773 | 0.0062834 | 0.0015602 | 0.0054052 | 0.0052535 | 0.0049269 | 0.0047202 | 0.0042884 | 0.0038323 | 0.003395 | 0.0029567 | 0.0025487 | 0.0022271 | 0.0018951 | 0.010379 | 0.012172 | 0.0098688 | 0.0028833 | 0.0059315 | 0.010495 | 0.0042348 | 0.0028773 | 0.0062834 | 0.0015602 | 0.0017707 | 0.00088021 | -1.0309e-05 | -0.00090083 | -0.0017913 | -0.0026819 | -0.0035724 | -0.0044629 | -0.0053534 | -0.0062439 | -0.0071344
Rangitikei | 0.0086532 | 0.0031885 | 0.0081497 | 0.0097334 | 0.018916 | 0.016619 | 0.011796 | 0.011781 | 0.009422 | 0.01167 | 0.0161 | 0.015676 | 0.015208 | 0.015195 | 0.015562 | 0.015729 | 0.015912 | 0.016265 | 0.016672 | 0.016946 | 0.017209 | 0.0086532 | 0.0031885 | 0.0081497 | 0.0097334 | 0.018916 | 0.016619 | 0.011796 | 0.011781 | 0.009422 | 0.01167 | 0.014087 | 0.01465 | 0.015213 | 0.015775 | 0.016338 | 0.016901 | 0.017463 | 0.018026 | 0.018588 | 0.019151 | 0.019714
Taranaki | 0.043924 | 0.049602 | 0.042553 | 0.054854 | 0.05564 | 0.041737 | 0.036367 | 0.033687 | 0.05245 | 0.048208 | 0.049161 | 0.049652 | 0.050248 | 0.048827 | 0.046238 | 0.043499 | 0.041247 | 0.040057 | 0.039212 | 0.038162 | 0.037131 | 0.043924 | 0.049602 | 0.042553 | 0.054854 | 0.05564 | 0.041737 | 0.036367 | 0.033687 | 0.05245 | 0.048208 | 0.044062 | 0.043728 | 0.043393 | 0.043059 | 0.042724 | 0.04239 | 0.042055 | 0.041721 | 0.041386 | 0.041052 | 0.040717
Tararua | 0.011626 | 0.0077345 | 0.0084404 | 0.009322 | 0.015985 | 0.012034 | 0.015581 | 0.013858 | 0.0074294 | 0.013841 | 0.013246 | 0.013249 | 0.013213 | 0.013553 | 0.013734 | 0.01366 | 0.013762 | 0.014097 | 0.014584 | 0.014675 | 0.014857 | 0.011626 | 0.0077345 | 0.0084404 | 0.009322 | 0.015985 | 0.012034 | 0.015581 | 0.013858 | 0.0074294 | 0.013841 | 0.013576 | 0.013938 | 0.0143 | 0.014662 | 0.015024 | 0.015386 | 0.015747 | 0.016109 | 0.016471 | 0.016833 | 0.017195
Tauranga | 0.026071 | 0.02856 | 0.0060578 | 0.018311 | 0.019304 | 0.011718 | 0.018362 | 0.021488 | 0.01954 | 0.011422 | 0.014621 | 0.013576 | 0.012464 | 0.012166 | 0.011171 | 0.0099951 | 0.0091684 | 0.0083686 | 0.007314 | 0.0065432 | 0.0058258 | 0.026071 | 0.02856 | 0.0060578 | 0.018311 | 0.019304 | 0.011718 | 0.018362 | 0.021488 | 0.01954 | 0.011422 | 0.013908 | 0.013148 | 0.012389 | 0.01163 | 0.010871 | 0.010112 | 0.0093524 | 0.0085932 | 0.007834 | 0.0070748 | 0.0063155
Waikato | 0.016594 | 0.013511 | 0.017475 | 0.014586 | 0.01881 | 0.032269 | 0.014602 | 0.0066922 | 0.020806 | 0.0081006 | 0.01822 | 0.018121 | 0.017943 | 0.017721 | 0.017557 | 0.017262 | 0.017111 | 0.016969 | 0.01668 | 0.016384 | 0.016034 | 0.016594 | 0.013511 | 0.017475 | 0.014586 | 0.01881 | 0.032269 | 0.014602 | 0.0066922 | 0.020806 | 0.0081006 | 0.014152 | 0.013753 | 0.013355 | 0.012956 | 0.012557 | 0.012159 | 0.01176 | 0.011361 | 0.010963 | 0.010564 | 0.010165
Waikino | 0.050247 | 0.016178 | 0.0078874 | 0.0070951 | 0.0080941 | 0.012817 | 0.01474 | 0.0051498 | 0.0069002 | 0.0001108 | 0.0084481 | 0.0086275 | 0.008721 | 0.0087022 | 0.0086256 | 0.0084585 | 0.0083163 | 0.0081752 | 0.0079909 | 0.0077548 | 0.0075404 | 0.050247 | 0.016178 | 0.0078874 | 0.0070951 | 0.0080941 | 0.012817 | 0.01474 | 0.0051498 | 0.0069002 | 0.0001108 | -0.0038181 | -0.0068618 | -0.0099054 | -0.012949 | -0.015993 | -0.019036 | -0.02208 | -0.025124 | -0.028167 | -0.031211 | -0.034255
Wairarapa | 0.010294 | 0.0083798 | 0.014176 | 0.015117 | 0.0086003 | 0.01228 | 0.022905 | 0.0094534 | 0.014665 | 0.01583 | 0.012022 | 0.012426 | 0.012756 | 0.013023 | 0.013218 | 0.013311 | 0.01349 | 0.013638 | 0.01381 | 0.014438 | 0.014808 | 0.010294 | 0.0083798 | 0.014176 | 0.015117 | 0.0086003 | 0.01228 | 0.022905 | 0.0094534 | 0.014665 | 0.01583 | 0.016412 | 0.017001 | 0.017591 | 0.01818 | 0.01877 | 0.019359 | 0.019948 | 0.020538 | 0.021127 | 0.021717 | 0.022306
Whanganui | 0.018696 | 0.0096514 | 0.016698 | 0.020591 | 0.013985 | 0.023255 | 0.027777 | 0.012545 | 0.0080311 | 0.031007 | 0.019713 | 0.020309 | 0.020695 | 0.020837 | 0.020785 | 0.020495 | 0.020154 | 0.019933 | 0.019844 | 0.019758 | 0.019619 | 0.018696 | 0.0096514 | 0.016698 | 0.020591 | 0.013985 | 0.023255 | 0.027777 | 0.012545 | 0.0080311 | 0.031007 | 0.021874 | 0.022538 | 0.023202 | 0.023866 | 0.024529 | 0.025193 | 0.025857 | 0.026521 | 0.027185 | 0.027848 | 0.028512
Conductor
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.13433 | 0.086659 | 0.13739 | 0.21679 | 0.17496 | 0.10372 | 0.15194 | 0.18652 | 0.19429 | 0.18056
[11 empty] | 0.16251 | 0.16236 | 0.16114 | 0.15895 | 0.15506 | 0.15026 | 0.14537 | 0.1403 | 0.13733 | 0.13487 | 0.13482 | [10 empty] | 0.19503 | 0.202 | 0.20896 | 0.21593 | 0.2229 | 0.22986 | 0.23683 | 0.24379 | 0.25076 | 0.25773 | 0.26469
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.0095465 | 0.0049306 | 0.011395 | 0.0095701 | 0.0063878 | 0.0082226 | 0.013557 | 0.024112 | 0.012803 | 0.005055 | 0.010801 | 0.010924 | 0.011036 | 0.011172 | 0.011296 | 0.011343 | 0.011481 | 0.011525 | 0.01154 | 0.011512 | 0.011511 | 0.0095465 | 0.0049306 | 0.011395 | 0.0095701 | 0.0063878 | 0.0082226 | 0.013557 | 0.024112 | 0.012803 | 0.005055 | 0.013627 | 0.014185 | 0.014742 | 0.0153 | 0.015858 | 0.016416 | 0.016974 | 0.017532 | 0.01809 | 0.018648 | 0.019206
Egmont | 0.0114 | 0.011943 | 0.012637 | 0.0096203 | 0.018276 | 0.024901 | 0.0088391 | 0.022255 | 0.018578 | 0.017959 | 0.01633 | 0.016328 | 0.015784 | 0.013906 | 0.012929 | 0.012806 | 0.012681 | 0.012597 | 0.01206 | 0.011489 | 0.011472 | 0.0114 | 0.011943 | 0.012637 | 0.0096203 | 0.018276 | 0.024901 | 0.0088391 | 0.022255 | 0.018578 | 0.017959 | 0.020902 | 0.021859 | 0.022815 | 0.023772 | 0.024729 | 0.025685 | 0.026642 | 0.027599 | 0.028555 | 0.029512 | 0.030469
Kinleith | 0.0010809 | 0.00089966 | 0.0015832 | 0.0010522 | 0.00047814 | 0.0024118 | 0.0004435 | 0 | 0.0010462 | 0.00041926 | 0.00087003 | 0.00086564 | 0.00086206 | 0.00086875 | 0.00087687 | 0.00087534 | 0.00088486 | 0.0008897 | 0.00087497 | 0.00087252 | 0.00087525 | 0.0010809 | 0.00089966 | 0.0015832 | 0.0010522 | 0.00047814 | 0.0024118 | 0.0004435 | 0 | 0.0010462 | 0.00041926 | 0.00051693 | 0.00043973 | 0.00036254 | 0.00028535 | 0.00020816 | 0.00013097 | 5.3774e-05 | -2.3418e-05 | -0.00010061 | -0.0001778 | -0.00025499
Manawatu | 0.033507 | 0.0044283 | 0.027053 | 0.030777 | 0.039542 | 0.013977 | 0.021014 | 0.030321 | 0.018472 | 0.030525 | 0.024364 | 0.024395 | 0.024584 | 0.024535 | 0.024683 | 0.023851 | 0.024045 | 0.024164 | 0.023711 | 0.023719 | 0.023701 | 0.033507 | 0.0044283 | 0.027053 | 0.030777 | 0.039542 | 0.013977 | 0.021014 | 0.030321 | 0.018472 | 0.030525 | 0.02606 | 0.02626 | 0.02646 | 0.026659 | 0.026859 | 0.027059 | 0.027259 | 0.027458 | 0.027658 | 0.027858 | 0.028058
Mt Maunganui | 0.0077822 | 0.0086596 | 0.01677 | 0.027058 | 0.010463 | 0.010765 | 0.001235 | 0.0061699 | 0.019591 | 0.011889 | 0.01248 | 0.012559 | 0.012489 | 0.012435 | 0.011364 | 0.010544 | 0.0088277 | 0.0071758 | 0.0070429 | 0.0067399 | 0.006746 | 0.0077822 | 0.0086596 | 0.01677 | 0.027058 | 0.010463 | 0.010765 | 0.001235 | 0.0061699 | 0.019591 | 0.011889 | 0.011482 | 0.011381 | 0.01128 | 0.011179 | 0.011077 | 0.010976 | 0.010875 | 0.010774 | 0.010673 | 0.010572 | 0.01047
Rangitikei | 0.0028007 | 0.0035033 | 0.008867 | 0.010946 | 0.0093816 | 0.0016544 | 0.0063476 | 0.0089067 | 0.013456 | 0.0058426 | 0.0080764 | 0.0080412 | 0.0080783 | 0.008111 | 0.0080389 | 0.0080012 | 0.0080289 | 0.0081593 | 0.0078914 | 0.0077429 | 0.0077355 | 0.0028007 | 0.0035033 | 0.008867 | 0.010946 | 0.0093816 | 0.0016544 | 0.0063476 | 0.0089067 | 0.013456 | 0.0058426 | 0.0096946 | 0.010154 | 0.010612 | 0.011071 | 0.01153 | 0.011989 | 0.012448 | 0.012907 | 0.013366 | 0.013825 | 0.014284
Taranaki | 0.01271 | 0.0073244 | 0.021318 | 0.015619 | 0.025207 | 0.008893 | 0.038871 | 0.023931 | 0.02647 | 0.032702 | 0.023458 | 0.022807 | 0.021887 | 0.02132 | 0.020425 | 0.019464 | 0.018981 | 0.018457 | 0.017548 | 0.016622 | 0.016599 | 0.01271 | 0.0073244 | 0.021318 | 0.015619 | 0.025207 | 0.008893 | 0.038871 | 0.023931 | 0.02647 | 0.032702 | 0.033987 | 0.036292 | 0.038598 | 0.040904 | 0.04321 | 0.045516 | 0.047821 | 0.050127 | 0.052433 | 0.054739 | 0.057045
Tararua | 0.0047939 | 0.0027276 | 0.0021014 | 0.0056409 | 0.011922 | 0.0020207 | 0.0050663 | 0.0060936 | 0.0061261 | 0.0022101 | 0.0047745 | 0.004773 | 0.0047954 | 0.0048573 | 0.0048437 | 0.0048543 | 0.0048957 | 0.0049445 | 0.0050581 | 0.0049462 | 0.0049118 | 0.0047939 | 0.0027276 | 0.0021014 | 0.0056409 | 0.011922 | 0.0020207 | 0.0050663 | 0.0060936 | 0.0061261 | 0.0022101 | 0.005166 | 0.0052198 | 0.0052735 | 0.0053273 | 0.005381 | 0.0054348 | 0.0054886 | 0.0055423 | 0.0055961 | 0.0056499 | 0.0057036
Tauranga | 0.014124 | 0.015879 | 0.004345 | 0.056425 | 0.018732 | 0.013751 | 0.01753 | 0.028278 | 0.023446 | 0.01901 | 0.022496 | 0.022605 | 0.022373 | 0.02239 | 0.021263 | 0.019416 | 0.016571 | 0.013031 | 0.012885 | 0.012754 | 0.012769 | 0.014124 | 0.015879 | 0.004345 | 0.056425 | 0.018732 | 0.013751 | 0.01753 | 0.028278 | 0.023446 | 0.01901 | 0.024317 | 0.024892 | 0.025468 | 0.026043 | 0.026619 | 0.027194 | 0.027769 | 0.028345 | 0.02892 | 0.029496 | 0.030071
Waikato | 0.0079252 | 0.0045936 | 0.010017 | 0.012742 | 0.0033814 | 0.0050503 | 0.0025686 | 0.010871 | 0.017771 | 0.0081695 | 0.0083051 | 0.0083965 | 0.0084976 | 0.0085964 | 0.0086689 | 0.0087442 | 0.0088284 | 0.0089298 | 0.0088017 | 0.0087604 | 0.0087686 | 0.0079252 | 0.0045936 | 0.010017 | 0.012742 | 0.0033814 | 0.0050503 | 0.0025686 | 0.010871 | 0.017771 | 0.0081695 | 0.010637 | 0.011061 | 0.011484 | 0.011907 | 0.012331 | 0.012754 | 0.013177 | 0.013601 | 0.014024 | 0.014447 | 0.014871
Waikino | 0.0097341 | 0.0044283 | 0.011702 | 0.0081913 | 0.0024001 | 0.0068816 | 0.0083926 | 0.01179 | 0.0054791 | 0.0070615 | 0.0075974 | 0.0077504 | 0.0078576 | 0.007984 | 0.008111 | 0.008265 | 0.0083836 | 0.0085413 | 0.0085317 | 0.0086717 | 0.0086961 | 0.0097341 | 0.0044283 | 0.011702 | 0.0081913 | 0.0024001 | 0.0068816 | 0.0083926 | 0.01179 | 0.0054791 | 0.0070615 | 0.0072337 | 0.007166 | 0.0070983 | 0.0070306 | 0.0069629 | 0.0068952 | 0.0068275 | 0.0067598 | 0.0066921 | 0.0066244 | 0.0065567
Wairarapa | 0.0080587 | 0.01257 | 0.0038489 | 0.012067 | 0.013932 | 0.0023715 | 0.020333 | 0.0073489 | 0.011977 | 0.026066 | 0.012413 | 0.012367 | 0.012382 | 0.012468 | 0.012313 | 0.012477 | 0.012365 | 0.012432 | 0.012278 | 0.012279 | 0.012288 | 0.0080587 | 0.01257 | 0.0038489 | 0.012067 | 0.013932 | 0.0023715 | 0.020333 | 0.0073489 | 0.011977 | 0.026066 | 0.018146 | 0.019289 | 0.020432 | 0.021576 | 0.022719 | 0.023862 | 0.025006 | 0.026149 | 0.027292 | 0.028436 | 0.029579
Whanganui | 0.010866 | 0.0047717 | 0.0057512 | 0.017077 | 0.014854 | 0.0028247 | 0.0077458 | 0.0064418 | 0.01908 | 0.013653 | 0.010546 | 0.010544 | 0.010514 | 0.01031 | 0.010248 | 0.0096164 | 0.0094007 | 0.0094516 | 0.0091129 | 0.0087654 | 0.0087523 | 0.010866 | 0.0047717 | 0.0057512 | 0.017077 | 0.014854 | 0.0028247 | 0.0077458 | 0.0064418 | 0.01908 | 0.013653 | 0.013262 | 0.0138 | 0.014337 | 0.014874 | 0.015412 | 0.015949 | 0.016487 | 0.017024 | 0.017561 | 0.018099 | 0.018636
Transformers
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.019821 | 0.021169 | 0.016103 | 0.0186 | 0.029526 | 0.023147 | 0.014041 | 0.018498 | 0.020175 | 0.026758
[11 empty] | 0.028546 | 0.029004 | 0.029618 | 0.030236 | 0.030865 | 0.031474 | 0.03231 | 0.033363 | 0.033894 | 0.034707 | 0.035288 | [10 empty] | 0.022363 | 0.02265 | 0.022937 | 0.023225 | 0.023512 | 0.023799 | 0.024086 | 0.024373 | 0.02466 | 0.024948 | 0.025235
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 2.8611e-05 | 0.0024955 | 0.0059124 | 0.00098936 | 0.0019251 | 0.00044698 | 0.00080076 | 0.00046122 | 0.000254 | 0.0040069 | 0.003759 | 0.0039293 | 0.0040452 | 0.0042094 | 0.0044069 | 0.004558 | 0.0048513 | 0.005161 | 0.0052967 | 0.0054689 | 0.0056141 | 2.8611e-05 | 0.0024955 | 0.0059124 | 0.00098936 | 0.0019251 | 0.00044698 | 0.00080076 | 0.00046122 | 0.000254 | 0.0040069 | 0.0014259 | 0.0013702 | 0.0013145 | 0.0012589 | 0.0012032 | 0.0011475 | 0.0010918 | 0.0010362 | 0.0009805 | 0.00092483 | 0.00086916
Egmont | 0.0012652 | 0.0074929 | 0.004266 | 0.0036653 | 0.0014688 | 0.0052644 | 0.0017155 | 0.0068389 | 0.0057482 | 0.0044022 | 0.0034559 | 0.0033241 | 0.003211 | 0.0030844 | 0.0029322 | 0.0029232 | 0.0028744 | 0.0029468 | 0.0029057 | 0.0029173 | 0.0028702 | 0.0012652 | 0.0074929 | 0.004266 | 0.0036653 | 0.0014688 | 0.0052644 | 0.0017155 | 0.0068389 | 0.0057482 | 0.0044022 | 0.0051071 | 0.0052697 | 0.0054323 | 0.0055949 | 0.0057575 | 0.0059201 | 0.0060827 | 0.0062453 | 0.0064079 | 0.0065705 | 0.0067331
Kinleith | 0.0041263 | 0.0026513 | 0.00039184 | 0.00018217 | 0.0018376 | 0.0001552 | 0 | 0 | 0.00012095 | 0.0020723 | 0.0011272 | 0.0011663 | 0.0011914 | 0.0012897 | 0.0013451 | 0.001422 | 0.0014635 | 0.0015185 | 0.0015371 | 0.0015716 | 0.0015811 | 0.0041263 | 0.0026513 | 0.00039184 | 0.00018217 | 0.0018376 | 0.0001552 | 0 | 0 | 0.00012095 | 0.0020723 | -0.00019245 | -0.00043722 | -0.00068198 | -0.00092675 | -0.0011715 | -0.0014163 | -0.001661 | -0.0019058 | -0.0021506 | -0.0023953 | -0.0026401
Manawatu | 0 | 3.179e-05 | 0 | 0.0013568 | 0.0071003 | 0.0043301 | 0.0004127 | 5.1925e-05 | 0.001533 | 0.0051598 | 0.0042638 | 0.0044208 | 0.004586 | 0.0047718 | 0.0050286 | 0.0051626 | 0.0053262 | 0.0054895 | 0.0056891 | 0.0058667 | 0.0059768 | 0 | 3.179e-05 | 0 | 0.0013568 | 0.0071003 | 0.0043301 | 0.0004127 | 5.1925e-05 | 0.001533 | 0.0051598 | 0.0037178 | 0.0040306 | 0.0043433 | 0.0046561 | 0.0049688 | 0.0052816 | 0.0055943 | 0.0059071 | 0.0062198 | 0.0065326 | 0.0068453
Mt Maunganui | 0 | 4.1327e-05 | 0.00099857 | 0.00032665 | 0.003147 | 7.1393e-05 | 0.00093935 | 5.498e-05 | 0.00014212 | 8.0856e-05 | 0.0008218 | 0.00084274 | 0.00087354 | 0.0008889 | 0.00090079 | 0.00092343 | 0.0009363 | 0.00097758 | 0.0010053 | 0.0010448 | 0.0010898 | 0 | 4.1327e-05 | 0.00099857 | 0.00032665 | 0.003147 | 7.1393e-05 | 0.00093935 | 5.498e-05 | 0.00014212 | 8.0856e-05 | 0.00042948 | 0.00040208 | 0.00037467 | 0.00034726 | 0.00031986 | 0.00029245 | 0.00026504 | 0.00023763 | 0.00021023 | 0.00018282 | 0.00015541
Rangitikei | 0.0018534 | 0.00031472 | 6.3201e-06 | 0.00094539 | 0.0035376 | 0.0019059 | 2.7719e-05 | 0.0013989 | 0.00015119 | 0.00010481 | 0.0015519 | 0.0015418 | 0.0015312 | 0.0015238 | 0.0015136 | 0.0014991 | 0.0014816 | 0.0014781 | 0.0014649 | 0.0014581 | 0.0014466 | 0.0018534 | 0.00031472 | 6.3201e-06 | 0.00094539 | 0.0035376 | 0.0019059 | 2.7719e-05 | 0.0013989 | 0.00015119 | 0.00010481 | 0.00054782 | 0.00046113 | 0.00037444 | 0.00028776 | 0.00020107 | 0.00011438 | 2.7696e-05 | -5.8991e-05 | -0.00014568 | -0.00023236 | -0.00031905
Taranaki | 0.00023842 | 0.0045015 | 6.3201e-05 | 0.0019536 | 0.0029876 | 0.0019742 | 0.0010225 | 0.0013287 | 0.0037011 | 0.0038392 | 0.0010562 | 0.0010517 | 0.0010525 | 0.0010455 | 0.0010464 | 0.001038 | 0.0010477 | 0.0010777 | 0.0011059 | 0.00111 | 0.0011452 | 0.00023842 | 0.0045015 | 6.3201e-05 | 0.0019536 | 0.0029876 | 0.0019742 | 0.0010225 | 0.0013287 | 0.0037011 | 0.0038392 | 0.0031385 | 0.0033162 | 0.0034939 | 0.0036717 | 0.0038494 | 0.0040271 | 0.0042048 | 0.0043826 | 0.0045603 | 0.004738 | 0.0049158
Tararua | 0 | 0 | 0.00017064 | 4.3972e-05 | 0.00035626 | 0.0013192 | 0.00072376 | 0.00048565 | 4.2333e-05 | 0.00092835 | 0.00083282 | 0.00082989 | 0.00082056 | 0.00086351 | 0.00088969 | 0.00090929 | 0.00093011 | 0.00094304 | 0.00096664 | 0.00097227 | 0.0010071 | 0 | 0 | 0.00017064 | 4.3972e-05 | 0.00035626 | 0.0013192 | 0.00072376 | 0.00048565 | 4.2333e-05 | 0.00092835 | 0.00084798 | 0.00092816 | 0.0010083 | 0.0010885 | 0.0011687 | 0.0012489 | 0.001329 | 0.0014092 | 0.0014894 | 0.0015696 | 0.0016497
Tauranga | 0.0050927 | 0.00097595 | 0.00041396 | 0.002632 | 0.00094066 | 0.0013378 | 0.0057531 | 0.0013409 | 0.0021197 | 0.00026353 | 0.0033411 | 0.00341 | 0.0036156 | 0.0037256 | 0.0037335 | 0.0038111 | 0.003927 | 0.0041483 | 0.0042668 | 0.0044292 | 0.0046493 | 0.0050927 | 0.00097595 | 0.00041396 | 0.002632 | 0.00094066 | 0.0013378 | 0.0057531 | 0.0013409 | 0.0021197 | 0.00026353 | 0.001385 | 0.0012573 | 0.0011297 | 0.001002 | 0.00087439 | 0.00074674 | 0.0006191 | 0.00049145 | 0.0003638 | 0.00023616 | 0.00010851
Waikato | 0.0054456 | 0.002505 | 0.0011502 | 0.001583 | 0.0021438 | 0.0015396 | 0.00040038 | 6.4143e-05 | 0.005848 | 0.0003384 | 0.0032516 | 0.0033304 | 0.0034406 | 0.0035249 | 0.0036465 | 0.003749 | 0.0039692 | 0.0041217 | 0.004147 | 0.0043121 | 0.0043336 | 0.0054456 | 0.002505 | 0.0011502 | 0.001583 | 0.0021438 | 0.0015396 | 0.00040038 | 6.4143e-05 | 0.005848 | 0.0003384 | 0.0010302 | 0.00083542 | 0.00064059 | 0.00044575 | 0.00025092 | 5.6092e-05 | -0.00013874 | -0.00033357 | -0.0005284 | -0.00072323 | -0.00091806
Waikino | 0.00051182 | 2.2253e-05 | 9.1641e-05 | 0.0001539 | 0.0016719 | 4.0352e-05 | 0.00067141 | 3.6653e-05 | 0.0003689 | 2.9947e-06 | 0.00078967 | 0.00087768 | 0.00096134 | 0.0010241 | 0.0011564 | 0.0012268 | 0.0012977 | 0.0013396 | 0.0013887 | 0.0014542 | 0.001504 | 0.00051182 | 2.2253e-05 | 9.1641e-05 | 0.0001539 | 0.0016719 | 4.0352e-05 | 0.00067141 | 3.6653e-05 | 0.0003689 | 2.9947e-06 | 0.00027362 | 0.00025843 | 0.00024324 | 0.00022804 | 0.00021285 | 0.00019766 | 0.00018246 | 0.00016727 | 0.00015208 | 0.00013688 | 0.00012169
Wairarapa | 0.0010205 | 0.0001367 | 0.0026386 | 0.0044097 | 0.00030939 | 0.00039732 | 0.0014691 | 0.0016494 | 0.00011793 | 0.0047885 | 0.0024617 | 0.0024583 | 0.0024713 | 0.0024696 | 0.0024709 | 0.0024623 | 0.0024396 | 0.002406 | 0.0023811 | 0.0023661 | 0.0023583 | 0.0010205 | 0.0001367 | 0.0026386 | 0.0044097 | 0.00030939 | 0.00039732 | 0.0014691 | 0.0016494 | 0.00011793 | 0.0047885 | 0.0023637 | 0.0024856 | 0.0026074 | 0.0027292 | 0.002851 | 0.0029729 | 0.0030947 | 0.0032165 | 0.0033383 | 0.0034602 | 0.003582
Whanganui | 0.00023842 | 0 | 0 | 0.00035805 | 0.0021001 | 0.0043643 | 0.00010471 | 0.0047863 | 2.7214e-05 | 0.00076963 | 0.0018333 | 0.001821 | 0.0018175 | 0.0018147 | 0.0017946 | 0.0017887 | 0.0017653 | 0.0017553 | 0.0017392 | 0.0017363 | 0.0017123 | 0.00023842 | 0 | 0 | 0.00035805 | 0.0021001 | 0.0043643 | 0.00010471 | 0.0047863 | 2.7214e-05 | 0.00076963 | 0.0022884 | 0.0024727 | 0.002657 | 0.0028413 | 0.0030256 | 0.0032099 | 0.0033941 | 0.0035784 | 0.0037627 | 0.003947 | 0.0041313
Fuses
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.022765 | 0.02644 | 0.022474 | 0.030962 | 0.027939 | 0.025841 | 0.025815 | 0.042817 | 0.044235 | 0.047175
[11 empty] | 0.059031 | 0.059988 | 0.060364 | 0.060975 | 0.061306 | 0.061656 | 0.061977 | 0.063728 | 0.065353 | 0.06618 | 0.066972 | [10 empty] | 0.045927 | 0.048524 | 0.051121 | 0.053717 | 0.056314 | 0.05891 | 0.061507 | 0.064103 | 0.0667 | 0.069297 | 0.071893
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.00059765 | 0.00064851 | 0.0012609 | 0.000446 | 0.0030657 | 0.0010988 | 0.0020265 | 0.0056232 | 0.0046052 | 0.0027851 | 0.0079777 | 0.0082819 | 0.0084531 | 0.0087356 | 0.0089715 | 0.0091858 | 0.0092917 | 0.009525 | 0.0097569 | 0.0099997 | 0.010221 | 0.00059765 | 0.00064851 | 0.0012609 | 0.000446 | 0.0030657 | 0.0010988 | 0.0020265 | 0.0056232 | 0.0046052 | 0.0027851 | 0.0046147 | 0.0050509 | 0.0054871 | 0.0059233 | 0.0063595 | 0.0067957 | 0.0072318 | 0.007668 | 0.0081042 | 0.0085404 | 0.0089766
Egmont | 0.00088376 | 0.00065169 | 0.0016969 | 0.0025786 | 0.0047564 | 0.0073938 | 0.0019465 | 0.0056568 | 0.0073175 | 0.0024856 | 0.0072198 | 0.0075185 | 0.0075657 | 0.0077159 | 0.0077527 | 0.0078696 | 0.007948 | 0.0084668 | 0.0087943 | 0.0089482 | 0.0091156 | 0.00088376 | 0.00065169 | 0.0016969 | 0.0025786 | 0.0047564 | 0.0073938 | 0.0019465 | 0.0056568 | 0.0073175 | 0.0024856 | 0.0062573 | 0.006752 | 0.0072466 | 0.0077413 | 0.0082359 | 0.0087306 | 0.0092252 | 0.0097199 | 0.010215 | 0.010709 | 0.011204
Kinleith | 0 | 0 | 5.688e-05 | 0.0022457 | 0.0012469 | 0.00040042 | 0 | 5.8034e-05 | 0.00013607 | 0.00015273 | 0.00087362 | 0.00088155 | 0.00087087 | 0.00087241 | 0.00086567 | 0.00085168 | 0.00086105 | 0.00086835 | 0.00086944 | 0.0008827 | 0.00089613 | 0 | 0 | 5.688e-05 | 0.0022457 | 0.0012469 | 0.00040042 | 0 | 5.8034e-05 | 0.00013607 | 0.00015273 | 0.00025465 | 0.00022283 | 0.000191 | 0.00015918 | 0.00012736 | 9.5536e-05 | 6.3713e-05 | 3.189e-05 | 6.7237e-08 | -3.1756e-05 | -6.3578e-05
Manawatu | 0.0018184 | 0.0035255 | 0.0038363 | 0.0069004 | 0.0042939 | 0.0017662 | 0.0034494 | 0.0038119 | 0.0056998 | 0.0046657 | 0.006072 | 0.0060741 | 0.0060827 | 0.0061123 | 0.0060959 | 0.0061815 | 0.006273 | 0.0069431 | 0.0071114 | 0.0072368 | 0.0073636 | 0.0018184 | 0.0035255 | 0.0038363 | 0.0069004 | 0.0042939 | 0.0017662 | 0.0034494 | 0.0038119 | 0.0056998 | 0.0046657 | 0.0049049 | 0.0050736 | 0.0052424 | 0.0054111 | 0.0055799 | 0.0057486 | 0.0059174 | 0.0060861 | 0.0062549 | 0.0064236 | 0.0065924
Mt Maunganui | 0.00053725 | 0.0002575 | 0.00058776 | 0.0002387 | 0.002222 | 0 | 0.00040962 | 0.0003482 | 0.0023464 | 0.00082953 | 0.0023092 | 0.0023361 | 0.0023533 | 0.0023658 | 0.0023855 | 0.0023656 | 0.0023737 | 0.0023686 | 0.0023756 | 0.0023826 | 0.0024049 | 0.00053725 | 0.0002575 | 0.00058776 | 0.0002387 | 0.002222 | 0 | 0.00040962 | 0.0003482 | 0.0023464 | 0.00082953 | 0.0012559 | 0.0013428 | 0.0014298 | 0.0015167 | 0.0016037 | 0.0016906 | 0.0017776 | 0.0018645 | 0.0019515 | 0.0020384 | 0.0021254
Rangitikei | 0.0012239 | 0.0007566 | 0.00033496 | 0.00030152 | 0.0021938 | 0.0018221 | 0.0019311 | 0.0011607 | 0.0018052 | 0.0060912 | 0.0052348 | 0.0051892 | 0.0051492 | 0.0051264 | 0.0050818 | 0.0050328 | 0.0049884 | 0.0049519 | 0.0048729 | 0.0048034 | 0.0047355 | 0.0012239 | 0.0007566 | 0.00033496 | 0.00030152 | 0.0021938 | 0.0018221 | 0.0019311 | 0.0011607 | 0.0018052 | 0.0060912 | 0.0037551 | 0.0041175 | 0.0044799 | 0.0048422 | 0.0052046 | 0.005567 | 0.0059294 | 0.0062917 | 0.0066541 | 0.0070165 | 0.0073788
Taranaki | 0.0051881 | 0.0062658 | 0.0051034 | 0.0078018 | 0.0045596 | 0.0047212 | 0.010456 | 0.0023122 | 0.0053218 | 0.0097567 | 0.011325 | 0.011519 | 0.011609 | 0.011611 | 0.011626 | 0.011618 | 0.011668 | 0.011791 | 0.012345 | 0.012479 | 0.012577 | 0.0051881 | 0.0062658 | 0.0051034 | 0.0078018 | 0.0045596 | 0.0047212 | 0.010456 | 0.0023122 | 0.0053218 | 0.0097567 | 0.0071046 | 0.0072784 | 0.0074522 | 0.007626 | 0.0077998 | 0.0079736 | 0.0081474 | 0.0083212 | 0.008495 | 0.0086688 | 0.0088426
Tararua | 0.0003942 | 0.00052135 | 0.0012419 | 0.00010993 | 0.00077191 | 0.0022721 | 0.00017247 | 0.00065059 | 0.0010583 | 0.0041746 | 0.0015751 | 0.0015341 | 0.0014879 | 0.0014905 | 0.0014554 | 0.0014268 | 0.0014054 | 0.0015018 | 0.0015175 | 0.0014928 | 0.001463 | 0.0003942 | 0.00052135 | 0.0012419 | 0.00010993 | 0.00077191 | 0.0022721 | 0.00017247 | 0.00065059 | 0.0010583 | 0.0041746 | 0.0023539 | 0.0025752 | 0.0027965 | 0.0030177 | 0.003239 | 0.0034603 | 0.0036816 | 0.0039029 | 0.0041242 | 0.0043455 | 0.0045668
Tauranga | 0.0036431 | 0.0059129 | 0.0022341 | 0.0064481 | 0.0012032 | 0.0044915 | 0.0037636 | 0.0031186 | 0.0066886 | 0.0065074 | 0.0017931 | 0.0018354 | 0.0018507 | 0.0018676 | 0.0018872 | 0.0018943 | 0.0019097 | 0.0019197 | 0.0019314 | 0.0019398 | 0.0019598 | 0.0036431 | 0.0059129 | 0.0022341 | 0.0064481 | 0.0012032 | 0.0044915 | 0.0037636 | 0.0031186 | 0.0066886 | 0.0065074 | 0.00543 | 0.005617 | 0.0058041 | 0.0059911 | 0.0061782 | 0.0063653 | 0.0065523 | 0.0067394 | 0.0069264 | 0.0071135 | 0.0073006
Waikato | 0.0042344 | 0.0036082 | 0.00079001 | 0.0020133 | 0.0011594 | 0.000537 | 0.00011703 | 0.00046122 | 0.001657 | 0.00073669 | 0.00068786 | 0.00070566 | 0.00071306 | 0.0007277 | 0.00072994 | 0.00073383 | 0.00073894 | 0.00074805 | 0.0007568 | 0.00076739 | 0.00078173 | 0.0042344 | 0.0036082 | 0.00079001 | 0.0020133 | 0.0011594 | 0.000537 | 0.00011703 | 0.00046122 | 0.001657 | 0.00073669 | -0.00023833 | -0.0005601 | -0.00088187 | -0.0012036 | -0.0015254 | -0.0018472 | -0.002169 | -0.0024907 | -0.0028125 | -0.0031343 | -0.0034561
Waikino | 0.0027053 | 0.0016912 | 0.0021551 | 0.0009077 | 9.0629e-05 | 0.00053389 | 9.8555e-05 | 0.0027154 | 0.00063801 | 0.0014524 | 0.0018821 | 0.0019396 | 0.0019795 | 0.0020451 | 0.002082 | 0.0021145 | 0.0021365 | 0.0021749 | 0.00222 | 0.0022334 | 0.0022732 | 0.0027053 | 0.0016912 | 0.0021551 | 0.0009077 | 9.0629e-05 | 0.00053389 | 9.8555e-05 | 0.0027154 | 0.00063801 | 0.0014524 | 0.00070444 | 0.00059637 | 0.0004883 | 0.00038023 | 0.00027216 | 0.00016409 | 5.6025e-05 | -5.2045e-05 | -0.00016012 | -0.00026819 | -0.00037625
Wairarapa | 0.0014337 | 0.0018661 | 0.002844 | 0.00094539 | 0.0022063 | 0.00070772 | 0.0012104 | 0.015742 | 0.0046143 | 0.0030486 | 0.0093985 | 0.0095124 | 0.0095986 | 0.0096417 | 0.0097284 | 0.0097621 | 0.0097988 | 0.0099173 | 0.010285 | 0.010546 | 0.010744 | 0.0014337 | 0.0018661 | 0.002844 | 0.00094539 | 0.0022063 | 0.00070772 | 0.0012104 | 0.015742 | 0.0046143 | 0.0030486 | 0.0067139 | 0.0073052 | 0.0078964 | 0.0084877 | 0.009079 | 0.0096703 | 0.010262 | 0.010853 | 0.011444 | 0.012035 | 0.012627
Whanganui | 0.00010491 | 0.00073435 | 0.0003318 | 2.5127e-05 | 0.00016876 | 9.6225e-05 | 0.00023407 | 0.0011576 | 0.0023464 | 0.004489 | 0.0026819 | 0.00266 | 0.0026504 | 0.0026624 | 0.0026433 | 0.0026191 | 0.0025838 | 0.0025524 | 0.0025166 | 0.0024669 | 0.0024365 | 0.00010491 | 0.00073435 | 0.0003318 | 2.5127e-05 | 0.00016876 | 9.6225e-05 | 0.00023407 | 0.0011576 | 0.0023464 | 0.004489 | 0.0028163 | 0.0031522 | 0.0034882 | 0.0038241 | 0.00416 | 0.0044959 | 0.0048318 | 0.0051677 | 0.0055036 | 0.0058395 | 0.0061754
Sub-Trans
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.15148 | 0.24777 | 0.21106 | 0.13725 | 0.11189 | 0.15451 | 0.19333 | 0.055395 | 0.10157 | 0.1258
[11 empty] | 0.10752 | 0.10756 | 0.10757 | 0.10764 | 0.10768 | 0.1077 | 0.10768 | 0.10768 | 0.10777 | 0.10776 | 0.10775 | [10 empty] | 0.088275 | 0.077233 | 0.066191 | 0.055149 | 0.044107 | 0.033065 | 0.022023 | 0.010981 | -6.0843e-05 | -0.011103 | -0.022145
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.05006 | 0.08397 | 0.13283 | 0 | 0.0072722 | 0.056549 | 0.0081647 | 3.0544e-06 | 0 | 0.014398 | 0.020575 | 0.020618 | 0.020665 | 0.020713 | 0.020783 | 0.020839 | 0.020834 | 0.020875 | 0.020925 | 0.020989 | 0.020987 | 0.05006 | 0.08397 | 0.13283 | 0 | 0.0072722 | 0.056549 | 0.0081647 | 3.0544e-06 | 0 | 0.014398 | -0.014645 | -0.023731 | -0.032816 | -0.041902 | -0.050987 | -0.060072 | -0.069158 | -0.078243 | -0.087329 | -0.096414 | -0.1055
Egmont | 0.0043997 | 0.0017071 | 0.0092494 | 0 | 0.0045377 | 0.0018407 | 0.0089716 | 0 | 0.0054609 | 0.0051808 | 0.003139 | 0.0031263 | 0.0031148 | 0.0031224 | 0.0031152 | 0.0031064 | 0.0031005 | 0.0031078 | 0.0030992 | 0.003093 | 0.0030883 | 0.0043997 | 0.0017071 | 0.0092494 | 0 | 0.0045377 | 0.0018407 | 0.0089716 | 0 | 0.0054609 | 0.0051808 | 0.0045107 | 0.004579 | 0.0046474 | 0.0047157 | 0.0047841 | 0.0048524 | 0.0049208 | 0.0049891 | 0.0050575 | 0.0051258 | 0.0051941
Kinleith | 0 | 0 | 0 | 0.0087535 | 0 | 0 | 0 | 0 | 0.020308 | 0.020364 | 0.0014307 | 0.0014164 | 0.0014029 | 0.0014054 | 0.0014092 | 0.0013972 | 0.0014014 | 0.0014034 | 0.0013919 | 0.0013956 | 0.0014 | 0 | 0 | 0 | 0.0087535 | 0 | 0 | 0 | 0 | 0.020308 | 0.020364 | 0.014915 | 0.016728 | 0.018541 | 0.020354 | 0.022167 | 0.02398 | 0.025794 | 0.027607 | 0.02942 | 0.031233 | 0.033046
Manawatu | 0.01798 | 0.032941 | 3.16e-06 | 0.018157 | 0.018235 | 0.01832 | 0.0074255 | 0 | 0.0064708 | 0.020867 | 0.013876 | 0.01387 | 0.01385 | 0.013814 | 0.013794 | 0.013767 | 0.013752 | 0.013735 | 0.013708 | 0.013692 | 0.013682 | 0.01798 | 0.032941 | 3.16e-06 | 0.018157 | 0.018235 | 0.01832 | 0.0074255 | 0 | 0.0064708 | 0.020867 | 0.0076588 | 0.0064986 | 0.0053384 | 0.0041781 | 0.0030179 | 0.0018577 | 0.00069749 | -0.00046273 | -0.0016229 | -0.0027832 | -0.0039434
Mt Maunganui | 0.017631 | 0 | 0.012068 | 0.033877 | 0 | 0 | 0.0094336 | 0.011295 | 0.014511 | 0.0010122 | 0.0093815 | 0.0093936 | 0.009408 | 0.0094025 | 0.009428 | 0.0094273 | 0.0094546 | 0.0094477 | 0.0094651 | 0.00947 | 0.0094785 | 0.017631 | 0 | 0.012068 | 0.033877 | 0 | 0 | 0.0094336 | 0.011295 | 0.014511 | 0.0010122 | 0.00581 | 0.0050513 | 0.0042926 | 0.0035339 | 0.0027752 | 0.0020165 | 0.0012579 | 0.00049917 | -0.00025952 | -0.0010182 | -0.0017769
Rangitikei | 0.0025432 | 0.0051881 | 0.0056375 | 0.0026885 | 0.010657 | 0.017823 | 0 | 0.0095512 | 0.0099391 | 0 | 0.004803 | 0.0047865 | 0.0047714 | 0.0047575 | 0.0047494 | 0.0047388 | 0.0047327 | 0.004749 | 0.0047385 | 0.0047317 | 0.0047272 | 0.0025432 | 0.0051881 | 0.0056375 | 0.0026885 | 0.010657 | 0.017823 | 0 | 0.0095512 | 0.0099391 | 0 | 0.0073707 | 0.0075467 | 0.0077227 | 0.0078986 | 0.0080746 | 0.0082506 | 0.0084266 | 0.0086026 | 0.0087786 | 0.0089546 | 0.0091305
Taranaki | 0.00043234 | 0 | 0.0072175 | 0.0031722 | 0.022635 | 0.0091569 | 0.0099725 | 0.0094198 | 0.0078678 | 0.0199 | 0.0087641 | 0.0087444 | 0.0087409 | 0.0087254 | 0.0087071 | 0.0086968 | 0.0086819 | 0.0086671 | 0.0086572 | 0.0086538 | 0.0086418 | 0.00043234 | 0 | 0.0072175 | 0.0031722 | 0.022635 | 0.0091569 | 0.0099725 | 0.0094198 | 0.0078678 | 0.0199 | 0.017251 | 0.018756 | 0.02026 | 0.021764 | 0.023269 | 0.024773 | 0.026277 | 0.027782 | 0.029286 | 0.03079 | 0.032295
Tararua | 0.0049974 | 0.0044252 | 0.0059819 | 0.00095481 | 0.0015626 | 0.0019648 | 0.0019465 | 0.0086318 | 0.0028423 | 0.0064356 | 0.0050385 | 0.0049882 | 0.0049405 | 0.0050076 | 0.0049674 | 0.004925 | 0.0048879 | 0.0048443 | 0.0049106 | 0.004874 | 0.0048401 | 0.0049974 | 0.0044252 | 0.0059819 | 0.00095481 | 0.0015626 | 0.0019648 | 0.0019465 | 0.0086318 | 0.0028423 | 0.0064356 | 0.0045906 | 0.0047027 | 0.0048148 | 0.0049268 | 0.0050389 | 0.005151 | 0.005263 | 0.0053751 | 0.0054872 | 0.0055992 | 0.0057113
Tauranga | 0 | 0.064321 | 0 | 0.018 | 0.017888 | 0.03529 | 0.0037328 | 0 | 0 | 0 | 0.0067145 | 0.0067191 | 0.0067255 | 0.0067324 | 0.0067382 | 0.0067483 | 0.0067556 | 0.006761 | 0.0067698 | 0.0067751 | 0.0067831 | 0 | 0.064321 | 0 | 0.018 | 0.017888 | 0.03529 | 0.0037328 | 0 | 0 | 0 | -0.0019317 | -0.0048144 | -0.0076971 | -0.01058 | -0.013462 | -0.016345 | -0.019228 | -0.022111 | -0.024993 | -0.027876 | -0.030759
Waikato | 0.029908 | 0.0037894 | 0.0090724 | 0 | 0 | 0.0025546 | 0.00409 | 0 | 0.0062501 | 0.0020184 | 0.0039407 | 0.0039495 | 0.0039593 | 0.0039691 | 0.0039717 | 0.0039833 | 0.0039867 | 0.0039953 | 0.0039948 | 0.0040078 | 0.0040115 | 0.029908 | 0.0037894 | 0.0090724 | 0 | 0 | 0.0025546 | 0.00409 | 0 | 0.0062501 | 0.0020184 | -0.0030423 | -0.0046442 | -0.0062462 | -0.0078481 | -0.00945 | -0.011052 | -0.012654 | -0.014256 | -0.015858 | -0.01746 | -0.019062
Waikino | 0.017465 | 0.035268 | 0 | 0.027771 | 0 | 0 | 0.12167 | 0 | 0.017199 | 0 | 0.010442 | 0.010516 | 0.010532 | 0.010549 | 0.010577 | 0.010598 | 0.010628 | 0.010641 | 0.010659 | 0.010632 | 0.010662 | 0.017465 | 0.035268 | 0 | 0.027771 | 0 | 0 | 0.12167 | 0 | 0.017199 | 0 | 0.021871 | 0.021859 | 0.021848 | 0.021836 | 0.021824 | 0.021812 | 0.0218 | 0.021788 | 0.021776 | 0.021764 | 0.021752
Wairarapa | 0.0060655 | 0.0070828 | 0.019643 | 0.016725 | 0.01941 | 0.0089706 | 0.0064092 | 0.016494 | 0.00166 | 0.035628 | 0.014292 | 0.014314 | 0.014341 | 0.014328 | 0.014331 | 0.014365 | 0.014372 | 0.014357 | 0.014351 | 0.014355 | 0.014365 | 0.0060655 | 0.0070828 | 0.019643 | 0.016725 | 0.01941 | 0.0089706 | 0.0064092 | 0.016494 | 0.00166 | 0.035628 | 0.019508 | 0.020544 | 0.02158 | 0.022616 | 0.023652 | 0.024689 | 0.025725 | 0.026761 | 0.027797 | 0.028833 | 0.02987
Whanganui | 0 | 0.009076 | 0.00936 | 0.0071485 | 0.0096879 | 0.0020362 | 0.011516 | 0 | 0.0090652 | 0 | 0.0051254 | 0.0051213 | 0.0051187 | 0.005117 | 0.005106 | 0.0051071 | 0.0050981 | 0.0050962 | 0.005097 | 0.0050871 | 0.0050795 | 0 | 0.009076 | 0.00936 | 0.0071485 | 0.0096879 | 0.0020362 | 0.011516 | 0 | 0.0090652 | 0 | 0.0044081 | 0.004157 | 0.0039059 | 0.0036549 | 0.0034038 | 0.0031527 | 0.0029017 | 0.0026506 | 0.0023995 | 0.0021485 | 0.0018974
The rest of the equipment
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.10817 | 0.16928 | 0.16869 | 0.16981 | 0.13722 | 0.14464 | 0.1569 | 0.15277 | 0.11386 | 0.25289
[11 empty] | 0.1546 | 0.15463 | 0.15458 | 0.15455 | 0.15456 | 0.15451 | 0.15451 | 0.15454 | 0.15447 | 0.15445 | 0.15447 | [10 empty] | 0.18421 | 0.18908 | 0.19395 | 0.19882 | 0.2037 | 0.20857 | 0.21344 | 0.21831 | 0.22318 | 0.22805 | 0.23292
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.0053757 | 0.024122 | 0.0082698 | 0.018952 | 0.0077941 | 0.029165 | 0.0029967 | 0.035489 | 0.0050002 | 0.0040518 | 0.01412 | 0.01415 | 0.014182 | 0.014215 | 0.014263 | 0.014301 | 0.014298 | 0.014326 | 0.014361 | 0.014404 | 0.014403 | 0.0053757 | 0.024122 | 0.0082698 | 0.018952 | 0.0077941 | 0.029165 | 0.0029967 | 0.035489 | 0.0050002 | 0.0040518 | 0.012916 | 0.012697 | 0.012478 | 0.012258 | 0.012039 | 0.01182 | 0.011601 | 0.011382 | 0.011162 | 0.010943 | 0.010724
Egmont | 0.00094098 | 0.0075342 | 0.0032927 | 0.0065266 | 0.0062565 | 0.0052365 | 0.020795 | 0.0074694 | 0.0060721 | 0.0091428 | 0.0072188 | 0.0071894 | 0.0071631 | 0.0071806 | 0.007164 | 0.0071436 | 0.0071302 | 0.0071468 | 0.0071271 | 0.0071129 | 0.0071021 | 0.00094098 | 0.0075342 | 0.0032927 | 0.0065266 | 0.0062565 | 0.0052365 | 0.020795 | 0.0074694 | 0.0060721 | 0.0091428 | 0.011535 | 0.0123 | 0.013065 | 0.01383 | 0.014596 | 0.015361 | 0.016126 | 0.016891 | 0.017656 | 0.018421 | 0.019187
Kinleith | 0.0052485 | 0.0027594 | 0.0076915 | 0.0050787 | 0.0016907 | 0.0015986 | 0.0076626 | 0.0048087 | 0.002494 | 0.016767 | 0.0056155 | 0.0055594 | 0.0055063 | 0.0055159 | 0.005531 | 0.0054838 | 0.0055002 | 0.0055084 | 0.0054629 | 0.0054777 | 0.0054948 | 0.0052485 | 0.0027594 | 0.0076915 | 0.0050787 | 0.0016907 | 0.0015986 | 0.0076626 | 0.0048087 | 0.002494 | 0.016767 | 0.0087485 | 0.0093246 | 0.0099007 | 0.010477 | 0.011053 | 0.011629 | 0.012205 | 0.012781 | 0.013357 | 0.013933 | 0.01451
Manawatu | 0.02967 | 0.076728 | 0.063144 | 0.030325 | 0.049524 | 0.048327 | 0.050072 | 0.043862 | 0.029764 | 0.061604 | 0.047526 | 0.047508 | 0.04744 | 0.047316 | 0.047248 | 0.047154 | 0.047103 | 0.047045 | 0.046954 | 0.046898 | 0.046862 | 0.02967 | 0.076728 | 0.063144 | 0.030325 | 0.049524 | 0.048327 | 0.050072 | 0.043862 | 0.029764 | 0.061604 | 0.045645 | 0.045162 | 0.044679 | 0.044196 | 0.043713 | 0.043229 | 0.042746 | 0.042263 | 0.04178 | 0.041297 | 0.040814
Mt Maunganui | 0.0045841 | 0.0001367 | 0.0059788 | 0.010286 | 0.0017219 | 0.0014806 | 0.0017155 | 0.00084799 | 0.0019672 | 0.012554 | 0.0037369 | 0.0037417 | 0.0037474 | 0.0037452 | 0.0037554 | 0.0037551 | 0.003766 | 0.0037633 | 0.0037702 | 0.0037721 | 0.0037755 | 0.0045841 | 0.0001367 | 0.0059788 | 0.010286 | 0.0017219 | 0.0014806 | 0.0017155 | 0.00084799 | 0.0019672 | 0.012554 | 0.005225 | 0.0054246 | 0.0056242 | 0.0058238 | 0.0060234 | 0.006223 | 0.0064226 | 0.0066222 | 0.0068218 | 0.0070213 | 0.0072209
Rangitikei | 0.0035033 | 0.00097913 | 0.0031284 | 0.0034989 | 0.0041627 | 0.00062701 | 0.0047553 | 0.0023307 | 0.0037364 | 0.0090499 | 0.0036011 | 0.0035887 | 0.0035774 | 0.003567 | 0.003561 | 0.003553 | 0.0035485 | 0.0035606 | 0.0035528 | 0.0035477 | 0.0035443 | 0.0035033 | 0.00097913 | 0.0031284 | 0.0034989 | 0.0041627 | 0.00062701 | 0.0047553 | 0.0023307 | 0.0037364 | 0.0090499 | 0.0057594 | 0.0061561 | 0.0065529 | 0.0069497 | 0.0073464 | 0.0077432 | 0.00814 | 0.0085367 | 0.0089335 | 0.0093303 | 0.009727
Taranaki | 0.019471 | 0.0075819 | 0.017134 | 0.0076448 | 0.01266 | 0.0099236 | 0.018488 | 0.012725 | 0.01353 | 0.014887 | 0.012426 | 0.012398 | 0.012393 | 0.012371 | 0.012345 | 0.01233 | 0.012309 | 0.012288 | 0.012274 | 0.012269 | 0.012252 | 0.019471 | 0.0075819 | 0.017134 | 0.0076448 | 0.01266 | 0.0099236 | 0.018488 | 0.012725 | 0.01353 | 0.014887 | 0.013675 | 0.013724 | 0.013774 | 0.013823 | 0.013872 | 0.013921 | 0.013971 | 0.01402 | 0.014069 | 0.014118 | 0.014168
Tararua | 0.00070574 | 7.9475e-05 | 0.001659 | 2.5127e-05 | 0.00035939 | 6.2081e-05 | 0 | 1.0156e-05 | 0 | 0.00069776 | 0.00032925 | 0.00032597 | 0.00032285 | 0.00032723 | 0.00032461 | 0.00032184 | 0.00031941 | 0.00031656 | 0.00032089 | 0.0003185 | 0.00031629 | 0.00070574 | 7.9475e-05 | 0.001659 | 2.5127e-05 | 0.00035939 | 6.2081e-05 | 0 | 1.0156e-05 | 0 | 0.00069776 | 5.1705e-05 | -4.3261e-06 | -6.0357e-05 | -0.00011639 | -0.00017242 | -0.00022845 | -0.00028448 | -0.00034051 | -0.00039654 | -0.00045257 | -0.0005086
Tauranga | 0.021302 | 0.035497 | 0.019886 | 0.018509 | 0.025967 | 0.012826 | 0.0207 | 0.026613 | 0.016487 | 0.059729 | 0.024951 | 0.024968 | 0.024992 | 0.025018 | 0.025039 | 0.025077 | 0.025104 | 0.025124 | 0.025157 | 0.025176 | 0.025206 | 0.021302 | 0.035497 | 0.019886 | 0.018509 | 0.025967 | 0.012826 | 0.0207 | 0.026613 | 0.016487 | 0.059729 | 0.033746 | 0.035199 | 0.036653 | 0.038107 | 0.03956 | 0.041014 | 0.042467 | 0.043921 | 0.045374 | 0.046828 | 0.048281
Waikato | 0.0030232 | 0.006784 | 0.0027492 | 0.015547 | 0.0071972 | 0.016309 | 0.0074193 | 0.0001371 | 0.020954 | 0.011718 | 0.009144 | 0.0091644 | 0.0091871 | 0.00921 | 0.0092161 | 0.0092428 | 0.0092509 | 0.0092707 | 0.0092695 | 0.0092997 | 0.0093083 | 0.0030232 | 0.006784 | 0.0027492 | 0.015547 | 0.0071972 | 0.016309 | 0.0074193 | 0.0001371 | 0.020954 | 0.011718 | 0.014154 | 0.015058 | 0.015962 | 0.016865 | 0.017769 | 0.018673 | 0.019576 | 0.02048 | 0.021384 | 0.022288 | 0.023191
Waikino | 0.012236 | 0.0022889 | 0.011771 | 0.034012 | 0.0066315 | 0.0023529 | 0.014484 | 0.0057684 | 0.0060203 | 0.043111 | 0.014093 | 0.014193 | 0.014214 | 0.014237 | 0.014275 | 0.014303 | 0.014343 | 0.014361 | 0.014386 | 0.014349 | 0.014389 | 0.012236 | 0.0022889 | 0.011771 | 0.034012 | 0.0066315 | 0.0023529 | 0.014484 | 0.0057684 | 0.0060203 | 0.043111 | 0.020905 | 0.022185 | 0.023464 | 0.024744 | 0.026023 | 0.027303 | 0.028582 | 0.029862 | 0.031142 | 0.032421 | 0.033701
Wairarapa | 0.0014973 | 0.0030169 | 0.008096 | 0.012331 | 0.0076503 | 0.0057145 | 0.0056269 | 0.0021225 | 0.00317 | 0.0054354 | 0.0055183 | 0.0055271 | 0.0055373 | 0.0055322 | 0.0055337 | 0.0055466 | 0.0055493 | 0.0055437 | 0.0055413 | 0.0055428 | 0.0055466 | 0.0014973 | 0.0030169 | 0.008096 | 0.012331 | 0.0076503 | 0.0057145 | 0.0056269 | 0.0021225 | 0.00317 | 0.0054354 | 0.0049527 | 0.0048594 | 0.004766 | 0.0046727 | 0.0045794 | 0.004486 | 0.0043927 | 0.0042994 | 0.004206 | 0.0041127 | 0.0040194
Whanganui | 0.00061037 | 0.0017739 | 0.015885 | 0.0070763 | 0.0056065 | 0.011022 | 0.0021836 | 0.010587 | 0.0046652 | 0.0041446 | 0.0063243 | 0.0063194 | 0.0063161 | 0.006314 | 0.0063004 | 0.0063018 | 0.0062906 | 0.0062883 | 0.0062893 | 0.0062771 | 0.0062677 | 0.00061037 | 0.0017739 | 0.015885 | 0.0070763 | 0.0056065 | 0.011022 | 0.0021836 | 0.010587 | 0.0046652 | 0.0041446 | 0.0068987 | 0.0069975 | 0.0070962 | 0.007195 | 0.0072937 | 0.0073925 | 0.0074912 | 0.00759 | 0.0076887 | 0.0077875 | 0.0078862
Vegetation
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.16169 | 0.14721 | 0.14033 | 0.30742 | 0.39861 | 0.16241 | 0.25891 | 0.3381 | 0.1231 | 0.24004
[11 empty] | 0.21391 | 0.21393 | 0.17773 | 0.14177 | 0.12739 | 0.099329 | 0.071182 | 0.05986 | 0.059872 | 0.059883 | 0.059876 | [10 empty] | 0.2659 | 0.27283 | 0.27976 | 0.28669 | 0.29362 | 0.30056 | 0.30749 | 0.31442 | 0.32135 | 0.32828 | 0.33521
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.040364 | 0.016086 | 0.019166 | 0.072101 | 0.029304 | 0.011454 | 0.022969 | 0.07738 | 0.01113 | 0.029141 | 0.031019 | 0.031084 | 0.031155 | 0.031228 | 0.031333 | 0.022004 | 0.012552 | 0.008812 | 0.0088333 | 0.0088601 | 0.0088595 | 0.040364 | 0.016086 | 0.019166 | 0.072101 | 0.029304 | 0.011454 | 0.022969 | 0.07738 | 0.01113 | 0.029141 | 0.032581 | 0.032521 | 0.032461 | 0.032401 | 0.032342 | 0.032282 | 0.032222 | 0.032162 | 0.032103 | 0.032043 | 0.031983
Egmont | 0.0001208 | 0.0018534 | 0 | 0.023273 | 0.019029 | 0.0049416 | 0.011152 | 0.0078406 | 0.0042605 | 0.0070525 | 0.0074689 | 0.0074386 | 0.0051763 | 0.0029659 | 0.0020684 | 0.0020626 | 0.0020587 | 0.0020635 | 0.0020578 | 0.0020537 | 0.0020506 | 0.0001208 | 0.0018534 | 0 | 0.023273 | 0.019029 | 0.0049416 | 0.011152 | 0.0078406 | 0.0042605 | 0.0070525 | 0.010219 | 0.010631 | 0.011043 | 0.011455 | 0.011867 | 0.012279 | 0.012691 | 0.013103 | 0.013515 | 0.013927 | 0.014339
Kinleith | 0.004333 | 0.0034778 | 0.0019719 | 0.003034 | 0.002697 | 0.00099019 | 0.0012443 | 0.00098435 | 0.00094644 | 0.00076963 | 0.0019775 | 0.0019577 | 0.001939 | 0.0019424 | 0.0019477 | 0.0013525 | 0.00077398 | 0.00054313 | 0.00053864 | 0.00054011 | 0.00054179 | 0.004333 | 0.0034778 | 0.0019719 | 0.003034 | 0.002697 | 0.00099019 | 0.0012443 | 0.00098435 | 0.00094644 | 0.00076963 | -1.5259e-05 | -0.00038982 | -0.00076439 | -0.001139 | -0.0015135 | -0.0018881 | -0.0022627 | -0.0026372 | -0.0030118 | -0.0033864 | -0.0037609
Manawatu | 0.011648 | 0.014054 | 0.040309 | 0.033695 | 0.032858 | 0.011898 | 0.035738 | 0.026163 | 0.018521 | 0.021918 | 0.023555 | 0.023546 | 0.016458 | 0.0093801 | 0.006548 | 0.0065349 | 0.0065279 | 0.0065199 | 0.0065072 | 0.0064995 | 0.0064945 | 0.011648 | 0.014054 | 0.040309 | 0.033695 | 0.032858 | 0.011898 | 0.035738 | 0.026163 | 0.018521 | 0.021918 | 0.025951 | 0.026183 | 0.026414 | 0.026645 | 0.026876 | 0.027107 | 0.027338 | 0.027569 | 0.0278 | 0.028032 | 0.028263
Mt Maunganui | 0.01318 | 0.01174 | 0.0012577 | 0.0099187 | 0.010894 | 0.0094145 | 0.0038714 | 0.037922 | 0.0066886 | 0.01391 | 0.0099078 | 0.0099205 | 0.0099358 | 0.00993 | 0.0099569 | 0.0069581 | 0.0040053 | 0.002787 | 0.0027922 | 0.0027936 | 0.0027961 | 0.01318 | 0.01174 | 0.0012577 | 0.0099187 | 0.010894 | 0.0094145 | 0.0038714 | 0.037922 | 0.0066886 | 0.01391 | 0.016377 | 0.017194 | 0.018012 | 0.01883 | 0.019647 | 0.020465 | 0.021283 | 0.0221 | 0.022918 | 0.023736 | 0.024553
Rangitikei | 0.0094416 | 0.0015577 | 0.0078937 | 0.01741 | 0.027179 | 0.013444 | 0.013715 | 0.014663 | 0.0094462 | 0.0072531 | 0.011653 | 0.011612 | 0.0081031 | 0.0046168 | 0.0032221 | 0.0032148 | 0.0032107 | 0.0032217 | 0.0032147 | 0.00321 | 0.0032069 | 0.0094416 | 0.0015577 | 0.0078937 | 0.01741 | 0.027179 | 0.013444 | 0.013715 | 0.014663 | 0.0094462 | 0.0072531 | 0.013685 | 0.013955 | 0.014225 | 0.014495 | 0.014765 | 0.015035 | 0.015305 | 0.015575 | 0.015845 | 0.016115 | 0.016385
Taranaki | 0.017532 | 0.020609 | 0.023258 | 0.055379 | 0.061803 | 0.020064 | 0.031842 | 0.02497 | 0.010913 | 0.032088 | 0.027797 | 0.027735 | 0.019363 | 0.011048 | 0.0077066 | 0.0076974 | 0.0076842 | 0.0076712 | 0.0076624 | 0.0076593 | 0.0076488 | 0.017532 | 0.020609 | 0.023258 | 0.055379 | 0.061803 | 0.020064 | 0.031842 | 0.02497 | 0.010913 | 0.032088 | 0.02849 | 0.028244 | 0.027998 | 0.027751 | 0.027505 | 0.027258 | 0.027012 | 0.026765 | 0.026519 | 0.026273 | 0.026026
Tararua | 0.0036368 | 0.0019392 | 0.0030431 | 0.0021075 | 0.0072315 | 0.0021573 | 0.0051279 | 0.0072211 | 0.0028181 | 0.0065374 | 0.0038091 | 0.003771 | 0.0026145 | 0.0015143 | 0.0010501 | 0.0010411 | 0.0010333 | 0.0010241 | 0.0010381 | 0.0010303 | 0.0010232 | 0.0036368 | 0.0019392 | 0.0030431 | 0.0021075 | 0.0072315 | 0.0021573 | 0.0051279 | 0.0072211 | 0.0028181 | 0.0065374 | 0.0060865 | 0.0064328 | 0.0067791 | 0.0071253 | 0.0074716 | 0.0078179 | 0.0081642 | 0.0085104 | 0.0088567 | 0.009203 | 0.0095493
Tauranga | 0.014496 | 0.040821 | 0.0043608 | 0.010823 | 0.09867 | 0.020962 | 0.020737 | 0.046162 | 0.014221 | 0.026299 | 0.027434 | 0.027452 | 0.027479 | 0.027507 | 0.027531 | 0.019269 | 0.011072 | 0.0077159 | 0.0077259 | 0.007732 | 0.0077411 | 0.014496 | 0.040821 | 0.0043608 | 0.010823 | 0.09867 | 0.020962 | 0.020737 | 0.046162 | 0.014221 | 0.026299 | 0.032457 | 0.032948 | 0.03344 | 0.033931 | 0.034422 | 0.034913 | 0.035405 | 0.035896 | 0.036387 | 0.036879 | 0.03737
Waikato | 0.020113 | 0.013422 | 0.010656 | 0.024593 | 0.027185 | 0.018575 | 0.0073115 | 0.014302 | 0.0069093 | 0.013797 | 0.015422 | 0.015457 | 0.015495 | 0.015534 | 0.015544 | 0.010918 | 0.0062348 | 0.004378 | 0.0043775 | 0.0043918 | 0.0043958 | 0.020113 | 0.013422 | 0.010656 | 0.024593 | 0.027185 | 0.018575 | 0.0073115 | 0.014302 | 0.0069093 | 0.013797 | 0.010864 | 0.0099873 | 0.0091106 | 0.0082338 | 0.0073571 | 0.0064803 | 0.0056036 | 0.0047268 | 0.0038501 | 0.0029733 | 0.0020966
Waikino | 0.011285 | 0.0041263 | 0.011711 | 0.0060147 | 0.007044 | 0.01214 | 0.0025162 | 0.011231 | 0.0028272 | 0.014839 | 0.0073766 | 0.007429 | 0.0074402 | 0.0074522 | 0.0074719 | 0.0052436 | 0.0030001 | 0.0021048 | 0.0021084 | 0.002103 | 0.0021089 | 0.011285 | 0.0041263 | 0.011711 | 0.0060147 | 0.007044 | 0.01214 | 0.0025162 | 0.011231 | 0.0028272 | 0.014839 | 0.0088762 | 0.0089676 | 0.0090591 | 0.0091505 | 0.0092419 | 0.0093333 | 0.0094247 | 0.0095162 | 0.0096076 | 0.009699 | 0.0097904
Wairarapa | 0.0078299 | 0.012846 | 0.012302 | 0.032077 | 0.041186 | 0.013111 | 0.085416 | 0.054322 | 0.016232 | 0.036011 | 0.030918 | 0.030967 | 0.021693 | 0.012421 | 0.0086671 | 0.0086874 | 0.0086916 | 0.0086829 | 0.0086791 | 0.0086814 | 0.0086874 | 0.0078299 | 0.012846 | 0.012302 | 0.032077 | 0.041186 | 0.013111 | 0.085416 | 0.054322 | 0.016232 | 0.036011 | 0.051779 | 0.055533 | 0.059286 | 0.06304 | 0.066794 | 0.070548 | 0.074301 | 0.078055 | 0.081809 | 0.085563 | 0.089316
Whanganui | 0.0077122 | 0.0046731 | 0.0043988 | 0.016998 | 0.033533 | 0.023255 | 0.017266 | 0.014944 | 0.018191 | 0.030429 | 0.015574 | 0.015561 | 0.010873 | 0.0062338 | 0.0043441 | 0.0043451 | 0.0043373 | 0.0043358 | 0.0043364 | 0.004328 | 0.0043215 | 0.0077122 | 0.0046731 | 0.0043988 | 0.016998 | 0.033533 | 0.023255 | 0.017266 | 0.014944 | 0.018191 | 0.030429 | 0.028551 | 0.030626 | 0.0327 | 0.034775 | 0.03685 | 0.038924 | 0.040999 | 0.043074 | 0.045148 | 0.047223 | 0.049298
Adverse Weather
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.3647 | 0.5318 | 0.24988 | 0.28569 | 0.24852 | 0.08803 | 0.28877 | 0.21972 | 0.053251 | 0.22566
[11 empty] | 0.23483 | 0.23479 | 0.23475 | 0.2349 | 0.23487 | 0.23489 | 0.2348 | 0.2349 | 0.23495 | 0.23493 | 0.23487 | [10 empty] | 0.092161 | 0.062445 | 0.032728 | 0.0030117 | -0.026705 | -0.056421 | -0.086138 | -0.11585 | -0.14557 | -0.17529 | -0.205
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.11936 | 0.12088 | 0.0053878 | 0.041091 | 0.030211 | 0.00040042 | 0.051858 | 0.054478 | 0.0052976 | 0.038092 | 0.036413 | 0.036489 | 0.036573 | 0.036658 | 0.036782 | 0.03688 | 0.036872 | 0.036944 | 0.037033 | 0.037145 | 0.037143 | 0.11936 | 0.12088 | 0.0053878 | 0.041091 | 0.030211 | 0.00040042 | 0.051858 | 0.054478 | 0.0052976 | 0.038092 | 0.0036213 | -0.0042123 | -0.012046 | -0.019879 | -0.027713 | -0.035546 | -0.04338 | -0.051213 | -0.059047 | -0.06688 | -0.074714
Egmont | 0.042173 | 0.024818 | 0.024869 | 0.021643 | 0.043324 | 0.013822 | 0.008679 | 0.015431 | 0.0035348 | 0.022011 | 0.025546 | 0.025443 | 0.025349 | 0.025411 | 0.025353 | 0.02528 | 0.025233 | 0.025292 | 0.025222 | 0.025172 | 0.025134 | 0.042173 | 0.024818 | 0.024869 | 0.021643 | 0.043324 | 0.013822 | 0.008679 | 0.015431 | 0.0035348 | 0.022011 | 0.0071629 | 0.0044597 | 0.0017565 | -0.00094674 | -0.0036499 | -0.0063531 | -0.0090563 | -0.01176 | -0.014463 | -0.017166 | -0.019869
Kinleith | 0.0034556 | 0 | 0.0039785 | 0.0072616 | 0 | 0.0011112 | 0.0016693 | 0.00041433 | 3.3261e-05 | 2.9947e-05 | 0.0015547 | 0.0015392 | 0.0015245 | 0.0015271 | 0.0015313 | 0.0015182 | 0.0015228 | 0.001525 | 0.0015125 | 0.0015166 | 0.0015213 | 0.0034556 | 0 | 0.0039785 | 0.0072616 | 0 | 0.0011112 | 0.0016693 | 0.00041433 | 3.3261e-05 | 2.9947e-05 | -0.00034077 | -0.00072916 | -0.0011175 | -0.0015059 | -0.0018943 | -0.0022827 | -0.0026711 | -0.0030595 | -0.0034479 | -0.0038363 | -0.0042247
Manawatu | 0.020609 | 0.081885 | 0.021728 | 0.022699 | 0.030495 | 0.0032375 | 0.026816 | 0.019143 | 0.004962 | 0.032774 | 0.021733 | 0.021725 | 0.021693 | 0.021637 | 0.021606 | 0.021563 | 0.021539 | 0.021513 | 0.021471 | 0.021446 | 0.021429 | 0.020609 | 0.081885 | 0.021728 | 0.022699 | 0.030495 | 0.0032375 | 0.026816 | 0.019143 | 0.004962 | 0.032774 | 0.011208 | 0.0084393 | 0.0056707 | 0.0029022 | 0.00013363 | -0.0026349 | -0.0054035 | -0.008172 | -0.010941 | -0.013709 | -0.016478
Mt Maunganui | 0.020555 | 0.012716 | 0.0076283 | 0.010716 | 0.0027282 | 0.0017445 | 0.0015276 | 0.011441 | 0.0033503 | 0.0033061 | 0.0058741 | 0.0058816 | 0.0058906 | 0.0058872 | 0.0059032 | 0.0059027 | 0.0059198 | 0.0059155 | 0.0059264 | 0.0059294 | 0.0059348 | 0.020555 | 0.012716 | 0.0076283 | 0.010716 | 0.0027282 | 0.0017445 | 0.0015276 | 0.011441 | 0.0033503 | 0.0033061 | -0.00010495 | -0.0015006 | -0.0028963 | -0.004292 | -0.0056877 | -0.0070834 | -0.0084791 | -0.0098748 | -0.011271 | -0.012666 | -0.014062
Rangitikei | 0.0083035 | 0.010799 | 0.029233 | 0.022202 | 0.013457 | 0.0067233 | 0.012861 | 0.0075683 | 0.00058963 | 0.0071513 | 0.013367 | 0.013321 | 0.013279 | 0.01324 | 0.013218 | 0.013188 | 0.013171 | 0.013216 | 0.013187 | 0.013168 | 0.013156 | 0.0083035 | 0.010799 | 0.029233 | 0.022202 | 0.013457 | 0.0067233 | 0.012861 | 0.0075683 | 0.00058963 | 0.0071513 | 0.0043916 | 0.0030285 | 0.0016654 | 0.00030223 | -0.0010609 | -0.0024241 | -0.0037872 | -0.0051503 | -0.0065135 | -0.0078766 | -0.0092398
Taranaki | 0.052453 | 0.049529 | 0.038148 | 0.025224 | 0.05558 | 0.017268 | 0.0098771 | 0.024218 | 0.0037132 | 0.042258 | 0.028145 | 0.028082 | 0.028071 | 0.028021 | 0.027962 | 0.027929 | 0.027881 | 0.027834 | 0.027802 | 0.027791 | 0.027752 | 0.052453 | 0.049529 | 0.038148 | 0.025224 | 0.05558 | 0.017268 | 0.0098771 | 0.024218 | 0.0037132 | 0.042258 | 0.012945 | 0.0095115 | 0.0060783 | 0.0026452 | -0.00078793 | -0.0042211 | -0.0076542 | -0.011087 | -0.01452 | -0.017954 | -0.021387
Tararua | 0.0039197 | 0.0049465 | 0.0023037 | 0.0085964 | 0.0090972 | 0.0051682 | 0.016218 | 0.0073578 | 0.0012791 | 0.0051539 | 0.0058874 | 0.0058286 | 0.0057729 | 0.0058513 | 0.0058043 | 0.0057547 | 0.0057113 | 0.0056604 | 0.0057379 | 0.0056951 | 0.0056555 | 0.0039197 | 0.0049465 | 0.0023037 | 0.0085964 | 0.0090972 | 0.0051682 | 0.016218 | 0.0073578 | 0.0012791 | 0.0051539 | 0.0073922 | 0.0075718 | 0.0077515 | 0.0079311 | 0.0081108 | 0.0082904 | 0.0084701 | 0.0086497 | 0.0088294 | 0.009009 | 0.0091887
Tauranga | 0.021773 | 0.048486 | 0.084979 | 0.057345 | 0.023592 | 0.0011112 | 0.070818 | 0.026988 | 0.01113 | 0.0044112 | 0.033036 | 0.033058 | 0.03309 | 0.033124 | 0.033152 | 0.033202 | 0.033238 | 0.033264 | 0.033307 | 0.033333 | 0.033373 | 0.021773 | 0.048486 | 0.084979 | 0.057345 | 0.023592 | 0.0011112 | 0.070818 | 0.026988 | 0.01113 | 0.0044112 | 0.012071 | 0.007891 | 0.0037106 | -0.00046973 | -0.0046501 | -0.0088305 | -0.013011 | -0.017191 | -0.021372 | -0.025552 | -0.029732
Waikato | 0.01655 | 0.076518 | 0.0045346 | 0.013433 | 0.0075597 | 0.011044 | 0.017204 | 0.016032 | 0.0034773 | 0.0040847 | 0.014196 | 0.014227 | 0.014263 | 0.014298 | 0.014308 | 0.014349 | 0.014362 | 0.014392 | 0.014391 | 0.014437 | 0.014451 | 0.01655 | 0.076518 | 0.0045346 | 0.013433 | 0.0075597 | 0.011044 | 0.017204 | 0.016032 | 0.0034773 | 0.0040847 | -0.0013292 | -0.0046697 | -0.0080103 | -0.011351 | -0.014691 | -0.018032 | -0.021372 | -0.024713 | -0.028054 | -0.031394 | -0.034735
Waikino | 0.011057 | 0.085782 | 0 | 0.023544 | 0.00063128 | 0.011001 | 0.010435 | 0.0099975 | 0.0019745 | 0.022879 | 0.015234 | 0.015342 | 0.015365 | 0.01539 | 0.015431 | 0.015461 | 0.015505 | 0.015524 | 0.015551 | 0.015511 | 0.015555 | 0.011057 | 0.085782 | 0 | 0.023544 | 0.00063128 | 0.011001 | 0.010435 | 0.0099975 | 0.0019745 | 0.022879 | 0.0024228 | -0.00036037 | -0.0031435 | -0.0059266 | -0.0087098 | -0.011493 | -0.014276 | -0.017059 | -0.019842 | -0.022625 | -0.025409
Wairarapa | 0.023773 | 0.012458 | 0.017908 | 0.013176 | 0.015669 | 0.0066426 | 0.038797 | 0.016463 | 0.0033534 | 0.014578 | 0.016249 | 0.016275 | 0.016305 | 0.01629 | 0.016295 | 0.016333 | 0.016341 | 0.016324 | 0.016317 | 0.016322 | 0.016333 | 0.023773 | 0.012458 | 0.017908 | 0.013176 | 0.015669 | 0.0066426 | 0.038797 | 0.016463 | 0.0033534 | 0.014578 | 0.013419 | 0.012899 | 0.012378 | 0.011858 | 0.011338 | 0.010817 | 0.010297 | 0.0097763 | 0.0092558 | 0.0087354 | 0.0082149
Whanganui | 0.020724 | 0.0029787 | 0.0091799 | 0.018754 | 0.016179 | 0.0087565 | 0.022009 | 0.010185 | 0.010556 | 0.028935 | 0.017594 | 0.01758 | 0.017571 | 0.017565 | 0.017528 | 0.017531 | 0.0175 | 0.017494 | 0.017496 | 0.017463 | 0.017436 | 0.020724 | 0.0029787 | 0.0091799 | 0.018754 | 0.016179 | 0.0087565 | 0.022009 | 0.010185 | 0.010556 | 0.028935 | 0.019302 | 0.020116 | 0.02093 | 0.021744 | 0.022558 | 0.023372 | 0.024186 | 0.025 | 0.025814 | 0.026628 | 0.027442
Unknown
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.39523 | 0.46588 | 0.57311 | 0.51271 | 0.52312 | 0.34058 | 0.42744 | 0.57572 | 0.64939 | 0.69985
[11 empty] | 0.67837 | 0.70417 | 0.71057 | 0.73772 | 0.76269 | 0.78626 | 0.8106 | 0.83434 | 0.86067 | 0.88639 | 0.912 | [10 empty] | 0.63633 | 0.65816 | 0.67998 | 0.70181 | 0.72363 | 0.74545 | 0.76728 | 0.7891 | 0.81093 | 0.83275 | 0.85458
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.063523 | 0.034009 | 0.078381 | 0.048896 | 0.051508 | 0.027877 | 0.02143 | 0.15603 | 0.022869 | 0.062275 | 0.05959 | 0.060613 | 0.060753 | 0.061345 | 0.062006 | 0.063305 | 0.064702 | 0.065936 | 0.067007 | 0.068125 | 0.069035 | 0.063523 | 0.034009 | 0.078381 | 0.048896 | 0.051508 | 0.027877 | 0.02143 | 0.15603 | 0.022869 | 0.062275 | 0.063113 | 0.064283 | 0.065453 | 0.066622 | 0.067792 | 0.068962 | 0.070131 | 0.071301 | 0.072471 | 0.073641 | 0.07481
Egmont | 0.006571 | 0.03221 | 0.02225 | 0.032611 | 0.057674 | 0.023072 | 0.026493 | 0.032889 | 0.01664 | 0.045759 | 0.050445 | 0.05335 | 0.054088 | 0.057635 | 0.060727 | 0.063213 | 0.065748 | 0.068561 | 0.071455 | 0.074389 | 0.077348 | 0.006571 | 0.03221 | 0.02225 | 0.032611 | 0.057674 | 0.023072 | 0.026493 | 0.032889 | 0.01664 | 0.045759 | 0.037748 | 0.039227 | 0.040705 | 0.042183 | 0.043662 | 0.04514 | 0.046619 | 0.048097 | 0.049576 | 0.051054 | 0.052532
Kinleith | 0.023664 | 0.0085133 | 0.0021804 | 0.0048557 | 0.0015126 | 0.015877 | 0.0087067 | 0.012283 | 0.003565 | 0.024751 | 0.01181 | 0.012025 | 0.01191 | 0.012096 | 0.012295 | 0.012601 | 0.01315 | 0.013572 | 0.013787 | 0.014153 | 0.014526 | 0.023664 | 0.0085133 | 0.0021804 | 0.0048557 | 0.0015126 | 0.015877 | 0.0087067 | 0.012283 | 0.003565 | 0.024751 | 0.01231 | 0.012623 | 0.012935 | 0.013248 | 0.01356 | 0.013873 | 0.014186 | 0.014498 | 0.014811 | 0.015123 | 0.015436
Manawatu | 0.038577 | 0.075476 | 0.10202 | 0.079617 | 0.10926 | 0.045061 | 0.079371 | 0.094847 | 0.047168 | 0.0703 | 0.086047 | 0.087996 | 0.088462 | 0.090401 | 0.092322 | 0.093829 | 0.095417 | 0.096987 | 0.098757 | 0.10059 | 0.10247 | 0.038577 | 0.075476 | 0.10202 | 0.079617 | 0.10926 | 0.045061 | 0.079371 | 0.094847 | 0.047168 | 0.0703 | 0.073721 | 0.073639 | 0.073558 | 0.073476 | 0.073395 | 0.073313 | 0.073231 | 0.07315 | 0.073068 | 0.072987 | 0.072905
Mt Maunganui | 0.01435 | 0.032025 | 0.0081244 | 0.0039072 | 0.022051 | 0.0065091 | 0.0081924 | 0.0058389 | 0.053282 | 0.00862 | 0.023022 | 0.024163 | 0.0242 | 0.024742 | 0.025367 | 0.026761 | 0.028565 | 0.029914 | 0.031088 | 0.032224 | 0.033374 | 0.01435 | 0.032025 | 0.0081244 | 0.0039072 | 0.022051 | 0.0065091 | 0.0081924 | 0.0058389 | 0.053282 | 0.00862 | 0.01906 | 0.019564 | 0.020068 | 0.020571 | 0.021075 | 0.021579 | 0.022083 | 0.022586 | 0.02309 | 0.023594 | 0.024097
Rangitikei | 0.0093971 | 0.018362 | 0.027078 | 0.027777 | 0.047324 | 0.0086975 | 0.022729 | 0.023237 | 0.060756 | 0.037115 | 0.046645 | 0.04925 | 0.049922 | 0.0528 | 0.055567 | 0.057798 | 0.060076 | 0.062642 | 0.065242 | 0.067883 | 0.070549 | 0.0093971 | 0.018362 | 0.027078 | 0.027777 | 0.047324 | 0.0086975 | 0.022729 | 0.023237 | 0.060756 | 0.037115 | 0.044022 | 0.04689 | 0.049759 | 0.052627 | 0.055495 | 0.058363 | 0.061231 | 0.064099 | 0.066967 | 0.069836 | 0.072704
Taranaki | 0.072987 | 0.042799 | 0.061481 | 0.061529 | 0.060415 | 0.044319 | 0.11901 | 0.067655 | 0.091178 | 0.12327 | 0.10678 | 0.11171 | 0.11322 | 0.11869 | 0.1238 | 0.12808 | 0.13228 | 0.13646 | 0.14142 | 0.14648 | 0.15139 | 0.072987 | 0.042799 | 0.061481 | 0.061529 | 0.060415 | 0.044319 | 0.11901 | 0.067655 | 0.091178 | 0.12327 | 0.10708 | 0.11301 | 0.11894 | 0.12487 | 0.1308 | 0.13673 | 0.14266 | 0.14859 | 0.15452 | 0.16045 | 0.16638
Tararua | 0.0075469 | 0.011991 | 0.017067 | 0.012146 | 0.020329 | 0.0054817 | 0.0072315 | 0.044076 | 0.044749 | 0.018174 | 0.028584 | 0.029723 | 0.029862 | 0.031841 | 0.033062 | 0.03399 | 0.034935 | 0.035814 | 0.037706 | 0.038817 | 0.03993 | 0.0075469 | 0.011991 | 0.017067 | 0.012146 | 0.020329 | 0.0054817 | 0.0072315 | 0.044076 | 0.044749 | 0.018174 | 0.033226 | 0.035834 | 0.038443 | 0.041052 | 0.04366 | 0.046269 | 0.048877 | 0.051486 | 0.054094 | 0.056703 | 0.059311
Tauranga | 0.10616 | 0.088977 | 0.13274 | 0.093565 | 0.04969 | 0.071706 | 0.049281 | 0.02527 | 0.063484 | 0.12566 | 0.081146 | 0.082059 | 0.082137 | 0.082651 | 0.083152 | 0.084354 | 0.085777 | 0.086902 | 0.087878 | 0.088811 | 0.089781 | 0.10616 | 0.088977 | 0.13274 | 0.093565 | 0.04969 | 0.071706 | 0.049281 | 0.02527 | 0.063484 | 0.12566 | 0.058949 | 0.055003 | 0.051056 | 0.04711 | 0.043164 | 0.039218 | 0.035271 | 0.031325 | 0.027379 | 0.023432 | 0.019486
Waikato | 0.015717 | 0.027037 | 0.049078 | 0.043108 | 0.026682 | 0.016662 | 0.0096245 | 0.012145 | 0.073039 | 0.028468 | 0.028503 | 0.028445 | 0.028516 | 0.028526 | 0.028484 | 0.028414 | 0.02825 | 0.028161 | 0.028035 | 0.028004 | 0.027907 | 0.015717 | 0.027037 | 0.049078 | 0.043108 | 0.026682 | 0.016662 | 0.0096245 | 0.012145 | 0.073039 | 0.028468 | 0.034877 | 0.035736 | 0.036594 | 0.037452 | 0.038311 | 0.039169 | 0.040027 | 0.040886 | 0.041744 | 0.042602 | 0.043461
Waikino | 0.012052 | 0.046623 | 0.015987 | 0.01441 | 0.0079503 | 0.0012323 | 0.0041085 | 0.0054837 | 0.014777 | 0.02306 | 0.016678 | 0.017161 | 0.017187 | 0.017398 | 0.017627 | 0.018121 | 0.018744 | 0.019217 | 0.01962 | 0.019938 | 0.020364 | 0.012052 | 0.046623 | 0.015987 | 0.01441 | 0.0079503 | 0.0012323 | 0.0041085 | 0.0054837 | 0.014777 | 0.02306 | 0.0074354 | 0.0061386 | 0.0048417 | 0.0035448 | 0.0022479 | 0.00095101 | -0.00034587 | -0.0016428 | -0.0029396 | -0.0042365 | -0.0055334
Wairarapa | 0.02273 | 0.026583 | 0.025966 | 0.052979 | 0.047352 | 0.026266 | 0.025603 | 0.029438 | 0.059341 | 0.051786 | 0.055953 | 0.059013 | 0.060017 | 0.06323 | 0.066346 | 0.069067 | 0.071668 | 0.07416 | 0.077107 | 0.080108 | 0.083146 | 0.02273 | 0.026583 | 0.025966 | 0.052979 | 0.047352 | 0.026266 | 0.025603 | 0.029438 | 0.059341 | 0.051786 | 0.050303 | 0.052757 | 0.055212 | 0.057666 | 0.06012 | 0.062575 | 0.065029 | 0.067483 | 0.069938 | 0.072392 | 0.074846
Whanganui | 0.0019487 | 0.021271 | 0.030757 | 0.03731 | 0.021366 | 0.047814 | 0.045662 | 0.066529 | 0.098547 | 0.080608 | 0.083173 | 0.088669 | 0.090295 | 0.096365 | 0.10193 | 0.10673 | 0.1113 | 0.11602 | 0.12157 | 0.12686 | 0.13218 | 0.0019487 | 0.021271 | 0.030757 | 0.03731 | 0.021366 | 0.047814 | 0.045662 | 0.066529 | 0.098547 | 0.080608 | 0.094489 | 0.10345 | 0.11242 | 0.12138 | 0.13035 | 0.13931 | 0.14828 | 0.15724 | 0.16621 | 0.17517 | 0.18414
The remainder
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 0.64985 | 0.52312 | 0.55009 | 0.43537 | 0.5864 | 0.3441 | 0.35757 | 0.28835 | 0.43099 | 0.41128
[11 empty] | 0.4266 | 0.42652 | 0.42645 | 0.42649 | 0.42645 | 0.42644 | 0.42636 | 0.42642 | 0.42638 | 0.42639 | 0.42637 | [10 empty] | 0.30517 | 0.27743 | 0.24969 | 0.22196 | 0.19422 | 0.16649 | 0.13875 | 0.11102 | 0.08328 | 0.055545 | 0.027809
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.081474 | 0.024141 | 0.11544 | 0.037766 | 0.074006 | 0.01742 | 0.017678 | 0.011638 | 0.023489 | 0.046633 | 0.042325 | 0.042414 | 0.042511 | 0.04261 | 0.042754 | 0.042868 | 0.04286 | 0.042943 | 0.043046 | 0.043177 | 0.043174 | 0.081474 | 0.024141 | 0.11544 | 0.037766 | 0.074006 | 0.01742 | 0.017678 | 0.011638 | 0.023489 | 0.046633 | 0.013169 | 0.0073873 | 0.0016056 | -0.0041761 | -0.0099578 | -0.015739 | -0.021521 | -0.027303 | -0.033085 | -0.038866 | -0.044648
Egmont | 0.0077758 | 0.018565 | 0.037317 | 0.0094344 | 0.0093379 | 0.02234 | 0.028402 | 0.012597 | 0.019301 | 0.027506 | 0.018813 | 0.018736 | 0.018668 | 0.018713 | 0.01867 | 0.018617 | 0.018582 | 0.018625 | 0.018574 | 0.018537 | 0.018509 | 0.0077758 | 0.018565 | 0.037317 | 0.0094344 | 0.0093379 | 0.02234 | 0.028402 | 0.012597 | 0.019301 | 0.027506 | 0.023558 | 0.02434 | 0.025122 | 0.025904 | 0.026686 | 0.027468 | 0.02825 | 0.029032 | 0.029814 | 0.030596 | 0.031378
Kinleith | 0.03336 | 0.0024796 | 0.0011344 | 0.022527 | 0.0013344 | 0.0077849 | 0.011827 | 0.013068 | 0.0026186 | 0.031435 | 0.011393 | 0.01128 | 0.011172 | 0.011191 | 0.011222 | 0.011126 | 0.011159 | 0.011176 | 0.011084 | 0.011114 | 0.011149 | 0.03336 | 0.0024796 | 0.0011344 | 0.022527 | 0.0013344 | 0.0077849 | 0.011827 | 0.013068 | 0.0026186 | 0.031435 | 0.013346 | 0.013453 | 0.01356 | 0.013667 | 0.013774 | 0.013881 | 0.013988 | 0.014095 | 0.014202 | 0.014309 | 0.014416
Manawatu | 0.12579 | 0.13249 | 0.10463 | 0.094959 | 0.030654 | 0.038183 | 0.035723 | 0.067944 | 0.040736 | 0.083582 | 0.068945 | 0.068919 | 0.06882 | 0.06864 | 0.068542 | 0.068404 | 0.068331 | 0.068247 | 0.068115 | 0.068033 | 0.067981 | 0.12579 | 0.13249 | 0.10463 | 0.094959 | 0.030654 | 0.038183 | 0.035723 | 0.067944 | 0.040736 | 0.083582 | 0.029612 | 0.021274 | 0.012936 | 0.0045988 | -0.0037388 | -0.012076 | -0.020414 | -0.028752 | -0.037089 | -0.045427 | -0.053764
Mt Maunganui | 0.048267 | 0.016337 | 0.028883 | 0.0064431 | 0.025745 | 0.015188 | 0.010419 | 0.0076049 | 0.0067672 | 0.0076694 | 0.013515 | 0.013532 | 0.013553 | 0.013545 | 0.013582 | 0.013581 | 0.01362 | 0.01361 | 0.013635 | 0.013642 | 0.013654 | 0.048267 | 0.016337 | 0.028883 | 0.0064431 | 0.025745 | 0.015188 | 0.010419 | 0.0076049 | 0.0067672 | 0.0076694 | -0.00058041 | -0.0038373 | -0.0070941 | -0.010351 | -0.013608 | -0.016865 | -0.020122 | -0.023378 | -0.026635 | -0.029892 | -0.033149
Rangitikei | 0.012939 | 0.0090633 | 0.010159 | 0.0066717 | 0.028451 | 0.0096349 | 0.017703 | 0.01101 | 0.026337 | 0.011907 | 0.01362 | 0.013573 | 0.01353 | 0.013491 | 0.013468 | 0.013438 | 0.013421 | 0.013467 | 0.013437 | 0.013418 | 0.013405 | 0.012939 | 0.0090633 | 0.010159 | 0.0066717 | 0.028451 | 0.0096349 | 0.017703 | 0.01101 | 0.026337 | 0.011907 | 0.018726 | 0.019515 | 0.020304 | 0.021093 | 0.021882 | 0.02267 | 0.023459 | 0.024248 | 0.025037 | 0.025826 | 0.026615
Taranaki | 0.10419 | 0.070418 | 0.044212 | 0.031249 | 0.080719 | 0.06529 | 0.079866 | 0.059067 | 0.065286 | 0.053919 | 0.059822 | 0.059687 | 0.059664 | 0.059557 | 0.059433 | 0.059362 | 0.05926 | 0.05916 | 0.059092 | 0.059069 | 0.058987 | 0.10419 | 0.070418 | 0.044212 | 0.031249 | 0.080719 | 0.06529 | 0.079866 | 0.059067 | 0.065286 | 0.053919 | 0.055967 | 0.054247 | 0.052528 | 0.050809 | 0.04909 | 0.047371 | 0.045652 | 0.043933 | 0.042214 | 0.040495 | 0.038776
Tararua | 0.0049115 | 0.0017866 | 0.0019181 | 0.0024149 | 0.009841 | 0.0023653 | 0.003665 | 0.0040525 | 0.012022 | 0.0088882 | 0.0052271 | 0.0051749 | 0.0051254 | 0.005195 | 0.0051533 | 0.0051093 | 0.0050708 | 0.0050256 | 0.0050944 | 0.0050564 | 0.0050212 | 0.0049115 | 0.0017866 | 0.0019181 | 0.0024149 | 0.009841 | 0.0023653 | 0.003665 | 0.0040525 | 0.012022 | 0.0088882 | 0.0089995 | 0.0096928 | 0.010386 | 0.011079 | 0.011773 | 0.012466 | 0.013159 | 0.013852 | 0.014546 | 0.015239 | 0.015932
Tauranga | 0.089886 | 0.13011 | 0.057961 | 0.1311 | 0.1989 | 0.046914 | 0.055154 | 0.042831 | 0.11675 | 0.041833 | 0.088147 | 0.088207 | 0.088291 | 0.088382 | 0.088458 | 0.08859 | 0.088687 | 0.088757 | 0.088872 | 0.088941 | 0.089047 | 0.089886 | 0.13011 | 0.057961 | 0.1311 | 0.1989 | 0.046914 | 0.055154 | 0.042831 | 0.11675 | 0.041833 | 0.058429 | 0.052481 | 0.046533 | 0.040585 | 0.034637 | 0.028688 | 0.02274 | 0.016792 | 0.010844 | 0.0048957 | -0.0010525
Waikato | 0.049173 | 0.03679 | 0.031221 | 0.027682 | 0.034517 | 0.015663 | 0.017327 | 0.006781 | 0.036034 | 0.013368 | 0.024203 | 0.024257 | 0.024317 | 0.024378 | 0.024394 | 0.024465 | 0.024486 | 0.024539 | 0.024536 | 0.024615 | 0.024638 | 0.049173 | 0.03679 | 0.031221 | 0.027682 | 0.034517 | 0.015663 | 0.017327 | 0.006781 | 0.036034 | 0.013368 | 0.010201 | 0.0071724 | 0.0041442 | 0.001116 | -0.0019122 | -0.0049404 | -0.0079686 | -0.010997 | -0.014025 | -0.017053 | -0.020081
Waikino | 0.013237 | 0.010472 | 0.037026 | 0.0045819 | 0.012322 | 0.022433 | 0.024395 | 0.0056877 | 0.038677 | 0.01492 | 0.018557 | 0.018689 | 0.018717 | 0.018747 | 0.018797 | 0.018834 | 0.018887 | 0.018911 | 0.018943 | 0.018895 | 0.018948 | 0.013237 | 0.010472 | 0.037026 | 0.0045819 | 0.012322 | 0.022433 | 0.024395 | 0.0056877 | 0.038677 | 0.01492 | 0.022556 | 0.023317 | 0.024077 | 0.024837 | 0.025597 | 0.026357 | 0.027118 | 0.027878 | 0.028638 | 0.029398 | 0.030159
Wairarapa | 0.018425 | 0.05252 | 0.016543 | 0.033474 | 0.039142 | 0.042711 | 0.018685 | 0.01059 | 0.013175 | 0.031178 | 0.027115 | 0.027158 | 0.027208 | 0.027184 | 0.027191 | 0.027254 | 0.027268 | 0.02724 | 0.027228 | 0.027236 | 0.027254 | 0.018425 | 0.05252 | 0.016543 | 0.033474 | 0.039142 | 0.042711 | 0.018685 | 0.01059 | 0.013175 | 0.031178 | 0.019937 | 0.018536 | 0.017135 | 0.015733 | 0.014332 | 0.012931 | 0.01153 | 0.010128 | 0.0087271 | 0.0073258 | 0.0059245
Whanganui | 0.060423 | 0.017949 | 0.063656 | 0.027067 | 0.041427 | 0.038176 | 0.036724 | 0.035479 | 0.029793 | 0.038446 | 0.034916 | 0.034888 | 0.03487 | 0.034859 | 0.034784 | 0.034792 | 0.03473 | 0.034717 | 0.034722 | 0.034655 | 0.034603 | 0.060423 | 0.017949 | 0.063656 | 0.027067 | 0.041427 | 0.038176 | 0.036724 | 0.035479 | 0.029793 | 0.038446 | 0.031246 | 0.029852 | 0.028457 | 0.027063 | 0.025669 | 0.024275 | 0.02288 | 0.021486 | 0.020092 | 0.018698 | 0.017304
Totals
[11 empty] | Forecast | [10 empty] | Linear trend
Total | 2.2909 | 2.4442 | 2.2671 | 2.354 | 2.4935 | 1.6383 | 2.1398 | 2.0953 | 1.954 | 2.4541
[11 empty] | 2.2945 | 2.3218 | 2.2905 | 2.278 | 2.2804 | 2.2651 | 2.2517 | 2.2599 | 2.2834 | 2.3061 | 2.3305 | [10 empty] | 2.0691 | 2.0429 | 2.0167 | 1.9905 | 1.9644 | 1.9382 | 1.912 | 1.8858 | 1.8596 | 1.8334 | 1.8073
Planning Area | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Coromandel | 0.39955 | 0.34477 | 0.38951 | 0.24029 | 0.224 | 0.16617 | 0.15164 | 0.38857 | 0.1087 | 0.22033 | 0.23702 | 0.23921 | 0.24027 | 0.24188 | 0.2437 | 0.23638 | 0.22883 | 0.22718 | 0.22889 | 0.23075 | 0.23197 | 0.39955 | 0.34477 | 0.38951 | 0.24029 | 0.224 | 0.16617 | 0.15164 | 0.38857 | 0.1087 | 0.22033 | 0.14356 | 0.12177 | 0.099992 | 0.078211 | 0.05643 | 0.034648 | 0.012867 | -0.0089146 | -0.030696 | -0.052477 | -0.074259
Egmont | 0.090967 | 0.11828 | 0.13829 | 0.12331 | 0.19153 | 0.12286 | 0.15444 | 0.13782 | 0.10719 | 0.17482 | 0.15699 | 0.15936 | 0.15674 | 0.15583 | 0.15625 | 0.15811 | 0.15974 | 0.1638 | 0.16652 | 0.1691 | 0.17205 | 0.090967 | 0.11828 | 0.13829 | 0.12331 | 0.19153 | 0.12286 | 0.15444 | 0.13782 | 0.10719 | 0.17482 | 0.15927 | 0.1635 | 0.16774 | 0.17198 | 0.17622 | 0.18046 | 0.1847 | 0.18894 | 0.19318 | 0.19742 | 0.20166
Kinleith | 0.081624 | 0.020784 | 0.019153 | 0.056253 | 0.010797 | 0.03077 | 0.031747 | 0.034412 | 0.031876 | 0.098492 | 0.037693 | 0.037745 | 0.037448 | 0.037783 | 0.038087 | 0.037661 | 0.037741 | 0.038022 | 0.038058 | 0.038521 | 0.038971 | 0.081624 | 0.020784 | 0.019153 | 0.056253 | 0.010797 | 0.03077 | 0.031747 | 0.034412 | 0.031876 | 0.098492 | 0.049998 | 0.051526 | 0.053055 | 0.054583 | 0.056112 | 0.05764 | 0.059169 | 0.060697 | 0.062226 | 0.063755 | 0.065283
Manawatu | 0.30856 | 0.44337 | 0.39086 | 0.36766 | 0.35843 | 0.22113 | 0.29435 | 0.3234 | 0.19464 | 0.38104 | 0.32797 | 0.33073 | 0.32457 | 0.31862 | 0.31712 | 0.31668 | 0.3178 | 0.31981 | 0.32098 | 0.32264 | 0.32442 | 0.30856 | 0.44337 | 0.39086 | 0.36766 | 0.35843 | 0.22113 | 0.29435 | 0.3234 | 0.19464 | 0.38104 | 0.2689 | 0.25809 | 0.24729 | 0.23648 | 0.22567 | 0.21486 | 0.20405 | 0.19325 | 0.18244 | 0.17163 | 0.16082
Mt Maunganui | 0.13727 | 0.094222 | 0.093922 | 0.10755 | 0.085944 | 0.056118 | 0.041978 | 0.084401 | 0.11497 | 0.061431 | 0.087016 | 0.088196 | 0.087959 | 0.088228 | 0.08749 | 0.084514 | 0.08127 | 0.079292 | 0.080002 | 0.080561 | 0.081466 | 0.13727 | 0.094222 | 0.093922 | 0.10755 | 0.085944 | 0.056118 | 0.041978 | 0.084401 | 0.11497 | 0.061431 | 0.060732 | 0.055814 | 0.050896 | 0.045979 | 0.041061 | 0.036143 | 0.031225 | 0.026307 | 0.02139 | 0.016472 | 0.011554
Rangitikei | 0.061237 | 0.056243 | 0.10049 | 0.10236 | 0.16556 | 0.079438 | 0.092423 | 0.092084 | 0.13585 | 0.096218 | 0.12574 | 0.12769 | 0.12415 | 0.12342 | 0.12491 | 0.12704 | 0.12934 | 0.13242 | 0.13497 | 0.13762 | 0.1404 | 0.061237 | 0.056243 | 0.10049 | 0.10236 | 0.16556 | 0.079438 | 0.092423 | 0.092084 | 0.13585 | 0.096218 | 0.12199 | 0.12632 | 0.13065 | 0.13498 | 0.13931 | 0.14363 | 0.14796 | 0.15229 | 0.15662 | 0.16094 | 0.16527
Taranaki | 0.33034 | 0.26028 | 0.26054 | 0.26448 | 0.38898 | 0.22558 | 0.35614 | 0.26007 | 0.28084 | 0.38087 | 0.32932 | 0.33398 | 0.32685 | 0.32181 | 0.31988 | 0.3203 | 0.32162 | 0.32403 | 0.32767 | 0.33087 | 0.33471 | 0.33034 | 0.26028 | 0.26054 | 0.26448 | 0.38898 | 0.22558 | 0.35614 | 0.26007 | 0.28084 | 0.38087 | 0.32441 | 0.3287 | 0.33299 | 0.33728 | 0.34157 | 0.34586 | 0.35015 | 0.35445 | 0.35874 | 0.36303 | 0.36732
Tararua | 0.043063 | 0.036603 | 0.044187 | 0.04176 | 0.079147 | 0.036249 | 0.05808 | 0.093195 | 0.078563 | 0.0672 | 0.07039 | 0.071266 | 0.069998 | 0.071508 | 0.072224 | 0.072869 | 0.073756 | 0.074927 | 0.077658 | 0.078594 | 0.079708 | 0.043063 | 0.036603 | 0.044187 | 0.04176 | 0.079147 | 0.036249 | 0.05808 | 0.093195 | 0.078563 | 0.0672 | 0.083207 | 0.087825 | 0.092444 | 0.097062 | 0.10168 | 0.1063 | 0.11092 | 0.11554 | 0.12016 | 0.12477 | 0.12939
Tauranga | 0.30446 | 0.46031 | 0.31434 | 0.41358 | 0.45489 | 0.22424 | 0.26585 | 0.22458 | 0.28144 | 0.29514 | 0.30525 | 0.30548 | 0.30439 | 0.3048 | 0.30324 | 0.29339 | 0.28317 | 0.27689 | 0.27695 | 0.27723 | 0.27789 | 0.30446 | 0.46031 | 0.31434 | 0.41358 | 0.45489 | 0.22424 | 0.26585 | 0.22458 | 0.28144 | 0.29514 | 0.24193 | 0.22703 | 0.21213 | 0.19723 | 0.18233 | 0.16743 | 0.15253 | 0.13763 | 0.12273 | 0.10783 | 0.092931
Waikato | 0.16911 | 0.18884 | 0.13695 | 0.15626 | 0.12916 | 0.12369 | 0.08116 | 0.068548 | 0.19319 | 0.090811 | 0.12715 | 0.12737 | 0.12769 | 0.12789 | 0.12796 | 0.12333 | 0.11872 | 0.11703 | 0.11654 | 0.11655 | 0.11622 | 0.16911 | 0.18884 | 0.13695 | 0.15626 | 0.12916 | 0.12369 | 0.08116 | 0.068548 | 0.19319 | 0.090811 | 0.092207 | 0.084649 | 0.077092 | 0.069534 | 0.061977 | 0.05442 | 0.046862 | 0.039305 | 0.031748 | 0.02419 | 0.016633
Waikino | 0.14053 | 0.20711 | 0.098331 | 0.12668 | 0.046836 | 0.069431 | 0.20326 | 0.05786 | 0.094861 | 0.12915 | 0.10159 | 0.10302 | 0.10348 | 0.10404 | 0.10468 | 0.10316 | 0.10179 | 0.10154 | 0.10196 | 0.10211 | 0.10261 | 0.14053 | 0.20711 | 0.098331 | 0.12668 | 0.046836 | 0.069431 | 0.20326 | 0.05786 | 0.094861 | 0.12915 | 0.089467 | 0.084388 | 0.079308 | 0.074228 | 0.069149 | 0.064069 | 0.058989 | 0.05391 | 0.04883 | 0.04375 | 0.038671
Wairarapa | 0.10282 | 0.14041 | 0.12446 | 0.20135 | 0.19854 | 0.12101 | 0.2374 | 0.16598 | 0.13152 | 0.22604 | 0.19047 | 0.19386 | 0.1858 | 0.17979 | 0.17902 | 0.18195 | 0.18444 | 0.18696 | 0.19009 | 0.19384 | 0.19737 | 0.10282 | 0.14041 | 0.12446 | 0.20135 | 0.19854 | 0.12101 | 0.2374 | 0.16598 | 0.13152 | 0.22604 | 0.20779 | 0.21557 | 0.22336 | 0.23115 | 0.23894 | 0.24672 | 0.25451 | 0.2623 | 0.27009 | 0.27788 | 0.28566
Whanganui | 0.12138 | 0.072971 | 0.15611 | 0.15249 | 0.15965 | 0.1616 | 0.17128 | 0.16435 | 0.20031 | 0.23253 | 0.19788 | 0.20386 | 0.20109 | 0.20244 | 0.20583 | 0.20968 | 0.21353 | 0.21801 | 0.22309 | 0.22775 | 0.23272 | 0.12138 | 0.072971 | 0.15611 | 0.15249 | 0.15965 | 0.1616 | 0.17128 | 0.16435 | 0.20031 | 0.23253 | 0.22564 | 0.23771 | 0.24978 | 0.26184 | 0.27391 | 0.28598 | 0.29805 | 0.31012 | 0.32218 | 0.33425 | 0.34632

## Output
Output - Unplanned SAIDI and SAIFI
Unplanned SAIDI
Forecast
|  | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Calculated Non-normalised Totals | 289.1515 | 236.2655 | 184.2754 | 217.6434 | 300.9311 | 115.7691 | 190.3603 | 231.7952 | 171.9007 | 196.1955 | 208.8175 | 210.8408 | 205.4531 | 201.1463 | 199.7925 | 197.4009 | 195.0392 | 195.4051 | 197.2708 | 198.5241 | 200.1069
| Historical Fault Information (Non-normalised) | 2008: 292.5216; 2009: 236.2655; 2010: 184.2754; 2011: 217.6434; 2012: 300.9311; 2013: 115.7691; 2014: 190.3603; 2015: 231.7952; 2016: 171.9007; 2017: 196.1955
| Disclosed (Normalised) | 2010: 160.2534; 2011: 185.4799; 2012: 179.4909; 2013: 115.7846; 2014: 170.8535; 2015: 171.65; 2016: 171.4; 2017: 158.52
| Forecast only | Forecast 2018: 208.8175; Forecast 2019: 210.8408; Forecast 2020: 205.4531; Forecast 2021: 201.1463; Forecast 2022: 199.7925; Forecast 2023: 197.4009; Forecast 2024: 195.0392; Forecast 2025: 195.4051; Forecast 2026: 197.2708; Forecast 2027: 198.5241; Forecast 2028: 200.1069
All | Category | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Equipment Related | Poles | 1.264 | 1.5166 | 1.2991 | 4.6808 | 3.5281 | 2.0677 | 4.4908 | 2.2979 | 3.6058 | 0.7913 | 3.0159 | 3.0349 | 2.923 | 2.85 | 2.7714 | 2.6902 | 2.5997 | 2.5239 | 2.4803 | 2.4411 | 2.3757
| Xarms | 21.7855 | 14.639 | 16.0717 | 23.0731 | 27.7836 | 17.4652 | 23.3919 | 19.8116 | 16.3802 | 17.834 | 19.7802 | 19.805 | 19.7584 | 19.566 | 19.1854 | 18.6475 | 18.225 | 18.1408 | 18.0585 | 17.9415 | 17.7931
| Conductor | 12.1573 | 9.9913 | 16.2623 | 33.1632 | 35.7275 | 11.4779 | 29.309 | 25.7811 | 21.1722 | 19.9193 | 23.919 | 23.8926 | 23.7054 | 23.3768 | 22.8243 | 22.1979 | 21.5718 | 20.9947 | 20.5481 | 20.0941 | 20.0795
| Transformers | 2.0792 | 3.7463 | 1.2509 | 2.3298 | 4.818 | 2.5609 | 1.159 | 4.2522 | 4.0459 | 2.3464 | 6.2506 | 6.5065 | 6.823 | 7.127 | 7.4561 | 7.7567 | 8.0796 | 8.487 | 8.7531 | 9.0057 | 9.194
| Fuses | 1.3151 | 1.0693 | 1.1135 | 1.9544 | 1.553 | 1.2722 | 1.4249 | 5.563 | 5.5067 | 5.3584 | 5.263 | 5.4869 | 5.6655 | 5.8709 | 6.0472 | 6.2281 | 6.3283 | 6.6131 | 6.8622 | 6.9341 | 7.0057
| Subtrans | 19.6485 | 13.4269 | 23.903 | 12.7745 | 6.769 | 10.2634 | 17.4055 | 2.5378 | 11.8489 | 11.6565 | 9.6075 | 9.5381 | 9.4636 | 9.3944 | 9.325 | 9.2508 | 9.2132 | 9.1535 | 9.1159 | 9.1164 | 9.1149
| Other Equipment | 9.0444 | 15.6301 | 10.7536 | 10.0579 | 11.2957 | 9.554 | 11.0704 | 21.5421 | 7.7417 | 12.8168 | 12.874 | 12.8537 | 12.8268 | 12.8035 | 12.7831 | 12.7566 | 12.7462 | 12.7317 | 12.7124 | 12.7108 | 12.7134
All others | Vegetation | 12.2271 | 12.4981 | 14.1164 | 39.4129 | 104.0789 | 13.4909 | 34.3336 | 60.0675 | 13.2679 | 22.9363 | 29.6148 | 29.7083 | 23.8619 | 18.0428 | 15.7446 | 12.7445 | 9.6758 | 8.4527 | 8.4704 | 8.4692 | 8.4665
| Adverse Weather | 158.1165 | 103.7444 | 17.039 | 36.9118 | 43.8584 | 6.527 | 24.4302 | 40.4887 | 9.4636 | 28.3485 | 29.2967 | 28.873 | 28.4424 | 28.0435 | 27.6065 | 27.1739 | 26.9458 | 26.8047 | 26.8437 | 26.815 | 26.8001
| Unknown | 11.4713 | 23.4565 | 23.8883 | 26.2833 | 26.5732 | 18.5295 | 19.7671 | 29.9752 | 37.5201 | 44.7277 | 36.888 | 38.6894 | 39.3869 | 41.3233 | 43.1557 | 44.911 | 46.5411 | 48.2675 | 50.1021 | 51.6692 | 53.2348
| Everything Else | 40.0427 | 36.5469 | 58.5777 | 27.0018 | 34.9459 | 22.5603 | 23.5778 | 19.4781 | 41.3476 | 29.4602 | 32.3078 | 32.4522 | 32.5961 | 32.7481 | 32.8931 | 33.0438 | 33.1126 | 33.2355 | 33.3242 | 33.3269 | 33.3291
Forecast Only | Category | [10 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Equipment Related | Poles | [10 empty] | 3.0159 | 3.0349 | 2.923 | 2.85 | 2.7714 | 2.6902 | 2.5997 | 2.5239 | 2.4803 | 2.4411 | 2.3757
| Xarms | [10 empty] | 19.7802 | 19.805 | 19.7584 | 19.566 | 19.1854 | 18.6475 | 18.225 | 18.1408 | 18.0585 | 17.9415 | 17.7931
| Conductor | [10 empty] | 23.919 | 23.8926 | 23.7054 | 23.3768 | 22.8243 | 22.1979 | 21.5718 | 20.9947 | 20.5481 | 20.0941 | 20.0795
| Transformers | [10 empty] | 6.2506 | 6.5065 | 6.823 | 7.127 | 7.4561 | 7.7567 | 8.0796 | 8.487 | 8.7531 | 9.0057 | 9.194
| Fuses | [10 empty] | 5.263 | 5.4869 | 5.6655 | 5.8709 | 6.0472 | 6.2281 | 6.3283 | 6.6131 | 6.8622 | 6.9341 | 7.0057
| Subtrans | [10 empty] | 9.6075 | 9.5381 | 9.4636 | 9.3944 | 9.325 | 9.2508 | 9.2132 | 9.1535 | 9.1159 | 9.1164 | 9.1149
| Other Equipment | [10 empty] | 12.874 | 12.8537 | 12.8268 | 12.8035 | 12.7831 | 12.7566 | 12.7462 | 12.7317 | 12.7124 | 12.7108 | 12.7134
All others | Vegetation | [10 empty] | 29.6148 | 29.7083 | 23.8619 | 18.0428 | 15.7446 | 12.7445 | 9.6758 | 8.4527 | 8.4704 | 8.4692 | 8.4665
| Adverse Weather | [10 empty] | 29.2967 | 28.873 | 28.4424 | 28.0435 | 27.6065 | 27.1739 | 26.9458 | 26.8047 | 26.8437 | 26.815 | 26.8001
| Unknown | [10 empty] | 36.888 | 38.6894 | 39.3869 | 41.3233 | 43.1557 | 44.911 | 46.5411 | 48.2675 | 50.1021 | 51.6692 | 53.2348
| Everything Else | [10 empty] | 32.3078 | 32.4522 | 32.5961 | 32.7481 | 32.8931 | 33.0438 | 33.1126 | 33.2355 | 33.3242 | 33.3269 | 33.3291
Uncertainity - Used on graph
Weather Uncertainty Upper Bound | [11 empty] | 185.1619 | 185.1619 | 185.1619 | 185.1619 | 185.1619 | 185.1619 | 185.1619 | 185.1619 | 185.1619 | 185.1619 | 185.1619
Weather Uncertainty base | [10 empty] | 213.7658 | 116.2365 | 118.2599 | 112.8722 | 108.5653 | 107.2116 | 104.8199 | 102.4582 | 102.8241 | 104.6898 | 105.9431 | 107.5259
Unplanned SAIFI
Forecast
|  | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
| Calculated Non-normalised Totals | 2.2909 | 2.4442 | 2.2671 | 2.354 | 2.4935 | 1.6383 | 2.1398 | 2.0953 | 1.954 | 2.4541 | 2.2945 | 2.3218 | 2.2905 | 2.278 | 2.2804 | 2.2651 | 2.2517 | 2.2599 | 2.2834 | 2.3061 | 2.3305
| Historical Fault Information (Non-normalised) | 2008: 2.3176; 2009: 2.4442; 2010: 2.2671; 2011: 2.354; 2012: 2.4935; 2013: 1.6383; 2014: 2.1398; 2015: 2.0953; 2016: 1.954; 2017: 2.4541
| Disclosed | 2010: 2.2689; 2011: 2.3524; 2012: 2.4346; 2013: 1.664; 2014: 2.1392; 2015: 2.09; 2016: 1.96; 2017: 2.2565
| Forecast | Forecast 2018: 2.2945; Forecast 2019: 2.3218; Forecast 2020: 2.2905; Forecast 2021: 2.278; Forecast 2022: 2.2804; Forecast 2023: 2.2651; Forecast 2024: 2.2517; Forecast 2025: 2.2599; Forecast 2026: 2.2834; Forecast 2027: 2.3061; Forecast 2028: 2.3305
All | Category | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Equipment Related | Poles | 0.0075501 | 0.012226 | 0.0076789 | 0.023361 | 0.016016 | 0.019236 | 0.017614 | 0.014344 | 0.019936 | 0.0048574 | 0.013951 | 0.013968 | 0.013525 | 0.013126 | 0.012722 | 0.012293 | 0.011832 | 0.011449 | 0.011199 | 0.011004 | 0.010719
| Xarms | 0.27531 | 0.21265 | 0.19034 | 0.21606 | 0.23926 | 0.23207 | 0.24742 | 0.20305 | 0.20314 | 0.23919 | 0.2146 | 0.21485 | 0.21417 | 0.21167 | 0.2068 | 0.20024 | 0.19511 | 0.19334 | 0.19149 | 0.18958 | 0.18738
| Conductor | 0.13433 | 0.086659 | 0.13739 | 0.21679 | 0.17496 | 0.10372 | 0.15194 | 0.18652 | 0.19429 | 0.18056 | 0.16251 | 0.16236 | 0.16114 | 0.15895 | 0.15506 | 0.15026 | 0.14537 | 0.1403 | 0.13733 | 0.13487 | 0.13482
| Transformers | 0.019821 | 0.021169 | 0.016103 | 0.0186 | 0.029526 | 0.023147 | 0.014041 | 0.018498 | 0.020175 | 0.026758 | 0.028546 | 0.029004 | 0.029618 | 0.030236 | 0.030865 | 0.031474 | 0.03231 | 0.033363 | 0.033894 | 0.034707 | 0.035288
| Fuses | 0.022765 | 0.02644 | 0.022474 | 0.030962 | 0.027939 | 0.025841 | 0.025815 | 0.042817 | 0.044235 | 0.047175 | 0.059031 | 0.059988 | 0.060364 | 0.060975 | 0.061306 | 0.061656 | 0.061977 | 0.063728 | 0.065353 | 0.06618 | 0.066972
| Subtrans | 0.15148 | 0.24777 | 0.21106 | 0.13725 | 0.11189 | 0.15451 | 0.19333 | 0.055395 | 0.10157 | 0.1258 | 0.10752 | 0.10756 | 0.10757 | 0.10764 | 0.10768 | 0.1077 | 0.10768 | 0.10768 | 0.10777 | 0.10776 | 0.10775
| Other Equipment | 0.10817 | 0.16928 | 0.16869 | 0.16981 | 0.13722 | 0.14464 | 0.1569 | 0.15277 | 0.11386 | 0.25289 | 0.1546 | 0.15463 | 0.15458 | 0.15455 | 0.15456 | 0.15451 | 0.15451 | 0.15454 | 0.15447 | 0.15445 | 0.15447
All others | Vegetation | 0.16169 | 0.14721 | 0.14033 | 0.30742 | 0.39861 | 0.16241 | 0.25891 | 0.3381 | 0.1231 | 0.24004 | 0.21391 | 0.21393 | 0.17773 | 0.14177 | 0.12739 | 0.099329 | 0.071182 | 0.05986 | 0.059872 | 0.059883 | 0.059876
| Adverse Weather | 0.3647 | 0.5318 | 0.24988 | 0.28569 | 0.24852 | 0.08803 | 0.28877 | 0.21972 | 0.053251 | 0.22566 | 0.23483 | 0.23479 | 0.23475 | 0.2349 | 0.23487 | 0.23489 | 0.2348 | 0.2349 | 0.23495 | 0.23493 | 0.23487
| Unknown | 0.39523 | 0.46588 | 0.57311 | 0.51271 | 0.52312 | 0.34058 | 0.42744 | 0.57572 | 0.64939 | 0.69985 | 0.67837 | 0.70417 | 0.71057 | 0.73772 | 0.76269 | 0.78626 | 0.8106 | 0.83434 | 0.86067 | 0.88639 | 0.912
| Everything Else | 0.64985 | 0.52312 | 0.55009 | 0.43537 | 0.5864 | 0.3441 | 0.35757 | 0.28835 | 0.43099 | 0.41128 | 0.4266 | 0.42652 | 0.42645 | 0.42649 | 0.42645 | 0.42644 | 0.42636 | 0.42642 | 0.42638 | 0.42639 | 0.42637
Forecast Only | Category | [10 empty] | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
Equipment Related | Poles | [10 empty] | 0.013951 | 0.013968 | 0.013525 | 0.013126 | 0.012722 | 0.012293 | 0.011832 | 0.011449 | 0.011199 | 0.011004 | 0.010719
| Xarms | [10 empty] | 0.2146 | 0.21485 | 0.21417 | 0.21167 | 0.2068 | 0.20024 | 0.19511 | 0.19334 | 0.19149 | 0.18958 | 0.18738
| Conductor | [10 empty] | 0.16251 | 0.16236 | 0.16114 | 0.15895 | 0.15506 | 0.15026 | 0.14537 | 0.1403 | 0.13733 | 0.13487 | 0.13482
| Transformers | [10 empty] | 0.028546 | 0.029004 | 0.029618 | 0.030236 | 0.030865 | 0.031474 | 0.03231 | 0.033363 | 0.033894 | 0.034707 | 0.035288
| Fuses | [10 empty] | 0.059031 | 0.059988 | 0.060364 | 0.060975 | 0.061306 | 0.061656 | 0.061977 | 0.063728 | 0.065353 | 0.06618 | 0.066972
| Subtrans | [10 empty] | 0.10752 | 0.10756 | 0.10757 | 0.10764 | 0.10768 | 0.1077 | 0.10768 | 0.10768 | 0.10777 | 0.10776 | 0.10775
| Other Equipment | [10 empty] | 0.1546 | 0.15463 | 0.15458 | 0.15455 | 0.15456 | 0.15451 | 0.15451 | 0.15454 | 0.15447 | 0.15445 | 0.15447
All others | Vegetation | [10 empty] | 0.21391 | 0.21393 | 0.17773 | 0.14177 | 0.12739 | 0.099329 | 0.071182 | 0.05986 | 0.059872 | 0.059883 | 0.059876
| Adverse Weather | [10 empty] | 0.23483 | 0.23479 | 0.23475 | 0.2349 | 0.23487 | 0.23489 | 0.2348 | 0.2349 | 0.23495 | 0.23493 | 0.23487
| Unknown | [10 empty] | 0.67837 | 0.70417 | 0.71057 | 0.73772 | 0.76269 | 0.78626 | 0.8106 | 0.83434 | 0.86067 | 0.88639 | 0.912
| Everything Else | [10 empty] | 0.4266 | 0.42652 | 0.42645 | 0.42649 | 0.42645 | 0.42644 | 0.42636 | 0.42642 | 0.42638 | 0.42639 | 0.42637
Uncertainity - Used on graph
Weather Uncertainty | [11 empty] | 0.85517 | 0.85517 | 0.85517 | 0.85517 | 0.85517 | 0.85517 | 0.85517 | 0.85517 | 0.85517 | 0.85517 | 0.85517
Weather Uncertainty base | [10 empty] | 2.2158 | 1.8669 | 1.8942 | 1.8629 | 1.8505 | 1.8528 | 1.8375 | 1.8242 | 1.8323 | 1.8558 | 1.8785 | 1.9029
Graphs
End