## CoverSheet
Electricity Distribution Business
Price-Quality Regulation from 1 April 2015
Supplementary Information Request Workbook v2.1
Issue date 13 August 2014
Return by 24 September 2014
| Company Name | Centralines Limited
| Return Date | 2014-09-24

## Table of Contents
Table of Contents
| Schedule | Description
| A | Clarification of expenditure on assets forecasts in constant prices
| B | Clarification of SAIDI and SAIFI data
Instructions for completing this workbook
1. Cells with a shaded background in the cover sheet and Schedules A and B must be populated.
2. Cells without a shaded background have been locked against data entry.
3. The completed return must be provided to the Commission by 24 September 2014.
4. Guidance specific to each schedule is provided at the bottom of the schedule.

## A. Asset Expenditure
A. Clarification of expenditure on assets forecasts
All financial values in $000 constant 2013/14 prices
| Company Name | Centralines Limited
| Return Date | 2014-09-24
A1. Actual expenditure (in nominal dollars) | Expenditure on assets forecast (in constant 2013/14 prices)
Year ending
|  | 2014-03-31 | 2015-03-31 | 2016-03-31 | 2017-03-31 | 2018-03-31 | 2019-03-31 | 2020-03-31
| Expenditure on network assets (in constant 2013/14 prices) | 2395 | 2678 | 2917 | 2807 | 2641 | 2689 | 2747
| Expenditure on non-network assets (in constant 2013/14 prices) | 556 | 535 | 568 | 268 | 568 | 268 | 268
Explanatory Note
In schedule 11a of the 31 March 2014 Asset Management Plan provided by Centralines, the forecast expenditure on network and non-network assets in nominal terms for the year to 31 March 2015 equalled the forecast expenditure on network and non-network assets in constant price terms.
The asset management plan disclosures require constant prices to be presented using the current disclosure year (i.e. in this case 2013/2014) as a base year. Therefore while we would expect constant and nominal forecasts to be the same in the year to 31 March 2014, these numbers would be expected to diverge in the year to 31 March 2015.
We require these forecasts in constant 2013/2014 prices and therefore request that they are resubmitted, or provide an explanation of why the constant prices for the year 2015 are the same as nominal value for the year 2015.

## B. Quality Data
B. Clarification of quality of supply information
[7 empty] | Company Name | Centralines Limited
[7 empty] | Return Date | 2014-09-24
The table below lists the potential data anomalies identified in the information you provided to the Commission in response to the s52ZD information request of 12 March 2014.
| Disclosure year | Date | Customers | Minutes | ICPs | Class | Cause | Comment | Explanation | sheet number | Corrected Customers | Corrected Minutes | Corrected SAIDI | Corrected SAIFI
| 2010 | 2010-01-22 | 36 | 2 | 8068 | C | Lightning | number of customers affected greater than customer minutes reported | fault record had not been completed correclty. Update was required | 8805 | 36 | 298.08 | 0.036946 | 0.004462
| 2010 | 2010-01-22 | 36 | 2 | 8068 | C | Lightning | number of customers affected greater than customer minutes reported | fault record had not been completed correclty. Update was required | 8802 | 36 | 109.8 | 0.013609 | 0.004462
| 2011 | 2010-04-24 | 395 | 202 | 8223.5 | C | Not Yet Known | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 9270 | 395 | 202.4 | 0.024612 | 0.048033
| 2011 | 2010-07-24 | 291 | 43 | 8223.5 | C | Not Yet Known | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 9640 | 291 | 43.02 | 0.005231 | 0.035386
| 2011 | 2010-12-17 | 140 | 76 | 8223.5 | C | Not Yet Known | number of customers affected greater than customer minutes reported | fault recorded incorrectly. This event saw a recloser operate, with all customers restored in less than 60 seconds and then another recloser operation some time later, again with all customers restored in less than 60 seconds. These two separate events have incorrectly been included as one. | 10402 | 140 | 0 | 0 | 0
| 2011 | 2010-12-18 | 396 | 316 | 8223.5 | C | Lightning | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 10420 | 396 | 316.068 | 0.038435 | 0.048155
| 2011 | 2010-12-24 | 455 | 409 | 8223.5 | C | Not Yet Known | number of customers affected greater than customer minutes reported | fault record had not been completed correclty. Update was required | 10549 | 455 | 515.6667 | 0.062706 | 0.055329
| 2011 | 2011-01-31 | 365 | 279 | 8223.5 | C | Not Yet Known | number of customers affected greater than customer minutes reported | fault recorded incorrectly. This event saw a recloser operate, with all customers restored in less than 60 seconds and then another recloser operation some time later, again with all customers restored in less than 60 seconds. These two separate events have incorrectly been included as one. | 10859 | 365 | 0 | 0 | 0
| 2011 | 2011-02-11 | 397 | 223 | 8223.5 | C | Old Age | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 10948 | 397 | 223.882 | 0.027225 | 0.048276
| 2012 | 2011-08-19 | 422 | 359 | 8268 | C | Not Yet Known | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 11978 | 422 | 359.924 | 0.043532 | 0.05104
| 2012 | 2011-10-28 | 365 | 87 | 8268 | C | Not Yet Known | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 12276 | 365 | 87.844 | 0.010625 | 0.044146
| 2012 | 2011-11-21 | 422 | 253 | 8268 | C | Other | number of customers affected greater than customer minutes reported | fault recorded incorrectly. This event saw a recloser operate, with all customers restored in less than 60 seconds and then another recloser operation some time later, again with all customers restored in less than 60 seconds. These two separate events have incorrectly been included as one. | 12423 | 422 | 0 | 0 | 0
| 2012 | 2012-01-01 | 295 | 214 | 8268 | C | Lightning | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 12730 | 295 | 214.276 | 0.025916 | 0.03568
| 2013 | 2012-08-16 | 425 | 134 | 8335 | C | Not Yet Known | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 14052 | 425 | 134.5 | 0.016137 | 0.05099
| 2013 | 2012-08-23 | 459 | 319 | 8335 | C | Not Yet Known | number of customers affected greater than customer minutes reported | fault recorded incorrectly. This event saw a recloser operate, with all customers restored in less than 60 seconds and then another recloser operation some time later, again with all customers restored in less than 60 seconds. These two separate events have incorrectly been included as one. | 14097 | 459 | 0 | 0 | 0
| 2013 | 2012-09-13 | 467 | 68 | 8335 | C | Bird Strike (Conductor Span) | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 14298 | 467 | 68.58 | 0.008228 | 0.056029
| 2013 | 2012-11-27 | 1226 | 795 | 8335 | C | Not Yet Known | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 14803 | 1226 | 795.38 | 0.095427 | 0.14709
| 2013 | 2012-12-02 | 425 | 161 | 8335 | C | Wind | number of customers affected greater than customer minutes reported | fault recorded incorrectly. This event saw a recloser operate, with all customers restored in less than 60 seconds and then another recloser operation some time later, again with all customers restored in less than 60 seconds. These two separate events have incorrectly been included as one. | 14839 | 425 | 0 | 0 | 0
| 2014 | 2013-08-20 | 375 | 199 | 8395 | C | Not Yet Known | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 16185 | 375 | 199.25 | 0.023734 | 0.044669
| 2014 | 2013-12-27 | 433 | 226 | 8395 | C | Old Age | number of customers affected greater than customer minutes reported | This fault record is correct. The outage saw a large number of customers interrupted for less than a minute and then the remainder of the customers effected by the outage restored some time later | 17054 | 433 | 226.2 | 0.026945 | 0.051578
Guidance
1. The data anomalies listed above are interruption dataset entries for your EDB.
2. Column I explains why we have identified the entry as being potentially anomalous.
3. We expect that, for each potential anomaly that cannot be corrected or adequately explained, we will remove the relevant interruption from our calculation of the SAIDI and SAIFI targets.
4. To correct anomalies, please provide a corrected version of the SAIDI and SAIFI data that you provided in response to the s52ZD information request of 12 March 2014.
5. To explain an anomaly, please provide the explanation in column J of the table.