## CoverSheet
Electricity Distribution Business
Price-Quality Regulation from 1 April 2015
Supplementary Information Request Workbook v2.1
Issue date 13 August 2014
Return by 24 September 2014
| Company Name | Network Tasman Limited
| Return Date | 2014-09-23

## Table of Contents
Table of Contents
| Schedule | Description
| A | Clarification of SAIDI and SAIFI data
Instructions for completing this workbook
1. Cells with a shaded background in the cover sheet and Schedule A must be populated.
2. Cells without a shaded background have been locked against data entry.
3. The completed return must be provided to the Commission by 24 September 2014.
4. Guidance specific to each schedule is provided at the bottom of the schedule.

## A. Quality Data
A. Clarification of quality of supply information
[7 empty] | Company Name | Network Tasman Limited
[7 empty] | Return Date | 2014-09-23
The table below lists the potential data anomalies identified in the information you provided to the Commission in response to the s52ZD information request of 12 March 2014.
| Disclosure year | Date | Customers | Minutes | ICPs | Class | Cause | Comment | Explanation
| 2005 | 2005-03-02 | 3800 | 0 | 33583 | C | Defective Equipment | number of customers affected greater than customer minutes reported | Record 2861 in our Outage Database describes a reclose operation on the 33kV network that occurred during planned switching on our 33kV network at 7am on 2 March 2005. The Description field in the record says “Slow operation of ABS 1221 caused TP CB to reclose”. TP CB is short for Transpower Circuit Breaker. Reclose operations take 10 seconds for the Circuit Breaker to execute. This means that the power supply would have been interrupted to the 3800 customers for only 10 seconds. This is not a recordable event for SAIDI and SAIFI calculations as the outage has to be for more than 1 minute. As such, then this event should not really have been entered into our database. The SAIDI and SAIFI counts that the record generates is zero however, which is correct for regulatory reporting purposes. On the day what happened is that load (a zone substation that supplies 3800 consumers) was being transferred from one 33kV feeder to another. This is done by temporarily connecting two feeders together by closing a normally open switch out in the network, and then opening another. During the time between the closing of the normally open switch and the opening of the other, the two feeders are said to be “in parallel”. When making or breaking parallels between feeders, if the three contacts of the field Air Break Switch do not all open or close together closely in time, then one or both of the feeder Circuit Breakers back at the supply substation may detect an unbalance current on the three lines that it supplies and interpret this as an “earth fault”. If this slow and uneven contact switching happens, as it did at Air Break Switch No 1221 on this morning, then a Circuit Breaker will trip (automatically open), but then automatically reclose and reliven the line approx. 10 seconds later. After the 10 seconds however all of the contacts on the paralleling Air Break Switch in the field have fully opened (or fully closed) and the apparent earth fault has gone. The Circuit Breaker thus closes back onto a balanced line and stays closed. This Circuit Breaker operation is termed a “successful reclose”.
Guidance
1. The data anomalies listed above are interruption dataset entries for your EDB.
2. Column I explains why we have identified the entry as being potentially anomalous.
3. We expect that, for each potential anomaly that cannot be corrected or adequately explained, we will remove the relevant interruption from our calculation of the SAIDI and SAIFI targets.
4. To correct anomalies, please provide a corrected version of the SAIDI and SAIFI data that you provided in response to the s52ZD information request of 12 March 2014.
5. To explain an anomaly, please provide the explanation in column J of the table.