## Summary
Eastland Network Limited
Annual Reliabilty Summary
| SAIDI |  |  |  |  | SAIFI
Year | Non-normalised | Normalised | Corrected 2005 - 2007 | As per Compliance Statements | As per Information Disclosures | Non-normalised | Normalised | Corrected 2005 - 2007 | As per Compliance Statements | As per Information Disclosures | SAIDI diff to ID | SAIFI diff to ID | SAIDI diff to TCS | SAIFI diff to TCS
2004/05 | 275.2242 | 255.9119 | 275.08 | 280.87 | 280.98 | 3.1159 | 2.9588 | 3.11 | 2.11 | 2.11 | 0.1442 | 0.0058814 | 0.1442 | 0.0058814
2005/06 | 342.0415 | 292.1617 | 342.08 | 349.36 | 349.3 | 3.9903 | 3.7444 | 3.99 | 2.62 | 2.61 | -0.038493 | 0.00026666 | -0.038493 | 0.00026666
2006/07 | 255.8552 | 245.9983 | 256.39 | 257.14 | 256.38 | 3.9199 | 3.9174 | 3.93 | 2.98 | 3.93 | -0.53481 | -0.010127 | -0.53481 | -0.010127 | Explained in notes below table.
2007/08 | 244.9599 | 214.3035 |  | 246.95 | 244.97 | 3.9152 | 3.4606 |  | 3.94 | 3.91 | -0.010102 | 0.0052117 | -1.9901 | -0.024788 | Explained in notes below table.
2008/09 | 243.0903 | 243.0903 |  | 243.09 | 243.09 | 3.3916 | 3.3916 |  | 3.39 | 3.4 | 0.00030418 | -0.008365 | 0.00030418 | 0.001635
2009/10 | 312.2629 | 312.2629 |  | 314.94 | 312.27 | 3.4784 | 3.4784 |  | 3.68 | 3.46 | -0.007089 | 0.018357 | -2.6771 | -0.20164 | Explained in notes below table.
2010/11 | 333.9967 | 333.9967 |  | 334 | 333.99 | 3.4827 | 3.4827 |  | 3.49 | 3.48 | 0.0066631 | 0.0027072 | -0.0033369 | -0.0072928
2011/12 | 395.2927 | 392.1459 |  | 392.15 | 395.28 | 3.4124 | 3.4124 |  | 3.41 | 3.41 | 0.012678 | 0.0024119 | 3.1427 | 0.0024119 | TC has normalised SAIDI others are Non-normalised
2012/13 | 287.1738 | 287.1738 |  | 287.17 | 287.16 | 3.8352 | 3.8352 |  | 3.82 | 3.82 | 0.013826 | 0.015237 | 0.0038258 | 0.015237
2013/14 | 284.7236 | 279.7998 |  | 279.8 | Not due yet | 2.67 | 2.67 |  | 2.67 | Not due yet | #VALUE! | #VALUE! | 4.9236 | -3.3003e-05
Notes:
The variance in the 2006/07 year is due to an outage on 9 March 2007 which was originally stated as a Class C outage but has been reclassified as Class I. This change is due to the Pole that was hit by a third partys' digger was found to be a private pole and not an ENL asset.
2007/08 variance is due to outages originally stated as a Class B or Class C outages but have now been reclassified as Class I = 1.85 SAIDI
2009/10 Variance due to outage on 1 Mar 2010 originally recorded as class C but was actually a transpower outage (Class D) = 67,828 mins, # of custs = 5,434
2011/12 variance is due to the Compliance Statement showing the normalised SAIDI instead of the non-normalised SAIDI
Original Results submitted for 12 March 2014 Request
| SAIDI |  |  |  |  | SAIFI
Year | Non-normalised | Normalised | Corrected 2005 - 2007 | As per Compliance Statements | As per Information Disclosures | Non-normalised | Normalised | Corrected 2005 - 2007 | As per Compliance Statements | As per Information Disclosures
2004/05 | 275.2242 | 255.9119 | 275.08 | 280.87 | 280.98 | 3.1159 | 2.9588 | 3.11 | 2.11 | 2.11
2005/06 | 342.0415 | 292.1617 | 342.08 | 349.36 | 349.3 | 3.9903 | 3.7444 | 3.99 | 2.62 | 2.61
2006/07 | 255.8552 | 245.9983 | 256.39 | 257.14 | 256.38 | 3.9199 | 3.9199 | 3.93 | 2.98 | 3.93
2007/08 | 244.9599 | 214.3035 |  | 246.95 | 244.97 | 3.9152 | 3.4606 |  | 3.94 | 3.91
2008/09 | 243.0903 | 243.0903 |  | 243.09 | 243.09 | 3.3916 | 3.3916 |  | 3.39 | 3.4
2009/10 | 312.2629 | 312.2629 |  | 314.94 | 312.27 | 3.4784 | 3.4784 |  | 3.68 | 3.46
2010/11 | 333.9967 | 333.9967 |  | 334 | 333.99 | 3.4827 | 3.4827 |  | 3.49 | 3.48
2011/12 | 395.2927 | 392.1459 |  | 392.15 | 395.28 | 3.4124 | 3.4124 |  | 3.41 | 3.41
2012/13 | 287.1738 | 287.1738 |  | 287.17 | 287.16 | 3.8352 | 3.8352 |  | 3.82 | 3.82
2013/14 | 284.7236 | 279.7998 |  | 279.8 | Not due yet | 2.67 | 2.67 |  | 2.67 | Not due yet
Difference
2004/05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2005/06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006/07 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0024877 | 0 | 0 | 0
2007/08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2008/09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2009/10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2010/11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2011/12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2012/13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2013/14 | 0 | 0 | 0 | 0 | #VALUE! | 0 | 0 | 0 | 0 | #VALUE!

## Pivot2
Year | Sum of Saidi | Sum of Safi | Sum of FixedSaidi | Sum of FixedSaifi
2004/05 | 275.2242 | 3.1159 | 255.9119 | 2.9588
2005/06 | 342.0415 | 3.9903 | 292.1617 | 3.7444
2006/07 | 255.8552 | 3.9199 | 245.9983 | 3.9174
2007/08 | 244.9599 | 3.9152 | 214.3035 | 3.4606
2008/09 | 243.0903 | 3.3916 | 243.0903 | 3.3916
Grand Total | 1361.1711 | 18.3329 | 1251.4658 | 17.4728

## Pivot
Data
Year | Sum of Saidi | Sum of Safi | Sum of FixedSaidi | Sum of FixedSaifi
2004/05 | 275.2242 | 3.1159 | 255.9119 | 2.9588
2005/06 | 342.0415 | 3.9903 | 292.1617 | 3.7444
2006/07 | 255.8552 | 3.9199 | 245.9983 | 3.9199
2007/08 | 244.9599 | 3.9152 | 214.3035 | 3.4606
2008/09 | 243.0903 | 3.3916 | 243.0903 | 3.3916
Grand Total | 1361.1711 | 18.3329 | 1251.4658 | 17.4753

## 1f-Customer Numbers
Year | Financial year | TotAVG
2003 | 2003/2004 | 25013
2004 | 2004/2005 | 24853
2005 | 2005/2006 | 24863
2006 | 2006/2007 | 24923
2007 | 2007/2008 | 25086
2008 | 2008/2009 | 25248
2009 | 2009/2010 | 25366
2010 | 2010/2011 | 25473
2011 | 2011/2012 | 25540
2012 | 2012/2013 | 25558
2013 | 2013/2014 | 25452

## 1a-5 Year Data raw
REPORT NUMBER | Date Outage | DATE ON | YEAR | Duration of Outage max (mins) | Customers Impacted | Total Customer Minutes Lost | CLASS A-G | CAUSE | NOTES
10937 | 01/04/2004 | 2004-04-02 | 2004 | 349 | 27 | 9423 | C | HUMAN ELEMENT | Repair 11kV line at T/x C356 Wharekopae Rd caused by House Shift
10935 | 02/04/2004 | 2004-04-02 | 2004 | 63 | 138 | 5789 | C | UNKNOWN | Reclose CB C18 Bell Rd Cause Unknown
10940 | 02/04/2004 | 2004-04-02 | 2004 | 59 | 27 | 1593 | B | PLANNED SHUTDOWN | Change DDOs & T/x C356 Wharekopae Rd Patutahi
10936 | 08/04/2004 | 2004-04-08 | 2004 | 31 | 11 | 341 | C | DEFECTIVE EQUIPMENT | Repair 11kV Jumper at pole J879 near Ruatoria Sub
10939 | 08/04/2004 | 2004-04-08 | 2004 | 244 | 5 | 1220 | B | PLANNED SHUTDOWN | Relocate 2 11kV poles & install 11kV cable Crn SH2 & Bloomfeild Rd Matawhero
10934 | 12/04/2004 | 2004-04-12 | 2004 | 50 | 217 | 10850 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at Pole W8918 Oraka Mahia
10938 | 13/04/2004 | 2004-04-13 | 2004 | 220 | 43 | 9460 | B | PLANNED SHUTDOWN | Replace 11kV pole H1720 Makarika Rd Ruatoria
10948 | 13/04/2004 | 2004-04-13 | 2004 | 40 | 50 | 2000 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Mangatarata St Tokomaru Bay
10941 | 15/04/2004 | 2004-04-15 | 2004 | 310 | 10 | 3100 | B | PLANNED SHUTDOWN | Replace 11kV poles E437,E434,E394& E391 Tarndale Rd near Arowhana Stn
10942 | 15/04/2004 | 2004-04-15 | 2004 | 315 | 5 | 1575 | B | PLANNED SHUTDOWN | Replace 11kV H Pole H1256 Tuakau Rd Tokomaru Bay
10943 | 16/04/2004 | 2004-04-16 | 2004 | 180 | 4 | 720 | B | PLANNED SHUTDOWN | Replace 11kV poles G2261 & G2262 in Hokoroa Rd Tolaga Bay
10933 | 20/04/2004 | 2004-04-20 | 2004 | 200 | 120 | 18212 | C | FOREIGN INTERFERENCE | Repair 11kv Lines between Poles G1795 & G1796 Tauwharaparae Rd
10944 | 20/04/2004 | 2004-04-20 | 2004 | 190 | 31 | 5890 | B | PLANNED SHUTDOWN | Replace 4 Red tagged 11kV poles Mahiwi Spur Ruakitiri
10946 | 20/04/2004 | 2004-04-20 | 2004 | 180 | 13 | 2340 | B | PLANNED SHUTDOWN | Replace 11kV pole J4656 in Waikura Valley Hicks Bay
10945 | 21/04/2004 | 2004-04-21 | 2004 | 120 | 63 | 756 | B | PLANNED SHUTDOWN | Replace 2 Red tagged 11kV poles near Waitai Valley Wairoa
10947 | 26/04/2004 | 2004-04-26 | 2004 | 140 | 67 | 9380 | B | PLANNED SHUTDOWN | Replace 11kV pole & T/x at A3919 Wharekiri Rd Panikau
10949 | 29/04/2004 | 2004-04-29 | 2004 | 27 | 195 | 4869 | C | UNKNOWN | Reclose CB C18 Bell Rd at Matawhero Sub Cause Unknown
10950 | 29/04/2004 | 2004-04-29 | 2004 | 209 | 40 | 7683 | B | PLANNED SHUTDOWN | Repair 11kV line at Pole A3924 Awanui Stn Wharekiri Rd Panikau
10951 | 30/04/2004 | 2004-04-30 | 2004 | 300 | 4 | 1200 | B | PLANNED SHUTDOWN | Replace 11kV T/x & Pole J57 Koia Rd Rangitukia Tikitiki
10958 | 03/05/2004 | 2004-05-03 | 2004 | 32 | 24 | 768 | B | PLANNED SHUTDOWN | Isolate 11kV Lines for tree cutting in Pilmers Rd
10961 | 03/05/2004 | 2004-05-03 | 2004 | 235 | 39 | 9165 | B | PLANNED SHUTDOWN | Change 11kV pole J1200 & erect new T/x Rangitukia Rd Tikitiki
10962 | 03/05/2004 | 2004-05-03 | 2004 | 55 | 5 | 275 | B | PLANNED SHUTDOWN | Install D/connectors at poles H504 & H663 in Ihungia Rd
10953 | 04/05/2004 | 2004-05-04 | 2004 | 175 | 34 | 3791 | C | DEFECTIVE EQUIPMENT | Restrain 11kV lines Titirangi Spur
10956 | 04/05/2004 | 2004-05-04 | 2004 | 64 | 4 | 256 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H1843 Matahia Stn Makarika
10955 | 05/05/2004 | 2004-05-05 | 2004 | 123 | 19 | 2337 | C | DEFECTIVE EQUIPMENT | Replace 3 DDO fuses at Pole G360 Kaiaua Rd Tolaga Bay
10963 | 05/05/2004 | 2004-05-05 | 2004 | 13 | 57 | 741 | C | UNKNOWN | Reclose CB W298 Cause Unknown
10954 | 06/05/2004 | 2004-05-06 | 2004 | 420 | 46 | 16835 | C | ADVERSE WEATHER | Replace 11kV Xarm at Pole F666 Rakauroa Rd
10960 | 07/05/2004 | 2004-05-07 | 2004 | 184 | 5 | 920 | B | PLANNED SHUTDOWN | Replace 11kV pole H1257 in Tuakau Rd Tokomaru Bay
10959 | 08/05/2004 | 2004-05-08 | 2004 | 60 | 13 | 780 | B | PLANNED SHUTDOWN | Replace 11kV pole H4375 in Ihungia Rd
10952 | 10/05/2004 | 2004-05-10 | 2004 | 48 | 8 | 384 | C | DEFECTIVE EQUIPMENT | Replace insulator on Pole F761 Makaretu Rd Otoko
10957 | 10/05/2004 | 2004-05-10 | 2004 | 83 | 15 | 1245 | B | PLANNED SHUTDOWN | Replace 11kV pole H784 Mata Rd Tokomaru Bay
10964 | 12/05/2004 | 2004-05-12 | 2004 | 14 | 1508 | 7566 | C | FOREIGN INTERFERENCE | Reclose CB W215 at Kiwi Sub
10965 | 13/05/2004 | 2004-05-13 | 2004 | 19 | 754 | 14326 | C | FOREIGN INTERFERENCE | Reclose CB W215 at Kiwi Sub
10966 | 14/05/2004 | 2004-05-15 | 2004 | 82 | 720 | 53624 | C | FOREIGN INTERFERENCE | Reclose CB D640 Lavenham Rd & CB D646 Waimata at Patutahi Sub
10967 | 14/05/2004 | 2004-05-14 | 2004 | 279 | 51 | 4788 | B | PLANNED SHUTDOWN | Replace 11kV pole H1811 SH35 Makarika
10968 | 16/05/2004 | 2004-05-16 | 2004 | 287 | 48 | 13776 | B | PLANNED SHUTDOWN | Replace 11kV pole & install DD/os T/x B688 Monk's
10969 | 17/05/2004 | 2004-05-17 | 2004 | 167 | 587 | 98029 | C | ADVERSE WEATHER | Reclose CB A614 at Port Sub Line Clash
10971 | 18/05/2004 | 2004-05-18 | 2004 | 39 | 10 | 300 | B | PLANNED SHUTDOWN | Install new SW/Gr for Capt Cook Motel Awapuni Rd
10970 | 20/05/2004 | 2004-05-20 | 2004 | 15 | 45 | 675 | B | PLANNED SHUTDOWN | Replace T/x B374 Whispering Sand Motel Salisbury Rd
10973 | 23/05/2004 | 2004-05-23 | 2004 | 60 | 60 | 3600 | C | DEFECTIVE EQUIPMENT | Repair 11kV Jumper at Pole B3270 in Lytton Rd
10974 | 24/05/2004 | 2004-05-24 | 2004 | 180 | 5 | 900 | B | PLANNED SHUTDOWN | Replace 11kV poles H4420 & H4422 Mata Rd Tokomaru Bay
10975 | 24/05/2004 | 2004-05-24 | 2004 | 310 | 171 | 26611 | C | ADVERSE WEATHER | Relocate 11kV pole W6087 Tukemokhi Rd (Slip)
10976 | 27/05/2004 | 2004-05-27 | 2004 | 230 | 12 | 2760 | B | PLANNED SHUTDOWN | Replace 11kV pole H1541 Horehore Rd Ruatoria
10977 | 28/05/2004 | 2004-05-28 | 2004 | 295 | 15 | 4425 | B | PLANNED SHUTDOWN | Replace 3 11kV Poles Mata Rd Tokomaru Bay
10978 | 28/05/2004 | 2004-05-28 | 2004 | 40 | 258 | 5190 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable at T/x A 563 Crn Maki & Rutene Rd
10979 | 29/05/2004 | 2004-05-29 | 2004 | 153 | 566 | 56791 | C | DEFECTIVE EQUIPMENT | Private 11kV pole down D5326 Waimata Valley Rd
10980 | 29/05/2004 | 2004-05-29 | 2004 | 25 | 655 | 16375 | C | UNKNOWN | Reclose CB Inc 1 G325 Tolaga Bay Sub Cause Unknown
10984 | 30/05/2004 | 2004-05-30 | 2004 | 180 | 70 | 12600 | B | PLANNED SHUTDOWN | Change T/x B638 at Central School
10981 | 31/05/2004 | 2004-05-31 | 2004 | 276 | 21 | 5796 | B | PLANNED SHUTDOWN | Replace 11kV poles & install line breaks at D1040
10982 | 31/05/2004 | 2004-05-31 | 2004 | 38 | 673 | 20931 | C | TREE CONTACTS | Repair 11kV lines pole W5881 Marumaru
10983 | 31/05/2004 | 2004-05-31 | 2004 | 278 | 45 | 12510 | C | UNKNOWN | Reclose CB W817 Te Reinga Cause Unknown
10992 | 01/06/2004 | 2004-06-01 | 2004 | 790 | 115 | 38105 | C | DEFECTIVE EQUIPMENT | Replace 11kV Xarm on Pole D3260 near Awapapa Stn
10993 | 01/06/2004 | 2004-06-01 | 2004 | 340 | 21 | 7140 | B | PLANNED SHUTDOWN | Install 11kV links at pole E1046 in Parakanapa Rd
10996 | 01/06/2004 | 2004-06-01 | 2004 | 240 | 202 | 30098 | B | PLANNED SHUTDOWN | Install new T/x & Sw/Gr Campion Rd
10991 | 02/06/2004 | 2004-06-02 | 2004 | 115 | 28 | 3220 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole D3654 Bushy Knoll Rd
10985 | 03/06/2004 | 2004-06-03 | 2004 | 177 | 211 | 21004 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable fault between A412 & A370 Wainui Rd
10990 | 03/06/2004 | 2004-06-03 | 2004 | 13 | 70 | 910 | C | UNKNOWN | Reclose CB D141 Wharekopae Rd Cause Unknown
10988 | 04/06/2004 | 2004-06-04 | 2004 | 108 | 71 | 3077 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole F1494 in Motu Rd Matawai
10989 | 04/06/2004 | 2004-06-04 | 2004 | 176 | 65 | 11440 | C | FOREIGN INTERFERENCE | Change Cable boot Chewed By Rat at T/x B995 Palm Court
10994 | 04/06/2004 | 2004-06-04 | 2004 | 300 | 15 | 4500 | B | PLANNED SHUTDOWN | Replace 2 11kV poles H2708 & H2709 Mata Rd Tokomaru Bay
10995 | 04/06/2004 | 2004-06-04 | 2004 | 37 | 10 | 370 | C | DEFECTIVE EQUIPMENT | Replace X Arn on pole W1168 at Ponui Wairoa
10986 | 08/06/2004 | 2004-06-08 | 2004 | 160 | 29 | 4640 | C | DEFECTIVE EQUIPMENT | Repair 11kV conductor between T/x F186 & F617 Rakaroa Rd
10987 | 08/06/2004 | 2004-06-08 | 2004 | 6 | 38 | 228 | C | UNKNOWN | Reclose CB W219 AFFCO at Kiwi Sub Cause Unknown
10997 | 10/06/2004 | 2004-06-10 | 2004 | 170 | 45 | 7650 | B | PLANNED SHUTDOWN | Change T/x B103 in Valley Rd
10998 | 10/06/2004 | 2004-06-10 | 2004 | 167 | 19 | 3173 | B | PLANNED SHUTDOWN | Relocate & change 11kV poles Mangahauini Valley Tokomaru Bay
10999 | 12/06/2004 | 2004-06-12 | 2004 | 123 | 262 | 24900 | C | FOREIGN INTERFERENCE | Temp repair 11kV truck hit pole B322 in Awapuni Rd near Tip Top
11000 | 13/06/2004 | 2004-06-13 | 2004 | 221 | 17 | 3651 | C | FOREIGN INTERFERENCE | Replace 11kV pole B1973 in Awapuni Rd near Stock Car Track
11001 | 13/06/2004 | 2004-06-13 | 2004 | 42 | 68 | 2856 | C | FOREIGN INTERFERENCE | Replace 11kV pole B322 in Awapuni Rd near Tip Top
11002 | 19/06/2004 | 2004-06-19 | 2004 | 459 | 102 | 19939 | C | TREE CONTACTS | Repair 11kV lines between J4439 & J4440 4186 SH35 Te Araroa
11003 | 22/06/2004 | 2004-06-22 | 2004 | 67 | 43 | 2881 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at T/x H234 near Makarika School Ruatoria
11004 | 23/06/2004 | 2004-06-23 | 2004 | 180 | 50 | 9000 | B | PLANNED SHUTDOWN | Change T/x A62 Pare St Wainui
11005 | 24/06/2004 | 2004-06-24 | 2004 | 57 | 797 | 35237 | C | DEFECTIVE EQUIPMENT | Repair faulty cable at B6217 Potae Ave
11006 | 28/06/2004 | 2004-06-28 | 2004 | 155 | 3 | 465 | B | PLANNED SHUTDOWN | Isolate 11kV lines for Tree cutting Ihungia Rd
11008 | 28/06/2004 | 2004-06-28 | 2004 | 71 | 5224 | 326478 | C | FOREIGN INTERFERENCE | Remove possum from pole in Valley Rd
11007 | 30/06/2004 | 2004-06-30 | 2004 | 25 | 12 | 252 | B | PLANNED SHUTDOWN | Replace 11kV T/x pole F181 Olivers Rd Matawai
11009 | 30/06/2004 | 2004-07-01 | 2004 | 790 | 323 | 70086 | C | ADVERSE WEATHER | Repair 11kV lines
11011 | 30/06/2004 | 2004-06-30 | 2004 | 59 | 1584 | 93456 | C | ADVERSE WEATHER | Repair 11kV lines
11013 | 30/06/2004 | 2004-07-01 | 2004 | 197 | 680 | 133960 | C | ADVERSE WEATHER | Repair 11kV lines
11022 | 30/06/2004 | 2004-06-30 | 2004 | 40 | 407 | 16280 | C | TREE CONTACTS | Remove tree from 11kV lines
11023 | 30/06/2004 | 2004-06-30 | 2004 | 332 | 29 | 9628 | C | TREE CONTACTS | Repair 11kV lines
11024 | 30/06/2004 | 2004-06-30 | 2004 | 80 | 1103 | 88240 | C | ADVERSE WEATHER | Repair 11kV lines
11026 | 30/06/2004 | 2004-07-01 | 2004 | 227 | 194 | 19568 | C | ADVERSE WEATHER | Repair 11kV Xarm
11027 | 30/06/2004 | 2004-07-01 | 2004 | 222 | 106 | 23532 | C | ADVERSE WEATHER | Replace 11kV pole Hicks Bay
11029 | 30/06/2004 | 2004-07-01 | 2004 | 504 | 63 | 12625 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines
11031 | 30/06/2004 | 2004-07-01 | 2004 | 84 | 56 | 4704 | C | ADVERSE WEATHER | Replace 11kV pole
11035 | 30/06/2004 | 2004-06-30 | 2004 | 29 | 143 | 4147 | C | ADVERSE WEATHER | Repair 11kV lines
11010 | 01/07/2004 | 2004-07-02 | 2004 | 790 | 185 | 146150 | C | ADVERSE WEATHER | Repair 11kV lines
11012 | 01/07/2004 | 2004-07-01 | 2004 | 87 | 1349 | 117363 | C | ADVERSE WEATHER | Repair 11kV lines
11014 | 01/07/2004 | 2004-07-01 | 2004 | 825 | 680 | 128397 | C | ADVERSE WEATHER | Repair 11kV lines
11015 | 01/07/2004 | 2004-07-01 | 2004 | 46 | 19 | 874 | C | TREE CONTACTS | Remove trees from LV Lines
11016 | 01/07/2004 | 2004-07-02 | 2004 | 60 | 283 | 16980 | C | ADVERSE WEATHER | Repair 11kV lines
11017 | 01/07/2004 | 2004-07-01 | 2004 | 298 | 19 | 5662 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines
11025 | 01/07/2004 | 2004-07-01 | 2004 | 769 | 122 | 30622 | C | ADVERSE WEATHER | Repair 11kV lines
11028 | 01/07/2004 | 2004-07-02 | 2004 | 801 | 106 | 84906 | C | ADVERSE WEATHER | Replace 11kV Pole
11030 | 01/07/2004 | 2004-07-02 | 2004 | 982 | 60 | 58920 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines
11032 | 01/07/2004 | 2004-07-02 | 2004 | 910 | 57 | 51870 | C | ADVERSE WEATHER | Replace 11kV pole
11033 | 01/07/2004 | 2004-07-01 | 2004 | 484 | 181 | 87604 | C | ADVERSE WEATHER | Replace 11kV pole
11034 | 01/07/2004 | 2004-07-01 | 2004 | 140 | 64 | 8960 | C | ADVERSE WEATHER | Replace private pole
11036 | 01/07/2004 | 2004-07-01 | 2004 | 90 | 107 | 9630 | C | ADVERSE WEATHER | Repair 11kV lines
11037 | 01/07/2004 | 2004-07-01 | 2004 | 436 | 129 | 44081 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines
11038 | 01/07/2004 | 2004-07-01 | 2004 | 225 | 27 | 6075 | C | ADVERSE WEATHER | Repair 11kV lines
11018 | 02/07/2004 | 2004-07-02 | 2004 | 185 | 79 | 14615 | C | TREE CONTACTS | Repair 11kV lines
11019 | 02/07/2004 | 2004-07-02 | 2004 | 75 | 63 | 4725 | C | ADVERSE WEATHER | Repair 11kV lines
11039 | 02/07/2004 | 2004-07-03 | 2004 | 928 | 22 | 20416 | C | TREE CONTACTS | Repair 11kV lines
11020 | 03/07/2004 | 2004-07-04 | 2004 | 1440 | 14 | 20160 | C | TREE CONTACTS | Repair 11kV lines
11021 | 03/07/2004 | 2004-07-04 | 2004 | 1580 | 12 | 18960 | C | TREE CONTACTS | Repair 11kV lines
11040 | 07/07/2004 | 2004-07-07 | 2004 | 126 | 26 | 2210 | C | DEFECTIVE EQUIPMENT | Extinguish fire on pole D3547 Ruakaka Rd Tiniroto
11041 | 08/07/2004 | 2004-07-08 | 2004 | 33 | 38 | 1254 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on ABS Pole W910 near AFFCO Works
11042 | 08/07/2004 | 2004-07-08 | 2004 | 216 | 8 | 1728 | C | DEFECTIVE EQUIPMENT | Replace Xarm & repair 11kV lines on Pole F754 Makaretu Rd Otoko
11043 | 13/07/2004 | 2004-07-13 | 2004 | 8 | 57 | 456 | C | UNKNOWN | Replace 11kV fuse at W298 Wairoa Township
11044 | 13/07/2004 | 2004-07-13 | 2004 | 26 | 5 | 130 | C | DEFECTIVE EQUIPMENT | Replace 11kV line on pole H1264 in Tuakau Rd
11045 | 15/07/2004 | 2004-07-15 | 2004 | 180 | 5 | 900 | B | PLANNED SHUTDOWN | Replace 2 11kV poles H1250 & H2701 Tuakau Rd
11046 | 15/07/2004 | 2004-07-15 | 2004 | 240 | 123 | 29520 | B | PLANNED SHUTDOWN | Install new LBS at W1221 Mahia
11051 | 15/07/2004 | 2004-07-15 | 2004 | 67 | 11 | 737 | C | DEFECTIVE EQUIPMENT | Restrain & stay 11kV pole J902 SH35 Tikitiki
11053 | 16/07/2004 | 2004-07-16 | 2004 | 40 | 5 | 200 | B | PLANNED SHUTDOWN | Replace 11kV poles H2701 & H2702 Tuakau Rd
11050 | 17/07/2004 | 2004-07-17 | 2004 | 161 | 273 | 36505 | C | FOREIGN INTERFERENCE | Replace 11kV pole E1483 Crn Muloolys Rd & SH2
11048 | 18/07/2004 | 2004-07-18 | 2004 | 217 | 15 | 3255 | C | DEFECTIVE EQUIPMENT | Repair 11kV line at pole E656 Tarndale Rd
11049 | 18/07/2004 | 2004-07-19 | 2004 | 902 | 217 | 113734 | C | ADVERSE WEATHER | Repair 11kV lines beond W1221 Mahia
11047 | 20/07/2004 | 2004-07-20 | 2004 | 222 | 7 | 1554 | B | PLANNED SHUTDOWN | Replace ABS pole H131 Mata Rd
11055 | 20/07/2004 | 2004-07-20 | 2004 | 235 | 15 | 3525 | C | ADVERSE WEATHER | Repair 11kV lines beond ABS E203 Tarndale Rd
11052 | 21/07/2004 | 2004-07-21 | 2004 | 27 | 9 | 243 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole F2768 Bridge Rd Puha
11054 | 21/07/2004 | 2004-07-21 | 2004 | 105 | 15 | 1575 | B | PLANNED SHUTDOWN | Install prop pole between H786 & H787 Mata Rd
11056 | 23/07/2004 | 2004-07-24 | 2004 | 821 | 70 | 38752 | C | ADVERSE WEATHER | Repair 11kV lines Moanui Rd Matawai at Pole F2501
11057 | 23/07/2004 | 2004-07-23 | 2004 | 127 | 270 | 17914 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between D398 & D3017 in Humphries Rd
11058 | 23/07/2004 | 2004-07-23 | 2004 | 77 | 66 | 4634 | C | ADVERSE WEATHER | Repair 11kV lines beyond D150 Wharekopae
11059 | 23/07/2004 | 2004-07-23 | 2004 | 173 | 28 | 4844 | C | ADVERSE WEATHER | Repair 11kV lines beyond W992 Ohuka
11060 | 24/07/2004 | 2004-07-25 | 2004 | 2240 | 10 | 22400 | C | ADVERSE WEATHER | Replace 11kv pole E504 & repair lines Tarndale Rd
11061 | 24/07/2004 | 2004-07-24 | 2004 | 108 | 11 | 1188 | C | ADVERSE WEATHER | Repair 11kV lines at pole W7357 Mangaroa
11062 | 24/07/2004 | 2004-07-24 | 2004 | 234 | 202 | 18689 | C | ADVERSE WEATHER | Repair 11kV lines in Arthur St Tokomaru Bay
11063 | 25/07/2004 | 2004-07-25 | 2004 | 33 | 70 | 2310 | C | ADVERSE WEATHER | Reinstate cut Jumpers after HV fault in Arthur St
11064 | 28/07/2004 | 2004-07-28 | 2004 | 10 | 1600 | 10620 | B | PLANNED SHUTDOWN | To allow change - over from Generator at Mahia
11065 | 28/07/2004 | 2004-07-28 | 2004 | 28 | 77 | 2156 | B | PLANNED SHUTDOWN | Install new 11kV fuses at H2634 Waima Tokomaru Bay
11066 | 29/07/2004 | 2004-07-29 | 2004 | 645 | 56 | 14985 | C | ADVERSE WEATHER | Replace 11kV pole G2426 & repair lines at Tamatea Stn Tauwhareparae
11067 | 29/07/2004 | 2004-07-29 | 2004 | 123 | 417 | 36988 | C | ADVERSE WEATHER | Repair 11kV lines between F767 & G768 Makaretu Rd Otoko
11068 | 29/07/2004 | 2004-07-29 | 2004 | 319 | 63 | 10512 | C | TREE CONTACTS | Repair 11kV lines between H1638 & H1636 Matahia Stn Ruatoria
11069 | 02/08/2004 | 2004-08-02 | 2004 | 552 | 12 | 6624 | B | PLANNED SHUTDOWN | Isolate11kV for tree cutting Mangaoporo Valley
11070 | 03/08/2004 | 2004-08-03 | 2004 | 232 | 53 | 12296 | B | PLANNED SHUTDOWN | Replace 11kV pole D1658 Waituhi Lavenham Rd
11072 | 03/08/2004 | 2004-08-03 | 2004 | 321 | 7 | 2247 | B | PLANNED SHUTDOWN | Replace poles H4434 & H4463 Mata Rd
11071 | 06/08/2004 | 2004-08-06 | 2004 | 132 | 77 | 7015 | C | ADVERSE WEATHER | Reclose E863 Cause Unknown
11074 | 11/08/2004 | 2004-08-11 | 2004 | 91 | 122 | 6347 | C | ADVERSE WEATHER | Replace 11kV pole H1641 Matahaia Rd
11075 | 11/08/2004 | 2004-08-11 | 2004 | 216 | 238 | 29636 | C | TREE CONTACTS | Repair 11kV lines at D646 Lavenham Rd
11076 | 11/08/2004 | 2004-08-11 | 2004 | 32 | 32 | 1024 | C | ADVERSE WEATHER | Temp prop pole C2231 outside Makaraka School
11077 | 11/08/2004 | 2004-08-11 | 2004 | 65 | 89 | 5785 | C | ADVERSE WEATHER | Reclose E863 High Winds
11078 | 11/08/2004 | 2004-08-11 | 2004 | 192 | 99 | 17033 | C | ADVERSE WEATHER | Replace H pole J2449 SH35 near Kuinui Stn
11079 | 11/08/2004 | 2004-08-11 | 2004 | 253 | 126 | 18109 | C | ADVERSE WEATHER | Isolate Smyths Rd Broken lines
11073 | 12/08/2004 | 2004-08-12 | 2004 | 50 | 28 | 1400 | C | ADVERSE WEATHER | Replace pole J2249 Poroporo Valley
11080 | 13/08/2004 | 2004-08-13 | 2004 | 321 | 21 | 6741 | C | ADVERSE WEATHER | Replace pole W9612 Tunanui Rd Kopuawhara
11087 | 13/08/2004 | 2004-08-13 | 2004 | 15 | 261 | 3733 | C | TREE CONTACTS | Repair 11kV lines W8383 near Morere
11082 | 15/08/2004 | 2004-08-15 | 2004 | 120 | 180 | 21600 | C | UNKNOWN | Reclose W826 at Kiwi Sub cause Unknown
11084 | 15/08/2004 | 2004-08-15 | 2004 | 97 | 87 | 8439 | C | UNKNOWN | Reclose E863 Whatatutu cause unknown
11085 | 15/08/2004 | 2004-08-15 | 2004 | 15 | 261 | 3915 | C | TREE CONTACTS | Repair 11kV lines at T/x W137
11081 | 16/08/2004 | 2004-08-16 | 2004 | 11 | 2534 | 24599 | C | UNKNOWN | Reclose CB A18 Goodwins Rd
11096 | 16/08/2004 | 2004-08-16 | 2004 | 33 | 683 | 17901 | C | ADVERSE WEATHER | Repair 11kV between A3494 & A3416 Tatapouri Hill
11088 | 17/08/2004 | 2004-08-17 | 2004 | 161 | 48 | 7728 | C | TREE CONTACTS | Isolate 11kV lines for tree cutting near Te Kowhai Stn
11089 | 17/08/2004 | 2004-08-18 | 2004 | 1893 | 174 | 85596 | C | ADVERSE WEATHER | Repair 11kv lines at W1102 Onenui Mahia
11090 | 17/08/2004 | 2004-08-18 | 2004 | 777 | 63 | 45709 | C | ADVERSE WEATHER | Repair 11kV line at W8146 Nuhaka
11091 | 17/08/2004 | 2004-08-17 | 2004 | 77 | 273 | 20839 | C | ADVERSE WEATHER | Reclose CB790 at Tahaenui High Winds
11092 | 17/08/2004 | 2004-08-17 | 2004 | 19 | 793 | 15067 | C | UNKNOWN | Reclose CB W241 Kiwi Sub cause Unknown
11086 | 18/08/2004 | 2004-08-19 | 2004 | 638 | 89 | 56782 | C | ADVERSE WEATHER | Reclose E863 High Winds
11093 | 18/08/2004 | 2004-08-18 | 2004 | 45 | 19 | 855 | C | ADVERSE WEATHER | Repair 11kV at pole W3007 in Rutherford St
11094 | 18/08/2004 | 2004-08-18 | 2004 | 525 | 4 | 2100 | C | ADVERSE WEATHER | Repair 11kV beond W1135 Whakamahi
11095 | 19/08/2004 | 2004-08-19 | 2004 | 500 | 57 | 28500 | C | ADVERSE WEATHER | Repair 11kV beond W708 Ruakitiri
11097 | 19/08/2004 | 2004-08-19 | 2004 | 100 | 5 | 500 | B | PLANNED SHUTDOWN | Isolate 11kV for Tree Cutting Ceasars Rd
11098 | 20/08/2004 | 2004-08-20 | 2004 | 255 | 6 | 1530 | B | PLANNED SHUTDOWN | Replace 11kV pole H1266 Waitahia Rd
11099 | 22/08/2004 | 2004-08-22 | 2004 | 28 | 1167 | 30182 | C | UNKNOWN | Reclose CB W808 Blacks Pad cause Unknown
11100 | 22/08/2004 | 2004-08-22 | 2004 | 16 | 1032 | 4696 | C | ADVERSE WEATHER | Repair 11kV lines at pole W9127 across Pond Mahunga
11101 | 22/08/2004 | 2004-08-22 | 2004 | 81 | 597 | 31779 | C | UNKNOWN | Reclose CB Inc H300 at Tokomaru Bay Sub cause Unknown
11102 | 23/08/2004 | 2004-08-23 | 2004 | 130 | 15 | 1950 | B | PLANNED SHUTDOWN | Change 11kV pole F3828 Crn Cliff & Main Rd TeKaraka
11103 | 24/08/2004 | 2004-08-24 | 2004 | 298 | 10 | 2980 | B | PLANNED SHUTDOWN | Replace 11kV poles H4375 & H4406 Mata Rd
11104 | 26/08/2004 | 2004-08-26 | 2004 | 296 | 15 | 4440 | C | ADVERSE WEATHER | Repair 11kV between J2138 & J2143 Sh35 Tikitiki North
11105 | 27/08/2004 | 2004-08-27 | 2004 | 155 | 5 | 775 | C | ADVERSE WEATHER | Repair 11kV at Pole E392 Tarndale Rd Whatatutu
11106 | 28/08/2004 | 2004-08-28 | 2004 | 198 | 991 | 105724 | C | UNKNOWN | Reclose CB A475 Tamarau at Kaiti Sub cause Unknown
11107 | 01/09/2004 | 2004-09-01 | 2004 | 340 | 63 | 21420 | B | PLANNED SHUTDOWN | Change T/x W1511 Kahawai St Mahia
11108 | 06/09/2004 | 2004-09-06 | 2004 | 165 | 73 | 12045 | B | PLANNED SHUTDOWN | Change T/x W1512 Ormond Drive Mahia
11109 | 06/09/2004 | 2004-09-06 | 2004 | 233 | 57 | 13281 | C | HUMAN ELEMENT | Replace 11kV pole B4058 Aberdeen Rd Hit by Car
11115 | 06/09/2004 | 2004-09-06 | 2004 | 315 | 84 | 25536 | B | PLANNED SHUTDOWN | Replace 11kV poles Parakanapa Rd
11110 | 08/09/2004 | 2004-09-08 | 2004 | 180 | 3 | 540 | B | PLANNED SHUTDOWN | Install 1 Span 'Dog" roadxing Matawhero Sub
11112 | 08/09/2004 | 2004-09-08 | 2004 | 180 | 3 | 540 | B | PLANNED SHUTDOWN | Erect new 50kV roadxing ouside Matawhero Sub
11111 | 15/09/2004 | 2004-09-15 | 2004 | 240 | 53 | 12720 | B | PLANNED SHUTDOWN | Relocate 11kV Crn Armstrong Rd Tarndale Rd & T/x E304
11113 | 15/09/2004 | 2004-09-15 | 2004 | 344 | 60 | 19897 | C | HUMAN ELEMENT | Repair 11kV lines between G1672 & G1670 Paroa Rd
11114 | 20/09/2004 | 2004-09-20 | 2004 | 312 | 102 | 15215 | C | DEFECTIVE EQUIPMENT | Repair 11kV line at pole J2982 Whakaangiangi Rd
11116 | 22/09/2004 | 2004-09-22 | 2004 | 7 | 754 | 4071 | C | UNKNOWN | Reclose CB808 at Blacks Pad cause Unknown
11117 | 22/09/2004 | 2004-09-22 | 2004 | 5 | 793 | 3965 | C | UNKNOWN | Reclose CB W214 at Kiwi Sub
11118 | 23/09/2004 | 2004-09-23 | 2004 | 4 | 407 | 1628 | C | TREE CONTACTS | Isolate 11kV to remove branches 47 Patutahi Rd
11119 | 24/09/2004 | 2004-09-24 | 2004 | 84 | 6 | 504 | B | PLANNED SHUTDOWN | Isolate T/x E337 for tree Cutting Main Rd Ormond
11121 | 26/09/2004 | 2004-09-26 | 2004 | 450 | 38 | 17100 | B | PLANNED SHUTDOWN | Reconductor 11kV AFFCO Line
11120 | 27/09/2004 | 2004-09-27 | 2004 | 120 | 3 | 360 | B | PLANNED SHUTDOWN | Change T/x C288 Bck Ormond Rd
11122 | 28/09/2004 | 2004-09-28 | 2004 | 250 | 24 | 6000 | B | PLANNED SHUTDOWN | 11kV Maintenance change poles & T/x F386 Library Rd Te Karaka
11123 | 29/09/2004 | 2004-09-29 | 2004 | 74 | 11 | 814 | C | DEFECTIVE EQUIPMENT | Repair lead on T/x E281 Waimata Rd
11124 | 29/09/2004 | 2004-09-29 | 2004 | 57 | 220 | 12540 | C | DEFECTIVE EQUIPMENT | Repair quadrant wire on ABS J616 Wharf Rd Hicks Bay
11125 | 29/09/2004 | 2004-09-29 | 2004 | 135 | 17 | 2295 | C | ADVERSE WEATHER | Repair 11kV lines at pole A4590 Glenroy Rd
11126 | 29/09/2004 | 2004-09-29 | 2004 | 240 | 11 | 2640 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree Cutting T/x E281 Waimata Valley
11127 | 29/09/2004 | 2004-09-29 | 2004 | 220 | 62 | 12320 | B | PLANNED SHUTDOWN | Isolate T/xs W 1504 W1505 & W1506 Mahia for New T/x W1222
11128 | 29/09/2004 | 2004-09-30 | 2004 | 135 | 1080 | 121890 | C | DEFECTIVE EQUIPMENT | Replace Xarm bolt at pole W3788 on 33kV line to Tahaenui
11129 | 30/09/2004 | 2004-09-30 | 2004 | 90 | 8 | 720 | B | PLANNED SHUTDOWN
11132 | 01/10/2004 | 2004-10-01 | 2004 | 98 | 15 | 1470 | C | ADVERSE WEATHER | Untwist 11kV line at Waipaoa Stn
11141 | 05/10/2004 | 2004-10-05 | 2004 | 60 | 15 | 900 | B | PLANNED SHUTDOWN | Isolate 11kV for Tree cutting at Turihau Stn
11142 | 06/10/2004 | 2004-10-06 | 2004 | 283 | 50 | 14150 | B | PLANNED SHUTDOWN | Replace 2 11kV poles SH2 near Ford Rd Ormond
11143 | 06/10/2004 | 2004-10-06 | 2004 | 339 | 38 | 12882 | B | PLANNED SHUTDOWN | Replace T/x F395 Cliff Rd Te Karaka
11144 | 08/10/2004 | 2004-10-08 | 2004 | 625 | 76 | 47500 | B | PLANNED SHUTDOWN | Straight joint HV cable Stanley Rd Footbridge
11133 | 10/10/2004 | 2004-10-10 | 2004 | 4 | 3947 | 15788 | C | LIGHTNING | Reclose CB 192 at Gisborne Sub Lighting hit Pole B3796 in Stanley Rd
11134 | 12/10/2004 | 2004-10-12 | 2004 | 163 | 83 | 10468 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole E1780 Car hit Pole
11135 | 13/10/2004 | 2004-10-13 | 2004 | 40 | 96 | 3840 | B | PLANNED SHUTDOWN | Rejoin Jumpers at Poles E1784 & E104
11137 | 14/10/2004 | 2004-10-14 | 2004 | 146 | 261 | 3955 | C | ADVERSE WEATHER | Repair 11kV lines between W8404 & W8405 Morere
11139 | 14/10/2004 | 2004-10-14 | 2004 | 58 | 8 | 464 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at Poles G4211 & G4224 at Three Bridges
11145 | 16/10/2004 | 2004-10-16 | 2004 | 226 | 654 | 64158 | C | TREE CONTACTS | Repair 11kV lines at pole C5014 75 Main Rd Makaraka
11138 | 19/10/2004 | 2004-10-19 | 2004 | 120 | 67 | 8040 | B | PLANNED SHUTDOWN | Repair 11kV lines between A3416 & A4394 Tatapouri Hill
11140 | 19/10/2004 | 2004-10-19 | 2004 | 50 | 8 | 400 | B | PLANNED SHUTDOWN | Rejoin jumpers at G42212 & G4224 Three Bridges
11146 | 20/10/2004 | 2004-10-20 | 2004 | 389 | 20 | 7780 | B | PLANNED SHUTDOWN | Replace 11kV poles near Tea Rooms Morere
11147 | 20/10/2004 | 2004-10-20 | 2004 | 198 | 130 | 25740 | B | PLANNED SHUTDOWN | Change T/x A405 in Endcliffe Rd Kaiti
11148 | 20/10/2004 | 2004-10-20 | 2004 | 205 | 2 | 410 | B | PLANNED SHUTDOWN | Change T/x G262 on Titirangi Hill Tolaga Bay
11149 | 22/10/2004 | 2004-10-22 | 2004 | 63 | 17 | 1071 | C | TREE CONTACTS | Repair 11kV lines at pole E1617 Manders Rd
11150 | 24/10/2004 | 2004-10-25 | 2004 | 1076 | 104 | 63490 | C | UNKNOWN | Repair 11kV line at pole W990 near Papuni Stn
11151 | 24/10/2004 | 2004-10-24 | 2004 | 257 | 466 | 119762 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at T/x pole F401 Otoko
11152 | 27/10/2004 | 2004-10-27 | 2004 | 252 | 23 | 5796 | B | PLANNED SHUTDOWN | Replace 2 pole sub J85 Waiomatatini Rd Ruatoria
11153 | 30/10/2004 | 2004-10-30 | 2004 | 60 | 18 | 1080 | C | TREE CONTACTS | Remove tree from 11kV lines at 209 Te Hau Rd Whatatutu
11154 | 30/10/2004 | 2004-10-30 | 2004 | 200 | 12 | 2400 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between H1515 & 1514 X arm twisted
11177 | 01/11/2004 | 2004-11-01 | 2004 | 306 | 84 | 16632 | B | PLANNED SHUTDOWN | Replace 11kV poles Parakanapa Rd
11181 | 01/11/2004 | 2004-11-01 | 2004 | 60 | 11 | 660 | B | PLANNED SHUTDOWN | Isolate 11kV lines to connect new fuses Lake Rd Patutahi
11182 | 01/11/2004 | 2004-11-01 | 2004 | 335 | 17 | 5695 | B | PLANNED SHUTDOWN | Replace 11kv poles and reconductor Titirangi Spur
11179 | 02/11/2004 | 2004-11-02 | 2004 | 176 | 68 | 11968 | B | PLANNED SHUTDOWN | Install new T/x and cut Trees Bck Ormond Rd E1878
11178 | 03/11/2004 | 2004-11-03 | 2004 | 160 | 16 | 2560 | B | PLANNED SHUTDOWN | Relocate DDOs Mangamaia Whatatutu
11180 | 03/11/2004 | 2004-11-03 | 2004 | 232 | 52 | 12064 | B | PLANNED SHUTDOWN | Isolate 11kV lines for Tree cutting near Mangatu Stud Farm
11183 | 03/11/2004 | 2004-11-03 | 2004 | 17 | 26 | 442 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumpers at pole W4170 Hereheretau Rd
11157 | 09/11/2004 | 2004-11-09 | 2004 | 158 | 69 | 10902 | C | DEFECTIVE EQUIPMENT | Replace T/x pole E118 Kanakanaia
11158 | 09/11/2004 | 2004-11-09 | 2004 | 399 | 133 | 33743 | C | ADVERSE WEATHER | Repair 11kV lines between D1137 and D1138 Parakanapa Rd
11160 | 09/11/2004 | 2004-11-09 | 2004 | 529 | 97 | 42903 | C | TREE CONTACTS | Repair 11kV lines between E617 and E618 Kanakanaia Rd
11159 | 10/11/2004 | 2004-11-10 | 2004 | 80 | 199 | 15920 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at ABS W944 Ruakitiri
11161 | 14/11/2004 | 2004-11-14 | 2004 | 176 | 300 | 29032 | C | ADVERSE WEATHER | Repair 11kV at pole J1039 near Tikitiki
11156 | 15/11/2004 | 2004-11-15 | 2004 | 97 | 69 | 6693 | C | DEFECTIVE EQUIPMENT | Replace cable to T/x B887 Albert St
11162 | 15/11/2004 | 2004-11-15 | 2004 | 270 | 7 | 1890 | B | PLANNED SHUTDOWN | Change Xarms on Tap off to Paokahu Dump line
11176 | 15/11/2004 | 2004-11-15 | 2004 | 169 | 11688 | 809474 | C | LIGHTNING | Reclose CBs 182 and 172 at Gisborne Sub
11163 | 17/11/2004 | 2004-11-17 | 2004 | 136 | 2 | 272 | C | DEFECTIVE EQUIPMENT | Change T/x W58 at Huramua
11155 | 19/11/2004 | 2004-11-19 | 2004 | 89 | 15 | 1335 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole E1227 Wharekiri Rd
11165 | 20/11/2004 | 2004-11-20 | 2004 | 95 | 13 | 1235 | C | ADVERSE WEATHER | Temp prop 11kV pole F1402 Te Wera Rd
11164 | 22/11/2004 | 2004-11-22 | 2004 | 587 | 19 | 11153 | C | DEFECTIVE EQUIPMENT | Replace burnt 11kV pole G1554 Kiore Rd Tolaga Bay
11174 | 22/11/2004 | 2004-11-22 | 2004 | 411 | 18 | 7398 | B | PLANNED SHUTDOWN | Run new 11kV conductor near Blue Bay Motor Camp
11166 | 24/11/2004 | 2004-11-24 | 2004 | 12 | 113 | 1356 | C | UNKNOWN | Reclose H341 in Mata Rd cause unknown
11171 | 25/11/2004 | 2004-11-25 | 2004 | 128 | 140 | 17920 | C | UNKNOWN | Reclose CB W816 at Ohuka cause unknown
11173 | 25/11/2004 | 2004-11-26 | 2004 | 1116 | 255 | 284580 | C | HUMAN ELEMENT | Replace 11kV pole and T/x J306 near Hicks Bay Hill
11169 | 26/11/2004 | 2004-11-27 | 2004 | 1041 | 16 | 16656 | C | ADVERSE WEATHER | Repair 11kV lines beyond W1059 Mangone Valley
11170 | 26/11/2004 | 2004-11-26 | 2004 | 170 | 27 | 4590 | C | ADVERSE WEATHER | Repair 11kV lines beteen A3952 and A3951 Wharekiri Rd
11172 | 26/11/2004 | 2004-11-26 | 2004 | 227 | 53 | 10899 | C | ADVERSE WEATHER | Repair 11kV lines between H1829 and H1830 Makarika
11167 | 27/11/2004 | 2004-11-27 | 2004 | 120 | 27 | 3240 | C | HUMAN ELEMENT | Isolate 11kV lines for crane after Motor Accident Tiniroto Rd
11168 | 27/11/2004 | 2004-11-27 | 2004 | 169 | 11 | 1859 | C | TREE CONTACTS | Isolate 11kV lines for tree cutting near Three Bridges
11184 | 30/11/2004 | 2004-12-01 | 2004 | 1230 | 4 | 4920 | C | ADVERSE WEATHER | Repair 11kV lines at pole W1139 Whakamahi
11185 | 30/11/2004 | 2004-11-30 | 2004 | 20 | 130 | 2600 | B | PLANNED SHUTDOWN | Change T/x A405 in Endcliffe Rd
11186 | 30/11/2004 | 2004-11-30 | 2004 | 93 | 7 | 651 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarms at W21008 Kopuawhara Valley
11187 | 01/12/2004 | 2004-12-01 | 2004 | 35 | 8 | 280 | C | TREE CONTACTS | Remove tree near G159 Tauwhareparae Rd
11188 | 02/12/2004 | 2004-12-02 | 2004 | 274 | 28 | 7672 | C | TREE CONTACTS | Remove trees from 50kV line Whitmore Rd Ormond
11190 | 02/12/2004 | 2004-12-02 | 2004 | 5 | 19 | 95 | C | TREE CONTACTS | Remove tree near pole E61 in Bond Rd Ormond
11189 | 03/12/2004 | 2004-12-03 | 2004 | 223 | 7 | 1561 | C | ADVERSE WEATHER | Replace 11kV pole C4907 Browns Beach Rd
11196 | 04/12/2004 | 2004-12-04 | 2004 | 140 | 2 | 280 | C | DEFECTIVE EQUIPMENT | Replace T/x W743 Clydebank Rd
11192 | 05/12/2004 | 2004-12-05 | 2004 | 165 | 28 | 4620 | C | ADVERSE WEATHER | Replace DDO fuse base on T/x E59 Ormond Valley Rd
11193 | 05/12/2004 | 2004-12-05 | 2004 | 289 | 115 | 27167 | C | TREE CONTACTS | Remove trees from 11kV Waingake Rd near T/x C384
11194 | 05/12/2004 | 2004-12-05 | 2004 | 351 | 291 | 34576 | C | DEFECTIVE EQUIPMENT | Repair 11kV at pole W9118 Mahunga Mahia
11195 | 05/12/2004 | 2004-12-05 | 2004 | 387 | 264 | 59532 | C | ADVERSE WEATHER | Replace H pole W7096 Ohuka
11191 | 06/12/2004 | 2004-12-06 | 2004 | 36 | 15 | 540 | C | DEFECTIVE EQUIPMENT | Replace insulator and X Arms on pole A4592 Glenroy Rd
11197 | 09/12/2004 | 2004-12-09 | 2004 | 113 | 77 | 6832 | C | DEFECTIVE EQUIPMENT | Replace jumper at ABS D491 Taumata Rd
11198 | 10/12/2004 | 2004-12-10 | 2004 | 360 | 16 | 5760 | B | PLANNED SHUTDOWN | Replace 2 pole sub H332 Waipiro Bay
11199 | 10/12/2004 | 2004-12-10 | 2004 | 337 | 161 | 11027 | C | TREE CONTACTS | Repair 11kV lines near Emirau Stn
11202 | 10/12/2004 | 2004-12-10 | 2004 | 31 | 3 | 93 | C | DEFECTIVE EQUIPMENT | Reconnect jumper at T/x F440 Te Karaka
11200 | 11/12/2004 | 2004-12-11 | 2004 | 60 | 6 | 360 | C | DEFECTIVE EQUIPMENT | Repair jumper at T/x A65 Lloyde George Rd
11201 | 11/12/2004 | 2004-12-11 | 2004 | 56 | 60 | 3360 | C | FOREIGN INTERFERENCE | Remove chain from 11kV line in Munro St
11203 | 13/12/2004 | 2004-12-14 | 2004 | 345 | 162 | 34635 | C | ADVERSE WEATHER | Repair 11kV line at pole G1658 in Tauwharaparae Rd
11204 | 14/12/2004 | 2004-12-14 | 2004 | 190 | 3 | 570 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting & Maintenance Tikitiki Radio Tap off
11205 | 15/12/2004 | 2004-12-15 | 2004 | 380 | 27 | 10260 | B | PLANNED SHUTDOWN | Replace 2 pole Sub G337 Monkhouse St Tolaga Bay
11212 | 15/12/2004 | 2004-12-15 | 2004 | 559 | 90 | 50310 | B | PLANNED SHUTDOWN | Install new SW/gr & T/x Lytton Rd
11206 | 16/12/2004 | 2004-12-16 | 2004 | 376 | 24 | 2504 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Caves Rd
11207 | 17/12/2004 | 2004-12-17 | 2004 | 224 | 34 | 7616 | B | PLANNED SHUTDOWN | Replace 2 pole sub G253 Tauwhareparae Rd Tolaga Bay
11210 | 17/12/2004 | 2004-12-17 | 2004 | 25 | 5 | 100 | C | TREE CONTACTS | Remove tree from 11kV lines Wharekaka Rd Tolaga Bay
11211 | 19/12/2004 | 2004-12-19 | 2004 | 613 | 216 | 28878 | C | TREE CONTACTS | Replace pole E2894 & repair 11kV lines Ngakaroa Rd
11208 | 20/12/2004 | 2004-12-20 | 2004 | 278 | 17 | 4726 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting Crawford Rd
11209 | 20/12/2004 | 2004-12-20 | 2004 | 40 | 51 | 2040 | B | PLANNED SHUTDOWN | Replace 1 span 11kV between H1829 & H1830 SH35 Ruatoria
11214 | 21/12/2004 | 2004-12-21 | 2004 | 206 | 82 | 14372 | C | DEFECTIVE EQUIPMENT | Replace 11kV lines between J2391 and J214 SH35 Tikitiki
11213 | 22/12/2004 | 2004-12-22 | 2004 | 316 | 44 | 13904 | B | PLANNED SHUTDOWN | Reconductor 11kV lines Papatu Rd Manutuke
11215 | 24/12/2004 | 2004-12-24 | 2004 | 70 | 8 | 560 | B | PLANNED SHUTDOWN | Change T/x C3224 in Cameron Rd
11216 | 24/12/2004 | 2004-12-24 | 2004 | 61 | 67 | 4087 | C | DEFECTIVE EQUIPMENT | Replace 3 DD/o Fuse Bases at T/x A99 Sirrah St Wainui
11217 | 25/12/2004 | 2004-12-25 | 2004 | 21 | 440 | 9027 | C | FOREIGN INTERFERENCE | Remove turkey from pole C3278 near Opou Stn Manutuke
11218 | 28/12/2004 | 2004-12-28 | 2004 | 108 | 37 | 3996 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarm on ple J1239 Haha Stn Rangitukia
11219 | 29/12/2004 | 2004-12-29 | 2004 | 73 | 15 | 1095 | C | DEFECTIVE EQUIPMENT | Refit Xarm on pole D6058 Waimaha Rd
11220 | 02/01/2005 | 2005-01-02 | 2004 | 61 | 352 | 16698 | C | ADVERSE ENVIRONMENT | Fuel fault at Mahia Generator
11221 | 07/01/2005 | 2005-01-07 | 2004 | 209 | 134 | 24643 | C | FOREIGN INTERFERENCE | Repair 11kV between H2619 & H2620 Waima Rd Tokomaru Bay
11222 | 08/01/2005 | 2005-01-08 | 2004 | 14 | 17 | 238 | C | TREE CONTACTS | Remove tree branch from 11kV pole A370 in Puatai Rd
11223 | 09/01/2005 | 2005-01-09 | 2004 | 56 | 270 | 10395 | C | FOREIGN INTERFERENCE | 11kV struck by Squash Harvester in Newmans Rd
11225 | 10/01/2005 | 2005-01-10 | 2004 | 100 | 22 | 2200 | C | UNKNOWN | Replace 3 11kV fuses at W1101 cause Unknown
11227 | 10/01/2005 | 2005-01-10 | 2004 | 360 | 3 | 1080 | B | PLANNED SHUTDOWN | Replace A91 in Riverside Rd with new LBS switch
11224 | 11/01/2005 | 2005-01-11 | 2004 | 323 | 25 | 8075 | B | PLANNED SHUTDOWN | Install new LBS at pole E867 in Armstrong Rd
11226 | 11/01/2005 | 2005-01-11 | 2004 | 98 | 52 | 5096 | C | DEFECTIVE EQUIPMENT | Replace 3 DD/o fuses at T/x E106 Kaiteratahi
11228 | 13/01/2005 | 2005-01-13 | 2004 | 51 | 730 | 24451 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable at pole W3164 Freyberg St
11229 | 14/01/2005 | 2005-01-14 | 2004 | 146 | 6 | 876 | C | DEFECTIVE EQUIPMENT | Replace T/x C71 Paritu Rd Wharatas
11235 | 14/01/2005 | 2005-01-14 | 2004 | 116 | 89 | 10324 | C | ADVERSE ENVIRONMENT | Isolate 11kV lines for Fire Service
11230 | 17/01/2005 | 2005-01-17 | 2004 | 45 | 181 | 7961 | C | DEFECTIVE EQUIPMENT | Temp repair ABS W926 Freyberg St
11231 | 17/01/2005 | 2005-01-17 | 2004 | 300 | 113 | 33900 | C | HUMAN ELEMENT | Temp repairs C3510 Car Vs Pole Murawai
11232 | 18/01/2005 | 2005-01-18 | 2004 | 71 | 23 | 1633 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J528 SH35 Maraehara Crn
11233 | 18/01/2005 | 2005-01-18 | 2004 | 61 | 52 | 3012 | C | TREE CONTACTS | Reclose CB W829 Ruapapa Trees
11234 | 18/01/2005 | 2005-01-18 | 2004 | 8 | 819 | 6552 | C | UNKNOWN | Reclose CB C95 at Makaraka Sub cause unknown
11236 | 23/01/2005 | 2005-01-23 | 2004 | 121 | 6 | 726 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole A4497 SH35 Pouawa
11237 | 23/01/2005 | 2005-01-23 | 2004 | 119 | 6 | 714 | C | FOREIGN INTERFERENCE | Replace 11kV pole A4496 SH35 Pouawa
11238 | 23/01/2005 | 2005-01-23 | 2004 | 112 | 60 | 6720 | C | FOREIGN INTERFERENCE | Replace 11kV pole D2152 Lavenham Rd
11239 | 26/01/2005 | 2005-01-26 | 2004 | 140 | 4 | 560 | B | PLANNED SHUTDOWN | Change T/x B1003 in Roebuck Rd
11240 | 27/01/2005 | 2005-01-27 | 2004 | 50 | 4 | 200 | B | PLANNED SHUTDOWN | Rejoin jumpers at pole W7229
11241 | 31/01/2005 | 2005-01-31 | 2004 | 279 | 488 | 73750 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole C990 Manutuke
11242 | 31/01/2005 | 2005-01-31 | 2004 | 88 | 49 | 4312 | C | DEFECTIVE EQUIPMENT | Repair ABS D488 near Tahunga Stn
11260 | 01/02/2005 | 2005-02-01 | 2004 | 100 | 56 | 5600 | B | PLANNED SHUTDOWN | Replace Xamrs & install DD/os H174 Bremner Stn Mata Rd
11262 | 02/02/2005 | 2005-02-02 | 2004 | 2 | 78 | 156 | B | PLANNED SHUTDOWN | Change T/x W1535 Hunterbrown St
11258 | 03/02/2005 | 2005-02-03 | 2004 | 266 | 41 | 1864 | B | PLANNED SHUTDOWN | Change 11kV pole & install Isolation Fuses Rangitukia Rd
11259 | 04/02/2005 | 2005-02-04 | 2004 | 189 | 79 | 14931 | B | PLANNED SHUTDOWN | Install new LBS Crn Middleton & Tiniroto Rds
11261 | 04/02/2005 | 2005-02-04 | 2004 | 234 | 24 | 5616 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree Cutting Paroa Rd Tolaga Bay
11244 | 06/02/2005 | 2005-02-06 | 2004 | 300 | 466 | 139800 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole F122 at Puha
11243 | 07/02/2005 | 2005-02-07 | 2004 | 89 | 19 | 1691 | C | TREE CONTACTS | Isolate last section of line for tree cutting Tapauwaroa Rd
11246 | 10/02/2005 | 2005-02-10 | 2004 | 40 | 48 | 1920 | B | PLANNED SHUTDOWN | Change T/x B556 at Lytton West Shops
11245 | 11/02/2005 | 2005-02-11 | 2004 | 71 | 154 | 9997 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole A4422 Turihau Stn
11247 | 15/02/2005 | 2005-02-15 | 2004 | 13 | 52 | 675 | B | PLANNED SHUTDOWN | Isolate 11kV cable between B359 & B867 Salvation Army fo lowering
11248 | 17/02/2005 | 2005-02-17 | 2004 | 180 | 40 | 7200 | B | PLANNED SHUTDOWN | Change T/x W1546 Black St Wairoa
11250 | 18/02/2005 | 2005-02-18 | 2004 | 6 | 802 | 4812 | C | UNKNOWN | Reclose CB W808 at Blacks Pad cause unknown
11249 | 20/02/2005 | 2005-02-20 | 2004 | 70 | 1136 | 79520 | C | UNKNOWN | Reclose CB W218 at Kiwi Sub cause unknown
11255 | 22/02/2005 | 2005-02-22 | 2004 | 570 | 12 | 6840 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Riverside Rd
11253 | 23/02/2005 | 2005-02-23 | 2004 | 264 | 93 | 21897 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole D3852 High Load near Hangaroa
11256 | 25/02/2005 | 2005-02-25 | 2004 | 6 | 226 | 1356 | C | UNKNOWN | Reclose CB G329 Rototahi cause unknown
11257 | 25/02/2005 | 2005-02-25 | 2004 | 177 | 220 | 31423 | C | FOREIGN INTERFERENCE | Repair 11kV lines D478 Lake Rd Patutahi
11254 | 28/02/2005 | 2005-02-28 | 2004 | 115 | 47 | 5405 | B | PLANNED SHUTDOWN | Change T/x C334 in McLaurins Rd
11265 | 01/03/2005 | 2005-03-01 | 2004 | 220 | 48 | 9792 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting Paroa Rd Tolaga Bay
11268 | 01/03/2005 | 2005-03-01 | 2004 | 18 | 402 | 7236 | C | UNKNOWN | Reclose CB D646 at Patutahi Sub cause unknown
11269 | 02/03/2005 | 2005-03-02 | 2004 | 120 | 47 | 5640 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole C1594 Mc Laurins Rd Hexton
11263 | 03/03/2005 | 2005-03-03 | 2004 | 79 | 48 | 3792 | B | PLANNED SHUTDOWN | Isolate11kV lines for tree cutting near Water Works Waingake
11264 | 03/03/2005 | 2005-03-03 | 2004 | 44 | 44 | 1936 | B | PLANNED SHUTDOWN | Breakout 11kV at T/x W1567 Haig St Wairoa
11270 | 05/03/2005 | 2005-03-05 | 2004 | 179 | 175 | 14633 | C | ADVERSE WEATHER | Repair 11kV lines between A219 and A221 Tatapouri
11271 | 07/03/2005 | 2005-03-07 | 2004 | 59 | 802 | 39813 | C | DEFECTIVE EQUIPMENT | Repair 11kV at pole W9457 at Nuhaka
11272 | 09/03/2005 | 2005-03-09 | 2004 | 97 | 82 | 7954 | C | DEFECTIVE EQUIPMENT | Replace faulty ABS W1015 at Kotemaori
11273 | 11/03/2005 | 2005-03-11 | 2004 | 14 | 16 | 224 | C | ADVERSE WEATHER | Rejoin jumpers at Pole E1280 Whatatutu
11274 | 11/03/2005 | 2005-03-11 | 2004 | 197 | 200 | 13746 | C | FOREIGN INTERFERENCE | Repair 11kV at pole H2259 Mangahauine Valley
11266 | 13/03/2005 | 2005-03-13 | 2004 | 30 | 332 | 8534 | B | PLANNED SHUTDOWN | Replace ABS W926 Freyberg St Wairoa
11275 | 14/03/2005 | 2005-03-14 | 2004 | 64 | 442 | 28288 | C | DEFECTIVE EQUIPMENT | Repair 11kv jumper at ABS B292 Aberdeen Rd
11267 | 15/03/2005 | 2005-03-15 | 2004 | 230 | 29 | 6670 | B | PLANNED SHUTDOWN | Replace 2 pole sub E30 at Waihirere Domain
11276 | 16/03/2005 | 2005-03-16 | 2004 | 75 | 725 | 25734 | C | ADVERSE WEATHER | Repair 11kV line at ABS W975 near Clydebank
11277 | 17/03/2005 | 2005-03-17 | 2004 | 5 | 328 | 1640 | C | UNKNOWN | Reclose CB J542 at Ruatoria Sub cause unknown
11278 | 18/03/2005 | 2005-03-18 | 2004 | 254 | 402 | 12972 | C | FOREIGN INTERFERENCE | Replace 11kV pole C5362 Hit by Light Truck in Bushmere Rd
11279 | 19/03/2005 | 2005-03-19 | 2004 | 115 | 99 | 9183 | C | DEFECTIVE EQUIPMENT | Restore 11kV after replacing Private pole E3132 Kanakanaia
11280 | 19/03/2005 | 2005-03-19 | 2004 | 55 | 188 | 10340 | C | UNKNOWN | Reclose CB F410 at Puha Sub cause Unknown
11281 | 19/03/2005 | 2005-03-19 | 2004 | 25 | 98 | 2406 | C | UNKNOWN | Reclose CB H341 in Mata Rd cause unknown
11282 | 21/03/2005 | 2005-03-21 | 2004 | 35 | 1496 | 42840 | C | UNKNOWN | Restart Generators at Te Araroa & Ruatoria cuase unknown
11283 | 22/03/2005 | 2005-03-22 | 2004 | 341 | 193 | 44605 | C | UNKNOWN | Checked lines Reclose CB D668 cause unknown
11284 | 22/03/2005 | 2005-03-22 | 2004 | 210 | 20 | 4200 | B | PLANNED SHUTDOWN | Replace pole & T/xs at J203 & J206 Poroporo Rd
11285 | 23/03/2005 | 2005-03-23 | 2004 | 223 | 36 | 8028 | B | PLANNED SHUTDOWN | Replace poles & T/xs J361 & J69 Maraehara Rd Tikitiki
11286 | 23/03/2005 | 2005-03-23 | 2004 | 323 | 43 | 13889 | B | PLANNED SHUTDOWN | Replace 2 pole sub E154 Te Whiti St Whatatutu
11288 | 23/03/2005 | 2005-03-23 | 2004 | 115 | 4 | 460 | B | PLANNED SHUTDOWN | Replace 11kV pole & T/x J241 Koia Rd Tikitiki
11287 | 24/03/2005 | 2005-03-25 | 2004 | 84 | 20 | 1680 | B | PLANNED SHUTDOWN | Replace 11kV pole & T/x J561 SH35 Te Araroa
11289 | 24/03/2005 | 2005-03-24 | 2004 | 100 | 39 | 3600 | B | PLANNED SHUTDOWN | Replace 11kV pole & T/x J170 in Tapuaeroa Rd Ruatoria
11290 | 24/03/2005 | 2005-03-24 | 2004 | 48 | 28 | 1344 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole D4915 hit by Tractor in Totangi Rd
11291 | 25/03/2005 | 2005-03-25 | 2004 | 144 | 204 | 23908 | C | TREE CONTACTS | Repair 11kV lines at pole W6080 Mangapoikie Rd
11292 | 25/03/2005 | 2005-03-25 | 2004 | 166 | 85 | 14110 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole F1962 in Te Wera Rd Matawai
11294 | 26/03/2005 | 2005-03-26 | 2004 | 183 | 13 | 2379 | C | LIGHTNING | Repair jumpers at pole D129 Taumata Rd Rere
11297 | 29/03/2005 | 2005-03-29 | 2004 | 100 | 32 | 3200 | B | PLANNED SHUTDOWN | Replace Red tagged 11kV poles Mahiwi & Hokinui
11298 | 29/03/2005 | 2005-03-29 | 2004 | 60 | 11 | 660 | B | PLANNED SHUTDOWN | Replace red tagged 11kV poles Te Tiki & Woodgreen
11293 | 30/03/2005 | 2005-03-30 | 2004 | 20 | 3 | 60 | C | DEFECTIVE EQUIPMENT | Replace fuses at pole E192 Moonlight Stn Rd
11295 | 30/03/2005 | 2005-03-30 | 2004 | 20 | 14 | 280 | B | PLANNED SHUTDOWN | Isolate 11kV cable between B359 to B867 at T/x B359 Gladstone Rd
11296 | 31/03/2005 | 2005-03-31 | 2004 | 143 | 5 | 715 | B | PLANNED SHUTDOWN | Replace 11kV pole & T/x J235 Te Hue Rd
11305 | 07/04/2005 | 2005-04-07 | 2005 | 22 | 5 | 180 | B | PLANNED SHUTDOWN | Relocate T/x F399 to pole F2813 at Motuhora Quarry
11303 | 08/04/2005 | 2005-04-08 | 2005 | 387 | 392 | 55932 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole C333 McLaurins Rd
11304 | 11/04/2005 | 2005-04-11 | 2005 | 136 | 17 | 2312 | C | FOREIGN INTERFERENCE | Remove possum of pole D3676 Bushy Knoll Rd
11300 | 12/04/2005 | 2005-04-12 | 2005 | 470 | 29 | 13630 | B | PLANNED SHUTDOWN | Reconductor 11kV between H1421 & H1426 Huriharama
11301 | 15/04/2005 | 2005-04-15 | 2005 | 487 | 29 | 6113 | B | PLANNED SHUTDOWN | Reconductor 11kV between H250 & H1421 Huriharama
11302 | 16/04/2005 | 2005-04-16 | 2005 | 75 | 79 | 5925 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable at B452 Aberdeen Rd
11299 | 18/04/2005 | 2005-04-18 | 2005 | 158 | 47 | 14758 | B | PLANNED SHUTDOWN | Isolate 11kV lines for Tree Cutting Ngakaroa Rd
11311 | 20/04/2005 | 2005-04-20 | 2005 | 32 | 98 | 2908 | C | UNKNOWN | Reclose H341 in Mata Rd cause unknown
11310 | 21/04/2005 | 2005-04-21 | 2005 | 29 | 48 | 2160 | B | PLANNED SHUTDOWN | Replace T/x J385 Waikura Rd Hicks Bay
11308 | 25/04/2005 | 2005-04-25 | 2005 | 640 | 54 | 23957 | C | TREE CONTACTS | Repair 11kV lines brtween poles G2383 & G2356 Tauwhareparae Rd
11309 | 25/04/2005 | 2005-04-25 | 2005 | 98 | 23 | 2254 | C | DEFECTIVE EQUIPMENT | Repair 11kV conductor at pole W8170 at Nuhaka
11306 | 27/04/2005 | 2005-04-27 | 2005 | 250 | 22 | 5500 | B | PLANNED SHUTDOWN | Replace pole & install new ABS F165 Makaretu Rd
11307 | 30/04/2005 | 2005-04-30 | 2005 | 238 | 18 | 4284 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Coopers Rd Tansley & Pipiwhakaio Rd
11316 | 01/05/2005 | 2005-05-01 | 2005 | 66 | 12 | 792 | C | FOREIGN INTERFERENCE | Repair 11kV pole D1409 in Waimata Valley Rd Hit by car
11315 | 03/05/2005 | 2005-05-03 | 2005 | 8 | 104 | 832 | C | ADVERSE WEATHER | Rejoin jumpers at pole J4411 Waikura Valley
11319 | 03/05/2005 | 2005-05-03 | 2005 | 352 | 126 | 15112 | B | PLANNED SHUTDOWN | Replace 11kV T/x pole J273 Paikea St Te Araroa
11318 | 05/05/2005 | 2005-05-05 | 2005 | 360 | 29 | 10440 | B | PLANNED SHUTDOWN | Replace 5 11kV poles Mangapoikie Rd
11320 | 05/05/2005 | 2005-05-05 | 2005 | 114 | 7 | 798 | B | PLANNED SHUTDOWN | Replace 11kV pole G3009 Nuhiti Stn Anaura Bay
11314 | 06/05/2005 | 2005-05-06 | 2005 | 107 | 593 | 22408 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole W6081 Mangapoikie Rd
11313 | 09/05/2005 | 2005-05-09 | 2005 | 82 | 30 | 2460 | B | PLANNED SHUTDOWN | Replace X arms on pole D2543 Pehiri Rd
11312 | 10/05/2005 | 2005-05-10 | 2005 | 166 | 46 | 6747 | C | TREE CONTACTS | Remove trees in 11kV at pole J2022 Tapuwaeroa
11317 | 10/05/2005 | 2005-05-10 | 2005 | 214 | 50 | 10700 | B | PLANNED SHUTDOWN | Change 11kV pole C1134 Taurau Valley Manutuke
11321 | 12/05/2005 | 2005-05-12 | 2005 | 60 | 15 | 900 | B | PLANNED SHUTDOWN | Erect new T/x on pole J1327 Kopuapounamu Rd
11322 | 16/05/2005 | 2005-05-16 | 2005 | 185 | 75 | 13875 | B | PLANNED SHUTDOWN | Replace 4 11kv poles in Bell Rd Cut trees Matawhero
11323 | 17/05/2005 | 2005-05-17 | 2005 | 174 | 74 | 12876 | C | TREE CONTACTS | Repair 11kV line at pole H2621 Waima Tokomaru Bay
11330 | 22/05/2005 | 2005-05-22 | 2005 | 324 | 97 | 20301 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole D3278 hit by Swan Tiniroto Rd
11329 | 23/05/2005 | 2005-05-23 | 2005 | 160 | 652 | 28001 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole W6084 Mangapoike Rd
11324 | 25/05/2005 | 2005-05-25 | 2005 | 24 | 24 | 540 | C | HUMAN ELEMENT | Reclose CB C13 & CB C15 at Matawhero Sub
11325 | 26/05/2005 | 2005-05-26 | 2005 | 274 | 25 | 6850 | B | PLANNED SHUTDOWN | Replace 11kV Pole C5158 Bell Rd
11326 | 27/05/2005 | 2005-05-27 | 2005 | 192 | 277 | 21936 | C | DEFECTIVE EQUIPMENT | Repair 11kV at pole W8328 at Morere
11327 | 30/05/2005 | 2005-05-30 | 2005 | 66 | 129 | 2898 | C | DEFECTIVE EQUIPMENT | Repair 11kV at pole J3744 Horoera Te Araroa
11328 | 30/05/2005 | 2005-05-30 | 2005 | 149 | 35 | 5215 | C | DEFECTIVE EQUIPMENT | Replace X Arms at pole J68 Maraehara Rd
11331 | 31/05/2005 | 2005-05-31 | 2005 | 30 | 16 | 480 | C | DEFECTIVE EQUIPMENT | Replace 2 11kV insulators on pole E2156 Omarpare Rd
11338 | 01/06/2005 | 2005-06-01 | 2005 | 72 | 13 | 936 | C | DEFECTIVE EQUIPMENT | Replace Xarm on T/x J262 in Te Wera Rd
11344 | 01/06/2005 | 2005-06-01 | 2005 | 475 | 25 | 11875 | B | PLANNED SHUTDOWN | Reconductor between C5144 & C5158 Bell Rd Matawhero
11337 | 02/06/2005 | 2005-06-02 | 2005 | 234 | 159 | 13298 | C | FOREIGN INTERFERENCE | Repair 11kV lines at T/x G27 Paramata Rd Tolaga Bay
11332 | 07/06/2005 | 2005-06-07 | 2005 | 110 | 24 | 2640 | B | PLANNED SHUTDOWN | Change T/x B518 in Mary St
11341 | 07/06/2005 | 2005-06-07 | 2005 | 27 | 36 | 972 | B | PLANNED SHUTDOWN | Change 11kV poles Lavenham Rd Patutahi
11342 | 07/06/2005 | 2005-06-07 | 2005 | 312 | 16 | 4992 | B | PLANNED SHUTDOWN | Change 11kv poles in Lavenham Rd Patutahi
11345 | 07/06/2005 | 2005-06-07 | 2005 | 211 | 77 | 10109 | C | FOREIGN INTERFERENCE | Repair 11kV lines at Pole G1480 Anaura Bay Rd
11346 | 07/06/2005 | 2005-06-07 | 2005 | 7 | 545 | 2177 | C | UNKNOWN | Reclose CB W215 at Kiwi Sub Cause unknown
11339 | 08/06/2005 | 2005-06-08 | 2005 | 17 | 47 | 1316 | B | PLANNED SHUTDOWN | Change 11kV poles Lavenham Rd Patutahi
11340 | 08/06/2005 | 2005-06-08 | 2005 | 311 | 5 | 1555 | B | PLANNED SHUTDOWN | Change 11kV poles Lavenham Rd Patutahi
11333 | 09/06/2005 | 2005-06-09 | 2005 | 135 | 12 | 1620 | B | PLANNED SHUTDOWN | Change T/x B571 in Charles St
11334 | 09/06/2005 | 2005-06-09 | 2005 | 35 | 41 | 1435 | B | PLANNED SHUTDOWN | Reconductor 11kV Lines Lavenham Rd
11335 | 09/06/2005 | 2005-06-09 | 2005 | 433 | 16 | 6928 | B | PLANNED SHUTDOWN | Reconductor 11kV lines Lavenham Rd Patutahi
11336 | 10/06/2005 | 2005-06-10 | 2005 | 323 | 18 | 5418 | B | PLANNED SHUTDOWN | Change 5 11kV poles in Bruce Rd Ormond
11343 | 15/06/2005 | 2005-06-15 | 2005 | 248 | 25 | 6200 | B | PLANNED SHUTDOWN | Relocate 11kV poles Horoera East Cape Rd
11349 | 15/06/2005 | 2005-06-15 | 2005 | 90 | 131 | 6989 | C | TREE CONTACTS | Repair 11kV lines at pole H1498 near Kopuaroa
11350 | 15/06/2005 | 2005-06-15 | 2005 | 125 | 29 | 3625 | C | DEFECTIVE EQUIPMENT | Peplace 11kV Xarm on pole E2897 Ngakaroa Rd
11348 | 16/06/2005 | 2005-06-16 | 2005 | 192 | 41 | 7872 | B | PLANNED SHUTDOWN | Replace poles C4701 & C4764 Muriwai Beach Rd
11347 | 17/06/2005 | 2005-06-17 | 2005 | 102 | 53 | 5406 | B | PLANNED SHUTDOWN | Repair 11kV lines & cut trees between H1497 & H1498 Kopuaroa
11351 | 18/06/2005 | 2005-06-18 | 2005 | 53 | 20 | 1060 | C | FOREIGN INTERFERENCE | Replace 11kV pole C3157 in Awapuni Rd Hit by Car
11352 | 20/06/2005 | 2005-06-20 | 2005 | 231 | 14 | 3234 | C | DEFECTIVE EQUIPMENT | Replace 11kV jumper on ABS C734 in McDonalds Rd Matawhero
11354 | 20/06/2005 | 2005-06-20 | 2005 | 270 | 30 | 7050 | B | PLANNED SHUTDOWN | Replace 5 11kV poles Humphries Rd
11353 | 21/06/2005 | 2005-06-21 | 2005 | 353 | 86 | 5543 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole W4997 Mangone Rd
11355 | 22/06/2005 | 2005-06-22 | 2005 | 126 | 7 | 882 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole D4137 in Campbell Rd Ngatapa
11356 | 23/06/2005 | 2005-06-23 | 2005 | 87 | 12 | 1044 | C | FOREIGN INTERFERENCE | Repair 11kV lines between G1822 & G178 Paramata Rd Tolaga Bay
11357 | 24/06/2005 | 2005-06-24 | 2005 | 111 | 533 | 25587 | C | DEFECTIVE EQUIPMENT | Replace 11kV lines at pole C5014 SH2 Main Rd Makaraka
11358 | 25/06/2005 | 2005-06-25 | 2005 | 258 | 336 | 42257 | C | FOREIGN INTERFERENCE | Repair 11kV lines between poles J821 & J3633 SH35 Ruatoria North
11359 | 26/06/2005 | 2005-06-26 | 2005 | 177 | 8 | 1416 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between poles W8394 & W8393 Morere
11360 | 27/06/2005 | 2005-06-27 | 2005 | 315 | 18 | 5670 | B | PLANNED SHUTDOWN | Replace 11kV pole D4196 Seddon St Patutahi
11361 | 28/06/2005 | 2005-06-28 | 2005 | 305 | 85 | 9580 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between H1033 & H1034 Mata Rd
11362 | 28/06/2005 | 2005-06-28 | 2005 | 95 | 1135 | 107825 | C | DEFECTIVE EQUIPMENT | Repair Tapchanger at Puha Sub
11363 | 29/06/2005 | 2005-06-29 | 2005 | 362 | 24 | 8688 | B | PLANNED SHUTDOWN | Reconductor 11kV Seddon St Patutahi
11364 | 30/06/2005 | 2005-06-30 | 2005 | 65 | 15 | 975 | C | DEFECTIVE EQUIPMENT | Replace broken binder on pole F2532 Maonui Tap Off
11365 | 05/07/2005 | 2005-07-05 | 2005 | 18 | 76 | 1258 | C | UNKNOWN | Reclose H341 Mata Rd cause unknown
11366 | 06/07/2005 | 2005-07-06 | 2005 | 287 | 260 | 29912 | C | DEFECTIVE EQUIPMENT | Replace RMU B751 Crn Anzac St & Stanley Rd
11369 | 08/07/2005 | 2005-07-08 | 2005 | 186 | 188 | 16397 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole E561 Kanakanaia Rd
11367 | 11/07/2005 | 2005-07-11 | 2005 | 400 | 13 | 5200 | B | PLANNED SHUTDOWN | Replace 11kV pole G3425 Tauwhareparae Rd
11368 | 11/07/2005 | 2005-07-11 | 2005 | 177 | 104 | 18408 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Hicks Bay Area
11370 | 12/07/2005 | 2005-07-12 | 2005 | 28 | 197 | 5516 | C | DEFECTIVE EQUIPMENT | Repair 11kV Jumper at ABS F229 Motu Rd Matawai
11371 | 12/07/2005 | 2005-07-12 | 2005 | 283 | 60 | 9990 | C | DEFECTIVE EQUIPMENT | Repair 11kV conductor at Pole A4038 Waiomoko Rd
11372 | 12/07/2005 | 2005-07-12 | 2005 | 54 | 18 | 972 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at pole F1469 Motu Rd
11373 | 12/07/2005 | 2005-07-12 | 2005 | 247 | 80 | 7961 | C | TREE CONTACTS | Repair 11kV between H562 & H563 SH35 Parenga
11374 | 15/07/2005 | 2005-07-15 | 2005 | 97 | 18 | 1746 | C | TREE CONTACTS | Isolate 11kV lines in Manders Rd to cut trees
11375 | 15/07/2005 | 2005-07-15 | 2005 | 134 | 8 | 1072 | B | PLANNED SHUTDOWN | Fit new DDO fuses to Tap off Loisels Beach
11376 | 15/07/2005 | 2005-07-15 | 2005 | 36 | 1135 | 40860 | C | DEFECTIVE EQUIPMENT | Replace 50kV pole F560 near Hihiroroa Rd Puha to Ngatapa line
11377 | 18/07/2005 | 2005-07-18 | 2005 | 226 | 645 | 14465 | C | UNKNOWN | Checked 11kV line by Helicopter Reclosed CB 215 Cause unknown
11378 | 18/07/2005 | 2005-07-18 | 2005 | 852 | 79 | 9998 | C | ADVERSE WEATHER | Repair 11kV lines SH35 Pole H538 Trees in Slip near Mangaroa
11379 | 19/07/2005 | 2005-07-19 | 2005 | 134 | 766 | 40145 | C | DEFECTIVE EQUIPMENT | Replace 11kV insulator on pole W1520 at Mahia
11380 | 19/07/2005 | 2005-07-19 | 2005 | 350 | 18 | 6300 | B | PLANNED SHUTDOWN | Reconductor 11kV in Seddon St & Kirkpatrick Rd Patutahi
11381 | 21/07/2005 | 2005-07-21 | 2005 | 156 | 11 | 1716 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole D1128 in Parakanapa Rd
11382 | 22/07/2005 | 2005-07-22 | 2005 | 13 | 18 | 234 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole F1469 Motu Rd
11383 | 26/07/2005 | 2005-07-26 | 2005 | 305 | 19 | 5795 | B | PLANNED SHUTDOWN | Replace 2 11kV poles Tawhara Valley
11384 | 27/07/2005 | 2005-07-27 | 2005 | 244 | 58 | 14152 | B | PLANNED SHUTDOWN | Replace 11kV poles Eripiti & Papuni Spurs
11385 | 27/07/2005 | 2005-07-27 | 2005 | 293 | 31 | 9083 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Tauwhareparae Rd
11387 | 28/07/2005 | 2005-07-28 | 2005 | 187 | 687 | 49127 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable ouside Community Centre Wairoa Township
11386 | 29/07/2005 | 2005-07-29 | 2005 | 278 | 10 | 2780 | B | PLANNED SHUTDOWN | Replace T/x Pole & restrain conductors Mangone Stn
11388 | 01/08/2005 | 2005-08-01 | 2005 | 48 | 402 | 17556 | C | TREE CONTACTS | Remove branch from 11kV pole D3070 Wharekopae Rd
11389 | 04/08/2005 | 2005-08-04 | 2005 | 60 | 9 | 540 | B | PLANNED SHUTDOWN | Connect New T/x on pole W5813 Te Kahu Rd Mohaka
11392 | 05/08/2005 | 2005-08-05 | 2005 | 185 | 172 | 4031 | C | TREE CONTACTS | Repair 11kV lines between W1708 & W21515 Ruapapa Waihi
11395 | 08/08/2005 | 2005-08-08 | 2005 | 100 | 46 | 4600 | B | PLANNED SHUTDOWN | Change T/x A366 in Rawiri St Kaiti
11393 | 10/08/2005 | 2005-08-10 | 2005 | 199 | 33 | 6567 | B | PLANNED SHUTDOWN | Change T/x B659 & Underground Sunvale Cres
11390 | 16/08/2005 | 2005-08-16 | 2005 | 446 | 10 | 4460 | B | PLANNED SHUTDOWN | Replace 11kV pole E203 Mangatu Rd
11391 | 17/08/2005 | 2005-08-17 | 2005 | 225 | 14 | 3150 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Mata Rd
11394 | 18/08/2005 | 2005-08-18 | 2005 | 232 | 14 | 3248 | B | PLANNED SHUTDOWN | Erect new T/x D3543 Ruakaka Rd Tiniroto
11396 | 23/08/2005 | 2005-08-23 | 2005 | 340 | 7 | 2380 | B | PLANNED SHUTDOWN | Replace poles & repair 11kV lines Rangiahua Spur
11397 | 26/08/2005 | 2005-08-26 | 2005 | 39 | 57 | 2223 | B | PLANNED SHUTDOWN | Repair 11kV jumper on pole C5014 at Makaraka
11402 | 26/08/2005 | 2005-08-26 | 2005 | 82 | 76 | 6232 | B | PLANNED SHUTDOWN | Replace 11kV pole D4332 W/O Hika
11400 | 27/08/2005 | 2005-08-27 | 2005 | 10 | 188 | 1880 | C | UNKNOWN | Reclose CB F408 at Puha Sub cause unknown
11398 | 28/08/2005 | 2005-08-28 | 2005 | 226 | 100 | 8292 | C | TREE CONTACTS | Repair 11kV lines pole E1581 Waipaoa Stn
11399 | 29/08/2005 | 2005-08-29 | 2005 | 520 | 116 | 58770 | C | FOREIGN INTERFERENCE | Replace 11kV pole J1161 Rangitukia Rd Tikitiki
11401 | 30/08/2005 | 2005-08-30 | 2005 | 360 | 29 | 10440 | B | PLANNED SHUTDOWN | Replace 5 11kV poles Papuni Spur
11429 | 01/09/2005 | 2005-09-01 | 2005 | 285 | 34 | 9690 | B | PLANNED SHUTDOWN | Replace H pole Mangatarata Stn Mata Rd
11403 | 05/09/2005 | 2005-09-05 | 2005 | 56 | 188 | 10528 | C | UNKNOWN | Reclose CB 410 at Puha Sub Cause unknown
11404 | 06/09/2005 | 2005-09-06 | 2005 | 160 | 12 | 1920 | B | PLANNED SHUTDOWN | Replace 2 11kV poles Hereheretau Rd
11405 | 06/09/2005 | 2005-09-06 | 2005 | 315 | 14 | 4410 | B | PLANNED SHUTDOWN | Replace 8 Heli poles Hereheretau Rd
11406 | 06/09/2005 | 2005-09-06 | 2005 | 225 | 29 | 6525 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole E2492 Ngakaroa Rd
11408 | 06/09/2005 | 2005-09-06 | 2005 | 185 | 43 | 5550 | B | PLANNED SHUTDOWN | Install new DDO fuses D153 & D485 Wharekopae Rd
11409 | 07/09/2005 | 2005-09-07 | 2005 | 63 | 486 | 19203 | C | FOREIGN INTERFERENCE | Replace 11kV pole C262 Kings Rd Hit by truck
11410 | 08/09/2005 | 2005-09-08 | 2005 | 85 | 7 | 595 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Ceasars Rd Ormond
11411 | 08/09/2005 | 2005-09-08 | 2005 | 155 | 91 | 6075 | C | TREE CONTACTS | Repair 11kv lines between A1945 & A1955 Uttings Rd Waimata
11412 | 08/09/2005 | 2005-09-08 | 2005 | 348 | 92 | 32016 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Upper Balance St
11428 | 13/09/2005 | 2005-09-13 | 2005 | 381 | 59 | 22479 | B | PLANNED SHUTDOWN | Replace 11kV pole B3270 in Lytton Rd
11413 | 15/09/2005 | 2005-09-15 | 2005 | 280 | 19 | 5320 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole D5953 Tansley Rd Patutahi
11414 | 16/09/2005 | 2005-09-16 | 2005 | 174 | 82 | 14268 | C | LIGHTNING | Repair 11kV jumper ABS J377 Waikura Valley
11415 | 17/09/2005 | 2005-09-17 | 2005 | 92 | 25 | 2300 | C | ADVERSE WEATHER | Repair 11kV line East Cape Rd Te Araroa
11416 | 17/09/2005 | 2005-09-17 | 2005 | 222 | 13 | 2886 | C | DEFECTIVE EQUIPMENT | Repair 11kV at pole W6276 Cricklewood Rd Wairoa
11417 | 18/09/2005 | 2005-09-18 | 2005 | 245 | 124 | 28182 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J1211 Beach Rd Rangitukia
11418 | 18/09/2005 | 2005-09-18 | 2005 | 230 | 101 | 8420 | C | DEFECTIVE EQUIPMENT | Cut jumpers to Tappoff Pole Down Private Line
11419 | 18/09/2005 | 2005-09-18 | 2005 | 176 | 150 | 26400 | C | TREE CONTACTS | Reclose CB G327 Tauwhareparae at Sub (Wind)
11420 | 18/09/2005 | 2005-09-18 | 2005 | 99 | 71 | 5909 | C | ADVERSE WEATHER | Temp prop up 11kV pole F1015 in Motu Village
11421 | 18/09/2005 | 2005-09-18 | 2005 | 31 | 38 | 1178 | C | DEFECTIVE EQUIPMENT | Replace bolt in Xarm pole D1367 Tiniroto Rd Patutahi
11422 | 19/09/2005 | 2005-09-19 | 2005 | 124 | 4 | 496 | C | TREE CONTACTS | Replace 11kV pole C4789 hit by tree Foxleys Rd Muriwai
11423 | 19/09/2005 | 2005-09-19 | 2005 | 71 | 21 | 1491 | C | ADVERSE WEATHER | Repair 11kV line at T/x J112 Tuparoa Rd Ruatoria
11424 | 19/09/2005 | 2005-09-19 | 2005 | 103 | 55 | 5665 | C | ADVERSE WEATHER | Replace 11kV pole F1015 in Motu Village
11425 | 19/09/2005 | 2005-09-19 | 2005 | 107 | 15 | 1605 | C | ADVERSE WEATHER | Repair 11kV lines between J2138 & J2139 Kopuponamu Valley
11426 | 20/09/2005 | 2005-09-20 | 2005 | 175 | 10 | 1750 | C | ADVERSE WEATHER | Replace T/x E151 Kanakanaia Rd
11427 | 20/09/2005 | 2005-09-20 | 2005 | 26 | 49 | 2303 | B | PLANNED SHUTDOWN | Replace 11kv Pole H1867 SH35 Ruatoria
11430 | 27/09/2005 | 2005-09-27 | 2005 | 298 | 52 | 15496 | B | PLANNED SHUTDOWN | Replace T/x & Sw/Gr W1566 Lahore St
11431 | 27/09/2005 | 2005-09-27 | 2005 | 440 | 27 | 11880 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Armstrong Rd Whatatutu
11432 | 01/10/2005 | 2005-10-01 | 2005 | 287 | 216 | 51142 | C | DEFECTIVE EQUIPMENT | Replace T/x on LBS E2467 Ngakaroa Rd
11440 | 02/10/2005 | 2005-10-02 | 2005 | 217 | 12 | 2604 | B | PLANNED SHUTDOWN | Install 12.5m 50kV pole Lytton Rd
11434 | 03/10/2005 | 2005-10-03 | 2005 | 130 | 34 | 4420 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Komihana Rd
11435 | 03/10/2005 | 2005-10-03 | 2005 | 133 | 131 | 16257 | C | TREE CONTACTS | Repair 11kV lines Makarika
11436 | 04/10/2005 | 2005-10-04 | 2005 | 164 | 65 | 1408 | C | FOREIGN INTERFERENCE | Repair 11kV cable hit by Cable driller Lytton Rd
11433 | 05/10/2005 | 2005-10-05 | 2005 | 3 | 13 | 39 | B | PLANNED SHUTDOWN | Change T/x A1478 Crawford Rd Generator in use
11437 | 05/10/2005 | 2005-10-05 | 2005 | 117 | 204 | 12877 | C | DEFECTIVE EQUIPMENT | Replace 11kV insulator on pole C5342 in Riverpoint Rd
11438 | 05/10/2005 | 2005-10-05 | 2005 | 453 | 63 | 12303 | C | TREE CONTACTS | Repair 11kV lines Between C11 & D793 Waingake Contractors tree Cutting
11439 | 07/10/2005 | 2005-10-07 | 2005 | 42 | 4294 | 121743 | C | FOREIGN INTERFERENCE | Remove wire from 11kV T/x bushing Kaiti Sub
11441 | 10/10/2005 | 2005-10-10 | 2005 | 44 | 767 | 31438 | C | ADVERSE WEATHER | Repair 11kV lines between W9111 & W9110 Kaiwatau Rd Mahia
11442 | 11/10/2005 | 2005-10-12 | 2005 | 685 | 17 | 4925 | C | ADVERSE WEATHER | Check 11kV line & Reclose CB D806
11445 | 14/10/2005 | 2005-10-14 | 2005 | 161 | 35 | 5635 | C | HUMAN ELEMENT | Repair 11kV lines Shot down with rifle Taumata Rd Rere
11444 | 17/10/2005 | 2005-10-17 | 2005 | 374 | 29 | 10846 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Tarndale Rd Whatatutu
11446 | 18/10/2005 | 2005-10-18 | 2005 | 174 | 18 | 4320 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole E2734 Bond Rd Ormond
11447 | 18/10/2005 | 2005-10-18 | 2005 | 103 | 49 | 5047 | C | LIGHTNING | Replace 11kV T/x H333 Waipiro Bay hit by Lightning
11448 | 19/10/2005 | 2005-10-19 | 2005 | 170 | 22 | 3740 | C | LIGHTNING | Change 11kV T/x D771 hit by Lightning Wharekopae Rd Ngatapa
11449 | 21/10/2005 | 2005-10-21 | 2005 | 220 | 204 | 35024 | C | DEFECTIVE EQUIPMENT | Replace 11kV Insulator on pole C5189 Riverpoint Rd Matawhero
11450 | 21/10/2005 | 2005-10-21 | 2005 | 17 | 23 | 391 | C | ADVERSE WEATHER | Rejoin 11kV jumpers on pole C2486 Pakawhai Rd Muriwai
11451 | 21/10/2005 | 2005-10-21 | 2005 | 107 | 244 | 16121 | C | UNKNOWN | Checked 11kV line & Reclosed CB D642 Cause unknown
11452 | 21/10/2005 | 2005-10-21 | 2005 | 346 | 175 | 14904 | C | TREE CONTACTS | Repair 11kV lines between H2312 & H2314 Carrol St Te Puia
11453 | 21/10/2005 | 2005-10-22 | 2005 | 1042 | 118 | 49028 | C | TREE CONTACTS | Repair 11kV lines at pole H1456 Kopuaroa
11454 | 21/10/2005 | 2005-10-22 | 2005 | 939 | 466 | 436625 | C | TREE CONTACTS | Remove tree from 11kV pole F1141 Otoko Hill
11455 | 21/10/2005 | 2005-10-21 | 2005 | 67 | 10 | 670 | C | ADVERSE ENVIRONMENT | Remove 11kV pole at Tarndale Slip
11456 | 21/10/2005 | 2005-10-22 | 2005 | 1217 | 67 | 81175 | C | TREE CONTACTS | Remove trees in 11kV line between ABS H123 & H340 Mata Rd
11457 | 21/10/2005 | 2005-10-22 | 2005 | 1301 | 43 | 34181 | C | TREE CONTACTS | Isolate 11kV lines Manghauine Valley Tokomaru Bay Cut Jumpers at H2192 & H37
11458 | 22/10/2005 | 2005-10-22 | 2005 | 1889 | 289 | 54238 | C | ADVERSE WEATHER | Repair twisted 11kV lines Kahungngu Spur Raupunga
11459 | 22/10/2005 | 2005-10-22 | 2005 | 523 | 96 | 44242 | C | TREE CONTACTS | Remove trees from 11kV lines E1219 Waimata Valley
11460 | 22/10/2005 | 2005-10-23 | 2005 | 738 | 266 | 81168 | C | TREE CONTACTS | Remove Branch from 11kV pole E368 Arakihi Rd Waimata
11461 | 22/10/2005 | 2005-10-23 | 2005 | 2425 | 154 | 241193 | C | TREE CONTACTS | Repair 11kV between G2047 & G2048 Tauwharaparae Rd
11462 | 22/10/2005 | 2005-10-22 | 2005 | 410 | 417 | 36702 | C | ADVERSE WEATHER | Isolate broken11kV lines across river near Kaiteratahi Bridge
11463 | 22/10/2005 | 2005-10-22 | 2005 | 74 | 8 | 592 | C | TREE CONTACTS | Isolate 11kV & 50Kv lines in Staffords Rd Pehiri
11464 | 22/10/2005 | 2005-10-22 | 2005 | 77 | 101 | 7777 | C | TREE CONTACTS | Remove tree from 11kV between J2756 & J525 SH35 Awatere
11465 | 22/10/2005 | 2005-10-22 | 2005 | 586 | 743 | 75092 | C | TREE CONTACTS | Repair 11kV beyond W6561 Tukemokihi
11466 | 22/10/2005 | 2005-10-22 | 2005 | 550 | 406 | 78596 | C | TREE CONTACTS | Replace 11kV pole C1066 near old Manutuke Bridge
11467 | 22/10/2005 | 2005-10-22 | 2005 | 135 | 11495 | 809474 | C | TREE CONTACTS | Remove tree from pole A5278 in 50kV line Shelly Rd
11468 | 23/10/2005 | 2005-10-23 | 2005 | 68 | 10 | 680 | C | DEFECTIVE EQUIPMENT | Replace 11kV insulator on pole D3032 Humphries Rd
11469 | 23/10/2005 | 2005-10-23 | 2005 | 141 | 8 | 1128 | C | TREE CONTACTS | Repair 50kV line Staffords Rd Pehiri
11470 | 23/10/2005 | 2005-10-23 | 2005 | 298 | 132 | 7368 | C | DEFECTIVE EQUIPMENT | Replace 11kV Sw/gr B631 at Woolworths
11471 | 25/10/2005 | 2005-10-25 | 2005 | 108 | 15 | 1620 | C | ADVERSE WEATHER | Replace 11kV across River after flood near Kaiteratahi Bridge
11472 | 25/10/2005 | 2005-10-25 | 2005 | 87 | 60 | 5220 | C | TREE CONTACTS | Repair 11kV line between H2786 & H2787 Mata Rd near Bremnar Stn
11473 | 31/10/2005 | 2005-10-31 | 2005 | 511 | 608 | 65588 | C | FOREIGN INTERFERENCE | Replace 11kV pole W7130 Ruatanawha St hit by Car
11474 | 31/10/2005 | 2005-10-31 | 2005 | 208 | 122 | 25376 | C | FOREIGN INTERFERENCE | Replace 11kV lines Crn Coops Rd & SH2 Muriwai Truck with Crane
11475 | 31/10/2005 | 2005-10-31 | 2005 | 263 | 444 | 116772 | C | TREE CONTACTS | Repair 11kV lines at pole F3179 near Puha turnoff
11476 | 01/11/2005 | 2005-11-01 | 2005 | 414 | 53 | 21942 | B | PLANNED SHUTDOWN | Change 2 H pole Structures near Mangatarata St Mata Rd
11477 | 02/11/2005 | 2005-11-02 | 2005 | 158 | 1128 | 114299 | C | TREE CONTACTS | Remove trees from 11kV near ABS A20 Darwin Rd
11478 | 03/11/2005 | 2005-11-03 | 2005 | 309 | 22 | 6798 | B | PLANNED SHUTDOWN | Replace 7 Heli Poles at Blue Gum Flats
11480 | 03/11/2005 | 2005-11-03 | 2005 | 412 | 193 | 27258 | C | DEFECTIVE EQUIPMENT | Replace 11kV line between D2927 & D2926 Ngatapa
11479 | 04/11/2005 | 2005-11-04 | 2005 | 287 | 1 | 287 | B | PLANNED SHUTDOWN | Replace 5 11kV poles River Road Nuhaka
11481 | 07/11/2005 | 2005-11-07 | 2005 | 176 | 296 | 23142 | C | FOREIGN INTERFERENCE | Repair 11kV lines river Xing Wai Stn Nuhaka
11482 | 11/11/2005 | 2005-11-11 | 2005 | 135 | 8 | 1080 | B | PLANNED SHUTDOWN | Change T/x A590 Hacche Rd
11483 | 13/11/2005 | 2005-11-13 | 2005 | 31 | 717 | 20916 | C | UNKNOWN | Reclose CB W215 at Kiwi Sub cause Unknown
11484 | 14/11/2005 | 2005-11-14 | 2005 | 96 | 159 | 5780 | C | DEFECTIVE EQUIPMENT | Replace T/x W8816 at Tahaenui SF6 Switch
11485 | 17/11/2005 | 2005-11-17 | 2005 | 275 | 17 | 1891 | B | PLANNED SHUTDOWN | Change T/x pole D496 Lake Rd Patutahi
11486 | 18/11/2005 | 2005-11-18 | 2005 | 150 | 22 | 3300 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting O'Gradys Rd
11487 | 22/11/2005 | 2005-11-22 | 2005 | 35 | 1282 | 25440 | C | TREE CONTACTS | Remove tree from 50kV line at pole J1806 near Radio Site Tikitiki
11491 | 23/11/2005 | 2005-11-23 | 2005 | 41 | 19 | 779 | C | DEFECTIVE EQUIPMENT | Repair broken jumper
11516 | 24/11/2005 | 2005-11-24 | 2005 | 41 | 46 | 1886 | B | PLANNED SHUTDOWN | Install new TX pole at G1471
11492 | 27/11/2005 | 2005-11-27 | 2005 | 363 | 138 | 36899 | C | TREE CONTACTS | Broken conductor at W7375
11493 | 27/11/2005 | 2005-11-27 | 2005 | 79 | 10 | 790 | C | TREE CONTACTS | Cut trees in line - sparking
11499 | 27/11/2005 | 2005-11-28 | 2005 | 311 | 324 | 37764 | C | TREE CONTACTS | Trees thru line J455
11509 | 27/11/2005 | 2005-11-28 | 2005 | 1006 | 246 | 210540 | C | ADVERSE WEATHER | Slip causing pole to fall at J4510
11494 | 28/11/2005 | 2005-11-28 | 2005 | 760 | 129 | 85905 | C | ADVERSE WEATHER | Broken conductors at H2565
11495 | 28/11/2005 | 2005-11-28 | 2005 | 99 | 762 | 34814 | C | ADVERSE WEATHER | Unknown tripping
11496 | 28/11/2005 | 2005-11-28 | 2005 | 253 | 60 | 15180 | C | TREE CONTACTS | Broken conductor W1701
11498 | 28/11/2005 | 2005-11-29 | 2005 | 865 | 328 | 157560 | C | TREE CONTACTS | Tree thru lines at J1652
11500 | 28/11/2005 | 2005-11-28 | 2005 | 265 | 87 | 21783 | C | TREE CONTACTS | Unknown tree contact
11501 | 28/11/2005 | 2005-11-28 | 2005 | 658 | 244 | 66696 | C | TREE CONTACTS | Treesthru line at C592 and C422
11504 | 28/11/2005 | 2005-11-28 | 2005 | 503 | 449 | 191737 | C | TREE CONTACTS | Trees in line at F135
11505 | 28/11/2005 | 2005-11-28 | 2005 | 38 | 2212 | 67465 | C | TREE CONTACTS | 50kV Coast trip Goodwin Rd
11506 | 28/11/2005 | 2005-11-28 | 2005 | 68 | 2118 | 142592 | C | UNKNOWN | 50kV Coast trip at Goodwin Rd
11507 | 28/11/2005 | 2005-11-28 | 2005 | 299 | 174 | 11943 | C | TREE CONTACTS | Tree thru line at A4526
11508 | 28/11/2005 | 2005-11-28 | 2005 | 604 | 124 | 52252 | C | TREE CONTACTS | Tree thru dble crt line at H1471
11497 | 29/11/2005 | 2005-11-29 | 2005 | 25 | 75 | 1599 | C | DEFECTIVE EQUIPMENT | Repair jumper A298
11502 | 29/11/2005 | 2005-11-29 | 2005 | 111 | 812 | 38353 | C | DEFECTIVE EQUIPMENT | Broken conductor
11503 | 29/11/2005 | 2005-11-29 | 2005 | 58 | 135 | 7118 | C | DEFECTIVE EQUIPMENT | ABS F88 faulty
11510 | 29/11/2005 | 2005-11-30 | 2005 | 156 | 88 | 7167 | C | UNKNOWN | Unknown
11511 | 29/11/2005 | 2005-11-29 | 2005 | 102 | 23 | 1962 | C | UNKNOWN | Unknown
11512 | 29/11/2005 | 2005-11-29 | 2005 | 26 | 53 | 1378 | C | TREE CONTACTS | Rejoin jumpers at H1471
11513 | 29/11/2005 | 2005-11-29 | 2005 | 189 | 8 | 1512 | C | FOREIGN INTERFERENCE | Insulators shot at C186
11514 | 29/11/2005 | 2005-11-29 | 2005 | 84 | 35 | 2940 | C | DEFECTIVE EQUIPMENT | Repair broken jumpers at E148
11515 | 29/11/2005 | 2005-11-29 | 2005 | 25 | 116 | 2900 | C | DEFECTIVE EQUIPMENT | Repair broken jumper at J73
11518 | 02/12/2005 | 2005-12-03 | 2005 | 555 | 501 | 77771 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at Pole W4139 near Frasertown
11526 | 04/12/2005 | 2005-12-04 | 2005 | 49 | 16 | 784 | C | FOREIGN INTERFERENCE | Restore 11kV after Car Hit Pole A6471 in Crawford Rd
11528 | 04/12/2005 | 2005-12-04 | 2005 | 18 | 16 | 288 | C | DEFECTIVE EQUIPMENT | Replace T/x A237 on Kaiti Hill
11489 | 05/12/2005 | 2005-12-05 | 2005 | 40 | 19 | 760 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole D322 Lavenham Rd
11527 | 05/12/2005 | 2005-12-05 | 2005 | 33 | 16 | 528 | C | FOREIGN INTERFERENCE | Replace 11kV jumpers at pole A237 on Kaiti Hill
11529 | 05/12/2005 | 2005-12-05 | 2005 | 177 | 133 | 10593 | B | PLANNED SHUTDOWN | Reconductor 11kV lines Mahunga Mahia
11520 | 07/12/2005 | 2005-12-07 | 2005 | 298 | 77 | 6461 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole H612 SH35 Tokomaru Bay
11522 | 07/12/2005 | 2005-12-07 | 2005 | 12 | 78 | 1560 | B | PLANNED SHUTDOWN | Reconductor 11kV lines Mahunga Mahia
11525 | 07/12/2005 | 2005-12-07 | 2005 | 183 | 7 | 1281 | B | PLANNED SHUTDOWN | Change T/x A99 Sirrah St Wainui
11523 | 09/12/2005 | 2005-12-09 | 2005 | 8 | 188 | 1504 | C | UNKNOWN | Reclose CB F140 Puha Sub Cause unknown
11530 | 11/12/2005 | 2005-12-12 | 2005 | 944 | 658 | 133554 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole J820 near Headleys Ruatoria
11519 | 12/12/2005 | 2005-12-12 | 2005 | 418 | 444 | 50147 | C | TREE CONTACTS | Repair 11kV lines near Otoko
11531 | 16/12/2005 | 2005-12-16 | 2005 | 177 | 33 | 5415 | C | DEFECTIVE EQUIPMENT | Isolate 11kV burnt pole D6194 Parakanapa Rd
11533 | 16/12/2005 | 2005-12-16 | 2005 | 150 | 62 | 9300 | B | PLANNED SHUTDOWN | Replace 11kV pole W1711 Mohaka
11532 | 17/12/2005 | 2005-12-17 | 2005 | 41 | 20 | 820 | C | DEFECTIVE EQUIPMENT | Rejoin 11kV jumpers at pole D1054 Parakanapa Rd
11534 | 20/12/2005 | 2005-12-20 | 2005 | 92 | 1087 | 42854 | C | DEFECTIVE EQUIPMENT | Repair broken O/H conductor between B1451 to B1452 Aberdeen Rd
11535 | 21/12/2005 | 2005-12-21 | 2005 | 223 | 175 | 39025 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers J1283 and tree cutting Bowling green Rd
11536 | 23/12/2005 | 2005-12-23 | 2005 | 56 | 119 | 6614 | C | FOREIGN INTERFERENCE | Replace 11kV pole D2868 Hit by Car in Bck Ormond Rd
11537 | 23/12/2005 | 2005-12-23 | 2005 | 158 | 672 | 51666 | C | LIGHTNING | Repair 11kV Cable on pole W1061 Hit by Lightining
11538 | 24/12/2005 | 2005-12-24 | 2005 | 136 | 153 | 8682 | C | TREE CONTACTS | Repair 11kV lines between E1382 & E1383 Kanakanaia Rd
11539 | 24/12/2005 | 2005-12-24 | 2005 | 166 | 6377 | 324238 | C | UNKNOWN | Reclose CB2 Kiwi A at Wairoa Sub Cause Unknown
11540 | 26/12/2005 | 2005-12-26 | 2005 | 264 | 326 | 50346 | C | DEFECTIVE EQUIPMENT | Replace 11kV Insulator on pole J897 SH35 Ruatoria North
11541 | 27/12/2005 | 2005-12-28 | 2005 | 369 | 216 | 63004 | C | FOREIGN INTERFERENCE | Replace 11kV pole E2136 SH2 Ormond Hit by Car
11542 | 31/12/2005 | 2005-12-31 | 2005 | 97 | 246 | 23862 | C | FOREIGN INTERFERENCE | Replace 11kV pole J2604 Hit by Car SH35 Te Araroa North
11543 | 31/12/2005 | 2005-12-31 | 2005 | 30 | 3965 | 118950 | C | TREE CONTACTS | Reclose CB 192 Carnarvon St at Gisborne Sub Tree in line pole B1857 in Oak St
11544 | 02/01/2006 | 2006-01-02 | 2005 | 971 | 100 | 15965 | C | TREE CONTACTS | Repair 11kv lines between E521 & E522 Tarndale Rd Whatatutu
11545 | 03/01/2006 | 2006-01-03 | 2005 | 256 | 80 | 10973 | C | TREE CONTACTS | Repair 11kV lines at pole J2023 near Tapuwaeroa Ruatoria
11546 | 04/01/2006 | 2006-01-04 | 2005 | 112 | 329 | 34862 | C | FOREIGN INTERFERENCE | Repair 11kV lines beyond J96 damaged by fire near Tikitiki Radio Site
11547 | 04/01/2006 | 2006-01-04 | 2005 | 145 | 218 | 18655 | C | UNKNOWN | Reclose CB H302 Inland at Tokomaru Bay Sub cause Unknown
11548 | 04/01/2006 | 2006-01-04 | 2005 | 273 | 217 | 59241 | C | DEFECTIVE EQUIPMENT | Reclose CB W820 Oraka Mahia
11549 | 06/01/2006 | 2006-01-07 | 2005 | 102 | 230 | 13432 | C | UNKNOWN | Reclose CB W814 at Cricklewood cause Unknown
11550 | 07/01/2006 | 2006-01-07 | 2005 | 83 | 739 | 19305 | C | UNKNOWN | Reclose CB W215 Frasertown at Kiwi Sub cause Unknown
11551 | 08/01/2006 | 2006-01-08 | 2005 | 385 | 95 | 21724 | C | TREE CONTACTS | Repair 11kV lines between G1672 & G1673 Paroa Rd Tolaga Bay
11552 | 11/01/2006 | 2006-01-11 | 2005 | 130 | 10 | 1300 | C | TREE CONTACTS | Repair 11kV lines between G1579 & G1580 Arikihi Rd Tolaga Bay
11553 | 12/01/2006 | 2006-01-12 | 2005 | 38 | 796 | 13653 | C | DEFECTIVE EQUIPMENT | Replace 11kV Insulator on ABS pole W922 Carroll St
11554 | 12/01/2006 | 2006-01-13 | 2005 | 546 | 1037 | 137836 | C | DEFECTIVE EQUIPMENT | Replace 33kV pole W3750 at Whakakihi
11555 | 16/01/2006 | 2006-01-16 | 2005 | 145 | 1085 | 35405 | C | FOREIGN INTERFERENCE | Repair 11kV lines Lloyde George Rd Wainui
11556 | 18/01/2006 | 2006-01-18 | 2005 | 50 | 188 | 9400 | C | UNKNOWN | Reclose CB F410 Kanakanaia at Puha Sub cause unknown
11557 | 18/01/2006 | 2006-01-18 | 2005 | 41 | 217 | 8317 | C | ADVERSE WEATHER | Repair 11kv lines at pole J402 Hicks Bay
11558 | 20/01/2006 | 2006-01-20 | 2005 | 214 | 95 | 10985 | C | FOREIGN INTERFERENCE | Repair 11kV lines between G1287 & G1288 Paroa Rd Tolaga Bay
11559 | 21/01/2006 | 2006-01-21 | 2005 | 41 | 821 | 26854 | C | UNKNOWN | Reclose CB A616 at Port Sub cause Unknown
11560 | 22/01/2006 | 2006-01-22 | 2005 | 165 | 67 | 11055 | C | FOREIGN INTERFERENCE | Replace 11kV pole A4371 at Makarori Hit by Car
11561 | 24/01/2006 | 2006-01-24 | 2005 | 22 | 98 | 2020 | C | UNKNOWN | Reclose CB H341 Mata Rd Cause Unknown
11562 | 24/01/2006 | 2006-01-24 | 2005 | 308 | 265 | 81620 | C | FOREIGN INTERFERENCE | Replace 11kV pole F2949 Whatatutu Rd Hit by Car
11563 | 24/01/2006 | 2006-01-24 | 2005 | 14 | 1066 | 8303 | C | FOREIGN INTERFERENCE | E/F Trip Mahia 33kV W1032 Patrol Line by Helicoptor
11564 | 24/01/2006 | 2006-01-24 | 2005 | 21 | 1496 | 29090 | C | FOREIGN INTERFERENCE | Start Generator Patrol 33 kV line Close CB W1032 at Wairoa Sub
11565 | 24/01/2006 | 2006-01-25 | 2005 | 264 | 737 | 50812 | C | ADVERSE WEATHER | Repair 11kV lines at pole A461 Wheatstone Rd
11566 | 24/01/2006 | 2006-01-24 | 2005 | 236 | 81 | 4024 | C | TREE CONTACTS | Repair 11kV lines H105 Mangaroa Rd Tokomaru Bay
11567 | 24/01/2006 | 2006-01-24 | 2005 | 582 | 370 | 62572 | C | ADVERSE WEATHER | Replace 2 11kV poles & Repair lines Uawa Parade
11568 | 24/01/2006 | 2006-01-25 | 2005 | 934 | 65 | 28174 | C | ADVERSE WEATHER | Repair 11kV lines pole A3945 Panikau Rd
11570 | 25/01/2006 | 2006-01-25 | 2005 | 40 | 27 | 1080 | C | ADVERSE WEATHER | Repair 11kV line pole A3653 Panikau Rd
11571 | 25/01/2006 | 2006-01-25 | 2005 | 215 | 646 | 135924 | C | ADVERSE WEATHER | Reclose CB G330 Town Feeder at Tolaga Bay Sub 11kV lines Clashing
11572 | 25/01/2006 | 2006-01-25 | 2005 | 90 | 217 | 17857 | C | FOREIGN INTERFERENCE | Reclose CBW820 at Mahia 11kV Hit by Goose
11573 | 26/01/2006 | 2006-01-26 | 2005 | 75 | 246 | 18024 | C | TREE CONTACTS | Remove branch from 11kV lines near Te Araroa Sub
11574 | 28/01/2006 | 2006-01-29 | 2005 | 46 | 188 | 8036 | C | UNKNOWN | Reclose CB F410 Kanakanaia at Puha Sub cause Unknown
11575 | 28/01/2006 | 2006-01-28 | 2005 | 87 | 117 | 4895 | C | FOREIGN INTERFERENCE | Replace burnt Xarm on pole H1663 Matahia Rd Ruatoria
11576 | 01/02/2006 | 2006-02-02 | 2005 | 647 | 131 | 11841 | C | TREE CONTACTS | Repair 11kV lines at pole H216 Matahia Rd Ruatoria
11577 | 01/02/2006 | 2006-02-01 | 2005 | 281 | 143 | 21503 | C | TREE CONTACTS | Repair 11kV lines at pole W634 Putere Rd
11578 | 01/02/2006 | 2006-02-01 | 2005 | 13 | 620 | 6945 | C | UNKNOWN | Reclose CB W213 at Kiwi Sub cause unknown
11579 | 01/02/2006 | 2006-02-01 | 2005 | 21 | 198 | 3456 | C | TREE CONTACTS | Remove trees burning at G2083 Waimea Stn Tap off
11580 | 02/02/2006 | 2006-02-02 | 2005 | 60 | 80 | 4640 | C | DEFECTIVE EQUIPMENT | Replace burnt T/x pole J292 at Hovell on Hill before Te Araroa
11581 | 02/02/2006 | 2006-02-02 | 2005 | 304 | 100 | 30400 | B | PLANNED SHUTDOWN | Install new 11kV switch gear W1240 Lucknow St
11582 | 03/02/2006 | 2006-02-03 | 2005 | 182 | 751 | 41058 | C | FOREIGN INTERFERENCE | Repair 11kv lines at pole W6717 possum on pole
11583 | 03/02/2006 | 2006-02-03 | 2005 | 580 | 204 | 26370 | C | FOREIGN INTERFERENCE | Replace 11kV pole C5162 SH2 Matawhero hit by car
11584 | 06/02/2006 | 2006-02-06 | 2005 | 54 | 193 | 9190 | C | TREE CONTACTS | Remove trees in 11kV at pole A453 at Tatapouri
11589 | 07/02/2006 | 2006-02-07 | 2005 | 86 | 88 | 7560 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on ABS A297 at Tatapouri
11590 | 07/02/2006 | 2006-02-07 | 2005 | 166 | 78 | 8308 | C | FOREIGN INTERFERENCE | Repair 11kV lines between poles G1444 to G1445 Anaura Bay
11587 | 11/02/2006 | 2006-02-11 | 2005 | 261 | 33 | 8613 | C | DEFECTIVE EQUIPMENT | Temp prop 11kV pole D3610 Ruakaka Rd
11595 | 11/02/2006 | 2006-02-11 | 2005 | 432 | 207 | 18077 | C | FOREIGN INTERFERENCE | Replace 11kV pole F367 Te Karaka hit by Car
11588 | 12/02/2006 | 2006-02-12 | 2005 | 175 | 12 | 2100 | B | PLANNED SHUTDOWN | Replace Faulty ABS W912 Carroll St
11594 | 12/02/2006 | 2006-02-12 | 2005 | 45 | 2594 | 95262 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
11585 | 13/02/2006 | 2006-02-13 | 2005 | 16 | 1747 | 26642 | C | UNKNOWN | Reclose CB 29 at Makaraka Sub cause unknown
11586 | 13/02/2006 | 2006-02-13 | 2005 | 244 | 33 | 8052 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole D3610 Ruakaka Rd
11591 | 16/02/2006 | 2006-02-16 | 2005 | 9 | 13 | 117 | B | PLANNED SHUTDOWN | Reroute 11kV Cable Lytton Rd
11596 | 19/02/2006 | 2006-02-19 | 2005 | 106 | 403 | 9264 | C | FOREIGN INTERFERENCE | Replace 11kV pole D3054 Wharekopae Rd Hit by Car
11597 | 21/02/2006 | 2006-02-22 | 2005 | 746 | 745 | 106185 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole W6595 Mangapoike Rd
11598 | 23/02/2006 | 2006-02-23 | 2005 | 170 | 15 | 2550 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole W6122 Awamate
11599 | 27/02/2006 | 2006-02-27 | 2005 | 148 | 19 | 2812 | C | DEFECTIVE EQUIPMENT | Replace 2 11kV poles E1613 & E1614 Manders Rd
11600 | 27/02/2006 | 2006-02-27 | 2005 | 56 | 1527 | 57287 | C | FOREIGN INTERFERENCE | Replace 50kV pole B5220 Lytton Rd Hit by Truck
11601 | 27/02/2006 | 2006-02-27 | 2005 | 68 | 4070 | 53331 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable at T/x B908 Anzac St
11602 | 28/02/2006 | 2006-02-28 | 2005 | 26 | 175 | 4086 | C | UNKNOWN | Reclose CB 353 at Kopuaroa cause unknown
11616 | 02/03/2006 | 2006-03-02 | 2005 | 312 | 460 | 42672 | B | PLANNED SHUTDOWN | Replace 11kV pole B2125 Crn Stout St & Dalrymple Rd
11611 | 04/03/2006 | 2006-03-04 | 2005 | 166 | 1600 | 95726 | C | TREE CONTACTS | Repair 11kV between poles A1745 & A1744 in Owen Rd
11613 | 04/03/2006 | 2006-03-04 | 2005 | 75 | 155 | 8788 | C | UNKNOWN | Reclose CB A283 at Tatapouri cause unknown
11610 | 05/03/2006 | 2006-03-05 | 2005 | 335 | 28 | 5207 | B | PLANNED SHUTDOWN | Run 50kV Conductor in Lytton Rd
11614 | 05/03/2006 | 2006-03-06 | 2005 | 793 | 272 | 18574 | C | ADVERSE WEATHER | Repair 11kV lines Pole W8405 Mangatoto St Nuhaka
11608 | 06/03/2006 | 2006-03-06 | 2005 | 180 | 72 | 4321 | B | PLANNED SHUTDOWN | Change 11kV pole & Switch gear Rutherford St & Hospital
11615 | 06/03/2006 | 2006-03-06 | 2005 | 556 | 104 | 57824 | C | FOREIGN INTERFERENCE | Repair 11kv lines at T/x J352 Waikura Stn
11607 | 07/03/2006 | 2006-03-07 | 2005 | 17 | 53 | 901 | B | PLANNED SHUTDOWN | Install new SDA3 Switch gear Rutherford St ( Generator)
11603 | 09/03/2006 | 2006-03-10 | 2005 | 233 | 185 | 18134 | C | TREE CONTACTS | Repair 11kV lines between H2335 to H2150 Puketiti Te Puia
11604 | 09/03/2006 | 2006-03-09 | 2005 | 26 | 55 | 1430 | C | DEFECTIVE EQUIPMENT | Replace 11kV Xarm on T/x 1586 Scott St
11605 | 09/03/2006 | 2006-03-09 | 2005 | 10 | 802 | 8020 | C | UNKNOWN | Reclose CB 808 at Blacks Pad cause unknown
11606 | 12/03/2006 | 2006-03-12 | 2005 | 206 | 111 | 27696 | C | TREE CONTACTS | Remove trees in 11kV at Coventry Stn & Reclose CB C4859
11609 | 16/03/2006 | 2006-03-16 | 2005 | 19 | 32 | 608 | B | PLANNED SHUTDOWN | Reterminate 11kV Cable on pole W1438 Clyde St
11617 | 18/03/2006 | 2006-03-18 | 2005 | 351 | 256 | 68538 | C | FOREIGN INTERFERENCE | Replace 11kV pole B1792 in Awapuni Rd
11618 | 20/03/2006 | 2006-03-20 | 2005 | 135 | 19 | 2565 | C | DEFECTIVE EQUIPMENT | Replace X arm on pole H1598 Puhunga Rd
11619 | 22/03/2006 | 2006-03-22 | 2005 | 128 | 39 | 4992 | B | PLANNED SHUTDOWN | Repair 11kV jumpers between poles A3695 & A3696 Panikau Rd
11620 | 22/03/2006 | 2006-03-22 | 2005 | 328 | 376 | 16768 | B | PLANNED SHUTDOWN | Install UG Cable between W3628 to W8902 at Mahia
11621 | 22/03/2006 | 2006-03-22 | 2005 | 106 | 423 | 11151 | C | DEFECTIVE EQUIPMENT | Disconnect & cut away T/x at Switch W8816 near Tahaenui
11622 | 23/03/2006 | 2006-03-23 | 2005 | 187 | 436 | 50944 | C | TREE CONTACTS | Remove tree from 11kV at pole J543 at Tikitiki
11623 | 23/03/2006 | 2006-03-23 | 2005 | 218 | 87 | 1956 | B | PLANNED SHUTDOWN | Replace 4 11kV poles Wainui Rd
11624 | 24/03/2006 | 2006-03-24 | 2005 | 95 | 199 | 18905 | C | UNKNOWN | Reclose CB 24 at Tuai cause Unknown
11625 | 26/03/2006 | 2006-03-26 | 2005 | 183 | 343 | 27751 | C | TREE CONTACTS | Remove trees in 11kV J2022 to J2023 in Tapuwaeroa Rd
11626 | 28/03/2006 | 2006-03-28 | 2005 | 18 | 226 | 4068 | C | UNKNOWN | Reclose CB G329 at Tolaga Bay Sub cause unknown
11627 | 28/03/2006 | 2006-03-28 | 2005 | 281 | 32 | 8992 | B | PLANNED SHUTDOWN | Replace 7 11kV poles Marumaru Spur
11628 | 28/03/2006 | 2006-03-28 | 2005 | 206 | 871 | 92878 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines Between A309 to A808 near Tolaga Bay
11629 | 30/03/2006 | 2006-03-30 | 2005 | 90 | 246 | 22140 | C | TREE CONTACTS | Remove trees from 11kV lines at pole J2640 Hicks Bay
11631 | 01/04/2006 | 2006-04-01 | 2006 | 261 | 65 | 11085 | C | DEFECTIVE EQUIPMENT | Replace broken Xarm on pole E699 near Wairere Stn
11632 | 01/04/2006 | 2006-04-01 | 2006 | 68 | 920 | 35607 | C | DEFECTIVE EQUIPMENT | Repair 11kV Oil Switch B918 in Pine St
11630 | 03/04/2006 | 2006-04-03 | 2006 | 202 | 8 | 1616 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarm on pole A3785 Stevens Rd
11633 | 05/04/2006 | 2006-04-05 | 2006 | 215 | 264 | 33444 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole W8346 Possum Bend Morere
11634 | 05/04/2006 | 2006-04-05 | 2006 | 173 | 180 | 16450 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole E596 Kanakanaia (Ducks)
11636 | 10/04/2006 | 2006-04-10 | 2006 | 295 | 36 | 10116 | B | PLANNED SHUTDOWN | Replace 4 11kV poles Ahirau Stn Rd Te Karaka
11635 | 12/04/2006 | 2006-04-12 | 2006 | 21 | 646 | 13317 | C | UNKNOWN | Reclose CB W213 at Kiwi Sub cause unknown
11637 | 18/04/2006 | 2006-04-18 | 2006 | 208 | 49 | 10192 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Waipiro Bay Rd
11638 | 18/04/2006 | 2006-04-18 | 2006 | 347 | 6 | 2082 | B | PLANNED SHUTDOWN | Reconductor 11kV lines Wainui Rd
11639 | 18/04/2006 | 2006-04-18 | 2006 | 4 | 81 | 324 | B | PLANNED SHUTDOWN | Install Generator for Reconductoring 11kV lines Wainui Rd
11642 | 18/04/2006 | 2006-04-19 | 2006 | 237 | 1051 | 122541 | C | FOREIGN INTERFERENCE | Replace Insulator on pole A3452 Goodwins Rd (possum)
11640 | 19/04/2006 | 2006-04-19 | 2006 | 298 | 87 | 2355 | B | PLANNED SHUTDOWN | Reconductor 11kV lines Wainui Rd
11641 | 19/04/2006 | 2006-04-19 | 2006 | 4 | 81 | 324 | B | PLANNED SHUTDOWN | Install Generator for Reconductoring 11kV lines Wainui Rd
11643 | 19/04/2006 | 2006-04-19 | 2006 | 180 | 14 | 2520 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole A1593 Glenroy Rd
11644 | 20/04/2006 | 2006-04-20 | 2006 | 307 | 110 | 5894 | B | PLANNED SHUTDOWN | Reconductor 11kV lines Wainui Rd
11646 | 21/04/2006 | 2006-04-21 | 2006 | 176 | 41 | 7216 | B | PLANNED SHUTDOWN | Replace 11kV pole J761 & Repair GVR Switch Tapuaeroa Rd
11645 | 24/04/2006 | 2006-04-24 | 2006 | 142 | 743 | 24920 | C | FOREIGN INTERFERENCE | Repair 11kV lines betwee W6065 & W6086 Mangapoikie Rd ( Turkey)
11647 | 26/04/2006 | 2006-04-26 | 2006 | 30 | 159 | 4670 | B | PLANNED SHUTDOWN | Replace burnt out DDO fuse C133 Browns Beach Rd Muriwai
11648 | 26/04/2006 | 2006-04-26 | 2006 | 153 | 58 | 4668 | C | TREE CONTACTS | Repair 11kV lines between poles C824 & C825 Tawera Rd Waingake
11649 | 27/04/2006 | 2006-04-27 | 2006 | 105 | 35 | 3675 | B | PLANNED SHUTDOWN | Install 11kV DDO fuses at E1093 Kanakanaia Rd
11650 | 27/04/2006 | 2006-04-27 | 2006 | 283 | 14 | 3962 | B | PLANNED SHUTDOWN | Replace 11kV poles & Xarms Onenui Stn Mahia
11653 | 27/04/2006 | 2006-04-27 | 2006 | 158 | 21 | 3318 | B | PLANNED SHUTDOWN | Replace T/x B6203 with new 300Kva at Harbourveiw Apartments
11651 | 28/04/2006 | 2006-04-28 | 2006 | 286 | 327 | 93522 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole J1310 Waiomatatini Rd Ruatoria
11652 | 30/04/2006 | 2006-05-01 | 2006 | 166 | 73 | 8554 | C | ADVERSE WEATHER | Replace 11kV pole F1870 Whakarau Rd washed out by river
11655 | 01/05/2006 | 2006-05-01 | 2006 | 42 | 52 | 2004 | C | ADVERSE WEATHER | Rejoin jumpers at pole F1875 Whakarau Rd after pole Replacement
11656 | 02/05/2006 | 2006-05-02 | 2006 | 325 | 26 | 8450 | B | PLANNED SHUTDOWN | Replace 4 11kV poles with Helicopter Waihua Valley
11657 | 03/05/2006 | 2006-05-03 | 2006 | 45 | 196 | 7623 | C | ADVERSE WEATHER | Replace 11kV pole W9254 Onenui Mahia (Wind)
11658 | 04/05/2006 | 2006-05-04 | 2006 | 305 | 11 | 3355 | B | PLANNED SHUTDOWN | Replace 4 11kV poles with Helicopter Cricklewood Rd Spur
11659 | 04/05/2006 | 2006-05-04 | 2006 | 183 | 849 | 25677 | C | FOREIGN INTERFERENCE | Replace 11kV pole D2834 Bck Ormond Rd Hit by Car
11661 | 06/05/2006 | 2006-05-06 | 2006 | 122 | 4 | 488 | C | LIGHTNING | Replace T/x C222 Bushmere Rd
11662 | 06/05/2006 | 2006-05-06 | 2006 | 286 | 181 | 45989 | C | DEFECTIVE EQUIPMENT | Check 11kV Switch W1450 Tuai
11663 | 07/05/2006 | 2006-05-07 | 2006 | 139 | 100 | 8126 | C | FOREIGN INTERFERENCE | Repair H Pole D3298 Tiniroto Rd Damaged by Slip
11664 | 08/05/2006 | 2006-05-08 | 2006 | 41 | 76 | 5016 | B | PLANNED SHUTDOWN | Replace Sw/Gr at T/X C446 Abereen Rd
11665 | 08/05/2006 | 2006-05-08 | 2006 | 230 | 393 | 74172 | C | DEFECTIVE EQUIPMENT | Replace T/x Xarm on F 137 Otoko Hill
11666 | 09/05/2006 | 2006-05-09 | 2006 | 189 | 119 | 22238 | C | TREE CONTACTS | Repair 11kV lines pole G1583 Arikihi Rd
11667 | 11/05/2006 | 2006-05-11 | 2006 | 248 | 9 | 2232 | B | PLANNED SHUTDOWN | Reconstruct 11kV lines Parkinson St Tolaga Bay
11668 | 11/05/2006 | 2006-05-11 | 2006 | 514 | 9 | 4626 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Goodwins Rd
11660 | 12/05/2006 | 2006-05-12 | 2006 | 11 | 2594 | 28534 | C | LIGHTNING | Reclose CB A8 Goodwins Rd
11669 | 12/05/2006 | 2006-05-12 | 2006 | 271 | 61 | 13805 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole A3736 Panikau Rd
11670 | 15/05/2006 | 2006-05-15 | 2006 | 17 | 1604 | 14434 | C | UNKNOWN | Reclose CB54 at Kaiti Sub cause unknown
11671 | 18/05/2006 | 2006-05-18 | 2006 | 247 | 35 | 8645 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Kanakanaia Rd
11673 | 19/05/2006 | 2006-05-19 | 2006 | 118 | 8 | 944 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Kanakanaia Rd
11672 | 22/05/2006 | 2006-05-22 | 2006 | 2 | 28 | 112 | B | PLANNED SHUTDOWN | Shutdown to change over to Generator to Replace T/x A78 Maoana Rd
11676 | 22/05/2006 | 2006-05-22 | 2006 | 328 | 11 | 7172 | B | PLANNED SHUTDOWN | Replace 5 11kV poles Motu Rd
11674 | 24/05/2006 | 2006-05-24 | 2006 | 233 | 23 | 5359 | B | PLANNED SHUTDOWN | Repair 11kV lines at pole C824 Waingake Rd
11675 | 24/05/2006 | 2006-05-24 | 2006 | 4 | 73 | 288 | B | PLANNED SHUTDOWN | Shutdown to Connect Generator for T/x Change B236 in Clifford St
11677 | 25/05/2006 | 2006-05-25 | 2006 | 4 | 45 | 180 | B | PLANNED SHUTDOWN | Connect generator to change T/x C433 Alfreco Motel Gladstone Rd
11679 | 27/05/2006 | 2006-05-27 | 2006 | 193 | 96 | 12694 | C | TREE CONTACTS | Remove trees in 11kV lines pole J780 Te Hue Rd Tikitiki
11678 | 28/05/2006 | 2006-05-28 | 2006 | 22 | 7530 | 165660 | C | DEFECTIVE EQUIPMENT | Isolate VT at Kaiti Sub & Reclose CB152 at Gisborne Sub
11680 | 28/05/2006 | 2006-05-28 | 2006 | 11 | 98 | 1078 | C | HUMAN ELEMENT | Reclose CB 817 after Earth Switch B1015 closed in error
11681 | 28/05/2006 | 2006-05-28 | 2006 | 302 | 4 | 1208 | B | PLANNED SHUTDOWN | Isolate 11kV lines for Building Demolition Grey St
11682 | 30/05/2006 | 2006-05-30 | 2006 | 305 | 53 | 16165 | B | PLANNED SHUTDOWN | Replace 5 11kV poles Motu Township
11686 | 03/06/2006 | 2006-06-03 | 2006 | 139 | 1193 | 93054 | C | DEFECTIVE EQUIPMENT | Replace 11kV SW/GR at B756 Lytton Rd Manuka St Crn
11687 | 03/06/2006 | 2006-06-03 | 2006 | 29 | 226 | 5981 | C | UNKNOWN | Reclose CB G329 at Tolaga Bay Sub cause Unknown
11688 | 04/06/2006 | 2006-06-04 | 2006 | 60 | 145 | 8073 | C | FOREIGN INTERFERENCE | Repair 11kV lines at T/x H231 Puhunga Rd
11683 | 05/06/2006 | 2006-06-05 | 2006 | 240 | 9 | 2160 | B | PLANNED SHUTDOWN | Replace 11kV pole F2688 Motu Falls Rd
11684 | 05/06/2006 | 2006-06-05 | 2006 | 335 | 13 | 4355 | B | PLANNED SHUTDOWN | Change T/x D479 Branson Rd to 100Kva
11685 | 06/06/2006 | 2006-06-06 | 2006 | 113 | 7 | 791 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree ctting Kaitara Lane Puha
11694 | 09/06/2006 | 2006-06-09 | 2006 | 20 | 78 | 1560 | C | UNKNOWN | Reclose CB 215 cause Unknown
11695 | 09/06/2006 | 2006-06-09 | 2006 | 19 | 802 | 10309 | C | UNKNOWN | Reclose CB W808 Blacks Pad cause unknown
11696 | 10/06/2006 | 2006-06-10 | 2006 | 27 | 729 | 17007 | C | UNKNOWN | Reclose CB W215 at Kiwi Sub cause unknown
11697 | 11/06/2006 | 2006-06-11 | 2006 | 69 | 1278 | 48380 | C | ADVERSE WEATHER | Repair 1 Span 50kV between J1837 to J1838 Te Araroa
11698 | 11/06/2006 | 2006-06-11 | 2006 | 41 | 230 | 9430 | C | UNKNOWN | Reclose W814 Chapmans cause unknown
11699 | 12/06/2006 | 2006-06-12 | 2006 | 304 | 246 | 71308 | C | ADVERSE WEATHER | Replace floating wire at pole J2597 Hicks Bay
11700 | 12/06/2006 | 2006-06-12 | 2006 | 156 | 17 | 2652 | C | ADVERSE WEATHER | Remove conductors from pole H319 Tokomaru Bay
11701 | 12/06/2006 | 2006-06-12 | 2006 | 1704 | 180 | 138704 | C | ADVERSE WEATHER | Replace 3 11kV poles and repair conductors Ohuka
11702 | 12/06/2006 | 2006-06-12 | 2006 | 619 | 85 | 52615 | C | ADVERSE WEATHER | Repair 11kV lines at pole F1947 Matawai North
11703 | 12/06/2006 | 2006-06-12 | 2006 | 767 | 71 | 44089 | C | TREE CONTACTS | Repair 11kV lines at pole F105 Motu Rd
11704 | 12/06/2006 | 2006-06-12 | 2006 | 103 | 27 | 1899 | C | TREE CONTACTS | Remove branch line from 11kV line at pole E156 Kanakanaia Rd
11705 | 12/06/2006 | 2006-06-12 | 2006 | 132 | 1069 | 120225 | C | UNKNOWN | Patrol Tahaenui to Wairoa Sub & Reclose W1032 cause unknown
11706 | 12/06/2006 | 2006-06-12 | 2006 | 99 | 155 | 15345 | C | TREE CONTACTS | Repair 11kV lines at pole W10034 Otoi trees
11707 | 12/06/2006 | 2006-06-12 | 2006 | 407 | 85 | 8139 | C | ADVERSE WEATHER | Repair 11kV lines at pole W36673 Waihi
11708 | 12/06/2006 | 2006-06-12 | 2006 | 72 | 252 | 18144 | C | ADVERSE WEATHER | Reclose CB D640 Lavenham Patutahi Sub cause unknown
11709 | 12/06/2006 | 2006-06-13 | 2006 | 1935 | 17 | 11295 | C | ADVERSE WEATHER | Isolate broken 11kV pole D3768 Bushy Knoll Rd
11710 | 12/06/2006 | 2006-06-12 | 2006 | 465 | 101 | 23495 | C | ADVERSE WEATHER | Repair 11kV between J312 to J396 Te Hue Rd
11711 | 12/06/2006 | 2006-06-13 | 2006 | 1868 | 94 | 24920 | C | ADVERSE WEATHER | Repair 11kV lines at pole E2225 Tarndale Rd
11712 | 12/06/2006 | 2006-06-14 | 2006 | 2589 | 104 | 143691 | C | ADVERSE WEATHER | Replace 11kV pole J4253 Waikura Valley
11713 | 12/06/2006 | 2006-06-12 | 2006 | 579 | 85 | 50983 | C | TREE CONTACTS | Replace 11kV pole & repair conductors in Ihungia Rd
11714 | 12/06/2006 | 2006-06-12 | 2006 | 391 | 335 | 24460 | C | ADVERSE WEATHER | Cut away T/x J176 on ground Tapuawaeroa Rd Ruatoria
11715 | 12/06/2006 | 2006-06-12 | 2006 | 1424 | 71 | 58590 | C | ADVERSE WEATHER | Isolate broken pole D5130 Tahora Rd
11716 | 12/06/2006 | 2006-06-12 | 2006 | 108 | 56 | 4800 | C | ADVERSE WEATHER | Isolate 11kV pole F1709 Whakarau Rd
11717 | 13/06/2006 | 2006-06-13 | 2006 | 119 | 5 | 595 | C | ADVERSE WEATHER | Isolate 11kV lines for tree cutting Te Hue Rd
11718 | 13/06/2006 | 2006-06-14 | 2006 | 1227 | 16 | 19632 | C | ADVERSE WEATHER | Replace 11kV pole E2185 Mangamaia Whatatutu
11719 | 13/06/2006 | 2006-06-13 | 2006 | 118 | 20 | 2360 | C | ADVERSE WEATHER | Repair 11kV lines beyond J408 Matakaoa Point
11689 | 14/06/2006 | 2006-06-14 | 2006 | 130 | 9 | 1170 | C | ADVERSE WEATHER | Repair 11kV between J3829 to J3830 Matakaoa
11690 | 14/06/2006 | 2006-06-14 | 2006 | 94 | 33 | 3102 | C | ADVERSE WEATHER | Temp repair 11kV pole D3622 Rukaka Rd
11691 | 14/06/2006 | 2006-06-14 | 2006 | 170 | 74 | 12580 | C | ADVERSE WEATHER | Replace Pole H2624 Waima Rd Tokomaru Bay
11720 | 14/06/2006 | 2006-06-14 | 2006 | 77 | 18 | 1386 | C | ADVERSE WEATHER | Isolate 11kV lines for tree cutting Huiarua Stn Mata Rd
11721 | 15/06/2006 | 2006-06-15 | 2006 | 26 | 18 | 468 | C | ADVERSE WEATHER | Rejoin 11kV jumpers at pole H2299 in Toa st Tokomaru Bay
11722 | 15/06/2006 | 2006-06-15 | 2006 | 356 | 3382 | 107451 | C | FOREIGN INTERFERENCE | Isolate 11kV Mangapoike Rd Digger in contact with lines and restore power to Kiwi Sub
11723 | 16/06/2006 | 2006-06-16 | 2006 | 159 | 54 | 8586 | C | TREE CONTACTS | Repair 11kV lines beyond G214 Tauwhareparae Rd
11724 | 16/06/2006 | 2006-06-16 | 2006 | 86 | 22 | 1892 | C | ADVERSE WEATHER | Repair 11kv lines pole F749 Makaertu Rd
11725 | 16/06/2006 | 2006-06-16 | 2006 | 35 | 49 | 1715 | C | DEFECTIVE EQUIPMENT | Replace burnt out DDo fuse base at T/x J6 Waikura Valley
11726 | 16/06/2006 | 2006-06-16 | 2006 | 31 | 1054 | 25429 | C | ADVERSE WEATHER | Repair 33kV T/x at Blacks Pad
11727 | 18/06/2006 | 2006-06-18 | 2006 | 130 | 11 | 1430 | C | DEFECTIVE EQUIPMENT | Replace 11kV fuse base at Tx F87 Whakarau Rd
11728 | 18/06/2006 | 2006-06-19 | 2006 | 1637 | 19 | 31103 | C | ADVERSE WEATHER | Repair 11kv lines pole W4576 Waikaremoana
11729 | 18/06/2006 | 2006-06-18 | 2006 | 134 | 377 | 47984 | C | ADVERSE WEATHER | Reclose CB F408 Matawai at Puha Sub cause unknown
11730 | 19/06/2006 | 2006-06-19 | 2006 | 515 | 215 | 30049 | C | ADVERSE WEATHER | Isolate 11kV lines Waihua W6369 to W1002 and Connect Generator
11731 | 19/06/2006 | 2006-06-19 | 2006 | 245 | 553 | 24909 | C | ADVERSE WEATHER | Repair 11kV lines at pole A4109 on Kaiti Hill
11732 | 19/06/2006 | 2006-06-19 | 2006 | 108 | 192 | 8834 | C | ADVERSE WEATHER | Repair 11kV lines E2675 Ngakaroa Rd
11733 | 19/06/2006 | 2006-06-19 | 2006 | 86 | 286 | 14616 | C | TREE CONTACTS | Isolate 11kV lines Lavenham Rd near T/x D383
11734 | 19/06/2006 | 2006-06-20 | 2006 | 1248 | 98 | 109320 | C | TREE CONTACTS | Repair 11kV lines between ABS poles H123 & H317 Fernside Rd
11735 | 19/06/2006 | 2006-06-20 | 2006 | 1151 | 156 | 50328 | C | TREE CONTACTS | Repair 11kv Lines at pole E1086 Kanakanaia Rd
11736 | 19/06/2006 | 2006-06-19 | 2006 | 306 | 235 | 31743 | C | TREE CONTACTS | Isolate 11kV at Cut jumpers pole E1762 & E103 SH2 Te Karaka
11737 | 19/06/2006 | 2006-06-19 | 2006 | 274 | 218 | 22520 | C | TREE CONTACTS | Repair 11kV lines pole C550 Rakaukaka Rd Manutuke
11738 | 19/06/2006 | 2006-06-19 | 2006 | 179 | 191 | 17168 | C | FOREIGN INTERFERENCE | Remove shed roof from 11kV lines near T/x 205 Riverpoint Rd
11739 | 19/06/2006 | 2006-06-19 | 2006 | 1212 | 110 | 14699 | C | ADVERSE WEATHER | Replace 11kv Pole C3755 SH2 Whararatas
11740 | 19/06/2006 | 2006-06-20 | 2006 | 619 | 191 | 39916 | C | ADVERSE WEATHER | Isolate 11kV & cut jumpers at C522 SH2 Matawhero
11741 | 19/06/2006 | 2006-06-19 | 2006 | 253 | 87 | 8312 | C | TREE CONTACTS | Isolate 11kV lines & cut jumpers at pole G4072 & G4070 Wharekaka Crn
11742 | 19/06/2006 | 2006-06-20 | 2006 | 817 | 101 | 25499 | C | TREE CONTACTS | Isolate 11kV & cut jumpers at J2980 SH35 Tikitiki
11743 | 19/06/2006 | 2006-06-19 | 2006 | 164 | 29 | 13967 | C | ADVERSE WEATHER | Cut 11kV jumpers H1832 & H1762 Ngaramus Hill Ruatoria
11692 | 20/06/2006 | 2006-06-20 | 2006 | 33 | 55 | 1815 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarm pole W1585 Scott St
11744 | 20/06/2006 | 2006-06-20 | 2006 | 171 | 57 | 9747 | C | TREE CONTACTS | Rejoin 11kV jumpers pole D383 Lavenham Rd
11745 | 20/06/2006 | 2006-06-20 | 2006 | 401 | 74 | 18982 | C | ADVERSE WEATHER | Atempt Replace pole F1870 Whakarau Rd
11746 | 20/06/2006 | 2006-06-20 | 2006 | 156 | 29 | 4524 | C | TREE CONTACTS | Repair 11kV lines E2903 Ngakaroa Rd
11747 | 20/06/2006 | 2006-06-20 | 2006 | 226 | 10 | 2260 | C | ADVERSE WEATHER | Repair 11kV lines D325 end Lake Rd Patutahi
11748 | 21/06/2006 | 2006-06-21 | 2006 | 155 | 77 | 4387 | C | ADVERSE WEATHER | Replace 11kV pole G1437 Anaura Bay
11749 | 22/06/2006 | 2006-06-22 | 2006 | 278 | 42 | 11676 | C | DEFECTIVE EQUIPMENT | Replace 11kV cable to T/x A485 Ocean Beach Motel Wainui
11750 | 22/06/2006 | 2006-06-23 | 2006 | 410 | 141 | 13464 | C | ADVERSE WEATHER | Isolate 11kV lines at W1158 Kakariki poles & wires down
11751 | 22/06/2006 | 2006-06-22 | 2006 | 66 | 103 | 3318 | C | ADVERSE WEATHER | Isolate 11kV lines between W1024 to W1040 Putere
11752 | 22/06/2006 | 2006-06-22 | 2006 | 215 | 32 | 6880 | B | PLANNED SHUTDOWN | Replace 11kV pole C2244 Makaraka
11753 | 23/06/2006 | 2006-06-24 | 2006 | 551 | 180 | 99180 | C | ADVERSE WEATHER | Isolate 11kV at links W1115 Waikaremoana
11754 | 23/06/2006 | 2006-06-23 | 2006 | 349 | 211 | 71164 | C | ADVERSE WEATHER | Patrol 11kV lines and reclose W820 at Oraka
11755 | 23/06/2006 | 2006-06-23 | 2006 | 676 | 129 | 42084 | C | TREE CONTACTS | Temp repair 11kV at pole J2411 SH35 Te Araroa
11756 | 23/06/2006 | 2006-06-23 | 2006 | 254 | 39 | 9906 | C | TREE CONTACTS | Isolate 11kV lines for tree cutting J2019 Tapauwaeroa
11757 | 23/06/2006 | 2006-06-23 | 2006 | 307 | 131 | 24413 | C | ADVERSE WEATHER | Repair 11kV lines between H1471 & H1472 Makarika
11758 | 23/06/2006 | 2006-06-23 | 2006 | 557 | 90 | 5840 | C | ADVERSE WEATHER | Repair 11kV lines between H146 & H154 Tuakau Rd
11768 | 25/06/2006 | 2006-06-26 | 2006 | 1921 | 12 | 23052 | C | ADVERSE WEATHER | Replace 11kV poles & conductors Woodlands
11769 | 25/06/2006 | 2006-07-03 | 2006 | 11465 | 5 | 57325 | C | ADVERSE WEATHER | Replace 11kV poles & conductors Willow Flat
11759 | 26/06/2006 | 2006-06-26 | 2006 | 74 | 16 | 1184 | C | ADVERSE WEATHER | Replace 2 11kV poles Opou Stn Papatu Rd
11763 | 26/06/2006 | 2006-06-26 | 2006 | 60 | 15 | 900 | C | TREE CONTACTS | Repair 11kV at T/x H328 Waipiro Bay
11766 | 26/06/2006 | 2006-07-02 | 2006 | 8192 | 10 | 81920 | C | ADVERSE WEATHER | Replace 11kV poles & conductors Mangone
11767 | 26/06/2006 | 2006-06-30 | 2006 | 5295 | 25 | 132375 | C | ADVERSE WEATHER | Replace 11kV poles & Conductor Otoi
11760 | 27/06/2006 | 2006-06-27 | 2006 | 148 | 49 | 7252 | C | ADVERSE WEATHER | Repair 11kV lines between J37 to J240 SH35 Tikitiki
11761 | 27/06/2006 | 2006-06-27 | 2006 | 261 | 53 | 13833 | C | ADVERSE WEATHER | Rejoin jumpers at H1465 & H1473 SH35 Makarika
11762 | 28/06/2006 | 2006-06-28 | 2006 | 87 | 30 | 2610 | C | ADVERSE WEATHER | Reconnect 11kV jumpers at pole F1875 Whakarau Rd
11764 | 29/06/2006 | 2006-07-05 | 2006 | 8192 | 18 | 147456 | C | ADVERSE WEATHER | Replace 11kV poles & repair conductors Maungataniwha
11765 | 29/06/2006 | 2006-07-07 | 2006 | 11465 | 5 | 57325 | C | ADVERSE WEATHER | Replace 11kV poles repair lines Maungataniwha
11775 | 05/07/2006 | 2006-07-05 | 2006 | 180 | 104 | 18720 | C | ADVERSE WEATHER | Repair 11kV lines at T/x J344 Hicks Bay
11776 | 05/07/2006 | 2006-07-05 | 2006 | 95 | 33 | 3135 | C | ADVERSE WEATHER | Replace 11kV pole D3622 Ruakaka Rd
11771 | 06/07/2006 | 2006-07-06 | 2006 | 55 | 21 | 1155 | B | PLANNED SHUTDOWN | Replace 11kV pole A2608 Monks Rd Waimata
11774 | 07/07/2006 | 2006-07-08 | 2006 | 605 | 188 | 83902 | C | FOREIGN INTERFERENCE | Reclose CB F410 Kanakanaia at Puha Sub Heron hit Line
11772 | 10/07/2006 | 2006-07-11 | 2006 | 842 | 197 | 19581 | C | FOREIGN INTERFERENCE | Replace 11kV pole C5310 in Bushmere Rd Hit by Car
11773 | 10/07/2006 | 2006-07-10 | 2006 | 31 | 642 | 19902 | C | FOREIGN INTERFERENCE | Replace 50kV pole B5252 Crn Kahuitia St & Carnarvon St Hit by Car
11770 | 14/07/2006 | 2006-07-14 | 2006 | 34 | 101 | 3953 | C | UNKNOWN | Reclose CB J525 Awatere at Te Araroa Sub cause unknown
11778 | 17/07/2006 | 2006-07-18 | 2006 | 148 | 84 | 8486 | C | DEFECTIVE EQUIPMENT | Replace burnt X Arm on ABS pole H123 Mata Rd
11780 | 18/07/2006 | 2006-07-18 | 2006 | 219 | 93 | 5570 | C | DEFECTIVE EQUIPMENT | Replace burnt 11kV pole D3573 Ruakaka Rd Tiniroto
11781 | 19/07/2006 | 2006-07-19 | 2006 | 85 | 440 | 23816 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable Pothead at T/x B208 Kingsley St
11782 | 19/07/2006 | 2006-07-19 | 2006 | 458 | 210 | 24801 | C | ADVERSE WEATHER | Repair 11kV lines at pole W7678 Mahia
11779 | 20/07/2006 | 2006-07-20 | 2006 | 170 | 62 | 10540 | B | PLANNED SHUTDOWN | Replace 2 11kV poles E1782 & E1783 SH2 Te Karaka
11783 | 20/07/2006 | 2006-07-20 | 2006 | 137 | 54 | 7398 | C | FOREIGN INTERFERENCE | Replace 11kV pole C5026 SH2 Makaraka hit by Car
11785 | 21/07/2006 | 2006-07-21 | 2006 | 76 | 256 | 15688 | C | ADVERSE WEATHER | Repair 11kV lines at pole W8717 Nuhaka
11786 | 21/07/2006 | 2006-07-21 | 2006 | 61 | 27 | 1647 | C | DEFECTIVE EQUIPMENT | Replace 11kV Xarm on pole A3986 Wharekiri Rd
11788 | 21/07/2006 | 2006-07-21 | 2006 | 326 | 14 | 4564 | C | ADVERSE WEATHER | Repair 11kV lines at T/x W382 Hereheretau Rd
11789 | 24/07/2006 | 2006-07-24 | 2006 | 241 | 28 | 6748 | B | PLANNED SHUTDOWN | Replace 11kV pole D1443 Bushy Knoll Rd
11790 | 24/07/2006 | 2006-07-24 | 2006 | 312 | 16 | 4424 | B | PLANNED SHUTDOWN | Replace 11kV poles Motu Rd
11791 | 26/07/2006 | 2006-07-26 | 2006 | 205 | 16 | 3280 | B | PLANNED SHUTDOWN | Replace 2 11kV poles in Opou Stn Papatu Rd
11792 | 27/07/2006 | 2006-07-27 | 2006 | 136 | 316 | 42976 | C | FOREIGN INTERFERENCE | Replace 11kV pole J1311 Main Rd Ruatoria hit by Car
11793 | 31/07/2006 | 2006-07-31 | 2006 | 241 | 94 | 17951 | C | DEFECTIVE EQUIPMENT | Repair 11kV at pole J3363 Kopupounamu Te Araroa
11799 | 01/08/2006 | 2006-08-01 | 2006 | 353 | 16 | 5048 | B | PLANNED SHUTDOWN | Replace 5 11kV poles Motu Rd Matawai
11796 | 04/08/2006 | 2006-08-04 | 2006 | 87 | 154 | 12573 | C | FOREIGN INTERFERENCE | Remove tractor mounted rammer from pole G1732 Tauwhareparae Rd
11794 | 07/08/2006 | 2006-08-07 | 2006 | 174 | 131 | 15921 | C | TREE CONTACTS | Repair 11kV F1875 to F1876 in Whakarau Rd
11795 | 08/08/2006 | 2006-08-08 | 2006 | 556 | 448 | 98023 | C | TREE CONTACTS | Repair 11kV lines between F3004 to F3005 SH2 Otoko Hill
11803 | 10/08/2006 | 2006-08-10 | 2006 | 424 | 21 | 7035 | B | PLANNED SHUTDOWN | Replace 3 11kV poles Motu Rd Matawai
11797 | 11/08/2006 | 2006-08-11 | 2006 | 29 | 221 | 4464 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable termination at Oil Switch B1014 Customhouse St
11798 | 11/08/2006 | 2006-08-11 | 2006 | 120 | 7 | 840 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Ceasars Rd Ormond
11800 | 13/08/2006 | 2006-08-13 | 2006 | 8 | 1085 | 8680 | C | UNKNOWN | Reclose CB A475 Tamarau at Kaiti Sub cause unknown
11801 | 13/08/2006 | 2006-08-13 | 2006 | 382 | 323 | 53584 | C | FOREIGN INTERFERENCE | Repair 11kV lines between J818 and J819 SH35 Ruatoria
11802 | 15/08/2006 | 2006-08-15 | 2006 | 28 | 29 | 812 | B | PLANNED SHUTDOWN | Isolate 11kV lines for erecting new T/x H6623 SH 35 at Makarika
11804 | 16/08/2006 | 2006-08-16 | 2006 | 323 | 9 | 2907 | B | PLANNED SHUTDOWN | Replace 4 11kV poles at Motuhora & Motu Rds Matawai
11805 | 17/08/2006 | 2006-08-17 | 2006 | 43 | 14 | 602 | C | TREE CONTACTS | Remove tree in 11kV at T/x F174 SH2 Rakauroa
11806 | 17/08/2006 | 2006-08-17 | 2006 | 179 | 12 | 2148 | C | ADVERSE ENVIRONMENT | Straighten 11kV poles & cut trees in Slip Morere Hill
11807 | 18/08/2006 | 2006-08-18 | 2006 | 147 | 437 | 26091 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarms on pole F1746 Olivers Rd Whakarau End
11808 | 19/08/2006 | 2006-08-19 | 2006 | 202 | 1177 | 110291 | C | FOREIGN INTERFERENCE | Replace Xarm on pole B383 Lytton Rd Hit by Car
11809 | 23/08/2006 | 2006-08-23 | 2006 | 255 | 65 | 12579 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole A3666 Panikau Rd Whangara
11810 | 23/08/2006 | 2006-08-23 | 2006 | 26 | 8 | 208 | C | DEFECTIVE EQUIPMENT | Repair broken binder on pole F761 Makeratu Rd
11812 | 24/08/2006 | 2006-08-24 | 2006 | 2 | 63 | 126 | B | PLANNED SHUTDOWN | Liven new 11kv cable & SWGR B6533, B6534, B6535 at Palm Court
11814 | 25/08/2006 | 2006-08-25 | 2006 | 243 | 33 | 7899 | C | FOREIGN INTERFERENCE | 3x broken conductors at pole D1024 - ducks
11815 | 26/08/2006 | 2006-08-26 | 2006 | 749 | 94 | 10546 | C | DEFECTIVE EQUIPMENT | 2x private poles (E3011 & E30120 failed
11817 | 29/08/2006 | 2006-08-29 | 2006 | 257 | 140 | 34340 | B | PLANNED SHUTDOWN | install 2x SF6 switches & remove W817
11816 | 30/08/2006 | 2006-08-30 | 2006 | 20 | 1085 | 21700 | C | UNKNOWN | Unknown OC Trip
11818 | 30/08/2006 | 2006-08-30 | 2006 | 50 | 1310 | 64742 | C | UNKNOWN | OC trip cause unknow - line patrolled 31/08/06
11819 | 31/08/2006 | 2006-08-31 | 2006 | 255 | 119 | 26450 | B | PLANNED SHUTDOWN | 6x pole change G1732 - G1738
11825 | 03/09/2006 | 2006-09-03 | 2006 | 21 | 802 | 16842 | C | UNKNOWN | W808 trip unknown
11821 | 05/09/2006 | 2006-09-05 | 2006 | 142 | 11 | 1562 | B | PLANNED SHUTDOWN | replace 11kV poles
11822 | 05/09/2006 | 2006-09-05 | 2006 | 76 | 32 | 2432 | B | PLANNED SHUTDOWN | replace 11kv poles
11823 | 05/09/2006 | 2006-09-05 | 2006 | 169 | 253 | 12405 | C | FOREIGN INTERFERENCE | replace poles C2819 & C2820 hit by tractor
11824 | 05/09/2006 | 2006-09-05 | 2006 | 961 | 70 | 15944 | C | FOREIGN INTERFERENCE | 1x conductor between poles F2095 & F2094 shot
11820 | 07/09/2006 | 2006-09-07 | 2006 | 230 | 28 | 6440 | B | PLANNED SHUTDOWN | TX pole C3289 relocate away from slip
11826 | 07/09/2006 | 2006-09-08 | 2006 | 161 | 592 | 93752 | C | FOREIGN INTERFERENCE | 2x conductors down between poles W3629 - W3631 hit by birds
11828 | 08/09/2006 | 2006-09-09 | 2006 | 286 | 224 | 30800 | C | DEFECTIVE EQUIPMENT | 2x Conductors down Wharf Rd, J523 OC & EF trip
11830 | 11/09/2006 | 2006-09-11 | 2006 | 172 | 126 | 4720 | C | ADVERSE WEATHER | Replace washed out T/x pole J639 Horera Te Araroa
11829 | 12/09/2006 | 2006-09-12 | 2006 | 2 | 36 | 144 | B | PLANNED SHUTDOWN | Install and liven new Switchgear at Big Save Gladstone Rd
11831 | 12/09/2006 | 2006-09-12 | 2006 | 230 | 5 | 1150 | B | PLANNED SHUTDOWN | Replace 11kV Pole H632 Ihungia Rd
11832 | 14/09/2006 | 2006-09-14 | 2006 | 309 | 5 | 1545 | B | PLANNED SHUTDOWN | Replace 3 11kV poles and tree cutting in Te Hue Rd
11833 | 19/09/2006 | 2006-09-19 | 2006 | 160 | 67 | 10720 | B | PLANNED SHUTDOWN | Replace red tagged pole A2190 and Stub Sirrah St Wainui
11834 | 21/09/2006 | 2006-09-21 | 2006 | 60 | 68 | 4080 | B | PLANNED SHUTDOWN | Replace T/x A322 and Swichgear Harris St Wainui Rd Crn
11835 | 26/09/2006 | 2006-09-26 | 2006 | 25 | 29 | 1015 | B | PLANNED SHUTDOWN | Replace T/x B724 Shelly Rd
11836 | 26/09/2006 | 2006-09-26 | 2006 | 137 | 77 | 10549 | B | PLANNED SHUTDOWN | Replace poles & cut trees Frasertown Village
11837 | 27/09/2006 | 2006-09-27 | 2006 | 300 | 18 | 5400 | B | PLANNED SHUTDOWN | Replace 11kV pole E214 Whatatutu
11838 | 27/09/2006 | 2006-09-27 | 2006 | 5 | 120 | 600 | B | PLANNED SHUTDOWN | Check 11kV Switch gear at B808 B809 B810 Mc Lean St
11839 | 29/09/2006 | 2006-09-29 | 2006 | 138 | 94 | 12894 | C | FOREIGN INTERFERENCE | Digger broke 2x 11kv OH conductors at TX E172
11840 | 30/09/2006 | 2006-09-30 | 2006 | 7 | 67 | 469 | B | PLANNED SHUTDOWN | Connect Generator to T/x B870 Mill Rd
11841 | 30/09/2006 | 2006-09-30 | 2006 | 10 | 87 | 870 | B | PLANNED SHUTDOWN | Connect Generator to T/x B840 Wellington St
11842 | 02/10/2006 | 2006-10-02 | 2006 | 123 | 275 | 4015 | C | FOREIGN INTERFERENCE | Replace 11kV pole F1133 Hit by Car Matawai
11855 | 02/10/2006 | 2006-10-02 | 2006 | 8 | 29 | 377 | B | PLANNED SHUTDOWN | Install generator and check Oil level in Tx B966 Shell Cobden St
11843 | 04/10/2006 | 2006-10-04 | 2006 | 143 | 836 | 34585 | C | DEFECTIVE EQUIPMENT | Replace faulty ABB Switch Gear Mill Rd
11844 | 05/10/2006 | 2006-10-05 | 2006 | 83 | 168 | 6104 | C | DEFECTIVE EQUIPMENT | Replace broken Private 11kV pole E3716 Ormond Valley
11845 | 05/10/2006 | 2006-10-05 | 2006 | 53 | 6 | 318 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting River Rd Matawhero
11846 | 05/10/2006 | 2006-10-05 | 2006 | 146 | 42 | 6132 | B | PLANNED SHUTDOWN | Change & relocate 11kV poles Tiniroto Village
11847 | 05/10/2006 | 2006-10-05 | 2006 | 156 | 160 | 9484 | C | ADVERSE WEATHER | Repair 11kV lines between W8148 & W8149 Whakakihi
11849 | 07/10/2006 | 2006-10-07 | 2006 | 158 | 827 | 48976 | C | FOREIGN INTERFERENCE | Replace 11kV pole W3115 in Wairoa Township
11850 | 08/10/2006 | 2006-10-09 | 2006 | 140 | 179 | 9580 | C | FOREIGN INTERFERENCE | Replace 11kV pole H2364 Mangahauine Valley
11851 | 09/10/2006 | 2006-10-09 | 2006 | 284 | 4 | 1136 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W3500 at Raupunga
11852 | 09/10/2006 | 2006-10-09 | 2006 | 186 | 217 | 10437 | C | DEFECTIVE EQUIPMENT | Replace X arm on pole W9248 Mahia
11848 | 10/10/2006 | 2006-10-10 | 2006 | 10 | 26 | 260 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between W8148 & W8149 Whakakihi
11853 | 10/10/2006 | 2006-10-10 | 2006 | 47 | 621 | 25651 | C | DEFECTIVE EQUIPMENT | Replace 11kV T/x pole D425 SH2 W/ O Hika
11854 | 13/10/2006 | 2006-10-13 | 2006 | 87 | 27 | 2349 | B | PLANNED SHUTDOWN | Replace 11kV pole E710 Armstrong Rd
11856 | 15/10/2006 | 2006-10-15 | 2006 | 14 | 849 | 11886 | C | UNKNOWN | Reclose CB C95 Haisman Rd cause Unknown
11857 | 15/10/2006 | 2006-10-16 | 2006 | 1349 | 226 | 33742 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between W5104 to W5547 Woodlands
11858 | 17/10/2006 | 2006-10-17 | 2006 | 40 | 171 | 6252 | C | TREE CONTACTS | Repair 11kV lines at pole C1275 SH2 Manutuke
11859 | 18/10/2006 | 2006-10-18 | 2006 | 15 | 23 | 345 | C | DEFECTIVE EQUIPMENT | Replace floating insulator on pole W8725 at Nuhaka
11860 | 18/10/2006 | 2006-10-18 | 2006 | 45 | 14 | 630 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole A4592 in Glenroy Rd
11861 | 24/10/2006 | 2006-10-24 | 2006 | 36 | 52 | 1872 | C | DEFECTIVE EQUIPMENT | Replace 11kV jumper at T/x D497 Lavenham Rd
11862 | 24/10/2006 | 2006-10-24 | 2006 | 198 | 110 | 13772 | C | TREE CONTACTS | Repair 11kV lines at pole C156 Coops Rd Muriwai
11863 | 25/10/2006 | 2006-10-25 | 2006 | 81 | 33 | 2673 | C | DEFECTIVE EQUIPMENT | Temp repair 11kV H pole D3594 Ruakaka Rd
11864 | 27/10/2006 | 2006-10-27 | 2006 | 4 | 200 | 800 | C | HUMAN ELEMENT | Remove tree branch from 11kV pole C218 l Bushmere Rd
11865 | 29/10/2006 | 2006-10-29 | 2006 | 217 | 199 | 41023 | C | ADVERSE WEATHER | Reclose CB 24 at Tuai due to High Winds
11866 | 31/10/2006 | 2006-10-31 | 2006 | 640 | 65 | 21584 | C | TREE CONTACTS | Remove trees in 11kV at poles D3333 & D3450 Taumata Rd
11867 | 02/11/2006 | 2006-11-02 | 2006 | 170 | 13 | 2210 | C | FOREIGN INTERFERENCE | Isolate & remove Digger from 11kV Lines Mangaoporo Valley
11869 | 06/11/2006 | 2006-11-06 | 2006 | 7 | 539 | 3773 | C | UNKNOWN | Reclose CB22L at Patutahi Sub cause unknown
11870 | 07/11/2006 | 2006-11-07 | 2006 | 10 | 189 | 1890 | C | UNKNOWN | Reclose CB 410 Kanakanaia cause unknown
11871 | 07/11/2006 | 2006-11-07 | 2006 | 149 | 159 | 12338 | C | DEFECTIVE EQUIPMENT | Replace X arm on pole W8157 Nuhaka
11872 | 07/11/2006 | 2006-11-07 | 2006 | 18 | 202 | 3636 | C | DEFECTIVE EQUIPMENT | Close Oil switch C6231 to restore supply Faulty OCB Matawhero sub
11873 | 08/11/2006 | 2006-11-08 | 2006 | 116 | 17 | 1792 | C | ADVERSE WEATHER | Untwist 11kV lines beyond ABS D264 Bushy Knoll Rd
11874 | 08/11/2006 | 2006-11-08 | 2006 | 355 | 112 | 13552 | C | TREE CONTACTS | Repair 11kV lines at pole C2490 near Coops Rd Crn
11875 | 08/11/2006 | 2006-11-08 | 2006 | 60 | 40 | 2400 | C | FOREIGN INTERFERENCE | Replace 11kV pole W8695 near LDS Church Nuhaka
11876 | 08/11/2006 | 2006-11-08 | 2006 | 20 | 891 | 12624 | C | UNKNOWN | Reclose CB C95 at Makaraka Sub cause unknown
11877 | 08/11/2006 | 2006-11-08 | 2006 | 18 | 199 | 3582 | C | UNKNOWN | Reclose CB 24 at Tuai cause unknown
11878 | 08/11/2006 | 2006-11-08 | 2006 | 132 | 372 | 24189 | C | TREE CONTACTS | Remove branch from 11kV lines at pole H1829 Makarika
11879 | 08/11/2006 | 2006-11-08 | 2006 | 104 | 20 | 2080 | C | ADVERSE WEATHER | Repair 11kV lines at pole A3976 Wharekiri Rd Whangara
11880 | 08/11/2006 | 2006-11-08 | 2006 | 115 | 86 | 5367 | C | UNKNOWN | Reclose CB W999 at Pokopoko cause unknown
11881 | 09/11/2006 | 2006-11-09 | 2006 | 22 | 95 | 2090 | C | UNKNOWN | Reclose CB J525 Awatere Te Araroa Sub cause unknown
11882 | 09/11/2006 | 2006-11-09 | 2006 | 78 | 5 | 390 | C | FOREIGN INTERFERENCE | Change 11kV pole H4189 hit by truck Waitahia Rd
11883 | 13/11/2006 | 2006-11-13 | 2006 | 64 | 216 | 11666 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole E2076 SH2 Ormond
11884 | 14/11/2006 | 2006-11-14 | 2006 | 40 | 17 | 680 | C | ADVERSE WEATHER | Repair 11kv lines at pole W5082 Mangone
11885 | 18/11/2006 | 2006-11-18 | 2006 | 11 | 61 | 1586 | C | ADVERSE WEATHER | Reclose CB D141 at Rere Very Windy
11886 | 18/11/2006 | 2006-11-18 | 2006 | 28 | 65 | 1820 | C | TREE CONTACTS | Remove branch off 11kV Aerodrome Rd & Reclose CB B711 Chalmers Rd at Parkinson Sub
11887 | 18/11/2006 | 2006-11-18 | 2006 | 14 | 200 | 2800 | C | UNKNOWN | Reclose CB H353 at Kopuaroa cause unknown
11888 | 18/11/2006 | 2006-11-18 | 2006 | 14 | 815 | 21190 | C | ADVERSE WEATHER | Reclose CB 808 Blacks Pad cause unknown
11889 | 18/11/2006 | 2006-11-18 | 2006 | 11 | 1089 | 11979 | C | ADVERSE WEATHER | Reclose CB1 at Wairoa Sub cause unknown
11892 | 19/11/2006 | 2006-11-19 | 2006 | 51 | 167 | 8322 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable Kahutia St feeder at Carnarvon St Sub
11890 | 20/11/2006 | 2006-11-20 | 2006 | 25 | 38 | 950 | B | PLANNED SHUTDOWN | Cut jumpers at poles G4009 & G4023 Tolaga Bay North
11891 | 21/11/2006 | 2006-11-21 | 2006 | 26 | 38 | 988 | B | PLANNED SHUTDOWN | Change 11kV poles & rejoin jumpers Tolaga Bay North
11893 | 23/11/2006 | 2006-11-23 | 2006 | 60 | 78 | 4680 | B | PLANNED SHUTDOWN | Repair 11kV Xarm on pole G2080 Waimea Stn Tauwhareparae
11894 | 24/11/2006 | 2006-11-24 | 2006 | 54 | 25 | 1350 | B | PLANNED SHUTDOWN | Reconnect 11kV jumpers at poles H37 & H2336 Te Puia
11895 | 24/11/2006 | 2006-11-24 | 2006 | 243 | 181 | 22385 | C | ADVERSE WEATHER | Repair 11kV lines between poles W5357 & W5354 Kotemaori
11896 | 24/11/2006 | 2006-11-24 | 2006 | 134 | 35 | 4690 | B | PLANNED SHUTDOWN | Replace 11kV pole G1741 Arikihi Rd Tolaga Bay
11897 | 24/11/2006 | 2006-11-24 | 2006 | 20 | 35 | 700 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W9137 Kaiwatau Rd Mahia
11898 | 26/11/2006 | 2006-11-26 | 2006 | 114 | 350 | 19698 | C | TREE CONTACTS | Repair 11kV lines between F205 & F1219 Rakauroa Rd
11899 | 28/11/2006 | 2006-11-28 | 2006 | 53 | 140 | 5650 | C | FOREIGN INTERFERENCE | Repair 11kV at T/x D725 Bruntons Rd Patutahi ( Bird Strike)
11900 | 28/11/2006 | 2006-11-28 | 2006 | 23 | 265 | 6095 | C | DEFECTIVE EQUIPMENT | Replace 11kV fuse base on T/x F277 Whatatutu Rd
11901 | 29/11/2006 | 2006-11-29 | 2006 | 427 | 25 | 10675 | B | PLANNED SHUTDOWN | Reconductor 11kV between H3222 & H2337 SH35 Te Puia
11902 | 30/11/2006 | 2006-11-30 | 2006 | 75 | 74 | 5550 | C | ADVERSE WEATHER | Reclose CB W999 Pokopoko High Winds
11903 | 30/11/2006 | 2006-11-30 | 2006 | 203 | 56 | 9382 | C | ADVERSE WEATHER | Repair 11kV lines at pole F1400 Whakarau Rd
11904 | 30/11/2006 | 2006-11-30 | 2006 | 141 | 85 | 11985 | C | ADVERSE WEATHER | Replace 11kV pole E414 & repair 11kV lines Tarndale Rd
11905 | 30/11/2006 | 2006-11-30 | 2006 | 199 | 66 | 5430 | C | ADVERSE WEATHER | Repair 11kV lines between H1046 to H1047 Waitahaia Rd
11906 | 30/11/2006 | 2006-11-30 | 2006 | 125 | 16 | 2000 | C | ADVERSE WEATHER | Repair 11kVlines at pole E2162 Mangamaia Rd
11907 | 30/11/2006 | 2006-11-30 | 2006 | 204 | 144 | 14714 | C | ADVERSE WEATHER | Repair 11kV lines at pole D3836 Tiniroto Rd
11908 | 30/11/2006 | 2006-11-30 | 2006 | 66 | 319 | 20118 | C | TREE CONTACTS | Repair 11kV lines between poles J966 & J967 Waiomatini
11909 | 30/11/2006 | 2006-11-30 | 2006 | 240 | 246 | 56390 | C | ADVERSE WEATHER | Repair 11kV lines near T/x J331 Te Araroa
11918 | 01/12/2006 | 2006-12-01 | 2006 | 50 | 175 | 6150 | C | FOREIGN INTERFERENCE | Remove 400V lines from 11kV Whitiwhiti Hill Hit by Truck
11920 | 03/12/2006 | 2006-12-03 | 2006 | 282 | 264 | 27990 | C | FOREIGN INTERFERENCE | Replace 11kV pole W8355 SH2 Nuhaka
11916 | 05/12/2006 | 2006-12-05 | 2006 | 237 | 11 | 2607 | B | PLANNED SHUTDOWN | Change 11kV pole G1275 Parkinson St Tolaga Bay
11917 | 05/12/2006 | 2006-12-05 | 2006 | 615 | 146 | 23922 | C | ADVERSE WEATHER | Repair 11kV lines between poles W967 to W1052 Hereheretau Rd
11915 | 06/12/2006 | 2006-12-06 | 2006 | 67 | 60 | 1160 | C | TREE CONTACTS | Remove branch from 11kV lines near pole F1018 Opp Motu School
11921 | 06/12/2006 | 2006-12-06 | 2006 | 64 | 86 | 18109 | C | TREE CONTACTS | Repair 11kV lines at pole W6426 Te Kumi Rd
11913 | 10/12/2006 | 2006-12-10 | 2006 | 116 | 39 | 3517 | C | TREE CONTACTS | Repair 11kV lines at pole J186 Tapuwaroa Valley Rd
11914 | 11/12/2006 | 2006-12-11 | 2006 | 203 | 155 | 6888 | C | TREE CONTACTS | Repair 11kV lines between poles W5588 to W5589 Kahuhgungu
11910 | 12/12/2006 | 2006-12-12 | 2006 | 529 | 45 | 17946 | B | PLANNED SHUTDOWN | Replace 13 - 11kV poles with 13 - 50kV poles Awapuni Rd
11911 | 12/12/2006 | 2006-12-12 | 2006 | 2 | 24 | 48 | B | PLANNED SHUTDOWN | Connect generator to replace 11kV pole W9898 Queen St
11912 | 12/12/2006 | 2006-12-12 | 2006 | 105 | 25 | 2625 | B | PLANNED SHUTDOWN | Remove OH T/x & Liven new 200kvA T/x Mahunga Beach
11922 | 16/12/2006 | 2006-12-16 | 2006 | 109 | 769 | 57212 | C | UNKNOWN | Reclose CB J3 at Ruatoria Sub cause Unknown
11919 | 18/12/2006 | 2006-12-18 | 2006 | 78 | 343 | 20638 | C | TREE CONTACTS | Remove tree branch from 11kV lines at pole J795 Waiomatatini
11923 | 19/12/2006 | 2006-12-19 | 2006 | 17 | 101 | 2929 | B | PLANNED SHUTDOWN | Replace 11kV pole & change T/x E159 Kanakanaia
11924 | 20/12/2006 | 2006-12-20 | 2006 | 312 | 140 | 16415 | C | TREE CONTACTS | Repair 11kV lines at pole W7536 Te Reinga
11925 | 21/12/2006 | 2006-12-21 | 2006 | 90 | 144 | 7200 | C | TREE CONTACTS | Reclose CB W816 Trees near Te Reinga
11926 | 21/12/2006 | 2006-12-21 | 2006 | 75 | 96 | 4826 | C | TREE CONTACTS | Isolate 11kV Cut jumpers at pole E1318 Waimata Valley(Trees)
11927 | 23/12/2006 | 2006-12-23 | 2006 | 42 | 2466 | 103572 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause Unknown
11928 | 24/12/2006 | 2006-12-24 | 2006 | 49 | 1244 | 49931 | C | UNKNOWN | Reclose CB H14 at Tokomaru Bay Sub cause unknown
11929 | 28/12/2006 | 2006-12-28 | 2006 | 28 | 19 | 532 | C | DEFECTIVE EQUIPMENT | broken 11kV jumper at W805
11930 | 02/01/2007 | 2007-01-02 | 2006 | 122 | 4141 | 57305 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable at pole A6467 De latour Rd
11932 | 04/01/2007 | 2007-01-04 | 2006 | 34 | 2466 | 55405 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
11931 | 05/01/2007 | 2007-01-05 | 2006 | 11 | 475 | 4496 | C | UNKNOWN | Reclose CB J526 Inc 1 Te Araroa Sub cause unknown
11934 | 10/01/2007 | 2007-01-10 | 2006 | 22 | 65 | 1430 | C | UNKNOWN | Reclose CB A158 Panikau Rd cause unknown
11933 | 11/01/2007 | 2007-01-11 | 2006 | 106 | 131 | 8966 | C | TREE CONTACTS | Repair 11kV lines at pole H1830 Reedys Hill Ruatoria
11942 | 13/01/2007 | 2007-01-13 | 2006 | 485 | 19 | 9215 | C | DEFECTIVE EQUIPMENT | Replace 11kV Xarm on pole E2373 Bond Rd Ormond
11935 | 14/01/2007 | 2007-01-14 | 2006 | 300 | 76 | 13554 | C | DEFECTIVE EQUIPMENT | Replace 11kV Insulator on pole A4017 Wharekiri Rd Panikau
11941 | 15/01/2007 | 2007-01-15 | 2006 | 140 | 305 | 9350 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable Grey St
11943 | 15/01/2007 | 2007-01-15 | 2006 | 98 | 18 | 1764 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole E1008 at Terrace Stn Kanakanaia
11940 | 20/01/2007 | 2007-01-20 | 2006 | 48 | 409 | 4203 | C | FOREIGN INTERFERENCE | Replace 11kV pole C354 hit by Trailer Muriwai
11936 | 22/01/2007 | 2007-01-22 | 2006 | 505 | 33 | 16352 | B | PLANNED SHUTDOWN | Replace 11kV poles with 50kV Awapuni Rd
11937 | 22/01/2007 | 2007-01-22 | 2006 | 33 | 111 | 3663 | C | FOREIGN INTERFERENCE | Replace 11kV pole C4862 SH2 Muriwai Hit by Car
11939 | 23/01/2007 | 2007-01-23 | 2006 | 56 | 9 | 504 | C | DEFECTIVE EQUIPMENT | Repair 11kV Cable at Pole C3976 Dunstan Rd
11938 | 26/01/2007 | 2007-01-26 | 2006 | 92 | 156 | 5574 | C | TREE CONTACTS | Repair 11kV lines at pole E1144 Kanakanaia Rd
11944 | 31/01/2007 | 2007-01-31 | 2006 | 228 | 181 | 23825 | C | FOREIGN INTERFERENCE | Repair 11kV lines between Poles W8346 & W8347 Morere
11945 | 31/01/2007 | 2007-01-31 | 2006 | 497 | 17 | 8143 | B | PLANNED SHUTDOWN | Install draw wire for pulling new 50kV conductor Awapuni Rd
11946 | 02/02/2007 | 2007-02-02 | 2006 | 429 | 17 | 7293 | B | PLANNED SHUTDOWN | Run new 50kV Conductor between pole 38 to 53 Awapuni Rd
11947 | 05/02/2007 | 2007-02-05 | 2006 | 20 | 201 | 4020 | C | UNKNOWN | Reclose CB G329 Rototahi at Tolaga Bay Sub cause unknown
11948 | 07/02/2007 | 2007-02-07 | 2006 | 30 | 54 | 2160 | B | PLANNED SHUTDOWN | Replace T/x B316 & connect new 95mm 11kV cable Awapuni Rd
11949 | 12/02/2007 | 2007-02-12 | 2006 | 107 | 4 | 428 | B | PLANNED SHUTDOWN | Replace 11kV pole J1304 Waiomatatini Ruatoria
11952 | 12/02/2007 | 2007-02-12 | 2006 | 540 | 50 | 24340 | B | PLANNED SHUTDOWN | Run new 50kV Conductor Matawhero to Parkinson St Sub Awapuni Rd
11950 | 15/02/2007 | 2007-02-15 | 2006 | 437 | 85 | 9739 | C | FOREIGN INTERFERENCE | Replace 11kV insulator on pole W3679 Waihi Rd
11951 | 16/02/2007 | 2007-02-16 | 2006 | 172 | 44 | 7568 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Ruakaka Rd Tiniroto
11953 | 17/02/2007 | 2007-02-18 | 2006 | 790 | 16 | 12640 | C | DEFECTIVE EQUIPMENT | Replace Burnt 11kV pole E958 Waitangi Rd Kanakanaia
11954 | 19/02/2007 | 2007-02-19 | 2006 | 330 | 150 | 20394 | C | DEFECTIVE EQUIPMENT | Replace 11kV Xarm on pole W692 Hereheretau Rd Nuhaka
11955 | 19/02/2007 | 2007-02-19 | 2006 | 432 | 10 | 4320 | B | PLANNED SHUTDOWN | Run new 11kVconductor Awapuni Rd
11956 | 21/02/2007 | 2007-02-21 | 2006 | 215 | 234 | 45126 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between Poles W506 & W8977 Mahia
11957 | 28/02/2007 | 2007-02-28 | 2006 | 180 | 6 | 1080 | C | FOREIGN INTERFERENCE | Replace 11kV Pole D1323 Tiniroto Rd outside Patutahi Sub
11958 | 05/03/2007 | 2007-03-05 | 2006 | 34 | 23 | 782 | B | PLANNED SHUTDOWN | Reconnect 11kV jumpers at pole E1318 Waimata Valley
11959 | 05/03/2007 | 2007-03-05 | 2006 | 240 | 18 | 4320 | B | PLANNED SHUTDOWN | Rebuild 11kV line between Tuai to Home Bay Waikaremoana
11985 | 05/03/2007 | 2007-03-05 | 2006 | 192 | 49 | 4874 | B | PLANNED SHUTDOWN | Replace T/x B531 & Sw/Gr Rainbow Fast Foods Grey St
11960 | 07/03/2007 | 2007-03-07 | 2006 | 54 | 49 | 2646 | C | DEFECTIVE EQUIPMENT | Replace 11kV insulator on pole W7132 Ruatanawha Rd
11961 | 09/03/2007 | 2007-03-09 | 2006 | 16 | 189 | 3024 | C | UNKNOWN | Reclose CB 410 Kanakanaia at Puha Sub cause unknown
11963 | 10/03/2007 | 2007-03-10 | 2006 | 21 | 5183 | 108843 | C | DEFECTIVE EQUIPMENT | Replace 50kV Xarm on pole A1159 in Riverside Rd
11964 | 13/03/2007 | 2007-03-13 | 2006 | 24 | 327 | 5122 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole F2282 Whakarau Rd
11965 | 13/03/2007 | 2007-03-13 | 2006 | 425 | 25 | 10625 | B | PLANNED SHUTDOWN | Reconductor 11kV lines Between poles C199 & C5156 SH2 Matawhero
11966 | 14/03/2007 | 2007-03-14 | 2006 | 155 | 33 | 5115 | C | DEFECTIVE EQUIPMENT | Temp prop 11kV pole E1102 Kanakanaia Rd
11967 | 14/03/2007 | 2007-03-14 | 2006 | 120 | 194 | 17649 | C | TREE CONTACTS | Repair 11kv lines at pole W5025 Raupunga
11968 | 14/03/2007 | 2007-03-14 | 2006 | 10 | 263 | 2262 | C | ADVERSE WEATHER | Repair 11kV lines between W965 to W137 Morere Hill
11969 | 14/03/2007 | 2007-03-14 | 2006 | 59 | 195 | 10938 | C | ADVERSE WEATHER | Reclose CB 24 at Tuai cause unknown Wind ?
11970 | 14/03/2007 | 2007-03-14 | 2006 | 186 | 10 | 1860 | C | ADVERSE WEATHER | Repair 11kV lines beyond A193 Panikau Rd
11971 | 14/03/2007 | 2007-03-14 | 2006 | 138 | 702 | 28246 | C | FOREIGN INTERFERENCE | Remove St light to allow clearance for 11kV lines opp Showgrounds
11972 | 15/03/2007 | 2007-03-15 | 2006 | 205 | 77 | 15785 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H2618 Beach Rd Tokomaru Bay
11973 | 15/03/2007 | 2007-03-15 | 2006 | 10 | 465 | 3622 | C | TREE CONTACTS | Remove tree from 50kV at pole J1832 Tikitiki
11975 | 15/03/2007 | 2007-03-15 | 2006 | 63 | 20 | 1260 | C | DEFECTIVE EQUIPMENT | Replace 11kV jumper on fuse C100 Paparatu Rd
11974 | 16/03/2007 | 2007-03-16 | 2006 | 11 | 5639 | 54157 | C | UNKNOWN | Reclose CB192 at Gisborne Sub Cause Unknown
11976 | 16/03/2007 | 2007-03-16 | 2006 | 32 | 17 | 544 | C | DEFECTIVE EQUIPMENT | Rejoin 11kV Jumpers on pole W5025 Otoi
11977 | 16/03/2007 | 2007-03-16 | 2006 | 195 | 147 | 12715 | B | PLANNED SHUTDOWN | Replace T/x W1569 & Switch Gear Lahore St
11978 | 16/03/2007 | 2007-03-16 | 2006 | 8 | 2466 | 19728 | C | UNKNOWN | Reclose CB A18 Goodwins Rd cause unknown
11979 | 16/03/2007 | 2007-03-16 | 2006 | 41 | 2455 | 74319 | C | DEFECTIVE EQUIPMENT | Replace 50kV pole A1049 near Glenroy Rd
11980 | 18/03/2007 | 2007-03-18 | 2006 | 90 | 165 | 9998 | C | TREE CONTACTS | Repair 11kv wire at H2040
11981 | 19/03/2007 | 2007-03-19 | 2006 | 122 | 21 | 2562 | C | TREE CONTACTS | Repair 11kV at pole J3748 East Cape Rd Horera
11982 | 19/03/2007 | 2007-03-19 | 2006 | 56 | 33 | 1848 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole E1102 Kanakanaia Rd
11983 | 19/03/2007 | 2007-03-19 | 2006 | 80 | 15 | 1200 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at pols A4109 & A6482 Kaiti Hill
11984 | 20/03/2007 | 2007-03-20 | 2006 | 176 | 24 | 4224 | B | PLANNED SHUTDOWN | Replace 11kV pole A3977 Wharekiri Rd
11987 | 25/03/2007 | 2007-03-25 | 2006 | 342 | 10 | 1710 | B | PLANNED SHUTDOWN | Replace 11kV poles near Olympic Pool Awapuni Rd
11986 | 26/03/2007 | 2007-03-26 | 2006 | 15 | 64 | 960 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W5330 Kotiemaori
11989 | 27/03/2007 | 2007-03-27 | 2006 | 31 | 33 | 1023 | B | PLANNED SHUTDOWN | Remove SW/GR B596, B597, B598 at Gear Meat Grey St
12087 | 27/03/2007 | 2007-03-27 | 2006 | 264 | 42 | 11088 | B | PLANNED SHUTDOWN | W826 to W1039
11988 | 28/03/2007 | 2007-03-28 | 2006 | 23 | 40 | 920 | C | FOREIGN INTERFERENCE | Isolate 11kVlines to Upright Petrol Tanker Nuhaka
11990 | 29/03/2007 | 2007-03-29 | 2006 | 33 | 33 | 1089 | B | PLANNED SHUTDOWN | Remove SW/GR at Gear Meat Grey St
12088 | 29/03/2007 | 2007-03-29 | 2006 | 588 | 62 | 0 | B | PLANNED SHUTDOWN | W1008 to W1204
11991 | 30/03/2007 | 2007-03-30 | 2006 | 93 | 228 | 14094 | C | DEFECTIVE EQUIPMENT | Temp Repair T/x Structure W729 Tuahura
11992 | 31/03/2007 | 2007-03-31 | 2006 | 155 | 14 | 2170 | C | DEFECTIVE EQUIPMENT | Temp prop T/x Pole H115 Mata Rd
11993 | 02/04/2007 | 2007-04-02 | 2007 | 210 | 14 | 2940 | C | DEFECTIVE EQUIPMENT | Replace T/x pole H115 Jeffards Mata Rd
11994 | 10/04/2007 | 2007-04-10 | 2007 | 43 | 14 | 602 | B | PLANNED SHUTDOWN | Replace 10 11kV poles Opou Stn Papatu Rd Manutuke
11995 | 10/04/2007 | 2007-04-10 | 2007 | 211 | 15 | 3165 | B | PLANNED SHUTDOWN | Change Transformer E13 Waimata Valley
11996 | 11/04/2007 | 2007-04-11 | 2007 | 107 | 29 | 3103 | C | DEFECTIVE EQUIPMENT | Replace fuse switch B477 Reads Quay Sub
11997 | 11/04/2007 | 2007-04-11 | 2007 | 178 | 12 | 2136 | B | PLANNED SHUTDOWN | Install new transformer on pole D1142 Parakanapa Rd
11998 | 13/04/2007 | 2007-04-13 | 2007 | 50 | 206 | 7977 | C | TREE CONTACTS | Remove tree branch from 11kV lines near T/x E91 SH2 Te Karaka
11999 | 13/04/2007 | 2007-04-13 | 2007 | 34 | 24 | 816 | C | TREE CONTACTS | Replace burnt out fuse base on T/x E91 SH2 Te Karaka
12000 | 13/04/2007 | 2007-04-13 | 2007 | 102 | 130 | 13260 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarm on pole A455 Murphy Rd Wainui
12001 | 16/04/2007 | 2007-04-16 | 2007 | 120 | 3 | 360 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Mangatokeru Rd Tolaga Bay
12002 | 16/04/2007 | 2007-04-16 | 2007 | 223 | 15 | 3345 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Mangatuna Rd Tolaga Bay
12003 | 17/04/2007 | 2007-04-17 | 2007 | 87 | 173 | 15051 | C | UNKNOWN | Reclose CB 23 Tuai Cause unknown
12004 | 17/04/2007 | 2007-04-17 | 2007 | 4 | 128 | 512 | B | PLANNED SHUTDOWN | Connect 300mm cable on pole A6477 Crawford Rd
12005 | 17/04/2007 | 2007-04-17 | 2007 | 172 | 91 | 15652 | B | PLANNED SHUTDOWN | Connect 300mm cable on pole A3208 Ranfurly Rd
12006 | 17/04/2007 | 2007-04-17 | 2007 | 25 | 15 | 375 | B | PLANNED SHUTDOWN | Reconnect 11kV jumpers at pole A4109 Kaiti Hill Rd
12007 | 18/04/2007 | 2007-04-18 | 2007 | 44 | 206 | 2732 | C | DEFECTIVE EQUIPMENT | Replace burnt out 11kV fuse base at T/x G343 Bank St Tolaga Bay
12009 | 26/04/2007 | 2007-04-26 | 2007 | 25 | 1082 | 27050 | C | FOREIGN INTERFERENCE | Replace jumper on DD/O fuse B712 Wellington St
12011 | 01/05/2007 | 2007-05-01 | 2007 | 31 | 38 | 2470 | B | PLANNED SHUTDOWN | D/con & Recon 11kV jumpers poles H1832 & H1762 SH 35 Ruatoria
12012 | 01/05/2007 | 2007-05-01 | 2007 | 405 | 9 | 3645 | B | PLANNED SHUTDOWN | Replace 11kV pole H8137 SH35 Ruatoria
12013 | 01/05/2007 | 2007-05-01 | 2007 | 360 | 180 | 14312 | C | LIGHTNING | Repair 11kV lines at pole D668 Tahora
12014 | 01/05/2007 | 2007-05-01 | 2007 | 501 | 303 | 44733 | B | PLANNED SHUTDOWN | Relocate 11kV poles & T/x Mahia Est Mahia
12015 | 01/05/2007 | 2007-05-01 | 2007 | 400 | 109 | 24543 | B | PLANNED SHUTDOWN | Replace 11kV poles & Maintenance Mahia Est Mahia
12016 | 01/05/2007 | 2007-05-01 | 2007 | 58 | 18 | 1044 | B | PLANNED SHUTDOWN | Install 3 DDO fuses on pole D1892 Wharekopae Rd
12017 | 03/05/2007 | 2007-05-03 | 2007 | 234 | 8 | 1872 | B | PLANNED SHUTDOWN | Replace 11kV pole A22 in Darwin Rd
12018 | 03/05/2007 | 2007-05-03 | 2007 | 53 | 917 | 10588 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole A4337 in Goodwins Rd
12019 | 03/05/2007 | 2007-05-03 | 2007 | 58 | 8 | 464 | B | PLANNED SHUTDOWN | Erect new T/x on pole B3127 Valley Rd
12020 | 06/05/2007 | 2007-05-06 | 2007 | 21 | 94 | 1840 | C | UNKNOWN | Reclose CB E863 at Whatatutu cause unknown
12021 | 08/05/2007 | 2007-05-08 | 2007 | 355 | 18 | 6390 | B | PLANNED SHUTDOWN | Replace 5 - 11kV poles in Makeretu Rd
12022 | 09/05/2007 | 2007-05-09 | 2007 | 45 | 17 | 1462 | B | PLANNED SHUTDOWN | Cut 11kV jumpers on poles H2259 & H2405 Mangahauine Valley
12023 | 09/05/2007 | 2007-05-09 | 2007 | 49 | 5063 | 100389 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable in De Latour Rd
12024 | 15/05/2007 | 2007-05-15 | 2007 | 360 | 18 | 6480 | B | PLANNED SHUTDOWN | Replace 6 - 11kV poles Makeretu Rd
12025 | 15/05/2007 | 2007-05-16 | 2007 | 725 | 42 | 15364 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole A3922 Wharekiri Rd
12028 | 15/05/2007 | 2007-05-15 | 2007 | 37 | 90 | 3141 | C | FOREIGN INTERFERENCE | Change burnt out DDO fuse base pole E316 Whatatutu
12027 | 18/05/2007 | 2007-05-18 | 2007 | 285 | 924 | 124048 | C | FOREIGN INTERFERENCE | Replace 11kV pole F3222 hit by car Otoko
12026 | 19/05/2007 | 2007-05-19 | 2007 | 239 | 11 | 2627 | B | PLANNED SHUTDOWN | Replace 50kV pole A831 in Waihau Rd
12030 | 21/05/2007 | 2007-05-21 | 2007 | 65 | 12 | 2040 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole A3961 Wharekiri Rd
12029 | 23/05/2007 | 2007-05-23 | 2007 | 370 | 276 | 37424 | B | PLANNED SHUTDOWN | HV cable alterations & install New ABS on pole B4070 Aberdeen Rd
12031 | 26/05/2007 | 2007-05-26 | 2007 | 172 | 7 | 1204 | C | UNKNOWN | Replace 3 - Isolation fuses pole E129 Bruce Rd cause unknown
12032 | 28/05/2007 | 2007-05-28 | 2007 | 51 | 70 | 1458 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole W1433 Mahia
12034 | 28/05/2007 | 2007-05-28 | 2007 | 345 | 44 | 13805 | B | PLANNED SHUTDOWN | Replace 12 11kV poles Waiomoko Rd
12036 | 29/05/2007 | 2007-05-29 | 2007 | 4 | 3 | 12 | B | PLANNED SHUTDOWN | Connect & Reconnect Generator Gladstone Rd
12035 | 30/05/2007 | 2007-05-30 | 2007 | 29 | 2 | 58 | B | PLANNED SHUTDOWN | To Connect &Reconnect Generator Gladstone Rd
12033 | 31/05/2007 | 2007-05-31 | 2007 | 125 | 958 | 56825 | C | DEFECTIVE EQUIPMENT | Repair faulty Tapchanger at Te Araroa Sub
12069 | 01/06/2007 | 2007-06-01 | 2007 | 315 | 11 | 3465 | B | PLANNED SHUTDOWN | Replace 11kV poles Waiomoko Rd
12072 | 01/06/2007 | 2007-06-01 | 2007 | 114 | 16 | 1824 | B | PLANNED SHUTDOWN | Replace 11kV pole W8761 at Waikokopu
12071 | 02/06/2007 | 2007-06-02 | 2007 | 182 | 90 | 12470 | B | PLANNED SHUTDOWN | Connect 11kV cable B6550 in Herbert Rd
12037 | 05/06/2007 | 2007-06-05 | 2007 | 109 | 61 | 3983 | C | ADVERSE WEATHER | Repair 11kV lines at pole A3672 Panikau Rd
12070 | 05/06/2007 | 2007-06-05 | 2007 | 26 | 65 | 1690 | B | PLANNED SHUTDOWN | Install new SW/Gr B6507 in Stanley Rd
12073 | 05/06/2007 | 2007-06-05 | 2007 | 248 | 42 | 10416 | B | PLANNED SHUTDOWN | Replace 3 11kV poles near Pongaroa Stn Mahia
12038 | 06/06/2007 | 2007-06-06 | 2007 | 52 | 62 | 3224 | C | UNKNOWN | Check T/x B290 Carnarvon St found Ok
12039 | 06/06/2007 | 2007-06-06 | 2007 | 212 | 74 | 12188 | C | FOREIGN INTERFERENCE | Repair 11kV jumper at fuses D76 outside Ngatapa Sub Bird
12040 | 07/06/2007 | 2007-06-07 | 2007 | 19 | 1106 | 13819 | C | UNKNOWN | Reclose Inc 1 F411 at Puha Sub cause unknown
12074 | 07/06/2007 | 2007-06-07 | 2007 | 204 | 35 | 7140 | B | PLANNED SHUTDOWN | Replace 11kV pole W5481 Cricklewood Stn
12075 | 07/06/2007 | 2007-06-07 | 2007 | 315 | 30 | 9450 | B | PLANNED SHUTDOWN | Replace 11kV pole A168 in Panikau Rd
12076 | 08/06/2007 | 2007-06-08 | 2007 | 289 | 16 | 4488 | B | PLANNED SHUTDOWN | Replace 3 11kV poles in Panikau Rd
12041 | 09/06/2007 | 2007-06-06 | 2007 | 75 | 21 | 1575 | C | TREE CONTACTS | Repair 11kV lines between poles J3753 & J3754 Horoera Rd
12042 | 12/06/2007 | 2007-06-12 | 2007 | 43 | 1946 | 7062 | C | UNKNOWN | Reclose Inc 1 B715 at Parkinson St Sub cause unknown
12043 | 13/06/2007 | 2007-06-13 | 2007 | 119 | 1154 | 27425 | C | DEFECTIVE EQUIPMENT | Replace DDO fuse base B739 in Wellington St
12077 | 13/06/2007 | 2007-06-13 | 2007 | 180 | 30 | 1904 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole A166 in Panikau Rd
12044 | 14/06/2007 | 2007-06-14 | 2007 | 18 | 143 | 2247 | C | UNKNOWN | Reclose CB W816 Ohuka cause unknown
12079 | 14/06/2007 | 2007-06-14 | 2007 | 160 | 58 | 9280 | B | PLANNED SHUTDOWN | Connect new 11kV line at pole C3233 in Cameron Rd
12078 | 15/06/2007 | 2007-06-15 | 2007 | 31 | 97 | 3007 | B | PLANNED SHUTDOWN | Replace T/x B636 in Gladstone Rd
12080 | 15/06/2007 | 2007-06-15 | 2007 | 10 | 24 | 240 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at pole A3930 in Wharekiri Rd
12045 | 16/06/2007 | 2007-06-16 | 2007 | 283 | 272 | 8374 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole W8381 Morere
12046 | 17/06/2007 | 2007-06-17 | 2007 | 92 | 4 | 368 | C | TREE CONTACTS | Remove tree from 11kV lines at pole A1937 Uttings Rd
12047 | 18/06/2007 | 2007-06-18 | 2007 | 16 | 141 | 2032 | C | UNKNOWN | Reclose CB W816 Ohuka cause unknown
12048 | 18/06/2007 | 2007-06-18 | 2007 | 150 | 26 | 3900 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable fault at T/x C670 Makaraka
12081 | 18/06/2007 | 2007-06-18 | 2007 | 295 | 38 | 9690 | B | PLANNED SHUTDOWN | Change 4 11kV poles in Wharekiri Rd
12049 | 20/06/2007 | 2007-06-20 | 2007 | 761 | 234 | 75422 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole W7639 East Coast Rd Mahia
12082 | 20/06/2007 | 2007-06-20 | 2007 | 27 | 24 | 648 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole A3930 in Wharekiri Rd
12050 | 21/06/2007 | 2007-06-21 | 2007 | 204 | 82 | 2399 | C | TREE CONTACTS | Repair 11kV lines between H649 & H650 Ihungia Rd
12051 | 21/06/2007 | 2007-06-21 | 2007 | 840 | 83 | 69720 | C | TREE CONTACTS | Remove tree form 11kV lines between F1982 & 1981 SH2 Matawai North
12083 | 21/06/2007 | 2007-06-21 | 2007 | 510 | 136 | 10235 | B | PLANNED SHUTDOWN | Replace 3 11kV poles in Mary St
12052 | 22/06/2007 | 2006-06-22 | 2007 | 81 | 2470 | 188608 | C | DEFECTIVE EQUIPMENT | Temp replace 50kV pole G2646 near Murphys Tolaga Bay
12053 | 23/06/2007 | 2007-06-23 | 2007 | 55 | 180 | 9765 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines on ABS pole W803 Mahia
12054 | 23/06/2007 | 2007-06-23 | 2007 | 541 | 82 | 11453 | C | TREE CONTACTS | Repair 11kV lines at pole H642 Ihungia Rd
12055 | 23/06/2007 | 2007-06-23 | 2007 | 290 | 105 | 7994 | C | TREE CONTACTS | Repair 11kV lines between poles E540 & E539 Tarndale Rd
12056 | 23/06/2007 | 2007-06-23 | 2007 | 716 | 141 | 81048 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole E748 & repair 11kV lines at pole E748 Whatatutu
12057 | 23/06/2007 | 2007-06-23 | 2007 | 39 | 28 | 1092 | C | DEFECTIVE EQUIPMENT | Temp prop up 11kV pole E3420 Whatatutu
12059 | 23/06/2007 | 2007-06-23 | 2007 | 77 | 28 | 2156 | C | DEFECTIVE EQUIPMENT | Temp prop 11kV pole E1269 Whatatutu
12060 | 23/06/2007 | 2007-06-23 | 2007 | 36 | 4 | 144 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on ABS pole D518 Ngatapa
12061 | 23/06/2007 | 2007-06-23 | 2007 | 165 | 383 | 63195 | C | ADVERSE WEATHER | Repair 11kV jumper at pole J2573 Te Araroa
12062 | 24/06/2007 | 2007-06-24 | 2007 | 12 | 202 | 2424 | C | UNKNOWN | Reclose CB G329 Rototahi cause unknown
12063 | 24/06/2007 | 2007-06-24 | 2007 | 120 | 1260 | 33176 | C | DEFECTIVE EQUIPMENT | Replace 50kV pole J1766 Ruatoria
12064 | 25/06/2007 | 2007-06-25 | 2007 | 170 | 412 | 12464 | C | FOREIGN INTERFERENCE | Untwist 11kV lines beyond W1006 Waitaha
12084 | 25/06/2007 | 2007-06-25 | 2007 | 283 | 9 | 2547 | B | PLANNED SHUTDOWN | Change T/x pole A169 in Stevens Rd
12065 | 26/06/2007 | 2007-06-26 | 2007 | 113 | 79 | 8927 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole W5866 Muramura
12066 | 26/06/2007 | 2007-06-26 | 2007 | 133 | 834 | 15518 | C | FOREIGN INTERFERENCE | Temp prop 11kV pole W1403 Wairoa CBD
12067 | 26/06/2007 | 2007-06-26 | 2007 | 313 | 922 | 13271 | C | FOREIGN INTERFERENCE | Replace 11kV pole C1516 Bck Ormond Rd
12068 | 27/06/2007 | 2007-06-27 | 2007 | 110 | 51 | 3066 | C | FOREIGN INTERFERENCE | Repair 11kV lines between poles A805 & A806 SH35 Rototahi
12085 | 27/06/2007 | 2007-06-27 | 2007 | 219 | 20 | 4380 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting in Bushmere Rd
12086 | 29/06/2007 | 2007-06-29 | 2007 | 160 | 7 | 1120 | B | PLANNED SHUTDOWN | Change T/x E196 in Whitmore Rd Ormond
12114 | 03/07/2007 | 2007-07-03 | 2007 | 328 | 32 | 10496 | B | PLANNED SHUTDOWN | Replace Poles D280 & D284
12100 | 04/07/2007 | 2007-07-04 | 2007 | 70 | 21 | 1470 | C | DEFECTIVE EQUIPMENT | Repair broken conductor H272
12101 | 05/07/2007 | 2007-07-05 | 2007 | 7 | 2470 | 13578 | C | UNKNOWN | Unknown OC Trip
12115 | 05/07/2007 | 2007-07-05 | 2007 | 9 | 4 | 36 | B | PLANNED SHUTDOWN | Change Tap Changer TX B1003
12102 | 06/07/2007 | 2007-07-07 | 2007 | 110 | 321 | 6422 | C | DEFECTIVE EQUIPMENT | Broken Conductor D4342 - D2869
12116 | 06/07/2007 | 2007-07-06 | 2007 | 197 | 18 | 3546 | B | PLANNED SHUTDOWN | Replace Poles G1006, G1087
12117 | 07/07/2007 | 2007-07-07 | 2007 | 270 | 18 | 4860 | B | PLANNED SHUTDOWN | Tree Cutting - Brown Road, Hika
12103 | 08/07/2007 | 2007-07-08 | 2007 | 140 | 190 | 14090 | C | UNKNOWN | Broken Conductor E618 - E619
12104 | 08/07/2007 | 2007-07-08 | 2007 | 110 | 24 | 2640 | C | FOREIGN INTERFERENCE | Car Hit Pole C3543
12118 | 08/07/2007 | 2007-07-08 | 2007 | 538 | 3 | 1614 | B | PLANNED SHUTDOWN | Isolate 11kV for Construction Work
12119 | 09/07/2007 | 2007-07-09 | 2007 | 215 | 3 | 645 | B | PLANNED SHUTDOWN | Tree Cutting TikiTiki Radio Site
12120 | 10/07/2007 | 2007-07-10 | 2007 | 162 | 50 | 8100 | B | PLANNED SHUTDOWN | Tree Cutting Waima
12105 | 11/07/2007 | 2007-07-11 | 2007 | 82 | 20 | 1640 | C | DEFECTIVE EQUIPMENT | Replace Rotten 11kV Pole C773
12121 | 12/07/2007 | 2007-07-12 | 2007 | 36 | 21 | 756 | B | PLANNED SHUTDOWN | Install New SF6 SW/GR B295
12106 | 13/07/2007 | 2007-07-13 | 2007 | 254 | 18 | 1835 | C | FOREIGN INTERFERENCE | Replace SW/GR B6544 - Hit by Car
12107 | 13/07/2007 | 2007-07-13 | 2007 | 165 | 43 | 7095 | C | DEFECTIVE EQUIPMENT | Broken Conductor J384
12113 | 14/07/2007 | 2007-07-14 | 2007 | 122 | 75 | 9150 | C | FOREIGN INTERFERENCE | Broken Conductors - W6089 - W6090 - Turkey
12108 | 16/07/2007 | 2007-07-16 | 2007 | 43 | 79 | 3397 | C | UNKNOWN | 11kV Fuses W1128 Blowen - Unknown
12109 | 17/07/2007 | 2007-07-17 | 2007 | 465 | 170 | 18550 | C | DEFECTIVE EQUIPMENT | Broken X-Arm A106
12110 | 18/07/2007 | 2007-07-18 | 2007 | 88 | 402 | 29502 | C | UNKNOWN | 2 Faults - Unknown
12122 | 19/07/2007 | 2007-07-19 | 2007 | 49 | 226 | 11074 | B | PLANNED SHUTDOWN | Replace 11kV Poles Sievwright Lane
12111 | 20/07/2007 | 2007-07-20 | 2007 | 64 | 201 | 12335 | C | UNKNOWN | Unknown - Suspect Trees
12123 | 23/07/2007 | 2007-07-23 | 2007 | 183 | 97 | 17751 | B | PLANNED SHUTDOWN | Lower 11kV for High Load
12124 | 25/07/2007 | 2007-07-25 | 2007 | 66 | 138 | 9108 | B | PLANNED SHUTDOWN | Install New GM SW/GR G372
12125 | 29/07/2007 | 2007-07-29 | 2007 | 237 | 3 | 711 | B | PLANNED SHUTDOWN | Isolate 11kV for Construction Work
12112 | 31/07/2007 | 2007-07-31 | 2007 | 185 | 79 | 14615 | C | TREE CONTACTS | Broken Conductor - Tree Felled Through Line W5870
12135 | 01/08/2007 | 2007-08-01 | 2007 | 241 | 237 | 45352 | C | DEFECTIVE EQUIPMENT | Replace X arm & insulators on pole C2689 in Harringtons Rd
12150 | 02/08/2007 | 2007-08-02 | 2007 | 289 | 7 | 2023 | B | PLANNED SHUTDOWN | Change 11kV pole F771 Makaretu Rd
12136 | 06/08/2007 | 2007-08-06 | 2007 | 66 | 16 | 1056 | C | DEFECTIVE EQUIPMENT | Rebind 11kV wire on pole E2156 Mangamaia Rd
12137 | 06/08/2007 | 2007-08-06 | 2007 | 5 | 191 | 955 | C | UNKNOWN | Reclose CB F410 Kanakanaia cause unknown
12151 | 06/08/2007 | 2007-08-06 | 2007 | 147 | 349 | 44491 | B | PLANNED SHUTDOWN | Replace 11kV Xarm on pole W6189 Raupunga
12152 | 07/08/2007 | 2007-08-07 | 2007 | 33 | 12 | 396 | B | PLANNED SHUTDOWN | Replace T/x B370 in Lowe St
12153 | 07/08/2007 | 2007-08-07 | 2007 | 300 | 38 | 11400 | B | PLANNED SHUTDOWN | Replace 11kV poles D166 & D1368 Tiniroto Rd
12138 | 08/08/2007 | 2007-08-08 | 2007 | 14 | 667 | 9025 | C | UNKNOWN | Reclose CB A612 at Port Sub cause unknown
12139 | 13/08/2007 | 2007-08-13 | 2007 | 213 | 26 | 5538 | C | DEFECTIVE EQUIPMENT | Restrain 11kVlines between F621 & f622 Rakauroa Rd
12140 | 14/08/2007 | 2007-08-14 | 2007 | 28 | 92 | 1173 | C | DEFECTIVE EQUIPMENT | Replace 11kV wire onto pole A3984 Wharekiri Rd
12154 | 15/08/2007 | 2007-08-15 | 2007 | 53 | 92 | 8132 | B | PLANNED SHUTDOWN | Remove 11kV lines in Roberts Rd
12141 | 17/08/2007 | 2007-08-17 | 2007 | 144 | 273 | 17394 | C | FOREIGN INTERFERENCE | Repair 11kV lines between poles W6559 & W6658 Mangapoikie Rd
12155 | 20/08/2007 | 2007-08-20 | 2007 | 246 | 22 | 5412 | B | PLANNED SHUTDOWN | Replace 11kV pole A805 SH35 Rototahi
12142 | 23/08/2007 | 2007-08-23 | 2007 | 33 | 47 | 1551 | C | DEFECTIVE EQUIPMENT | Replace shackle on pole H1824 Makarika Rd
12143 | 23/08/2007 | 2007-08-23 | 2007 | 97 | 201 | 19497 | C | DEFECTIVE EQUIPMENT | Replace faulty ABS W989 at Tuai
12156 | 23/08/2007 | 2007-08-23 | 2007 | 217 | 165 | 35805 | B | PLANNED SHUTDOWN | Replace 5 11kV poles Tuai / Kokako / Onepoto
12144 | 24/08/2007 | 2007-08-24 | 2007 | 264 | 3 | 792 | C | TREE CONTACTS | Isolate 11kV lines for tree cutting Armstrong Rd
12145 | 27/08/2007 | 2007-08-27 | 2007 | 70 | 26 | 1820 | C | UNKNOWN | Repair 11kV lines at pole W8518 Hereheretau Rd
12146 | 28/08/2007 | 2007-08-28 | 2007 | 24 | 444 | 8863 | C | TREE CONTACTS | Remove trees in 11kV lines between poles F2562 & F2563 Hihiroroa Rd
12157 | 28/08/2007 | 2007-08-28 | 2007 | 79 | 136 | 7334 | B | PLANNED SHUTDOWN | Replace T/x A185 in Darwin Rd
12147 | 29/08/2007 | 2007-08-29 | 2007 | 48 | 9 | 432 | C | TREE CONTACTS | Restrain 11kV lines Hihiroroa Rd
12158 | 29/08/2007 | 2007-08-29 | 2007 | 104 | 10 | 1040 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting between D380 & D3026 Humphries Rd
12159 | 30/08/2007 | 2007-08-30 | 2007 | 349 | 14 | 4886 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting between D3075 & D341 Wharekopae Rd
12149 | 31/08/2007 | 2007-08-31 | 2007 | 300 | 50 | 4293 | C | TREE CONTACTS | Repair 11kV lines at pole D1016 at W/ O Kuri
12166 | 01/09/2007 | 2007-09-01 | 2007 | 157 | 7 | 1099 | C | DEFECTIVE EQUIPMENT | Temp prop 11kV pole W3923 Kaihunahuna
12167 | 03/09/2007 | 2007-09-03 | 2007 | 80 | 7 | 560 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W3923 at Kaihunahuna
12174 | 03/09/2007 | 2007-09-03 | 2007 | 6 | 53 | 318 | B | PLANNED SHUTDOWN | Replace T/x A191 in Alice St
12168 | 05/09/2007 | 2007-09-05 | 2007 | 250 | 71 | 9100 | C | TREE CONTACTS | Repair 11kV lines at pole D2707 Wharekopae Rd
12175 | 05/09/2007 | 2007-09-05 | 2007 | 10 | 3 | 30 | B | PLANNED SHUTDOWN | Install new fuse switch B6510 Peel St
12169 | 06/09/2007 | 2007-09-06 | 2007 | 475 | 743 | 69025 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole W6090 Mangapoikie Rd
12170 | 07/09/2007 | 2007-09-07 | 2007 | 172 | 18 | 3096 | C | DEFECTIVE EQUIPMENT | Replace faulty disc on pole D2934 Wharekopae Rd
12171 | 11/09/2007 | 2007-09-11 | 2007 | 228 | 94 | 1551 | C | TREE CONTACTS | Remove trees from 11kV lines between poles E192 to E1736 Arnstrong Rd Whatatutu
12176 | 11/09/2007 | 2007-09-11 | 2007 | 166 | 21 | 3486 | B | PLANNED SHUTDOWN | Replace 3 11kV poles Kiwi Valley Rd
12172 | 15/09/2007 | 2007-09-15 | 2007 | 47 | 1106 | 44469 | C | DEFECTIVE EQUIPMENT | Isolate faulty Bucholtz Relay & Reclose Inc 1 F411 at Puha Sub
12177 | 18/09/2007 | 2007-09-18 | 2007 | 50 | 4 | 200 | B | PLANNED SHUTDOWN | Change T/x C400 1964 Wharerata Rd Muriwai
12178 | 18/09/2007 | 2007-09-18 | 2007 | 50 | 4 | 348 | B | PLANNED SHUTDOWN | Change T/x B439 Corson Grain Awapuni Rd
12173 | 20/09/2007 | 2007-09-20 | 2007 | 177 | 75 | 13275 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole W6558 Magapoikie Valley
12179 | 20/09/2007 | 2007-09-20 | 2007 | 355 | 5 | 1775 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Riverside Rd
12181 | 27/09/2007 | 2007-09-27 | 2007 | 78 | 7 | 546 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting in Ceasars Rd Ormond
12183 | 02/10/2007 | 2007-10-02 | 2007 | 1040 | 115 | 98544 | C | TREE CONTACTS | Replace 11kV Xarm on pole J4475 Oweka Stn
12184 | 03/10/2007 | 2007-10-03 | 2007 | 56 | 5 | 280 | C | DEFECTIVE EQUIPMENT | Restrain 11kv lines at pole D3699 Bushy Knoll Rd
12232 | 03/10/2007 | 2007-10-03 | 2007 | 264 | 83 | 21912 | B | PLANNED SHUTDOWN | Replace 3 11kV poles Mary St
12186 | 04/10/2007 | 2007-10-04 | 2007 | 75 | 675 | 50625 | C | UNKNOWN | Reclose CB A612 Crawford Rd at Port Sub cause Unknown
12185 | 05/10/2007 | 2007-10-05 | 2007 | 1031 | 26 | 12646 | C | DEFECTIVE EQUIPMENT | Replace 11kV jumper on pole D262 Bushy Knoll Rd
12187 | 05/10/2007 | 2007-10-05 | 2007 | 72 | 26 | 1872 | C | DEFECTIVE EQUIPMENT | Rejoin 11kV jumper at pole D3679 Bushy Knoll Rd
12188 | 05/10/2007 | 2007-10-05 | 2007 | 125 | 8 | 1000 | C | ADVERSE WEATHER | Repair 11kV lines between W5831 & W5830 Te Kahu Rd
12189 | 05/10/2007 | 2007-10-05 | 2007 | 282 | 7 | 1974 | C | ADVERSE WEATHER | Repair 11kV lines between W6176 & W6178 Heremau Kiwi Valley
12190 | 05/10/2007 | 2007-10-05 | 2007 | 500 | 12 | 6000 | C | ADVERSE WEATHER | Repair 11kV lines at pole E688 Wairere Rd Whatatutu
12191 | 05/10/2007 | 2007-10-05 | 2007 | 754 | 106 | 44992 | C | TREE CONTACTS | Repair 11kV lines at pole H4121 Waitahia Rd
12192 | 05/10/2007 | 2007-10-05 | 2007 | 755 | 94 | 21993 | C | TREE CONTACTS | Repair 11kV Lines at pole E1581 Armstrong Rd
12193 | 05/10/2007 | 2007-10-05 | 2007 | 565 | 130 | 16993 | C | ADVERSE WEATHER | Repair 11kV lines between J2487 & J2486 East Cape
12194 | 05/10/2007 | 2007-10-05 | 2007 | 128 | 195 | 24681 | C | UNKNOWN | Reclose CB24 at Tuai cause Unknown
12195 | 05/10/2007 | 2007-10-05 | 2007 | 478 | 158 | 63499 | C | TREE CONTACTS | Repair 11kV lines at pole D5010 Wharekopae Rd Rere
12196 | 05/10/2007 | 2007-10-05 | 2007 | 332 | 412 | 45319 | C | ADVERSE WEATHER | Reclose CB W830 Very High Winds nothing found
12197 | 06/10/2007 | 2007-10-06 | 2007 | 48 | 18 | 864 | C | DEFECTIVE EQUIPMENT | Replace 11kV conductor on pole D2989 Rere Farm Settlement Rd
12198 | 07/10/2007 | 2007-10-07 | 2007 | 443 | 140 | 21952 | C | DEFECTIVE EQUIPMENT | Replace 2 11kV poles Strathblane Stn Busy Knoll Rd
12199 | 07/10/2007 | 2007-10-07 | 2007 | 29 | 3281 | 95149 | C | DEFECTIVE EQUIPMENT | Reset Bucholtz Relay & Reclose CB C 94 at Makaraka Sub
12200 | 08/10/2007 | 2007-10-08 | 2007 | 128 | 354 | 12231 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole A4109 Queens Drive
12201 | 09/10/2007 | 2007-10-09 | 2007 | 48 | 135 | 6480 | C | DEFECTIVE EQUIPMENT | Replace 11kV insulator on pole G1706 Tauwhareparae Rd
12233 | 09/10/2007 | 2007-10-09 | 2007 | 251 | 51 | 12801 | B | PLANNED SHUTDOWN | Replace T/x W1575 Apatu St
12234 | 10/10/2007 | 2007-10-10 | 2007 | 271 | 28 | 7588 | B | PLANNED SHUTDOWN | Replace T/x W1574 Apatu St
12235 | 10/10/2007 | 2007-10-10 | 2007 | 163 | 4 | 652 | B | PLANNED SHUTDOWN | Replace 3 11kV insulators and Stay wire at pole F2424 Marumoko Rd
12202 | 11/10/2007 | 2007-10-11 | 2007 | 193 | 201 | 38793 | C | DEFECTIVE EQUIPMENT | Repair 11kV ABS W980 at Ardkeen
12203 | 11/10/2007 | 2007-10-11 | 2007 | 503 | 444 | 49421 | C | TREE CONTACTS | Repair 11kV lines between F3052 to F3053 Otoko
12236 | 11/10/2007 | 2007-10-11 | 2007 | 146 | 41 | 5986 | B | PLANNED SHUTDOWN | Replace T/x W1573 Apatu St
12204 | 14/10/2007 | 2007-10-14 | 2007 | 107 | 407 | 3449 | C | ADVERSE WEATHER | Repair 11kV lines between poles A2406 to A2408 Sponge Bay Rd
12205 | 14/10/2007 | 2007-10-14 | 2007 | 156 | 54 | 8424 | C | DEFECTIVE EQUIPMENT | Replace X Arm on pole C258 SH2 opp Bloomfeild Rd
12206 | 14/10/2007 | 2007-10-14 | 2007 | 344 | 149 | 17748 | C | TREE CONTACTS | Repair 11kV at pole H324 Waipiro Bay
12207 | 14/10/2007 | 2007-10-14 | 2007 | 209 | 296 | 37264 | C | TREE CONTACTS | Repair 11kV lines at pole W8338 Morere
12208 | 14/10/2007 | 2007-10-14 | 2007 | 1058 | 13 | 5610 | C | TREE CONTACTS | Repair 11kV lines between J2704 to J2705 Mangaoporo
12209 | 14/10/2007 | 2007-10-14 | 2007 | 449 | 106 | 16994 | C | TREE CONTACTS | Repair 11kV lines at pole H635 Ihungia Rd
12210 | 15/10/2007 | 2007-10-15 | 2007 | 1260 | 18 | 22680 | C | DEFECTIVE EQUIPMENT | Repair 11kV conductor at pole F660 Rakauroa Rd
12211 | 15/10/2007 | 2005-10-15 | 2007 | 23 | 263 | 5959 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on T/x J173 Ngati Poru Radio Ruatoria
12237 | 15/10/2007 | 2007-10-15 | 2007 | 152 | 22 | 3344 | B | PLANNED SHUTDOWN | Remove T/x B6237 & Check Oil Switchs B6211 B6212 & B6210 Valley Rd
12212 | 16/10/2007 | 2007-10-16 | 2007 | 319 | 60 | 5717 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W4996 Mangone
12213 | 16/10/2007 | 2007-10-16 | 2007 | 38 | 32 | 1216 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole D3579 Ruakaka Rd
12214 | 17/10/2007 | 2007-10-17 | 2007 | 384 | 61 | 23352 | C | TREE CONTACTS | Repair 11kV lines between G213 to G2098 Tauwhareparae Rd
12215 | 17/10/2007 | 2007-10-17 | 2007 | 261 | 47 | 12267 | C | DEFECTIVE EQUIPMENT | Replace 11kV jumper at pole W4804 Ruapapa Rd
12216 | 17/10/2007 | 2007-10-17 | 2007 | 196 | 10 | 1960 | C | TREE CONTACTS | Repair 11kV lines at pole F2563 Hihioroa Rd
12217 | 17/10/2007 | 2007-10-17 | 2007 | 142 | 5961 | 209458 | C | DEFECTIVE EQUIPMENT | Replace 50kV pole A1126 Goodwins Rd
12218 | 17/10/2007 | 2007-10-17 | 2007 | 63 | 1446 | 45322 | C | ADVERSE WEATHER | Reclose Inc CB 25 at Patutahi Sub Cause unknown High Winds
12219 | 18/10/2007 | 2007-10-18 | 2007 | 162 | 570 | 59918 | C | UNKNOWN | Reclose CB C95 Haisman Rd Cause unknown High Winds
12238 | 18/10/2007 | 2007-10-18 | 2007 | 513 | 100 | 34650 | B | PLANNED SHUTDOWN | Replace T/x B653 in Domett St
12239 | 18/10/2007 | 2007-10-18 | 2007 | 27 | 268 | 7236 | B | PLANNED SHUTDOWN | To cut & rejoin 11kV jumpers at pole B4873 in Russell St
12220 | 19/10/2007 | 2007-10-19 | 2007 | 72 | 625 | 15048 | C | TREE CONTACTS | Repair 11kV lines pole W7112 Ruatanawha St
12221 | 19/10/2007 | 2007-10-19 | 2007 | 245 | 38 | 5398 | C | TREE CONTACTS | Remove tree in line at pole J776 Tapauwaeroa
12222 | 20/10/2007 | 2007-10-20 | 2007 | 169 | 164 | 6773 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole A663 at Whangara
12223 | 22/10/2007 | 2007-10-22 | 2007 | 17 | 783 | 12816 | C | UNKNOWN | Reclose CB W808 cause unknown High Winds
12224 | 22/10/2007 | 2007-10-22 | 2007 | 4 | 202 | 808 | C | UNKNOWN | Reclose Inc CB G329 at Tolaga Bay Sub cause unknown
12225 | 22/10/2007 | 2007-10-22 | 2007 | 13 | 118 | 1534 | C | UNKNOWN | Reclose CB 4859 at Muriwai Cause unknown High Winds
12226 | 23/10/2007 | 2007-10-23 | 2007 | 55 | 118 | 6490 | C | TREE CONTACTS | Remove branch from pole C370 Muriwai
12227 | 26/10/2007 | 2007-10-26 | 2007 | 140 | 60 | 3524 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole D2197 in Branson Rd
12228 | 27/10/2007 | 2007-10-27 | 2007 | 154 | 75 | 11550 | C | DEFECTIVE EQUIPMENT | Replace 11kV insulator on pole W6540 Mangapoike Rd
12229 | 28/10/2007 | 2007-10-28 | 2007 | 11 | 1446 | 15906 | C | UNKNOWN | Reclose Inc CB D678 Patutahi Sub cause unknown
12230 | 29/10/2007 | 2007-10-29 | 2007 | 153 | 118 | 15684 | C | TREE CONTACTS | Repair 11kV lines between H1926 to H1927 Waipiro Bay Rd
12240 | 01/11/2007 | 2007-11-01 | 2007 | 120 | 12 | 1440 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H546 Arero
12241 | 02/11/2007 | 2007-11-02 | 2007 | 279 | 138 | 6674 | C | UNKNOWN | Reclose CB W816 Ohuka cause unknown
12242 | 04/11/2007 | 2007-11-04 | 2007 | 185 | 68 | 12580 | C | DEFECTIVE EQUIPMENT | Replace LV panel at T/x B638 in Central St
12243 | 06/11/2007 | 2007-11-06 | 2007 | 35 | 1041 | 33025 | C | DEFECTIVE EQUIPMENT | Replace 33kV pole W3793 at Whakakihi
12244 | 07/11/2007 | 2007-11-07 | 2007 | 16 | 2470 | 35872 | C | UNKNOWN | Reclose 50kV CB A8 Goodwins Rd cause unknown
12245 | 09/11/2007 | 2007-11-09 | 2007 | 158 | 177 | 6095 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole G1803 Paramata Rd
12246 | 09/11/2007 | 2007-11-09 | 2007 | 52 | 42 | 2184 | C | FOREIGN INTERFERENCE | Repair 11kV jumper on pole G2863 Paramata Rd Tolaga Bay
12247 | 10/11/2007 | 2007-11-10 | 2007 | 201 | 1062 | 34902 | C | FOREIGN INTERFERENCE | Replace 11kV pole B2041 in Riverside Rd
12248 | 13/11/2007 | 2007-11-13 | 2007 | 36 | 106 | 3816 | C | UNKNOWN | Replace 11kV pole B2041 in Riverside Rd
12249 | 13/11/2007 | 2007-11-13 | 2007 | 156 | 5 | 780 | C | ADVERSE WEATHER | Repair 11kV binder on pole D3761 Bushy Knoll Rd
12257 | 13/11/2007 | 2007-11-13 | 2007 | 25 | 29 | 1015 | B | PLANNED SHUTDOWN | Change 50kV pole B1814 in Howarth St
12250 | 14/11/2007 | 2007-11-14 | 2007 | 384 | 56 | 17632 | C | DEFECTIVE EQUIPMENT | Replace 11kV disc on pole A3924 Wharekiri Rd
12251 | 14/11/2007 | 2007-11-14 | 2007 | 206 | 106 | 12528 | C | TREE CONTACTS | Repair 11kV lines at pole H797 Mata Rd
12252 | 14/11/2007 | 2007-11-14 | 2007 | 463 | 210 | 69015 | C | ADVERSE WEATHER | Repair 11kv lines at pole W9000 at Mahia
12253 | 21/11/2007 | 2007-11-21 | 2007 | 269 | 11 | 2959 | C | TREE CONTACTS | Remove tree in 11kV Waihau Beach Rd
12254 | 21/11/2007 | 2007-11-21 | 2007 | 275 | 47 | 3845 | C | TREE CONTACTS | Repair 11kV lines between D1701 to D1016 Tiniroto Rd
12258 | 21/11/2007 | 2007-11-21 | 2007 | 200 | 3 | 600 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Tiniroto Rd
12255 | 22/11/2007 | 2007-11-22 | 2007 | 245 | 20 | 4900 | C | HUMAN ELEMENT | Relocate 11kV pole H4196 Ihungia Rd due to Roadworks
12259 | 24/11/2007 | 2007-11-24 | 2007 | 240 | 40 | 9600 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Tiniroto Rd
12261 | 26/11/2007 | 2007-11-26 | 2007 | 7 | 21 | 147 | B | PLANNED SHUTDOWN | Isolate 11kV lines for high load SH35 Rototahi
12256 | 28/11/2007 | 2007-11-28 | 2007 | 88 | 712 | 32224 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole W4255 Frasertown
12285 | 01/12/2007 | 2007-12-01 | 2007 | 200 | 10 | 2000 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Hokoroa Rd Waimata
12262 | 03/12/2007 | 2007-12-03 | 2007 | 226 | 139 | 13864 | C | TREE CONTACTS | Repair 11kV lines at pole D3264 Bushy Knoll Rd
12263 | 06/12/2007 | 2007-12-06 | 2007 | 129 | 46 | 3594 | C | TREE CONTACTS | Remove tree from 11kV at pole D2456 Pehiri Rd
12264 | 06/12/2007 | 2007-12-06 | 2007 | 142 | 70 | 8500 | C | DEFECTIVE EQUIPMENT | Repair broken 11kV jumper at pole D70 Totangi Rd
12265 | 06/12/2007 | 2007-12-06 | 2007 | 117 | 645 | 56834 | C | UNKNOWN | Reclose CB C96 at Makaraka Sub cause unknown
12266 | 06/12/2007 | 2007-12-06 | 2007 | 430 | 178 | 60641 | C | DEFECTIVE EQUIPMENT | Replace insulator on pole D787 Taumata Rd
12267 | 07/12/2007 | 2007-12-07 | 2007 | 468 | 802 | 148390 | C | HUMAN ELEMENT | Repair 11kV cable hit by Directional Driller beyond W8897 Mahia
12268 | 07/12/2007 | 2007-12-07 | 2007 | 593 | 258 | 8803 | C | DEFECTIVE EQUIPMENT | Repair 11kV conductors at pole J3875 Hicks Bay Rd
12269 | 07/12/2007 | 2007-12-07 | 2007 | 246 | 129 | 5058 | C | TREE CONTACTS | Repair 11kV conductors between poles H4321 & H4322 Tokomaru Bay
12270 | 09/12/2007 | 2007-12-09 | 2007 | 34 | 191 | 6494 | C | UNKNOWN | Reclose CB F410 Puha Sub cause unknown
12286 | 12/12/2007 | 2007-12-12 | 2007 | 360 | 57 | 20520 | B | PLANNED SHUTDOWN | Replace 10 11kV poles Beach Rd Waima Rd Parua St Tokomaru Bay
12271 | 13/12/2007 | 2007-12-13 | 2007 | 15 | 67 | 1005 | C | DEFECTIVE EQUIPMENT | Replace 11kV Ddo fuse base at T/x A509 Makarori
12287 | 13/12/2007 | 2007-12-13 | 2007 | 325 | 21 | 6825 | B | PLANNED SHUTDOWN | Replace 3 11kV poles SH35 Rototahi Tolaga Bay
12288 | 13/12/2007 | 2007-12-13 | 2007 | 231 | 5 | 1155 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting & restrain at pole A663 Whangara
12289 | 18/12/2007 | 2007-12-18 | 2007 | 225 | 67 | 15075 | B | PLANNED SHUTDOWN | Replace 11kV pole B1450 & T/x B635 Bayley St
12272 | 19/12/2007 | 2007-12-19 | 2007 | 11 | 66 | 726 | C | UNKNOWN | Reclose CB D141 in Wharekopae Rd cause unknown
12273 | 19/12/2007 | 2007-12-19 | 2007 | 523 | 18 | 9414 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J1407 Poroporo Valley
12274 | 20/12/2007 | 2007-12-20 | 2007 | 152 | 8 | 1216 | C | ADVERSE WEATHER | Untwist 11kV lines beyond pole W1158 Kai Kai
12276 | 20/12/2007 | 2007-12-20 | 2007 | 20 | 201 | 4020 | C | UNKNOWN | Reclose CB W814 at Chapmans cause unknown
12278 | 20/12/2007 | 2007-12-20 | 2007 | 27 | 78 | 2106 | C | TREE CONTACTS | Remove branch from 11kV lines near pole D4329 Matawai Rd
12284 | 20/12/2007 | 2007-12-20 | 2007 | 330 | 19051 | 1335121 | C | ADVERSE ENVIRONMENT | Loss of supply due to Earthquake
12279 | 21/12/2007 | 2007-12-21 | 2007 | 24 | 31 | 744 | C | ADVERSE ENVIRONMENT | Straighten 11kV SW/GR B2469 in Potae Ave
12280 | 21/12/2007 | 2007-12-21 | 2007 | 43 | 61 | 2623 | C | ADVERSE ENVIRONMENT | Untwist 11kV lines in Munro St
12281 | 21/12/2007 | 2007-12-21 | 2007 | 75 | 3 | 225 | C | ADVERSE ENVIRONMENT | Change damaged T/x C527 in Nelson Rd
12282 | 28/12/2007 | 2007-12-28 | 2007 | 307 | 77 | 9989 | C | ADVERSE WEATHER | Untwist 11kV lines pole F53 Mahiki Farm Settlement Rd
12283 | 30/12/2007 | 2007-12-30 | 2007 | 235 | 180 | 35615 | C | ADVERSE ENVIRONMENT | Reclose CB W820 Mahia
12290 | 05/01/2008 | 2008-01-05 | 2007 | 266 | 334 | 29961 | C | TREE CONTACTS | Repair 11kV lines between J2369 & J2368 Poroporo Valley( (Trees)
12291 | 05/01/2008 | 2008-01-05 | 2007 | 501 | 743 | 78983 | C | FOREIGN INTERFERENCE | Repair 2 11kV lines beyond W6613 Tukemokihi Rd
12292 | 08/01/2008 | 2008-01-08 | 2007 | 212 | 26 | 3424 | C | TREE CONTACTS | Replace 2 11kV poles J2369 & J2368 Poroporo Valley
12293 | 08/01/2008 | 2008-01-09 | 2007 | 384 | 170 | 4523 | C | ADVERSE WEATHER | Repair 11kV lines at pole W5235 Willow Flat
12316 | 08/01/2008 | 2008-01-08 | 2007 | 86 | 118 | 9394 | B | PLANNED SHUTDOWN | Repair cable fault Porter St
12294 | 10/01/2008 | 2008-01-10 | 2007 | 968 | 132 | 31840 | C | TREE CONTACTS | Repair 11kV lines at pole G102 Anaura Bay
12295 | 10/01/2008 | 2008-01-10 | 2007 | 87 | 936 | 35022 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable in Alice St
12317 | 10/01/2008 | 2008-01-10 | 2007 | 175 | 24 | 4200 | B | PLANNED SHUTDOWN | Change T/x G340 Hauiti Tolaga Bay
12296 | 12/01/2008 | 2008-01-12 | 2007 | 191 | 143 | 20658 | C | TREE CONTACTS | Remove tree from 11kV lines near pole H1456 Makarika Rd
12297 | 18/01/2008 | 2008-01-18 | 2007 | 85 | 13 | 1105 | C | DEFECTIVE EQUIPMENT | Temp repair 11kV pole W1523 Ormond Rd Wairoa
12298 | 18/01/2008 | 2008-01-18 | 2007 | 35 | 9 | 315 | C | TREE CONTACTS | Remove tree from 11kV lines at pole E1646 Riverside Rd
12299 | 19/01/2008 | 2008-01-19 | 2007 | 50 | 82 | 2624 | C | DEFECTIVE EQUIPMENT | Replace faulty T/x A311 in Einstein St
12300 | 19/01/2008 | 2008-01-19 | 2007 | 15 | 8 | 120 | C | TREE CONTACTS | Remove trees in 11kV beyond E9 in Manders Rd
12301 | 19/01/2008 | 2008-01-19 | 2007 | 81 | 79 | 6399 | C | DEFECTIVE EQUIPMENT | Repair 11kV at T/x J365 in Waikura Valley
12302 | 19/01/2008 | 2008-01-19 | 2007 | 195 | 31 | 6045 | C | TREE CONTACTS | Repair 3 11kV conductors at pole E1067 Kanakanaia Rd
12303 | 19/01/2008 | 2008-01-19 | 2007 | 172 | 88 | 8120 | C | DEFECTIVE EQUIPMENT | Replace burnt 11kV pole J2839 near Awatere Hill Te Araroa
12304 | 20/01/2008 | 2008-01-20 | 2007 | 73 | 38 | 2774 | C | DEFECTIVE EQUIPMENT | Rejoin 11kV jumpers at poles J2836 & J3903 after pole replacement
12305 | 20/01/2008 | 2008-01-20 | 2007 | 80 | 2470 | 117637 | C | DEFECTIVE EQUIPMENT | Replace 50kV pole G2799 near Christophers Rd
12306 | 20/01/2008 | 2008-01-20 | 2007 | 80 | 12 | 960 | C | TREE CONTACTS | Remove tree from 11kV beyond A484 Lynsnar Rd
12307 | 22/01/2008 | 2008-01-22 | 2007 | 1465 | 88 | 6236 | C | ADVERSE WEATHER | Repair 11kV lines between J787 & J788 & replace pole J2867 Te Hue
12308 | 22/01/2008 | 2008-01-22 | 2007 | 46 | 2470 | 68258 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarm on pole A1068 near Christophers Rd
12309 | 22/01/2008 | 2008-01-22 | 2007 | 45 | 19 | 855 | C | ADVERSE WEATHER | Repair 11kV lines beyond pole W1184 Awamate Rd
12310 | 22/01/2008 | 2008-01-22 | 2007 | 283 | 166 | 1094 | C | ADVERSE WEATHER | Repair 11kV lines beyond pole W1184 Awamate Rd
12311 | 22/01/2008 | 2008-01-22 | 2007 | 798 | 86 | 28442 | C | ADVERSE WEATHER | Patrol 11kV lines and reclose LBS F469 Matawai
12312 | 28/01/2008 | 2008-01-28 | 2007 | 13 | 374 | 4862 | C | UNKNOWN | Reclose CB C96 at Makaraka Sub cause unknown
12313 | 29/01/2008 | 2008-01-29 | 2007 | 47 | 76 | 3382 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J2839 on Te Araroa Hill
12314 | 31/01/2008 | 2008-01-31 | 2007 | 10 | 43 | 430 | C | DEFECTIVE EQUIPMENT | Temp replace Kidney insulator on pole H1500 Makarika Valley
12318 | 31/01/2008 | 2008-01-31 | 2007 | 125 | 14 | 1750 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Gordons Rd Manutuke
12319 | 31/01/2008 | 2008-01-31 | 2007 | 155 | 12 | 1860 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Paparatu Rd Waingake
12320 | 01/02/2008 | 2008-02-01 | 2007 | 181 | 43 | 7783 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H1500 Makarika Valley
12321 | 06/02/2008 | 2008-02-06 | 2007 | 12 | 922 | 11064 | C | UNKNOWN | Reclose CB C95 Haisman Rd cause unknown
12322 | 07/02/2008 | 2008-02-07 | 2007 | 214 | 103 | 22042 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between poles J4556 & J4555 Waikura Valley
12323 | 07/02/2008 | 2008-02-07 | 2007 | 196 | 122 | 8598 | C | ADVERSE ENVIRONMENT | Replace T/x pole J75 Beach Rd Rangitukia
12335 | 07/02/2008 | 2008-02-07 | 2007 | 218 | 12 | 2616 | B | PLANNED SHUTDOWN | Replace 11kV pole A3422 in Lynsar Rd Wainui
12324 | 10/02/2008 | 2008-02-10 | 2007 | 102 | 118 | 12036 | C | FOREIGN INTERFERENCE | Replace 11kV pole C3512 SH2 Muriwai
12325 | 11/02/2008 | 2008-02-11 | 2007 | 18 | 119 | 2142 | C | DEFECTIVE EQUIPMENT | Replace 11kV link W1201 near Rai Cotters Titirangi
12326 | 14/02/2008 | 2008-02-14 | 2007 | 116 | 227 | 11017 | C | TREE CONTACTS | Repair 11kV lines beyond E81 Ngakaroa Rd
12336 | 14/02/2008 | 2008-02-14 | 2007 | 104 | 59 | 4732 | B | PLANNED SHUTDOWN | Isolate LBS H1920 for servicing Waipiro Bay Rd
12327 | 17/02/2008 | 2008-02-17 | 2007 | 12 | 271 | 3252 | C | UNKNOWN | Reclose Inc D776 at Pehiri Sub cause unknown
12328 | 17/02/2008 | 2008-02-17 | 2007 | 150 | 40 | 6000 | C | FOREIGN INTERFERENCE | Replace 11kV pole W8621 Hit by Truck Tahaenui
12337 | 17/02/2008 | 2008-02-17 | 2007 | 420 | 53 | 22260 | B | PLANNED SHUTDOWN | Replace 11kV poles & replace Oil Switchs W1061 & W1062 Carroll St
12338 | 19/02/2008 | 2008-02-19 | 2007 | 74 | 5 | 370 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Whareponga Rd
12329 | 21/02/2008 | 2005-02-21 | 2007 | 68 | 73 | 4964 | C | DEFECTIVE EQUIPMENT | Replace DDO fuse on T/x C5863 Waughs Rd Waingake
12339 | 21/02/2008 | 2008-02-21 | 2007 | 295 | 87 | 25665 | B | PLANNED SHUTDOWN | Replace 7 11kV poles Beach Rd Tokomaru Bay
12330 | 23/02/2008 | 2008-02-23 | 2007 | 184 | 465 | 29983 | C | FOREIGN INTERFERENCE | Replace 11kV pole F1297 near Matawai
12340 | 26/02/2008 | 2008-02-26 | 2007 | 142 | 65 | 9230 | B | PLANNED SHUTDOWN | Remove trees & Illegal lights from 11kV poles Harringtons Rd Manutuke
12331 | 27/02/2008 | 2008-02-27 | 2007 | 97 | 54 | 5238 | C | FOREIGN INTERFERENCE | Replace 11kV pole C5054 SH2 near Kings Rd
12332 | 28/02/2008 | 2008-02-28 | 2007 | 6 | 91 | 546 | C | ADVERSE WEATHER | Rejoin 11kV jumpers pole H874 Kaiawha Rd
12334 | 29/02/2008 | 2008-02-29 | 2007 | 11 | 925 | 10175 | C | UNKNOWN | Reclose CB A616 Harris St at Port Sub cause unknown
12341 | 29/02/2008 | 2008-02-29 | 2007 | 50 | 217 | 10850 | B | PLANNED SHUTDOWN | Install new T/x J130 & 11kV Maintenance Main Rd Hicks Bay
12342 | 02/03/2008 | 2008-03-02 | 2007 | 564 | 96 | 11350 | C | TREE CONTACTS | Repair 11kV lines at pole J2387 SH35 near Te Hue Crn
12343 | 03/03/2008 | 2008-03-03 | 2007 | 723 | 66 | 47718 | C | TREE CONTACTS | Repair 11kV lines at pole D5041 Wharekopae Rd
12349 | 03/03/2008 | 2008-03-03 | 2007 | 224 | 22 | 4928 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Wharekopae Rd
12350 | 03/03/2008 | 2008-03-03 | 2007 | 302 | 5 | 1510 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Lavenham Rd
12355 | 03/03/2008 | 2008-03-03 | 2007 | 46 | 91 | 4186 | B | PLANNED SHUTDOWN | Install 3 DDO fuses at pole H865 Kaiawha Rd Tokomaru Bay
12344 | 04/03/2008 | 2008-03-04 | 2007 | 229 | 94 | 7710 | C | TREE CONTACTS | Repair 11kV lines at T/x D309 Tiniroto Rd
12351 | 04/03/2008 | 2008-03-04 | 2007 | 112 | 33 | 3696 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting SH35 Tolaga Bay
12345 | 05/03/2008 | 2008-03-05 | 2007 | 84 | 70 | 3930 | C | TREE CONTACTS | Remove tree from 11kV at pole D4914 Totangi Rd
12352 | 07/03/2008 | 2008-03-07 | 2007 | 50 | 40 | 2000 | B | PLANNED SHUTDOWN | To connect 11kV jumpers on pole D1732 for new connection Tiniroto Rd
12353 | 11/03/2008 | 2008-03-11 | 2007 | 31 | 226 | 7006 | B | PLANNED SHUTDOWN | Replace 4 11kV poles Russell St B4869 B4897 B4898 & B4899
12354 | 12/03/2008 | 2008-03-12 | 2007 | 60 | 58 | 3480 | B | PLANNED SHUTDOWN | Connect 11kV jumpers at pole W7375 Ruakitiri Valley
12346 | 17/03/2008 | 2008-03-17 | 2007 | 96 | 113 | 10848 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on T/x J59 Rangitukia
12358 | 19/03/2008 | 2008-03-19 | 2007 | 24 | 10 | 240 | B | PLANNED SHUTDOWN | Isolate T/x C315 Stirling Park for relevelling
12347 | 22/03/2008 | 2008-03-22 | 2007 | 114 | 50 | 3206 | C | DEFECTIVE EQUIPMENT | Replace 11kV jumper at pole D91 outside Pehiri Sub
12359 | 27/03/2008 | 2008-03-27 | 2007 | 325 | 5 | 1625 | B | PLANNED SHUTDOWN | Remove 11kV fuses to allow 50kV pole Change Kaiawha Rd
12348 | 28/03/2008 | 2008-03-28 | 2007 | 11 | 27 | 297 | C | DEFECTIVE EQUIPMENT | Replace Xarm brace on 11kV pole G2142 Paroa Rd
12357 | 29/03/2008 | 2008-03-29 | 2007 | 113 | 175 | 19775 | B | PLANNED SHUTDOWN | Isolate 11kV to allow replacement of 50kV pole G2781 at Mangatuna
12356 | 31/03/2008 | 2008-03-31 | 2007 | 233 | 142 | 33086 | B | PLANNED SHUTDOWN | Replace 2 11kV poles H2570 & H2571 Tokomaru Bay
12360 | 01/04/2008 | 2008-04-01 | 2008 | 34 | 1106 | 30284 | C | UNKNOWN | Reclose Inc CB F411 at Puha Sub cause unknown
12361 | 01/04/2008 | 2008-04-01 | 2008 | 275 | 286 | 57478 | C | FOREIGN INTERFERENCE | Remove possom from T/x J102 behind School Ruatoria
12383 | 02/04/2008 | 2008-04-02 | 2008 | 325 | 26 | 8450 | B | PLANNED SHUTDOWN | Replace 11kV poles Poroporo Valley
12362 | 04/04/2008 | 2008-04-04 | 2008 | 87 | 26 | 2262 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole J2370 Poroporo Valley
12363 | 07/04/2008 | 2008-04-07 | 2008 | 95 | 118 | 4181 | C | TREE CONTACTS | Remove tree from 11kV between W8858 to W8854 Kahangungu
12364 | 08/04/2008 | 2008-04-08 | 2008 | 207 | 374 | 15693 | C | TREE CONTACTS | Replace Xarm on pole E1432 Kawatiri Rd
12365 | 08/04/2008 | 2008-04-08 | 2008 | 524 | 143 | 27408 | C | TREE CONTACTS | Repair 11kV lines at pole H1829 Reedys Hill Ruatoria
12366 | 08/04/2008 | 2008-04-08 | 2008 | 56 | 5 | 280 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole J2135 Koia Rd Rangitukia
12367 | 09/04/2008 | 2008-04-09 | 2008 | 130 | 75 | 9750 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole W6801 Mangapoikie Rd Wairoa
12368 | 10/04/2008 | 2008-04-10 | 2008 | 21 | 2487 | 47368 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
12369 | 12/04/2008 | 2008-04-12 | 2008 | 40 | 29 | 1160 | C | FOREIGN INTERFERENCE | Repair 11kV jumper on pole F420 Whakarau Rd
12370 | 15/04/2008 | 2008-04-15 | 2008 | 131 | 399 | 17790 | C | DEFECTIVE EQUIPMENT | Replace burnt 11kV pole D1667 at Waituhi
12371 | 16/04/2008 | 2008-04-16 | 2008 | 941 | 92 | 28964 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between poles J1225 & J1226 Kopuponamu river Xing
12372 | 17/04/2008 | 2008-04-17 | 2008 | 1250 | 218 | 58376 | C | ADVERSE WEATHER | Repair 11kV lines at pole W7689 Onenui Stn Mahia
12373 | 17/04/2008 | 2008-04-17 | 2008 | 260 | 38 | 7540 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole W7021 Hokinui
12374 | 17/04/2008 | 2008-04-17 | 2008 | 201 | 127 | 5577 | C | TREE CONTACTS | Repair 11kV lines between poles J3714 to J3715 Moewra Te Araroa
12375 | 17/04/2008 | 2008-04-17 | 2008 | 314 | 182 | 43638 | C | UNKNOWN | Reclose CB 23 at Tuai cause unknown
12376 | 18/04/2008 | 2008-04-18 | 2008 | 188 | 199 | 25531 | C | TREE CONTACTS | Isolate 11kV to cut trees at pole W4649 Tuai
12384 | 18/04/2008 | 2008-04-18 | 2008 | 189 | 38 | 7182 | B | PLANNED SHUTDOWN | Install 3 DDO fuses & Isolate 11kV for tree cutting Ormond Valley
12377 | 19/04/2008 | 2008-04-19 | 2008 | 10 | 202 | 2020 | C | UNKNOWN | Reclose CB C18 Bell Rd at Matawhero Sub
12378 | 21/04/2008 | 2008-04-21 | 2008 | 7 | 206 | 1276 | C | UNKNOWN | Reclose CB G329 Rototahi at Tolaga Bay Sub
12385 | 22/04/2008 | 2008-04-22 | 2008 | 122 | 16 | 1952 | B | PLANNED SHUTDOWN | Repair 11kV lines & install prop pole at Waiokopu Mahia
12386 | 23/04/2008 | 2008-04-23 | 2008 | 282 | 9 | 2538 | B | PLANNED SHUTDOWN | Replace T/x structure at W1782 Eripiti
12379 | 25/04/2008 | 2008-04-25 | 2008 | 6 | 636 | 2872 | C | UNKNOWN | Reclose CB W213 Brickworks at Kiwi Sub cause unknown
12380 | 26/04/2008 | 2008-04-26 | 2008 | 8 | 2487 | 19896 | C | UNKNOWN | Reclose CB A8 at Goodwins Rd cause unknown
12387 | 28/04/2008 | 2008-04-28 | 2008 | 51 | 78 | 3978 | B | PLANNED SHUTDOWN | Fit 3 DDO fuses to pole C5805 Crn Parkers Lane Makaraka
12381 | 29/04/2008 | 2008-04-29 | 2008 | 74 | 51 | 3774 | C | FOREIGN INTERFERENCE | Isolate 11kV pole D1464 Kaimoe Rd hit by Car
12388 | 29/04/2008 | 2008-04-29 | 2008 | 89 | 44 | 655 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Waingake Rd near Water Works
12389 | 29/04/2008 | 2008-04-29 | 2008 | 89 | 135 | 12015 | B | PLANNED SHUTDOWN | Change 2 11kV poles Tauwhareparae Rd
12382 | 30/04/2008 | 2008-04-30 | 2008 | 119 | 51 | 6069 | C | FOREIGN INTERFERENCE | Replace 11kV pole D1416 in Kaimoe Rd Patutahi
12390 | 30/04/2008 | 2008-04-30 | 2008 | 211 | 23 | 4853 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Totangi Rd Ngatapa
12391 | 30/04/2008 | 2008-04-30 | 2008 | 210 | 23 | 4830 | B | PLANNED SHUTDOWN | Install new SF6 W788 Switch at Putere
12392 | 01/05/2008 | 2008-05-01 | 2008 | 94 | 146 | 6164 | C | ADVERSE WEATHER | CB W826 possible lightning
12393 | 01/05/2008 | 2008-05-01 | 2008 | 2161 | 253 | 357594 | C | DEFECTIVE EQUIPMENT | 11Kv CONDUCTOR BROKEN J4507 - J4508
12394 | 01/05/2008 | 2008-05-01 | 2008 | 55 | 70 | 3850 | B | PLANNED SHUTDOWN | install new tx W7613
12395 | 01/05/2008 | 2008-05-01 | 2008 | 190 | 48 | 9120 | B | PLANNED SHUTDOWN | tree cutting
12396 | 05/05/2008 | 2008-05-05 | 2008 | 863 | 120 | 21366 | C | UNKNOWN | unknown J1078 O/C & E/F
12397 | 07/05/2008 | 2008-05-07 | 2008 | 36 | 63 | 2268 | C | DEFECTIVE EQUIPMENT | repair 11kV conductor A2585
12398 | 08/05/2008 | 2008-05-08 | 2008 | 125 | 175 | 21835 | C | TREE CONTACTS | cut trees H991
12399 | 08/05/2008 | 2008-05-08 | 2008 | 6 | 119 | 714 | B | PLANNED SHUTDOWN | replace 11kV SwGr B808, B809, B810
12400 | 11/05/2008 | 2008-05-12 | 2008 | 1282 | 104 | 53048 | C | DEFECTIVE EQUIPMENT | broken jumper ABS J356
12401 | 11/05/2008 | 2008-05-12 | 2008 | 956 | 329 | 21561 | C | DEFECTIVE EQUIPMENT | broken 11kV conductors J969 - J970
12402 | 12/05/2008 | 2008-05-12 | 2008 | 4 | 103 | 412 | B | PLANNED SHUTDOWN | replace 11kv SwGr B805
12403 | 12/05/2008 | 2008-05-12 | 2008 | 318 | 16 | 5098 | C | FOREIGN INTERFERENCE | possum - burnt xarms Pole D2044
12404 | 14/05/2008 | 2008-05-14 | 2008 | 2 | 13 | 26 | B | PLANNED SHUTDOWN | replace 11kV SwGr B308
12405 | 14/05/2008 | 2008-05-14 | 2008 | 77 | 446 | 15778 | C | FOREIGN INTERFERENCE | mouse in CB A472
12406 | 14/05/2008 | 2008-05-14 | 2008 | 297 | 202 | 14802 | C | FOREIGN INTERFERENCE | car vs pole C2212
12407 | 14/05/2008 | 2008-05-14 | 2008 | 121 | 46 | 2676 | C | DEFECTIVE EQUIPMENT | cable cucifix fault pole B6322
12414 | 16/05/2008 | 2008-05-16 | 2008 | 41 | 80 | 3280 | C | FOREIGN INTERFERENCE | rocks broke insulators pole A445
12415 | 16/05/2008 | 2008-05-16 | 2008 | 157 | 16 | 2372 | C | DEFECTIVE EQUIPMENT | reconnect cable after repaired to pole B6322
12408 | 20/05/2008 | 2008-05-20 | 2008 | 178 | 37 | 6586 | B | PLANNED SHUTDOWN | shelterbelt trimming
12410 | 23/05/2008 | 2008-05-23 | 2008 | 199 | 16 | 3286 | B | PLANNED SHUTDOWN | connect new cable & SwGr at Equties sub division
12409 | 25/05/2008 | 2008-05-05 | 2008 | 241 | 218 | 28694 | C | DEFECTIVE EQUIPMENT | conductor broken W7636
12411 | 26/05/2008 | 2008-05-26 | 2008 | 218 | 63 | 13734 | C | DEFECTIVE EQUIPMENT | broken conductor at D511
12416 | 26/05/2008 | 2008-05-26 | 2008 | 50 | 175 | 8078 | C | DEFECTIVE EQUIPMENT | broken conductor pole A2582
12412 | 27/05/2008 | 2008-05-27 | 2008 | 90 | 936 | 60765 | C | UNKNOWN | unknown OC trip A475
12413 | 27/05/2008 | 2008-05-27 | 2008 | 409 | 360 | 20375 | C | TREE CONTACTS | tree broke conductor and pole W6288
12417 | 29/05/2008 | 2008-05-29 | 2008 | 447 | 26 | 5190 | C | FOREIGN INTERFERENCE | car vs pole C3350
12418 | 29/05/2008 | 2008-05-29 | 2008 | 161 | 13 | 2093 | C | DEFECTIVE EQUIPMENT | tree through lines, broke pole w6288
12419 | 29/05/2008 | 2008-05-29 | 2008 | 21 | 1791 | 37611 | C | FOREIGN INTERFERENCE | car vs pole C3350
12420 | 30/05/2008 | 2008-05-30 | 2008 | 50 | 936 | 30635 | C | DEFECTIVE EQUIPMENT | faulty cable insulator boot on SwGr A397
12421 | 31/05/2008 | 2008-05-31 | 2008 | 150 | 399 | 30828 | C | DEFECTIVE EQUIPMENT | shackle insulator pulled out of xarm C1277
12422 | 01/06/2008 | 2008-06-01 | 2008 | 58 | 734 | 32311 | C | DEFECTIVE EQUIPMENT | Replace lightining arrestor on pole W6668
12423 | 03/06/2008 | 2008-06-03 | 2008 | 9 | 399 | 3121 | C | DEFECTIVE EQUIPMENT | Isolate faulty ABS C1098 Manutuke
12425 | 03/06/2008 | 2008-06-03 | 2008 | 200 | 28 | 5600 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole E2479 Ngakaroa Rd
12447 | 04/06/2008 | 2008-06-04 | 2008 | 168 | 47 | 7896 | B | PLANNED SHUTDOWN | Isolate 11kV lines for Tree cutting Bck Ormond Rd
12448 | 06/06/2008 | 2008-06-06 | 2008 | 175 | 78 | 13650 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Bushmere Rd
12426 | 07/06/2008 | 2008-06-07 | 2008 | 6 | 1514 | 13626 | C | TREE CONTACTS | Remove tree branch from pole B229 Riverside Rd
12427 | 07/06/2008 | 2008-06-07 | 2008 | 37 | 90 | 3330 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole W1115 Onepoto
12428 | 07/06/2008 | 2008-06-07 | 2008 | 120 | 255 | 30600 | C | FOREIGN INTERFERENCE | Replace pole J278 Hicks Bay Hit by car towing trailer
12429 | 07/06/2008 | 2008-06-07 | 2008 | 263 | 435 | 81340 | C | TREE CONTACTS | Repair 11kV lines at pole F135 Matawai
12430 | 08/06/2008 | 2008-06-08 | 2008 | 380 | 93 | 12833 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole D3564 Ruakaka Rd Tiniroto
12431 | 08/06/2008 | 2008-06-08 | 2008 | 625 | 1170 | 22321 | C | FOREIGN INTERFERENCE | Replace 11kV pole C937 Wharekopae Rd
12449 | 12/06/2008 | 2008-06-12 | 2008 | 346 | 49 | 2914 | B | PLANNED SHUTDOWN | Replace 11kV pole H196 Ruatoria South
12450 | 12/06/2008 | 2008-06-12 | 2008 | 96 | 6 | 576 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Tiniroto Rd
12433 | 13/06/2008 | 2008-06-13 | 2008 | 119 | 378 | 37748 | C | UNKNOWN | Reclose CB24 at Tuai Strong Winds in Area
12446 | 15/06/2008 | 2008-06-15 | 2008 | 17 | 60 | 1020 | B | PLANNED SHUTDOWN | Replace SW/Gr at T/x B290 Carnarvon St
12434 | 16/06/2008 | 2008-06-16 | 2008 | 97 | 20 | 1940 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole J4879 Tuparoa Rd
12435 | 16/06/2008 | 2008-06-16 | 2008 | 334 | 268 | 41633 | C | DEFECTIVE EQUIPMENT | Replace 11kV SW/gr at B694 Anzac St Crn
12436 | 17/06/2008 | 2008-06-17 | 2008 | 35 | 258 | 9030 | C | ADVERSE WEATHER | Rejoin 11kV jumpers at pole A1745 Live line cut
12451 | 17/06/2008 | 2008-06-17 | 2008 | 382 | 47 | 17954 | B | PLANNED SHUTDOWN | Replace 4 11kV poles in Kelvin St
12452 | 19/06/2008 | 2008-06-19 | 2008 | 370 | 63 | 23310 | B | PLANNED SHUTDOWN | Replace 4 11kV poles in Munro St
12437 | 23/06/2008 | 2008-06-23 | 2008 | 35 | 7 | 406 | C | LIGHTNING | Replace burnt Xarms on pole J3831 Hicks Bay
12444 | 24/06/2008 | 2008-06-24 | 2008 | 0 | 165 | 12375 | B | PLANNED SHUTDOWN | Cut & join 11kV cable to T/x B294 Chip Housing
12445 | 24/06/2008 | 2008-06-24 | 2008 | 7 | 88 | 616 | B | PLANNED SHUTDOWN | Install generator at T/x B294 Chip Housing
12438 | 26/06/2008 | 2007-06-26 | 2008 | 60 | 222 | 13320 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole J53 Hicks Bay
12439 | 27/06/2008 | 2008-06-27 | 2008 | 105 | 275 | 12595 | C | TREE CONTACTS | Remove tree from pole W687 River Rock Rd
12440 | 27/06/2008 | 2008-06-27 | 2008 | 1113 | 156 | 35518 | C | TREE CONTACTS | Remove tree from 11kV at pole G1580 Arikihi Rd Tolaga
12441 | 27/06/2008 | 2008-06-27 | 2008 | 300 | 172 | 14256 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between poles W5367 to W5366 Puterino
12442 | 27/06/2008 | 2008-06-27 | 2008 | 831 | 90 | 16572 | C | ADVERSE WEATHER | Repair 11kv lines between poles G614 & G615 Waimata Valley
12443 | 29/06/2008 | 2008-06-29 | 2008 | 337 | 404 | 43979 | C | LIGHTNING | Replace Burnt 11kV pole W460 at Waitaha
12495 | 01/07/2008 | 2008-07-01 | 2008 | 323 | 5 | 1615 | B | PLANNED SHUTDOWN | To replace TX structure J58
12453 | 03/07/2008 | 2008-07-03 | 2008 | 135 | 12 | 1620 | C | TREE CONTACTS | Rejoin 11kV jumpers at pole J2730 Poroporo Valley
12496 | 03/07/2008 | 2008-07-03 | 2008 | 317 | 28 | 1071 | B | PLANNED SHUTDOWN | Cut jumpers - Replace ABS W1024 - Rejoin jumpers
12497 | 03/07/2008 | 2008-07-03 | 2008 | 2 | 15 | 30 | B | PLANNED SHUTDOWN | Joint & recloate 11kV cables to new gas switch A6546, A6548, A6549 and fuse switch A6547
12454 | 04/07/2008 | 2008-07-04 | 2008 | 394 | 169 | 17004 | C | FOREIGN INTERFERENCE | Car hit TX pole E293
12455 | 04/07/2008 | 2008-07-04 | 2008 | 837 | 92 | 7827 | C | TREE CONTACTS | 1 x 11kV wire down at pole J1157 - Tree
12456 | 06/07/2008 | 2008-07-06 | 2008 | 124 | 958 | 41477 | C | FOREIGN INTERFERENCE | Car hit TX pole D599
12457 | 06/07/2008 | 2008-07-06 | 2008 | 34 | 418 | 13952 | C | UNKNOWN | Unknown
12458 | 06/07/2008 | 2008-07-06 | 2008 | 112 | 145 | 10160 | C | DEFECTIVE EQUIPMENT | Wire down at W9185
12459 | 06/07/2008 | 2008-07-06 | 2008 | 219 | 485 | 47544 | C | ADVERSE WEATHER | Conductor clashed and welded at C2709 - C127
12460 | 06/07/2008 | 2008-07-06 | 2008 | 474 | 73 | 12785 | C | UNKNOWN | Unknown - to be investigated further
12461 | 07/07/2008 | 2008-07-07 | 2008 | 15 | 833 | 11571 | C | UNKNOWN | Reclose CBW808 Blacks Pad cause unknown
12462 | 07/07/2008 | 2008-07-07 | 2008 | 1175 | 81 | 23985 | C | FOREIGN INTERFERENCE | Fire at Mahunga - Replace pole W1213 and conductor
12498 | 07/07/2008 | 2008-07-07 | 2008 | 16 | 63 | 1827 | B | PLANNED SHUTDOWN | Replace 11kV poles A2585 & A2586 at Wainui near the okitu bridge SHW35
12499 | 08/07/2008 | 2008-07-08 | 2008 | 210 | 28 | 5880 | B | PLANNED SHUTDOWN | isolate 11kV so Arborcare can clear trees out of close zone near lines
12463 | 09/07/2008 | 2008-07-06 | 2008 | 46 | 24 | 1104 | C | DEFECTIVE EQUIPMENT | Replace x-arm on pole W8731 Nuhaka
12500 | 09/07/2008 | 2008-07-09 | 2008 | 161 | 9 | 1449 | B | PLANNED SHUTDOWN | Isolate 11kV so Arborcare can clear trees out of close zone near lines
12501 | 09/07/2008 | 2008-07-09 | 2008 | 225 | 3 | 675 | B | PLANNED SHUTDOWN | Replace 11kV poles H3277 & H39 Cemetery Rd, Te Puia
12502 | 10/07/2008 | 2008-07-10 | 2008 | 289 | 26 | 7514 | B | PLANNED SHUTDOWN | Replace TX W1076 with 300kVA TX and overlay 95mm AL with 185mm AL
12503 | 10/07/2008 | 2008-07-10 | 2008 | 287 | 16 | 4592 | B | PLANNED SHUTDOWN | Replace 6 x 11kV poles - E2159, E2171, E2176, E2177, E2182, E2183
12464 | 14/07/2008 | 2008-07-14 | 2008 | 28 | 22 | 718 | C | TREE CONTACTS | Rejoin 11kV jumpers at poles D4944 - D4952 - Trees
12504 | 14/07/2008 | 2008-07-14 | 2008 | 275 | 5 | 1375 | B | PLANNED SHUTDOWN | Change 11kV pole H324
12505 | 15/07/2008 | 2008-07-15 | 2008 | 399 | 276 | 39640 | B | PLANNED SHUTDOWN | Replace 11kV & 400V poles A2260, A2262, A2263, A321 & remove redundant ABS A269
12465 | 16/07/2008 | 2008-07-16 | 2008 | 144 | 92 | 9414 | C | FOREIGN INTERFERENCE | Cut 11kV jumpers at G4001 & G4013 / Repair 11kV lines G4009 - G4010
12506 | 16/07/2008 | 2008-07-16 | 2008 | 82 | 10 | 820 | B | PLANNED SHUTDOWN | Remove redundant ABS A462 & join jumpers through
12508 | 17/07/2008 | 2008-07-17 | 2008 | 220 | 7 | 1540 | B | PLANNED SHUTDOWN | Lower 11kV lines at J4438 for tree removal
12509 | 17/07/2008 | 2008-07-17 | 2008 | 54 | 31 | 3317 | B | PLANNED SHUTDOWN | Rejoin 11kv lines at J4438 after tree removal
12510 | 18/07/2008 | 2008-07-18 | 2008 | 15 | 257 | 3855 | B | PLANNED SHUTDOWN | Put 11kV link between oil swithc B1424 & B753 and phase out at Carnarvon
12511 | 18/07/2008 | 2008-07-18 | 2008 | 122 | 23 | 2806 | B | PLANNED SHUTDOWN | Tree cutting O'Grady & Tucker Rds
12466 | 19/07/2008 | 2008-07-19 | 2008 | 211 | 92 | 12647 | C | FOREIGN INTERFERENCE | Repair 11kV lines between G1458 - G1459 Anaura Bay
12467 | 21/07/2008 | 2008-07-21 | 2008 | 114 | 120 | 23160 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J2074 Rangitukia Rd
12512 | 24/07/2008 | 2008-07-24 | 2008 | 190 | 15 | 2850 | B | PLANNED SHUTDOWN | Isolate 11kV so Arborcare can clear trees out of close zone near lines - E1218 & E1220
12513 | 24/07/2008 | 2008-07-24 | 2008 | 71 | 135 | 9585 | B | PLANNED SHUTDOWN | Change damaged load break switch C1098 Whakato Rd
12468 | 27/07/2008 | 2008-07-27 | 2008 | 40 | 16 | 784 | c | DEFECTIVE EQUIPMENT | Replace 11kV pole G1081 Sheltons Rd
12469 | 27/07/2008 | 2008-07-27 | 2008 | 35 | 352 | 12320 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on ABS W939
12470 | 29/07/2008 | 2008-07-29 | 2008 | 91 | 10 | 910 | C | DEFECTIVE EQUIPMENT | Broken pole / replace A4313 Goodwins Rd
12471 | 30/07/2008 | 2008-07-30 | 2008 | 1198 | 93 | 21114 | C | TREE CONTACTS | Fault beond E203 - Trees in 11kV E549 - E548
12472 | 30/07/2008 | 2008-07-30 | 2008 | 1195 | 9 | 10755 | C | DEFECTIVE EQUIPMENT | Isolate 11kV pole A3718 Panikau Rd
12473 | 30/07/2008 | 2008-07-30 | 2008 | 335 | 241 | 18534 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole E4010 & x-arm on pole E4012 Bond Road
12474 | 30/07/2008 | 2008-07-30 | 2008 | 238 | 341 | 55009 | C | ADVERSE WEATHER | Untwist 11kV conductor at pole J805 & J806 river xing
12475 | 30/07/2008 | 2008-07-30 | 2008 | 300 | 45 | 6405 | C | ADVERSE WEATHER | Check lines nothing found reclose C2175
12476 | 30/07/2008 | 2008-07-30 | 2008 | 161 | 29 | 4669 | C | ADVERSE WEATHER | Replace x-arm pole E2415 Ormond Valley Rd
12477 | 30/07/2008 | 2008-07-30 | 2008 | 1082 | 218 | 28898 | C | ADVERSE WEATHER | Repair 11kV lines beond W1221 Onenui
12478 | 30/07/2008 | 2008-07-30 | 2008 | 179 | 732 | 74043 | C | ADVERSE WEATHER | Repair 11kV lines at pole W6516 Mangapokie
12479 | 30/07/2008 | 2008-07-30 | 2008 | 22 | 1108 | 21391 | C | UNKNOWN | Reclose W790 Tahaenui, cause unknown
12480 | 30/07/2008 | 2008-07-30 | 2008 | 1328 | 261 | 40474 | C | TREE CONTACTS | Repair 11kV beond TX W134 Morere
12481 | 30/07/2008 | 2008-07-30 | 2008 | 102 | 691 | 11372 | C | TREE CONTACTS | Isolate 11kV lines at A4113 Kaiti hill
12482 | 30/07/2008 | 2008-07-30 | 2008 | 300 | 76 | 4008 | C | ADVERSE WEATHER | Repair 11kV lines H4179 Ihunga Rd
12483 | 30/07/2008 | 2008-07-30 | 2008 | 310 | 339 | 11592 | C | DEFECTIVE EQUIPMENT | Isolate 11kV pole J984 Waiomatatini
12484 | 30/07/2008 | 2008-07-30 | 2008 | 183 | 437 | 16527 | C | ADVERSE WEATHER | Repair 11kV at pole A4336 Goodwinds Rd
12485 | 31/07/2008 | 2008-07-31 | 2008 | 147 | 72 | 5484 | C | TREE CONTACTS | Remove Tree from 11kV pole D68 Totangi Rd
12486 | 31/07/2008 | 2008-07-31 | 2008 | 295 | 150 | 36465 | C | TREE CONTACTS | Repair 11kV lines at pole G1700 Tauwharepare
12487 | 31/07/2008 | 2008-07-31 | 2008 | 18 | 58 | 1002 | C | UNKNOWN | Reclose CB W999 Pokopoko (High winds)
12488 | 31/07/2008 | 2008-07-31 | 2008 | 48 | 176 | 8015 | C | UNKNOWN | Reclose CB24 Tuai cause unknown
12489 | 31/07/2008 | 2008-07-31 | 2008 | 30 | 142 | 4215 | C | TREE CONTACTS | Cut 11kV jumpers at A4115 - A4118 - broken conductors trees
12490 | 31/07/2008 | 2008-07-31 | 2008 | 23 | 8 | 414 | C | DEFECTIVE EQUIPMENT | insulator fault at J1701 - repair
12491 | 31/07/2008 | 2008-07-31 | 2008 | 37 | 57 | 2109 | C | DEFECTIVE EQUIPMENT | Broken 11kV jumper to DDO TX C335 McClaurin Rd
12492 | 31/07/2008 | 2008-07-31 | 2008 | 184 | 275 | 21386 | C | DEFECTIVE EQUIPMENT | Cut 11kV jumpers at pole W8064 Mangone Rd
12493 | 31/07/2008 | 2008-07-31 | 2008 | 821 | 77 | 51085 | C | DEFECTIVE EQUIPMENT | Pole down F2151 - No wire broken
12514 | 01/08/2008 | 2008-08-01 | 2008 | 16 | 14 | 224 | C | ADVERSE WEATHER | Rejoin 11kV jumpers pole W8064 Klonkeen Stn
12515 | 01/08/2008 | 2008-08-01 | 2008 | 298 | 9 | 2682 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between poles E652 & E653 Tarndale Rd
12516 | 01/08/2008 | 2008-08-01 | 2008 | 145 | 29 | 3095 | C | ADVERSE WEATHER | Replace 11kV lines J983 to J981 Waiomatatini Rd
12517 | 02/08/2008 | 2008-08-02 | 2008 | 278 | 169 | 13738 | C | TREE CONTACTS | Cut 11kV jumpers at pole D3956 Tahunga Rd
12518 | 03/08/2008 | 2008-08-03 | 2008 | 20 | 90 | 1800 | C | TREE CONTACTS | Remove tree from 11kV beyond fuses W1115 Onepoto
12519 | 03/08/2008 | 2008-08-03 | 2008 | 366 | 155 | 10219 | C | ADVERSE WEATHER | Repair 11kV lines between poles W5215 & W5216 Woodlands
12520 | 04/08/2008 | 2008-08-04 | 2008 | 32 | 13 | 416 | C | TREE CONTACTS | Rejoin 11kV jumpers pole D3956 Tahunga Rd
12536 | 04/08/2008 | 2008-08-04 | 2008 | 66 | 129 | 13158 | B | PLANNED SHUTDOWN | Isolate to cut jumpers C5053 & C5056 to replace ABS C260 SH2 Matawai Rd
12539 | 05/08/2008 | 2008-08-05 | 2008 | 162 | 117 | 18954 | B | PLANNED SHUTDOWN | Replace 11kV pole G1715 Tauwhareparae Rd
12537 | 06/08/2008 | 2008-08-06 | 2008 | 158 | 18 | 2844 | B | PLANNED SHUTDOWN | Replace 11kV pole J748 Tapuaeroa Rd
12540 | 06/08/2008 | 2008-08-06 | 2008 | 185 | 9 | 1665 | B | PLANNED SHUTDOWN | Replace 11kV pole A3738 Panikau Rd
12542 | 06/08/2008 | 2008-08-06 | 2008 | 104 | 10 | 1040 | B | PLANNED SHUTDOWN | Replace 11kV pole A4313 Goodwins Rd
12544 | 06/08/2008 | 2008-08-06 | 2008 | 26 | 142 | 2452 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers pole A4115 Kaiti Hill
12521 | 07/08/2008 | 2008-08-07 | 2008 | 104 | 1962 | 52775 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable under Wairoa Bridge
12545 | 07/08/2008 | 2008-08-07 | 2008 | 184 | 27 | 4968 | B | PLANNED SHUTDOWN | Replace 11kV pole E723 Armstrong Rd
12522 | 08/08/2008 | 2008-08-08 | 2008 | 13 | 1688 | 33866 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause Unknown
12525 | 09/08/2008 | 2008-08-09 | 2008 | 138 | 878 | 53437 | C | DEFECTIVE EQUIPMENT | Repair SW/Gr B758 crn Lytton Rd & Manuka St
12524 | 10/08/2008 | 2008-08-10 | 2008 | 141 | 215 | 17480 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole F3300 Te Karaka
12526 | 10/08/2008 | 2008-08-10 | 2008 | 33 | 65 | 2145 | C | FOREIGN INTERFERENCE | Repair 11kV jumper pole F3300 Te Karaka Car hit pole
12535 | 12/08/2008 | 2008-08-12 | 2008 | 199 | 17 | 3383 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Pehiri Rd
12543 | 13/08/2008 | 2008-08-13 | 2008 | 295 | 4 | 2128 | B | PLANNED SHUTDOWN | Replace 5 11kV poles Taihamiti Rd
12527 | 14/08/2008 | 2008-08-14 | 2008 | 547 | 255 | 29157 | C | FOREIGN INTERFERENCE | Repair 11kV line pole J620 to J404 SH35 Te Araroa
12528 | 14/08/2008 | 2008-08-14 | 2008 | 51 | 106 | 1663 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole D1817 Crn Bruntons Rd & Wharekopae Rd
12541 | 14/08/2008 | 2008-08-14 | 2008 | 105 | 65 | 6825 | B | PLANNED SHUTDOWN | Check T/x B119 Scott St
12529 | 15/08/2008 | 2008-08-15 | 2008 | 213 | 93 | 12373 | C | TREE CONTACTS | Repair 11kV lines D3306 to D3307 Tiniroto Rd
12530 | 15/08/2008 | 2008-08-15 | 2008 | 227 | 10 | 2270 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole D3023 Humphries Rd
12531 | 15/08/2008 | 2008-08-15 | 2008 | 267 | 404 | 49450 | C | DEFECTIVE EQUIPMENT | Repair 11kV line W6217 Ohinepaka
12532 | 18/08/2008 | 2008-08-18 | 2008 | 145 | 156 | 10707 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole G1845 Tauwhareparae Rd
12533 | 18/08/2008 | 2008-08-18 | 2008 | 302 | 255 | 42242 | C | DEFECTIVE EQUIPMENT | Repair 11kV between poles J3898 & J3899 Wharf Rd Hicks Bay
12534 | 19/08/2008 | 2008-08-19 | 2008 | 40 | 18 | 720 | C | FOREIGN INTERFERENCE | Rejoin 11kV jumpers at pole G1845 Paramata Rd Tolaga Bay
12538 | 20/08/2008 | 2008-08-20 | 2008 | 406 | 57 | 7625 | B | PLANNED SHUTDOWN | Isolate 11kV lines to Cut jumpers poles C5684 & C3154 Awapuni Rd
12547 | 26/08/2008 | 2008-08-26 | 2008 | 309 | 27 | 15417 | B | PLANNED SHUTDOWN | Replace 7 11kV poles Armstrong Rd
12546 | 27/08/2008 | 2008-08-27 | 2008 | 456 | 169 | 23330 | B | PLANNED SHUTDOWN | Relocate 2 11kV poles SH2 near Bond Rd E2140 & E60
12570 | 03/09/2008 | 2008-09-03 | 2008 | 9 | 66 | 594 | B | PLANNED SHUTDOWN | Replace boots on 11kV cable SW/Gr A382 Wairere Rd
12548 | 04/09/2008 | 2008-09-04 | 2008 | 48 | 4 | 192 | C | FOREIGN INTERFERENCE | Remove bird from top of 11kV pole H627 Arero
12572 | 04/09/2008 | 2008-09-04 | 2008 | 321 | 17 | 5457 | B | PLANNED SHUTDOWN | Replace 11kV poles A718 A724 A756 A763 A765 & A767 Mokairau
12549 | 05/09/2008 | 2008-09-05 | 2008 | 35 | 958 | 32730 | C | DEFECTIVE EQUIPMENT | Repair 11kV CB B414 at Gisborne Hospital
12550 | 05/09/2008 | 2008-09-05 | 2008 | 273 | 737 | 61128 | C | FOREIGN INTERFERENCE | Replace 11kV pole D3126 SH2 Makaraka
12556 | 09/09/2008 | 2008-09-09 | 2008 | 215 | 17 | 3655 | B | PLANNED SHUTDOWN | Replace 11kV poles A820 & A823 Rototahi Stn
12551 | 10/09/2008 | 2008-09-10 | 2008 | 52 | 15 | 780 | C | DEFECTIVE EQUIPMENT | Repair quadrant on ABS H59 at Te Puia
12557 | 10/09/2008 | 2008-09-10 | 2008 | 300 | 16 | 4800 | B | PLANNED SHUTDOWN | Replace 11kV poles G1041 & G1043 Wharf Rd Tolaga
12552 | 11/09/2008 | 2008-09-11 | 2008 | 204 | 127 | 5643 | C | FOREIGN INTERFERENCE | Repair 11kV lines between J3714 & J3715 Horera
12560 | 11/09/2008 | 2008-09-11 | 2008 | 347 | 4 | 1388 | B | PLANNED SHUTDOWN | Replace 11kV poles G1014 & G1021 Sheltons Rd Tolaga
12569 | 11/09/2008 | 2008-09-11 | 2008 | 235 | 177 | 41595 | B | PLANNED SHUTDOWN | Replace 11kV ABS B211 Fox St
12553 | 12/09/2008 | 2008-09-12 | 2008 | 128 | 734 | 24976 | C | FOREIGN INTERFERENCE | Repair 11kV jumpers on pole C5014 & Replace pole C5048 SH2 Makaraka
12564 | 12/09/2008 | 2008-09-12 | 2008 | 277 | 16 | 4432 | B | PLANNED SHUTDOWN | Change Xarms on pole G1009 Sheltons Rd Tolaga
12561 | 15/09/2008 | 2008-09-15 | 2008 | 300 | 4 | 1200 | B | PLANNED SHUTDOWN | Replace 11kV poles G1026 & G1027 Sheltons Rd Tolaga
12562 | 16/09/2008 | 2008-09-16 | 2008 | 234 | 16 | 1496 | B | PLANNED SHUTDOWN | Remove temp fuses pole G1009 Wharf Rd Tolaga
12567 | 22/09/2008 | 2008-09-22 | 2008 | 270 | 14 | 3780 | B | PLANNED SHUTDOWN | Relocate 11kV pole J967 Waiomatatini
12558 | 23/09/2008 | 2008-09-23 | 2008 | 30 | 30 | 900 | B | PLANNED SHUTDOWN | Cut & turn 11kV cable into Gas switch B1428 Disralie St
12559 | 24/09/2008 | 2008-09-24 | 2008 | 37 | 30 | 1110 | B | PLANNED SHUTDOWN | Connect 11kV jumpers at pole B3701 Disralie St
12563 | 24/09/2008 | 2008-09-24 | 2008 | 90 | 56 | 5040 | B | PLANNED SHUTDOWN | Install DDOs on pole C3233 in Cameron Rd
12571 | 25/09/2008 | 2008-09-25 | 2008 | 285 | 73 | 20805 | B | PLANNED SHUTDOWN | Change 11kV ABS C199 Bloomfeild Rd Matawhero
12555 | 29/09/2008 | 2008-09-29 | 2008 | 248 | 92 | 11800 | C | TREE CONTACTS | Remove branch from 11kV lines at pole J2411 Te Hue
12565 | 30/09/2008 | 2008-09-30 | 2008 | 352 | 17 | 5984 | B | PLANNED SHUTDOWN | Replace 11kV poles W8833 W8834 W8650 & W8654 Kokohu
12566 | 30/09/2008 | 2008-09-30 | 2008 | 45 | 23 | 1035 | B | PLANNED SHUTDOWN | Install & remove Line breaks at pole W8655 Kokohu
12568 | 30/09/2008 | 2008-09-30 | 2008 | 80 | 5 | 400 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting E3993 Ceasars Rd
12573 | 02/10/2008 | 2008-10-02 | 2008 | 157 | 4 | 628 | C | FOREIGN INTERFERENCE | Replace Xarm on pole H627 Arero Rd Tokomaru Bay
12574 | 02/10/2008 | 2008-10-02 | 2008 | 383 | 142 | 36845 | C | TREE CONTACTS | Repair 11kV between D3874 & D3875 Tiniroto Rd
12621 | 03/10/2008 | 2008-10-03 | 2008 | 71 | 54 | 3834 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Lavenham Rd
12622 | 03/10/2008 | 2008-10-03 | 2008 | 60 | 9 | 540 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Kirkpatrick Rd
12575 | 04/10/2008 | 2008-10-04 | 2008 | 63 | 733 | 24778 | C | ADVERSE WEATHER | Repair 11kV at pole W4255 Mangapoikie Valley
12576 | 07/10/2008 | 2008-10-07 | 2008 | 1493 | 174 | 262461 | C | ADVERSE WEATHER | Reclose CB 24 Tuai High winds conductor clashes
12578 | 07/10/2008 | 2008-10-07 | 2008 | 99 | 11 | 1089 | C | ADVERSE ENVIRONMENT | Repair 11kV line at pole W1234 in Tawhara Valley
12579 | 07/10/2008 | 2008-10-07 | 2008 | 440 | 230 | 34028 | C | ADVERSE WEATHER | Repair numerious 11kV faults due to high winds Raupunga to Putere
12580 | 07/10/2008 | 2008-10-07 | 2008 | 940 | 92 | 7315 | C | ADVERSE WEATHER | Repair 11kV jumpers on ABS pole J396 Te Hue Rd
12581 | 07/10/2008 | 2008-10-07 | 2008 | 132 | 123 | 14178 | C | TREE CONTACTS | Remove trees from 11kV near Huriharama
12583 | 07/10/2008 | 2008-10-07 | 2008 | 187 | 418 | 19898 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole D1672 Lavenham Rd
12584 | 07/10/2008 | 2008-10-07 | 2008 | 165 | 93 | 17745 | C | TREE CONTACTS | Repair 11kV lines at pole E221 Tarndale Rd
12585 | 07/10/2008 | 2008-10-07 | 2008 | 45 | 9 | 405 | C | ADVERSE WEATHER | Untwist 11kV lines at pole H188 Ihungia Rd
12586 | 07/10/2008 | 2008-10-07 | 2008 | 1110 | 89 | 70229 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole G1413 Anaura Bay
12587 | 07/10/2008 | 2008-10-07 | 2008 | 161 | 734 | 36974 | C | ADVERSE WEATHER | Repair 11kV lines opp Pilmers Rd
12588 | 07/10/2008 | 2008-10-07 | 2008 | 494 | 123 | 24375 | C | ADVERSE WEATHER | Repair 11kV lines at pole H1666 Makarika
12589 | 07/10/2008 | 2008-10-07 | 2008 | 1610 | 63 | 51100 | C | ADVERSE WEATHER | Replace 11kV pole D5183 at Tahora
12590 | 07/10/2008 | 2008-10-07 | 2008 | 192 | 438 | 24143 | C | ADVERSE WEATHER | Repair 11kV lines beyond F185 Matawai
12617 | 07/10/2008 | 2008-10-07 | 2008 | 72 | 178 | 12816 | B | PLANNED SHUTDOWN | Replace oil Switch B347 Abbott St
12591 | 08/10/2008 | 2008-10-08 | 2008 | 120 | 11 | 1870 | C | TREE CONTACTS | Remove tree from 11kV W5126 Mangataniwha
12592 | 08/10/2008 | 2008-10-08 | 2008 | 116 | 14 | 1624 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W381 Tangiwai Stn
12593 | 08/10/2008 | 2008-10-08 | 2008 | 74 | 15 | 2010 | C | ADVERSE WEATHER | Replace 11kV pole J333 Kopuponamu Rd
12595 | 08/10/2008 | 2008-10-08 | 2008 | 77 | 47 | 3619 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole D70 Totangi Rd
12596 | 08/10/2008 | 2008-10-08 | 2008 | 121 | 25 | 3025 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole D4002 Totangi Rd
12597 | 08/10/2008 | 2008-10-08 | 2008 | 245 | 25 | 6125 | C | ADVERSE WEATHER | Replace 11kV pole D713 Brunton Rd
12618 | 08/10/2008 | 2008-10-08 | 2008 | 253 | 99 | 25047 | B | PLANNED SHUTDOWN | Replace Oil switch B1419 Abbott St
12619 | 08/10/2008 | 2008-10-08 | 2008 | 22 | 79 | 1738 | B | PLANNED SHUTDOWN | Replace oil switch B1420 Abbott St
12620 | 08/10/2008 | 2008-10-08 | 2008 | 30 | 178 | 5340 | B | PLANNED SHUTDOWN | Replace oil switch B1431 Abbott St
12623 | 08/10/2008 | 2008-10-08 | 2008 | 495 | 4 | 1980 | B | PLANNED SHUTDOWN | Replace 11kV pole J3010 Whakaangiangi Rd
12635 | 08/10/2008 | 2008-10-08 | 2008 | 55 | 29 | 1595 | B | PLANNED SHUTDOWN | Replace 11kV pole J3010 Whakaangiangi Rd
12598 | 09/10/2008 | 2008-10-09 | 2008 | 177 | 10 | 1770 | C | ADVERSE WEATHER | Replace 11kV pole D713 Brunton Rd
12599 | 09/10/2008 | 2008-10-09 | 2008 | 58 | 6 | 348 | C | DEFECTIVE EQUIPMENT | Replace faulty T/x F343 Puha
12600 | 09/10/2008 | 2008-10-09 | 2008 | 34 | 13 | 442 | C | ADVERSE WEATHER | Repair 11kV lines at pole F4824 Tahora
12601 | 09/10/2008 | 2008-10-09 | 2008 | 82 | 28 | 2296 | C | ADVERSE WEATHER | Repair 11kV lines pole F651 Shaws Rd
12602 | 09/10/2008 | 2008-10-09 | 2008 | 166 | 3 | 498 | C | ADVERSE WEATHER | Replace 11kV pole D3765 Bushy Knoll
12603 | 09/10/2008 | 2008-10-09 | 2008 | 28 | 54 | 1512 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole D1672 Lavenham Rd
12604 | 09/10/2008 | 2008-10-09 | 2008 | 3004 | 9 | 27036 | C | TREE CONTACTS | Repair 11kV lines pole E221 Tanrdale Rd
12606 | 10/10/2008 | 2008-10-10 | 2008 | 19 | 53 | 1007 | C | ADVERSE WEATHER | Replace 11kV Xarm on pole D4189 Kirkpatrick Rd
12607 | 13/10/2008 | 2008-10-13 | 2008 | 97 | 642 | 62274 | C | DEFECTIVE EQUIPMENT | Replace 11kV jumper on ABS W909 Station Rd
12608 | 14/10/2008 | 2008-10-14 | 2008 | 175 | 20 | 3500 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole D1080 Parakanapa Rd
12609 | 15/10/2008 | 2008-10-15 | 2008 | 89 | 51 | 4539 | C | DEFECTIVE EQUIPMENT | Replace strain insulator on pole H1948 Waipiro Bay
12624 | 15/10/2008 | 2008-10-15 | 2008 | 285 | 54 | 15390 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Waipiro Bay Rd
12610 | 16/10/2008 | 2008-10-16 | 2008 | 18 | 1297 | 23346 | C | TREE CONTACTS | Remove tree from 11kV pole C392 Nelson Rd
12611 | 17/10/2008 | 2008-10-17 | 2008 | 116 | 77 | 8024 | C | LIGHTNING | Repair 11kV between poles W6611 to W1747 Mangapoike Rd
12612 | 17/10/2008 | 2008-10-17 | 2008 | 134 | 16 | 2144 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole G1083 Sheltons Rd
12629 | 17/10/2008 | 2008-10-17 | 2008 | 114 | 22 | 2508 | B | PLANNED SHUTDOWN | Replace 11kV pole J5000 East Cape Rd
12614 | 21/10/2008 | 2008-10-21 | 2008 | 22 | 63 | 1386 | C | UNKNOWN | Reclose D141 cause unknown
12625 | 22/10/2008 | 2008-10-22 | 2008 | 80 | 9 | 720 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Beach Rd Rangitukia
12626 | 22/10/2008 | 2008-10-22 | 2008 | 102 | 24 | 2448 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Mc Neil Rd
12627 | 22/10/2008 | 2008-10-22 | 2008 | 60 | 41 | 2460 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Tapuaeroa Rd
12628 | 23/10/2008 | 2008-10-23 | 2008 | 120 | 5 | 600 | B | PLANNED SHUTDOWN | Replace T/x G55 Waiapu Rd
12615 | 24/10/2008 | 2008-10-24 | 2008 | 179 | 69 | 5276 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H4487 Waitahaia Rd
12630 | 28/10/2008 | 2008-10-28 | 2008 | 283 | 99 | 28017 | B | PLANNED SHUTDOWN | Replace 11kV T/x B347 Abbott St
12631 | 28/10/2008 | 2008-10-28 | 2008 | 217 | 23 | 4991 | B | PLANNED SHUTDOWN | Replace 11kV pole D2031 Repongare Rd
12616 | 29/10/2008 | 2008-10-29 | 2008 | 30 | 85 | 2250 | C | DEFECTIVE EQUIPMENT | Top up oil in T/x A233 Cambridge Trc
12632 | 31/10/2008 | 2008-10-31 | 2008 | 268 | 6 | 1608 | B | PLANNED SHUTDOWN | Replace 11kV pole D1974 Renners Rd
12636 | 01/11/2008 | 2008-11-01 | 2008 | 36 | 40 | 1440 | C | TREE CONTACTS | Remove tree branch from 11kV pole W6842
12637 | 01/11/2008 | 2008-11-01 | 2008 | 803 | 389 | 27325 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole F741 Matawai
12638 | 01/11/2008 | 2008-11-01 | 2008 | 128 | 93 | 11252 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarm on pole D3350 Tiniroto
12639 | 03/11/2008 | 2008-11-03 | 2008 | 31 | 812 | 14508 | C | UNKNOWN | Restart Generator1 & reclose CB Te Araroa Sub cause unknown
12640 | 05/11/2008 | 2008-11-05 | 2008 | 10 | 76 | 678 | C | UNKNOWN | Reclose CB H341 Mata Rd cause unknown
12641 | 06/11/2008 | 2008-11-06 | 2008 | 93 | 900 | 8245 | C | UNKNOWN | Restart Generator 5 & close CB cause unknown
12642 | 07/11/2008 | 2008-11-07 | 2008 | 92 | 734 | 8542 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between poles C5039 & C5040 SH2 Makaraka
12643 | 09/11/2008 | 2008-11-09 | 2008 | 383 | 833 | 175720 | C | FOREIGN INTERFERENCE | Replace 11kV pole W3613 Mahia hit by Car
12647 | 10/11/2008 | 2008-11-10 | 2008 | 24 | 26 | 1196 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at ple D4002 Wharekopae Rd
12653 | 10/11/2008 | 2008-11-10 | 2008 | 282 | 24 | 2253 | B | PLANNED SHUTDOWN | Replace 11kV pole D1926 Wharekopae Rd
12644 | 12/11/2008 | 2008-11-12 | 2008 | 508 | 187 | 49036 | C | FOREIGN INTERFERENCE | Repair 11kV lines River Xing pole E613 Kanakanaia
12654 | 13/11/2008 | 2008-11-13 | 2008 | 420 | 21 | 819 | B | PLANNED SHUTDOWN | Replace 2 11kV poles D41 & D1894 Lavenham Rd
12655 | 17/11/2008 | 2008-11-17 | 2008 | 282 | 21 | 1329 | B | PLANNED SHUTDOWN | Replace 3 11kV poles D1887, D1881, & D1873 Lavenham Rd
12648 | 18/11/2008 | 2008-11-18 | 2008 | 315 | 24 | 7560 | B | PLANNED SHUTDOWN | Change T/x W1571 Chambelin Ave
12652 | 18/11/2008 | 2008-11-18 | 2008 | 19 | 180 | 3420 | B | PLANNED SHUTDOWN | Connect 2 DDO fuses for new T/X E1992 Whatatutu Rd
12645 | 19/11/2008 | 2008-11-19 | 2008 | 345 | 92 | 17870 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between poles J2227 to J2229 Kopuponamu Rd
12650 | 19/11/2008 | 2008-11-19 | 2008 | 284 | 37 | 10508 | B | PLANNED SHUTDOWN | Change T/x W1554 Kowhai Plc
12651 | 20/11/2008 | 2008-11-20 | 2008 | 188 | 5 | 940 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Uttings Rd Waimata
12657 | 21/11/2008 | 2008-11-21 | 2008 | 180 | 26 | 4680 | B | PLANNED SHUTDOWN | Replace 11kV pole F1257 Matawai Rd
12660 | 21/11/2008 | 2008-11-21 | 2008 | 396 | 13 | 5148 | B | PLANNED SHUTDOWN | Replace 11kV pole D3071 Lavenham Rd
12662 | 22/11/2008 | 2008-11-22 | 2008 | 180 | 8 | 1920 | B | PLANNED SHUTDOWN | Replace 11kV Sw/Gr A540, A541 & A542 Port Cool Store
12646 | 24/11/2008 | 2008-11-24 | 2008 | 131 | 172 | 6795 | C | ADVERSE WEATHER | Untwist 11kV lines at pole W5285 Kakariki Rd
12658 | 25/11/2008 | 2008-11-25 | 2008 | 24 | 234 | 2331 | B | PLANNED SHUTDOWN | Replace 11kV pole A4109 Ranfurly Rd
12661 | 25/11/2008 | 2008-11-25 | 2008 | 289 | 32 | 8954 | B | PLANNED SHUTDOWN | Replace 2 T/xs W448 & W564 Lake Waikaremoana
12656 | 27/11/2008 | 2008-11-27 | 2008 | 179 | 173 | 30967 | B | PLANNED SHUTDOWN | Replace oil in Sws A287, A288, A290, A314, A315, A316, A133, A111, & A130 Tyndall Rd
12659 | 27/11/2008 | 2008-11-27 | 2008 | 26 | 223 | 6230 | B | PLANNED SHUTDOWN | Replace 11kV poles A3206 & A3207 Ranfurly Rd
12664 | 27/11/2008 | 2008-11-27 | 2008 | 240 | 9 | 2160 | B | PLANNED SHUTDOWN | Replace T/x C378 Bck Ormond Rd
12676 | 01/12/2008 | 2008-12-01 | 2008 | 300 | 3 | 900 | B | PLANNED SHUTDOWN | Replace T/x C3218 Hansen Rd
12665 | 03/12/2008 | 2008-12-03 | 2008 | 81 | 254 | 7834 | C | DEFECTIVE EQUIPMENT | Isolate 11kV cable Oil switch B697 Anzac St
12675 | 03/12/2008 | 2008-12-03 | 2008 | 434 | 47 | 20398 | B | PLANNED SHUTDOWN | Replace T/x B515 Totara St
12677 | 03/12/2008 | 2008-12-03 | 2008 | 220 | 143 | 30650 | B | PLANNED SHUTDOWN | Isolate 11kV lines for 50kV work to replace 3 poles G2779 G2791 & G2792 Mangatuna
12678 | 03/12/2008 | 2008-12-03 | 2008 | 315 | 27 | 18123 | B | PLANNED SHUTDOWN | Replace 11 11kV poles Wharekopae Rd
12680 | 05/12/2008 | 2008-12-05 | 2008 | 83 | 219 | 13697 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole A3210 Cambridge Trce
12666 | 06/12/2008 | 2008-12-06 | 2008 | 0 | 2512 | 59712 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
12667 | 08/12/2008 | 2008-12-08 | 2008 | 213 | 120 | 17304 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole J2206 Maraehara Rd
12674 | 08/12/2008 | 2008-12-08 | 2008 | 300 | 313 | 76830 | B | PLANNED SHUTDOWN | Replace 11kV pole W3607 Mahia
12679 | 08/12/2008 | 2008-12-08 | 2008 | 344 | 48 | 5758 | B | PLANNED SHUTDOWN | Replace 3 11kV poles Bruntons Rd D1815 D1814 & D721
12681 | 09/12/2008 | 2008-12-09 | 2008 | 66 | 9 | 594 | B | PLANNED SHUTDOWN | Replace T/x D394 Humphries Rd
12688 | 09/12/2008 | 2008-12-09 | 2008 | 370 | 6 | 2220 | B | PLANNED SHUTDOWN | Replace 3 11kV poles D1327 D1332 & D1333 Tiniroto Rd
12690 | 09/12/2008 | 2008-12-09 | 2008 | 159 | 25 | 9618 | B | PLANNED SHUTDOWN | Replace 7 11kV poles Coopers Rd & Pipiwhako Rd D1353 D1344 D1602 D1607 D4219 D1614 & D1627
12689 | 10/12/2008 | 2008-12-10 | 2008 | 238 | 27 | 6426 | B | PLANNED SHUTDOWN | Replace 3 11kV poles D1387 D167 & D1521 Tiniroto Rd
12668 | 11/12/2008 | 2008-12-11 | 2008 | 59 | 23 | 1357 | C | FOREIGN INTERFERENCE | Replace Xarm on pole C3622 Waingake Rd
12692 | 15/12/2008 | 2008-12-15 | 2008 | 28 | 20 | 560 | B | PLANNED SHUTDOWN | Temp repair 11kV pole C3397 Awapuni Rd
12669 | 16/12/2008 | 2008-12-16 | 2008 | 21 | 14 | 294 | C | TREE CONTACTS | Untwist 11kV lines at pole D3743 Bushy Knoll Rd
12682 | 16/12/2008 | 2008-12-16 | 2008 | 34 | 219 | 7446 | B | PLANNED SHUTDOWN | Install 11kV links pole A6477 Crawford Rd
12683 | 16/12/2008 | 2008-12-16 | 2008 | 120 | 12 | 1440 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting D3519 Tiniroto
12684 | 16/12/2008 | 2008-12-16 | 2008 | 98 | 32 | 3136 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting D3602 Ruakaka Rd
12685 | 16/12/2008 | 2008-12-16 | 2008 | 93 | 49 | 4557 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting D3305 Awapapa Stn Tiniroto Rd
12691 | 16/12/2008 | 2008-12-16 | 2008 | 23 | 33 | 1221 | B | PLANNED SHUTDOWN | Replace 11kV pole J2206 Maraehara Rd
12686 | 19/12/2008 | 2008-12-19 | 2008 | 200 | 46 | 9200 | B | PLANNED SHUTDOWN | Replace 11kV pole G1458 Anaura Bay Rd
12687 | 20/12/2008 | 2008-12-20 | 2008 | 124 | 34 | 4216 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting C2201 Matawai Rd
12670 | 22/12/2008 | 2008-12-22 | 2008 | 8 | 173 | 1384 | C | UNKNOWN | Reclose CB A283 at Tatapouri cause unknown
12671 | 25/12/2008 | 2008-12-25 | 2008 | 240 | 654 | 32373 | C | TREE CONTACTS | Repair 11kV lines between poles A777 & A778 Rototahi
12672 | 30/12/2008 | 2008-12-30 | 2008 | 46 | 1152 | 28737 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole W3087 Mc lean St
12673 | 30/12/2008 | 2008-12-30 | 2008 | 38 | 23 | 874 | C | TREE CONTACTS | Repair 11kV lines at pole A778 Rototahi
12693 | 02/01/2009 | 2009-01-02 | 2008 | 287 | 207 | 16443 | C | FOREIGN INTERFERENCE | Replace 11kV pole E2068 Waihirere
12694 | 05/01/2009 | 2009-01-05 | 2008 | 388 | 40 | 15520 | C | TREE CONTACTS | Repair 11kV lines at pole J2024 Tapuwharoa Rd
12703 | 05/01/2009 | 2009-01-05 | 2008 | 28 | 131 | 6943 | B | PLANNED SHUTDOWN | Replace 6 11kV poles Wainui Rd A2056 A2055 A2050 A2048 A2045 & A2044
12696 | 06/01/2009 | 2009-01-06 | 2008 | 154 | 11 | 1694 | C | DEFECTIVE EQUIPMENT | Replace Xarms on pole F1740 Davis Rd
12695 | 07/01/2009 | 2009-01-07 | 2008 | 259 | 33 | 4719 | C | HUMAN ELEMENT | Repair 11kV lines between poles D1135 & D1128 Parakanapa Stn Wire thrown over 11kV
12697 | 08/01/2009 | 2009-01-08 | 2008 | 467 | 229 | 22515 | C | FOREIGN INTERFERENCE | Replace 11kV pole C3606 Waingake Rd
12698 | 08/01/2009 | 2009-01-08 | 2008 | 57 | 169 | 3727 | C | HUMAN ELEMENT | Repair 11kV line at pole C3604 Waingake Rd
12699 | 11/01/2009 | 2009-01-11 | 2008 | 1163 | 72 | 30870 | C | TREE CONTACTS | Untwist 11kV lines between poles A4033 & A4034 Waiomoko Rd
12700 | 11/01/2009 | 2009-01-11 | 2008 | 7 | 80 | 560 | C | TREE CONTACTS | Remove trees from 11kV lines pole W4463 Ohuka Rd
12701 | 12/01/2009 | 2009-01-12 | 2008 | 78 | 9 | 702 | C | DEFECTIVE EQUIPMENT | Re-sag 11kV lines pole D630 Seddon St Patutahi
12702 | 17/01/2009 | 2009-01-17 | 2008 | 114 | 1085 | 49604 | C | UNKNOWN | Reclose Inc 1 F411 at Puha Sub cause unknown
12706 | 23/01/2009 | 2009-01-23 | 2008 | 98 | 6 | 588 | B | PLANNED SHUTDOWN | Replace 11kV pole D1477 Knights Rd Patutahi
12707 | 23/01/2009 | 2009-01-23 | 2008 | 140 | 5 | 700 | B | PLANNED SHUTDOWN | Replace 11kV pole D1941 Judds Rd Patutahi
12704 | 27/01/2009 | 2009-01-27 | 2008 | 54 | 44 | 3916 | B | PLANNED SHUTDOWN | Isolate 11kV lines for Tree cutting Tiniroto Rd
12708 | 27/01/2009 | 2009-01-27 | 2008 | 365 | 10 | 7070 | B | PLANNED SHUTDOWN | Replace 5 11kV poles Humphries Rd D3018 D398 D3019 D3012 & D3022
12705 | 28/01/2009 | 2009-01-28 | 2008 | 408 | 6 | 2448 | B | PLANNED SHUTDOWN | Replace 3 11kV poles A2401 A2402 & A2403 Sponge Bay Rd
12709 | 01/02/2009 | 2009-02-01 | 2008 | 226 | 634 | 13854 | C | ADVERSE ENVIRONMENT | Isolate 11kV for fire fighting Mahia
12710 | 01/02/2009 | 2009-02-01 | 2008 | 235 | 13 | 3455 | C | ADVERSE ENVIRONMENT | Isolate 11kV lines for Fire Fighting Glen Roy Rd
12711 | 02/02/2009 | 2009-02-02 | 2008 | 264 | 156 | 25184 | C | TREE CONTACTS | Repair 11kV Lines between G2059 & G2063 Doonholm Hill
12727 | 03/02/2009 | 2009-02-03 | 2008 | 280 | 23 | 6440 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting SH35 Rototahi
12712 | 04/02/2009 | 2009-02-04 | 2008 | 83 | 8 | 664 | C | TREE CONTACTS | Isolate 11kV for tree cutting Hikuwai Arero
12725 | 04/02/2009 | 2009-02-04 | 2008 | 53 | 24 | 1272 | B | PLANNED SHUTDOWN | Relocate 2 11kV poles A2323 & A56 Sponge Bay Rd
12713 | 05/02/2009 | 2009-02-05 | 2008 | 45 | 4496 | 103993 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole W1031Kiwi Sub
12728 | 05/02/2009 | 2009-02-05 | 2008 | 80 | 29 | 2320 | B | PLANNED SHUTDOWN | Erect new Xarms & T/x fuses on pole E2425 Ormond Valley Rd
12714 | 08/02/2009 | 2009-02-08 | 2008 | 238 | 20 | 4392 | C | ADVERSE ENVIRONMENT | Isolate 11kV lines for fire fighting B9 hill Tikitiki
12715 | 09/02/2009 | 2009-02-09 | 2008 | 33 | 87 | 2646 | C | UNKNOWN | Reclose E864 Waimata cause unknown
12716 | 09/02/2009 | 2009-02-09 | 2008 | 65 | 9 | 585 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Hihiroroa Rd Otoko
12730 | 09/02/2009 | 2009-02-09 | 2008 | 30 | 76 | 2280 | B | PLANNED SHUTDOWN | Install line breaks at pole E2056 SH2 W /O Hika
12717 | 10/02/2009 | 2009-02-10 | 2008 | 65 | 311 | 20215 | C | DEFECTIVE EQUIPMENT | Power off due to Generator Trip would not restart restored to grid
12726 | 11/02/2009 | 2009-02-11 | 2008 | 456 | 6 | 2736 | B | PLANNED SHUTDOWN | Replace 11kV pole A56 Sponge Bay Rd
12739 | 11/02/2009 | 2009-02-11 | 2008 | 144 | 32 | 4608 | B | PLANNED SHUTDOWN | Replace 11kV pole W9712 Y M C A Rd Mahia
12718 | 12/02/2009 | 2009-02-12 | 2008 | 0 | 283 | 14666 | C | FOREIGN INTERFERENCE | Repair 11 kV lines pole B322 Awapuni Rd (Truck hit pole)
12732 | 12/02/2009 | 2009-02-12 | 2008 | 115 | 28 | 3220 | B | PLANNED SHUTDOWN | Replace 2 11kV poles E236 & E826 Mangamaia Rd
12733 | 12/02/2009 | 2009-02-12 | 2008 | 56 | 11 | 616 | B | PLANNED SHUTDOWN | Install DDO fuses on pole F1754 Olivers Rd
12719 | 13/02/2009 | 2009-02-13 | 2008 | 119 | 797 | 63808 | C | DEFECTIVE EQUIPMENT | Replace insulator on pole A245 Endcliffe Rd
12731 | 13/02/2009 | 2009-02-13 | 2008 | 50 | 76 | 3800 | B | PLANNED SHUTDOWN | Remove line breaks pole E2056 SH2 W /O Hika
12735 | 13/02/2009 | 2009-02-13 | 2008 | 360 | 9 | 3240 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Hihiroroa Rd Otoko end
12720 | 14/02/2009 | 2009-02-14 | 2008 | 28 | 145 | 4060 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole W1207 Mahunga Mahia
12734 | 14/02/2009 | 2009-02-14 | 2008 | 106 | 11 | 1166 | B | PLANNED SHUTDOWN | Replace T/x B605 Lowe St with 500KVA T/x
12729 | 16/02/2009 | 2009-02-16 | 2008 | 435 | 159 | 63052 | B | PLANNED SHUTDOWN | Install new Sub Station Ngatapa
12740 | 17/02/2009 | 2009-02-17 | 2008 | 418 | 10 | 14860 | B | PLANNED SHUTDOWN | Replace 8 11kV poles Goodwins Rd over 4 Days
12736 | 18/02/2009 | 2009-02-18 | 2008 | 394 | 8 | 3152 | B | PLANNED SHUTDOWN | Replace 11kV Disc on pole H540 Hikuwai
12743 | 18/02/2009 | 2009-02-18 | 2008 | 102 | 11 | 1122 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at pole F74 Olivers Rd for pipe laying
12745 | 19/02/2009 | 2009-02-19 | 2008 | 154 | 37 | 5698 | B | PLANNED SHUTDOWN | Isolate 11kV for Tree cutting Tapuaeroa Rd
12721 | 23/02/2009 | 2009-02-23 | 2008 | 11 | 31 | 341 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A3991 Waiomoko Rd
12737 | 23/02/2009 | 2009-02-23 | 2008 | 361 | 10 | 3610 | B | PLANNED SHUTDOWN | Isolate 11kV for 50kV pole Replacements Mangatuna
12742 | 23/02/2009 | 2009-02-23 | 2008 | 464 | 30 | 13920 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting Tahunga Rd
12746 | 23/02/2009 | 2009-02-23 | 2008 | 117 | 10 | 1170 | B | PLANNED SHUTDOWN | Replace 11kV pole A4326 Goodwins Rd
12722 | 24/02/2009 | 2009-02-24 | 2008 | 79 | 13 | 1027 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole W62879 Cricklewood Rd
12738 | 24/02/2009 | 2009-02-24 | 2008 | 225 | 12 | 2700 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Ohuka Rd
12741 | 24/02/2009 | 2009-02-24 | 2008 | 180 | 7 | 1260 | B | PLANNED SHUTDOWN | Replace 2 11kV poles Riverside Rd A4240 & A4243
12723 | 25/02/2009 | 2009-02-25 | 2008 | 1169 | 172 | 19221 | C | TREE CONTACTS | Replace 11kV pole H2301 Te Puia
12744 | 25/02/2009 | 2009-02-25 | 2008 | 188 | 10 | 1880 | B | PLANNED SHUTDOWN | Replace 11kV pole A547 Goodwins Rd
12724 | 28/02/2009 | 2009-02-28 | 2008 | 159 | 56 | 4105 | B | PLANNED SHUTDOWN | Remove tree from 11kV lines pole C858 Paparatu Rd
12747 | 01/03/2009 | 2009-03-01 | 2008 | 166 | 92 | 4107 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between J2227 & J2229 Kopuponamu Valley
12748 | 02/03/2009 | 2009-03-02 | 2008 | 203 | 222 | 24315 | C | FOREIGN INTERFERENCE | Replace 11kV pole E2097 SH 2 Ormond
12749 | 02/03/2009 | 2009-03-02 | 2008 | 41 | 434 | 17794 | C | UNKNOWN | Reclose CB1 on Generator 2 at Ruatoria
12750 | 02/03/2009 | 2009-03-02 | 2008 | 24 | 418 | 10032 | C | UNKNOWN | Reclose CB D646 Bushmere at Patutahi Sub cause unknown
12751 | 02/03/2009 | 2009-03-02 | 2008 | 11 | 399 | 4389 | C | UNKNOWN | Reclose CB D644 Muriwai cause unknown
12752 | 02/03/2009 | 2009-03-02 | 2008 | 60 | 222 | 13320 | C | ADVERSE WEATHER | Relocate 11kV pole J4028 Hicks Bay
12768 | 02/03/2009 | 2009-03-02 | 2008 | 93 | 23 | 2139 | B | PLANNED SHUTDOWN | To cut jumpers at pole A800 & A803 SH35 Rototahi
12753 | 03/03/2009 | 2009-03-03 | 2008 | 263 | 168 | 12364 | C | TREE CONTACTS | Repair 11kV lines D3446 to D3447 Taumata Rd
12787 | 03/03/2009 | 2009-03-03 | 2008 | 334 | 21 | 5993 | B | PLANNED SHUTDOWN | Cut 11kV jumpers pole D2088 Lavenham Rd
12788 | 04/03/2009 | 2009-03-04 | 2008 | 317 | 17 | 5389 | B | PLANNED SHUTDOWN | Replace 2 11kV poles D2088 & D361 Lavenham Rd
12790 | 04/03/2009 | 2009-03-04 | 2008 | 136 | 4 | 544 | B | PLANNED SHUTDOWN | Replace 11kV pole D2083 Lavenham Rd
12754 | 05/03/2009 | 2009-03-05 | 2008 | 101 | 33 | 3333 | C | TREE CONTACTS | Repair 11kV between poles E1067 to E1068 Kanakanaia Rd
12755 | 05/03/2009 | 2009-03-05 | 2008 | 22 | 283 | 6226 | C | HUMAN ELEMENT | Close ABS B206 in Fox St
12767 | 05/03/2009 | 2009-03-05 | 2008 | 54 | 38 | 2052 | B | PLANNED SHUTDOWN | Replace 11kV pole A4309 Goodwins Rd
12769 | 05/03/2009 | 2009-03-05 | 2008 | 88 | 10 | 880 | B | PLANNED SHUTDOWN | Replace 11kV pole A4080 Darwin Rd
12772 | 05/03/2009 | 2009-03-05 | 2008 | 403 | 53 | 21359 | B | PLANNED SHUTDOWN | Install new T/x W309 Karaka St
12773 | 05/03/2009 | 2009-03-05 | 2008 | 38 | 26 | 988 | B | PLANNED SHUTDOWN | Phase out across Gas Switch W245 & W247 Kitchener St
12789 | 05/03/2009 | 2009-03-05 | 2008 | 362 | 4 | 1448 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers pole D2088 Lavenham Rd
12798 | 05/03/2009 | 2009-03-05 | 2008 | 59 | 12 | 708 | B | PLANNED SHUTDOWN | Repair 11kV lines at between poles C858 to C859 Paparatu Rd
12770 | 06/03/2009 | 2009-03-06 | 2008 | 17 | 72 | 1037 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at poles B2038 & B5008 Riverside Rd
12771 | 06/03/2009 | 2009-03-06 | 2008 | 267 | 61 | 16287 | B | PLANNED SHUTDOWN | Replace 2 11kV poles B2040 & B2041 Riverside Rd
12756 | 07/03/2009 | 2009-03-07 | 2008 | 110 | 11 | 1210 | C | DEFECTIVE EQUIPMENT | Repair 11kv cable B222 Waimata Cheese Riverside Rd
12757 | 09/03/2009 | 2009-03-09 | 2008 | 779 | 169 | 62009 | C | DEFECTIVE EQUIPMENT | Replace T/x D120 Rere
12758 | 10/03/2009 | 2009-03-10 | 2008 | 37 | 19 | 703 | C | TREE CONTACTS | Repair 11kV line pole W6209 Kiwi Valley
12775 | 10/03/2009 | 2009-03-10 | 2008 | 71 | 26 | 1846 | B | PLANNED SHUTDOWN | Cut 11kV jumpers on pole H2356 Te Puia
12776 | 10/03/2009 | 2009-03-10 | 2008 | 60 | 26 | 780 | B | PLANNED SHUTDOWN | Rejion 11kV jumper at poles H2357 & H2359 Te Puia
12802 | 10/03/2009 | 2009-03-10 | 2008 | 431 | 11 | 8877 | B | PLANNED SHUTDOWN | Replace 11kV poles F1754 to F328 Olivers Rd
12759 | 11/03/2009 | 2009-03-11 | 2008 | 396 | 89 | 11084 | C | TREE CONTACTS | Repair 11kV line H563 to H561 SH 35 Parenga Crn
12760 | 11/03/2009 | 2009-03-11 | 2008 | 242 | 359 | 15534 | C | FOREIGN INTERFERENCE | Replace 11kV pole E1465 Kaiteratahi
12783 | 11/03/2009 | 2009-03-11 | 2008 | 155 | 13 | 2015 | B | PLANNED SHUTDOWN | Replace 11kV pole A4063 Haache Rd
12784 | 11/03/2009 | 2009-03-11 | 2008 | 392 | 13 | 5096 | B | PLANNED SHUTDOWN | Replace T/x J275 to 50kVA Waione Rd
12785 | 11/03/2009 | 2009-03-11 | 2008 | 21 | 22 | 462 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole J3979 Waione Rd
12786 | 11/03/2009 | 2009-03-11 | 2008 | 15 | 22 | 330 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at pole J3979 Waione Rd
12777 | 16/03/2009 | 2009-03-16 | 2008 | 172 | 63 | 10836 | B | PLANNED SHUTDOWN | Install line breaks D4328 & D4318 SH2 W/O Hika
12761 | 17/03/2009 | 2009-03-17 | 2008 | 534 | 195 | 15454 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W8258 Whakakihi
12762 | 17/03/2009 | 2009-03-17 | 2008 | 192 | 141 | 8793 | C | DEFECTIVE EQUIPMENT | Replace insulator on pole A3970 Wharekiri Rd
12781 | 17/03/2009 | 2009-03-17 | 2008 | 15 | 51 | 765 | B | PLANNED SHUTDOWN | To Connect & Disconnect Generator Sunvale Cres T/X B175
12782 | 17/03/2009 | 2009-03-17 | 2008 | 279 | 126 | 35154 | B | PLANNED SHUTDOWN | Replace 2 11kV Poles B1280 & B1283 Fox St
12791 | 17/03/2009 | 2009-03-17 | 2008 | 240 | 24 | 5760 | B | PLANNED SHUTDOWN | Replace 6 11kV poles Between W733 to W807 Nuhaka
12779 | 18/03/2009 | 2009-03-18 | 2008 | 438 | 13 | 14157 | B | PLANNED SHUTDOWN | Replace 11kV poles D4325 D4322 D659 & D4324 SH2 W /O Hika
12780 | 18/03/2009 | 2009-03-18 | 2008 | 300 | 52 | 15600 | B | PLANNED SHUTDOWN | Replace H Pole F170 Makaretu Crn
12792 | 18/03/2009 | 2009-03-18 | 2008 | 261 | 43 | 11223 | B | PLANNED SHUTDOWN | Replace 9 11kV poles Between W7487 to W7533 Ruakituri Valley
12763 | 19/03/2009 | 2009-03-19 | 2008 | 5 | 861 | 4320 | C | HUMAN ELEMENT | Remove pole B2038 from 11kV lines Riverside Rd
12793 | 19/03/2009 | 2009-03-19 | 2008 | 252 | 58 | 14616 | B | PLANNED SHUTDOWN | Replace 7 11kV poles Upper Ruakituri Valley W7368 to W7458
12794 | 19/03/2009 | 2009-03-19 | 2008 | 100 | 32 | 3200 | B | PLANNED SHUTDOWN | Connect & Disconnect Generator Ruakituiri Valley W7358
12795 | 19/03/2009 | 2009-03-19 | 2008 | 335 | 71 | 23785 | B | PLANNED SHUTDOWN | Replace 2 11kV poles B2033 & B2038 Riverside Rd
12778 | 20/03/2009 | 2009-03-20 | 2008 | 33 | 76 | 2508 | B | PLANNED SHUTDOWN | Remove line breaks poles D4318 & D4328 SH2 W / O Hika
12774 | 22/03/2009 | 2009-03-22 | 2008 | 294 | 83 | 24568 | B | PLANNED SHUTDOWN | Install new Oil Switch B593 Roberts Rd
12799 | 24/03/2009 | 2009-03-24 | 2008 | 197 | 83 | 16351 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting J1396 to J1358 Harrison Rd
12800 | 24/03/2009 | 2009-03-24 | 2008 | 127 | 4 | 508 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting J88 Mangaharei St Ruatoria
12804 | 24/03/2009 | 2009-03-24 | 2008 | 39 | 72 | 4968 | B | PLANNED SHUTDOWN | Replace 11kV poles B2072 & B2074 Riverside Rd
12796 | 25/03/2009 | 2009-03-25 | 2008 | 281 | 37 | 10397 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting J1954 Tapuaero Rd
12805 | 25/03/2009 | 2009-03-25 | 2008 | 29 | 43 | 1247 | B | PLANNED SHUTDOWN | Install line breaks pole D1998 Lavenham Rd
12806 | 25/03/2009 | 2009-03-25 | 2008 | 42 | 43 | 1806 | B | PLANNED SHUTDOWN | To remove line breaks at pole D1998 Lavenham Rd
12807 | 25/03/2009 | 2009-03-25 | 2008 | 502 | 11 | 5522 | B | PLANNED SHUTDOWN | Replace 11kv poles between D1998 to D361 Lavenham Rd
12797 | 26/03/2009 | 2009-03-26 | 2008 | 227 | 8 | 1816 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Arero G4226 to G4225
12764 | 28/03/2009 | 2009-03-28 | 2008 | 164 | 97 | 1699 | C | UNKNOWN | Patrol 11kV lines Waimata Valley from Recloser E864
12765 | 30/03/2009 | 2009-03-30 | 2008 | 105 | 93 | 8725 | C | TREE CONTACTS | Remove tree from 11kV pole E804 Mangatu Stud Farm
12801 | 30/03/2009 | 2009-03-30 | 2008 | 236 | 7 | 1652 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting D489 to D3405 Taumata Rd
12766 | 31/03/2009 | 2009-03-31 | 2008 | 31 | 5076 | 81712 | C | DEFECTIVE EQUIPMENT | Repair 11kV line pole W6785 Frasertown Rd
12803 | 31/03/2009 | 2009-03-31 | 2008 | 178 | 18 | 3204 | B | PLANNED SHUTDOWN | Erect 11kV pole E1606 Manders Rd
12808 | 31/03/2009 | 2009-03-31 | 2008 | 191 | 96 | 18336 | B | PLANNED SHUTDOWN | Replace T/x A419 Murdouch St
34003612

## 1b-5 Year Daily Totals
[6 empty] | Average of ln() | -0.85907 | -5.313
[6 empty] | Std deviation of ln() | 1.5954 | 1.6648
[6 empty] | boundary value | 22.8581 | 0.3163
Date Outage | Year | TotAVG | Customers Impacted | Total Customer Minutes Lost | Saidi | Safi | LogSaidi | LogSaifi
01/04/2004 | 2004 | 24853 | 27 | 9423 | 0.37915 | 0.0010864 | -0.96982 | -6.8249 | 0.37915 | 0.0010864 | -0.96982 | -6.8249
02/04/2004 | 2004 | 24853 | 165 | 7382 | 0.29703 | 0.006639 | -1.2139 | -5.0148
08/04/2004 | 2004 | 24853 | 16 | 1561 | 0.062809 | 0.00064379 | -2.7677 | -7.3481
12/04/2004 | 2004 | 24853 | 217 | 10850 | 0.43657 | 0.0087313 | -0.82881 | -4.7408
13/04/2004 | 2004 | 24853 | 93 | 11460 | 0.46111 | 0.003742 | -0.77412 | -5.5881
15/04/2004 | 2004 | 24853 | 15 | 4675 | 0.18811 | 0.00060355 | -1.6707 | -7.4127
16/04/2004 | 2004 | 24853 | 4 | 720 | 0.02897 | 0.00016095 | -3.5415 | -8.7344
20/04/2004 | 2004 | 24853 | 164 | 26442 | 1.0639 | 0.0065988 | 0.061975 | -5.0209
21/04/2004 | 2004 | 24853 | 63 | 756 | 0.030419 | 0.0025349 | -3.4927 | -5.9776
26/04/2004 | 2004 | 24853 | 67 | 9380 | 0.37742 | 0.0026959 | -0.9744 | -5.916
29/04/2004 | 2004 | 24853 | 235 | 12552 | 0.50505 | 0.0094556 | -0.6831 | -4.6611
30/04/2004 | 2004 | 24853 | 4 | 1200 | 0.048284 | 0.00016095 | -3.0307 | -8.7344
03/05/2004 | 2004 | 24853 | 68 | 10208 | 0.41074 | 0.0027361 | -0.88981 | -5.9012
04/05/2004 | 2004 | 24853 | 38 | 4047 | 0.16284 | 0.001529 | -1.815 | -6.4831
05/05/2004 | 2004 | 24853 | 76 | 3078 | 0.12385 | 0.003058 | -2.0887 | -5.79
06/05/2004 | 2004 | 24853 | 46 | 16835 | 0.67738 | 0.0018509 | -0.38952 | -6.2921
07/05/2004 | 2004 | 24853 | 5 | 920 | 0.037018 | 0.00020118 | -3.2964 | -8.5113
08/05/2004 | 2004 | 24853 | 13 | 780 | 0.031385 | 0.00052308 | -3.4614 | -7.5558
10/05/2004 | 2004 | 24853 | 23 | 1629 | 0.065545 | 0.00092544 | -2.725 | -6.9852
12/05/2004 | 2004 | 24853 | 1508 | 7566 | 0.30443 | 0.060677 | -1.1893 | -2.8022
13/05/2004 | 2004 | 24853 | 754 | 14326 | 0.57643 | 0.030338 | -0.5509 | -3.4953
14/05/2004 | 2004 | 24853 | 771 | 58412 | 2.3503 | 0.031022 | 0.85454 | -3.473
16/05/2004 | 2004 | 24853 | 48 | 13776 | 0.5543 | 0.0019314 | -0.59005 | -6.2495
17/05/2004 | 2004 | 24853 | 587 | 98029 | 3.9444 | 0.023619 | 1.3723 | -3.7457
18/05/2004 | 2004 | 24853 | 10 | 300 | 0.012071 | 0.00040237 | -4.417 | -7.8181
20/05/2004 | 2004 | 24853 | 45 | 675 | 0.02716 | 0.0018106 | -3.606 | -6.3141
23/05/2004 | 2004 | 24853 | 60 | 3600 | 0.14485 | 0.0024142 | -1.932 | -6.0264
24/05/2004 | 2004 | 24853 | 176 | 27511 | 1.1069 | 0.0070816 | 0.10161 | -4.9502
27/05/2004 | 2004 | 24853 | 12 | 2760 | 0.11105 | 0.00048284 | -2.1977 | -7.6358
28/05/2004 | 2004 | 24853 | 273 | 9615 | 0.38687 | 0.010985 | -0.94965 | -4.5113
29/05/2004 | 2004 | 24853 | 1221 | 73166 | 2.944 | 0.049129 | 1.0798 | -3.0133
30/05/2004 | 2004 | 24853 | 70 | 12600 | 0.50698 | 0.0028166 | -0.67928 | -5.8722
31/05/2004 | 2004 | 24853 | 739 | 39237 | 1.5788 | 0.029735 | 0.45664 | -3.5154
01/06/2004 | 2004 | 24853 | 338 | 75343 | 3.0315 | 0.0136 | 1.1091 | -4.2977
02/06/2004 | 2004 | 24853 | 28 | 3220 | 0.12956 | 0.0011266 | -2.0436 | -6.7885
03/06/2004 | 2004 | 24853 | 281 | 21914 | 0.88174 | 0.011306 | -0.12585 | -4.4824
04/06/2004 | 2004 | 24853 | 161 | 19387 | 0.78007 | 0.0064781 | -0.24838 | -5.0393
08/06/2004 | 2004 | 24853 | 67 | 4868 | 0.19587 | 0.0026959 | -1.6303 | -5.916
10/06/2004 | 2004 | 24853 | 64 | 10823 | 0.43548 | 0.0025751 | -0.8313 | -5.9619
12/06/2004 | 2004 | 24853 | 262 | 24900 | 1.0019 | 0.010542 | 0.0018893 | -4.5524
13/06/2004 | 2004 | 24853 | 85 | 6507 | 0.26182 | 0.0034201 | -1.3401 | -5.6781
19/06/2004 | 2004 | 24853 | 102 | 19939 | 0.80228 | 0.0041041 | -0.2203 | -5.4958
22/06/2004 | 2004 | 24853 | 43 | 2881 | 0.11592 | 0.0017302 | -2.1548 | -6.3595
23/06/2004 | 2004 | 24853 | 50 | 9000 | 0.36213 | 0.0020118 | -1.0158 | -6.2087
24/06/2004 | 2004 | 24853 | 797 | 35237 | 1.4178 | 0.032069 | 0.34912 | -3.4399
28/06/2004 | 2004 | 24853 | 5227 | 326943 | 13.1551 | 0.21032 | 2.5768 | -1.5591
30/06/2004 | 2004 | 24853 | 4700 | 476478 | 19.1719 | 0.18911 | 2.9534 | -1.6654
01/07/2004 | 2004 | 24853 | 3388 | 798094 | 32.1126 | 0.13632 | 3.4692 | -1.9927
02/07/2004 | 2004 | 24853 | 164 | 39756 | 1.5996 | 0.0065988 | 0.46978 | -5.0209
03/07/2004 | 2004 | 24853 | 26 | 39120 | 1.5741 | 0.0010462 | 0.45366 | -6.8626
07/07/2004 | 2004 | 24853 | 26 | 2210 | 0.088923 | 0.0010462 | -2.42 | -6.8626
08/07/2004 | 2004 | 24853 | 46 | 2982 | 0.11999 | 0.0018509 | -2.1204 | -6.2921
13/07/2004 | 2004 | 24853 | 62 | 586 | 0.023579 | 0.0024947 | -3.7474 | -5.9936
15/07/2004 | 2004 | 24853 | 139 | 31157 | 1.2537 | 0.0055929 | 0.22606 | -5.1863
16/07/2004 | 2004 | 24853 | 5 | 200 | 0.0080473 | 0.00020118 | -4.8224 | -8.5113
17/07/2004 | 2004 | 24853 | 273 | 36505 | 1.4688 | 0.010985 | 0.38447 | -4.5113
18/07/2004 | 2004 | 24853 | 232 | 116989 | 4.7072 | 0.0093349 | 1.5491 | -4.674
20/07/2004 | 2004 | 24853 | 22 | 5079 | 0.20436 | 0.00088521 | -1.5879 | -7.0297
21/07/2004 | 2004 | 24853 | 24 | 1818 | 0.07315 | 0.00096568 | -2.6152 | -6.9427
23/07/2004 | 2004 | 24853 | 434 | 66144 | 2.6614 | 0.017463 | 0.97886 | -4.0477
24/07/2004 | 2004 | 24853 | 223 | 42277 | 1.7011 | 0.0089728 | 0.53126 | -4.7136
25/07/2004 | 2004 | 24853 | 70 | 2310 | 0.092947 | 0.0028166 | -2.3757 | -5.8722
28/07/2004 | 2004 | 24853 | 1677 | 12776 | 0.51406 | 0.067477 | -0.66541 | -2.696
29/07/2004 | 2004 | 24853 | 536 | 62485 | 2.5142 | 0.021567 | 0.92195 | -3.8366
02/08/2004 | 2004 | 24853 | 12 | 6624 | 0.26653 | 0.00048284 | -1.3223 | -7.6358
03/08/2004 | 2004 | 24853 | 60 | 14543 | 0.58516 | 0.0024142 | -0.53587 | -6.0264
06/08/2004 | 2004 | 24853 | 77 | 7015 | 0.28226 | 0.0030982 | -1.2649 | -5.7769
11/08/2004 | 2004 | 24853 | 706 | 77934 | 3.1358 | 0.028407 | 1.1429 | -3.5611
12/08/2004 | 2004 | 24853 | 28 | 1400 | 0.056331 | 0.0011266 | -2.8765 | -6.7885
13/08/2004 | 2004 | 24853 | 282 | 10474 | 0.42144 | 0.011347 | -0.86408 | -4.4788
15/08/2004 | 2004 | 24853 | 528 | 33954 | 1.3662 | 0.021245 | 0.31203 | -3.8516
16/08/2004 | 2004 | 24853 | 3217 | 42500 | 1.7101 | 0.12944 | 0.53653 | -2.0445
17/08/2004 | 2004 | 24853 | 1351 | 174939 | 7.0389 | 0.05436 | 1.9515 | -2.9121
18/08/2004 | 2004 | 24853 | 112 | 59737 | 2.4036 | 0.0045065 | 0.87697 | -5.4022
19/08/2004 | 2004 | 24853 | 62 | 29000 | 1.1669 | 0.0024947 | 0.15432 | -5.9936
20/08/2004 | 2004 | 24853 | 6 | 1530 | 0.061562 | 0.00024142 | -2.7877 | -8.329
22/08/2004 | 2004 | 24853 | 2796 | 66657 | 2.6821 | 0.1125 | 0.98658 | -2.1848
23/08/2004 | 2004 | 24853 | 15 | 1950 | 0.078461 | 0.00060355 | -2.5451 | -7.4127
24/08/2004 | 2004 | 24853 | 10 | 2980 | 0.11991 | 0.00040237 | -2.1211 | -7.8181
26/08/2004 | 2004 | 24853 | 15 | 4440 | 0.17865 | 0.00060355 | -1.7223 | -7.4127
27/08/2004 | 2004 | 24853 | 5 | 775 | 0.031183 | 0.00020118 | -3.4679 | -8.5113
28/08/2004 | 2004 | 24853 | 991 | 105724 | 4.254 | 0.039874 | 1.4479 | -3.222
01/09/2004 | 2004 | 24853 | 63 | 21420 | 0.86187 | 0.0025349 | -0.14865 | -5.9776
06/09/2004 | 2004 | 24853 | 214 | 50862 | 2.0465 | 0.0086106 | 0.71614 | -4.7548
08/09/2004 | 2004 | 24853 | 6 | 1080 | 0.043456 | 0.00024142 | -3.136 | -8.329
15/09/2004 | 2004 | 24853 | 113 | 32617 | 1.3124 | 0.0045467 | 0.27186 | -5.3933
20/09/2004 | 2004 | 24853 | 102 | 15215 | 0.6122 | 0.0041041 | -0.4907 | -5.4958
22/09/2004 | 2004 | 24853 | 1547 | 8036 | 0.32334 | 0.062246 | -1.129 | -2.7767
23/09/2004 | 2004 | 24853 | 407 | 1628 | 0.065505 | 0.016376 | -2.7256 | -4.1119
24/09/2004 | 2004 | 24853 | 6 | 504 | 0.020279 | 0.00024142 | -3.8982 | -8.329
26/09/2004 | 2004 | 24853 | 38 | 17100 | 0.68805 | 0.001529 | -0.3739 | -6.4831
27/09/2004 | 2004 | 24853 | 3 | 360 | 0.014485 | 0.00012071 | -4.2346 | -9.0221
28/09/2004 | 2004 | 24853 | 24 | 6000 | 0.24142 | 0.00096568 | -1.4212 | -6.9427
29/09/2004 | 2004 | 24853 | 1401 | 152499 | 6.136 | 0.056371 | 1.8142 | -2.8758
30/09/2004 | 2004 | 24853 | 8 | 720 | 0.02897 | 0.00032189 | -3.5415 | -8.0413
01/10/2004 | 2004 | 24853 | 15 | 1470 | 0.059148 | 0.00060355 | -2.8277 | -7.4127
05/10/2004 | 2004 | 24853 | 15 | 900 | 0.036213 | 0.00060355 | -3.3183 | -7.4127
06/10/2004 | 2004 | 24853 | 88 | 27032 | 1.0877 | 0.0035408 | 0.084043 | -5.6434
08/10/2004 | 2004 | 24853 | 76 | 47500 | 1.9112 | 0.003058 | 0.64775 | -5.79
10/10/2004 | 2004 | 24853 | 3947 | 15788 | 0.63526 | 0.15881 | -0.45373 | -1.84
12/10/2004 | 2004 | 24853 | 83 | 10468 | 0.4212 | 0.0033396 | -0.86466 | -5.7019
13/10/2004 | 2004 | 24853 | 96 | 3840 | 0.15451 | 0.0038627 | -1.8675 | -5.5564
14/10/2004 | 2004 | 24853 | 269 | 4419 | 0.17781 | 0.010824 | -1.7271 | -4.526
16/10/2004 | 2004 | 24853 | 654 | 64158 | 2.5815 | 0.026315 | 0.94837 | -3.6376
19/10/2004 | 2004 | 24853 | 75 | 8440 | 0.3396 | 0.0030177 | -1.08 | -5.8032
20/10/2004 | 2004 | 24853 | 152 | 33930 | 1.3652 | 0.006116 | 0.31132 | -5.0969
22/10/2004 | 2004 | 24853 | 17 | 1071 | 0.043093 | 0.00068402 | -3.1444 | -7.2875
24/10/2004 | 2004 | 24853 | 570 | 183252 | 7.3734 | 0.022935 | 1.9979 | -3.7751
27/10/2004 | 2004 | 24853 | 23 | 5796 | 0.23321 | 0.00092544 | -1.4558 | -6.9852
30/10/2004 | 2004 | 24853 | 30 | 3480 | 0.14002 | 0.0012071 | -1.9659 | -6.7195
01/11/2004 | 2004 | 24853 | 112 | 22987 | 0.92492 | 0.0045065 | -0.07805 | -5.4022
02/11/2004 | 2004 | 24853 | 68 | 11968 | 0.48155 | 0.0027361 | -0.73074 | -5.9012
03/11/2004 | 2004 | 24853 | 94 | 15066 | 0.6062 | 0.0037822 | -0.50054 | -5.5774
09/11/2004 | 2004 | 24853 | 299 | 87548 | 3.5226 | 0.012031 | 1.2592 | -4.4203
10/11/2004 | 2004 | 24853 | 199 | 15920 | 0.64057 | 0.0080071 | -0.4454 | -4.8274
14/11/2004 | 2004 | 24853 | 300 | 29032 | 1.1681 | 0.012071 | 0.15542 | -4.417
15/11/2004 | 2004 | 24853 | 11764 | 818057 | 32.9158 | 0.47334 | 3.494 | -0.74793
17/11/2004 | 2004 | 24853 | 2 | 272 | 0.010944 | 8.0473e-05 | -4.5149 | -9.4276
19/11/2004 | 2004 | 24853 | 15 | 1335 | 0.053716 | 0.00060355 | -2.924 | -7.4127
20/11/2004 | 2004 | 24853 | 13 | 1235 | 0.049692 | 0.00052308 | -3.0019 | -7.5558
22/11/2004 | 2004 | 24853 | 37 | 18551 | 0.74643 | 0.0014888 | -0.29245 | -6.5098
24/11/2004 | 2004 | 24853 | 113 | 1356 | 0.054561 | 0.0045467 | -2.9084 | -5.3933
25/11/2004 | 2004 | 24853 | 395 | 302500 | 12.1716 | 0.015893 | 2.4991 | -4.1418
26/11/2004 | 2004 | 24853 | 96 | 32145 | 1.2934 | 0.0038627 | 0.25728 | -5.5564
27/11/2004 | 2004 | 24853 | 38 | 5099 | 0.20517 | 0.001529 | -1.5839 | -6.4831
30/11/2004 | 2004 | 24853 | 141 | 8171 | 0.32877 | 0.0056734 | -1.1124 | -5.172
01/12/2004 | 2004 | 24853 | 8 | 280 | 0.011266 | 0.00032189 | -4.4859 | -8.0413
02/12/2004 | 2004 | 24853 | 47 | 7767 | 0.31252 | 0.0018911 | -1.1631 | -6.2706
03/12/2004 | 2004 | 24853 | 7 | 1561 | 0.062809 | 0.00028166 | -2.7677 | -8.1748
04/12/2004 | 2004 | 24853 | 2 | 280 | 0.011266 | 8.0473e-05 | -4.4859 | -9.4276
05/12/2004 | 2004 | 24853 | 698 | 125895 | 5.0656 | 0.028085 | 1.6225 | -3.5725
06/12/2004 | 2004 | 24853 | 15 | 540 | 0.021728 | 0.00060355 | -3.8292 | -7.4127
09/12/2004 | 2004 | 24853 | 77 | 6832 | 0.2749 | 0.0030982 | -1.2914 | -5.7769
10/12/2004 | 2004 | 24853 | 180 | 16880 | 0.67919 | 0.0072426 | -0.38685 | -4.9278
11/12/2004 | 2004 | 24853 | 66 | 3720 | 0.14968 | 0.0026556 | -1.8993 | -5.9311
13/12/2004 | 2004 | 24853 | 162 | 34635 | 1.3936 | 0.0065183 | 0.33189 | -5.0331
14/12/2004 | 2004 | 24853 | 3 | 570 | 0.022935 | 0.00012071 | -3.7751 | -9.0221
15/12/2004 | 2004 | 24853 | 117 | 60570 | 2.4371 | 0.0047077 | 0.89082 | -5.3586
16/12/2004 | 2004 | 24853 | 24 | 2504 | 0.10075 | 0.00096568 | -2.2951 | -6.9427
17/12/2004 | 2004 | 24853 | 39 | 7716 | 0.31047 | 0.0015692 | -1.1697 | -6.4572
19/12/2004 | 2004 | 24853 | 216 | 28878 | 1.162 | 0.0086911 | 0.1501 | -4.7455
20/12/2004 | 2004 | 24853 | 68 | 6766 | 0.27224 | 0.0027361 | -1.3011 | -5.9012
21/12/2004 | 2004 | 24853 | 82 | 14372 | 0.57828 | 0.0032994 | -0.5477 | -5.714
22/12/2004 | 2004 | 24853 | 44 | 13904 | 0.55945 | 0.0017704 | -0.5808 | -6.3365
24/12/2004 | 2004 | 24853 | 75 | 4647 | 0.18698 | 0.0030177 | -1.6768 | -5.8032
25/12/2004 | 2004 | 24853 | 440 | 9027 | 0.36322 | 0.017704 | -1.0128 | -4.034
28/12/2004 | 2004 | 24853 | 37 | 3996 | 0.16079 | 0.0014888 | -1.8277 | -6.5098
29/12/2004 | 2004 | 24853 | 15 | 1095 | 0.044059 | 0.00060355 | -3.1222 | -7.4127
02/01/2005 | 2004 | 24853 | 352 | 16698 | 0.67187 | 0.014163 | -0.39769 | -4.2571
07/01/2005 | 2004 | 24853 | 134 | 24643 | 0.99155 | 0.0053917 | -0.0084856 | -5.2229
08/01/2005 | 2004 | 24853 | 17 | 238 | 0.0095763 | 0.00068402 | -4.6485 | -7.2875
09/01/2005 | 2004 | 24853 | 270 | 10395 | 0.41826 | 0.010864 | -0.87165 | -4.5223
10/01/2005 | 2004 | 24853 | 25 | 3280 | 0.13198 | 0.0010059 | -2.0251 | -6.9019
11/01/2005 | 2004 | 24853 | 77 | 13171 | 0.52996 | 0.0030982 | -0.63496 | -5.7769
13/01/2005 | 2004 | 24853 | 730 | 24451 | 0.98382 | 0.029373 | -0.016307 | -3.5277
14/01/2005 | 2004 | 24853 | 95 | 11200 | 0.45065 | 0.0038225 | -0.79706 | -5.5669
17/01/2005 | 2004 | 24853 | 294 | 41861 | 1.6843 | 0.01183 | 0.52138 | -4.4372
18/01/2005 | 2004 | 24853 | 894 | 11197 | 0.45053 | 0.035972 | -0.79733 | -3.325
23/01/2005 | 2004 | 24853 | 72 | 8160 | 0.32833 | 0.002897 | -1.1137 | -5.8441
26/01/2005 | 2004 | 24853 | 4 | 560 | 0.022532 | 0.00016095 | -3.7928 | -8.7344
27/01/2005 | 2004 | 24853 | 4 | 200 | 0.0080473 | 0.00016095 | -4.8224 | -8.7344
31/01/2005 | 2004 | 24853 | 537 | 78062 | 3.1409 | 0.021607 | 1.1445 | -3.8347
01/02/2005 | 2004 | 24853 | 56 | 5600 | 0.22532 | 0.0022532 | -1.4902 | -6.0954
02/02/2005 | 2004 | 24853 | 78 | 156 | 0.0062769 | 0.0031385 | -5.0709 | -5.764
03/02/2005 | 2004 | 24853 | 41 | 1864 | 0.075001 | 0.0016497 | -2.5903 | -6.4072
04/02/2005 | 2004 | 24853 | 103 | 20547 | 0.82674 | 0.0041444 | -0.19026 | -5.486
06/02/2005 | 2004 | 24853 | 466 | 139800 | 5.6251 | 0.01875 | 1.7272 | -3.9765
07/02/2005 | 2004 | 24853 | 19 | 1691 | 0.06804 | 0.0007645 | -2.6877 | -7.1763
10/02/2005 | 2004 | 24853 | 48 | 1920 | 0.077254 | 0.0019314 | -2.5607 | -6.2495
11/02/2005 | 2004 | 24853 | 154 | 9997 | 0.40225 | 0.0061964 | -0.91069 | -5.0838
15/02/2005 | 2004 | 24853 | 52 | 675 | 0.02716 | 0.0020923 | -3.606 | -6.1695
17/02/2005 | 2004 | 24853 | 40 | 7200 | 0.2897 | 0.0016095 | -1.2389 | -6.4319
18/02/2005 | 2004 | 24853 | 802 | 4812 | 0.19362 | 0.03227 | -1.6419 | -3.4336
20/02/2005 | 2004 | 24853 | 1136 | 79520 | 3.1996 | 0.045709 | 1.163 | -3.0855
22/02/2005 | 2004 | 24853 | 12 | 6840 | 0.27522 | 0.00048284 | -1.2902 | -7.6358
23/02/2005 | 2004 | 24853 | 93 | 21897 | 0.88106 | 0.003742 | -0.12663 | -5.5881
25/02/2005 | 2004 | 24853 | 446 | 32779 | 1.3189 | 0.017946 | 0.27681 | -4.0204
28/02/2005 | 2004 | 24853 | 47 | 5405 | 0.21748 | 0.0018911 | -1.5257 | -6.2706
01/03/2005 | 2004 | 24853 | 450 | 17028 | 0.68515 | 0.018106 | -0.37812 | -4.0115
02/03/2005 | 2004 | 24853 | 47 | 5640 | 0.22693 | 0.0018911 | -1.4831 | -6.2706
03/03/2005 | 2004 | 24853 | 92 | 5728 | 0.23048 | 0.0037018 | -1.4676 | -5.5989
05/03/2005 | 2004 | 24853 | 175 | 14633 | 0.58878 | 0.0070414 | -0.5297 | -4.9559
07/03/2005 | 2004 | 24853 | 802 | 39813 | 1.6019 | 0.03227 | 0.47122 | -3.4336
09/03/2005 | 2004 | 24853 | 82 | 7954 | 0.32004 | 0.0032994 | -1.1393 | -5.714
11/03/2005 | 2004 | 24853 | 216 | 13970 | 0.56211 | 0.0086911 | -0.57607 | -4.7455
13/03/2005 | 2004 | 24853 | 332 | 8534 | 0.34338 | 0.013359 | -1.0689 | -4.3156
14/03/2005 | 2004 | 24853 | 442 | 28288 | 1.1382 | 0.017785 | 0.12946 | -4.0294
15/03/2005 | 2004 | 24853 | 29 | 6670 | 0.26838 | 0.0011669 | -1.3154 | -6.7534
16/03/2005 | 2004 | 24853 | 725 | 25734 | 1.0354 | 0.029172 | 0.034835 | -3.5346
17/03/2005 | 2004 | 24853 | 328 | 1640 | 0.065988 | 0.013198 | -2.7183 | -4.3277
18/03/2005 | 2004 | 24853 | 402 | 12972 | 0.52195 | 0.016175 | -0.65019 | -4.1243
19/03/2005 | 2004 | 24853 | 385 | 21929 | 0.88235 | 0.015491 | -0.12517 | -4.1675
21/03/2005 | 2004 | 24853 | 1496 | 42840 | 1.7237 | 0.060194 | 0.54449 | -2.8102
22/03/2005 | 2004 | 24853 | 213 | 48805 | 1.9637 | 0.0085704 | 0.67485 | -4.7594
23/03/2005 | 2004 | 24853 | 83 | 22377 | 0.90037 | 0.0033396 | -0.10494 | -5.7019
24/03/2005 | 2004 | 24853 | 87 | 6624 | 0.26653 | 0.0035006 | -1.3223 | -5.6548
25/03/2005 | 2004 | 24853 | 289 | 38018 | 1.5297 | 0.011628 | 0.42508 | -4.4543
26/03/2005 | 2004 | 24853 | 13 | 2379 | 0.095723 | 0.00052308 | -2.3463 | -7.5558
29/03/2005 | 2004 | 24853 | 43 | 3860 | 0.15531 | 0.0017302 | -1.8623 | -6.3595
30/03/2005 | 2004 | 24853 | 17 | 340 | 0.01368 | 0.00068402 | -4.2918 | -7.2875
31/03/2005 | 2004 | 24853 | 5 | 715 | 0.028769 | 0.00020118 | -3.5485 | -8.5113
07/04/2005 | 2005 | 24863 | 5 | 180 | 0.0072397 | 0.0002011 | -4.9282 | -8.5117
08/04/2005 | 2005 | 24863 | 392 | 55932 | 2.2496 | 0.015766 | 0.81076 | -4.1499
11/04/2005 | 2005 | 24863 | 17 | 2312 | 0.09299 | 0.00068375 | -2.3753 | -7.2879
12/04/2005 | 2005 | 24863 | 29 | 13630 | 0.5482 | 0.0011664 | -0.60111 | -6.7538
15/04/2005 | 2005 | 24863 | 29 | 6113 | 0.24587 | 0.0011664 | -1.403 | -6.7538
16/04/2005 | 2005 | 24863 | 79 | 5925 | 0.23831 | 0.0031774 | -1.4342 | -5.7517
18/04/2005 | 2005 | 24863 | 47 | 14758 | 0.59357 | 0.0018904 | -0.5216 | -6.271
20/04/2005 | 2005 | 24863 | 98 | 2908 | 0.11696 | 0.0039416 | -2.1459 | -5.5362
21/04/2005 | 2005 | 24863 | 48 | 2160 | 0.086876 | 0.0019306 | -2.4433 | -6.2499
25/04/2005 | 2005 | 24863 | 77 | 26211 | 1.0542 | 0.003097 | 0.052798 | -5.7773
27/04/2005 | 2005 | 24863 | 22 | 5500 | 0.22121 | 0.00088485 | -1.5086 | -7.0301
30/04/2005 | 2005 | 24863 | 18 | 4284 | 0.1723 | 0.00072397 | -1.7585 | -7.2308
01/05/2005 | 2005 | 24863 | 12 | 792 | 0.031855 | 0.00048264 | -3.4466 | -7.6362
03/05/2005 | 2005 | 24863 | 230 | 15944 | 0.64127 | 0.0092507 | -0.4443 | -4.6831
05/05/2005 | 2005 | 24863 | 36 | 11238 | 0.452 | 0.0014479 | -0.79408 | -6.5376
06/05/2005 | 2005 | 24863 | 593 | 22408 | 0.90126 | 0.023851 | -0.10396 | -3.7359
09/05/2005 | 2005 | 24863 | 30 | 2460 | 0.098942 | 0.0012066 | -2.3132 | -6.7199
10/05/2005 | 2005 | 24863 | 96 | 17447 | 0.70173 | 0.0038612 | -0.35421 | -5.5568
12/05/2005 | 2005 | 24863 | 15 | 900 | 0.036198 | 0.00060331 | -3.3187 | -7.4131
16/05/2005 | 2005 | 24863 | 75 | 13875 | 0.55806 | 0.0030165 | -0.58329 | -5.8036
17/05/2005 | 2005 | 24863 | 74 | 12876 | 0.51788 | 0.0029763 | -0.65802 | -5.8171
22/05/2005 | 2005 | 24863 | 97 | 20301 | 0.81651 | 0.0039014 | -0.20271 | -5.5464
23/05/2005 | 2005 | 24863 | 652 | 28001 | 1.1262 | 0.026224 | 0.11886 | -3.6411
25/05/2005 | 2005 | 24863 | 24 | 540 | 0.021719 | 0.00096529 | -3.8296 | -6.9431
26/05/2005 | 2005 | 24863 | 25 | 6850 | 0.27551 | 0.0010055 | -1.2891 | -6.9023
27/05/2005 | 2005 | 24863 | 277 | 21936 | 0.88227 | 0.011141 | -0.12525 | -4.4971
30/05/2005 | 2005 | 24863 | 164 | 8113 | 0.32631 | 0.0065961 | -1.1199 | -5.0213
31/05/2005 | 2005 | 24863 | 16 | 480 | 0.019306 | 0.00064353 | -3.9473 | -7.3485
01/06/2005 | 2005 | 24863 | 38 | 12811 | 0.51526 | 0.0015284 | -0.66308 | -6.4835
02/06/2005 | 2005 | 24863 | 159 | 13298 | 0.53485 | 0.006395 | -0.62577 | -5.0522
07/06/2005 | 2005 | 24863 | 698 | 20890 | 0.8402 | 0.028074 | -0.17411 | -3.5729
08/06/2005 | 2005 | 24863 | 52 | 2871 | 0.11547 | 0.0020915 | -2.1587 | -6.1699
09/06/2005 | 2005 | 24863 | 69 | 9983 | 0.40152 | 0.0027752 | -0.9125 | -5.887
10/06/2005 | 2005 | 24863 | 18 | 5418 | 0.21791 | 0.00072397 | -1.5237 | -7.2308
15/06/2005 | 2005 | 24863 | 185 | 16814 | 0.67627 | 0.0074408 | -0.39117 | -4.9008
16/06/2005 | 2005 | 24863 | 41 | 7872 | 0.31662 | 0.001649 | -1.1501 | -6.4076
17/06/2005 | 2005 | 24863 | 53 | 5406 | 0.21743 | 0.0021317 | -1.5259 | -6.1508
18/06/2005 | 2005 | 24863 | 20 | 1060 | 0.042634 | 0.00080441 | -3.1551 | -7.1254
20/06/2005 | 2005 | 24863 | 44 | 10284 | 0.41363 | 0.0017697 | -0.88279 | -6.3369
21/06/2005 | 2005 | 24863 | 86 | 5543 | 0.22294 | 0.003459 | -1.5008 | -5.6668
22/06/2005 | 2005 | 24863 | 7 | 882 | 0.035474 | 0.00028154 | -3.3389 | -8.1752
23/06/2005 | 2005 | 24863 | 12 | 1044 | 0.04199 | 0.00048264 | -3.1703 | -7.6362
24/06/2005 | 2005 | 24863 | 533 | 25587 | 1.0291 | 0.021437 | 0.028704 | -3.8426
25/06/2005 | 2005 | 24863 | 336 | 42257 | 1.6996 | 0.013514 | 0.53039 | -4.304
26/06/2005 | 2005 | 24863 | 8 | 1416 | 0.056952 | 0.00032176 | -2.8655 | -8.0417
27/06/2005 | 2005 | 24863 | 18 | 5670 | 0.22805 | 0.00072397 | -1.4782 | -7.2308
28/06/2005 | 2005 | 24863 | 1220 | 117405 | 4.7221 | 0.049069 | 1.5522 | -3.0145
29/06/2005 | 2005 | 24863 | 24 | 8688 | 0.34943 | 0.00096529 | -1.0514 | -6.9431
30/06/2005 | 2005 | 24863 | 15 | 975 | 0.039215 | 0.00060331 | -3.2387 | -7.4131
05/07/2005 | 2005 | 24863 | 76 | 1258 | 0.050597 | 0.0030568 | -2.9839 | -5.7904
06/07/2005 | 2005 | 24863 | 260 | 29912 | 1.2031 | 0.010457 | 0.18488 | -4.5605
08/07/2005 | 2005 | 24863 | 188 | 16397 | 0.65949 | 0.0075614 | -0.41628 | -4.8847
11/07/2005 | 2005 | 24863 | 117 | 23608 | 0.94952 | 0.0047058 | -0.051795 | -5.359
12/07/2005 | 2005 | 24863 | 355 | 24439 | 0.98295 | 0.014278 | -0.017201 | -4.249
15/07/2005 | 2005 | 24863 | 1161 | 43678 | 1.7567 | 0.046696 | 0.56346 | -3.0641
18/07/2005 | 2005 | 24863 | 724 | 24463 | 0.98391 | 0.02912 | -0.016219 | -3.5363
19/07/2005 | 2005 | 24863 | 784 | 46445 | 1.868 | 0.031533 | 0.62489 | -3.4567
21/07/2005 | 2005 | 24863 | 11 | 1716 | 0.069018 | 0.00044242 | -2.6734 | -7.7232
22/07/2005 | 2005 | 24863 | 18 | 234 | 0.0094116 | 0.00072397 | -4.6658 | -7.2308
26/07/2005 | 2005 | 24863 | 19 | 5795 | 0.23308 | 0.00076419 | -1.4564 | -7.1767
27/07/2005 | 2005 | 24863 | 89 | 23235 | 0.93452 | 0.0035796 | -0.067721 | -5.6325
28/07/2005 | 2005 | 24863 | 687 | 49127 | 1.9759 | 0.027631 | 0.68103 | -3.5888
29/07/2005 | 2005 | 24863 | 10 | 2780 | 0.11181 | 0.0004022 | -2.1909 | -7.8186
01/08/2005 | 2005 | 24863 | 402 | 17556 | 0.70611 | 0.016169 | -0.34798 | -4.1247
04/08/2005 | 2005 | 24863 | 9 | 540 | 0.021719 | 0.00036198 | -3.8296 | -7.9239
05/08/2005 | 2005 | 24863 | 172 | 4031 | 0.16213 | 0.0069179 | -1.8194 | -4.9736
08/08/2005 | 2005 | 24863 | 46 | 4600 | 0.18501 | 0.0018501 | -1.6873 | -6.2925
10/08/2005 | 2005 | 24863 | 33 | 6567 | 0.26413 | 0.0013273 | -1.3313 | -6.6246
16/08/2005 | 2005 | 24863 | 10 | 4460 | 0.17938 | 0.0004022 | -1.7182 | -7.8186
17/08/2005 | 2005 | 24863 | 14 | 3150 | 0.12669 | 0.00056309 | -2.066 | -7.4821
18/08/2005 | 2005 | 24863 | 14 | 3248 | 0.13064 | 0.00056309 | -2.0353 | -7.4821
23/08/2005 | 2005 | 24863 | 7 | 2380 | 0.095725 | 0.00028154 | -2.3463 | -8.1752
26/08/2005 | 2005 | 24863 | 133 | 8455 | 0.34006 | 0.0053493 | -1.0786 | -5.2308
27/08/2005 | 2005 | 24863 | 188 | 1880 | 0.075614 | 0.0075614 | -2.5821 | -4.8847
28/08/2005 | 2005 | 24863 | 100 | 8292 | 0.33351 | 0.004022 | -1.0981 | -5.516
29/08/2005 | 2005 | 24863 | 116 | 58770 | 2.3638 | 0.0046656 | 0.86025 | -5.3675
30/08/2005 | 2005 | 24863 | 29 | 10440 | 0.4199 | 0.0011664 | -0.86774 | -6.7538
01/09/2005 | 2005 | 24863 | 34 | 9690 | 0.38974 | 0.0013675 | -0.94229 | -6.5948
05/09/2005 | 2005 | 24863 | 188 | 10528 | 0.42344 | 0.0075614 | -0.85934 | -4.8847
06/09/2005 | 2005 | 24863 | 98 | 18405 | 0.74026 | 0.0039416 | -0.30076 | -5.5362
07/09/2005 | 2005 | 24863 | 486 | 19203 | 0.77235 | 0.019547 | -0.25831 | -3.9349
08/09/2005 | 2005 | 24863 | 190 | 38686 | 1.556 | 0.0076419 | 0.4421 | -4.8741
13/09/2005 | 2005 | 24863 | 59 | 22479 | 0.90411 | 0.002373 | -0.1008 | -6.0436
15/09/2005 | 2005 | 24863 | 19 | 5320 | 0.21397 | 0.00076419 | -1.5419 | -7.1767
16/09/2005 | 2005 | 24863 | 82 | 14268 | 0.57386 | 0.0032981 | -0.55536 | -5.7144
17/09/2005 | 2005 | 24863 | 38 | 5186 | 0.20858 | 0.0015284 | -1.5674 | -6.4835
18/09/2005 | 2005 | 24863 | 484 | 70089 | 2.819 | 0.019467 | 1.0364 | -3.9391
19/09/2005 | 2005 | 24863 | 95 | 9257 | 0.37232 | 0.0038209 | -0.988 | -5.5673
20/09/2005 | 2005 | 24863 | 59 | 4053 | 0.16301 | 0.002373 | -1.8139 | -6.0436
27/09/2005 | 2005 | 24863 | 79 | 27376 | 1.1011 | 0.0031774 | 0.096286 | -5.7517
01/10/2005 | 2005 | 24863 | 216 | 51142 | 2.057 | 0.0086876 | 0.72123 | -4.7459
02/10/2005 | 2005 | 24863 | 12 | 2604 | 0.10473 | 0.00048264 | -2.2563 | -7.6362
03/10/2005 | 2005 | 24863 | 165 | 20677 | 0.83164 | 0.0066364 | -0.18436 | -5.0152
04/10/2005 | 2005 | 24863 | 65 | 1408 | 0.05663 | 0.0026143 | -2.8712 | -5.9467
05/10/2005 | 2005 | 24863 | 280 | 25219 | 1.0143 | 0.011262 | 0.014217 | -4.4863
07/10/2005 | 2005 | 24863 | 4294 | 121743 | 4.8966 | 0.17271 | 1.5885 | -1.7562
10/10/2005 | 2005 | 24863 | 767 | 31438 | 1.2644 | 0.030849 | 0.23464 | -3.4786
11/10/2005 | 2005 | 24863 | 17 | 4925 | 0.19809 | 0.00068375 | -1.6191 | -7.2879
14/10/2005 | 2005 | 24863 | 35 | 5635 | 0.22664 | 0.0014077 | -1.4844 | -6.5658
17/10/2005 | 2005 | 24863 | 29 | 10846 | 0.43623 | 0.0011664 | -0.82958 | -6.7538
18/10/2005 | 2005 | 24863 | 67 | 9367 | 0.37674 | 0.0026948 | -0.97619 | -5.9164
19/10/2005 | 2005 | 24863 | 22 | 3740 | 0.15042 | 0.00088485 | -1.8943 | -7.0301
21/10/2005 | 2005 | 24863 | 1350 | 668119 | 26.872 | 0.054298 | 3.2911 | -2.9133
22/10/2005 | 2005 | 24863 | 13975 | 1429074 | 57.4779 | 0.56208 | 4.0514 | -0.57611
23/10/2005 | 2005 | 24863 | 150 | 9176 | 0.36906 | 0.0060331 | -0.99679 | -5.1105
25/10/2005 | 2005 | 24863 | 75 | 6840 | 0.27511 | 0.0030165 | -1.2906 | -5.8036
31/10/2005 | 2005 | 24863 | 1174 | 207736 | 8.3552 | 0.047219 | 2.1229 | -3.053
01/11/2005 | 2005 | 24863 | 53 | 21942 | 0.88252 | 0.0021317 | -0.12498 | -6.1508
02/11/2005 | 2005 | 24863 | 1128 | 114299 | 4.5972 | 0.045369 | 1.5254 | -3.0929
03/11/2005 | 2005 | 24863 | 215 | 34056 | 1.3697 | 0.0086474 | 0.31463 | -4.7505
04/11/2005 | 2005 | 24863 | 1 | 287 | 0.011543 | 4.022e-05 | -4.4617 | -10.1211
07/11/2005 | 2005 | 24863 | 296 | 23142 | 0.93078 | 0.011905 | -0.071732 | -4.4308
11/11/2005 | 2005 | 24863 | 8 | 1080 | 0.043438 | 0.00032176 | -3.1364 | -8.0417
13/11/2005 | 2005 | 24863 | 717 | 20916 | 0.84125 | 0.028838 | -0.17287 | -3.5461
14/11/2005 | 2005 | 24863 | 159 | 5780 | 0.23247 | 0.006395 | -1.459 | -5.0522
17/11/2005 | 2005 | 24863 | 17 | 1891 | 0.076057 | 0.00068375 | -2.5763 | -7.2879
18/11/2005 | 2005 | 24863 | 22 | 3300 | 0.13273 | 0.00088485 | -2.0195 | -7.0301
22/11/2005 | 2005 | 24863 | 1282 | 25440 | 1.0232 | 0.051563 | 0.022942 | -2.965
23/11/2005 | 2005 | 24863 | 19 | 779 | 0.031332 | 0.00076419 | -3.4631 | -7.1767
24/11/2005 | 2005 | 24863 | 46 | 1886 | 0.075856 | 0.0018501 | -2.5789 | -6.2925
27/11/2005 | 2005 | 24863 | 718 | 285993 | 11.5028 | 0.028878 | 2.4426 | -3.5447
28/11/2005 | 2005 | 24863 | 6687 | 847927 | 34.104 | 0.26895 | 3.5294 | -1.3132
29/11/2005 | 2005 | 24863 | 1345 | 64929 | 2.6115 | 0.054096 | 0.95991 | -2.917
02/12/2005 | 2005 | 24863 | 501 | 77771 | 3.128 | 0.02015 | 1.1404 | -3.9045
04/12/2005 | 2005 | 24863 | 32 | 1072 | 0.043116 | 0.0012871 | -3.1439 | -6.6554
05/12/2005 | 2005 | 24863 | 168 | 11881 | 0.47786 | 0.006757 | -0.73844 | -4.9972
07/12/2005 | 2005 | 24863 | 162 | 9302 | 0.37413 | 0.0065157 | -0.98315 | -5.0335
09/12/2005 | 2005 | 24863 | 188 | 1504 | 0.060491 | 0.0075614 | -2.8053 | -4.8847
11/12/2005 | 2005 | 24863 | 658 | 133554 | 5.3716 | 0.026465 | 1.6811 | -3.6319
12/12/2005 | 2005 | 24863 | 444 | 50147 | 2.0169 | 0.017858 | 0.70158 | -4.0253
16/12/2005 | 2005 | 24863 | 95 | 14715 | 0.59184 | 0.0038209 | -0.52451 | -5.5673
17/12/2005 | 2005 | 24863 | 20 | 820 | 0.032981 | 0.00080441 | -3.4118 | -7.1254
20/12/2005 | 2005 | 24863 | 1087 | 42854 | 1.7236 | 0.04372 | 0.54442 | -3.13
21/12/2005 | 2005 | 24863 | 175 | 39025 | 1.5696 | 0.0070386 | 0.45082 | -4.9564
23/12/2005 | 2005 | 24863 | 791 | 58280 | 2.344 | 0.031814 | 0.85188 | -3.4478
24/12/2005 | 2005 | 24863 | 6530 | 332920 | 13.3902 | 0.26264 | 2.5945 | -1.337
26/12/2005 | 2005 | 24863 | 326 | 50346 | 2.0249 | 0.013112 | 0.70554 | -4.3342
27/12/2005 | 2005 | 24863 | 216 | 63004 | 2.534 | 0.0086876 | 0.92982 | -4.7459
31/12/2005 | 2005 | 24863 | 4211 | 142812 | 5.744 | 0.16937 | 1.7481 | -1.7757
02/01/2006 | 2005 | 24863 | 100 | 15965 | 0.64212 | 0.004022 | -0.44298 | -5.516
03/01/2006 | 2005 | 24863 | 80 | 10973 | 0.44134 | 0.0032176 | -0.81794 | -5.7391
04/01/2006 | 2005 | 24863 | 764 | 112758 | 4.5352 | 0.030728 | 1.5119 | -3.4826
06/01/2006 | 2005 | 24863 | 230 | 13432 | 0.54024 | 0.0092507 | -0.61574 | -4.6831
07/01/2006 | 2005 | 24863 | 739 | 19305 | 0.77645 | 0.029723 | -0.25302 | -3.5158
08/01/2006 | 2005 | 24863 | 95 | 21724 | 0.87375 | 0.0038209 | -0.13496 | -5.5673
11/01/2006 | 2005 | 24863 | 10 | 1300 | 0.052287 | 0.0004022 | -2.951 | -7.8186
12/01/2006 | 2005 | 24863 | 1833 | 151489 | 6.0929 | 0.073724 | 1.8071 | -2.6074
16/01/2006 | 2005 | 24863 | 1085 | 35405 | 1.424 | 0.043639 | 0.35347 | -3.1318
18/01/2006 | 2005 | 24863 | 405 | 17717 | 0.71258 | 0.016289 | -0.33886 | -4.1172
20/01/2006 | 2005 | 24863 | 95 | 10985 | 0.44182 | 0.0038209 | -0.81685 | -5.5673
21/01/2006 | 2005 | 24863 | 821 | 26854 | 1.0801 | 0.033021 | 0.077034 | -3.4106
22/01/2006 | 2005 | 24863 | 67 | 11055 | 0.44464 | 0.0026948 | -0.8105 | -5.9164
24/01/2006 | 2005 | 24863 | 4178 | 266615 | 10.7234 | 0.16804 | 2.3724 | -1.7835
25/01/2006 | 2005 | 24863 | 890 | 154861 | 6.2286 | 0.035796 | 1.8291 | -3.3299
26/01/2006 | 2005 | 24863 | 246 | 18024 | 0.72493 | 0.0098942 | -0.32168 | -4.6158
28/01/2006 | 2005 | 24863 | 305 | 12931 | 0.52009 | 0.012267 | -0.65375 | -4.4008
01/02/2006 | 2005 | 24863 | 1092 | 43745 | 1.7594 | 0.043921 | 0.565 | -3.1254
02/02/2006 | 2005 | 24863 | 180 | 35040 | 1.4093 | 0.0072397 | 0.34311 | -4.9282
03/02/2006 | 2005 | 24863 | 955 | 67428 | 2.712 | 0.03841 | 0.99768 | -3.2594
06/02/2006 | 2005 | 24863 | 193 | 9190 | 0.36963 | 0.0077625 | -0.99526 | -4.8584
07/02/2006 | 2005 | 24863 | 166 | 15868 | 0.63822 | 0.0066766 | -0.44908 | -5.0091
11/02/2006 | 2005 | 24863 | 240 | 26690 | 1.0735 | 0.0096529 | 0.070908 | -4.6405
12/02/2006 | 2005 | 24863 | 2606 | 97362 | 3.9159 | 0.10481 | 1.3651 | -2.2556
13/02/2006 | 2005 | 24863 | 1780 | 34694 | 1.3954 | 0.071592 | 0.33319 | -2.6368
16/02/2006 | 2005 | 24863 | 13 | 117 | 0.0047058 | 0.00052287 | -5.359 | -7.5562
19/02/2006 | 2005 | 24863 | 403 | 9264 | 0.3726 | 0.016209 | -0.98724 | -4.1222
21/02/2006 | 2005 | 24863 | 745 | 106185 | 4.2708 | 0.029964 | 1.4518 | -3.5078
23/02/2006 | 2005 | 24863 | 15 | 2550 | 0.10256 | 0.00060331 | -2.2773 | -7.4131
27/02/2006 | 2005 | 24863 | 5616 | 113430 | 4.5622 | 0.22588 | 1.5178 | -1.4878
28/02/2006 | 2005 | 24863 | 175 | 4086 | 0.16434 | 0.0070386 | -1.8058 | -4.9564
02/03/2006 | 2005 | 24863 | 460 | 42672 | 1.7163 | 0.018501 | 0.54016 | -3.9899
04/03/2006 | 2005 | 24863 | 1755 | 104514 | 4.2036 | 0.070587 | 1.4359 | -2.6509
05/03/2006 | 2005 | 24863 | 300 | 23781 | 0.95648 | 0.012066 | -0.044494 | -4.4174
06/03/2006 | 2005 | 24863 | 176 | 62145 | 2.4995 | 0.0070788 | 0.91609 | -4.9507
07/03/2006 | 2005 | 24863 | 53 | 901 | 0.036239 | 0.0021317 | -3.3176 | -6.1508
09/03/2006 | 2005 | 24863 | 1042 | 27584 | 1.1094 | 0.04191 | 0.10386 | -3.1722
12/03/2006 | 2005 | 24863 | 111 | 27696 | 1.1139 | 0.0044645 | 0.10791 | -5.4116
16/03/2006 | 2005 | 24863 | 32 | 608 | 0.024454 | 0.0012871 | -3.711 | -6.6554
18/03/2006 | 2005 | 24863 | 256 | 68538 | 2.7566 | 0.010296 | 1.014 | -4.576
20/03/2006 | 2005 | 24863 | 19 | 2565 | 0.10317 | 0.00076419 | -2.2714 | -7.1767
22/03/2006 | 2005 | 24863 | 838 | 32911 | 1.3237 | 0.033705 | 0.28043 | -3.3901
23/03/2006 | 2005 | 24863 | 523 | 52900 | 2.1277 | 0.021035 | 0.75502 | -3.8616
24/03/2006 | 2005 | 24863 | 199 | 18905 | 0.76037 | 0.0080039 | -0.27395 | -4.8278
26/03/2006 | 2005 | 24863 | 343 | 27751 | 1.1162 | 0.013796 | 0.10989 | -4.2834
28/03/2006 | 2005 | 24863 | 1129 | 105938 | 4.2609 | 0.045409 | 1.4495 | -3.092
30/03/2006 | 2005 | 24863 | 246 | 22140 | 0.89048 | 0.0098942 | -0.11599 | -4.6158
01/04/2006 | 2006 | 24923 | 985 | 46692 | 1.8735 | 0.039522 | 0.62778 | -3.2309
03/04/2006 | 2006 | 24923 | 8 | 1616 | 0.06484 | 0.00032099 | -2.7358 | -8.0441
05/04/2006 | 2006 | 24923 | 444 | 49894 | 2.0019 | 0.017815 | 0.69411 | -4.0277
10/04/2006 | 2006 | 24923 | 36 | 10116 | 0.40589 | 0.0014444 | -0.90167 | -6.54
12/04/2006 | 2006 | 24923 | 646 | 13317 | 0.53433 | 0.02592 | -0.62675 | -3.6527
18/04/2006 | 2006 | 24923 | 1187 | 135139 | 5.4223 | 0.047627 | 1.6905 | -3.0444
19/04/2006 | 2006 | 24923 | 182 | 5199 | 0.2086 | 0.0073025 | -1.5673 | -4.9195
20/04/2006 | 2006 | 24923 | 110 | 5894 | 0.23649 | 0.0044136 | -1.4419 | -5.4231
21/04/2006 | 2006 | 24923 | 41 | 7216 | 0.28953 | 0.0016451 | -1.2395 | -6.41
24/04/2006 | 2006 | 24923 | 743 | 24920 | 0.99988 | 0.029812 | -0.00012038 | -3.5129
26/04/2006 | 2006 | 24923 | 217 | 9338 | 0.37467 | 0.0087068 | -0.9817 | -4.7436
27/04/2006 | 2006 | 24923 | 70 | 10955 | 0.43955 | 0.0028087 | -0.822 | -5.8751
28/04/2006 | 2006 | 24923 | 327 | 93522 | 3.7524 | 0.01312 | 1.3224 | -4.3336
30/04/2006 | 2006 | 24923 | 73 | 8554 | 0.34322 | 0.002929 | -1.0694 | -5.8331
01/05/2006 | 2006 | 24923 | 52 | 2004 | 0.080408 | 0.0020864 | -2.5206 | -6.1723
02/05/2006 | 2006 | 24923 | 26 | 8450 | 0.33904 | 0.0010432 | -1.0816 | -6.8654
03/05/2006 | 2006 | 24923 | 196 | 7623 | 0.30586 | 0.0078642 | -1.1846 | -4.8454
04/05/2006 | 2006 | 24923 | 860 | 29032 | 1.1649 | 0.034506 | 0.15261 | -3.3666
06/05/2006 | 2006 | 24923 | 185 | 46477 | 1.8648 | 0.0074229 | 0.62317 | -4.9032
07/05/2006 | 2006 | 24923 | 100 | 8126 | 0.32604 | 0.0040124 | -1.1207 | -5.5184
08/05/2006 | 2006 | 24923 | 469 | 79188 | 3.1773 | 0.018818 | 1.156 | -3.9729
09/05/2006 | 2006 | 24923 | 119 | 22238 | 0.89227 | 0.0047747 | -0.11399 | -5.3444
11/05/2006 | 2006 | 24923 | 18 | 6858 | 0.27517 | 0.00072222 | -1.2904 | -7.2332
12/05/2006 | 2006 | 24923 | 2655 | 42339 | 1.6988 | 0.10653 | 0.52992 | -2.2393
15/05/2006 | 2006 | 24923 | 1604 | 14434 | 0.57914 | 0.064358 | -0.5462 | -2.7433
18/05/2006 | 2006 | 24923 | 35 | 8645 | 0.34687 | 0.0014043 | -1.0588 | -6.5682
19/05/2006 | 2006 | 24923 | 8 | 944 | 0.037877 | 0.00032099 | -3.2734 | -8.0441
22/05/2006 | 2006 | 24923 | 39 | 7284 | 0.29226 | 0.0015648 | -1.2301 | -6.46
24/05/2006 | 2006 | 24923 | 96 | 5647 | 0.22658 | 0.0038519 | -1.4847 | -5.5592
25/05/2006 | 2006 | 24923 | 45 | 180 | 0.0072222 | 0.0018056 | -4.9306 | -6.3169
27/05/2006 | 2006 | 24923 | 96 | 12694 | 0.50933 | 0.0038519 | -0.67466 | -5.5592
28/05/2006 | 2006 | 24923 | 7632 | 167946 | 6.7386 | 0.30622 | 1.9079 | -1.1834
30/05/2006 | 2006 | 24923 | 53 | 16165 | 0.6486 | 0.0021265 | -0.43294 | -6.1533
03/06/2006 | 2006 | 24923 | 1419 | 99035 | 3.9736 | 0.056935 | 1.3797 | -2.8658
04/06/2006 | 2006 | 24923 | 145 | 8073 | 0.32392 | 0.0058179 | -1.1273 | -5.1468
05/06/2006 | 2006 | 24923 | 22 | 6515 | 0.26141 | 0.00088272 | -1.3417 | -7.0325
06/06/2006 | 2006 | 24923 | 7 | 791 | 0.031738 | 0.00028087 | -3.4502 | -8.1776
09/06/2006 | 2006 | 24923 | 880 | 11869 | 0.47623 | 0.035309 | -0.74186 | -3.3436
10/06/2006 | 2006 | 24923 | 729 | 17007 | 0.68238 | 0.02925 | -0.38217 | -3.5319
11/06/2006 | 2006 | 24923 | 1508 | 57810 | 2.3195 | 0.060506 | 0.84137 | -2.805
12/06/2006 | 2006 | 24923 | 3050 | 815354 | 32.7149 | 0.12238 | 3.4878 | -2.1006
13/06/2006 | 2006 | 24923 | 41 | 22587 | 0.90627 | 0.0016451 | -0.098417 | -6.41
14/06/2006 | 2006 | 24923 | 134 | 18238 | 0.73177 | 0.0053766 | -0.31228 | -5.2257
15/06/2006 | 2006 | 24923 | 3400 | 107919 | 4.3301 | 0.13642 | 1.4656 | -1.992
16/06/2006 | 2006 | 24923 | 1179 | 37622 | 1.5095 | 0.047306 | 0.4118 | -3.0511
18/06/2006 | 2006 | 24923 | 407 | 80517 | 3.2306 | 0.01633 | 1.1727 | -4.1147
19/06/2006 | 2006 | 24923 | 2662 | 411880 | 16.5261 | 0.10681 | 2.8049 | -2.2367
20/06/2006 | 2006 | 24923 | 225 | 37328 | 1.4977 | 0.0090278 | 0.40395 | -4.7074
21/06/2006 | 2006 | 24923 | 77 | 4387 | 0.17602 | 0.0030895 | -1.7371 | -5.7797
22/06/2006 | 2006 | 24923 | 318 | 35338 | 1.4179 | 0.012759 | 0.34917 | -4.3615
23/06/2006 | 2006 | 24923 | 780 | 252587 | 10.1347 | 0.031296 | 2.316 | -3.4643
25/06/2006 | 2006 | 24923 | 17 | 80377 | 3.225 | 0.0006821 | 1.1709 | -7.2903
26/06/2006 | 2006 | 24923 | 66 | 216379 | 8.6819 | 0.0026482 | 2.1612 | -5.9339
27/06/2006 | 2006 | 24923 | 102 | 21085 | 0.84601 | 0.0040926 | -0.16723 | -5.4986
28/06/2006 | 2006 | 24923 | 30 | 2610 | 0.10472 | 0.0012037 | -2.2564 | -6.7223
29/06/2006 | 2006 | 24923 | 23 | 204781 | 8.2165 | 0.00092284 | 2.1062 | -6.9881
05/07/2006 | 2006 | 24923 | 137 | 21855 | 0.8769 | 0.0054969 | -0.13136 | -5.2036
06/07/2006 | 2006 | 24923 | 21 | 1155 | 0.046343 | 0.0008426 | -3.0717 | -7.079
07/07/2006 | 2006 | 24923 | 188 | 83902 | 3.3664 | 0.0075432 | 1.2139 | -4.8871
10/07/2006 | 2006 | 24923 | 839 | 39483 | 1.5842 | 0.033664 | 0.46008 | -3.3913
14/07/2006 | 2006 | 24923 | 101 | 3953 | 0.15861 | 0.0040525 | -1.8413 | -5.5084
17/07/2006 | 2006 | 24923 | 84 | 8486 | 0.34049 | 0.0033704 | -1.0774 | -5.6927
18/07/2006 | 2006 | 24923 | 93 | 5570 | 0.22349 | 0.0037315 | -1.4984 | -5.5909
19/07/2006 | 2006 | 24923 | 650 | 48617 | 1.9507 | 0.02608 | 0.66818 | -3.6466
20/07/2006 | 2006 | 24923 | 116 | 17938 | 0.71974 | 0.0046543 | -0.32887 | -5.37
21/07/2006 | 2006 | 24923 | 297 | 21899 | 0.87867 | 0.011917 | -0.12935 | -4.4298
24/07/2006 | 2006 | 24923 | 44 | 11172 | 0.44826 | 0.0017654 | -0.80238 | -6.3394
26/07/2006 | 2006 | 24923 | 16 | 3280 | 0.13161 | 0.00064198 | -2.0279 | -7.351
27/07/2006 | 2006 | 24923 | 316 | 42976 | 1.7244 | 0.012679 | 0.54485 | -4.3678
31/07/2006 | 2006 | 24923 | 94 | 17951 | 0.72026 | 0.0037716 | -0.32815 | -5.5803
01/08/2006 | 2006 | 24923 | 16 | 5048 | 0.20254 | 0.00064198 | -1.5968 | -7.351
04/08/2006 | 2006 | 24923 | 154 | 12573 | 0.50447 | 0.006179 | -0.68424 | -5.0866
07/08/2006 | 2006 | 24923 | 131 | 15921 | 0.63881 | 0.0052562 | -0.44815 | -5.2483
08/08/2006 | 2006 | 24923 | 448 | 98023 | 3.933 | 0.017975 | 1.3694 | -4.0188
10/08/2006 | 2006 | 24923 | 21 | 7035 | 0.28227 | 0.0008426 | -1.2649 | -7.079
11/08/2006 | 2006 | 24923 | 228 | 5304 | 0.21282 | 0.0091482 | -1.5473 | -4.6942
13/08/2006 | 2006 | 24923 | 1408 | 62264 | 2.4983 | 0.056494 | 0.91559 | -2.8736
15/08/2006 | 2006 | 24923 | 29 | 812 | 0.03258 | 0.0011636 | -3.424 | -6.7563
16/08/2006 | 2006 | 24923 | 9 | 2907 | 0.11664 | 0.00036111 | -2.1487 | -7.9263
17/08/2006 | 2006 | 24923 | 26 | 2750 | 0.11034 | 0.0010432 | -2.2042 | -6.8654
18/08/2006 | 2006 | 24923 | 437 | 26091 | 1.0469 | 0.017534 | 0.045799 | -4.0436
19/08/2006 | 2006 | 24923 | 1177 | 110291 | 4.4253 | 0.047225 | 1.4873 | -3.0528
23/08/2006 | 2006 | 24923 | 73 | 12787 | 0.51306 | 0.002929 | -0.66736 | -5.8331
24/08/2006 | 2006 | 24923 | 63 | 126 | 0.0050556 | 0.0025278 | -5.2873 | -5.9804
25/08/2006 | 2006 | 24923 | 33 | 7899 | 0.31694 | 0.0013241 | -1.1491 | -6.627
26/08/2006 | 2006 | 24923 | 94 | 10546 | 0.42314 | 0.0037716 | -0.86004 | -5.5803
29/08/2006 | 2006 | 24923 | 140 | 34340 | 1.3778 | 0.0056173 | 0.32052 | -5.1819
30/08/2006 | 2006 | 24923 | 2395 | 86442 | 3.4684 | 0.096096 | 1.2437 | -2.3424
31/08/2006 | 2006 | 24923 | 119 | 26450 | 1.0613 | 0.0047747 | 0.059465 | -5.3444
03/09/2006 | 2006 | 24923 | 802 | 16842 | 0.67576 | 0.032179 | -0.39192 | -3.4364
05/09/2006 | 2006 | 24923 | 366 | 32343 | 1.2977 | 0.014685 | 0.26061 | -4.2209
07/09/2006 | 2006 | 24923 | 620 | 100192 | 4.0201 | 0.024877 | 1.3913 | -3.6938
08/09/2006 | 2006 | 24923 | 224 | 30800 | 1.2358 | 0.0089877 | 0.21172 | -4.7119
11/09/2006 | 2006 | 24923 | 126 | 4720 | 0.18938 | 0.0050556 | -1.664 | -5.2873
12/09/2006 | 2006 | 24923 | 41 | 1294 | 0.05192 | 0.0016451 | -2.9581 | -6.41
14/09/2006 | 2006 | 24923 | 5 | 1545 | 0.061991 | 0.00020062 | -2.7808 | -8.5141
19/09/2006 | 2006 | 24923 | 67 | 10720 | 0.43012 | 0.0026883 | -0.84368 | -5.9189
21/09/2006 | 2006 | 24923 | 68 | 4080 | 0.1637 | 0.0027284 | -1.8097 | -5.904
26/09/2006 | 2006 | 24923 | 106 | 11564 | 0.46399 | 0.0042531 | -0.76789 | -5.4601
27/09/2006 | 2006 | 24923 | 138 | 6000 | 0.24074 | 0.0055371 | -1.424 | -5.1963
29/09/2006 | 2006 | 24923 | 94 | 12894 | 0.51735 | 0.0037716 | -0.65903 | -5.5803
30/09/2006 | 2006 | 24923 | 154 | 1339 | 0.053725 | 0.006179 | -2.9239 | -5.0866
02/10/2006 | 2006 | 24923 | 304 | 4392 | 0.17622 | 0.012198 | -1.736 | -4.4065
04/10/2006 | 2006 | 24923 | 836 | 34585 | 1.3877 | 0.033543 | 0.32763 | -3.3949
05/10/2006 | 2006 | 24923 | 376 | 22038 | 0.88424 | 0.015086 | -0.12302 | -4.194
07/10/2006 | 2006 | 24923 | 827 | 48976 | 1.9651 | 0.033182 | 0.67554 | -3.4057
08/10/2006 | 2006 | 24923 | 179 | 9580 | 0.38438 | 0.0071821 | -0.95611 | -4.9362
09/10/2006 | 2006 | 24923 | 221 | 11573 | 0.46435 | 0.0088673 | -0.76712 | -4.7254
10/10/2006 | 2006 | 24923 | 647 | 25911 | 1.0396 | 0.02596 | 0.038877 | -3.6512
13/10/2006 | 2006 | 24923 | 27 | 2349 | 0.09425 | 0.0010833 | -2.3618 | -6.8277
15/10/2006 | 2006 | 24923 | 1075 | 45628 | 1.8308 | 0.043133 | 0.60473 | -3.1435
17/10/2006 | 2006 | 24923 | 171 | 6252 | 0.25085 | 0.0068611 | -1.3829 | -4.9819
18/10/2006 | 2006 | 24923 | 37 | 975 | 0.03912 | 0.0014846 | -3.2411 | -6.5126
24/10/2006 | 2006 | 24923 | 162 | 15644 | 0.62769 | 0.0065 | -0.4657 | -5.036
25/10/2006 | 2006 | 24923 | 33 | 2673 | 0.10725 | 0.0013241 | -2.2326 | -6.627
27/10/2006 | 2006 | 24923 | 200 | 800 | 0.032099 | 0.0080247 | -3.4389 | -4.8252
29/10/2006 | 2006 | 24923 | 199 | 41023 | 1.646 | 0.0079846 | 0.49834 | -4.8302
31/10/2006 | 2006 | 24923 | 65 | 21584 | 0.86603 | 0.002608 | -0.14384 | -5.9492
02/11/2006 | 2006 | 24923 | 13 | 2210 | 0.088673 | 0.00052161 | -2.4228 | -7.5586
06/11/2006 | 2006 | 24923 | 539 | 3773 | 0.15139 | 0.021627 | -1.8879 | -3.8338
07/11/2006 | 2006 | 24923 | 550 | 17864 | 0.71677 | 0.022068 | -0.333 | -3.8136
08/11/2006 | 2006 | 24923 | 1737 | 65586 | 2.6315 | 0.069695 | 0.96757 | -2.6636
09/11/2006 | 2006 | 24923 | 100 | 2480 | 0.099506 | 0.0040124 | -2.3075 | -5.5184
13/11/2006 | 2006 | 24923 | 216 | 11666 | 0.46808 | 0.0086667 | -0.75911 | -4.7483
14/11/2006 | 2006 | 24923 | 17 | 680 | 0.027284 | 0.0006821 | -3.6015 | -7.2903
18/11/2006 | 2006 | 24923 | 2230 | 39375 | 1.5799 | 0.089476 | 0.45734 | -2.4138
19/11/2006 | 2006 | 24923 | 167 | 8322 | 0.33391 | 0.0067006 | -1.0969 | -5.0056
20/11/2006 | 2006 | 24923 | 38 | 950 | 0.038117 | 0.0015247 | -3.2671 | -6.486
21/11/2006 | 2006 | 24923 | 38 | 988 | 0.039642 | 0.0015247 | -3.2279 | -6.486
23/11/2006 | 2006 | 24923 | 78 | 4680 | 0.18778 | 0.0031296 | -1.6725 | -5.7668
24/11/2006 | 2006 | 24923 | 276 | 29125 | 1.1686 | 0.011074 | 0.15581 | -4.5031
26/11/2006 | 2006 | 24923 | 350 | 19698 | 0.79035 | 0.014043 | -0.23527 | -4.2656
28/11/2006 | 2006 | 24923 | 405 | 11745 | 0.47125 | 0.01625 | -0.75236 | -4.1197
29/11/2006 | 2006 | 24923 | 25 | 10675 | 0.42832 | 0.0010031 | -0.84789 | -6.9047
30/11/2006 | 2006 | 24923 | 1006 | 125569 | 5.0383 | 0.040364 | 1.6171 | -3.2098
01/12/2006 | 2006 | 24923 | 175 | 6150 | 0.24676 | 0.0070216 | -1.3993 | -4.9588
03/12/2006 | 2006 | 24923 | 264 | 27990 | 1.1231 | 0.010593 | 0.11606 | -4.5476
05/12/2006 | 2006 | 24923 | 157 | 26529 | 1.0644 | 0.0062994 | 0.062447 | -5.0673
06/12/2006 | 2006 | 24923 | 146 | 19269 | 0.77314 | 0.005858 | -0.25729 | -5.1399
10/12/2006 | 2006 | 24923 | 39 | 3517 | 0.14111 | 0.0015648 | -1.9582 | -6.46
11/12/2006 | 2006 | 24923 | 155 | 6888 | 0.27637 | 0.0062192 | -1.286 | -5.0801
12/12/2006 | 2006 | 24923 | 94 | 20619 | 0.82731 | 0.0037716 | -0.18958 | -5.5803
16/12/2006 | 2006 | 24923 | 769 | 57212 | 2.2956 | 0.030855 | 0.83097 | -3.4785
18/12/2006 | 2006 | 24923 | 343 | 20638 | 0.82807 | 0.013762 | -0.18866 | -4.2858
19/12/2006 | 2006 | 24923 | 101 | 2929 | 0.11752 | 0.0040525 | -2.1411 | -5.5084
20/12/2006 | 2006 | 24923 | 140 | 16415 | 0.65863 | 0.0056173 | -0.4176 | -5.1819
21/12/2006 | 2006 | 24923 | 240 | 12026 | 0.48253 | 0.0096297 | -0.72872 | -4.6429
23/12/2006 | 2006 | 24923 | 2466 | 103572 | 4.1557 | 0.098945 | 1.4245 | -2.3132
24/12/2006 | 2006 | 24923 | 1244 | 49931 | 2.0034 | 0.049914 | 0.69485 | -2.9975
28/12/2006 | 2006 | 24923 | 19 | 532 | 0.021346 | 0.00076235 | -3.8469 | -7.1791
02/01/2007 | 2006 | 24923 | 4141 | 57305 | 2.2993 | 0.16615 | 0.8326 | -1.7949
04/01/2007 | 2006 | 24923 | 2466 | 55405 | 2.223 | 0.098945 | 0.79888 | -2.3132
05/01/2007 | 2006 | 24923 | 475 | 4496 | 0.1804 | 0.019059 | -1.7126 | -3.9602
10/01/2007 | 2006 | 24923 | 65 | 1430 | 0.057377 | 0.002608 | -2.8581 | -5.9492
11/01/2007 | 2006 | 24923 | 131 | 8966 | 0.35975 | 0.0052562 | -1.0224 | -5.2483
13/01/2007 | 2006 | 24923 | 19 | 9215 | 0.36974 | 0.00076235 | -0.99496 | -7.1791
14/01/2007 | 2006 | 24923 | 76 | 13554 | 0.54384 | 0.0030494 | -0.60911 | -5.7928
15/01/2007 | 2006 | 24923 | 323 | 11114 | 0.44593 | 0.01296 | -0.80759 | -4.3459
20/01/2007 | 2006 | 24923 | 409 | 4203 | 0.16864 | 0.016411 | -1.78 | -4.1098
22/01/2007 | 2006 | 24923 | 144 | 20015 | 0.80307 | 0.0057778 | -0.21931 | -5.1537
23/01/2007 | 2006 | 24923 | 9 | 504 | 0.020222 | 0.00036111 | -3.901 | -7.9263
26/01/2007 | 2006 | 24923 | 156 | 5574 | 0.22365 | 0.0062593 | -1.4977 | -5.0737
31/01/2007 | 2006 | 24923 | 198 | 31968 | 1.2827 | 0.0079445 | 0.24894 | -4.8353
02/02/2007 | 2006 | 24923 | 17 | 7293 | 0.29262 | 0.0006821 | -1.2289 | -7.2903
05/02/2007 | 2006 | 24923 | 201 | 4020 | 0.1613 | 0.0080648 | -1.8245 | -4.8202
07/02/2007 | 2006 | 24923 | 54 | 2160 | 0.086667 | 0.0021667 | -2.4457 | -6.1346
12/02/2007 | 2006 | 24923 | 54 | 24768 | 0.99378 | 0.0021667 | -0.0062386 | -6.1346
15/02/2007 | 2006 | 24923 | 85 | 9739 | 0.39076 | 0.0034105 | -0.93965 | -5.6809
16/02/2007 | 2006 | 24923 | 44 | 7568 | 0.30366 | 0.0017654 | -1.1919 | -6.3394
17/02/2007 | 2006 | 24923 | 16 | 12640 | 0.50716 | 0.00064198 | -0.67892 | -7.351
19/02/2007 | 2006 | 24923 | 160 | 24714 | 0.99161 | 0.0064198 | -0.0084212 | -5.0484
21/02/2007 | 2006 | 24923 | 234 | 45126 | 1.8106 | 0.0093889 | 0.59367 | -4.6682
28/02/2007 | 2006 | 24923 | 6 | 1080 | 0.043333 | 0.00024074 | -3.1388 | -8.3318
05/03/2007 | 2006 | 24923 | 90 | 9976 | 0.40027 | 0.0036111 | -0.91561 | -5.6237
07/03/2007 | 2006 | 24923 | 49 | 2646 | 0.10617 | 0.0019661 | -2.2427 | -6.2317
09/03/2007 | 2006 | 24923 | 189 | 3024 | 0.12133 | 0.0075834 | -2.1092 | -4.8818
10/03/2007 | 2006 | 24923 | 5183 | 108843 | 4.3672 | 0.20796 | 1.4741 | -1.5704
13/03/2007 | 2006 | 24923 | 352 | 15747 | 0.63183 | 0.014124 | -0.45914 | -4.2599
14/03/2007 | 2006 | 24923 | 1397 | 66070 | 2.651 | 0.056053 | 0.97492 | -2.8815
15/03/2007 | 2006 | 24923 | 562 | 20667 | 0.82923 | 0.022549 | -0.18725 | -3.792
16/03/2007 | 2006 | 24923 | 10724 | 161463 | 6.4785 | 0.43029 | 1.8685 | -0.84331
18/03/2007 | 2006 | 24923 | 165 | 9998 | 0.40116 | 0.0066204 | -0.91341 | -5.0176
19/03/2007 | 2006 | 24923 | 69 | 5610 | 0.22509 | 0.0027685 | -1.4912 | -5.8894
20/03/2007 | 2006 | 24923 | 24 | 4224 | 0.16948 | 0.00096297 | -1.775 | -6.9455
25/03/2007 | 2006 | 24923 | 10 | 1710 | 0.068611 | 0.00040124 | -2.6793 | -7.821
26/03/2007 | 2006 | 24923 | 64 | 960 | 0.038519 | 0.0025679 | -3.2566 | -5.9647 | 0.038519 | 0.0025679
27/03/2007 | 2006 | 24923 | 75 | 12111 | 0.48594 | 0.0030093 | -0.72168 | -5.8061 | 0.48594 | 0.0030093
28/03/2007 | 2006 | 24923 | 40 | 920 | 0.036914 | 0.0016049 | -3.2992 | -6.4347 | 0.036914 | 0.0016049
29/03/2007 | 2006 | 24923 | 33 | 1089 | 0.043695 | 0.0013241 | -3.1305 | -6.627 | 0.043695 | 0.0013241 | -3.1305
30/03/2007 | 2006 | 24923 | 228 | 14094 | 0.5655 | 0.0091482 | -0.57004 | -4.6942 | 0.5655 | 0.0091482
31/03/2007 | 2006 | 24923 | 14 | 2170 | 0.087068 | 0.00056173 | -2.4411 | -7.4845 | 0.087068 | 0.00056173
02/04/2007 | 2007 | 25086 | 14 | 2940 | 0.1172 | 0.00055808 | -2.1439 | -7.491 | 0.1172 | 0.00055808
10/04/2007 | 2007 | 25086 | 29 | 3767 | 0.15016 | 0.001156 | -1.896 | -6.7628 | 0.15016 | 0.001156
11/04/2007 | 2007 | 25086 | 41 | 5239 | 0.20884 | 0.0016344 | -1.5662 | -6.4165 | 0.20884 | 0.0016344
13/04/2007 | 2007 | 25086 | 360 | 22053 | 0.8791 | 0.014351 | -0.12886 | -4.244 | 0.8791 | 0.014351
16/04/2007 | 2007 | 25086 | 18 | 3705 | 0.14769 | 0.00071753 | -1.9126 | -7.2397 | 0.14769 | 0.00071753
17/04/2007 | 2007 | 25086 | 407 | 31590 | 1.2593 | 0.016224 | 0.23053 | -4.1213 | 1.2593 | 0.016224
18/04/2007 | 2007 | 25086 | 206 | 2732 | 0.10891 | 0.0082118 | -2.2173 | -4.8022 | 0.10891 | 0.0082118
26/04/2007 | 2007 | 25086 | 1082 | 27050 | 1.0783 | 0.043132 | 0.075377 | -3.1435
01/05/2007 | 2007 | 25086 | 657 | 90747 | 3.6174 | 0.02619 | 1.2858 | -3.6424
03/05/2007 | 2007 | 25086 | 933 | 12924 | 0.51519 | 0.037192 | -0.66322 | -3.2917
06/05/2007 | 2007 | 25086 | 94 | 1840 | 0.073348 | 0.0037471 | -2.6125 | -5.5868
08/05/2007 | 2007 | 25086 | 18 | 6390 | 0.25472 | 0.00071753 | -1.3676 | -7.2397
09/05/2007 | 2007 | 25086 | 5080 | 101851 | 4.0601 | 0.2025 | 1.4012 | -1.597
15/05/2007 | 2007 | 25086 | 150 | 24985 | 0.99597 | 0.0059794 | -0.0040343 | -5.1194
18/05/2007 | 2007 | 25086 | 924 | 124048 | 4.9449 | 0.036833 | 1.5984 | -3.3014
19/05/2007 | 2007 | 25086 | 11 | 2627 | 0.10472 | 0.00043849 | -2.2565 | -7.7322
21/05/2007 | 2007 | 25086 | 12 | 2040 | 0.08132 | 0.00047835 | -2.5094 | -7.6452
23/05/2007 | 2007 | 25086 | 276 | 37424 | 1.4918 | 0.011002 | 0.4 | -4.5097
26/05/2007 | 2007 | 25086 | 7 | 1204 | 0.047995 | 0.00027904 | -3.0367 | -8.1842
28/05/2007 | 2007 | 25086 | 114 | 15263 | 0.60843 | 0.0045444 | -0.49688 | -5.3939
29/05/2007 | 2007 | 25086 | 3 | 12 | 0.00047835 | 0.00011959 | -7.6452 | -9.0315
30/05/2007 | 2007 | 25086 | 2 | 58 | 0.002312 | 7.9726e-05 | -6.0696 | -9.4369
31/05/2007 | 2007 | 25086 | 958 | 56825 | 2.2652 | 0.038189 | 0.81767 | -3.2652
01/06/2007 | 2007 | 25086 | 27 | 5289 | 0.21083 | 0.0010763 | -1.5567 | -6.8342
02/06/2007 | 2007 | 25086 | 90 | 12470 | 0.49709 | 0.0035877 | -0.69898 | -5.6303
05/06/2007 | 2007 | 25086 | 168 | 16089 | 0.64135 | 0.006697 | -0.44417 | -5.0061
06/06/2007 | 2007 | 25086 | 136 | 15412 | 0.61437 | 0.0054214 | -0.48716 | -5.2174
07/06/2007 | 2007 | 25086 | 1171 | 30409 | 1.2122 | 0.046679 | 0.19243 | -3.0645
08/06/2007 | 2007 | 25086 | 16 | 4488 | 0.1789 | 0.00063781 | -1.7209 | -7.3575
09/06/2007 | 2007 | 25086 | 21 | 1575 | 0.062784 | 0.00083712 | -2.7681 | -7.0855
12/06/2007 | 2007 | 25086 | 1946 | 7062 | 0.28151 | 0.077573 | -1.2676 | -2.5565
13/06/2007 | 2007 | 25086 | 1184 | 29329 | 1.1691 | 0.047198 | 0.15627 | -3.0534
14/06/2007 | 2007 | 25086 | 201 | 11527 | 0.4595 | 0.0080124 | -0.77762 | -4.8268
15/06/2007 | 2007 | 25086 | 121 | 3247 | 0.12943 | 0.0048234 | -2.0446 | -5.3343
16/06/2007 | 2007 | 25086 | 272 | 8374 | 0.33381 | 0.010843 | -1.0972 | -4.5243
17/06/2007 | 2007 | 25086 | 4 | 368 | 0.01467 | 0.00015945 | -4.222 | -8.7438
18/06/2007 | 2007 | 25086 | 205 | 15622 | 0.62274 | 0.0081719 | -0.47363 | -4.8071
20/06/2007 | 2007 | 25086 | 258 | 76070 | 3.0324 | 0.010285 | 1.1093 | -4.5771
21/06/2007 | 2007 | 25086 | 301 | 82354 | 3.2829 | 0.011999 | 1.1887 | -4.423
22/06/2007 | 2007 | 25086 | 2470 | 188608 | 7.5185 | 0.098461 | 2.0174 | -2.3181
23/06/2007 | 2007 | 25086 | 951 | 176847 | 7.0496 | 0.03791 | 1.953 | -3.2726
24/06/2007 | 2007 | 25086 | 1462 | 35600 | 1.4191 | 0.05828 | 0.35004 | -2.8425
25/06/2007 | 2007 | 25086 | 421 | 15011 | 0.59838 | 0.016782 | -0.51353 | -4.0874
26/06/2007 | 2007 | 25086 | 1835 | 37716 | 1.5035 | 0.073148 | 0.40777 | -2.6153
27/06/2007 | 2007 | 25086 | 71 | 7446 | 0.29682 | 0.0028303 | -1.2146 | -5.8674
29/06/2007 | 2007 | 25086 | 7 | 1120 | 0.044646 | 0.00027904 | -3.109 | -8.1842
03/07/2007 | 2007 | 25086 | 32 | 10496 | 0.4184 | 0.0012756 | -0.87132 | -6.6643
04/07/2007 | 2007 | 25086 | 21 | 1470 | 0.058598 | 0.00083712 | -2.837 | -7.0855
05/07/2007 | 2007 | 25086 | 2474 | 13614 | 0.54269 | 0.098621 | -0.61121 | -2.3165
06/07/2007 | 2007 | 25086 | 339 | 9968 | 0.39735 | 0.013514 | -0.92293 | -4.3041
07/07/2007 | 2007 | 25086 | 18 | 4860 | 0.19373 | 0.00071753 | -1.6413 | -7.2397
08/07/2007 | 2007 | 25086 | 217 | 18344 | 0.73124 | 0.0086502 | -0.31301 | -4.7502
09/07/2007 | 2007 | 25086 | 3 | 645 | 0.025712 | 0.00011959 | -3.6608 | -9.0315
10/07/2007 | 2007 | 25086 | 50 | 8100 | 0.32289 | 0.0019931 | -1.1304 | -6.218
11/07/2007 | 2007 | 25086 | 20 | 1640 | 0.065375 | 0.00079726 | -2.7276 | -7.1343
12/07/2007 | 2007 | 25086 | 21 | 756 | 0.030136 | 0.00083712 | -3.502 | -7.0855
13/07/2007 | 2007 | 25086 | 61 | 8930 | 0.35598 | 0.0024316 | -1.0329 | -6.0192
14/07/2007 | 2007 | 25086 | 75 | 9150 | 0.36475 | 0.0029897 | -1.0086 | -5.8126
16/07/2007 | 2007 | 25086 | 79 | 3397 | 0.13541 | 0.0031492 | -1.9994 | -5.7606
17/07/2007 | 2007 | 25086 | 170 | 18550 | 0.73946 | 0.0067767 | -0.30184 | -4.9943
18/07/2007 | 2007 | 25086 | 402 | 29502 | 1.176 | 0.016025 | 0.16215 | -4.1336
19/07/2007 | 2007 | 25086 | 226 | 11074 | 0.44144 | 0.009009 | -0.81771 | -4.7095
20/07/2007 | 2007 | 25086 | 201 | 12335 | 0.49171 | 0.0080124 | -0.70987 | -4.8268
23/07/2007 | 2007 | 25086 | 97 | 17751 | 0.70761 | 0.0038667 | -0.34587 | -5.5554
25/07/2007 | 2007 | 25086 | 138 | 9108 | 0.36307 | 0.0055011 | -1.0132 | -5.2028
29/07/2007 | 2007 | 25086 | 3 | 711 | 0.028343 | 0.00011959 | -3.5634 | -9.0315
31/07/2007 | 2007 | 25086 | 79 | 14615 | 0.5826 | 0.0031492 | -0.54026 | -5.7606
01/08/2007 | 2007 | 25086 | 237 | 45352 | 1.8079 | 0.0094475 | 0.59214 | -4.662
02/08/2007 | 2007 | 25086 | 7 | 2023 | 0.080643 | 0.00027904 | -2.5177 | -8.1842
06/08/2007 | 2007 | 25086 | 556 | 46502 | 1.8537 | 0.022164 | 0.61719 | -3.8093
07/08/2007 | 2007 | 25086 | 50 | 11796 | 0.47022 | 0.0019931 | -0.75455 | -6.218
08/08/2007 | 2007 | 25086 | 667 | 9025 | 0.35976 | 0.026589 | -1.0223 | -3.6273
13/08/2007 | 2007 | 25086 | 26 | 5538 | 0.22076 | 0.0010364 | -1.5107 | -6.872
14/08/2007 | 2007 | 25086 | 92 | 1173 | 0.046759 | 0.0036674 | -3.0627 | -5.6083
15/08/2007 | 2007 | 25086 | 92 | 8132 | 0.32416 | 0.0036674 | -1.1265 | -5.6083
17/08/2007 | 2007 | 25086 | 273 | 17394 | 0.69337 | 0.010883 | -0.36618 | -4.5206
20/08/2007 | 2007 | 25086 | 22 | 5412 | 0.21574 | 0.00087698 | -1.5337 | -7.039
23/08/2007 | 2007 | 25086 | 413 | 56853 | 2.2663 | 0.016463 | 0.81816 | -4.1066
24/08/2007 | 2007 | 25086 | 3 | 792 | 0.031571 | 0.00011959 | -3.4555 | -9.0315
27/08/2007 | 2007 | 25086 | 26 | 1820 | 0.07255 | 0.0010364 | -2.6235 | -6.872
28/08/2007 | 2007 | 25086 | 580 | 16197 | 0.64566 | 0.02312 | -0.43748 | -3.767
29/08/2007 | 2007 | 25086 | 19 | 1472 | 0.058678 | 0.00075739 | -2.8357 | -7.1856
30/08/2007 | 2007 | 25086 | 14 | 4886 | 0.19477 | 0.00055808 | -1.6359 | -7.491
31/08/2007 | 2007 | 25086 | 50 | 4293 | 0.17113 | 0.0019931 | -1.7653 | -6.218
01/09/2007 | 2007 | 25086 | 7 | 1099 | 0.043809 | 0.00027904 | -3.1279 | -8.1842
03/09/2007 | 2007 | 25086 | 60 | 878 | 0.035 | 0.0023918 | -3.3524 | -6.0357
05/09/2007 | 2007 | 25086 | 74 | 9130 | 0.36395 | 0.0029499 | -1.0107 | -5.826
06/09/2007 | 2007 | 25086 | 743 | 69025 | 2.7515 | 0.029618 | 1.0122 | -3.5194
07/09/2007 | 2007 | 25086 | 18 | 3096 | 0.12342 | 0.00071753 | -2.0922 | -7.2397
11/09/2007 | 2007 | 25086 | 115 | 5037 | 0.20079 | 0.0045842 | -1.6055 | -5.3851
15/09/2007 | 2007 | 25086 | 1106 | 44469 | 1.7727 | 0.044088 | 0.57248 | -3.1216
18/09/2007 | 2007 | 25086 | 8 | 548 | 0.021845 | 0.0003189 | -3.8238 | -8.0506
20/09/2007 | 2007 | 25086 | 80 | 15050 | 0.59994 | 0.003189 | -0.51093 | -5.748
27/09/2007 | 2007 | 25086 | 7 | 546 | 0.021765 | 0.00027904 | -3.8274 | -8.1842
02/10/2007 | 2007 | 25086 | 115 | 98544 | 3.9282 | 0.0045842 | 1.3682 | -5.3851
03/10/2007 | 2007 | 25086 | 88 | 22192 | 0.88464 | 0.0035079 | -0.12258 | -5.6527
04/10/2007 | 2007 | 25086 | 675 | 50625 | 2.0181 | 0.026907 | 0.70214 | -3.6154
05/10/2007 | 2007 | 25086 | 1174 | 240969 | 9.6057 | 0.046799 | 2.2624 | -3.0619
06/10/2007 | 2007 | 25086 | 18 | 864 | 0.034442 | 0.00071753 | -3.3685 | -7.2397
07/10/2007 | 2007 | 25086 | 3421 | 117101 | 4.668 | 0.13637 | 1.5407 | -1.9924
08/10/2007 | 2007 | 25086 | 354 | 12231 | 0.48756 | 0.014111 | -0.71834 | -4.2608
09/10/2007 | 2007 | 25086 | 186 | 19281 | 0.7686 | 0.0074145 | -0.26319 | -4.9043
10/10/2007 | 2007 | 25086 | 32 | 8240 | 0.32847 | 0.0012756 | -1.1133 | -6.6643
11/10/2007 | 2007 | 25086 | 686 | 94200 | 3.7551 | 0.027346 | 1.3231 | -3.5992
14/10/2007 | 2007 | 25086 | 1025 | 89489 | 3.5673 | 0.040859 | 1.2718 | -3.1976
15/10/2007 | 2007 | 25086 | 303 | 31983 | 1.2749 | 0.012078 | 0.24289 | -4.4163
16/10/2007 | 2007 | 25086 | 92 | 6933 | 0.27637 | 0.0036674 | -1.286 | -5.6083
17/10/2007 | 2007 | 25086 | 7525 | 292359 | 11.6543 | 0.29997 | 2.4557 | -1.2041
18/10/2007 | 2007 | 25086 | 938 | 101804 | 4.0582 | 0.037391 | 1.4007 | -3.2863
19/10/2007 | 2007 | 25086 | 663 | 20446 | 0.81504 | 0.026429 | -0.20452 | -3.6333
20/10/2007 | 2007 | 25086 | 164 | 6773 | 0.26999 | 0.0065375 | -1.3094 | -5.0302
22/10/2007 | 2007 | 25086 | 1103 | 15158 | 0.60424 | 0.043969 | -0.50378 | -3.1243
23/10/2007 | 2007 | 25086 | 118 | 6490 | 0.25871 | 0.0047038 | -1.352 | -5.3594
26/10/2007 | 2007 | 25086 | 60 | 3524 | 0.14048 | 0.0023918 | -1.9627 | -6.0357
27/10/2007 | 2007 | 25086 | 75 | 11550 | 0.46042 | 0.0029897 | -0.77562 | -5.8126
28/10/2007 | 2007 | 25086 | 1446 | 15906 | 0.63406 | 0.057642 | -0.45561 | -2.8535
29/10/2007 | 2007 | 25086 | 118 | 15684 | 0.62521 | 0.0047038 | -0.46967 | -5.3594
01/11/2007 | 2007 | 25086 | 12 | 1440 | 0.057403 | 0.00047835 | -2.8577 | -7.6452
02/11/2007 | 2007 | 25086 | 138 | 6674 | 0.26604 | 0.0055011 | -1.3241 | -5.2028
04/11/2007 | 2007 | 25086 | 68 | 12580 | 0.50147 | 0.0027107 | -0.6902 | -5.9106
06/11/2007 | 2007 | 25086 | 1041 | 33025 | 1.3165 | 0.041497 | 0.27495 | -3.1821
07/11/2007 | 2007 | 25086 | 2470 | 35872 | 1.43 | 0.098461 | 0.35765 | -2.3181
09/11/2007 | 2007 | 25086 | 219 | 8279 | 0.33002 | 0.00873 | -1.1086 | -4.741
10/11/2007 | 2007 | 25086 | 1062 | 34902 | 1.3913 | 0.042334 | 0.33023 | -3.1622
13/11/2007 | 2007 | 25086 | 140 | 5611 | 0.22367 | 0.0055808 | -1.4976 | -5.1884
14/11/2007 | 2007 | 25086 | 372 | 99175 | 3.9534 | 0.014829 | 1.3746 | -4.2112
21/11/2007 | 2007 | 25086 | 61 | 7404 | 0.29514 | 0.0024316 | -1.2203 | -6.0192
22/11/2007 | 2007 | 25086 | 20 | 4900 | 0.19533 | 0.00079726 | -1.6331 | -7.1343
24/11/2007 | 2007 | 25086 | 40 | 9600 | 0.38268 | 0.0015945 | -0.96055 | -6.4412
26/11/2007 | 2007 | 25086 | 21 | 147 | 0.0058598 | 0.00083712 | -5.1396 | -7.0855
28/11/2007 | 2007 | 25086 | 712 | 32224 | 1.2845 | 0.028382 | 0.2504 | -3.562
01/12/2007 | 2007 | 25086 | 10 | 2000 | 0.079726 | 0.00039863 | -2.5292 | -7.8275
03/12/2007 | 2007 | 25086 | 139 | 13864 | 0.55266 | 0.0055409 | -0.59301 | -5.1956
06/12/2007 | 2007 | 25086 | 939 | 129569 | 5.165 | 0.037431 | 1.6419 | -3.2852
07/12/2007 | 2007 | 25086 | 1189 | 162251 | 6.4678 | 0.047397 | 1.8668 | -3.0492
09/12/2007 | 2007 | 25086 | 191 | 6494 | 0.25887 | 0.0076138 | -1.3514 | -4.8778
12/12/2007 | 2007 | 25086 | 57 | 20520 | 0.81799 | 0.0022722 | -0.20091 | -6.087
13/12/2007 | 2007 | 25086 | 93 | 8985 | 0.35817 | 0.0037072 | -1.0268 | -5.5975
18/12/2007 | 2007 | 25086 | 67 | 15075 | 0.60093 | 0.0026708 | -0.50927 | -5.9254
19/12/2007 | 2007 | 25086 | 84 | 10140 | 0.40421 | 0.0033485 | -0.90582 | -5.6992
20/12/2007 | 2007 | 25086 | 19338 | 1342463 | 53.5144 | 0.77087 | 3.98 | -0.26024
21/12/2007 | 2007 | 25086 | 95 | 3592 | 0.14319 | 0.003787 | -1.9436 | -5.5762
28/12/2007 | 2007 | 25086 | 77 | 9989 | 0.39819 | 0.0030694 | -0.92083 | -5.7863
30/12/2007 | 2007 | 25086 | 180 | 35615 | 1.4197 | 0.0071753 | 0.35046 | -4.9371
05/01/2008 | 2007 | 25086 | 1077 | 108944 | 4.3428 | 0.042932 | 1.4685 | -3.1481
08/01/2008 | 2007 | 25086 | 314 | 17341 | 0.69126 | 0.012517 | -0.36924 | -4.3807
10/01/2008 | 2007 | 25086 | 1092 | 71062 | 2.8327 | 0.04353 | 1.0412 | -3.1343
12/01/2008 | 2007 | 25086 | 143 | 20658 | 0.82349 | 0.0057004 | -0.19421 | -5.1672
18/01/2008 | 2007 | 25086 | 22 | 1420 | 0.056605 | 0.00087698 | -2.8717 | -7.039
19/01/2008 | 2007 | 25086 | 288 | 23308 | 0.92912 | 0.011481 | -0.073513 | -4.4671
20/01/2008 | 2007 | 25086 | 2520 | 121371 | 4.8382 | 0.10045 | 1.5765 | -2.2981
22/01/2008 | 2007 | 25086 | 2829 | 104885 | 4.181 | 0.11277 | 1.4306 | -2.1824
28/01/2008 | 2007 | 25086 | 374 | 4862 | 0.19381 | 0.014909 | -1.6409 | -4.2058
29/01/2008 | 2007 | 25086 | 76 | 3382 | 0.13482 | 0.0030296 | -2.0038 | -5.7993
31/01/2008 | 2007 | 25086 | 69 | 4040 | 0.16105 | 0.0027505 | -1.8261 | -5.896
01/02/2008 | 2007 | 25086 | 43 | 7783 | 0.31025 | 0.0017141 | -1.1704 | -6.3689
06/02/2008 | 2007 | 25086 | 922 | 11064 | 0.44104 | 0.036754 | -0.81861 | -3.3035
07/02/2008 | 2007 | 25086 | 237 | 33256 | 1.3257 | 0.0094475 | 0.28193 | -4.662
10/02/2008 | 2007 | 25086 | 118 | 12036 | 0.47979 | 0.0047038 | -0.73441 | -5.3594
11/02/2008 | 2007 | 25086 | 119 | 2142 | 0.085386 | 0.0047437 | -2.4606 | -5.3509
14/02/2008 | 2007 | 25086 | 286 | 15749 | 0.6278 | 0.011401 | -0.46553 | -4.4741
17/02/2008 | 2007 | 25086 | 364 | 31512 | 1.2562 | 0.01451 | 0.22806 | -4.2329
19/02/2008 | 2007 | 25086 | 5 | 370 | 0.014749 | 0.00019931 | -4.2166 | -8.5206
21/02/2008 | 2007 | 25086 | 160 | 30629 | 1.221 | 0.0063781 | 0.19964 | -5.0549
23/02/2008 | 2007 | 25086 | 465 | 29983 | 1.1952 | 0.018536 | 0.17832 | -3.988
26/02/2008 | 2007 | 25086 | 65 | 9230 | 0.36793 | 0.0025911 | -0.99985 | -5.9557
27/02/2008 | 2007 | 25086 | 54 | 5238 | 0.2088 | 0.0021526 | -1.5664 | -6.1411
28/02/2008 | 2007 | 25086 | 91 | 546 | 0.021765 | 0.0036275 | -3.8274 | -5.6192
29/02/2008 | 2007 | 25086 | 1142 | 21025 | 0.83812 | 0.045523 | -0.1766 | -3.0895
02/03/2008 | 2007 | 25086 | 96 | 11350 | 0.45244 | 0.0038268 | -0.79309 | -5.5657
03/03/2008 | 2007 | 25086 | 184 | 58342 | 2.3257 | 0.0073348 | 0.84401 | -4.9151
04/03/2008 | 2007 | 25086 | 127 | 11406 | 0.45468 | 0.0050626 | -0.78817 | -5.2859
05/03/2008 | 2007 | 25086 | 70 | 3930 | 0.15666 | 0.0027904 | -1.8537 | -5.8816
07/03/2008 | 2007 | 25086 | 40 | 2000 | 0.079726 | 0.0015945 | -2.5292 | -6.4412
11/03/2008 | 2007 | 25086 | 226 | 7006 | 0.27928 | 0.009009 | -1.2755 | -4.7095
12/03/2008 | 2007 | 25086 | 58 | 3480 | 0.13872 | 0.002312 | -1.9753 | -6.0696
17/03/2008 | 2007 | 25086 | 113 | 10848 | 0.43243 | 0.0045045 | -0.83833 | -5.4027
19/03/2008 | 2007 | 25086 | 10 | 240 | 0.0095671 | 0.00039863 | -4.6494 | -7.8275
22/03/2008 | 2007 | 25086 | 50 | 3206 | 0.1278 | 0.0019931 | -2.0573 | -6.218
27/03/2008 | 2007 | 25086 | 5 | 1625 | 0.064777 | 0.00019931 | -2.7368 | -8.5206
28/03/2008 | 2007 | 25086 | 27 | 297 | 0.011839 | 0.0010763 | -4.4363 | -6.8342
29/03/2008 | 2007 | 25086 | 175 | 19775 | 0.78829 | 0.006976 | -0.23789 | -4.9653
31/03/2008 | 2007 | 25086 | 142 | 33086 | 1.3189 | 0.0056605 | 0.2768 | -5.1742
01/04/2008 | 2008 | 25248 | 1392 | 87762 | 3.476 | 0.055133 | 1.2459 | -2.898
02/04/2008 | 2008 | 25248 | 26 | 8450 | 0.33468 | 0.0010298 | -1.0946 | -6.8784
04/04/2008 | 2008 | 25248 | 26 | 2262 | 0.089591 | 0.0010298 | -2.4125 | -6.8784
07/04/2008 | 2008 | 25248 | 118 | 4181 | 0.1656 | 0.0046736 | -1.7982 | -5.3658
08/04/2008 | 2008 | 25248 | 522 | 43381 | 1.7182 | 0.020675 | 0.54127 | -3.8788
09/04/2008 | 2008 | 25248 | 75 | 9750 | 0.38617 | 0.0029705 | -0.95148 | -5.819
10/04/2008 | 2008 | 25248 | 2487 | 47368 | 1.8761 | 0.098503 | 0.6292 | -2.3177
12/04/2008 | 2008 | 25248 | 29 | 1160 | 0.045944 | 0.0011486 | -3.0803 | -6.7692
15/04/2008 | 2008 | 25248 | 399 | 17790 | 0.70461 | 0.015803 | -0.35011 | -4.1475
16/04/2008 | 2008 | 25248 | 92 | 28964 | 1.1472 | 0.0036439 | 0.13731 | -5.6147
17/04/2008 | 2008 | 25248 | 565 | 115131 | 4.56 | 0.022378 | 1.5173 | -3.7997
18/04/2008 | 2008 | 25248 | 237 | 32713 | 1.2957 | 0.0093869 | 0.25903 | -4.6684
19/04/2008 | 2008 | 25248 | 202 | 2020 | 0.080006 | 0.0080006 | -2.5256 | -4.8282
21/04/2008 | 2008 | 25248 | 206 | 1276 | 0.050539 | 0.0081591 | -2.985 | -4.8086
22/04/2008 | 2008 | 25248 | 16 | 1952 | 0.077313 | 0.00063371 | -2.5599 | -7.3639
23/04/2008 | 2008 | 25248 | 9 | 2538 | 0.10052 | 0.00035646 | -2.2974 | -7.9393
25/04/2008 | 2008 | 25248 | 636 | 2872 | 0.11375 | 0.02519 | -2.1737 | -3.6813
26/04/2008 | 2008 | 25248 | 2487 | 19896 | 0.78802 | 0.098503 | -0.23823 | -2.3177
28/04/2008 | 2008 | 25248 | 78 | 3978 | 0.15756 | 0.0030894 | -1.848 | -5.7798
29/04/2008 | 2008 | 25248 | 230 | 16444 | 0.6513 | 0.0091096 | -0.42879 | -4.6984
30/04/2008 | 2008 | 25248 | 97 | 15752 | 0.62389 | 0.0038419 | -0.47178 | -5.5618
01/05/2008 | 2008 | 25248 | 517 | 376728 | 14.9211 | 0.020477 | 2.7028 | -3.8885
05/05/2008 | 2008 | 25248 | 120 | 21366 | 0.84625 | 0.0047529 | -0.16695 | -5.349
07/05/2008 | 2008 | 25248 | 63 | 2268 | 0.089829 | 0.0024952 | -2.4098 | -5.9934
08/05/2008 | 2008 | 25248 | 294 | 22549 | 0.8931 | 0.011644 | -0.11306 | -4.4529
11/05/2008 | 2008 | 25248 | 433 | 74609 | 2.955 | 0.01715 | 1.0835 | -4.0658
12/05/2008 | 2008 | 25248 | 119 | 5510 | 0.21824 | 0.0047132 | -1.5222 | -5.3574
14/05/2008 | 2008 | 25248 | 707 | 33282 | 1.3182 | 0.028002 | 0.27627 | -3.5755
16/05/2008 | 2008 | 25248 | 96 | 5652 | 0.22386 | 0.0038023 | -1.4967 | -5.5722
20/05/2008 | 2008 | 25248 | 37 | 6586 | 0.26085 | 0.0014655 | -1.3438 | -6.5256
23/05/2008 | 2008 | 25248 | 16 | 3286 | 0.13015 | 0.00063371 | -2.0391 | -7.3639
25/05/2008 | 2008 | 25248 | 218 | 28694 | 1.1365 | 0.0086343 | 0.12794 | -4.752
26/05/2008 | 2008 | 25248 | 238 | 21812 | 0.86391 | 0.0094265 | -0.14629 | -4.6642
27/05/2008 | 2008 | 25248 | 1296 | 81140 | 3.2137 | 0.051331 | 1.1674 | -2.9695
29/05/2008 | 2008 | 25248 | 1830 | 44894 | 1.7781 | 0.072481 | 0.57556 | -2.6244
30/05/2008 | 2008 | 25248 | 936 | 30635 | 1.2134 | 0.037072 | 0.1934 | -3.2949
31/05/2008 | 2008 | 25248 | 399 | 30828 | 1.221 | 0.015803 | 0.19968 | -4.1475
01/06/2008 | 2008 | 25248 | 734 | 32311 | 1.2797 | 0.029072 | 0.24666 | -3.538
03/06/2008 | 2008 | 25248 | 427 | 8721 | 0.34541 | 0.016912 | -1.063 | -4.0797
04/06/2008 | 2008 | 25248 | 47 | 7896 | 0.31274 | 0.0018615 | -1.1624 | -6.2864
06/06/2008 | 2008 | 25248 | 78 | 13650 | 0.54064 | 0.0030894 | -0.61501 | -5.7798
07/06/2008 | 2008 | 25248 | 2294 | 128896 | 5.1052 | 0.090859 | 1.6303 | -2.3984
08/06/2008 | 2008 | 25248 | 1263 | 35154 | 1.3923 | 0.050024 | 0.33099 | -2.9953
12/06/2008 | 2008 | 25248 | 55 | 3490 | 0.13823 | 0.0021784 | -1.9788 | -6.1292
13/06/2008 | 2008 | 25248 | 378 | 37748 | 1.4951 | 0.014971 | 0.40219 | -4.2016
15/06/2008 | 2008 | 25248 | 60 | 1020 | 0.040399 | 0.0023764 | -3.2089 | -6.0422
16/06/2008 | 2008 | 25248 | 288 | 43573 | 1.7258 | 0.011407 | 0.54569 | -4.4735
17/06/2008 | 2008 | 25248 | 305 | 26984 | 1.0688 | 0.01208 | 0.066497 | -4.4162
19/06/2008 | 2008 | 25248 | 63 | 23310 | 0.92324 | 0.0024952 | -0.079864 | -5.9934
23/06/2008 | 2008 | 25248 | 7 | 406 | 0.01608 | 0.00027725 | -4.1301 | -8.1906
24/06/2008 | 2008 | 25248 | 253 | 12991 | 0.51454 | 0.010021 | -0.66449 | -4.6031
26/06/2008 | 2008 | 25248 | 222 | 13320 | 0.52757 | 0.0087928 | -0.63948 | -4.7338
27/06/2008 | 2008 | 25248 | 693 | 78941 | 3.1266 | 0.027448 | 1.14 | -3.5955
29/06/2008 | 2008 | 25248 | 404 | 43979 | 1.7419 | 0.016001 | 0.55497 | -4.1351
01/07/2008 | 2008 | 25248 | 5 | 1615 | 0.063965 | 0.00019804 | -2.7494 | -8.5271
03/07/2008 | 2008 | 25248 | 55 | 2721 | 0.10777 | 0.0021784 | -2.2277 | -6.1292
04/07/2008 | 2008 | 25248 | 261 | 24831 | 0.98348 | 0.010337 | -0.016654 | -4.572
06/07/2008 | 2008 | 25248 | 2079 | 125918 | 4.9872 | 0.082343 | 1.6069 | -2.4969
07/07/2008 | 2008 | 25248 | 977 | 37383 | 1.4806 | 0.038696 | 0.39247 | -3.252
08/07/2008 | 2008 | 25248 | 28 | 5880 | 0.23289 | 0.001109 | -1.4572 | -6.8043
09/07/2008 | 2008 | 25248 | 36 | 3228 | 0.12785 | 0.0014259 | -2.0569 | -6.553
10/07/2008 | 2008 | 25248 | 42 | 12106 | 0.47948 | 0.0016635 | -0.73505 | -6.3988
14/07/2008 | 2008 | 25248 | 27 | 2093 | 0.082898 | 0.0010694 | -2.4901 | -6.8407
15/07/2008 | 2008 | 25248 | 276 | 39640 | 1.57 | 0.010932 | 0.45109 | -4.5161
16/07/2008 | 2008 | 25248 | 102 | 10234 | 0.40534 | 0.0040399 | -0.90303 | -5.5115
17/07/2008 | 2008 | 25248 | 38 | 4857 | 0.19237 | 0.0015051 | -1.6483 | -6.4989
18/07/2008 | 2008 | 25248 | 280 | 6661 | 0.26382 | 0.01109 | -1.3325 | -4.5017
19/07/2008 | 2008 | 25248 | 92 | 12647 | 0.50091 | 0.0036439 | -0.69133 | -5.6147
21/07/2008 | 2008 | 25248 | 120 | 23160 | 0.9173 | 0.0047529 | -0.08632 | -5.349
24/07/2008 | 2008 | 25248 | 150 | 12435 | 0.49251 | 0.0059411 | -0.70823 | -5.1259
27/07/2008 | 2008 | 25248 | 368 | 13104 | 0.51901 | 0.014575 | -0.65583 | -4.2284
29/07/2008 | 2008 | 25248 | 10 | 910 | 0.036042 | 0.00039607 | -3.3231 | -7.8339
30/07/2008 | 2008 | 25248 | 4620 | 324791 | 12.864 | 0.18298 | 2.5544 | -1.6984
31/07/2008 | 2008 | 25248 | 1015 | 130175 | 5.1559 | 0.040201 | 1.6401 | -3.2139
01/08/2008 | 2008 | 25248 | 52 | 6001 | 0.23768 | 0.0020596 | -1.4368 | -6.1853
02/08/2008 | 2008 | 25248 | 169 | 13738 | 0.54412 | 0.0066936 | -0.60858 | -5.0066
03/08/2008 | 2008 | 25248 | 245 | 12019 | 0.47604 | 0.0097037 | -0.74226 | -4.6352
04/08/2008 | 2008 | 25248 | 142 | 13574 | 0.53763 | 0.0056242 | -0.62059 | -5.1807
05/08/2008 | 2008 | 25248 | 117 | 18954 | 0.75071 | 0.004634 | -0.28673 | -5.3743
06/08/2008 | 2008 | 25248 | 179 | 8001 | 0.3169 | 0.0070897 | -1.1492 | -4.9491
07/08/2008 | 2008 | 25248 | 1989 | 57743 | 2.287 | 0.078779 | 0.82726 | -2.5411
08/08/2008 | 2008 | 25248 | 1688 | 33866 | 1.3413 | 0.066857 | 0.29366 | -2.7052
09/08/2008 | 2008 | 25248 | 878 | 53437 | 2.1165 | 0.034775 | 0.74976 | -3.3589
10/08/2008 | 2008 | 25248 | 280 | 19625 | 0.77729 | 0.01109 | -0.25194 | -4.5017
12/08/2008 | 2008 | 25248 | 17 | 3383 | 0.13399 | 0.00067332 | -2.01 | -7.3033
13/08/2008 | 2008 | 25248 | 4 | 2128 | 0.084284 | 0.00015843 | -2.4736 | -8.7502
14/08/2008 | 2008 | 25248 | 426 | 37645 | 1.491 | 0.016873 | 0.39945 | -4.0821
15/08/2008 | 2008 | 25248 | 507 | 64093 | 2.5385 | 0.020081 | 0.93159 | -3.908
18/08/2008 | 2008 | 25248 | 411 | 52949 | 2.0972 | 0.016279 | 0.74058 | -4.1179
19/08/2008 | 2008 | 25248 | 18 | 720 | 0.028517 | 0.00071293 | -3.5573 | -7.2461
20/08/2008 | 2008 | 25248 | 57 | 7625 | 0.302 | 0.0022576 | -1.1973 | -6.0935
26/08/2008 | 2008 | 25248 | 27 | 15417 | 0.61062 | 0.0010694 | -0.49328 | -6.8407
27/08/2008 | 2008 | 25248 | 169 | 23330 | 0.92403 | 0.0066936 | -0.079007 | -5.0066
03/09/2008 | 2008 | 25248 | 66 | 594 | 0.023527 | 0.0026141 | -3.7496 | -5.9468
04/09/2008 | 2008 | 25248 | 21 | 5649 | 0.22374 | 0.00083175 | -1.4973 | -7.092
05/09/2008 | 2008 | 25248 | 1695 | 93858 | 3.7174 | 0.067134 | 1.313 | -2.7011
09/09/2008 | 2008 | 25248 | 17 | 3655 | 0.14476 | 0.00067332 | -1.9327 | -7.3033
10/09/2008 | 2008 | 25248 | 31 | 5580 | 0.22101 | 0.0012278 | -1.5096 | -6.7025
11/09/2008 | 2008 | 25248 | 308 | 48626 | 1.9259 | 0.012199 | 0.65541 | -4.4064
12/09/2008 | 2008 | 25248 | 750 | 29408 | 1.1648 | 0.029705 | 0.15252 | -3.5164
15/09/2008 | 2008 | 25248 | 4 | 1200 | 0.047529 | 0.00015843 | -3.0464 | -8.7502
16/09/2008 | 2008 | 25248 | 16 | 1496 | 0.059252 | 0.00063371 | -2.826 | -7.3639
22/09/2008 | 2008 | 25248 | 14 | 3780 | 0.14971 | 0.0005545 | -1.899 | -7.4974
23/09/2008 | 2008 | 25248 | 30 | 900 | 0.035646 | 0.0011882 | -3.3341 | -6.7353
24/09/2008 | 2008 | 25248 | 86 | 6150 | 0.24358 | 0.0034062 | -1.4123 | -5.6822
25/09/2008 | 2008 | 25248 | 73 | 20805 | 0.82403 | 0.0028913 | -0.19355 | -5.846
29/09/2008 | 2008 | 25248 | 92 | 11800 | 0.46736 | 0.0036439 | -0.76065 | -5.6147
30/09/2008 | 2008 | 25248 | 45 | 7419 | 0.29385 | 0.0017823 | -1.2247 | -6.3298
02/10/2008 | 2008 | 25248 | 146 | 37473 | 1.4842 | 0.0057826 | 0.39487 | -5.1529
03/10/2008 | 2008 | 25248 | 63 | 4374 | 0.17324 | 0.0024952 | -1.7531 | -5.9934
04/10/2008 | 2008 | 25248 | 733 | 24778 | 0.98138 | 0.029032 | -0.018791 | -3.5394
07/10/2008 | 2008 | 25248 | 2775 | 576756 | 22.8436 | 0.10991 | 3.1287 | -2.2081
08/10/2008 | 2008 | 25248 | 526 | 53973 | 2.1377 | 0.020833 | 0.75974 | -3.8712
09/10/2008 | 2008 | 25248 | 123 | 33902 | 1.3428 | 0.0048717 | 0.29473 | -5.3243
10/10/2008 | 2008 | 25248 | 53 | 1007 | 0.039884 | 0.0020992 | -3.2218 | -6.1662
13/10/2008 | 2008 | 25248 | 642 | 62274 | 2.4665 | 0.025428 | 0.9028 | -3.6719
14/10/2008 | 2008 | 25248 | 20 | 3500 | 0.13862 | 0.00079214 | -1.976 | -7.1408
15/10/2008 | 2008 | 25248 | 105 | 19929 | 0.78933 | 0.0041587 | -0.23657 | -5.4825
16/10/2008 | 2008 | 25248 | 1297 | 23346 | 0.92467 | 0.05137 | -0.078321 | -2.9687
17/10/2008 | 2008 | 25248 | 115 | 12676 | 0.50206 | 0.0045548 | -0.68904 | -5.3916
21/10/2008 | 2008 | 25248 | 63 | 1386 | 0.054895 | 0.0024952 | -2.9023 | -5.9934
22/10/2008 | 2008 | 25248 | 74 | 5628 | 0.22291 | 0.0029309 | -1.501 | -5.8324
23/10/2008 | 2008 | 25248 | 5 | 600 | 0.023764 | 0.00019804 | -3.7396 | -8.5271
24/10/2008 | 2008 | 25248 | 69 | 5276 | 0.20897 | 0.0027329 | -1.5656 | -5.9024
28/10/2008 | 2008 | 25248 | 122 | 33008 | 1.3074 | 0.0048321 | 0.268 | -5.3325
29/10/2008 | 2008 | 25248 | 85 | 2250 | 0.089116 | 0.0033666 | -2.4178 | -5.6939
31/10/2008 | 2008 | 25248 | 6 | 1608 | 0.063688 | 0.00023764 | -2.7538 | -8.3447
01/11/2008 | 2008 | 25248 | 522 | 40017 | 1.585 | 0.020675 | 0.46056 | -3.8788
03/11/2008 | 2008 | 25248 | 812 | 14508 | 0.57462 | 0.032161 | -0.55405 | -3.437
05/11/2008 | 2008 | 25248 | 76 | 678 | 0.026854 | 0.0030101 | -3.6174 | -5.8058
06/11/2008 | 2008 | 25248 | 900 | 8245 | 0.32656 | 0.035646 | -1.1191 | -3.3341
07/11/2008 | 2008 | 25248 | 734 | 8542 | 0.33832 | 0.029072 | -1.0838 | -3.538
09/11/2008 | 2008 | 25248 | 833 | 175720 | 6.9598 | 0.032993 | 1.9401 | -3.4115
10/11/2008 | 2008 | 25248 | 50 | 3449 | 0.1366 | 0.0019804 | -1.9907 | -6.2245
12/11/2008 | 2008 | 25248 | 187 | 49036 | 1.9422 | 0.0074065 | 0.66381 | -4.9054
13/11/2008 | 2008 | 25248 | 21 | 819 | 0.032438 | 0.00083175 | -3.4284 | -7.092
17/11/2008 | 2008 | 25248 | 21 | 1329 | 0.052638 | 0.00083175 | -2.9443 | -7.092
18/11/2008 | 2008 | 25248 | 204 | 10980 | 0.43489 | 0.0080798 | -0.83267 | -4.8184
19/11/2008 | 2008 | 25248 | 129 | 28378 | 1.124 | 0.0051093 | 0.11687 | -5.2767
20/11/2008 | 2008 | 25248 | 5 | 940 | 0.037231 | 0.00019804 | -3.2906 | -8.5271
21/11/2008 | 2008 | 25248 | 39 | 9828 | 0.38926 | 0.0015447 | -0.94351 | -6.4729
22/11/2008 | 2008 | 25248 | 8 | 1920 | 0.076046 | 0.00031686 | -2.5764 | -8.0571
24/11/2008 | 2008 | 25248 | 172 | 6795 | 0.26913 | 0.0068124 | -1.3126 | -4.989
25/11/2008 | 2008 | 25248 | 266 | 11285 | 0.44697 | 0.010535 | -0.80527 | -4.553
27/11/2008 | 2008 | 25248 | 405 | 39357 | 1.5588 | 0.016041 | 0.44393 | -4.1326
01/12/2008 | 2008 | 25248 | 3 | 900 | 0.035646 | 0.00011882 | -3.3341 | -9.0379
03/12/2008 | 2008 | 25248 | 471 | 77005 | 3.0499 | 0.018655 | 1.1151 | -3.9816
05/12/2008 | 2008 | 25248 | 219 | 13697 | 0.5425 | 0.008674 | -0.61157 | -4.7474
06/12/2008 | 2008 | 25248 | 2512 | 59712 | 2.365 | 0.099493 | 0.86079 | -2.3077
08/12/2008 | 2008 | 25248 | 481 | 99892 | 3.9564 | 0.019051 | 1.3753 | -3.9606
09/12/2008 | 2008 | 25248 | 40 | 12432 | 0.4924 | 0.0015843 | -0.70847 | -6.4476
10/12/2008 | 2008 | 25248 | 27 | 6426 | 0.25452 | 0.0010694 | -1.3684 | -6.8407
11/12/2008 | 2008 | 25248 | 23 | 1357 | 0.053747 | 0.00091096 | -2.9235 | -7.001
15/12/2008 | 2008 | 25248 | 20 | 560 | 0.02218 | 0.00079214 | -3.8086 | -7.1408
16/12/2008 | 2008 | 25248 | 359 | 18094 | 0.71665 | 0.014219 | -0.33317 | -4.2532
19/12/2008 | 2008 | 25248 | 46 | 9200 | 0.36439 | 0.0018219 | -1.0095 | -6.3079
20/12/2008 | 2008 | 25248 | 34 | 4216 | 0.16698 | 0.0013466 | -1.7899 | -6.6101
22/12/2008 | 2008 | 25248 | 173 | 1384 | 0.054816 | 0.006852 | -2.9038 | -4.9832
25/12/2008 | 2008 | 25248 | 654 | 32373 | 1.2822 | 0.025903 | 0.24858 | -3.6534
30/12/2008 | 2008 | 25248 | 1175 | 29611 | 1.1728 | 0.046538 | 0.1594 | -3.0675
02/01/2009 | 2008 | 25248 | 207 | 16443 | 0.65126 | 0.0081987 | -0.42885 | -4.8038
05/01/2009 | 2008 | 25248 | 171 | 22463 | 0.88969 | 0.0067728 | -0.11688 | -4.9948
06/01/2009 | 2008 | 25248 | 11 | 1694 | 0.067094 | 0.00043568 | -2.7017 | -7.7386
07/01/2009 | 2008 | 25248 | 33 | 4719 | 0.18691 | 0.001307 | -1.6772 | -6.64
08/01/2009 | 2008 | 25248 | 398 | 26242 | 1.0394 | 0.015764 | 0.038614 | -4.1501
11/01/2009 | 2008 | 25248 | 152 | 31430 | 1.2449 | 0.0060203 | 0.21902 | -5.1126
12/01/2009 | 2008 | 25248 | 9 | 702 | 0.027804 | 0.00035646 | -3.5826 | -7.9393
17/01/2009 | 2008 | 25248 | 1085 | 49604 | 1.9647 | 0.042974 | 0.67532 | -3.1472
23/01/2009 | 2008 | 25248 | 11 | 1288 | 0.051014 | 0.00043568 | -2.9757 | -7.7386
27/01/2009 | 2008 | 25248 | 54 | 10986 | 0.43512 | 0.0021388 | -0.83213 | -6.1475
28/01/2009 | 2008 | 25248 | 6 | 2448 | 0.096958 | 0.00023764 | -2.3335 | -8.3447
01/02/2009 | 2008 | 25248 | 647 | 17309 | 0.68556 | 0.025626 | -0.37752 | -3.6642
02/02/2009 | 2008 | 25248 | 156 | 25184 | 0.99747 | 0.0061787 | -0.0025381 | -5.0866
03/02/2009 | 2008 | 25248 | 23 | 6440 | 0.25507 | 0.00091096 | -1.3662 | -7.001
04/02/2009 | 2008 | 25248 | 32 | 1936 | 0.076679 | 0.0012674 | -2.5681 | -6.6708
05/02/2009 | 2008 | 25248 | 4525 | 106313 | 4.2107 | 0.17922 | 1.4376 | -1.7191
08/02/2009 | 2008 | 25248 | 20 | 4392 | 0.17395 | 0.00079214 | -1.749 | -7.1408
09/02/2009 | 2008 | 25248 | 172 | 5511 | 0.21827 | 0.0068124 | -1.522 | -4.989
10/02/2009 | 2008 | 25248 | 311 | 20215 | 0.80066 | 0.012318 | -0.22232 | -4.3967
11/02/2009 | 2008 | 25248 | 38 | 7344 | 0.29087 | 0.0015051 | -1.2349 | -6.4989
12/02/2009 | 2008 | 25248 | 322 | 18502 | 0.73281 | 0.012753 | -0.31087 | -4.362
13/02/2009 | 2008 | 25248 | 882 | 70848 | 2.8061 | 0.034933 | 1.0318 | -3.3543
14/02/2009 | 2008 | 25248 | 156 | 5226 | 0.20699 | 0.0061787 | -1.5751 | -5.0866
16/02/2009 | 2008 | 25248 | 159 | 63052 | 2.4973 | 0.0062975 | 0.91521 | -5.0676
17/02/2009 | 2008 | 25248 | 10 | 14860 | 0.58856 | 0.00039607 | -0.53007 | -7.8339
18/02/2009 | 2008 | 25248 | 19 | 4274 | 0.16928 | 0.00075253 | -1.7762 | -7.1921
19/02/2009 | 2008 | 25248 | 37 | 5698 | 0.22568 | 0.0014655 | -1.4886 | -6.5256
23/02/2009 | 2008 | 25248 | 81 | 19041 | 0.75416 | 0.0032082 | -0.28215 | -5.7421
24/02/2009 | 2008 | 25248 | 32 | 4987 | 0.19752 | 0.0012674 | -1.6219 | -6.6708
25/02/2009 | 2008 | 25248 | 182 | 21101 | 0.83575 | 0.0072085 | -0.17943 | -4.9325
28/02/2009 | 2008 | 25248 | 56 | 4105 | 0.16259 | 0.002218 | -1.8165 | -6.1112
01/03/2009 | 2008 | 25248 | 92 | 4107 | 0.16267 | 0.0036439 | -1.8161 | -5.6147
02/03/2009 | 2008 | 25248 | 1718 | 71989 | 2.8513 | 0.068045 | 1.0478 | -2.6876
03/03/2009 | 2008 | 25248 | 189 | 18357 | 0.72707 | 0.0074857 | -0.31874 | -4.8948
04/03/2009 | 2008 | 25248 | 21 | 5933 | 0.23499 | 0.00083175 | -1.4482 | -7.092
05/03/2009 | 2008 | 25248 | 459 | 36994 | 1.4652 | 0.01818 | 0.38201 | -4.0075
06/03/2009 | 2008 | 25248 | 133 | 17324 | 0.68615 | 0.0052677 | -0.37665 | -5.2462
07/03/2009 | 2008 | 25248 | 11 | 1210 | 0.047925 | 0.00043568 | -3.0381 | -7.7386
09/03/2009 | 2008 | 25248 | 169 | 62009 | 2.456 | 0.0066936 | 0.89853 | -5.0066
10/03/2009 | 2008 | 25248 | 82 | 12206 | 0.48344 | 0.0032478 | -0.72682 | -5.7298
11/03/2009 | 2008 | 25248 | 518 | 34521 | 1.3673 | 0.020516 | 0.31282 | -3.8865
16/03/2009 | 2008 | 25248 | 63 | 10836 | 0.42918 | 0.0024952 | -0.84587 | -5.9934
17/03/2009 | 2008 | 25248 | 537 | 65926 | 2.6111 | 0.021269 | 0.95979 | -3.8505
18/03/2009 | 2008 | 25248 | 108 | 40980 | 1.6231 | 0.0042776 | 0.48434 | -5.4544
19/03/2009 | 2008 | 25248 | 1022 | 45921 | 1.8188 | 0.040478 | 0.59818 | -3.207
20/03/2009 | 2008 | 25248 | 76 | 2508 | 0.099335 | 0.0030101 | -2.3093 | -5.8058
22/03/2009 | 2008 | 25248 | 83 | 24568 | 0.97307 | 0.0032874 | -0.027302 | -5.7177
24/03/2009 | 2008 | 25248 | 159 | 21827 | 0.8645 | 0.0062975 | -0.1456 | -5.0676
25/03/2009 | 2008 | 25248 | 134 | 18972 | 0.75143 | 0.0053074 | -0.28578 | -5.2387
26/03/2009 | 2008 | 25248 | 8 | 1816 | 0.071926 | 0.00031686 | -2.6321 | -8.0571
28/03/2009 | 2008 | 25248 | 97 | 1699 | 0.067292 | 0.0038419 | -2.6987 | -5.5618
30/03/2009 | 2008 | 25248 | 100 | 10377 | 0.411 | 0.0039607 | -0.88916 | -5.5313
31/03/2009 | 2008 | 25248 | 5190 | 103252 | 4.0895 | 0.20556 | 1.4084 | -1.582
34003612

## 1c-.5 Year Boundary Values
AvgOfLogSaidi | SumOfLogSaidi | CountOfLogSaidi | StDevOfLogSaidi |  |  | AvgOfLogSaifi | SumOfLogSaifi | CountOfLogSaifi | StDevOfLogSaifi
-0.85907 | -836.7383 | 974 | 1.5954 |  |  | -5.313 | -5174.8939 | 974 | 1.6648
AvgOfLogSaidi |  |  | StDevOfLogSaidi | LogBoundarySaidi | BoundarySaidi | AvgOfLogSaifi |  |  | StDevOfLogSaifi | LogBoundarySaifi | BoundarySaifi
-0.85907 |  |  | 1.5954 | 3.1293 | 22.8581 | -5.3119 |  |  | 1.6648 | -1.1511 | 0.3163

## 1d-5 Year Fixed Data
[5 empty] | Sum of daily values in normalised dataset | 1251.4658 | 17.4728
[5 empty] | Average annual value | 250.2932 | 3.4946
2.7263
[5 empty] | Standard deviation x SQRT(365) | 52.0861 | 0.76226 |  |  | 19.105
52.0861
[5 empty] | Reliability Limit | 302.3793 | 4.2568
Date Outage | Year | Saidi | Safi | BoundarySaidi | BoundarySaifi | FixedSaidi | FixedSaifi
01/04/2004 | 2004 | 0.37915 | 0.0010864 | 22.8581 | 0.316240339279304 | 0.37915 | 0.0010864 | 0
02/04/2004 | 2004 | 0.29703 | 0.006639 | 22.8580564336757 | 0.316240339279304 | 0.29703 | 0.006639 | 0
08/04/2004 | 2004 | 0.062809 | 0.00064379 | 22.8580564336757 | 0.316240339279304 | 0.062809 | 0.00064379 | 0
12/04/2004 | 2004 | 0.43657 | 0.0087313 | 22.8580564336757 | 0.316240339279304 | 0.43657 | 0.0087313 | 0
13/04/2004 | 2004 | 0.46111 | 0.003742 | 22.8580564336757 | 0.316240339279304 | 0.46111 | 0.003742 | 0
15/04/2004 | 2004 | 0.18811 | 0.00060355 | 22.8580564336757 | 0.316240339279304 | 0.18811 | 0.00060355 | 0
16/04/2004 | 2004 | 0.02897 | 0.00016095 | 22.8580564336757 | 0.316240339279304 | 0.02897 | 0.00016095 | 0
20/04/2004 | 2004 | 1.0639 | 0.0065988 | 22.8580564336757 | 0.316240339279304 | 1.0639 | 0.0065988 | 0
21/04/2004 | 2004 | 0.030419 | 0.0025349 | 22.8580564336757 | 0.316240339279304 | 0.030419 | 0.0025349 | 0
26/04/2004 | 2004 | 0.37742 | 0.0026959 | 22.8580564336757 | 0.316240339279304 | 0.37742 | 0.0026959 | 0
29/04/2004 | 2004 | 0.50505 | 0.0094556 | 22.8580564336757 | 0.316240339279304 | 0.50505 | 0.0094556 | 0
30/04/2004 | 2004 | 0.048284 | 0.00016095 | 22.8580564336757 | 0.316240339279304 | 0.048284 | 0.00016095 | 0
03/05/2004 | 2004 | 0.41074 | 0.0027361 | 22.8580564336757 | 0.316240339279304 | 0.41074 | 0.0027361 | 0
04/05/2004 | 2004 | 0.16284 | 0.001529 | 22.8580564336757 | 0.316240339279304 | 0.16284 | 0.001529 | 0
05/05/2004 | 2004 | 0.12385 | 0.003058 | 22.8580564336757 | 0.316240339279304 | 0.12385 | 0.003058 | 0
06/05/2004 | 2004 | 0.67738 | 0.0018509 | 22.8580564336757 | 0.316240339279304 | 0.67738 | 0.0018509 | 0
07/05/2004 | 2004 | 0.037018 | 0.00020118 | 22.8580564336757 | 0.316240339279304 | 0.037018 | 0.00020118 | 0
08/05/2004 | 2004 | 0.031385 | 0.00052308 | 22.8580564336757 | 0.316240339279304 | 0.031385 | 0.00052308 | 0
10/05/2004 | 2004 | 0.065545 | 0.00092544 | 22.8580564336757 | 0.316240339279304 | 0.065545 | 0.00092544 | 0
12/05/2004 | 2004 | 0.30443 | 0.060677 | 22.8580564336757 | 0.316240339279304 | 0.30443 | 0.060677 | 0
13/05/2004 | 2004 | 0.57643 | 0.030338 | 22.8580564336757 | 0.316240339279304 | 0.57643 | 0.030338 | 0
14/05/2004 | 2004 | 2.3503 | 0.031022 | 22.8580564336757 | 0.316240339279304 | 2.3503 | 0.031022 | 0
16/05/2004 | 2004 | 0.5543 | 0.0019314 | 22.8580564336757 | 0.316240339279304 | 0.5543 | 0.0019314 | 0
17/05/2004 | 2004 | 3.9444 | 0.023619 | 22.8580564336757 | 0.316240339279304 | 3.9444 | 0.023619 | 0
18/05/2004 | 2004 | 0.012071 | 0.00040237 | 22.8580564336757 | 0.316240339279304 | 0.012071 | 0.00040237 | 0
20/05/2004 | 2004 | 0.02716 | 0.0018106 | 22.8580564336757 | 0.316240339279304 | 0.02716 | 0.0018106 | 0
23/05/2004 | 2004 | 0.14485 | 0.0024142 | 22.8580564336757 | 0.316240339279304 | 0.14485 | 0.0024142 | 0
24/05/2004 | 2004 | 1.1069 | 0.0070816 | 22.8580564336757 | 0.316240339279304 | 1.1069 | 0.0070816 | 0
27/05/2004 | 2004 | 0.11105 | 0.00048284 | 22.8580564336757 | 0.316240339279304 | 0.11105 | 0.00048284 | 0
28/05/2004 | 2004 | 0.38687 | 0.010985 | 22.8580564336757 | 0.316240339279304 | 0.38687 | 0.010985 | 0
29/05/2004 | 2004 | 2.944 | 0.049129 | 22.8580564336757 | 0.316240339279304 | 2.944 | 0.049129 | 0
30/05/2004 | 2004 | 0.50698 | 0.0028166 | 22.8580564336757 | 0.316240339279304 | 0.50698 | 0.0028166 | 0
31/05/2004 | 2004 | 1.5788 | 0.029735 | 22.8580564336757 | 0.316240339279304 | 1.5788 | 0.029735 | 0
01/06/2004 | 2004 | 3.0315 | 0.0136 | 22.8580564336757 | 0.316240339279304 | 3.0315 | 0.0136 | 0
02/06/2004 | 2004 | 0.12956 | 0.0011266 | 22.8580564336757 | 0.316240339279304 | 0.12956 | 0.0011266 | 0
03/06/2004 | 2004 | 0.88174 | 0.011306 | 22.8580564336757 | 0.316240339279304 | 0.88174 | 0.011306 | 0
04/06/2004 | 2004 | 0.78007 | 0.0064781 | 22.8580564336757 | 0.316240339279304 | 0.78007 | 0.0064781 | 0
08/06/2004 | 2004 | 0.19587 | 0.0026959 | 22.8580564336757 | 0.316240339279304 | 0.19587 | 0.0026959 | 0
10/06/2004 | 2004 | 0.43548 | 0.0025751 | 22.8580564336757 | 0.316240339279304 | 0.43548 | 0.0025751 | 0
12/06/2004 | 2004 | 1.0019 | 0.010542 | 22.8580564336757 | 0.316240339279304 | 1.0019 | 0.010542 | 0
13/06/2004 | 2004 | 0.26182 | 0.0034201 | 22.8580564336757 | 0.316240339279304 | 0.26182 | 0.0034201 | 0
19/06/2004 | 2004 | 0.80228 | 0.0041041 | 22.8580564336757 | 0.316240339279304 | 0.80228 | 0.0041041 | 0
22/06/2004 | 2004 | 0.11592 | 0.0017302 | 22.8580564336757 | 0.316240339279304 | 0.11592 | 0.0017302 | 0
23/06/2004 | 2004 | 0.36213 | 0.0020118 | 22.8580564336757 | 0.316240339279304 | 0.36213 | 0.0020118 | 0
24/06/2004 | 2004 | 1.4178 | 0.032069 | 22.8580564336757 | 0.316240339279304 | 1.4178 | 0.032069 | 0
28/06/2004 | 2004 | 13.1551 | 0.21032 | 22.8580564336757 | 0.316240339279304 | 13.1551 | 0.21032 | 0
30/06/2004 | 2004 | 19.1719 | 0.18911 | 22.8580564336757 | 0.316240339279304 | 19.1719 | 0.18911 | 0
01/07/2004 | 2004 | 32.1126 | 0.13632 | 22.8580564336757 | 0.316240339279304 | 22.8581 | 0.13632 | 1 | 9.2545 | 0
02/07/2004 | 2004 | 1.5996 | 0.0065988 | 22.8580564336757 | 0.316240339279304 | 1.5996 | 0.0065988 | 0
03/07/2004 | 2004 | 1.5741 | 0.0010462 | 22.8580564336757 | 0.316240339279304 | 1.5741 | 0.0010462 | 0
07/07/2004 | 2004 | 0.088923 | 0.0010462 | 22.8580564336757 | 0.316240339279304 | 0.088923 | 0.0010462 | 0
08/07/2004 | 2004 | 0.11999 | 0.0018509 | 22.8580564336757 | 0.316240339279304 | 0.11999 | 0.0018509 | 0
13/07/2004 | 2004 | 0.023579 | 0.0024947 | 22.8580564336757 | 0.316240339279304 | 0.023579 | 0.0024947 | 0
15/07/2004 | 2004 | 1.2537 | 0.0055929 | 22.8580564336757 | 0.316240339279304 | 1.2537 | 0.0055929 | 0
16/07/2004 | 2004 | 0.0080473 | 0.00020118 | 22.8580564336757 | 0.316240339279304 | 0.0080473 | 0.00020118 | 0
17/07/2004 | 2004 | 1.4688 | 0.010985 | 22.8580564336757 | 0.316240339279304 | 1.4688 | 0.010985 | 0
18/07/2004 | 2004 | 4.7072 | 0.0093349 | 22.8580564336757 | 0.316240339279304 | 4.7072 | 0.0093349 | 0
20/07/2004 | 2004 | 0.20436 | 0.00088521 | 22.8580564336757 | 0.316240339279304 | 0.20436 | 0.00088521 | 0
21/07/2004 | 2004 | 0.07315 | 0.00096568 | 22.8580564336757 | 0.316240339279304 | 0.07315 | 0.00096568 | 0
23/07/2004 | 2004 | 2.6614 | 0.017463 | 22.8580564336757 | 0.316240339279304 | 2.6614 | 0.017463 | 0
24/07/2004 | 2004 | 1.7011 | 0.0089728 | 22.8580564336757 | 0.316240339279304 | 1.7011 | 0.0089728 | 0
25/07/2004 | 2004 | 0.092947 | 0.0028166 | 22.8580564336757 | 0.316240339279304 | 0.092947 | 0.0028166 | 0
28/07/2004 | 2004 | 0.51406 | 0.067477 | 22.8580564336757 | 0.316240339279304 | 0.51406 | 0.067477 | 0
29/07/2004 | 2004 | 2.5142 | 0.021567 | 22.8580564336757 | 0.316240339279304 | 2.5142 | 0.021567 | 0
02/08/2004 | 2004 | 0.26653 | 0.00048284 | 22.8580564336757 | 0.316240339279304 | 0.26653 | 0.00048284 | 0
03/08/2004 | 2004 | 0.58516 | 0.0024142 | 22.8580564336757 | 0.316240339279304 | 0.58516 | 0.0024142 | 0
06/08/2004 | 2004 | 0.28226 | 0.0030982 | 22.8580564336757 | 0.316240339279304 | 0.28226 | 0.0030982 | 0
11/08/2004 | 2004 | 3.1358 | 0.028407 | 22.8580564336757 | 0.316240339279304 | 3.1358 | 0.028407 | 0
12/08/2004 | 2004 | 0.056331 | 0.0011266 | 22.8580564336757 | 0.316240339279304 | 0.056331 | 0.0011266 | 0
13/08/2004 | 2004 | 0.42144 | 0.011347 | 22.8580564336757 | 0.316240339279304 | 0.42144 | 0.011347 | 0
15/08/2004 | 2004 | 1.3662 | 0.021245 | 22.8580564336757 | 0.316240339279304 | 1.3662 | 0.021245 | 0
16/08/2004 | 2004 | 1.7101 | 0.12944 | 22.8580564336757 | 0.316240339279304 | 1.7101 | 0.12944 | 0
17/08/2004 | 2004 | 7.0389 | 0.05436 | 22.8580564336757 | 0.316240339279304 | 7.0389 | 0.05436 | 0
18/08/2004 | 2004 | 2.4036 | 0.0045065 | 22.8580564336757 | 0.316240339279304 | 2.4036 | 0.0045065 | 0
19/08/2004 | 2004 | 1.1669 | 0.0024947 | 22.8580564336757 | 0.316240339279304 | 1.1669 | 0.0024947 | 0
20/08/2004 | 2004 | 0.061562 | 0.00024142 | 22.8580564336757 | 0.316240339279304 | 0.061562 | 0.00024142 | 0
22/08/2004 | 2004 | 2.6821 | 0.1125 | 22.8580564336757 | 0.316240339279304 | 2.6821 | 0.1125 | 0
23/08/2004 | 2004 | 0.078461 | 0.00060355 | 22.8580564336757 | 0.316240339279304 | 0.078461 | 0.00060355 | 0
24/08/2004 | 2004 | 0.11991 | 0.00040237 | 22.8580564336757 | 0.316240339279304 | 0.11991 | 0.00040237 | 0
26/08/2004 | 2004 | 0.17865 | 0.00060355 | 22.8580564336757 | 0.316240339279304 | 0.17865 | 0.00060355 | 0
27/08/2004 | 2004 | 0.031183 | 0.00020118 | 22.8580564336757 | 0.316240339279304 | 0.031183 | 0.00020118 | 0
28/08/2004 | 2004 | 4.254 | 0.039874 | 22.8580564336757 | 0.316240339279304 | 4.254 | 0.039874 | 0
01/09/2004 | 2004 | 0.86187 | 0.0025349 | 22.8580564336757 | 0.316240339279304 | 0.86187 | 0.0025349 | 0
06/09/2004 | 2004 | 2.0465 | 0.0086106 | 22.8580564336757 | 0.316240339279304 | 2.0465 | 0.0086106 | 0
08/09/2004 | 2004 | 0.043456 | 0.00024142 | 22.8580564336757 | 0.316240339279304 | 0.043456 | 0.00024142 | 0
15/09/2004 | 2004 | 1.3124 | 0.0045467 | 22.8580564336757 | 0.316240339279304 | 1.3124 | 0.0045467 | 0
20/09/2004 | 2004 | 0.6122 | 0.0041041 | 22.8580564336757 | 0.316240339279304 | 0.6122 | 0.0041041 | 0
22/09/2004 | 2004 | 0.32334 | 0.062246 | 22.8580564336757 | 0.316240339279304 | 0.32334 | 0.062246 | 0
23/09/2004 | 2004 | 0.065505 | 0.016376 | 22.8580564336757 | 0.316240339279304 | 0.065505 | 0.016376 | 0
24/09/2004 | 2004 | 0.020279 | 0.00024142 | 22.8580564336757 | 0.316240339279304 | 0.020279 | 0.00024142 | 0
26/09/2004 | 2004 | 0.68805 | 0.001529 | 22.8580564336757 | 0.316240339279304 | 0.68805 | 0.001529 | 0
27/09/2004 | 2004 | 0.014485 | 0.00012071 | 22.8580564336757 | 0.316240339279304 | 0.014485 | 0.00012071 | 0
28/09/2004 | 2004 | 0.24142 | 0.00096568 | 22.8580564336757 | 0.316240339279304 | 0.24142 | 0.00096568 | 0
29/09/2004 | 2004 | 6.136 | 0.056371 | 22.8580564336757 | 0.316240339279304 | 6.136 | 0.056371 | 0
30/09/2004 | 2004 | 0.02897 | 0.00032189 | 22.8580564336757 | 0.316240339279304 | 0.02897 | 0.00032189 | 0
01/10/2004 | 2004 | 0.059148 | 0.00060355 | 22.8580564336757 | 0.316240339279304 | 0.059148 | 0.00060355 | 0
05/10/2004 | 2004 | 0.036213 | 0.00060355 | 22.8580564336757 | 0.316240339279304 | 0.036213 | 0.00060355 | 0
06/10/2004 | 2004 | 1.0877 | 0.0035408 | 22.8580564336757 | 0.316240339279304 | 1.0877 | 0.0035408 | 0
08/10/2004 | 2004 | 1.9112 | 0.003058 | 22.8580564336757 | 0.316240339279304 | 1.9112 | 0.003058 | 0
10/10/2004 | 2004 | 0.63526 | 0.15881 | 22.8580564336757 | 0.316240339279304 | 0.63526 | 0.15881 | 0
12/10/2004 | 2004 | 0.4212 | 0.0033396 | 22.8580564336757 | 0.316240339279304 | 0.4212 | 0.0033396 | 0
13/10/2004 | 2004 | 0.15451 | 0.0038627 | 22.8580564336757 | 0.316240339279304 | 0.15451 | 0.0038627 | 0
14/10/2004 | 2004 | 0.17781 | 0.010824 | 22.8580564336757 | 0.316240339279304 | 0.17781 | 0.010824 | 0
16/10/2004 | 2004 | 2.5815 | 0.026315 | 22.8580564336757 | 0.316240339279304 | 2.5815 | 0.026315 | 0
19/10/2004 | 2004 | 0.3396 | 0.0030177 | 22.8580564336757 | 0.316240339279304 | 0.3396 | 0.0030177 | 0
20/10/2004 | 2004 | 1.3652 | 0.006116 | 22.8580564336757 | 0.316240339279304 | 1.3652 | 0.006116 | 0
22/10/2004 | 2004 | 0.043093 | 0.00068402 | 22.8580564336757 | 0.316240339279304 | 0.043093 | 0.00068402 | 0
24/10/2004 | 2004 | 7.3734 | 0.022935 | 22.8580564336757 | 0.316240339279304 | 7.3734 | 0.022935 | 0
27/10/2004 | 2004 | 0.23321 | 0.00092544 | 22.8580564336757 | 0.316240339279304 | 0.23321 | 0.00092544 | 0
30/10/2004 | 2004 | 0.14002 | 0.0012071 | 22.8580564336757 | 0.316240339279304 | 0.14002 | 0.0012071 | 0
01/11/2004 | 2004 | 0.92492 | 0.0045065 | 22.8580564336757 | 0.316240339279304 | 0.92492 | 0.0045065 | 0
02/11/2004 | 2004 | 0.48155 | 0.0027361 | 22.8580564336757 | 0.316240339279304 | 0.48155 | 0.0027361 | 0
03/11/2004 | 2004 | 0.6062 | 0.0037822 | 22.8580564336757 | 0.316240339279304 | 0.6062 | 0.0037822 | 0
09/11/2004 | 2004 | 3.5226 | 0.012031 | 22.8580564336757 | 0.316240339279304 | 3.5226 | 0.012031 | 0
10/11/2004 | 2004 | 0.64057 | 0.0080071 | 22.8580564336757 | 0.316240339279304 | 0.64057 | 0.0080071 | 0
14/11/2004 | 2004 | 1.1681 | 0.012071 | 22.8580564336757 | 0.316240339279304 | 1.1681 | 0.012071 | 0
15/11/2004 | 2004 | 32.9158 | 0.47334 | 22.8580564336757 | 0.316240339279304 | 22.8581 | 0.31624 | 1 | 10.0578 | 0.1571
17/11/2004 | 2004 | 0.010944 | 8.0473e-05 | 22.8580564336757 | 0.316240339279304 | 0.010944 | 8.0473e-05 | 0
19/11/2004 | 2004 | 0.053716 | 0.00060355 | 22.8580564336757 | 0.316240339279304 | 0.053716 | 0.00060355 | 0
20/11/2004 | 2004 | 0.049692 | 0.00052308 | 22.8580564336757 | 0.316240339279304 | 0.049692 | 0.00052308 | 0
22/11/2004 | 2004 | 0.74643 | 0.0014888 | 22.8580564336757 | 0.316240339279304 | 0.74643 | 0.0014888 | 0
24/11/2004 | 2004 | 0.054561 | 0.0045467 | 22.8580564336757 | 0.316240339279304 | 0.054561 | 0.0045467 | 0
25/11/2004 | 2004 | 12.1716 | 0.015893 | 22.8580564336757 | 0.316240339279304 | 12.1716 | 0.015893 | 0
26/11/2004 | 2004 | 1.2934 | 0.0038627 | 22.8580564336757 | 0.316240339279304 | 1.2934 | 0.0038627 | 0
27/11/2004 | 2004 | 0.20517 | 0.001529 | 22.8580564336757 | 0.316240339279304 | 0.20517 | 0.001529 | 0
30/11/2004 | 2004 | 0.32877 | 0.0056734 | 22.8580564336757 | 0.316240339279304 | 0.32877 | 0.0056734 | 0
01/12/2004 | 2004 | 0.011266 | 0.00032189 | 22.8580564336757 | 0.316240339279304 | 0.011266 | 0.00032189 | 0
02/12/2004 | 2004 | 0.31252 | 0.0018911 | 22.8580564336757 | 0.316240339279304 | 0.31252 | 0.0018911 | 0
03/12/2004 | 2004 | 0.062809 | 0.00028166 | 22.8580564336757 | 0.316240339279304 | 0.062809 | 0.00028166 | 0
04/12/2004 | 2004 | 0.011266 | 8.0473e-05 | 22.8580564336757 | 0.316240339279304 | 0.011266 | 8.0473e-05 | 0
05/12/2004 | 2004 | 5.0656 | 0.028085 | 22.8580564336757 | 0.316240339279304 | 5.0656 | 0.028085 | 0
06/12/2004 | 2004 | 0.021728 | 0.00060355 | 22.8580564336757 | 0.316240339279304 | 0.021728 | 0.00060355 | 0
09/12/2004 | 2004 | 0.2749 | 0.0030982 | 22.8580564336757 | 0.316240339279304 | 0.2749 | 0.0030982 | 0
10/12/2004 | 2004 | 0.67919 | 0.0072426 | 22.8580564336757 | 0.316240339279304 | 0.67919 | 0.0072426 | 0
11/12/2004 | 2004 | 0.14968 | 0.0026556 | 22.8580564336757 | 0.316240339279304 | 0.14968 | 0.0026556 | 0
13/12/2004 | 2004 | 1.3936 | 0.0065183 | 22.8580564336757 | 0.316240339279304 | 1.3936 | 0.0065183 | 0
14/12/2004 | 2004 | 0.022935 | 0.00012071 | 22.8580564336757 | 0.316240339279304 | 0.022935 | 0.00012071 | 0
15/12/2004 | 2004 | 2.4371 | 0.0047077 | 22.8580564336757 | 0.316240339279304 | 2.4371 | 0.0047077 | 0
16/12/2004 | 2004 | 0.10075 | 0.00096568 | 22.8580564336757 | 0.316240339279304 | 0.10075 | 0.00096568 | 0
17/12/2004 | 2004 | 0.31047 | 0.0015692 | 22.8580564336757 | 0.316240339279304 | 0.31047 | 0.0015692 | 0
19/12/2004 | 2004 | 1.162 | 0.0086911 | 22.8580564336757 | 0.316240339279304 | 1.162 | 0.0086911 | 0
20/12/2004 | 2004 | 0.27224 | 0.0027361 | 22.8580564336757 | 0.316240339279304 | 0.27224 | 0.0027361 | 0
21/12/2004 | 2004 | 0.57828 | 0.0032994 | 22.8580564336757 | 0.316240339279304 | 0.57828 | 0.0032994 | 0
22/12/2004 | 2004 | 0.55945 | 0.0017704 | 22.8580564336757 | 0.316240339279304 | 0.55945 | 0.0017704 | 0
24/12/2004 | 2004 | 0.18698 | 0.0030177 | 22.8580564336757 | 0.316240339279304 | 0.18698 | 0.0030177 | 0
25/12/2004 | 2004 | 0.36322 | 0.017704 | 22.8580564336757 | 0.316240339279304 | 0.36322 | 0.017704 | 0
28/12/2004 | 2004 | 0.16079 | 0.0014888 | 22.8580564336757 | 0.316240339279304 | 0.16079 | 0.0014888 | 0
29/12/2004 | 2004 | 0.044059 | 0.00060355 | 22.8580564336757 | 0.316240339279304 | 0.044059 | 0.00060355 | 0
02/01/2005 | 2004 | 0.67187 | 0.014163 | 22.8580564336757 | 0.316240339279304 | 0.67187 | 0.014163 | 0
07/01/2005 | 2004 | 0.99155 | 0.0053917 | 22.8580564336757 | 0.316240339279304 | 0.99155 | 0.0053917 | 0
08/01/2005 | 2004 | 0.0095763 | 0.00068402 | 22.8580564336757 | 0.316240339279304 | 0.0095763 | 0.00068402 | 0
09/01/2005 | 2004 | 0.41826 | 0.010864 | 22.8580564336757 | 0.316240339279304 | 0.41826 | 0.010864 | 0
10/01/2005 | 2004 | 0.13198 | 0.0010059 | 22.8580564336757 | 0.316240339279304 | 0.13198 | 0.0010059 | 0
11/01/2005 | 2004 | 0.52996 | 0.0030982 | 22.8580564336757 | 0.316240339279304 | 0.52996 | 0.0030982 | 0
13/01/2005 | 2004 | 0.98382 | 0.029373 | 22.8580564336757 | 0.316240339279304 | 0.98382 | 0.029373 | 0
14/01/2005 | 2004 | 0.45065 | 0.0038225 | 22.8580564336757 | 0.316240339279304 | 0.45065 | 0.0038225 | 0
17/01/2005 | 2004 | 1.6843 | 0.01183 | 22.8580564336757 | 0.316240339279304 | 1.6843 | 0.01183 | 0
18/01/2005 | 2004 | 0.45053 | 0.035972 | 22.8580564336757 | 0.316240339279304 | 0.45053 | 0.035972 | 0
23/01/2005 | 2004 | 0.32833 | 0.002897 | 22.8580564336757 | 0.316240339279304 | 0.32833 | 0.002897 | 0
26/01/2005 | 2004 | 0.022532 | 0.00016095 | 22.8580564336757 | 0.316240339279304 | 0.022532 | 0.00016095 | 0
27/01/2005 | 2004 | 0.0080473 | 0.00016095 | 22.8580564336757 | 0.316240339279304 | 0.0080473 | 0.00016095 | 0
31/01/2005 | 2004 | 3.1409 | 0.021607 | 22.8580564336757 | 0.316240339279304 | 3.1409 | 0.021607 | 0
01/02/2005 | 2004 | 0.22532 | 0.0022532 | 22.8580564336757 | 0.316240339279304 | 0.22532 | 0.0022532 | 0
02/02/2005 | 2004 | 0.0062769 | 0.0031385 | 22.8580564336757 | 0.316240339279304 | 0.0062769 | 0.0031385 | 0
03/02/2005 | 2004 | 0.075001 | 0.0016497 | 22.8580564336757 | 0.316240339279304 | 0.075001 | 0.0016497 | 0
04/02/2005 | 2004 | 0.82674 | 0.0041444 | 22.8580564336757 | 0.316240339279304 | 0.82674 | 0.0041444 | 0
06/02/2005 | 2004 | 5.6251 | 0.01875 | 22.8580564336757 | 0.316240339279304 | 5.6251 | 0.01875 | 0
07/02/2005 | 2004 | 0.06804 | 0.0007645 | 22.8580564336757 | 0.316240339279304 | 0.06804 | 0.0007645 | 0
10/02/2005 | 2004 | 0.077254 | 0.0019314 | 22.8580564336757 | 0.316240339279304 | 0.077254 | 0.0019314 | 0
11/02/2005 | 2004 | 0.40225 | 0.0061964 | 22.8580564336757 | 0.316240339279304 | 0.40225 | 0.0061964 | 0
15/02/2005 | 2004 | 0.02716 | 0.0020923 | 22.8580564336757 | 0.316240339279304 | 0.02716 | 0.0020923 | 0
17/02/2005 | 2004 | 0.2897 | 0.0016095 | 22.8580564336757 | 0.316240339279304 | 0.2897 | 0.0016095 | 0
18/02/2005 | 2004 | 0.19362 | 0.03227 | 22.8580564336757 | 0.316240339279304 | 0.19362 | 0.03227 | 0
20/02/2005 | 2004 | 3.1996 | 0.045709 | 22.8580564336757 | 0.316240339279304 | 3.1996 | 0.045709 | 0
22/02/2005 | 2004 | 0.27522 | 0.00048284 | 22.8580564336757 | 0.316240339279304 | 0.27522 | 0.00048284 | 0
23/02/2005 | 2004 | 0.88106 | 0.003742 | 22.8580564336757 | 0.316240339279304 | 0.88106 | 0.003742 | 0
25/02/2005 | 2004 | 1.3189 | 0.017946 | 22.8580564336757 | 0.316240339279304 | 1.3189 | 0.017946 | 0
28/02/2005 | 2004 | 0.21748 | 0.0018911 | 22.8580564336757 | 0.316240339279304 | 0.21748 | 0.0018911 | 0
01/03/2005 | 2004 | 0.68515 | 0.018106 | 22.8580564336757 | 0.316240339279304 | 0.68515 | 0.018106 | 0
02/03/2005 | 2004 | 0.22693 | 0.0018911 | 22.8580564336757 | 0.316240339279304 | 0.22693 | 0.0018911 | 0
03/03/2005 | 2004 | 0.23048 | 0.0037018 | 22.8580564336757 | 0.316240339279304 | 0.23048 | 0.0037018 | 0
05/03/2005 | 2004 | 0.58878 | 0.0070414 | 22.8580564336757 | 0.316240339279304 | 0.58878 | 0.0070414 | 0
07/03/2005 | 2004 | 1.6019 | 0.03227 | 22.8580564336757 | 0.316240339279304 | 1.6019 | 0.03227 | 0
09/03/2005 | 2004 | 0.32004 | 0.0032994 | 22.8580564336757 | 0.316240339279304 | 0.32004 | 0.0032994 | 0
11/03/2005 | 2004 | 0.56211 | 0.0086911 | 22.8580564336757 | 0.316240339279304 | 0.56211 | 0.0086911 | 0
13/03/2005 | 2004 | 0.34338 | 0.013359 | 22.8580564336757 | 0.316240339279304 | 0.34338 | 0.013359 | 0
14/03/2005 | 2004 | 1.1382 | 0.017785 | 22.8580564336757 | 0.316240339279304 | 1.1382 | 0.017785 | 0
15/03/2005 | 2004 | 0.26838 | 0.0011669 | 22.8580564336757 | 0.316240339279304 | 0.26838 | 0.0011669 | 0
16/03/2005 | 2004 | 1.0354 | 0.029172 | 22.8580564336757 | 0.316240339279304 | 1.0354 | 0.029172 | 0
17/03/2005 | 2004 | 0.065988 | 0.013198 | 22.8580564336757 | 0.316240339279304 | 0.065988 | 0.013198 | 0
18/03/2005 | 2004 | 0.52195 | 0.016175 | 22.8580564336757 | 0.316240339279304 | 0.52195 | 0.016175 | 0
19/03/2005 | 2004 | 0.88235 | 0.015491 | 22.8580564336757 | 0.316240339279304 | 0.88235 | 0.015491 | 0
21/03/2005 | 2004 | 1.7237 | 0.060194 | 22.8580564336757 | 0.316240339279304 | 1.7237 | 0.060194 | 0
22/03/2005 | 2004 | 1.9637 | 0.0085704 | 22.8580564336757 | 0.316240339279304 | 1.9637 | 0.0085704 | 0
23/03/2005 | 2004 | 0.90037 | 0.0033396 | 22.8580564336757 | 0.316240339279304 | 0.90037 | 0.0033396 | 0
24/03/2005 | 2004 | 0.26653 | 0.0035006 | 22.8580564336757 | 0.316240339279304 | 0.26653 | 0.0035006 | 0
25/03/2005 | 2004 | 1.5297 | 0.011628 | 22.8580564336757 | 0.316240339279304 | 1.5297 | 0.011628 | 0
26/03/2005 | 2004 | 0.095723 | 0.00052308 | 22.8580564336757 | 0.316240339279304 | 0.095723 | 0.00052308 | 0
29/03/2005 | 2004 | 0.15531 | 0.0017302 | 22.8580564336757 | 0.316240339279304 | 0.15531 | 0.0017302 | 0
30/03/2005 | 2004 | 0.01368 | 0.00068402 | 22.8580564336757 | 0.316240339279304 | 0.01368 | 0.00068402 | 0
31/03/2005 | 2004 | 0.028769 | 0.00020118 | 22.8580564336757 | 0.316240339279304 | 0.028769 | 0.00020118 | 0
07/04/2005 | 2005 | 0.0072397 | 0.0002011 | 22.8580564336757 | 0.316240339279304 | 0.0072397 | 0.0002011 | 0
08/04/2005 | 2005 | 2.2496 | 0.015766 | 22.8580564336757 | 0.316240339279304 | 2.2496 | 0.015766 | 0
11/04/2005 | 2005 | 0.09299 | 0.00068375 | 22.8580564336757 | 0.316240339279304 | 0.09299 | 0.00068375 | 0
12/04/2005 | 2005 | 0.5482 | 0.0011664 | 22.8580564336757 | 0.316240339279304 | 0.5482 | 0.0011664 | 0
15/04/2005 | 2005 | 0.24587 | 0.0011664 | 22.8580564336757 | 0.316240339279304 | 0.24587 | 0.0011664 | 0
16/04/2005 | 2005 | 0.23831 | 0.0031774 | 22.8580564336757 | 0.316240339279304 | 0.23831 | 0.0031774 | 0
18/04/2005 | 2005 | 0.59357 | 0.0018904 | 22.8580564336757 | 0.316240339279304 | 0.59357 | 0.0018904 | 0
20/04/2005 | 2005 | 0.11696 | 0.0039416 | 22.8580564336757 | 0.316240339279304 | 0.11696 | 0.0039416 | 0
21/04/2005 | 2005 | 0.086876 | 0.0019306 | 22.8580564336757 | 0.316240339279304 | 0.086876 | 0.0019306 | 0
25/04/2005 | 2005 | 1.0542 | 0.003097 | 22.8580564336757 | 0.316240339279304 | 1.0542 | 0.003097 | 0
27/04/2005 | 2005 | 0.22121 | 0.00088485 | 22.8580564336757 | 0.316240339279304 | 0.22121 | 0.00088485 | 0
30/04/2005 | 2005 | 0.1723 | 0.00072397 | 22.8580564336757 | 0.316240339279304 | 0.1723 | 0.00072397 | 0
01/05/2005 | 2005 | 0.031855 | 0.00048264 | 22.8580564336757 | 0.316240339279304 | 0.031855 | 0.00048264 | 0
03/05/2005 | 2005 | 0.64127 | 0.0092507 | 22.8580564336757 | 0.316240339279304 | 0.64127 | 0.0092507 | 0
05/05/2005 | 2005 | 0.452 | 0.0014479 | 22.8580564336757 | 0.316240339279304 | 0.452 | 0.0014479 | 0
06/05/2005 | 2005 | 0.90126 | 0.023851 | 22.8580564336757 | 0.316240339279304 | 0.90126 | 0.023851 | 0
09/05/2005 | 2005 | 0.098942 | 0.0012066 | 22.8580564336757 | 0.316240339279304 | 0.098942 | 0.0012066 | 0
10/05/2005 | 2005 | 0.70173 | 0.0038612 | 22.8580564336757 | 0.316240339279304 | 0.70173 | 0.0038612 | 0
12/05/2005 | 2005 | 0.036198 | 0.00060331 | 22.8580564336757 | 0.316240339279304 | 0.036198 | 0.00060331 | 0
16/05/2005 | 2005 | 0.55806 | 0.0030165 | 22.8580564336757 | 0.316240339279304 | 0.55806 | 0.0030165 | 0
17/05/2005 | 2005 | 0.51788 | 0.0029763 | 22.8580564336757 | 0.316240339279304 | 0.51788 | 0.0029763 | 0
22/05/2005 | 2005 | 0.81651 | 0.0039014 | 22.8580564336757 | 0.316240339279304 | 0.81651 | 0.0039014 | 0
23/05/2005 | 2005 | 1.1262 | 0.026224 | 22.8580564336757 | 0.316240339279304 | 1.1262 | 0.026224 | 0
25/05/2005 | 2005 | 0.021719 | 0.00096529 | 22.8580564336757 | 0.316240339279304 | 0.021719 | 0.00096529 | 0
26/05/2005 | 2005 | 0.27551 | 0.0010055 | 22.8580564336757 | 0.316240339279304 | 0.27551 | 0.0010055 | 0
27/05/2005 | 2005 | 0.88227 | 0.011141 | 22.8580564336757 | 0.316240339279304 | 0.88227 | 0.011141 | 0
30/05/2005 | 2005 | 0.32631 | 0.0065961 | 22.8580564336757 | 0.316240339279304 | 0.32631 | 0.0065961 | 0
31/05/2005 | 2005 | 0.019306 | 0.00064353 | 22.8580564336757 | 0.316240339279304 | 0.019306 | 0.00064353 | 0
01/06/2005 | 2005 | 0.51526 | 0.0015284 | 22.8580564336757 | 0.316240339279304 | 0.51526 | 0.0015284 | 0
02/06/2005 | 2005 | 0.53485 | 0.006395 | 22.8580564336757 | 0.316240339279304 | 0.53485 | 0.006395 | 0
07/06/2005 | 2005 | 0.8402 | 0.028074 | 22.8580564336757 | 0.316240339279304 | 0.8402 | 0.028074 | 0
08/06/2005 | 2005 | 0.11547 | 0.0020915 | 22.8580564336757 | 0.316240339279304 | 0.11547 | 0.0020915 | 0
09/06/2005 | 2005 | 0.40152 | 0.0027752 | 22.8580564336757 | 0.316240339279304 | 0.40152 | 0.0027752 | 0
10/06/2005 | 2005 | 0.21791 | 0.00072397 | 22.8580564336757 | 0.316240339279304 | 0.21791 | 0.00072397 | 0
15/06/2005 | 2005 | 0.67627 | 0.0074408 | 22.8580564336757 | 0.316240339279304 | 0.67627 | 0.0074408 | 0
16/06/2005 | 2005 | 0.31662 | 0.001649 | 22.8580564336757 | 0.316240339279304 | 0.31662 | 0.001649 | 0
17/06/2005 | 2005 | 0.21743 | 0.0021317 | 22.8580564336757 | 0.316240339279304 | 0.21743 | 0.0021317 | 0
18/06/2005 | 2005 | 0.042634 | 0.00080441 | 22.8580564336757 | 0.316240339279304 | 0.042634 | 0.00080441 | 0
20/06/2005 | 2005 | 0.41363 | 0.0017697 | 22.8580564336757 | 0.316240339279304 | 0.41363 | 0.0017697 | 0
21/06/2005 | 2005 | 0.22294 | 0.003459 | 22.8580564336757 | 0.316240339279304 | 0.22294 | 0.003459 | 0
22/06/2005 | 2005 | 0.035474 | 0.00028154 | 22.8580564336757 | 0.316240339279304 | 0.035474 | 0.00028154 | 0
23/06/2005 | 2005 | 0.04199 | 0.00048264 | 22.8580564336757 | 0.316240339279304 | 0.04199 | 0.00048264 | 0
24/06/2005 | 2005 | 1.0291 | 0.021437 | 22.8580564336757 | 0.316240339279304 | 1.0291 | 0.021437 | 0
25/06/2005 | 2005 | 1.6996 | 0.013514 | 22.8580564336757 | 0.316240339279304 | 1.6996 | 0.013514 | 0
26/06/2005 | 2005 | 0.056952 | 0.00032176 | 22.8580564336757 | 0.316240339279304 | 0.056952 | 0.00032176 | 0
27/06/2005 | 2005 | 0.22805 | 0.00072397 | 22.8580564336757 | 0.316240339279304 | 0.22805 | 0.00072397 | 0
28/06/2005 | 2005 | 4.7221 | 0.049069 | 22.8580564336757 | 0.316240339279304 | 4.7221 | 0.049069 | 0
29/06/2005 | 2005 | 0.34943 | 0.00096529 | 22.8580564336757 | 0.316240339279304 | 0.34943 | 0.00096529 | 0
30/06/2005 | 2005 | 0.039215 | 0.00060331 | 22.8580564336757 | 0.316240339279304 | 0.039215 | 0.00060331 | 0
05/07/2005 | 2005 | 0.050597 | 0.0030568 | 22.8580564336757 | 0.316240339279304 | 0.050597 | 0.0030568 | 0
06/07/2005 | 2005 | 1.2031 | 0.010457 | 22.8580564336757 | 0.316240339279304 | 1.2031 | 0.010457 | 0
08/07/2005 | 2005 | 0.65949 | 0.0075614 | 22.8580564336757 | 0.316240339279304 | 0.65949 | 0.0075614 | 0
11/07/2005 | 2005 | 0.94952 | 0.0047058 | 22.8580564336757 | 0.316240339279304 | 0.94952 | 0.0047058 | 0
12/07/2005 | 2005 | 0.98295 | 0.014278 | 22.8580564336757 | 0.316240339279304 | 0.98295 | 0.014278 | 0
15/07/2005 | 2005 | 1.7567 | 0.046696 | 22.8580564336757 | 0.316240339279304 | 1.7567 | 0.046696 | 0
18/07/2005 | 2005 | 0.98391 | 0.02912 | 22.8580564336757 | 0.316240339279304 | 0.98391 | 0.02912 | 0
19/07/2005 | 2005 | 1.868 | 0.031533 | 22.8580564336757 | 0.316240339279304 | 1.868 | 0.031533 | 0
21/07/2005 | 2005 | 0.069018 | 0.00044242 | 22.8580564336757 | 0.316240339279304 | 0.069018 | 0.00044242 | 0
22/07/2005 | 2005 | 0.0094116 | 0.00072397 | 22.8580564336757 | 0.316240339279304 | 0.0094116 | 0.00072397 | 0
26/07/2005 | 2005 | 0.23308 | 0.00076419 | 22.8580564336757 | 0.316240339279304 | 0.23308 | 0.00076419 | 0
27/07/2005 | 2005 | 0.93452 | 0.0035796 | 22.8580564336757 | 0.316240339279304 | 0.93452 | 0.0035796 | 0
28/07/2005 | 2005 | 1.9759 | 0.027631 | 22.8580564336757 | 0.316240339279304 | 1.9759 | 0.027631 | 0
29/07/2005 | 2005 | 0.11181 | 0.0004022 | 22.8580564336757 | 0.316240339279304 | 0.11181 | 0.0004022 | 0
01/08/2005 | 2005 | 0.70611 | 0.016169 | 22.8580564336757 | 0.316240339279304 | 0.70611 | 0.016169 | 0
04/08/2005 | 2005 | 0.021719 | 0.00036198 | 22.8580564336757 | 0.316240339279304 | 0.021719 | 0.00036198 | 0
05/08/2005 | 2005 | 0.16213 | 0.0069179 | 22.8580564336757 | 0.316240339279304 | 0.16213 | 0.0069179 | 0
08/08/2005 | 2005 | 0.18501 | 0.0018501 | 22.8580564336757 | 0.316240339279304 | 0.18501 | 0.0018501 | 0
10/08/2005 | 2005 | 0.26413 | 0.0013273 | 22.8580564336757 | 0.316240339279304 | 0.26413 | 0.0013273 | 0
16/08/2005 | 2005 | 0.17938 | 0.0004022 | 22.8580564336757 | 0.316240339279304 | 0.17938 | 0.0004022 | 0
17/08/2005 | 2005 | 0.12669 | 0.00056309 | 22.8580564336757 | 0.316240339279304 | 0.12669 | 0.00056309 | 0
18/08/2005 | 2005 | 0.13064 | 0.00056309 | 22.8580564336757 | 0.316240339279304 | 0.13064 | 0.00056309 | 0
23/08/2005 | 2005 | 0.095725 | 0.00028154 | 22.8580564336757 | 0.316240339279304 | 0.095725 | 0.00028154 | 0
26/08/2005 | 2005 | 0.34006 | 0.0053493 | 22.8580564336757 | 0.316240339279304 | 0.34006 | 0.0053493 | 0
27/08/2005 | 2005 | 0.075614 | 0.0075614 | 22.8580564336757 | 0.316240339279304 | 0.075614 | 0.0075614 | 0
28/08/2005 | 2005 | 0.33351 | 0.004022 | 22.8580564336757 | 0.316240339279304 | 0.33351 | 0.004022 | 0
29/08/2005 | 2005 | 2.3638 | 0.0046656 | 22.8580564336757 | 0.316240339279304 | 2.3638 | 0.0046656 | 0
30/08/2005 | 2005 | 0.4199 | 0.0011664 | 22.8580564336757 | 0.316240339279304 | 0.4199 | 0.0011664 | 0
01/09/2005 | 2005 | 0.38974 | 0.0013675 | 22.8580564336757 | 0.316240339279304 | 0.38974 | 0.0013675 | 0
05/09/2005 | 2005 | 0.42344 | 0.0075614 | 22.8580564336757 | 0.316240339279304 | 0.42344 | 0.0075614 | 0
06/09/2005 | 2005 | 0.74026 | 0.0039416 | 22.8580564336757 | 0.316240339279304 | 0.74026 | 0.0039416 | 0
07/09/2005 | 2005 | 0.77235 | 0.019547 | 22.8580564336757 | 0.316240339279304 | 0.77235 | 0.019547 | 0
08/09/2005 | 2005 | 1.556 | 0.0076419 | 22.8580564336757 | 0.316240339279304 | 1.556 | 0.0076419 | 0
13/09/2005 | 2005 | 0.90411 | 0.002373 | 22.8580564336757 | 0.316240339279304 | 0.90411 | 0.002373 | 0
15/09/2005 | 2005 | 0.21397 | 0.00076419 | 22.8580564336757 | 0.316240339279304 | 0.21397 | 0.00076419 | 0
16/09/2005 | 2005 | 0.57386 | 0.0032981 | 22.8580564336757 | 0.316240339279304 | 0.57386 | 0.0032981 | 0
17/09/2005 | 2005 | 0.20858 | 0.0015284 | 22.8580564336757 | 0.316240339279304 | 0.20858 | 0.0015284 | 0
18/09/2005 | 2005 | 2.819 | 0.019467 | 22.8580564336757 | 0.316240339279304 | 2.819 | 0.019467 | 0
19/09/2005 | 2005 | 0.37232 | 0.0038209 | 22.8580564336757 | 0.316240339279304 | 0.37232 | 0.0038209 | 0
20/09/2005 | 2005 | 0.16301 | 0.002373 | 22.8580564336757 | 0.316240339279304 | 0.16301 | 0.002373 | 0
27/09/2005 | 2005 | 1.1011 | 0.0031774 | 22.8580564336757 | 0.316240339279304 | 1.1011 | 0.0031774 | 0
01/10/2005 | 2005 | 2.057 | 0.0086876 | 22.8580564336757 | 0.316240339279304 | 2.057 | 0.0086876 | 0
02/10/2005 | 2005 | 0.10473 | 0.00048264 | 22.8580564336757 | 0.316240339279304 | 0.10473 | 0.00048264 | 0
03/10/2005 | 2005 | 0.83164 | 0.0066364 | 22.8580564336757 | 0.316240339279304 | 0.83164 | 0.0066364 | 0
04/10/2005 | 2005 | 0.05663 | 0.0026143 | 22.8580564336757 | 0.316240339279304 | 0.05663 | 0.0026143 | 0
05/10/2005 | 2005 | 1.0143 | 0.011262 | 22.8580564336757 | 0.316240339279304 | 1.0143 | 0.011262 | 0
07/10/2005 | 2005 | 4.8966 | 0.17271 | 22.8580564336757 | 0.316240339279304 | 4.8966 | 0.17271 | 0
10/10/2005 | 2005 | 1.2644 | 0.030849 | 22.8580564336757 | 0.316240339279304 | 1.2644 | 0.030849 | 0
11/10/2005 | 2005 | 0.19809 | 0.00068375 | 22.8580564336757 | 0.316240339279304 | 0.19809 | 0.00068375 | 0
14/10/2005 | 2005 | 0.22664 | 0.0014077 | 22.8580564336757 | 0.316240339279304 | 0.22664 | 0.0014077 | 0
17/10/2005 | 2005 | 0.43623 | 0.0011664 | 22.8580564336757 | 0.316240339279304 | 0.43623 | 0.0011664 | 0
18/10/2005 | 2005 | 0.37674 | 0.0026948 | 22.8580564336757 | 0.316240339279304 | 0.37674 | 0.0026948 | 0
19/10/2005 | 2005 | 0.15042 | 0.00088485 | 22.8580564336757 | 0.316240339279304 | 0.15042 | 0.00088485 | 0
21/10/2005 | 2005 | 26.872 | 0.054298 | 22.8580564336757 | 0.316240339279304 | 22.8581 | 0.054298 | 1 | 4.014 | 0
22/10/2005 | 2005 | 57.4779 | 0.56208 | 22.8580564336757 | 0.316240339279304 | 22.8581 | 0.31624 | 1 | 34.6199 | 0.24584
23/10/2005 | 2005 | 0.36906 | 0.0060331 | 22.8580564336757 | 0.316240339279304 | 0.36906 | 0.0060331 | 0
25/10/2005 | 2005 | 0.27511 | 0.0030165 | 22.8580564336757 | 0.316240339279304 | 0.27511 | 0.0030165 | 0
31/10/2005 | 2005 | 8.3552 | 0.047219 | 22.8580564336757 | 0.316240339279304 | 8.3552 | 0.047219 | 0
01/11/2005 | 2005 | 0.88252 | 0.0021317 | 22.8580564336757 | 0.316240339279304 | 0.88252 | 0.0021317 | 0
02/11/2005 | 2005 | 4.5972 | 0.045369 | 22.8580564336757 | 0.316240339279304 | 4.5972 | 0.045369 | 0
03/11/2005 | 2005 | 1.3697 | 0.0086474 | 22.8580564336757 | 0.316240339279304 | 1.3697 | 0.0086474 | 0
04/11/2005 | 2005 | 0.011543 | 4.022e-05 | 22.8580564336757 | 0.316240339279304 | 0.011543 | 4.022e-05 | 0
07/11/2005 | 2005 | 0.93078 | 0.011905 | 22.8580564336757 | 0.316240339279304 | 0.93078 | 0.011905 | 0
11/11/2005 | 2005 | 0.043438 | 0.00032176 | 22.8580564336757 | 0.316240339279304 | 0.043438 | 0.00032176 | 0
13/11/2005 | 2005 | 0.84125 | 0.028838 | 22.8580564336757 | 0.316240339279304 | 0.84125 | 0.028838 | 0
14/11/2005 | 2005 | 0.23247 | 0.006395 | 22.8580564336757 | 0.316240339279304 | 0.23247 | 0.006395 | 0
17/11/2005 | 2005 | 0.076057 | 0.00068375 | 22.8580564336757 | 0.316240339279304 | 0.076057 | 0.00068375 | 0
18/11/2005 | 2005 | 0.13273 | 0.00088485 | 22.8580564336757 | 0.316240339279304 | 0.13273 | 0.00088485 | 0
22/11/2005 | 2005 | 1.0232 | 0.051563 | 22.8580564336757 | 0.316240339279304 | 1.0232 | 0.051563 | 0
23/11/2005 | 2005 | 0.031332 | 0.00076419 | 22.8580564336757 | 0.316240339279304 | 0.031332 | 0.00076419 | 0
24/11/2005 | 2005 | 0.075856 | 0.0018501 | 22.8580564336757 | 0.316240339279304 | 0.075856 | 0.0018501 | 0
27/11/2005 | 2005 | 11.5028 | 0.028878 | 22.8580564336757 | 0.316240339279304 | 11.5028 | 0.028878 | 0
28/11/2005 | 2005 | 34.104 | 0.26895 | 22.8580564336757 | 0.316240339279304 | 22.8581 | 0.26895 | 1 | 11.2459 | 0
29/11/2005 | 2005 | 2.6115 | 0.054096 | 22.8580564336757 | 0.316240339279304 | 2.6115 | 0.054096 | 0
02/12/2005 | 2005 | 3.128 | 0.02015 | 22.8580564336757 | 0.316240339279304 | 3.128 | 0.02015 | 0
04/12/2005 | 2005 | 0.043116 | 0.0012871 | 22.8580564336757 | 0.316240339279304 | 0.043116 | 0.0012871 | 0
05/12/2005 | 2005 | 0.47786 | 0.006757 | 22.8580564336757 | 0.316240339279304 | 0.47786 | 0.006757 | 0
07/12/2005 | 2005 | 0.37413 | 0.0065157 | 22.8580564336757 | 0.316240339279304 | 0.37413 | 0.0065157 | 0
09/12/2005 | 2005 | 0.060491 | 0.0075614 | 22.8580564336757 | 0.316240339279304 | 0.060491 | 0.0075614 | 0
11/12/2005 | 2005 | 5.3716 | 0.026465 | 22.8580564336757 | 0.316240339279304 | 5.3716 | 0.026465 | 0
12/12/2005 | 2005 | 2.0169 | 0.017858 | 22.8580564336757 | 0.316240339279304 | 2.0169 | 0.017858 | 0
16/12/2005 | 2005 | 0.59184 | 0.0038209 | 22.8580564336757 | 0.316240339279304 | 0.59184 | 0.0038209 | 0
17/12/2005 | 2005 | 0.032981 | 0.00080441 | 22.8580564336757 | 0.316240339279304 | 0.032981 | 0.00080441 | 0
20/12/2005 | 2005 | 1.7236 | 0.04372 | 22.8580564336757 | 0.316240339279304 | 1.7236 | 0.04372 | 0
21/12/2005 | 2005 | 1.5696 | 0.0070386 | 22.8580564336757 | 0.316240339279304 | 1.5696 | 0.0070386 | 0
23/12/2005 | 2005 | 2.344 | 0.031814 | 22.8580564336757 | 0.316240339279304 | 2.344 | 0.031814 | 0
24/12/2005 | 2005 | 13.3902 | 0.26264 | 22.8580564336757 | 0.316240339279304 | 13.3902 | 0.26264 | 0
26/12/2005 | 2005 | 2.0249 | 0.013112 | 22.8580564336757 | 0.316240339279304 | 2.0249 | 0.013112 | 0
27/12/2005 | 2005 | 2.534 | 0.0086876 | 22.8580564336757 | 0.316240339279304 | 2.534 | 0.0086876 | 0
31/12/2005 | 2005 | 5.744 | 0.16937 | 22.8580564336757 | 0.316240339279304 | 5.744 | 0.16937 | 0
02/01/2006 | 2005 | 0.64212 | 0.004022 | 22.8580564336757 | 0.316240339279304 | 0.64212 | 0.004022 | 0
03/01/2006 | 2005 | 0.44134 | 0.0032176 | 22.8580564336757 | 0.316240339279304 | 0.44134 | 0.0032176 | 0
04/01/2006 | 2005 | 4.5352 | 0.030728 | 22.8580564336757 | 0.316240339279304 | 4.5352 | 0.030728 | 0
06/01/2006 | 2005 | 0.54024 | 0.0092507 | 22.8580564336757 | 0.316240339279304 | 0.54024 | 0.0092507 | 0
07/01/2006 | 2005 | 0.77645 | 0.029723 | 22.8580564336757 | 0.316240339279304 | 0.77645 | 0.029723 | 0
08/01/2006 | 2005 | 0.87375 | 0.0038209 | 22.8580564336757 | 0.316240339279304 | 0.87375 | 0.0038209 | 0
11/01/2006 | 2005 | 0.052287 | 0.0004022 | 22.8580564336757 | 0.316240339279304 | 0.052287 | 0.0004022 | 0
12/01/2006 | 2005 | 6.0929 | 0.073724 | 22.8580564336757 | 0.316240339279304 | 6.0929 | 0.073724 | 0
16/01/2006 | 2005 | 1.424 | 0.043639 | 22.8580564336757 | 0.316240339279304 | 1.424 | 0.043639 | 0
18/01/2006 | 2005 | 0.71258 | 0.016289 | 22.8580564336757 | 0.316240339279304 | 0.71258 | 0.016289 | 0
20/01/2006 | 2005 | 0.44182 | 0.0038209 | 22.8580564336757 | 0.316240339279304 | 0.44182 | 0.0038209 | 0
21/01/2006 | 2005 | 1.0801 | 0.033021 | 22.8580564336757 | 0.316240339279304 | 1.0801 | 0.033021 | 0
22/01/2006 | 2005 | 0.44464 | 0.0026948 | 22.8580564336757 | 0.316240339279304 | 0.44464 | 0.0026948 | 0
24/01/2006 | 2005 | 10.7234 | 0.16804 | 22.8580564336757 | 0.316240339279304 | 10.7234 | 0.16804 | 0
25/01/2006 | 2005 | 6.2286 | 0.035796 | 22.8580564336757 | 0.316240339279304 | 6.2286 | 0.035796 | 0
26/01/2006 | 2005 | 0.72493 | 0.0098942 | 22.8580564336757 | 0.316240339279304 | 0.72493 | 0.0098942 | 0
28/01/2006 | 2005 | 0.52009 | 0.012267 | 22.8580564336757 | 0.316240339279304 | 0.52009 | 0.012267 | 0
01/02/2006 | 2005 | 1.7594 | 0.043921 | 22.8580564336757 | 0.316240339279304 | 1.7594 | 0.043921 | 0
02/02/2006 | 2005 | 1.4093 | 0.0072397 | 22.8580564336757 | 0.316240339279304 | 1.4093 | 0.0072397 | 0
03/02/2006 | 2005 | 2.712 | 0.03841 | 22.8580564336757 | 0.316240339279304 | 2.712 | 0.03841 | 0
06/02/2006 | 2005 | 0.36963 | 0.0077625 | 22.8580564336757 | 0.316240339279304 | 0.36963 | 0.0077625 | 0
07/02/2006 | 2005 | 0.63822 | 0.0066766 | 22.8580564336757 | 0.316240339279304 | 0.63822 | 0.0066766 | 0
11/02/2006 | 2005 | 1.0735 | 0.0096529 | 22.8580564336757 | 0.316240339279304 | 1.0735 | 0.0096529 | 0
12/02/2006 | 2005 | 3.9159 | 0.10481 | 22.8580564336757 | 0.316240339279304 | 3.9159 | 0.10481 | 0
13/02/2006 | 2005 | 1.3954 | 0.071592 | 22.8580564336757 | 0.316240339279304 | 1.3954 | 0.071592 | 0
16/02/2006 | 2005 | 0.0047058 | 0.00052287 | 22.8580564336757 | 0.316240339279304 | 0.0047058 | 0.00052287 | 0
19/02/2006 | 2005 | 0.3726 | 0.016209 | 22.8580564336757 | 0.316240339279304 | 0.3726 | 0.016209 | 0
21/02/2006 | 2005 | 4.2708 | 0.029964 | 22.8580564336757 | 0.316240339279304 | 4.2708 | 0.029964 | 0
23/02/2006 | 2005 | 0.10256 | 0.00060331 | 22.8580564336757 | 0.316240339279304 | 0.10256 | 0.00060331 | 0
27/02/2006 | 2005 | 4.5622 | 0.22588 | 22.8580564336757 | 0.316240339279304 | 4.5622 | 0.22588 | 0
28/02/2006 | 2005 | 0.16434 | 0.0070386 | 22.8580564336757 | 0.316240339279304 | 0.16434 | 0.0070386 | 0
02/03/2006 | 2005 | 1.7163 | 0.018501 | 22.8580564336757 | 0.316240339279304 | 1.7163 | 0.018501 | 0
04/03/2006 | 2005 | 4.2036 | 0.070587 | 22.8580564336757 | 0.316240339279304 | 4.2036 | 0.070587 | 0
05/03/2006 | 2005 | 0.95648 | 0.012066 | 22.8580564336757 | 0.316240339279304 | 0.95648 | 0.012066 | 0
06/03/2006 | 2005 | 2.4995 | 0.0070788 | 22.8580564336757 | 0.316240339279304 | 2.4995 | 0.0070788 | 0
07/03/2006 | 2005 | 0.036239 | 0.0021317 | 22.8580564336757 | 0.316240339279304 | 0.036239 | 0.0021317 | 0
09/03/2006 | 2005 | 1.1094 | 0.04191 | 22.8580564336757 | 0.316240339279304 | 1.1094 | 0.04191 | 0
12/03/2006 | 2005 | 1.1139 | 0.0044645 | 22.8580564336757 | 0.316240339279304 | 1.1139 | 0.0044645 | 0
16/03/2006 | 2005 | 0.024454 | 0.0012871 | 22.8580564336757 | 0.316240339279304 | 0.024454 | 0.0012871 | 0
18/03/2006 | 2005 | 2.7566 | 0.010296 | 22.8580564336757 | 0.316240339279304 | 2.7566 | 0.010296 | 0
20/03/2006 | 2005 | 0.10317 | 0.00076419 | 22.8580564336757 | 0.316240339279304 | 0.10317 | 0.00076419 | 0
22/03/2006 | 2005 | 1.3237 | 0.033705 | 22.8580564336757 | 0.316240339279304 | 1.3237 | 0.033705 | 0
23/03/2006 | 2005 | 2.1277 | 0.021035 | 22.8580564336757 | 0.316240339279304 | 2.1277 | 0.021035 | 0
24/03/2006 | 2005 | 0.76037 | 0.0080039 | 22.8580564336757 | 0.316240339279304 | 0.76037 | 0.0080039 | 0
26/03/2006 | 2005 | 1.1162 | 0.013796 | 22.8580564336757 | 0.316240339279304 | 1.1162 | 0.013796 | 0
28/03/2006 | 2005 | 4.2609 | 0.045409 | 22.8580564336757 | 0.316240339279304 | 4.2609 | 0.045409 | 0
30/03/2006 | 2005 | 0.89048 | 0.0098942 | 22.8580564336757 | 0.316240339279304 | 0.89048 | 0.0098942 | 0
01/04/2006 | 2006 | 1.8735 | 0.039522 | 22.8580564336757 | 0.316240339279304 | 1.8735 | 0.039522 | 0
03/04/2006 | 2006 | 0.06484 | 0.00032099 | 22.8580564336757 | 0.316240339279304 | 0.06484 | 0.00032099 | 0
05/04/2006 | 2006 | 2.0019 | 0.017815 | 22.8580564336757 | 0.316240339279304 | 2.0019 | 0.017815 | 0
10/04/2006 | 2006 | 0.40589 | 0.0014444 | 22.8580564336757 | 0.316240339279304 | 0.40589 | 0.0014444 | 0
12/04/2006 | 2006 | 0.53433 | 0.02592 | 22.8580564336757 | 0.316240339279304 | 0.53433 | 0.02592 | 0
18/04/2006 | 2006 | 5.4223 | 0.047627 | 22.8580564336757 | 0.316240339279304 | 5.4223 | 0.047627 | 0
19/04/2006 | 2006 | 0.2086 | 0.0073025 | 22.8580564336757 | 0.316240339279304 | 0.2086 | 0.0073025 | 0
20/04/2006 | 2006 | 0.23649 | 0.0044136 | 22.8580564336757 | 0.316240339279304 | 0.23649 | 0.0044136 | 0
21/04/2006 | 2006 | 0.28953 | 0.0016451 | 22.8580564336757 | 0.316240339279304 | 0.28953 | 0.0016451 | 0
24/04/2006 | 2006 | 0.99988 | 0.029812 | 22.8580564336757 | 0.316240339279304 | 0.99988 | 0.029812 | 0
26/04/2006 | 2006 | 0.37467 | 0.0087068 | 22.8580564336757 | 0.316240339279304 | 0.37467 | 0.0087068 | 0
27/04/2006 | 2006 | 0.43955 | 0.0028087 | 22.8580564336757 | 0.316240339279304 | 0.43955 | 0.0028087 | 0
28/04/2006 | 2006 | 3.7524 | 0.01312 | 22.8580564336757 | 0.316240339279304 | 3.7524 | 0.01312 | 0
30/04/2006 | 2006 | 0.34322 | 0.002929 | 22.8580564336757 | 0.316240339279304 | 0.34322 | 0.002929 | 0
01/05/2006 | 2006 | 0.080408 | 0.0020864 | 22.8580564336757 | 0.316240339279304 | 0.080408 | 0.0020864 | 0
02/05/2006 | 2006 | 0.33904 | 0.0010432 | 22.8580564336757 | 0.316240339279304 | 0.33904 | 0.0010432 | 0
03/05/2006 | 2006 | 0.30586 | 0.0078642 | 22.8580564336757 | 0.316240339279304 | 0.30586 | 0.0078642 | 0
04/05/2006 | 2006 | 1.1649 | 0.034506 | 22.8580564336757 | 0.316240339279304 | 1.1649 | 0.034506 | 0
06/05/2006 | 2006 | 1.8648 | 0.0074229 | 22.8580564336757 | 0.316240339279304 | 1.8648 | 0.0074229 | 0
07/05/2006 | 2006 | 0.32604 | 0.0040124 | 22.8580564336757 | 0.316240339279304 | 0.32604 | 0.0040124 | 0
08/05/2006 | 2006 | 3.1773 | 0.018818 | 22.8580564336757 | 0.316240339279304 | 3.1773 | 0.018818 | 0
09/05/2006 | 2006 | 0.89227 | 0.0047747 | 22.8580564336757 | 0.316240339279304 | 0.89227 | 0.0047747 | 0
11/05/2006 | 2006 | 0.27517 | 0.00072222 | 22.8580564336757 | 0.316240339279304 | 0.27517 | 0.00072222 | 0
12/05/2006 | 2006 | 1.6988 | 0.10653 | 22.8580564336757 | 0.316240339279304 | 1.6988 | 0.10653 | 0
15/05/2006 | 2006 | 0.57914 | 0.064358 | 22.8580564336757 | 0.316240339279304 | 0.57914 | 0.064358 | 0
18/05/2006 | 2006 | 0.34687 | 0.0014043 | 22.8580564336757 | 0.316240339279304 | 0.34687 | 0.0014043 | 0
19/05/2006 | 2006 | 0.037877 | 0.00032099 | 22.8580564336757 | 0.316240339279304 | 0.037877 | 0.00032099 | 0
22/05/2006 | 2006 | 0.29226 | 0.0015648 | 22.8580564336757 | 0.316240339279304 | 0.29226 | 0.0015648 | 0
24/05/2006 | 2006 | 0.22658 | 0.0038519 | 22.8580564336757 | 0.316240339279304 | 0.22658 | 0.0038519 | 0
25/05/2006 | 2006 | 0.0072222 | 0.0018056 | 22.8580564336757 | 0.316240339279304 | 0.0072222 | 0.0018056 | 0
27/05/2006 | 2006 | 0.50933 | 0.0038519 | 22.8580564336757 | 0.316240339279304 | 0.50933 | 0.0038519 | 0
28/05/2006 | 2006 | 6.7386 | 0.30622 | 22.8580564336757 | 0.316240339279304 | 6.7386 | 0.30622 | 0
30/05/2006 | 2006 | 0.6486 | 0.0021265 | 22.8580564336757 | 0.316240339279304 | 0.6486 | 0.0021265 | 0
03/06/2006 | 2006 | 3.9736 | 0.056935 | 22.8580564336757 | 0.316240339279304 | 3.9736 | 0.056935 | 0
04/06/2006 | 2006 | 0.32392 | 0.0058179 | 22.8580564336757 | 0.316240339279304 | 0.32392 | 0.0058179 | 0
05/06/2006 | 2006 | 0.26141 | 0.00088272 | 22.8580564336757 | 0.316240339279304 | 0.26141 | 0.00088272 | 0
06/06/2006 | 2006 | 0.031738 | 0.00028087 | 22.8580564336757 | 0.316240339279304 | 0.031738 | 0.00028087 | 0
09/06/2006 | 2006 | 0.47623 | 0.035309 | 22.8580564336757 | 0.316240339279304 | 0.47623 | 0.035309 | 0
10/06/2006 | 2006 | 0.68238 | 0.02925 | 22.8580564336757 | 0.316240339279304 | 0.68238 | 0.02925 | 0
11/06/2006 | 2006 | 2.3195 | 0.060506 | 22.8580564336757 | 0.316240339279304 | 2.3195 | 0.060506 | 0
12/06/2006 | 2006 | 32.7149 | 0.12238 | 22.8580564336757 | 0.316240339279304 | 22.8581 | 0.12238 | 1 | 9.8569 | 0
13/06/2006 | 2006 | 0.90627 | 0.0016451 | 22.8580564336757 | 0.316240339279304 | 0.90627 | 0.0016451 | 0
14/06/2006 | 2006 | 0.73177 | 0.0053766 | 22.8580564336757 | 0.316240339279304 | 0.73177 | 0.0053766 | 0
15/06/2006 | 2006 | 4.3301 | 0.13642 | 22.8580564336757 | 0.316240339279304 | 4.3301 | 0.13642 | 0
16/06/2006 | 2006 | 1.5095 | 0.047306 | 22.8580564336757 | 0.316240339279304 | 1.5095 | 0.047306 | 0
18/06/2006 | 2006 | 3.2306 | 0.01633 | 22.8580564336757 | 0.316240339279304 | 3.2306 | 0.01633 | 0
19/06/2006 | 2006 | 16.5261 | 0.10681 | 22.8580564336757 | 0.316240339279304 | 16.5261 | 0.10681 | 0
20/06/2006 | 2006 | 1.4977 | 0.0090278 | 22.8580564336757 | 0.316240339279304 | 1.4977 | 0.0090278 | 0
21/06/2006 | 2006 | 0.17602 | 0.0030895 | 22.8580564336757 | 0.316240339279304 | 0.17602 | 0.0030895 | 0
22/06/2006 | 2006 | 1.4179 | 0.012759 | 22.8580564336757 | 0.316240339279304 | 1.4179 | 0.012759 | 0
23/06/2006 | 2006 | 10.1347 | 0.031296 | 22.8580564336757 | 0.316240339279304 | 10.1347 | 0.031296 | 0
25/06/2006 | 2006 | 3.225 | 0.0006821 | 22.8580564336757 | 0.316240339279304 | 3.225 | 0.0006821 | 0
26/06/2006 | 2006 | 8.6819 | 0.0026482 | 22.8580564336757 | 0.316240339279304 | 8.6819 | 0.0026482 | 0
27/06/2006 | 2006 | 0.84601 | 0.0040926 | 22.8580564336757 | 0.316240339279304 | 0.84601 | 0.0040926 | 0
28/06/2006 | 2006 | 0.10472 | 0.0012037 | 22.8580564336757 | 0.316240339279304 | 0.10472 | 0.0012037 | 0
29/06/2006 | 2006 | 8.2165 | 0.00092284 | 22.8580564336757 | 0.316240339279304 | 8.2165 | 0.00092284 | 0
05/07/2006 | 2006 | 0.8769 | 0.0054969 | 22.8580564336757 | 0.316240339279304 | 0.8769 | 0.0054969 | 0
06/07/2006 | 2006 | 0.046343 | 0.0008426 | 22.8580564336757 | 0.316240339279304 | 0.046343 | 0.0008426 | 0
07/07/2006 | 2006 | 3.3664 | 0.0075432 | 22.8580564336757 | 0.316240339279304 | 3.3664 | 0.0075432 | 0
10/07/2006 | 2006 | 1.5842 | 0.033664 | 22.8580564336757 | 0.316240339279304 | 1.5842 | 0.033664 | 0
14/07/2006 | 2006 | 0.15861 | 0.0040525 | 22.8580564336757 | 0.316240339279304 | 0.15861 | 0.0040525 | 0
17/07/2006 | 2006 | 0.34049 | 0.0033704 | 22.8580564336757 | 0.316240339279304 | 0.34049 | 0.0033704 | 0
18/07/2006 | 2006 | 0.22349 | 0.0037315 | 22.8580564336757 | 0.316240339279304 | 0.22349 | 0.0037315 | 0
19/07/2006 | 2006 | 1.9507 | 0.02608 | 22.8580564336757 | 0.316240339279304 | 1.9507 | 0.02608 | 0
20/07/2006 | 2006 | 0.71974 | 0.0046543 | 22.8580564336757 | 0.316240339279304 | 0.71974 | 0.0046543 | 0
21/07/2006 | 2006 | 0.87867 | 0.011917 | 22.8580564336757 | 0.316240339279304 | 0.87867 | 0.011917 | 0
24/07/2006 | 2006 | 0.44826 | 0.0017654 | 22.8580564336757 | 0.316240339279304 | 0.44826 | 0.0017654 | 0
26/07/2006 | 2006 | 0.13161 | 0.00064198 | 22.8580564336757 | 0.316240339279304 | 0.13161 | 0.00064198 | 0
27/07/2006 | 2006 | 1.7244 | 0.012679 | 22.8580564336757 | 0.316240339279304 | 1.7244 | 0.012679 | 0
31/07/2006 | 2006 | 0.72026 | 0.0037716 | 22.8580564336757 | 0.316240339279304 | 0.72026 | 0.0037716 | 0
01/08/2006 | 2006 | 0.20254 | 0.00064198 | 22.8580564336757 | 0.316240339279304 | 0.20254 | 0.00064198 | 0
04/08/2006 | 2006 | 0.50447 | 0.006179 | 22.8580564336757 | 0.316240339279304 | 0.50447 | 0.006179 | 0
07/08/2006 | 2006 | 0.63881 | 0.0052562 | 22.8580564336757 | 0.316240339279304 | 0.63881 | 0.0052562 | 0
08/08/2006 | 2006 | 3.933 | 0.017975 | 22.8580564336757 | 0.316240339279304 | 3.933 | 0.017975 | 0
10/08/2006 | 2006 | 0.28227 | 0.0008426 | 22.8580564336757 | 0.316240339279304 | 0.28227 | 0.0008426 | 0
11/08/2006 | 2006 | 0.21282 | 0.0091482 | 22.8580564336757 | 0.316240339279304 | 0.21282 | 0.0091482 | 0
13/08/2006 | 2006 | 2.4983 | 0.056494 | 22.8580564336757 | 0.316240339279304 | 2.4983 | 0.056494 | 0
15/08/2006 | 2006 | 0.03258 | 0.0011636 | 22.8580564336757 | 0.316240339279304 | 0.03258 | 0.0011636 | 0
16/08/2006 | 2006 | 0.11664 | 0.00036111 | 22.8580564336757 | 0.316240339279304 | 0.11664 | 0.00036111 | 0
17/08/2006 | 2006 | 0.11034 | 0.0010432 | 22.8580564336757 | 0.316240339279304 | 0.11034 | 0.0010432 | 0
18/08/2006 | 2006 | 1.0469 | 0.017534 | 22.8580564336757 | 0.316240339279304 | 1.0469 | 0.017534 | 0
19/08/2006 | 2006 | 4.4253 | 0.047225 | 22.8580564336757 | 0.316240339279304 | 4.4253 | 0.047225 | 0
23/08/2006 | 2006 | 0.51306 | 0.002929 | 22.8580564336757 | 0.316240339279304 | 0.51306 | 0.002929 | 0
24/08/2006 | 2006 | 0.0050556 | 0.0025278 | 22.8580564336757 | 0.316240339279304 | 0.0050556 | 0.0025278 | 0
25/08/2006 | 2006 | 0.31694 | 0.0013241 | 22.8580564336757 | 0.316240339279304 | 0.31694 | 0.0013241 | 0
26/08/2006 | 2006 | 0.42314 | 0.0037716 | 22.8580564336757 | 0.316240339279304 | 0.42314 | 0.0037716 | 0
29/08/2006 | 2006 | 1.3778 | 0.0056173 | 22.8580564336757 | 0.316240339279304 | 1.3778 | 0.0056173 | 0
30/08/2006 | 2006 | 3.4684 | 0.096096 | 22.8580564336757 | 0.316240339279304 | 3.4684 | 0.096096 | 0
31/08/2006 | 2006 | 1.0613 | 0.0047747 | 22.8580564336757 | 0.316240339279304 | 1.0613 | 0.0047747 | 0
03/09/2006 | 2006 | 0.67576 | 0.032179 | 22.8580564336757 | 0.316240339279304 | 0.67576 | 0.032179 | 0
05/09/2006 | 2006 | 1.2977 | 0.014685 | 22.8580564336757 | 0.316240339279304 | 1.2977 | 0.014685 | 0
07/09/2006 | 2006 | 4.0201 | 0.024877 | 22.8580564336757 | 0.316240339279304 | 4.0201 | 0.024877 | 0
08/09/2006 | 2006 | 1.2358 | 0.0089877 | 22.8580564336757 | 0.316240339279304 | 1.2358 | 0.0089877 | 0
11/09/2006 | 2006 | 0.18938 | 0.0050556 | 22.8580564336757 | 0.316240339279304 | 0.18938 | 0.0050556 | 0
12/09/2006 | 2006 | 0.05192 | 0.0016451 | 22.8580564336757 | 0.316240339279304 | 0.05192 | 0.0016451 | 0
14/09/2006 | 2006 | 0.061991 | 0.00020062 | 22.8580564336757 | 0.316240339279304 | 0.061991 | 0.00020062 | 0
19/09/2006 | 2006 | 0.43012 | 0.0026883 | 22.8580564336757 | 0.316240339279304 | 0.43012 | 0.0026883 | 0
21/09/2006 | 2006 | 0.1637 | 0.0027284 | 22.8580564336757 | 0.316240339279304 | 0.1637 | 0.0027284 | 0
26/09/2006 | 2006 | 0.46399 | 0.0042531 | 22.8580564336757 | 0.316240339279304 | 0.46399 | 0.0042531 | 0
27/09/2006 | 2006 | 0.24074 | 0.0055371 | 22.8580564336757 | 0.316240339279304 | 0.24074 | 0.0055371 | 0
29/09/2006 | 2006 | 0.51735 | 0.0037716 | 22.8580564336757 | 0.316240339279304 | 0.51735 | 0.0037716 | 0
30/09/2006 | 2006 | 0.053725 | 0.006179 | 22.8580564336757 | 0.316240339279304 | 0.053725 | 0.006179 | 0
02/10/2006 | 2006 | 0.17622 | 0.012198 | 22.8580564336757 | 0.316240339279304 | 0.17622 | 0.012198 | 0
04/10/2006 | 2006 | 1.3877 | 0.033543 | 22.8580564336757 | 0.316240339279304 | 1.3877 | 0.033543 | 0
05/10/2006 | 2006 | 0.88424 | 0.015086 | 22.8580564336757 | 0.316240339279304 | 0.88424 | 0.015086 | 0
07/10/2006 | 2006 | 1.9651 | 0.033182 | 22.8580564336757 | 0.316240339279304 | 1.9651 | 0.033182 | 0
08/10/2006 | 2006 | 0.38438 | 0.0071821 | 22.8580564336757 | 0.316240339279304 | 0.38438 | 0.0071821 | 0
09/10/2006 | 2006 | 0.46435 | 0.0088673 | 22.8580564336757 | 0.316240339279304 | 0.46435 | 0.0088673 | 0
10/10/2006 | 2006 | 1.0396 | 0.02596 | 22.8580564336757 | 0.316240339279304 | 1.0396 | 0.02596 | 0
13/10/2006 | 2006 | 0.09425 | 0.0010833 | 22.8580564336757 | 0.316240339279304 | 0.09425 | 0.0010833 | 0
15/10/2006 | 2006 | 1.8308 | 0.043133 | 22.8580564336757 | 0.316240339279304 | 1.8308 | 0.043133 | 0
17/10/2006 | 2006 | 0.25085 | 0.0068611 | 22.8580564336757 | 0.316240339279304 | 0.25085 | 0.0068611 | 0
18/10/2006 | 2006 | 0.03912 | 0.0014846 | 22.8580564336757 | 0.316240339279304 | 0.03912 | 0.0014846 | 0
24/10/2006 | 2006 | 0.62769 | 0.0065 | 22.8580564336757 | 0.316240339279304 | 0.62769 | 0.0065 | 0
25/10/2006 | 2006 | 0.10725 | 0.0013241 | 22.8580564336757 | 0.316240339279304 | 0.10725 | 0.0013241 | 0
27/10/2006 | 2006 | 0.032099 | 0.0080247 | 22.8580564336757 | 0.316240339279304 | 0.032099 | 0.0080247 | 0
29/10/2006 | 2006 | 1.646 | 0.0079846 | 22.8580564336757 | 0.316240339279304 | 1.646 | 0.0079846 | 0
31/10/2006 | 2006 | 0.86603 | 0.002608 | 22.8580564336757 | 0.316240339279304 | 0.86603 | 0.002608 | 0
02/11/2006 | 2006 | 0.088673 | 0.00052161 | 22.8580564336757 | 0.316240339279304 | 0.088673 | 0.00052161 | 0
06/11/2006 | 2006 | 0.15139 | 0.021627 | 22.8580564336757 | 0.316240339279304 | 0.15139 | 0.021627 | 0
07/11/2006 | 2006 | 0.71677 | 0.022068 | 22.8580564336757 | 0.316240339279304 | 0.71677 | 0.022068 | 0
08/11/2006 | 2006 | 2.6315 | 0.069695 | 22.8580564336757 | 0.316240339279304 | 2.6315 | 0.069695 | 0
09/11/2006 | 2006 | 0.099506 | 0.0040124 | 22.8580564336757 | 0.316240339279304 | 0.099506 | 0.0040124 | 0
13/11/2006 | 2006 | 0.46808 | 0.0086667 | 22.8580564336757 | 0.316240339279304 | 0.46808 | 0.0086667 | 0
14/11/2006 | 2006 | 0.027284 | 0.0006821 | 22.8580564336757 | 0.316240339279304 | 0.027284 | 0.0006821 | 0
18/11/2006 | 2006 | 1.5799 | 0.089476 | 22.8580564336757 | 0.316240339279304 | 1.5799 | 0.089476 | 0
19/11/2006 | 2006 | 0.33391 | 0.0067006 | 22.8580564336757 | 0.316240339279304 | 0.33391 | 0.0067006 | 0
20/11/2006 | 2006 | 0.038117 | 0.0015247 | 22.8580564336757 | 0.316240339279304 | 0.038117 | 0.0015247 | 0
21/11/2006 | 2006 | 0.039642 | 0.0015247 | 22.8580564336757 | 0.316240339279304 | 0.039642 | 0.0015247 | 0
23/11/2006 | 2006 | 0.18778 | 0.0031296 | 22.8580564336757 | 0.316240339279304 | 0.18778 | 0.0031296 | 0
24/11/2006 | 2006 | 1.1686 | 0.011074 | 22.8580564336757 | 0.316240339279304 | 1.1686 | 0.011074 | 0
26/11/2006 | 2006 | 0.79035 | 0.014043 | 22.8580564336757 | 0.316240339279304 | 0.79035 | 0.014043 | 0
28/11/2006 | 2006 | 0.47125 | 0.01625 | 22.8580564336757 | 0.316240339279304 | 0.47125 | 0.01625 | 0
29/11/2006 | 2006 | 0.42832 | 0.0010031 | 22.8580564336757 | 0.316240339279304 | 0.42832 | 0.0010031 | 0
30/11/2006 | 2006 | 5.0383 | 0.040364 | 22.8580564336757 | 0.316240339279304 | 5.0383 | 0.040364 | 0
01/12/2006 | 2006 | 0.24676 | 0.0070216 | 22.8580564336757 | 0.316240339279304 | 0.24676 | 0.0070216 | 0
03/12/2006 | 2006 | 1.1231 | 0.010593 | 22.8580564336757 | 0.316240339279304 | 1.1231 | 0.010593 | 0
05/12/2006 | 2006 | 1.0644 | 0.0062994 | 22.8580564336757 | 0.316240339279304 | 1.0644 | 0.0062994 | 0
06/12/2006 | 2006 | 0.77314 | 0.005858 | 22.8580564336757 | 0.316240339279304 | 0.77314 | 0.005858 | 0
10/12/2006 | 2006 | 0.14111 | 0.0015648 | 22.8580564336757 | 0.316240339279304 | 0.14111 | 0.0015648 | 0
11/12/2006 | 2006 | 0.27637 | 0.0062192 | 22.8580564336757 | 0.316240339279304 | 0.27637 | 0.0062192 | 0
12/12/2006 | 2006 | 0.82731 | 0.0037716 | 22.8580564336757 | 0.316240339279304 | 0.82731 | 0.0037716 | 0
16/12/2006 | 2006 | 2.2956 | 0.030855 | 22.8580564336757 | 0.316240339279304 | 2.2956 | 0.030855 | 0
18/12/2006 | 2006 | 0.82807 | 0.013762 | 22.8580564336757 | 0.316240339279304 | 0.82807 | 0.013762 | 0
19/12/2006 | 2006 | 0.11752 | 0.0040525 | 22.8580564336757 | 0.316240339279304 | 0.11752 | 0.0040525 | 0
20/12/2006 | 2006 | 0.65863 | 0.0056173 | 22.8580564336757 | 0.316240339279304 | 0.65863 | 0.0056173 | 0
21/12/2006 | 2006 | 0.48253 | 0.0096297 | 22.8580564336757 | 0.316240339279304 | 0.48253 | 0.0096297 | 0
23/12/2006 | 2006 | 4.1557 | 0.098945 | 22.8580564336757 | 0.316240339279304 | 4.1557 | 0.098945 | 0
24/12/2006 | 2006 | 2.0034 | 0.049914 | 22.8580564336757 | 0.316240339279304 | 2.0034 | 0.049914 | 0
28/12/2006 | 2006 | 0.021346 | 0.00076235 | 22.8580564336757 | 0.316240339279304 | 0.021346 | 0.00076235 | 0
02/01/2007 | 2006 | 2.2993 | 0.16615 | 22.8580564336757 | 0.316240339279304 | 2.2993 | 0.16615 | 0
04/01/2007 | 2006 | 2.223 | 0.098945 | 22.8580564336757 | 0.316240339279304 | 2.223 | 0.098945 | 0
05/01/2007 | 2006 | 0.1804 | 0.019059 | 22.8580564336757 | 0.316240339279304 | 0.1804 | 0.019059 | 0
10/01/2007 | 2006 | 0.057377 | 0.002608 | 22.8580564336757 | 0.316240339279304 | 0.057377 | 0.002608 | 0
11/01/2007 | 2006 | 0.35975 | 0.0052562 | 22.8580564336757 | 0.316240339279304 | 0.35975 | 0.0052562 | 0
13/01/2007 | 2006 | 0.36974 | 0.00076235 | 22.8580564336757 | 0.316240339279304 | 0.36974 | 0.00076235 | 0
14/01/2007 | 2006 | 0.54384 | 0.0030494 | 22.8580564336757 | 0.316240339279304 | 0.54384 | 0.0030494 | 0
15/01/2007 | 2006 | 0.44593 | 0.01296 | 22.8580564336757 | 0.316240339279304 | 0.44593 | 0.01296 | 0
20/01/2007 | 2006 | 0.16864 | 0.016411 | 22.8580564336757 | 0.316240339279304 | 0.16864 | 0.016411 | 0
22/01/2007 | 2006 | 0.80307 | 0.0057778 | 22.8580564336757 | 0.316240339279304 | 0.80307 | 0.0057778 | 0
23/01/2007 | 2006 | 0.020222 | 0.00036111 | 22.8580564336757 | 0.316240339279304 | 0.020222 | 0.00036111 | 0
26/01/2007 | 2006 | 0.22365 | 0.0062593 | 22.8580564336757 | 0.316240339279304 | 0.22365 | 0.0062593 | 0
31/01/2007 | 2006 | 1.2827 | 0.0079445 | 22.8580564336757 | 0.316240339279304 | 1.2827 | 0.0079445 | 0
02/02/2007 | 2006 | 0.29262 | 0.0006821 | 22.8580564336757 | 0.316240339279304 | 0.29262 | 0.0006821 | 0
05/02/2007 | 2006 | 0.1613 | 0.0080648 | 22.8580564336757 | 0.316240339279304 | 0.1613 | 0.0080648 | 0
07/02/2007 | 2006 | 0.086667 | 0.0021667 | 22.8580564336757 | 0.316240339279304 | 0.086667 | 0.0021667 | 0
12/02/2007 | 2006 | 0.99378 | 0.0021667 | 22.8580564336757 | 0.316240339279304 | 0.99378 | 0.0021667 | 0
15/02/2007 | 2006 | 0.39076 | 0.0034105 | 22.8580564336757 | 0.316240339279304 | 0.39076 | 0.0034105 | 0
16/02/2007 | 2006 | 0.30366 | 0.0017654 | 22.8580564336757 | 0.316240339279304 | 0.30366 | 0.0017654 | 0
17/02/2007 | 2006 | 0.50716 | 0.00064198 | 22.8580564336757 | 0.316240339279304 | 0.50716 | 0.00064198 | 0
19/02/2007 | 2006 | 0.99161 | 0.0064198 | 22.8580564336757 | 0.316240339279304 | 0.99161 | 0.0064198 | 0
21/02/2007 | 2006 | 1.8106 | 0.0093889 | 22.8580564336757 | 0.316240339279304 | 1.8106 | 0.0093889 | 0
28/02/2007 | 2006 | 0.043333 | 0.00024074 | 22.8580564336757 | 0.316240339279304 | 0.043333 | 0.00024074 | 0
05/03/2007 | 2006 | 0.40027 | 0.0036111 | 22.8580564336757 | 0.316240339279304 | 0.40027 | 0.0036111 | 0
07/03/2007 | 2006 | 0.10617 | 0.0019661 | 22.8580564336757 | 0.316240339279304 | 0.10617 | 0.0019661 | 0
09/03/2007 | 2006 | 0.12133 | 0.0075834 | 22.8580564336757 | 0.316240339279304 | 0.12133 | 0.0075834 | 0
10/03/2007 | 2006 | 4.3672 | 0.20796 | 22.8580564336757 | 0.316240339279304 | 4.3672 | 0.20796 | 0
13/03/2007 | 2006 | 0.63183 | 0.014124 | 22.8580564336757 | 0.316240339279304 | 0.63183 | 0.014124 | 0
14/03/2007 | 2006 | 2.651 | 0.056053 | 22.8580564336757 | 0.316240339279304 | 2.651 | 0.056053 | 0
15/03/2007 | 2006 | 0.82923 | 0.022549 | 22.8580564336757 | 0.316240339279304 | 0.82923 | 0.022549 | 0
16/03/2007 | 2006 | 6.4785 | 0.43029 | 22.8580564336757 | 0.316240339279304 | 6.4785 | 0.43029 | 0
18/03/2007 | 2006 | 0.40116 | 0.0066204 | 22.8580564336757 | 0.316240339279304 | 0.40116 | 0.0066204 | 0
19/03/2007 | 2006 | 0.22509 | 0.0027685 | 22.8580564336757 | 0.316240339279304 | 0.22509 | 0.0027685 | 0
20/03/2007 | 2006 | 0.16948 | 0.00096297 | 22.8580564336757 | 0.316240339279304 | 0.16948 | 0.00096297 | 0
25/03/2007 | 2006 | 0.068611 | 0.00040124 | 22.8580564336757 | 0.316240339279304 | 0.068611 | 0.00040124 | 0
26/03/2007 | 2006 | 0.038519 | 0.0025679 | 22.8580564336757 | 0.316240339279304 | 0.038519 | 0.0025679 | 0
27/03/2007 | 2006 | 0.48594 | 0.0030093 | 22.8580564336757 | 0.316240339279304 | 0.48594 | 0.0030093 | 0
28/03/2007 | 2006 | 0.036914 | 0.0016049 | 22.8580564336757 | 0.316240339279304 | 0.036914 | 0.0016049 | 0
29/03/2007 | 2006 | 0.043695 | 0.0038117 | 22.8580564336757 | 0.316240339279304 | 0.043695 | 0.0013241 | 0
30/03/2007 | 2006 | 0.5655 | 0.0091482 | 22.8580564336757 | 0.316240339279304 | 0.5655 | 0.0091482 | 0
31/03/2007 | 2006 | 0.087068 | 0.00056173 | 22.8580564336757 | 0.316240339279304 | 0.087068 | 0.00056173 | 0
02/04/2007 | 2007 | 0.1172 | 0.00055808 | 22.8580564336757 | 0.316240339279304 | 0.1172 | 0.00055808 | 0
10/04/2007 | 2007 | 0.15016 | 0.001156 | 22.8580564336757 | 0.316240339279304 | 0.15016 | 0.001156 | 0
11/04/2007 | 2007 | 0.20884 | 0.0016344 | 22.8580564336757 | 0.316240339279304 | 0.20884 | 0.0016344 | 0
13/04/2007 | 2007 | 0.8791 | 0.014351 | 22.8580564336757 | 0.316240339279304 | 0.8791 | 0.014351 | 0
16/04/2007 | 2007 | 0.14769 | 0.00071753 | 22.8580564336757 | 0.316240339279304 | 0.14769 | 0.00071753 | 0
17/04/2007 | 2007 | 1.2593 | 0.016224 | 22.8580564336757 | 0.316240339279304 | 1.2593 | 0.016224 | 0
18/04/2007 | 2007 | 0.10891 | 0.0082118 | 22.8580564336757 | 0.316240339279304 | 0.10891 | 0.0082118 | 0
26/04/2007 | 2007 | 1.0783 | 0.043132 | 22.8580564336757 | 0.316240339279304 | 1.0783 | 0.043132 | 0
01/05/2007 | 2007 | 3.6174 | 0.02619 | 22.8580564336757 | 0.316240339279304 | 3.6174 | 0.02619 | 0
03/05/2007 | 2007 | 0.51519 | 0.037192 | 22.8580564336757 | 0.316240339279304 | 0.51519 | 0.037192 | 0
06/05/2007 | 2007 | 0.073348 | 0.0037471 | 22.8580564336757 | 0.316240339279304 | 0.073348 | 0.0037471 | 0
08/05/2007 | 2007 | 0.25472 | 0.00071753 | 22.8580564336757 | 0.316240339279304 | 0.25472 | 0.00071753 | 0
09/05/2007 | 2007 | 4.0601 | 0.2025 | 22.8580564336757 | 0.316240339279304 | 4.0601 | 0.2025 | 0
15/05/2007 | 2007 | 0.99597 | 0.0059794 | 22.8580564336757 | 0.316240339279304 | 0.99597 | 0.0059794 | 0
18/05/2007 | 2007 | 4.9449 | 0.036833 | 22.8580564336757 | 0.316240339279304 | 4.9449 | 0.036833 | 0
19/05/2007 | 2007 | 0.10472 | 0.00043849 | 22.8580564336757 | 0.316240339279304 | 0.10472 | 0.00043849 | 0
21/05/2007 | 2007 | 0.08132 | 0.00047835 | 22.8580564336757 | 0.316240339279304 | 0.08132 | 0.00047835 | 0
23/05/2007 | 2007 | 1.4918 | 0.011002 | 22.8580564336757 | 0.316240339279304 | 1.4918 | 0.011002 | 0
26/05/2007 | 2007 | 0.047995 | 0.00027904 | 22.8580564336757 | 0.316240339279304 | 0.047995 | 0.00027904 | 0
28/05/2007 | 2007 | 0.60843 | 0.0045444 | 22.8580564336757 | 0.316240339279304 | 0.60843 | 0.0045444 | 0
29/05/2007 | 2007 | 0.00047835 | 0.00011959 | 22.8580564336757 | 0.316240339279304 | 0.00047835 | 0.00011959 | 0
30/05/2007 | 2007 | 0.002312 | 7.9726e-05 | 22.8580564336757 | 0.316240339279304 | 0.002312 | 7.9726e-05 | 0
31/05/2007 | 2007 | 2.2652 | 0.038189 | 22.8580564336757 | 0.316240339279304 | 2.2652 | 0.038189 | 0
01/06/2007 | 2007 | 0.21083 | 0.0010763 | 22.8580564336757 | 0.316240339279304 | 0.21083 | 0.0010763 | 0
02/06/2007 | 2007 | 0.49709 | 0.0035877 | 22.8580564336757 | 0.316240339279304 | 0.49709 | 0.0035877 | 0
05/06/2007 | 2007 | 0.64135 | 0.006697 | 22.8580564336757 | 0.316240339279304 | 0.64135 | 0.006697 | 0
06/06/2007 | 2007 | 0.61437 | 0.0054214 | 22.8580564336757 | 0.316240339279304 | 0.61437 | 0.0054214 | 0
07/06/2007 | 2007 | 1.2122 | 0.046679 | 22.8580564336757 | 0.316240339279304 | 1.2122 | 0.046679 | 0
08/06/2007 | 2007 | 0.1789 | 0.00063781 | 22.8580564336757 | 0.316240339279304 | 0.1789 | 0.00063781 | 0
09/06/2007 | 2007 | 0.062784 | 0.00083712 | 22.8580564336757 | 0.316240339279304 | 0.062784 | 0.00083712 | 0
12/06/2007 | 2007 | 0.28151 | 0.077573 | 22.8580564336757 | 0.316240339279304 | 0.28151 | 0.077573 | 0
13/06/2007 | 2007 | 1.1691 | 0.047198 | 22.8580564336757 | 0.316240339279304 | 1.1691 | 0.047198 | 0
14/06/2007 | 2007 | 0.4595 | 0.0080124 | 22.8580564336757 | 0.316240339279304 | 0.4595 | 0.0080124 | 0
15/06/2007 | 2007 | 0.12943 | 0.0048234 | 22.8580564336757 | 0.316240339279304 | 0.12943 | 0.0048234 | 0
16/06/2007 | 2007 | 0.33381 | 0.010843 | 22.8580564336757 | 0.316240339279304 | 0.33381 | 0.010843 | 0
17/06/2007 | 2007 | 0.01467 | 0.00015945 | 22.8580564336757 | 0.316240339279304 | 0.01467 | 0.00015945 | 0
18/06/2007 | 2007 | 0.62274 | 0.0081719 | 22.8580564336757 | 0.316240339279304 | 0.62274 | 0.0081719 | 0
20/06/2007 | 2007 | 3.0324 | 0.010285 | 22.8580564336757 | 0.316240339279304 | 3.0324 | 0.010285 | 0
21/06/2007 | 2007 | 3.2829 | 0.011999 | 22.8580564336757 | 0.316240339279304 | 3.2829 | 0.011999 | 0
22/06/2007 | 2007 | 7.5185 | 0.098461 | 22.8580564336757 | 0.316240339279304 | 7.5185 | 0.098461 | 0
23/06/2007 | 2007 | 7.0496 | 0.03791 | 22.8580564336757 | 0.316240339279304 | 7.0496 | 0.03791 | 0
24/06/2007 | 2007 | 1.4191 | 0.05828 | 22.8580564336757 | 0.316240339279304 | 1.4191 | 0.05828 | 0
25/06/2007 | 2007 | 0.59838 | 0.016782 | 22.8580564336757 | 0.316240339279304 | 0.59838 | 0.016782 | 0
26/06/2007 | 2007 | 1.5035 | 0.073148 | 22.8580564336757 | 0.316240339279304 | 1.5035 | 0.073148 | 0
27/06/2007 | 2007 | 0.29682 | 0.0028303 | 22.8580564336757 | 0.316240339279304 | 0.29682 | 0.0028303 | 0
29/06/2007 | 2007 | 0.044646 | 0.00027904 | 22.8580564336757 | 0.316240339279304 | 0.044646 | 0.00027904 | 0
03/07/2007 | 2007 | 0.4184 | 0.0012756 | 22.8580564336757 | 0.316240339279304 | 0.4184 | 0.0012756 | 0
04/07/2007 | 2007 | 0.058598 | 0.00083712 | 22.8580564336757 | 0.316240339279304 | 0.058598 | 0.00083712 | 0
05/07/2007 | 2007 | 0.54269 | 0.098621 | 22.8580564336757 | 0.316240339279304 | 0.54269 | 0.098621 | 0
06/07/2007 | 2007 | 0.39735 | 0.013514 | 22.8580564336757 | 0.316240339279304 | 0.39735 | 0.013514 | 0
07/07/2007 | 2007 | 0.19373 | 0.00071753 | 22.8580564336757 | 0.316240339279304 | 0.19373 | 0.00071753 | 0
08/07/2007 | 2007 | 0.73124 | 0.0086502 | 22.8580564336757 | 0.316240339279304 | 0.73124 | 0.0086502 | 0
09/07/2007 | 2007 | 0.025712 | 0.00011959 | 22.8580564336757 | 0.316240339279304 | 0.025712 | 0.00011959 | 0
10/07/2007 | 2007 | 0.32289 | 0.0019931 | 22.8580564336757 | 0.316240339279304 | 0.32289 | 0.0019931 | 0
11/07/2007 | 2007 | 0.065375 | 0.00079726 | 22.8580564336757 | 0.316240339279304 | 0.065375 | 0.00079726 | 0
12/07/2007 | 2007 | 0.030136 | 0.00083712 | 22.8580564336757 | 0.316240339279304 | 0.030136 | 0.00083712 | 0
13/07/2007 | 2007 | 0.35598 | 0.0024316 | 22.8580564336757 | 0.316240339279304 | 0.35598 | 0.0024316 | 0
14/07/2007 | 2007 | 0.36475 | 0.0029897 | 22.8580564336757 | 0.316240339279304 | 0.36475 | 0.0029897 | 0
16/07/2007 | 2007 | 0.13541 | 0.0031492 | 22.8580564336757 | 0.316240339279304 | 0.13541 | 0.0031492 | 0
17/07/2007 | 2007 | 0.73946 | 0.0067767 | 22.8580564336757 | 0.316240339279304 | 0.73946 | 0.0067767 | 0
18/07/2007 | 2007 | 1.176 | 0.016025 | 22.8580564336757 | 0.316240339279304 | 1.176 | 0.016025 | 0
19/07/2007 | 2007 | 0.44144 | 0.009009 | 22.8580564336757 | 0.316240339279304 | 0.44144 | 0.009009 | 0
20/07/2007 | 2007 | 0.49171 | 0.0080124 | 22.8580564336757 | 0.316240339279304 | 0.49171 | 0.0080124 | 0
23/07/2007 | 2007 | 0.70761 | 0.0038667 | 22.8580564336757 | 0.316240339279304 | 0.70761 | 0.0038667 | 0
25/07/2007 | 2007 | 0.36307 | 0.0055011 | 22.8580564336757 | 0.316240339279304 | 0.36307 | 0.0055011 | 0
29/07/2007 | 2007 | 0.028343 | 0.00011959 | 22.8580564336757 | 0.316240339279304 | 0.028343 | 0.00011959 | 0
31/07/2007 | 2007 | 0.5826 | 0.0031492 | 22.8580564336757 | 0.316240339279304 | 0.5826 | 0.0031492 | 0
01/08/2007 | 2007 | 1.8079 | 0.0094475 | 22.8580564336757 | 0.316240339279304 | 1.8079 | 0.0094475 | 0
02/08/2007 | 2007 | 0.080643 | 0.00027904 | 22.8580564336757 | 0.316240339279304 | 0.080643 | 0.00027904 | 0
06/08/2007 | 2007 | 1.8537 | 0.022164 | 22.8580564336757 | 0.316240339279304 | 1.8537 | 0.022164 | 0
07/08/2007 | 2007 | 0.47022 | 0.0019931 | 22.8580564336757 | 0.316240339279304 | 0.47022 | 0.0019931 | 0
08/08/2007 | 2007 | 0.35976 | 0.026589 | 22.8580564336757 | 0.316240339279304 | 0.35976 | 0.026589 | 0
13/08/2007 | 2007 | 0.22076 | 0.0010364 | 22.8580564336757 | 0.316240339279304 | 0.22076 | 0.0010364 | 0
14/08/2007 | 2007 | 0.046759 | 0.0036674 | 22.8580564336757 | 0.316240339279304 | 0.046759 | 0.0036674 | 0
15/08/2007 | 2007 | 0.32416 | 0.0036674 | 22.8580564336757 | 0.316240339279304 | 0.32416 | 0.0036674 | 0
17/08/2007 | 2007 | 0.69337 | 0.010883 | 22.8580564336757 | 0.316240339279304 | 0.69337 | 0.010883 | 0
20/08/2007 | 2007 | 0.21574 | 0.00087698 | 22.8580564336757 | 0.316240339279304 | 0.21574 | 0.00087698 | 0
23/08/2007 | 2007 | 2.2663 | 0.016463 | 22.8580564336757 | 0.316240339279304 | 2.2663 | 0.016463 | 0
24/08/2007 | 2007 | 0.031571 | 0.00011959 | 22.8580564336757 | 0.316240339279304 | 0.031571 | 0.00011959 | 0
27/08/2007 | 2007 | 0.07255 | 0.0010364 | 22.8580564336757 | 0.316240339279304 | 0.07255 | 0.0010364 | 0
28/08/2007 | 2007 | 0.64566 | 0.02312 | 22.8580564336757 | 0.316240339279304 | 0.64566 | 0.02312 | 0
29/08/2007 | 2007 | 0.058678 | 0.00075739 | 22.8580564336757 | 0.316240339279304 | 0.058678 | 0.00075739 | 0
30/08/2007 | 2007 | 0.19477 | 0.00055808 | 22.8580564336757 | 0.316240339279304 | 0.19477 | 0.00055808 | 0
31/08/2007 | 2007 | 0.17113 | 0.0019931 | 22.8580564336757 | 0.316240339279304 | 0.17113 | 0.0019931 | 0
01/09/2007 | 2007 | 0.043809 | 0.00027904 | 22.8580564336757 | 0.316240339279304 | 0.043809 | 0.00027904 | 0
03/09/2007 | 2007 | 0.035 | 0.0023918 | 22.8580564336757 | 0.316240339279304 | 0.035 | 0.0023918 | 0
05/09/2007 | 2007 | 0.36395 | 0.0029499 | 22.8580564336757 | 0.316240339279304 | 0.36395 | 0.0029499 | 0
06/09/2007 | 2007 | 2.7515 | 0.029618 | 22.8580564336757 | 0.316240339279304 | 2.7515 | 0.029618 | 0
07/09/2007 | 2007 | 0.12342 | 0.00071753 | 22.8580564336757 | 0.316240339279304 | 0.12342 | 0.00071753 | 0
11/09/2007 | 2007 | 0.20079 | 0.0045842 | 22.8580564336757 | 0.316240339279304 | 0.20079 | 0.0045842 | 0
15/09/2007 | 2007 | 1.7727 | 0.044088 | 22.8580564336757 | 0.316240339279304 | 1.7727 | 0.044088 | 0
18/09/2007 | 2007 | 0.021845 | 0.0003189 | 22.8580564336757 | 0.316240339279304 | 0.021845 | 0.0003189 | 0
20/09/2007 | 2007 | 0.59994 | 0.003189 | 22.8580564336757 | 0.316240339279304 | 0.59994 | 0.003189 | 0
27/09/2007 | 2007 | 0.021765 | 0.00027904 | 22.8580564336757 | 0.316240339279304 | 0.021765 | 0.00027904 | 0
02/10/2007 | 2007 | 3.9282 | 0.0045842 | 22.8580564336757 | 0.316240339279304 | 3.9282 | 0.0045842 | 0
03/10/2007 | 2007 | 0.88464 | 0.0035079 | 22.8580564336757 | 0.316240339279304 | 0.88464 | 0.0035079 | 0
04/10/2007 | 2007 | 2.0181 | 0.026907 | 22.8580564336757 | 0.316240339279304 | 2.0181 | 0.026907 | 0
05/10/2007 | 2007 | 9.6057 | 0.046799 | 22.8580564336757 | 0.316240339279304 | 9.6057 | 0.046799 | 0
06/10/2007 | 2007 | 0.034442 | 0.00071753 | 22.8580564336757 | 0.316240339279304 | 0.034442 | 0.00071753 | 0
07/10/2007 | 2007 | 4.668 | 0.13637 | 22.8580564336757 | 0.316240339279304 | 4.668 | 0.13637 | 0
08/10/2007 | 2007 | 0.48756 | 0.014111 | 22.8580564336757 | 0.316240339279304 | 0.48756 | 0.014111 | 0
09/10/2007 | 2007 | 0.7686 | 0.0074145 | 22.8580564336757 | 0.316240339279304 | 0.7686 | 0.0074145 | 0
10/10/2007 | 2007 | 0.32847 | 0.0012756 | 22.8580564336757 | 0.316240339279304 | 0.32847 | 0.0012756 | 0
11/10/2007 | 2007 | 3.7551 | 0.027346 | 22.8580564336757 | 0.316240339279304 | 3.7551 | 0.027346 | 0
14/10/2007 | 2007 | 3.5673 | 0.040859 | 22.8580564336757 | 0.316240339279304 | 3.5673 | 0.040859 | 0
15/10/2007 | 2007 | 1.2749 | 0.012078 | 22.8580564336757 | 0.316240339279304 | 1.2749 | 0.012078 | 0
16/10/2007 | 2007 | 0.27637 | 0.0036674 | 22.8580564336757 | 0.316240339279304 | 0.27637 | 0.0036674 | 0
17/10/2007 | 2007 | 11.6543 | 0.29997 | 22.8580564336757 | 0.316240339279304 | 11.6543 | 0.29997 | 0
18/10/2007 | 2007 | 4.0582 | 0.037391 | 22.8580564336757 | 0.316240339279304 | 4.0582 | 0.037391 | 0
19/10/2007 | 2007 | 0.81504 | 0.026429 | 22.8580564336757 | 0.316240339279304 | 0.81504 | 0.026429 | 0
20/10/2007 | 2007 | 0.26999 | 0.0065375 | 22.8580564336757 | 0.316240339279304 | 0.26999 | 0.0065375 | 0
22/10/2007 | 2007 | 0.60424 | 0.043969 | 22.8580564336757 | 0.316240339279304 | 0.60424 | 0.043969 | 0
23/10/2007 | 2007 | 0.25871 | 0.0047038 | 22.8580564336757 | 0.316240339279304 | 0.25871 | 0.0047038 | 0
26/10/2007 | 2007 | 0.14048 | 0.0023918 | 22.8580564336757 | 0.316240339279304 | 0.14048 | 0.0023918 | 0
27/10/2007 | 2007 | 0.46042 | 0.0029897 | 22.8580564336757 | 0.316240339279304 | 0.46042 | 0.0029897 | 0
28/10/2007 | 2007 | 0.63406 | 0.057642 | 22.8580564336757 | 0.316240339279304 | 0.63406 | 0.057642 | 0
29/10/2007 | 2007 | 0.62521 | 0.0047038 | 22.8580564336757 | 0.316240339279304 | 0.62521 | 0.0047038 | 0
01/11/2007 | 2007 | 0.057403 | 0.00047835 | 22.8580564336757 | 0.316240339279304 | 0.057403 | 0.00047835 | 0
02/11/2007 | 2007 | 0.26604 | 0.0055011 | 22.8580564336757 | 0.316240339279304 | 0.26604 | 0.0055011 | 0
04/11/2007 | 2007 | 0.50147 | 0.0027107 | 22.8580564336757 | 0.316240339279304 | 0.50147 | 0.0027107 | 0
06/11/2007 | 2007 | 1.3165 | 0.041497 | 22.8580564336757 | 0.316240339279304 | 1.3165 | 0.041497 | 0
07/11/2007 | 2007 | 1.43 | 0.098461 | 22.8580564336757 | 0.316240339279304 | 1.43 | 0.098461 | 0
09/11/2007 | 2007 | 0.33002 | 0.00873 | 22.8580564336757 | 0.316240339279304 | 0.33002 | 0.00873 | 0
10/11/2007 | 2007 | 1.3913 | 0.042334 | 22.8580564336757 | 0.316240339279304 | 1.3913 | 0.042334 | 0
13/11/2007 | 2007 | 0.22367 | 0.0055808 | 22.8580564336757 | 0.316240339279304 | 0.22367 | 0.0055808 | 0
14/11/2007 | 2007 | 3.9534 | 0.014829 | 22.8580564336757 | 0.316240339279304 | 3.9534 | 0.014829 | 0
21/11/2007 | 2007 | 0.29514 | 0.0024316 | 22.8580564336757 | 0.316240339279304 | 0.29514 | 0.0024316 | 0
22/11/2007 | 2007 | 0.19533 | 0.00079726 | 22.8580564336757 | 0.316240339279304 | 0.19533 | 0.00079726 | 0
24/11/2007 | 2007 | 0.38268 | 0.0015945 | 22.8580564336757 | 0.316240339279304 | 0.38268 | 0.0015945 | 0
26/11/2007 | 2007 | 0.0058598 | 0.00083712 | 22.8580564336757 | 0.316240339279304 | 0.0058598 | 0.00083712 | 0
28/11/2007 | 2007 | 1.2845 | 0.028382 | 22.8580564336757 | 0.316240339279304 | 1.2845 | 0.028382 | 0
01/12/2007 | 2007 | 0.079726 | 0.00039863 | 22.8580564336757 | 0.316240339279304 | 0.079726 | 0.00039863 | 0
03/12/2007 | 2007 | 0.55266 | 0.0055409 | 22.8580564336757 | 0.316240339279304 | 0.55266 | 0.0055409 | 0
06/12/2007 | 2007 | 5.165 | 0.037431 | 22.8580564336757 | 0.316240339279304 | 5.165 | 0.037431 | 0
07/12/2007 | 2007 | 6.4678 | 0.047397 | 22.8580564336757 | 0.316240339279304 | 6.4678 | 0.047397 | 0
09/12/2007 | 2007 | 0.25887 | 0.0076138 | 22.8580564336757 | 0.316240339279304 | 0.25887 | 0.0076138 | 0
12/12/2007 | 2007 | 0.81799 | 0.0022722 | 22.8580564336757 | 0.316240339279304 | 0.81799 | 0.0022722 | 0
13/12/2007 | 2007 | 0.35817 | 0.0037072 | 22.8580564336757 | 0.316240339279304 | 0.35817 | 0.0037072 | 0
18/12/2007 | 2007 | 0.60093 | 0.0026708 | 22.8580564336757 | 0.316240339279304 | 0.60093 | 0.0026708 | 0
19/12/2007 | 2007 | 0.40421 | 0.0033485 | 22.8580564336757 | 0.316240339279304 | 0.40421 | 0.0033485 | 0
20/12/2007 | 2007 | 53.5144 | 0.77087 | 22.8580564336757 | 0.316240339279304 | 22.8581 | 0.31624 | 1 | 30.6564 | 0.45463
21/12/2007 | 2007 | 0.14319 | 0.003787 | 22.8580564336757 | 0.316240339279304 | 0.14319 | 0.003787 | 0
28/12/2007 | 2007 | 0.39819 | 0.0030694 | 22.8580564336757 | 0.316240339279304 | 0.39819 | 0.0030694 | 0
30/12/2007 | 2007 | 1.4197 | 0.0071753 | 22.8580564336757 | 0.316240339279304 | 1.4197 | 0.0071753 | 0
05/01/2008 | 2007 | 4.3428 | 0.042932 | 22.8580564336757 | 0.316240339279304 | 4.3428 | 0.042932 | 0
08/01/2008 | 2007 | 0.69126 | 0.012517 | 22.8580564336757 | 0.316240339279304 | 0.69126 | 0.012517 | 0
10/01/2008 | 2007 | 2.8327 | 0.04353 | 22.8580564336757 | 0.316240339279304 | 2.8327 | 0.04353 | 0
12/01/2008 | 2007 | 0.82349 | 0.0057004 | 22.8580564336757 | 0.316240339279304 | 0.82349 | 0.0057004 | 0
18/01/2008 | 2007 | 0.056605 | 0.00087698 | 22.8580564336757 | 0.316240339279304 | 0.056605 | 0.00087698 | 0
19/01/2008 | 2007 | 0.92912 | 0.011481 | 22.8580564336757 | 0.316240339279304 | 0.92912 | 0.011481 | 0
20/01/2008 | 2007 | 4.8382 | 0.10045 | 22.8580564336757 | 0.316240339279304 | 4.8382 | 0.10045 | 0
22/01/2008 | 2007 | 4.181 | 0.11277 | 22.8580564336757 | 0.316240339279304 | 4.181 | 0.11277 | 0
28/01/2008 | 2007 | 0.19381 | 0.014909 | 22.8580564336757 | 0.316240339279304 | 0.19381 | 0.014909 | 0
29/01/2008 | 2007 | 0.13482 | 0.0030296 | 22.8580564336757 | 0.316240339279304 | 0.13482 | 0.0030296 | 0
31/01/2008 | 2007 | 0.16105 | 0.0027505 | 22.8580564336757 | 0.316240339279304 | 0.16105 | 0.0027505 | 0
01/02/2008 | 2007 | 0.31025 | 0.0017141 | 22.8580564336757 | 0.316240339279304 | 0.31025 | 0.0017141 | 0
06/02/2008 | 2007 | 0.44104 | 0.036754 | 22.8580564336757 | 0.316240339279304 | 0.44104 | 0.036754 | 0
07/02/2008 | 2007 | 1.3257 | 0.0094475 | 22.8580564336757 | 0.316240339279304 | 1.3257 | 0.0094475 | 0
10/02/2008 | 2007 | 0.47979 | 0.0047038 | 22.8580564336757 | 0.316240339279304 | 0.47979 | 0.0047038 | 0
11/02/2008 | 2007 | 0.085386 | 0.0047437 | 22.8580564336757 | 0.316240339279304 | 0.085386 | 0.0047437 | 0
14/02/2008 | 2007 | 0.6278 | 0.011401 | 22.8580564336757 | 0.316240339279304 | 0.6278 | 0.011401 | 0
17/02/2008 | 2007 | 1.2562 | 0.01451 | 22.8580564336757 | 0.316240339279304 | 1.2562 | 0.01451 | 0
19/02/2008 | 2007 | 0.014749 | 0.00019931 | 22.8580564336757 | 0.316240339279304 | 0.014749 | 0.00019931 | 0
21/02/2008 | 2007 | 1.221 | 0.0063781 | 22.8580564336757 | 0.316240339279304 | 1.221 | 0.0063781 | 0
23/02/2008 | 2007 | 1.1952 | 0.018536 | 22.8580564336757 | 0.316240339279304 | 1.1952 | 0.018536 | 0
26/02/2008 | 2007 | 0.36793 | 0.0025911 | 22.8580564336757 | 0.316240339279304 | 0.36793 | 0.0025911 | 0
27/02/2008 | 2007 | 0.2088 | 0.0021526 | 22.8580564336757 | 0.316240339279304 | 0.2088 | 0.0021526 | 0
28/02/2008 | 2007 | 0.021765 | 0.0036275 | 22.8580564336757 | 0.316240339279304 | 0.021765 | 0.0036275 | 0
29/02/2008 | 2007 | 0.83812 | 0.045523 | 22.8580564336757 | 0.316240339279304 | 0.83812 | 0.045523 | 0
02/03/2008 | 2007 | 0.45244 | 0.0038268 | 22.8580564336757 | 0.316240339279304 | 0.45244 | 0.0038268 | 0
03/03/2008 | 2007 | 2.3257 | 0.0073348 | 22.8580564336757 | 0.316240339279304 | 2.3257 | 0.0073348 | 0
04/03/2008 | 2007 | 0.45468 | 0.0050626 | 22.8580564336757 | 0.316240339279304 | 0.45468 | 0.0050626 | 0
05/03/2008 | 2007 | 0.15666 | 0.0027904 | 22.8580564336757 | 0.316240339279304 | 0.15666 | 0.0027904 | 0
07/03/2008 | 2007 | 0.079726 | 0.0015945 | 22.8580564336757 | 0.316240339279304 | 0.079726 | 0.0015945 | 0
11/03/2008 | 2007 | 0.27928 | 0.009009 | 22.8580564336757 | 0.316240339279304 | 0.27928 | 0.009009 | 0
12/03/2008 | 2007 | 0.13872 | 0.002312 | 22.8580564336757 | 0.316240339279304 | 0.13872 | 0.002312 | 0
17/03/2008 | 2007 | 0.43243 | 0.0045045 | 22.8580564336757 | 0.316240339279304 | 0.43243 | 0.0045045 | 0
19/03/2008 | 2007 | 0.0095671 | 0.00039863 | 22.8580564336757 | 0.316240339279304 | 0.0095671 | 0.00039863 | 0
22/03/2008 | 2007 | 0.1278 | 0.0019931 | 22.8580564336757 | 0.316240339279304 | 0.1278 | 0.0019931 | 0
27/03/2008 | 2007 | 0.064777 | 0.00019931 | 22.8580564336757 | 0.316240339279304 | 0.064777 | 0.00019931 | 0
28/03/2008 | 2007 | 0.011839 | 0.0010763 | 22.8580564336757 | 0.316240339279304 | 0.011839 | 0.0010763 | 0
29/03/2008 | 2007 | 0.78829 | 0.006976 | 22.8580564336757 | 0.316240339279304 | 0.78829 | 0.006976 | 0
31/03/2008 | 2007 | 1.3189 | 0.0056605 | 22.8580564336757 | 0.316240339279304 | 1.3189 | 0.0056605 | 0
01/04/2008 | 2008 | 3.476 | 0.055133 | 22.8580564336757 | 0.316240339279304 | 3.476 | 0.055133 | 0
02/04/2008 | 2008 | 0.33468 | 0.0010298 | 22.8580564336757 | 0.316240339279304 | 0.33468 | 0.0010298 | 0
04/04/2008 | 2008 | 0.089591 | 0.0010298 | 22.8580564336757 | 0.316240339279304 | 0.089591 | 0.0010298 | 0
07/04/2008 | 2008 | 0.1656 | 0.0046736 | 22.8580564336757 | 0.316240339279304 | 0.1656 | 0.0046736 | 0
08/04/2008 | 2008 | 1.7182 | 0.020675 | 22.8580564336757 | 0.316240339279304 | 1.7182 | 0.020675 | 0
09/04/2008 | 2008 | 0.38617 | 0.0029705 | 22.8580564336757 | 0.316240339279304 | 0.38617 | 0.0029705 | 0
10/04/2008 | 2008 | 1.8761 | 0.098503 | 22.8580564336757 | 0.316240339279304 | 1.8761 | 0.098503 | 0
12/04/2008 | 2008 | 0.045944 | 0.0011486 | 22.8580564336757 | 0.316240339279304 | 0.045944 | 0.0011486 | 0
15/04/2008 | 2008 | 0.70461 | 0.015803 | 22.8580564336757 | 0.316240339279304 | 0.70461 | 0.015803 | 0
16/04/2008 | 2008 | 1.1472 | 0.0036439 | 22.8580564336757 | 0.316240339279304 | 1.1472 | 0.0036439 | 0
17/04/2008 | 2008 | 4.56 | 0.022378 | 22.8580564336757 | 0.316240339279304 | 4.56 | 0.022378 | 0
18/04/2008 | 2008 | 1.2957 | 0.0093869 | 22.8580564336757 | 0.316240339279304 | 1.2957 | 0.0093869 | 0
19/04/2008 | 2008 | 0.080006 | 0.0080006 | 22.8580564336757 | 0.316240339279304 | 0.080006 | 0.0080006 | 0
21/04/2008 | 2008 | 0.050539 | 0.0081591 | 22.8580564336757 | 0.316240339279304 | 0.050539 | 0.0081591 | 0
22/04/2008 | 2008 | 0.077313 | 0.00063371 | 22.8580564336757 | 0.316240339279304 | 0.077313 | 0.00063371 | 0
23/04/2008 | 2008 | 0.10052 | 0.00035646 | 22.8580564336757 | 0.316240339279304 | 0.10052 | 0.00035646 | 0
25/04/2008 | 2008 | 0.11375 | 0.02519 | 22.8580564336757 | 0.316240339279304 | 0.11375 | 0.02519 | 0
26/04/2008 | 2008 | 0.78802 | 0.098503 | 22.8580564336757 | 0.316240339279304 | 0.78802 | 0.098503 | 0
28/04/2008 | 2008 | 0.15756 | 0.0030894 | 22.8580564336757 | 0.316240339279304 | 0.15756 | 0.0030894 | 0
29/04/2008 | 2008 | 0.6513 | 0.0091096 | 22.8580564336757 | 0.316240339279304 | 0.6513 | 0.0091096 | 0
30/04/2008 | 2008 | 0.62389 | 0.0038419 | 22.8580564336757 | 0.316240339279304 | 0.62389 | 0.0038419 | 0
01/05/2008 | 2008 | 14.9211 | 0.020477 | 22.8580564336757 | 0.316240339279304 | 14.9211 | 0.020477 | 0
05/05/2008 | 2008 | 0.84625 | 0.0047529 | 22.8580564336757 | 0.316240339279304 | 0.84625 | 0.0047529 | 0
07/05/2008 | 2008 | 0.089829 | 0.0024952 | 22.8580564336757 | 0.316240339279304 | 0.089829 | 0.0024952 | 0
08/05/2008 | 2008 | 0.8931 | 0.011644 | 22.8580564336757 | 0.316240339279304 | 0.8931 | 0.011644 | 0
11/05/2008 | 2008 | 2.955 | 0.01715 | 22.8580564336757 | 0.316240339279304 | 2.955 | 0.01715 | 0
12/05/2008 | 2008 | 0.21824 | 0.0047132 | 22.8580564336757 | 0.316240339279304 | 0.21824 | 0.0047132 | 0
14/05/2008 | 2008 | 1.3182 | 0.028002 | 22.8580564336757 | 0.316240339279304 | 1.3182 | 0.028002 | 0
16/05/2008 | 2008 | 0.22386 | 0.0038023 | 22.8580564336757 | 0.316240339279304 | 0.22386 | 0.0038023 | 0
20/05/2008 | 2008 | 0.26085 | 0.0014655 | 22.8580564336757 | 0.316240339279304 | 0.26085 | 0.0014655 | 0
23/05/2008 | 2008 | 0.13015 | 0.00063371 | 22.8580564336757 | 0.316240339279304 | 0.13015 | 0.00063371 | 0
25/05/2008 | 2008 | 1.1365 | 0.0086343 | 22.8580564336757 | 0.316240339279304 | 1.1365 | 0.0086343 | 0
26/05/2008 | 2008 | 0.86391 | 0.0094265 | 22.8580564336757 | 0.316240339279304 | 0.86391 | 0.0094265 | 0
27/05/2008 | 2008 | 3.2137 | 0.051331 | 22.8580564336757 | 0.316240339279304 | 3.2137 | 0.051331 | 0
29/05/2008 | 2008 | 1.7781 | 0.072481 | 22.8580564336757 | 0.316240339279304 | 1.7781 | 0.072481 | 0
30/05/2008 | 2008 | 1.2134 | 0.037072 | 22.8580564336757 | 0.316240339279304 | 1.2134 | 0.037072 | 0
31/05/2008 | 2008 | 1.221 | 0.015803 | 22.8580564336757 | 0.316240339279304 | 1.221 | 0.015803 | 0
01/06/2008 | 2008 | 1.2797 | 0.029072 | 22.8580564336757 | 0.316240339279304 | 1.2797 | 0.029072 | 0
03/06/2008 | 2008 | 0.34541 | 0.016912 | 22.8580564336757 | 0.316240339279304 | 0.34541 | 0.016912 | 0
04/06/2008 | 2008 | 0.31274 | 0.0018615 | 22.8580564336757 | 0.316240339279304 | 0.31274 | 0.0018615 | 0
06/06/2008 | 2008 | 0.54064 | 0.0030894 | 22.8580564336757 | 0.316240339279304 | 0.54064 | 0.0030894 | 0
07/06/2008 | 2008 | 5.1052 | 0.090859 | 22.8580564336757 | 0.316240339279304 | 5.1052 | 0.090859 | 0
08/06/2008 | 2008 | 1.3923 | 0.050024 | 22.8580564336757 | 0.316240339279304 | 1.3923 | 0.050024 | 0
12/06/2008 | 2008 | 0.13823 | 0.0021784 | 22.8580564336757 | 0.316240339279304 | 0.13823 | 0.0021784 | 0
13/06/2008 | 2008 | 1.4951 | 0.014971 | 22.8580564336757 | 0.316240339279304 | 1.4951 | 0.014971 | 0
15/06/2008 | 2008 | 0.040399 | 0.0023764 | 22.8580564336757 | 0.316240339279304 | 0.040399 | 0.0023764 | 0
16/06/2008 | 2008 | 1.7258 | 0.011407 | 22.8580564336757 | 0.316240339279304 | 1.7258 | 0.011407 | 0
17/06/2008 | 2008 | 1.0688 | 0.01208 | 22.8580564336757 | 0.316240339279304 | 1.0688 | 0.01208 | 0
19/06/2008 | 2008 | 0.92324 | 0.0024952 | 22.8580564336757 | 0.316240339279304 | 0.92324 | 0.0024952 | 0
23/06/2008 | 2008 | 0.01608 | 0.00027725 | 22.8580564336757 | 0.316240339279304 | 0.01608 | 0.00027725 | 0
24/06/2008 | 2008 | 0.51454 | 0.010021 | 22.8580564336757 | 0.316240339279304 | 0.51454 | 0.010021 | 0
26/06/2008 | 2008 | 0.52757 | 0.0087928 | 22.8580564336757 | 0.316240339279304 | 0.52757 | 0.0087928 | 0
27/06/2008 | 2008 | 3.1266 | 0.027448 | 22.8580564336757 | 0.316240339279304 | 3.1266 | 0.027448 | 0
29/06/2008 | 2008 | 1.7419 | 0.016001 | 22.8580564336757 | 0.316240339279304 | 1.7419 | 0.016001 | 0
01/07/2008 | 2008 | 0.063965 | 0.00019804 | 22.8580564336757 | 0.316240339279304 | 0.063965 | 0.00019804 | 0
03/07/2008 | 2008 | 0.10777 | 0.0021784 | 22.8580564336757 | 0.316240339279304 | 0.10777 | 0.0021784 | 0
04/07/2008 | 2008 | 0.98348 | 0.010337 | 22.8580564336757 | 0.316240339279304 | 0.98348 | 0.010337 | 0
06/07/2008 | 2008 | 4.9872 | 0.082343 | 22.8580564336757 | 0.316240339279304 | 4.9872 | 0.082343 | 0
07/07/2008 | 2008 | 1.4806 | 0.038696 | 22.8580564336757 | 0.316240339279304 | 1.4806 | 0.038696 | 0
08/07/2008 | 2008 | 0.23289 | 0.001109 | 22.8580564336757 | 0.316240339279304 | 0.23289 | 0.001109 | 0
09/07/2008 | 2008 | 0.12785 | 0.0014259 | 22.8580564336757 | 0.316240339279304 | 0.12785 | 0.0014259 | 0
10/07/2008 | 2008 | 0.47948 | 0.0016635 | 22.8580564336757 | 0.316240339279304 | 0.47948 | 0.0016635 | 0
14/07/2008 | 2008 | 0.082898 | 0.0010694 | 22.8580564336757 | 0.316240339279304 | 0.082898 | 0.0010694 | 0
15/07/2008 | 2008 | 1.57 | 0.010932 | 22.8580564336757 | 0.316240339279304 | 1.57 | 0.010932 | 0
16/07/2008 | 2008 | 0.40534 | 0.0040399 | 22.8580564336757 | 0.316240339279304 | 0.40534 | 0.0040399 | 0
17/07/2008 | 2008 | 0.19237 | 0.0015051 | 22.8580564336757 | 0.316240339279304 | 0.19237 | 0.0015051 | 0
18/07/2008 | 2008 | 0.26382 | 0.01109 | 22.8580564336757 | 0.316240339279304 | 0.26382 | 0.01109 | 0
19/07/2008 | 2008 | 0.50091 | 0.0036439 | 22.8580564336757 | 0.316240339279304 | 0.50091 | 0.0036439 | 0
21/07/2008 | 2008 | 0.9173 | 0.0047529 | 22.8580564336757 | 0.316240339279304 | 0.9173 | 0.0047529 | 0
24/07/2008 | 2008 | 0.49251 | 0.0059411 | 22.8580564336757 | 0.316240339279304 | 0.49251 | 0.0059411 | 0
27/07/2008 | 2008 | 0.51901 | 0.014575 | 22.8580564336757 | 0.316240339279304 | 0.51901 | 0.014575 | 0
29/07/2008 | 2008 | 0.036042 | 0.00039607 | 22.8580564336757 | 0.316240339279304 | 0.036042 | 0.00039607 | 0
30/07/2008 | 2008 | 12.864 | 0.18298 | 22.8580564336757 | 0.316240339279304 | 12.864 | 0.18298 | 0
31/07/2008 | 2008 | 5.1559 | 0.040201 | 22.8580564336757 | 0.316240339279304 | 5.1559 | 0.040201 | 0
01/08/2008 | 2008 | 0.23768 | 0.0020596 | 22.8580564336757 | 0.316240339279304 | 0.23768 | 0.0020596 | 0
02/08/2008 | 2008 | 0.54412 | 0.0066936 | 22.8580564336757 | 0.316240339279304 | 0.54412 | 0.0066936 | 0
03/08/2008 | 2008 | 0.47604 | 0.0097037 | 22.8580564336757 | 0.316240339279304 | 0.47604 | 0.0097037 | 0
04/08/2008 | 2008 | 0.53763 | 0.0056242 | 22.8580564336757 | 0.316240339279304 | 0.53763 | 0.0056242 | 0
05/08/2008 | 2008 | 0.75071 | 0.004634 | 22.8580564336757 | 0.316240339279304 | 0.75071 | 0.004634 | 0
06/08/2008 | 2008 | 0.3169 | 0.0070897 | 22.8580564336757 | 0.316240339279304 | 0.3169 | 0.0070897 | 0
07/08/2008 | 2008 | 2.287 | 0.078779 | 22.8580564336757 | 0.316240339279304 | 2.287 | 0.078779 | 0
08/08/2008 | 2008 | 1.3413 | 0.066857 | 22.8580564336757 | 0.316240339279304 | 1.3413 | 0.066857 | 0
09/08/2008 | 2008 | 2.1165 | 0.034775 | 22.8580564336757 | 0.316240339279304 | 2.1165 | 0.034775 | 0
10/08/2008 | 2008 | 0.77729 | 0.01109 | 22.8580564336757 | 0.316240339279304 | 0.77729 | 0.01109 | 0
12/08/2008 | 2008 | 0.13399 | 0.00067332 | 22.8580564336757 | 0.316240339279304 | 0.13399 | 0.00067332 | 0
13/08/2008 | 2008 | 0.084284 | 0.00015843 | 22.8580564336757 | 0.316240339279304 | 0.084284 | 0.00015843 | 0
14/08/2008 | 2008 | 1.491 | 0.016873 | 22.8580564336757 | 0.316240339279304 | 1.491 | 0.016873 | 0
15/08/2008 | 2008 | 2.5385 | 0.020081 | 22.8580564336757 | 0.316240339279304 | 2.5385 | 0.020081 | 0
18/08/2008 | 2008 | 2.0972 | 0.016279 | 22.8580564336757 | 0.316240339279304 | 2.0972 | 0.016279 | 0
19/08/2008 | 2008 | 0.028517 | 0.00071293 | 22.8580564336757 | 0.316240339279304 | 0.028517 | 0.00071293 | 0
20/08/2008 | 2008 | 0.302 | 0.0022576 | 22.8580564336757 | 0.316240339279304 | 0.302 | 0.0022576 | 0
26/08/2008 | 2008 | 0.61062 | 0.0010694 | 22.8580564336757 | 0.316240339279304 | 0.61062 | 0.0010694 | 0
27/08/2008 | 2008 | 0.92403 | 0.0066936 | 22.8580564336757 | 0.316240339279304 | 0.92403 | 0.0066936 | 0
03/09/2008 | 2008 | 0.023527 | 0.0026141 | 22.8580564336757 | 0.316240339279304 | 0.023527 | 0.0026141 | 0
04/09/2008 | 2008 | 0.22374 | 0.00083175 | 22.8580564336757 | 0.316240339279304 | 0.22374 | 0.00083175 | 0
05/09/2008 | 2008 | 3.7174 | 0.067134 | 22.8580564336757 | 0.316240339279304 | 3.7174 | 0.067134 | 0
09/09/2008 | 2008 | 0.14476 | 0.00067332 | 22.8580564336757 | 0.316240339279304 | 0.14476 | 0.00067332 | 0
10/09/2008 | 2008 | 0.22101 | 0.0012278 | 22.8580564336757 | 0.316240339279304 | 0.22101 | 0.0012278 | 0
11/09/2008 | 2008 | 1.9259 | 0.012199 | 22.8580564336757 | 0.316240339279304 | 1.9259 | 0.012199 | 0
12/09/2008 | 2008 | 1.1648 | 0.029705 | 22.8580564336757 | 0.316240339279304 | 1.1648 | 0.029705 | 0
15/09/2008 | 2008 | 0.047529 | 0.00015843 | 22.8580564336757 | 0.316240339279304 | 0.047529 | 0.00015843 | 0
16/09/2008 | 2008 | 0.059252 | 0.00063371 | 22.8580564336757 | 0.316240339279304 | 0.059252 | 0.00063371 | 0
22/09/2008 | 2008 | 0.14971 | 0.0005545 | 22.8580564336757 | 0.316240339279304 | 0.14971 | 0.0005545 | 0
23/09/2008 | 2008 | 0.035646 | 0.0011882 | 22.8580564336757 | 0.316240339279304 | 0.035646 | 0.0011882 | 0
24/09/2008 | 2008 | 0.24358 | 0.0034062 | 22.8580564336757 | 0.316240339279304 | 0.24358 | 0.0034062 | 0
25/09/2008 | 2008 | 0.82403 | 0.0028913 | 22.8580564336757 | 0.316240339279304 | 0.82403 | 0.0028913 | 0
29/09/2008 | 2008 | 0.46736 | 0.0036439 | 22.8580564336757 | 0.316240339279304 | 0.46736 | 0.0036439 | 0
30/09/2008 | 2008 | 0.29385 | 0.0017823 | 22.8580564336757 | 0.316240339279304 | 0.29385 | 0.0017823 | 0
02/10/2008 | 2008 | 1.4842 | 0.0057826 | 22.8580564336757 | 0.316240339279304 | 1.4842 | 0.0057826 | 0
03/10/2008 | 2008 | 0.17324 | 0.0024952 | 22.8580564336757 | 0.316240339279304 | 0.17324 | 0.0024952 | 0
04/10/2008 | 2008 | 0.98138 | 0.029032 | 22.8580564336757 | 0.316240339279304 | 0.98138 | 0.029032 | 0
07/10/2008 | 2008 | 22.8436 | 0.10991 | 22.8580564336757 | 0.316240339279304 | 22.8436 | 0.10991 | 0
08/10/2008 | 2008 | 2.1377 | 0.020833 | 22.8580564336757 | 0.316240339279304 | 2.1377 | 0.020833 | 0
09/10/2008 | 2008 | 1.3428 | 0.0048717 | 22.8580564336757 | 0.316240339279304 | 1.3428 | 0.0048717 | 0
10/10/2008 | 2008 | 0.039884 | 0.0020992 | 22.8580564336757 | 0.316240339279304 | 0.039884 | 0.0020992 | 0
13/10/2008 | 2008 | 2.4665 | 0.025428 | 22.8580564336757 | 0.316240339279304 | 2.4665 | 0.025428 | 0
14/10/2008 | 2008 | 0.13862 | 0.00079214 | 22.8580564336757 | 0.316240339279304 | 0.13862 | 0.00079214 | 0
15/10/2008 | 2008 | 0.78933 | 0.0041587 | 22.8580564336757 | 0.316240339279304 | 0.78933 | 0.0041587 | 0
16/10/2008 | 2008 | 0.92467 | 0.05137 | 22.8580564336757 | 0.316240339279304 | 0.92467 | 0.05137 | 0
17/10/2008 | 2008 | 0.50206 | 0.0045548 | 22.8580564336757 | 0.316240339279304 | 0.50206 | 0.0045548 | 0
21/10/2008 | 2008 | 0.054895 | 0.0024952 | 22.8580564336757 | 0.316240339279304 | 0.054895 | 0.0024952 | 0
22/10/2008 | 2008 | 0.22291 | 0.0029309 | 22.8580564336757 | 0.316240339279304 | 0.22291 | 0.0029309 | 0
23/10/2008 | 2008 | 0.023764 | 0.00019804 | 22.8580564336757 | 0.316240339279304 | 0.023764 | 0.00019804 | 0
24/10/2008 | 2008 | 0.20897 | 0.0027329 | 22.8580564336757 | 0.316240339279304 | 0.20897 | 0.0027329 | 0
28/10/2008 | 2008 | 1.3074 | 0.0048321 | 22.8580564336757 | 0.316240339279304 | 1.3074 | 0.0048321 | 0
29/10/2008 | 2008 | 0.089116 | 0.0033666 | 22.8580564336757 | 0.316240339279304 | 0.089116 | 0.0033666 | 0
31/10/2008 | 2008 | 0.063688 | 0.00023764 | 22.8580564336757 | 0.316240339279304 | 0.063688 | 0.00023764 | 0
01/11/2008 | 2008 | 1.585 | 0.020675 | 22.8580564336757 | 0.316240339279304 | 1.585 | 0.020675 | 0
03/11/2008 | 2008 | 0.57462 | 0.032161 | 22.8580564336757 | 0.316240339279304 | 0.57462 | 0.032161 | 0
05/11/2008 | 2008 | 0.026854 | 0.0030101 | 22.8580564336757 | 0.316240339279304 | 0.026854 | 0.0030101 | 0
06/11/2008 | 2008 | 0.32656 | 0.035646 | 22.8580564336757 | 0.316240339279304 | 0.32656 | 0.035646 | 0
07/11/2008 | 2008 | 0.33832 | 0.029072 | 22.8580564336757 | 0.316240339279304 | 0.33832 | 0.029072 | 0
09/11/2008 | 2008 | 6.9598 | 0.032993 | 22.8580564336757 | 0.316240339279304 | 6.9598 | 0.032993 | 0
10/11/2008 | 2008 | 0.1366 | 0.0019804 | 22.8580564336757 | 0.316240339279304 | 0.1366 | 0.0019804 | 0
12/11/2008 | 2008 | 1.9422 | 0.0074065 | 22.8580564336757 | 0.316240339279304 | 1.9422 | 0.0074065 | 0
13/11/2008 | 2008 | 0.032438 | 0.00083175 | 22.8580564336757 | 0.316240339279304 | 0.032438 | 0.00083175 | 0
17/11/2008 | 2008 | 0.052638 | 0.00083175 | 22.8580564336757 | 0.316240339279304 | 0.052638 | 0.00083175 | 0
18/11/2008 | 2008 | 0.43489 | 0.0080798 | 22.8580564336757 | 0.316240339279304 | 0.43489 | 0.0080798 | 0
19/11/2008 | 2008 | 1.124 | 0.0051093 | 22.8580564336757 | 0.316240339279304 | 1.124 | 0.0051093 | 0
20/11/2008 | 2008 | 0.037231 | 0.00019804 | 22.8580564336757 | 0.316240339279304 | 0.037231 | 0.00019804 | 0
21/11/2008 | 2008 | 0.38926 | 0.0015447 | 22.8580564336757 | 0.316240339279304 | 0.38926 | 0.0015447 | 0
22/11/2008 | 2008 | 0.076046 | 0.00031686 | 22.8580564336757 | 0.316240339279304 | 0.076046 | 0.00031686 | 0
24/11/2008 | 2008 | 0.26913 | 0.0068124 | 22.8580564336757 | 0.316240339279304 | 0.26913 | 0.0068124 | 0
25/11/2008 | 2008 | 0.44697 | 0.010535 | 22.8580564336757 | 0.316240339279304 | 0.44697 | 0.010535 | 0
27/11/2008 | 2008 | 1.5588 | 0.016041 | 22.8580564336757 | 0.316240339279304 | 1.5588 | 0.016041 | 0
01/12/2008 | 2008 | 0.035646 | 0.00011882 | 22.8580564336757 | 0.316240339279304 | 0.035646 | 0.00011882 | 0
03/12/2008 | 2008 | 3.0499 | 0.018655 | 22.8580564336757 | 0.316240339279304 | 3.0499 | 0.018655 | 0
05/12/2008 | 2008 | 0.5425 | 0.008674 | 22.8580564336757 | 0.316240339279304 | 0.5425 | 0.008674 | 0
06/12/2008 | 2008 | 2.365 | 0.099493 | 22.8580564336757 | 0.316240339279304 | 2.365 | 0.099493 | 0
08/12/2008 | 2008 | 3.9564 | 0.019051 | 22.8580564336757 | 0.316240339279304 | 3.9564 | 0.019051 | 0
09/12/2008 | 2008 | 0.4924 | 0.0015843 | 22.8580564336757 | 0.316240339279304 | 0.4924 | 0.0015843 | 0
10/12/2008 | 2008 | 0.25452 | 0.0010694 | 22.8580564336757 | 0.316240339279304 | 0.25452 | 0.0010694 | 0
11/12/2008 | 2008 | 0.053747 | 0.00091096 | 22.8580564336757 | 0.316240339279304 | 0.053747 | 0.00091096 | 0
15/12/2008 | 2008 | 0.02218 | 0.00079214 | 22.8580564336757 | 0.316240339279304 | 0.02218 | 0.00079214 | 0
16/12/2008 | 2008 | 0.71665 | 0.014219 | 22.8580564336757 | 0.316240339279304 | 0.71665 | 0.014219 | 0
19/12/2008 | 2008 | 0.36439 | 0.0018219 | 22.8580564336757 | 0.316240339279304 | 0.36439 | 0.0018219 | 0
20/12/2008 | 2008 | 0.16698 | 0.0013466 | 22.8580564336757 | 0.316240339279304 | 0.16698 | 0.0013466 | 0
22/12/2008 | 2008 | 0.054816 | 0.006852 | 22.8580564336757 | 0.316240339279304 | 0.054816 | 0.006852 | 0
25/12/2008 | 2008 | 1.2822 | 0.025903 | 22.8580564336757 | 0.316240339279304 | 1.2822 | 0.025903 | 0
30/12/2008 | 2008 | 1.1728 | 0.046538 | 22.8580564336757 | 0.316240339279304 | 1.1728 | 0.046538 | 0
02/01/2009 | 2008 | 0.65126 | 0.0081987 | 22.8580564336757 | 0.316240339279304 | 0.65126 | 0.0081987 | 0
05/01/2009 | 2008 | 0.88969 | 0.0067728 | 22.8580564336757 | 0.316240339279304 | 0.88969 | 0.0067728 | 0
06/01/2009 | 2008 | 0.067094 | 0.00043568 | 22.8580564336757 | 0.316240339279304 | 0.067094 | 0.00043568 | 0
07/01/2009 | 2008 | 0.18691 | 0.001307 | 22.8580564336757 | 0.316240339279304 | 0.18691 | 0.001307 | 0
08/01/2009 | 2008 | 1.0394 | 0.015764 | 22.8580564336757 | 0.316240339279304 | 1.0394 | 0.015764 | 0
11/01/2009 | 2008 | 1.2449 | 0.0060203 | 22.8580564336757 | 0.316240339279304 | 1.2449 | 0.0060203 | 0
12/01/2009 | 2008 | 0.027804 | 0.00035646 | 22.8580564336757 | 0.316240339279304 | 0.027804 | 0.00035646 | 0
17/01/2009 | 2008 | 1.9647 | 0.042974 | 22.8580564336757 | 0.316240339279304 | 1.9647 | 0.042974 | 0
23/01/2009 | 2008 | 0.051014 | 0.00043568 | 22.8580564336757 | 0.316240339279304 | 0.051014 | 0.00043568 | 0
27/01/2009 | 2008 | 0.43512 | 0.0021388 | 22.8580564336757 | 0.316240339279304 | 0.43512 | 0.0021388 | 0
28/01/2009 | 2008 | 0.096958 | 0.00023764 | 22.8580564336757 | 0.316240339279304 | 0.096958 | 0.00023764 | 0
01/02/2009 | 2008 | 0.68556 | 0.025626 | 22.8580564336757 | 0.316240339279304 | 0.68556 | 0.025626 | 0
02/02/2009 | 2008 | 0.99747 | 0.0061787 | 22.8580564336757 | 0.316240339279304 | 0.99747 | 0.0061787 | 0
03/02/2009 | 2008 | 0.25507 | 0.00091096 | 22.8580564336757 | 0.316240339279304 | 0.25507 | 0.00091096 | 0
04/02/2009 | 2008 | 0.076679 | 0.0012674 | 22.8580564336757 | 0.316240339279304 | 0.076679 | 0.0012674 | 0
05/02/2009 | 2008 | 4.2107 | 0.17922 | 22.8580564336757 | 0.316240339279304 | 4.2107 | 0.17922 | 0
08/02/2009 | 2008 | 0.17395 | 0.00079214 | 22.8580564336757 | 0.316240339279304 | 0.17395 | 0.00079214 | 0
09/02/2009 | 2008 | 0.21827 | 0.0068124 | 22.8580564336757 | 0.316240339279304 | 0.21827 | 0.0068124 | 0
10/02/2009 | 2008 | 0.80066 | 0.012318 | 22.8580564336757 | 0.316240339279304 | 0.80066 | 0.012318 | 0
11/02/2009 | 2008 | 0.29087 | 0.0015051 | 22.8580564336757 | 0.316240339279304 | 0.29087 | 0.0015051 | 0
12/02/2009 | 2008 | 0.73281 | 0.012753 | 22.8580564336757 | 0.316240339279304 | 0.73281 | 0.012753 | 0
13/02/2009 | 2008 | 2.8061 | 0.034933 | 22.8580564336757 | 0.316240339279304 | 2.8061 | 0.034933 | 0
14/02/2009 | 2008 | 0.20699 | 0.0061787 | 22.8580564336757 | 0.316240339279304 | 0.20699 | 0.0061787 | 0
16/02/2009 | 2008 | 2.4973 | 0.0062975 | 22.8580564336757 | 0.316240339279304 | 2.4973 | 0.0062975 | 0
17/02/2009 | 2008 | 0.58856 | 0.00039607 | 22.8580564336757 | 0.316240339279304 | 0.58856 | 0.00039607 | 0
18/02/2009 | 2008 | 0.16928 | 0.00075253 | 22.8580564336757 | 0.316240339279304 | 0.16928 | 0.00075253 | 0
19/02/2009 | 2008 | 0.22568 | 0.0014655 | 22.8580564336757 | 0.316240339279304 | 0.22568 | 0.0014655 | 0
23/02/2009 | 2008 | 0.75416 | 0.0032082 | 22.8580564336757 | 0.316240339279304 | 0.75416 | 0.0032082 | 0
24/02/2009 | 2008 | 0.19752 | 0.0012674 | 22.8580564336757 | 0.316240339279304 | 0.19752 | 0.0012674 | 0
25/02/2009 | 2008 | 0.83575 | 0.0072085 | 22.8580564336757 | 0.316240339279304 | 0.83575 | 0.0072085 | 0
28/02/2009 | 2008 | 0.16259 | 0.002218 | 22.8580564336757 | 0.316240339279304 | 0.16259 | 0.002218 | 0
01/03/2009 | 2008 | 0.16267 | 0.0036439 | 22.8580564336757 | 0.316240339279304 | 0.16267 | 0.0036439 | 0
02/03/2009 | 2008 | 2.8513 | 0.068045 | 22.8580564336757 | 0.316240339279304 | 2.8513 | 0.068045 | 0
03/03/2009 | 2008 | 0.72707 | 0.0074857 | 22.8580564336757 | 0.316240339279304 | 0.72707 | 0.0074857 | 0
04/03/2009 | 2008 | 0.23499 | 0.00083175 | 22.8580564336757 | 0.316240339279304 | 0.23499 | 0.00083175 | 0
05/03/2009 | 2008 | 1.4652 | 0.01818 | 22.8580564336757 | 0.316240339279304 | 1.4652 | 0.01818 | 0
06/03/2009 | 2008 | 0.68615 | 0.0052677 | 22.8580564336757 | 0.316240339279304 | 0.68615 | 0.0052677 | 0
07/03/2009 | 2008 | 0.047925 | 0.00043568 | 22.8580564336757 | 0.316240339279304 | 0.047925 | 0.00043568 | 0
09/03/2009 | 2008 | 2.456 | 0.0066936 | 22.8580564336757 | 0.316240339279304 | 2.456 | 0.0066936 | 0
10/03/2009 | 2008 | 0.48344 | 0.0032478 | 22.8580564336757 | 0.316240339279304 | 0.48344 | 0.0032478 | 0
11/03/2009 | 2008 | 1.3673 | 0.020516 | 22.8580564336757 | 0.316240339279304 | 1.3673 | 0.020516 | 0
16/03/2009 | 2008 | 0.42918 | 0.0024952 | 22.8580564336757 | 0.316240339279304 | 0.42918 | 0.0024952 | 0
17/03/2009 | 2008 | 2.6111 | 0.021269 | 22.8580564336757 | 0.316240339279304 | 2.6111 | 0.021269 | 0
18/03/2009 | 2008 | 1.6231 | 0.0042776 | 22.8580564336757 | 0.316240339279304 | 1.6231 | 0.0042776 | 0
19/03/2009 | 2008 | 1.8188 | 0.040478 | 22.8580564336757 | 0.316240339279304 | 1.8188 | 0.040478 | 0
20/03/2009 | 2008 | 0.099335 | 0.0030101 | 22.8580564336757 | 0.316240339279304 | 0.099335 | 0.0030101 | 0
22/03/2009 | 2008 | 0.97307 | 0.0032874 | 22.8580564336757 | 0.316240339279304 | 0.97307 | 0.0032874 | 0
24/03/2009 | 2008 | 0.8645 | 0.0062975 | 22.8580564336757 | 0.316240339279304 | 0.8645 | 0.0062975 | 0
25/03/2009 | 2008 | 0.75143 | 0.0053074 | 22.8580564336757 | 0.316240339279304 | 0.75143 | 0.0053074 | 0
26/03/2009 | 2008 | 0.071926 | 0.00031686 | 22.8580564336757 | 0.316240339279304 | 0.071926 | 0.00031686 | 0
28/03/2009 | 2008 | 0.067292 | 0.0038419 | 22.8580564336757 | 0.316240339279304 | 0.067292 | 0.0038419 | 0
30/03/2009 | 2008 | 0.411 | 0.0039607 | 22.8580564336757 | 0.316240339279304 | 0.411 | 0.0039607 | 0
31/03/2009 | 2008 | 4.0895 | 0.20556 | 22.8580564336757 | 0.316240339279304 | 4.0895 | 0.20556 | 0

## 1e-5 Year Limits
SumOfFixedSaidi | SumOfFixedSaifi | uFixedSaididiv5 | StDevOfFixedSaidi | stdevsigsaidixroot365i | SaidiLimit | ufixedsaifidiv5 | stdevsigsaifixroot365i | SaifiLimit
1251.4658 | 17.4728 | 250.2932 | 2.7263 | 52.0861 | 302.3793 | 3.4946 | 0.76226 | 4.2568

## 20132014CustomnerNumbers
id | Year | Financial year | GisAVG | WraAVG | TotAVG | Gis Start | Wra Start | Total Start | Gis End | Wra End | Total End
220 | 2013 | 2013/2014 | 25660 | 4792 | 25452 | 20740 | 4810 | 25550 | 20579 | 4774 | 25353

## 20132014Data
REPORT NUMBER | Date Outage | YEAR | DATE ON | Duration of Outage | Customers Impacted | Total Customer Minutes Lost | CLASS A-G | DESCRIPTION | CAUSE
14756 | 02/04/2013 | 2013 | 2013-04-02 | 27 | 67 | 1809 | C | FOREIGN INTERFERENCE | Replace 11kV pole E1879 Bck Ormond Rd Hit by Car
14776 | 03/04/2013 | 2013 | 2013-04-03 | 110 | 25 | 2750 | B | PLANNED SHUTDOWN | Isolate 11kV lines for Tree cutting D3036 to D3039 Kaimoe Rd
14758 | 04/04/2013 | 2013 | 2013-04-04 | 23 | 498 | 11454 | C | UNKNOWN | Reclose CB A472 Whangara at Kaiti sub cause unknown
14777 | 04/04/2013 | 2013 | 2013-04-04 | 343 | 46 | 5449 | B | PLANNED SHUTDOWN | Replace 11kV poles E200 E640 E642 E1055 E1056 E1057 Kanakanaia Rd
14759 | 05/04/2013 | 2013 | 2013-04-05 | 36 | 44 | 1584 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J575 Tikitiki
14779 | 05/04/2013 | 2013 | 2013-04-05 | 71 | 21 | 1491 | B | PLANNED SHUTDOWN | Isolate 11kV lines & install DDO fuses pole C1354 Wharekopae Rd
14760 | 06/04/2013 | 2013 | 2013-04-06 | 82 | 227 | 18020 | C | FOREIGN INTERFERENCE | Remove bird from pole C2138 W/O Hika
14761 | 06/04/2013 | 2013 | 2013-04-06 | 23 | 81 | 1863 | C | DEFECTIVE EQUIPMENT | Replace 2 strain insulators pole B1792 Awapuni Rd
14762 | 06/04/2013 | 2013 | 2013-04-06 | 267 | 52 | 7057 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole D546 Tahunga
14763 | 07/04/2013 | 2013 | 2013-04-07 | 410 | 208 | 21594 | C | FOREIGN INTERFERENCE | Replace 11kV pole G1309 Tauwhareparae Rd
14778 | 08/04/2013 | 2013 | 2013-04-08 | 8 | 27 | 216 | B | PLANNED SHUTDOWN | Remove DDO fuses C3803 & connect cables D O L Chalmers Rd
14786 | 08/04/2013 | 2013 | 2013-04-08 | 362 | 10 | 3620 | B | PLANNED SHUTDOWN | Isolate lines for Contractor Pole C1354 Wharekopae Rd
14782 | 09/04/2013 | 2013 | 2013-04-09 | 1 | 1452 | 1452 | B | PLANNED SHUTDOWN | Isolate lines A8 to allow change over from Generators East Coast
14783 | 09/04/2013 | 2013 | 2013-04-09 | 375 | 48 | 5373 | B | PLANNED SHUTDOWN | Replace 11kV poles E1063 E1057 E126 E1055 Kanakanaia
14780 | 10/04/2013 | 2013 | 2013-04-10 | 197 | 12 | 1293 | B | PLANNED SHUTDOWN | Install DDO fuses pole E22 Waimata Valley
14781 | 10/04/2013 | 2013 | 2013-04-10 | 438 | 34 | 14982 | B | PLANNED SHUTDOWN | Replace 11kV ploes D5084 D5048 D5099 Wharekopae Rd
14764 | 11/04/2013 | 2013 | 2013-04-11 | 179 | 480 | 31024 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole A4231 Riverside Rd
14766 | 12/04/2013 | 2013 | 2013-04-12 | 95 | 42 | 3990 | C | TREE CONTACTS | Repair 11kV lines btween poles A4204 to A90 Riverside Rd
14784 | 12/04/2013 | 2013 | 2013-04-12 | 332 | 48 | 5772 | B | PLANNED SHUTDOWN | Replace 11kV poles E637 E640 E646 E648 E650 Kanakanaia Rd
14765 | 13/04/2013 | 2013 | 2013-04-13 | 430 | 16 | 2768 | C | FOREIGN INTERFERENCE | Replace 11kV pole G346 Wharf Rd Tolaga Bay
14767 | 15/04/2013 | 2013 | 2013-04-15 | 200 | 861 | 25390 | C | TREE CONTACTS | Repair 11kV lines pole W9135 Kaiwaitau Rd
14785 | 17/04/2013 | 2013 | 2013-04-17 | 304 | 25 | 7780 | B | PLANNED SHUTDOWN | Replace 11kV poles G2158 G2159 Paroa Rd
14768 | 18/04/2013 | 2013 | 2013-04-18 | 1491 | 102 | 60215 | C | FOREIGN INTERFERENCE | Remove bird from T/x J395 Waikura Valley
14770 | 19/04/2013 | 2013 | 2013-04-19 | 15 | 53 | 795 | C | TREE CONTACTS | Remove trees from 11kV pole E1508 Matawai Rd
14787 | 19/04/2013 | 2013 | 2013-04-19 | 437 | 104 | 18782 | B | PLANNED SHUTDOWN | Isolate 11kV lines pole C3212 Bck Ormond Rd for Contractor
14771 | 22/04/2013 | 2013 | 2013-04-22 | 579 | 11 | 3002 | C | FOREIGN INTERFERENCE | Replace 11kV pole C1377 Wharekopae Rd Hit by car
14772 | 24/04/2013 | 2013 | 2013-04-24 | 357 | 102 | 21510 | C | DEFECTIVE EQUIPMENT | Replace faulty insulator pole J4291 Waikura Valley
14788 | 24/04/2013 | 2013 | 2013-04-24 | 308 | 6 | 1848 | B | PLANNED SHUTDOWN | Replace 11kV poles G2158 & G2122 Paroa Rd
14773 | 27/04/2013 | 2013 | 2013-04-27 | 368 | 48 | 11952 | C | TREE CONTACTS | Repair 11kV lines between poles G2355 to G2357 Tauwhareparae Rd
14774 | 28/04/2013 | 2013 | 2013-04-28 | 10 | 8 | 80 | C | DEFECTIVE EQUIPMENT | Replace insulator pole W6742 Frasertown Rd
14775 | 28/04/2013 | 2013 | 2013-04-28 | 189 | 1178 | 47395 | C | DEFECTIVE EQUIPMENT | Jumper through faulty PMR C4859 Muriwai
14806 | 01/05/2013 | 2013 | 2013-05-01 | 343 | 48 | 6003 | B | PLANNED SHUTDOWN | Replace 11kV poles E650 E1052 E640 E1055 Kanakanaia Rd
14789 | 02/05/2013 | 2013 | 2013-05-02 | 72 | 1527 | 40414 | C | DEFECTIVE EQUIPMENT | Isolate O/S A557 cable fault outside 91 Iranui Rd
14790 | 02/05/2013 | 2013 | 2013-05-02 | 105 | 183 | 10107 | C | TREE CONTACTS | Isolate O/S A557 cable fault outside 91 Iranui Rd
14791 | 02/05/2013 | 2013 | 2013-05-02 | 9 | 234 | 2106 | C | TREE CONTACTS | Remove tree from 11kV lines pole C3684 Waingake Rd
14808 | 02/05/2013 | 2013 | 2013-05-02 | 29 | 45 | 2385 | B | PLANNED SHUTDOWN | Isolate 11kV lines pole C4138 Waingake Rd for tree cutting
14792 | 03/05/2013 | 2013 | 2013-05-03 | 54 | 30 | 1620 | C | DEFECTIVE EQUIPMENT | Replace T/x A164 & install DDO fuses Mihiwhitu Rd
14805 | 03/05/2013 | 2013 | 2013-05-03 | 387 | 46 | 17802 | B | PLANNED SHUTDOWN | Replace 11kV poles D5084 D5048 D5099 D5110 Mutuera Rd
14809 | 03/05/2013 | 2013 | 2013-05-03 | 299 | 4 | 1199 | B | PLANNED SHUTDOWN | Replace 11kV pole W20563 Wai Stn
14793 | 04/05/2013 | 2013 | 2013-05-04 | 270 | 11 | 2970 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable pole C672 Dunstan Rd
14795 | 04/05/2013 | 2013 | 2013-05-04 | 17 | 73 | 1178 | C | UNKNOWN | Reclose CB H341 Mata Rd cause unknown
14794 | 05/05/2013 | 2013 | 2013-05-05 | 1173 | 29 | 3783 | C | DEFECTIVE EQUIPMENT | Replace 11kv T/x pole H44 Carroll St Te Puia
14807 | 06/05/2013 | 2013 | 2013-05-06 | 338 | 48 | 5698 | B | PLANNED SHUTDOWN | Replace 11kV poles E1056 E1063 E648 E646 Kanakanaia Rd
14796 | 07/05/2013 | 2013 | 2013-05-07 | 54 | 1034 | 35026 | C | DEFECTIVE EQUIPMENT | Replace 33kV pole W3717 Clydebank Rd
14810 | 07/05/2013 | 2013 | 2013-05-07 | 512 | 45 | 2896 | B | PLANNED SHUTDOWN | Reconductor 11kV lines Between poles H1865 to H1854 SH35 Ruatoria
14797 | 08/05/2013 | 2013 | 2013-05-08 | 884 | 168 | 58706 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole E602 Kanakanaia Rd
14798 | 08/05/2013 | 2013 | 2013-05-08 | 248 | 152 | 24576 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole G2018 Tauwhareparae Rd
14799 | 08/05/2013 | 2013 | 2013-05-08 | 212 | 165 | 26144 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole C4876 SH2 Muriwai
14811 | 08/05/2013 | 2013 | 2013-05-08 | 396 | 15 | 5940 | B | PLANNED SHUTDOWN | Reconductor lines between poles H1831 to H2907 SH35 Ruatoria
14812 | 09/05/2013 | 2013 | 2013-05-09 | 370 | 30 | 3083 | B | PLANNED SHUTDOWN | Reconductor lines between poles H1842 to H1839 SH35 Ruatoria
14813 | 10/05/2013 | 2013 | 2013-05-10 | 374 | 44 | 6248 | B | PLANNED SHUTDOWN | Reconductor lines between poles H1831 to H2907 SH35 Ruatoria
14800 | 11/05/2013 | 2013 | 2013-05-11 | 111 | 375 | 22029 | C | FOREIGN INTERFERENCE | Replace 11kV pole B4866 Russell St Hit by Car
14801 | 11/05/2013 | 2013 | 2013-05-11 | 170 | 44 | 7480 | C | FOREIGN INTERFERENCE | Replace 11kV pole D3308 Pareroa Stn Tiniroto Rd
14814 | 15/05/2013 | 2013 | 2013-05-15 | 413 | 19 | 13021 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting W1009 Kahungngu
14816 | 15/05/2013 | 2013 | 2013-05-15 | 337 | 102 | 13198 | B | PLANNED SHUTDOWN | Replace 11kV poles J4041 J4042 J4045 Hicks Bay
14817 | 16/05/2013 | 2013 | 2013-05-16 | 58 | 77 | 4466 | B | PLANNED SHUTDOWN | Replace 11kV poles J4496 J4498 Hicks Bay
14815 | 17/05/2013 | 2013 | 2013-05-17 | 450 | 29 | 20712 | B | PLANNED SHUTDOWN | Replace 11kV poles F2046 to ABS F63 Whakarau Rd
14818 | 17/05/2013 | 2013 | 2013-05-17 | 275 | 48 | 13200 | B | PLANNED SHUTDOWN | Replace 11kV poles J4217 J4228 J4244 J4251 Waikura Valley Rd
14819 | 20/05/2013 | 2013 | 2013-05-20 | 49 | 259 | 12691 | B | PLANNED SHUTDOWN | Install DDO fuses on pole F2948 Whatatutu Rd
14820 | 21/05/2013 | 2013 | 2013-05-21 | 439 | 48 | 7806 | B | PLANNED SHUTDOWN | Replace 11kV poles E1052 E640 E1055 Kanakanaia Rd
14821 | 22/05/2013 | 2013 | 2013-05-22 | 478 | 48 | 8768 | B | PLANNED SHUTDOWN | Reconductor lines between poles H1839 to J622 Waiapu Rd
14802 | 27/05/2013 | 2013 | 2013-05-27 | 197 | 1177 | 32025 | C | FOREIGN INTERFERENCE | Repair 11kV lines between poles C3582 to C3583 Maraetaha
14822 | 27/05/2013 | 2013 | 2013-05-27 | 452 | 16 | 2733 | B | PLANNED SHUTDOWN | Install DDO fuses on pole A896 Wheatstone Rd
14803 | 29/05/2013 | 2013 | 2013-05-29 | 83 | 37 | 3071 | C | UNKNOWN | Reclose CBW9859 Te Reinga cause unknown
14804 | 29/05/2013 | 2013 | 2013-05-29 | 486 | 272 | 8515 | C | TREE CONTACTS | Repair 11kV lines pole W8383 Morere Hill
14823 | 31/05/2013 | 2013 | 2013-05-31 | 240 | 48 | 11520 | B | PLANNED SHUTDOWN | Replace 11kV poles J4244 J4251 Waikura Valley Rd
14824 | 05/06/2013 | 2013 | 2013-06-05 | 918 | 48 | 34700 | C | DEFECTIVE EQUIPMENT | Replace Xarms T/x pole W330 Pihanui Stn
14847 | 05/06/2013 | 2013 | 2013-06-05 | 235 | 5 | 1175 | B | PLANNED SHUTDOWN | Replace 1 11kV poles W21128 & W21130 Ohuia Rd
14825 | 06/06/2013 | 2013 | 2013-06-06 | 439 | 102 | 37053 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J3829 Hicks Bay
14826 | 06/06/2013 | 2013 | 2013-06-06 | 62 | 388 | 24056 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J2574 Shortcut Rd Te Araroa
14827 | 07/06/2013 | 2013 | 2013-06-07 | 316 | 216 | 68256 | C | ADVERSE WEATHER | Repair 11kV lines pole W7678 Kinikini
14828 | 07/06/2013 | 2013 | 2013-06-07 | 1245 | 15 | 16575 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole A4122 Kaiti Beach Rd
14848 | 07/06/2013 | 2013 | 2013-06-07 | 434 | 22 | 1468 | B | PLANNED SHUTDOWN | Replace 11kV poles F2063 F2064 F2065 Whakarau Rd
14850 | 11/06/2013 | 2013 | 2013-06-11 | 54 | 75 | 4050 | B | PLANNED SHUTDOWN | Install DDO fuses on pole C2505 Nelson Rd
14851 | 11/06/2013 | 2013 | 2013-06-11 | 306 | 114 | 10164 | B | PLANNED SHUTDOWN | Replace 11kV poles G1717 G1716 G1714 G134 Tauwhareparae Rd
14829 | 12/06/2013 | 2013 | 2013-06-12 | 61 | 80 | 4880 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A1209 Whitiwhiti Hill
14845 | 12/06/2013 | 2013 | 2013-06-12 | 126 | 11 | 1738 | B | PLANNED SHUTDOWN | Isolate 11kV lines A4350 Goodwins Rd for tree cutting
14846 | 13/06/2013 | 2013 | 2013-06-13 | 406 | 3 | 1218 | B | PLANNED SHUTDOWN | Replace 11kV poles between F2081 to F68 Whakarau Rd
14852 | 13/06/2013 | 2013 | 2013-06-13 | 243 | 12 | 2915 | B | PLANNED SHUTDOWN | Replace poles between G40 to G2130 Paroa Rd
14830 | 15/06/2013 | 2013 | 2013-06-15 | 121 | 234 | 19080 | C | UNKNOWN | Reclose CB D462 Te Arai at Patutahi Sub cause unknown
14831 | 18/06/2013 | 2013 | 2013-06-18 | 103 | 37 | 2831 | C | ADVERSE WEATHER | Replace 2 11kV poles J654 & J752 Tapuaeroa Rd
14859 | 18/06/2013 | 2013 | 2013-06-18 | 45 | 4 | 236 | B | PLANNED SHUTDOWN | Install line breaks pole A4346 Goodwins Rd
14832 | 19/06/2013 | 2013 | 2013-06-19 | 11 | 275 | 3025 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W979 Frasertown Rd
14844 | 19/06/2013 | 2013 | 2013-06-19 | 67 | 32 | 2144 | B | PLANNED SHUTDOWN | Reconductor 11kV between poles H1839 to J622 Waiapu Rd
14853 | 20/06/2013 | 2013 | 2013-06-20 | 468 | 343 | 28744 | B | PLANNED SHUTDOWN | Install new SW/Gr W863 W865 Locheill St Mahia
14854 | 20/06/2013 | 2013 | 2013-06-20 | 382 | 159 | 24384 | B | PLANNED SHUTDOWN | Replace 11kV poles G1301 G1302 G1307 G243 Tauwharaparae Rd
14834 | 21/06/2013 | 2013 | 2013-06-21 | 44 | 1134 | 49352 | C | ADVERSE WEATHER | Reclose CB1 & W1032 Wairoa Sub High Winds
14835 | 21/06/2013 | 2013 | 2013-06-21 | 1276 | 216 | 41867 | C | ADVERSE WEATHER | Repair 11kV lines pole W1433 Waikokopu
14849 | 21/06/2013 | 2013 | 2013-06-21 | 381 | 114 | 10989 | B | PLANNED SHUTDOWN | Replace 11kV poles G1705 G1706 G1707 G1709 Tauwhareparae Rd
14836 | 22/06/2013 | 2013 | 2013-06-22 | 290 | 366 | 65489 | C | TREE CONTACTS | Repair 11kV lines poles W6316 to W6315
14837 | 22/06/2013 | 2013 | 2013-06-22 | 60 | 91 | 5460 | C | TREE CONTACTS | Replace T/x W463 Trees broke conductor & T/x bushing
14838 | 24/06/2013 | 2013 | 2013-06-24 | 259 | 83 | 10547 | C | FOREIGN INTERFERENCE | Repair 11kV lines between poles H1092 to H1093 Mata Rd ( Ducks)
14839 | 25/06/2013 | 2013 | 2013-06-25 | 18 | 35 | 630 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W1173 Flaxmill Rd
14856 | 26/06/2013 | 2013 | 2013-06-26 | 154 | 5 | 770 | B | PLANNED SHUTDOWN | 11kV Maintenance poles W21128 W21130 Ohuia Rd
14860 | 26/06/2013 | 2013 | 2013-06-26 | 463 | 4 | 4720 | B | PLANNED SHUTDOWN | Replace 11kV poles between F2081 & F1705 Whakarau Rd
14840 | 28/06/2013 | 2013 | 2013-06-28 | 300 | 6 | 1800 | C | TREE CONTACTS | Repair 11kV lines pole J2076 Koia Rd Rangitukia
14855 | 28/06/2013 | 2013 | 2013-06-28 | 116 | 168 | 19488 | B | PLANNED SHUTDOWN | Replace Recloser C4859 SH2 Muriwai
14857 | 28/06/2013 | 2013 | 2013-06-28 | 406 | 151 | 42001 | B | PLANNED SHUTDOWN | Replace 11kV poles W9127 W9135 Kaiwaitau Rd
14841 | 29/06/2013 | 2013 | 2013-06-29 | 45 | 1066 | 29908 | C | DEFECTIVE EQUIPMENT | Replace Jumpers on ABS C674 Nelson Rd
14842 | 29/06/2013 | 2013 | 2013-06-29 | 84 | 891 | 62149 | C | DEFECTIVE EQUIPMENT | Isolate 11kV cable fault A299 Huxley Rd
14843 | 30/06/2013 | 2013 | 2013-06-30 | 30 | 144 | 4320 | C | DEFECTIVE EQUIPMENT | Check cable termination Oil Switch A299 Huxley Rd
14858 | 30/06/2013 | 2013 | 2013-06-30 | 262 | 4 | 1048 | B | PLANNED SHUTDOWN | Upgrade T/x B187 Firestone Gladstone Rd
14883 | 02/07/2013 | 2013 | 2013-07-02 | 489 | 102 | 15159 | B | PLANNED SHUTDOWN | Replace 11kV poles J4496 J4498 & ABS J356 Hicks Bay
14861 | 03/07/2013 | 2013 | 2013-07-03 | 175 | 479 | 25137 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable A229 Huxley Rd
14862 | 03/07/2013 | 2013 | 2013-07-03 | 10 | 1751 | 17510 | C | ADVERSE WEATHER | Reclose CB 2 Wairoa Sub High Winds
14884 | 03/07/2013 | 2013 | 2013-07-03 | 330 | 48 | 15840 | B | PLANNED SHUTDOWN | Replace 11kV poles J4244 Waikura Valley
14885 | 05/07/2013 | 2013 | 2013-07-05 | 190 | 225 | 27552 | B | PLANNED SHUTDOWN | Replace 11kV poles J493 J620 Wharf Rd Hicks Bay
14863 | 09/07/2013 | 2013 | 2013-07-09 | 28 | 76 | 2128 | C | DEFECTIVE EQUIPMENT | Replace 3 DDO fuses pole B896 Island Rd
14886 | 09/07/2013 | 2013 | 2013-07-09 | 358 | 37 | 13246 | B | PLANNED SHUTDOWN | Replace 11kV poles G1302 G1307 Tauwhareparae Rd
14887 | 10/07/2013 | 2013 | 2013-07-10 | 57 | 114 | 6498 | B | PLANNED SHUTDOWN | Replace 11kV poles G1717 G1716 G134 Tauwhareparae Rd
14864 | 11/07/2013 | 2013 | 2013-07-11 | 228 | 184 | 9676 | C | TREE CONTACTS | Repair 11kV lines Pole H2064 SH35 Te Puia
14888 | 12/07/2013 | 2013 | 2013-07-12 | 101 | 126 | 12469 | B | PLANNED SHUTDOWN | Replace SW/GR B770 B771 B772 Awapuni Rd
14889 | 12/07/2013 | 2013 | 2013-07-12 | 454 | 7 | 6048 | B | PLANNED SHUTDOWN | Replace 11kV poles F1707 F1710 F1714 Whakarau Rd
14865 | 13/07/2013 | 2013 | 2013-07-13 | 884 | 89 | 15594 | C | TREE CONTACTS | Repair 11kV lines pole D3313 Tiniroto Rd
14866 | 15/07/2013 | 2013 | 2013-07-15 | 13 | 1107 | 13899 | C | ADVERSE WEATHER | Replace 33kV poleW3757 near Hereheretau Rd
14867 | 15/07/2013 | 2013 | 2013-07-15 | 37 | 788 | 15046 | C | TREE CONTACTS | Repair 11kV jumper pole W922 Kaimoana Rd
14869 | 15/07/2013 | 2013 | 2013-07-15 | 941 | 37 | 19573 | C | TREE CONTACTS | Repair 11kV lines pole J3397 Tapuaeroa Valley
14870 | 15/07/2013 | 2013 | 2013-07-15 | 735 | 19 | 13965 | C | TREE CONTACTS | Repair 11kV lines pole D3314 Wharerata Rd
14871 | 15/07/2013 | 2013 | 2013-07-15 | 25 | 394 | 9850 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumpers poles W813 & W5851 Frasertown Rd
14872 | 15/07/2013 | 2013 | 2013-07-15 | 10 | 118 | 1180 | C | ADVERSE WEATHER | Replace 11kV pole C1938 Muriwai
14875 | 15/07/2013 | 2013 | 2013-07-15 | 41 | 34 | 1394 | C | TREE CONTACTS | Repair 11kV lines pole W4009 Mangpoikie Rd
14873 | 16/07/2013 | 2013 | 2013-07-16 | 180 | 9 | 9000 | C | ADVERSE WEATHER | Replace 2 11kV poles E855 & E856 Tarndale Rd Whatatutu
14876 | 16/07/2013 | 2013 | 2013-07-16 | 77 | 23 | 1771 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W672 Nuhaka
14874 | 17/07/2013 | 2013 | 2013-07-17 | 280 | 20 | 10266 | C | ADVERSE WEATHER | Replace 2 11kV poles E855 & E856 Tarndale Rd Whatatutu
14877 | 17/07/2013 | 2013 | 2013-07-17 | 123 | 37 | 4551 | C | DEFECTIVE EQUIPMENT | Temp prop 11kV pole F2276 Whakarau Rd
14868 | 19/07/2013 | 2013 | 2013-07-19 | 148 | 58 | 3853 | C | TREE CONTACTS | Repair 11kV lines pole C811 Waingake
14878 | 19/07/2013 | 2013 | 2013-07-19 | 50 | 20 | 1000 | C | DEFECTIVE EQUIPMENT | Replace Kidney insulator pole H1017 Waitahaia Rd
14890 | 19/07/2013 | 2013 | 2013-07-19 | 36 | 127 | 8382 | B | PLANNED SHUTDOWN | Replace 11kV UG Cable B4070 to B351 Roebuck Rd
14879 | 20/07/2013 | 2013 | 2013-07-20 | 202 | 73 | 14746 | C | TREE CONTACTS | Repair 11kV lines pole W6562 Mangapoikie Rd
14880 | 22/07/2013 | 2013 | 2013-07-22 | 50 | 155 | 7750 | C | DEFECTIVE EQUIPMENT | Replace 3 DDO fuses B888 Albert St
14881 | 23/07/2013 | 2013 | 2013-07-23 | 120 | 728 | 50868 | C | DEFECTIVE EQUIPMENT | Replace SW/GR C447 C448 C449 Aberdeen Rd
14892 | 25/07/2013 | 2013 | 2013-07-25 | 442 | 33 | 14589 | B | PLANNED SHUTDOWN | Replace 11kV poles J322 J3002 J3003 Whakaangiangi Rd
14893 | 26/07/2013 | 2013 | 2013-07-26 | 156 | 15 | 2340 | B | PLANNED SHUTDOWN | Replace 11kV poles J2214 J2215 J2216 Kopuaponamu Rd
14882 | 28/07/2013 | 2013 | 2013-07-28 | 363 | 167 | 60621 | C | FOREIGN INTERFERENCE | Replace 11kV pole B172 Aberdeen Rd Hit by Car
14891 | 29/07/2013 | 2013 | 2013-07-29 | 318 | 6 | 1908 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting B189 Paratu Rd
14894 | 30/07/2013 | 2013 | 2013-07-30 | 455 | 21 | 16779 | B | PLANNED SHUTDOWN | Replace 11kV poles W3873 W3870 Waihua Valley
14910 | 01/08/2013 | 2013 | 2013-08-01 | 330 | 54 | 17820 | B | PLANNED SHUTDOWN | Replace 11kV poles E42 E2556 E2559 E2561 Ford Rd
14895 | 03/08/2013 | 2013 | 2013-08-03 | 55 | 2510 | 94879 | C | TREE CONTACTS | Remove branch from pole A1061 Christophers Rd
14912 | 06/08/2013 | 2013 | 2013-08-06 | 330 | 12 | 3960 | B | PLANNED SHUTDOWN | Replace 11kV poles E237 E2568 E2569 Ford Rd
14913 | 08/08/2013 | 2013 | 2013-08-08 | 248 | 81 | 20088 | B | PLANNED SHUTDOWN | Isolate 11kV lines D409 Ferry Rd for tree cutting
14896 | 10/08/2013 | 2013 | 2013-08-10 | 912 | 91 | 18711 | C | TREE CONTACTS | Repair 11kV lines pole J2043 Awatere
14897 | 10/08/2013 | 2013 | 2013-08-10 | 955 | 63 | 17109 | C | TREE CONTACTS | Repair 11kV Lines pole H2233 Waipiro Bay Rd
14898 | 10/08/2013 | 2013 | 2013-08-10 | 280 | 419 | 65006 | C | TREE CONTACTS | Repair 11kV lines pole F1848 Matawai Rd
14899 | 11/08/2013 | 2013 | 2013-08-11 | 802 | 197 | 41077 | C | UNKNOWN | Reclose CB J4035 cause unknown High Winds
14900 | 11/08/2013 | 2013 | 2013-08-11 | 2020 | 14 | 6392 | C | ADVERSE WEATHER | Replace 2 11kV poles A510 & A1529 & repair lines Waihau Rd
14914 | 11/08/2013 | 2013 | 2013-08-11 | 330 | 23 | 7590 | B | PLANNED SHUTDOWN | Upgrade T/x B195 Reads Quay
14901 | 13/08/2013 | 2013 | 2013-08-13 | 29 | 274 | 7946 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole B3187 Mary St
14902 | 14/08/2013 | 2013 | 2013-08-14 | 46 | 25 | 1150 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole A3442 SH35 Rototahi
14911 | 14/08/2013 | 2013 | 2013-08-14 | 348 | 12 | 4176 | B | PLANNED SHUTDOWN | Replace 11kV poles F2479 F3094 F174 SH2 Matawai Rd
14915 | 14/08/2013 | 2013 | 2013-08-14 | 49 | 32 | 1568 | B | PLANNED SHUTDOWN | Install 3 DDO fuses pole C5672 Saleyards Rd
14903 | 15/08/2013 | 2013 | 2013-08-15 | 94 | 12 | 1128 | C | TREE CONTACTS | Remove trees in 11kV lines pole F178 Matawai Rd
14904 | 15/08/2013 | 2013 | 2013-08-15 | 17 | 1076 | 15702 | C | UNKNOWN | Reclose CB F411 at Puha sub cause unknown
14917 | 15/08/2013 | 2013 | 2013-08-15 | 372 | 14 | 5208 | B | PLANNED SHUTDOWN | Replace 11kV poles J3002 J3003 J3004 Whakaangiangi
14918 | 16/08/2013 | 2013 | 2013-08-16 | 368 | 36 | 7600 | B | PLANNED SHUTDOWN | Replace 11kV poles J3985 J3984 J3983 Waione Rd
14916 | 18/08/2013 | 2013 | 2013-08-18 | 334 | 30 | 10020 | B | PLANNED SHUTDOWN | Replace faulty Oil fuse Switch B1038 Parkinson St
14905 | 19/08/2013 | 2013 | 2013-08-19 | 223 | 235 | 40081 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole W8021 Nuhaka (bird clash)
14921 | 20/08/2013 | 2013 | 2013-08-20 | 433 | 30 | 8166 | B | PLANNED SHUTDOWN | Replace 11kV ABS pole F1770 Whakarau Rd
14906 | 21/08/2013 | 2013 | 2013-08-21 | 160 | 30 | 4800 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole G1580 Arikihi Rd
14919 | 21/08/2013 | 2013 | 2013-08-21 | 420 | 38 | 15960 | B | PLANNED SHUTDOWN | Erect 3 11kV fuses pole J166 Tapuearoa Rd
14922 | 22/08/2013 | 2013 | 2013-08-22 | 325 | 19 | 4243 | B | PLANNED SHUTDOWN | Replace 11kV pole F75 & remove ABS Whakarau Rd
14907 | 23/08/2013 | 2013 | 2013-08-23 | 82 | 4 | 328 | C | FOREIGN INTERFERENCE | Isolate 11kV pole D733 Smiths Rd Ngatapa
14920 | 23/08/2013 | 2013 | 2013-08-23 | 360 | 33 | 11880 | B | PLANNED SHUTDOWN | Replace 11kV poles J3000 J2974 J2975 J2976 Whakaangiangi Rd
14924 | 23/08/2013 | 2013 | 2013-08-23 | 36 | 419 | 15084 | B | PLANNED SHUTDOWN | Repair 11kV ABS F467 Matawai Rd Otoko
14923 | 26/08/2013 | 2013 | 2013-08-26 | 400 | 38 | 8040 | B | PLANNED SHUTDOWN | Replace 11kV poles J4439 J4440 J2837 Waione Rd
14925 | 28/08/2013 | 2013 | 2013-08-28 | 317 | 38 | 12046 | B | PLANNED SHUTDOWN | Replace 11kV poles J314 J2771 J2764 J2751 Te Araroa Rd
14908 | 29/08/2013 | 2013 | 2013-08-29 | 12 | 61 | 732 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W6834 North Clyde
14909 | 31/08/2013 | 2013 | 2013-08-31 | 76 | 254 | 9911 | C | FOREIGN INTERFERENCE | Restore power to T/x F383 Te Karaka
14926 | 03/09/2013 | 2013 | 2013-09-03 | 280 | 22 | 2912 | C | DEFECTIVE EQUIPMENT | Replace DDO Fuses F56 Mahiki Rd
14978 | 03/09/2013 | 2013 | 2013-09-03 | 59 | 123 | 12177 | B | PLANNED SHUTDOWN | Replace 11 kV pole G1206 Tolaga Bay
14979 | 03/09/2013 | 2013 | 2013-09-03 | 350 | 12 | 4200 | B | PLANNED SHUTDOWN | Replace poles E2559 E2561 E2865 Ford Rd
14980 | 03/09/2013 | 2013 | 2013-09-03 | 172 | 49 | 8428 | B | PLANNED SHUTDOWN | Replace T/x B849 Oak St
14927 | 04/09/2013 | 2013 | 2013-09-04 | 117 | 8 | 936 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole F2023 Mahiki Rd
14928 | 05/09/2013 | 2013 | 2013-09-05 | 298 | 13 | 3874 | C | DEFECTIVE EQUIPMENT | Replace insulator pole D3677 Bushy Knoll Rd
14929 | 06/09/2013 | 2013 | 2013-09-06 | 113 | 9 | 1017 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole F4806 Tapuihikitia Rd
14981 | 06/09/2013 | 2013 | 2013-09-06 | 330 | 15 | 4950 | B | PLANNED SHUTDOWN | Replace 11kV poles J2215 J2216 J2212 Kopuapounamu
14945 | 11/09/2013 | 2013 | 2013-09-11 | 527 | 441 | 210478 | C | TREE CONTACTS | Repair 11kV lines between poles W21679 to W606 Frasertown
14982 | 11/09/2013 | 2013 | 2013-09-11 | 448 | 22 | 8930 | B | PLANNED SHUTDOWN | Replace 11kV poles F1551 F1546 F1532 Whakarau Rd
14941 | 12/09/2013 | 2013 | 2013-09-12 | 844 | 159 | 82838 | C | TREE CONTACTS | Repair 11kV lines pole D2959 Wharekopae Rd
14943 | 12/09/2013 | 2013 | 2013-09-12 | 1210 | 69 | 16792 | C | TREE CONTACTS | Repair 11kV lines pole H510 Ihungia Rd
14948 | 12/09/2013 | 2013 | 2013-09-12 | 93 | 15 | 1393 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole F1131 Otoko Hill
14949 | 12/09/2013 | 2013 | 2013-09-12 | 483 | 83 | 38083 | C | ADVERSE WEATHER | Repair 11kV lines Pole G277 Three Bridges
14950 | 12/09/2013 | 2013 | 2013-09-12 | 893 | 102 | 74651 | C | DEFECTIVE EQUIPMENT | Cut jumpers pole A1949 Ballies Rd Waimata
14951 | 12/09/2013 | 2013 | 2013-09-12 | 1314 | 51 | 41503 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole D410 Pehiri Rd
14953 | 12/09/2013 | 2013 | 2013-09-12 | 1517 | 48 | 72816 | C | ADVERSE WEATHER | Repair 11kV line poles G211 to G2331 Tauwhareparae Rd
14958 | 12/09/2013 | 2013 | 2013-09-12 | 1542 | 183 | 104926 | C | TREE CONTACTS | Repair 11kV lines between poles W5022 to W1040 Putere
14965 | 12/09/2013 | 2013 | 2013-09-12 | 382 | 502 | 54256 | C | TREE CONTACTS | Repair 11kV lines pole W5584 Raupunga
14944 | 13/09/2013 | 2013 | 2013-09-13 | 1390 | 170 | 239818 | C | TREE CONTACTS | Repair 11kV lines pole W7033 Ohuka
14946 | 13/09/2013 | 2013 | 2013-09-13 | 2464 | 233 | 154106 | C | TREE CONTACTS | Repair 11kV lines pole C849 Waingake Rd
14947 | 13/09/2013 | 2013 | 2013-09-13 | 2489 | 167 | 85219 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole E1072 Kanakanaia Rd
14952 | 13/09/2013 | 2013 | 2013-09-13 | 1992 | 61 | 41148 | C | ADVERSE WEATHER | Repair 11kV line pole A3991 Waiomoko Rd
14954 | 13/09/2013 | 2013 | 2013-09-13 | 80 | 11 | 880 | C | TREE CONTACTS | Repair 11kV lines pole E157 Te Hau Rd
14956 | 13/09/2013 | 2013 | 2013-09-13 | 1799 | 185 | 14531 | C | TREE CONTACTS | Repair 11kV lines pole H2020 Kopuaroa
14957 | 13/09/2013 | 2013 | 2013-09-13 | 2049 | 272 | 134084 | C | TREE CONTACTS | Repair 11kV lines between poles W905 to W575 Tahaenui
14960 | 13/09/2013 | 2013 | 2013-09-13 | 43 | 10 | 430 | C | ADVERSE WEATHER | Repair twisted lines poles W69 to W6280 Cricklewood
14976 | 13/09/2013 | 2013 | 2013-09-13 | 1272 | 29 | 36888 | C | TREE CONTACTS | Repair 11kV lines pole W6022 Kotare
14942 | 14/09/2013 | 2013 | 2013-09-14 | 4195 | 92 | 237855 | C | TREE CONTACTS | Repair 11kV lines pole E676 Tarndale Rd
14961 | 14/09/2013 | 2013 | 2013-09-14 | 283 | 5 | 1415 | C | TREE CONTACTS | Repair 11kV lines pole H509 Ihungia Rd
14966 | 14/09/2013 | 2013 | 2013-09-14 | 1479 | 12 | 4168 | C | TREE CONTACTS | Replace 11kV poleW1746 Waihua Valley
14977 | 14/09/2013 | 2013 | 2013-09-14 | 906 | 13 | 11778 | C | ADVERSE WEATHER | Repair 11kV Lines beyond pole W1003 Otoi
14955 | 15/09/2013 | 2013 | 2013-09-15 | 267 | 5 | 1335 | C | ADVERSE WEATHER | Repair 11kV lines pole H231 Karewa Rd
14962 | 15/09/2013 | 2013 | 2013-09-15 | 1251 | 134 | 19114 | C | TREE CONTACTS | Replace 11kV pole W5372 Kotiemaori
14963 | 15/09/2013 | 2013 | 2013-09-15 | 298 | 20 | 5960 | C | TREE CONTACTS | Replace poles C2486 C4390 C2494 Pakowhai Rd
14964 | 15/09/2013 | 2013 | 2013-09-15 | 102 | 10 | 1020 | C | TREE CONTACTS | Repair 11kV lines pole W1780 Erepiti
14967 | 15/09/2013 | 2013 | 2013-09-15 | 170 | 11 | 1870 | C | ADVERSE WEATHER | Repair 11kV lines pole H1668 Matahiia Rd
14968 | 17/09/2013 | 2013 | 2013-09-17 | 42 | 12 | 504 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J887 Tikitiki
14970 | 17/09/2013 | 2013 | 2013-09-17 | 153 | 29 | 4437 | C | ADVERSE WEATHER | Replace 11kV pole F1468 Koranga Valley
14971 | 17/09/2013 | 2013 | 2013-09-17 | 281 | 8 | 2248 | C | TREE CONTACTS | Repair 11kV lines pole E1152 Kanakanaia Rd
14972 | 17/09/2013 | 2013 | 2013-09-17 | 35 | 15 | 525 | C | TREE CONTACTS | Repair 11kV line poles W5022 to W1040 Putere
14969 | 18/09/2013 | 2013 | 2013-09-18 | 352 | 41 | 13732 | C | ADVERSE WEATHER | Replace 11kV pole H1242 Tuakau Rd
14973 | 18/09/2013 | 2013 | 2013-09-18 | 428 | 2 | 856 | C | ADVERSE WEATHER | Replace 11kV pole A1951 Ballies Rd
14974 | 18/09/2013 | 2013 | 2013-09-18 | 236 | 4 | 2124 | C | TREE CONTACTS | Replace 11kV pole G2255 Hokoroa Rd
14930 | 19/09/2013 | 2013 | 2013-09-19 | 88 | 1174 | 36333 | C | DEFECTIVE EQUIPMENT | Isolate 11kV cable pole D4160 Kirkpatrick Rd
14931 | 20/09/2013 | 2013 | 2013-09-20 | 55 | 66 | 3630 | C | DEFECTIVE EQUIPMENT | Reconnect cable pole D4160 Kirkpatrick Rd
14934 | 23/09/2013 | 2013 | 2013-09-23 | 511 | 168 | 11263 | C | TREE CONTACTS | Repair 11kV lines pole W5550 Raupunga
14935 | 25/09/2013 | 2013 | 2013-09-25 | 834 | 124 | 49341 | C | TREE CONTACTS | Repair 11kV lines between poles H1498 to H1499 Kopuaroa
14936 | 25/09/2013 | 2013 | 2013-09-25 | 40 | 23 | 920 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W8710 Nuhaka
14938 | 25/09/2013 | 2013 | 2013-09-25 | 195 | 33 | 6435 | C | TREE CONTACTS | Repair 11kV lines pole E1069 Kanakanaia Rd
14932 | 26/09/2013 | 2013 | 2013-09-26 | 10 | 148 | 1480 | C | DEFECTIVE EQUIPMENT | Replace 11kV cable to T/x W1534 River Parade
14939 | 26/09/2013 | 2013 | 2013-09-26 | 65 | 12 | 780 | C | DEFECTIVE EQUIPMENT | Remove faulty lightining arrestors T/x pole D573 Tiniroto Rd
14940 | 26/09/2013 | 2013 | 2013-09-26 | 67 | 36 | 2412 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumpers poles J2809 Rangitukia Rd
14933 | 28/09/2013 | 2013 | 2013-09-28 | 130 | 107 | 6292 | C | DEFECTIVE EQUIPMENT | Remove lightining arrestor T/x pole D314 Tiniroto Rd
14985 | 01/10/2013 | 2013 | 2013-10-01 | 80 | 6 | 480 | B | PLANNED SHUTDOWN | Replace T/x J130 Wharf Rd Hicks Bay
15026 | 01/10/2013 | 2013 | 2013-10-01 | 92 | 30 | 2760 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole A3467 Miniwhetu Rd
15027 | 01/10/2013 | 2013 | 2013-10-01 | 642 | 137 | 25517 | C | TREE CONTACTS | Repair 11kV lines between D3239 to D3240 Tiniroto Rd
14983 | 02/10/2013 | 2013 | 2013-10-02 | 143 | 13 | 1859 | B | PLANNED SHUTDOWN | Upgrade T/x H289 with 100kVA Hiruharama Rd
14984 | 02/10/2013 | 2013 | 2013-10-02 | 520 | 126 | 65520 | B | PLANNED SHUTDOWN | Replace 11kV pole W4330 Frasertown
14986 | 08/10/2013 | 2013 | 2013-10-08 | 98 | 53 | 5194 | B | PLANNED SHUTDOWN | Isolate for tree cutting B51 to E865 Ormond
15028 | 09/10/2013 | 2013 | 2013-10-09 | 58 | 34 | 1972 | C | TREE CONTACTS | Repair 11kV lines pole W9119 Kaiwaitau Rd
14989 | 10/10/2013 | 2013 | 2013-10-10 | 300 | 78 | 11336 | B | PLANNED SHUTDOWN | Install new 300kVA T/x C254P Lytton High Nelson Rd
14990 | 10/10/2013 | 2013 | 2013-10-10 | 540 | 160 | 84284 | B | PLANNED SHUTDOWN | Replace 11kV poles J2859 J1064 J1076 J1079 Rangitukia
14987 | 11/10/2013 | 2013 | 2013-10-11 | 88 | 27 | 2376 | B | PLANNED SHUTDOWN | Isolate for tree cutting D603 O'Gradys Rd
15019 | 11/10/2013 | 2013 | 2013-10-11 | 560 | 192 | 104185 | C | FOREIGN INTERFERENCE | Remove possum from 11kV pole W4632 Onepoto
15020 | 11/10/2013 | 2013 | 2013-10-11 | 706 | 44 | 28659 | C | TREE CONTACTS | Remove branches off 11kV lines pole W998 Waihi
15029 | 11/10/2013 | 2013 | 2013-10-11 | 756 | 167 | 126252 | C | TREE CONTACTS | Repair 11kV lines poles W4631 to W630 Tuai Village
14995 | 12/10/2013 | 2013 | 2013-10-12 | 8 | 479 | 3468 | C | TREE CONTACTS | Remove tree from pole J1830 Te Araroa
15000 | 12/10/2013 | 2013 | 2013-10-12 | 417 | 60 | 25313 | C | TREE CONTACTS | Repair 11kV lines pole F2139 Tahora
15003 | 12/10/2013 | 2013 | 2013-10-12 | 1025 | 92 | 66430 | C | TREE CONTACTS | Repair 11kV lines pole E772 Whatatutu
15007 | 12/10/2013 | 2013 | 2013-10-12 | 600 | 59 | 11477 | C | TREE CONTACTS | Repair 11kV lines pole F170 Matawai Rd
15017 | 12/10/2013 | 2013 | 2013-10-12 | 51 | 95 | 3741 | C | TREE CONTACTS | Replace Centre bolt on pole J1052 Hit by tree Rangitukia
15018 | 12/10/2013 | 2013 | 2013-10-12 | 420 | 170 | 69667 | C | ADVERSE WEATHER | Reclose CB24 Ruakituri at Tuai Sub High winds
15013 | 13/10/2013 | 2013 | 2013-10-13 | 215 | 5 | 1075 | C | TREE CONTACTS | Replace 11kV pole G1382 hit by (Tree) Tauwhareparae Rd
15021 | 14/10/2013 | 2013 | 2013-10-14 | 17 | 170 | 2755 | C | ADVERSE WEATHER | Reclose CB24 at Tuai Sub High Winds
14996 | 15/10/2013 | 2013 | 2013-10-15 | 3 | 1077 | 3231 | C | DEFECTIVE EQUIPMENT | Repair Xarm on pole E2339 Hexton Puha 50kV line
14997 | 15/10/2013 | 2013 | 2013-10-15 | 10 | 479 | 4143 | C | TREE CONTACTS | Repair lines 50 kV pole J1832 Tikitiki
14998 | 15/10/2013 | 2013 | 2013-10-15 | 484 | 13 | 5644 | C | ADVERSE WEATHER | Repair 11kV lines between poles D3732 to D3734 Bushy Knoll
15001 | 15/10/2013 | 2013 | 2013-10-15 | 197 | 50 | 8970 | C | TREE CONTACTS | Cut 11kV jumpers pole D168 W/O Kuri
15004 | 15/10/2013 | 2013 | 2013-10-15 | 399 | 167 | 22632 | C | TREE CONTACTS | Repair 11kV lines pole E1706 Kanakanaia
15008 | 15/10/2013 | 2013 | 2013-10-15 | 257 | 419 | 42027 | C | TREE CONTACTS | Repair 11kV lines between poles F2304 & F2303 Matawai Rd
15009 | 15/10/2013 | 2013 | 2013-10-15 | 43 | 8 | 344 | C | ADVERSE WEATHER | Replace broken Stay on pole F767 Makaretu Rd
15010 | 15/10/2013 | 2013 | 2013-10-15 | 46 | 18 | 828 | C | ADVERSE WEATHER | Repair 11kV lines pole F2139 Te Wera Rd
15015 | 15/10/2013 | 2013 | 2013-10-15 | 505 | 73 | 25540 | C | TREE CONTACTS | Repair 11kv lines between poles H641 to H642 Ihungia Rd
15016 | 15/10/2013 | 2013 | 2013-10-15 | 103 | 5 | 515 | C | TREE CONTACTS | Remove tree from 11kV pole H188 Ihungia Rd
15022 | 15/10/2013 | 2013 | 2013-10-15 | 127 | 170 | 19728 | C | ADVERSE WEATHER | Reclose CB24 at Tuai Sub High Winds
14999 | 16/10/2013 | 2013 | 2013-10-16 | 127 | 13 | 1651 | C | ADVERSE WEATHER | Cut Jumpers pole D3998 Totangi Feeder pole down D3983
15014 | 16/10/2013 | 2013 | 2013-10-16 | 221 | 5 | 1105 | C | TREE CONTACTS | Replace 11kV pole G1351 Matanui Rd
15024 | 16/10/2013 | 2013 | 2013-10-16 | 227 | 11 | 2497 | C | DEFECTIVE EQUIPMENT | Repair 11 kV jumper pole W7357 Mangaroa
15002 | 17/10/2013 | 2013 | 2013-10-17 | 280 | 40 | 11200 | C | TREE CONTACTS | Repair 11kV lines pole D1214 Tiniroto Rd
15005 | 17/10/2013 | 2013 | 2013-10-17 | 85 | 9 | 765 | C | ADVERSE WEATHER | Repair 11kV lines pole E414 Tarndale Rd
15011 | 17/10/2013 | 2013 | 2013-10-17 | 98 | 20 | 1960 | C | ADVERSE WEATHER | Replace 11kV pole F2668 Motu Rd
15023 | 17/10/2013 | 2013 | 2013-10-17 | 239 | 8 | 1912 | C | TREE CONTACTS | Replace 11kV pole W7479 Hit by tree Eriptiti Rd
15025 | 17/10/2013 | 2013 | 2013-10-17 | 86 | 11 | 946 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W1804 Mangaroa Rd
15006 | 18/10/2013 | 2013 | 2013-10-18 | 189 | 226 | 8247 | C | TREE CONTACTS | Remove tree on line pole E2500 Ngakaroa Rd
15012 | 18/10/2013 | 2013 | 2013-10-18 | 220 | 13 | 2860 | C | TREE CONTACTS | Replace 2 11kV poles F2253 & D2250 Whakarau Rd
15032 | 20/10/2013 | 2013 | 2013-10-20 | 17 | 37 | 629 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J172 Tapuaeroa Rd
14991 | 23/10/2013 | 2013 | 2013-10-23 | 79 | 15 | 1185 | B | PLANNED SHUTDOWN | Install new T/x A899 Kaiti Hill
15033 | 23/10/2013 | 2013 | 2013-10-23 | 97 | 259 | 25123 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole J523 Hicks Bay Hit by truck
15034 | 23/10/2013 | 2013 | 2013-10-23 | 38 | 9 | 342 | C | TREE CONTACTS | Repair 11kV lines pole W3644 to W3640 Waihi
14993 | 24/10/2013 | 2013 | 2013-10-24 | 308 | 65 | 11812 | B | PLANNED SHUTDOWN | Install 3 DDO fuses pole C4964 Kings Rd
15035 | 25/10/2013 | 2013 | 2013-10-25 | 340 | 216 | 54468 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W9416 Mahia
15036 | 25/10/2013 | 2013 | 2013-10-25 | 756 | 583 | 38258 | C | TREE CONTACTS | Repair 11kV lines pole H2266 Tokomaru Bay
15037 | 26/10/2013 | 2013 | 2013-10-26 | 114 | 1177 | 24037 | C | TREE CONTACTS | Repair 11kV line pole D41 Wharekopae Rd Ngatapa
15038 | 29/10/2013 | 2013 | 2013-10-29 | 173 | 424 | 14808 | C | TREE CONTACTS | Remove tree from 11kV pole D1646 Lavenham Rd
15039 | 29/10/2013 | 2013 | 2013-10-29 | 852 | 76 | 22952 | C | TREE CONTACTS | Repair 11kV lines pole E1581 Armstrong Rd
14988 | 30/10/2013 | 2013 | 2013-10-30 | 424 | 47 | 19928 | B | PLANNED SHUTDOWN | Replace 11kV poles J1188 J1189 J1191 Rangitukia
14992 | 30/10/2013 | 2013 | 2013-10-30 | 400 | 15 | 6000 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting J260 Waiomatini Rd
15040 | 30/10/2013 | 2013 | 2013-10-30 | 178 | 72 | 12816 | C | FOREIGN INTERFERENCE | Remove cable from 11kV pole J2065 Rangitukia Rd
14994 | 31/10/2013 | 2013 | 2013-10-31 | 275 | 4 | 1100 | B | PLANNED SHUTDOWN | Change T/x C413 Bushmere Rd
15041 | 01/11/2013 | 2013 | 2013-11-01 | 12 | 176 | 2112 | C | DEFECTIVE EQUIPMENT | Repair PMR J1078 Rangitukia Rd
15061 | 04/11/2013 | 2013 | 2013-11-04 | 24 | 71 | 2880 | B | PLANNED SHUTDOWN | Replace 11kV poles F89 F99 F100 Motu Rd
15062 | 05/11/2013 | 2013 | 2013-11-05 | 410 | 12 | 4920 | B | PLANNED SHUTDOWN | Replace 11kV poles E2559 E2561 E2865 Ford Rd
15066 | 05/11/2013 | 2013 | 2013-11-05 | 95 | 80 | 2516 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting D409 Ingram Rd
15042 | 07/11/2013 | 2013 | 2013-11-07 | 263 | 90 | 10255 | C | DEFECTIVE EQUIPMENT | Replace Xarm pole G4237 Parkinson St Tolaga Bay
15043 | 07/11/2013 | 2013 | 2013-11-07 | 263 | 25 | 2389 | C | TREE CONTACTS | Repair 11kV lines pole E3872 Ngakaroa Rd
15064 | 07/11/2013 | 2013 | 2013-11-07 | 387 | 38 | 14706 | B | PLANNED SHUTDOWN | Replace 11kV poles J314 J310 Te Araroa Rd
15068 | 07/11/2013 | 2013 | 2013-11-07 | 427 | 11 | 8539 | B | PLANNED SHUTDOWN | Replace poles F1504 F1507 F1513 Whakarau Rd
15044 | 08/11/2013 | 2013 | 2013-11-08 | 200 | 9 | 1800 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole G4237 Parkinson St
15045 | 08/11/2013 | 2013 | 2013-11-08 | 175 | 49 | 4003 | C | FOREIGN INTERFERENCE | Replace 11kV pole D2568 Pehiri Rd Hit by tractor
15046 | 11/11/2013 | 2013 | 2013-11-11 | 90 | 18 | 1620 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole G1848 Paramata Rd
15047 | 11/11/2013 | 2013 | 2013-11-11 | 153 | 73 | 11169 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole W6559 Mangapoikie Rd
15048 | 12/11/2013 | 2013 | 2013-11-12 | 17 | 13 | 221 | C | DEFECTIVE EQUIPMENT | Replace centre bolt on pole C5842 Mc Donalds Rd
15049 | 12/11/2013 | 2013 | 2013-11-12 | 36 | 15 | 540 | C | DEFECTIVE EQUIPMENT | Fit Stay on 11kV pole D2569 Pehiri Rd
15050 | 12/11/2013 | 2013 | 2013-11-12 | 612 | 44 | 26704 | C | DEFECTIVE EQUIPMENT | Replace insulator on 11kV pole W4804 Ruapapa Rd
15065 | 12/11/2013 | 2013 | 2013-11-12 | 130 | 25 | 3250 | B | PLANNED SHUTDOWN | Replace 11kV poles G2140 G1676 G2196 Paroa Rd
15051 | 13/11/2013 | 2013 | 2013-11-13 | 686 | 64 | 43904 | C | TREE CONTACTS | Repair 11kV lines pole G2018 Tauwharparae Rd
15067 | 14/11/2013 | 2013 | 2013-11-14 | 289 | 225 | 22640 | B | PLANNED SHUTDOWN | Replace 11kV pole J270 Onepoto Hicks Bay
15052 | 19/11/2013 | 2013 | 2013-11-19 | 141 | 48 | 6768 | C | DEFECTIVE EQUIPMENT | Replace 11kV fuses W298 Mc Lean St
15063 | 20/11/2013 | 2013 | 2013-11-20 | 196 | 33 | 6468 | B | PLANNED SHUTDOWN | Replace 11kV poles J2159 J2162 J2168 J2175 Maraehara Rd
15069 | 21/11/2013 | 2013 | 2013-11-21 | 24 | 41 | 1722 | B | PLANNED SHUTDOWN | Replace 11kV poles beyond J447 Rangitukia Rd
15053 | 22/11/2013 | 2013 | 2013-11-22 | 20 | 21 | 420 | C | TREE CONTACTS | Rejoin jumpers pole W82 Waihua Valley after tree felling
15070 | 24/11/2013 | 2013 | 2013-11-24 | 231 | 12 | 2772 | B | PLANNED SHUTDOWN | Install SW GR B279 B280 B281 Logan Print Grey St
15071 | 25/11/2013 | 2013 | 2013-11-25 | 432 | 56 | 46312 | B | PLANNED SHUTDOWN | Reconductor 11kV lines B4017 to B4028 Aberdeen Rd
15054 | 27/11/2013 | 2013 | 2013-11-27 | 452 | 53 | 16736 | C | DEFECTIVE EQUIPMENT | Replace faulty T/X W326 Cricklewood Rd
15072 | 27/11/2013 | 2013 | 2013-11-27 | 241 | 76 | 18316 | B | PLANNED SHUTDOWN | Upgrade 11kV cable between B927 to B928 Pine St
15169 | 27/11/2013 | 2013 | 2013-11-27 | 122 | 37 | 3750 | B | PLANNED SHUTDOWN | Replace 11kV poles G1327 G1705 G1706 G1707 Tauwhareparae Rd
15055 | 29/11/2013 | 2013 | 2013-11-29 | 36 | 49 | 1764 | C | DEFECTIVE EQUIPMENT | Isolate 11kV to change 50kV insulators poles W4565 W4810 W4830 & W4731 Ruapapa & Cricklewood Rds
15056 | 29/11/2013 | 2013 | 2013-11-29 | 226 | 17 | 3842 | C | TREE CONTACTS | Isolate 11kV lines between H285 to H302 Waiapu Rd Tokomaru Bay
15060 | 29/11/2013 | 2013 | 2013-12-29 | 139 | 183 | 8180 | C | TREE CONTACTS | Repair 11kV lines pole W5886 Putere Rd
15073 | 29/11/2013 | 2013 | 2013-11-29 | 330 | 6 | 1980 | B | PLANNED SHUTDOWN | Replace T/x pole F366 Taihimiti St Whatatutu
15057 | 30/11/2013 | 2013 | 2013-11-30 | 46 | 11 | 770 | C | DEFECTIVE EQUIPMENT | Cut & rejoin jumpers pole D4106 Russells Rd to replace Private pole D5479
15058 | 30/11/2013 | 2013 | 2013-11-30 | 372 | 43 | 1836 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W634 Putere Rd
15059 | 30/11/2013 | 2013 | 2013-11-30 | 933 | 27 | 25191 | C | TREE CONTACTS | Repair 11kV lines pole G2381 Tauwhareparae Rd
15074 | 03/12/2013 | 2013 | 2013-12-03 | 348 | 4 | 1392 | B | PLANNED SHUTDOWN | replace TX D331
15075 | 05/12/2013 | 2013 | 2013-12-05 | 325 | 22 | 7150 | B | PLANNED SHUTDOWN | Replace pole D4956
15089 | 05/12/2013 | 2013 | 2013-12-05 | 23 | 12 | 276 | C | DEFECTIVE EQUIPMENT | Cut jumpers to replace pole D6163
15076 | 06/12/2013 | 2013 | 2013-12-06 | 241 | 80 | 19280 | B | PLANNED SHUTDOWN | Replace GM TX A320
15077 | 09/12/2013 | 2013 | 2013-12-09 | 426 | 55 | 24748 | B | PLANNED SHUTDOWN | Pole changing Brunton Rd
15078 | 10/12/2013 | 2013 | 2013-12-10 | 422 | 43 | 8993 | B | PLANNED SHUTDOWN | Reconductor 11kV H201 - H315
15079 | 12/12/2013 | 2013 | 2013-12-12 | 308 | 33 | 10164 | B | PLANNED SHUTDOWN | Replace poles J341, J2179, J2192
15080 | 13/12/2013 | 2013 | 2013-12-13 | 130 | 14 | 1820 | B | PLANNED SHUTDOWN | Replace TX B76
15091 | 15/12/2013 | 2013 | 2013-12-15 | 41 | 18 | 738 | C | FOREIGN INTERFERENCE | Stay wire hit by tractor A3423
15081 | 16/12/2013 | 2013 | 2013-12-16 | 370 | 19 | 7030 | B | PLANNED SHUTDOWN | Replace TX pole W8357
15082 | 17/12/2013 | 2013 | 2013-12-17 | 278 | 10 | 2780 | B | PLANNED SHUTDOWN | Replace TX & pole G3010
15084 | 17/12/2013 | 2013 | 2013-12-17 | 252 | 114 | 27869 | B | PLANNED SHUTDOWN | Replace poles G1705, G1706, G1707
15090 | 17/12/2013 | 2013 | 2013-12-17 | 14 | 48 | 658 | C | LIGHTNING | Isolate to change 11kV GM fuse W298
15092 | 17/12/2013 | 2013 | 2013-12-17 | 16 | 5 | 305 | C | TREE CONTACTS | tree cutting J341
15085 | 18/12/2013 | 2013 | 2013-12-18 | 243 | 47 | 11421 | B | PLANNED SHUTDOWN | Replace pole J1184 J1238 J1242
15093 | 18/12/2013 | 2013 | 2013-12-18 | 80 | 13 | 1040 | C | LIGHTNING | Repair blown jumper at D3075
15094 | 18/12/2013 | 2013 | 2013-12-18 | 349 | 9 | 3141 | C | LIGHTNING | Tree hit by lightening - contacted line
15083 | 19/12/2013 | 2013 | 2013-12-19 | 28 | 30 | 840 | B | PLANNED SHUTDOWN | Install TX fuses on G198
15086 | 19/12/2013 | 2013 | 2013-12-19 | 304 | 46 | 13984 | B | PLANNED SHUTDOWN | Tree cutting H285 - H73
15087 | 19/12/2013 | 2013 | 2013-12-19 | 203 | 139 | 28217 | B | PLANNED SHUTDOWN | Maint/repair ABS A244
15088 | 19/12/2013 | 2013 | 2013-12-19 | 260 | 48 | 12450 | B | PLANNED SHUTDOWN | Replace pole E1063 E648
15095 | 20/12/2013 | 2013 | 2013-12-20 | 59 | 14 | 826 | C | LIGHTNING | Replace blown fuse holder at D593
15096 | 20/12/2013 | 2013 | 2013-12-20 | 91 | 7 | 637 | C | LIGHTNING | lightening damaged fuses at H190
15097 | 30/12/2013 | 2013 | 2013-12-30 | 114 | 73 | 8282 | C | DEFECTIVE EQUIPMENT | Slack span at W1019
15098 | 31/12/2013 | 2013 | 2013-12-31 | 111 | 73 | 8103 | C | DEFECTIVE EQUIPMENT | Repair jumpers at ABS W1019
15099 | 31/12/2013 | 2013 | 2013-12-31 | 8 | 1802 | 14416 | C | UNKNOWN | 50kV CB 31 E/F trip - unknow, suspect vandala
15102 | 03/01/2014 | 2013 | 2014-01-03 | 190 | 75 | 7572 | C | TREE CONTACTS | Repair 11kV lines pole C605 Papatu Rd
15103 | 04/01/2014 | 2013 | 2014-01-04 | 130 | 29 | 3770 | C | DEFECTIVE EQUIPMENT | Replace Xarm pole H1081 Mata Rd
15129 | 05/01/2014 | 2013 | 2014-01-05 | 1085 | 699 | 138471 | C | TREE CONTACTS | Repair 11kV lines pole W4282 Frasertown (Trees)
15104 | 06/01/2014 | 2013 | 2014-01-06 | 527 | 17 | 8359 | C | TREE CONTACTS | Replace 11kV pole D2048 Lake Rd (Tree)
15113 | 06/01/2014 | 2013 | 2014-01-06 | 310 | 3 | 930 | B | PLANNED SHUTDOWN | Isolate 11kV lines Between C271 to C637 Makaraka for tree cutting
15105 | 07/01/2014 | 2013 | 2014-01-07 | 167 | 152 | 18891 | C | TREE CONTACTS | Repair 11kV lines between poles G1799 to G164 Tauwhareparae Rd
15106 | 08/01/2014 | 2013 | 2014-01-08 | 309 | 325 | 80922 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W5994 Awamate
15114 | 08/01/2014 | 2013 | 2014-01-08 | 334 | 47 | 15687 | B | PLANNED SHUTDOWN | Replace 11kV poles J1242 J1934 J2179 Rangitukia
15115 | 09/01/2014 | 2013 | 2014-01-09 | 441 | 36 | 8390 | B | PLANNED SHUTDOWN | Replace 11kV H pole H3983 Waione Rd
15116 | 10/01/2014 | 2013 | 2014-01-10 | 23 | 29 | 667 | B | PLANNED SHUTDOWN | Install DDO fuses pole J834 Te Araroa Rd
15107 | 12/01/2014 | 2013 | 2014-01-12 | 57 | 117 | 6669 | C | FOREIGN INTERFERENCE | Check T/x B386 Elgin Shops hit by car and top up oil
15108 | 14/01/2014 | 2013 | 2014-01-14 | 382 | 29 | 11078 | C | TREE CONTACTS | Repair lines pole H1208 Mata Rd
15117 | 14/01/2014 | 2013 | 2014-01-14 | 366 | 17 | 6222 | B | PLANNED SHUTDOWN | Isolate 11kV lines between poles H285 and H73 Waiapu Rd for tree cutting
15120 | 15/01/2014 | 2013 | 2014-01-15 | 512 | 51 | 16852 | B | PLANNED SHUTDOWN | Replace 11kV poles J2808 J2804 Kopuapounamu Rd
15118 | 16/01/2014 | 2013 | 2014-01-16 | 364 | 14 | 5096 | B | PLANNED SHUTDOWN | Replace 11kV poles J3011 J3012 Whakaangiangi Rd
15119 | 16/01/2014 | 2013 | 2014-01-16 | 449 | 38 | 4445 | B | PLANNED SHUTDOWN | Replace 11kV ples C2205 C2208 C2209 Main Rd Makaraka
15121 | 21/01/2014 | 2013 | 2014-01-21 | 478 | 35 | 16730 | B | PLANNED SHUTDOWN | Replace 11kV poles C2201 C2204 C2205 Kipling Rd
15122 | 22/01/2014 | 2013 | 2014-01-22 | 426 | 424 | 173586 | B | PLANNED SHUTDOWN | Replace ABSs W979 W975 W813 Frasertown
15123 | 24/01/2014 | 2013 | 2014-01-24 | 410 | 4 | 1640 | B | PLANNED SHUTDOWN | Replace 11kV poles W4516 W4517 W4518 Mc Donald Rd Wairoa
15124 | 24/01/2014 | 2013 | 2014-01-24 | 421 | 31 | 13051 | B | PLANNED SHUTDOWN | Replace 11kV poles C244 C2223 C2213 Main Rd Makara
15109 | 25/01/2014 | 2013 | 2014-01-25 | 810 | 61 | 13073 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A4035 Waiomoko Rd
15125 | 29/01/2014 | 2013 | 2014-01-29 | 504 | 35 | 15816 | B | PLANNED SHUTDOWN | Remove line breaks pole C2210 Main Rd Makaraka
15110 | 30/01/2014 | 2013 | 2014-01-30 | 641 | 118 | 20495 | C | TREE CONTACTS | Repair 11kV lines Between poles C3598 to C3599 Maraetaha
15111 | 30/01/2014 | 2013 | 2014-01-30 | 80 | 24 | 1920 | C | DEFECTIVE EQUIPMENT | Replace DDO fuses T/x J183 East Cape Rd
15112 | 30/01/2014 | 2013 | 2014-01-30 | 201 | 151 | 10792 | C | TREE CONTACTS | Repair 11kV lines pole W8132 Otiki Stn Nuhaka
15126 | 30/01/2014 | 2013 | 2014-01-31 | 236 | 9 | 2124 | B | PLANNED SHUTDOWN | Replace T/x W1545 The Cresent Wairoa
15128 | 30/01/2014 | 2013 | 2014-01-30 | 371 | 12 | 4452 | B | PLANNED SHUTDOWN | Replace 11kV poles E1301 E1303 Waimata Valley Rd
15127 | 31/01/2014 | 2013 | 2014-01-31 | 309 | 50 | 11562 | B | PLANNED SHUTDOWN | Replace 11kV poles J336 J2212 Kopuapouamu Rd
15131 | 01/02/2014 | 2013 | 2014-02-01 | 258 | 76 | 15342 | C | TREE CONTACTS | Replace strain insulator on pole H72 Makarika
15132 | 01/02/2014 | 2013 | 2014-02-01 | 23 | 17 | 373 | C | TREE CONTACTS | Isolate 11kv lines ABS H142 customer to cut trees (Private) Ihungia Rd
15148 | 04/02/2014 | 2013 | 2014-02-04 | 278 | 20 | 5560 | B | PLANNED SHUTDOWN | Replace 11kV poles J2437 & ABS pole J240 Tikitiki
15149 | 04/02/2014 | 2013 | 2014-02-04 | 119 | 23 | 2737 | B | PLANNED SHUTDOWN | Replace T/x W625 Carroll St Frasertown
15151 | 06/02/2014 | 2013 | 2014-02-06 | 176 | 18 | 3168 | B | PLANNED SHUTDOWN | Replace 11kV poles J2397 J2402 J2407 Te Hue Rd
15133 | 07/02/2014 | 2013 | 2014-02-07 | 37 | 37 | 1369 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W991 Ohuka
15134 | 08/02/2014 | 2013 | 2014-02-08 | 330 | 14 | 4620 | C | FOREIGN INTERFERENCE | Replace 11kV pole D3556 hit by lightining Tiniroto
15135 | 09/02/2014 | 2013 | 2014-02-09 | 36 | 25 | 900 | C | DEFECTIVE EQUIPMENT | Replace 11kV Isolation fuse A153 Tatapouri (Lightining)
15136 | 09/02/2014 | 2013 | 2014-02-09 | 240 | 88 | 10202 | C | TREE CONTACTS | Repair 11kV lines pole D3636 Ruakaka Rd
15137 | 09/02/2014 | 2013 | 2014-02-09 | 628 | 68 | 9287 | C | TREE CONTACTS | Repair 11kV lines pole H2227 Waipiro Bay
15138 | 09/02/2014 | 2013 | 2014-02-09 | 26 | 947 | 17068 | C | LIGHTNING | Replace 33kV pole W3793 Tahaenui hit by Lightining
15139 | 10/02/2014 | 2013 | 2014-02-10 | 156 | 54 | 5334 | C | TREE CONTACTS | Repair 11kV lines between poles A3913 to A3918 Waiomoko
15150 | 11/02/2014 | 2013 | 2014-02-11 | 564 | 92 | 8018 | B | PLANNED SHUTDOWN | Replace 50kV pole G2605 Uawa Parade Tolaga
15147 | 12/02/2014 | 2013 | 2014-02-12 | 561 | 129 | 13812 | B | PLANNED SHUTDOWN | Replace 11 kV pole G1327 Tauwhareparae Rd
15140 | 13/02/2014 | 2013 | 2014-02-13 | 97 | 743 | 19556 | C | FOREIGN INTERFERENCE | Repair 11kV lines between poles C4933 to C4932 Tuckers Rd
15146 | 13/02/2014 | 2013 | 2014-02-13 | 19 | 331 | 6289 | B | PLANNED SHUTDOWN | Replace T/x pole W136 Morere
15153 | 13/02/2014 | 2013 | 2014-02-13 | 317 | 160 | 9820 | B | PLANNED SHUTDOWN | Replace 11kV pole J2860 & T/x 36 Tikitiki
15141 | 17/02/2014 | 2013 | 2014-02-17 | 321 | 153 | 13068 | C | ADVERSE WEATHER | Reposition 2 -11kV poles G1588 & G1589 Tauwhareparae Rd river washout
15143 | 18/02/2014 | 2013 | 2014-02-18 | 5 | 175 | 1575 | B | PLANNED SHUTDOWN | Replace protection relays CB A473 Hershell Rd at Kaiti Sub
15152 | 18/02/2014 | 2013 | 2014-02-18 | 12 | 6 | 114 | B | PLANNED SHUTDOWN | Relocate 11kV pole W7669 Mahia
15156 | 18/02/2014 | 2013 | 2014-02-18 | 380 | 25 | 6170 | B | PLANNED SHUTDOWN | Replace 11kV poles G2140 G2139 G2138 Paroa Rd
15142 | 19/02/2014 | 2013 | 2014-02-19 | 115 | 29 | 3335 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W5357 Kotiemaori
15155 | 19/02/2014 | 2013 | 2014-02-19 | 516 | 35 | 15514 | B | PLANNED SHUTDOWN | Replace 11kV poles beyond pole H4118 Ihungia Rd
15157 | 20/02/2014 | 2013 | 2014-02-20 | 285 | 25 | 4581 | B | PLANNED SHUTDOWN | Replace 11kV poles G2196 G2197 G2198 Paroa Rd
15158 | 20/02/2014 | 2013 | 2014-02-20 | 445 | 35 | 15172 | B | PLANNED SHUTDOWN | Replace 11kV pole beyond H187 Ihungia Rd
15145 | 21/02/2014 | 2013 | 2014-02-21 | 43 | 93 | 3999 | B | PLANNED SHUTDOWN | Install stay on pole B1147 Balance St
15154 | 23/02/2014 | 2013 | 2014-02-23 | 435 | 244 | 69773 | B | PLANNED SHUTDOWN | Replace 11kV pole B110 & T/x B386 Elgin Lane
15144 | 26/02/2014 | 2013 | 2014-02-26 | 340 | 115 | 12581 | B | PLANNED SHUTDOWN | Replace 11kV poles J2159 J2175 J341 Maraehara
15170 | 01/03/2014 | 2013 | 2014-03-01 | 334 | 226 | 13269 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole E75 Kaiteratahi
15171 | 01/03/2014 | 2013 | 2014-03-01 | 59 | 19 | 1031 | C | UNKNOWN | Reclose CB C15 Matawhero Sub cause unknown
15172 | 04/03/2014 | 2013 | 2014-03-04 | 39 | 1528 | 42964 | C | UNKNOWN | Reclose CB A616 Crawford Rd cause unknown
15197 | 04/03/2014 | 2013 | 2014-03-04 | 61 | 7 | 581 | B | PLANNED SHUTDOWN | Replace 11kV poles F2083 & F2085 Whakarau Rd
15198 | 04/03/2014 | 2013 | 2014-03-04 | 467 | 23 | 7121 | B | PLANNED SHUTDOWN | Replace 11kV poles D468 D4001 D4000 Totangi Rd
15173 | 05/03/2014 | 2013 | 2014-03-05 | 32 | 1022 | 24053 | C | UNKNOWN | Reclose CB C95 Haisman Rd cause unknown
15199 | 05/03/2014 | 2013 | 2014-03-05 | 274 | 10 | 2740 | B | PLANNED SHUTDOWN | Replace 11kV poles G2198 G2215 Mangatuna Rd
15174 | 06/03/2014 | 2013 | 2014-03-06 | 87 | 696 | 20540 | C | TREE CONTACTS | Repair 11kV lines pole A248 Kaiti Hill
15175 | 06/03/2014 | 2013 | 2014-03-06 | 59 | 12 | 708 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W7976 Omana Rd
15176 | 06/03/2014 | 2013 | 2014-03-06 | 136 | 744 | 16926 | C | FOREIGN INTERFERENCE | Replace 11kV pole C5037 Crn SH2 & Pilmers Rd
15177 | 07/03/2014 | 2013 | 2014-03-07 | 429 | 120 | 34047 | C | TREE CONTACTS | Repair 11kV lines pole W20494 Papuni
15178 | 07/03/2014 | 2013 | 2014-03-07 | 46 | 1801 | 60730 | C | UNKNOWN | Reclose CB 31 at Parkinson St Sub cause unknown
15179 | 07/03/2014 | 2013 | 2014-03-07 | 769 | 243 | 45572 | C | FOREIGN INTERFERENCE | Replace 11kV pole G337 Monkhouse St Tolaga Bay hit by car
15180 | 11/03/2014 | 2013 | 2014-03-11 | 316 | 591 | 19409 | C | DEFECTIVE EQUIPMENT | Replace Sw GR W242 W243 W244 Black St Wairoa
15200 | 11/03/2014 | 2013 | 2014-03-11 | 430 | 33 | 14190 | B | PLANNED SHUTDOWN | Replace 11kV pole W23526 Haliburton Rd
15201 | 13/03/2014 | 2013 | 2014-03-13 | 416 | 47 | 19552 | B | PLANNED SHUTDOWN | Replace 11kV poles J1238 J1242 J1934 Rangitukia
15203 | 14/03/2014 | 2013 | 2014-03-14 | 352 | 33 | 11616 | B | PLANNED SHUTDOWN | Replace 11kV poles J341 J2159 Maraehara Rd
15182 | 15/03/2014 | 2013 | 2014-03-15 | 392 | 71 | 11725 | C | TREE CONTACTS | Repair 11kV lines pole G1076 Mata Rd
15184 | 15/03/2014 | 2013 | 2014-03-15 | 5 | 2510 | 10651 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
15181 | 16/03/2014 | 2013 | 2014-03-16 | 27 | 30 | 780 | C | TREE CONTACTS | Isolate 11kV lines pole G6036 Sheltons Rd Tolaga Bay
15183 | 16/03/2014 | 2013 | 2014-03-16 | 1275 | 21 | 9240 | C | TREE CONTACTS | Repair 11kV lines pole J4439 Waione Rd
15185 | 16/03/2014 | 2013 | 2014-03-16 | 807 | 63 | 36541 | C | TREE CONTACTS | Repair 11kV lines poles H2230 to H2231 Waipiro Bay
15186 | 16/03/2014 | 2013 | 2014-03-16 | 295 | 48 | 14160 | C | TREE CONTACTS | Repair 11kV lines pole G2330 Tauwhareparae Rd
15187 | 16/03/2014 | 2013 | 2014-03-16 | 145 | 59 | 4972 | C | TREE CONTACTS | Repair 11kV lines pole F1200 to F1161 Otoko
15188 | 17/03/2014 | 2013 | 2014-03-17 | 354 | 61 | 14867 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A3685 Panikau Rd
15189 | 17/03/2014 | 2013 | 2014-03-17 | 106 | 31 | 3353 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H1076 Mata Rd
15190 | 20/03/2014 | 2013 | 2014-03-20 | 369 | 25 | 3505 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole D1869 Ngatapa
15202 | 20/03/2014 | 2013 | 2014-03-20 | 427 | 8 | 7296 | B | PLANNED SHUTDOWN | Replace 11kV poles H565 H566 H562 H889 SH35 Waiapu Rd
15191 | 22/03/2014 | 2013 | 2014-03-22 | 154 | 343 | 19602 | C | DEFECTIVE EQUIPMENT | Replace shackle insulator pole J802 Tikitiki
15205 | 26/03/2014 | 2013 | 2014-03-26 | 162 | 47 | 7614 | B | PLANNED SHUTDOWN | Replace 11kV poles J1242 J250 J1934 Rangitukia Rd
15204 | 27/03/2014 | 2013 | 2014-03-27 | 420 | 7 | 2940 | B | PLANNED SHUTDOWN | Replace 11kV pole F1687 Motuhora Rd
15206 | 27/03/2014 | 2013 | 2014-03-27 | 405 | 33 | 13365 | B | PLANNED SHUTDOWN | Replace 11kV poles J341 J2159 Maraehara Rd
15192 | 28/03/2014 | 2013 | 2014-03-28 | 274 | 131 | 29460 | C | DEFECTIVE EQUIPMENT | Replace 2 11kV insulators T/X pole W610 Crosshills
15193 | 30/03/2014 | 2013 | 2014-03-30 | 523 | 424 | 17528 | C | FOREIGN INTERFERENCE | Replace 11kV pole E1341 Kaiteratahi Hit by truck
15194 | 31/03/2014 | 2013 | 2014-03-31 | 173 | 32 | 4120 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole D1057 Parikanapa Rd

## 20132014DailyTotals
Date Outage | YEAR | Duration of Outage | Customers Impacted | Total Customer Minutes Lost
02/04/2013 | 2013 | 27 | 67 | 1809
03/04/2013 | 2013 | 110 | 25 | 2750
04/04/2013 | 2013 | 343 | 544 | 16903
05/04/2013 | 2013 | 71 | 65 | 3075
06/04/2013 | 2013 | 267 | 360 | 26940
07/04/2013 | 2013 | 410 | 208 | 21594
08/04/2013 | 2013 | 362 | 37 | 3836
09/04/2013 | 2013 | 375 | 1500 | 6825
10/04/2013 | 2013 | 438 | 46 | 16275
11/04/2013 | 2013 | 179 | 480 | 31024
12/04/2013 | 2013 | 332 | 90 | 9762
13/04/2013 | 2013 | 430 | 16 | 2768
15/04/2013 | 2013 | 200 | 861 | 25390
17/04/2013 | 2013 | 304 | 25 | 7780
18/04/2013 | 2013 | 1491 | 102 | 60215
19/04/2013 | 2013 | 437 | 157 | 19577
22/04/2013 | 2013 | 579 | 11 | 3002
24/04/2013 | 2013 | 357 | 108 | 23358
27/04/2013 | 2013 | 368 | 48 | 11952
28/04/2013 | 2013 | 189 | 1186 | 47475
01/05/2013 | 2013 | 343 | 48 | 6003
02/05/2013 | 2013 | 105 | 1989 | 55012
03/05/2013 | 2013 | 387 | 80 | 20621
04/05/2013 | 2013 | 270 | 84 | 4148
05/05/2013 | 2013 | 1173 | 29 | 3783
06/05/2013 | 2013 | 338 | 48 | 5698
07/05/2013 | 2013 | 512 | 1079 | 37922
08/05/2013 | 2013 | 884 | 500 | 115366
09/05/2013 | 2013 | 370 | 30 | 3083
10/05/2013 | 2013 | 374 | 44 | 6248
11/05/2013 | 2013 | 170 | 419 | 29509
15/05/2013 | 2013 | 413 | 121 | 26219
16/05/2013 | 2013 | 58 | 77 | 4466
17/05/2013 | 2013 | 450 | 77 | 33912
20/05/2013 | 2013 | 49 | 259 | 12691
21/05/2013 | 2013 | 439 | 48 | 7806
22/05/2013 | 2013 | 478 | 48 | 8768
27/05/2013 | 2013 | 452 | 1193 | 34758
29/05/2013 | 2013 | 486 | 309 | 11586
31/05/2013 | 2013 | 240 | 48 | 11520
05/06/2013 | 2013 | 918 | 53 | 35875
06/06/2013 | 2013 | 439 | 490 | 61109
07/06/2013 | 2013 | 1245 | 253 | 86299
11/06/2013 | 2013 | 306 | 189 | 14214
12/06/2013 | 2013 | 126 | 91 | 6618
13/06/2013 | 2013 | 406 | 15 | 4133
15/06/2013 | 2013 | 121 | 234 | 19080
18/06/2013 | 2013 | 103 | 41 | 3067
19/06/2013 | 2013 | 67 | 307 | 5169
20/06/2013 | 2013 | 468 | 502 | 53128
21/06/2013 | 2013 | 1276 | 1464 | 102208
22/06/2013 | 2013 | 290 | 457 | 70949
24/06/2013 | 2013 | 259 | 83 | 10547
25/06/2013 | 2013 | 18 | 35 | 630
26/06/2013 | 2013 | 463 | 9 | 5490
28/06/2013 | 2013 | 406 | 325 | 63289
29/06/2013 | 2013 | 84 | 1957 | 92057
30/06/2013 | 2013 | 262 | 148 | 5368
02/07/2013 | 2013 | 489 | 102 | 15159
03/07/2013 | 2013 | 330 | 2278 | 58487
05/07/2013 | 2013 | 190 | 225 | 27552
09/07/2013 | 2013 | 358 | 113 | 15374
10/07/2013 | 2013 | 57 | 114 | 6498
11/07/2013 | 2013 | 228 | 184 | 9676
12/07/2013 | 2013 | 454 | 133 | 18517
13/07/2013 | 2013 | 884 | 89 | 15594
15/07/2013 | 2013 | 941 | 2497 | 74907
16/07/2013 | 2013 | 180 | 32 | 10771
17/07/2013 | 2013 | 280 | 57 | 14817
19/07/2013 | 2013 | 148 | 205 | 13235
20/07/2013 | 2013 | 202 | 73 | 14746
22/07/2013 | 2013 | 50 | 155 | 7750
23/07/2013 | 2013 | 120 | 728 | 50868
25/07/2013 | 2013 | 442 | 33 | 14589
26/07/2013 | 2013 | 156 | 15 | 2340
28/07/2013 | 2013 | 363 | 167 | 60621
29/07/2013 | 2013 | 318 | 6 | 1908
30/07/2013 | 2013 | 455 | 21 | 16779
01/08/2013 | 2013 | 330 | 54 | 17820
03/08/2013 | 2013 | 55 | 2510 | 94879
06/08/2013 | 2013 | 330 | 12 | 3960
08/08/2013 | 2013 | 248 | 81 | 20088
10/08/2013 | 2013 | 955 | 573 | 100826
11/08/2013 | 2013 | 2020 | 234 | 55059
13/08/2013 | 2013 | 29 | 274 | 7946
14/08/2013 | 2013 | 348 | 69 | 6894
15/08/2013 | 2013 | 372 | 1102 | 22038
16/08/2013 | 2013 | 368 | 36 | 7600
18/08/2013 | 2013 | 334 | 30 | 10020
19/08/2013 | 2013 | 223 | 235 | 40081
20/08/2013 | 2013 | 433 | 30 | 8166
21/08/2013 | 2013 | 420 | 68 | 20760
22/08/2013 | 2013 | 325 | 19 | 4243
23/08/2013 | 2013 | 360 | 456 | 27292
26/08/2013 | 2013 | 400 | 38 | 8040
28/08/2013 | 2013 | 317 | 38 | 12046
29/08/2013 | 2013 | 12 | 61 | 732
31/08/2013 | 2013 | 76 | 254 | 9911
03/09/2013 | 2013 | 350 | 206 | 27717
04/09/2013 | 2013 | 117 | 8 | 936
05/09/2013 | 2013 | 298 | 13 | 3874
06/09/2013 | 2013 | 330 | 24 | 5967
11/09/2013 | 2013 | 527 | 463 | 219408
12/09/2013 | 2013 | 1542 | 1212 | 487258
13/09/2013 | 2013 | 2489 | 1138 | 707104
14/09/2013 | 2013 | 4195 | 122 | 255216
15/09/2013 | 2013 | 1251 | 180 | 29299
17/09/2013 | 2013 | 281 | 64 | 7714
18/09/2013 | 2013 | 428 | 47 | 16712
19/09/2013 | 2013 | 88 | 1174 | 36333
20/09/2013 | 2013 | 55 | 66 | 3630
23/09/2013 | 2013 | 511 | 168 | 11263
25/09/2013 | 2013 | 834 | 180 | 56696
26/09/2013 | 2013 | 67 | 196 | 4672
28/09/2013 | 2013 | 130 | 107 | 6292
01/10/2013 | 2013 | 642 | 173 | 28757
02/10/2013 | 2013 | 520 | 139 | 67379
08/10/2013 | 2013 | 98 | 53 | 5194
09/10/2013 | 2013 | 58 | 34 | 1972
10/10/2013 | 2013 | 540 | 238 | 95620
11/10/2013 | 2013 | 756 | 430 | 261472
12/10/2013 | 2013 | 1025 | 955 | 180096
13/10/2013 | 2013 | 215 | 5 | 1075
14/10/2013 | 2013 | 0 | 170 | 2755
15/10/2013 | 2013 | 505 | 2479 | 133602
16/10/2013 | 2013 | 227 | 29 | 5253
17/10/2013 | 2013 | 280 | 88 | 16783
18/10/2013 | 2013 | 220 | 239 | 11107
20/10/2013 | 2013 | 17 | 37 | 629
23/10/2013 | 2013 | 97 | 283 | 26650
24/10/2013 | 2013 | 308 | 65 | 11812
25/10/2013 | 2013 | 756 | 799 | 92726
26/10/2013 | 2013 | 114 | 1177 | 24037
29/10/2013 | 2013 | 852 | 500 | 37760
30/10/2013 | 2013 | 424 | 134 | 38744
31/10/2013 | 2013 | 275 | 4 | 1100
01/11/2013 | 2013 | 12 | 176 | 2112
04/11/2013 | 2013 | 24 | 71 | 2880
05/11/2013 | 2013 | 410 | 92 | 7436
07/11/2013 | 2013 | 427 | 164 | 35889
08/11/2013 | 2013 | 200 | 58 | 5803
11/11/2013 | 2013 | 153 | 91 | 12789
12/11/2013 | 2013 | 612 | 97 | 30715
13/11/2013 | 2013 | 686 | 64 | 43904
14/11/2013 | 2013 | 289 | 225 | 22640
19/11/2013 | 2013 | 141 | 48 | 6768
20/11/2013 | 2013 | 196 | 33 | 6468
21/11/2013 | 2013 | 24 | 41 | 1722
22/11/2013 | 2013 | 20 | 21 | 420
24/11/2013 | 2013 | 231 | 12 | 2772
25/11/2013 | 2013 | 432 | 56 | 46312
27/11/2013 | 2013 | 452 | 166 | 38802
29/11/2013 | 2013 | 330 | 255 | 15766
30/11/2013 | 2013 | 933 | 81 | 27797
03/12/2013 | 2013 | 348 | 4 | 1392
05/12/2013 | 2013 | 325 | 34 | 7426
06/12/2013 | 2013 | 241 | 80 | 19280
09/12/2013 | 2013 | 426 | 55 | 24748
10/12/2013 | 2013 | 422 | 43 | 8993
12/12/2013 | 2013 | 308 | 33 | 10164
13/12/2013 | 2013 | 130 | 14 | 1820
15/12/2013 | 2013 | 41 | 18 | 738
16/12/2013 | 2013 | 370 | 19 | 7030
17/12/2013 | 2013 | 278 | 177 | 31612
18/12/2013 | 2013 | 349 | 69 | 15602
19/12/2013 | 2013 | 304 | 263 | 55491
20/12/2013 | 2013 | 91 | 21 | 1463
30/12/2013 | 2013 | 114 | 73 | 8282
31/12/2013 | 2013 | 111 | 1875 | 22519
03/01/2014 | 2013 | 190 | 75 | 7572
04/01/2014 | 2013 | 130 | 29 | 3770
05/01/2014 | 2013 | 1085 | 699 | 138471
06/01/2014 | 2013 | 527 | 20 | 9289
07/01/2014 | 2013 | 167 | 152 | 18891
08/01/2014 | 2013 | 334 | 372 | 96609
09/01/2014 | 2013 | 441 | 36 | 8390
10/01/2014 | 2013 | 23 | 29 | 667
12/01/2014 | 2013 | 57 | 117 | 6669
14/01/2014 | 2013 | 382 | 46 | 17300
15/01/2014 | 2013 | 512 | 51 | 16852
16/01/2014 | 2013 | 449 | 52 | 9541
21/01/2014 | 2013 | 478 | 35 | 16730
22/01/2014 | 2013 | 426 | 424 | 173586
24/01/2014 | 2013 | 421 | 35 | 14691
25/01/2014 | 2013 | 810 | 61 | 13073
29/01/2014 | 2013 | 504 | 35 | 15816
30/01/2014 | 2013 | 641 | 314 | 39783
31/01/2014 | 2013 | 309 | 50 | 11562
01/02/2014 | 2013 | 258 | 93 | 15715
04/02/2014 | 2013 | 278 | 43 | 8297
06/02/2014 | 2013 | 176 | 18 | 3168
07/02/2014 | 2013 | 37 | 37 | 1369
08/02/2014 | 2013 | 330 | 14 | 4620
09/02/2014 | 2013 | 628 | 1128 | 37457
10/02/2014 | 2013 | 156 | 54 | 5334
11/02/2014 | 2013 | 564 | 92 | 8018
12/02/2014 | 2013 | 561 | 129 | 13812
13/02/2014 | 2013 | 317 | 1234 | 35665
17/02/2014 | 2013 | 321 | 153 | 13068
18/02/2014 | 2013 | 380 | 206 | 7859
19/02/2014 | 2013 | 516 | 64 | 18849
20/02/2014 | 2013 | 445 | 60 | 19753
21/02/2014 | 2013 | 43 | 93 | 3999
23/02/2014 | 2013 | 435 | 244 | 69773
26/02/2014 | 2013 | 340 | 115 | 12581
01/03/2014 | 2013 | 334 | 245 | 14300
04/03/2014 | 2013 | 467 | 1558 | 50666
05/03/2014 | 2013 | 274 | 1032 | 26793
06/03/2014 | 2013 | 136 | 1452 | 38174
07/03/2014 | 2013 | 769 | 2164 | 140349
11/03/2014 | 2013 | 430 | 624 | 33599
13/03/2014 | 2013 | 416 | 47 | 19552
14/03/2014 | 2013 | 352 | 33 | 11616
15/03/2014 | 2013 | 392 | 2581 | 22376
16/03/2014 | 2013 | 1275 | 221 | 65693
17/03/2014 | 2013 | 354 | 92 | 18220
20/03/2014 | 2013 | 427 | 33 | 10801
22/03/2014 | 2013 | 154 | 343 | 19602
26/03/2014 | 2013 | 162 | 47 | 7614
27/03/2014 | 2013 | 420 | 40 | 16305
28/03/2014 | 2013 | 274 | 131 | 29460
30/03/2014 | 2013 | 523 | 424 | 17528
31/03/2014 | 2013 | 173 | 32 | 4120

## 20132014NormailsedDailyTotals
Date Outage | Year | TotAVG | Customers Impacted | Total Customer Minutes Lost | Saidi | Safi
02/04/2013 | 2013 | 25452 | 67 | 1809 | 0.071075 | 0.0026324
03/04/2013 | 2013 | 25452 | 25 | 2750 | 0.10805 | 0.00098224
04/04/2013 | 2013 | 25452 | 544 | 16903 | 0.66411 | 0.021374
05/04/2013 | 2013 | 25452 | 65 | 3075 | 0.12082 | 0.0025538
06/04/2013 | 2013 | 25452 | 360 | 26940 | 1.0585 | 0.014144
07/04/2013 | 2013 | 25452 | 208 | 21594 | 0.84842 | 0.0081722
08/04/2013 | 2013 | 25452 | 37 | 3836 | 0.15072 | 0.0014537
09/04/2013 | 2013 | 25452 | 1500 | 6825 | 0.26815 | 0.058934
10/04/2013 | 2013 | 25452 | 46 | 16275 | 0.63944 | 0.0018073
11/04/2013 | 2013 | 25452 | 480 | 31024 | 1.2189 | 0.018859
12/04/2013 | 2013 | 25452 | 90 | 9762 | 0.38355 | 0.0035361
13/04/2013 | 2013 | 25452 | 16 | 2768 | 0.10875 | 0.00062863
15/04/2013 | 2013 | 25452 | 861 | 25390 | 0.99756 | 0.033828
17/04/2013 | 2013 | 25452 | 25 | 7780 | 0.30567 | 0.00098224
18/04/2013 | 2013 | 25452 | 102 | 60215 | 2.3658 | 0.0040075
19/04/2013 | 2013 | 25452 | 157 | 19577 | 0.76917 | 0.0061685
22/04/2013 | 2013 | 25452 | 11 | 3002 | 0.11795 | 0.00043219
24/04/2013 | 2013 | 25452 | 108 | 23358 | 0.91773 | 0.0042433
27/04/2013 | 2013 | 25452 | 48 | 11952 | 0.46959 | 0.0018859
28/04/2013 | 2013 | 25452 | 1186 | 47475 | 1.8653 | 0.046598
01/05/2013 | 2013 | 25452 | 48 | 6003 | 0.23586 | 0.0018859
02/05/2013 | 2013 | 25452 | 1989 | 55012 | 2.1614 | 0.078147
03/05/2013 | 2013 | 25452 | 80 | 20621 | 0.81019 | 0.0031432
04/05/2013 | 2013 | 25452 | 84 | 4148 | 0.16297 | 0.0033003
05/05/2013 | 2013 | 25452 | 29 | 3783 | 0.14863 | 0.0011394
06/05/2013 | 2013 | 25452 | 48 | 5698 | 0.22387 | 0.0018859
07/05/2013 | 2013 | 25452 | 1079 | 37922 | 1.4899 | 0.042394
08/05/2013 | 2013 | 25452 | 500 | 115366 | 4.5327 | 0.019645
09/05/2013 | 2013 | 25452 | 30 | 3083 | 0.12113 | 0.0011787
10/05/2013 | 2013 | 25452 | 44 | 6248 | 0.24548 | 0.0017287
11/05/2013 | 2013 | 25452 | 419 | 29509 | 1.1594 | 0.016462
15/05/2013 | 2013 | 25452 | 121 | 26219 | 1.0301 | 0.004754
16/05/2013 | 2013 | 25452 | 77 | 4466 | 0.17547 | 0.0030253
17/05/2013 | 2013 | 25452 | 77 | 33912 | 1.3324 | 0.0030253
20/05/2013 | 2013 | 25452 | 259 | 12691 | 0.49862 | 0.010176
21/05/2013 | 2013 | 25452 | 48 | 7806 | 0.30669 | 0.0018859
22/05/2013 | 2013 | 25452 | 48 | 8768 | 0.34449 | 0.0018859
27/05/2013 | 2013 | 25452 | 1193 | 34758 | 1.3656 | 0.046873
29/05/2013 | 2013 | 25452 | 309 | 11586 | 0.45521 | 0.01214
31/05/2013 | 2013 | 25452 | 48 | 11520 | 0.45262 | 0.0018859
05/06/2013 | 2013 | 25452 | 53 | 35875 | 1.4095 | 0.0020824
06/06/2013 | 2013 | 25452 | 490 | 61109 | 2.401 | 0.019252
07/06/2013 | 2013 | 25452 | 253 | 86299 | 3.3907 | 0.0099403
11/06/2013 | 2013 | 25452 | 189 | 14214 | 0.55846 | 0.0074257
12/06/2013 | 2013 | 25452 | 91 | 6618 | 0.26002 | 0.0035754
13/06/2013 | 2013 | 25452 | 15 | 4133 | 0.16238 | 0.00058934
15/06/2013 | 2013 | 25452 | 234 | 19080 | 0.74965 | 0.0091938
18/06/2013 | 2013 | 25452 | 41 | 3067 | 0.1205 | 0.0016109
19/06/2013 | 2013 | 25452 | 307 | 5169 | 0.20309 | 0.012062
20/06/2013 | 2013 | 25452 | 502 | 53128 | 2.0874 | 0.019723
21/06/2013 | 2013 | 25452 | 1464 | 102208 | 4.0157 | 0.05752
22/06/2013 | 2013 | 25452 | 457 | 70949 | 2.7876 | 0.017955
24/06/2013 | 2013 | 25452 | 83 | 10547 | 0.41439 | 0.003261
25/06/2013 | 2013 | 25452 | 35 | 630 | 0.024752 | 0.0013751
26/06/2013 | 2013 | 25452 | 9 | 5490 | 0.2157 | 0.00035361
28/06/2013 | 2013 | 25452 | 325 | 63289 | 2.4866 | 0.012769
29/06/2013 | 2013 | 25452 | 1957 | 92057 | 3.6169 | 0.07689
30/06/2013 | 2013 | 25452 | 148 | 5368 | 0.21091 | 0.0058149
02/07/2013 | 2013 | 25452 | 102 | 15159 | 0.59559 | 0.0040075
03/07/2013 | 2013 | 25452 | 2278 | 58487 | 2.2979 | 0.089502
05/07/2013 | 2013 | 25452 | 225 | 27552 | 1.0825 | 0.0088402
09/07/2013 | 2013 | 25452 | 113 | 15374 | 0.60404 | 0.0044397
10/07/2013 | 2013 | 25452 | 114 | 6498 | 0.2553 | 0.004479
11/07/2013 | 2013 | 25452 | 184 | 9676 | 0.38017 | 0.0072293
12/07/2013 | 2013 | 25452 | 133 | 18517 | 0.72753 | 0.0052255
13/07/2013 | 2013 | 25452 | 89 | 15594 | 0.61268 | 0.0034968
15/07/2013 | 2013 | 25452 | 2497 | 74907 | 2.9431 | 0.098106
16/07/2013 | 2013 | 25452 | 32 | 10771 | 0.42319 | 0.0012573
17/07/2013 | 2013 | 25452 | 57 | 14817 | 0.58215 | 0.0022395
19/07/2013 | 2013 | 25452 | 205 | 13235 | 0.52 | 0.0080544
20/07/2013 | 2013 | 25452 | 73 | 14746 | 0.57937 | 0.0028681
22/07/2013 | 2013 | 25452 | 155 | 7750 | 0.30449 | 0.0060899
23/07/2013 | 2013 | 25452 | 728 | 50868 | 1.9986 | 0.028603
25/07/2013 | 2013 | 25452 | 33 | 14589 | 0.5732 | 0.0012966
26/07/2013 | 2013 | 25452 | 15 | 2340 | 0.091938 | 0.00058934
28/07/2013 | 2013 | 25452 | 167 | 60621 | 2.3818 | 0.0065614
29/07/2013 | 2013 | 25452 | 6 | 1908 | 0.074965 | 0.00023574
30/07/2013 | 2013 | 25452 | 21 | 16779 | 0.65924 | 0.00082508
01/08/2013 | 2013 | 25452 | 54 | 17820 | 0.70014 | 0.0021216
03/08/2013 | 2013 | 25452 | 2510 | 94879 | 3.7278 | 0.098617
06/08/2013 | 2013 | 25452 | 12 | 3960 | 0.15559 | 0.00047148
08/08/2013 | 2013 | 25452 | 81 | 20088 | 0.78925 | 0.0031825
10/08/2013 | 2013 | 25452 | 573 | 100826 | 3.9614 | 0.022513
11/08/2013 | 2013 | 25452 | 234 | 55059 | 2.1632 | 0.0091938
13/08/2013 | 2013 | 25452 | 274 | 7946 | 0.3122 | 0.010765
14/08/2013 | 2013 | 25452 | 69 | 6894 | 0.27086 | 0.002711
15/08/2013 | 2013 | 25452 | 1102 | 22038 | 0.86587 | 0.043297
16/08/2013 | 2013 | 25452 | 36 | 7600 | 0.2986 | 0.0014144
18/08/2013 | 2013 | 25452 | 30 | 10020 | 0.39368 | 0.0011787
19/08/2013 | 2013 | 25452 | 235 | 40081 | 1.5748 | 0.0092331
20/08/2013 | 2013 | 25452 | 30 | 8166 | 0.32084 | 0.0011787
21/08/2013 | 2013 | 25452 | 68 | 20760 | 0.81565 | 0.0026717
22/08/2013 | 2013 | 25452 | 19 | 4243 | 0.16671 | 0.0007465
23/08/2013 | 2013 | 25452 | 456 | 27292 | 1.0723 | 0.017916
26/08/2013 | 2013 | 25452 | 38 | 8040 | 0.31589 | 0.001493
28/08/2013 | 2013 | 25452 | 38 | 12046 | 0.47328 | 0.001493
29/08/2013 | 2013 | 25452 | 61 | 732 | 0.02876 | 0.0023967
31/08/2013 | 2013 | 25452 | 254 | 9911 | 0.3894 | 0.0099796
03/09/2013 | 2013 | 25452 | 206 | 27717 | 1.089 | 0.0080937
04/09/2013 | 2013 | 25452 | 8 | 936 | 0.036775 | 0.00031432
05/09/2013 | 2013 | 25452 | 13 | 3874 | 0.15221 | 0.00051077
06/09/2013 | 2013 | 25452 | 24 | 5967 | 0.23444 | 0.00094295
11/09/2013 | 2013 | 25452 | 463 | 219408 | 8.6205 | 0.018191
12/09/2013 | 2013 | 25452 | 1212 | 487258 | 19.1442 | 0.047619
13/09/2013 | 2013 | 25452 | 1138 | 707104 | 27.7819 | 0.044712
14/09/2013 | 2013 | 25452 | 122 | 255216 | 10.0273 | 0.0047933
15/09/2013 | 2013 | 25452 | 180 | 29299 | 1.1511 | 0.0070721
17/09/2013 | 2013 | 25452 | 64 | 7714 | 0.30308 | 0.0025145
18/09/2013 | 2013 | 25452 | 47 | 16712 | 0.65661 | 0.0018466
19/09/2013 | 2013 | 25452 | 1174 | 36333 | 1.4275 | 0.046126
20/09/2013 | 2013 | 25452 | 66 | 3630 | 0.14262 | 0.0025931
23/09/2013 | 2013 | 25452 | 168 | 11263 | 0.44252 | 0.0066007
25/09/2013 | 2013 | 25452 | 180 | 56696 | 2.2276 | 0.0070721
26/09/2013 | 2013 | 25452 | 196 | 4672 | 0.18356 | 0.0077008
28/09/2013 | 2013 | 25452 | 107 | 6292 | 0.24721 | 0.004204
01/10/2013 | 2013 | 25452 | 173 | 28757 | 1.1299 | 0.0067971
02/10/2013 | 2013 | 25452 | 139 | 67379 | 2.6473 | 0.0054613
08/10/2013 | 2013 | 25452 | 53 | 5194 | 0.20407 | 0.0020824
09/10/2013 | 2013 | 25452 | 34 | 1972 | 0.077479 | 0.0013358
10/10/2013 | 2013 | 25452 | 238 | 95620 | 3.7569 | 0.0093509
11/10/2013 | 2013 | 25452 | 430 | 261472 | 10.2731 | 0.016895
12/10/2013 | 2013 | 25452 | 955 | 180096 | 7.0759 | 0.037522
13/10/2013 | 2013 | 25452 | 5 | 1075 | 0.042236 | 0.00019645
14/10/2013 | 2013 | 25452 | 170 | 2755 | 0.10824 | 0.0066792
15/10/2013 | 2013 | 25452 | 2479 | 133602 | 5.2492 | 0.097399
16/10/2013 | 2013 | 25452 | 29 | 5253 | 0.20639 | 0.0011394
17/10/2013 | 2013 | 25452 | 88 | 16783 | 0.6594 | 0.0034575
18/10/2013 | 2013 | 25452 | 239 | 11107 | 0.43639 | 0.0093902
20/10/2013 | 2013 | 25452 | 37 | 629 | 0.024713 | 0.0014537
23/10/2013 | 2013 | 25452 | 283 | 26650 | 1.0471 | 0.011119
24/10/2013 | 2013 | 25452 | 65 | 11812 | 0.46409 | 0.0025538
25/10/2013 | 2013 | 25452 | 799 | 92726 | 3.6432 | 0.031392
26/10/2013 | 2013 | 25452 | 1177 | 24037 | 0.94441 | 0.046244
29/10/2013 | 2013 | 25452 | 500 | 37760 | 1.4836 | 0.019645
30/10/2013 | 2013 | 25452 | 134 | 38744 | 1.5222 | 0.0052648
31/10/2013 | 2013 | 25452 | 4 | 1100 | 0.043219 | 0.00015716
01/11/2013 | 2013 | 25452 | 176 | 2112 | 0.08298 | 0.006915
04/11/2013 | 2013 | 25452 | 71 | 2880 | 0.11315 | 0.0027896
05/11/2013 | 2013 | 25452 | 92 | 7436 | 0.29216 | 0.0036146
07/11/2013 | 2013 | 25452 | 164 | 35889 | 1.4101 | 0.0064435
08/11/2013 | 2013 | 25452 | 58 | 5803 | 0.228 | 0.0022788
11/11/2013 | 2013 | 25452 | 91 | 12789 | 0.50248 | 0.0035754
12/11/2013 | 2013 | 25452 | 97 | 30715 | 1.2068 | 0.0038111
13/11/2013 | 2013 | 25452 | 64 | 43904 | 1.725 | 0.0025145
14/11/2013 | 2013 | 25452 | 225 | 22640 | 0.88952 | 0.0088402
19/11/2013 | 2013 | 25452 | 48 | 6768 | 0.26591 | 0.0018859
20/11/2013 | 2013 | 25452 | 33 | 6468 | 0.25413 | 0.0012966
21/11/2013 | 2013 | 25452 | 41 | 1722 | 0.067657 | 0.0016109
22/11/2013 | 2013 | 25452 | 21 | 420 | 0.016502 | 0.00082508
24/11/2013 | 2013 | 25452 | 12 | 2772 | 0.10891 | 0.00047148
25/11/2013 | 2013 | 25452 | 56 | 46312 | 1.8196 | 0.0022002
27/11/2013 | 2013 | 25452 | 166 | 38802 | 1.5245 | 0.0065221
29/11/2013 | 2013 | 25452 | 255 | 15766 | 0.61944 | 0.010019
30/11/2013 | 2013 | 25452 | 81 | 27797 | 1.0921 | 0.0031825
03/12/2013 | 2013 | 25452 | 4 | 1392 | 0.054691 | 0.00015716
05/12/2013 | 2013 | 25452 | 34 | 7426 | 0.29176 | 0.0013358
06/12/2013 | 2013 | 25452 | 80 | 19280 | 0.7575 | 0.0031432
09/12/2013 | 2013 | 25452 | 55 | 24748 | 0.97234 | 0.0021609
10/12/2013 | 2013 | 25452 | 43 | 8993 | 0.35333 | 0.0016895
12/12/2013 | 2013 | 25452 | 33 | 10164 | 0.39934 | 0.0012966
13/12/2013 | 2013 | 25452 | 14 | 1820 | 0.071507 | 0.00055006
15/12/2013 | 2013 | 25452 | 18 | 738 | 0.028996 | 0.00070721
16/12/2013 | 2013 | 25452 | 19 | 7030 | 0.27621 | 0.0007465
17/12/2013 | 2013 | 25452 | 177 | 31612 | 1.242 | 0.0069543
18/12/2013 | 2013 | 25452 | 69 | 15602 | 0.613 | 0.002711
19/12/2013 | 2013 | 25452 | 263 | 55491 | 2.1802 | 0.010333
20/12/2013 | 2013 | 25452 | 21 | 1463 | 0.057481 | 0.00082508
30/12/2013 | 2013 | 25452 | 73 | 8282 | 0.3254 | 0.0028681
31/12/2013 | 2013 | 25452 | 1875 | 22519 | 0.88476 | 0.073668
03/01/2014 | 2013 | 25452 | 75 | 7572 | 0.2975 | 0.0029467
04/01/2014 | 2013 | 25452 | 29 | 3770 | 0.14812 | 0.0011394
05/01/2014 | 2013 | 25452 | 699 | 138471 | 5.4405 | 0.027463
06/01/2014 | 2013 | 25452 | 20 | 9289 | 0.36496 | 0.00078579
07/01/2014 | 2013 | 25452 | 152 | 18891 | 0.74222 | 0.005972
08/01/2014 | 2013 | 25452 | 372 | 96609 | 3.7957 | 0.014616
09/01/2014 | 2013 | 25452 | 36 | 8390 | 0.32964 | 0.0014144
10/01/2014 | 2013 | 25452 | 29 | 667 | 0.026206 | 0.0011394
12/01/2014 | 2013 | 25452 | 117 | 6669 | 0.26202 | 0.0045969
14/01/2014 | 2013 | 25452 | 46 | 17300 | 0.67971 | 0.0018073
15/01/2014 | 2013 | 25452 | 51 | 16852 | 0.66211 | 0.0020038
16/01/2014 | 2013 | 25452 | 52 | 9541 | 0.37486 | 0.0020431
21/01/2014 | 2013 | 25452 | 35 | 16730 | 0.65732 | 0.0013751
22/01/2014 | 2013 | 25452 | 424 | 173586 | 6.8201 | 0.016659
24/01/2014 | 2013 | 25452 | 35 | 14691 | 0.5772 | 0.0013751
25/01/2014 | 2013 | 25452 | 61 | 13073 | 0.51363 | 0.0023967
29/01/2014 | 2013 | 25452 | 35 | 15816 | 0.6214 | 0.0013751
30/01/2014 | 2013 | 25452 | 314 | 39783 | 1.5631 | 0.012337
31/01/2014 | 2013 | 25452 | 50 | 11562 | 0.45427 | 0.0019645
01/02/2014 | 2013 | 25452 | 93 | 15715 | 0.61744 | 0.0036539
04/02/2014 | 2013 | 25452 | 43 | 8297 | 0.32599 | 0.0016895
06/02/2014 | 2013 | 25452 | 18 | 3168 | 0.12447 | 0.00070721
07/02/2014 | 2013 | 25452 | 37 | 1369 | 0.053788 | 0.0014537
08/02/2014 | 2013 | 25452 | 14 | 4620 | 0.18152 | 0.00055006
09/02/2014 | 2013 | 25452 | 1128 | 37457 | 1.4717 | 0.044319
10/02/2014 | 2013 | 25452 | 54 | 5334 | 0.20957 | 0.0021216
11/02/2014 | 2013 | 25452 | 92 | 8018 | 0.31502 | 0.0036146
12/02/2014 | 2013 | 25452 | 129 | 13812 | 0.54267 | 0.0050684
13/02/2014 | 2013 | 25452 | 1234 | 35665 | 1.4013 | 0.048483
17/02/2014 | 2013 | 25452 | 153 | 13068 | 0.51344 | 0.0060113
18/02/2014 | 2013 | 25452 | 206 | 7859 | 0.30878 | 0.0080937
19/02/2014 | 2013 | 25452 | 64 | 18849 | 0.74057 | 0.0025145
20/02/2014 | 2013 | 25452 | 60 | 19753 | 0.77609 | 0.0023574
21/02/2014 | 2013 | 25452 | 93 | 3999 | 0.15712 | 0.0036539
23/02/2014 | 2013 | 25452 | 244 | 69773 | 2.7414 | 0.0095867
26/02/2014 | 2013 | 25452 | 115 | 12581 | 0.4943 | 0.0045183
01/03/2014 | 2013 | 25452 | 245 | 14300 | 0.56184 | 0.009626
04/03/2014 | 2013 | 25452 | 1558 | 50666 | 1.9906 | 0.061213
05/03/2014 | 2013 | 25452 | 1032 | 26793 | 1.0527 | 0.040547
06/03/2014 | 2013 | 25452 | 1452 | 38174 | 1.4998 | 0.057049
07/03/2014 | 2013 | 25452 | 2164 | 140349 | 5.5143 | 0.085023
11/03/2014 | 2013 | 25452 | 624 | 33599 | 1.3201 | 0.024517
13/03/2014 | 2013 | 25452 | 47 | 19552 | 0.76819 | 0.0018466
14/03/2014 | 2013 | 25452 | 33 | 11616 | 0.45639 | 0.0012966
15/03/2014 | 2013 | 25452 | 2581 | 22376 | 0.87915 | 0.10141
16/03/2014 | 2013 | 25452 | 221 | 65693 | 2.5811 | 0.008683
17/03/2014 | 2013 | 25452 | 92 | 18220 | 0.71586 | 0.0036146
20/03/2014 | 2013 | 25452 | 33 | 10801 | 0.42437 | 0.0012966
22/03/2014 | 2013 | 25452 | 343 | 19602 | 0.77016 | 0.013476
26/03/2014 | 2013 | 25452 | 47 | 7614 | 0.29915 | 0.0018466
27/03/2014 | 2013 | 25452 | 40 | 16305 | 0.64062 | 0.0015716
28/03/2014 | 2013 | 25452 | 131 | 29460 | 1.1575 | 0.0051469
30/03/2014 | 2013 | 25452 | 424 | 17528 | 0.68867 | 0.016659
31/03/2014 | 2013 | 25452 | 32 | 4120 | 0.16187 | 0.0012573

## 20132014FixedData
Date Outage | Saidi | Safi | FixedSaidi | FixedSaifi
02/04/2013 | 0.071075 | 0.0026324 | 0.071075 | 0.0026324
03/04/2013 | 0.10805 | 0.00098224 | 0.10805 | 0.00098224
04/04/2013 | 0.66411 | 0.021374 | 0.66411 | 0.021374
05/04/2013 | 0.12082 | 0.0025538 | 0.12082 | 0.0025538
06/04/2013 | 1.0585 | 0.014144 | 1.0585 | 0.014144
07/04/2013 | 0.84842 | 0.0081722 | 0.84842 | 0.0081722
08/04/2013 | 0.15072 | 0.0014537 | 0.15072 | 0.0014537
09/04/2013 | 0.26815 | 0.058934 | 0.26815 | 0.058934
10/04/2013 | 0.63944 | 0.0018073 | 0.63944 | 0.0018073
11/04/2013 | 1.2189 | 0.018859 | 1.2189 | 0.018859
12/04/2013 | 0.38355 | 0.0035361 | 0.38355 | 0.0035361
13/04/2013 | 0.10875 | 0.00062863 | 0.10875 | 0.00062863
15/04/2013 | 0.99756 | 0.033828 | 0.99756 | 0.033828
17/04/2013 | 0.30567 | 0.00098224 | 0.30567 | 0.00098224
18/04/2013 | 2.3658 | 0.0040075 | 2.3658 | 0.0040075
19/04/2013 | 0.76917 | 0.0061685 | 0.76917 | 0.0061685
22/04/2013 | 0.11795 | 0.00043219 | 0.11795 | 0.00043219
24/04/2013 | 0.91773 | 0.0042433 | 0.91773 | 0.0042433
27/04/2013 | 0.46959 | 0.0018859 | 0.46959 | 0.0018859
28/04/2013 | 1.8653 | 0.046598 | 1.8653 | 0.046598
01/05/2013 | 0.23586 | 0.0018859 | 0.23586 | 0.0018859
02/05/2013 | 2.1614 | 0.078147 | 2.1614 | 0.078147
03/05/2013 | 0.81019 | 0.0031432 | 0.81019 | 0.0031432
04/05/2013 | 0.16297 | 0.0033003 | 0.16297 | 0.0033003
05/05/2013 | 0.14863 | 0.0011394 | 0.14863 | 0.0011394
06/05/2013 | 0.22387 | 0.0018859 | 0.22387 | 0.0018859
07/05/2013 | 1.4899 | 0.042394 | 1.4899 | 0.042394
08/05/2013 | 4.5327 | 0.019645 | 4.5327 | 0.019645
09/05/2013 | 0.12113 | 0.0011787 | 0.12113 | 0.0011787
10/05/2013 | 0.24548 | 0.0017287 | 0.24548 | 0.0017287
11/05/2013 | 1.1594 | 0.016462 | 1.1594 | 0.016462
15/05/2013 | 1.0301 | 0.004754 | 1.0301 | 0.004754
16/05/2013 | 0.17547 | 0.0030253 | 0.17547 | 0.0030253
17/05/2013 | 1.3324 | 0.0030253 | 1.3324 | 0.0030253
20/05/2013 | 0.49862 | 0.010176 | 0.49862 | 0.010176
21/05/2013 | 0.30669 | 0.0018859 | 0.30669 | 0.0018859
22/05/2013 | 0.34449 | 0.0018859 | 0.34449 | 0.0018859
27/05/2013 | 1.3656 | 0.046873 | 1.3656 | 0.046873
29/05/2013 | 0.45521 | 0.01214 | 0.45521 | 0.01214
31/05/2013 | 0.45262 | 0.0018859 | 0.45262 | 0.0018859
05/06/2013 | 1.4095 | 0.0020824 | 1.4095 | 0.0020824
06/06/2013 | 2.401 | 0.019252 | 2.401 | 0.019252
07/06/2013 | 3.3907 | 0.0099403 | 3.3907 | 0.0099403
11/06/2013 | 0.55846 | 0.0074257 | 0.55846 | 0.0074257
12/06/2013 | 0.26002 | 0.0035754 | 0.26002 | 0.0035754
13/06/2013 | 0.16238 | 0.00058934 | 0.16238 | 0.00058934
15/06/2013 | 0.74965 | 0.0091938 | 0.74965 | 0.0091938
18/06/2013 | 0.1205 | 0.0016109 | 0.1205 | 0.0016109
19/06/2013 | 0.20309 | 0.012062 | 0.20309 | 0.012062
20/06/2013 | 2.0874 | 0.019723 | 2.0874 | 0.019723
21/06/2013 | 4.0157 | 0.05752 | 4.0157 | 0.05752
22/06/2013 | 2.7876 | 0.017955 | 2.7876 | 0.017955
24/06/2013 | 0.41439 | 0.003261 | 0.41439 | 0.003261
25/06/2013 | 0.024752 | 0.0013751 | 0.024752 | 0.0013751
26/06/2013 | 0.2157 | 0.00035361 | 0.2157 | 0.00035361
28/06/2013 | 2.4866 | 0.012769 | 2.4866 | 0.012769
29/06/2013 | 3.6169 | 0.07689 | 3.6169 | 0.07689
30/06/2013 | 0.21091 | 0.0058149 | 0.21091 | 0.0058149
02/07/2013 | 0.59559 | 0.0040075 | 0.59559 | 0.0040075
03/07/2013 | 2.2979 | 0.089502 | 2.2979 | 0.089502
05/07/2013 | 1.0825 | 0.0088402 | 1.0825 | 0.0088402
09/07/2013 | 0.60404 | 0.0044397 | 0.60404 | 0.0044397
10/07/2013 | 0.2553 | 0.004479 | 0.2553 | 0.004479
11/07/2013 | 0.38017 | 0.0072293 | 0.38017 | 0.0072293
12/07/2013 | 0.72753 | 0.0052255 | 0.72753 | 0.0052255
13/07/2013 | 0.61268 | 0.0034968 | 0.61268 | 0.0034968
15/07/2013 | 2.9431 | 0.098106 | 2.9431 | 0.098106
16/07/2013 | 0.42319 | 0.0012573 | 0.42319 | 0.0012573
17/07/2013 | 0.58215 | 0.0022395 | 0.58215 | 0.0022395
19/07/2013 | 0.52 | 0.0080544 | 0.52 | 0.0080544
20/07/2013 | 0.57937 | 0.0028681 | 0.57937 | 0.0028681
22/07/2013 | 0.30449 | 0.0060899 | 0.30449 | 0.0060899
23/07/2013 | 1.9986 | 0.028603 | 1.9986 | 0.028603
25/07/2013 | 0.5732 | 0.0012966 | 0.5732 | 0.0012966
26/07/2013 | 0.091938 | 0.00058934 | 0.091938 | 0.00058934
28/07/2013 | 2.3818 | 0.0065614 | 2.3818 | 0.0065614
29/07/2013 | 0.074965 | 0.00023574 | 0.074965 | 0.00023574
30/07/2013 | 0.65924 | 0.00082508 | 0.65924 | 0.00082508
01/08/2013 | 0.70014 | 0.0021216 | 0.70014 | 0.0021216
03/08/2013 | 3.7278 | 0.098617 | 3.7278 | 0.098617
06/08/2013 | 0.15559 | 0.00047148 | 0.15559 | 0.00047148
08/08/2013 | 0.78925 | 0.0031825 | 0.78925 | 0.0031825
10/08/2013 | 3.9614 | 0.022513 | 3.9614 | 0.022513
11/08/2013 | 2.1632 | 0.0091938 | 2.1632 | 0.0091938
13/08/2013 | 0.3122 | 0.010765 | 0.3122 | 0.010765
14/08/2013 | 0.27086 | 0.002711 | 0.27086 | 0.002711
15/08/2013 | 0.86587 | 0.043297 | 0.86587 | 0.043297
16/08/2013 | 0.2986 | 0.0014144 | 0.2986 | 0.0014144
18/08/2013 | 0.39368 | 0.0011787 | 0.39368 | 0.0011787
19/08/2013 | 1.5748 | 0.0092331 | 1.5748 | 0.0092331
20/08/2013 | 0.32084 | 0.0011787 | 0.32084 | 0.0011787
21/08/2013 | 0.81565 | 0.0026717 | 0.81565 | 0.0026717
22/08/2013 | 0.16671 | 0.0007465 | 0.16671 | 0.0007465
23/08/2013 | 1.0723 | 0.017916 | 1.0723 | 0.017916
26/08/2013 | 0.31589 | 0.001493 | 0.31589 | 0.001493
28/08/2013 | 0.47328 | 0.001493 | 0.47328 | 0.001493
29/08/2013 | 0.02876 | 0.0023967 | 0.02876 | 0.0023967
31/08/2013 | 0.3894 | 0.0099796 | 0.3894 | 0.0099796
03/09/2013 | 1.089 | 0.0080937 | 1.089 | 0.0080937
04/09/2013 | 0.036775 | 0.00031432 | 0.036775 | 0.00031432
05/09/2013 | 0.15221 | 0.00051077 | 0.15221 | 0.00051077
06/09/2013 | 0.23444 | 0.00094295 | 0.23444 | 0.00094295
11/09/2013 | 8.6205 | 0.018191 | 8.6205 | 0.018191
12/09/2013 | 19.1442 | 0.047619 | 19.1442 | 0.047619
13/09/2013 | 27.7819 | 0.044712 | 22.8581 | 0.044712
14/09/2013 | 10.0273 | 0.0047933 | 10.0273 | 0.0047933
15/09/2013 | 1.1511 | 0.0070721 | 1.1511 | 0.0070721
17/09/2013 | 0.30308 | 0.0025145 | 0.30308 | 0.0025145
18/09/2013 | 0.65661 | 0.0018466 | 0.65661 | 0.0018466
19/09/2013 | 1.4275 | 0.046126 | 1.4275 | 0.046126
20/09/2013 | 0.14262 | 0.0025931 | 0.14262 | 0.0025931
23/09/2013 | 0.44252 | 0.0066007 | 0.44252 | 0.0066007
25/09/2013 | 2.2276 | 0.0070721 | 2.2276 | 0.0070721
26/09/2013 | 0.18356 | 0.0077008 | 0.18356 | 0.0077008
28/09/2013 | 0.24721 | 0.004204 | 0.24721 | 0.004204
01/10/2013 | 1.1299 | 0.0067971 | 1.1299 | 0.0067971
02/10/2013 | 2.6473 | 0.0054613 | 2.6473 | 0.0054613
08/10/2013 | 0.20407 | 0.0020824 | 0.20407 | 0.0020824
09/10/2013 | 0.077479 | 0.0013358 | 0.077479 | 0.0013358
10/10/2013 | 3.7569 | 0.0093509 | 3.7569 | 0.0093509
11/10/2013 | 10.2731 | 0.016895 | 10.2731 | 0.016895
12/10/2013 | 7.0759 | 0.037522 | 7.0759 | 0.037522
13/10/2013 | 0.042236 | 0.00019645 | 0.042236 | 0.00019645
14/10/2013 | 0.10824 | 0.0066792 | 0.10824 | 0.0066792
15/10/2013 | 5.2492 | 0.097399 | 5.2492 | 0.097399
16/10/2013 | 0.20639 | 0.0011394 | 0.20639 | 0.0011394
17/10/2013 | 0.6594 | 0.0034575 | 0.6594 | 0.0034575
18/10/2013 | 0.43639 | 0.0093902 | 0.43639 | 0.0093902
20/10/2013 | 0.024713 | 0.0014537 | 0.024713 | 0.0014537
23/10/2013 | 1.0471 | 0.011119 | 1.0471 | 0.011119
24/10/2013 | 0.46409 | 0.0025538 | 0.46409 | 0.0025538
25/10/2013 | 3.6432 | 0.031392 | 3.6432 | 0.031392
26/10/2013 | 0.94441 | 0.046244 | 0.94441 | 0.046244
29/10/2013 | 1.4836 | 0.019645 | 1.4836 | 0.019645
30/10/2013 | 1.5222 | 0.0052648 | 1.5222 | 0.0052648
31/10/2013 | 0.043219 | 0.00015716 | 0.043219 | 0.00015716
01/11/2013 | 0.08298 | 0.006915 | 0.08298 | 0.006915
04/11/2013 | 0.11315 | 0.0027896 | 0.11315 | 0.0027896
05/11/2013 | 0.29216 | 0.0036146 | 0.29216 | 0.0036146
07/11/2013 | 1.4101 | 0.0064435 | 1.4101 | 0.0064435
08/11/2013 | 0.228 | 0.0022788 | 0.228 | 0.0022788
11/11/2013 | 0.50248 | 0.0035754 | 0.50248 | 0.0035754
12/11/2013 | 1.2068 | 0.0038111 | 1.2068 | 0.0038111
13/11/2013 | 1.725 | 0.0025145 | 1.725 | 0.0025145
14/11/2013 | 0.88952 | 0.0088402 | 0.88952 | 0.0088402
19/11/2013 | 0.26591 | 0.0018859 | 0.26591 | 0.0018859
20/11/2013 | 0.25413 | 0.0012966 | 0.25413 | 0.0012966
21/11/2013 | 0.067657 | 0.0016109 | 0.067657 | 0.0016109
22/11/2013 | 0.016502 | 0.00082508 | 0.016502 | 0.00082508
24/11/2013 | 0.10891 | 0.00047148 | 0.10891 | 0.00047148
25/11/2013 | 1.8196 | 0.0022002 | 1.8196 | 0.0022002
27/11/2013 | 1.5245 | 0.0065221 | 1.5245 | 0.0065221
29/11/2013 | 0.61944 | 0.010019 | 0.61944 | 0.010019
30/11/2013 | 1.0921 | 0.0031825 | 1.0921 | 0.0031825
03/12/2013 | 0.054691 | 0.00015716 | 0.054691 | 0.00015716
05/12/2013 | 0.29176 | 0.0013358 | 0.29176 | 0.0013358
06/12/2013 | 0.7575 | 0.0031432 | 0.7575 | 0.0031432
09/12/2013 | 0.97234 | 0.0021609 | 0.97234 | 0.0021609
10/12/2013 | 0.35333 | 0.0016895 | 0.35333 | 0.0016895
12/12/2013 | 0.39934 | 0.0012966 | 0.39934 | 0.0012966
13/12/2013 | 0.071507 | 0.00055006 | 0.071507 | 0.00055006
15/12/2013 | 0.028996 | 0.00070721 | 0.028996 | 0.00070721
16/12/2013 | 0.27621 | 0.0007465 | 0.27621 | 0.0007465
17/12/2013 | 1.242 | 0.0069543 | 1.242 | 0.0069543
18/12/2013 | 0.613 | 0.002711 | 0.613 | 0.002711
19/12/2013 | 2.1802 | 0.010333 | 2.1802 | 0.010333
20/12/2013 | 0.057481 | 0.00082508 | 0.057481 | 0.00082508
30/12/2013 | 0.3254 | 0.0028681 | 0.3254 | 0.0028681
31/12/2013 | 0.88476 | 0.073668 | 0.88476 | 0.073668
03/01/2014 | 0.2975 | 0.0029467 | 0.2975 | 0.0029467
04/01/2014 | 0.14812 | 0.0011394 | 0.14812 | 0.0011394
05/01/2014 | 5.4405 | 0.027463 | 5.4405 | 0.027463
06/01/2014 | 0.36496 | 0.00078579 | 0.36496 | 0.00078579
07/01/2014 | 0.74222 | 0.005972 | 0.74222 | 0.005972
08/01/2014 | 3.7957 | 0.014616 | 3.7957 | 0.014616
09/01/2014 | 0.32964 | 0.0014144 | 0.32964 | 0.0014144
10/01/2014 | 0.026206 | 0.0011394 | 0.026206 | 0.0011394
12/01/2014 | 0.26202 | 0.0045969 | 0.26202 | 0.0045969
14/01/2014 | 0.67971 | 0.0018073 | 0.67971 | 0.0018073
15/01/2014 | 0.66211 | 0.0020038 | 0.66211 | 0.0020038
16/01/2014 | 0.37486 | 0.0020431 | 0.37486 | 0.0020431
21/01/2014 | 0.65732 | 0.0013751 | 0.65732 | 0.0013751
22/01/2014 | 6.8201 | 0.016659 | 6.8201 | 0.016659
24/01/2014 | 0.5772 | 0.0013751 | 0.5772 | 0.0013751
25/01/2014 | 0.51363 | 0.0023967 | 0.51363 | 0.0023967
29/01/2014 | 0.6214 | 0.0013751 | 0.6214 | 0.0013751
30/01/2014 | 1.5631 | 0.012337 | 1.5631 | 0.012337
31/01/2014 | 0.45427 | 0.0019645 | 0.45427 | 0.0019645
01/02/2014 | 0.61744 | 0.0036539 | 0.61744 | 0.0036539
04/02/2014 | 0.32599 | 0.0016895 | 0.32599 | 0.0016895
06/02/2014 | 0.12447 | 0.00070721 | 0.12447 | 0.00070721
07/02/2014 | 0.053788 | 0.0014537 | 0.053788 | 0.0014537
08/02/2014 | 0.18152 | 0.00055006 | 0.18152 | 0.00055006
09/02/2014 | 1.4717 | 0.044319 | 1.4717 | 0.044319
10/02/2014 | 0.20957 | 0.0021216 | 0.20957 | 0.0021216
11/02/2014 | 0.31502 | 0.0036146 | 0.31502 | 0.0036146
12/02/2014 | 0.54267 | 0.0050684 | 0.54267 | 0.0050684
13/02/2014 | 1.4013 | 0.048483 | 1.4013 | 0.048483
17/02/2014 | 0.51344 | 0.0060113 | 0.51344 | 0.0060113
18/02/2014 | 0.30878 | 0.0080937 | 0.30878 | 0.0080937
19/02/2014 | 0.74057 | 0.0025145 | 0.74057 | 0.0025145
20/02/2014 | 0.77609 | 0.0023574 | 0.77609 | 0.0023574
21/02/2014 | 0.15712 | 0.0036539 | 0.15712 | 0.0036539
23/02/2014 | 2.7414 | 0.0095867 | 2.7414 | 0.0095867
26/02/2014 | 0.4943 | 0.0045183 | 0.4943 | 0.0045183
01/03/2014 | 0.56184 | 0.009626 | 0.56184 | 0.009626
04/03/2014 | 1.9906 | 0.061213 | 1.9906 | 0.061213
05/03/2014 | 1.0527 | 0.040547 | 1.0527 | 0.040547
06/03/2014 | 1.4998 | 0.057049 | 1.4998 | 0.057049
07/03/2014 | 5.5143 | 0.085023 | 5.5143 | 0.085023
11/03/2014 | 1.3201 | 0.024517 | 1.3201 | 0.024517
13/03/2014 | 0.76819 | 0.0018466 | 0.76819 | 0.0018466
14/03/2014 | 0.45639 | 0.0012966 | 0.45639 | 0.0012966
15/03/2014 | 0.87915 | 0.10141 | 0.87915 | 0.10141
16/03/2014 | 2.5811 | 0.008683 | 2.5811 | 0.008683
17/03/2014 | 0.71586 | 0.0036146 | 0.71586 | 0.0036146
20/03/2014 | 0.42437 | 0.0012966 | 0.42437 | 0.0012966
22/03/2014 | 0.77016 | 0.013476 | 0.77016 | 0.013476
26/03/2014 | 0.29915 | 0.0018466 | 0.29915 | 0.0018466
27/03/2014 | 0.64062 | 0.0015716 | 0.64062 | 0.0015716
28/03/2014 | 1.1575 | 0.0051469 | 1.1575 | 0.0051469
30/03/2014 | 0.68867 | 0.016659 | 0.68867 | 0.016659
31/03/2014 | 0.16187 | 0.0012573 | 0.16187 | 0.0012573

## 20132014 Answer
Actual | Actual | Normalised and Fixed | Normalised and Fixed
SumOfSaidi | SumOfSafi | SumOfFixedSaidi | SumOfFixedSaifi
284.7236 | 2.67 | 279.7998 | 2.67
|  | SaidiLimit | SaifiLimit
|  | 302.3793 | 4.26

## 20122013Data
REPORT NUMBER | Date Outage | YEAR | DATE ON | Duration of Outage | Customers Impacted | Total Customer Minutes Lost | CLASS A-G | CAUSE | NOTES
14330 | 02/04/2012 | 2012 | 2012-04-02 | 278 | 150 | 11940 | C | TREE CONTACTS | Replace pole G1686 Arikihi Rd
14331 | 03/04/2012 | 2012 | 2012-04-03 | 96 | 328 | 24988 | C | TREE CONTACTS | Remove branch from 11kV pole J1669 Bowling Green Rd
14332 | 03/04/2012 | 2012 | 2012-04-03 | 131 | 122 | 11091 | C | TREE CONTACTS | Repair lines poles H1474 & H1475 Makarika Rd
14333 | 03/04/2012 | 2012 | 2012-04-03 | 51 | 26 | 1326 | C | TREE CONTACTS | Remove tree branch from line pole W1107 Harrison Rd
14334 | 03/04/2012 | 2012 | 2012-04-03 | 1378 | 75 | 12754 | C | TREE CONTACTS | Remove branch from line Pole H4155 Ihungia Rd
14335 | 04/04/2012 | 2012 | 2012-04-04 | 62 | 21 | 789 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W9412 Onenui
14337 | 04/04/2012 | 2012 | 2012-04-04 | 46 | 30 | 1380 | C | FOREIGN INTERFERENCE | Relocate 11kV pole G1685 due to river shiffting
14336 | 05/04/2012 | 2012 | 2012-04-05 | 17 | 488 | 5843 | C | TREE CONTACTS | Replace broken pole J1770 Kemps Hill
14338 | 05/04/2012 | 2012 | 2012-04-05 | 428 | 87 | 18012 | C | TREE CONTACTS | Repair 11kV lines pole D3012 Tiniroto Rd
14339 | 05/04/2012 | 2012 | 2012-04-05 | 210 | 33 | 6930 | C | DEFECTIVE EQUIPMENT | Replace 3 11kV poles C2227 C2228 & C244 Main Rd Makaraka
14340 | 05/04/2012 | 2012 | 2012-04-05 | 112 | 51 | 8748 | C | TREE CONTACTS | Repair 11kV lines pole D1793 Gentle Annie Hill
14341 | 05/04/2012 | 2012 | 2012-04-05 | 408 | 75 | 9665 | C | TREE CONTACTS | Repair 11kV lines poles H135 to H1230 Tuakau Rd
14342 | 06/04/2012 | 2012 | 2012-04-06 | 337 | 69 | 23253 | C | FOREIGN INTERFERENCE | Replace 11kV pole J3553 Tuparoa Rd hit by Car
14343 | 08/04/2012 | 2012 | 2012-04-08 | 28 | 791 | 16796 | C | DEFECTIVE EQUIPMENT | Repair tapchanger T3 at Ruatoria Sub
14344 | 08/04/2012 | 2012 | 2012-04-08 | 60 | 1154 | 14420 | C | TREE CONTACTS | Isolate 11kV lines pole D5335 Lavenham Rd
14345 | 09/04/2012 | 2012 | 2012-04-09 | 25 | 77 | 1925 | C | DEFECTIVE EQUIPMENT | Repair lines pole W5880 Tiniroto Rd
14346 | 10/04/2012 | 2012 | 2012-04-10 | 577 | 12 | 4204 | C | TREE CONTACTS | Repair 11kV lines pole H154 to H146 Ihungia Rd
14358 | 12/04/2012 | 2012 | 2012-04-12 | 90 | 10 | 900 | B | PLANNED SHUTDOWN | Install T/x on pole C4995 Nelson Rd
14359 | 13/04/2012 | 2012 | 2012-04-13 | 354 | 51 | 18054 | B | PLANNED SHUTDOWN | Replace 11kV pole W3995 Mohaka
14347 | 16/04/2012 | 2012 | 2012-04-16 | 276 | 161 | 5008 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H527 Waihau Rd
14360 | 16/04/2012 | 2012 | 2012-04-16 | 206 | 69 | 14214 | B | PLANNED SHUTDOWN | Replace 11kV poles H2512 H2541 Arthur St
14348 | 17/04/2012 | 2012 | 2012-04-17 | 203 | 153 | 16761 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole G1696 Arikihi Rd
14361 | 17/04/2012 | 2012 | 2012-04-17 | 460 | 139 | 22873 | B | PLANNED SHUTDOWN | Repair ABS C1091 Waingake Rd
14363 | 18/04/2012 | 2012 | 2012-04-18 | 284 | 37 | 10508 | B | PLANNED SHUTDOWN | Replace 11kV poles H1505 H1506 H1505 H1505 Makarika
14356 | 19/04/2012 | 2012 | 2012-04-19 | 428 | 27 | 11556 | B | PLANNED SHUTDOWN | Replace 11kV poles F3374 & F3378 Kipling Rd
14357 | 19/04/2012 | 2012 | 2012-04-19 | 326 | 19 | 6194 | B | PLANNED SHUTDOWN | Replace poles beyond E157 Te Hau Rd
14355 | 20/04/2012 | 2012 | 2012-04-20 | 404 | 340 | 32360 | B | PLANNED SHUTDOWN | Replace ABS B213 Russel St
14349 | 23/04/2012 | 2012 | 2012-04-23 | 37 | 78 | 2886 | C | DEFECTIVE EQUIPMENT | Replace insulator pole J363 Hicks Bay
14350 | 23/04/2012 | 2012 | 2012-04-23 | 90 | 23 | 2070 | C | DEFECTIVE EQUIPMENT | Replace T/x J303 East Cape Rd
14364 | 24/04/2012 | 2012 | 2012-04-24 | 325 | 34 | 11050 | B | PLANNED SHUTDOWN | Replace 11kV poles D492 & D3927 Taumata Rd
14351 | 26/04/2012 | 2012 | 2012-04-26 | 1197 | 67 | 9765 | C | DEFECTIVE EQUIPMENT | Replace 2 broken poles F2400 & F2401 Marumoko Rd Motu
14352 | 26/04/2012 | 2012 | 2012-04-26 | 283 | 227 | 23347 | C | FOREIGN INTERFERENCE | Replace 11kV pole E2147 SH2 Ormond
14362 | 27/04/2012 | 2012 | 2012-04-27 | 54 | 15 | 1455 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting A4431 Turihau Stn
14353 | 28/04/2012 | 2012 | 2012-04-28 | 590 | 51 | 32202 | C | FOREIGN INTERFERENCE | Replace burnt pole H1948 Kopuaroa Rd possum on pole
14354 | 30/04/2012 | 2012 | 2012-04-30 | 121 | 198 | 16229 | C | TREE CONTACTS | Isolate lines pole W1112 Titirangi Rd
14365 | 01/05/2012 | 2012 | 2012-05-01 | 1134 | 59 | 65095 | C | DEFECTIVE EQUIPMENT | Repair LBS D141 Wharekopae Rd
14378 | 01/05/2012 | 2012 | 2012-05-01 | 358 | 27 | 3261 | B | PLANNED SHUTDOWN | Replace 11kV poles G2213 & G2211 Mangatuna Rd
14381 | 01/05/2012 | 2012 | 2012-05-01 | 160 | 80 | 12800 | B | PLANNED SHUTDOWN | Replace 11kV poles W5868 & W5860 Brownlie Rd
14366 | 02/05/2012 | 2012 | 2012-05-02 | 98 | 128 | 12544 | C | TREE CONTACTS | Isolate 11kV lines for tree cutting pole J2565 Te Araroa
14380 | 02/05/2012 | 2012 | 2012-05-02 | 21 | 18 | 738 | B | PLANNED SHUTDOWN | Replace 11kV poles D491 to D3494 Taumata Rd
14382 | 02/05/2012 | 2012 | 2012-05-02 | 70 | 27 | 1890 | B | PLANNED SHUTDOWN | Replace T/x F369 Matawai Rd Te Karaka
14367 | 03/05/2012 | 2012 | 2012-05-03 | 94 | 226 | 21244 | C | DEFECTIVE EQUIPMENT | Straighten 11kV pole J4510 Hicks Bay
14368 | 07/05/2012 | 2012 | 2012-05-07 | 233 | 273 | 15873 | C | UNKNOWN | Repair 11kV lies pole W8835 Morere
14383 | 07/05/2012 | 2012 | 2012-05-07 | 59 | 10 | 590 | B | PLANNED SHUTDOWN | Relocate stay wire 11kV pole E310 Waimata Valley Rd
14369 | 08/05/2012 | 2012 | 2012-05-08 | 136 | 74 | 10064 | C | ADVERSE ENVIRONMENT | Reposition pole C2165 Waingake Valley Rd
14384 | 08/05/2012 | 2012 | 2012-05-08 | 29 | 20 | 940 | B | PLANNED SHUTDOWN | Replace 11kV poles D2686 D2687 D2688 Pehiri Rd
14385 | 08/05/2012 | 2012 | 2012-05-08 | 157 | 32 | 5024 | B | PLANNED SHUTDOWN | Replace poles B1991 & B1993 Matokitoki Valley
14370 | 09/05/2012 | 2012 | 2012-05-09 | 267 | 58 | 17340 | C | TREE CONTACTS | Repair 11kV jumper pole G1773 Tauwhareparae Rd
14387 | 09/05/2012 | 2012 | 2012-05-09 | 125 | 15 | 1875 | B | PLANNED SHUTDOWN | Replace ABS H59 Waiapu Rd Te Puia
14388 | 09/05/2012 | 2012 | 2012-05-09 | 295 | 27 | 2883 | B | PLANNED SHUTDOWN | Replace 11kV poles beyond G1674 Mangatuna Rd
14371 | 11/05/2012 | 2012 | 2012-05-11 | 4 | 93 | 372 | C | DEFECTIVE EQUIPMENT | Reclose Arcing ABS E188 Mangamaia Rd
14386 | 15/05/2012 | 2012 | 2012-05-15 | 67 | 44 | 5060 | B | PLANNED SHUTDOWN | Connect & reconnect Recloser W999 for Maintenance Pokopoko
14389 | 15/05/2012 | 2012 | 2012-05-15 | 293 | 12 | 3516 | B | PLANNED SHUTDOWN | Replace 11kV poles H1531 H1511 H1519 H1517 Horehore Rd
14392 | 15/05/2012 | 2012 | 2012-05-15 | 134 | 9 | 1206 | B | PLANNED SHUTDOWN | Isolate 11kV lines poles H188 to H186 Puketoro Rd
14379 | 16/05/2012 | 2012 | 2012-05-16 | 268 | 27 | 7236 | B | PLANNED SHUTDOWN | Replace 11kV poles beyond fuses H229 Kawera Rd
14390 | 16/05/2012 | 2012 | 2012-05-16 | 48 | 7 | 336 | B | PLANNED SHUTDOWN | Install T/x on pole 11kV pole J3834 Matakaoa Rd
14393 | 16/05/2012 | 2012 | 2012-05-16 | 403 | 4 | 1612 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting beyond G175 Hokoroa Rd
14372 | 17/05/2012 | 2012 | 2012-05-17 | 14 | 70 | 980 | C | DEFECTIVE EQUIPMENT | Replace faulty DDO fuses pole F384 Te Karaka
14373 | 18/05/2012 | 2012 | 2012-05-18 | 315 | 13 | 2795 | C | FOREIGN INTERFERENCE | Replace 50kV 11kV pole C5852 Mc Donalds Rd
14394 | 18/05/2012 | 2012 | 2012-05-18 | 445 | 13 | 5785 | B | PLANNED SHUTDOWN | Replace 11kV poles C5445 C5406 C5428 C5426 Kirkpatrick Rd
14374 | 21/05/2012 | 2012 | 2012-05-21 | 140 | 21 | 2940 | C | TREE CONTACTS | Repair 11kV lies pole W1316 Tawhara Rd Wairoa
14391 | 22/05/2012 | 2012 | 2012-05-22 | 358 | 12 | 4296 | B | PLANNED SHUTDOWN | Isolate 11kV lines pole H146 Ihungia Rd
14395 | 22/05/2012 | 2012 | 2012-05-22 | 316 | 88 | 11168 | B | PLANNED SHUTDOWN | Replace 11kV poles E1456 E1455 F1075 F1074 F1073 Kanakanaia Rd
14396 | 23/05/2012 | 2012 | 2012-05-23 | 378 | 13 | 4914 | B | PLANNED SHUTDOWN | Replace 11kV poles C5429 C5431 C5433 C5435 Kirkpatrick Rd
14397 | 25/05/2012 | 2012 | 2012-05-25 | 360 | 6 | 2160 | B | PLANNED SHUTDOWN | Replace 11kV poles H1960 H1962 Kiekie Rd
14375 | 26/05/2012 | 2012 | 2012-05-26 | 110 | 17 | 1870 | C | DEFECTIVE EQUIPMENT | Replace T/x J187 Tapuwaeroa Rd
14398 | 28/05/2012 | 2012 | 2012-05-28 | 393 | 13 | 5109 | B | PLANNED SHUTDOWN | Replace 11kV poles C5438 C5439 C5404 Kirkpatrick Rd
14399 | 29/05/2012 | 2012 | 2012-05-29 | 313 | 25 | 7825 | B | PLANNED SHUTDOWN | Replace 11kV poles H1677 H1678 H1502 Makarika Rd
14376 | 30/05/2012 | 2012 | 2012-05-30 | 30 | 68 | 1878 | C | DEFECTIVE EQUIPMENT | Re adjust ABSs E109 & E92 Matawai Rd
14377 | 30/05/2012 | 2012 | 2012-05-30 | 165 | 80 | 8610 | C | TREE CONTACTS | Remove branch from 11kV pole G1469 Anaura Bay
14400 | 30/05/2012 | 2012 | 2012-05-30 | 377 | 10 | 3770 | B | PLANNED SHUTDOWN | Isolate 11kV lines W1165 Putere Rd for tree cutting
14401 | 30/05/2012 | 2012 | 2012-05-30 | 333 | 88 | 21960 | B | PLANNED SHUTDOWN | Replace 11kV poles F378 F1063 F1062 Kanakanaia Rd
14424 | 01/06/2012 | 2012 | 2012-06-01 | 365 | 13 | 4745 | B | PLANNED SHUTDOWN | Scheduled pole replacement
14417 | 05/06/2012 | 2012 | 2012-06-05 | 697 | 42 | 21865 | C | DEFECTIVE EQUIPMENT | Broken jumper
14416 | 06/06/2012 | 2012 | 2012-06-06 | 1795 | 47 | 13045 | C | DEFECTIVE EQUIPMENT | HV U/G cable faulty
14418 | 06/06/2012 | 2012 | 2012-06-06 | 71 | 76 | 5396 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable termination at C3402
14425 | 07/06/2012 | 2012 | 2012-06-07 | 230 | 93 | 21390 | B | PLANNED SHUTDOWN | Scheduled shutdown
14421 | 08/06/2012 | 2012 | 2012-06-08 | 323 | 88 | 9864 | B | PLANNED SHUTDOWN | Planned
14423 | 08/06/2012 | 2012 | 2012-06-08 | 140 | 6 | 840 | B | PLANNED SHUTDOWN | Replace 11kV pole
14415 | 12/06/2012 | 2012 | 2012-06-12 | 125 | 260 | 16307 | C | DEFECTIVE EQUIPMENT | Unknown
14427 | 13/06/2012 | 2012 | 2012-06-13 | 312 | 9 | 2808 | B | PLANNED SHUTDOWN | Scheduled Shutdown
14431 | 13/06/2012 | 2012 | 2012-06-13 | 428 | 34 | 12772 | B | PLANNED SHUTDOWN | Scheduled shutdown
14429 | 14/06/2012 | 2012 | 2012-06-14 | 319 | 25 | 7975 | B | PLANNED SHUTDOWN | Scheduled shutdown
14414 | 15/06/2012 | 2012 | 2012-06-15 | 272 | 115 | 30348 | C | DEFECTIVE EQUIPMENT | Faulty switch J1078
14422 | 15/06/2012 | 2012 | 2012-06-15 | 405 | 24 | 9985 | B | PLANNED SHUTDOWN | Replace old poles
14430 | 15/06/2012 | 2012 | 2012-06-15 | 60 | 69 | 4280 | B | PLANNED SHUTDOWN | Scheduled Shuutdown
14412 | 18/06/2012 | 2012 | 2012-06-18 | 2 | 3005 | 6010 | C | DEFECTIVE EQUIPMENT | Differential trip (Cause Unknwon)
14439 | 18/06/2012 | 2012 | 2012-06-18 | 29 | 80 | 2320 | B | PLANNED SHUTDOWN | won't close properly
14440 | 18/06/2012 | 2012 | 2012-07-18 | 22 | 344 | 3554 | B | PLANNED SHUTDOWN | CB rectifier repaired
14413 | 19/06/2012 | 2012 | 2012-06-19 | 28 | 788 | 18112 | C | DEFECTIVE EQUIPMENT | Tap changer faulty
14432 | 19/06/2012 | 2012 | 2012-06-19 | 149 | 3 | 447 | B | PLANNED SHUTDOWN | Scheduled Shutdown
14441 | 19/06/2012 | 2012 | 2012-06-19 | 53 | 134 | 7102 | B | PLANNED SHUTDOWN | burnt HV fuse carrier
14442 | 19/06/2012 | 2012 | 2012-07-19 | 57 | 13 | 741 | C | HUMAN ELEMENT | pole broken
14434 | 20/06/2012 | 2012 | 2012-06-20 | 333 | 9 | 2997 | B | PLANNED SHUTDOWN | Scheduled Shutdown
14433 | 21/06/2012 | 2012 | 2012-06-21 | 296 | 82 | 24272 | B | PLANNED SHUTDOWN | Scheduled Shutdown
14435 | 21/06/2012 | 2012 | 2012-06-21 | 359 | 88 | 10024 | B | PLANNED SHUTDOWN | Scheduled Shutdowns
14403 | 22/06/2012 | 2012 | 2012-06-22 | 41 | 49 | 2009 | C | UNKNOWN | Unknown, suspect bird strike
14411 | 22/06/2012 | 2012 | 2012-06-22 | 41 | 49 | 2009 | C | FOREIGN INTERFERENCE | Unknown
14426 | 22/06/2012 | 2012 | 2012-06-22 | 176 | 30 | 5280 | B | PLANNED SHUTDOWN | Scheduled shutdown
14420 | 23/06/2012 | 2012 | 2012-06-24 | 508 | 1184 | 205377 | C | ADVERSE WEATHER | Feeder fault pole down W6251
14409 | 24/06/2012 | 2012 | 2012-06-25 | 1152 | 128 | 22018 | C | TREE CONTACTS | Trees not outside 'fall zone'
14404 | 25/06/2012 | 2012 | 2012-06-25 | 18 | 272 | 4182 | C | UNKNOWN | unknown
14428 | 25/06/2012 | 2012 | 2012-06-25 | 385 | 713 | 13786 | C | HUMAN ELEMENT | Car hit pole
14410 | 26/06/2012 | 2012 | 2012-06-26 | 46 | 1700 | 53422 | C | UNKNOWN | intermittent fault
14405 | 27/06/2012 | 2012 | 2012-06-27 | 103 | 11 | 1133 | C | DEFECTIVE EQUIPMENT
14406 | 27/06/2012 | 2012 | 2012-06-27 | 187 | 122 | 13817 | C | DEFECTIVE EQUIPMENT
14443 | 27/06/2012 | 2012 | 2012-06-27 | 164 | 23 | 3772 | C | DEFECTIVE EQUIPMENT | only holding by steel core
14419 | 28/06/2012 | 2012 | 2012-06-28 | 59 | 6 | 354 | C | DEFECTIVE EQUIPMENT | Repair 11kV lead to Tx F94
14436 | 28/06/2012 | 2012 | 2012-06-28 | 171 | 84 | 14403 | B | PLANNED SHUTDOWN | Scheduled shutdown
14437 | 28/06/2012 | 2012 | 2012-06-28 | 103 | 389 | 40067 | B | PLANNED SHUTDOWN
14438 | 29/06/2012 | 2012 | 2012-06-29 | 319 | 23 | 7337 | B | PLANNED SHUTDOWN | nearly falling in sea
14444 | 29/06/2012 | 2012 | 2012-06-29 | 98 | 16 | 15.64 | B | PLANNED SHUTDOWN | rotten
14407 | 30/06/2012 | 2012 | 2012-07-01 | 465 | 81 | 17471 | C | HUMAN ELEMENT | car vs pole
14446 | 01/07/2012 | 2012 | 2012-07-01 | 128 | 1301 | 77650 | C | DEFECTIVE EQUIPMENT | Repair faulty Gas Switch B351 Aberdeen Rd
14467 | 01/07/2012 | 2012 | 2012-07-01 | 402 | 103 | 5652 | B | PLANNED SHUTDOWN | Replace 11kV poles between D2784 to D2904 Wharekopae Rd
14447 | 02/07/2012 | 2012 | 2012-07-02 | 84 | 202 | 12093 | C | DEFECTIVE EQUIPMENT | Repair 11kV ABS B292 Aberdeen Rd
14468 | 03/07/2012 | 2012 | 2012-07-03 | 363 | 70 | 25410 | B | PLANNED SHUTDOWN | Replace 11kV poles H2511 H2512 H2541 H2542 H2543 H2544 Arthur St
14448 | 04/07/2012 | 2012 | 2012-07-04 | 379 | 127 | 10018 | C | TREE CONTACTS | Repair 11kV lines pole J3714 East Coast Rd Te Araroa
14449 | 05/07/2012 | 2012 | 2012-07-05 | 58 | 76 | 4408 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W6064 Mangapoikie Rd
14469 | 05/07/2012 | 2012 | 2012-07-05 | 427 | 103 | 11171 | B | PLANNED SHUTDOWN | Replace 11kV poles D2908 D2911 D2912 D2914 Wharekopae Rd
14470 | 05/07/2012 | 2012 | 2012-07-05 | 294 | 40 | 11760 | B | PLANNED SHUTDOWN | Replace 11kV poles H1721 & H1722 Makarika Rd
14450 | 06/07/2012 | 2012 | 2012-07-06 | 282 | 15 | 4230 | C | TREE CONTACTS | Repair 11kV lines pole J1004 to J1006 Poroporo Valley
14471 | 06/07/2012 | 2012 | 2012-07-06 | 417 | 103 | 10311 | B | PLANNED SHUTDOWN | Replace 11kV poles D2922 D509 D123 Wharekopae Rd
14474 | 06/07/2012 | 2012 | 2012-07-06 | 247 | 71 | 17537 | B | PLANNED SHUTDOWN | Replace 11kV poles between H311 to H351 Arthur St Tokomaru Bay
14451 | 09/07/2012 | 2012 | 2012-07-09 | 111 | 44 | 4884 | C | FOREIGN INTERFERENCE | Repair 11kV lines poles J554 to J3633 Ruatoria North
14452 | 10/07/2012 | 2012 | 2012-07-10 | 24 | 56 | 1344 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole C250 Makaraka
14473 | 10/07/2012 | 2012 | 2012-07-10 | 325 | 103 | 8740 | B | PLANNED SHUTDOWN | Replace 11kV poles D2931 D2935 D2939 Wharekopae Rd
14476 | 11/07/2012 | 2012 | 2012-07-11 | 284 | 20 | 5680 | B | PLANNED SHUTDOWN | Isolate 11kV for tree Cutting D1045 Parakanapa Rd
14477 | 12/07/2012 | 2012 | 2012-07-12 | 315 | 115 | 17793 | B | PLANNED SHUTDOWN | Replace 11kV poles F1049 F1050 F1051 Kanakanaia Rd
14478 | 13/07/2012 | 2012 | 2012-07-13 | 63 | 13 | 819 | B | PLANNED SHUTDOWN | Isolate 11kV lines between C397 to D642 for LV pole Changes Kirkpatrick Rd
14453 | 15/07/2012 | 2012 | 2012-07-15 | 40 | 196 | 6241 | C | UNKNOWN | Reclose CB 24 at Tuai Cause unknown
14454 | 16/07/2012 | 2012 | 2012-07-16 | 65 | 12 | 780 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W1102 Mahia
14455 | 16/07/2012 | 2012 | 2012-07-16 | 43 | 42 | 2021 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J3633 Ruatoria
14456 | 16/07/2012 | 2012 | 2012-07-16 | 290 | 385 | 75640 | C | FOREIGN INTERFERENCE | Repair 11kV line Poles W6286 to W6287 Raupunga
14457 | 16/07/2012 | 2012 | 2012-07-16 | 285 | 71 | 9843 | C | TREE CONTACTS | Repair 11kV lines pole F264 Te Wera Rd
14475 | 17/07/2012 | 2012 | 2012-07-17 | 368 | 115 | 18768 | B | PLANNED SHUTDOWN | Replace 11kV poles F1037 F1038 F1041 Kanakanaia Rd
14472 | 20/07/2012 | 2012 | 2012-07-20 | 291 | 14 | 4074 | B | PLANNED SHUTDOWN | Relocate 11kV pole D301 Ruakaka Rd
14480 | 22/07/2012 | 2012 | 2012-07-22 | 344 | 43 | 15965 | B | PLANNED SHUTDOWN | Replace 11kV pole J4400 Te Araroa
14482 | 24/07/2012 | 2012 | 2012-07-24 | 35 | 204 | 8364 | B | PLANNED SHUTDOWN | Replace 11kV poles B2114 B2115 Stout St
14458 | 25/07/2012 | 2012 | 2012-07-25 | 123 | 29 | 3567 | C | DEFECTIVE EQUIPMENT | Repair 11kV X arm pole F272 Journeys End Te Wera
14481 | 25/07/2012 | 2012 | 2012-07-25 | 371 | 115 | 20649 | B | PLANNED SHUTDOWN | Replace 11kV poles F1047 F1046 F1044 Kanakanaia Rd
14459 | 26/07/2012 | 2012 | 2012-07-26 | 943 | 169 | 26377 | C | TREE CONTACTS | Repair 11kV lines pole W349 to W5048 Ruapapa Rd
14479 | 26/07/2012 | 2012 | 2012-07-26 | 112 | 64 | 7168 | B | PLANNED SHUTDOWN | Replace 11kV T/x B119 Scott St
14460 | 27/07/2012 | 2012 | 2012-07-27 | 365 | 385 | 95901 | C | TREE CONTACTS | Repair 11kV lines poles W6307 to W70 Cricklewood
14461 | 27/07/2012 | 2012 | 2012-07-27 | 1111 | 174 | 36033 | C | TREE CONTACTS | Repair 11kV lines pole A1216 Whangara Pa Rd
14462 | 29/07/2012 | 2012 | 2012-07-29 | 204 | 170 | 7874 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines Poles W3949 to W5043 Raupunga
14463 | 30/07/2012 | 2012 | 2012-07-30 | 164 | 26 | 4264 | C | DEFECTIVE EQUIPMENT | Repair 11kV line pole W3949 to W5047 Raupunga
14464 | 30/07/2012 | 2012 | 2012-07-30 | 179 | 208 | 12268 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole G1101 Rototahi
14465 | 31/07/2012 | 2012 | 2012-07-31 | 355 | 338 | 10715 | C | DEFECTIVE EQUIPMENT | Temp repair pole J980 Waiomatatini
14466 | 31/07/2012 | 2012 | 2012-07-31 | 18 | 788 | 14184 | C | DEFECTIVE EQUIPMENT | Isolate Faulty Tap Changer J3 at Ruatoria Sub
14498 | 01/08/2012 | 2012 | 2012-08-01 | 302 | 3 | 906 | B | PLANNED SHUTDOWN | Replace 11kV poles H1904 H1910 H1912 Kopuaroa Rd
14483 | 02/08/2012 | 2012 | 2012-08-02 | 120 | 58 | 4962 | C | TREE CONTACTS | Repair 11kv lines beyond pole C811 Waingake
14484 | 03/08/2012 | 2012 | 2012-08-03 | 856 | 193 | 10018 | C | TREE CONTACTS | Repair 11kV lines pole E251 Kanakanaia Rd
14485 | 03/08/2012 | 2012 | 2012-08-03 | 347 | 1125 | 38913 | C | FOREIGN INTERFERENCE | Replace 11kV pole D383 Lavenham Rd
14500 | 03/08/2012 | 2012 | 2012-08-03 | 376 | 66 | 24816 | B | PLANNED SHUTDOWN | Replace 11kV poles H329 H1986 Waipiro Bay Rd
14486 | 04/08/2012 | 2012 | 2012-08-04 | 293 | 108 | 17453 | C | TREE CONTACTS | Repair 11kV lines poles H2783 to H3891 Mata Rd
14487 | 06/08/2012 | 2012 | 2012-08-06 | 65 | 12 | 780 | C | TREE CONTACTS | Replace T/x pole D308 Tiniroto tree hit pole
14488 | 06/08/2012 | 2012 | 2012-08-06 | 32 | 8057 | 168155 | C | UNKNOWN | CBs 172 & 152 Trip at Gisborne Sub cause unknown
14501 | 07/08/2012 | 2012 | 2012-08-07 | 366 | 4 | 1464 | B | PLANNED SHUTDOWN | Isloate 11kV pole H142 Waitahia Rd for tree cutting
14508 | 07/08/2012 | 2012 | 2012-08-07 | 37 | 63 | 2331 | B | PLANNED SHUTDOWN | Reboot 11kV cables T/x B112 Queens Rd
14489 | 08/08/2012 | 2012 | 2012-08-08 | 229 | 65 | 14399 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines poles H1931 to H1932 Waipiro Bay Rd
14502 | 08/08/2012 | 2012 | 2012-08-08 | 435 | 7 | 3045 | B | PLANNED SHUTDOWN | Replace 11kV pole H4408 Ihungia Rd
14507 | 08/08/2012 | 2012 | 2012-08-08 | 19 | 159 | 2150 | B | PLANNED SHUTDOWN | Replace 11kV SW/GR B556 B986 B141 Lytton Rd
14509 | 08/08/2012 | 2012 | 2012-08-08 | 345 | 51 | 9890 | B | PLANNED SHUTDOWN | Replace 11kV poles H1981 H1978 H1977 Kopauroa Rd
14503 | 09/08/2012 | 2012 | 2012-08-09 | 348 | 10 | 3840 | B | PLANNED SHUTDOWN | Isolate 11kV lines pole H135 Tuakau Rd for tree cutting
14510 | 09/08/2012 | 2012 | 2012-08-09 | 409 | 74 | 4873 | B | PLANNED SHUTDOWN | Replace 11kV poles C955 C957 C958 Wharerata Rd
14511 | 10/08/2012 | 2012 | 2012-08-10 | 208 | 52 | 5138 | B | PLANNED SHUTDOWN | Replace 11kV poles H2849 H2852 H2236 H2859 Waipiro Bay Rd
14490 | 12/08/2012 | 2012 | 2012-08-12 | 461 | 121 | 10011 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J2127 Koia Rd Tikitiki
14491 | 13/08/2012 | 2012 | 2012-08-13 | 125 | 19 | 2375 | C | ADVERSE ENVIRONMENT | Replace 11kV pole J2415 Tikitiki
14493 | 14/08/2012 | 2012 | 2012-08-14 | 37 | 78 | 2886 | C | DEFECTIVE EQUIPMENT | Replace 11kV disc on pole D5566 Kings Rd
14512 | 14/08/2012 | 2012 | 2012-08-14 | 474 | 137 | 24800 | B | PLANNED SHUTDOWN | Replace 11kV poles C1211 C1209 C1203 C1200 C1099 Whakato Rd
14492 | 15/08/2012 | 2012 | 2012-08-15 | 148 | 13 | 1924 | C | ADVERSE ENVIRONMENT | Relocate 11kV pole A4590 Glenroy Rd
14514 | 15/08/2012 | 2012 | 2012-08-15 | 65 | 291 | 18915 | B | PLANNED SHUTDOWN | Reconductor 11kV lines B2114 to B2108 Stout St
14499 | 16/08/2012 | 2012 | 2012-08-16 | 377 | 11 | 4147 | B | PLANNED SHUTDOWN | Replace 11kV poles H2233 H2221 H254 H2208 Waipiro Bay Rd
14513 | 16/08/2012 | 2012 | 2012-08-16 | 346 | 11 | 1494 | B | PLANNED SHUTDOWN | Replace T/x B685 & G/S B707 B708 B868 Lytton Rd
14494 | 19/08/2012 | 2012 | 2012-08-19 | 271 | 32 | 8672 | C | FOREIGN INTERFERENCE | Replace 11kV pole C1340 Papatu Rd hit by car
14515 | 20/08/2012 | 2012 | 2012-08-20 | 60 | 10 | 600 | B | PLANNED SHUTDOWN | Isolate 11kV lines C516 Dunstan Rd for tree cutting
14506 | 21/08/2012 | 2012 | 2012-08-21 | 374 | 4 | 1496 | B | PLANNED SHUTDOWN | Isolate 11kV lines pole H134 Mata Rd for tree cutting
14517 | 21/08/2012 | 2012 | 2012-08-21 | 273 | 8 | 2184 | B | PLANNED SHUTDOWN | Relocate 50kV 11kV pole C6705 Awapuni Rd
14504 | 22/08/2012 | 2012 | 2012-08-22 | 295 | 2 | 590 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting pole H340 Mata Rd
14516 | 22/08/2012 | 2012 | 2012-08-22 | 458 | 115 | 25534 | B | PLANNED SHUTDOWN | Replace 11kV poles F1036 F1037 F1044 Kanakanaia Rd
14505 | 23/08/2012 | 2012 | 2012-08-23 | 307 | 13 | 3991 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting pole H114 Mata Rd
14497 | 24/08/2012 | 2012 | 2012-08-24 | 434 | 21 | 35679 | B | PLANNED SHUTDOWN | Replace 11kV poles between D878 to D483 Waimaha Rd
14495 | 25/08/2012 | 2012 | 2012-08-25 | 161 | 272 | 17684 | C | TREE CONTACTS | Repair 11kV lines pole W8327 Nuhaka
14518 | 28/08/2012 | 2012 | 2012-08-28 | 308 | 10 | 3080 | B | PLANNED SHUTDOWN | Replace T/x W1530 Glengarry Place
14496 | 29/08/2012 | 2012 | 2012-08-29 | 102 | 18 | 1836 | C | DEFECTIVE EQUIPMENT | Replace Xarm 11kV pole G1842 Paramata Rd
14520 | 01/09/2012 | 2012 | 2012-09-01 | 314 | 16 | 5024 | B | PLANNED SHUTDOWN | Replace 11kV poles x 2
14519 | 04/09/2012 | 2012 | 2012-09-04 | 146 | 506 | 27287 | B | PLANNED SHUTDOWN | Service 11kV ABS's (x 18) C & D areas
14521 | 04/09/2012 | 2012 | 2012-09-04 | 543 | 196 | 35148 | B | PLANNED SHUTDOWN | Replace 11kV poles
14522 | 04/09/2012 | 2012 | 2012-09-04 | 50 | 154 | 656 | B | PLANNED SHUTDOWN | Replace 11kV poles
14540 | 04/09/2012 | 2012 | 2012-09-04 | 423 | 62 | 12272 | C | DEFECTIVE EQUIPMENT | Repair broken wires Wharekiri rd
14523 | 06/09/2012 | 2012 | 2012-09-06 | 507 | 34 | 17238 | B | PLANNED SHUTDOWN | Replace 11kV Poles.
14526 | 06/09/2012 | 2012 | 2012-09-06 | 255 | 39 | 9945 | B | PLANNED SHUTDOWN | Upgrade transformer W1582
14524 | 07/09/2012 | 2012 | 2012-09-07 | 520 | 184 | 10144 | B | PLANNED SHUTDOWN | Replace 11kV ABS Pole
14525 | 07/09/2012 | 2012 | 2012-09-07 | 255 | 237 | 7571 | B | PLANNED SHUTDOWN | Cut trees
14527 | 07/09/2012 | 2012 | 2012-09-07 | 131 | 5 | 655 | B | PLANNED SHUTDOWN | Replace 11kV pole
14541 | 07/09/2012 | 2012 | 2012-09-07 | 78 | 115 | 5533 | C | UNKNOWN | Unknown
14542 | 07/09/2012 | 2012 | 2012-09-07 | 44 | 3020 | 125214 | C | UNKNOWN | Cause unknown
14543 | 08/09/2012 | 2012 | 2012-09-09 | 155 | 170 | 78550 | C | ADVERSE WEATHER | Cause Unkown ( Could be high winds)
14544 | 08/09/2012 | 2012 | 2012-09-08 | 113 | 11 | 1243 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole
14545 | 08/09/2012 | 2012 | 2012-09-08 | 748 | 72 | 11081 | C | TREE CONTACTS | Repair 11kv lines
14546 | 09/09/2012 | 2012 | 2012-09-09 | 1621 | 29 | 47009 | C | DEFECTIVE EQUIPMENT | Repair 11kV Cable Queen St
14547 | 10/09/2012 | 2012 | 2012-09-10 | 118 | 53 | 6254 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole F2201
14548 | 10/09/2012 | 2012 | 2012-09-10 | 36 | 786 | 24926 | C | UNKNOWN | T/c fault Ruatoria Sub
14529 | 11/09/2012 | 2012 | 2012-09-11 | 365 | 73 | 9849 | B | PLANNED SHUTDOWN | Replace 11kV Poles
14549 | 11/09/2012 | 2012 | 2012-09-11 | 1241 | 65 | 23709 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole F2046
14550 | 11/09/2012 | 2012 | 2012-09-11 | 36 | 21 | 756 | C | DEFECTIVE EQUIPMENT | Replace failed DDO fuses
14530 | 12/09/2012 | 2012 | 2012-09-12 | 388 | 73 | 5484 | B | PLANNED SHUTDOWN | Replace 11kV poles (x4)
14551 | 13/09/2012 | 2012 | 2012-09-13 | 37 | 23 | 851 | B | PLANNED SHUTDOWN | Install Solid links Pole J2270
14528 | 14/09/2012 | 2012 | 2012-09-14 | 98 | 50 | 4900 | B | PLANNED SHUTDOWN | 11kV Line work
14531 | 14/09/2012 | 2012 | 2012-09-14 | 130 | 62 | 8060 | B | PLANNED SHUTDOWN | Upgrade Transformer B120
14552 | 15/09/2012 | 2012 | 2012-09-15 | 15 | 6958 | 104370 | C | UNKNOWN | Unkown
14553 | 16/09/2012 | 2012 | 2012-09-17 | 123 | 91 | 6064 | C | UNKNOWN | Cause Unkown
14554 | 16/09/2012 | 2012 | 2012-09-16 | 50 | 60 | 3000 | C | FOREIGN INTERFERENCE | Car hit pole
14555 | 17/09/2012 | 2012 | 2012-09-17 | 114 | 385 | 22189 | C | TREE CONTACTS | Tree in 11kV pole W5708
14533 | 18/09/2012 | 2012 | 2012-09-18 | 376 | 16 | 6016 | B | PLANNED SHUTDOWN | Replace 11kV poles & install new fuses
14556 | 18/09/2012 | 2012 | 2012-09-18 | 26 | 15 | 390 | C | DEFECTIVE EQUIPMENT | Straighten Xarm at pole J2901
14534 | 19/09/2012 | 2012 | 2012-09-19 | 360 | 8 | 2880 | B | PLANNED SHUTDOWN | Replace 1kV poles (x4)
14535 | 20/09/2012 | 2012 | 2012-09-20 | 357 | 63 | 4045 | B | PLANNED SHUTDOWN | Replace 11kV poles (x4)
14539 | 20/09/2012 | 2012 | 2012-09-20 | 404 | 21 | 16107 | B | PLANNED SHUTDOWN | Replace 11kV poles (x2)
14536 | 24/09/2012 | 2012 | 2012-09-24 | 360 | 73 | 26280 | B | PLANNED SHUTDOWN | Replace 11kV poles (x4)
14537 | 26/09/2012 | 2012 | 2012-09-26 | 316 | 8 | 2528 | B | PLANNED SHUTDOWN | Replace 11kV poles (x4)
14538 | 27/09/2012 | 2012 | 2012-09-27 | 325 | 9 | 2925 | B | PLANNED SHUTDOWN | Replace 11kV poles
14532 | 28/09/2012 | 2012 | 2012-09-28 | 443 | 41 | 3282 | B | PLANNED SHUTDOWN | Tree cutting
14557 | 28/09/2012 | 2012 | 2012-09-29 | 815 | 5227 | 122188 | C | HUMAN ELEMENT | Suspect concrete boxing support peg been hammered into HV cable
14558 | 28/09/2012 | 2012 | 2012-09-28 | 19 | 30 | 570 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper G4001
14559 | 28/09/2012 | 2012 | 2012-09-28 | 100 | 30 | 3000 | C | TREE CONTACTS | Remove tree off line at G3657
14560 | 30/09/2012 | 2012 | 2012-09-30 | 150 | 225 | 25050 | C | DEFECTIVE EQUIPMENT | HV Pothead on pole W1408 blew up
14587 | 02/10/2012 | 2012 | 2012-10-02 | 350 | 70 | 24500 | B | PLANNED SHUTDOWN | replace polesH2541 - H2544
14588 | 02/10/2012 | 2012 | 2012-10-02 | 377 | 79 | 25176 | B | PLANNED SHUTDOWN | Murrae St HV upgrades, new DDO, new Tx W1037
14589 | 02/10/2012 | 2012 | 2012-10-02 | 394 | 21 | 8274 | B | PLANNED SHUTDOWN | replace poles D878 & D483 Waimaha Rd
14578 | 03/10/2012 | 2012 | 2012-10-03 | 150 | 17 | 2550 | C | DEFECTIVE EQUIPMENT | replace broken xarm
14590 | 03/10/2012 | 2012 | 2012-10-03 | 371 | 13 | 4823 | B | PLANNED SHUTDOWN | replace poles E1978, E158
14591 | 03/10/2012 | 2012 | 2012-10-03 | 192 | 362 | 68568 | B | PLANNED SHUTDOWN | Tree cutting & replace pole
14592 | 04/10/2012 | 2012 | 2012-10-04 | 329 | 9 | 2961 | B | PLANNED SHUTDOWN | replace poles A3783, A3784, A3788, A3789
14581 | 05/10/2012 | 2012 | 2012-10-05 | 489 | 422 | 18889 | C | DEFECTIVE EQUIPMENT | 11kV wire broken at pole F222
14582 | 05/10/2012 | 2012 | 2012-10-05 | 52 | 27 | 1404 | C | DEFECTIVE EQUIPMENT | repair 11kV disc on pole G2197
14580 | 06/10/2012 | 2012 | 2012-10-06 | 84 | 338 | 10456 | C | DEFECTIVE EQUIPMENT | broken insulator pole J802
14594 | 07/10/2012 | 2012 | 2012-10-07 | 253 | 43 | 10879 | B | PLANNED SHUTDOWN | replace pole F2217
14572 | 08/10/2012 | 2012 | 2012-10-08 | 31 | 467 | 12827 | C | DEFECTIVE EQUIPMENT | blown off jumper pole W978
14573 | 08/10/2012 | 2012 | 2012-10-09 | 941 | 170 | 159885 | C | TREE CONTACTS | trees caused line clash at pole W6978, flipped xarm
14579 | 08/10/2012 | 2012 | 2012-10-08 | 191 | 38 | 7258 | C | DEFECTIVE EQUIPMENT | replace broken pole J1987
14574 | 09/10/2012 | 2012 | 2012-10-09 | 753 | 75 | 6247 | C | TREE CONTACTS | trees broke wire pole H4123
14593 | 09/10/2012 | 2012 | 2012-10-09 | 265 | 61 | 6233 | B | PLANNED SHUTDOWN | replace poles G164 G166 install Gen
14595 | 10/10/2012 | 2012 | 2012-10-10 | 467 | 37 | 14461 | B | PLANNED SHUTDOWN | Install replacement poles F1322 - F1330
14596 | 10/10/2012 | 2012 | 2012-10-10 | 403 | 186 | 25458 | B | PLANNED SHUTDOWN | replace poles F1036 F1034 F1033
14597 | 11/10/2012 | 2012 | 2012-10-11 | 367 | 49 | 17983 | B | PLANNED SHUTDOWN | replace poles H2652 H2674 h2675
14598 | 12/10/2012 | 2012 | 2012-10-12 | 218 | 18 | 3924 | B | PLANNED SHUTDOWN | Replace poles Manders Rd
14606 | 13/10/2012 | 2012 | 2012-10-14 | 1336 | 332 | 326768 | C | TREE CONTACTS | trees on line w599, repair conductor
14608 | 13/10/2012 | 2012 | 2012-10-14 | 856 | 95 | 33227 | C | TREE CONTACTS | trees brought wires down at J2809
14609 | 13/10/2012 | 2012 | 2012-10-14 | 1513 | 58 | 21069 | C | TREE CONTACTS | trees brought wires down pole C846, caused fire
14610 | 13/10/2012 | 2012 | 2012-11-14 | 850 | 804 | 37644 | C | ADVERSE WEATHER | Extreme winds - conductor broke A6491 - caused fire Sirrah St
14611 | 13/10/2012 | 2012 | 2012-10-15 | 1278 | 4 | 5112 | C | ADVERSE WEATHER | extreme weather pole F4238 blown over
14612 | 13/10/2012 | 2012 | 2012-10-13 | 182 | 174 | 8698 | C | ADVERSE WEATHER | extreme winds, wire broken A4410 & A4414
14613 | 13/10/2012 | 2012 | 2012-10-14 | 775 | 17 | 13175 | C | TREE CONTACTS | tree through line D2045
14614 | 13/10/2012 | 2012 | 2012-10-13 | 36 | 375 | 9090 | C | TREE CONTACTS | trees broken wire w6369
14568 | 14/10/2012 | 2012 | 2012-10-14 | 132 | 49 | 6468 | C | TREE CONTACTS | Tree in wind flogged out shackle
14569 | 14/10/2012 | 2012 | 2012-10-14 | 37 | 21 | 777 | C | TREE CONTACTS | Burnt Xarm after tree branch hit jumper
14570 | 14/10/2012 | 2012 | 2012-10-14 | 140 | 40 | 8565 | C | DEFECTIVE EQUIPMENT | replace centre bolt, temp. replace pole
14571 | 14/10/2012 | 2012 | 2012-10-14 | 54 | 3 | 162 | C | TREE CONTACTS | tree broke wires
14604 | 14/10/2012 | 2012 | 2012-10-16 | 1384 | 16 | 39532 | C | TREE CONTACTS | Trees in line W5285 - W5276 damaged conductor - strong winds
14605 | 14/10/2012 | 2012 | 2012-10-14 | 1075 | 171 | 104390 | C | TREE CONTACTS | trees on line w916
14607 | 14/10/2012 | 2012 | 2012-10-14 | 2835 | 152 | 81758 | C | TREE CONTACTS | trees brought pole G2278 down
14577 | 15/10/2012 | 2012 | 2012-10-15 | 30 | 23 | 1150 | C | DEFECTIVE EQUIPMENT | replace broken pole
14615 | 15/10/2012 | 2012 | 2012-10-15 | 104 | 1191 | 113903 | C | DEFECTIVE EQUIPMENT | cable fault between SWGR W247 - W1074
14586 | 16/10/2012 | 2012 | 2012-10-16 | 409 | 12 | 4908 | B | PLANNED SHUTDOWN | replace poles H1531, H1511, H1517, H227
14576 | 17/10/2012 | 2012 | 2012-10-17 | 133 | 26 | 3458 | C | TREE CONTACTS | Tree vs lines, broken wires
14567 | 18/10/2012 | 2012 | 2012-10-18 | 180 | 75 | 2280 | C | TREE CONTACTS | Trees broke lines
14599 | 18/10/2012 | 2012 | 2012-10-18 | 120 | 12 | 1440 | B | PLANNED SHUTDOWN | replace poles H235 H1667 H1674
14600 | 18/10/2012 | 2012 | 2012-10-18 | 149 | 4 | 596 | B | PLANNED SHUTDOWN | Replace Tx J35
14562 | 22/10/2012 | 2012 | 2012-11-23 | 1332 | 76 | 31712 | C | TREE CONTACTS | trees brought Wire down before W312 - pole W6662
14563 | 23/10/2012 | 2012 | 2012-10-23 | 141 | 385 | 29611 | C | ADVERSE WEATHER | strong wind brought down lines
14564 | 23/10/2012 | 2012 | 2012-10-23 | 385 | 166 | 42083 | C | TREE CONTACTS | Tree vs line in wind
14601 | 24/10/2012 | 2012 | 2012-10-24 | 407 | 255 | 23562 | B | PLANNED SHUTDOWN | cut jumpers @ A268
14561 | 25/10/2012 | 2012 | 2012-10-25 | 75 | 704 | 38513 | C | DEFECTIVE EQUIPMENT | HV cable blow up
14602 | 25/10/2012 | 2012 | 2012-10-25 | 284 | 49 | 13916 | B | PLANNED SHUTDOWN | Replace poles H2652 H2674 H2675
14603 | 26/10/2012 | 2012 | 2012-10-26 | 137 | 73 | 10001 | B | PLANNED SHUTDOWN | Replace pole G166
14585 | 28/10/2012 | 2012 | 2012-10-28 | 418 | 28 | 11704 | B | PLANNED SHUTDOWN | replace pole B1510, B2219 + LV alterations
14583 | 31/10/2012 | 2012 | 2012-10-31 | 395 | 24 | 4740 | B | PLANNED SHUTDOWN | replace poles H235 & H1667
14584 | 31/10/2012 | 2012 | 2012-10-31 | 340 | 49 | 16660 | B | PLANNED SHUTDOWN | replace Tx A351
14616 | 01/11/2012 | 2012 | 2012-11-01 | 25 | 60 | 1500 | C | DEFECTIVE EQUIPMENT | Replace insulator pole F3447 Te Karaka
14617 | 01/11/2012 | 2012 | 2012-11-01 | 52 | 7 | 354 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole H61 Ihungia Rd
14635 | 01/11/2012 | 2012 | 2012-11-01 | 348 | 49 | 17052 | B | PLANNED SHUTDOWN | Replace poles H2652 H2674 H2642 Waima Rd
14636 | 03/11/2012 | 2012 | 2012-11-03 | 89 | 104 | 9256 | B | PLANNED SHUTDOWN | Isolate 11kV lines pole C92 Campion Rd for building shift
14618 | 06/11/2012 | 2012 | 2012-11-06 | 406 | 126 | 51156 | C | DEFECTIVE EQUIPMENT | Replace polymers pole J4415 Te Araroa
14619 | 08/11/2012 | 2012 | 2012-11-08 | 447 | 10 | 4470 | C | TREE CONTACTS | Replace Xarm pole W7043 & cut trees Ohuka Rd
14620 | 08/11/2012 | 2012 | 2012-11-08 | 70 | 5 | 350 | C | TREE CONTACTS | Repair 11kV lines pole W101 Ohuia
14637 | 08/11/2012 | 2012 | 2012-11-08 | 268 | 19 | 5092 | B | PLANNED SHUTDOWN | Repair LBS J45 Poroporo
14638 | 08/11/2012 | 2012 | 2012-11-08 | 324 | 62 | 6012 | B | PLANNED SHUTDOWN | Replace 11kV poles H2222 H2212 & Tx on pole H244 Waipiro Bay Rd
14639 | 10/11/2012 | 2012 | 2012-11-10 | 50 | 253 | 12650 | B | PLANNED SHUTDOWN | Repair 11kV ABS A244 Endcliffe Rd
14641 | 13/11/2012 | 2012 | 2012-11-13 | 246 | 78 | 19188 | B | PLANNED SHUTDOWN | Replace poles J4472 J4475 J4476 J377 Waikura Valley
14621 | 14/11/2012 | 2012 | 2012-11-14 | 121 | 46 | 5566 | C | TREE CONTACTS | Repair 11kV lines poles W8991 to W8992 Mahia
14622 | 14/11/2012 | 2012 | 2012-11-14 | 19 | 8 | 152 | C | DEFECTIVE EQUIPMENT | Replace Xarm pole W492 Mangone
14623 | 14/11/2012 | 2012 | 2012-11-14 | 31 | 19 | 589 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W554 Ruapapa Rd
14624 | 18/11/2012 | 2012 | 2012-11-18 | 611 | 184 | 21479 | C | TREE CONTACTS | Repair 11kV lines poles H2853 to H2235 Waipiro Bay Rd
14642 | 20/11/2012 | 2012 | 2012-11-20 | 440 | 55 | 5846 | B | PLANNED SHUTDOWN | Replace 11kV poles D5003 D1413 Wharekopae Rd
14648 | 20/11/2012 | 2012 | 2012-11-20 | 117 | 93 | 10881 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting B193 to B6206 Balance St
14625 | 21/11/2012 | 2012 | 2012-11-21 | 279 | 65 | 9110 | C | TREE CONTACTS | Repair 11kV lines pole F1884 Whakarau Rd
14643 | 21/11/2012 | 2012 | 2012-11-21 | 374 | 55 | 4838 | B | PLANNED SHUTDOWN | Replace 11kV poles D5015 D5016 Wharekopae Rd
14645 | 21/11/2012 | 2012 | 2012-11-21 | 189 | 18 | 3402 | B | PLANNED SHUTDOWN | Replace 11kV pole E1978 Te Hau Rd Whatatutu
14644 | 22/11/2012 | 2012 | 2012-11-22 | 349 | 96 | 33504 | B | PLANNED SHUTDOWN | Replace Tx B34 Victoria St
14626 | 23/11/2012 | 2012 | 2012-11-23 | 129 | 858 | 44208 | C | DEFECTIVE EQUIPMENT | Isolate 11kV cable Between B485 to B484 Centennial Cres
14627 | 23/11/2012 | 2012 | 2012-11-23 | 91 | 42 | 3822 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole A87 Goodwins Rd
14646 | 23/11/2012 | 2012 | 2012-11-23 | 351 | 12 | 4212 | B | PLANNED SHUTDOWN | Replace 11kV tx pole C385 Nelson Rd
14628 | 24/11/2012 | 2012 | 2012-11-24 | 124 | 498 | 23904 | C | TREE CONTACTS | Repair 11kV lines pole A4309 Goodwins Rd
14629 | 25/11/2012 | 2012 | 2012-11-25 | 508 | 279 | 55185 | C | FOREIGN INTERFERENCE | Replace 11kV pole W1117 Omana Crn Nuhaka
14630 | 26/11/2012 | 2012 | 2012-11-26 | 457 | 65 | 13295 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W1117 Omana Crn Nuhaka
14647 | 27/11/2012 | 2012 | 2012-11-27 | 365 | 226 | 45786 | B | PLANNED SHUTDOWN | Replace 11kV poles J4472 J4475 J4476 Waikura Valley
14631 | 28/11/2012 | 2012 | 2012-11-28 | 244 | 170 | 8636 | C | TREE CONTACTS | Repair 11kV lines pole W5075 Otoi Rd
14640 | 29/11/2012 | 2012 | 2012-11-29 | 285 | 49 | 13965 | B | PLANNED SHUTDOWN | Replace 11kV poles J4214 J4217 Waikura Valley
14632 | 30/11/2012 | 2012 | 2012-11-30 | 78 | 16 | 1278 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole W1184 Awamate Rd
14633 | 30/11/2012 | 2012 | 2012-11-30 | 126 | 62 | 4622 | C | FOREIGN INTERFERENCE | Replace 11kV pole F1796 hit by digger Whakarau Rd
14634 | 30/11/2012 | 2012 | 2012-11-30 | 53 | 9 | 477 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole E9 Manders Rd
14649 | 01/12/2012 | 2012 | 2012-12-01 | 49 | 49 | 2401 | C | DEFECTIVE EQUIPMENT | Cable fault between N502 & N231 Affco Site
14662 | 01/12/2012 | 2012 | 2012-12-01 | 135 | 13 | 1755 | B | PLANNED SHUTDOWN | Isolate 11kV lines pole C242 Mc Donalds Rd
14650 | 04/12/2012 | 2012 | 2012-12-04 | 197 | 724 | 22748 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines poles W6083 to W6084 Mangapoikie Rd
14663 | 04/12/2012 | 2012 | 2012-12-04 | 392 | 11 | 4312 | B | PLANNED SHUTDOWN | Replace 11kV poles F1531 F1526 F1520 Whakarau Rd
14671 | 04/12/2012 | 2012 | 2012-12-04 | 364 | 26 | 16796 | B | PLANNED SHUTDOWN | Install new 11kV pole between poles W7017 to W7018 Ruakituri Valley
14664 | 05/12/2012 | 2012 | 2012-12-05 | 357 | 13 | 4611 | B | PLANNED SHUTDOWN | Replace 11kV poles F2260 F2253 F2249 Whakarau Rd
14651 | 06/12/2012 | 2012 | 2012-12-06 | 267 | 132 | 34122 | C | TREE CONTACTS | Repair lines poles W1779 to W7485 Ruakituri
14652 | 06/12/2012 | 2012 | 2012-12-06 | 57 | 12 | 684 | C | TREE CONTACTS | Remove tree from 11kV lines poles J2707 to J2708 Mangaoporo
14653 | 06/12/2012 | 2012 | 2012-12-06 | 185 | 86 | 15910 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J1350 Harrison Rd Ruatoria
14654 | 06/12/2012 | 2012 | 2012-12-06 | 18 | 170 | 1318 | C | ADVERSE WEATHER | Reclose CB 24 Ruakituri at Tuai High Winds
14655 | 07/12/2012 | 2012 | 2012-12-07 | 405 | 1526 | 96028 | C | FOREIGN INTERFERENCE | Replace 11kV pole B4873 Russell St
14656 | 07/12/2012 | 2012 | 2012-12-07 | 192 | 86 | 16512 | C | FOREIGN INTERFERENCE | Replace 11kV pole J1748 Ruatoria
14667 | 07/12/2012 | 2012 | 2012-12-07 | 418 | 13 | 5434 | B | PLANNED SHUTDOWN | Replace 11kV poles F79 F2240 F1792 Whakarau Rd
14668 | 08/12/2012 | 2012 | 2012-12-08 | 142 | 74 | 6332 | B | PLANNED SHUTDOWN | Install DDO fuses pole C2507 Nelson Rd
14657 | 09/12/2012 | 2012 | 2012-12-09 | 362 | 95 | 12585 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable SW/GR B6276 Awapuni Rd
14658 | 11/12/2012 | 2012 | 2012-12-11 | 71 | 40 | 2040 | C | TREE CONTACTS | Install DDO fuses pole W5685 Raupunga
14666 | 11/12/2012 | 2012 | 2012-12-11 | 118 | 31 | 3658 | B | PLANNED SHUTDOWN | Isolate 11kV lines poles D431 to D625 Harpers Rd tree cutting
14669 | 13/12/2012 | 2012 | 2012-12-13 | 484 | 74 | 35816 | B | PLANNED SHUTDOWN | Replace 11kV poles W6342 W6244 W6355 W6356 W6359 Raupunga
14659 | 14/12/2012 | 2012 | 2012-12-14 | 128 | 76 | 9728 | C | TREE CONTACTS | Repair 11kV lines poles G4204 to G4025 Three Bridges
14670 | 14/12/2012 | 2012 | 2012-12-14 | 360 | 41 | 14760 | B | PLANNED SHUTDOWN | Replace 11kV poles W6268 & W6270 Waihua Hill
14672 | 17/12/2012 | 2012 | 2012-12-17 | 310 | 49 | 15190 | B | PLANNED SHUTDOWN | Isolate 11kV lines J129 for tree cutting
14665 | 18/12/2012 | 2012 | 2012-12-18 | 290 | 9 | 2610 | B | PLANNED SHUTDOWN | Replace 11kV pole E187 Armstrong Rd
14673 | 20/12/2012 | 2012 | 2012-12-20 | 338 | 9 | 3042 | B | PLANNED SHUTDOWN | Replace 11kV poles A3797 A3798 A3799 Stevens Rd
14660 | 23/12/2012 | 2012 | 2012-12-23 | 581 | 421 | 50953 | C | DEFECTIVE EQUIPMENT | Replace insulators pole J2441 Te Hue Rd Crn
14661 | 28/12/2012 | 2012 | 2012-12-28 | 59 | 151 | 4589 | C | DEFECTIVE EQUIPMENT | Isolate 11kV cable between switches B251 to B371 Cosy Club
14675 | 07/01/2013 | 2012 | 2013-01-07 | 59 | 1272 | 52564 | C | DEFECTIVE EQUIPMENT | Replace burnt 50kV pole H709 Ruatoria
14676 | 10/01/2013 | 2012 | 2013-01-10 | 189 | 498 | 28458 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A4204 Riverside Rd
14677 | 10/01/2013 | 2012 | 2013-01-10 | 24 | 65 | 1560 | C | UNKNOWN | Reclose F419 Whakarau Rd cause unknown
14678 | 10/01/2013 | 2012 | 2013-01-10 | 129 | 191 | 24920 | C | TREE CONTACTS | Repair 11kV lines pole C4037 Taurau Valley
14686 | 10/01/2013 | 2012 | 2013-01-10 | 312 | 41 | 12792 | B | PLANNED SHUTDOWN | Replace 11kV poles H1713 H1721 H1722 Makarika Rd
14688 | 11/01/2013 | 2012 | 2013-01-11 | 258 | 9 | 2322 | B | PLANNED SHUTDOWN | Replace 11kV poles A3783 A3784 A3788 Stevens Rd
14680 | 13/01/2013 | 2012 | 2013-01-13 | 38 | 1009 | 33448 | C | FOREIGN INTERFERENCE | Reclose CB95 at Makaraka Sub Bird Strike pole C1501
14689 | 13/01/2013 | 2012 | 2013-01-13 | 65 | 44 | 2860 | B | PLANNED SHUTDOWN | Remove ABS B746 Awapuni Rd
14696 | 13/01/2013 | 2012 | 2013-01-13 | 242 | 46 | 6407 | B | PLANNED SHUTDOWN | Replace 11kV poles H197 Ruatoria South
14692 | 14/01/2013 | 2012 | 2013-01-14 | 290 | 18 | 5220 | B | PLANNED SHUTDOWN | Replace poles D2976 D5225 Settlement Rd
14679 | 15/01/2013 | 2012 | 2013-01-15 | 32 | 161 | 5152 | C | DEFECTIVE EQUIPMENT | Replace DDO fuses pole C141 Pakawhai Rd
14690 | 17/01/2013 | 2012 | 2013-01-17 | 290 | 41 | 11890 | B | PLANNED SHUTDOWN | Replace 11kV poles H1667 H1674 H1675 Makarika Rd
14681 | 18/01/2013 | 2012 | 2013-01-18 | 11 | 2516 | 27676 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
14682 | 18/01/2013 | 2012 | 2013-01-18 | 248 | 34 | 8432 | C | TREE CONTACTS | Cut trees pole G367 Tauwhareparae Rd
14691 | 18/01/2013 | 2012 | 2013-01-18 | 184 | 252 | 41484 | B | PLANNED SHUTDOWN | Replace ABS A244 Endcliffe Rd
14683 | 19/01/2013 | 2012 | 2013-01-19 | 12 | 945 | 4792 | C | UNKNOWN | Reclose CB 95 Makaraka Sub Suspect fault T/x C500 Bck Ormond Rd
14684 | 22/01/2013 | 2012 | 2013-01-22 | 1440 | 67 | 96480 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable B254 to B766 Sheridan St
14694 | 22/01/2013 | 2012 | 2013-01-22 | 420 | 34 | 16476 | B | PLANNED SHUTDOWN | Replace 11kV poles D1565 D5194 D5181 D5185 Tahora Rd
14695 | 24/01/2013 | 2012 | 2013-01-24 | 333 | 34 | 11322 | B | PLANNED SHUTDOWN | Replace 11kV poles H2840 Waipiro Bay Rd
14687 | 25/01/2013 | 2012 | 2013-01-25 | 406 | 80 | 11048 | B | PLANNED SHUTDOWN | Reposition 2 11kV poles A1223 & A1229 Pa Rd Whangara
14693 | 25/01/2013 | 2012 | 2013-01-25 | 400 | 70 | 6700 | B | PLANNED SHUTDOWN | Replace 11kV poles H2541 H2542 Arthur St Tokomaru Bay
14685 | 31/01/2013 | 2012 | 2013-01-31 | 194 | 12 | 2328 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H1511 Horehore Rd
14707 | 01/02/2013 | 2012 | 2013-02-01 | 334 | 49 | 16366 | B | PLANNED SHUTDOWN | Replace 11kV poles H2667 H2694 H4341 Waima Rd
14697 | 04/02/2013 | 2012 | 2013-02-04 | 21 | 170 | 3321 | C | ADVERSE WEATHER | Reclose CB 24 Ruakituri Feeder atTuai Sub High Winds
14706 | 04/02/2013 | 2012 | 2013-02-04 | 460 | 14 | 11900 | B | PLANNED SHUTDOWN | Replace 11kV poles D5195 D5193 D5198 Tahora Rd
14708 | 05/02/2013 | 2012 | 2013-02-05 | 293 | 32 | 9376 | B | PLANNED SHUTDOWN | Replace 11kV pole B1991 Matokitoki Valley
14709 | 05/02/2013 | 2012 | 2013-02-05 | 178 | 17 | 914 | B | PLANNED SHUTDOWN | Straighten 11kV poles G1883 & G274 Paremata Rd
14710 | 07/02/2013 | 2012 | 2013-02-07 | 330 | 13 | 4290 | B | PLANNED SHUTDOWN | Replace 11kV poles F1770 F1732 F1776 F1779 Whakarau Rd
14698 | 11/02/2013 | 2012 | 2013-02-11 | 5855 | 10 | 58550 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable fault between C3922 to C3102 Kemps Rd
14699 | 11/02/2013 | 2012 | 2013-02-11 | 135 | 90 | 6710 | C | FOREIGN INTERFERENCE | Cut jumpers pole G4118 Mangatuna Truck hit pole
14712 | 11/02/2013 | 2012 | 2013-02-11 | 58 | 103 | 5974 | B | PLANNED SHUTDOWN | Install DDO fuses pole C1507 Bck Ormond Rd
14711 | 12/02/2013 | 2012 | 2013-02-12 | 448 | 60 | 32904 | B | PLANNED SHUTDOWN | Replace 11kV poles D149 D5120 Tahora Rd
14713 | 13/02/2013 | 2012 | 2013-02-13 | 425 | 12 | 5100 | B | PLANNED SHUTDOWN | Isolate 11kV lines at pole J216 for tree cutting Mangaproporo Valley
14714 | 13/02/2013 | 2012 | 2013-02-13 | 55 | 260 | 14300 | B | PLANNED SHUTDOWN | Isolate 11kV lines at pole CB F406 for tree cutting Whatatutu
14715 | 14/02/2013 | 2012 | 2013-02-14 | 413 | 70 | 8789 | B | PLANNED SHUTDOWN | Replace 11kV poles H2547 H2538 Arthur St Tokomaru Bay
14716 | 15/02/2013 | 2012 | 2013-02-15 | 463 | 52 | 24076 | B | PLANNED SHUTDOWN | Replace 11kV poles G2088 G2096 Tauwhareparae Rd
14700 | 16/02/2013 | 2012 | 2013-02-16 | 23 | 75 | 1725 | C | ADVERSE WEATHER | Reclose CB H341 Mata Rd lightining in Area
14701 | 20/02/2013 | 2012 | 2013-03-20 | 103 | 114 | 8080 | C | UNKNOWN | Reclose CB D644 Muriwai at Patutahi Sub cause unknown
14702 | 21/02/2013 | 2012 | 2013-02-21 | 136 | 173 | 23528 | C | FOREIGN INTERFERENCE | Isolate 11kV at pole E51to remove crashed Truck Ormond
14718 | 21/02/2013 | 2012 | 2013-02-21 | 359 | 16 | 5744 | B | PLANNED SHUTDOWN | Replace 11kV poles W6369 W6371 W75 Raupunga
14703 | 22/02/2013 | 2012 | 2013-02-22 | 19 | 498 | 9462 | C | DEFECTIVE EQUIPMENT | Repair 2 - 11kV jumpers pole W5651 Frasertown
14704 | 23/02/2013 | 2012 | 2013-02-23 | 75 | 226 | 14035 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole E2359 Ormond
14721 | 24/02/2013 | 2012 | 2013-02-24 | 93 | 361 | 33382 | B | PLANNED SHUTDOWN | 11kV Line Maintenance Tuai Area CB23 & CB24
14705 | 25/02/2013 | 2012 | 2013-02-25 | 393 | 32 | 12576 | C | TREE CONTACTS | Repair 11kV lines pole D1048 Parakanapa Rd
14719 | 27/02/2013 | 2012 | 2013-02-27 | 380 | 41 | 15580 | B | PLANNED SHUTDOWN | Replace 11kV poles W6251 W6256 W6258 W6261 Raupunga
14720 | 28/02/2013 | 2012 | 2013-02-28 | 480 | 11 | 5280 | B | PLANNED SHUTDOWN | Isolate 11kVat pole A547 for tree cutting Goodwins Rd
14722 | 01/03/2013 | 2012 | 2013-03-01 | 112 | 138 | 11005 | C | TREE CONTACTS | Repair 11kV lines pole W 4465 Ohuka Rd
14723 | 01/03/2013 | 2012 | 2013-03-01 | 69 | 5458 | 260979 | C | UNKNOWN | Reclose CB 182 Makaraka at Gisborne Sub cause unknown
14740 | 01/03/2013 | 2012 | 2013-03-01 | 252 | 33 | 8316 | B | PLANNED SHUTDOWN | Replace 11kV poles W6322 W6329 W6330 W6341 W6345 W6354 Raupunga
14724 | 03/03/2013 | 2012 | 2013-03-03 | 67 | 95 | 6365 | C | FOREIGN INTERFERENCE | Replace Xarm pole C5810 Main Rd Makaraka
14741 | 05/03/2013 | 2012 | 2013-03-05 | 83 | 662 | 92010 | B | PLANNED SHUTDOWN | Cut jumpers poles W8892 & W8895 for Voltage Regulator Change
14725 | 06/03/2013 | 2012 | 2013-03-06 | 125 | 643 | 18373 | C | TREE CONTACTS | Repair 11kV lines pole W5866 Brownlie Rd
14742 | 06/03/2013 | 2012 | 2013-03-06 | 572 | 133 | 76076 | B | PLANNED SHUTDOWN | Install New ABS's poles W3939 & W5726 Raupunga
14743 | 06/03/2013 | 2012 | 2013-03-06 | 163 | 8 | 1304 | B | PLANNED SHUTDOWN | Replace UG cable to T/x W1521 Carroll St
14744 | 08/03/2013 | 2012 | 2013-03-08 | 318 | 5 | 1590 | B | PLANNED SHUTDOWN | Replace 11kV poles W6429 W6426 W6425 W6415 W6410 Raupunga
14726 | 10/03/2013 | 2012 | 2013-03-10 | 170 | 81 | 9534 | C | FOREIGN INTERFERENCE | Reclose CB E864 Waimata Valley Bird on wire pole G1169
14727 | 11/03/2013 | 2012 | 2013-03-11 | 31 | 216 | 6353 | C | UNKNOWN | Reclose CB C95 Haisman Rd cause unknown
14745 | 12/03/2013 | 2012 | 2013-03-12 | 358 | 24 | 8592 | B | PLANNED SHUTDOWN | Replace 11kV poles W8518 W8523 Harrison Rd
14728 | 14/03/2013 | 2012 | 2013-03-14 | 56 | 31 | 1736 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole E316 Wairere Rd Whatatutu
14746 | 14/03/2013 | 2012 | 2013-03-14 | 377 | 33 | 12441 | B | PLANNED SHUTDOWN | Replace 11kV poles W1717 W5707 W5706 W5703 Raupunga
14729 | 17/03/2013 | 2012 | 2013-03-17 | 153 | 868 | 75396 | C | ADVERSE WEATHER | Repair 11kV lines Pole W9139 Mahia
14747 | 19/03/2013 | 2012 | 2013-03-19 | 495 | 51 | 14608 | B | PLANNED SHUTDOWN | Replace 11kV poles D5087 D5085 D5066 D5062 D5061 Wharekopae Rd
14730 | 20/03/2013 | 2012 | 2013-03-20 | 14 | 6958 | 64677 | C | FOREIGN INTERFERENCE | Reclose CB 192 Carnarvon at Gisborne Sub digger hit lines pole B1854
14731 | 20/03/2013 | 2012 | 2013-03-20 | 484 | 261 | 126324 | C | FOREIGN INTERFERENCE | Replace T/x pole J306 Te Araroa hit by Car
14732 | 21/03/2013 | 2012 | 2013-03-21 | 118 | 1364 | 68516 | C | DEFECTIVE EQUIPMENT | Isolate 11kV cable fault between B351 to B4070 Wi Pere St
14733 | 22/03/2013 | 2012 | 2013-03-22 | 64 | 11 | 704 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole W5121 Putere
14749 | 22/03/2013 | 2012 | 2013-03-22 | 420 | 128 | 35390 | B | PLANNED SHUTDOWN | Replace 11kV poles W5833 W751 W1717 W5712 Raupunga
14734 | 25/03/2013 | 2012 | 2013-03-25 | 69 | 74 | 5106 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W7634 Mahia
14735 | 25/03/2013 | 2012 | 2013-03-25 | 158 | 33 | 5214 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W5707 Raupunga
14748 | 25/03/2013 | 2012 | 2013-03-25 | 61 | 662 | 66862 | B | PLANNED SHUTDOWN | Replace ABS W945 at Mahia Regulator
14736 | 26/03/2013 | 2012 | 2013-03-26 | 111 | 58 | 6438 | C | TREE CONTACTS | Repair 11kV lines pole C3316 to C3317 Waingake Rd
14751 | 26/03/2013 | 2012 | 2013-03-26 | 400 | 3 | 1200 | B | PLANNED SHUTDOWN | Isolate for tree cutting pole H1803 Kopuaroa
14752 | 26/03/2013 | 2012 | 2013-03-26 | 360 | 4 | 1440 | B | PLANNED SHUTDOWN | Replace 11kV poles H197 H198 Ruatoria South
14753 | 26/03/2013 | 2012 | 2013-03-26 | 392 | 171 | 30002 | B | PLANNED SHUTDOWN | Replace 11kV pole E2359 Ormond
14750 | 27/03/2013 | 2012 | 2013-03-27 | 374 | 3 | 1122 | B | PLANNED SHUTDOWN | Isolate for tree cutting H1803 Kopuaroa
14754 | 27/03/2013 | 2012 | 2013-03-27 | 352 | 25 | 8800 | B | PLANNED SHUTDOWN | Replace 11kV pole H1667 Matahiia Rd
14737 | 28/03/2013 | 2012 | 2013-03-28 | 382 | 7 | 2674 | C | DEFECTIVE EQUIPMENT | Replace 11kV poles G2232 G1755 G2118 Takapau Rd
14755 | 28/03/2013 | 2012 | 2013-03-28 | 9 | 25 | 425 | B | PLANNED SHUTDOWN | Install New SW/GR C6631 Aerodrome Rd
14738 | 30/03/2013 | 2012 | 2013-03-30 | 62 | 36 | 2232 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W8280 Whakaki
14739 | 30/03/2013 | 2012 | 2013-03-30 | 46 | 46 | 2116 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W943 Kinikini

## 20122013DailyTotals
Date Outage | YEAR | Duration of Outage | Customers Impacted | Total Customer Minutes Lost
02/04/2012 | 2012 | 278 | 150 | 11940
03/04/2012 | 2012 | 1378 | 551 | 50159
04/04/2012 | 2012 | 62 | 51 | 2169
05/04/2012 | 2012 | 428 | 734 | 49198
06/04/2012 | 2012 | 337 | 69 | 23253
08/04/2012 | 2012 | 60 | 1945 | 31216
09/04/2012 | 2012 | 25 | 77 | 1925
10/04/2012 | 2012 | 577 | 12 | 4204
12/04/2012 | 2012 | 90 | 10 | 900
13/04/2012 | 2012 | 354 | 51 | 18054
16/04/2012 | 2012 | 276 | 230 | 19222
17/04/2012 | 2012 | 460 | 292 | 39634
18/04/2012 | 2012 | 284 | 37 | 10508
19/04/2012 | 2012 | 428 | 46 | 17750
20/04/2012 | 2012 | 404 | 340 | 32360
23/04/2012 | 2012 | 90 | 101 | 4956
24/04/2012 | 2012 | 325 | 34 | 11050
26/04/2012 | 2012 | 1197 | 294 | 33112
27/04/2012 | 2012 | 54 | 15 | 1455
28/04/2012 | 2012 | 590 | 51 | 32202
30/04/2012 | 2012 | 121 | 198 | 16229
01/05/2012 | 2012 | 1134 | 166 | 81156
02/05/2012 | 2012 | 98 | 173 | 15172
03/05/2012 | 2012 | 94 | 226 | 21244
07/05/2012 | 2012 | 233 | 283 | 16463
08/05/2012 | 2012 | 157 | 126 | 16028
09/05/2012 | 2012 | 295 | 100 | 22098
11/05/2012 | 2012 | 4 | 93 | 372
15/05/2012 | 2012 | 293 | 65 | 9782
16/05/2012 | 2012 | 403 | 38 | 9184
17/05/2012 | 2012 | 14 | 70 | 980
18/05/2012 | 2012 | 445 | 26 | 8580
21/05/2012 | 2012 | 140 | 21 | 2940
22/05/2012 | 2012 | 358 | 100 | 15464
23/05/2012 | 2012 | 378 | 13 | 4914
25/05/2012 | 2012 | 360 | 6 | 2160
26/05/2012 | 2012 | 110 | 17 | 1870
28/05/2012 | 2012 | 393 | 13 | 5109
29/05/2012 | 2012 | 313 | 25 | 7825
30/05/2012 | 2012 | 377 | 246 | 36218
01/06/2012 | 2012 | 365 | 13 | 4745
05/06/2012 | 2012 | 697 | 42 | 21865
06/06/2012 | 2012 | 1795 | 123 | 18441
07/06/2012 | 2012 | 230 | 93 | 21390
08/06/2012 | 2012 | 323 | 94 | 10704
12/06/2012 | 2012 | 125 | 260 | 16307
13/06/2012 | 2012 | 428 | 43 | 15580
14/06/2012 | 2012 | 319 | 25 | 7975
15/06/2012 | 2012 | 405 | 208 | 44613
18/06/2012 | 2012 | 29 | 3429 | 11884
19/06/2012 | 2012 | 149 | 938 | 26402
20/06/2012 | 2012 | 333 | 9 | 2997
21/06/2012 | 2012 | 359 | 170 | 34296
22/06/2012 | 2012 | 176 | 128 | 9298
23/06/2012 | 2012 | 508 | 1184 | 205377
24/06/2012 | 2012 | 1152 | 128 | 22018
25/06/2012 | 2012 | 385 | 985 | 17968
26/06/2012 | 2012 | 46 | 1700 | 53422
27/06/2012 | 2012 | 187 | 156 | 18722
28/06/2012 | 2012 | 171 | 479 | 54824
29/06/2012 | 2012 | 319 | 39 | 7352.64
30/06/2012 | 2012 | 465 | 81 | 17471
01/07/2012 | 2012 | 402 | 1404 | 83302
02/07/2012 | 2012 | 84 | 202 | 12093
03/07/2012 | 2012 | 363 | 70 | 25410
04/07/2012 | 2012 | 379 | 127 | 10018
05/07/2012 | 2012 | 427 | 219 | 27339
06/07/2012 | 2012 | 417 | 189 | 32078
09/07/2012 | 2012 | 111 | 44 | 4884
10/07/2012 | 2012 | 325 | 159 | 10084
11/07/2012 | 2012 | 284 | 20 | 5680
12/07/2012 | 2012 | 315 | 115 | 17793
13/07/2012 | 2012 | 63 | 13 | 819
15/07/2012 | 2012 | 40 | 196 | 6241
16/07/2012 | 2012 | 290 | 510 | 88284
17/07/2012 | 2012 | 368 | 115 | 18768
20/07/2012 | 2012 | 291 | 14 | 4074
22/07/2012 | 2012 | 344 | 43 | 15965
24/07/2012 | 2012 | 35 | 204 | 8364
25/07/2012 | 2012 | 371 | 144 | 24216
26/07/2012 | 2012 | 943 | 233 | 33545
27/07/2012 | 2012 | 1111 | 559 | 131934
29/07/2012 | 2012 | 204 | 170 | 7874
30/07/2012 | 2012 | 179 | 234 | 16532
31/07/2012 | 2012 | 355 | 1126 | 24899
01/08/2012 | 2012 | 302 | 3 | 906
02/08/2012 | 2012 | 120 | 58 | 4962
03/08/2012 | 2012 | 856 | 1384 | 73747
04/08/2012 | 2012 | 293 | 108 | 17453
06/08/2012 | 2012 | 65 | 8069 | 168935
07/08/2012 | 2012 | 366 | 67 | 3795
08/08/2012 | 2012 | 435 | 282 | 29484
09/08/2012 | 2012 | 409 | 84 | 8713
10/08/2012 | 2012 | 208 | 52 | 5138
12/08/2012 | 2012 | 461 | 121 | 10011
13/08/2012 | 2012 | 125 | 19 | 2375
14/08/2012 | 2012 | 474 | 215 | 27686
15/08/2012 | 2012 | 148 | 304 | 20839
16/08/2012 | 2012 | 377 | 22 | 5641
19/08/2012 | 2012 | 271 | 32 | 8672
20/08/2012 | 2012 | 60 | 10 | 600
21/08/2012 | 2012 | 374 | 12 | 3680
22/08/2012 | 2012 | 458 | 117 | 26124
23/08/2012 | 2012 | 307 | 13 | 3991
24/08/2012 | 2012 | 434 | 21 | 35679
25/08/2012 | 2012 | 161 | 272 | 17684
28/08/2012 | 2012 | 308 | 10 | 3080
29/08/2012 | 2012 | 102 | 18 | 1836
01/09/2012 | 2012 | 314 | 16 | 5024
04/09/2012 | 2012 | 543 | 918 | 75363
06/09/2012 | 2012 | 507 | 73 | 27183
07/09/2012 | 2012 | 520 | 3561 | 149117
08/09/2012 | 2012 | 748 | 253 | 90874
09/09/2012 | 2012 | 1621 | 29 | 47009
10/09/2012 | 2012 | 118 | 839 | 31180
11/09/2012 | 2012 | 1241 | 159 | 34314
12/09/2012 | 2012 | 388 | 73 | 5484
13/09/2012 | 2012 | 37 | 23 | 851
14/09/2012 | 2012 | 130 | 112 | 12960
15/09/2012 | 2012 | 15 | 6958 | 104370
16/09/2012 | 2012 | 123 | 151 | 9064
17/09/2012 | 2012 | 114 | 385 | 22189
18/09/2012 | 2012 | 376 | 31 | 6406
19/09/2012 | 2012 | 360 | 8 | 2880
20/09/2012 | 2012 | 404 | 84 | 20152
24/09/2012 | 2012 | 360 | 73 | 26280
26/09/2012 | 2012 | 316 | 8 | 2528
27/09/2012 | 2012 | 325 | 9 | 2925
28/09/2012 | 2012 | 815 | 5328 | 129040
30/09/2012 | 2012 | 150 | 225 | 25050
02/10/2012 | 2012 | 394 | 170 | 57950
03/10/2012 | 2012 | 371 | 392 | 75941
04/10/2012 | 2012 | 329 | 9 | 2961
05/10/2012 | 2012 | 489 | 449 | 20293
06/10/2012 | 2012 | 84 | 338 | 10456
07/10/2012 | 2012 | 253 | 43 | 10879
08/10/2012 | 2012 | 941 | 675 | 179970
09/10/2012 | 2012 | 753 | 136 | 12480
10/10/2012 | 2012 | 467 | 223 | 39919
11/10/2012 | 2012 | 367 | 49 | 17983
12/10/2012 | 2012 | 218 | 18 | 3924
13/10/2012 | 2012 | 1513 | 1859 | 454783
14/10/2012 | 2012 | 2835 | 452 | 241652
15/10/2012 | 2012 | 104 | 1214 | 115053
16/10/2012 | 2012 | 409 | 12 | 4908
17/10/2012 | 2012 | 133 | 26 | 3458
18/10/2012 | 2012 | 180 | 91 | 4316
22/10/2012 | 2012 | 1332 | 76 | 31712
23/10/2012 | 2012 | 385 | 551 | 71694
24/10/2012 | 2012 | 407 | 255 | 23562
25/10/2012 | 2012 | 284 | 753 | 52429
26/10/2012 | 2012 | 137 | 73 | 10001
28/10/2012 | 2012 | 418 | 28 | 11704
31/10/2012 | 2012 | 395 | 73 | 21400
01/11/2012 | 2012 | 348 | 116 | 18906
03/11/2012 | 2012 | 89 | 104 | 9256
06/11/2012 | 2012 | 406 | 126 | 51156
08/11/2012 | 2012 | 447 | 96 | 15924
10/11/2012 | 2012 | 50 | 253 | 12650
13/11/2012 | 2012 | 246 | 78 | 19188
14/11/2012 | 2012 | 121 | 73 | 6307
18/11/2012 | 2012 | 611 | 184 | 21479
20/11/2012 | 2012 | 440 | 148 | 16727
21/11/2012 | 2012 | 374 | 138 | 17350
22/11/2012 | 2012 | 349 | 96 | 33504
23/11/2012 | 2012 | 351 | 912 | 52242
24/11/2012 | 2012 | 124 | 498 | 23904 | 0.020833
25/11/2012 | 2012 | 508 | 279 | 55185
26/11/2012 | 2012 | 457 | 65 | 13295
27/11/2012 | 2012 | 365 | 226 | 45786
28/11/2012 | 2012 | 244 | 170 | 8636
29/11/2012 | 2012 | 285 | 49 | 13965
30/11/2012 | 2012 | 126 | 87 | 6377
01/12/2012 | 2012 | 135 | 62 | 4156
04/12/2012 | 2012 | 392 | 761 | 43856
05/12/2012 | 2012 | 357 | 13 | 4611
06/12/2012 | 2012 | 267 | 400 | 52034
07/12/2012 | 2012 | 418 | 1625 | 117974
08/12/2012 | 2012 | 142 | 74 | 6332
09/12/2012 | 2012 | 362 | 95 | 12585
11/12/2012 | 2012 | 118 | 71 | 5698
13/12/2012 | 2012 | 484 | 74 | 35816
14/12/2012 | 2012 | 360 | 117 | 24488
17/12/2012 | 2012 | 310 | 49 | 15190
18/12/2012 | 2012 | 290 | 9 | 2610
20/12/2012 | 2012 | 338 | 9 | 3042
23/12/2012 | 2012 | 581 | 421 | 50953
28/12/2012 | 2012 | 59 | 151 | 4589
07/01/2013 | 2012 | 59 | 1272 | 52564
10/01/2013 | 2012 | 312 | 795 | 67730
11/01/2013 | 2012 | 258 | 9 | 2322
13/01/2013 | 2012 | 242 | 1099 | 42715
14/01/2013 | 2012 | 290 | 18 | 5220
15/01/2013 | 2012 | 32 | 161 | 5152
17/01/2013 | 2012 | 290 | 41 | 11890
18/01/2013 | 2012 | 248 | 2802 | 77592
19/01/2013 | 2012 | 12 | 945 | 4792
22/01/2013 | 2012 | 1440 | 101 | 112956
24/01/2013 | 2012 | 333 | 34 | 11322
25/01/2013 | 2012 | 406 | 150 | 17748
31/01/2013 | 2012 | 194 | 12 | 2328
01/02/2013 | 2012 | 334 | 49 | 16366
04/02/2013 | 2012 | 460 | 184 | 15221
05/02/2013 | 2012 | 293 | 49 | 10290
07/02/2013 | 2012 | 330 | 13 | 4290
11/02/2013 | 2012 | 5855 | 203 | 71234
12/02/2013 | 2012 | 448 | 60 | 32904
13/02/2013 | 2012 | 425 | 272 | 19400
14/02/2013 | 2012 | 413 | 70 | 8789
15/02/2013 | 2012 | 463 | 52 | 24076
16/02/2013 | 2012 | 23 | 75 | 1725
20/02/2013 | 2012 | 103 | 114 | 8080
21/02/2013 | 2012 | 359 | 189 | 29272
22/02/2013 | 2012 | 19 | 498 | 9462
23/02/2013 | 2012 | 75 | 226 | 14035
24/02/2013 | 2012 | 93 | 361 | 33382
25/02/2013 | 2012 | 393 | 32 | 12576
27/02/2013 | 2012 | 380 | 41 | 15580
28/02/2013 | 2012 | 480 | 11 | 5280
01/03/2013 | 2012 | 252 | 5629 | 280300
03/03/2013 | 2012 | 67 | 95 | 6365
05/03/2013 | 2012 | 83 | 662 | 92010
06/03/2013 | 2012 | 572 | 784 | 95753
08/03/2013 | 2012 | 318 | 5 | 1590
10/03/2013 | 2012 | 170 | 81 | 9534
11/03/2013 | 2012 | 31 | 216 | 6353
12/03/2013 | 2012 | 358 | 24 | 8592
14/03/2013 | 2012 | 377 | 64 | 14177
17/03/2013 | 2012 | 153 | 868 | 75396
19/03/2013 | 2012 | 495 | 51 | 14608
20/03/2013 | 2012 | 484 | 7219 | 191001
21/03/2013 | 2012 | 118 | 1364 | 68516
22/03/2013 | 2012 | 420 | 139 | 36094
25/03/2013 | 2012 | 158 | 769 | 77182
26/03/2013 | 2012 | 400 | 236 | 39080
27/03/2013 | 2012 | 374 | 28 | 9922
28/03/2013 | 2012 | 382 | 32 | 3099
30/03/2013 | 2012 | 62 | 82 | 4348

## 20122013NormalisedDailyTotals
Date Outage | Year | TotAVG | Customers Impacted | Total Customer Minutes Lost | Saidi | Safi
10/09/2012 | 2012 | 25558 | 839 | 31180 | 1.22 | 0.032827
12/06/2012 | 2012 | 25558 | 260 | 16307 | 0.63804 | 0.010173
12/04/2012 | 2012 | 25558 | 10 | 900 | 0.035214 | 0.00039127
12/03/2013 | 2012 | 25558 | 24 | 8592 | 0.33618 | 0.00093904
12/02/2013 | 2012 | 25558 | 60 | 32904 | 1.2874 | 0.0023476
11/12/2012 | 2012 | 25558 | 71 | 5698 | 0.22294 | 0.002778
11/10/2012 | 2012 | 25558 | 49 | 17983 | 0.70362 | 0.0019172
11/09/2012 | 2012 | 25558 | 159 | 34314 | 1.3426 | 0.0062211
11/07/2012 | 2012 | 25558 | 20 | 5680 | 0.22224 | 0.00078253
11/05/2012 | 2012 | 25558 | 93 | 372 | 0.014555 | 0.0036388
11/03/2013 | 2012 | 25558 | 216 | 6353 | 0.24857 | 0.0084514
11/02/2013 | 2012 | 25558 | 203 | 71234 | 2.7872 | 0.0079427
11/01/2013 | 2012 | 25558 | 9 | 2322 | 0.090852 | 0.00035214
15/10/2012 | 2012 | 25558 | 1214 | 115053 | 4.5016 | 0.0475
10/10/2012 | 2012 | 25558 | 223 | 39919 | 1.5619 | 0.0087253
12/09/2012 | 2012 | 25558 | 73 | 5484 | 0.21457 | 0.0028562
10/08/2012 | 2012 | 25558 | 52 | 5138 | 0.20103 | 0.0020346
10/07/2012 | 2012 | 25558 | 159 | 10084 | 0.39455 | 0.0062211
10/04/2012 | 2012 | 25558 | 12 | 4204 | 0.16449 | 0.00046952
10/03/2013 | 2012 | 25558 | 81 | 9534 | 0.37303 | 0.0031693
10/01/2013 | 2012 | 25558 | 795 | 67730 | 2.6501 | 0.031106
09/12/2012 | 2012 | 25558 | 95 | 12585 | 0.49241 | 0.003717
09/10/2012 | 2012 | 25558 | 136 | 12480 | 0.4883 | 0.0053212
09/09/2012 | 2012 | 25558 | 29 | 47009 | 1.8393 | 0.0011347
09/08/2012 | 2012 | 25558 | 84 | 8713 | 0.34091 | 0.0032866
09/07/2012 | 2012 | 25558 | 44 | 4884 | 0.19109 | 0.0017216
09/05/2012 | 2012 | 25558 | 100 | 22098 | 0.86462 | 0.0039127
09/04/2012 | 2012 | 25558 | 77 | 1925 | 0.075319 | 0.0030128
10/11/2012 | 2012 | 25558 | 253 | 12650 | 0.49495 | 0.0098991
14/02/2013 | 2012 | 25558 | 70 | 8789 | 0.34388 | 0.0027389
01/02/2013 | 2012 | 25558 | 49 | 16366 | 0.64035 | 0.0019172
15/08/2012 | 2012 | 25558 | 304 | 20839 | 0.81536 | 0.011895
15/07/2012 | 2012 | 25558 | 196 | 6241 | 0.24419 | 0.0076688
15/06/2012 | 2012 | 25558 | 208 | 44613 | 1.7456 | 0.0081384
15/05/2012 | 2012 | 25558 | 65 | 9782 | 0.38274 | 0.0025432
15/02/2013 | 2012 | 25558 | 52 | 24076 | 0.94201 | 0.0020346
15/01/2013 | 2012 | 25558 | 161 | 5152 | 0.20158 | 0.0062994
14/12/2012 | 2012 | 25558 | 117 | 24488 | 0.95813 | 0.0045778
14/11/2012 | 2012 | 25558 | 73 | 6307 | 0.24677 | 0.0028562
14/10/2012 | 2012 | 25558 | 452 | 241652 | 9.455 | 0.017685
14/09/2012 | 2012 | 25558 | 112 | 12960 | 0.50708 | 0.0043822
14/08/2012 | 2012 | 25558 | 215 | 27686 | 1.0833 | 0.0084122
12/07/2012 | 2012 | 25558 | 115 | 17793 | 0.69618 | 0.0044996
14/03/2013 | 2012 | 25558 | 64 | 14177 | 0.5547 | 0.0025041
12/08/2012 | 2012 | 25558 | 121 | 10011 | 0.3917 | 0.0047343
14/01/2013 | 2012 | 25558 | 18 | 5220 | 0.20424 | 0.00070428
13/12/2012 | 2012 | 25558 | 74 | 35816 | 1.4014 | 0.0028954
13/11/2012 | 2012 | 25558 | 78 | 19188 | 0.75076 | 0.0030519
13/10/2012 | 2012 | 25558 | 1859 | 454783 | 17.7942 | 0.072737
13/09/2012 | 2012 | 25558 | 23 | 851 | 0.033297 | 0.00089991
13/08/2012 | 2012 | 25558 | 19 | 2375 | 0.092926 | 0.00074341
13/07/2012 | 2012 | 25558 | 13 | 819 | 0.032045 | 0.00050865
13/06/2012 | 2012 | 25558 | 43 | 15580 | 0.60959 | 0.0016824
13/04/2012 | 2012 | 25558 | 51 | 18054 | 0.70639 | 0.0019955
13/02/2013 | 2012 | 25558 | 272 | 19400 | 0.75906 | 0.010642
13/01/2013 | 2012 | 25558 | 1099 | 42715 | 1.6713 | 0.043
12/10/2012 | 2012 | 25558 | 18 | 3924 | 0.15353 | 0.00070428
08/10/2012 | 2012 | 25558 | 675 | 179970 | 7.0416 | 0.026411
14/06/2012 | 2012 | 25558 | 25 | 7975 | 0.31204 | 0.00097817
03/03/2013 | 2012 | 25558 | 95 | 6365 | 0.24904 | 0.003717
08/12/2012 | 2012 | 25558 | 74 | 6332 | 0.24775 | 0.0028954
04/12/2012 | 2012 | 25558 | 761 | 43856 | 1.7159 | 0.029775
04/10/2012 | 2012 | 25558 | 9 | 2961 | 0.11585 | 0.00035214
04/09/2012 | 2012 | 25558 | 918 | 75363 | 2.9487 | 0.035918
04/08/2012 | 2012 | 25558 | 108 | 17453 | 0.68288 | 0.0042257
04/07/2012 | 2012 | 25558 | 127 | 10018 | 0.39197 | 0.0049691
04/04/2012 | 2012 | 25558 | 51 | 2169 | 0.084866 | 0.0019955
04/02/2013 | 2012 | 25558 | 184 | 15221 | 0.59555 | 0.0071993
03/11/2012 | 2012 | 25558 | 104 | 9256 | 0.36216 | 0.0040692
03/10/2012 | 2012 | 25558 | 392 | 75941 | 2.9713 | 0.015338
03/08/2012 | 2012 | 25558 | 1384 | 73747 | 2.8855 | 0.054151
03/07/2012 | 2012 | 25558 | 70 | 25410 | 0.99421 | 0.0027389
05/03/2013 | 2012 | 25558 | 662 | 92010 | 3.6 | 0.025902
03/04/2012 | 2012 | 25558 | 551 | 50159 | 1.9626 | 0.021559
05/04/2012 | 2012 | 25558 | 734 | 49198 | 1.925 | 0.028719
02/10/2012 | 2012 | 25558 | 170 | 57950 | 2.2674 | 0.0066515
02/08/2012 | 2012 | 25558 | 58 | 4962 | 0.19415 | 0.0022693
02/07/2012 | 2012 | 25558 | 202 | 12093 | 0.47316 | 0.0079036
02/05/2012 | 2012 | 25558 | 173 | 15172 | 0.59363 | 0.0067689
02/04/2012 | 2012 | 25558 | 150 | 11940 | 0.46717 | 0.005869
01/12/2012 | 2012 | 25558 | 62 | 4156 | 0.16261 | 0.0024259
01/11/2012 | 2012 | 25558 | 116 | 18906 | 0.73973 | 0.0045387
01/09/2012 | 2012 | 25558 | 16 | 5024 | 0.19657 | 0.00062603
01/08/2012 | 2012 | 25558 | 3 | 906 | 0.035449 | 0.00011738
01/07/2012 | 2012 | 25558 | 1404 | 83302 | 3.2593 | 0.054934
01/06/2012 | 2012 | 25558 | 13 | 4745 | 0.18566 | 0.00050865
01/05/2012 | 2012 | 25558 | 166 | 81156 | 3.1754 | 0.006495
01/03/2013 | 2012 | 25558 | 5629 | 280300 | 10.9672 | 0.22024
03/05/2012 | 2012 | 25558 | 226 | 21244 | 0.83121 | 0.0088426
07/01/2013 | 2012 | 25558 | 1272 | 52564 | 2.0567 | 0.049769
16/02/2013 | 2012 | 25558 | 75 | 1725 | 0.067494 | 0.0029345
08/09/2012 | 2012 | 25558 | 253 | 90874 | 3.5556 | 0.0098991
08/08/2012 | 2012 | 25558 | 282 | 29484 | 1.1536 | 0.011034
08/06/2012 | 2012 | 25558 | 94 | 10704 | 0.41881 | 0.0036779
08/05/2012 | 2012 | 25558 | 126 | 16028 | 0.62712 | 0.00493
08/04/2012 | 2012 | 25558 | 1945 | 31216 | 1.2214 | 0.076101
08/03/2013 | 2012 | 25558 | 5 | 1590 | 0.062211 | 0.00019563
07/12/2012 | 2012 | 25558 | 1625 | 117974 | 4.6159 | 0.063581
07/10/2012 | 2012 | 25558 | 43 | 10879 | 0.42566 | 0.0016824
07/09/2012 | 2012 | 25558 | 3561 | 149117 | 5.8345 | 0.13933
07/08/2012 | 2012 | 25558 | 67 | 3795 | 0.14849 | 0.0026215
07/06/2012 | 2012 | 25558 | 93 | 21390 | 0.83692 | 0.0036388
05/02/2013 | 2012 | 25558 | 49 | 10290 | 0.40261 | 0.0019172
07/02/2013 | 2012 | 25558 | 13 | 4290 | 0.16785 | 0.00050865
08/11/2012 | 2012 | 25558 | 96 | 15924 | 0.62305 | 0.0037562
06/12/2012 | 2012 | 25558 | 400 | 52034 | 2.0359 | 0.015651
06/11/2012 | 2012 | 25558 | 126 | 51156 | 2.0016 | 0.00493
06/10/2012 | 2012 | 25558 | 338 | 10456 | 0.40911 | 0.013225
06/09/2012 | 2012 | 25558 | 73 | 27183 | 1.0636 | 0.0028562
06/08/2012 | 2012 | 25558 | 8069 | 168935 | 6.6099 | 0.31571
06/07/2012 | 2012 | 25558 | 189 | 32078 | 1.2551 | 0.0073949
06/06/2012 | 2012 | 25558 | 123 | 18441 | 0.72154 | 0.0048126
06/04/2012 | 2012 | 25558 | 69 | 23253 | 0.90981 | 0.0026997
06/03/2013 | 2012 | 25558 | 784 | 95753 | 3.7465 | 0.030675
05/12/2012 | 2012 | 25558 | 13 | 4611 | 0.18041 | 0.00050865
05/10/2012 | 2012 | 25558 | 449 | 20293 | 0.794 | 0.017568
05/07/2012 | 2012 | 25558 | 219 | 27339 | 1.0697 | 0.0085687
05/06/2012 | 2012 | 25558 | 42 | 21865 | 0.85551 | 0.0016433
07/05/2012 | 2012 | 25558 | 283 | 16463 | 0.64414 | 0.011073
25/05/2012 | 2012 | 25558 | 6 | 2160 | 0.084514 | 0.00023476
27/02/2013 | 2012 | 25558 | 41 | 15580 | 0.60959 | 0.0016042
26/11/2012 | 2012 | 25558 | 65 | 13295 | 0.52019 | 0.0025432
26/10/2012 | 2012 | 25558 | 73 | 10001 | 0.39131 | 0.0028562
26/09/2012 | 2012 | 25558 | 8 | 2528 | 0.098912 | 0.00031301
26/07/2012 | 2012 | 25558 | 233 | 33545 | 1.3125 | 0.0091165
26/06/2012 | 2012 | 25558 | 1700 | 53422 | 2.0902 | 0.066515
26/05/2012 | 2012 | 25558 | 17 | 1870 | 0.073167 | 0.00066515
26/04/2012 | 2012 | 25558 | 294 | 33112 | 1.2956 | 0.011503
26/03/2013 | 2012 | 25558 | 236 | 39080 | 1.5291 | 0.0092339
25/11/2012 | 2012 | 25558 | 279 | 55185 | 2.1592 | 0.010916
25/10/2012 | 2012 | 25558 | 753 | 52429 | 2.0514 | 0.029462
25/08/2012 | 2012 | 25558 | 272 | 17684 | 0.69192 | 0.010642
15/09/2012 | 2012 | 25558 | 6958 | 104370 | 4.0837 | 0.27224
25/06/2012 | 2012 | 25558 | 985 | 17968 | 0.70303 | 0.03854
27/06/2012 | 2012 | 25558 | 156 | 18722 | 0.73253 | 0.0061038
25/03/2013 | 2012 | 25558 | 769 | 77182 | 3.0199 | 0.030088
25/02/2013 | 2012 | 25558 | 32 | 12576 | 0.49206 | 0.0012521
25/01/2013 | 2012 | 25558 | 150 | 17748 | 0.69442 | 0.005869
24/11/2012 | 2012 | 25558 | 498 | 23904 | 0.93528 | 0.019485 | 0.019485
24/10/2012 | 2012 | 25558 | 255 | 23562 | 0.9219 | 0.0099773
24/09/2012 | 2012 | 25558 | 73 | 26280 | 1.0282 | 0.0028562
24/08/2012 | 2012 | 25558 | 21 | 35679 | 1.396 | 0.00082166
24/07/2012 | 2012 | 25558 | 204 | 8364 | 0.32726 | 0.0079818
24/06/2012 | 2012 | 25558 | 128 | 22018 | 0.86149 | 0.0050082
24/04/2012 | 2012 | 25558 | 34 | 11050 | 0.43235 | 0.0013303
24/02/2013 | 2012 | 25558 | 361 | 33382 | 1.3061 | 0.014125
24/01/2013 | 2012 | 25558 | 34 | 11322 | 0.44299 | 0.0013303
25/07/2012 | 2012 | 25558 | 144 | 24216 | 0.94749 | 0.0056342
28/12/2012 | 2012 | 25558 | 151 | 4589 | 0.17955 | 0.0059081
31/07/2012 | 2012 | 25558 | 1126 | 24899 | 0.97422 | 0.044057
31/01/2013 | 2012 | 25558 | 12 | 2328 | 0.091087 | 0.00046952
30/11/2012 | 2012 | 25558 | 87 | 6377 | 0.24951 | 0.003404
30/09/2012 | 2012 | 25558 | 225 | 25050 | 0.98012 | 0.0088035
30/07/2012 | 2012 | 25558 | 234 | 16532 | 0.64684 | 0.0091556
30/06/2012 | 2012 | 25558 | 81 | 17471 | 0.68358 | 0.0031693
30/05/2012 | 2012 | 25558 | 246 | 36218 | 1.4171 | 0.0096252
30/04/2012 | 2012 | 25558 | 198 | 16229 | 0.63499 | 0.0077471
30/03/2013 | 2012 | 25558 | 82 | 4348 | 0.17012 | 0.0032084
29/11/2012 | 2012 | 25558 | 49 | 13965 | 0.5464 | 0.0019172
29/08/2012 | 2012 | 25558 | 18 | 1836 | 0.071837 | 0.00070428
29/07/2012 | 2012 | 25558 | 170 | 7874 | 0.30808 | 0.0066515
27/03/2013 | 2012 | 25558 | 28 | 9922 | 0.38822 | 0.0010955
29/05/2012 | 2012 | 25558 | 25 | 7825 | 0.30617 | 0.00097817
27/04/2012 | 2012 | 25558 | 15 | 1455 | 0.056929 | 0.0005869
28/11/2012 | 2012 | 25558 | 170 | 8636 | 0.3379 | 0.0066515
28/10/2012 | 2012 | 25558 | 28 | 11704 | 0.45794 | 0.0010955
28/09/2012 | 2012 | 25558 | 5328 | 129040 | 5.0489 | 0.20847
28/08/2012 | 2012 | 25558 | 10 | 3080 | 0.12051 | 0.00039127
28/06/2012 | 2012 | 25558 | 479 | 54824 | 2.1451 | 0.018742
28/05/2012 | 2012 | 25558 | 13 | 5109 | 0.1999 | 0.00050865
28/04/2012 | 2012 | 25558 | 51 | 32202 | 1.26 | 0.0019955
28/03/2013 | 2012 | 25558 | 32 | 3099 | 0.12125 | 0.0012521
28/02/2013 | 2012 | 25558 | 11 | 5280 | 0.20659 | 0.00043039
27/11/2012 | 2012 | 25558 | 226 | 45786 | 1.7915 | 0.0088426
27/09/2012 | 2012 | 25558 | 9 | 2925 | 0.11445 | 0.00035214
27/07/2012 | 2012 | 25558 | 559 | 131934 | 5.1621 | 0.021872
23/10/2012 | 2012 | 25558 | 551 | 71694 | 2.8051 | 0.021559
29/06/2012 | 2012 | 25558 | 39 | 7352.64 | 0.28768 | 0.0015259
17/12/2012 | 2012 | 25558 | 49 | 15190 | 0.59433 | 0.0019172
23/12/2012 | 2012 | 25558 | 421 | 50953 | 1.9936 | 0.016472
19/08/2012 | 2012 | 25558 | 32 | 8672 | 0.33931 | 0.0012521
19/06/2012 | 2012 | 25558 | 938 | 26402 | 1.033 | 0.036701
19/04/2012 | 2012 | 25558 | 46 | 17750 | 0.6945 | 0.0017998
19/03/2013 | 2012 | 25558 | 51 | 14608 | 0.57156 | 0.0019955
19/01/2013 | 2012 | 25558 | 945 | 4792 | 0.1875 | 0.036975
18/12/2012 | 2012 | 25558 | 9 | 2610 | 0.10212 | 0.00035214
18/11/2012 | 2012 | 25558 | 184 | 21479 | 0.8404 | 0.0071993
18/10/2012 | 2012 | 25558 | 91 | 4316 | 0.16887 | 0.0035605
18/09/2012 | 2012 | 25558 | 31 | 6406 | 0.25065 | 0.0012129
18/06/2012 | 2012 | 25558 | 3429 | 11884 | 0.46498 | 0.13417
18/05/2012 | 2012 | 25558 | 26 | 8580 | 0.33571 | 0.0010173
20/02/2013 | 2012 | 25558 | 114 | 8080 | 0.31614 | 0.0044604
18/01/2013 | 2012 | 25558 | 2802 | 77592 | 3.0359 | 0.10963
20/03/2013 | 2012 | 25558 | 7219 | 191001 | 7.4732 | 0.28246
17/10/2012 | 2012 | 25558 | 26 | 3458 | 0.1353 | 0.0010173
17/09/2012 | 2012 | 25558 | 385 | 22189 | 0.86818 | 0.015064
17/07/2012 | 2012 | 25558 | 115 | 18768 | 0.73433 | 0.0044996
17/05/2012 | 2012 | 25558 | 70 | 980 | 0.038344 | 0.0027389
17/04/2012 | 2012 | 25558 | 292 | 39634 | 1.5507 | 0.011425
17/03/2013 | 2012 | 25558 | 868 | 75396 | 2.95 | 0.033962
17/01/2013 | 2012 | 25558 | 41 | 11890 | 0.46522 | 0.0016042
16/10/2012 | 2012 | 25558 | 12 | 4908 | 0.19203 | 0.00046952
16/09/2012 | 2012 | 25558 | 151 | 9064 | 0.35464 | 0.0059081
16/08/2012 | 2012 | 25558 | 22 | 5641 | 0.22071 | 0.00086079
16/07/2012 | 2012 | 25558 | 510 | 88284 | 3.4543 | 0.019955
16/05/2012 | 2012 | 25558 | 38 | 9184 | 0.35934 | 0.0014868
16/04/2012 | 2012 | 25558 | 230 | 19222 | 0.75209 | 0.0089991
18/04/2012 | 2012 | 25558 | 37 | 10508 | 0.41114 | 0.0014477
22/01/2013 | 2012 | 25558 | 101 | 112956 | 4.4196 | 0.0039518
31/10/2012 | 2012 | 25558 | 73 | 21400 | 0.83731 | 0.0028562
23/08/2012 | 2012 | 25558 | 13 | 3991 | 0.15615 | 0.00050865
23/06/2012 | 2012 | 25558 | 1184 | 205377 | 8.0357 | 0.046326
23/05/2012 | 2012 | 25558 | 13 | 4914 | 0.19227 | 0.00050865
23/04/2012 | 2012 | 25558 | 101 | 4956 | 0.19391 | 0.0039518
23/02/2013 | 2012 | 25558 | 226 | 14035 | 0.54914 | 0.0088426
22/11/2012 | 2012 | 25558 | 96 | 33504 | 1.3109 | 0.0037562
22/10/2012 | 2012 | 25558 | 76 | 31712 | 1.2408 | 0.0029736
22/08/2012 | 2012 | 25558 | 117 | 26124 | 1.0221 | 0.0045778
22/07/2012 | 2012 | 25558 | 43 | 15965 | 0.62466 | 0.0016824
22/06/2012 | 2012 | 25558 | 128 | 9298 | 0.3638 | 0.0050082
22/05/2012 | 2012 | 25558 | 100 | 15464 | 0.60506 | 0.0039127
19/09/2012 | 2012 | 25558 | 8 | 2880 | 0.11268 | 0.00031301
22/02/2013 | 2012 | 25558 | 498 | 9462 | 0.37022 | 0.019485
23/11/2012 | 2012 | 25558 | 912 | 52242 | 2.0441 | 0.035684
21/11/2012 | 2012 | 25558 | 138 | 17350 | 0.67885 | 0.0053995
21/08/2012 | 2012 | 25558 | 12 | 3680 | 0.14399 | 0.00046952
21/06/2012 | 2012 | 25558 | 170 | 34296 | 1.3419 | 0.0066515
21/05/2012 | 2012 | 25558 | 21 | 2940 | 0.11503 | 0.00082166
21/03/2013 | 2012 | 25558 | 1364 | 68516 | 2.6808 | 0.053369
21/02/2013 | 2012 | 25558 | 189 | 29272 | 1.1453 | 0.0073949
20/12/2012 | 2012 | 25558 | 9 | 3042 | 0.11902 | 0.00035214
20/11/2012 | 2012 | 25558 | 148 | 16727 | 0.65447 | 0.0057908
20/09/2012 | 2012 | 25558 | 84 | 20152 | 0.78848 | 0.0032866
20/08/2012 | 2012 | 25558 | 10 | 600 | 0.023476 | 0.00039127
20/07/2012 | 2012 | 25558 | 14 | 4074 | 0.1594 | 0.00054777
20/06/2012 | 2012 | 25558 | 9 | 2997 | 0.11726 | 0.00035214
20/04/2012 | 2012 | 25558 | 340 | 32360 | 1.2661 | 0.013303
22/03/2013 | 2012 | 25558 | 139 | 36094 | 1.4122 | 0.0054386

## 20122013FixedData
Date Outage | Saidi | Safi | FixedSaidi | FixedSaifi
10/09/2012 | 1.22 | 0.032827 | 1.22 | 0.032827
12/06/2012 | 0.63804 | 0.010173 | 0.63804 | 0.010173
12/04/2012 | 0.035214 | 0.00039127 | 0.035214 | 0.00039127
12/03/2013 | 0.33618 | 0.00093904 | 0.33618 | 0.00093904
12/02/2013 | 1.2874 | 0.0023476 | 1.2874 | 0.0023476
11/12/2012 | 0.22294 | 0.002778 | 0.22294 | 0.002778
11/10/2012 | 0.70362 | 0.0019172 | 0.70362 | 0.0019172
11/09/2012 | 1.3426 | 0.0062211 | 1.3426 | 0.0062211
11/07/2012 | 0.22224 | 0.00078253 | 0.22224 | 0.00078253
11/05/2012 | 0.014555 | 0.0036388 | 0.014555 | 0.0036388
11/03/2013 | 0.24857 | 0.0084514 | 0.24857 | 0.0084514
11/02/2013 | 2.7872 | 0.0079427 | 2.7872 | 0.0079427
11/01/2013 | 0.090852 | 0.00035214 | 0.090852 | 0.00035214
15/10/2012 | 4.5016 | 0.0475 | 4.5016 | 0.0475
10/10/2012 | 1.5619 | 0.0087253 | 1.5619 | 0.0087253
12/09/2012 | 0.21457 | 0.0028562 | 0.21457 | 0.0028562
10/08/2012 | 0.20103 | 0.0020346 | 0.20103 | 0.0020346
10/07/2012 | 0.39455 | 0.0062211 | 0.39455 | 0.0062211
10/04/2012 | 0.16449 | 0.00046952 | 0.16449 | 0.00046952
10/03/2013 | 0.37303 | 0.0031693 | 0.37303 | 0.0031693
10/01/2013 | 2.6501 | 0.031106 | 2.6501 | 0.031106
09/12/2012 | 0.49241 | 0.003717 | 0.49241 | 0.003717
09/10/2012 | 0.4883 | 0.0053212 | 0.4883 | 0.0053212
09/09/2012 | 1.8393 | 0.0011347 | 1.8393 | 0.0011347
09/08/2012 | 0.34091 | 0.0032866 | 0.34091 | 0.0032866
09/07/2012 | 0.19109 | 0.0017216 | 0.19109 | 0.0017216
09/05/2012 | 0.86462 | 0.0039127 | 0.86462 | 0.0039127
09/04/2012 | 0.075319 | 0.0030128 | 0.075319 | 0.0030128
10/11/2012 | 0.49495 | 0.0098991 | 0.49495 | 0.0098991
14/02/2013 | 0.34388 | 0.0027389 | 0.34388 | 0.0027389
01/02/2013 | 0.64035 | 0.0019172 | 0.64035 | 0.0019172
15/08/2012 | 0.81536 | 0.011895 | 0.81536 | 0.011895
15/07/2012 | 0.24419 | 0.0076688 | 0.24419 | 0.0076688
15/06/2012 | 1.7456 | 0.0081384 | 1.7456 | 0.0081384
15/05/2012 | 0.38274 | 0.0025432 | 0.38274 | 0.0025432
15/02/2013 | 0.94201 | 0.0020346 | 0.94201 | 0.0020346
15/01/2013 | 0.20158 | 0.0062994 | 0.20158 | 0.0062994
14/12/2012 | 0.95813 | 0.0045778 | 0.95813 | 0.0045778
14/11/2012 | 0.24677 | 0.0028562 | 0.24677 | 0.0028562
14/10/2012 | 9.455 | 0.017685 | 9.455 | 0.017685
14/09/2012 | 0.50708 | 0.0043822 | 0.50708 | 0.0043822
14/08/2012 | 1.0833 | 0.0084122 | 1.0833 | 0.0084122
12/07/2012 | 0.69618 | 0.0044996 | 0.69618 | 0.0044996
14/03/2013 | 0.5547 | 0.0025041 | 0.5547 | 0.0025041
12/08/2012 | 0.3917 | 0.0047343 | 0.3917 | 0.0047343
14/01/2013 | 0.20424 | 0.00070428 | 0.20424 | 0.00070428
13/12/2012 | 1.4014 | 0.0028954 | 1.4014 | 0.0028954
13/11/2012 | 0.75076 | 0.0030519 | 0.75076 | 0.0030519
13/10/2012 | 17.7942 | 0.072737 | 17.7942 | 0.072737
13/09/2012 | 0.033297 | 0.00089991 | 0.033297 | 0.00089991
13/08/2012 | 0.092926 | 0.00074341 | 0.092926 | 0.00074341
13/07/2012 | 0.032045 | 0.00050865 | 0.032045 | 0.00050865
13/06/2012 | 0.60959 | 0.0016824 | 0.60959 | 0.0016824
13/04/2012 | 0.70639 | 0.0019955 | 0.70639 | 0.0019955
13/02/2013 | 0.75906 | 0.010642 | 0.75906 | 0.010642
13/01/2013 | 1.6713 | 0.043 | 1.6713 | 0.043
12/10/2012 | 0.15353 | 0.00070428 | 0.15353 | 0.00070428
08/10/2012 | 7.0416 | 0.026411 | 7.0416 | 0.026411
14/06/2012 | 0.31204 | 0.00097817 | 0.31204 | 0.00097817
03/03/2013 | 0.24904 | 0.003717 | 0.24904 | 0.003717
08/12/2012 | 0.24775 | 0.0028954 | 0.24775 | 0.0028954
04/12/2012 | 1.7159 | 0.029775 | 1.7159 | 0.029775
04/10/2012 | 0.11585 | 0.00035214 | 0.11585 | 0.00035214
04/09/2012 | 2.9487 | 0.035918 | 2.9487 | 0.035918
04/08/2012 | 0.68288 | 0.0042257 | 0.68288 | 0.0042257
04/07/2012 | 0.39197 | 0.0049691 | 0.39197 | 0.0049691
04/04/2012 | 0.084866 | 0.0019955 | 0.084866 | 0.0019955
04/02/2013 | 0.59555 | 0.0071993 | 0.59555 | 0.0071993
03/11/2012 | 0.36216 | 0.0040692 | 0.36216 | 0.0040692
03/10/2012 | 2.9713 | 0.015338 | 2.9713 | 0.015338
03/08/2012 | 2.8855 | 0.054151 | 2.8855 | 0.054151
03/07/2012 | 0.99421 | 0.0027389 | 0.99421 | 0.0027389
05/03/2013 | 3.6 | 0.025902 | 3.6 | 0.025902
03/04/2012 | 1.9626 | 0.021559 | 1.9626 | 0.021559
05/04/2012 | 1.925 | 0.028719 | 1.925 | 0.028719
02/10/2012 | 2.2674 | 0.0066515 | 2.2674 | 0.0066515
02/08/2012 | 0.19415 | 0.0022693 | 0.19415 | 0.0022693
02/07/2012 | 0.47316 | 0.0079036 | 0.47316 | 0.0079036
02/05/2012 | 0.59363 | 0.0067689 | 0.59363 | 0.0067689
02/04/2012 | 0.46717 | 0.005869 | 0.46717 | 0.005869
01/12/2012 | 0.16261 | 0.0024259 | 0.16261 | 0.0024259
01/11/2012 | 0.73973 | 0.0045387 | 0.73973 | 0.0045387
01/09/2012 | 0.19657 | 0.00062603 | 0.19657 | 0.00062603
01/08/2012 | 0.035449 | 0.00011738 | 0.035449 | 0.00011738
01/07/2012 | 3.2593 | 0.054934 | 3.2593 | 0.054934
01/06/2012 | 0.18566 | 0.00050865 | 0.18566 | 0.00050865
01/05/2012 | 3.1754 | 0.006495 | 3.1754 | 0.006495
01/03/2013 | 10.9672 | 0.22024 | 10.9672 | 0.22024
03/05/2012 | 0.83121 | 0.0088426 | 0.83121 | 0.0088426
07/01/2013 | 2.0567 | 0.049769 | 2.0567 | 0.049769
16/02/2013 | 0.067494 | 0.0029345 | 0.067494 | 0.0029345
08/09/2012 | 3.5556 | 0.0098991 | 3.5556 | 0.0098991
08/08/2012 | 1.1536 | 0.011034 | 1.1536 | 0.011034
08/06/2012 | 0.41881 | 0.0036779 | 0.41881 | 0.0036779
08/05/2012 | 0.62712 | 0.00493 | 0.62712 | 0.00493
08/04/2012 | 1.2214 | 0.076101 | 1.2214 | 0.076101
08/03/2013 | 0.062211 | 0.00019563 | 0.062211 | 0.00019563
07/12/2012 | 4.6159 | 0.063581 | 4.6159 | 0.063581
07/10/2012 | 0.42566 | 0.0016824 | 0.42566 | 0.0016824
07/09/2012 | 5.8345 | 0.13933 | 5.8345 | 0.13933
07/08/2012 | 0.14849 | 0.0026215 | 0.14849 | 0.0026215
07/06/2012 | 0.83692 | 0.0036388 | 0.83692 | 0.0036388
05/02/2013 | 0.40261 | 0.0019172 | 0.40261 | 0.0019172
07/02/2013 | 0.16785 | 0.00050865 | 0.16785 | 0.00050865
08/11/2012 | 0.62305 | 0.0037562 | 0.62305 | 0.0037562
06/12/2012 | 2.0359 | 0.015651 | 2.0359 | 0.015651
06/11/2012 | 2.0016 | 0.00493 | 2.0016 | 0.00493
06/10/2012 | 0.40911 | 0.013225 | 0.40911 | 0.013225
06/09/2012 | 1.0636 | 0.0028562 | 1.0636 | 0.0028562
06/08/2012 | 6.6099 | 0.31571 | 6.6099 | 0.31571
06/07/2012 | 1.2551 | 0.0073949 | 1.2551 | 0.0073949
06/06/2012 | 0.72154 | 0.0048126 | 0.72154 | 0.0048126
06/04/2012 | 0.90981 | 0.0026997 | 0.90981 | 0.0026997
06/03/2013 | 3.7465 | 0.030675 | 3.7465 | 0.030675
05/12/2012 | 0.18041 | 0.00050865 | 0.18041 | 0.00050865
05/10/2012 | 0.794 | 0.017568 | 0.794 | 0.017568
05/07/2012 | 1.0697 | 0.0085687 | 1.0697 | 0.0085687
05/06/2012 | 0.85551 | 0.0016433 | 0.85551 | 0.0016433
07/05/2012 | 0.64414 | 0.011073 | 0.64414 | 0.011073
25/05/2012 | 0.084514 | 0.00023476 | 0.084514 | 0.00023476
27/02/2013 | 0.60959 | 0.0016042 | 0.60959 | 0.0016042
26/11/2012 | 0.52019 | 0.0025432 | 0.52019 | 0.0025432
26/10/2012 | 0.39131 | 0.0028562 | 0.39131 | 0.0028562
26/09/2012 | 0.098912 | 0.00031301 | 0.098912 | 0.00031301
26/07/2012 | 1.3125 | 0.0091165 | 1.3125 | 0.0091165
26/06/2012 | 2.0902 | 0.066515 | 2.0902 | 0.066515
26/05/2012 | 0.073167 | 0.00066515 | 0.073167 | 0.00066515
26/04/2012 | 1.2956 | 0.011503 | 1.2956 | 0.011503
26/03/2013 | 1.5291 | 0.0092339 | 1.5291 | 0.0092339
25/11/2012 | 2.1592 | 0.010916 | 2.1592 | 0.010916
25/10/2012 | 2.0514 | 0.029462 | 2.0514 | 0.029462
25/08/2012 | 0.69192 | 0.010642 | 0.69192 | 0.010642
15/09/2012 | 4.0837 | 0.27224 | 4.0837 | 0.27224
25/06/2012 | 0.70303 | 0.03854 | 0.70303 | 0.03854
27/06/2012 | 0.73253 | 0.0061038 | 0.73253 | 0.0061038
25/03/2013 | 3.0199 | 0.030088 | 3.0199 | 0.030088
25/02/2013 | 0.49206 | 0.0012521 | 0.49206 | 0.0012521
25/01/2013 | 0.69442 | 0.005869 | 0.69442 | 0.005869
24/11/2012 | 0.93528 | 0.019485 | 0.93528 | 0.019485
24/10/2012 | 0.9219 | 0.0099773 | 0.9219 | 0.0099773
24/09/2012 | 1.0282 | 0.0028562 | 1.0282 | 0.0028562
24/08/2012 | 1.396 | 0.00082166 | 1.396 | 0.00082166
24/07/2012 | 0.32726 | 0.0079818 | 0.32726 | 0.0079818
24/06/2012 | 0.86149 | 0.0050082 | 0.86149 | 0.0050082
24/04/2012 | 0.43235 | 0.0013303 | 0.43235 | 0.0013303
24/02/2013 | 1.3061 | 0.014125 | 1.3061 | 0.014125
24/01/2013 | 0.44299 | 0.0013303 | 0.44299 | 0.0013303
25/07/2012 | 0.94749 | 0.0056342 | 0.94749 | 0.0056342
28/12/2012 | 0.17955 | 0.0059081 | 0.17955 | 0.0059081
31/07/2012 | 0.97422 | 0.044057 | 0.97422 | 0.044057
31/01/2013 | 0.091087 | 0.00046952 | 0.091087 | 0.00046952
30/11/2012 | 0.24951 | 0.003404 | 0.24951 | 0.003404
30/09/2012 | 0.98012 | 0.0088035 | 0.98012 | 0.0088035
30/07/2012 | 0.64684 | 0.0091556 | 0.64684 | 0.0091556
30/06/2012 | 0.68358 | 0.0031693 | 0.68358 | 0.0031693
30/05/2012 | 1.4171 | 0.0096252 | 1.4171 | 0.0096252
30/04/2012 | 0.63499 | 0.0077471 | 0.63499 | 0.0077471
30/03/2013 | 0.17012 | 0.0032084 | 0.17012 | 0.0032084
29/11/2012 | 0.5464 | 0.0019172 | 0.5464 | 0.0019172
29/08/2012 | 0.071837 | 0.00070428 | 0.071837 | 0.00070428
29/07/2012 | 0.30808 | 0.0066515 | 0.30808 | 0.0066515
27/03/2013 | 0.38822 | 0.0010955 | 0.38822 | 0.0010955
29/05/2012 | 0.30617 | 0.00097817 | 0.30617 | 0.00097817
27/04/2012 | 0.056929 | 0.0005869 | 0.056929 | 0.0005869
28/11/2012 | 0.3379 | 0.0066515 | 0.3379 | 0.0066515
28/10/2012 | 0.45794 | 0.0010955 | 0.45794 | 0.0010955
28/09/2012 | 5.0489 | 0.20847 | 5.0489 | 0.20847
28/08/2012 | 0.12051 | 0.00039127 | 0.12051 | 0.00039127
28/06/2012 | 2.1451 | 0.018742 | 2.1451 | 0.018742
28/05/2012 | 0.1999 | 0.00050865 | 0.1999 | 0.00050865
28/04/2012 | 1.26 | 0.0019955 | 1.26 | 0.0019955
28/03/2013 | 0.12125 | 0.0012521 | 0.12125 | 0.0012521
28/02/2013 | 0.20659 | 0.00043039 | 0.20659 | 0.00043039
27/11/2012 | 1.7915 | 0.0088426 | 1.7915 | 0.0088426
27/09/2012 | 0.11445 | 0.00035214 | 0.11445 | 0.00035214
27/07/2012 | 5.1621 | 0.021872 | 5.1621 | 0.021872
23/10/2012 | 2.8051 | 0.021559 | 2.8051 | 0.021559
29/06/2012 | 0.28768 | 0.0015259 | 0.28768 | 0.0015259
17/12/2012 | 0.59433 | 0.0019172 | 0.59433 | 0.0019172
23/12/2012 | 1.9936 | 0.016472 | 1.9936 | 0.016472
19/08/2012 | 0.33931 | 0.0012521 | 0.33931 | 0.0012521
19/06/2012 | 1.033 | 0.036701 | 1.033 | 0.036701
19/04/2012 | 0.6945 | 0.0017998 | 0.6945 | 0.0017998
19/03/2013 | 0.57156 | 0.0019955 | 0.57156 | 0.0019955
19/01/2013 | 0.1875 | 0.036975 | 0.1875 | 0.036975
18/12/2012 | 0.10212 | 0.00035214 | 0.10212 | 0.00035214
18/11/2012 | 0.8404 | 0.0071993 | 0.8404 | 0.0071993
18/10/2012 | 0.16887 | 0.0035605 | 0.16887 | 0.0035605
18/09/2012 | 0.25065 | 0.0012129 | 0.25065 | 0.0012129
18/06/2012 | 0.46498 | 0.13417 | 0.46498 | 0.13417
18/05/2012 | 0.33571 | 0.0010173 | 0.33571 | 0.0010173
20/02/2013 | 0.31614 | 0.0044604 | 0.31614 | 0.0044604
18/01/2013 | 3.0359 | 0.10963 | 3.0359 | 0.10963
20/03/2013 | 7.4732 | 0.28246 | 7.4732 | 0.28246
17/10/2012 | 0.1353 | 0.0010173 | 0.1353 | 0.0010173
17/09/2012 | 0.86818 | 0.015064 | 0.86818 | 0.015064
17/07/2012 | 0.73433 | 0.0044996 | 0.73433 | 0.0044996
17/05/2012 | 0.038344 | 0.0027389 | 0.038344 | 0.0027389
17/04/2012 | 1.5507 | 0.011425 | 1.5507 | 0.011425
17/03/2013 | 2.95 | 0.033962 | 2.95 | 0.033962
17/01/2013 | 0.46522 | 0.0016042 | 0.46522 | 0.0016042
16/10/2012 | 0.19203 | 0.00046952 | 0.19203 | 0.00046952
16/09/2012 | 0.35464 | 0.0059081 | 0.35464 | 0.0059081
16/08/2012 | 0.22071 | 0.00086079 | 0.22071 | 0.00086079
16/07/2012 | 3.4543 | 0.019955 | 3.4543 | 0.019955
16/05/2012 | 0.35934 | 0.0014868 | 0.35934 | 0.0014868
16/04/2012 | 0.75209 | 0.0089991 | 0.75209 | 0.0089991
18/04/2012 | 0.41114 | 0.0014477 | 0.41114 | 0.0014477
22/01/2013 | 4.4196 | 0.0039518 | 4.4196 | 0.0039518
31/10/2012 | 0.83731 | 0.0028562 | 0.83731 | 0.0028562
23/08/2012 | 0.15615 | 0.00050865 | 0.15615 | 0.00050865
23/06/2012 | 8.0357 | 0.046326 | 8.0357 | 0.046326
23/05/2012 | 0.19227 | 0.00050865 | 0.19227 | 0.00050865
23/04/2012 | 0.19391 | 0.0039518 | 0.19391 | 0.0039518
23/02/2013 | 0.54914 | 0.0088426 | 0.54914 | 0.0088426
22/11/2012 | 1.3109 | 0.0037562 | 1.3109 | 0.0037562
22/10/2012 | 1.2408 | 0.0029736 | 1.2408 | 0.0029736
22/08/2012 | 1.0221 | 0.0045778 | 1.0221 | 0.0045778
22/07/2012 | 0.62466 | 0.0016824 | 0.62466 | 0.0016824
22/06/2012 | 0.3638 | 0.0050082 | 0.3638 | 0.0050082
22/05/2012 | 0.60506 | 0.0039127 | 0.60506 | 0.0039127
19/09/2012 | 0.11268 | 0.00031301 | 0.11268 | 0.00031301
22/02/2013 | 0.37022 | 0.019485 | 0.37022 | 0.019485
23/11/2012 | 2.0441 | 0.035684 | 2.0441 | 0.035684
21/11/2012 | 0.67885 | 0.0053995 | 0.67885 | 0.0053995
21/08/2012 | 0.14399 | 0.00046952 | 0.14399 | 0.00046952
21/06/2012 | 1.3419 | 0.0066515 | 1.3419 | 0.0066515
21/05/2012 | 0.11503 | 0.00082166 | 0.11503 | 0.00082166
21/03/2013 | 2.6808 | 0.053369 | 2.6808 | 0.053369
21/02/2013 | 1.1453 | 0.0073949 | 1.1453 | 0.0073949
20/12/2012 | 0.11902 | 0.00035214 | 0.11902 | 0.00035214
20/11/2012 | 0.65447 | 0.0057908 | 0.65447 | 0.0057908
20/09/2012 | 0.78848 | 0.0032866 | 0.78848 | 0.0032866
20/08/2012 | 0.023476 | 0.00039127 | 0.023476 | 0.00039127
20/07/2012 | 0.1594 | 0.00054777 | 0.1594 | 0.00054777
20/06/2012 | 0.11726 | 0.00035214 | 0.11726 | 0.00035214
20/04/2012 | 1.2661 | 0.013303 | 1.2661 | 0.013303
22/03/2013 | 1.4122 | 0.0054386 | 1.4122 | 0.0054386

## 20122013Answer
SumOfSaidi | SumOfSafi | SumOfFixedSaidi | SumOfFixedSaifi
287.1738 | 3.8352 | 287.1738 | 3.8352

## 20112012Data
REPORT NUMBER | Date Outage | YEAR | DATE ON | Duration of Outage | Customers Impacted | Total Customer Minutes Lost | CLASS A-G | CAUSE | CAUSE
13815 | 02/04/2011 | 2011 | 2011-04-02 | 88 | 737 | 32994 | C | DEFECTIVE EQUIPMENT | Repair cable SW/GR B984 Potae Ave
13842 | 03/04/2011 | 2011 | 2011-04-03 | 117 | 30 | 3510 | B | PLANNED SHUTDOWN | Install DDO fuses pole C243 Dunstan Rd
13816 | 04/04/2011 | 2011 | 2011-04-04 | 60 | 58 | 3480 | C | DEFECTIVE EQUIPMENT | Clean cable terminations SW/GR B984 B985 B986 Potae Ave
13841 | 05/04/2011 | 2011 | 2011-04-05 | 405 | 30 | 12150 | B | PLANNED SHUTDOWN | Replace poles D3585 D3589 D3618 D3627 Ruakaka Rd
13847 | 06/04/2011 | 2011 | 2011-04-06 | 226 | 17 | 3842 | B | PLANNED SHUTDOWN | Connect 11kV cable pole W4622 Lake Waikaremoana
13817 | 07/04/2011 | 2011 | 2011-04-07 | 173 | 275 | 19599 | C | DEFECTIVE EQUIPMENT | Repair lines pole W1047 Morere
13818 | 07/04/2011 | 2011 | 2011-04-07 | 98 | 2552 | 89015 | C | UNKNOWN | Reclose CB A8 Goodwins Rd Cause unknown
13843 | 07/04/2011 | 2011 | 2011-04-07 | 365 | 38 | 13870 | B | PLANNED SHUTDOWN | Replace 11kV pole F3041 Otoko
13819 | 08/04/2011 | 2011 | 2011-04-08 | 83 | 17 | 1411 | C | TREE CONTACTS | Repair 11kV lines pole W5619 Putere
13838 | 08/04/2011 | 2011 | 2011-04-08 | 337 | 70 | 24489 | B | PLANNED SHUTDOWN | Replace ABS pole E174 Whatatutu
13820 | 11/04/2011 | 2011 | 2011-04-11 | 7 | 944 | 6608 | C | UNKNOWN | Reclose CB A475 Tamarau at Kaiti Sub
13846 | 12/04/2011 | 2011 | 2011-04-12 | 410 | 38 | 20491 | B | PLANNED SHUTDOWN | Replace poles H1331 H1830 H1829 H1288 SH35 Ruatoria South
13845 | 13/04/2011 | 2011 | 2011-04-13 | 408 | 14 | 5712 | B | PLANNED SHUTDOWN | Isolate 11kV lines H114 to H340 for tree cutting Mata Rd
13821 | 14/04/2011 | 2011 | 2011-04-14 | 126 | 750 | 22636 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W5877 Marumaru
13822 | 18/04/2011 | 2011 | 2011-04-18 | 22 | 48 | 1056 | C | TREE CONTACTS | Remove branch from 11kV line pole W6847
13840 | 19/04/2011 | 2011 | 2011-04-19 | 240 | 43 | 10320 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting C1077 to C384 Waingake Rd
13844 | 19/04/2011 | 2011 | 2011-04-19 | 454 | 9 | 11614 | B | PLANNED SHUTDOWN | Replace 11kV poles D2435 D2436 D2441 D2445 Pehiri Rd
13848 | 19/04/2011 | 2011 | 2011-04-19 | 463 | 45 | 21105 | B | PLANNED SHUTDOWN | Replace 11kV pole A324 & remove poles A2213 & A2214 Graham Rd
13849 | 20/04/2011 | 2011 | 2011-04-20 | 405 | 30 | 12150 | B | PLANNED SHUTDOWN | Replace 11kV poles D3585 D3589 D3599 Ruakaka Rd
13823 | 26/04/2011 | 2011 | 2011-04-26 | 24 | 63 | 1512 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W1420 Clyde Rd
13824 | 26/04/2011 | 2011 | 2011-04-26 | 2904 | 395 | 568963 | C | TREE CONTACTS | Replace pole WW6358 and repair 11kV lines W6351 to W1157 Raupunga
13826 | 26/04/2011 | 2011 | 2011-04-26 | 260 | 857 | 89090 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W1510 Moana Drive Mahia
13827 | 26/04/2011 | 2011 | 2011-04-26 | 19 | 242 | 4598 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W1673 Lake Rd Wairoa
13825 | 27/04/2011 | 2011 | 2011-04-27 | 1550 | 264 | 56623 | C | ADVERSE WEATHER | Repair 11kV line pole W8338 Morere
13828 | 27/04/2011 | 2011 | 2011-04-27 | 971 | 352 | 77773 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J803 SH35 Ruatoria
13829 | 27/04/2011 | 2011 | 2011-04-27 | 196 | 187 | 21307 | C | TREE CONTACTS | Repair 11kV lines pole W1014 Raupunga
13830 | 27/04/2011 | 2011 | 2011-04-27 | 47 | 101 | 4747 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W6830 opp Kiwi Sub
13831 | 28/04/2011 | 2011 | 2011-04-28 | 79 | 14 | 1106 | C | TREE CONTACTS | Repair 11kV lines pole H2793 Mata Rd
13832 | 28/04/2011 | 2011 | 2011-04-28 | 151 | 66 | 9966 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarm pole H1922 Waipiro Bay Rd
13833 | 28/04/2011 | 2011 | 2011-04-28 | 1275 | 12 | 15300 | C | ADVERSE WEATHER | Relocate 11kV pole J4890 from creek Mangaporo Valley
13834 | 28/04/2011 | 2011 | 2011-04-28 | 150 | 93 | 7330 | C | TREE CONTACTS | Remove tree from 11kV lines between poles E549 to E550 Tarndale Rd
13835 | 28/04/2011 | 2011 | 2011-04-28 | 213 | 14 | 2982 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W9602 Tininui Rd
13836 | 28/04/2011 | 2011 | 2011-04-28 | 148 | 363 | 40646 | C | UNKNOWN | Reclose CB J543 Tikitiki at Ruatoria Sub cause unknown
13839 | 29/04/2011 | 2011 | 2011-04-29 | 451 | 229 | 20746 | B | PLANNED SHUTDOWN | Replace 11kV poles C1303 C621 C1191 & C1192 Muriwai
13837 | 30/04/2011 | 2011 | 2011-04-30 | 44 | 26 | 1144 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper ABS W1003 Putere
13850 | 01/05/2011 | 2011 | 2011-05-01 | 147 | 799 | 35270 | C | DEFECTIVE EQUIPMENT | Repair end cap on cable SW/GR B986 Potae Ave
13851 | 01/05/2011 | 2011 | 2011-05-01 | 88 | 584 | 17370 | C | UNKNOWN | Reclose Inc H300 Tokomaru Bay sub cause unknown
13852 | 02/05/2011 | 2011 | 2011-05-02 | 28 | 173 | 4844 | C | TREE CONTACTS | Rejion jumpers pole W6426 Te Hami
13853 | 02/05/2011 | 2011 | 2011-05-02 | 133 | 432 | 55917 | C | TREE CONTACTS | Repair 11kV lines pole F3771 Puha
13855 | 03/05/2011 | 2011 | 2011-05-03 | 91 | 8 | 728 | C | DEFECTIVE EQUIPMENT | Replace insulators pole D3178 Berry Rd Tiniroto
13856 | 03/05/2011 | 2011 | 2011-05-03 | 357 | 273 | 31457 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W963 Morere
13877 | 04/05/2011 | 2011 | 2011-05-04 | 426 | 14 | 22274 | B | PLANNED SHUTDOWN | Replace poles between C101 to C886 Paparatu Rd
13879 | 04/05/2011 | 2011 | 2011-05-04 | 419 | 47 | 15325 | B | PLANNED SHUTDOWN | Replace 11kV poles H1854 H1842 H1837 H1831 H1830 Waiapu Rd
13883 | 04/05/2011 | 2011 | 2011-05-04 | 316 | 14 | 4424 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting H114 Mata Rd
13857 | 05/05/2011 | 2011 | 2011-05-05 | 123 | 217 | 3079 | C | DEFECTIVE EQUIPMENT | Replace Xarm pole W9414 Onenui Stn Mahia
13878 | 05/05/2011 | 2011 | 2011-05-05 | 232 | 16 | 3712 | B | PLANNED SHUTDOWN | Isolate 11kV lines for Teee cutting H329 to H2853 Waipiro Rd
13882 | 05/05/2011 | 2011 | 2011-05-05 | 351 | 20 | 13580 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting F105 Motu
13858 | 09/05/2011 | 2011 | 2011-05-09 | 199 | 171 | 10109 | C | TREE CONTACTS | Remove tree from 11kV pole W5579 Raupunga
13880 | 09/05/2011 | 2011 | 2011-05-09 | 218 | 58 | 12644 | B | PLANNED SHUTDOWN | Connect 11kV cable B5835 Lowe St
13884 | 10/05/2011 | 2011 | 2011-05-10 | 390 | 9 | 3519 | B | PLANNED SHUTDOWN | Replace 11kV poles H896 & H563 Busbys Hill
13859 | 11/05/2011 | 2011 | 2011-05-11 | 41 | 12 | 684 | C | DEFECTIVE EQUIPMENT | Cut jumpers pole C4074 to change private pole Gordons Rd
13860 | 12/05/2011 | 2011 | 2011-05-12 | 256 | 153 | 24588 | C | TREE CONTACTS | Repair 11kV lines between G2047 to G2048 Tauwhareparae Rd
13885 | 13/05/2011 | 2011 | 2011-05-13 | 405 | 22 | 8910 | B | PLANNED SHUTDOWN | Replace H Pole C844 Waingake
13861 | 14/05/2011 | 2011 | 2011-05-14 | 125 | 19 | 2375 | C | DEFECTIVE EQUIPMENT | Replace T/x fuses J239 & jumper Te Araroa
13862 | 16/05/2011 | 2011 | 2011-05-16 | 152 | 117 | 9062 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole C3580 Muriwai
13863 | 16/05/2011 | 2011 | 2011-05-16 | 115 | 60 | 6900 | C | TREE CONTACTS | Untwist 11kV pole D5068 Wharekopae Rd
13864 | 16/05/2011 | 2011 | 2011-05-16 | 45 | 153 | 6360 | C | UNKNOWN | Reclose CB G367 Tauwhareparae at Tolaga Bay Sub Cause unknown
13865 | 16/05/2011 | 2011 | 2011-05-16 | 198 | 776 | 42354 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between poles A4384 to A3401 Makarori
13866 | 16/05/2011 | 2011 | 2011-05-16 | 372 | 91 | 15054 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole G2183 to G2184 Paroa Rd
13867 | 17/05/2011 | 2011 | 2011-05-17 | 329 | 13 | 4277 | C | TREE CONTACTS | Isolate 11kV lines for tree cutting G146 Arakihi Rd
13868 | 17/05/2011 | 2011 | 2011-05-17 | 1732 | 92 | 41444 | C | DEFECTIVE EQUIPMENT | Replace poles E696 & E691 Tarndale Rd
13869 | 17/05/2011 | 2011 | 2011-05-17 | 134 | 246 | 22916 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between poles W8405 to W8411 Morere
13887 | 17/05/2011 | 2011 | 2011-05-17 | 399 | 317 | 35515 | B | PLANNED SHUTDOWN | Replace 11kV poles B3508 B3511 B3512 B3543 Lytton Rd
13871 | 19/05/2011 | 2011 | 2011-05-19 | 387 | 27 | 10449 | C | ADVERSE ENVIRONMENT | Replace & relocate pole F2066 Whakarau Rd
13888 | 19/05/2011 | 2011 | 2011-05-19 | 397 | 175 | 40396 | B | PLANNED SHUTDOWN | Replace 11kV poles B4037 B4038 B453 B4039 B1711 Aberdeen Rd
13894 | 20/05/2011 | 2011 | 2011-05-20 | 320 | 75 | 24000 | B | PLANNED SHUTDOWN | Replace 11kV poles C2164 C2165 Waingake Rd
13886 | 22/05/2011 | 2011 | 2011-05-22 | 10 | 3 | 120 | B | PLANNED SHUTDOWN | Repair Earthing T/X B349 Carters Gladstone Rd
13889 | 23/05/2011 | 2011 | 2011-05-23 | 287 | 50 | 14350 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting E2894 Ngakaroa Rd
13895 | 23/05/2011 | 2011 | 2011-05-23 | 95 | 17 | 1615 | B | PLANNED SHUTDOWN | Remove temp links poles D2727 D2446 D2473 Pehiri Rd
13890 | 24/05/2011 | 2011 | 2011-05-24 | 27 | 151 | 4077 | B | PLANNED SHUTDOWN | Replace 11kV poles B4017 B4019 B4032 Aberdeen Rd
13896 | 24/05/2011 | 2011 | 2011-05-24 | 373 | 4 | 1492 | B | PLANNED SHUTDOWN | Replace T/x D216 Stafford Rd
13891 | 25/05/2011 | 2011 | 2011-05-25 | 40 | 156 | 6820 | B | PLANNED SHUTDOWN | Replace 11kV poles B4039 B4040 B4045 Aberdeen Rd
13872 | 26/05/2011 | 2011 | 2011-05-26 | 265 | 1130 | 263760 | C | TREE CONTACTS | Repair 11kV lines between poles J4508 to J4507 Hicks Bay
13873 | 26/05/2011 | 2011 | 2011-05-26 | 841 | 122 | 33418 | C | DEFECTIVE EQUIPMENT | Untwist 11kV lines beyond J72 Maraehara Rd Rangitukia
13874 | 26/05/2011 | 2011 | 2011-05-26 | 689 | 36 | 12492 | C | TREE CONTACTS | Remove tree for 11kV pole J177 Tapuaweroa Rd
13875 | 27/05/2011 | 2011 | 2011-05-27 | 88 | 122 | 10376 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J161 Rangitukia Rd
13876 | 27/05/2011 | 2011 | 2011-05-27 | 92 | 27 | 3591 | C | DEFECTIVE EQUIPMENT | Replace X arm pole D2012 Lavenham Rd
13881 | 27/05/2011 | 2011 | 2011-05-27 | 59 | 50 | 2950 | B | PLANNED SHUTDOWN | Replace 11kV pole W5190 Cricklewood
13892 | 31/05/2011 | 2011 | 2011-05-31 | 254 | 9 | 2286 | B | PLANNED SHUTDOWN | Replace 11kV cable between W1448 & W304 Tuai
13893 | 31/05/2011 | 2011 | 2011-05-31 | 385 | 242 | 19466 | B | PLANNED SHUTDOWN | Replace 11kV poles B3463 B3464 B3465 B3466 Bulwer Rd
13911 | 01/06/2011 | 2011 | 2011-06-01 | 306 | 36 | 11016 | B | PLANNED SHUTDOWN | Replace 11kV cable between W1450 to W1772 Tuai
13897 | 02/06/2011 | 2011 | 2011-06-02 | 165 | 217 | 8104 | C | DEFECTIVE EQUIPMENT | Rebind 11kV wire pole W9416 Onenui
13898 | 02/06/2011 | 2011 | 2011-06-02 | 916 | 151 | 32176 | C | DEFECTIVE EQUIPMENT | Repair 11kV line pole W109 Hereheretau
13913 | 02/06/2011 | 2011 | 2011-06-02 | 0 | 305 | 49745 | B | PLANNED SHUTDOWN | Replace poles B931 B4034 B4035 Aberdeen Rd
13899 | 05/06/2011 | 2011 | 2011-06-05 | 59 | 1283 | 76744 | C | TREE CONTACTS | Remove tree from poles J1835 to J1836 Tikitiki
13900 | 06/06/2011 | 2011 | 2011-06-06 | 45 | 23 | 1035 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J195 Ruatoria
13915 | 08/06/2011 | 2011 | 2011-06-08 | 242 | 56 | 4052 | B | PLANNED SHUTDOWN | Maintenance on poles H333 H1966 & H1950 Waipiro Bay
13901 | 09/06/2011 | 2011 | 2011-06-09 | 50 | 102 | 5100 | C | DEFECTIVE EQUIPMENT | Replace DDO fuses E162 Mangamaia
13912 | 09/06/2011 | 2011 | 2011-06-09 | 123 | 15 | 1845 | B | PLANNED SHUTDOWN | Replace poles F2265 & F81 Whakarau Rd
13902 | 10/06/2011 | 2011 | 2011-06-10 | 119 | 6 | 714 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A848 Pakarae Stn
13903 | 11/06/2011 | 2011 | 2011-06-11 | 391 | 12 | 2172 | C | TREE CONTACTS | Replace broken pole J2716 Mangaporo Valley
13904 | 12/06/2011 | 2011 | 2011-06-12 | 144 | 974 | 13536 | C | TREE CONTACTS | Repair 11kV lines pole B3105 Valley Rd
13914 | 14/06/2011 | 2011 | 2011-06-14 | 367 | 25 | 18325 | B | PLANNED SHUTDOWN | Replace 11kV poles J2411 J2409 Tikitiki
13905 | 17/06/2011 | 2011 | 2011-06-17 | 139 | 17 | 2363 | C | DEFECTIVE EQUIPMENT | Repair 11kv lines pole A3630 Waiomoko Rd
13916 | 22/06/2011 | 2011 | 2011-06-22 | 427 | 75 | 10372 | B | PLANNED SHUTDOWN | Replace 11kV poles C2198 C2685 Waingake Rd
13917 | 23/06/2011 | 2011 | 2011-06-23 | 409 | 152 | 29768 | B | PLANNED SHUTDOWN | Replace poles B4037 B4038 B1711 Aberdeen Rd
13918 | 23/06/2011 | 2011 | 2011-06-23 | 29 | 18 | 738 | B | PLANNED SHUTDOWN | Replace 11kV poles C2150 & C2151 Waingake Rd
13919 | 24/06/2011 | 2011 | 2011-06-24 | 22 | 18 | 756 | B | PLANNED SHUTDOWN | Replace 11kV poles C2107 & C3699 Waingake Rd
13921 | 24/06/2011 | 2011 | 2011-06-24 | 418 | 187 | 35695 | B | PLANNED SHUTDOWN | Replace 11kV poles B535 & adjust ABS B11o Lytton Rd
13907 | 26/06/2011 | 2011 | 2011-06-26 | 208 | 235 | 22658 | C | FOREIGN INTERFERENCE | Repair 11kV line pole W8727 Nuhaka
13908 | 26/06/2011 | 2011 | 2011-06-26 | 51 | 36 | 1836 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole W9116 Kaiwaitau Rd
13909 | 26/06/2011 | 2011 | 2011-06-26 | 500 | 272 | 54907 | C | FOREIGN INTERFERENCE | Replace 11kV pole W7940 Nuhaka
13920 | 27/06/2011 | 2011 | 2011-06-27 | 310 | 18 | 3546 | B | PLANNED SHUTDOWN | Replace 11kV polesC3674 C3676 C3683 C3686 C2687 C3688 Waingake Rd
13910 | 29/06/2011 | 2011 | 2011-06-29 | 338 | 266 | 12782 | C | TREE CONTACTS | Repair 11kV lines pole H2539 Mata Rd
13922 | 29/06/2011 | 2011 | 2011-06-29 | 65 | 14 | 910 | B | PLANNED SHUTDOWN | Erect 3 11kV DDO fuses pole B3105 Valley Rd
13923 | 30/06/2011 | 2011 | 2011-06-30 | 96 | 29 | 2784 | B | PLANNED SHUTDOWN | Upgrade 200kvA T/x B287 Childers Rd
13924 | 30/06/2011 | 2011 | 2011-06-30 | 384 | 242 | 28787 | B | PLANNED SHUTDOWN | Replace 11kV poles B3464 & B3465 Bulwer Rd
13970 | 01/07/2011 | 2011 | 2011-07-01 | 308 | 155 | 20440 | B | PLANNED SHUTDOWN | Replace poles B4066 B4067 B35 Aberdeen Rd
13974 | 04/07/2011 | 2011 | 2011-07-04 | 92 | 20 | 1840 | B | PLANNED SHUTDOWN | Terminate 11kV cable pole C3162 Awapuni Rd
13925 | 05/07/2011 | 2011 | 2011-07-05 | 59 | 28 | 1652 | C | DEFECTIVE EQUIPMENT | Repair ABS F278 Koranga Valley
13926 | 05/07/2011 | 2011 | 2011-07-05 | 140 | 17 | 2924 | C | DEFECTIVE EQUIPMENT | Replace insulator on pole W6231 Kiwi Valley
13972 | 05/07/2011 | 2011 | 2011-07-05 | 225 | 47 | 5323 | B | PLANNED SHUTDOWN | Replace 11kV pole H1817 SH35 Ruatoria South
13929 | 07/07/2011 | 2011 | 2011-07-07 | 39 | 11 | 429 | C | TREE CONTACTS | Remove from 11kV near T/x F76 Whakarau Rd
13930 | 07/07/2011 | 2011 | 2011-07-07 | 203 | 149 | 20623 | C | ADVERSE WEATHER | Reclose CB G327 Tauwhareparae Feeder Tolaga Sub High Winds
13931 | 07/07/2011 | 2011 | 2011-07-07 | 76 | 101 | 7676 | C | TREE CONTACTS | Remove tree 11kV pole H238 Makarika Crn
13928 | 08/07/2011 | 2011 | 2011-07-08 | 175 | 62 | 10287 | C | ADVERSE WEATHER | Repair 11kV lines pole A3912 Wharekiri Rd
13932 | 08/07/2011 | 2011 | 2011-07-08 | 74 | 264 | 2881 | C | TREE CONTACTS | Repair 11kV lines poles H2715 to H249 Busbys Hill
13933 | 09/07/2011 | 2011 | 2011-07-09 | 432 | 102 | 26109 | C | TREE CONTACTS | Replace pole F761 & repair lines pole F475 Makaretu
13934 | 09/07/2011 | 2011 | 2011-07-09 | 432 | 160 | 28480 | C | TREE CONTACTS | Repair 11kV lines poles F455 to F221 Main Rd Matawai
13935 | 09/07/2011 | 2011 | 2011-07-09 | 346 | 75 | 9222 | C | TREE CONTACTS | Repair 11kv lines poles H123 to H341 Mata Rd
13936 | 09/07/2011 | 2011 | 2011-07-09 | 754 | 633 | 32449 | C | ADVERSE WEATHER | Repair 11kV lines poles W5617 to W5619 Kahangungu
13937 | 10/07/2011 | 2011 | 2011-07-10 | 721 | 205 | 69679 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole G1222 Crn Banks & Cook Sts
13938 | 10/07/2011 | 2011 | 2011-07-10 | 17 | 149 | 2533 | C | DEFECTIVE EQUIPMENT | Replace faulty DDOs pole W1409 Bridge St
13939 | 10/07/2011 | 2011 | 2011-07-10 | 307 | 7 | 2149 | C | DEFECTIVE EQUIPMENT | Cut jumpers pole A4258 Tatapouri to repair line pole A4400 later
13940 | 10/07/2011 | 2011 | 2011-07-10 | 1440 | 27 | 38880 | C | ADVERSE WEATHER | Repair 11kV lines pole W993 Mahiwi
13941 | 10/07/2011 | 2011 | 2011-07-10 | 1703 | 327 | 44634 | C | TREE CONTACTS | Repair 11kV lines poles J634 to J1271 Ruatoria
13942 | 10/07/2011 | 2011 | 2011-07-10 | 632 | 92 | 33900 | C | TREE CONTACTS | Repair 11kV lines pole G4071 Wharekaka
13943 | 10/07/2011 | 2011 | 2011-07-10 | 59 | 86 | 5054 | C | TREE CONTACTS | Cut jumpers pole G4115 Wharekaka lines0 down Poles G4109 to G4110
13944 | 10/07/2011 | 2011 | 2011-07-10 | 76 | 124 | 11133 | C | UNKNOWN | Reclose W812 Mangapoikie Rd cause unknown
13945 | 10/07/2011 | 2011 | 2011-07-10 | 609 | 55 | 27636 | C | TREE CONTACTS | Remove tree from 11kV pole A3964 Wharekiri Rd
13946 | 10/07/2011 | 2011 | 2011-07-10 | 923 | 150 | 78930 | C | TREE CONTACTS | Repair 11kV lines pole G1583 Arikihi Rd
13947 | 10/07/2011 | 2011 | 2011-07-10 | 69 | 74 | 1313 | C | ADVERSE WEATHER | Repair 11kV lines pole G1100 Rototahi
13948 | 11/07/2011 | 2011 | 2011-07-11 | 370 | 41 | 4460 | C | DEFECTIVE EQUIPMENT | Replace pole G1100 Rototahi
13949 | 11/07/2011 | 2011 | 2011-07-11 | 63 | 65 | 16237 | C | TREE CONTACTS | Repair 11kV lines pole F283 Whakarau Rd
13950 | 11/07/2011 | 2011 | 2011-07-11 | 767 | 75 | 15085 | C | TREE CONTACTS | Repair 11kV lines poles H508 to H509 Mata Rd
13951 | 11/07/2011 | 2011 | 2011-07-11 | 237 | 76 | 15869 | C | ADVERSE WEATHER | Repair 11kv lines beyond W906 Mangapoikie Rd
13952 | 12/07/2011 | 2011 | 2011-07-12 | 17 | 27 | 459 | C | ADVERSE WEATHER | Repair 11kV lines pole F221 Matawai Rd
13953 | 12/07/2011 | 2011 | 2011-07-12 | 118 | 72 | 8496 | C | DEFECTIVE EQUIPMENT | Jumper out Faulty ABS G175 Tauwhareparae Rd
13954 | 12/07/2011 | 2011 | 2011-07-12 | 47 | 16 | 752 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole G4071 Wharekaka Rd
13955 | 12/07/2011 | 2011 | 2011-07-12 | 19 | 10 | 190 | C | ADVERSE ENVIRONMENT | Install 11kV extra pole G4115 for clearance from 50kV Wharakaka
13956 | 13/07/2011 | 2011 | 2011-07-13 | 51 | 76 | 3876 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W34 Mangapoikie Rd
13957 | 13/07/2011 | 2011 | 2011-07-13 | 33 | 7 | 231 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole A2841 Tatapouri
13958 | 13/07/2011 | 2011 | 2011-07-13 | 133 | 90 | 11970 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole F373 Kanakanaia Rd
13959 | 14/07/2011 | 2011 | 2011-07-14 | 117 | 56 | 6552 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole E685 Tarndale Rd
13960 | 15/07/2011 | 2011 | 2011-07-15 | 42 | 41 | 1287 | C | DEFECTIVE EQUIPMENT | Repair 11kV ABS W1040 Mangone
13975 | 15/07/2011 | 2011 | 2011-07-15 | 82 | 57 | 4674 | B | PLANNED SHUTDOWN | Upgrade T/x A32 to 200kva Tyndall Rd
13962 | 17/07/2011 | 2011 | 2011-07-17 | 87 | 432 | 16721 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines beyond F217 Matawai
13976 | 18/07/2011 | 2011 | 2011-07-18 | 351 | 60 | 18462 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting F99 Motu Rd
13979 | 18/07/2011 | 2011 | 2011-07-18 | 103 | 239 | 24617 | B | PLANNED SHUTDOWN | Replace poles B4040 B4045 & B4053 Aberdeen Rd
13963 | 19/07/2011 | 2011 | 2011-07-19 | 70 | 59 | 4130 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole C3326 Waingake Rd
13971 | 21/07/2011 | 2011 | 2011-07-21 | 224 | 5 | 1120 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting C321 Bck Ormond Rd
13980 | 21/07/2011 | 2011 | 2011-07-21 | 405 | 81 | 7992 | B | PLANNED SHUTDOWN | Replace 11kV poles C2680 & C2679 Waughs Rd
13984 | 21/07/2011 | 2011 | 2011-07-21 | 34 | 151 | 5061 | B | PLANNED SHUTDOWN | Replace 11kV poles B4019 B4032 B4034 Aberdeen Rd
13964 | 22/07/2011 | 2011 | 2011-07-22 | 31 | 5499 | 114020 | C | TREE CONTACTS | Remove tree from 50kV line pole B5285 Darwin Rd
13965 | 23/07/2011 | 2011 | 2011-07-23 | 846 | 95 | 15539 | C | TREE CONTACTS | Repair 11kV lines poles E1046 to E1219 Waimata Valley Rd
13966 | 24/07/2011 | 2011 | 2011-07-24 | 3304 | 48 | 51680 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole J1910 Haha Stn Rd Rangitukia
13967 | 25/07/2011 | 2011 | 2011-07-25 | 8 | 25 | 200 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W672 Nuhaka
13973 | 25/07/2011 | 2011 | 2011-07-25 | 105 | 73 | 7665 | B | PLANNED SHUTDOWN | Replace T/x B870 with 300kva Mill Rd
13978 | 25/07/2011 | 2011 | 2011-07-25 | 85 | 32 | 4576 | B | PLANNED SHUTDOWN | Isolate 11kV lines at A91 for tree cutting Caves Rd
13981 | 27/07/2011 | 2011 | 2011-07-27 | 30 | 11 | 594 | B | PLANNED SHUTDOWN | Cut jumpers poles C3631 & C3658 Waingake Rd
13977 | 28/07/2011 | 2011 | 2011-07-28 | 394 | 39 | 15366 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting F146 Otoko
13982 | 28/07/2011 | 2011 | 2011-07-28 | 372 | 3 | 1116 | B | PLANNED SHUTDOWN | Replace pole C3648 Waingake Rd
13969 | 29/07/2011 | 2011 | 2011-07-29 | 359 | 79 | 22841 | B | PLANNED SHUTDOWN | Replace 11kV poles H2646 & H2681 Beach Rd Tokomaru Bay
13983 | 29/07/2011 | 2011 | 2011-07-29 | 399 | 24 | 4675 | B | PLANNED SHUTDOWN | Replace 11kV poles C3605 C3630 & C3628 Waingake Rd
13968 | 30/07/2011 | 2011 | 2011-07-30 | 81 | 61 | 7087 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole F3439 & repair 11kV lines poles F3444 to F3353 Dymocks Rd
13985 | 01/08/2011 | 2011 | 2011-08-01 | 172 | 1030 | 54822 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A1277 Tamarau
14007 | 01/08/2011 | 2011 | 2011-08-01 | 300 | 11 | 3300 | B | PLANNED SHUTDOWN | Connect 11kV tapp off to pole A3568 Wheatstone Rd
13986 | 02/08/2011 | 2011 | 2011-08-02 | 362 | 8 | 8312 | C | ADVERSE WEATHER | Reposition poles due to bank falling Away poles H581 to H579 Hikuwai
14006 | 02/08/2011 | 2011 | 2011-08-02 | 35 | 69 | 4485 | B | PLANNED SHUTDOWN | Replace poles C467 & C2826 Waingake Rd
14009 | 02/08/2011 | 2011 | 2011-08-02 | 366 | 60 | 21960 | B | PLANNED SHUTDOWN | Replace 11kV poles W967 Tukemokihi
14011 | 02/08/2011 | 2011 | 2011-08-02 | 80 | 39 | 3120 | B | PLANNED SHUTDOWN | Replace T/x H75 Tokomaru Bay
14010 | 04/08/2011 | 2011 | 2011-08-04 | 146 | 31 | 4526 | B | PLANNED SHUTDOWN | Upgrade T/x A430 Darwin Rd
14014 | 04/08/2011 | 2011 | 2011-08-04 | 510 | 6 | 3060 | B | PLANNED SHUTDOWN | Replace 11kV pole C2679 Waughs Rd
14012 | 05/08/2011 | 2011 | 2011-08-05 | 373 | 133 | 19019 | B | PLANNED SHUTDOWN | Install new ABS G1133 SH35 Tolaga Bay South
14004 | 06/08/2011 | 2011 | 2011-08-06 | 404 | 23 | 9292 | B | PLANNED SHUTDOWN | Reconductor lines Ruatoria Sub to pole H1862
13987 | 07/08/2011 | 2011 | 2011-08-07 | 20 | 170 | 3128 | C | UNKNOWN | Reclose CB 24 Ruakituri at Tuai Sub cause unknown
13988 | 07/08/2011 | 2011 | 2011-08-07 | 880 | 118 | 48472 | C | ADVERSE WEATHER | Repair 11kv lines pole W8988 Pongaroa
14005 | 08/08/2011 | 2011 | 2011-08-08 | 300 | 26 | 7800 | B | PLANNED SHUTDOWN | Reconductor lines H1862 to H238 Ruatoria South
14008 | 10/08/2011 | 2011 | 2011-08-10 | 418 | 24 | 58028 | B | PLANNED SHUTDOWN | Replace poles A4527 A4530 A4532 A4533 Glenroy Rd
14013 | 11/08/2011 | 2011 | 2011-08-11 | 525 | 137 | 13615 | B | PLANNED SHUTDOWN | Replace 11kV poles H85 H2556 & H2557 Tokomaru St
13989 | 12/08/2011 | 2011 | 2011-08-12 | 324 | 150 | 34482 | C | TREE CONTACTS | Repair 11kV lines pole G2000 Tauwharparae Rd
13990 | 12/08/2011 | 2011 | 2011-08-12 | 370 | 36 | 7088 | C | ADVERSE WEATHER | Repair 11kV lines pole J373 Tapuawaeroa Valley Rd
13991 | 12/08/2011 | 2011 | 2011-08-12 | 98 | 15 | 1470 | C | LIGHTNING | Replace DDO fuses J42 & J1003 Poroporo Valley
13993 | 14/08/2011 | 2011 | 2011-08-14 | 176 | 240 | 8370 | C | ADVERSE WEATHER | Repair 11kV lines pole C2786 Paparatu Rd
13992 | 15/08/2011 | 2011 | 2011-08-15 | 648 | 131 | 5184 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W1210 Eripiti Rd
13994 | 17/08/2011 | 2011 | 2011-08-17 | 660 | 131 | 53560 | C | ADVERSE WEATHER | Repair 11kV lines pole W7545 to W1778 Te Reinga
13995 | 17/08/2011 | 2011 | 2011-08-17 | 497 | 150 | 44404 | C | ADVERSE WEATHER | Repair 11kV lines pole G2359 Tauwhareparae Rd
13996 | 17/08/2011 | 2011 | 2011-08-17 | 190 | 151 | 5587 | C | DEFECTIVE EQUIPMENT | Cut jumpers pole W8563 Hereheretau Rd
13997 | 17/08/2011 | 2011 | 2011-08-17 | 24 | 12 | 288 | C | DEFECTIVE EQUIPMENT | Remove redundant pole D3393 Tiniroto
13998 | 17/08/2011 | 2011 | 2011-08-17 | 1325 | 201 | 10098 | C | TREE CONTACTS | Repair 11kV lines pole W5126 Putere
13999 | 18/08/2011 | 2011 | 2011-08-18 | 897 | 92 | 32226 | C | ADVERSE WEATHER | Repair 11kV lines pole W5126 Putere
14001 | 19/08/2011 | 2011 | 2011-08-19 | 387 | 92 | 10108 | C | ADVERSE WEATHER | Repair 11kV lines beyond ABS E219 Tarndale Rd
14015 | 23/08/2011 | 2011 | 2011-08-23 | 388 | 71 | 15388 | B | PLANNED SHUTDOWN | Replace 11kV poles A3172 A3173 A3174 Endcliffe Rd
14016 | 24/08/2011 | 2011 | 2011-08-24 | 392 | 58 | 22736 | B | PLANNED SHUTDOWN | Replace 11kV poles A279 A3312 Norwood Rd
14018 | 24/08/2011 | 2011 | 2011-08-24 | 396 | 17 | 25007 | B | PLANNED SHUTDOWN | Replace Isolation fuse pole A271 Waiomoko Rd Whangara
14017 | 25/08/2011 | 2011 | 2011-08-25 | 236 | 462 | 44580 | B | PLANNED SHUTDOWN | Replace 11kV poles B4065 B4034 Aberdeen Rd
14019 | 25/08/2011 | 2011 | 2011-08-25 | 335 | 11 | 4048 | B | PLANNED SHUTDOWN | Replace 11kV pole H1628 Makarika Rd
14002 | 26/08/2011 | 2011 | 2011-08-26 | 191 | 12 | 2292 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole H1520 Makarika
14003 | 26/08/2011 | 2011 | 2011-08-26 | 37 | 79 | 2923 | C | DEFECTIVE EQUIPMENT | Replace DDO fuses D603 O Gradys Rd Crn
14020 | 31/08/2011 | 2011 | 2011-08-31 | 380 | 125 | 29075 | B | PLANNED SHUTDOWN | Replace 11kV poles B3502 B3503 B3504 Lytton Rd
14022 | 01/09/2011 | 2011 | 2011-09-01 | 424 | 31 | 4864 | B | PLANNED SHUTDOWN | install line breaks C2257
14023 | 01/09/2011 | 2011 | 2011-09-01 | 374 | 58 | 21692 | B | PLANNED SHUTDOWN | Replace poles A3310, A3311, A3312
14061 | 01/09/2011 | 2011 | 2011-09-01 | 380 | 13 | 4940 | B | PLANNED SHUTDOWN | Pole replacement
14024 | 02/09/2011 | 2011 | 2011-09-02 | 239 | 85 | 20315 | B | PLANNED SHUTDOWN | Replace pole D5055 & install links at D141
14025 | 05/09/2011 | 2011 | 2011-09-05 | 414 | 60 | 24840 | B | PLANNED SHUTDOWN | Deviate line D5051 - D5055
14026 | 05/09/2011 | 2011 | 2011-09-05 | 60 | 5 | 300 | B | PLANNED SHUTDOWN | Upgrade LV Bd at TX A565
14021 | 07/09/2011 | 2011 | 2011-09-07 | 364 | 79 | 23626 | B | PLANNED SHUTDOWN | new Tx H2638
14033 | 07/09/2011 | 2011 | 2011-09-08 | 1589 | 9 | 14301 | B | PLANNED SHUTDOWN | Replace H pole E519
14041 | 07/09/2011 | 2011 | 2011-09-07 | 155 | 95 | 7647 | C | TREE CONTACTS | pole E281 tree fell broke conductors
14027 | 08/09/2011 | 2011 | 2011-09-08 | 316 | 96 | 28916 | B | PLANNED SHUTDOWN | Replace TX A350
14028 | 08/09/2011 | 2011 | 2011-09-08 | 61 | 32 | 2012 | B | PLANNED SHUTDOWN | Rejoin jumpers at A3503
14029 | 08/09/2011 | 2011 | 2011-09-08 | 412 | 58 | 23896 | B | PLANNED SHUTDOWN | Replace poles A3307, A3182
14030 | 08/09/2011 | 2011 | 2011-09-08 | 398 | 58 | 23085 | B | PLANNED SHUTDOWN | Replace poles A3190, A3181
14042 | 08/09/2011 | 2011 | 2011-09-08 | 239 | 35 | 478 | C | TREE CONTACTS | Urgent tree cutting A3509
14035 | 09/09/2011 | 2011 | 2011-09-09 | 175 | 18 | 3150 | B | PLANNED SHUTDOWN | Replace pole C506
14036 | 12/09/2011 | 2011 | 2011-09-12 | 144 | 52 | 7488 | B | PLANNED SHUTDOWN | Replace pole H2808
14043 | 12/09/2011 | 2011 | 2011-09-12 | 170 | 21 | 3570 | C | DEFECTIVE EQUIPMENT | Broken Jumper W1056
14044 | 12/09/2011 | 2011 | 2011-09-12 | 685 | 92 | 8738 | C | DEFECTIVE EQUIPMENT | Broken conductor beyond E219
14045 | 12/09/2011 | 2011 | 2011-09-12 | 823 | 12 | 8584 | C | TREE CONTACTS | tree across line G563
14046 | 13/09/2011 | 2011 | 2011-09-13 | 31 | 11 | 308 | C | DEFECTIVE EQUIPMENT | Repair jumpers C5053
14047 | 14/09/2011 | 2011 | 2011-09-14 | 298 | 687 | 64596 | C | HUMAN ELEMENT | Truck hit pole B2108 - replace pole
14031 | 15/09/2011 | 2011 | 2011-09-15 | 390 | 130 | 19680 | B | PLANNED SHUTDOWN | Replace poles A2144, A2146, A482
14048 | 15/09/2011 | 2011 | 2011-09-15 | 51 | 6 | 306 | C | DEFECTIVE EQUIPMENT | TX W775 - lightening arrestor failed
14049 | 16/09/2011 | 2011 | 2011-09-16 | 234 | 35 | 8190 | C | FOREIGN INTERFERENCE | Magpie broke conductor G2325
14050 | 18/09/2011 | 2011 | 2011-09-18 | 112 | 687 | 20056 | C | DEFECTIVE EQUIPMENT | SWGR C596 extension failed
14051 | 19/09/2011 | 2011 | 2011-09-19 | 245 | 21 | 5145 | C | DEFECTIVE EQUIPMENT | Broken conductor W6637
14052 | 19/09/2011 | 2011 | 2011-09-19 | 36 | 1523 | 51348 | C | HUMAN ELEMENT | Car hit pole B4868
14053 | 20/09/2011 | 2011 | 2011-09-20 | 455 | 13 | 5915 | C | DEFECTIVE EQUIPMENT | Burnt pole G2101
14054 | 21/09/2011 | 2011 | 2011-09-21 | 55 | 13 | 715 | C | DEFECTIVE EQUIPMENT | Broken jumper D3075
14055 | 21/09/2011 | 2011 | 2011-09-21 | 60 | 25 | 2350 | C | DEFECTIVE EQUIPMENT | Broken jumper W8710
14032 | 22/09/2011 | 2011 | 2011-09-22 | 225 | 13 | 2925 | B | PLANNED SHUTDOWN | Replace poles D235, D3974, D3975
14034 | 22/09/2011 | 2011 | 2011-09-22 | 379 | 245 | 20688 | B | PLANNED SHUTDOWN | Replace poles B3503, B3501
14056 | 23/09/2011 | 2011 | 2011-09-23 | 53 | 40 | 2120 | C | DEFECTIVE EQUIPMENT | Broken jumper W64
14057 | 23/09/2011 | 2011 | 2011-09-24 | 110 | 76 | 5968 | C | DEFECTIVE EQUIPMENT | TX to CB H1219 failed
14058 | 27/09/2011 | 2011 | 2011-09-27 | 402 | 753 | 55288 | C | DEFECTIVE EQUIPMENT | Pole faied W5874 & W5875
14037 | 28/09/2011 | 2011 | 2011-09-28 | 65 | 36 | 2340 | B | PLANNED SHUTDOWN | Replace GM TX A77
14039 | 28/09/2011 | 2011 | 2011-09-28 | 386 | 139 | 18954 | B | PLANNED SHUTDOWN | replace poles A2147, A484, A3421
14038 | 29/09/2011 | 2011 | 2011-09-29 | 371 | 129 | 27269 | B | PLANNED SHUTDOWN | Replace poles A3179, A3176
14059 | 29/09/2011 | 2011 | 2011-09-29 | 229 | 8 | 1832 | C | TREE CONTACTS | Tree on line beyond F757
14060 | 29/09/2011 | 2011 | 2011-09-29 | 131 | 39 | 5109 | C | TREE CONTACTS | Tree on line beyond W1173
14040 | 30/09/2011 | 2011 | 2011-09-30 | 339 | 35 | 4785 | B | PLANNED SHUTDOWN | Replace pole C2210
14062 | 01/10/2011 | 2011 | 2011-10-01 | 265 | 187 | 23081 | C | HUMAN ELEMENT | Replace 11kV pole E597 hit by tractor Kanakanaia Rd
14079 | 03/10/2011 | 2011 | 2011-10-03 | 59 | 456 | 5154 | B | PLANNED SHUTDOWN | Replace 11kV poles C2191 C2192 C2193 C3301 C3306 Waingake Rd
14063 | 04/10/2011 | 2011 | 2011-10-04 | 126 | 47 | 1460 | C | DEFECTIVE EQUIPMENT | Replace 3 11kV fuse bases pole C5864 Waingake Rd
14080 | 04/10/2011 | 2011 | 2011-10-04 | 30 | 185 | 8861 | B | PLANNED SHUTDOWN | Replace 11kV poles A70 & A2490 Wairere Rd
14064 | 05/10/2011 | 2011 | 2011-10-05 | 575 | 27 | 16497 | C | TREE CONTACTS | Replace 2 11kV poles G2349 & G2348 Tree cutters dropped tree on line
14081 | 05/10/2011 | 2011 | 2011-10-05 | 485 | 59 | 7303 | B | PLANNED SHUTDOWN | Replace 11kV poles C3321 C3325 C5867 C2907 Waingake Rd
14082 | 05/10/2011 | 2011 | 2011-10-05 | 313 | 45 | 9205 | B | PLANNED SHUTDOWN | Replace 11kV ABS G174 Tauwhareparae Rd
14065 | 06/10/2011 | 2011 | 2011-10-06 | 50 | 25 | 1250 | C | DEFECTIVE EQUIPMENT | Replace burnt out DDO fuse base W355 Putere
14066 | 07/10/2011 | 2011 | 2011-10-07 | 361 | 7 | 2527 | C | DEFECTIVE EQUIPMENT | Replace T/x C415 Shanks Rd Waingake
14067 | 10/10/2011 | 2011 | 2011-10-10 | 373 | 42 | 5684 | C | TREE CONTACTS | Remove trees from 11kV H2301 Carroll St Te Puia
14083 | 10/10/2011 | 2011 | 2011-10-10 | 433 | 21 | 8872 | B | PLANNED SHUTDOWN | Replace 11kV poles C753 & C762 Waingake Rd
14095 | 10/10/2011 | 2011 | 2011-10-10 | 376 | 12 | 4512 | B | PLANNED SHUTDOWN | Replace H pole D1110 Parikanapa Rd
14068 | 11/10/2011 | 2011 | 2011-10-11 | 51 | 69 | 3519 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole H4008 Crn Arthur St & SH35 Tokomaru Bay
14085 | 11/10/2011 | 2011 | 2011-10-11 | 97 | 74 | 7178 | B | PLANNED SHUTDOWN | Replace T/x B622 Stout St
14069 | 12/10/2011 | 2011 | 2011-10-12 | 499 | 270 | 37218 | C | TREE CONTACTS | Repair 11kV lines pole D3444 Taumata Rd
14070 | 12/10/2011 | 2011 | 2011-10-12 | 65 | 83 | 5395 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole D3444 Taumata Rd
14086 | 12/10/2011 | 2011 | 2011-10-12 | 318 | 94 | 11874 | B | PLANNED SHUTDOWN | Replace 11kV poles A2369 A2372 A2376 Wairere Rd
14088 | 12/10/2011 | 2011 | 2011-10-12 | 403 | 139 | 56017 | B | PLANNED SHUTDOWN | Replace 11kV poles G2960 & G2965 Solander St Tolaga Bay
14071 | 13/10/2011 | 2011 | 2011-10-13 | 73 | 194 | 7272 | C | DEFECTIVE EQUIPMENT | Isolate faulty T/x H598 Ihungia Rd
14087 | 13/10/2011 | 2011 | 2011-10-13 | 41 | 47 | 1823 | B | PLANNED SHUTDOWN | Replace 11kV poles H1761 H1760 & H1865 SH35 Ruatoria South
14089 | 13/10/2011 | 2011 | 2011-10-13 | 326 | 139 | 45314 | B | PLANNED SHUTDOWN | Replace 11kV poles G2959 G275 & G2963 Solander St Tolaga Bay
14072 | 14/10/2011 | 2011 | 2011-10-14 | 120 | 5 | 600 | C | DEFECTIVE EQUIPMENT | Replace faulty T/x H598 Ihungia Rd
14090 | 14/10/2011 | 2011 | 2011-10-14 | 83 | 65 | 5395 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting pole E280
14097 | 14/10/2011 | 2011 | 2011-10-14 | 100 | 6 | 600 | B | PLANNED SHUTDOWN | Install DDOs on pole C3956 Dunstan Rd
14098 | 14/10/2011 | 2011 | 2011-10-14 | 131 | 35 | 4585 | B | PLANNED SHUTDOWN | Replace LBS T/x H1219 Mata Rd
14073 | 17/10/2011 | 2011 | 2011-10-17 | 296 | 184 | 54464 | C | FOREIGN INTERFERENCE | Replace 11kV pole J1050 Rangitukia Rd hit by Truck
14092 | 18/10/2011 | 2011 | 2011-10-18 | 431 | 179 | 66361 | B | PLANNED SHUTDOWN | Replace 11kV poles E1678 E796 Whatatutu Rd
14091 | 19/10/2011 | 2011 | 2011-10-19 | 157 | 115 | 18055 | B | PLANNED SHUTDOWN | Replace T/x B42 King St
14093 | 19/10/2011 | 2011 | 2011-10-19 | 238 | 91 | 21658 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting D409
14094 | 20/10/2011 | 2011 | 2011-10-20 | 350 | 67 | 23450 | B | PLANNED SHUTDOWN | Replace 11kV poles Beyond W1128 Marumaru
14074 | 21/10/2011 | 2011 | 2011-10-21 | 338 | 98 | 33124 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable B517 to T/x B518 Patrick St
14096 | 21/10/2011 | 2011 | 2011-10-21 | 255 | 139 | 21165 | B | PLANNED SHUTDOWN | Replace 11kV poles A3176 A3302 Encliffe Rd
14075 | 23/10/2011 | 2011 | 2011-10-23 | 377 | 195 | 31178 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole E614 Kanakanaia Rd
14099 | 26/10/2011 | 2011 | 2011-10-26 | 437 | 95 | 6955 | B | PLANNED SHUTDOWN | Replace 2 11kV poles F1064 & F1069 Kanakanaia Rd
14076 | 27/10/2011 | 2011 | 2011-10-27 | 65 | 27 | 1755 | C | DEFECTIVE EQUIPMENT | Replace burnt 11kV pole D3646 Bushy Knoll Rd
14084 | 28/10/2011 | 2011 | 2011-10-28 | 326 | 137 | 44662 | B | PLANNED SHUTDOWN | Replace poles J61 & J71 Rangitukia Rd
14077 | 30/10/2011 | 2011 | 2011-10-30 | 288 | 706 | 75196 | C | FOREIGN INTERFERENCE | Replace 50kV pole A6467 De Latour Rd
14078 | 30/10/2011 | 2011 | 2011-10-30 | 1263 | 92 | 17357 | C | FOREIGN INTERFERENCE | Remove Magpie bird from 11kV pole E669 Tarndale Rd
14100 | 01/11/2011 | 2011 | 2011-12-01 | 399 | 1139 | 346936 | C | TREE CONTACTS | Remove branch from pole W3836 to W3837 Wai St Nuhaka
14131 | 01/11/2011 | 2011 | 2011-11-01 | 480 | 34 | 8530 | B | PLANNED SHUTDOWN | Replace 11kV poles C769 C772 C774 Waingake Rd
14134 | 01/11/2011 | 2011 | 2011-11-01 | 52 | 21 | 1092 | B | PLANNED SHUTDOWN | Install line breaks pole C922 Tiniroto Rd
14136 | 01/11/2011 | 2011 | 2011-11-01 | 331 | 94 | 22910 | B | PLANNED SHUTDOWN | Replace poles A2376 A2356 Wairere Rd
14132 | 02/11/2011 | 2011 | 2011-11-02 | 547 | 34 | 9478 | B | PLANNED SHUTDOWN | Replace 11kV poles C778 C789 Waingake Rd
14135 | 02/11/2011 | 2011 | 2011-11-02 | 407 | 8 | 2578 | B | PLANNED SHUTDOWN | Replace 11kV poles C928 C933 Tiniroto Rd
14138 | 02/11/2011 | 2011 | 2011-11-02 | 388 | 12 | 47916 | B | PLANNED SHUTDOWN | Replace 11kVpoles G1537 G1535 G1534 Kiore Rd
14137 | 08/11/2011 | 2011 | 2011-11-08 | 400 | 33 | 13200 | B | PLANNED SHUTDOWN | Replace 11kV poles B4595 B4594 B4593 B4592 B4591 Matokitoki Valley
14101 | 09/11/2011 | 2011 | 2011-11-09 | 498 | 35 | 13500 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole D231 Pehiri
14102 | 10/11/2011 | 2011 | 2011-11-10 | 212 | 74 | 13708 | C | TREE CONTACTS | Repair 11kV lines pole F1602 to F264 Te Wera Rd
14103 | 10/11/2011 | 2011 | 2011-11-10 | 573 | 76 | 22588 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines W1747 to W6612 Mangapoikie
14104 | 10/11/2011 | 2011 | 2011-11-10 | 674 | 14 | 9436 | C | UNKNOWN | Patrol line and Checked Cause unknown D2753 Totangi Rd
14105 | 10/11/2011 | 2011 | 2011-11-10 | 302 | 565 | 28070 | C | TREE CONTACTS | Remove trees 11kV lines W1610 to W1609 Ruatanawha Rd
14107 | 10/11/2011 | 2011 | 2011-11-10 | 1277 | 14 | 17878 | C | TREE CONTACTS | Repair 11kV lines W8052 to W8051 Mangone Valley
14108 | 10/11/2011 | 2011 | 2011-11-10 | 346 | 217 | 50754 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W7636 to W7637 Pongaroa
14109 | 10/11/2011 | 2011 | 2011-11-10 | 130 | 14 | 2520 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W9609 Tuanui Rd
14110 | 10/11/2011 | 2011 | 2011-11-10 | 31 | 21 | 651 | C | TREE CONTACTS | Remove tree from 11kV pole C802 Waingake Rd
14111 | 10/11/2011 | 2011 | 2011-11-10 | 235 | 75 | 3440 | C | TREE CONTACTS | Remove branch 11kV pole H502 Mata Rd
14146 | 10/11/2011 | 2011 | 2011-11-10 | 420 | 5 | 3800 | B | PLANNED SHUTDOWN | Replace 11kV poles F1054 F1055 F1056 Paulson Rd
14106 | 11/11/2011 | 2011 | 2011-11-11 | 106 | 432 | 22741 | C | TREE CONTACTS | Isolate 50kV / 11kV lines F1577 to F1576 Otoko
14112 | 11/11/2011 | 2011 | 2011-11-11 | 11 | 87 | 957 | C | TREE CONTACTS | Remove tree branch from 11kV pole W1106 Mahunga Mahia
14115 | 11/11/2011 | 2011 | 2011-11-11 | 463 | 146 | 15615 | C | TREE CONTACTS | Repair 11kV line beyond pole W5585 Kahangungu
14116 | 11/11/2011 | 2011 | 2011-11-11 | 1655 | 146 | 33095 | C | TREE CONTACTS | Repair 11kV line poles W5592 to W5590 Kahangungu
14139 | 11/11/2011 | 2011 | 2011-11-11 | 47 | 47 | 2209 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers pole H1772 Ruatoria South
14117 | 15/11/2011 | 2011 | 2011-11-15 | 25 | 42 | 945 | C | DEFECTIVE EQUIPMENT | Repair handle on ABS C221 Bushmere Rd
14118 | 18/11/2011 | 2011 | 2011-11-18 | 101 | 663 | 17602 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W1218 Ruatanawha Rd
14141 | 18/11/2011 | 2011 | 2011-11-18 | 221 | 30 | 6630 | B | PLANNED SHUTDOWN | Replace poles D3585 D3589 D3599 Ruakaka Rd
14119 | 19/11/2011 | 2011 | 2011-11-19 | 63 | 36 | 2268 | C | DEFECTIVE EQUIPMENT | Repair 11kV lead on T/x W1762 Whakakihi
14120 | 20/11/2011 | 2011 | 2011-11-20 | 30 | 2528 | 75840 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
14121 | 21/11/2011 | 2011 | 2011-11-21 | 577 | 74 | 26558 | C | TREE CONTACTS | Repair 11kV lines pole F1602 Te Wera Rd
14122 | 21/11/2011 | 2011 | 2011-11-21 | 231 | 1139 | 205909 | C | TREE CONTACTS | Remove tree from 33kV lines pole W3837 Nuhaka
14123 | 21/11/2011 | 2011 | 2011-11-21 | 212 | 33 | 3036 | C | TREE CONTACTS | Repair 11kV line pole D198 to D1118 Parakanapa Rd
14143 | 21/11/2011 | 2011 | 2011-11-21 | 503 | 157 | 40824 | B | PLANNED SHUTDOWN | Reconductor 11kV poles B4051 to B4060 Aberdeen Rd
14124 | 22/11/2011 | 2011 | 2011-11-22 | 409 | 17 | 6953 | C | FOREIGN INTERFERENCE | Replace 11kV river Xing W5590 to W5591 Kahangungu
14144 | 22/11/2011 | 2011 | 2011-11-22 | 486 | 42 | 20412 | B | PLANNED SHUTDOWN | Replace poles F2183 & F2194 Koranga Valley
14125 | 23/11/2011 | 2011 | 2011-11-23 | 105 | 9 | 945 | C | DEFECTIVE EQUIPMENT | Repair Xarm on pole W5001 Waireka Rd
14126 | 23/11/2011 | 2011 | 2011-11-23 | 208 | 170 | 35360 | C | DEFECTIVE EQUIPMENT | Isolate 11kV lines pole W656 Eripiti
14147 | 23/11/2011 | 2011 | 2011-11-23 | 376 | 73 | 15353 | B | PLANNED SHUTDOWN | Replace 11kV poles B1988 B1989 B1841 B4600 Matokitoki Valley
14127 | 24/11/2011 | 2011 | 2011-11-24 | 567 | 18 | 4882 | C | DEFECTIVE EQUIPMENT | Cut jumpers pole W6210 Kiwi Valley
14142 | 24/11/2011 | 2011 | 2011-11-24 | 305 | 29 | 8845 | B | PLANNED SHUTDOWN | Isolate for tree cutting ABS E188 Whatatutu
14145 | 24/11/2011 | 2011 | 2011-11-24 | 119 | 21 | 2499 | B | PLANNED SHUTDOWN | Replace Isolation fuses C100 Waingake
14148 | 25/11/2011 | 2011 | 2011-11-25 | 36 | 68 | 2448 | B | PLANNED SHUTDOWN | Install DDO fuses ploe A2585 Wainui Rd
14149 | 25/11/2011 | 2011 | 2011-11-25 | 333 | 8 | 2150 | B | PLANNED SHUTDOWN | Replace 11kV poles C111 C931 C932 Tiniroto Rd
14128 | 26/11/2011 | 2011 | 2011-11-26 | 81 | 47 | 3807 | C | DEFECTIVE EQUIPMENT | Replace faulty DDO fuses T/x J93 Ruatoria
14129 | 28/11/2011 | 2011 | 2011-11-28 | 203 | 195 | 38595 | C | ADVERSE WEATHER | Repair 11kV lines pole W1212 Tuai
14133 | 28/11/2011 | 2011 | 2011-11-28 | 275 | 7 | 3563 | B | PLANNED SHUTDOWN | Reposition pole C5873 Shanks Rd Waingake
14130 | 30/11/2011 | 2011 | 2011-11-30 | 30 | 6 | 180 | C | DEFECTIVE EQUIPMENT | Replace 11kV lines pole A2407 Sponge Bay
14166 | 01/12/2011 | 2011 | 2011-12-01 | 377 | 32 | 12064 | B | PLANNED SHUTDOWN | Replace 11kV poles B4582 B4584 B4585 B4587 B4588 Matokitoki Valley
14176 | 01/12/2011 | 2011 | 2011-12-01 | 264 | 34 | 8976 | B | PLANNED SHUTDOWN | Replace 11kV poles E1940 & E1941 Whatatutu
14167 | 02/12/2011 | 2011 | 2011-12-02 | 306 | 118 | 36020 | B | PLANNED SHUTDOWN | Rep[lace 11kV poles B3503 Lytton Rd
14150 | 04/12/2011 | 2011 | 2011-12-04 | 154 | 53 | 7832 | C | DEFECTIVE EQUIPMENT | Isolate 11kV line F300 Phillips Rd
14173 | 05/12/2011 | 2011 | 2011-12-05 | 393 | 42 | 42852 | B | PLANNED SHUTDOWN | Replace 11kV polesG1572 & G1593 Kiore Rd
14168 | 06/12/2011 | 2011 | 2011-12-06 | 456 | 63 | 17971 | B | PLANNED SHUTDOWN | Replace 11kV poles C5034 C5032 C5031 Makaraka Rd
14170 | 07/12/2011 | 2011 | 2011-12-07 | 276 | 32 | 12672 | B | PLANNED SHUTDOWN | Replace poles B1984 B1988 B1987 B640 Matokitoki Valley
14169 | 08/12/2011 | 2011 | 2011-12-08 | 170 | 13 | 2210 | B | PLANNED SHUTDOWN | Install new T/x F4315 Olivers Rd
14171 | 08/12/2011 | 2011 | 2011-12-08 | 399 | 122 | 48678 | B | PLANNED SHUTDOWN | Replace 11kV poles J71 & J72 Rangitukia Rd
14151 | 09/12/2011 | 2011 | 2011-12-09 | 140 | 15 | 2100 | C | DEFECTIVE EQUIPMENT | Repl;ace 11kV pole C778 Waingake Rd
14152 | 09/12/2011 | 2011 | 2011-12-09 | 54 | 49 | 2646 | C | DEFECTIVE EQUIPMENT | Replace Kidney pole H2646 Beach Rd Tokomaru Bay
14164 | 09/12/2011 | 2011 | 2011-12-09 | 480 | 8 | 3840 | B | PLANNED SHUTDOWN | Replace 11kV pole C806 Tarewa Rd
14172 | 09/12/2011 | 2011 | 2011-12-09 | 335 | 8 | 2680 | B | PLANNED SHUTDOWN | Replace 11kV poles C111 & C930 Tiniroto Rd
14153 | 12/12/2011 | 2011 | 2011-12-12 | 132 | 333 | 43956 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W3621 Newcastle St Mahia
14154 | 12/12/2011 | 2011 | 2011-12-12 | 7 | 59 | 413 | C | TREE CONTACTS | Remove tree from 11kV pole C2624 Taurau Valley Rd
14155 | 13/12/2011 | 2011 | 2011-12-13 | 223 | 96 | 17936 | C | DEFECTIVE EQUIPMENT | Replace 3 11kV Discs pole J3986 outside Te Araroa Sub
14175 | 13/12/2011 | 2011 | 2011-12-13 | 396 | 30 | 4263 | B | PLANNED SHUTDOWN | Replace 11kV poles D2543 D2556 D2558 D2562 Pehiri Rd
14177 | 13/12/2011 | 2011 | 2011-12-13 | 354 | 32 | 11328 | B | PLANNED SHUTDOWN | Replace 11kV poles B4585 B4584 Matokitoki Valley
14157 | 14/12/2011 | 2011 | 2011-12-14 | 303 | 145 | 7851 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W827 Mohaka
14174 | 15/12/2011 | 2011 | 2011-12-15 | 401 | 61 | 4319 | B | PLANNED SHUTDOWN | Replace 11kV poles C2007 C2008 C2009 C2010 Mc laurins Rd
14158 | 16/12/2011 | 2011 | 2011-12-16 | 542 | 508 | 23154 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarm pole G329 SH35 Tolaga Bay South
14159 | 16/12/2011 | 2011 | 2011-12-16 | 18 | 75 | 1350 | C | UNKNOWN | Reclose CB H341 Mata Rd cause unknown
14178 | 19/12/2011 | 2011 | 2011-12-19 | 47 | 21 | 987 | B | PLANNED SHUTDOWN | Replace 11kV poles C926 & C927 Tiniroto Rd
14182 | 19/12/2011 | 2011 | 2011-12-19 | 260 | 4 | 1040 | B | PLANNED SHUTDOWN | Erect Xrm on 11kV pole F346 for Tapp Off Otara Stn Whatatutu
14180 | 20/12/2011 | 2011 | 2011-12-20 | 245 | 75 | 18375 | B | PLANNED SHUTDOWN | Replace 11kV pole C2169 Waingake Rd
14160 | 21/12/2011 | 2011 | 2011-12-21 | 29 | 1093 | 28841 | C | UNKNOWN | Reclose CB F411 Inc 1 at Puha Sub cause unknown
14179 | 21/12/2011 | 2011 | 2011-12-21 | 170 | 26 | 4420 | B | PLANNED SHUTDOWN | Relocate 11kV pole H1439 Hiruharama
14181 | 21/12/2011 | 2011 | 2011-12-21 | 400 | 281 | 59439 | B | PLANNED SHUTDOWN | Replace 11kV poles B3503 B3511 B3512 Lytton Rd
14161 | 22/12/2011 | 2011 | 2011-12-22 | 91 | 145 | 3555 | C | DEFECTIVE EQUIPMENT | Replace 11kV T/x pole W1743 Putere Rd
14165 | 22/12/2011 | 2011 | 2011-12-22 | 360 | 9 | 3240 | B | PLANNED SHUTDOWN | Isolate 11kV lines A173 for tree cutting Panikau Rd
14162 | 23/12/2011 | 2011 | 2011-12-23 | 16 | 36 | 576 | C | DEFECTIVE EQUIPMENT | Reposition Xarm on pole W9135 Kaiwaitau Rd
14163 | 23/12/2011 | 2011 | 2011-12-23 | 16 | 172 | 2752 | C | TREE CONTACTS | Remove tree from 11kV pole B2433 Hospital Rd
14183 | 02/01/2012 | 2011 | 2012-01-02 | 109 | 724 | 18184 | C | TREE CONTACTS | Remove tree from 11kV pole W1127 Tiniroto Rd
14184 | 08/01/2012 | 2011 | 2012-01-08 | 700 | 165 | 65733 | C | TREE CONTACTS | Repair 11kV lines pole D787 Tahunga
14185 | 08/01/2012 | 2011 | 2012-01-08 | 948 | 278 | 91434 | C | TREE CONTACTS | Remove tree from 11kV pole D1205 W/O/Kuri
14186 | 08/01/2012 | 2011 | 2012-01-08 | 78 | 266 | 14212 | C | TREE CONTACTS | Remove tree branch from 11kV pole H4305 Tokomaru Bay Township
14187 | 10/01/2012 | 2011 | 2012-01-10 | 59 | 579 | 18656 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable pole A2058 Wainui Rd
14206 | 10/01/2012 | 2011 | 2012-01-10 | 327 | 94 | 23654 | B | PLANNED SHUTDOWN | Replace 11kV poles A2356 & resite pole A2376 Wairere Rd
14208 | 12/01/2012 | 2011 | 2012-01-12 | 352 | 25 | 2985 | B | PLANNED SHUTDOWN | Replace poles C933 Tiniroto Rd
14188 | 13/01/2012 | 2011 | 2012-01-13 | 91 | 21 | 1911 | C | ADVERSE WEATHER | Repair 11kV lines pole W312 Tukemokihi Rd
14189 | 13/01/2012 | 2011 | 2012-01-13 | 370 | 68 | 15484 | C | TREE CONTACTS | Repair 11kV lines pole H4163 to H4165 Ihungia Rd
14190 | 13/01/2012 | 2011 | 2012-01-13 | 262 | 170 | 9152 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W992 Mahiwi
14191 | 13/01/2012 | 2011 | 2012-01-13 | 117 | 168 | 33516 | C | ADVERSE WEATHER | Reclose CB W816 Ohuka High Winds
14192 | 13/01/2012 | 2011 | 2012-01-13 | 460 | 75 | 5889 | C | TREE CONTACTS | Remove tree from 11kV pole H145 Ihungia Rd
14193 | 13/01/2012 | 2011 | 2012-01-13 | 35 | 653 | 16037 | C | TREE CONTACTS | Remove tree from 11kV pole E34 Bck Ormond Rd
14207 | 13/01/2012 | 2011 | 2012-01-13 | 205 | 55 | 11275 | B | PLANNED SHUTDOWN | Replace T/x pole C249 Makaraka Rd
14194 | 14/01/2012 | 2011 | 2012-01-14 | 670 | 92 | 28689 | C | TREE CONTACTS | Repair 11kV lines past poles E670 to E672 Tarndale Rd
14195 | 14/01/2012 | 2011 | 2012-01-14 | 425 | 181 | 47461 | C | TREE CONTACTS | Repair 11kV lines pole H57 SH35 Tokomaru Bay
14196 | 16/01/2012 | 2011 | 2012-01-16 | 355 | 14 | 4970 | C | DEFECTIVE EQUIPMENT | Replace 2 11kV poles W21009 7 W21008 Tininui
14197 | 16/01/2012 | 2011 | 2012-01-16 | 8 | 5534 | 27619 | C | FOREIGN INTERFERENCE | Check 50kV lines poles C1031 to C1032 Taruheru Cemetery
14198 | 17/01/2012 | 2011 | 2012-01-17 | 50 | 589 | 25153 | C | UNKNOWN | Patrol 11kV lines reclose CB C93 Nelson Rd Makaraka Sub
14210 | 17/01/2012 | 2011 | 2012-01-17 | 408 | 171 | 14440 | B | PLANNED SHUTDOWN | Replace ABS pole E214 Te Hau Rd
14211 | 19/01/2012 | 2011 | 2012-01-19 | 370 | 19 | 7030 | B | PLANNED SHUTDOWN | Replace pole E1952 Te Hau Rd Whatatutu
14212 | 20/01/2012 | 2011 | 2012-01-20 | 387 | 49 | 18963 | B | PLANNED SHUTDOWN | Isolate and Earth 11kV lines for 50kV ABS change W1441 Patunamu Rd
14199 | 21/01/2012 | 2011 | 2012-01-21 | 126 | 151 | 8319 | C | TREE CONTACTS | Repair 11kV lines pole W8523 Whakakihi
14200 | 21/01/2012 | 2011 | 2012-01-21 | 88 | 19 | 1672 | C | DEFECTIVE EQUIPMENT | Repair 11kV Cable pole C295 Aerodrome Rd
14201 | 23/01/2012 | 2011 | 2012-01-23 | 68 | 202 | 12360 | C | TREE CONTACTS | Remove tree 11kV lines pole D2904 Wharekopae Rd
14209 | 23/01/2012 | 2011 | 2012-01-23 | 410 | 21 | 3140 | B | PLANNED SHUTDOWN | Replace poles C933 Tiniroto Rd
14202 | 25/01/2012 | 2011 | 2012-01-25 | 91 | 17 | 2091 | C | TREE CONTACTS | Remove tree 11kV poles H342 to H74 Tokomaru Bay
14213 | 25/01/2012 | 2011 | 2012-01-25 | 239 | 175 | 41825 | B | PLANNED SHUTDOWN | Isolate 11kV lines B777 Hospital Rd for tree Cutting
14204 | 26/01/2012 | 2011 | 2012-01-26 | 5 | 76 | 380 | C | FOREIGN INTERFERENCE | Remove kite from 11kV lines pole B2040 Riverside Rd
14214 | 26/01/2012 | 2011 | 2012-01-26 | 384 | 117 | 29978 | B | PLANNED SHUTDOWN | Replace poles A2397 A2388 Wairere Rd
14205 | 28/01/2012 | 2011 | 2012-01-28 | 173 | 61 | 3892 | C | DEFECTIVE EQUIPMENT | Cut away conductor poles H3241 to H3242 Te Puia
14215 | 01/02/2012 | 2011 | 2012-02-01 | 154 | 32 | 3211 | C | TREE CONTACTS | Repair lines pole D2604 Pehiri Rd
14236 | 01/02/2012 | 2011 | 2012-02-01 | 358 | 19 | 6802 | B | PLANNED SHUTDOWN | Replace poles beyond E157 Te Hau Rd Whatatutu
14234 | 02/02/2012 | 2011 | 2012-02-02 | 92 | 27 | 2484 | B | PLANNED SHUTDOWN | Replace pole W7039 Ebbett Rd Wairoa
14237 | 02/02/2012 | 2011 | 2012-02-02 | 328 | 47 | 15416 | B | PLANNED SHUTDOWN | Replace 11kV poles H1831 H1830 H1817 Ruatoria South
14216 | 03/02/2012 | 2011 | 2012-02-03 | 32 | 265 | 15092 | C | DEFECTIVE EQUIPMENT | Replace T/x pole J352 & install polymers
14217 | 08/02/2012 | 2011 | 2012-02-08 | 126 | 15 | 1890 | C | TREE CONTACTS | Repair 11kV lines pole A206 Kaiti Hill
14238 | 08/02/2012 | 2011 | 2012-02-08 | 234 | 10 | 2340 | B | PLANNED SHUTDOWN | Replace 11kV pole Beyond F141 Hihiroroa Rd
14244 | 09/02/2012 | 2011 | 2012-02-09 | 345 | 5 | 1725 | B | PLANNED SHUTDOWN | Replace 11kV poles beyond H229 Karewa Rd
14241 | 10/02/2012 | 2011 | 2012-02-10 | 388 | 10 | 3880 | B | PLANNED SHUTDOWN | Replace 11kV poles H1517 H1519 H1520 H1521 Horehore Rd
14218 | 12/02/2012 | 2011 | 2012-02-12 | 80 | 51 | 4080 | C | FOREIGN INTERFERENCE | Repair 11kv lines pole E1773 SH2 Te Karaka
14219 | 12/02/2012 | 2011 | 2012-02-12 | 354 | 204 | 35432 | C | FOREIGN INTERFERENCE | Replace 50kV pole C3901 Willows Rd
14233 | 12/02/2012 | 2011 | 2012-02-12 | 325 | 25 | 8125 | B | PLANNED SHUTDOWN | Replace T/x F231 Matawai Township
14220 | 13/02/2012 | 2011 | 2012-02-13 | 18 | 114 | 3762 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole G135 Tauwhareparae Rd
14221 | 14/02/2012 | 2011 | 2012-02-14 | 16 | 1139 | 18224 | C | ADVERSE WEATHER | Reclose CB W2 Kiwi B at Wairoa Sub Lightining
14239 | 14/02/2012 | 2011 | 2012-02-14 | 241 | 31 | 7471 | B | PLANNED SHUTDOWN | Replace T/x D622 Glenelg Rd & LV Re sag
14222 | 15/02/2012 | 2011 | 2012-02-15 | 461 | 21 | 3105 | C | DEFECTIVE EQUIPMENT | Replace 11kV poles G2165 G2166 & G89 Paroa Rd
14223 | 15/02/2012 | 2011 | 2012-02-15 | 814 | 150 | 39010 | C | DEFECTIVE EQUIPMENT | Repair jumper pole G1773 Tauwhareparae Rd
14235 | 15/02/2012 | 2011 | 2012-02-15 | 323 | 31 | 10013 | B | PLANNED SHUTDOWN | Isolate 11kV E29 Waihirere Rd for tree cutting
14242 | 17/02/2012 | 2011 | 2012-02-17 | 296 | 11 | 3256 | B | PLANNED SHUTDOWN | Replace 11kV poles H1662 H1653 H1651 Matahia Rd
14224 | 20/02/2012 | 2011 | 2012-02-20 | 790 | 21 | 4265 | C | FOREIGN INTERFERENCE | Repair lines pole G1670 Paroa Rd tree pushed over by Bulldozer
14243 | 20/02/2012 | 2011 | 2012-02-20 | 380 | 10 | 3800 | B | PLANNED SHUTDOWN | Replace 11kV poles H1522 H1523 H1524 H1525 Horehore Rd
14245 | 21/02/2012 | 2011 | 2012-02-21 | 365 | 11 | 4015 | B | PLANNED SHUTDOWN | Replace 11kV poles H1650 H1645 H1644 Matahia Rd
14225 | 22/02/2012 | 2011 | 2012-02-22 | 74 | 16 | 1184 | C | TREE CONTACTS | Remove tree from 11kV pole J208 Poroporo Rd
14226 | 23/02/2012 | 2011 | 2012-02-23 | 7 | 567 | 3969 | C | DEFECTIVE EQUIPMENT | Isolate ABS E1892 Bck Ormond Rd
14227 | 23/02/2012 | 2011 | 2012-02-23 | 726 | 105 | 60725 | C | FOREIGN INTERFERENCE | Remove pussom from pole J4476 Hicks Bay
14246 | 23/02/2012 | 2011 | 2012-02-23 | 166 | 93 | 15438 | B | PLANNED SHUTDOWN | Repair 11kV lines pole D4410 Bck Ormond Rd
14228 | 24/02/2012 | 2011 | 2012-02-24 | 1402 | 402 | 183031 | C | TREE CONTACTS | Repair 11kV lines poles W6424 Mohaka
14247 | 24/02/2012 | 2011 | 2012-02-24 | 327 | 19 | 6213 | B | PLANNED SHUTDOWN | Replace poles beyond E157 Te Hau Rd Whatatutu
14229 | 25/02/2012 | 2011 | 2012-02-25 | 84 | 175 | 12958 | C | DEFECTIVE EQUIPMENT | Jumper out faulty ABS W1010 Waihua
14230 | 25/02/2012 | 2011 | 2012-02-25 | 285 | 122 | 34770 | C | DEFECTIVE EQUIPMENT | Replace burnt Xarm pole J1193 Rangitikia Rd
14231 | 25/02/2012 | 2011 | 2012-02-25 | 13 | 173 | 2249 | C | TREE CONTACTS | Remove tree 11kV pole E3992 Whitmore Rd Ormond
14232 | 27/02/2012 | 2011 | 2012-02-27 | 606 | 57 | 10686 | C | TREE CONTACTS | Repair 11kv lines pole W486 Waireka Rd
14240 | 27/02/2012 | 2011 | 2012-02-27 | 360 | 44 | 15840 | B | PLANNED SHUTDOWN | Replace 11kV poles C2818 C2821 C2833 Papatu Rd
14248 | 29/02/2012 | 2011 | 2012-02-29 | 401 | 29 | 63191 | B | PLANNED SHUTDOWN | Replace 11kV poles beyond E188 Mangamaia Rd
14249 | 01/03/2012 | 2011 | 2012-03-01 | 1166 | 322 | 169686 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumpers pole W8986 Mohaka
14250 | 02/03/2012 | 2011 | 2012-03-02 | 22 | 953 | 11650 | C | UNKNOWN | Reclose CB A475 Kaiti Sub cause unknown
14251 | 02/03/2012 | 2011 | 2012-03-02 | 278 | 127 | 15858 | C | DEFECTIVE EQUIPMENT | Replace ABS E1892 Bck Ormond Rd
14309 | 02/03/2012 | 2011 | 2012-03-02 | 197 | 18 | 3546 | B | PLANNED SHUTDOWN | Isolate 11kV lines H1586 to H1500 Whakapourangi Rd for tree Cutting
14310 | 02/03/2012 | 2011 | 2012-03-02 | 367 | 19 | 6661 | B | PLANNED SHUTDOWN | Replace 11kV poles & resag lines at pole E1952 Te Hau Rd
14252 | 03/03/2012 | 2011 | 2012-03-03 | 1195 | 31 | 41819 | C | TREE CONTACTS | Repair 11kV lines pole W8986 Kinikini
14253 | 03/03/2012 | 2011 | 2012-03-03 | 1389 | 75 | 29892 | C | TREE CONTACTS | Replace broken pole H1420 Mata Rd (Trees)
14254 | 03/03/2012 | 2011 | 2012-03-03 | 186 | 92 | 9181 | C | ADVERSE WEATHER | Cut jumpers poles G2138 & G2148 Paroa Rd (Broken poles)
14255 | 03/03/2012 | 2011 | 2012-03-03 | 96 | 62 | 4808 | C | TREE CONTACTS | Repair 11kV lines poles D203 to D3355 Tiniroto Rd
14256 | 03/03/2012 | 2011 | 2012-03-03 | 57 | 687 | 32269 | C | DEFECTIVE EQUIPMENT | Alter 11kV jumpers on cable pole T/x C599 Nelson Rd
14257 | 03/03/2012 | 2011 | 2012-03-03 | 1370 | 90 | 76890 | C | TREE CONTACTS | Repair 11kV lines pole W8316 Morere
14258 | 03/03/2012 | 2011 | 2012-03-03 | 260 | 36 | 9360 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W8293 Whakaki
14259 | 03/03/2012 | 2011 | 2012-03-03 | 329 | 151 | 8360 | C | TREE CONTACTS | Repair 11kV lines pole W382 Hereheretau
14260 | 03/03/2012 | 2011 | 2012-03-03 | 24 | 110 | 2583 | C | ADVERSE WEATHER | Reclose W6835 High winds clashing conductors
14261 | 03/03/2012 | 2011 | 2012-03-03 | 60 | 525 | 38430 | C | ADVERSE WEATHER | Summary of Faults Adverse WeatherW1032 Mahia
14262 | 03/03/2012 | 2011 | 2012-03-03 | 69 | 153 | 9720 | C | ADVERSE WEATHER | Cut jumpers poles W9087 & W20694 Mahunga Mahia
14263 | 03/03/2012 | 2011 | 2012-03-03 | 1526 | 265 | 313164 | C | TREE CONTACTS | Repair 11kV lines pole E3163 Whatatutu
14264 | 04/03/2012 | 2011 | 2012-03-04 | 1623 | 14 | 22722 | B | PLANNED SHUTDOWN | Repair 11kV lines pole W850 Mangone Rd Morere
14265 | 04/03/2012 | 2011 | 2012-03-04 | 18 | 21 | 378 | C | DEFECTIVE EQUIPMENT | Replace 11kV jumper pole W3007 Rutherford St
14266 | 04/03/2012 | 2011 | 2012-03-04 | 170 | 16 | 1920 | C | FOREIGN INTERFERENCE | Temp prop 11kV pole E1370 Kaiteratahi hit by Car
14267 | 04/03/2012 | 2011 | 2012-03-04 | 208 | 122 | 14726 | C | TREE CONTACTS | Repair 11kV lines pole J7242 Makarika
14268 | 04/03/2012 | 2011 | 2012-03-04 | 935 | 19 | 17765 | C | ADVERSE WEATHER | Repair 11kV lines pole W8754 Mahia
14269 | 04/03/2012 | 2011 | 2012-03-04 | 1453 | 150 | 83358 | C | TREE CONTACTS | Repair 11kV lines poles G2004 & G2267 Tauwhareparae Rd
14270 | 05/03/2012 | 2011 | 2012-03-05 | 104 | 56 | 4592 | C | TREE CONTACTS | Repair 11kV lines Poles D1118 & D205 Parakanapa Rd
14271 | 05/03/2012 | 2011 | 2012-03-05 | 1272 | 186 | 53556 | C | ADVERSE WEATHER | Repair 11kV lines poles W8893 & W7680 Kinikini Mahia
14272 | 06/03/2012 | 2011 | 2012-03-06 | 112 | 56 | 6272 | C | DEFECTIVE EQUIPMENT | Temp replace Xarm on pole E793 Whatatutu
14273 | 06/03/2012 | 2011 | 2012-03-06 | 42 | 153 | 6426 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W20694 Kaiwatai Rd Mahia
14274 | 06/03/2012 | 2011 | 2012-03-06 | 62 | 90 | 5580 | C | TREE CONTACTS | Repair 11kV lines pole W8005 Morere
14275 | 07/03/2012 | 2011 | 2012-03-07 | 41 | 27 | 1107 | C | ADVERSE WEATHER | Rejoin jumpers poles G2138 & G2149 after 5 poles replaced Paroa Rd
14311 | 07/03/2012 | 2011 | 2012-03-07 | 228 | 124 | 28272 | B | PLANNED SHUTDOWN | Replace 11kV SW/GR B808 McLean St
14276 | 08/03/2012 | 2011 | 2012-03-08 | 5 | 208 | 1040 | C | DEFECTIVE EQUIPMENT | Temp prop broken 11kV pole J933 SH35 Tikitiki Feeder
14277 | 08/03/2012 | 2011 | 2012-03-08 | 228 | 837 | 53448 | C | DEFECTIVE EQUIPMENT | Clean cable terminations on O/S C714 & C713 Bck Ormond Rd
14278 | 08/03/2012 | 2011 | 2012-03-08 | 283 | 95 | 20091 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J4073 Waikohu Stn Hicks Bay
14279 | 09/03/2012 | 2011 | 2012-03-09 | 23 | 184 | 4232 | C | DEFECTIVE EQUIPMENT | Temp prop 11kV pole J933 Tikitiki Township
14280 | 09/03/2012 | 2011 | 2012-03-09 | 176 | 87 | 7920 | C | ADVERSE WEATHER | Repair 11kV lines poles & poles J533 Hicks Bay
14281 | 09/03/2012 | 2011 | 2012-03-09 | 112 | 105 | 11760 | C | DEFECTIVE EQUIPMENT | Replace pole J4073 & rejoin jumpers poles J4074 & J4071 Hicks Bay
14282 | 09/03/2012 | 2011 | 2012-03-09 | 76 | 11 | 836 | C | DEFECTIVE EQUIPMENT | Replace 2 faulty DDO fuse bases T/x F87 Whakarau Rd
14313 | 09/03/2012 | 2011 | 2012-03-09 | 109 | 32 | 3488 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting C5144 Bushmere Rd
14283 | 11/03/2012 | 2011 | 2012-03-11 | 138 | 953 | 48750 | C | ADVERSE WEATHER | Repair 11kV lines pole A2378 Wairere Rd
14284 | 11/03/2012 | 2011 | 2012-03-11 | 248 | 12 | 2976 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole G594 Waimata Valley Rd
14285 | 12/03/2012 | 2011 | 2012-03-12 | 35 | 837 | 19327 | C | UNKNOWN | Reclose CB C95 Haisman Rd at Makaraka Sub cause unknown
14322 | 12/03/2012 | 2011 | 2012-03-12 | 39 | 20 | 780 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers pole D2683 Pehiri Rd
14314 | 13/03/2012 | 2011 | 2012-03-13 | 462 | 109 | 24978 | B | PLANNED SHUTDOWN | Replace 11kV poles D489 D499 D2962 Wharekopae Rd
14324 | 13/03/2012 | 2011 | 2012-03-13 | 530 | 50 | 26500 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Waikura Valley Rd J129
14315 | 14/03/2012 | 2011 | 2012-03-14 | 514 | 145 | 35175 | B | PLANNED SHUTDOWN | Install ABS on pole D2784 & Replace pole D117 Wharekopae Rd
14320 | 14/03/2012 | 2011 | 2012-03-14 | 366 | 29 | 25576 | B | PLANNED SHUTDOWN | Replace 11kV poles beyond E188 Mangamaia Rd
14286 | 15/03/2012 | 2011 | 2012-03-15 | 418 | 50 | 20900 | C | TREE CONTACTS | Isolate 11kV lines for tree cutting J129 Waikura Valley
14307 | 15/03/2012 | 2011 | 2012-03-15 | 387 | 47 | 18189 | B | PLANNED SHUTDOWN | Reconductor Lines H1865 J622 SH 35 Ruatoria South
14317 | 15/03/2012 | 2011 | 2012-03-15 | 270 | 10 | 940 | B | PLANNED SHUTDOWN | Cut & rejoin jumpers poles W8394 Mungatoto Stn Morere
14287 | 16/03/2012 | 2011 | 2012-03-16 | 15 | 47 | 705 | C | DEFECTIVE EQUIPMENT | Rejoin cable jumpers pole J4873 Makarika
14312 | 16/03/2012 | 2011 | 2012-03-16 | 360 | 37 | 13320 | B | PLANNED SHUTDOWN | Replace 11kV poles H1722 H1721 H1718 H1717 Makarika Rd
14316 | 16/03/2012 | 2011 | 2012-03-16 | 15 | 218 | 6229 | B | PLANNED SHUTDOWN | Replace O/SW to Gas Switch B251 Stout St
14306 | 18/03/2012 | 2011 | 2012-03-18 | 317 | 384 | 37318 | B | PLANNED SHUTDOWN | Replace ABS B90 Stout St
14288 | 19/03/2012 | 2011 | 2012-03-19 | 47 | 711 | 26607 | C | ADVERSE WEATHER | Reclose CB C96 Bushmere Rd at Makaraka Sub High Winds
14289 | 19/03/2012 | 2011 | 2012-03-19 | 11 | 711 | 7821 | C | ADVERSE WEATHER | Reclose CB C96 Bushmere Rd at Makaraka Sub cause unknown
14318 | 19/03/2012 | 2011 | 2012-03-19 | 117 | 11 | 1287 | B | PLANNED SHUTDOWN | Install DDO fuse on pole D4100 Russell Rd Ngatapa
14290 | 20/03/2012 | 2011 | 2012-03-20 | 302 | 124 | 19360 | C | ADVERSE WEATHER | Reclose CB F409 Te Karaka at Puha Sub cause High Winds
14291 | 20/03/2012 | 2011 | 2012-03-20 | 136 | 131 | 8272 | B | PLANNED SHUTDOWN | Remove tree branch from 11kV at pole W7554 Te Reinga
14292 | 20/03/2012 | 2011 | 2012-03-20 | 212 | 319 | 12862 | C | TREE CONTACTS | Repair 11kV lines pole J1274 Ruatoria
14293 | 20/03/2012 | 2011 | 2012-03-20 | 424 | 227 | 58337 | C | TREE CONTACTS | Repair 11kV lines pole E2118 Matawai Rd
14294 | 20/03/2012 | 2011 | 2012-03-20 | 38 | 370 | 10550 | C | TREE CONTACTS | Remove branch from 11kV lines pole W6203 Cricklewood Rd
14295 | 20/03/2012 | 2011 | 2012-03-20 | 1337 | 171 | 25029 | C | DEFECTIVE EQUIPMENT | Replace Xarm pole W5602 & cut jumpers pole W5619 Kahangungu
14296 | 20/03/2012 | 2011 | 2012-03-20 | 96 | 4 | 384 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W6288 Cricklewood Rd
14297 | 20/03/2012 | 2011 | 2012-03-20 | 99 | 353 | 23001 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole J556 SH35 Ruatoria
14298 | 20/03/2012 | 2011 | 2012-03-20 | 603 | 132 | 45506 | C | ADVERSE WEATHER | Replace 2 11kV poles F3430 & F3431 Te Karaka North
14299 | 21/03/2012 | 2011 | 2012-03-21 | 199 | 10 | 1990 | C | TREE CONTACTS | Repair 11kv lines pole J1278 Ruatoria
14300 | 21/03/2012 | 2011 | 2012-03-21 | 337 | 6 | 2022 | C | TREE CONTACTS | Repair 11kV lines pole C3142 Paratu Rd Whareratas
14301 | 21/03/2012 | 2011 | 2012-03-21 | 14 | 264 | 3015 | C | ADVERSE WEATHER | Repair 11kV lines pole W8374 Morere
14302 | 21/03/2012 | 2011 | 2012-03-21 | 101 | 75 | 3325 | C | TREE CONTACTS | Remove tree from 11kV lines pole H1062 Huarua Stn Mata Rd
14319 | 21/03/2012 | 2011 | 2012-03-21 | 366 | 39 | 14274 | B | PLANNED SHUTDOWN | Replace ABS D491 & poles Taumata Rd
14303 | 22/03/2012 | 2011 | 2012-03-22 | 432 | 153 | 41121 | C | TREE CONTACTS | Repair 11kV lines pole G2019 Tauwhareparae Rd
14321 | 23/03/2012 | 2011 | 2012-03-23 | 573 | 296 | 79929 | B | PLANNED SHUTDOWN | Replace 11kV SW/GR A382 Oneroa Rd Wainui
14308 | 25/03/2012 | 2011 | 2012-03-25 | 240 | 8 | 660 | B | PLANNED SHUTDOWN | Replace SW/GR B614 Lowe St
14323 | 27/03/2012 | 2011 | 2012-03-27 | 487 | 23 | 15379 | B | PLANNED SHUTDOWN | Replace 11kV poles E1846 E1848 E2007 E1849 Te Karaka
14325 | 28/03/2012 | 2011 | 2012-03-28 | 175 | 44 | 7700 | B | PLANNED SHUTDOWN | Isolate 11kV lines at C550 for tree cutting Papatu Rd
14326 | 28/03/2012 | 2011 | 2012-03-28 | 374 | 16 | 5984 | B | PLANNED SHUTDOWN | Replace ABS pole H123 Mata Rd
14328 | 28/03/2012 | 2011 | 2012-03-28 | 130 | 5 | 650 | B | PLANNED SHUTDOWN | Isolate 11kV line ABS W1014 Woodgreen Stn Raupunga
14304 | 29/03/2012 | 2011 | 2012-03-29 | 45 | 5 | 225 | C | DEFECTIVE EQUIPMENT | Replace 11kV DDO fuse T/x J243 Haig Rd Tikitiki
14305 | 29/03/2012 | 2011 | 2012-03-29 | 390 | 30 | 11700 | B | PLANNED SHUTDOWN | Replace 11kV poles D3613 D3642 D3601 Ruakaka Rd Tiniroto
14327 | 29/03/2012 | 2011 | 2012-03-29 | 15 | 53 | 954 | B | PLANNED SHUTDOWN | Replace O/SW A200 to Gas Switch Alice St Kaiti
14329 | 30/03/2012 | 2011 | 2012-03-30 | 355 | 74 | 26270 | B | PLANNED SHUTDOWN | Replace 11kV poles F1903 F1010 & relocate F1911 Te Wera Rd Matawai

## 20112012DailyTotals
Date Outage | YEAR | Duration of Outage | Customers Impacted | Total Customer Minutes Lost
02/04/2011 | 2011 | 88 | 737 | 32994
03/04/2011 | 2011 | 117 | 30 | 3510
04/04/2011 | 2011 | 60 | 58 | 3480
05/04/2011 | 2011 | 405 | 30 | 12150
06/04/2011 | 2011 | 226 | 17 | 3842
07/04/2011 | 2011 | 365 | 2865 | 122484
08/04/2011 | 2011 | 337 | 87 | 25900
11/04/2011 | 2011 | 7 | 944 | 6608
12/04/2011 | 2011 | 410 | 38 | 20491
13/04/2011 | 2011 | 408 | 14 | 5712
14/04/2011 | 2011 | 126 | 750 | 22636
18/04/2011 | 2011 | 22 | 48 | 1056
19/04/2011 | 2011 | 463 | 97 | 43039
20/04/2011 | 2011 | 405 | 30 | 12150
26/04/2011 | 2011 | 2904 | 1557 | 664163
27/04/2011 | 2011 | 1550 | 904 | 160450
28/04/2011 | 2011 | 1275 | 562 | 77330
29/04/2011 | 2011 | 451 | 229 | 20746
30/04/2011 | 2011 | 44 | 26 | 1144
01/05/2011 | 2011 | 147 | 1383 | 52640
02/05/2011 | 2011 | 133 | 605 | 60761
03/05/2011 | 2011 | 357 | 281 | 32185
04/05/2011 | 2011 | 426 | 75 | 42023
05/05/2011 | 2011 | 351 | 253 | 20371
09/05/2011 | 2011 | 218 | 229 | 22753
10/05/2011 | 2011 | 390 | 9 | 3519
11/05/2011 | 2011 | 41 | 12 | 684
12/05/2011 | 2011 | 256 | 153 | 24588
13/05/2011 | 2011 | 405 | 22 | 8910
14/05/2011 | 2011 | 125 | 19 | 2375
16/05/2011 | 2011 | 372 | 1197 | 79730
17/05/2011 | 2011 | 1732 | 668 | 104152
19/05/2011 | 2011 | 397 | 202 | 50845
20/05/2011 | 2011 | 320 | 75 | 24000
22/05/2011 | 2011 | 10 | 3 | 120
23/05/2011 | 2011 | 287 | 67 | 15965
24/05/2011 | 2011 | 373 | 155 | 5569
25/05/2011 | 2011 | 40 | 156 | 6820
26/05/2011 | 2011 | 841 | 1288 | 309670
27/05/2011 | 2011 | 92 | 199 | 16917
31/05/2011 | 2011 | 385 | 251 | 21752
01/06/2011 | 2011 | 306 | 36 | 11016
02/06/2011 | 2011 | 916 | 673 | 90025
05/06/2011 | 2011 | 59 | 1283 | 76744
06/06/2011 | 2011 | 45 | 23 | 1035
08/06/2011 | 2011 | 242 | 56 | 4052
09/06/2011 | 2011 | 123 | 117 | 6945
10/06/2011 | 2011 | 119 | 6 | 714
11/06/2011 | 2011 | 391 | 12 | 2172
12/06/2011 | 2011 | 144 | 974 | 13536
14/06/2011 | 2011 | 367 | 25 | 18325
17/06/2011 | 2011 | 139 | 17 | 2363
22/06/2011 | 2011 | 427 | 75 | 10372
23/06/2011 | 2011 | 409 | 170 | 30506
24/06/2011 | 2011 | 418 | 205 | 36451
26/06/2011 | 2011 | 500 | 543 | 79401
27/06/2011 | 2011 | 310 | 18 | 3546
29/06/2011 | 2011 | 338 | 280 | 13692
30/06/2011 | 2011 | 384 | 271 | 31571
01/07/2011 | 2011 | 308 | 155 | 20440
04/07/2011 | 2011 | 92 | 20 | 1840
05/07/2011 | 2011 | 225 | 92 | 9899
07/07/2011 | 2011 | 203 | 261 | 28728
08/07/2011 | 2011 | 175 | 326 | 13168
09/07/2011 | 2011 | 754 | 970 | 96260
10/07/2011 | 2011 | 1703 | 1296 | 315841
11/07/2011 | 2011 | 767 | 257 | 51651
12/07/2011 | 2011 | 118 | 125 | 9897
13/07/2011 | 2011 | 133 | 173 | 16077
14/07/2011 | 2011 | 117 | 56 | 6552
15/07/2011 | 2011 | 82 | 98 | 5961
17/07/2011 | 2011 | 87 | 432 | 16721
18/07/2011 | 2011 | 351 | 299 | 43079
19/07/2011 | 2011 | 70 | 59 | 4130
21/07/2011 | 2011 | 405 | 237 | 14173
22/07/2011 | 2011 | 31 | 5499 | 114020
23/07/2011 | 2011 | 846 | 95 | 15539
24/07/2011 | 2011 | 3304 | 48 | 51680
25/07/2011 | 2011 | 105 | 130 | 12441
27/07/2011 | 2011 | 30 | 11 | 594
28/07/2011 | 2011 | 394 | 42 | 16482
29/07/2011 | 2011 | 399 | 103 | 27516
30/07/2011 | 2011 | 81 | 61 | 7087
01/08/2011 | 2011 | 300 | 1041 | 58122
02/08/2011 | 2011 | 366 | 176 | 37877
04/08/2011 | 2011 | 510 | 37 | 7586
05/08/2011 | 2011 | 373 | 133 | 19019
06/08/2011 | 2011 | 404 | 23 | 9292
07/08/2011 | 2011 | 880 | 288 | 51600
08/08/2011 | 2011 | 300 | 26 | 7800
10/08/2011 | 2011 | 418 | 24 | 58028
11/08/2011 | 2011 | 525 | 137 | 13615
12/08/2011 | 2011 | 370 | 201 | 43040
14/08/2011 | 2011 | 176 | 240 | 8370
15/08/2011 | 2011 | 648 | 131 | 5184
17/08/2011 | 2011 | 1325 | 645 | 113937
18/08/2011 | 2011 | 897 | 92 | 32226
19/08/2011 | 2011 | 387 | 92 | 10108
23/08/2011 | 2011 | 388 | 71 | 15388
24/08/2011 | 2011 | 396 | 75 | 47743
25/08/2011 | 2011 | 335 | 473 | 48628
26/08/2011 | 2011 | 191 | 91 | 5215
31/08/2011 | 2011 | 380 | 125 | 29075
01/09/2011 | 2011 | 424 | 102 | 31496
02/09/2011 | 2011 | 239 | 85 | 20315
05/09/2011 | 2011 | 414 | 65 | 25140
07/09/2011 | 2011 | 1589 | 183 | 45574
08/09/2011 | 2011 | 412 | 279 | 78387
09/09/2011 | 2011 | 175 | 18 | 3150
12/09/2011 | 2011 | 823 | 177 | 28380
13/09/2011 | 2011 | 31 | 11 | 308
14/09/2011 | 2011 | 298 | 687 | 64596
15/09/2011 | 2011 | 390 | 136 | 19986
16/09/2011 | 2011 | 234 | 35 | 8190
18/09/2011 | 2011 | 112 | 687 | 20056
19/09/2011 | 2011 | 245 | 1544 | 56493
20/09/2011 | 2011 | 455 | 13 | 5915
21/09/2011 | 2011 | 60 | 38 | 3065
22/09/2011 | 2011 | 379 | 258 | 23613
23/09/2011 | 2011 | 110 | 116 | 8088
27/09/2011 | 2011 | 402 | 753 | 55288
28/09/2011 | 2011 | 386 | 175 | 21294
29/09/2011 | 2011 | 371 | 176 | 34210
30/09/2011 | 2011 | 339 | 35 | 4785
01/10/2011 | 2011 | 265 | 187 | 23081
03/10/2011 | 2011 | 59 | 456 | 5154
04/10/2011 | 2011 | 126 | 232 | 10321
05/10/2011 | 2011 | 575 | 131 | 33005
06/10/2011 | 2011 | 50 | 25 | 1250
07/10/2011 | 2011 | 361 | 7 | 2527
10/10/2011 | 2011 | 433 | 75 | 19068
11/10/2011 | 2011 | 97 | 143 | 10697
12/10/2011 | 2011 | 499 | 586 | 110504
13/10/2011 | 2011 | 326 | 380 | 54409
14/10/2011 | 2011 | 131 | 111 | 11180
17/10/2011 | 2011 | 296 | 184 | 54464
18/10/2011 | 2011 | 431 | 179 | 66361
19/10/2011 | 2011 | 238 | 206 | 39713
20/10/2011 | 2011 | 350 | 67 | 23450
21/10/2011 | 2011 | 338 | 237 | 54289
23/10/2011 | 2011 | 377 | 195 | 31178
26/10/2011 | 2011 | 437 | 95 | 6955
27/10/2011 | 2011 | 65 | 27 | 1755
28/10/2011 | 2011 | 326 | 137 | 44662
30/10/2011 | 2011 | 1263 | 798 | 92553
01/11/2011 | 2011 | 480 | 1288 | 379468
02/11/2011 | 2011 | 547 | 54 | 59972
08/11/2011 | 2011 | 400 | 33 | 13200
09/11/2011 | 2011 | 498 | 35 | 13500
10/11/2011 | 2011 | 1277 | 1075 | 152845
11/11/2011 | 2011 | 1655 | 858 | 74617
15/11/2011 | 2011 | 25 | 42 | 945
18/11/2011 | 2011 | 221 | 693 | 24232
19/11/2011 | 2011 | 63 | 36 | 2268
20/11/2011 | 2011 | 30 | 2528 | 75840
21/11/2011 | 2011 | 577 | 1403 | 276327
22/11/2011 | 2011 | 486 | 59 | 27365
23/11/2011 | 2011 | 376 | 252 | 51658
24/11/2011 | 2011 | 567 | 68 | 16226
25/11/2011 | 2011 | 333 | 76 | 4598
26/11/2011 | 2011 | 81 | 47 | 3807
28/11/2011 | 2011 | 275 | 202 | 42158
30/11/2011 | 2011 | 30 | 6 | 180
01/12/2011 | 2011 | 377 | 66 | 21040
02/12/2011 | 2011 | 306 | 118 | 36020
04/12/2011 | 2011 | 154 | 53 | 7832
05/12/2011 | 2011 | 393 | 42 | 42852
06/12/2011 | 2011 | 456 | 63 | 17971
07/12/2011 | 2011 | 276 | 32 | 12672
08/12/2011 | 2011 | 399 | 135 | 50888
09/12/2011 | 2011 | 480 | 80 | 11266
12/12/2011 | 2011 | 132 | 392 | 44369
13/12/2011 | 2011 | 396 | 158 | 33527
14/12/2011 | 2011 | 303 | 145 | 7851
15/12/2011 | 2011 | 401 | 61 | 4319
16/12/2011 | 2011 | 542 | 583 | 24504
19/12/2011 | 2011 | 260 | 25 | 2027
20/12/2011 | 2011 | 245 | 75 | 18375
21/12/2011 | 2011 | 400 | 1400 | 92700
22/12/2011 | 2011 | 360 | 154 | 6795
23/12/2011 | 2011 | 16 | 208 | 3328
02/01/2012 | 2011 | 109 | 724 | 18184
08/01/2012 | 2011 | 948 | 709 | 171379
10/01/2012 | 2011 | 327 | 673 | 42310
12/01/2012 | 2011 | 352 | 25 | 2985
13/01/2012 | 2011 | 460 | 1210 | 93264
14/01/2012 | 2011 | 670 | 273 | 76150
16/01/2012 | 2011 | 355 | 5548 | 32589
17/01/2012 | 2011 | 408 | 760 | 39593
19/01/2012 | 2011 | 370 | 19 | 7030
20/01/2012 | 2011 | 387 | 49 | 18963
21/01/2012 | 2011 | 126 | 170 | 9991
23/01/2012 | 2011 | 410 | 223 | 15500
25/01/2012 | 2011 | 239 | 192 | 43916
26/01/2012 | 2011 | 384 | 193 | 30358
28/01/2012 | 2011 | 173 | 61 | 3892
01/02/2012 | 2011 | 358 | 51 | 10013
02/02/2012 | 2011 | 328 | 74 | 17900
03/02/2012 | 2011 | 32 | 265 | 15092
08/02/2012 | 2011 | 234 | 25 | 4230
09/02/2012 | 2011 | 345 | 5 | 1725
10/02/2012 | 2011 | 388 | 10 | 3880
12/02/2012 | 2011 | 354 | 280 | 47637
13/02/2012 | 2011 | 18 | 114 | 3762
14/02/2012 | 2011 | 241 | 1170 | 25695
15/02/2012 | 2011 | 814 | 202 | 52128
17/02/2012 | 2011 | 296 | 11 | 3256
20/02/2012 | 2011 | 790 | 31 | 8065
21/02/2012 | 2011 | 365 | 11 | 4015
22/02/2012 | 2011 | 74 | 16 | 1184
23/02/2012 | 2011 | 726 | 765 | 80132
24/02/2012 | 2011 | 1402 | 421 | 189244
25/02/2012 | 2011 | 285 | 470 | 49977
27/02/2012 | 2011 | 606 | 101 | 26526
29/02/2012 | 2011 | 401 | 29 | 63191
01/03/2012 | 2011 | 1166 | 322 | 169686
02/03/2012 | 2011 | 367 | 1117 | 37715
03/03/2012 | 2011 | 1526 | 2277 | 576476
04/03/2012 | 2011 | 1623 | 342 | 140869
05/03/2012 | 2011 | 1272 | 242 | 58148
06/03/2012 | 2011 | 112 | 299 | 18278
07/03/2012 | 2011 | 228 | 151 | 29379
08/03/2012 | 2011 | 283 | 1140 | 74579
09/03/2012 | 2011 | 176 | 419 | 28236
11/03/2012 | 2011 | 248 | 965 | 51726
12/03/2012 | 2011 | 39 | 857 | 20107
13/03/2012 | 2011 | 530 | 159 | 51478
14/03/2012 | 2011 | 514 | 174 | 60751
15/03/2012 | 2011 | 418 | 107 | 40029
16/03/2012 | 2011 | 360 | 302 | 20254
18/03/2012 | 2011 | 317 | 384 | 37318
19/03/2012 | 2011 | 117 | 1433 | 35715
20/03/2012 | 2011 | 1337 | 1831 | 203301
21/03/2012 | 2011 | 366 | 394 | 24626
22/03/2012 | 2011 | 432 | 153 | 41121
23/03/2012 | 2011 | 573 | 296 | 79929
25/03/2012 | 2011 | 240 | 8 | 660
27/03/2012 | 2011 | 487 | 23 | 15379
28/03/2012 | 2011 | 374 | 65 | 14334
29/03/2012 | 2011 | 390 | 88 | 12879
30/03/2012 | 2011 | 355 | 74 | 26270

## 20112012NormalisedDailyTotals
Date Outage | Year | TotAVG | Customers Impacted | Total Customer Minutes Lost | Saidi | Safi
01/02/2012 | 2011 | 25540 | 51 | 10013 | 0.39205 | 0.0019969
01/03/2012 | 2011 | 25540 | 322 | 169686 | 6.6439 | 0.012608
01/05/2011 | 2011 | 25540 | 1383 | 52640 | 2.0611 | 0.05415
01/06/2011 | 2011 | 25540 | 36 | 11016 | 0.43132 | 0.0014096
01/07/2011 | 2011 | 25540 | 155 | 20440 | 0.80031 | 0.0060689
01/08/2011 | 2011 | 25540 | 1041 | 58122 | 2.2757 | 0.04076
01/09/2011 | 2011 | 25540 | 102 | 31496 | 1.2332 | 0.0039937
01/10/2011 | 2011 | 25540 | 187 | 23081 | 0.90372 | 0.0073218
01/11/2011 | 2011 | 25540 | 1288 | 379468 | 14.8578 | 0.050431
01/12/2011 | 2011 | 25540 | 66 | 21040 | 0.82381 | 0.0025842
02/01/2012 | 2011 | 25540 | 724 | 18184 | 0.71198 | 0.028348
02/02/2012 | 2011 | 25540 | 74 | 17900 | 0.70086 | 0.0028974
02/03/2012 | 2011 | 25540 | 1117 | 37715 | 1.4767 | 0.043735
02/04/2011 | 2011 | 25540 | 737 | 32994 | 1.2919 | 0.028857
02/05/2011 | 2011 | 25540 | 605 | 60761 | 2.3791 | 0.023688
02/06/2011 | 2011 | 25540 | 673 | 90025 | 3.5249 | 0.026351
02/08/2011 | 2011 | 25540 | 176 | 37877 | 1.483 | 0.0068912
02/09/2011 | 2011 | 25540 | 85 | 20315 | 0.79542 | 0.0033281
02/11/2011 | 2011 | 25540 | 54 | 59972 | 2.3482 | 0.0021143
02/12/2011 | 2011 | 25540 | 118 | 36020 | 1.4103 | 0.0046202
03/02/2012 | 2011 | 25540 | 265 | 15092 | 0.59092 | 0.010376
03/03/2012 | 2011 | 25540 | 2277 | 576476 | 22.5715 | 0.089154
03/04/2011 | 2011 | 25540 | 30 | 3510 | 0.13743 | 0.0011746
03/05/2011 | 2011 | 25540 | 281 | 32185 | 1.2602 | 0.011002
03/10/2011 | 2011 | 25540 | 456 | 5154 | 0.2018 | 0.017854
04/03/2012 | 2011 | 25540 | 342 | 140869 | 5.5156 | 0.013391
04/04/2011 | 2011 | 25540 | 58 | 3480 | 0.13626 | 0.0022709
04/05/2011 | 2011 | 25540 | 75 | 42023 | 1.6454 | 0.0029366
04/07/2011 | 2011 | 25540 | 20 | 1840 | 0.072044 | 0.00078309
04/08/2011 | 2011 | 25540 | 37 | 7586 | 0.29702 | 0.0014487
04/10/2011 | 2011 | 25540 | 232 | 10321 | 0.40411 | 0.0090838
04/12/2011 | 2011 | 25540 | 53 | 7832 | 0.30666 | 0.0020752
05/03/2012 | 2011 | 25540 | 242 | 58148 | 2.2767 | 0.0094753
05/04/2011 | 2011 | 25540 | 30 | 12150 | 0.47572 | 0.0011746
05/05/2011 | 2011 | 25540 | 253 | 20371 | 0.79761 | 0.009906
05/06/2011 | 2011 | 25540 | 1283 | 76744 | 3.0049 | 0.050235
05/07/2011 | 2011 | 25540 | 92 | 9899 | 0.38759 | 0.0036022
05/08/2011 | 2011 | 25540 | 133 | 19019 | 0.74468 | 0.0052075
05/09/2011 | 2011 | 25540 | 65 | 25140 | 0.98434 | 0.002545
05/10/2011 | 2011 | 25540 | 131 | 33005 | 1.2923 | 0.0051292
05/12/2011 | 2011 | 25540 | 42 | 42852 | 1.6778 | 0.0016445
06/03/2012 | 2011 | 25540 | 299 | 18278 | 0.71566 | 0.011707
06/04/2011 | 2011 | 25540 | 17 | 3842 | 0.15043 | 0.00066562
06/06/2011 | 2011 | 25540 | 23 | 1035 | 0.040525 | 0.00090055
06/08/2011 | 2011 | 25540 | 23 | 9292 | 0.36382 | 0.00090055
06/10/2011 | 2011 | 25540 | 25 | 1250 | 0.048943 | 0.00097886
06/12/2011 | 2011 | 25540 | 63 | 17971 | 0.70364 | 0.0024667
07/03/2012 | 2011 | 25540 | 151 | 29379 | 1.1503 | 0.0059123
07/04/2011 | 2011 | 25540 | 2865 | 122484 | 4.7958 | 0.11218
07/07/2011 | 2011 | 25540 | 261 | 28728 | 1.1248 | 0.010219
07/08/2011 | 2011 | 25540 | 288 | 51600 | 2.0204 | 0.011276
07/09/2011 | 2011 | 25540 | 183 | 45574 | 1.7844 | 0.0071652
07/10/2011 | 2011 | 25540 | 7 | 2527 | 0.098943 | 0.00027408
07/12/2011 | 2011 | 25540 | 32 | 12672 | 0.49616 | 0.0012529
08/01/2012 | 2011 | 25540 | 709 | 171379 | 6.7102 | 0.02776
08/02/2012 | 2011 | 25540 | 25 | 4230 | 0.16562 | 0.00097886
08/03/2012 | 2011 | 25540 | 1140 | 74579 | 2.9201 | 0.044636
08/04/2011 | 2011 | 25540 | 87 | 25900 | 1.0141 | 0.0034064
08/06/2011 | 2011 | 25540 | 56 | 4052 | 0.15865 | 0.0021926
08/07/2011 | 2011 | 25540 | 326 | 13168 | 0.51558 | 0.012764
08/08/2011 | 2011 | 25540 | 26 | 7800 | 0.3054 | 0.001018
08/09/2011 | 2011 | 25540 | 279 | 78387 | 3.0692 | 0.010924
08/11/2011 | 2011 | 25540 | 33 | 13200 | 0.51684 | 0.0012921
08/12/2011 | 2011 | 25540 | 135 | 50888 | 1.9925 | 0.0052858
09/02/2012 | 2011 | 25540 | 5 | 1725 | 0.067541 | 0.00019577
09/03/2012 | 2011 | 25540 | 419 | 28236 | 1.1056 | 0.016406
09/05/2011 | 2011 | 25540 | 229 | 22753 | 0.89088 | 0.0089663
09/06/2011 | 2011 | 25540 | 117 | 6945 | 0.27193 | 0.004581
09/07/2011 | 2011 | 25540 | 970 | 96260 | 3.769 | 0.03798
09/09/2011 | 2011 | 25540 | 18 | 3150 | 0.12334 | 0.00070478
09/11/2011 | 2011 | 25540 | 35 | 13500 | 0.52858 | 0.0013704
09/12/2011 | 2011 | 25540 | 80 | 11266 | 0.44111 | 0.0031323
10/01/2012 | 2011 | 25540 | 673 | 42310 | 1.6566 | 0.026351
10/02/2012 | 2011 | 25540 | 10 | 3880 | 0.15192 | 0.00039154
10/05/2011 | 2011 | 25540 | 9 | 3519 | 0.13778 | 0.00035239
10/06/2011 | 2011 | 25540 | 6 | 714 | 0.027956 | 0.00023493
10/07/2011 | 2011 | 25540 | 1296 | 315841 | 12.3665 | 0.050744
10/08/2011 | 2011 | 25540 | 24 | 58028 | 2.272 | 0.0009397
10/10/2011 | 2011 | 25540 | 75 | 19068 | 0.74659 | 0.0029366
10/11/2011 | 2011 | 25540 | 1075 | 152845 | 5.9845 | 0.042091
11/03/2012 | 2011 | 25540 | 965 | 51726 | 2.0253 | 0.037784
11/04/2011 | 2011 | 25540 | 944 | 6608 | 0.25873 | 0.036962
11/05/2011 | 2011 | 25540 | 12 | 684 | 0.026782 | 0.00046985
11/06/2011 | 2011 | 25540 | 12 | 2172 | 0.085043 | 0.00046985
11/07/2011 | 2011 | 25540 | 257 | 51651 | 2.0224 | 0.010063
11/08/2011 | 2011 | 25540 | 137 | 13615 | 0.53309 | 0.0053641
11/10/2011 | 2011 | 25540 | 143 | 10697 | 0.41883 | 0.0055991
11/11/2011 | 2011 | 25540 | 858 | 74617 | 2.9216 | 0.033594
12/01/2012 | 2011 | 25540 | 25 | 2985 | 0.11688 | 0.00097886
12/02/2012 | 2011 | 25540 | 280 | 47637 | 1.8652 | 0.010963
12/03/2012 | 2011 | 25540 | 857 | 20107 | 0.78727 | 0.033555
12/04/2011 | 2011 | 25540 | 38 | 20491 | 0.80231 | 0.0014879
12/05/2011 | 2011 | 25540 | 153 | 24588 | 0.96273 | 0.0059906
12/06/2011 | 2011 | 25540 | 974 | 13536 | 0.52999 | 0.038136
12/07/2011 | 2011 | 25540 | 125 | 9897 | 0.38751 | 0.0048943
12/08/2011 | 2011 | 25540 | 201 | 43040 | 1.6852 | 0.00787
12/09/2011 | 2011 | 25540 | 177 | 28380 | 1.1112 | 0.0069303
12/10/2011 | 2011 | 25540 | 586 | 110504 | 4.3267 | 0.022944
12/12/2011 | 2011 | 25540 | 392 | 44369 | 1.7372 | 0.015348
13/01/2012 | 2011 | 25540 | 1210 | 93264 | 3.6517 | 0.047377
13/02/2012 | 2011 | 25540 | 114 | 3762 | 0.1473 | 0.0044636
13/03/2012 | 2011 | 25540 | 159 | 51478 | 2.0156 | 0.0062255
13/04/2011 | 2011 | 25540 | 14 | 5712 | 0.22365 | 0.00054816
13/05/2011 | 2011 | 25540 | 22 | 8910 | 0.34886 | 0.00086139
13/07/2011 | 2011 | 25540 | 173 | 16077 | 0.62948 | 0.0067737
13/09/2011 | 2011 | 25540 | 11 | 308 | 0.01206 | 0.0004307
13/10/2011 | 2011 | 25540 | 380 | 54409 | 2.1303 | 0.014879
13/12/2011 | 2011 | 25540 | 158 | 33527 | 1.3127 | 0.0061864
14/01/2012 | 2011 | 25540 | 273 | 76150 | 2.9816 | 0.010689
14/02/2012 | 2011 | 25540 | 1170 | 25695 | 1.0061 | 0.04581
14/03/2012 | 2011 | 25540 | 174 | 60751 | 2.3787 | 0.0068128
14/04/2011 | 2011 | 25540 | 750 | 22636 | 0.8863 | 0.029366
14/05/2011 | 2011 | 25540 | 19 | 2375 | 0.092991 | 0.00074393
14/06/2011 | 2011 | 25540 | 25 | 18325 | 0.7175 | 0.00097886
14/07/2011 | 2011 | 25540 | 56 | 6552 | 0.25654 | 0.0021926
14/08/2011 | 2011 | 25540 | 240 | 8370 | 0.32772 | 0.009397
14/09/2011 | 2011 | 25540 | 687 | 64596 | 2.5292 | 0.026899
14/10/2011 | 2011 | 25540 | 111 | 11180 | 0.43774 | 0.0043461
14/12/2011 | 2011 | 25540 | 145 | 7851 | 0.3074 | 0.0056774
15/02/2012 | 2011 | 25540 | 202 | 52128 | 2.041 | 0.0079092
15/03/2012 | 2011 | 25540 | 107 | 40029 | 1.5673 | 0.0041895
15/07/2011 | 2011 | 25540 | 98 | 5961 | 0.2334 | 0.0038371
15/08/2011 | 2011 | 25540 | 131 | 5184 | 0.20298 | 0.0051292
15/09/2011 | 2011 | 25540 | 136 | 19986 | 0.78254 | 0.005325
15/11/2011 | 2011 | 25540 | 42 | 945 | 0.037001 | 0.0016445
15/12/2011 | 2011 | 25540 | 61 | 4319 | 0.16911 | 0.0023884
16/01/2012 | 2011 | 25540 | 5548 | 32589 | 1.276 | 0.21723
16/03/2012 | 2011 | 25540 | 302 | 20254 | 0.79303 | 0.011825
16/05/2011 | 2011 | 25540 | 1197 | 79730 | 3.1218 | 0.046868
16/09/2011 | 2011 | 25540 | 35 | 8190 | 0.32067 | 0.0013704
16/12/2011 | 2011 | 25540 | 583 | 24504 | 0.95944 | 0.022827
17/01/2012 | 2011 | 25540 | 760 | 39593 | 1.5502 | 0.029757
17/02/2012 | 2011 | 25540 | 11 | 3256 | 0.12749 | 0.0004307
17/05/2011 | 2011 | 25540 | 668 | 104152 | 4.078 | 0.026155
17/06/2011 | 2011 | 25540 | 17 | 2363 | 0.092522 | 0.00066562
17/07/2011 | 2011 | 25540 | 432 | 16721 | 0.6547 | 0.016915
17/08/2011 | 2011 | 25540 | 645 | 113937 | 4.4611 | 0.025255
17/10/2011 | 2011 | 25540 | 184 | 54464 | 2.1325 | 0.0072044
18/03/2012 | 2011 | 25540 | 384 | 37318 | 1.4612 | 0.015035
18/04/2011 | 2011 | 25540 | 48 | 1056 | 0.041347 | 0.0018794
18/07/2011 | 2011 | 25540 | 299 | 43079 | 1.6867 | 0.011707
18/08/2011 | 2011 | 25540 | 92 | 32226 | 1.2618 | 0.0036022
18/09/2011 | 2011 | 25540 | 687 | 20056 | 0.78528 | 0.026899
18/10/2011 | 2011 | 25540 | 179 | 66361 | 2.5983 | 0.0070086
18/11/2011 | 2011 | 25540 | 693 | 24232 | 0.94879 | 0.027134
19/01/2012 | 2011 | 25540 | 19 | 7030 | 0.27525 | 0.00074393
19/03/2012 | 2011 | 25540 | 1433 | 35715 | 1.3984 | 0.056108
19/04/2011 | 2011 | 25540 | 97 | 43039 | 1.6852 | 0.003798
19/05/2011 | 2011 | 25540 | 202 | 50845 | 1.9908 | 0.0079092
19/07/2011 | 2011 | 25540 | 59 | 4130 | 0.16171 | 0.0023101
19/08/2011 | 2011 | 25540 | 92 | 10108 | 0.39577 | 0.0036022
19/09/2011 | 2011 | 25540 | 1544 | 56493 | 2.2119 | 0.060454
19/10/2011 | 2011 | 25540 | 206 | 39713 | 1.5549 | 0.0080658
19/11/2011 | 2011 | 25540 | 36 | 2268 | 0.088802 | 0.0014096
19/12/2011 | 2011 | 25540 | 25 | 2027 | 0.079366 | 0.00097886
20/01/2012 | 2011 | 25540 | 49 | 18963 | 0.74248 | 0.0019186
20/02/2012 | 2011 | 25540 | 31 | 8065 | 0.31578 | 0.0012138
20/03/2012 | 2011 | 25540 | 1831 | 203301 | 7.9601 | 0.071691
20/04/2011 | 2011 | 25540 | 30 | 12150 | 0.47572 | 0.0011746
20/05/2011 | 2011 | 25540 | 75 | 24000 | 0.9397 | 0.0029366
20/09/2011 | 2011 | 25540 | 13 | 5915 | 0.2316 | 0.00050901
20/10/2011 | 2011 | 25540 | 67 | 23450 | 0.91817 | 0.0026233
20/11/2011 | 2011 | 25540 | 2528 | 75840 | 2.9695 | 0.098982
20/12/2011 | 2011 | 25540 | 75 | 18375 | 0.71946 | 0.0029366
21/01/2012 | 2011 | 25540 | 170 | 9991 | 0.39119 | 0.0066562
21/02/2012 | 2011 | 25540 | 11 | 4015 | 0.1572 | 0.0004307
21/03/2012 | 2011 | 25540 | 394 | 24626 | 0.96421 | 0.015427
21/07/2011 | 2011 | 25540 | 237 | 14173 | 0.55493 | 0.0092796
21/09/2011 | 2011 | 25540 | 38 | 3065 | 0.12001 | 0.0014879
21/10/2011 | 2011 | 25540 | 237 | 54289 | 2.1256 | 0.0092796
21/11/2011 | 2011 | 25540 | 1403 | 276327 | 10.8194 | 0.054933
21/12/2011 | 2011 | 25540 | 1400 | 92700 | 3.6296 | 0.054816
22/02/2012 | 2011 | 25540 | 16 | 1184 | 0.046359 | 0.00062647
22/03/2012 | 2011 | 25540 | 153 | 41121 | 1.6101 | 0.0059906
22/05/2011 | 2011 | 25540 | 3 | 120 | 0.0046985 | 0.00011746
22/06/2011 | 2011 | 25540 | 75 | 10372 | 0.40611 | 0.0029366
22/07/2011 | 2011 | 25540 | 5499 | 114020 | 4.4644 | 0.21531
22/09/2011 | 2011 | 25540 | 258 | 23613 | 0.92455 | 0.010102
22/11/2011 | 2011 | 25540 | 59 | 27365 | 1.0715 | 0.0023101
22/12/2011 | 2011 | 25540 | 154 | 6795 | 0.26605 | 0.0060298
23/01/2012 | 2011 | 25540 | 223 | 15500 | 0.60689 | 0.0087314
23/02/2012 | 2011 | 25540 | 765 | 80132 | 3.1375 | 0.029953
23/03/2012 | 2011 | 25540 | 296 | 79929 | 3.1296 | 0.01159
23/05/2011 | 2011 | 25540 | 67 | 15965 | 0.6251 | 0.0026233
23/06/2011 | 2011 | 25540 | 170 | 30506 | 1.1944 | 0.0066562
23/07/2011 | 2011 | 25540 | 95 | 15539 | 0.60842 | 0.0037197
23/08/2011 | 2011 | 25540 | 71 | 15388 | 0.60251 | 0.00278
23/09/2011 | 2011 | 25540 | 116 | 8088 | 0.31668 | 0.0045419
23/10/2011 | 2011 | 25540 | 195 | 31178 | 1.2208 | 0.0076351
23/11/2011 | 2011 | 25540 | 252 | 51658 | 2.0226 | 0.0098669
23/12/2011 | 2011 | 25540 | 208 | 3328 | 0.13031 | 0.0081441
24/02/2012 | 2011 | 25540 | 421 | 189244 | 7.4097 | 0.016484
24/05/2011 | 2011 | 25540 | 155 | 5569 | 0.21805 | 0.0060689
24/06/2011 | 2011 | 25540 | 205 | 36451 | 1.4272 | 0.0080266
24/07/2011 | 2011 | 25540 | 48 | 51680 | 2.0235 | 0.0018794
24/08/2011 | 2011 | 25540 | 75 | 47743 | 1.8693 | 0.0029366
24/11/2011 | 2011 | 25540 | 68 | 16226 | 0.63532 | 0.0026625
25/01/2012 | 2011 | 25540 | 192 | 43916 | 1.7195 | 0.0075176
25/02/2012 | 2011 | 25540 | 470 | 49977 | 1.9568 | 0.018403
25/03/2012 | 2011 | 25540 | 8 | 660 | 0.025842 | 0.00031323
25/05/2011 | 2011 | 25540 | 156 | 6820 | 0.26703 | 0.0061081
25/07/2011 | 2011 | 25540 | 130 | 12441 | 0.48712 | 0.0050901
25/08/2011 | 2011 | 25540 | 473 | 48628 | 1.904 | 0.01852
25/11/2011 | 2011 | 25540 | 76 | 4598 | 0.18003 | 0.0029757
26/01/2012 | 2011 | 25540 | 193 | 30358 | 1.1886 | 0.0075568
26/04/2011 | 2011 | 25540 | 1557 | 664163 | 26.0048 | 0.060963
26/05/2011 | 2011 | 25540 | 1288 | 309670 | 12.1249 | 0.050431
26/06/2011 | 2011 | 25540 | 543 | 79401 | 3.1089 | 0.021261
26/08/2011 | 2011 | 25540 | 91 | 5215 | 0.20419 | 0.003563
26/10/2011 | 2011 | 25540 | 95 | 6955 | 0.27232 | 0.0037197
26/11/2011 | 2011 | 25540 | 47 | 3807 | 0.14906 | 0.0018403
27/02/2012 | 2011 | 25540 | 101 | 26526 | 1.0386 | 0.0039546
27/03/2012 | 2011 | 25540 | 23 | 15379 | 0.60215 | 0.00090055
27/04/2011 | 2011 | 25540 | 904 | 160450 | 6.2823 | 0.035395
27/05/2011 | 2011 | 25540 | 199 | 16917 | 0.66237 | 0.0077917
27/06/2011 | 2011 | 25540 | 18 | 3546 | 0.13884 | 0.00070478
27/07/2011 | 2011 | 25540 | 11 | 594 | 0.023258 | 0.0004307
27/09/2011 | 2011 | 25540 | 753 | 55288 | 2.1648 | 0.029483
27/10/2011 | 2011 | 25540 | 27 | 1755 | 0.068716 | 0.0010572
28/01/2012 | 2011 | 25540 | 61 | 3892 | 0.15239 | 0.0023884
28/03/2012 | 2011 | 25540 | 65 | 14334 | 0.56124 | 0.002545
28/04/2011 | 2011 | 25540 | 562 | 77330 | 3.0278 | 0.022005
28/07/2011 | 2011 | 25540 | 42 | 16482 | 0.64534 | 0.0016445
28/09/2011 | 2011 | 25540 | 175 | 21294 | 0.83375 | 0.006852
28/10/2011 | 2011 | 25540 | 137 | 44662 | 1.7487 | 0.0053641
28/11/2011 | 2011 | 25540 | 202 | 42158 | 1.6507 | 0.0079092
29/02/2012 | 2011 | 25540 | 29 | 63191 | 2.4742 | 0.0011355
29/03/2012 | 2011 | 25540 | 88 | 12879 | 0.50427 | 0.0034456
29/04/2011 | 2011 | 25540 | 229 | 20746 | 0.81229 | 0.0089663
29/06/2011 | 2011 | 25540 | 280 | 13692 | 0.5361 | 0.010963
29/07/2011 | 2011 | 25540 | 103 | 27516 | 1.0774 | 0.0040329
29/09/2011 | 2011 | 25540 | 176 | 34210 | 1.3395 | 0.0068912
30/03/2012 | 2011 | 25540 | 74 | 26270 | 1.0286 | 0.0028974
30/04/2011 | 2011 | 25540 | 26 | 1144 | 0.044792 | 0.001018
30/06/2011 | 2011 | 25540 | 271 | 31571 | 1.2361 | 0.010611
30/07/2011 | 2011 | 25540 | 61 | 7087 | 0.27749 | 0.0023884
30/09/2011 | 2011 | 25540 | 35 | 4785 | 0.18735 | 0.0013704
30/10/2011 | 2011 | 25540 | 798 | 92553 | 3.6238 | 0.031245
30/11/2011 | 2011 | 25540 | 6 | 180 | 0.0070478 | 0.00023493
31/05/2011 | 2011 | 25540 | 251 | 21752 | 0.85168 | 0.0098277
31/08/2011 | 2011 | 25540 | 125 | 29075 | 1.1384 | 0.0048943

## 20112012FixedData
Date Outage | Saidi | Safi | FixedSaidi | FixedSaifi
01/02/2012 | 0.39205 | 0.0019969 | 0.39205 | 0.0019969
01/03/2012 | 6.6439 | 0.012608 | 6.6439 | 0.012608
01/05/2011 | 2.0611 | 0.05415 | 2.0611 | 0.05415
01/06/2011 | 0.43132 | 0.0014096 | 0.43132 | 0.0014096
01/07/2011 | 0.80031 | 0.0060689 | 0.80031 | 0.0060689
01/08/2011 | 2.2757 | 0.04076 | 2.2757 | 0.04076
01/09/2011 | 1.2332 | 0.0039937 | 1.2332 | 0.0039937
01/10/2011 | 0.90372 | 0.0073218 | 0.90372 | 0.0073218
01/11/2011 | 14.8578 | 0.050431 | 14.8578 | 0.050431
01/12/2011 | 0.82381 | 0.0025842 | 0.82381 | 0.0025842
02/01/2012 | 0.71198 | 0.028348 | 0.71198 | 0.028348
02/02/2012 | 0.70086 | 0.0028974 | 0.70086 | 0.0028974
02/03/2012 | 1.4767 | 0.043735 | 1.4767 | 0.043735
02/04/2011 | 1.2919 | 0.028857 | 1.2919 | 0.028857
02/05/2011 | 2.3791 | 0.023688 | 2.3791 | 0.023688
02/06/2011 | 3.5249 | 0.026351 | 3.5249 | 0.026351
02/08/2011 | 1.483 | 0.0068912 | 1.483 | 0.0068912
02/09/2011 | 0.79542 | 0.0033281 | 0.79542 | 0.0033281
02/11/2011 | 2.3482 | 0.0021143 | 2.3482 | 0.0021143
02/12/2011 | 1.4103 | 0.0046202 | 1.4103 | 0.0046202
03/02/2012 | 0.59092 | 0.010376 | 0.59092 | 0.010376
03/03/2012 | 22.5715 | 0.089154 | 22.5715 | 0.089154
03/04/2011 | 0.13743 | 0.0011746 | 0.13743 | 0.0011746
03/05/2011 | 1.2602 | 0.011002 | 1.2602 | 0.011002
03/10/2011 | 0.2018 | 0.017854 | 0.2018 | 0.017854
04/03/2012 | 5.5156 | 0.013391 | 5.5156 | 0.013391
04/04/2011 | 0.13626 | 0.0022709 | 0.13626 | 0.0022709
04/05/2011 | 1.6454 | 0.0029366 | 1.6454 | 0.0029366
04/07/2011 | 0.072044 | 0.00078309 | 0.072044 | 0.00078309
04/08/2011 | 0.29702 | 0.0014487 | 0.29702 | 0.0014487
04/10/2011 | 0.40411 | 0.0090838 | 0.40411 | 0.0090838
04/12/2011 | 0.30666 | 0.0020752 | 0.30666 | 0.0020752
05/03/2012 | 2.2767 | 0.0094753 | 2.2767 | 0.0094753
05/04/2011 | 0.47572 | 0.0011746 | 0.47572 | 0.0011746
05/05/2011 | 0.79761 | 0.009906 | 0.79761 | 0.009906
05/06/2011 | 3.0049 | 0.050235 | 3.0049 | 0.050235
05/07/2011 | 0.38759 | 0.0036022 | 0.38759 | 0.0036022
05/08/2011 | 0.74468 | 0.0052075 | 0.74468 | 0.0052075
05/09/2011 | 0.98434 | 0.002545 | 0.98434 | 0.002545
05/10/2011 | 1.2923 | 0.0051292 | 1.2923 | 0.0051292
05/12/2011 | 1.6778 | 0.0016445 | 1.6778 | 0.0016445
06/03/2012 | 0.71566 | 0.011707 | 0.71566 | 0.011707
06/04/2011 | 0.15043 | 0.00066562 | 0.15043 | 0.00066562
06/06/2011 | 0.040525 | 0.00090055 | 0.040525 | 0.00090055
06/08/2011 | 0.36382 | 0.00090055 | 0.36382 | 0.00090055
06/10/2011 | 0.048943 | 0.00097886 | 0.048943 | 0.00097886
06/12/2011 | 0.70364 | 0.0024667 | 0.70364 | 0.0024667
07/03/2012 | 1.1503 | 0.0059123 | 1.1503 | 0.0059123
07/04/2011 | 4.7958 | 0.11218 | 4.7958 | 0.11218
07/07/2011 | 1.1248 | 0.010219 | 1.1248 | 0.010219
07/08/2011 | 2.0204 | 0.011276 | 2.0204 | 0.011276
07/09/2011 | 1.7844 | 0.0071652 | 1.7844 | 0.0071652
07/10/2011 | 0.098943 | 0.00027408 | 0.098943 | 0.00027408
07/12/2011 | 0.49616 | 0.0012529 | 0.49616 | 0.0012529
08/01/2012 | 6.7102 | 0.02776 | 6.7102 | 0.02776
08/02/2012 | 0.16562 | 0.00097886 | 0.16562 | 0.00097886
08/03/2012 | 2.9201 | 0.044636 | 2.9201 | 0.044636
08/04/2011 | 1.0141 | 0.0034064 | 1.0141 | 0.0034064
08/06/2011 | 0.15865 | 0.0021926 | 0.15865 | 0.0021926
08/07/2011 | 0.51558 | 0.012764 | 0.51558 | 0.012764
08/08/2011 | 0.3054 | 0.001018 | 0.3054 | 0.001018
08/09/2011 | 3.0692 | 0.010924 | 3.0692 | 0.010924
08/11/2011 | 0.51684 | 0.0012921 | 0.51684 | 0.0012921
08/12/2011 | 1.9925 | 0.0052858 | 1.9925 | 0.0052858
09/02/2012 | 0.067541 | 0.00019577 | 0.067541 | 0.00019577
09/03/2012 | 1.1056 | 0.016406 | 1.1056 | 0.016406
09/05/2011 | 0.89088 | 0.0089663 | 0.89088 | 0.0089663
09/06/2011 | 0.27193 | 0.004581 | 0.27193 | 0.004581
09/07/2011 | 3.769 | 0.03798 | 3.769 | 0.03798
09/09/2011 | 0.12334 | 0.00070478 | 0.12334 | 0.00070478
09/11/2011 | 0.52858 | 0.0013704 | 0.52858 | 0.0013704
09/12/2011 | 0.44111 | 0.0031323 | 0.44111 | 0.0031323
10/01/2012 | 1.6566 | 0.026351 | 1.6566 | 0.026351
10/02/2012 | 0.15192 | 0.00039154 | 0.15192 | 0.00039154
10/05/2011 | 0.13778 | 0.00035239 | 0.13778 | 0.00035239
10/06/2011 | 0.027956 | 0.00023493 | 0.027956 | 0.00023493
10/07/2011 | 12.3665 | 0.050744 | 12.3665 | 0.050744
10/08/2011 | 2.272 | 0.0009397 | 2.272 | 0.0009397
10/10/2011 | 0.74659 | 0.0029366 | 0.74659 | 0.0029366
10/11/2011 | 5.9845 | 0.042091 | 5.9845 | 0.042091
11/03/2012 | 2.0253 | 0.037784 | 2.0253 | 0.037784
11/04/2011 | 0.25873 | 0.036962 | 0.25873 | 0.036962
11/05/2011 | 0.026782 | 0.00046985 | 0.026782 | 0.00046985
11/06/2011 | 0.085043 | 0.00046985 | 0.085043 | 0.00046985
11/07/2011 | 2.0224 | 0.010063 | 2.0224 | 0.010063
11/08/2011 | 0.53309 | 0.0053641 | 0.53309 | 0.0053641
11/10/2011 | 0.41883 | 0.0055991 | 0.41883 | 0.0055991
11/11/2011 | 2.9216 | 0.033594 | 2.9216 | 0.033594
12/01/2012 | 0.11688 | 0.00097886 | 0.11688 | 0.00097886
12/02/2012 | 1.8652 | 0.010963 | 1.8652 | 0.010963
12/03/2012 | 0.78727 | 0.033555 | 0.78727 | 0.033555
12/04/2011 | 0.80231 | 0.0014879 | 0.80231 | 0.0014879
12/05/2011 | 0.96273 | 0.0059906 | 0.96273 | 0.0059906
12/06/2011 | 0.52999 | 0.038136 | 0.52999 | 0.038136
12/07/2011 | 0.38751 | 0.0048943 | 0.38751 | 0.0048943
12/08/2011 | 1.6852 | 0.00787 | 1.6852 | 0.00787
12/09/2011 | 1.1112 | 0.0069303 | 1.1112 | 0.0069303
12/10/2011 | 4.3267 | 0.022944 | 4.3267 | 0.022944
12/12/2011 | 1.7372 | 0.015348 | 1.7372 | 0.015348
13/01/2012 | 3.6517 | 0.047377 | 3.6517 | 0.047377
13/02/2012 | 0.1473 | 0.0044636 | 0.1473 | 0.0044636
13/03/2012 | 2.0156 | 0.0062255 | 2.0156 | 0.0062255
13/04/2011 | 0.22365 | 0.00054816 | 0.22365 | 0.00054816
13/05/2011 | 0.34886 | 0.00086139 | 0.34886 | 0.00086139
13/07/2011 | 0.62948 | 0.0067737 | 0.62948 | 0.0067737
13/09/2011 | 0.01206 | 0.0004307 | 0.01206 | 0.0004307
13/10/2011 | 2.1303 | 0.014879 | 2.1303 | 0.014879
13/12/2011 | 1.3127 | 0.0061864 | 1.3127 | 0.0061864
14/01/2012 | 2.9816 | 0.010689 | 2.9816 | 0.010689
14/02/2012 | 1.0061 | 0.04581 | 1.0061 | 0.04581
14/03/2012 | 2.3787 | 0.0068128 | 2.3787 | 0.0068128
14/04/2011 | 0.8863 | 0.029366 | 0.8863 | 0.029366
14/05/2011 | 0.092991 | 0.00074393 | 0.092991 | 0.00074393
14/06/2011 | 0.7175 | 0.00097886 | 0.7175 | 0.00097886
14/07/2011 | 0.25654 | 0.0021926 | 0.25654 | 0.0021926
14/08/2011 | 0.32772 | 0.009397 | 0.32772 | 0.009397
14/09/2011 | 2.5292 | 0.026899 | 2.5292 | 0.026899
14/10/2011 | 0.43774 | 0.0043461 | 0.43774 | 0.0043461
14/12/2011 | 0.3074 | 0.0056774 | 0.3074 | 0.0056774
15/02/2012 | 2.041 | 0.0079092 | 2.041 | 0.0079092
15/03/2012 | 1.5673 | 0.0041895 | 1.5673 | 0.0041895
15/07/2011 | 0.2334 | 0.0038371 | 0.2334 | 0.0038371
15/08/2011 | 0.20298 | 0.0051292 | 0.20298 | 0.0051292
15/09/2011 | 0.78254 | 0.005325 | 0.78254 | 0.005325
15/11/2011 | 0.037001 | 0.0016445 | 0.037001 | 0.0016445
15/12/2011 | 0.16911 | 0.0023884 | 0.16911 | 0.0023884
16/01/2012 | 1.276 | 0.21723 | 1.276 | 0.21723
16/03/2012 | 0.79303 | 0.011825 | 0.79303 | 0.011825
16/05/2011 | 3.1218 | 0.046868 | 3.1218 | 0.046868
16/09/2011 | 0.32067 | 0.0013704 | 0.32067 | 0.0013704
16/12/2011 | 0.95944 | 0.022827 | 0.95944 | 0.022827
17/01/2012 | 1.5502 | 0.029757 | 1.5502 | 0.029757
17/02/2012 | 0.12749 | 0.0004307 | 0.12749 | 0.0004307
17/05/2011 | 4.078 | 0.026155 | 4.078 | 0.026155
17/06/2011 | 0.092522 | 0.00066562 | 0.092522 | 0.00066562
17/07/2011 | 0.6547 | 0.016915 | 0.6547 | 0.016915
17/08/2011 | 4.4611 | 0.025255 | 4.4611 | 0.025255
17/10/2011 | 2.1325 | 0.0072044 | 2.1325 | 0.0072044
18/03/2012 | 1.4612 | 0.015035 | 1.4612 | 0.015035
18/04/2011 | 0.041347 | 0.0018794 | 0.041347 | 0.0018794
18/07/2011 | 1.6867 | 0.011707 | 1.6867 | 0.011707
18/08/2011 | 1.2618 | 0.0036022 | 1.2618 | 0.0036022
18/09/2011 | 0.78528 | 0.026899 | 0.78528 | 0.026899
18/10/2011 | 2.5983 | 0.0070086 | 2.5983 | 0.0070086
18/11/2011 | 0.94879 | 0.027134 | 0.94879 | 0.027134
19/01/2012 | 0.27525 | 0.00074393 | 0.27525 | 0.00074393
19/03/2012 | 1.3984 | 0.056108 | 1.3984 | 0.056108
19/04/2011 | 1.6852 | 0.003798 | 1.6852 | 0.003798
19/05/2011 | 1.9908 | 0.0079092 | 1.9908 | 0.0079092
19/07/2011 | 0.16171 | 0.0023101 | 0.16171 | 0.0023101
19/08/2011 | 0.39577 | 0.0036022 | 0.39577 | 0.0036022
19/09/2011 | 2.2119 | 0.060454 | 2.2119 | 0.060454
19/10/2011 | 1.5549 | 0.0080658 | 1.5549 | 0.0080658
19/11/2011 | 0.088802 | 0.0014096 | 0.088802 | 0.0014096
19/12/2011 | 0.079366 | 0.00097886 | 0.079366 | 0.00097886
20/01/2012 | 0.74248 | 0.0019186 | 0.74248 | 0.0019186
20/02/2012 | 0.31578 | 0.0012138 | 0.31578 | 0.0012138
20/03/2012 | 7.9601 | 0.071691 | 7.9601 | 0.071691
20/04/2011 | 0.47572 | 0.0011746 | 0.47572 | 0.0011746
20/05/2011 | 0.9397 | 0.0029366 | 0.9397 | 0.0029366
20/09/2011 | 0.2316 | 0.00050901 | 0.2316 | 0.00050901
20/10/2011 | 0.91817 | 0.0026233 | 0.91817 | 0.0026233
20/11/2011 | 2.9695 | 0.098982 | 2.9695 | 0.098982
20/12/2011 | 0.71946 | 0.0029366 | 0.71946 | 0.0029366
21/01/2012 | 0.39119 | 0.0066562 | 0.39119 | 0.0066562
21/02/2012 | 0.1572 | 0.0004307 | 0.1572 | 0.0004307
21/03/2012 | 0.96421 | 0.015427 | 0.96421 | 0.015427
21/07/2011 | 0.55493 | 0.0092796 | 0.55493 | 0.0092796
21/09/2011 | 0.12001 | 0.0014879 | 0.12001 | 0.0014879
21/10/2011 | 2.1256 | 0.0092796 | 2.1256 | 0.0092796
21/11/2011 | 10.8194 | 0.054933 | 10.8194 | 0.054933
21/12/2011 | 3.6296 | 0.054816 | 3.6296 | 0.054816
22/02/2012 | 0.046359 | 0.00062647 | 0.046359 | 0.00062647
22/03/2012 | 1.6101 | 0.0059906 | 1.6101 | 0.0059906
22/05/2011 | 0.0046985 | 0.00011746 | 0.0046985 | 0.00011746
22/06/2011 | 0.40611 | 0.0029366 | 0.40611 | 0.0029366
22/07/2011 | 4.4644 | 0.21531 | 4.4644 | 0.21531
22/09/2011 | 0.92455 | 0.010102 | 0.92455 | 0.010102
22/11/2011 | 1.0715 | 0.0023101 | 1.0715 | 0.0023101
22/12/2011 | 0.26605 | 0.0060298 | 0.26605 | 0.0060298
23/01/2012 | 0.60689 | 0.0087314 | 0.60689 | 0.0087314
23/02/2012 | 3.1375 | 0.029953 | 3.1375 | 0.029953
23/03/2012 | 3.1296 | 0.01159 | 3.1296 | 0.01159
23/05/2011 | 0.6251 | 0.0026233 | 0.6251 | 0.0026233
23/06/2011 | 1.1944 | 0.0066562 | 1.1944 | 0.0066562
23/07/2011 | 0.60842 | 0.0037197 | 0.60842 | 0.0037197
23/08/2011 | 0.60251 | 0.00278 | 0.60251 | 0.00278
23/09/2011 | 0.31668 | 0.0045419 | 0.31668 | 0.0045419
23/10/2011 | 1.2208 | 0.0076351 | 1.2208 | 0.0076351
23/11/2011 | 2.0226 | 0.0098669 | 2.0226 | 0.0098669
23/12/2011 | 0.13031 | 0.0081441 | 0.13031 | 0.0081441
24/02/2012 | 7.4097 | 0.016484 | 7.4097 | 0.016484
24/05/2011 | 0.21805 | 0.0060689 | 0.21805 | 0.0060689
24/06/2011 | 1.4272 | 0.0080266 | 1.4272 | 0.0080266
24/07/2011 | 2.0235 | 0.0018794 | 2.0235 | 0.0018794
24/08/2011 | 1.8693 | 0.0029366 | 1.8693 | 0.0029366
24/11/2011 | 0.63532 | 0.0026625 | 0.63532 | 0.0026625
25/01/2012 | 1.7195 | 0.0075176 | 1.7195 | 0.0075176
25/02/2012 | 1.9568 | 0.018403 | 1.9568 | 0.018403
25/03/2012 | 0.025842 | 0.00031323 | 0.025842 | 0.00031323
25/05/2011 | 0.26703 | 0.0061081 | 0.26703 | 0.0061081
25/07/2011 | 0.48712 | 0.0050901 | 0.48712 | 0.0050901
25/08/2011 | 1.904 | 0.01852 | 1.904 | 0.01852
25/11/2011 | 0.18003 | 0.0029757 | 0.18003 | 0.0029757
26/01/2012 | 1.1886 | 0.0075568 | 1.1886 | 0.0075568
26/04/2011 | 26.0048 | 0.060963 | 22.8581 | 0.060963
26/05/2011 | 12.1249 | 0.050431 | 12.1249 | 0.050431
26/06/2011 | 3.1089 | 0.021261 | 3.1089 | 0.021261
26/08/2011 | 0.20419 | 0.003563 | 0.20419 | 0.003563
26/10/2011 | 0.27232 | 0.0037197 | 0.27232 | 0.0037197
26/11/2011 | 0.14906 | 0.0018403 | 0.14906 | 0.0018403
27/02/2012 | 1.0386 | 0.0039546 | 1.0386 | 0.0039546
27/03/2012 | 0.60215 | 0.00090055 | 0.60215 | 0.00090055
27/04/2011 | 6.2823 | 0.035395 | 6.2823 | 0.035395
27/05/2011 | 0.66237 | 0.0077917 | 0.66237 | 0.0077917
27/06/2011 | 0.13884 | 0.00070478 | 0.13884 | 0.00070478
27/07/2011 | 0.023258 | 0.0004307 | 0.023258 | 0.0004307
27/09/2011 | 2.1648 | 0.029483 | 2.1648 | 0.029483
27/10/2011 | 0.068716 | 0.0010572 | 0.068716 | 0.0010572
28/01/2012 | 0.15239 | 0.0023884 | 0.15239 | 0.0023884
28/03/2012 | 0.56124 | 0.002545 | 0.56124 | 0.002545
28/04/2011 | 3.0278 | 0.022005 | 3.0278 | 0.022005
28/07/2011 | 0.64534 | 0.0016445 | 0.64534 | 0.0016445
28/09/2011 | 0.83375 | 0.006852 | 0.83375 | 0.006852
28/10/2011 | 1.7487 | 0.0053641 | 1.7487 | 0.0053641
28/11/2011 | 1.6507 | 0.0079092 | 1.6507 | 0.0079092
29/02/2012 | 2.4742 | 0.0011355 | 2.4742 | 0.0011355
29/03/2012 | 0.50427 | 0.0034456 | 0.50427 | 0.0034456
29/04/2011 | 0.81229 | 0.0089663 | 0.81229 | 0.0089663
29/06/2011 | 0.5361 | 0.010963 | 0.5361 | 0.010963
29/07/2011 | 1.0774 | 0.0040329 | 1.0774 | 0.0040329
29/09/2011 | 1.3395 | 0.0068912 | 1.3395 | 0.0068912
30/03/2012 | 1.0286 | 0.0028974 | 1.0286 | 0.0028974
30/04/2011 | 0.044792 | 0.001018 | 0.044792 | 0.001018
30/06/2011 | 1.2361 | 0.010611 | 1.2361 | 0.010611
30/07/2011 | 0.27749 | 0.0023884 | 0.27749 | 0.0023884
30/09/2011 | 0.18735 | 0.0013704 | 0.18735 | 0.0013704
30/10/2011 | 3.6238 | 0.031245 | 3.6238 | 0.031245
30/11/2011 | 0.0070478 | 0.00023493 | 0.0070478 | 0.00023493
31/05/2011 | 0.85168 | 0.0098277 | 0.85168 | 0.0098277
31/08/2011 | 1.1384 | 0.0048943 | 1.1384 | 0.0048943

## 20112012Answer
SumOfSaidi | SumOfSafi | SumOfFixedSaidi | SumOfFixedSaifi
395.2927 | 3.4124 | 392.1459 | 3.4124
|  | SaidiLimit | SaifiLimit
|  | 302.3793 | 4.2143

## 20102011Data
REPORT NUMBER | Date Outage | YEAR | DATE ON | Duration of Outage | Customers Impacted | Total Customer Minutes Lost | CLASS A-G | CAUSE | NOTES
13312 | 02/04/2010 | 2010 | 2010-04-02 | 62 | 1173 | 21958 | C | UNKNOWN | Reclose CB B825 Aberdeen Rd at Carnarvon St Sub cause unknown
13313 | 02/04/2010 | 2010 | 2010-04-02 | 93 | 53 | 4929 | C | TREE CONTACTS | Repair 11kV lines beyond W8118 Tahaenui
13314 | 07/04/2010 | 2010 | 2010-04-07 | 57 | 16 | 1616 | C | FOREIGN INTERFERENCE | Replace 50kV pole C3350 McDonalds Rd
13321 | 07/04/2010 | 2010 | 2010-04-07 | 136 | 31 | 4216 | B | PLANNED SHUTDOWN | Erect 2 11kV poles beyond E53 Private Ormond Valley
13323 | 08/04/2010 | 2010 | 2010-04-08 | 416 | 13 | 5408 | B | PLANNED SHUTDOWN | Replace 3 11kV poles D2304 D2305 D2306 Kawatiri Rd
13325 | 08/04/2010 | 2010 | 2010-04-08 | 57 | 12 | 684 | B | PLANNED SHUTDOWN | Fit temp fuses on pole D534 Hihiroroa Rd
13322 | 09/04/2010 | 2010 | 2010-04-09 | 47 | 23 | 1081 | B | PLANNED SHUTDOWN | Connect 11kV jumpers pole A747 Rototahi
13324 | 09/04/2010 | 2010 | 2010-04-09 | 372 | 3 | 1116 | B | PLANNED SHUTDOWN | Replace 2 11kV poles D5307 D538 Kawatiri Rd
13329 | 15/04/2010 | 2010 | 2010-04-15 | 283 | 43 | 5479 | B | PLANNED SHUTDOWN | Relocate GVR switch E864 Waimata Valley Hill
13315 | 16/04/2010 | 2010 | 2010-04-16 | 183 | 61 | 8168 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A3964 Wharekiri Rd
13316 | 16/04/2010 | 2010 | 2010-04-16 | 131 | 167 | 8488 | C | UNKNOWN | Reclose CB A283 at Tatapouri cause unknown
13317 | 17/04/2010 | 2010 | 2010-04-17 | 67 | 311 | 20837 | C | DEFECTIVE EQUIPMENT | Replace 2 DDO fuses T/x W525 Newcastle St Mahia
13318 | 18/04/2010 | 2010 | 2010-04-18 | 54 | 981 | 41710 | C | UNKNOWN | Reclose CB C95 Haisman Rd at makaraka Sub cause unknown
13331 | 26/04/2010 | 2010 | 2010-04-26 | 195 | 9 | 1755 | B | PLANNED SHUTDOWN | Replumb pole E2228 Arawhana Rd
13319 | 27/04/2010 | 2010 | 2010-04-27 | 29 | 172 | 2648 | C | UNKNOWN | Reclose CB C95 Haisman Rd at Makaraka Sub cause unknown
13320 | 27/04/2010 | 2010 | 2010-04-27 | 10 | 1359 | 13590 | C | UNKNOWN | Reclose CB C1 at Hexton cause unknown
13326 | 27/04/2010 | 2010 | 2010-04-27 | 145 | 75 | 10875 | B | PLANNED SHUTDOWN | Replace T/x F473 Kanakanaia Rd
13328 | 27/04/2010 | 2010 | 2010-04-27 | 105 | 25 | 2625 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting D422 Harpers Rd
13330 | 27/04/2010 | 2010 | 2010-04-27 | 365 | 80 | 29200 | B | PLANNED SHUTDOWN | Isolate 11kV lines for lime stablilisation work SH35 at pole J356
13327 | 30/04/2010 | 2010 | 2010-04-30 | 257 | 7 | 1799 | B | PLANNED SHUTDOWN | Install new Gas switch B5837 & B5839 Awapuni Rd
13333 | 05/05/2010 | 2010 | 2010-05-05 | 12 | 16 | 192 | C | TREE CONTACTS | Reclose CB G368 Hokoroa Rd Trees
13357 | 05/05/2010 | 2010 | 2010-05-05 | 312 | 33 | 10296 | B | PLANNED SHUTDOWN | Replace 11kV poles B1800 B1798 B1794 Awapuni Rd
13334 | 06/05/2010 | 2010 | 2010-05-06 | 45 | 1520 | 40484 | C | UNKNOWN | Reclose CB A616 Harris St at Port Sub cause unknown
13335 | 06/05/2010 | 2010 | 2010-05-06 | 148 | 9 | 1332 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W20795 Onenui Mahia
13359 | 06/05/2010 | 2010 | 2010-05-06 | 382 | 12 | 16380 | B | PLANNED SHUTDOWN | Replace 14 11kV poles D2759 D2757 Hihiroroa Rd
13336 | 08/05/2010 | 2010 | 2010-05-08 | 134 | 730 | 53348 | C | DEFECTIVE EQUIPMENT | Repair broken jumper pole W5866 Marumaru
13337 | 08/05/2010 | 2010 | 2010-05-08 | 500 | 55 | 14162 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable from B530 to T/x B375 Desmond Rd
13358 | 08/05/2010 | 2010 | 2010-05-08 | 395 | 120 | 31920 | B | PLANNED SHUTDOWN | Replace 3 11kV poles B1790 B1788 B1771 Awapuni Rd
13338 | 09/05/2010 | 2010 | 2010-05-09 | 29 | 64 | 1856 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole F3328 Crn Cliff Rd & Rangitira Rd
13339 | 12/05/2010 | 2010 | 2010-05-12 | 758 | 91 | 11176 | C | TREE CONTACTS | Repair 11kV lines pole G759 Kaiaua Rd
13360 | 12/05/2010 | 2010 | 2010-05-12 | 388 | 12 | 27708 | B | PLANNED SHUTDOWN | Replace 11kV poles D108 D4881 D4888 D4898 Hihiroroa Rd
13363 | 14/05/2010 | 2010 | 2010-05-14 | 360 | 21 | 6543 | B | PLANNED SHUTDOWN | Replace 3 11kV poles G1670 G1667 G87 Paroa Rd
13340 | 17/05/2010 | 2010 | 2010-05-17 | 61 | 2516 | 153476 | C | UNKNOWN | Reclose A8 Goodwins Rd cause unknown
13342 | 18/05/2010 | 2010 | 2010-05-18 | 22 | 1520 | 27490 | C | TREE CONTACTS | Reclose CB A616 Harris St Kaiti Sub Contractors tree in Lines
13361 | 18/05/2010 | 2010 | 2010-05-18 | 180 | 38 | 6840 | B | PLANNED SHUTDOWN | Erect new T/x on pole D1398 Tiniroto Rd
13364 | 18/05/2010 | 2010 | 2010-05-18 | 14 | 63 | 1638 | B | PLANNED SHUTDOWN | Cut 11kV jumpers pole C3243 Nelson Rd
13365 | 18/05/2010 | 2010 | 2010-05-18 | 435 | 6 | 2610 | B | PLANNED SHUTDOWN | Install DDO fuses on pole C306 Nelson Rd
13343 | 19/05/2010 | 2010 | 2010-05-19 | 41 | 222 | 9102 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J356 Hicks Bay
13356 | 19/05/2010 | 2010 | 2010-05-19 | 502 | 20 | 30669 | B | PLANNED SHUTDOWN | Replace poles D104 D2743 D2730 D2725 Hihiroroa Rd
13368 | 19/05/2010 | 2010 | 2010-05-19 | 48 | 165 | 7920 | B | PLANNED SHUTDOWN | Replace DDO fuses pole C133 Muriwai
13344 | 21/05/2010 | 2010 | 2010-05-21 | 58 | 17 | 986 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole A3622 Waiomoko Rd
13345 | 21/05/2010 | 2010 | 2010-05-21 | 142 | 18 | 2556 | C | DEFECTIVE EQUIPMENT | Repair floating wire pole G1810 Paramata Rd
13346 | 24/05/2010 | 2010 | 2010-05-24 | 197 | 695 | 20635 | C | TREE CONTACTS | Remove tree from 11kV pole A4109 Kaiti Hill
13347 | 24/05/2010 | 2010 | 2010-05-24 | 50 | 1273 | 497008 | C | TREE CONTACTS | Repair 50kV lines Between H992 to H993 Te Puia
13348 | 24/05/2010 | 2010 | 2010-05-24 | 613 | 216 | 29124 | C | ADVERSE WEATHER | Repair 11kV lines pole W9214 Pongaroa Mahia
13349 | 25/05/2010 | 2010 | 2010-05-25 | 23 | 483 | 19759 | C | TREE CONTACTS | Isolate 11kV fault J72 Rangitukia and Restart Generator 1 Te Araroa
13350 | 26/05/2010 | 2010 | 2010-05-26 | 142 | 73 | 3048 | C | TREE CONTACTS | Repair 11kV lines poles G613 to G614 Hokoroa Rd
13351 | 26/05/2010 | 2010 | 2010-05-26 | 167 | 398 | 42886 | C | DEFECTIVE EQUIPMENT | Repair 11kV line between W6380 & W6381 Waihua
13352 | 26/05/2010 | 2010 | 2010-05-26 | 772 | 57 | 39896 | C | TREE CONTACTS | Remove trees from 11kV lines between J1238 to J1916 Rangitukia Rd
13353 | 27/05/2010 | 2010 | 2010-05-27 | 18 | 16 | 288 | C | DEFECTIVE EQUIPMENT | Rejoin 11kV jumpers pole W6375 Waihua
13354 | 27/05/2010 | 2010 | 2010-05-27 | 16 | 117 | 1872 | C | FOREIGN INTERFERENCE | Check conductors poles D1376 to D717 Dead Swan Tiniroto Rd
13362 | 27/05/2010 | 2010 | 2010-05-27 | 392 | 50 | 11660 | B | PLANNED SHUTDOWN | Replace 14 11kV poles E1788 to E1826 Kaiteratahi
13367 | 27/05/2010 | 2010 | 2010-05-27 | 262 | 76 | 11538 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting D3825 to D818 Tiniroto Rd
13355 | 30/05/2010 | 2010 | 2010-05-30 | 890 | 172 | 43594 | C | TREE CONTACTS | Repair 11kV lines poles W5579 to W5580 Raupunga
13366 | 31/05/2010 | 2010 | 2010-05-31 | 44 | 20 | 1160 | B | PLANNED SHUTDOWN | Replace ABS pole D84 Wharekopae Rd
13369 | 01/06/2010 | 2010 | 2010-06-01 | 35 | 58 | 2030 | C | DEFECTIVE EQUIPMENT | Replace 11kV Disc pole C2635 Taurau Valley
13385 | 02/06/2010 | 2010 | 2010-06-02 | 355 | 102 | 14192 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting D3825 Tiniroto Rd
13370 | 08/06/2010 | 2010 | 2010-06-08 | 1875 | 366 | 21836 | C | TREE CONTACTS | Repair 11kV lines W6287 to W6288 Cricklewood Rd
13371 | 08/06/2010 | 2010 | 2010-06-08 | 1191 | 53 | 18318 | C | TREE CONTACTS | Repair 11kV lines pole D2543 Tuhunga Rd
13372 | 08/06/2010 | 2010 | 2010-06-08 | 333 | 6 | 1998 | C | DEFECTIVE EQUIPMENT | Relocate 3 11kV poles D1485 D1484 D1483 Knights Rd
13373 | 08/06/2010 | 2010 | 2010-06-08 | 88 | 46 | 3460 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper ABS pole D491 Taumata Rd
13375 | 10/06/2010 | 2010 | 2010-06-10 | 66 | 81 | 3003 | C | FOREIGN INTERFERENCE | Reclose CB G327 Rototahi cause truck caugh tin 11kV lines pole A800
13386 | 13/06/2010 | 2010 | 2010-06-13 | 95 | 272 | 25840 | B | PLANNED SHUTDOWN | Install line breaks pole A3121 Huxley Rd
13374 | 14/06/2010 | 2010 | 2010-06-14 | 30 | 2516 | 67620 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
13387 | 15/06/2010 | 2010 | 2010-06-15 | 38 | 62 | 4092 | B | PLANNED SHUTDOWN | Relocate 11kV pole D144 Wharekopae Rd
13384 | 16/06/2010 | 2010 | 2010-06-16 | 481 | 50 | 6362 | B | PLANNED SHUTDOWN | Replace poles E104 E1776 E1778 E1779 SH2 Kaiteratahi
13388 | 18/06/2010 | 2010 | 2010-06-18 | 29 | 15 | 435 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers A4109 Queens Drive
13376 | 19/06/2010 | 2010 | 2010-06-19 | 445 | 730 | 220015 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W6506 Mangapoikie Rd
13377 | 20/06/2010 | 2010 | 2010-06-20 | 187 | 128 | 23936 | C | TREE CONTACTS | Repair 11kV lines pole J2553 Te Araroa
13378 | 21/06/2010 | 2010 | 2010-06-21 | 19 | 176 | 3344 | C | UNKNOWN | Reclose CB 24 Ruakituri at Tuai Sub cause unknown
13379 | 22/06/2010 | 2010 | 2010-06-22 | 166 | 274 | 4719 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W8381 Morere Hill
13380 | 24/06/2010 | 2010 | 2010-06-24 | 60 | 11 | 660 | C | TREE CONTACTS | Repair 11kV lines pole H2227 Waipiro Bay Rd
13381 | 26/06/2010 | 2010 | 2010-06-26 | 88 | 75 | 6600 | C | UNKNOWN | Reclose CB H341 Mata Rd cause unknown
13382 | 26/06/2010 | 2010 | 2010-06-26 | 76 | 17 | 1751 | C | ADVERSE WEATHER | Relocate pole J748 Tapueroa Rd river bank co lappsed
13383 | 28/06/2010 | 2010 | 2010-06-28 | 271 | 82 | 15832 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole G1410 to G1412 Anaura Bay Rd
13389 | 28/06/2010 | 2010 | 2010-06-28 | 60 | 46 | 2760 | B | PLANNED SHUTDOWN | Install 3 DDO fuses pole C757 Waingake
13426 | 01/07/2010 | 2010 | 2010-07-01 | 54 | 605 | 32670 | B | PLANNED SHUTDOWN | Connect Terrace Subdivision pole W8897 Mahia
13427 | 01/07/2010 | 2010 | 2010-07-01 | 415 | 81 | 6762 | B | PLANNED SHUTDOWN | Replace 11kV poles A1796 A254 A1798 A1799 Huxley Rd
13428 | 01/07/2010 | 2010 | 2010-07-01 | 385 | 6 | 2310 | B | PLANNED SHUTDOWN | Isolate 11kV at ABS C189 Wharerata Rd for tree cutting
13390 | 02/07/2010 | 2010 | 2010-07-02 | 1041 | 248 | 95703 | C | FOREIGN INTERFERENCE | Replace 11kV pole W8009 Nuhaka
13391 | 02/07/2010 | 2010 | 2010-07-02 | 27 | 16 | 432 | C | DEFECTIVE EQUIPMENT | Replace 3 DDO fuses pole A533 Wheatstone Rd
13392 | 05/07/2010 | 2010 | 2010-07-05 | 1034 | 75 | 5741 | C | TREE CONTACTS | Repair 11kV lines H357 to H2784 Mata Rd
13393 | 05/07/2010 | 2010 | 2010-07-05 | 189 | 54 | 10066 | C | DEFECTIVE EQUIPMENT | By pass PMR G367 Tauwhareparae Rd
13394 | 05/07/2010 | 2010 | 2010-07-05 | 1505 | 60 | 28998 | C | TREE CONTACTS | Repair 11kV lines pole C852 Paparatu Rd
13395 | 06/07/2010 | 2010 | 2010-07-06 | 985 | 258 | 87816 | C | ADVERSE WEATHER | Repair 11kV lines J4242 to J4243 Hicks Bay
13396 | 06/07/2010 | 2010 | 2010-07-06 | 155 | 36 | 5580 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W1473 Ohopo
13397 | 06/07/2010 | 2010 | 2010-07-06 | 17 | 136 | 2312 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole A455 Murphy Rd
13398 | 06/07/2010 | 2010 | 2010-07-06 | 150 | 177 | 3116 | C | ADVERSE WEATHER | Restand 11kV pole H652 Ihungia Rd Due to slip
13399 | 06/07/2010 | 2010 | 2010-07-06 | 193 | 167 | 13652 | C | TREE CONTACTS | Repair 11kV lines pole H2329 Te Puia
13430 | 06/07/2010 | 2010 | 2010-07-06 | 371 | 6 | 5076 | B | PLANNED SHUTDOWN | Replace 10 11kV Poles Between F2743 to F2756 Whatatutu Rd
13400 | 07/07/2010 | 2010 | 2010-07-07 | 504 | 5 | 2520 | C | TREE CONTACTS | Repair 11kV lines pole H639 Mata Rd
13401 | 07/07/2010 | 2010 | 2010-07-07 | 1219 | 82 | 64877 | C | TREE CONTACTS | Repair 11kV lines pole G1410 Anaura Bay
13402 | 07/07/2010 | 2010 | 2010-07-07 | 108 | 168 | 6579 | C | TREE CONTACTS | Repair 11kV Lines pole H2290 Tokomaru Bay
13403 | 08/07/2010 | 2010 | 2010-07-08 | 83 | 421 | 18120 | C | FOREIGN INTERFERENCE | Replace T/x D520 Lavenham Rd Car hit pole
13404 | 08/07/2010 | 2010 | 2010-07-08 | 157 | 50 | 7850 | C | ADVERSE WEATHER | Replace 11kV pole H1982 Waipiro Bay Rd
13405 | 09/07/2010 | 2010 | 2010-07-09 | 360 | 2 | 786 | C | TREE CONTACTS | Remove tree in 11kV pole H2009 Kopouroa
13406 | 09/07/2010 | 2010 | 2010-07-09 | 24 | 1275 | 17453 | C | TREE CONTACTS | Repair 50kV lines pole J1835 Tikitiki
13407 | 10/07/2010 | 2010 | 2010-07-10 | 14 | 20 | 280 | C | DEFECTIVE EQUIPMENT | Replace 11kV fuse B1016 Customhouse St
13431 | 12/07/2010 | 2010 | 2010-07-12 | 302 | 36 | 10872 | B | PLANNED SHUTDOWN | Replace 11kV Poles F203 F184 F185 Rakauroa Rd
13408 | 13/07/2010 | 2010 | 2010-07-13 | 127 | 11 | 1190 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines between W1021 to W7262 Waste Water Plant
13409 | 14/07/2010 | 2010 | 2010-07-14 | 128 | 18 | 2304 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole C2148 Waingake Rd
13432 | 14/07/2010 | 2010 | 2010-07-14 | 404 | 69 | 9991 | B | PLANNED SHUTDOWN | Install 11kV cable & DDO fuses pole W1626 Goldsmith Rd
13433 | 14/07/2010 | 2010 | 2010-07-14 | 401 | 23 | 9223 | B | PLANNED SHUTDOWN | Replace 11kV poles C5421 C830 Damm Rd
13434 | 14/07/2010 | 2010 | 2010-07-14 | 40 | 131 | 5004 | B | PLANNED SHUTDOWN | Replace 11kV poles A1799 A1798 Huxley Rd
13410 | 17/07/2010 | 2010 | 2010-07-17 | 80 | 388 | 31040 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper ABS pole J268 Te Araroa
13411 | 17/07/2010 | 2010 | 2010-07-17 | 273 | 83 | 12197 | C | UNKNOWN | Reclose GVR F469 Matawai cause unknown
13412 | 17/07/2010 | 2010 | 2010-07-17 | 134 | 76 | 10184 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole W6081Mangapoike
13413 | 17/07/2010 | 2010 | 2010-07-17 | 204 | 75 | 4132 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole H156 broken by Digger Ihungia Rd
13414 | 18/07/2010 | 2010 | 2010-07-18 | 15 | 32 | 480 | C | DEFECTIVE EQUIPMENT | Replace 11kV DDO fuse G1210 Cook St Tolaga Bay
13415 | 19/07/2010 | 2010 | 2010-07-19 | 10 | 24 | 240 | C | DEFECTIVE EQUIPMENT | Replace DDO fuse base D325 Lake Rd
13436 | 19/07/2010 | 2010 | 2010-07-19 | 58 | 49 | 2842 | B | PLANNED SHUTDOWN | Isolate 11kV lines D818 for tree cutting Tiniroto Rd
13417 | 20/07/2010 | 2010 | 2010-07-20 | 344 | 74 | 12376 | C | DEFECTIVE EQUIPMENT | Rebind insulator on pole F2513 Moanui Valley
13418 | 20/07/2010 | 2010 | 2010-07-20 | 138 | 438 | 60354 | C | TREE CONTACTS | Remove tree from 11kV pole F3196 Otoko
13419 | 20/07/2010 | 2010 | 2010-07-20 | 95 | 20 | 1900 | C | DEFECTIVE EQUIPMENT | Repair 11kV boot on cable Fuse Switch B1016 Customhouse St
13420 | 20/07/2010 | 2010 | 2010-07-20 | 368 | 12 | 2057 | C | FOREIGN INTERFERENCE | Relocate 11kV pole H369 Ihungia Rd caused by slip
13435 | 20/07/2010 | 2010 | 2010-07-20 | 100 | 62 | 6200 | B | PLANNED SHUTDOWN | Replace pole F2739 & rejoin jumpers pole F3461 Whatatutu Rd
13437 | 21/07/2010 | 2010 | 2010-07-21 | 298 | 92 | 14215 | B | PLANNED SHUTDOWN | Replace poles B1145 B1146 B2499 Balance St
13421 | 22/07/2010 | 2010 | 2010-07-22 | 36 | 8 | 288 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J3831 Matakoa Point
13438 | 22/07/2010 | 2010 | 2010-07-22 | 395 | 35 | 13825 | B | PLANNED SHUTDOWN | Replace 11kV poles B1144 B6227 B1162 Hill Rd
13422 | 23/07/2010 | 2010 | 2010-07-23 | 8 | 438 | 3504 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole F3726 Waihuka Rd
13423 | 24/07/2010 | 2010 | 2010-07-24 | 24 | 176 | 4224 | C | UNKNOWN | Reclose CB24 Tuai Sub cause unknown
13424 | 25/07/2010 | 2010 | 2010-07-25 | 133 | 253 | 16154 | C | FOREIGN INTERFERENCE | Remove possum & change insulator pole D2293 Lavenham Rd
13439 | 27/07/2010 | 2010 | 2010-07-27 | 420 | 177 | 78942 | B | PLANNED SHUTDOWN | Replace 11kV poles B3182 B3187 Valley Rd
13440 | 28/07/2010 | 2010 | 2010-07-28 | 450 | 35 | 15750 | B | PLANNED SHUTDOWN | Replace poles B1161 B1160 B1159 B1158 B1157 Hill Rd
13441 | 29/07/2010 | 2010 | 2010-07-29 | 356 | 96 | 25632 | B | PLANNED SHUTDOWN | Replace 11kV poles B2367 B6301 B6305 James St
13425 | 31/07/2010 | 2010 | 2010-07-31 | 103 | 72 | 7416 | C | UNKNOWN | Reclose KFE F419 Whakarau Rd cause unknown
13442 | 01/08/2010 | 2010 | 2010-08-01 | 27 | 421 | 10499 | C | UNKNOWN | Reclose CB D464 Waimata at Patutahi Sub cause unkown
13443 | 02/08/2010 | 2010 | 2010-08-02 | 10 | 93 | 796 | C | UNKNOWN | Reclose CB E863 Whatatutu cause unknown
13444 | 02/08/2010 | 2010 | 2010-08-02 | 83 | 108 | 8964 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole W4682 Kokako
13466 | 03/08/2010 | 2010 | 2010-08-03 | 390 | 70 | 13650 | B | PLANNED SHUTDOWN | Replace 11kV poles B1160 & B1159 Hill Rd
13468 | 04/08/2010 | 2010 | 2010-08-04 | 438 | 44 | 3964 | B | PLANNED SHUTDOWN | Isolate 11kV lines D1784 to D1791 for tree cutting Tiniroto Rd
13445 | 05/08/2010 | 2010 | 2010-08-05 | 51 | 39 | 1989 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper T/x J174 Tapuwaeroa
13467 | 05/08/2010 | 2010 | 2010-08-05 | 360 | 179 | 30873 | B | PLANNED SHUTDOWN | Replace polesB3186 B3185 & B3184 Mary St
13446 | 06/08/2010 | 2010 | 2010-08-06 | 407 | 122 | 17692 | C | FOREIGN INTERFERENCE | Replace 11kV pole H1432 Hiruharama hit by car
13469 | 10/08/2010 | 2010 | 2010-08-10 | 428 | 81 | 34668 | B | PLANNED SHUTDOWN | Replace 11kV poles B438 & remove pole B3139 Mary St
13477 | 10/08/2010 | 2010 | 2010-08-10 | 322 | 15 | 4830 | B | PLANNED SHUTDOWN | Replace 11kV poles F660 F195 F659 F658 Rakauroa Rd
13447 | 11/08/2010 | 2010 | 2010-08-11 | 66 | 10 | 660 | C | DEFECTIVE EQUIPMENT | Replace 11kV disc on ABS H141 Tuakau Rd
13470 | 11/08/2010 | 2010 | 2010-08-11 | 461 | 82 | 37802 | B | PLANNED SHUTDOWN | Replace 11kV poles B92 B3189 B2386 B3316 Mary St
13448 | 12/08/2010 | 2010 | 2010-08-12 | 34 | 7 | 238 | C | DEFECTIVE EQUIPMENT | Replace DDO fuses F1762 Motuhora Rd
13471 | 12/08/2010 | 2010 | 2010-08-12 | 416 | 273 | 30975 | B | PLANNED SHUTDOWN | Replace 11kV poles B517 B3183 B82 Mary St
13472 | 12/08/2010 | 2010 | 2010-08-12 | 513 | 12 | 6156 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting W337 to W338 Karkariki
13449 | 14/08/2010 | 2010 | 2010-08-14 | 33 | 92 | 2806 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole D143 Wharekopae Rd
13450 | 14/08/2010 | 2010 | 2010-08-14 | 82 | 57 | 4674 | C | DEFECTIVE EQUIPMENT | Replace DDO fuses A1222 Pa Rd Whangara
13451 | 14/08/2010 | 2010 | 2010-08-14 | 226 | 86 | 7918 | C | ADVERSE WEATHER | Patrolled lines W998 to W1024 Reclose CB24 Tuai Sub
13452 | 14/08/2010 | 2010 | 2010-08-14 | 52 | 175 | 11923 | C | ADVERSE WEATHER | Reclose CB24 Tuai Sub Strong winds in area
13476 | 14/08/2010 | 2010 | 2010-08-14 | 195 | 23 | 4485 | B | PLANNED SHUTDOWN | Isolate 11kV A1223 for Rural Fire for House burn Pa Rd
13453 | 16/08/2010 | 2010 | 2010-08-16 | 189 | 120 | 11970 | C | DEFECTIVE EQUIPMENT | Replace Insulators poles W4722 & W4718 Rangiahua
13473 | 17/08/2010 | 2010 | 2010-08-17 | 494 | 23 | 11362 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting C89 to C94 Tarewa Rd Waingake
13454 | 18/08/2010 | 2010 | 2010-08-18 | 45 | 10 | 450 | C | DEFECTIVE EQUIPMENT | Replace Xarms on poles W4992 & W4989 Waireka Rd
13455 | 18/08/2010 | 2010 | 2010-08-18 | 495 | 8 | 3960 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole E1135 Kanakanaia Rd (trees)
13465 | 18/08/2010 | 2010 | 2010-08-18 | 184 | 8 | 1472 | B | PLANNED SHUTDOWN | Install DDO fuses pole C3965 & C3975 Dunstan Rd
13475 | 18/08/2010 | 2010 | 2010-08-18 | 342 | 9 | 3078 | B | PLANNED SHUTDOWN | Replace 11kV poles C1533 C1548 Bck Ormond Rd
13456 | 19/08/2010 | 2010 | 2010-08-19 | 69 | 175 | 12075 | C | TREE CONTACTS | Repair 11kV line pole W6426 Mohaka
13474 | 19/08/2010 | 2010 | 2010-08-19 | 413 | 6 | 2478 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting C189 to C4957 Opoutama Rd
13481 | 20/08/2010 | 2010 | 2010-08-20 | 420 | 15 | 6300 | B | PLANNED SHUTDOWN | Replace 11kV poles F659 & F660 Rakauroa Rd
13478 | 24/08/2010 | 2010 | 2010-08-24 | 320 | 92 | 15646 | B | PLANNED SHUTDOWN | Replace pole B1159 Balance St & rejoin jumpers B1146
13479 | 25/08/2010 | 2010 | 2010-08-25 | 434 | 209 | 54034 | B | PLANNED SHUTDOWN | Replace 11kV poles B3183 B3147 Mary St
13457 | 26/08/2010 | 2010 | 2010-08-26 | 299 | 16 | 4784 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole G2670 Wharf Rd Tolaga
13458 | 26/08/2010 | 2010 | 2010-08-26 | 105 | 212 | 9574 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole G1134 SH35 Tolaga Bay South
13480 | 26/08/2010 | 2010 | 2010-08-26 | 383 | 72 | 22241 | B | PLANNED SHUTDOWN | Replace poles D2824 D2826 D2827 D2831 Bck Ormond Rd
13459 | 27/08/2010 | 2010 | 2010-08-27 | 100 | 280 | 12276 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable B593 Awapuni Rd
13460 | 27/08/2010 | 2010 | 2010-08-27 | 1963 | 93 | 22803 | C | ADVERSE WEATHER | Restrain 11kV lines poles E523 to E519 Tarndale Rd
13461 | 30/08/2010 | 2010 | 2010-08-30 | 103 | 18 | 1854 | C | ADVERSE WEATHER | Replace DDO fuses T/x G30 Paramata Rd Lightining
13462 | 30/08/2010 | 2010 | 2010-08-30 | 139 | 20 | 2780 | C | ADVERSE WEATHER | Replace DDO fuses T/x G89 Paroa Rd Lightining
13463 | 30/08/2010 | 2010 | 2010-08-30 | 27 | 176 | 4752 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W816 Ohuka
13464 | 30/08/2010 | 2010 | 2010-08-30 | 133 | 17 | 2261 | C | DEFECTIVE EQUIPMENT | Replace DDO T/x fuses H29 Mangahaine Valley
13551 | 01/09/2010 | 2010 | 2010-09-01 | 396 | 10 | 3960 | B | PLANNED SHUTDOWN | Replace poles D2835, D2836, D2837, D2853, D2856 BK Ormond Rd
13482 | 02/09/2010 | 2010 | 2010-09-02 | 233 | 26 | 3847 | C | DEFECTIVE EQUIPMENT | Repair jumper pole F660 Rakauroa Rd
13552 | 02/09/2010 | 2010 | 2010-09-02 | 436 | 88 | 18864 | B | PLANNED SHUTDOWN | Replace poles D2857, D2859, D2860, D2861 & remove line breaks at D2833 BK Ormond Rd
13556 | 02/09/2010 | 2010 | 2010-09-02 | 390 | 16 | 6240 | B | PLANNED SHUTDOWN | Issue assurance to Hop Saddlier for tree cutting Lake Rd Patutahi
13483 | 03/09/2010 | 2010 | 2010-09-03 | 93 | 41 | 3813 | C | ADVERSE ENVIRONMENT | Reposition pole A4210 Riverside Rd
13484 | 03/09/2010 | 2010 | 2010-09-03 | 29 | 78 | 2262 | C | DEFECTIVE EQUIPMENT | Replace 11kV disc pole G1758 Tauwhareparae Rd
13485 | 03/09/2010 | 2010 | 2000-09-03 | 382 | 272 | 21678 | C | TREE CONTACTS | Repair 11kV lines pole W22113 Mangone Valley
13486 | 04/09/2010 | 2010 | 2010-09-04 | 258 | 72 | 14791 | C | TREE CONTACTS | Tree through line at private pole D5471 - 2 x Broken Poles
13487 | 05/09/2010 | 2010 | 2010-09-05 | 129 | 353 | 37479 | C | UNKNOWN | Reclose CB J543 Tikitiki at Ruatoria Sub
13488 | 06/09/2010 | 2010 | 2010-09-06 | 124 | 10 | 1240 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole TX W675 Waireka Road
13489 | 06/09/2010 | 2010 | 2010-09-06 | 136 | 56 | 7616 | C | DEFECTIVE EQUIPMENT | Replace x-arm at Pole F2209 Te Wera Rd
13490 | 06/09/2010 | 2010 | 2010-09-06 | 341 | 53 | 12045 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole G2385 Puketawa STN, Tauwhareparae
13491 | 06/09/2010 | 2010 | 2010-09-06 | 62 | 852 | 45786 | C | TREE CONTACTS | Tree through line, wires down at pole C1779. Private No DDO's
13492 | 07/09/2010 | 2010 | 2010-09-07 | 123 | 31 | 3224 | C | DEFECTIVE EQUIPMENT | Cut jumpers at pole J3398, Tapuwharau Valley Replace pole J3399
13493 | 07/09/2010 | 2010 | 2010-09-07 | 9 | 46 | 782 | C | TREE CONTACTS | Cut 11kV jumpers at pole J804 old Waiapu metal supplies - line not in use
13494 | 07/09/2010 | 2010 | 2010-09-07 | 54 | 623 | 22638 | C | UNKNOWN | Unknown went back in not found. Reclose CBA612 Crawford Rd Port Sub
13553 | 07/09/2010 | 2010 | 2010-09-07 | 360 | 12 | 4320 | B | PLANNED SHUTDOWN | Replace poles D527, D2862, D2864, D2865, D2866 Bk Ormond Rd
13495 | 08/09/2010 | 2010 | 2010-09-08 | 464 | 6 | 2784 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole C4906 Browns Beach Rd
13554 | 09/09/2010 | 2010 | 2010-09-09 | 479 | 181 | 13482 | B | PLANNED SHUTDOWN | Replace poles D2869, D431 (ABS), D4409 Bk Ormond Rd & Harpers Rd
13562 | 09/09/2010 | 2010 | 2010-09-09 | 42 | 27 | 1863 | B | PLANNED SHUTDOWN | Replace 11 x poles D3249,D3250,D3251,D3252,D3253,D3254,D3255,D3256,D3257,D3258,D3259 Bushy knoll & Elmers Rd
13496 | 10/09/2010 | 2010 | 2010-09-10 | 68 | 7 | 476 | C | DEFECTIVE EQUIPMENT | Straighten 11kV pole C812 Tarewa Rd, Waingake
13497 | 10/09/2010 | 2010 | 2010-09-10 | 40 | 129 | 5160 | C | DEFECTIVE EQUIPMENT | Replace Disc with polymer at pole J2571 Dump Rd, Te Araroa
13498 | 12/09/2010 | 2010 | 2010-09-12 | 720 | 156 | 12639 | C | DEFECTIVE EQUIPMENT | Replace pole G1510 - Burnt top & xarm. Cut jumpers at G1513
13558 | 14/09/2010 | 2010 | 2010-09-14 | 218 | 23 | 5014 | B | PLANNED SHUTDOWN | Tree cutting between poles A152 & A782 Rototahi
13559 | 14/09/2010 | 2010 | 2010-09-14 | 386 | 63 | 24318 | B | PLANNED SHUTDOWN | Replace poles D2824, D2827, D2831 - BK Ormond Rd
13499 | 15/09/2010 | 2010 | 2010-09-15 | 184 | 7 | 1288 | C | DEFECTIVE EQUIPMENT | Address to low clearance 11kV span between poles F2094 & F2095 (install prop pole?)
13500 | 15/09/2010 | 2010 | 2010-09-15 | 65 | 25 | 1625 | C | DEFECTIVE EQUIPMENT | Replace xarm at pole W8535
13555 | 16/09/2010 | 2010 | 2010-09-16 | 121 | 27 | 3267 | B | PLANNED SHUTDOWN | Relocate poles C3539 & C3540 Nicks Head Stn Muriwai
13560 | 16/09/2010 | 2010 | 2010-09-16 | 400 | 27 | 8562 | B | PLANNED SHUTDOWN | Replace poles D4403, D4402, D4700, D4698 Harpers Road
13501 | 17/09/2010 | 2010 | 2010-09-17 | 198 | 136 | 25159 | C | ADVERSE WEATHER | Reclose CB W816 High Winds
13502 | 17/09/2010 | 2010 | 2010-09-17 | 227 | 46 | 7246 | C | TREE CONTACTS | Broken wire at D2663 - Tree
13503 | 17/09/2010 | 2010 | 2010-09-17 | 86 | 1456 | 35788 | C | DEFECTIVE EQUIPMENT | 11kV cable pothead failed at B1356
13504 | 17/09/2010 | 2010 | 2010-09-17 | 956 | 24 | 25716 | C | ADVERSE WEATHER | Repair 11kV lines at pole A3964 Wharekiri Rd
13505 | 17/09/2010 | 2010 | 2010-09-17 | 7 | 1105 | 1735 | C | ADVERSE WEATHER | Reclose CB C1 Hexton Hight winds cause unknown
13506 | 17/09/2010 | 2010 | 2010-09-17 | 1143 | 264 | 84652 | C | TREE CONTACTS | Fault Beyond ABS H142 Ihungia Road - H142 left open No access thru gate to pole & trees
13508 | 17/09/2010 | 2010 | 2010-09-17 | 229 | 438 | 98745 | C | TREE CONTACTS | Tree on line F3209
13511 | 17/09/2010 | 2010 | 2010-09-17 | 1350 | 54 | 54615 | C | TREE CONTACTS | Repair 11kV lines at pole H272 Tauwhareparae Rd
13565 | 17/09/2010 | 2010 | 2010-09-17 | 428 | 7 | 2996 | B | PLANNED SHUTDOWN | Replace poles C804, C812 Tewera Rd & private poles in Damn Rd
13507 | 18/09/2010 | 2010 | 2010-09-18 | 119 | 24 | 2856 | C | FOREIGN INTERFERENCE | Remove plastic off lines at pole D605
13509 | 18/09/2010 | 2010 | 2010-09-18 | 568 | 38 | 14308 | C | TREE CONTACTS | Repair 11kV lines at poles J2022 & J2023
13510 | 18/09/2010 | 2010 | 2010-09-18 | 26 | 31 | 806 | C | DEFECTIVE EQUIPMENT | 11kV jumper off G1252 cnr Banks & Solanders St
13512 | 18/09/2010 | 2010 | 2010-09-18 | 408 | 136 | 53102 | C | UNKNOWN | Cause not found - Wind, trees, uneven spans?
13513 | 18/09/2010 | 2010 | 2010-09-18 | 88 | 183 | 5958 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines H650 Ihungia Rd
13514 | 18/09/2010 | 2010 | 2010-09-18 | 26 | 193 | 2123 | C | UNKNOWN | Fault not found - strong winds at time
13515 | 18/09/2010 | 2010 | 2010-09-18 | 95 | 15 | 1425 | C | ADVERSE WEATHER | Prop up pole F1790
13516 | 18/09/2010 | 2010 | 2010-09-18 | 349 | 40 | 17101 | C | DEFECTIVE EQUIPMENT | Repair 11kV pole H230 Makarika Rd
13517 | 18/09/2010 | 2010 | 2010-09-18 | 38 | 178 | 5124 | C | ADVERSE WEATHER | 2 wires down tap off to H58. Cut away and left
13518 | 18/09/2010 | 2010 | 2010-09-18 | 170 | 176 | 18838 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper W816 & Wires at W1802
13519 | 18/09/2010 | 2010 | 2010-09-18 | 24 | 88 | 2112 | C | TREE CONTACTS | Tree thru line beyond D298. Isolate 11kV fuses
13543 | 18/09/2010 | 2010 | 2010-09-18 | 1241 | 43 | 6054 | C | ADVERSE WEATHER | Repair broken wire between H134 & H340
13567 | 18/09/2010 | 2010 | 2010-09-18 | 1143 | 4 | 4572 | C | TREE CONTACTS | Remove tree from 11kV Lines H142
13520 | 19/09/2010 | 2010 | 2010-09-19 | 149 | 26 | 3874 | C | TREE CONTACTS | Tree in line F652 - Need to be cut
13521 | 19/09/2010 | 2010 | 2010-09-19 | 1086 | 39 | 39939 | C | TREE CONTACTS | Cut Jumpers at pole J1966 due to trees in line J1966, JH1965, J667 & wires down
13522 | 19/09/2010 | 2010 | 2010-09-19 | 870 | 225 | 88105 | C | DEFECTIVE EQUIPMENT | Pole W5380 wires down
13523 | 19/09/2010 | 2010 | 2010-09-19 | 9 | 140 | 1260 | C | TREE CONTACTS | Tree contact on OH lines between TXs B3127 & B77. Blown OFS Fuses B760
13524 | 19/09/2010 | 2010 | 2010-09-19 | 534 | 131 | 26572 | C | TREE CONTACTS | Tree Through lines poles H649 - H650
13525 | 19/09/2010 | 2010 | 2010-09-19 | 87 | 38 | 3306 | C | DEFECTIVE EQUIPMENT | Replaced pole J951
13526 | 20/09/2010 | 2010 | 2010-09-20 | 365 | 4 | 1460 | C | TREE CONTACTS | Trees brought lines down G2280
13527 | 20/09/2010 | 2010 | 2010-09-20 | 233 | 12 | 2796 | C | TREE CONTACTS | Repair 11kV wires at G585
13528 | 20/09/2010 | 2010 | 2010-09-20 | 47 | 31 | 1457 | C | DEFECTIVE EQUIPMENT | Broken aerial jumper and line down at pole G1221
13529 | 20/09/2010 | 2010 | 2010-09-20 | 952 | 75 | 25385 | C | TREE CONTACTS | Wire down caused by trees(again) in wind at pole H3362
13530 | 20/09/2010 | 2010 | 2010-09-20 | 154 | 161 | 17325 | C | ADVERSE WEATHER | Wire down beyond G214
13531 | 20/09/2010 | 2010 | 2010-09-20 | 1700 | 6 | 10200 | C | ADVERSE WEATHER | Isolate and replace broken pole G1344
13532 | 20/09/2010 | 2010 | 2010-09-20 | 898 | 94 | 35374 | C | TREE CONTACTS | Trees caused 2 x spans down and broken xarm at TX pole J417
13533 | 20/09/2010 | 2010 | 2010-09-20 | 134 | 43 | 4774 | C | DEFECTIVE EQUIPMENT | Replace pole H2320 Te Puia
13534 | 20/09/2010 | 2010 | 2010-09-20 | 69 | 34 | 2346 | C | ADVERSE ENVIRONMENT | 11kV wire broken between double pins on tap-off pole to TX J322
13535 | 20/09/2010 | 2010 | 2010-09-20 | 1243 | 21 | 9571 | C | ADVERSE WEATHER | Repairs to wire & pole at J1610 (after multi cut/join jumpers on pole J1604
13566 | 20/09/2010 | 2010 | 2010-09-20 | 748 | 93 | 95468 | C | ADVERSE WEATHER | Replace pole E741 Riki Stn
13536 | 21/09/2010 | 2010 | 2010-09-21 | 248 | 20 | 4960 | C | DEFECTIVE EQUIPMENT | Replace pole G2160 Paroa Rd
13537 | 21/09/2010 | 2010 | 2010-09-21 | 243 | 12 | 2916 | C | TREE CONTACTS | O/Le Tag J188 Fault beyond
13538 | 21/09/2010 | 2010 | 2010-09-21 | 54 | 4 | 216 | C | DEFECTIVE EQUIPMENT | Cut 11kV jumpers at J790, broken 11kV lines
13561 | 21/09/2010 | 2010 | 2010-09-21 | 269 | 20 | 5380 | B | PLANNED SHUTDOWN | Replace poles D4693, D4695, D430, D4696, D4697 Harpers Road
13539 | 22/09/2010 | 2010 | 2010-09-22 | 38 | 17 | 646 | C | ADVERSE WEATHER | Rejoin jumpers after repairs at pole W486
13540 | 22/09/2010 | 2010 | 2010-09-22 | 227 | 9 | 2043 | C | ADVERSE WEATHER | Broken wires between poles E2228 - E414
13541 | 23/09/2010 | 2010 | 2010-09-23 | 4496 | 30 | 67540 | C | DEFECTIVE EQUIPMENT | Wire burnt down outside Wairoa sub on Golf course W216
13542 | 23/09/2010 | 2010 | 2010-09-23 | 210 | 96 | 19015 | C | TREE CONTACTS | Tree on line at pole A1956
13544 | 23/09/2010 | 2010 | 2010-09-23 | 83 | 14 | 1162 | C | ADVERSE WEATHER | Rejoin jumpers at pole H2039 SH35
13545 | 23/09/2010 | 2010 | 2010-09-23 | 245 | 208 | 10941 | C | DEFECTIVE EQUIPMENT | 1 lug H pole G4287 burnt & repair (used cut jumpers at pole G1102
13546 | 23/09/2010 | 2010 | 2010-09-23 | 289 | 60 | 14194 | C | ADVERSE WEATHER | Wire down at pole A3967 (cut and rejoined jumpers at A3961)
13547 | 24/09/2010 | 2010 | 2010-09-24 | 70 | 12 | 840 | C | DEFECTIVE EQUIPMENT | Repair floating insulator at pole G1553 Kiore Rd
13548 | 26/09/2010 | 2010 | 2010-09-26 | 243 | 95 | 5929 | C | ADVERSE WEATHER | Line down at pole J2419
13557 | 27/09/2010 | 2010 | 2010-09-27 | 415 | 12 | 4980 | B | PLANNED SHUTDOWN | Isolate & Remove lines for tree cutting (Eastland Treecare) W337 - W338 Karkariki/Woodland
13563 | 28/09/2010 | 2010 | 2010-09-28 | 367 | 10 | 3670 | B | PLANNED SHUTDOWN | Replace poles D4673, D4668, D4666, D427 Harpers Rd
13549 | 29/09/2010 | 2010 | 2010-09-29 | 350 | 11 | 3850 | C | TREE CONTACTS | Isolate for Hop to cut trees. Customers advised individually - G3353
13550 | 29/09/2010 | 2010 | 2010-09-29 | 115 | 187 | 10647 | C | DEFECTIVE EQUIPMENT | Rejoin cable-line jumpers at pole B1356
13564 | 30/09/2010 | 2010 | 2010-09-30 | 417 | 7 | 2919 | B | PLANNED SHUTDOWN | Replace poles D4663,D4662,D4661,D4659,D4658,D4657 Harpers Rd
13568 | 30/09/2010 | 2010 | 2010-09-30 | 470 | 34 | 15342 | B | PLANNED SHUTDOWN | Replace Poles D4002,D4004,D4006,D5243,D4009,D5244,D4011,D4013,D4014 Wharekopae Rd & cut jumpers at D4016
13569 | 01/10/2010 | 2010 | 2010-10-01 | 142 | 73 | 7097 | C | DEFECTIVE EQUIPMENT | Replace disc on pole H4459 Fernside Rd
13570 | 05/10/2010 | 2010 | 2010-10-05 | 151 | 152 | 9357 | C | DEFECTIVE EQUIPMENT | Repair 11kV line Pole W8118 Whakaki
13571 | 06/10/2010 | 2010 | 2010-10-06 | 91 | 143 | 13552 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper ABS pole A4116 Kaiti Hill
13613 | 06/10/2010 | 2010 | 2010-10-06 | 221 | 136 | 30056 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting H314 to H2568 Toa St
13573 | 11/10/2010 | 2010 | 2010-10-11 | 34 | 422 | 9978 | C | TREE CONTACTS | Repair 11kV lines pole E1586 Lavenham Rd
13574 | 11/10/2010 | 2010 | 2010-10-11 | 252 | 77 | 19404 | C | TREE CONTACTS | Patrol lines beyond E863 Tarndale Rd
13575 | 11/10/2010 | 2010 | 2010-10-11 | 47 | 8 | 376 | C | DEFECTIVE EQUIPMENT | Replace 11kV line jumper pole F164 Makaretu Rd
13576 | 11/10/2010 | 2010 | 2010-10-11 | 312 | 730 | 149224 | C | TREE CONTACTS | Repair 11kV lines pole W4240 Frasertown
13577 | 11/10/2010 | 2010 | 2010-10-11 | 50 | 489 | 28888 | C | DEFECTIVE EQUIPMENT | Replace 11kV links pole A6477 Crawford Rd
13579 | 11/10/2010 | 2010 | 2010-10-11 | 383 | 31 | 9593 | C | DEFECTIVE EQUIPMENT | Replace broken Xarm pole A3759 Panikau Rd
13580 | 11/10/2010 | 2010 | 2010-10-11 | 26 | 74 | 1924 | C | DEFECTIVE EQUIPMENT | Temp prop broken pole F1919 Matawai Rd
13572 | 12/10/2010 | 2010 | 2010-10-12 | 1352 | 128 | 21979 | C | TREE CONTACTS | Repair 11kV lines pole W1012 Eripiti
13578 | 12/10/2010 | 2010 | 2010-10-12 | 64 | 184 | 12381 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J946 Tikitiki
13581 | 12/10/2010 | 2010 | 2010-10-12 | 19 | 1117 | 15277 | C | DEFECTIVE EQUIPMENT | Replace 33kV pole W3800 Tahaenui
13582 | 12/10/2010 | 2010 | 2010-10-12 | 19 | 67 | 1273 | C | DEFECTIVE EQUIPMENT | Reposition Xam on pole D4569 SH2 W/O Hika
13583 | 12/10/2010 | 2010 | 2010-10-12 | 347 | 884 | 276223 | C | DEFECTIVE EQUIPMENT | Replace insulator pole B4867 Russell St
13584 | 12/10/2010 | 2010 | 2010-10-12 | 1094 | 191 | 40168 | C | TREE CONTACTS | Repair 11kv pole H48 Mangahauine Valley
13585 | 12/10/2010 | 2010 | 2010-10-12 | 1634 | 104 | 47450 | C | ADVERSE WEATHER | Repair 11kV lines pole J4452 SH2 Hicks Bay
13586 | 12/10/2010 | 2010 | 2010-10-12 | 131 | 93 | 4623 | C | ADVERSE WEATHER | Reclose CB E863 Whatatutu cause unknown
13587 | 13/10/2010 | 2010 | 2010-10-13 | 138 | 141 | 9203 | C | TREE CONTACTS | Repair 11kV pole D3892 Tiniroto Rd
13589 | 13/10/2010 | 2010 | 2010-10-13 | 1408 | 8 | 11264 | C | ADVERSE WEATHER | Repair 11kV lines pole J449 Matakoa Point
13590 | 13/10/2010 | 2010 | 2010-10-13 | 245 | 50 | 8650 | C | TREE CONTACTS | Repair 11kV lines pole C786 Waingake Rd
13591 | 13/10/2010 | 2010 | 2010-10-13 | 58 | 15 | 870 | C | ADVERSE WEATHER | Disconnect Generator pole F202 Rakauroa Rd
13588 | 14/10/2010 | 2010 | 2010-10-14 | 1197 | 54 | 58587 | C | TREE CONTACTS | Temp replace pole G2345 Tauwhareparae Rd
13592 | 14/10/2010 | 2010 | 2010-10-14 | 74 | 20 | 1320 | C | DEFECTIVE EQUIPMENT | Replace pole G2157 Paroa Rd
13593 | 14/10/2010 | 2010 | 2010-10-14 | 186 | 71 | 5758 | C | DEFECTIVE EQUIPMENT | Replace kidney insulator pole D62 Totangi Rd
13594 | 14/10/2010 | 2010 | 2010-10-14 | 194 | 218 | 18177 | C | ADVERSE ENVIRONMENT | Relocate 11kV pole C2823 Waingake Rd drop out in river bank
13595 | 14/10/2010 | 2010 | 2010-10-14 | 597 | 5 | 2985 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J4230 Haig Rd Tikitiki
13596 | 14/10/2010 | 2010 | 2010-10-14 | 247 | 1122 | 86499 | C | ADVERSE ENVIRONMENT | Reposition pole B1145 Hill Rd Slip
13597 | 14/10/2010 | 2010 | 2010-10-14 | 39 | 2521 | 98319 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
13598 | 14/10/2010 | 2010 | 2010-10-14 | 983 | 369 | 27039 | C | TREE CONTACTS | Repair 11kV lines beyond pole W71 Cricklewood Rd
13599 | 15/10/2010 | 2010 | 2010-10-15 | 312 | 93 | 16325 | C | TREE CONTACTS | Repair 11kV lines Pole D3636 Ruakaka Rd
13600 | 15/10/2010 | 2010 | 2010-10-15 | 60 | 57 | 3420 | C | ADVERSE ENVIRONMENT | Reposition poles B1146 B1147 B1148 Hill Rd
13601 | 16/10/2010 | 2010 | 2010-10-16 | 675 | 369 | 132054 | C | TREE CONTACTS | Repair 11kV lines W6414 Waihua
13602 | 18/10/2010 | 2010 | 2010-10-18 | 321 | 5 | 1605 | C | ADVERSE WEATHER | Repair 11kV lines J2431 to J2432 Haig Rd
13603 | 18/10/2010 | 2010 | 2010-10-18 | 48 | 490 | 14380 | C | TREE CONTACTS | Remove tree pole A208 Caves Rd
13604 | 19/10/2010 | 2010 | 2010-10-19 | 173 | 60 | 10380 | C | ADVERSE ENVIRONMENT | Relocate pole C2903 Waingake Rd
13605 | 21/10/2010 | 2010 | 2010-10-21 | 10 | 1117 | 11170 | C | UNKNOWN | Reclose CBs W2 & W1032 Wairoa Sub cause unknown
13615 | 21/10/2010 | 2010 | 2010-10-21 | 291 | 20 | 5820 | B | PLANNED SHUTDOWN | Replace poles D2862 & D2863 Bck Ormond Rd
13606 | 22/10/2010 | 2010 | 2010-10-22 | 39 | 510 | 19890 | C | DEFECTIVE EQUIPMENT | Bridge out ABS W979 Tiniroto Rd
13607 | 22/10/2010 | 2010 | 2010-10-22 | 49 | 248 | 5805 | C | TREE CONTACTS | Remove tree branch pole G70 SH35 Wharekaka
13616 | 22/10/2010 | 2010 | 2010-10-22 | 418 | 78 | 7328 | B | PLANNED SHUTDOWN | Replace poles D601 & D3114 Matawai Rd
13608 | 23/10/2010 | 2010 | 2010-10-23 | 42 | 260 | 11530 | C | DEFECTIVE EQUIPMENT | Replace burnt down pole J4535 Hicks Bay
13609 | 24/10/2010 | 2010 | 2010-10-24 | 21 | 210 | 4410 | C | UNKNOWN | Reclose CB G329 Rototahi at Tolaga Sub cause unknown
13610 | 24/10/2010 | 2010 | 2010-10-24 | 373 | 130 | 48490 | C | FOREIGN INTERFERENCE | Replace T/x A405 Endcliffe Rd hit by Car
13611 | 26/10/2010 | 2010 | 2010-10-26 | 32 | 225 | 7200 | C | DEFECTIVE EQUIPMENT | Replace burnt pole & rejoin jumpers J512 Hicks Bay
13612 | 26/10/2010 | 2010 | 2010-10-26 | 84 | 47 | 3948 | C | DEFECTIVE EQUIPMENT | Replace X arm pole H1768 Ruatoria South
13614 | 27/10/2010 | 2010 | 2010-10-27 | 18 | 52 | 936 | B | PLANNED SHUTDOWN | Install 3 DDO fuses pole G4128 Waiapu Rd
13617 | 01/11/2010 | 2010 | 2010-01-01 | 155 | 7 | 1085 | C | TREE CONTACTS | Isolate 11kV for LV Repairs pole A365 Wharekiri Rd
13636 | 01/11/2010 | 2010 | 2010-11-01 | 491 | 74 | 46200 | B | PLANNED SHUTDOWN | Replace 11kV poles F179 F180 F621 F625 Rakauroa Rd
13638 | 01/11/2010 | 2010 | 2010-11-01 | 381 | 3 | 1143 | B | PLANNED SHUTDOWN | Remove 2 spans 11kV lines from pole H306 Busbys Hill
13639 | 03/11/2010 | 2010 | 2010-11-03 | 357 | 12 | 4284 | B | PLANNED SHUTDOWN | Replace 11kV poles D4691 D4690 D4688 D4686 Harpers Rd
13637 | 04/11/2010 | 2010 | 2010-11-04 | 381 | 10 | 3810 | B | PLANNED SHUTDOWN | Replace 11kV poles D4654 D4656 E4657 E4658 E4665 E4673 Harpers Rd
13640 | 08/11/2010 | 2010 | 2010-11-08 | 86 | 65 | 5590 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting E2453 Lavenham Rd
13641 | 08/11/2010 | 2010 | 2010-11-08 | 50 | 6 | 300 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Ceasars Rd pole E2550
13642 | 09/11/2010 | 2010 | 2001-11-09 | 307 | 58 | 17806 | B | PLANNED SHUTDOWN | Replace 11kV poles W7702 W7721 W7815 W7820 W7834 W7855 W7888 Iwitea Whakakihi
13644 | 09/11/2010 | 2010 | 2010-11-09 | 167 | 34 | 5678 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Mata Rd H135
13643 | 10/11/2010 | 2010 | 2010-11-10 | 434 | 57 | 24738 | B | PLANNED SHUTDOWN | Install new ABS W1021 & remove ABSs W940 W948 & W1030 Mc Lean St
13618 | 11/11/2010 | 2010 | 2010-11-11 | 117 | 17 | 1989 | C | ADVERSE ENVIRONMENT | Install prop pole Between W5028 to W5029 Waireka Rd
13645 | 12/11/2010 | 2010 | 2010-11-12 | 357 | 12 | 4284 | B | PLANNED SHUTDOWN | Replace 11kV poles D532 D4686 D4688 Harpers Rd
13619 | 13/11/2010 | 2010 | 2010-11-13 | 151 | 90 | 4947 | C | TREE CONTACTS | Repair 11kV lines between poles E1736 to E3450 Moonlight Stn
13620 | 13/11/2010 | 2010 | 2010-11-13 | 18 | 47 | 846 | C | DEFECTIVE EQUIPMENT | Replace T/x H255 & 3 DDO fuses Makatoke Rd
13621 | 14/11/2010 | 2010 | 2010-11-14 | 39 | 994 | 38766 | C | UNKNOWN | Reclose CB C95 Haisman Rd cause unknown
13622 | 15/11/2010 | 2010 | 2010-11-15 | 296 | 36 | 6616 | C | ADVERSE ENVIRONMENT | Reposition H pole J2803 due to river diversion Awatere
13646 | 15/11/2010 | 2010 | 2010-11-15 | 452 | 44 | 10213 | B | PLANNED SHUTDOWN | Replace 11kV poles D4017 D4019 D4020 D4023 D4024 D4025 D4026 Wharekopae Rd
13623 | 16/11/2010 | 2010 | 2010-11-16 | 72 | 803 | 57816 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable W271 to W1069 Clyde Rd
13648 | 16/11/2010 | 2010 | 2010-11-16 | 408 | 53 | 15600 | B | PLANNED SHUTDOWN | Replace pole D3248 Bushy Knoll Rd
13635 | 17/11/2010 | 2010 | 2010-11-17 | 33 | 10 | 570 | B | PLANNED SHUTDOWN | Install 11kV cable & T/x A894 Wheatstone Rd
13624 | 18/11/2010 | 2010 | 2010-11-18 | 379 | 11 | 4169 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H2220 Waipiro Bay
13625 | 19/11/2010 | 2010 | 2010-11-19 | 171 | 31 | 5301 | C | DEFECTIVE EQUIPMENT | Replace poles A3964 & A3965 Wharekiri Rd
13626 | 19/11/2010 | 2010 | 2010-11-19 | 23 | 9 | 207 | C | DEFECTIVE EQUIPMENT | Replace insulator pole A4032 Waiomoko Rd
13649 | 19/11/2010 | 2010 | 2010-11-19 | 421 | 11 | 4631 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Pakawhai & Ramoto Rds W1132
13627 | 20/11/2010 | 2010 | 2010-11-20 | 222 | 129 | 28531 | C | DEFECTIVE EQUIPMENT | Replace insulators pole J272 Te Araroa
13628 | 20/11/2010 | 2010 | 2010-11-20 | 251 | 94 | 9236 | C | DEFECTIVE EQUIPMENT | Repair 11kv pole J2966 Whakaangiangi
13629 | 21/11/2010 | 2010 | 2010-11-21 | 163 | 1325 | 77459 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable crutch pole C738 Nelson Rd
13630 | 21/11/2010 | 2010 | 2010-11-21 | 262 | 21 | 5502 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J1589 Tuparoa Rd
13631 | 21/11/2010 | 2010 | 2010-11-21 | 196 | 142 | 11337 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole W8163 Tahaenui hit by car
13632 | 23/11/2010 | 2010 | 2010-11-23 | 41 | 60 | 2460 | C | DEFECTIVE EQUIPMENT | Reconnect jumpers pole C3245 Nelson Rd after repairs
13651 | 23/11/2010 | 2010 | 2010-11-23 | 386 | 12 | 4632 | B | PLANNED SHUTDOWN | Replace 11kV poles D4680 D532 D4689 Harpers Rd
13652 | 24/11/2010 | 2010 | 2010-11-24 | 169 | 150 | 25350 | B | PLANNED SHUTDOWN | Replace 11kV pole J2079 Rangitukia Rd
13653 | 25/11/2010 | 2010 | 2010-11-25 | 405 | 42 | 17010 | B | PLANNED SHUTDOWN | Replace 11kV poles D3579 D3581 Ruakaka Rd
13633 | 28/11/2010 | 2010 | 2010-11-28 | 19 | 803 | 7432 | C | DEFECTIVE EQUIPMENT | Replace fuse S/W G/R W279 Mc Lean St
13650 | 28/11/2010 | 2010 | 2010-11-28 | 362 | 35 | 12670 | B | PLANNED SHUTDOWN | Replace 11kV poles B3697 B3699 B617 Disralie St
13634 | 29/11/2010 | 2010 | 2010-11-29 | 119 | 66 | 4389 | C | TREE CONTACTS | Remove tree from 11kV between poles H2227 to H2226 Waipiro Bay
13647 | 29/11/2010 | 2010 | 2010-11-29 | 250 | 33 | 8250 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting F417 Whakarau Rd
13654 | 01/12/2010 | 2010 | 2010-12-01 | 204 | 170 | 7530 | C | TREE CONTACTS | Remove tree from 11kV pole A4502 Turihau
13687 | 01/12/2010 | 2010 | 2010-12-01 | 420 | 32 | 13440 | B | PLANNED SHUTDOWN | Replace 11kV poles D3559 D3594 D3595 D3599 Ruakaka Rd
13655 | 02/12/2010 | 2010 | 2010-12-02 | 21 | 15 | 315 | C | TREE CONTACTS | Isolate 11kV lines for tree cutting H351 to H4013 Kaiawha Rd
13686 | 02/12/2010 | 2010 | 2010-12-02 | 443 | 29 | 12847 | B | PLANNED SHUTDOWN | Replace 11kV poles D3248 D3249 D3250 Bushy Knoll Rd
13691 | 03/12/2010 | 2010 | 2010-12-03 | 324 | 41 | 4862 | B | PLANNED SHUTDOWN | Replace H pole G4287 Tolaga Bay
13657 | 06/12/2010 | 2010 | 2010-12-06 | 227 | 44 | 9988 | C | DEFECTIVE EQUIPMENT | Replace 3 DDO fuses pole D302 Tiniroto
13658 | 06/12/2010 | 2010 | 2010-12-06 | 14 | 994 | 13916 | C | UNKNOWN | Reclose CBC95 Haisman Rd at Makaraka Sub
13684 | 06/12/2010 | 2010 | 2010-12-06 | 30 | 26 | 1508 | B | PLANNED SHUTDOWN | Isolate 11kV lines pole H2353 for tree cutting SH35 Waiapu Rd
13690 | 06/12/2010 | 2010 | 2010-12-06 | 39 | 46 | 1794 | B | PLANNED SHUTDOWN | Remove isolation fuses C757 Waingake Rd
13692 | 06/12/2010 | 2010 | 2010-12-06 | 358 | 60 | 21480 | B | PLANNED SHUTDOWN | Replace 11kV poles D2764 & D2768 Ngatapa
13693 | 07/12/2010 | 2010 | 2010-12-07 | 300 | 127 | 19812 | B | PLANNED SHUTDOWN | Replace 11kV pole J272 Te Araroa
13659 | 08/12/2010 | 2010 | 2010-12-08 | 223 | 62 | 15869 | C | FOREIGN INTERFERENCE | Remove possum from pole A3989 Panikau Rd
13660 | 08/12/2010 | 2010 | 2010-12-08 | 30 | 631 | 18930 | C | UNKNOWN | Reclose CB W213 Brickworks at Kiwi Sub
13689 | 08/12/2010 | 2010 | 2010-12-08 | 420 | 11 | 4620 | B | PLANNED SHUTDOWN | Install DDOs pole A4734 Wheatstone Rd
13694 | 08/12/2010 | 2010 | 2010-12-08 | 280 | 74 | 20720 | B | PLANNED SHUTDOWN | Replace 11kV poles F1919 & F1920 Matawai
13661 | 09/12/2010 | 2010 | 2010-12-09 | 194 | 152 | 8013 | C | FOREIGN INTERFERENCE | Repair 11kV lines W8286 to W8285 Ohue Whakakihi
13662 | 09/12/2010 | 2010 | 2010-12-09 | 43 | 49 | 2107 | C | DEFECTIVE EQUIPMENT | Replace shackle on pole J802 Ruatoria
13695 | 09/12/2010 | 2010 | 2010-12-09 | 118 | 15 | 1770 | B | PLANNED SHUTDOWN | Replace 11kV pole F1790 Whakarau Rd
13696 | 09/12/2010 | 2010 | 2010-12-09 | 127 | 12 | 1524 | B | PLANNED SHUTDOWN | Replace 11kV poles D4698 D4690 D4691 Harpers Rd
13663 | 10/12/2010 | 2010 | 2010-12-10 | 148 | 194 | 16199 | C | TREE CONTACTS | Repair 11kV lines pole E122 to E610 Kanakanaia
13664 | 11/12/2010 | 2010 | 2010-12-11 | 485 | 216 | 33169 | C | DEFECTIVE EQUIPMENT | Replace insulator pole W4789 Ruapapa Rd
13665 | 13/12/2010 | 2010 | 2010-12-13 | 69 | 41 | 2829 | C | DEFECTIVE EQUIPMENT | Repair ABS W802 Whakakihi
13666 | 13/12/2010 | 2010 | 2010-12-13 | 53 | 175 | 9275 | C | TREE CONTACTS | Remove burning tree pole W1019 Raupunga
13688 | 13/12/2010 | 2010 | 2010-12-13 | 145 | 13 | 1885 | B | PLANNED SHUTDOWN | Replace T/x A436 Waihau Beach Rd
13702 | 13/12/2010 | 2010 | 2010-12-13 | 491 | 13 | 42484 | B | PLANNED SHUTDOWN | Replace 11kV poles D3659 & T/x D268 Bushy Knoll Rd
13667 | 15/12/2010 | 2010 | 2010-12-15 | 156 | 729 | 58402 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable termination pole A397 Oneroa Rd
13685 | 18/12/2010 | 2010 | 2010-12-18 | 393 | 106 | 11858 | B | PLANNED SHUTDOWN | Replace 6 11kV poles D4653 to D409 Harpers Rd
13699 | 18/12/2010 | 2010 | 2010-12-18 | 125 | 65 | 8125 | B | PLANNED SHUTDOWN | Isolate 11kv lines pole E122 Kanakanaia Rd
13668 | 19/12/2010 | 2010 | 2010-12-19 | 136 | 86 | 4754 | C | DEFECTIVE EQUIPMENT | Replace bolt on Xarm pole W3604 Waihi Rd
13669 | 20/12/2010 | 2010 | 2010-12-20 | 746 | 76 | 56696 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole W6083 Mangapoikie Rd
13697 | 21/12/2010 | 2010 | 2010-12-21 | 372 | 66 | 24552 | B | PLANNED SHUTDOWN | Relocate T/x B453 Polytech Stout St
13698 | 22/12/2010 | 2010 | 2010-12-22 | 422 | 62 | 22912 | B | PLANNED SHUTDOWN | Replace 11kV poles F3457 E3459 E3458 Te Karaka
13701 | 23/12/2010 | 2010 | 2010-12-23 | 110 | 24 | 2640 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting O Gradys Rd D4601
13670 | 24/12/2010 | 2010 | 2010-12-24 | 268 | 433 | 35716 | C | TREE CONTACTS | Repair 11kV lines pole W6083 Mangapoikie Rd
13671 | 25/12/2010 | 2010 | 2010-12-25 | 1181 | 79 | 23620 | C | TREE CONTACTS | Repair 11kV lines pole G1495 Anaura Bay
13672 | 28/12/2010 | 2010 | 2010-12-28 | 25 | 242 | 5418 | C | ADVERSE WEATHER | Reclose CB D642 Te Arai at Patutahi Sub
13673 | 28/12/2010 | 2010 | 2010-12-28 | 201 | 72 | 14472 | C | ADVERSE WEATHER | Repair 11kV lines pole W5319 Raupunga
13674 | 28/12/2010 | 2010 | 2010-12-28 | 217 | 124 | 15769 | C | TREE CONTACTS | Remove tree kV lines Pole H74 Makarika Rd
13675 | 28/12/2010 | 2010 | 2010-12-28 | 319 | 328 | 11937 | C | TREE CONTACTS | Remove tree from pole J971 Waiomatatini
13676 | 28/12/2010 | 2010 | 2010-12-28 | 214 | 439 | 19714 | C | TREE CONTACTS | Remove tree from 11kV pole A4310 Goodwins Rd
13677 | 28/12/2010 | 2010 | 2010-12-28 | 23 | 51 | 1173 | C | DEFECTIVE EQUIPMENT | Replace 11kV DDO pole E99 Pointers Lane
13678 | 28/12/2010 | 2010 | 2010-12-28 | 266 | 49 | 6786 | C | TREE CONTACTS | Isolate 11kV lines beyond pole H4118 Waitahaia Rd
13679 | 28/12/2010 | 2010 | 2010-12-28 | 78 | 72 | 1716 | C | TREE CONTACTS | Cut 11kV jumpers pole D1312 Totangi Rd trees in line
13680 | 29/12/2010 | 2010 | 2010-12-29 | 48 | 19 | 912 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J258 Te Hue
13681 | 29/12/2010 | 2010 | 2010-12-29 | 34 | 10 | 340 | C | DEFECTIVE EQUIPMENT | Repair 11kV conductor pole W587 Mangone Rd
13682 | 30/12/2010 | 2010 | 2010-12-30 | 67 | 81 | 5994 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable pole B962 Aberdeen Rd
13700 | 30/12/2010 | 2010 | 2010-12-30 | 55 | 10 | 550 | B | PLANNED SHUTDOWN | Install DDO fuses pole C4982 7 replace pole C4654 Nelson Rd
13725 | 04/01/2011 | 2010 | 2011-01-04 | 198 | 96 | 9042 | C | FOREIGN INTERFERENCE | Repair 11kV pole E1153 Waimata Valley Rd
13726 | 06/01/2011 | 2010 | 2011-01-06 | 30 | 23 | 690 | B | PLANNED SHUTDOWN | Repair Conductor pole J971 Kakariki Rd
13727 | 07/01/2011 | 2010 | 2011-01-07 | 40 | 22 | 880 | B | PLANNED SHUTDOWN | Replace DDO fuses D62 Totangi Rd
13703 | 08/01/2011 | 2010 | 2011-01-08 | 18 | 907 | 16326 | C | UNKNOWN | Reclose CB C95 Haisman Rd at Makaraka Sub cause unknown
13704 | 10/01/2011 | 2010 | 2011-01-10 | 1085 | 21 | 22785 | C | TREE CONTACTS | Remove trees from 11kV lines pole W311 Tukemokihi
13705 | 10/01/2011 | 2010 | 2011-01-10 | 60 | 55 | 3300 | C | DEFECTIVE EQUIPMENT | Replace pole W752 Mangapoikie Rd
13706 | 10/01/2011 | 2010 | 2011-01-10 | 849 | 159 | 34487 | C | DEFECTIVE EQUIPMENT | Temp repair ABS J616 Hicks Bay
13707 | 12/01/2011 | 2010 | 2011-01-12 | 11 | 258 | 4956 | C | UNKNOWN | Reclose CB J523 Hicks Bay at Te Araroa Sub cause unknown
13708 | 13/01/2011 | 2010 | 2011-01-13 | 72 | 223 | 16056 | C | DEFECTIVE EQUIPMENT | Replace faulty ABS J616 Hicks Bay Rd
13737 | 13/01/2011 | 2010 | 2011-01-13 | 416 | 30 | 24180 | B | PLANNED SHUTDOWN | Replace poles D3597 D2599 D3601 Ruakaka Rd
13736 | 18/01/2011 | 2010 | 2011-01-18 | 442 | 91 | 18231 | B | PLANNED SHUTDOWN | Cut & Rejoin jumpers pole B1145 Hill Rd for contractor
13709 | 19/01/2011 | 2010 | 2011-01-19 | 62 | 11 | 682 | C | TREE CONTACTS | Repair 11kV lines pole W8389 Morere
13732 | 19/01/2011 | 2010 | 2011-01-19 | 458 | 13 | 16965 | B | PLANNED SHUTDOWN | Replace poles between D3659 to D268 Bushy Knoll Rd
13710 | 20/01/2011 | 2010 | 2011-01-20 | 175 | 145 | 5554 | C | TREE CONTACTS | Repair 11kV lines between poles W5584 to W5586 Kahungungu
13735 | 20/01/2011 | 2010 | 2011-01-20 | 375 | 32 | 5664 | B | PLANNED SHUTDOWN | Replace poles D3627 D3625 D3621 D3629 Ruakaka Rd
13711 | 21/01/2011 | 2010 | 2011-01-21 | 107 | 272 | 10345 | C | DEFECTIVE EQUIPMENT | Replace crook insulator pole W8707 Nuhaka
13733 | 21/01/2011 | 2010 | 2011-01-21 | 725 | 490 | 7671 | C | TREE CONTACTS | Remove tree 11kv pole B1991 Matokitoki Valley
13734 | 22/01/2011 | 2010 | 2011-01-22 | 313 | 14 | 4382 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole B1991 Matokitoki Valley
13712 | 23/01/2011 | 2010 | 2011-01-23 | 723 | 252 | 16251 | C | TREE CONTACTS | Repair 11kV lines pole W4454 Pokopoko
13713 | 23/01/2011 | 2010 | 2011-01-23 | 1282 | 93 | 7335 | C | TREE CONTACTS | Repair 11kV lines pole E1736 to E3450 Mangatu Rd
13714 | 24/01/2011 | 2010 | 2011-01-24 | 73 | 9 | 657 | C | DEFECTIVE EQUIPMENT | Reposition Xarm on pole W3640 Pokopoko
13715 | 24/01/2011 | 2010 | 2011-01-24 | 313 | 17 | 5321 | C | ADVERSE WEATHER | Reposition pole J748 washed out from river bank Tapuearoa Rd
13716 | 24/01/2011 | 2010 | 2011-01-24 | 254 | 30 | 7620 | C | DEFECTIVE EQUIPMENT | Replace pole G1689 Arakihi Rd
13731 | 24/01/2011 | 2010 | 2011-01-24 | 447 | 47 | 6023 | B | PLANNED SHUTDOWN | Replace poles D70 & D4901 Totangi Rd
13717 | 25/01/2011 | 2010 | 2011-01-25 | 69 | 490 | 3124 | C | TREE CONTACTS | Remove tree from 11kV pole A3476 208 Caves Rd
13738 | 25/01/2011 | 2010 | 2011-01-25 | 422 | 17 | 28033 | B | PLANNED SHUTDOWN | Replace poles from E142 to end of line Waitangi Rd
13718 | 26/01/2011 | 2010 | 2011-01-26 | 364 | 9 | 3276 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W3640 Waihi Rd
13719 | 27/01/2011 | 2010 | 2011-01-27 | 153 | 19 | 2907 | C | TREE CONTACTS | Repair 11kV lines pole W5584 Kahungungu
13720 | 27/01/2011 | 2010 | 2011-01-27 | 23 | 485 | 9981 | C | DEFECTIVE EQUIPMENT | Bypass CB J8 Te Araroa Sub bushing failed
13729 | 27/01/2011 | 2010 | 2011-01-27 | 390 | 30 | 11700 | B | PLANNED SHUTDOWN | Replace poles D3603 D3605 D3606 D3611 Ruakaka Rd
13730 | 27/01/2011 | 2010 | 2011-01-27 | 348 | 18 | 6264 | B | PLANNED SHUTDOWN | Isolate 11kV line poles G1834 G1852 G1851 G1832 for tree cutting Paramata Rd
13728 | 28/01/2011 | 2010 | 2011-01-28 | 376 | 91 | 34216 | B | PLANNED SHUTDOWN | Replace DDO fuses B739 & B178 Wellington St
13721 | 29/01/2011 | 2010 | 2011-01-29 | 1335 | 44 | 22180 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole G2425 Tauwhareparae Rd
13722 | 29/01/2011 | 2010 | 2011-01-29 | 169 | 150 | 5295 | C | TREE CONTACTS | Repair 11kV lines pole G1523 Arahihi Rd Tolaga Bay
13723 | 29/01/2011 | 2010 | 2011-01-29 | 135 | 121 | 13995 | C | TREE CONTACTS | Repair 11kV lines pole J2204 Rangitukia Rd
13724 | 29/01/2011 | 2010 | 2011-01-29 | 290 | 433 | 71426 | C | TREE CONTACTS | Remove tree from 11kV pole F2563 Hihiroroa Rd North
13763 | 02/02/2011 | 2010 | 2011-02-02 | 316 | 11 | 3476 | B | PLANNED SHUTDOWN | Install new T/x C3224 & connect 11kV cable pole C3224 Cameron Rd
13739 | 03/02/2011 | 2010 | 2011-02-03 | 745 | 401 | 24361 | C | FOREIGN INTERFERENCE | Replace 11kV pole C1354 Wharekopae Rd
13765 | 03/02/2011 | 2010 | 2011-02-03 | 188 | 36 | 6768 | B | PLANNED SHUTDOWN | Upgrade T/x A67 to 300kVA Wairere Rd
13766 | 03/02/2011 | 2010 | 2011-02-03 | 250 | 50 | 12500 | B | PLANNED SHUTDOWN | Replace Recloser W821 Lake Rd Ruapapa Rd
13740 | 04/02/2011 | 2010 | 2011-02-04 | 9 | 2701 | 22902 | C | UNKNOWN | Patrol 50kV line nothing found cause unknown CB B4 tripped
13741 | 04/02/2011 | 2010 | 2011-02-04 | 38 | 18 | 1152 | C | DEFECTIVE EQUIPMENT | Replace T/x pole C65 Waingake Rd
13742 | 05/02/2011 | 2010 | 2011-02-05 | 110 | 206 | 15188 | C | FOREIGN INTERFERENCE | Replace 11kV pole C5197 Riverpoint Rd
13743 | 06/02/2011 | 2010 | 2011-02-06 | 12 | 454 | 5448 | C | UNKNOWN | Patrolled lines nothing found cause unknown CB C95
13744 | 07/02/2011 | 2010 | 2011-02-07 | 628 | 39 | 17095 | C | TREE CONTACTS | Repair 11kV lines J2022 to J2023 Tapuawaeroa Rd
13759 | 08/02/2011 | 2010 | 2011-02-08 | 368 | 54 | 19872 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting G53 to G217 Tauwhareparae Rd
13762 | 08/02/2011 | 2010 | 2011-02-08 | 240 | 65 | 15600 | B | PLANNED SHUTDOWN | Replace 11kV poles E610 & E643 Kanakanaia Rd
13764 | 08/02/2011 | 2010 | 2011-02-08 | 224 | 129 | 17489 | B | PLANNED SHUTDOWN | Replace SW/GR C246 C247 C571 C572 Makaraka Lay By
13745 | 09/02/2011 | 2010 | 2011-02-09 | 45 | 1164 | 49170 | C | DEFECTIVE EQUIPMENT | Reclose CB 25 at Patutahi Sub Bucholtz Trip
13746 | 09/02/2011 | 2010 | 2011-02-09 | 1459 | 206 | 18318 | C | FOREIGN INTERFERENCE | Replace poles C5260 & C208 Bloomfeild Rd Hit by car
13747 | 09/02/2011 | 2010 | 2011-02-09 | 364 | 17 | 6188 | C | TREE CONTACTS | Isolate at pole E142 to Cut trees in lines Waitangi Rd
13768 | 09/02/2011 | 2010 | 2011-02-09 | 390 | 30 | 11700 | B | PLANNED SHUTDOWN | Replace poles D3602 D3585 D3589 D3599 D3618 Ruakaka Rd
13769 | 09/02/2011 | 2010 | 2011-02-09 | 351 | 6 | 2106 | B | PLANNED SHUTDOWN | Isolate 11kV lines H135 to H141 for tree cutting Tuakau Rd
13748 | 10/02/2011 | 2010 | 2011-02-10 | 19 | 8 | 152 | C | DEFECTIVE EQUIPMENT | Replace insulator pole W8595 Kokohu Rd
13749 | 10/02/2011 | 2010 | 2011-02-10 | 36 | 32 | 1152 | C | DEFECTIVE EQUIPMENT | Replace DDO fuse G2210 Cook St Tolaga Bay
13770 | 10/02/2011 | 2010 | 2011-02-10 | 405 | 45 | 23139 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting F63 to F88 Whakarau Rd
13750 | 14/02/2011 | 2010 | 2011-02-14 | 15 | 22 | 330 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole W109 Hereheretau Rd
13751 | 14/02/2011 | 2010 | 2011-02-14 | 58 | 9 | 432 | C | DEFECTIVE EQUIPMENT | Change faulty T/X C378 Bck Ormond Rd
13760 | 15/02/2011 | 2010 | 2011-02-15 | 426 | 22 | 9372 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting F1231 to F4509 SH2 Matawai Rd
13752 | 16/02/2011 | 2010 | 2011-02-16 | 62 | 2521 | 146805 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
13761 | 16/02/2011 | 2010 | 2011-02-16 | 346 | 12 | 4152 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting SH2 Otoko F140 to F178
13767 | 16/02/2011 | 2010 | 2011-02-16 | 408 | 79 | 32232 | B | PLANNED SHUTDOWN | Replace T/x B147 & SW/GR B1895 B1896 B1897 Abbott St
13753 | 18/02/2011 | 2010 | 2011-02-18 | 116 | 777 | 33895 | C | UNKNOWN | Reclose CB A612 Crawford Rd at Port Sub cause unknown
13771 | 18/02/2011 | 2010 | 2011-02-18 | 390 | 65 | 11664 | B | PLANNED SHUTDOWN | Re-route 11kV lines D2173 to D2169 Lavenham Rd
13754 | 22/02/2011 | 2010 | 2011-02-22 | 140 | 18 | 2520 | C | TREE CONTACTS | Isolate 11kV lines trees burning between poles C1551 to C1555 Somertons Rd
13758 | 22/02/2011 | 2010 | 2011-02-22 | 387 | 29 | 11223 | B | PLANNED SHUTDOWN | Replace 6 poles W6498 W6496 W6491 W6479 W6467 W6465 Marumaru
13774 | 23/02/2011 | 2010 | 2011-02-23 | 350 | 30 | 10500 | B | PLANNED SHUTDOWN | Replace 11kV poles D3605 D3606 D3611 Ruakaka Rd
13755 | 24/02/2011 | 2010 | 2011-02-24 | 57 | 90 | 5130 | C | DEFECTIVE EQUIPMENT | Replace pole F1042 Balfour Rd Te Karaka
13772 | 25/02/2011 | 2010 | 2011-02-25 | 60 | 79 | 4740 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting A119 Pa Rd Whangara
13773 | 25/02/2011 | 2010 | 2011-02-25 | 109 | 23 | 2507 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting SH35 Rototahi A152 to A825
13756 | 27/02/2011 | 2010 | 2011-02-27 | 91 | 218 | 19838 | C | TREE CONTACTS | Remove tree from 11kV pole W8940 Mahia
13757 | 28/02/2011 | 2010 | 2011-02-28 | 172 | 21 | 3612 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole W6620 Tukemokihi
13794 | 01/03/2011 | 2010 | 2011-03-01 | 400 | 47 | 13193 | B | PLANNED SHUTDOWN | Replace poles H1775 H1772 H1771 H1768 SH2 Ruatoria South
13798 | 01/03/2011 | 2010 | 2011-03-01 | 376 | 14 | 8160 | B | PLANNED SHUTDOWN | Replace 11kV pole W71 Cricklewood Rd
13804 | 03/03/2011 | 2010 | 2011-03-03 | 122 | 12 | 1464 | B | PLANNED SHUTDOWN | Replace GM T/x B400 Joanne St
13796 | 04/03/2011 | 2010 | 2011-03-04 | 216 | 159 | 34344 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting F437 Puha Settlement Rd
13775 | 05/03/2011 | 2010 | 2011-03-05 | 125 | 12 | 1500 | C | TREE CONTACTS | Repair 11kV lines pole G566 Arikihi Rd
13776 | 05/03/2011 | 2010 | 2011-03-05 | 26 | 3814 | 83819 | C | FOREIGN INTERFERENCE | Replace 50kV pole B3749 Stanley Rd
13799 | 07/03/2011 | 2010 | 2011-03-07 | 33 | 49 | 3136 | B | PLANNED SHUTDOWN | Isolate for tree cutting H1496 Ihungia Rd
13802 | 08/03/2011 | 2010 | 2011-03-08 | 425 | 12 | 5100 | B | PLANNED SHUTDOWN | Replace H poles G575 G613 and tree cutting Waimata Valley Rd
13797 | 09/03/2011 | 2010 | 2011-03-09 | 216 | 45 | 9720 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Te Kowhai Rd Whatatutu E171
13795 | 10/03/2011 | 2010 | 2011-03-10 | 359 | 179 | 13994 | B | PLANNED SHUTDOWN | Replace poles B6301 B6305 James St
13805 | 10/03/2011 | 2010 | 2011-03-10 | 93 | 18 | 1674 | B | PLANNED SHUTDOWN | Isolate T/x A416 for maintenance Gaddums Hill Rd
13777 | 12/03/2011 | 2010 | 2011-03-12 | 46 | 7 | 322 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole H149 Ihungia Rd
13801 | 13/03/2011 | 2010 | 2011-03-13 | 163 | 16 | 2608 | B | PLANNED SHUTDOWN | Term 11kV cable SDAF SW/GR B1899 Kahutia St
13778 | 14/03/2011 | 2010 | 2011-03-14 | 78 | 53 | 2748 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable F/S C696 Saleyards Rd
13806 | 14/03/2011 | 2010 | 2011-03-14 | 372 | 30 | 11160 | B | PLANNED SHUTDOWN | Replace poles D3602 D3585 D3589 D3599 D3618 D3623 D3627 Ruakaka Rd
13809 | 15/03/2011 | 2010 | 2011-03-15 | 415 | 16 | 14886 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Tahunga D488
13779 | 16/03/2011 | 2010 | 2011-03-16 | 224 | 12 | 2688 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H154 Ihungia Rd
13803 | 16/03/2011 | 2010 | 2011-03-16 | 270 | 39 | 10530 | B | PLANNED SHUTDOWN | Install new T/x on pole W5722 Ruakituri Valley
13807 | 16/03/2011 | 2010 | 2011-03-16 | 439 | 71 | 10214 | B | PLANNED SHUTDOWN | Connect 11kV line pole A4381 Makarori Beach
13808 | 16/03/2011 | 2010 | 2011-03-16 | 339 | 47 | 12335 | B | PLANNED SHUTDOWN | Replace poles H1854 H1853 H1853 H1852 H1851 SH35 Ruatoria South
13810 | 21/03/2011 | 2010 | 2011-03-21 | 420 | 24 | 10080 | B | PLANNED SHUTDOWN | Install new T/x D2043 Lake Rd
13780 | 22/03/2011 | 2010 | 2011-03-22 | 267 | 763 | 159677 | C | DEFECTIVE EQUIPMENT | Replace insulators pole W6815 Kiwi Alley
13781 | 22/03/2011 | 2010 | 2011-03-22 | 266 | 54 | 19872 | C | TREE CONTACTS | Repair 11kV lines pole G2322 Tauwhareparae Rd
13782 | 23/03/2011 | 2010 | 2011-03-23 | 290 | 422 | 33459 | C | FOREIGN INTERFERENCE | Replace Xarm pole D2154 Lavenham Rd
13783 | 23/03/2011 | 2010 | 2011-03-23 | 176 | 260 | 45431 | C | DEFECTIVE EQUIPMENT | Repair 11kV conductor pole J2607 Te Araroa
13784 | 23/03/2011 | 2010 | 2011-03-23 | 457 | 69 | 26463 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole F1786 Whakarau Rd
13785 | 23/03/2011 | 2010 | 2011-03-23 | 285 | 23 | 6555 | C | ADVERSE WEATHER | Reposition pole J359 Ruatoria (Washout)
13812 | 23/03/2011 | 2010 | 2011-03-23 | 318 | 18 | 5724 | B | PLANNED SHUTDOWN | Isolate 11kV line for tree cutting Tawhara Valley W1138
13786 | 24/03/2011 | 2010 | 2011-03-24 | 73 | 61 | 4453 | C | DEFECTIVE EQUIPMENT | Check connections GRV W6835 Kiwi Alley
13787 | 24/03/2011 | 2010 | 2011-03-24 | 40 | 22 | 880 | C | DEFECTIVE EQUIPMENT | Repair 11kV strands T/x D469 Totangi Rd
13813 | 24/03/2011 | 2010 | 2011-03-24 | 96 | 71 | 6816 | B | PLANNED SHUTDOWN | Install DDO fuses pole E2241 Snowsills Rd
13811 | 25/03/2011 | 2010 | 2011-03-25 | 417 | 11 | 4587 | B | PLANNED SHUTDOWN | Replace poles W8378 W8397 W8400 W8402 Morere
13788 | 27/03/2011 | 2010 | 2011-03-27 | 185 | 17 | 3145 | C | HUMAN ELEMENT | Isolate 11kV lines for installation of Temp Bailie Bridge near pole H2431
13800 | 29/03/2011 | 2010 | 2011-03-29 | 427 | 5 | 3805 | B | PLANNED SHUTDOWN | Isolate for tree cutting H159 Ihungia Rd
13814 | 29/03/2011 | 2010 | 2011-03-29 | 438 | 17 | 6334 | B | PLANNED SHUTDOWN | Replace 11kV poles D98 D2404 D2405 D2406 D2418 Pehiri Rd
13789 | 30/03/2011 | 2010 | 2011-03-30 | 52 | 206 | 10712 | C | UNKNOWN | Reclose CB C18 Bell Rd at Matawhero Sub cause unknown
13790 | 30/03/2011 | 2010 | 2011-03-30 | 75 | 62 | 4650 | C | DEFECTIVE EQUIPMENT | Replace faulty Recloser W6835 Kiwi Alley
13791 | 30/03/2011 | 2010 | 2011-03-30 | 652 | 154 | 26553 | C | DEFECTIVE EQUIPMENT | Replace Xarm pole G1509 Rangikohua Rd Tolaga Bay
13792 | 30/03/2011 | 2010 | 2011-03-30 | 239 | 327 | 51288 | C | TREE CONTACTS | Repair 11kV lines poles J1388 to J1385 Harrison Rd
13793 | 30/03/2011 | 2010 | 2011-03-30 | 375 | 50 | 19736 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole J4244 Waikura

## 20102011DailyTotals
Date Outage | Year | TotAVG | Customers Impacted | Total Customer Minutes Lost | Saidi | Safi
02/04/2010 | 2010 | 25473 | 1226 | 26887 | 1.0555 | 0.048129
07/04/2010 | 2010 | 25473 | 47 | 5832 | 0.22895 | 0.0018451
08/04/2010 | 2010 | 25473 | 25 | 6092 | 0.23916 | 0.00098143
09/04/2010 | 2010 | 25473 | 26 | 2197 | 0.086248 | 0.0010207
15/04/2010 | 2010 | 25473 | 43 | 5479 | 0.21509 | 0.0016881
16/04/2010 | 2010 | 25473 | 228 | 16656 | 0.65387 | 0.0089507
17/04/2010 | 2010 | 25473 | 311 | 20837 | 0.818 | 0.012209
18/04/2010 | 2010 | 25473 | 981 | 41710 | 1.6374 | 0.038511
26/04/2010 | 2010 | 25473 | 9 | 1755 | 0.068896 | 0.00035332
27/04/2010 | 2010 | 25473 | 1711 | 58938 | 2.3137 | 0.067169
30/04/2010 | 2010 | 25473 | 7 | 1799 | 0.070624 | 0.0002748
05/05/2010 | 2010 | 25473 | 49 | 10488 | 0.41173 | 0.0019236
06/05/2010 | 2010 | 25473 | 1541 | 58196 | 2.2846 | 0.060495
08/05/2010 | 2010 | 25473 | 785 | 99430 | 3.9033 | 0.030817
09/05/2010 | 2010 | 25473 | 64 | 1856 | 0.072861 | 0.0025125
12/05/2010 | 2010 | 25473 | 103 | 38884 | 1.5265 | 0.0040435
14/05/2010 | 2010 | 25473 | 21 | 6543 | 0.25686 | 0.0008244
17/05/2010 | 2010 | 25473 | 2516 | 153476 | 6.025 | 0.098771
18/05/2010 | 2010 | 25473 | 1621 | 38578 | 1.5145 | 0.063636
19/05/2010 | 2010 | 25473 | 407 | 47691 | 1.8722 | 0.015978
21/05/2010 | 2010 | 25473 | 35 | 3542 | 0.13905 | 0.001374
24/05/2010 | 2010 | 25473 | 2184 | 546767 | 21.4646 | 0.085738
25/05/2010 | 2010 | 25473 | 483 | 19759 | 0.77568 | 0.018961
26/05/2010 | 2010 | 25473 | 528 | 85830 | 3.3695 | 0.020728
27/05/2010 | 2010 | 25473 | 259 | 25358 | 0.99549 | 0.010168
30/05/2010 | 2010 | 25473 | 172 | 43594 | 1.7114 | 0.0067522
31/05/2010 | 2010 | 25473 | 20 | 1160 | 0.045538 | 0.00078515
01/06/2010 | 2010 | 25473 | 58 | 2030 | 0.079692 | 0.0022769
02/06/2010 | 2010 | 25473 | 102 | 14192 | 0.55714 | 0.0040042
08/06/2010 | 2010 | 25473 | 471 | 45612 | 1.7906 | 0.01849
10/06/2010 | 2010 | 25473 | 81 | 3003 | 0.11789 | 0.0031798
13/06/2010 | 2010 | 25473 | 272 | 25840 | 1.0144 | 0.010678
14/06/2010 | 2010 | 25473 | 2516 | 67620 | 2.6546 | 0.098771
15/06/2010 | 2010 | 25473 | 62 | 4092 | 0.16064 | 0.0024339
16/06/2010 | 2010 | 25473 | 50 | 6362 | 0.24975 | 0.0019629
18/06/2010 | 2010 | 25473 | 15 | 435 | 0.017077 | 0.00058886
19/06/2010 | 2010 | 25473 | 730 | 220015 | 8.6372 | 0.028658
20/06/2010 | 2010 | 25473 | 128 | 23936 | 0.93966 | 0.0050249
21/06/2010 | 2010 | 25473 | 176 | 3344 | 0.13128 | 0.0069093
22/06/2010 | 2010 | 25473 | 274 | 4719 | 0.18525 | 0.010756
24/06/2010 | 2010 | 25473 | 11 | 660 | 0.02591 | 0.00043183
26/06/2010 | 2010 | 25473 | 92 | 8351 | 0.32784 | 0.0036117
28/06/2010 | 2010 | 25473 | 128 | 18592 | 0.72987 | 0.0050249
01/07/2010 | 2010 | 25473 | 692 | 41742 | 1.6387 | 0.027166
02/07/2010 | 2010 | 25473 | 264 | 96135 | 3.774 | 0.010364
05/07/2010 | 2010 | 25473 | 189 | 44805 | 1.7589 | 0.0074196
06/07/2010 | 2010 | 25473 | 780 | 117552 | 4.6148 | 0.030621
07/07/2010 | 2010 | 25473 | 255 | 73976 | 2.9041 | 0.010011
08/07/2010 | 2010 | 25473 | 471 | 25970 | 1.0195 | 0.01849
09/07/2010 | 2010 | 25473 | 1277 | 18239 | 0.71601 | 0.050132
10/07/2010 | 2010 | 25473 | 20 | 280 | 0.010992 | 0.00078515
12/07/2010 | 2010 | 25473 | 36 | 10872 | 0.4268 | 0.0014133
13/07/2010 | 2010 | 25473 | 11 | 1190 | 0.046716 | 0.00043183
14/07/2010 | 2010 | 25473 | 241 | 26522 | 1.0412 | 0.009461
17/07/2010 | 2010 | 25473 | 622 | 57553 | 2.2594 | 0.024418
18/07/2010 | 2010 | 25473 | 32 | 480 | 0.018843 | 0.0012562
19/07/2010 | 2010 | 25473 | 73 | 3082 | 0.12099 | 0.0028658
20/07/2010 | 2010 | 25473 | 606 | 82887 | 3.2539 | 0.02379
21/07/2010 | 2010 | 25473 | 92 | 14215 | 0.55804 | 0.0036117
22/07/2010 | 2010 | 25473 | 43 | 14113 | 0.55404 | 0.0016881
23/07/2010 | 2010 | 25473 | 438 | 3504 | 0.13756 | 0.017195
24/07/2010 | 2010 | 25473 | 176 | 4224 | 0.16582 | 0.0069093
25/07/2010 | 2010 | 25473 | 253 | 16154 | 0.63416 | 0.0099321
27/07/2010 | 2010 | 25473 | 177 | 78942 | 3.099 | 0.0069485
28/07/2010 | 2010 | 25473 | 35 | 15750 | 0.6183 | 0.001374
29/07/2010 | 2010 | 25473 | 96 | 25632 | 1.0062 | 0.0037687
31/07/2010 | 2010 | 25473 | 72 | 7416 | 0.29113 | 0.0028265
01/08/2010 | 2010 | 25473 | 421 | 10499 | 0.41216 | 0.016527
02/08/2010 | 2010 | 25473 | 201 | 9760 | 0.38315 | 0.0078907
03/08/2010 | 2010 | 25473 | 70 | 13650 | 0.53586 | 0.002748
04/08/2010 | 2010 | 25473 | 44 | 3964 | 0.15562 | 0.0017273
05/08/2010 | 2010 | 25473 | 218 | 32862 | 1.2901 | 0.0085581
06/08/2010 | 2010 | 25473 | 122 | 17692 | 0.69454 | 0.0047894
10/08/2010 | 2010 | 25473 | 96 | 39498 | 1.5506 | 0.0037687
11/08/2010 | 2010 | 25473 | 92 | 38462 | 1.5099 | 0.0036117
12/08/2010 | 2010 | 25473 | 292 | 37369 | 1.467 | 0.011463
14/08/2010 | 2010 | 25473 | 433 | 31806 | 1.2486 | 0.016998
16/08/2010 | 2010 | 25473 | 120 | 11970 | 0.46991 | 0.0047109
17/08/2010 | 2010 | 25473 | 23 | 11362 | 0.44604 | 0.00090292
18/08/2010 | 2010 | 25473 | 35 | 8960 | 0.35174 | 0.001374
19/08/2010 | 2010 | 25473 | 181 | 14553 | 0.57131 | 0.0071056
20/08/2010 | 2010 | 25473 | 15 | 6300 | 0.24732 | 0.00058886
24/08/2010 | 2010 | 25473 | 92 | 15646 | 0.61422 | 0.0036117
25/08/2010 | 2010 | 25473 | 209 | 54034 | 2.1212 | 0.0082048
26/08/2010 | 2010 | 25473 | 300 | 36599 | 1.4368 | 0.011777
27/08/2010 | 2010 | 25473 | 373 | 35079 | 1.3771 | 0.014643
30/08/2010 | 2010 | 25473 | 231 | 11647 | 0.45723 | 0.0090684
01/09/2010 | 2010 | 25473 | 10 | 3960 | 0.15546 | 0.00039257
02/09/2010 | 2010 | 25473 | 130 | 28951 | 1.1365 | 0.0051034
03/09/2010 | 2010 | 25473 | 391 | 27753 | 1.0895 | 0.01535
04/09/2010 | 2010 | 25473 | 72 | 14791 | 0.58065 | 0.0028265
05/09/2010 | 2010 | 25473 | 353 | 37479 | 1.4713 | 0.013858
06/09/2010 | 2010 | 25473 | 971 | 66687 | 2.6179 | 0.038119
07/09/2010 | 2010 | 25473 | 712 | 30964 | 1.2156 | 0.027951
08/09/2010 | 2010 | 25473 | 6 | 2784 | 0.10929 | 0.00023554
09/09/2010 | 2010 | 25473 | 208 | 15345 | 0.6024 | 0.0081655
10/09/2010 | 2010 | 25473 | 136 | 5636 | 0.22125 | 0.005339
12/09/2010 | 2010 | 25473 | 156 | 12639 | 0.49617 | 0.0061241
14/09/2010 | 2010 | 25473 | 86 | 29332 | 1.1515 | 0.0033761
15/09/2010 | 2010 | 25473 | 32 | 2913 | 0.11436 | 0.0012562
16/09/2010 | 2010 | 25473 | 54 | 11829 | 0.46437 | 0.0021199
17/09/2010 | 2010 | 25473 | 3530 | 336652 | 13.216 | 0.13858
18/09/2010 | 2010 | 25473 | 1149 | 134379 | 5.2754 | 0.045107
19/09/2010 | 2010 | 25473 | 599 | 163056 | 6.4011 | 0.023515
20/09/2010 | 2010 | 25473 | 574 | 206156 | 8.0931 | 0.022534
21/09/2010 | 2010 | 25473 | 56 | 13472 | 0.52887 | 0.0021984
22/09/2010 | 2010 | 25473 | 26 | 2689 | 0.10556 | 0.0010207
23/09/2010 | 2010 | 25473 | 408 | 112852 | 4.4303 | 0.016017
24/09/2010 | 2010 | 25473 | 12 | 840 | 0.032976 | 0.00047109
26/09/2010 | 2010 | 25473 | 95 | 5929 | 0.23276 | 0.0037294
27/09/2010 | 2010 | 25473 | 12 | 4980 | 0.1955 | 0.00047109
28/09/2010 | 2010 | 25473 | 10 | 3670 | 0.14407 | 0.00039257
29/09/2010 | 2010 | 25473 | 198 | 14497 | 0.56911 | 0.0077729
30/09/2010 | 2010 | 25473 | 41 | 18261 | 0.71688 | 0.0016095
01/10/2010 | 2010 | 25473 | 73 | 7097 | 0.27861 | 0.0028658
05/10/2010 | 2010 | 25473 | 152 | 9357 | 0.36733 | 0.0059671
06/10/2010 | 2010 | 25473 | 279 | 43608 | 1.7119 | 0.010953
11/10/2010 | 2010 | 25473 | 1831 | 219387 | 8.6125 | 0.07188
12/10/2010 | 2010 | 25473 | 2768 | 419374 | 16.4635 | 0.10866
13/10/2010 | 2010 | 25473 | 214 | 29987 | 1.1772 | 0.0084011
14/10/2010 | 2010 | 25473 | 4380 | 298684 | 11.7255 | 0.17195
15/10/2010 | 2010 | 25473 | 150 | 19745 | 0.77513 | 0.0058886
16/10/2010 | 2010 | 25473 | 369 | 132054 | 5.1841 | 0.014486
18/10/2010 | 2010 | 25473 | 495 | 15985 | 0.62753 | 0.019432
19/10/2010 | 2010 | 25473 | 60 | 10380 | 0.40749 | 0.0023554
21/10/2010 | 2010 | 25473 | 1137 | 16990 | 0.66698 | 0.044635
22/10/2010 | 2010 | 25473 | 836 | 33023 | 1.2964 | 0.032819
23/10/2010 | 2010 | 25473 | 260 | 11530 | 0.45264 | 0.010207
24/10/2010 | 2010 | 25473 | 210 | 52900 | 2.0767 | 0.008244
26/10/2010 | 2010 | 25473 | 272 | 11148 | 0.43764 | 0.010678
27/10/2010 | 2010 | 25473 | 52 | 936 | 0.036745 | 0.0020414
01/11/2010 | 2010 | 25473 | 84 | 48428 | 1.9012 | 0.0032976
03/11/2010 | 2010 | 25473 | 12 | 4284 | 0.16818 | 0.00047109
04/11/2010 | 2010 | 25473 | 10 | 3810 | 0.14957 | 0.00039257
08/11/2010 | 2010 | 25473 | 71 | 5890 | 0.23123 | 0.0027873
09/11/2010 | 2010 | 25473 | 92 | 23484 | 0.92192 | 0.0036117
10/11/2010 | 2010 | 25473 | 57 | 24738 | 0.97115 | 0.0022377
11/11/2010 | 2010 | 25473 | 17 | 1989 | 0.078083 | 0.00066737
12/11/2010 | 2010 | 25473 | 12 | 4284 | 0.16818 | 0.00047109
13/11/2010 | 2010 | 25473 | 137 | 5793 | 0.22742 | 0.0053782
14/11/2010 | 2010 | 25473 | 994 | 38766 | 1.5218 | 0.039022
15/11/2010 | 2010 | 25473 | 80 | 16829 | 0.66066 | 0.0031406
16/11/2010 | 2010 | 25473 | 856 | 73416 | 2.8821 | 0.033604
17/11/2010 | 2010 | 25473 | 10 | 570 | 0.022377 | 0.00039257
18/11/2010 | 2010 | 25473 | 11 | 4169 | 0.16366 | 0.00043183
19/11/2010 | 2010 | 25473 | 51 | 10139 | 0.39803 | 0.0020021
20/11/2010 | 2010 | 25473 | 223 | 37767 | 1.4826 | 0.0087544
21/11/2010 | 2010 | 25473 | 1488 | 94298 | 3.7019 | 0.058415
23/11/2010 | 2010 | 25473 | 72 | 7092 | 0.27841 | 0.0028265
24/11/2010 | 2010 | 25473 | 150 | 25350 | 0.99517 | 0.0058886
25/11/2010 | 2010 | 25473 | 42 | 17010 | 0.66777 | 0.0016488
28/11/2010 | 2010 | 25473 | 838 | 20102 | 0.78915 | 0.032898
29/11/2010 | 2010 | 25473 | 99 | 12639 | 0.49617 | 0.0038865
01/12/2010 | 2010 | 25473 | 202 | 20970 | 0.82322 | 0.00793
02/12/2010 | 2010 | 25473 | 44 | 13162 | 0.5167 | 0.0017273
03/12/2010 | 2010 | 25473 | 41 | 4862 | 0.19087 | 0.0016095
06/12/2010 | 2010 | 25473 | 1170 | 48686 | 1.9113 | 0.045931
07/12/2010 | 2010 | 25473 | 127 | 19812 | 0.77776 | 0.0049857
08/12/2010 | 2010 | 25473 | 778 | 60139 | 2.3609 | 0.030542
09/12/2010 | 2010 | 25473 | 228 | 13414 | 0.5266 | 0.0089507
10/12/2010 | 2010 | 25473 | 194 | 16199 | 0.63593 | 0.0076159
11/12/2010 | 2010 | 25473 | 216 | 33169 | 1.3021 | 0.0084796
13/12/2010 | 2010 | 25473 | 242 | 56473 | 2.217 | 0.0095003
15/12/2010 | 2010 | 25473 | 729 | 58402 | 2.2927 | 0.028619
18/12/2010 | 2010 | 25473 | 171 | 19983 | 0.78448 | 0.006713
19/12/2010 | 2010 | 25473 | 86 | 4754 | 0.18663 | 0.0033761
20/12/2010 | 2010 | 25473 | 76 | 56696 | 2.2257 | 0.0029836
21/12/2010 | 2010 | 25473 | 66 | 24552 | 0.96384 | 0.002591
22/12/2010 | 2010 | 25473 | 62 | 22912 | 0.89946 | 0.0024339
23/12/2010 | 2010 | 25473 | 24 | 2640 | 0.10364 | 0.00094217
24/12/2010 | 2010 | 25473 | 433 | 35716 | 1.4021 | 0.016998
25/12/2010 | 2010 | 25473 | 79 | 23620 | 0.92726 | 0.0031013
28/12/2010 | 2010 | 25473 | 1377 | 76985 | 3.0222 | 0.054057
29/12/2010 | 2010 | 25473 | 29 | 1252 | 0.04915 | 0.0011385
30/12/2010 | 2010 | 25473 | 91 | 6544 | 0.2569 | 0.0035724
04/01/2011 | 2010 | 25473 | 96 | 9042 | 0.35496 | 0.0037687
06/01/2011 | 2010 | 25473 | 23 | 690 | 0.027088 | 0.00090292
07/01/2011 | 2010 | 25473 | 22 | 880 | 0.034546 | 0.00086366
08/01/2011 | 2010 | 25473 | 907 | 16326 | 0.64091 | 0.035606
10/01/2011 | 2010 | 25473 | 235 | 60572 | 2.3779 | 0.0092255
12/01/2011 | 2010 | 25473 | 258 | 4956 | 0.19456 | 0.010128
13/01/2011 | 2010 | 25473 | 253 | 40236 | 1.5796 | 0.0099321
18/01/2011 | 2010 | 25473 | 91 | 18231 | 0.7157 | 0.0035724
19/01/2011 | 2010 | 25473 | 24 | 17647 | 0.69277 | 0.00094217
20/01/2011 | 2010 | 25473 | 177 | 11218 | 0.44039 | 0.0069485
21/01/2011 | 2010 | 25473 | 762 | 18016 | 0.70726 | 0.029914
22/01/2011 | 2010 | 25473 | 14 | 4382 | 0.17203 | 0.0005496
23/01/2011 | 2010 | 25473 | 345 | 23586 | 0.92592 | 0.013544
24/01/2011 | 2010 | 25473 | 103 | 19621 | 0.77027 | 0.0040435
25/01/2011 | 2010 | 25473 | 507 | 31157 | 1.2231 | 0.019903
26/01/2011 | 2010 | 25473 | 9 | 3276 | 0.12861 | 0.00035332
27/01/2011 | 2010 | 25473 | 552 | 30852 | 1.2112 | 0.02167
28/01/2011 | 2010 | 25473 | 91 | 34216 | 1.3432 | 0.0035724
29/01/2011 | 2010 | 25473 | 748 | 112896 | 4.432 | 0.029364
02/02/2011 | 2010 | 25473 | 11 | 3476 | 0.13646 | 0.00043183
03/02/2011 | 2010 | 25473 | 487 | 43629 | 1.7128 | 0.019118
04/02/2011 | 2010 | 25473 | 2719 | 24054 | 0.94429 | 0.10674
05/02/2011 | 2010 | 25473 | 206 | 15188 | 0.59624 | 0.008087
06/02/2011 | 2010 | 25473 | 454 | 5448 | 0.21387 | 0.017823
07/02/2011 | 2010 | 25473 | 39 | 17095 | 0.6711 | 0.001531
08/02/2011 | 2010 | 25473 | 248 | 52961 | 2.0791 | 0.0097358
09/02/2011 | 2010 | 25473 | 1423 | 87482 | 3.4343 | 0.055863
10/02/2011 | 2010 | 25473 | 85 | 24443 | 0.95957 | 0.0033369
14/02/2011 | 2010 | 25473 | 31 | 762 | 0.029914 | 0.001217
15/02/2011 | 2010 | 25473 | 22 | 9372 | 0.36792 | 0.00086366
16/02/2011 | 2010 | 25473 | 2612 | 183189 | 7.1915 | 0.10254
18/02/2011 | 2010 | 25473 | 842 | 45559 | 1.7885 | 0.033055
22/02/2011 | 2010 | 25473 | 47 | 13743 | 0.53951 | 0.0018451
23/02/2011 | 2010 | 25473 | 30 | 10500 | 0.4122 | 0.0011777
24/02/2011 | 2010 | 25473 | 90 | 5130 | 0.20139 | 0.0035332
25/02/2011 | 2010 | 25473 | 102 | 7247 | 0.2845 | 0.0040042
27/02/2011 | 2010 | 25473 | 218 | 19838 | 0.77879 | 0.0085581
28/02/2011 | 2010 | 25473 | 21 | 3612 | 0.1418 | 0.0008244
01/03/2011 | 2010 | 25473 | 61 | 21353 | 0.83826 | 0.0023947
03/03/2011 | 2010 | 25473 | 12 | 1464 | 0.057473 | 0.00047109
04/03/2011 | 2010 | 25473 | 159 | 34344 | 1.3483 | 0.0062419
05/03/2011 | 2010 | 25473 | 3826 | 85319 | 3.3494 | 0.1502
07/03/2011 | 2010 | 25473 | 49 | 3136 | 0.12311 | 0.0019236
08/03/2011 | 2010 | 25473 | 12 | 5100 | 0.20021 | 0.00047109
09/03/2011 | 2010 | 25473 | 45 | 9720 | 0.38158 | 0.0017666
10/03/2011 | 2010 | 25473 | 197 | 15668 | 0.61508 | 0.0077337
12/03/2011 | 2010 | 25473 | 7 | 322 | 0.012641 | 0.0002748
13/03/2011 | 2010 | 25473 | 16 | 2608 | 0.10238 | 0.00062812
14/03/2011 | 2010 | 25473 | 83 | 13908 | 0.54599 | 0.0032584
15/03/2011 | 2010 | 25473 | 16 | 14886 | 0.58438 | 0.00062812
16/03/2011 | 2010 | 25473 | 169 | 35767 | 1.4041 | 0.0066345
21/03/2011 | 2010 | 25473 | 24 | 10080 | 0.39571 | 0.00094217
22/03/2011 | 2010 | 25473 | 817 | 179549 | 7.0486 | 0.032073
23/03/2011 | 2010 | 25473 | 792 | 117632 | 4.6179 | 0.031092
24/03/2011 | 2010 | 25473 | 154 | 12149 | 0.47694 | 0.0060456
25/03/2011 | 2010 | 25473 | 11 | 4587 | 0.18007 | 0.00043183
27/03/2011 | 2010 | 25473 | 17 | 3145 | 0.12346 | 0.00066737
29/03/2011 | 2010 | 25473 | 22 | 10139 | 0.39803 | 0.00086366
30/03/2011 | 2010 | 25473 | 799 | 112939 | 4.4337 | 0.031367

## 20102011Fixeddata
|  | Sum of Normalised Data | 333.9967 | 3.4827
Date Outage | Saidi | Safi | FixedSaidi | FixedSaifi
02/04/2010 | 1.0555 | 0.048129 | 1.0555 | 0.048129
07/04/2010 | 0.22895 | 0.0018451 | 0.22895 | 0.0018451
08/04/2010 | 0.23916 | 0.00098143 | 0.23916 | 0.00098143
09/04/2010 | 0.086248 | 0.0010207 | 0.086248 | 0.0010207
15/04/2010 | 0.21509 | 0.0016881 | 0.21509 | 0.0016881
16/04/2010 | 0.65387 | 0.0089507 | 0.65387 | 0.0089507
17/04/2010 | 0.818 | 0.012209 | 0.818 | 0.012209
18/04/2010 | 1.6374 | 0.038511 | 1.6374 | 0.038511
26/04/2010 | 0.068896 | 0.00035332 | 0.068896 | 0.00035332
27/04/2010 | 2.3137 | 0.067169 | 2.3137 | 0.067169
30/04/2010 | 0.070624 | 0.0002748 | 0.070624 | 0.0002748
05/05/2010 | 0.41173 | 0.0019236 | 0.41173 | 0.0019236
06/05/2010 | 2.2846 | 0.060495 | 2.2846 | 0.060495
08/05/2010 | 3.9033 | 0.030817 | 3.9033 | 0.030817
09/05/2010 | 0.072861 | 0.0025125 | 0.072861 | 0.0025125
12/05/2010 | 1.5265 | 0.0040435 | 1.5265 | 0.0040435
14/05/2010 | 0.25686 | 0.0008244 | 0.25686 | 0.0008244
17/05/2010 | 6.025 | 0.098771 | 6.025 | 0.098771
18/05/2010 | 1.5145 | 0.063636 | 1.5145 | 0.063636
19/05/2010 | 1.8722 | 0.015978 | 1.8722 | 0.015978
21/05/2010 | 0.13905 | 0.001374 | 0.13905 | 0.001374
24/05/2010 | 21.4646 | 0.085738 | 21.4646 | 0.085738
25/05/2010 | 0.77568 | 0.018961 | 0.77568 | 0.018961
26/05/2010 | 3.3695 | 0.020728 | 3.3695 | 0.020728
27/05/2010 | 0.99549 | 0.010168 | 0.99549 | 0.010168
30/05/2010 | 1.7114 | 0.0067522 | 1.7114 | 0.0067522
31/05/2010 | 0.045538 | 0.00078515 | 0.045538 | 0.00078515
01/06/2010 | 0.079692 | 0.0022769 | 0.079692 | 0.0022769
02/06/2010 | 0.55714 | 0.0040042 | 0.55714 | 0.0040042
08/06/2010 | 1.7906 | 0.01849 | 1.7906 | 0.01849
10/06/2010 | 0.11789 | 0.0031798 | 0.11789 | 0.0031798
13/06/2010 | 1.0144 | 0.010678 | 1.0144 | 0.010678
14/06/2010 | 2.6546 | 0.098771 | 2.6546 | 0.098771
15/06/2010 | 0.16064 | 0.0024339 | 0.16064 | 0.0024339
16/06/2010 | 0.24975 | 0.0019629 | 0.24975 | 0.0019629
18/06/2010 | 0.017077 | 0.00058886 | 0.017077 | 0.00058886
19/06/2010 | 8.6372 | 0.028658 | 8.6372 | 0.028658
20/06/2010 | 0.93966 | 0.0050249 | 0.93966 | 0.0050249
21/06/2010 | 0.13128 | 0.0069093 | 0.13128 | 0.0069093
22/06/2010 | 0.18525 | 0.010756 | 0.18525 | 0.010756
24/06/2010 | 0.02591 | 0.00043183 | 0.02591 | 0.00043183
26/06/2010 | 0.32784 | 0.0036117 | 0.32784 | 0.0036117
28/06/2010 | 0.72987 | 0.0050249 | 0.72987 | 0.0050249
01/07/2010 | 1.6387 | 0.027166 | 1.6387 | 0.027166
02/07/2010 | 3.774 | 0.010364 | 3.774 | 0.010364
05/07/2010 | 1.7589 | 0.0074196 | 1.7589 | 0.0074196
06/07/2010 | 4.6148 | 0.030621 | 4.6148 | 0.030621
07/07/2010 | 2.9041 | 0.010011 | 2.9041 | 0.010011
08/07/2010 | 1.0195 | 0.01849 | 1.0195 | 0.01849
09/07/2010 | 0.71601 | 0.050132 | 0.71601 | 0.050132
10/07/2010 | 0.010992 | 0.00078515 | 0.010992 | 0.00078515
12/07/2010 | 0.4268 | 0.0014133 | 0.4268 | 0.0014133
13/07/2010 | 0.046716 | 0.00043183 | 0.046716 | 0.00043183
14/07/2010 | 1.0412 | 0.009461 | 1.0412 | 0.009461
17/07/2010 | 2.2594 | 0.024418 | 2.2594 | 0.024418
18/07/2010 | 0.018843 | 0.0012562 | 0.018843 | 0.0012562
19/07/2010 | 0.12099 | 0.0028658 | 0.12099 | 0.0028658
20/07/2010 | 3.2539 | 0.02379 | 3.2539 | 0.02379
21/07/2010 | 0.55804 | 0.0036117 | 0.55804 | 0.0036117
22/07/2010 | 0.55404 | 0.0016881 | 0.55404 | 0.0016881
23/07/2010 | 0.13756 | 0.017195 | 0.13756 | 0.017195
24/07/2010 | 0.16582 | 0.0069093 | 0.16582 | 0.0069093
25/07/2010 | 0.63416 | 0.0099321 | 0.63416 | 0.0099321
27/07/2010 | 3.099 | 0.0069485 | 3.099 | 0.0069485
28/07/2010 | 0.6183 | 0.001374 | 0.6183 | 0.001374
29/07/2010 | 1.0062 | 0.0037687 | 1.0062 | 0.0037687
31/07/2010 | 0.29113 | 0.0028265 | 0.29113 | 0.0028265
01/08/2010 | 0.41216 | 0.016527 | 0.41216 | 0.016527
02/08/2010 | 0.38315 | 0.0078907 | 0.38315 | 0.0078907
03/08/2010 | 0.53586 | 0.002748 | 0.53586 | 0.002748
04/08/2010 | 0.15562 | 0.0017273 | 0.15562 | 0.0017273
05/08/2010 | 1.2901 | 0.0085581 | 1.2901 | 0.0085581
06/08/2010 | 0.69454 | 0.0047894 | 0.69454 | 0.0047894
10/08/2010 | 1.5506 | 0.0037687 | 1.5506 | 0.0037687
11/08/2010 | 1.5099 | 0.0036117 | 1.5099 | 0.0036117
12/08/2010 | 1.467 | 0.011463 | 1.467 | 0.011463
14/08/2010 | 1.2486 | 0.016998 | 1.2486 | 0.016998
16/08/2010 | 0.46991 | 0.0047109 | 0.46991 | 0.0047109
17/08/2010 | 0.44604 | 0.00090292 | 0.44604 | 0.00090292
18/08/2010 | 0.35174 | 0.001374 | 0.35174 | 0.001374
19/08/2010 | 0.57131 | 0.0071056 | 0.57131 | 0.0071056
20/08/2010 | 0.24732 | 0.00058886 | 0.24732 | 0.00058886
24/08/2010 | 0.61422 | 0.0036117 | 0.61422 | 0.0036117
25/08/2010 | 2.1212 | 0.0082048 | 2.1212 | 0.0082048
26/08/2010 | 1.4368 | 0.011777 | 1.4368 | 0.011777
27/08/2010 | 1.3771 | 0.014643 | 1.3771 | 0.014643
30/08/2010 | 0.45723 | 0.0090684 | 0.45723 | 0.0090684
01/09/2010 | 0.15546 | 0.00039257 | 0.15546 | 0.00039257
02/09/2010 | 1.1365 | 0.0051034 | 1.1365 | 0.0051034
03/09/2010 | 1.0895 | 0.01535 | 1.0895 | 0.01535
04/09/2010 | 0.58065 | 0.0028265 | 0.58065 | 0.0028265
05/09/2010 | 1.4713 | 0.013858 | 1.4713 | 0.013858
06/09/2010 | 2.6179 | 0.038119 | 2.6179 | 0.038119
07/09/2010 | 1.2156 | 0.027951 | 1.2156 | 0.027951
08/09/2010 | 0.10929 | 0.00023554 | 0.10929 | 0.00023554
09/09/2010 | 0.6024 | 0.0081655 | 0.6024 | 0.0081655
10/09/2010 | 0.22125 | 0.005339 | 0.22125 | 0.005339
12/09/2010 | 0.49617 | 0.0061241 | 0.49617 | 0.0061241
14/09/2010 | 1.1515 | 0.0033761 | 1.1515 | 0.0033761
15/09/2010 | 0.11436 | 0.0012562 | 0.11436 | 0.0012562
16/09/2010 | 0.46437 | 0.0021199 | 0.46437 | 0.0021199
17/09/2010 | 13.216 | 0.13858 | 13.216 | 0.13858
18/09/2010 | 5.2754 | 0.045107 | 5.2754 | 0.045107
19/09/2010 | 6.4011 | 0.023515 | 6.4011 | 0.023515
20/09/2010 | 8.0931 | 0.022534 | 8.0931 | 0.022534
21/09/2010 | 0.52887 | 0.0021984 | 0.52887 | 0.0021984
22/09/2010 | 0.10556 | 0.0010207 | 0.10556 | 0.0010207
23/09/2010 | 4.4303 | 0.016017 | 4.4303 | 0.016017
24/09/2010 | 0.032976 | 0.00047109 | 0.032976 | 0.00047109
26/09/2010 | 0.23276 | 0.0037294 | 0.23276 | 0.0037294
27/09/2010 | 0.1955 | 0.00047109 | 0.1955 | 0.00047109
28/09/2010 | 0.14407 | 0.00039257 | 0.14407 | 0.00039257
29/09/2010 | 0.56911 | 0.0077729 | 0.56911 | 0.0077729
30/09/2010 | 0.71688 | 0.0016095 | 0.71688 | 0.0016095
01/10/2010 | 0.27861 | 0.0028658 | 0.27861 | 0.0028658
05/10/2010 | 0.36733 | 0.0059671 | 0.36733 | 0.0059671
06/10/2010 | 1.7119 | 0.010953 | 1.7119 | 0.010953
11/10/2010 | 8.6125 | 0.07188 | 8.6125 | 0.07188
12/10/2010 | 16.4635 | 0.10866 | 16.4635 | 0.10866
13/10/2010 | 1.1772 | 0.0084011 | 1.1772 | 0.0084011
14/10/2010 | 11.7255 | 0.17195 | 11.7255 | 0.17195
15/10/2010 | 0.77513 | 0.0058886 | 0.77513 | 0.0058886
16/10/2010 | 5.1841 | 0.014486 | 5.1841 | 0.014486
18/10/2010 | 0.62753 | 0.019432 | 0.62753 | 0.019432
19/10/2010 | 0.40749 | 0.0023554 | 0.40749 | 0.0023554
21/10/2010 | 0.66698 | 0.044635 | 0.66698 | 0.044635
22/10/2010 | 1.2964 | 0.032819 | 1.2964 | 0.032819
23/10/2010 | 0.45264 | 0.010207 | 0.45264 | 0.010207
24/10/2010 | 2.0767 | 0.008244 | 2.0767 | 0.008244
26/10/2010 | 0.43764 | 0.010678 | 0.43764 | 0.010678
27/10/2010 | 0.036745 | 0.0020414 | 0.036745 | 0.0020414
01/11/2010 | 1.9012 | 0.0032976 | 1.9012 | 0.0032976
03/11/2010 | 0.16818 | 0.00047109 | 0.16818 | 0.00047109
04/11/2010 | 0.14957 | 0.00039257 | 0.14957 | 0.00039257
08/11/2010 | 0.23123 | 0.0027873 | 0.23123 | 0.0027873
09/11/2010 | 0.92192 | 0.0036117 | 0.92192 | 0.0036117
10/11/2010 | 0.97115 | 0.0022377 | 0.97115 | 0.0022377
11/11/2010 | 0.078083 | 0.00066737 | 0.078083 | 0.00066737
12/11/2010 | 0.16818 | 0.00047109 | 0.16818 | 0.00047109
13/11/2010 | 0.22742 | 0.0053782 | 0.22742 | 0.0053782
14/11/2010 | 1.5218 | 0.039022 | 1.5218 | 0.039022
15/11/2010 | 0.66066 | 0.0031406 | 0.66066 | 0.0031406
16/11/2010 | 2.8821 | 0.033604 | 2.8821 | 0.033604
17/11/2010 | 0.022377 | 0.00039257 | 0.022377 | 0.00039257
18/11/2010 | 0.16366 | 0.00043183 | 0.16366 | 0.00043183
19/11/2010 | 0.39803 | 0.0020021 | 0.39803 | 0.0020021
20/11/2010 | 1.4826 | 0.0087544 | 1.4826 | 0.0087544
21/11/2010 | 3.7019 | 0.058415 | 3.7019 | 0.058415
23/11/2010 | 0.27841 | 0.0028265 | 0.27841 | 0.0028265
24/11/2010 | 0.99517 | 0.0058886 | 0.99517 | 0.0058886
25/11/2010 | 0.66777 | 0.0016488 | 0.66777 | 0.0016488
28/11/2010 | 0.78915 | 0.032898 | 0.78915 | 0.032898
29/11/2010 | 0.49617 | 0.0038865 | 0.49617 | 0.0038865
01/12/2010 | 0.82322 | 0.00793 | 0.82322 | 0.00793
02/12/2010 | 0.5167 | 0.0017273 | 0.5167 | 0.0017273
03/12/2010 | 0.19087 | 0.0016095 | 0.19087 | 0.0016095
06/12/2010 | 1.9113 | 0.045931 | 1.9113 | 0.045931
07/12/2010 | 0.77776 | 0.0049857 | 0.77776 | 0.0049857
08/12/2010 | 2.3609 | 0.030542 | 2.3609 | 0.030542
09/12/2010 | 0.5266 | 0.0089507 | 0.5266 | 0.0089507
10/12/2010 | 0.63593 | 0.0076159 | 0.63593 | 0.0076159
11/12/2010 | 1.3021 | 0.0084796 | 1.3021 | 0.0084796
13/12/2010 | 2.217 | 0.0095003 | 2.217 | 0.0095003
15/12/2010 | 2.2927 | 0.028619 | 2.2927 | 0.028619
18/12/2010 | 0.78448 | 0.006713 | 0.78448 | 0.006713
19/12/2010 | 0.18663 | 0.0033761 | 0.18663 | 0.0033761
20/12/2010 | 2.2257 | 0.0029836 | 2.2257 | 0.0029836
21/12/2010 | 0.96384 | 0.002591 | 0.96384 | 0.002591
22/12/2010 | 0.89946 | 0.0024339 | 0.89946 | 0.0024339
23/12/2010 | 0.10364 | 0.00094217 | 0.10364 | 0.00094217
24/12/2010 | 1.4021 | 0.016998 | 1.4021 | 0.016998
25/12/2010 | 0.92726 | 0.0031013 | 0.92726 | 0.0031013
28/12/2010 | 3.0222 | 0.054057 | 3.0222 | 0.054057
29/12/2010 | 0.04915 | 0.0011385 | 0.04915 | 0.0011385
30/12/2010 | 0.2569 | 0.0035724 | 0.2569 | 0.0035724
04/01/2011 | 0.35496 | 0.0037687 | 0.35496 | 0.0037687
06/01/2011 | 0.027088 | 0.00090292 | 0.027088 | 0.00090292
07/01/2011 | 0.034546 | 0.00086366 | 0.034546 | 0.00086366
08/01/2011 | 0.64091 | 0.035606 | 0.64091 | 0.035606
10/01/2011 | 2.3779 | 0.0092255 | 2.3779 | 0.0092255
12/01/2011 | 0.19456 | 0.010128 | 0.19456 | 0.010128
13/01/2011 | 1.5796 | 0.0099321 | 1.5796 | 0.0099321
18/01/2011 | 0.7157 | 0.0035724 | 0.7157 | 0.0035724
19/01/2011 | 0.69277 | 0.00094217 | 0.69277 | 0.00094217
20/01/2011 | 0.44039 | 0.0069485 | 0.44039 | 0.0069485
21/01/2011 | 0.70726 | 0.029914 | 0.70726 | 0.029914
22/01/2011 | 0.17203 | 0.0005496 | 0.17203 | 0.0005496
23/01/2011 | 0.92592 | 0.013544 | 0.92592 | 0.013544
24/01/2011 | 0.77027 | 0.0040435 | 0.77027 | 0.0040435
25/01/2011 | 1.2231 | 0.019903 | 1.2231 | 0.019903
26/01/2011 | 0.12861 | 0.00035332 | 0.12861 | 0.00035332
27/01/2011 | 1.2112 | 0.02167 | 1.2112 | 0.02167
28/01/2011 | 1.3432 | 0.0035724 | 1.3432 | 0.0035724
29/01/2011 | 4.432 | 0.029364 | 4.432 | 0.029364
02/02/2011 | 0.13646 | 0.00043183 | 0.13646 | 0.00043183
03/02/2011 | 1.7128 | 0.019118 | 1.7128 | 0.019118
04/02/2011 | 0.94429 | 0.10674 | 0.94429 | 0.10674
05/02/2011 | 0.59624 | 0.008087 | 0.59624 | 0.008087
06/02/2011 | 0.21387 | 0.017823 | 0.21387 | 0.017823
07/02/2011 | 0.6711 | 0.001531 | 0.6711 | 0.001531
08/02/2011 | 2.0791 | 0.0097358 | 2.0791 | 0.0097358
09/02/2011 | 3.4343 | 0.055863 | 3.4343 | 0.055863
10/02/2011 | 0.95957 | 0.0033369 | 0.95957 | 0.0033369
14/02/2011 | 0.029914 | 0.001217 | 0.029914 | 0.001217
15/02/2011 | 0.36792 | 0.00086366 | 0.36792 | 0.00086366
16/02/2011 | 7.1915 | 0.10254 | 7.1915 | 0.10254
18/02/2011 | 1.7885 | 0.033055 | 1.7885 | 0.033055
22/02/2011 | 0.53951 | 0.0018451 | 0.53951 | 0.0018451
23/02/2011 | 0.4122 | 0.0011777 | 0.4122 | 0.0011777
24/02/2011 | 0.20139 | 0.0035332 | 0.20139 | 0.0035332
25/02/2011 | 0.2845 | 0.0040042 | 0.2845 | 0.0040042
27/02/2011 | 0.77879 | 0.0085581 | 0.77879 | 0.0085581
28/02/2011 | 0.1418 | 0.0008244 | 0.1418 | 0.0008244
01/03/2011 | 0.83826 | 0.0023947 | 0.83826 | 0.0023947
03/03/2011 | 0.057473 | 0.00047109 | 0.057473 | 0.00047109
04/03/2011 | 1.3483 | 0.0062419 | 1.3483 | 0.0062419
05/03/2011 | 3.3494 | 0.1502 | 3.3494 | 0.1502
07/03/2011 | 0.12311 | 0.0019236 | 0.12311 | 0.0019236
08/03/2011 | 0.20021 | 0.00047109 | 0.20021 | 0.00047109
09/03/2011 | 0.38158 | 0.0017666 | 0.38158 | 0.0017666
10/03/2011 | 0.61508 | 0.0077337 | 0.61508 | 0.0077337
12/03/2011 | 0.012641 | 0.0002748 | 0.012641 | 0.0002748
13/03/2011 | 0.10238 | 0.00062812 | 0.10238 | 0.00062812
14/03/2011 | 0.54599 | 0.0032584 | 0.54599 | 0.0032584
15/03/2011 | 0.58438 | 0.00062812 | 0.58438 | 0.00062812
16/03/2011 | 1.4041 | 0.0066345 | 1.4041 | 0.0066345
21/03/2011 | 0.39571 | 0.00094217 | 0.39571 | 0.00094217
22/03/2011 | 7.0486 | 0.032073 | 7.0486 | 0.032073
23/03/2011 | 4.6179 | 0.031092 | 4.6179 | 0.031092
24/03/2011 | 0.47694 | 0.0060456 | 0.47694 | 0.0060456
25/03/2011 | 0.18007 | 0.00043183 | 0.18007 | 0.00043183
27/03/2011 | 0.12346 | 0.00066737 | 0.12346 | 0.00066737
29/03/2011 | 0.39803 | 0.00086366 | 0.39803 | 0.00086366
30/03/2011 | 4.4337 | 0.031367 | 4.4337 | 0.031367

## 20102011Answer
SumOfSaidi | SumOfSafi | SumOfFixedSaidi | SumOfFixedSaifi
333.9967 | 3.4827 | 333.9967 | 3.4827

## 20092010Data
REPORT NUMBER | Date Outage | YEAR | DATE ON | Duration of Outage | Customers Impacted | Total Customer Minutes Lost | CLASS A-G | CAUSE | NOTES
12824 | 01/04/2009 | 2009 | 2009-04-01 | 46 | 25 | 1150 | B | PLANNED SHUTDOWN | Install 3 DDO fuses pole C5158 in Bells Rd
12826 | 02/04/2009 | 2009 | 2009-04-02 | 127 | 88 | 11176 | B | PLANNED SHUTDOWN | Relocate and Replace T/x B40 Wellington St
12828 | 02/04/2009 | 2009 | 2009-04-02 | 34 | 48 | 2448 | B | PLANNED SHUTDOWN | Install line breaks pole D1662 Lavenham Rd
12829 | 02/04/2009 | 2009 | 2009-04-02 | 395 | 17 | 6715 | B | PLANNED SHUTDOWN | Replace pole D1668 Lavenham Rd
12809 | 05/04/2009 | 2009 | 2009-04-05 | 51 | 132 | 2251 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable between B889 to B969 Cobden St
12823 | 07/04/2009 | 2009 | 2009-04-07 | 30 | 57 | 1710 | B | PLANNED SHUTDOWN | Connect 2 11kV DDO fuses pole C5704 Mc Laurins Rd
12810 | 08/04/2009 | 2009 | 2009-04-08 | 246 | 17 | 4182 | C | DEFECTIVE EQUIPMENT | Repair 11kv lines between F660 to F195 Rakauroa Rd
12811 | 09/04/2009 | 2009 | 2009-04-09 | 51 | 30 | 1530 | C | DEFECTIVE EQUIPMENT | Replace DDO fuse on T/x D379 Tahunga Rd
12827 | 09/04/2009 | 2009 | 2009-04-09 | 41 | 6 | 246 | B | PLANNED SHUTDOWN | Install 2 DDO fuses for T/x pole D1331 Tiniroto Rd
12812 | 12/04/2009 | 2009 | 2009-04-12 | 125 | 127 | 15875 | C | HUMAN ELEMENT | Isolate 11kV pole A3165 Endcliffe Rd Hit by Car
12830 | 15/04/2009 | 2009 | 2009-04-15 | 438 | 9 | 3942 | B | PLANNED SHUTDOWN | Install 11kV pole D1658 Lavenham Rd
12831 | 15/04/2009 | 2009 | 2009-04-15 | 7 | 45 | 315 | B | PLANNED SHUTDOWN | Remove line breaks at pole D1658 Lavenham Rd
12833 | 15/04/2009 | 2009 | 2009-04-15 | 60 | 33 | 1980 | B | PLANNED SHUTDOWN | Replace 11kV pole F1656 Koranga Valley Rd
12834 | 16/04/2009 | 2009 | 2009-04-16 | 26 | 21 | 546 | B | PLANNED SHUTDOWN | Cut 11kV jumpers Pole D2119 Lavenham Rd
12835 | 16/04/2009 | 2009 | 2009-04-16 | 396 | 8 | 3168 | B | PLANNED SHUTDOWN | Replace 5 11kV poles D2110 D2307 D2102 D370 D371 Lavenham Rd
12836 | 17/04/2009 | 2009 | 2009-04-17 | 370 | 12 | 4440 | B | PLANNED SHUTDOWN | Replace 2 11kV poles D2112 & D1671 Lavenham Rd
12837 | 17/04/2009 | 2009 | 2009-04-17 | 17 | 21 | 357 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole D2119 Lavenham Rd
12813 | 18/04/2009 | 2009 | 2009-04-18 | 309 | 75 | 4550 | C | HUMAN ELEMENT | Repair 11kV lines between H4400 to H3800 Tuakau Rd tree cut down by Owner
12814 | 20/04/2009 | 2009 | 2009-04-20 | 26 | 48 | 1248 | C | TREE CONTACTS | Remove branch from 11kV pole W6856 near Affco
12825 | 20/04/2009 | 2009 | 2009-04-20 | 55 | 48 | 4896 | B | PLANNED SHUTDOWN | Isolate 11kV Between poles C5270 to C211 Bloomfeild Rd
12815 | 21/04/2009 | 2009 | 2009-04-21 | 235 | 272 | 22732 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H757 Tuakau Rd
12816 | 21/04/2009 | 2009 | 2009-04-21 | 172 | 21 | 3612 | C | TREE CONTACTS | Repair 11kV lines between J1645 to J1646 Tuparoa Rd
12817 | 21/04/2009 | 2009 | 2009-04-21 | 85 | 225 | 4648 | C | FOREIGN INTERFERENCE | Remove possum from 11kV pole E2906 Ngakaroa Rd
12818 | 21/04/2009 | 2009 | 2009-04-21 | 122 | 8 | 1264 | C | ADVERSE WEATHER | Cut 11kV jumpers at pole J3831 Matakoa Point
12819 | 23/04/2009 | 2009 | 2009-04-23 | 60 | 80 | 4800 | C | DEFECTIVE EQUIPMENT | Install generator & repair 11kV cable to T/x A17 De Lautour Rd
12820 | 24/04/2009 | 2009 | 2009-04-24 | 8 | 230 | 1840 | C | TREE CONTACTS | Remove branch from 11kV pole W314 Nuhaka
12832 | 25/04/2009 | 2009 | 2009-04-25 | 113 | 7 | 791 | B | PLANNED SHUTDOWN | Relocate 11kV pole C483 Dunstan Rd
12821 | 26/04/2009 | 2009 | 2009-04-26 | 48 | 30 | 1440 | C | DEFECTIVE EQUIPMENT | Replace insulator on pole D2543 Pehiri Rd
12822 | 27/04/2009 | 2009 | 2009-04-27 | 101 | 77 | 7777 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole W6085 Mangapoikie Rd
12838 | 27/04/2009 | 2009 | 2009-04-27 | 43 | 87 | 2641 | B | PLANNED SHUTDOWN | Cut 11kV jumpers pole W6692 Ruakituri
12839 | 27/04/2009 | 2009 | 2009-04-27 | 3338 | 2 | 6676 | B | PLANNED SHUTDOWN | Replace poles between W993 to W6692 Ruakituri
12840 | 28/04/2009 | 2009 | 2009-04-28 | 22 | 37 | 814 | B | PLANNED SHUTDOWN | Replace poles between W993 to W6692 Ruakituri
12841 | 28/04/2009 | 2009 | 2009-04-28 | 1 | 138 | 138 | B | PLANNED SHUTDOWN | Change over to Generator Ruakituri at pole W7358
12842 | 30/04/2009 | 2009 | 2009-04-30 | 28 | 43 | 1204 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at pole W985 Ruakituri
12843 | 30/04/2009 | 2009 | 2009-04-30 | 488 | 7 | 3416 | B | PLANNED SHUTDOWN | Replace 14 11kV poles W 985 to W 1056 Ruakituri
12858 | 01/05/2009 | 2009 | 2009-05-01 | 22 | 91 | 2002 | B | PLANNED SHUTDOWN | Isolate 11kV to connect Generator W7358 Crosshills Stn
12859 | 01/05/2009 | 2009 | 2009-05-01 | 18 | 40 | 720 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole W985 Te Tuhi Stn
12844 | 04/05/2009 | 2009 | 2009-05-04 | 169 | 193 | 16348 | C | FOREIGN INTERFERENCE | Repair 11kV between poles E618 & E619 Kanakanaia Rd
12845 | 04/05/2009 | 2009 | 2009-05-04 | 65 | 28 | 1820 | C | DEFECTIVE EQUIPMENT | Repair 11kV ABS F309 Rakauroa Rd
12846 | 05/05/2009 | 2009 | 2009-05-05 | 180 | 6 | 1080 | C | TREE CONTACTS | Repair 11kV ABS F309 Rakauroa Rd
12847 | 05/05/2009 | 2009 | 2009-05-05 | 22 | 91 | 2002 | B | PLANNED SHUTDOWN | Connect Generator & pole W7358 Crosshills Stn
12860 | 05/05/2009 | 2009 | 2009-05-05 | 52 | 65 | 3380 | B | PLANNED SHUTDOWN | Remove Temp links D2153 Lavenham Rd
12865 | 07/05/2009 | 2009 | 2009-05-07 | 14 | 40 | 1080 | B | PLANNED SHUTDOWN | Cut 11kV jumpers pole W985 Ruakituri
12848 | 13/05/2009 | 2009 | 2009-05-13 | 152 | 8 | 1216 | C | LIGHTNING | Repair 11kV jumper pole E148 Kanakanaia Rd
12849 | 18/05/2009 | 2009 | 2009-05-18 | 238 | 208 | 11423 | C | TREE CONTACTS | Repair 11kV lines pole A821 Rototahi Stn
12866 | 18/05/2009 | 2009 | 2009-05-18 | 14 | 40 | 560 | B | PLANNED SHUTDOWN | Disconnect Generator 7 at Crosshill Stn W7358
12861 | 21/05/2009 | 2009 | 2009-05-21 | 496 | 134 | 32760 | B | PLANNED SHUTDOWN | Cut 11kV jumpers pole A2561 Lloyd George Rd Murphy Rd Crn
12864 | 21/05/2009 | 2009 | 2009-05-21 | 26 | 135 | 5940 | B | PLANNED SHUTDOWN | Connect 3 DDO fuses pole A4135 Huxley Rd
12850 | 22/05/2009 | 2009 | 2009-05-22 | 12 | 2784 | 33408 | C | HUMAN ELEMENT | Reclose CB A516 at Kaiti Sub
12851 | 23/05/2009 | 2009 | 2009-05-23 | 142 | 642 | 48100 | C | HUMAN ELEMENT | Repair 11kV cable Pole A2268 Lyell Rd damaged by Screw Anchour
12852 | 24/05/2009 | 2009 | 2009-05-24 | 17 | 128 | 1855 | C | DEFECTIVE EQUIPMENT | Isolate T/x J590 East Cape Rd & reclose CBJ524 Te Araroa Sub
12854 | 25/05/2009 | 2009 | 2009-05-25 | 93 | 12 | 1116 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W7990 Omana Rd
12862 | 25/05/2009 | 2009 | 2009-05-25 | 22 | 65 | 1430 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at pole A2104 Moana Rd
12853 | 26/05/2009 | 2009 | 2009-05-26 | 33 | 836 | 23143 | C | DEFECTIVE EQUIPMENT | Close ABS W807 & Start generator to Support Voltage
12867 | 26/05/2009 | 2009 | 2009-05-26 | 263 | 51 | 9948 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting Opoutama W950
12855 | 27/05/2009 | 2009 | 2009-05-27 | 111 | 16 | 1776 | C | DEFECTIVE EQUIPMENT | Replace 11kV disc on ABS H123 Mata Rd
12868 | 27/05/2009 | 2009 | 2009-05-27 | 140 | 21 | 2940 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting Hillcrest W1234
12869 | 27/05/2009 | 2009 | 2009-05-27 | 140 | 82 | 11480 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting Mahunga Beach W1106
12870 | 28/05/2009 | 2009 | 2009-05-28 | 408 | 52 | 4176 | B | PLANNED SHUTDOWN | Cut & rejoin 11kV jumpers D1469 & replace poles Kaimoe Rd
12863 | 29/05/2009 | 2009 | 2009-05-29 | 22 | 65 | 1430 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole A2104 Moana Rd
12871 | 29/05/2009 | 2009 | 2009-05-29 | 406 | 29 | 3062 | B | PLANNED SHUTDOWN | Install line breaks D3088 & change pole D3082 Wharekopae Rd
12856 | 30/05/2009 | 2009 | 2009-05-30 | 127 | 97 | 12319 | C | FOREIGN INTERFERENCE | Replace 11kV pole C1210 Whakatoa Rd hit by Car
12857 | 31/05/2009 | 2009 | 2009-05-31 | 2340 | 92 | 22139 | C | TREE CONTACTS | Remove branchs from 11kV Tarndale Rd & Close ABS E203
12872 | 01/06/2009 | 2009 | 2009-06-01 | 529 | 138 | 72822 | C | ADVERSE WEATHER | Reclose CB816 cause Snow
12873 | 01/06/2009 | 2009 | 2009-06-01 | 574 | 59 | 26984 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole C821 Waingake Rd
12874 | 01/06/2009 | 2009 | 2009-06-01 | 212 | 17 | 3604 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole A3618 Waiomoko Rd
12875 | 01/06/2009 | 2009 | 2009-06-01 | 756 | 67 | 28686 | C | TREE CONTACTS | Repair 11kV lines pole F2443 Motu Fall Rd
12876 | 02/06/2009 | 2009 | 2009-06-02 | 152 | 12 | 1824 | C | TREE CONTACTS | Remove tree from 11kV at pole G225 Tutamoe Rd
12877 | 02/06/2009 | 2009 | 2009-06-02 | 84 | 11 | 924 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at T/x F86 Whakarau Rd
12878 | 03/06/2009 | 2009 | 2009-06-03 | 254 | 64 | 16256 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole C2637 Tau rau Valley
12879 | 03/06/2009 | 2009 | 2009-06-03 | 250 | 24 | 6000 | C | DEFECTIVE EQUIPMENT | Repair 11kV pole A4588 Glenroy Rd
12901 | 04/06/2009 | 2009 | 2009-06-04 | 45 | 262 | 11790 | B | PLANNED SHUTDOWN | Remove 11kV jumpers pole A2331 Wainui Rd
12903 | 06/06/2009 | 2009 | 2009-06-06 | 148 | 19 | 2812 | B | PLANNED SHUTDOWN | Isolate 11kV lines at W1134 for tree cutting Ruapapa Rd
12904 | 10/06/2009 | 2009 | 2009-06-10 | 321 | 19 | 6099 | B | PLANNED SHUTDOWN | Replace 11kV pole F757 Makaretu Rd
12880 | 13/06/2009 | 2009 | 2009-06-13 | 402 | 480 | 44890 | C | DEFECTIVE EQUIPMENT | Isolate T/x A84 Riverside Rd
12881 | 13/06/2009 | 2009 | 2009-06-13 | 32 | 335 | 10720 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole A4137 Huxley Rd
12882 | 13/06/2009 | 2009 | 2009-06-13 | 156 | 583 | 37810 | C | ADVERSE WEATHER | Repair 11kV lines at pole A3572 Wainui
12883 | 13/06/2009 | 2009 | 2009-06-13 | 112 | 169 | 18928 | C | DEFECTIVE EQUIPMENT | Temp prop 11kV pole B32 Hospital Rd
12884 | 13/06/2009 | 2009 | 2009-06-13 | 694 | 193 | 15481 | C | ADVERSE WEATHER | Repair 11kV lines between E1109 to E1110 Kanakanaia Rd
12885 | 13/06/2009 | 2009 | 2009-06-13 | 264 | 160 | 15712 | C | DEFECTIVE EQUIPMENT | Replace 11kV Xarm on pole G1840 Paramata Rd
12886 | 13/06/2009 | 2009 | 2009-06-13 | 7 | 3680 | 25760 | C | ADVERSE WEATHER | Reclose CB 35 at Makaraka Sub High Winds
12887 | 13/06/2009 | 2009 | 2009-06-13 | 43 | 1087 | 36135 | C | ADVERSE WEATHER | Reclose CB B825 Carnarvon St Sub High Winds
12888 | 13/06/2009 | 2009 | 2009-06-13 | 19 | 271 | 4206 | C | ADVERSE WEATHER | Reclose CB W790 Tahaenui Sub High Winds
12889 | 13/06/2009 | 2009 | 2009-06-13 | 16 | 311 | 4976 | C | DEFECTIVE EQUIPMENT | Change fuse carrier T/x W1510 Mahia
12890 | 13/06/2009 | 2009 | 2009-06-13 | 225 | 5 | 1125 | C | TREE CONTACTS | Repair 11kV lines at pole C321 Bck Ormond Rd
12891 | 14/06/2009 | 2009 | 2009-06-14 | 23 | 38 | 874 | C | DEFECTIVE EQUIPMENT | Rejoin 11kV jumpers pole A4231 Riverside Rd
12892 | 15/06/2009 | 2009 | 2009-06-15 | 16 | 8 | 128 | C | TREE CONTACTS | Remove tree from 11kV pole G4224 SH35 Arero
12893 | 18/06/2009 | 2009 | 2009-06-18 | 28 | 27 | 756 | C | DEFECTIVE EQUIPMENT | Temp replace 11kV disc pole E3778 Ngakaroa Rd
12902 | 18/06/2009 | 2009 | 2009-06-18 | 60 | 262 | 15720 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers at pole A2331 Wainui Rd
12894 | 20/06/2009 | 2009 | 2009-06-20 | 105 | 32 | 3360 | C | DEFECTIVE EQUIPMENT | Isolate T/x D531 at cut jumpers D284 Ruakaka Rd
12895 | 22/06/2009 | 2009 | 2009-06-22 | 21 | 32 | 672 | C | DEFECTIVE EQUIPMENT | Rejoin 11kV jumpers pole at D284 Ruakaka Rd
12905 | 22/06/2009 | 2009 | 2009-06-22 | 143 | 19 | 2717 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting W1157 Kiwi Valley Rd
12907 | 23/06/2009 | 2009 | 2009-06-23 | 306 | 18 | 5508 | B | PLANNED SHUTDOWN | Isolate 11kV for 13 Pole replacements Mohaka beyond W1006
12906 | 25/06/2009 | 2009 | 2009-06-25 | 328 | 27 | 8856 | B | PLANNED SHUTDOWN | Isolate 11kV lines W992 for tree cutting Ohuka Mahiwi
12908 | 25/06/2009 | 2009 | 2009-06-25 | 43 | 112 | 7168 | B | PLANNED SHUTDOWN | Replace 11kV poles B1183 & B1184 Sheehan St
12896 | 26/06/2009 | 2009 | 2009-06-26 | 108 | 138 | 11760 | C | TREE CONTACTS | Repair 11kV lines pole W7327 Ruaktituri
12897 | 26/06/2009 | 2009 | 2009-06-26 | 1170 | 193 | 14310 | C | TREE CONTACTS | Repair 11kV lines pole E1129 Kanakanaia Rd
12898 | 29/06/2009 | 2009 | 2009-06-29 | 10 | 99 | 990 | C | ADVERSE WEATHER | Reclose E864 Waimata Valley High Winds
12900 | 29/06/2009 | 2009 | 2009-06-29 | 598 | 367 | 30641 | C | DEFECTIVE EQUIPMENT | Isolate 11kV lines pole W71 Cricklewood Rd
12899 | 30/06/2009 | 2009 | 2009-06-30 | 382 | 72 | 3591 | C | TREE CONTACTS | Remove tree from 11kV pole G627 Hokoroa Rd
12909 | 01/07/2009 | 2009 | 2009-07-01 | 1514 | 22 | 33308 | C | ADVERSE ENVIRONMENT | Reposition 11kV Pole J3711 road slipped away Horoera
12961 | 01/07/2009 | 2009 | 2009-07-01 | 46 | 58 | 2668 | B | PLANNED SHUTDOWN | Install SDAF3 Oil Switch J643 Ruatoria
12910 | 02/07/2009 | 2009 | 2009-07-02 | 908 | 95 | 38036 | C | TREE CONTACTS | Reposition 11kV Pole J3711 road slipped away Horoera
12911 | 02/07/2009 | 2009 | 2009-07-02 | 1762 | 22 | 32568 | C | ADVERSE ENVIRONMENT | Relocate 11kV pole W6659 from river slip Tukemokihi Rd
12962 | 02/07/2009 | 2009 | 2009-07-02 | 54 | 46 | 3650 | B | PLANNED SHUTDOWN | Cut 11kV jumpers at pole J4750 Ruatoria
12912 | 03/07/2009 | 2009 | 2009-07-03 | 5407 | 5 | 27035 | C | ADVERSE WEATHER | Replace 11kV pole W6289 Cricklewood Rd
12913 | 03/07/2009 | 2009 | 2009-07-03 | 227 | 156 | 8448 | C | FOREIGN INTERFERENCE | Repair 11kV lines between poles G1585 & G1586 Arakihi Rd
12914 | 04/07/2009 | 2009 | 2009-07-04 | 530 | 156 | 45254 | C | FOREIGN INTERFERENCE | Repair 11kV lines at pole G1844 Paramata Rd
12915 | 04/07/2009 | 2009 | 2009-07-04 | 51 | 18 | 918 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole G1822 Paramata Rd
12916 | 04/07/2009 | 2009 | 2009-07-04 | 142 | 123 | 9182 | C | DEFECTIVE EQUIPMENT | Isolate 11kV lines at poles H1854 & H1853 SH35 Makarika
12917 | 05/07/2009 | 2009 | 2009-07-05 | 239 | 77 | 18403 | C | DEFECTIVE EQUIPMENT | Replace 11kV lines pole W7862 Mangapoikie Rd
12918 | 06/07/2009 | 2009 | 2009-07-06 | 175 | 16 | 2800 | C | ADVERSE WEATHER | Isolate 11kV lines for 400V LV repairs pole E2185
12963 | 07/07/2009 | 2009 | 2009-07-07 | 180 | 8 | 1440 | B | PLANNED SHUTDOWN | Erect 3 DDO fuse on pole E1147 Kanakanaia Rd
12965 | 07/07/2009 | 2009 | 2009-07-07 | 38 | 62 | 6758 | B | PLANNED SHUTDOWN | Replace 11kV poles A2104 A2105 A2107 A2108 A2110 Moana Rd
12966 | 07/07/2009 | 2009 | 2009-07-07 | 303 | 183 | 14865 | B | PLANNED SHUTDOWN | Replace 11kV pole J1267 Ruatoria
12969 | 07/07/2009 | 2009 | 2009-07-07 | 265 | 17 | 4505 | B | PLANNED SHUTDOWN | Isolate E142 11kV lines for tree cutting Waitangi Rd
12919 | 08/07/2009 | 2009 | 2009-07-08 | 110 | 29 | 3190 | C | ADVERSE WEATHER | Replace 11kV lines between poles H1858 to H1853 Reedys Hill SH35
12967 | 08/07/2009 | 2009 | 2009-07-08 | 462 | 128 | 24878 | B | PLANNED SHUTDOWN | Replace 11kV poles J1276 J1278 Ruatoria
12920 | 13/07/2009 | 2009 | 2009-07-13 | 2469 | 351 | 81755 | C | TREE CONTACTS | Repair 11kV lines pole J2913 Waiomatatini Rd
12921 | 13/07/2009 | 2009 | 2009-07-13 | 302 | 122 | 21046 | C | TREE CONTACTS | Repair 11kV lines Poles H1497 to H1498 SH35 Makarika
12922 | 13/07/2009 | 2009 | 2009-07-13 | 69 | 8 | 552 | C | ADVERSE WEATHER | Repair 11kV lines between poles J3276 & J3277 Matakoa Point
12968 | 13/07/2009 | 2009 | 2009-07-13 | 193 | 25 | 4825 | B | PLANNED SHUTDOWN | Relocate 11kV pole J1010 Poroporo Valley Rd
12930 | 14/07/2009 | 2009 | 2009-07-14 | 353 | 104 | 17142 | B | PLANNED SHUTDOWN | Install line breaks pole C5819 Gladstone Rd
12970 | 14/07/2009 | 2009 | 2009-07-14 | 102 | 5 | 510 | B | PLANNED SHUTDOWN | Replace 11kV pole J1039 Ruatoria
12971 | 14/07/2009 | 2009 | 2009-07-14 | 115 | 66 | 7590 | B | PLANNED SHUTDOWN | Replace 11kV pole J1157 Ruatoria
12964 | 15/07/2009 | 2009 | 2009-07-15 | 450 | 98 | 20320 | B | PLANNED SHUTDOWN | Replace 11kV pole B32 Hospital Rd
12972 | 15/07/2009 | 2009 | 2009-07-15 | 250 | 48 | 12000 | B | PLANNED SHUTDOWN | Replace 11kV poles J4742 J4744 J4746 J4748 Ruatoria
12923 | 16/07/2009 | 2009 | 2009-07-16 | 5 | 844 | 4220 | C | HUMAN ELEMENT | Reclose CB B824 Childers Rd Switching Error
12973 | 16/07/2009 | 2009 | 2009-07-16 | 219 | 48 | 10512 | B | PLANNED SHUTDOWN | Replace 11kV poles J4746 & J4748 Ruatoria
12924 | 19/07/2009 | 2009 | 2009-07-19 | 1329 | 167 | 19368 | C | TREE CONTACTS | Repair 11kV lines between poles A3531 to A3532 Glenroy Rd
12925 | 19/07/2009 | 2009 | 2009-07-19 | 459 | 176 | 80784 | C | DEFECTIVE EQUIPMENT | Relocate 11kV pole W6928 at Ohuka
12926 | 20/07/2009 | 2009 | 2009-07-20 | 557 | 176 | 23597 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole W7006 Ohuka Rd
12927 | 20/07/2009 | 2009 | 2009-07-20 | 68 | 35 | 2380 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole H1069 Bremner Stn Mata Rd
12928 | 21/07/2009 | 2009 | 2009-07-21 | 49 | 176 | 8008 | C | UNKNOWN | Reclose CB W816 Ohuka cause unknown
12932 | 21/07/2009 | 2009 | 2009-07-21 | 314 | 100 | 9360 | B | PLANNED SHUTDOWN | Replace 11kV poles J1357 & J1328 Ruatoria
12958 | 21/07/2009 | 2009 | 2009-07-21 | 404 | 58 | 6794 | B | PLANNED SHUTDOWN | Replace 11kV ABS pole C604 Taurau Valley
12960 | 21/07/2009 | 2009 | 2009-07-21 | 44 | 7 | 308 | B | PLANNED SHUTDOWN | Reconnect jumpers at pole H153 Ihungia Rd
12931 | 22/07/2009 | 2009 | 2009-07-22 | 498 | 21 | 10458 | B | PLANNED SHUTDOWN | Replace 11kV poles J1599 J1621 & J1634 Ruatoria
12959 | 22/07/2009 | 2009 | 2009-07-22 | 403 | 5 | 2015 | B | PLANNED SHUTDOWN | Replace 11kV pole C4791 Foxley Rd
12929 | 23/07/2009 | 2009 | 2009-07-23 | 48 | 6 | 288 | C | DEFECTIVE EQUIPMENT | Repair 11kV pole J2473 East Cape Rd
12933 | 23/07/2009 | 2009 | 2009-07-23 | 108 | 26 | 2808 | C | ADVERSE WEATHER | Reposition T/x pole D3095 Wharekopae Rd
12935 | 23/07/2009 | 2009 | 2009-07-23 | 684 | 123 | 45039 | C | ADVERSE WEATHER | Repair 11kV lines between H1494 to H66 SH35 Makarika
12936 | 23/07/2009 | 2009 | 2009-07-23 | 1196 | 92 | 69458 | C | ADVERSE WEATHER | Repair 11kV lines at pole E861Armstrong Rd
12937 | 23/07/2009 | 2009 | 2009-07-23 | 778 | 176 | 136639 | C | ADVERSE WEATHER | Patrol line Helicopter Reclosed CB 24 Tuai Cause unknown
12938 | 23/07/2009 | 2009 | 2009-07-23 | 1431 | 62 | 77178 | C | TREE CONTACTS | Replace 11kV pole D5068 Wharekopae Rd
12954 | 23/07/2009 | 2009 | 2009-07-23 | 197 | 18 | 3546 | B | PLANNED SHUTDOWN | Replace poles J1702 J1703 J1683 J120 J118 Ruatoria
12934 | 24/07/2009 | 2009 | 2009-07-24 | 860 | 825 | 153575 | C | ADVERSE WEATHER | Repair 11kV lines between J2411 to J2412 SH35 Te Araroa
12939 | 24/07/2009 | 2009 | 2009-07-24 | 38 | 6 | 228 | C | TREE CONTACTS | Remove tree from 11kV pole J242 Koia Rd Tikitiki
12940 | 24/07/2009 | 2009 | 2009-07-24 | 147 | 71 | 10437 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole A4539 Wainui
12941 | 24/07/2009 | 2009 | 2009-07-24 | 57 | 3 | 171 | C | TREE CONTACTS | Repair 11kV lines at pole J3625 Tikitiki Radio Tapp Off
12942 | 24/07/2009 | 2009 | 2009-07-24 | 498 | 13 | 6474 | C | TREE CONTACTS | Remove tree from 11kV pole H32 Pukititi Stn Te Puia
12943 | 24/07/2009 | 2009 | 2009-07-24 | 160 | 136 | 4896 | C | TREE CONTACTS | Replace 11kV pole H4320 Tokomaru Bay
12944 | 24/07/2009 | 2009 | 2009-07-24 | 197 | 76 | 19129 | C | DEFECTIVE EQUIPMENT | Replace insulator on pole F2513 Te Wera Rd Matawai
12945 | 24/07/2009 | 2009 | 2009-07-24 | 1172 | 17 | 19924 | C | ADVERSE WEATHER | Restrain 11kV at pole F309 Rakauroa Rd
12946 | 25/07/2009 | 2009 | 2009-07-25 | 37 | 13 | 481 | C | ADVERSE WEATHER | Repair 11kV jumper pole F4825 Rakauroa Rd
12947 | 25/07/2009 | 2009 | 2009-07-25 | 80 | 2 | 160 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole H2796 Mata Rd
12948 | 26/07/2009 | 2009 | 2009-07-26 | 72 | 10 | 720 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole H1048 Ihungia Rd
12949 | 27/07/2009 | 2009 | 2009-07-27 | 277 | 2 | 554 | C | ADVERSE WEATHER | Change T/x H270 Makarika
12951 | 27/07/2009 | 2009 | 2009-07-27 | 89 | 119 | 5191 | C | TREE CONTACTS | Repair 11kV lines at pole C183 Muriwai
12957 | 29/07/2009 | 2009 | 2009-07-29 | 375 | 134 | 34220 | B | PLANNED SHUTDOWN | Replace 11kV Poles A2524 A2531 A2536 & A2541 Lloyd George Rd
12953 | 30/07/2009 | 2009 | 2009-07-30 | 13 | 152 | 1976 | B | PLANNED SHUTDOWN | Install 3 DDO fuses on pole A2969 Lynsar Rd Wainui
12955 | 30/07/2009 | 2009 | 2009-07-30 | 46 | 447 | 20562 | B | PLANNED SHUTDOWN | Replace 11kV poles A2571 A2570 A524 A2566 A2564 A2562 Murphy Rd
12956 | 30/07/2009 | 2009 | 2009-07-30 | 41 | 88 | 3608 | B | PLANNED SHUTDOWN | Cut jumpers at pole A2538 Murphy Rd
12950 | 31/07/2009 | 2009 | 2009-07-31 | 8 | 27 | 216 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole D2013 Lavenham Rd
12952 | 31/07/2009 | 2009 | 2009-07-31 | 41 | 58 | 2378 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines at pole F2513 Mangatu Rd
12974 | 04/08/2009 | 2009 | 2009-08-04 | 183 | 41 | 4063 | C | FOREIGN INTERFERENCE | Replace 11kV pole G4283 Rototahi
13013 | 04/08/2009 | 2009 | 2009-08-04 | 415 | 67 | 7824 | B | PLANNED SHUTDOWN | Replace poles D424 D4568 & D4566 Jackson Rd
13022 | 05/08/2009 | 2009 | 2009-08-05 | 318 | 85 | 27030 | B | PLANNED SHUTDOWN | Replace T/x pole B915 Atkinson St
12975 | 06/08/2009 | 2009 | 2009-08-06 | 234 | 935 | 95663 | C | TREE CONTACTS | Repair 11kV lines between A2922 & A2923 Surf Shop Crn
13014 | 06/08/2009 | 2009 | 2009-08-06 | 420 | 67 | 7205 | B | PLANNED SHUTDOWN | Replace poles D4573 D4572 & D4567 Jackson Rd
13023 | 07/08/2009 | 2009 | 2009-08-07 | 314 | 50 | 15700 | B | PLANNED SHUTDOWN | Replace Poles G1466 G3057 Anaura Bay
12976 | 08/08/2009 | 2009 | 2009-08-08 | 790 | 274 | 16843 | C | ADVERSE WEATHER | Repair 11kV lines pole W137 Morere
12977 | 08/08/2009 | 2009 | 2009-08-08 | 232 | 154 | 9068 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole G1693 Tauwhareparae Rd
12978 | 10/08/2009 | 2009 | 2009-08-10 | 78 | 253 | 15107 | C | UNKNOWN | Reclose CB D14 cause unknown
12979 | 10/08/2009 | 2009 | 2009-08-10 | 49 | 16 | 784 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole H2202 Waipiro Bay Rd
13017 | 10/08/2009 | 2009 | 2009-08-10 | 408 | 509 | 58103 | B | PLANNED SHUTDOWN | Replace 11kV pole B924 Dalrymple Rd
13016 | 11/08/2009 | 2009 | 2009-08-11 | 455 | 67 | 18288 | B | PLANNED SHUTDOWN | Replace ABS pole J95 & T/x J118 Ruatoria
13018 | 11/08/2009 | 2009 | 2009-08-11 | 306 | 140 | 27552 | B | PLANNED SHUTDOWN | Replace pole B2285 Dalrymple Rd
12980 | 12/08/2009 | 2009 | 2009-08-12 | 456 | 61 | 10500 | C | TREE CONTACTS | Repair 11kV lines at pole A3759 Panikau Rd
12981 | 12/08/2009 | 2009 | 2009-08-12 | 26 | 254 | 6604 | C | UNKNOWN | Reclose Inc D13 at Ngatapa Sub cause unknown
13019 | 12/08/2009 | 2009 | 2009-08-12 | 311 | 46 | 14306 | B | PLANNED SHUTDOWN | Replace poles B2280 & B2279 Dalrymple Rd
13020 | 13/08/2009 | 2009 | 2009-08-13 | 420 | 487 | 47858 | B | PLANNED SHUTDOWN | Replace pole B572 & line breaks B2282 & B2123 Stout St
12982 | 14/08/2009 | 2009 | 2009-08-14 | 16 | 6 | 96 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper T/x pole B5057 Centennial Marine Drive
13015 | 14/08/2009 | 2009 | 2009-08-14 | 71 | 12 | 852 | B | PLANNED SHUTDOWN | Replace poles C2020 C1594 & C1548 Bck Ormond Rd
12983 | 17/08/2009 | 2009 | 2009-08-17 | 55 | 7 | 385 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole C45 Papatu Rd
12984 | 18/08/2009 | 2009 | 2009-08-18 | 18 | 28 | 504 | C | DEFECTIVE EQUIPMENT | Temp prop 11kV pole E1269 Komihana Rd
13021 | 18/08/2009 | 2009 | 2009-08-18 | 447 | 57 | 25479 | B | PLANNED SHUTDOWN | Replace poles E680 E1578 E682 E683 E183 Mangatu Rd
13025 | 19/08/2009 | 2009 | 2009-08-19 | 310 | 16 | 4960 | B | PLANNED SHUTDOWN | Install ABS pole E1329 & cut jumpers pole E1469 Kaiteratahi
12986 | 20/08/2009 | 2009 | 2009-08-20 | 133 | 75 | 7187 | C | TREE CONTACTS | Remove tree from 11kV lines pole H796 Mata Rd
13024 | 20/08/2009 | 2009 | 2009-08-20 | 60 | 52 | 3120 | B | PLANNED SHUTDOWN | Install Ddo fuse on pole C5704 Mc Laurins Rd
13026 | 20/08/2009 | 2009 | 2009-08-20 | 395 | 96 | 13032 | B | PLANNED SHUTDOWN | Replace ABS E280 7 cut jumpers D383 Kaiteratahi
12985 | 22/08/2009 | 2009 | 2009-08-22 | 277 | 77 | 21329 | C | ADVERSE WEATHER | Repair 11kv lines between W6041 to W6042 Mangapoikie Rd
12987 | 23/08/2009 | 2009 | 2009-08-23 | 175 | 438 | 75602 | C | FOREIGN INTERFERENCE | Replace 11kV Xarm on pole F3212 Puha
13031 | 24/08/2009 | 2009 | 2009-08-24 | 180 | 6 | 1080 | B | PLANNED SHUTDOWN | Restrain 11kV lines beyond fuses C133 Browns Beach Rd
12988 | 25/08/2009 | 2009 | 2009-08-25 | 82 | 14 | 1148 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper on pole D3574 Ruakaka Rd
13012 | 25/08/2009 | 2009 | 2009-08-25 | 329 | 13 | 4277 | B | PLANNED SHUTDOWN | Replace 11kV pole D3078 Wharekopae Rd
13028 | 25/08/2009 | 2009 | 2009-08-25 | 44 | 65 | 2860 | B | PLANNED SHUTDOWN | Fit D shackles to ABS C604 Taurau Valley
13029 | 25/08/2009 | 2009 | 2009-08-25 | 269 | 128 | 19215 | B | PLANNED SHUTDOWN | Cut jumpers J1253 Replace ABS J95 & remove temp links J4748 Ruatoria
13032 | 25/08/2009 | 2009 | 2009-08-25 | 172 | 10 | 1720 | B | PLANNED SHUTDOWN | Fit Ddo fuses pole E1302 Waimata Valley Rd
12989 | 26/08/2009 | 2009 | 2009-08-26 | 291 | 259 | 25101 | C | ADVERSE WEATHER | Repair 11kV lines between W1023 to W807 Nuhaka
12990 | 26/08/2009 | 2009 | 2009-08-26 | 357 | 28 | 9996 | C | DEFECTIVE EQUIPMENT | Replace 11kV burnt pole J2177 Maraehara Rd
12991 | 26/08/2009 | 2009 | 2009-08-26 | 582 | 271 | 63602 | C | ADVERSE WEATHER | Repair 11kV lines between W8377 to W8378 Morere Hill
12992 | 27/08/2009 | 2009 | 2009-08-27 | 200 | 8 | 1600 | C | TREE CONTACTS | Replace 11kV pole G2225 Takapau Rd
12993 | 27/08/2009 | 2009 | 2009-08-27 | 227 | 138 | 13123 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole D3656 Bushy Knoll Rd
12994 | 27/08/2009 | 2009 | 2009-08-27 | 62 | 5 | 310 | C | DEFECTIVE EQUIPMENT | Replace 11kV Xarm pole H1703 Kawera Rd
12995 | 27/08/2009 | 2009 | 2009-08-27 | 1539 | 176 | 26737 | C | TREE CONTACTS | Repair 11kV line pole W5281 to W5280 Kakariki
13027 | 27/08/2009 | 2009 | 2009-08-27 | 93 | 187 | 16463 | B | PLANNED SHUTDOWN | Remove ABS E144 & replace jumpers pole E1469 Kaiteratahi
13030 | 27/08/2009 | 2009 | 2009-08-27 | 192 | 96 | 6882 | B | PLANNED SHUTDOWN | Cut 11kV jumpers J1371 & replace pole J1377 Ruatoria
12996 | 28/08/2009 | 2009 | 2009-08-28 | 82 | 24 | 3146 | C | DEFECTIVE EQUIPMENT | Repair 11kV Pole D3656 Bushy Knoll Rd
12997 | 30/08/2009 | 2009 | 2009-08-30 | 757 | 168 | 28862 | C | TREE CONTACTS | Repair 11kV lines pole D3446 Taumata Rd
12998 | 31/08/2009 | 2009 | 2009-08-31 | 77 | 215 | 3544 | C | ADVERSE WEATHER | Isolate Broken 11kV pole W3686 Pokopoko
12999 | 31/08/2009 | 2009 | 2009-08-31 | 218 | 141 | 26995 | C | ADVERSE WEATHER | Repair 11kV lines pole D239 Kiteroa Stn Hangaroa
13000 | 31/08/2009 | 2009 | 2009-08-31 | 362 | 266 | 28588 | C | ADVERSE WEATHER | Replace 11kV pole E1961 Te Hau Rd Whatatutu
13001 | 31/08/2009 | 2009 | 2009-08-31 | 29 | 13 | 377 | C | ADVERSE WEATHER | Cut 11kV jumpers W7793 Waitai Rd
13002 | 31/08/2009 | 2009 | 2009-08-31 | 149 | 2 | 298 | C | ADVERSE WEATHER | Repair 11kV lines pole J312 Awatete
13003 | 31/08/2009 | 2009 | 2009-08-31 | 194 | 4 | 776 | C | ADVERSE WEATHER | Repair 11kv lines pole J2772 Kiwinui Stn
13004 | 31/08/2009 | 2009 | 2009-08-31 | 30 | 122 | 1710 | C | ADVERSE WEATHER | Reclose CB J545 Makarika Ruatoria Sub High Winds
13005 | 31/08/2009 | 2009 | 2009-08-31 | 8 | 1105 | 8840 | C | ADVERSE WEATHER | Reclose Inc 1 F411 Puha Sub High Wins Start Generator
13006 | 31/08/2009 | 2009 | 2009-08-31 | 94 | 9 | 846 | C | ADVERSE WEATHER | Repair 11kV lines D1173 Bellerbys Rd
13007 | 31/08/2009 | 2009 | 2009-08-31 | 228 | 382 | 31251 | C | ADVERSE WEATHER | Repair 11kV lines D1173 Bellerbys Rd
13008 | 31/08/2009 | 2009 | 2009-08-31 | 195 | 71 | 6549 | C | ADVERSE WEATHER | Repair floating wire pole F2062 Whakarau Rd
13009 | 31/08/2009 | 2009 | 2009-08-31 | 8 | 1110 | 71040 | C | ADVERSE WEATHER | Close W2 at Wairoa Sub after line Check High Winds
13010 | 31/08/2009 | 2009 | 2009-08-31 | 291 | 176 | 57552 | C | ADVERSE WEATHER | Reclose CB 24 at Tuai High Winds
13011 | 31/08/2009 | 2009 | 2009-08-31 | 41 | 523 | 18310 | C | ADVERSE WEATHER | Cut jumpers pole A3572 Wheatstone Rd
13033 | 01/09/2009 | 2009 | 2009-09-01 | 48 | 13 | 624 | C | DEFECTIVE EQUIPMENT | Repair 11kV line at pole W7798 Waitai Valley
13034 | 01/09/2009 | 2009 | 2009-09-01 | 56 | 398 | 22288 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper at pole W1157 Kiwi Valley Rd
13035 | 01/09/2009 | 2009 | 2009-09-01 | 170 | 5 | 850 | C | TREE CONTACTS | Remove tree form 11kV at T/x pole D434 Faulkners Rd
13036 | 01/09/2009 | 2009 | 2009-09-01 | 163 | 10 | 1630 | C | ADVERSE WEATHER | Rejoin jumpers & fit DDO fuses pole A3572 Wheatstone Rd
13037 | 01/09/2009 | 2009 | 2009-09-01 | 369 | 5 | 1845 | C | ADVERSE WEATHER | Isolate 11kV pole H3340 Bexhaven Stn Mata Rd
13038 | 03/09/2009 | 2009 | 2009-09-03 | 134 | 28 | 3752 | C | DEFECTIVE EQUIPMENT | Replace 11kV poles E1270 & H1269 Mangamaia Rd
13039 | 03/09/2009 | 2009 | 2009-09-03 | 69 | 836 | 26847 | C | FOREIGN INTERFERENCE | Remove possum from 11kV ploe W804 Mahia
13058 | 03/09/2009 | 2009 | 2009-09-03 | 472 | 62 | 21200 | B | PLANNED SHUTDOWN | Install line breaks pole A2116 Moana Rd
13040 | 04/09/2009 | 2009 | 2009-09-04 | 398 | 92 | 10491 | C | UNKNOWN | Patrol 11kV lines nothing found Very High Winds
13059 | 04/09/2009 | 2009 | 2009-09-04 | 475 | 62 | 32528 | B | PLANNED SHUTDOWN | Replace 11kV poles A2121 A2122 A2123 A2124 A2125 Moana Rd
13041 | 07/09/2009 | 2009 | 2009-09-07 | 59 | 9 | 531 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole E392 Tarndale Rd
13060 | 07/09/2009 | 2009 | 2009-09-07 | 460 | 130 | 42234 | B | PLANNED SHUTDOWN | Replace 11kV poles A2170 & A2171 Douglas St
13042 | 08/09/2009 | 2009 | 2009-09-08 | 295 | 13 | 3835 | C | ADVERSE ENVIRONMENT | Relocate 11kV pole D4886 Hihiroroa Rd
13043 | 08/09/2009 | 2009 | 2009-09-08 | 104 | 10 | 1040 | C | ADVERSE ENVIRONMENT | Relocate 11kV pole A4332 end of Air Strip Goodwins Rd
13061 | 08/09/2009 | 2009 | 2009-09-08 | 504 | 134 | 45364 | B | PLANNED SHUTDOWN | Replace 11kV poles A2531 Murphy Rd
13062 | 10/09/2009 | 2009 | 2009-09-10 | 413 | 46 | 18998 | B | PLANNED SHUTDOWN | Replace 11kV poles A2570 & A2564 Lloyd George Rd
13070 | 10/09/2009 | 2009 | 2009-09-10 | 45 | 78 | 3510 | B | PLANNED SHUTDOWN | Repair ABS A297 Tatapouri Regulator
13044 | 11/09/2009 | 2009 | 2009-09-11 | 4 | 1105 | 4420 | C | UNKNOWN | Patrol Line & Reclose CB 1 at Hexton Cause unknown
13045 | 11/09/2009 | 2009 | 2009-09-11 | 95 | 92 | 8380 | C | UNKNOWN | Reclose E863 cause unknown High Winds?
13063 | 11/09/2009 | 2009 | 2009-09-11 | 276 | 155 | 47430 | B | PLANNED SHUTDOWN | Replace poles A2134 A2148 A2163 & A2141 Lynsar Rd
13072 | 11/09/2009 | 2009 | 2009-09-11 | 97 | 108 | 10476 | B | PLANNED SHUTDOWN | Repair 11kV ABS A2128 Moana Rd Wainui
13046 | 14/09/2009 | 2009 | 2009-09-14 | 1098 | 138 | 23582 | C | ADVERSE WEATHER | Replace 3 11kV poles D3655 D3656 & D3672 Bushy Knoll Rd
13047 | 15/09/2009 | 2009 | 2009-09-15 | 419 | 4 | 1908 | C | DEFECTIVE EQUIPMENT | Replace T/x pole D478 Repongare Rd
13048 | 16/09/2009 | 2009 | 2009-09-16 | 0 | 695 | 28495 | C | FOREIGN INTERFERENCE | Remove bird from ABS A4110 Kaiti Hill
13065 | 16/09/2009 | 2009 | 2009-09-16 | 363 | 24 | 2366 | B | PLANNED SHUTDOWN | Replace T/x pole D736 Wharekopae Rd
13049 | 17/09/2009 | 2009 | 2009-09-17 | 144 | 21 | 3024 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole J1621 Reporoa Rd Ruatoria
13057 | 17/09/2009 | 2009 | 2009-09-17 | 397 | 350 | 36108 | B | PLANNED SHUTDOWN | Relocate ABS A56 Wainui Rd
13064 | 17/09/2009 | 2009 | 2009-09-17 | 53 | 37 | 1961 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Darwin Rd
13050 | 19/09/2009 | 2009 | 2009-09-19 | 307 | 656 | 40888 | C | DEFECTIVE EQUIPMENT | Replace insulator on pole C5580 Kings Rd
13051 | 21/09/2009 | 2009 | 2009-09-21 | 9 | 18 | 162 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole G3135 Paramata Rd
13052 | 21/09/2009 | 2009 | 2009-09-21 | 525 | 13 | 6825 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole H1028 Mata Rd
13053 | 22/09/2009 | 2009 | 2009-09-22 | 111 | 1808 | 18841 | C | DEFECTIVE EQUIPMENT | Isolate 11kV cable pole B6322 Awapuni Rd
13066 | 22/09/2009 | 2009 | 2009-09-22 | 282 | 100 | 3903 | B | PLANNED SHUTDOWN | Replace 11kV poles B1345 & B1362 Stafford St
13054 | 23/09/2009 | 2009 | 1932-09-09 | 205 | 22 | 4510 | C | ADVERSE WEATHER | Replace 11kV pole C821 Tawera Rd Waingake
13067 | 23/09/2009 | 2009 | 2009-09-23 | 473 | 324 | 45788 | B | PLANNED SHUTDOWN | Replace 11kV poles B1103 B4893 & ABS B193 Balance St
13068 | 24/09/2009 | 2009 | 2009-09-24 | 13 | 75 | 975 | B | PLANNED SHUTDOWN | Replace 11kV poles B1103 B4893 & ABS B193 Balance St
13069 | 24/09/2009 | 2009 | 2009-09-24 | 83 | 36 | 2988 | B | PLANNED SHUTDOWN | Isolate 11kV lines for Tree cutting Papatu Rd
13071 | 24/09/2009 | 2009 | 2009-09-24 | 68 | 20 | 1360 | B | PLANNED SHUTDOWN | Install Tapp off arms on 11kV pole W9257 East Coast Rd Mahia
13055 | 25/09/2009 | 2009 | 2009-09-25 | 120 | 54 | 2708 | C | TREE CONTACTS | Remove tree from 11kV pole A234 Panikau Rd
13056 | 28/09/2009 | 2009 | 2009-09-28 | 49 | 120 | 5880 | C | DEFECTIVE EQUIPMENT | Temp relocate 11kV disc on pole G1709 Tauwhareparae Rd
13076 | 28/09/2009 | 2009 | 2009-09-28 | 116 | 10 | 632 | B | PLANNED SHUTDOWN | Reconnect 11kV jumpers pole B6322 Awapuni Rd
13073 | 29/09/2009 | 2009 | 2009-09-29 | 23 | 91 | 2093 | B | PLANNED SHUTDOWN | Replace 11kV poles B1107 & B1108 Balance St
13075 | 29/09/2009 | 2009 | 2009-09-29 | 305 | 33 | 10065 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Kanakanaia
13074 | 30/09/2009 | 2009 | 2009-09-30 | 19 | 182 | 3458 | B | PLANNED SHUTDOWN | Replace poles B4892 B4890 B4888 B4886 B4883 Balance St
13128 | 01/10/2009 | 2009 | 2009-10-01 | 430 | 18 | 7740 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting W8357 Morere
13129 | 01/10/2009 | 2009 | 2009-10-01 | 22 | 318 | 5984 | B | PLANNED SHUTDOWN | Replace 3 11kV poles B4876 B4875 & B4873 Russell St
13131 | 01/10/2009 | 2009 | 2009-10-01 | 45 | 45 | 3465 | B | PLANNED SHUTDOWN | Install 3 DDO fuses pole W698 East Coast Rd Mahia
13077 | 02/10/2009 | 2009 | 2009-10-02 | 51 | 3 | 153 | C | DEFECTIVE EQUIPMENT | Replace 3 DDO fuses D761 W/O Kuri Quarry Tappoff
13125 | 02/10/2009 | 2009 | 2009-10-02 | 296 | 48 | 14208 | B | PLANNED SHUTDOWN | Replace 50kV pole C3027 Bloomfeild Rd
13127 | 02/10/2009 | 2009 | 2009-10-02 | 160 | 7 | 1120 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting at pole E3993
13091 | 04/10/2009 | 2009 | 2009-10-04 | 4141 | 41 | 169781 | C | ADVERSE WEATHER | Replace 11kV pole W4971 Waihi
13092 | 04/10/2009 | 2009 | 2009-10-04 | 873 | 62 | 27146 | C | ADVERSE WEATHER | Repair 11kV lines pole D5142 Wharekopae Rd
13093 | 04/10/2009 | 2009 | 2009-10-04 | 276 | 137 | 32616 | C | ADVERSE WEATHER | Cut 11kV jumpers pole W5282 Kakariki
13094 | 05/10/2009 | 2009 | 2009-10-05 | 2818 | 176 | 248409 | C | ADVERSE WEATHER | Install Elecrinet Generator & Generator 6 at Ruakituri
13095 | 05/10/2009 | 2009 | 2009-10-05 | 40 | 695 | 23072 | C | FOREIGN INTERFERENCE | Remove bark from ABS A235 Cambridge Trc
13096 | 05/10/2009 | 2009 | 2009-10-05 | 198 | 318 | 52344 | C | ADVERSE WEATHER | Cut jumpers pole W6426 Raupunga lines down W518
13097 | 05/10/2009 | 2009 | 2009-10-05 | 28 | 91 | 2158 | C | TREE CONTACTS | Remove tree from 11kV pole G4070 SH35 Wharekaka Crn
13098 | 06/10/2009 | 2009 | 2009-10-06 | 186 | 107 | 19902 | C | ADVERSE WEATHER | Repair 11kV lines pole W4635 Tuai Village
13099 | 06/10/2009 | 2009 | 2009-10-06 | 1595 | 216 | 79198 | C | ADVERSE WEATHER | Replace 11kV pole W22495 Mahia
13100 | 06/10/2009 | 2009 | 2009-10-06 | 1678 | 20 | 33544 | C | TREE CONTACTS | Repair 11kV lines pole H1030 to H179 Mata Rd
13133 | 06/10/2009 | 2009 | 2009-10-06 | 494 | 370 | 63160 | B | PLANNED SHUTDOWN | Replace 11kV poles B198 B4881 B4880 B48 79 & ABS B193 Russell St
13101 | 07/10/2009 | 2009 | 2009-10-07 | 5496 | 21 | 115416 | C | ADVERSE WEATHER | Repair 11kV lines pole W5211 Woodlands
13102 | 07/10/2009 | 2009 | 2009-10-07 | 3995 | 9 | 35955 | C | ADVERSE WEATHER | Repair 11kV line pole W4598 Lake Waikaremoana
13103 | 07/10/2009 | 2009 | 2009-10-07 | 360 | 21 | 7758 | C | ADVERSE WEATHER | Rejion jumpers pole W5124 Mangatanawha
13106 | 07/10/2009 | 2009 | 2009-10-07 | 2154 | 9 | 19386 | C | ADVERSE WEATHER | Repair 11kV lines & replace poles beyond W5002 Mangone Rd
13107 | 07/10/2009 | 2009 | 2009-10-07 | 1007 | 72 | 13999 | C | ADVERSE WEATHER | Repair 11kV line pole W446 Otoi
13104 | 08/10/2009 | 2009 | 2009-10-08 | 62 | 200 | 12400 | C | ADVERSE WEATHER | Reconnect tapp off to T/x W518 pole W6426 Mohaka
13105 | 08/10/2009 | 2009 | 2009-10-08 | 1434 | 9 | 12906 | C | TREE CONTACTS | Repair 11kV lines between poles E518 to E519 Tarndale Rd
13108 | 08/10/2009 | 2009 | 2009-10-08 | 9600 | 5 | 48000 | C | ADVERSE WEATHER | Replace 11kV poles & lines between W5317 to W5222 Willowflat
13109 | 09/10/2009 | 2009 | 2009-10-09 | 822 | 42 | 34524 | C | ADVERSE WEATHER | Cut jumpers pole W4984 Terapartiki
13110 | 09/10/2009 | 2009 | 2009-10-09 | 78 | 176 | 13728 | C | ADVERSE WEATHER | Rejoin 11kV jumpers pole W6982 Tuai
13111 | 09/10/2009 | 2009 | 2009-10-09 | 60 | 6 | 360 | C | DEFECTIVE EQUIPMENT | Replace connector on pole B5057 Centennial Marine Drive
13112 | 10/10/2009 | 2009 | 2009-10-10 | 276 | 208 | 22920 | C | DEFECTIVE EQUIPMENT | Cut 11kV jumpers poles A154 & A807 Rototahi
13113 | 10/10/2009 | 2009 | 2009-10-10 | 235 | 93 | 10248 | C | TREE CONTACTS | Remove trees from 11kV pole E1647 Manders Rd
13114 | 10/10/2009 | 2009 | 2009-10-10 | 29 | 3367 | 25796 | C | ADVERSE WEATHER | Cut jumpers poles W6772 & W6779 Near Wairoa Sub
13115 | 11/10/2009 | 2009 | 2009-10-11 | 92 | 512 | 47104 | C | ADVERSE WEATHER | Repair 11kV lines between W6776 & W6778 Wairoa Sub
13116 | 12/10/2009 | 2009 | 2009-10-12 | 51 | 91 | 4641 | C | ADVERSE WEATHER | Disconnect Generator 6 at Ruakituri pole W1801
13117 | 12/10/2009 | 2009 | 2009-10-12 | 69 | 23 | 1587 | C | ADVERSE WEATHER | Replace 11kV pole A806 Rototahi
13119 | 13/10/2009 | 2009 | 2009-10-13 | 55 | 20 | 1100 | C | DEFECTIVE EQUIPMENT | Replace Xarm on pole G2197 Mangatokorau Rd
13120 | 13/10/2009 | 2009 | 2009-10-13 | 381 | 14 | 2736 | C | DEFECTIVE EQUIPMENT | Replace pole A203 Baillies Rd Waimata
13132 | 13/10/2009 | 2009 | 2009-10-13 | 175 | 58 | 4542 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting Ferry Rd at D4535
13136 | 13/10/2009 | 2009 | 2009-10-13 | 320 | 90 | 28800 | B | PLANNED SHUTDOWN | Replace pole W8330 & cut trees Morere
13118 | 14/10/2009 | 2009 | 2009-10-14 | 27 | 17 | 459 | C | ADVERSE WEATHER | Rejoin jumpers pole W4984 Mangone
13135 | 14/10/2009 | 2009 | 2009-10-14 | 197 | 185 | 15156 | B | PLANNED SHUTDOWN | Install Oil Switchs C6620 C6621 & C6622 Ormond Rd
13121 | 15/10/2009 | 2009 | 2009-10-15 | 64 | 222 | 14208 | C | DEFECTIVE EQUIPMENT | Replace 2 DDO fuse bases T/x J286 Hicks Bay
13122 | 15/10/2009 | 2009 | 2009-10-15 | 265 | 9 | 2385 | C | TREE CONTACTS | Repair 11kV lines pole E412 Tarndale Rd
13123 | 15/10/2009 | 2009 | 2009-10-15 | 38 | 12 | 456 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole J96 Tikitiki
13124 | 15/10/2009 | 2009 | 2009-10-15 | 118 | 14 | 1652 | C | DEFECTIVE EQUIPMENT | Replace kidney on T/x pole D514 Hihiroroa Rd
13126 | 15/10/2009 | 2009 | 2009-10-15 | 143 | 21 | 3003 | B | PLANNED SHUTDOWN | Replace 50kV pole C3022 Bushmere Rd
13137 | 15/10/2009 | 2009 | 2009-10-15 | 144 | 43 | 6192 | B | PLANNED SHUTDOWN | Isolate 11kV for tree cutting Tahaenui at W1119
13138 | 16/10/2009 | 2009 | 2009-10-16 | 97 | 12 | 1164 | B | PLANNED SHUTDOWN | Erect new 11kV pole D6161 Pohuturoa Stn Tiniroto
13139 | 20/10/2009 | 2009 | 2009-10-20 | 13 | 10 | 230 | B | PLANNED SHUTDOWN | Replace T/x Structure J102 College Rd
13140 | 20/10/2009 | 2009 | 2009-10-20 | 38 | 50 | 2882 | B | PLANNED SHUTDOWN | Replace poles E1764 E1766 E1768 E1769 E1770 & E1772 SH2 Te Karaka
13142 | 20/10/2009 | 2009 | 2009-10-20 | 103 | 65 | 6695 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting pole E374 Lavenham Rd
13143 | 20/10/2009 | 2009 | 2009-10-20 | 116 | 65 | 7540 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting E42 Ford Rd Ormond
13141 | 21/10/2009 | 2009 | 2009-10-21 | 29 | 198 | 7430 | B | PLANNED SHUTDOWN | Replace 11kV pole B210 Seddon Cres
13144 | 21/10/2009 | 2009 | 2009-10-21 | 545 | 8 | 4360 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting G159 Takapau Rd
13130 | 22/10/2009 | 2009 | 2009-10-22 | 178 | 25 | 4450 | B | PLANNED SHUTDOWN | Change T/x J289 to 50 Kva Onepoto Hicks Bay
13079 | 23/10/2009 | 2009 | 2009-10-23 | 33 | 30 | 990 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A3710 Panikau Rd Whangara
13080 | 23/10/2009 | 2009 | 2009-10-23 | 19 | 16 | 304 | C | DEFECTIVE EQUIPMENT | Repair Quadrant wire on ABS G73 Wharekaka Rd
13081 | 23/10/2009 | 2009 | 2009-10-23 | 107 | 2918 | 30661 | C | DEFECTIVE EQUIPMENT | Repair 11kV lines pole A2531 Murphy Rd
13082 | 27/10/2009 | 2009 | 2009-10-27 | 28 | 1179 | 19732 | C | UNKNOWN | Reclose CB D678 at Patutahi Sub cause unknown
13083 | 28/10/2009 | 2009 | 2009-10-28 | 39 | 50 | 1950 | C | DEFECTIVE EQUIPMENT | Reclose CB D678 at Patutahi Sub cause unknown
13134 | 28/10/2009 | 2009 | 2009-10-28 | 329 | 26 | 8554 | B | PLANNED SHUTDOWN | Replace poles D726 D3096 & D3094 Wharekopae Rd
13084 | 29/10/2009 | 2009 | 2009-10-29 | 95 | 635 | 60325 | C | ADVERSE WEATHER | Repair 11kV lines pole W1218 Ruatanawha Rd
13085 | 29/10/2009 | 2009 | 2009-10-29 | 25 | 172 | 4300 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W711 Ruatanawha Rd
13086 | 29/10/2009 | 2009 | 2009-10-29 | 238 | 274 | 19450 | C | ADVERSE WEATHER | Repair 11kV line pole W8377 Morere
13087 | 29/10/2009 | 2009 | 2009-10-29 | 64 | 1110 | 64480 | C | TREE CONTACTS | Remove tree from 33kV pole W3806 Tahaenui
13088 | 29/10/2009 | 2009 | 2009-10-29 | 235 | 136 | 29189 | C | TREE CONTACTS | Remove tree branches from 11kV pole H2568 Tokomaru St
13089 | 29/10/2009 | 2009 | 2009-10-29 | 75 | 12 | 900 | C | ADVERSE WEATHER | Repair 11kV lines pole G540 Arikihi Rd Waimata
13090 | 30/10/2009 | 2009 | 2009-10-30 | 294 | 730 | 27862 | C | DEFECTIVE EQUIPMENT | Replace 11kV pole W6607 Mangapoikie Rd
13159 | 02/11/2009 | 2009 | 2009-11-02 | 81 | 27 | 2187 | B | PLANNED SHUTDOWN | Isolate 11kV at C3523 for tree cutting Whareratas
13160 | 03/11/2009 | 2009 | 2009-11-03 | 356 | 34 | 2773 | B | PLANNED SHUTDOWN | Replace T/x & pole E76 Ngakaroa Rd
13145 | 04/11/2009 | 2009 | 2009-11-04 | 332 | 67 | 12515 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole F2671 Motu Falls Rd
13161 | 05/11/2009 | 2009 | 2009-11-05 | 560 | 91 | 25137 | B | PLANNED SHUTDOWN | Replace 11kV poles B1109 & B1143 Balance St
13162 | 10/11/2009 | 2009 | 2009-11-10 | 418 | 130 | 30852 | B | PLANNED SHUTDOWN | Replace 11kV poles A2134 A2141 A2142 A2143 Lysnar Rd
13167 | 10/11/2009 | 2009 | 2009-11-10 | 440 | 3 | 1320 | B | PLANNED SHUTDOWN | Isolate 11kV lines Fuses E285 for tree cutting Ngakaroa Rd
13146 | 15/11/2009 | 2009 | 2009-11-15 | 638 | 398 | 37359 | C | DEFECTIVE EQUIPMENT | Cut 11kV jumpers pole W82 Waihua Valley Rd
13147 | 15/11/2009 | 2009 | 2009-11-15 | 190 | 176 | 24965 | C | DEFECTIVE EQUIPMENT | By pass Faulty PMR Rangitukia Rd
13158 | 15/11/2009 | 2009 | 2009-11-15 | 442 | 181 | 17602 | B | PLANNED SHUTDOWN | Replace pole B1189 B1188 B639 B1187 Sheehan St
13148 | 16/11/2009 | 2009 | 2009-11-16 | 101 | 182 | 18382 | C | DEFECTIVE EQUIPMENT | Repair PMR J1078 Rangitukia Rd Tikitiki
13165 | 16/11/2009 | 2009 | 2009-11-16 | 501 | 16 | 8016 | B | PLANNED SHUTDOWN | Isolate 11kV lines at J41 for 50kV Poroporo Valley Rd
13149 | 17/11/2009 | 2009 | 2009-11-17 | 130 | 50 | 6500 | C | DEFECTIVE EQUIPMENT | Repair Quadrant wire ABS J389 Waikura Valley Rd
13150 | 17/11/2009 | 2009 | 2009-11-17 | 42 | 1807 | 37448 | C | FOREIGN INTERFERENCE | Reclose CB 42 & 46 Parkinson St Sub pole fire Arson B583
13163 | 17/11/2009 | 2009 | 2009-11-17 | 462 | 4 | 1848 | B | PLANNED SHUTDOWN | Replace 9 11kV poles G611 G612 G617 G619 G621 G622 G624 G632 G634 Waimata Valley Rd
13166 | 17/11/2009 | 2009 | 2009-11-17 | 374 | 4 | 1496 | B | PLANNED SHUTDOWN | Isolate 11kVlines ABS J396 for 50kV pole changes Te Hue Rd
13164 | 19/11/2009 | 2009 | 2009-11-19 | 480 | 44 | 15180 | B | PLANNED SHUTDOWN | Replace 16 11kV poles E1201 to E1229 Waimata Valley Rd
13151 | 22/11/2009 | 2009 | 2009-11-22 | 26 | 2516 | 65416 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
13152 | 23/11/2009 | 2009 | 2009-11-23 | 75 | 65 | 4875 | C | DEFECTIVE EQUIPMENT | Replace 11kV cable to T/x W1222 Fortesque St Mahia
13168 | 24/11/2009 | 2009 | 2009-11-24 | 27 | 49 | 1323 | B | PLANNED SHUTDOWN | Replace 11kV pole B1143 Balance St
13153 | 25/11/2009 | 2009 | 2009-11-25 | 89 | 12 | 1068 | C | DEFECTIVE EQUIPMENT | Relocate 11kV disc pole G1448 Koire Rd
13154 | 26/11/2009 | 2009 | 2009-11-26 | 216 | 372 | 58029 | C | DEFECTIVE EQUIPMENT | Temp prop 11kV pole W3943 Mohaka Hill
13170 | 26/11/2009 | 2009 | 2009-11-26 | 359 | 14 | 5026 | B | PLANNED SHUTDOWN | Replace 14 11kV poles between E11 & E19 Waimata Valley Rd
13155 | 27/11/2009 | 2009 | 2009-11-27 | 18 | 1180 | 21240 | C | DEFECTIVE EQUIPMENT | Reclose CB 25 & Inc D678 at Patutahi Sub
13169 | 27/11/2009 | 2009 | 2009-11-27 | 240 | 17 | 4080 | B | PLANNED SHUTDOWN | Isolate 11kV lines at C175 Wharerata Rd for tree cutting
13157 | 30/11/2009 | 2009 | 2009-11-30 | 85 | 4477 | 70515 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W1042 Wairoa Sub
13171 | 30/11/2009 | 2009 | 2009-11-30 | 36 | 49 | 1764 | B | PLANNED SHUTDOWN | Install links on pole D3355 Parakanapa Rd
13188 | 01/12/2009 | 2009 | 2009-12-01 | 45 | 17 | 765 | B | PLANNED SHUTDOWN | Install new 11kV TX pole E3601 Te Hau Rd Whatatutu
13173 | 02/12/2009 | 2009 | 2009-12-02 | 1077 | 216 | 46992 | C | DEFECTIVE EQUIPMENT | Replace 11kV disc pole W7686 Mahia
13174 | 02/12/2009 | 2009 | 2009-12-02 | 331 | 53 | 10334 | C | TREE CONTACTS | Repair 11kV lines poles D2474 to D2475 Pehiri Rd
13189 | 02/12/2009 | 2009 | 2009-12-02 | 128 | 23 | 2944 | B | PLANNED SHUTDOWN | Isolate 11kV lines C251 for Tree cutting Pilmers Rd
13190 | 02/12/2009 | 2009 | 2009-12-02 | 172 | 193 | 33196 | B | PLANNED SHUTDOWN | Connect and Disconnect Generator pole W1460 Waihua
13191 | 02/12/2009 | 2009 | 2009-12-02 | 172 | 62 | 10664 | B | PLANNED SHUTDOWN | Relocate 11kV pole W68 Cricklewood Crn
13175 | 03/12/2009 | 2009 | 2009-12-03 | 237 | 76 | 18012 | C | TREE CONTACTS | Remove tree from 11kV pole F241 Matawai Rd North
13176 | 03/12/2009 | 2009 | 2009-12-03 | 79 | 32 | 2528 | C | DEFECTIVE EQUIPMENT | Temp repair Xarm on pole D3611 Ruakaka Rd Tiniroto
13177 | 03/12/2009 | 2009 | 2009-12-03 | 355 | 30 | 2772 | C | TREE CONTACTS | Cut and rejoin jumpers pole E1911 for tree cutting Waihirere
13178 | 03/12/2009 | 2009 | 2009-12-03 | 275 | 59 | 8492 | C | ADVERSE ENVIRONMENT | Repair PMR C2175 and temp repair C89 Waingake Rd
13192 | 03/12/2009 | 2009 | 2009-12-03 | 366 | 11 | 4026 | B | PLANNED SHUTDOWN | Replace 14 11kV poles E19 to E199 Waimata Valley Rd
13179 | 04/12/2009 | 2009 | 2009-12-04 | 348 | 193 | 13244 | C | TREE CONTACTS | Repair 11kv lines pole E1072 Kanakanaia Rd
13180 | 06/12/2009 | 2009 | 2009-12-06 | 52 | 2516 | 111468 | C | UNKNOWN | Reclose CB A8 Goodwins Rd cause unknown
13181 | 07/12/2009 | 2009 | 2009-12-07 | 87 | 935 | 38883 | C | UNKNOWN | Reclose CB A475 Tamarau at Kaiti sub cause unknown
13193 | 08/12/2009 | 2009 | 2009-12-08 | 90 | 182 | 16380 | B | PLANNED SHUTDOWN | Install Links pole J1074 Rangitukia Rd Tikitiki
13194 | 08/12/2009 | 2009 | 2009-12-08 | 648 | 6 | 3888 | B | PLANNED SHUTDOWN | Replace 3 11kV pole G611 G612 G619 Waimata Valley Rd
13195 | 09/12/2009 | 2009 | 2009-12-09 | 255 | 30 | 6762 | B | PLANNED SHUTDOWN | Install links pole E1152 and replace pole E7 Waimata Valley Rd
13196 | 10/12/2009 | 2009 | 2009-12-10 | 435 | 11 | 4785 | B | PLANNED SHUTDOWN | Replace 11kV poles E1305 E1668 E1306 E1299 E1310 Waimata Valley Rd
13197 | 15/12/2009 | 2009 | 2009-12-15 | 492 | 17 | 8364 | B | PLANNED SHUTDOWN | Isolate 11kV lines fuses W4336 Titirangi Rd
13182 | 17/12/2009 | 2009 | 2009-12-17 | 80 | 247 | 19719 | C | DEFECTIVE EQUIPMENT | Cut away T/x supplying SF6 W7902 switch Nuhaka
13183 | 22/12/2009 | 2009 | 2009-12-22 | 67 | 247 | 16180 | C | DEFECTIVE EQUIPMENT | Replace 11kV Tx supplying SF6 Switch W7902 Nuhaka
13198 | 22/12/2009 | 2009 | 2009-12-22 | 327 | 46 | 11514 | B | PLANNED SHUTDOWN | Replace SF6 Switch C89 Waingake Rd
13199 | 23/12/2009 | 2009 | 2009-12-23 | 60 | 20 | 1200 | B | PLANNED SHUTDOWN | Erect 3 11kV fuses pole D2722 Hihiroroa Rd
13184 | 24/12/2009 | 2009 | 2009-12-24 | 335 | 120 | 40200 | B | PLANNED SHUTDOWN | Replace 11kV pole J1088 Rangitukia Rd
13185 | 27/12/2009 | 2009 | 2009-12-27 | 120 | 6 | 720 | C | TREE CONTACTS | Repair 11kV lines poles E3078 to E3079 Whatatutu
13186 | 29/12/2009 | 2009 | 2009-12-29 | 21 | 200 | 2240 | C | UNKNOWN | Reclose CB W826 at Raupunga cause unknown
13187 | 29/12/2009 | 2009 | 2009-12-29 | 6 | 37 | 198 | C | TREE CONTACTS | Remove bark from 11kV pole E142 Kanakanaia Rd
13200 | 03/01/2010 | 2009 | 2010-01-03 | 210 | 22 | 4620 | C | TREE CONTACTS | Repair 11kV lines pole A1248 Pa Rd Whangara
13201 | 04/01/2010 | 2009 | 2010-01-04 | 248 | 156 | 16850 | C | TREE CONTACTS | Repair 11kV lines G1824 to G1825 Paramata Rd
13202 | 07/01/2010 | 2009 | 2010-01-07 | 13 | 38 | 494 | C | DEFECTIVE EQUIPMENT | Replace insulator pole W7151 Ruatanawha Rd
13203 | 07/01/2010 | 2009 | 2010-01-07 | 8 | 4 | 32 | C | DEFECTIVE EQUIPMENT | Change Phase jumper over on T/x pole W426 Ngamoto Rd
13204 | 08/01/2010 | 2009 | 2010-01-08 | 78 | 41 | 3198 | C | TREE CONTACTS | Cut trees in 11kV pole D1788 Gentle Annie Hill
13205 | 08/01/2010 | 2009 | 2010-01-08 | 394 | 76 | 29692 | C | TREE CONTACTS | Repair 11kV lines pole F1942 Te Wera
13206 | 10/01/2010 | 2009 | 2010-01-10 | 1033 | 61 | 16959 | C | TREE CONTACTS | Repair 11kV lines pole W4545 Piripaua
13207 | 11/01/2010 | 2009 | 2010-01-11 | 873 | 13 | 11349 | C | TREE CONTACTS | Repair 11kVlines between poles A436 to A520 Waihau Bay
13208 | 11/01/2010 | 2009 | 2010-01-11 | 399 | 31 | 12369 | C | TREE CONTACTS | Cut trees in 11kV pole W171 Piripaua
13209 | 11/01/2010 | 2009 | 2010-01-11 | 1314 | 173 | 57743 | C | TREE CONTACTS | Repair 11kV lines pole W5357 Putorino
13210 | 11/01/2010 | 2009 | 2010-01-11 | 951 | 138 | 17642 | C | TREE CONTACTS | Repair 11kV lines pole W7534 River Rd Te Reinga
13230 | 11/01/2010 | 2009 | 2010-01-11 | 53 | 76 | 4028 | B | PLANNED SHUTDOWN | Install 3 DDO fuses pole D3119 Crn O"Gradys Rd
13211 | 12/01/2010 | 2009 | 2010-01-12 | 285 | 114 | 19218 | C | DEFECTIVE EQUIPMENT | Replace faulty insulator pole W1731 Kotemaori
13212 | 12/01/2010 | 2009 | 2010-01-12 | 427 | 49 | 20923 | C | TREE CONTACTS | Replace 2 11kV poles E1054 & E1060 Kanakanaia
13234 | 12/01/2010 | 2009 | 2010-01-12 | 30 | 5 | 150 | B | PLANNED SHUTDOWN | Isolate 11kV lines for tree cutting C3959 to C3961 Dunstan Rd
13213 | 13/01/2010 | 2009 | 2010-01-13 | 61 | 981 | 53311 | C | UNKNOWN | Reclose CB C95 at Makaraka Sub cause unknown
13228 | 13/01/2010 | 2009 | 2010-01-13 | 192 | 17 | 3264 | B | PLANNED SHUTDOWN | Isolate & lower lines for tree cutting G3708 to C3711 Whareratas
13214 | 15/01/2010 | 2009 | 2010-01-15 | 281 | 75 | 3900 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole H2713 Fernside Rd
13215 | 16/01/2010 | 2009 | 2010-01-16 | 79 | 1518 | 80217 | C | DEFECTIVE EQUIPMENT | Replace SW/GR RMU A337 S339 A340 Ropata St
13216 | 18/01/2010 | 2009 | 2010-01-18 | 155 | 128 | 19840 | C | FOREIGN INTERFERENCE | Replace 11kV pole A3184 Endcliffe Rd
13232 | 20/01/2010 | 2009 | 2010-01-20 | 468 | 14 | 6552 | B | PLANNED SHUTDOWN | Replace 6 Poles E1214 E1215 E1216 E1218 E1220 E1219 Waimata Rd
13217 | 21/01/2010 | 2009 | 2010-01-21 | 825 | 113 | 23765 | C | TREE CONTACTS | Repair 11kV lines pole W5633 Kahugungu
13233 | 22/01/2010 | 2009 | 2010-01-22 | 411 | 11 | 4521 | B | PLANNED SHUTDOWN | Replace 11kV poles E1238 & E1239 Waimata Rd
13218 | 23/01/2010 | 2009 | 2010-01-23 | 411 | 14 | 5230 | C | DEFECTIVE EQUIPMENT | Replace poles E1220 & E1221 due to faulty Crimp Joint
13231 | 23/01/2010 | 2009 | 2010-01-23 | 165 | 18 | 2970 | B | PLANNED SHUTDOWN | Erect 3 DDO fuses on pole E2001 Te Hau Rd
13219 | 25/01/2010 | 2009 | 2010-01-25 | 223 | 95 | 18970 | C | DEFECTIVE EQUIPMENT | Replace 11kV T/x pole J293 Te Araroa
13220 | 25/01/2010 | 2009 | 2010-01-25 | 1380 | 76 | 23006 | C | TREE CONTACTS | Replace 11kV pole E655 & repair lines Tarndale Rd
13221 | 26/01/2010 | 2009 | 2010-01-26 | 528 | 176 | 92928 | C | DEFECTIVE EQUIPMENT | Repair 11kV cable between CB24 to links W1447 Tuai
13222 | 26/01/2010 | 2009 | 2010-01-26 | 201 | 11 | 2211 | C | ADVERSE WEATHER | Repair 11kV jumper pole W550 Waihi
13229 | 28/01/2010 | 2009 | 2010-01-28 | 84 | 21 | 1764 | B | PLANNED SHUTDOWN | Replace 11kV pole J1599 Tuparoa Rd
13235 | 29/01/2010 | 2009 | 2010-01-29 | 253 | 12 | 3036 | B | PLANNED SHUTDOWN | Replace 22 poles Between G368 to G367 Waimata Valley
13223 | 30/01/2010 | 2009 | 2010-01-30 | 1714 | 189 | 200345 | C | ADVERSE WEATHER | Reclose CB 23 at Tuai Sub
13224 | 30/01/2010 | 2009 | 2010-01-30 | 86 | 213 | 9284 | C | TREE CONTACTS | Repair 11kV lines between H2774 to H2238 Mata Rd
13225 | 31/01/2010 | 2009 | 2010-01-31 | 574 | 156 | 72680 | C | TREE CONTACTS | Repair 11kV lines poles G2045 to G2050 to G2051 Tauwhareparae
13226 | 31/01/2010 | 2009 | 2010-01-31 | 431 | 59 | 18573 | C | TREE CONTACTS | Reclose CB C2175 Waingake Rd Trees in line
13227 | 31/01/2010 | 2009 | 2010-01-31 | 196 | 9 | 1764 | C | TREE CONTACTS | Repair 11kV lines poles G606 G607 Waimata Valley Rd
13236 | 01/02/2010 | 2009 | 2010-02-01 | 300 | 54 | 16200 | C | TREE CONTACTS | Repair 11kV lines pole G214 Tauwhareparae Rd
13238 | 01/02/2010 | 2009 | 2010-02-01 | 994 | 62 | 61628 | C | ADVERSE WEATHER | Reposition T/x pole D132 Rere School Wharekopae Rd
13239 | 01/02/2010 | 2009 | 2010-02-01 | 40 | 635 | 25400 | C | UNKNOWN | Reclose CB W213 Raupunga at Kiwi Sub cause unknown
13240 | 02/02/2010 | 2009 | 2010-02-02 | 584 | 13 | 7592 | C | TREE CONTACTS | Repair 11kV lines pole H2181 Puketiti Rd Te Puia
13241 | 02/02/2010 | 2009 | 2010-02-02 | 1151 | 59 | 18312 | C | TREE CONTACTS | Repair 11kV lines pole C898 Paparatu Rd Waingake
13242 | 03/02/2010 | 2009 | 2010-02-03 | 148 | 11 | 1628 | C | DEFECTIVE EQUIPMENT | Repair 11kV Jumper on pole G3307 Tutamoe Rd
13243 | 03/02/2010 | 2009 | 2010-02-03 | 57 | 12 | 684 | C | DEFECTIVE EQUIPMENT | Repair 11kV Jumper on pole G1601 Arikihi Rd
13254 | 04/02/2010 | 2009 | 2010-02-04 | 243 | 47 | 11421 | B | PLANNED SHUTDOWN | Replace 50kV pole H711near 11kV lines Ngarimus Hill Ruatoria
13258 | 04/02/2010 | 2009 | 2010-02-04 | 437 | 24 | 6960 | B | PLANNED SHUTDOWN | Replace 8 11kV poles G848 G547 G551 G558 G561 G567 Waimata Valley
13244 | 06/02/2010 | 2009 | 2010-02-06 | 42 | 8 | 336 | C | DEFECTIVE EQUIPMENT | Replace T/x pole F30 Kaitara Lane
13255 | 07/02/2010 | 2009 | 2010-02-07 | 240 | 57 | 18639 | B | PLANNED SHUTDOWN | Replace T/x A256 Jackson St
13256 | 07/02/2010 | 2009 | 2010-02-07 | 77 | 60 | 4620 | B | PLANNED SHUTDOWN | Install Gas switch A6600 Jackson St
13259 | 08/02/2010 | 2009 | 2010-02-08 | 60 | 33 | 3135 | B | PLANNED SHUTDOWN | Replace 8 11kV poles G848 G547 G551 G558 G561 G567 Waimata Valley
13262 | 08/02/2010 | 2009 | 2010-02-08 | 54 | 41 | 2214 | B | PLANNED SHUTDOWN | Connect jumpers pole D1789 Tiniroto Rd
13245 | 09/02/2010 | 2009 | 2010-02-09 | 433 | 53 | 8597 | C | TREE CONTACTS | Repair 11kV lines pole H796 Mata Rd
13257 | 09/02/2010 | 2009 | 2010-02-09 | 343 | 60 | 20580 | B | PLANNED SHUTDOWN | Replace T/x A250 Porter St
13260 | 09/02/2010 | 2009 | 2010-02-09 | 41 | 33 | 8118 | B | PLANNED SHUTDOWN | Replace 6 11kV poles beyond E1090 Kanakanaia Rd
13263 | 09/02/2010 | 2009 | 2010-02-09 | 17 | 16 | 272 | B | PLANNED SHUTDOWN | Connect 11kV jumpers pole W6124 Awamate Rd Wairoa
13246 | 10/02/2010 | 2009 | 2010-02-10 | 165 | 172 | 5642 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole W5108 near Putere School
13261 | 10/02/2010 | 2009 | 2010-02-10 | 32 | 18 | 846 | B | PLANNED SHUTDOWN | Erect 11kV fuses on pole D3155 Rere Farm Settlement Rd
13264 | 11/02/2010 | 2009 | 2010-02-11 | 57 | 58 | 3306 | B | PLANNED SHUTDOWN | Cut jumpers & install DDO fuses pole E1456 Kanakanaia Rd
13248 | 16/02/2010 | 2009 | 2010-02-16 | 375 | 60 | 14677 | C | TREE CONTACTS | Repair 11kV lines pole W5531 Ruapapa Rd
13249 | 16/02/2010 | 2009 | 2010-02-16 | 67 | 400 | 21312 | C | UNKNOWN | Reclose CB D644 Muriwai at Patutahi Sub cause unknown
13265 | 16/02/2010 | 2009 | 2010-02-16 | 183 | 11 | 2013 | B | PLANNED SHUTDOWN | Replace 11kV pole E1239 Waimata Valley Rd
13266 | 16/02/2010 | 2009 | 2010-02-16 | 340 | 12 | 4080 | B | PLANNED SHUTDOWN | Replace 6 11kV poles between G368 to G197 Waimata Valley Rd
13267 | 18/02/2010 | 2009 | 2010-02-18 | 373 | 12 | 4476 | B | PLANNED SHUTDOWN | Replace 6 11kV poles between G368 to G197 Waimata Valley Rd
13268 | 22/02/2010 | 2009 | 2010-02-22 | 11 | 21 | 231 | B | PLANNED SHUTDOWN | Replace 11kV pole W20124 & rejoin jumpers W82 Waihua Valley
13250 | 23/02/2010 | 2009 | 2010-02-23 | 490 | 8 | 3920 | C | TREE CONTACTS | Replace 2 11kV poles E1130 & E1129 Kanakanaia Rd
13269 | 23/02/2010 | 2009 | 2010-02-23 | 524 | 75 | 25403 | B | PLANNED SHUTDOWN | Replace 11kV poles H1429 H1434 H1439 H1440 H1443 H1445 SH35 Makarika
13251 | 25/02/2010 | 2009 | 2010-02-25 | 21 | 221 | 3278 | C | UNKNOWN | Reclose CB G326 Toko Tie at Tolaga Bay Sub cause unknown
13270 | 25/02/2010 | 2009 | 2010-02-25 | 10 | 11 | 176 | B | PLANNED SHUTDOWN | Install T/X B243 & fuse switch B1437 Bank St
13252 | 27/02/2010 | 2009 | 2010-02-27 | 298 | 1105 | 146673 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole F4033 near Puha Sub
13253 | 28/02/2010 | 2009 | 2010-02-28 | 271 | 156 | 18193 | C | FOREIGN INTERFERENCE | Repair 11kv lines pole W7900 Tahaenui
13289 | 01/03/2010 | 2009 | 2010-03-01 | 355 | 14 | 8330 | B | PLANNED SHUTDOWN | Replace 11kV pole D4891 Hihiroroa Rd
13299 | 01/03/2010 | 2009 | 2010-03-01 | 68 | 9 | 612 | B | PLANNED SHUTDOWN | Replace Xarm on pole C2851 Ruakaka Rd
13290 | 02/03/2010 | 2009 | 2010-03-02 | 518 | 6 | 3108 | B | PLANNED SHUTDOWN | Isolate 11kV lines poles C184 to C189 Wharerata Rd
13272 | 04/03/2010 | 2009 | 2010-03-04 | 346 | 14 | 4844 | C | DEFECTIVE EQUIPMENT | Replace pole D998 Hihiroroa Rd
13273 | 05/03/2010 | 2009 | 2010-03-05 | 225 | 54 | 12150 | C | DEFECTIVE EQUIPMENT | Replace ABB RMU W251 Kauri St Wairoa
13274 | 05/03/2010 | 2009 | 2010-03-05 | 74 | 800 | 39494 | C | DEFECTIVE EQUIPMENT | Repair 11kV jumper pole W930 Carroll St
13288 | 05/03/2010 | 2009 | 2010-03-05 | 85 | 4 | 340 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers pole H306 Busby's Hill
13291 | 05/03/2010 | 2009 | 2010-03-05 | 50 | 103 | 5150 | B | PLANNED SHUTDOWN | Connect 3 11kV jumpers pole J4052 Hicks Bay
13305 | 05/03/2010 | 2009 | 2010-03-05 | 109 | 4 | 436 | B | PLANNED SHUTDOWN | Replace T/x A471 Port Gisborne
13275 | 07/03/2010 | 2009 | 2010-03-07 | 390 | 172 | 16667 | C | FOREIGN INTERFERENCE | Replace 11kV pole G1134 Rototahi
13276 | 07/03/2010 | 2009 | 2010-03-07 | 181 | 400 | 36614 | C | FOREIGN INTERFERENCE | Replace 11kV pole C951near Waipaoa Roundabout
13293 | 09/03/2010 | 2009 | 2010-03-09 | 16 | 32 | 896 | B | PLANNED SHUTDOWN | Cut 11kV jumpers pole D3588 Ruakaka Rd
13294 | 10/03/2010 | 2009 | 2010-03-10 | 23 | 32 | 1216 | B | PLANNED SHUTDOWN | Rejoin 11kV jumpers pole D3588 Ruakaka Rd
13295 | 10/03/2010 | 2009 | 2010-03-10 | 421 | 42 | 17682 | B | PLANNED SHUTDOWN | Replace 3 11kV poles G520 G522 & G519 Waimata Valley Rd
13277 | 12/03/2010 | 2009 | 2010-03-12 | 86 | 48 | 4128 | C | TREE CONTACTS | Remove tree from 11kV pole W918 in AFFCO Compound
13296 | 12/03/2010 | 2009 | 2010-03-12 | 278 | 12 | 3336 | B | PLANNED SHUTDOWN | Replace 5 11kV poles G540 G548 G538 G189 G587 Waimata Valley Rd
13278 | 13/03/2010 | 2009 | 2010-03-13 | 208 | 208 | 12215 | C | FOREIGN INTERFERENCE | Repair 11kV lines pole A753 Mokirau Stn (Duck)
13279 | 15/03/2010 | 2009 | 2010-03-15 | 130 | 24 | 3120 | C | TREE CONTACTS | Repair 11kv lines pole A4526 Glen Roy Rd
13297 | 16/03/2010 | 2009 | 2010-03-16 | 378 | 14 | 5292 | B | PLANNED SHUTDOWN | Replace 11kV pole C104 Paparatu Rd
13301 | 16/03/2010 | 2009 | 2010-03-16 | 394 | 85 | 33490 | B | PLANNED SHUTDOWN | Replace 11kV SW/GR B637 B500 B648 B589 & T/x B650 Centennial Cres
13302 | 16/03/2010 | 2009 | 2010-03-16 | 26 | 117 | 2225 | B | PLANNED SHUTDOWN | Phase out across Gas Switch B528 Centennial Cres
13303 | 16/03/2010 | 2009 | 2010-03-16 | 368 | 20 | 7360 | B | PLANNED SHUTDOWN | Replace 5 11kV poles G540 G548 G538 G189 G587 Waimata Valley Rd
13280 | 17/03/2010 | 2009 | 2010-03-17 | 254 | 4 | 1016 | C | TREE CONTACTS | Isolate 11kV for tree cutting pole D183 Rockhill Rd
13300 | 17/03/2010 | 2009 | 2010-03-17 | 240 | 91 | 21840 | B | PLANNED SHUTDOWN | Replace T/x A336 Parau St
13292 | 18/03/2010 | 2009 | 2010-03-18 | 485 | 12 | 19824 | B | PLANNED SHUTDOWN | Replace 10 11kV poles D1410 D1470 D1401D1412 D1571 D1415 D1440 D435 D1416 D1417 Waimata Valley
13304 | 22/03/2010 | 2009 | 2010-03-22 | 413 | 56 | 23128 | B | PLANNED SHUTDOWN | Replace 4 11kV poles D2763 D2762 D2761 D2760 Hihiroroa Rd
13281 | 23/03/2010 | 2009 | 2010-03-23 | 187 | 172 | 5389 | C | TREE CONTACTS | Repair 11kV lines pole W827 Kahungungu
13282 | 23/03/2010 | 2009 | 2010-03-23 | 483 | 59 | 28349 | C | DEFECTIVE EQUIPMENT | Repair PMR CB C2175 Waingake Valley
13298 | 23/03/2010 | 2009 | 2010-03-23 | 246 | 8 | 1968 | B | PLANNED SHUTDOWN | Replace 11kV pole C108 Paparatu Rd
13283 | 24/03/2010 | 2009 | 2010-03-24 | 107 | 193 | 5131 | C | TREE CONTACTS | Repair 11kV lines pole E1106 Kanakanaia Rd
13284 | 24/03/2010 | 2009 | 2010-03-24 | 143 | 19 | 2717 | C | TREE CONTACTS | Isolate 11kV for tree cutting pole W5150 Ruapapa Rd
13307 | 24/03/2010 | 2009 | 2010-03-24 | 297 | 42 | 12474 | B | PLANNED SHUTDOWN | Replace 2 11kV poles E523 E526 Waimata Valley Rd
13285 | 25/03/2010 | 2009 | 2010-03-25 | 302 | 8 | 2416 | C | DEFECTIVE EQUIPMENT | Replace X arm on pole F772 Makaretu Rd
13286 | 25/03/2010 | 2009 | 2010-03-25 | 54 | 3 | 162 | C | DEFECTIVE EQUIPMENT | Replace 3 DDO fuses pole H218 Makarika Rd
13308 | 26/03/2010 | 2009 | 2010-03-26 | 424 | 12 | 5088 | B | PLANNED SHUTDOWN | Replace 3 11kV poles G540 G548 G538 Waimata Valley Rd
13311 | 29/03/2010 | 2009 | 2010-03-29 | 38 | 764 | 11468 | C | DEFECTIVE EQUIPMENT | Reliven CB J544 Ruatoria Sub due to Generator Overload
13287 | 30/03/2010 | 2009 | 2010-03-30 | 43 | 18 | 774 | C | DEFECTIVE EQUIPMENT | Replace X arm on pole G725 Kaiaua Rd
13306 | 30/03/2010 | 2009 | 2010-03-30 | 83 | 6 | 498 | B | PLANNED SHUTDOWN | Relocate 11kV cable Gas switch B6275 Awapuni Rd
13310 | 30/03/2010 | 2009 | 2010-03-30 | 180 | 32 | 5760 | B | PLANNED SHUTDOWN | Erect 3 DDO fuses on pole A3505 Caves Rd
13309 | 31/03/2010 | 2009 | 2010-03-31 | 59 | 4 | 236 | B | PLANNED SHUTDOWN | Replace T/x C173 2278 Wharerata Rd
7920861

## 20092010NormalisedDailyTotals
Date Outage | Year | TotAVG | Customers Impacted | Total Customer Minutes Lost | Saidi | Safi
31/08/2009 | 2009 | 25366 | 4139 | 256676 | 10.1189 | 0.16317
31/07/2009 | 2009 | 25366 | 85 | 2594 | 0.10226 | 0.0033509
31/05/2009 | 2009 | 25366 | 92 | 22139 | 0.87278 | 0.0036269
31/03/2010 | 2009 | 25366 | 4 | 236 | 0.0093038 | 0.00015769
31/01/2010 | 2009 | 25366 | 224 | 93017 | 3.667 | 0.0088307
30/11/2009 | 2009 | 25366 | 4526 | 72279 | 2.8494 | 0.17843
30/10/2009 | 2009 | 25366 | 730 | 27862 | 1.0984 | 0.028779
30/09/2009 | 2009 | 25366 | 182 | 3458 | 0.13632 | 0.007175
30/08/2009 | 2009 | 25366 | 168 | 28862 | 1.1378 | 0.006623
30/07/2009 | 2009 | 25366 | 687 | 26146 | 1.0307 | 0.027083
30/06/2009 | 2009 | 25366 | 72 | 3591 | 0.14157 | 0.0028384
30/05/2009 | 2009 | 25366 | 97 | 12319 | 0.48565 | 0.003824
30/04/2009 | 2009 | 25366 | 50 | 4620 | 0.18213 | 0.0019711
30/03/2010 | 2009 | 25366 | 56 | 7032 | 0.27722 | 0.0022077
30/01/2010 | 2009 | 25366 | 402 | 209629 | 8.2642 | 0.015848
29/12/2009 | 2009 | 25366 | 237 | 2438 | 0.096113 | 0.0093432
29/10/2009 | 2009 | 25366 | 2339 | 178644 | 7.0427 | 0.09221
29/09/2009 | 2009 | 25366 | 124 | 12158 | 0.4793 | 0.0048884
29/07/2009 | 2009 | 25366 | 134 | 34220 | 1.349 | 0.0052827
29/06/2009 | 2009 | 25366 | 466 | 31631 | 1.247 | 0.018371
29/05/2009 | 2009 | 25366 | 94 | 4492 | 0.17709 | 0.0037057
29/03/2010 | 2009 | 25366 | 764 | 11468 | 0.4521 | 0.030119
29/01/2010 | 2009 | 25366 | 12 | 3036 | 0.11969 | 0.00047307
28/10/2009 | 2009 | 25366 | 76 | 10504 | 0.4141 | 0.0029961
28/09/2009 | 2009 | 25366 | 130 | 6512 | 0.25672 | 0.005125
28/08/2009 | 2009 | 25366 | 24 | 3146 | 0.12402 | 0.00094615
28/05/2009 | 2009 | 25366 | 52 | 4176 | 0.16463 | 0.00205
28/04/2009 | 2009 | 25366 | 175 | 952 | 0.037531 | 0.006899
28/02/2010 | 2009 | 25366 | 156 | 18193 | 0.71722 | 0.00615
28/01/2010 | 2009 | 25366 | 21 | 1764 | 0.069542 | 0.00082788
27/12/2009 | 2009 | 25366 | 6 | 720 | 0.028384 | 0.00023654
27/11/2009 | 2009 | 25366 | 1197 | 25320 | 0.99819 | 0.047189
27/10/2009 | 2009 | 25366 | 1179 | 19732 | 0.77789 | 0.04648
27/08/2009 | 2009 | 25366 | 610 | 65115 | 2.567 | 0.024048
27/07/2009 | 2009 | 25366 | 121 | 5745 | 0.22648 | 0.0047702
27/05/2009 | 2009 | 25366 | 119 | 16196 | 0.63849 | 0.0046913
27/04/2009 | 2009 | 25366 | 166 | 17094 | 0.67389 | 0.0065442
27/02/2010 | 2009 | 25366 | 1105 | 146673 | 5.7823 | 0.043562
26/11/2009 | 2009 | 25366 | 386 | 63055 | 2.4858 | 0.015217
26/08/2009 | 2009 | 25366 | 558 | 98699 | 3.891 | 0.021998
26/07/2009 | 2009 | 25366 | 10 | 720 | 0.028384 | 0.00039423
26/06/2009 | 2009 | 25366 | 331 | 26070 | 1.0278 | 0.013049
26/05/2009 | 2009 | 25366 | 887 | 33091 | 1.3045 | 0.034968
26/04/2009 | 2009 | 25366 | 30 | 1440 | 0.056769 | 0.0011827
26/03/2010 | 2009 | 25366 | 12 | 5088 | 0.20058 | 0.00047307
26/01/2010 | 2009 | 25366 | 187 | 95139 | 3.7507 | 0.0073721
25/11/2009 | 2009 | 25366 | 12 | 1068 | 0.042104 | 0.00047307
25/09/2009 | 2009 | 25366 | 54 | 2708 | 0.10676 | 0.0021288
25/08/2009 | 2009 | 25366 | 230 | 29220 | 1.1519 | 0.0090673
25/07/2009 | 2009 | 25366 | 15 | 641 | 0.02527 | 0.00059134
25/06/2009 | 2009 | 25366 | 139 | 16024 | 0.63171 | 0.0054798
25/05/2009 | 2009 | 25366 | 77 | 2546 | 0.10037 | 0.0030356
25/04/2009 | 2009 | 25366 | 7 | 791 | 0.031183 | 0.00027596
25/03/2010 | 2009 | 25366 | 11 | 2578 | 0.10163 | 0.00043365
25/02/2010 | 2009 | 25366 | 232 | 3454 | 0.13617 | 0.0091461
25/01/2010 | 2009 | 25366 | 171 | 41976 | 1.6548 | 0.0067413
24/12/2009 | 2009 | 25366 | 120 | 40200 | 1.5848 | 0.0047307
24/11/2009 | 2009 | 25366 | 49 | 1323 | 0.052156 | 0.0019317
24/09/2009 | 2009 | 25366 | 131 | 5323 | 0.20985 | 0.0051644
24/08/2009 | 2009 | 25366 | 6 | 1080 | 0.042577 | 0.00023654
24/07/2009 | 2009 | 25366 | 1147 | 214834 | 8.4694 | 0.045218
24/05/2009 | 2009 | 25366 | 128 | 1855 | 0.073129 | 0.0050461
24/04/2009 | 2009 | 25366 | 230 | 1840 | 0.072538 | 0.0090673
24/03/2010 | 2009 | 25366 | 254 | 20322 | 0.80115 | 0.010013
23/12/2009 | 2009 | 25366 | 20 | 1200 | 0.047307 | 0.00078846
23/11/2009 | 2009 | 25366 | 65 | 4875 | 0.19219 | 0.0025625
23/10/2009 | 2009 | 25366 | 2964 | 31955 | 1.2598 | 0.11685
23/09/2009 | 2009 | 25366 | 346 | 50298 | 1.9829 | 0.01364
23/08/2009 | 2009 | 25366 | 438 | 75602 | 2.9804 | 0.017267
23/07/2009 | 2009 | 25366 | 503 | 334956 | 13.2049 | 0.01983
23/06/2009 | 2009 | 25366 | 18 | 5508 | 0.21714 | 0.00070961
23/05/2009 | 2009 | 25366 | 642 | 48100 | 1.8962 | 0.025309
23/04/2009 | 2009 | 25366 | 80 | 4800 | 0.18923 | 0.0031538
23/03/2010 | 2009 | 25366 | 239 | 35706 | 1.4076 | 0.0094221
23/02/2010 | 2009 | 25366 | 83 | 29323 | 1.156 | 0.0032721
23/01/2010 | 2009 | 25366 | 32 | 8200 | 0.32327 | 0.0012615
22/12/2009 | 2009 | 25366 | 293 | 27694 | 1.0918 | 0.011551
22/11/2009 | 2009 | 25366 | 2516 | 65416 | 2.5789 | 0.099188
22/10/2009 | 2009 | 25366 | 25 | 4450 | 0.17543 | 0.00098557
22/09/2009 | 2009 | 25366 | 1908 | 22744 | 0.89663 | 0.075219
22/08/2009 | 2009 | 25366 | 77 | 21329 | 0.84085 | 0.0030356
22/07/2009 | 2009 | 25366 | 26 | 12473 | 0.49172 | 0.001025
22/06/2009 | 2009 | 25366 | 51 | 3389 | 0.1336 | 0.0020106
22/05/2009 | 2009 | 25366 | 2784 | 33408 | 1.317 | 0.10975
22/03/2010 | 2009 | 25366 | 56 | 23128 | 0.91177 | 0.0022077
22/02/2010 | 2009 | 25366 | 21 | 231 | 0.0091067 | 0.00082788
22/01/2010 | 2009 | 25366 | 11 | 4521 | 0.17823 | 0.00043365
21/10/2009 | 2009 | 25366 | 206 | 11790 | 0.4648 | 0.0081211
21/09/2009 | 2009 | 25366 | 31 | 6987 | 0.27545 | 0.0012221
21/07/2009 | 2009 | 25366 | 341 | 24470 | 0.96468 | 0.013443
21/05/2009 | 2009 | 25366 | 269 | 38700 | 1.5257 | 0.010605
21/04/2009 | 2009 | 25366 | 526 | 32256 | 1.2716 | 0.020736
21/01/2010 | 2009 | 25366 | 113 | 23765 | 0.93688 | 0.0044548
20/10/2009 | 2009 | 25366 | 190 | 17347 | 0.68387 | 0.0074903
20/08/2009 | 2009 | 25366 | 223 | 23339 | 0.92009 | 0.0087913
20/07/2009 | 2009 | 25366 | 211 | 25977 | 1.0241 | 0.0083182
20/06/2009 | 2009 | 25366 | 32 | 3360 | 0.13246 | 0.0012615
20/04/2009 | 2009 | 25366 | 96 | 6144 | 0.24221 | 0.0037846
20/01/2010 | 2009 | 25366 | 14 | 6552 | 0.2583 | 0.00055192
19/11/2009 | 2009 | 25366 | 44 | 15180 | 0.59844 | 0.0017346
19/09/2009 | 2009 | 25366 | 656 | 40888 | 1.6119 | 0.025861
19/08/2009 | 2009 | 25366 | 16 | 4960 | 0.19554 | 0.00063077
19/07/2009 | 2009 | 25366 | 343 | 100152 | 3.9483 | 0.013522
18/08/2009 | 2009 | 25366 | 85 | 25983 | 1.0243 | 0.0033509
18/06/2009 | 2009 | 25366 | 289 | 16476 | 0.64953 | 0.011393
18/05/2009 | 2009 | 25366 | 248 | 11983 | 0.4724 | 0.0097769
18/04/2009 | 2009 | 25366 | 75 | 4550 | 0.17937 | 0.0029567
18/03/2010 | 2009 | 25366 | 12 | 19824 | 0.78152 | 0.00047307
18/02/2010 | 2009 | 25366 | 12 | 4476 | 0.17646 | 0.00047307
18/01/2010 | 2009 | 25366 | 128 | 19840 | 0.78215 | 0.0050461
17/12/2009 | 2009 | 25366 | 247 | 19719 | 0.77738 | 0.0097374
17/11/2009 | 2009 | 25366 | 1865 | 47292 | 1.8644 | 0.073524
17/09/2009 | 2009 | 25366 | 408 | 41093 | 1.62 | 0.016085
17/08/2009 | 2009 | 25366 | 7 | 385 | 0.015178 | 0.00027596
17/04/2009 | 2009 | 25366 | 33 | 4797 | 0.18911 | 0.001301
17/03/2010 | 2009 | 25366 | 95 | 22856 | 0.90105 | 0.0037452
16/11/2009 | 2009 | 25366 | 198 | 26398 | 1.0407 | 0.0078057
16/10/2009 | 2009 | 25366 | 12 | 1164 | 0.045888 | 0.00047307
16/09/2009 | 2009 | 25366 | 719 | 30861 | 1.2166 | 0.028345
16/07/2009 | 2009 | 25366 | 892 | 14732 | 0.58078 | 0.035165
16/04/2009 | 2009 | 25366 | 29 | 3714 | 0.14642 | 0.0011433
16/03/2010 | 2009 | 25366 | 236 | 48367 | 1.9068 | 0.0093038
16/02/2010 | 2009 | 25366 | 483 | 42082 | 1.659 | 0.019041
16/01/2010 | 2009 | 25366 | 1518 | 80217 | 3.1624 | 0.059844
15/12/2009 | 2009 | 25366 | 17 | 8364 | 0.32973 | 0.00067019
15/11/2009 | 2009 | 25366 | 755 | 79926 | 3.1509 | 0.029764
15/10/2009 | 2009 | 25366 | 321 | 27896 | 1.0997 | 0.012655
15/09/2009 | 2009 | 25366 | 4 | 1908 | 0.075219 | 0.00015769
15/07/2009 | 2009 | 25366 | 146 | 32320 | 1.2741 | 0.0057557
15/06/2009 | 2009 | 25366 | 8 | 128 | 0.0050461 | 0.00031538
15/04/2009 | 2009 | 25366 | 87 | 6237 | 0.24588 | 0.0034298
15/03/2010 | 2009 | 25366 | 24 | 3120 | 0.123 | 0.00094615
15/01/2010 | 2009 | 25366 | 75 | 3900 | 0.15375 | 0.0029567
14/10/2009 | 2009 | 25366 | 202 | 15615 | 0.61559 | 0.0079634
14/09/2009 | 2009 | 25366 | 138 | 23582 | 0.92967 | 0.0054404
14/08/2009 | 2009 | 25366 | 18 | 948 | 0.037373 | 0.00070961
14/07/2009 | 2009 | 25366 | 175 | 25242 | 0.99511 | 0.006899
14/06/2009 | 2009 | 25366 | 38 | 874 | 0.034456 | 0.0014981
13/10/2009 | 2009 | 25366 | 182 | 37178 | 1.4657 | 0.007175
13/08/2009 | 2009 | 25366 | 487 | 47858 | 1.8867 | 0.019199
13/07/2009 | 2009 | 25366 | 506 | 108178 | 4.2647 | 0.019948
13/06/2009 | 2009 | 25366 | 7274 | 215743 | 8.5052 | 0.28676
13/05/2009 | 2009 | 25366 | 8 | 1216 | 0.047938 | 0.00031538
13/03/2010 | 2009 | 25366 | 208 | 12215 | 0.48155 | 0.0082
13/01/2010 | 2009 | 25366 | 998 | 56575 | 2.2303 | 0.039344
12/10/2009 | 2009 | 25366 | 114 | 6228 | 0.24553 | 0.0044942
12/08/2009 | 2009 | 25366 | 361 | 31410 | 1.2383 | 0.014232
12/04/2009 | 2009 | 25366 | 127 | 15875 | 0.62584 | 0.0050067
12/03/2010 | 2009 | 25366 | 60 | 7464 | 0.29425 | 0.0023654
12/01/2010 | 2009 | 25366 | 168 | 40291 | 1.5884 | 0.006623
11/10/2009 | 2009 | 25366 | 512 | 47104 | 1.857 | 0.020184
11/09/2009 | 2009 | 25366 | 1460 | 70706 | 2.7874 | 0.057557
11/08/2009 | 2009 | 25366 | 207 | 45840 | 1.8071 | 0.0081605
11/02/2010 | 2009 | 25366 | 58 | 3306 | 0.13033 | 0.0022865
11/01/2010 | 2009 | 25366 | 431 | 103131 | 4.0657 | 0.016991
10/12/2009 | 2009 | 25366 | 11 | 4785 | 0.18864 | 0.00043365
10/11/2009 | 2009 | 25366 | 133 | 32172 | 1.2683 | 0.0052432
10/10/2009 | 2009 | 25366 | 3668 | 58964 | 2.3245 | 0.1446
10/09/2009 | 2009 | 25366 | 124 | 22508 | 0.88733 | 0.0048884
10/08/2009 | 2009 | 25366 | 778 | 73994 | 2.9171 | 0.030671
10/06/2009 | 2009 | 25366 | 19 | 6099 | 0.24044 | 0.00074903
10/03/2010 | 2009 | 25366 | 74 | 18898 | 0.74501 | 0.0029173
10/02/2010 | 2009 | 25366 | 190 | 6488 | 0.25578 | 0.0074903
10/01/2010 | 2009 | 25366 | 61 | 16959 | 0.66857 | 0.0024048
09/12/2009 | 2009 | 25366 | 30 | 6762 | 0.26658 | 0.0011827
09/10/2009 | 2009 | 25366 | 224 | 48612 | 1.9164 | 0.0088307
09/04/2009 | 2009 | 25366 | 36 | 1776 | 0.070015 | 0.0014192
09/03/2010 | 2009 | 25366 | 32 | 896 | 0.035323 | 0.0012615
09/02/2010 | 2009 | 25366 | 162 | 37567 | 1.481 | 0.0063865
08/12/2009 | 2009 | 25366 | 188 | 20268 | 0.79902 | 0.0074115
08/10/2009 | 2009 | 25366 | 214 | 73306 | 2.8899 | 0.0084365
08/09/2009 | 2009 | 25366 | 157 | 50239 | 1.9806 | 0.0061894
08/08/2009 | 2009 | 25366 | 428 | 25911 | 1.0215 | 0.016873
08/07/2009 | 2009 | 25366 | 157 | 28068 | 1.1065 | 0.0061894
08/04/2009 | 2009 | 25366 | 17 | 4182 | 0.16487 | 0.00067019
08/02/2010 | 2009 | 25366 | 74 | 5349 | 0.21087 | 0.0029173
08/01/2010 | 2009 | 25366 | 117 | 32890 | 1.2966 | 0.0046125
07/12/2009 | 2009 | 25366 | 935 | 38883 | 1.5329 | 0.03686
07/10/2009 | 2009 | 25366 | 132 | 192514 | 7.5895 | 0.0052038
07/09/2009 | 2009 | 25366 | 139 | 42765 | 1.6859 | 0.0054798
07/08/2009 | 2009 | 25366 | 50 | 15700 | 0.61894 | 0.0019711
07/07/2009 | 2009 | 25366 | 270 | 27568 | 1.0868 | 0.010644
07/05/2009 | 2009 | 25366 | 40 | 1080 | 0.042577 | 0.0015769
07/04/2009 | 2009 | 25366 | 57 | 1710 | 0.067413 | 0.0022471
07/03/2010 | 2009 | 25366 | 572 | 53281 | 2.1005 | 0.02255
07/02/2010 | 2009 | 25366 | 117 | 23259 | 0.91694 | 0.0046125
07/01/2010 | 2009 | 25366 | 42 | 526 | 0.020736 | 0.0016558
06/12/2009 | 2009 | 25366 | 2516 | 111468 | 4.3944 | 0.099188
06/10/2009 | 2009 | 25366 | 713 | 195804 | 7.7192 | 0.028108
06/08/2009 | 2009 | 25366 | 1002 | 102868 | 4.0553 | 0.039502
06/07/2009 | 2009 | 25366 | 16 | 2800 | 0.11038 | 0.00063077
06/06/2009 | 2009 | 25366 | 19 | 2812 | 0.11086 | 0.00074903
06/02/2010 | 2009 | 25366 | 8 | 336 | 0.013246 | 0.00031538
05/11/2009 | 2009 | 25366 | 91 | 25137 | 0.99097 | 0.0035875
05/10/2009 | 2009 | 25366 | 1280 | 325983 | 12.8512 | 0.050461
05/08/2009 | 2009 | 25366 | 85 | 27030 | 1.0656 | 0.0033509
05/07/2009 | 2009 | 25366 | 77 | 18403 | 0.7255 | 0.0030356
05/05/2009 | 2009 | 25366 | 162 | 6462 | 0.25475 | 0.0063865
05/04/2009 | 2009 | 25366 | 132 | 2251 | 0.088741 | 0.0052038
05/03/2010 | 2009 | 25366 | 965 | 57570 | 2.2696 | 0.038043
04/12/2009 | 2009 | 25366 | 193 | 13244 | 0.52212 | 0.0076086
04/11/2009 | 2009 | 25366 | 67 | 12515 | 0.49338 | 0.0026413
04/10/2009 | 2009 | 25366 | 240 | 229543 | 9.0492 | 0.0094615
04/09/2009 | 2009 | 25366 | 154 | 43019 | 1.6959 | 0.0060711
04/08/2009 | 2009 | 25366 | 108 | 11887 | 0.46862 | 0.0042577
04/07/2009 | 2009 | 25366 | 297 | 55354 | 2.1822 | 0.011709
04/06/2009 | 2009 | 25366 | 262 | 11790 | 0.4648 | 0.010329
04/05/2009 | 2009 | 25366 | 221 | 18168 | 0.71623 | 0.0087124
04/03/2010 | 2009 | 25366 | 14 | 4844 | 0.19096 | 0.00055192
04/02/2010 | 2009 | 25366 | 71 | 18381 | 0.72463 | 0.002799
04/01/2010 | 2009 | 25366 | 156 | 16850 | 0.66428 | 0.00615
03/12/2009 | 2009 | 25366 | 208 | 35830 | 1.4125 | 0.0082
03/11/2009 | 2009 | 25366 | 34 | 2773 | 0.10932 | 0.0013404
03/09/2009 | 2009 | 25366 | 926 | 51799 | 2.0421 | 0.036506
03/07/2009 | 2009 | 25366 | 161 | 35483 | 1.3988 | 0.0063471
03/06/2009 | 2009 | 25366 | 88 | 22256 | 0.87739 | 0.0034692
03/02/2010 | 2009 | 25366 | 23 | 2312 | 0.091146 | 0.00090673
03/01/2010 | 2009 | 25366 | 22 | 4620 | 0.18213 | 0.0008673
02/12/2009 | 2009 | 25366 | 547 | 104130 | 4.1051 | 0.021564
02/11/2009 | 2009 | 25366 | 27 | 2187 | 0.086218 | 0.0010644
02/10/2009 | 2009 | 25366 | 58 | 15481 | 0.61031 | 0.0022865
02/07/2009 | 2009 | 25366 | 163 | 74254 | 2.9273 | 0.0064259
02/06/2009 | 2009 | 25366 | 23 | 2748 | 0.10833 | 0.00090673
02/04/2009 | 2009 | 25366 | 153 | 20339 | 0.80182 | 0.0060317
02/03/2010 | 2009 | 25366 | 6 | 3108 | 0.12253 | 0.00023654
02/02/2010 | 2009 | 25366 | 72 | 25904 | 1.0212 | 0.0028384
01/12/2009 | 2009 | 25366 | 17 | 765 | 0.030158 | 0.00067019
01/10/2009 | 2009 | 25366 | 381 | 17189 | 0.67764 | 0.01502
01/09/2009 | 2009 | 25366 | 431 | 27237 | 1.0738 | 0.016991
01/07/2009 | 2009 | 25366 | 80 | 35976 | 1.4183 | 0.0031538
01/06/2009 | 2009 | 25366 | 281 | 132096 | 5.2076 | 0.011078
01/05/2009 | 2009 | 25366 | 131 | 2722 | 0.10731 | 0.0051644
01/04/2009 | 2009 | 25366 | 25 | 1150 | 0.045336 | 0.00098557
01/03/2010 | 2009 | 25366 | 23 | 8942 | 0.35252 | 0.00090673
01/02/2010 | 2009 | 25366 | 751 | 103228 | 4.0695 | 0.029607

## 20092010FixedData
Date Outage | Saidi | Safi | FixedSaidi | FixedSaifi
10/02/2010 | 0.25578 | 0.0074903 | 0.25578 | 0.0074903 | 312.2629 | 3.4784
01/02/2010 | 4.0695 | 0.029607 | 4.0695 | 0.029607
12/01/2010 | 1.5884 | 0.006623 | 1.5884 | 0.006623
11/10/2009 | 1.857 | 0.020184 | 1.857 | 0.020184
11/09/2009 | 2.7874 | 0.057557 | 2.7874 | 0.057557
11/08/2009 | 1.8071 | 0.0081605 | 1.8071 | 0.0081605
11/02/2010 | 0.13033 | 0.0022865 | 0.13033 | 0.0022865
11/01/2010 | 4.0657 | 0.016991 | 4.0657 | 0.016991
10/12/2009 | 0.18864 | 0.00043365 | 0.18864 | 0.00043365
10/11/2009 | 1.2683 | 0.0052432 | 1.2683 | 0.0052432
10/10/2009 | 2.3245 | 0.1446 | 2.3245 | 0.1446
10/09/2009 | 0.88733 | 0.0048884 | 0.88733 | 0.0048884
10/08/2009 | 2.9171 | 0.030671 | 2.9171 | 0.030671
12/04/2009 | 0.62584 | 0.0050067 | 0.62584 | 0.0050067
10/03/2010 | 0.74501 | 0.0029173 | 0.74501 | 0.0029173
12/08/2009 | 1.2383 | 0.014232 | 1.2383 | 0.014232
10/01/2010 | 0.66857 | 0.0024048 | 0.66857 | 0.0024048
09/12/2009 | 0.26658 | 0.0011827 | 0.26658 | 0.0011827
09/10/2009 | 1.9164 | 0.0088307 | 1.9164 | 0.0088307
09/04/2009 | 0.070015 | 0.0014192 | 0.070015 | 0.0014192
09/03/2010 | 0.035323 | 0.0012615 | 0.035323 | 0.0012615
09/02/2010 | 1.481 | 0.0063865 | 1.481 | 0.0063865
08/12/2009 | 0.79902 | 0.0074115 | 0.79902 | 0.0074115
08/10/2009 | 2.8899 | 0.0084365 | 2.8899 | 0.0084365
08/09/2009 | 1.9806 | 0.0061894 | 1.9806 | 0.0061894
08/08/2009 | 1.0215 | 0.016873 | 1.0215 | 0.016873
08/07/2009 | 1.1065 | 0.0061894 | 1.1065 | 0.0061894
08/04/2009 | 0.16487 | 0.00067019 | 0.16487 | 0.00067019
10/06/2009 | 0.24044 | 0.00074903 | 0.24044 | 0.00074903
14/10/2009 | 0.61559 | 0.0079634 | 0.61559 | 0.0079634
16/07/2009 | 0.58078 | 0.035165 | 0.58078 | 0.035165
16/04/2009 | 0.14642 | 0.0011433 | 0.14642 | 0.0011433
16/03/2010 | 1.9068 | 0.0093038 | 1.9068 | 0.0093038
16/02/2010 | 1.659 | 0.019041 | 1.659 | 0.019041
16/01/2010 | 3.1624 | 0.059844 | 3.1624 | 0.059844
15/12/2009 | 0.32973 | 0.00067019 | 0.32973 | 0.00067019
15/11/2009 | 3.1509 | 0.029764 | 3.1509 | 0.029764
15/10/2009 | 1.0997 | 0.012655 | 1.0997 | 0.012655
15/09/2009 | 0.075219 | 0.00015769 | 0.075219 | 0.00015769
15/07/2009 | 1.2741 | 0.0057557 | 1.2741 | 0.0057557
15/06/2009 | 0.0050461 | 0.00031538 | 0.0050461 | 0.00031538
15/04/2009 | 0.24588 | 0.0034298 | 0.24588 | 0.0034298
12/03/2010 | 0.29425 | 0.0023654 | 0.29425 | 0.0023654
15/01/2010 | 0.15375 | 0.0029567 | 0.15375 | 0.0029567
07/12/2009 | 1.5329 | 0.03686 | 1.5329 | 0.03686
14/09/2009 | 0.92967 | 0.0054404 | 0.92967 | 0.0054404
14/08/2009 | 0.037373 | 0.00070961 | 0.037373 | 0.00070961
14/07/2009 | 0.99511 | 0.006899 | 0.99511 | 0.006899
14/06/2009 | 0.034456 | 0.0014981 | 0.034456 | 0.0014981
13/10/2009 | 1.4657 | 0.007175 | 1.4657 | 0.007175
13/08/2009 | 1.8867 | 0.019199 | 1.8867 | 0.019199
13/07/2009 | 4.2647 | 0.019948 | 4.2647 | 0.019948
13/06/2009 | 8.5052 | 0.28676 | 8.5052 | 0.28676
13/05/2009 | 0.047938 | 0.00031538 | 0.047938 | 0.00031538
13/03/2010 | 0.48155 | 0.0082 | 0.48155 | 0.0082
13/01/2010 | 2.2303 | 0.039344 | 2.2303 | 0.039344
12/10/2009 | 0.24553 | 0.0044942 | 0.24553 | 0.0044942
15/03/2010 | 0.123 | 0.00094615 | 0.123 | 0.00094615
02/07/2009 | 2.9273 | 0.0064259 | 2.9273 | 0.0064259
04/05/2009 | 0.71623 | 0.0087124 | 0.71623 | 0.0087124
04/03/2010 | 0.19096 | 0.00055192 | 0.19096 | 0.00055192
04/02/2010 | 0.72463 | 0.002799 | 0.72463 | 0.002799
04/01/2010 | 0.66428 | 0.00615 | 0.66428 | 0.00615
03/12/2009 | 1.4125 | 0.0082 | 1.4125 | 0.0082
03/11/2009 | 0.10932 | 0.0013404 | 0.10932 | 0.0013404
03/09/2009 | 2.0421 | 0.036506 | 2.0421 | 0.036506
03/07/2009 | 1.3988 | 0.0063471 | 1.3988 | 0.0063471
03/06/2009 | 0.87739 | 0.0034692 | 0.87739 | 0.0034692
03/02/2010 | 0.091146 | 0.00090673 | 0.091146 | 0.00090673
03/01/2010 | 0.18213 | 0.0008673 | 0.18213 | 0.0008673
02/12/2009 | 4.1051 | 0.021564 | 4.1051 | 0.021564
08/02/2010 | 0.21087 | 0.0029173 | 0.21087 | 0.0029173
02/10/2009 | 0.61031 | 0.0022865 | 0.61031 | 0.0022865
04/08/2009 | 0.46862 | 0.0042577 | 0.46862 | 0.0042577
02/06/2009 | 0.10833 | 0.00090673 | 0.10833 | 0.00090673
02/04/2009 | 0.80182 | 0.0060317 | 0.80182 | 0.0060317
02/03/2010 | 0.12253 | 0.00023654 | 0.12253 | 0.00023654
02/02/2010 | 1.0212 | 0.0028384 | 1.0212 | 0.0028384
01/12/2009 | 0.030158 | 0.00067019 | 0.030158 | 0.00067019
01/10/2009 | 0.67764 | 0.01502 | 0.67764 | 0.01502
01/09/2009 | 1.0738 | 0.016991 | 1.0738 | 0.016991
01/07/2009 | 1.4183 | 0.0031538 | 1.4183 | 0.0031538
01/06/2009 | 5.2076 | 0.011078 | 5.2076 | 0.011078
01/05/2009 | 0.10731 | 0.0051644 | 0.10731 | 0.0051644
01/04/2009 | 0.045336 | 0.00098557 | 0.045336 | 0.00098557
01/03/2010 | 0.35252 | 0.00090673 | 0.35252 | 0.00090673
02/11/2009 | 0.086218 | 0.0010644 | 0.086218 | 0.0010644
06/06/2009 | 0.11086 | 0.00074903 | 0.11086 | 0.00074903
16/11/2009 | 1.0407 | 0.0078057 | 1.0407 | 0.0078057
07/10/2009 | 7.5895 | 0.0052038 | 7.5895 | 0.0052038
07/09/2009 | 1.6859 | 0.0054798 | 1.6859 | 0.0054798
07/08/2009 | 0.61894 | 0.0019711 | 0.61894 | 0.0019711
07/07/2009 | 1.0868 | 0.010644 | 1.0868 | 0.010644
07/05/2009 | 0.042577 | 0.0015769 | 0.042577 | 0.0015769
07/04/2009 | 0.067413 | 0.0022471 | 0.067413 | 0.0022471
07/03/2010 | 2.1005 | 0.02255 | 2.1005 | 0.02255
07/02/2010 | 0.91694 | 0.0046125 | 0.91694 | 0.0046125
07/01/2010 | 0.020736 | 0.0016558 | 0.020736 | 0.0016558
06/12/2009 | 4.3944 | 0.099188 | 4.3944 | 0.099188
06/10/2009 | 7.7192 | 0.028108 | 7.7192 | 0.028108
04/06/2009 | 0.4648 | 0.010329 | 0.4648 | 0.010329
06/07/2009 | 0.11038 | 0.00063077 | 0.11038 | 0.00063077
04/07/2009 | 2.1822 | 0.011709 | 2.1822 | 0.011709
06/02/2010 | 0.013246 | 0.00031538 | 0.013246 | 0.00031538
05/11/2009 | 0.99097 | 0.0035875 | 0.99097 | 0.0035875
05/10/2009 | 12.8512 | 0.050461 | 12.8512 | 0.050461
05/08/2009 | 1.0656 | 0.0033509 | 1.0656 | 0.0033509
05/07/2009 | 0.7255 | 0.0030356 | 0.7255 | 0.0030356
05/05/2009 | 0.25475 | 0.0063865 | 0.25475 | 0.0063865
05/04/2009 | 0.088741 | 0.0052038 | 0.088741 | 0.0052038
05/03/2010 | 2.2696 | 0.038043 | 2.2696 | 0.038043
04/12/2009 | 0.52212 | 0.0076086 | 0.52212 | 0.0076086
04/11/2009 | 0.49338 | 0.0026413 | 0.49338 | 0.0026413
04/10/2009 | 9.0492 | 0.0094615 | 9.0492 | 0.0094615
04/09/2009 | 1.6959 | 0.0060711 | 1.6959 | 0.0060711
08/01/2010 | 1.2966 | 0.0046125 | 1.2966 | 0.0046125
06/08/2009 | 4.0553 | 0.039502 | 4.0553 | 0.039502
26/01/2010 | 3.7507 | 0.0073721 | 3.7507 | 0.0073721
27/11/2009 | 0.99819 | 0.047189 | 0.99819 | 0.047189
27/10/2009 | 0.77789 | 0.04648 | 0.77789 | 0.04648
27/08/2009 | 2.567 | 0.024048 | 2.567 | 0.024048
27/07/2009 | 0.22648 | 0.0047702 | 0.22648 | 0.0047702
27/05/2009 | 0.63849 | 0.0046913 | 0.63849 | 0.0046913
27/04/2009 | 0.67389 | 0.0065442 | 0.67389 | 0.0065442
27/02/2010 | 5.7823 | 0.043562 | 5.7823 | 0.043562
26/11/2009 | 2.4858 | 0.015217 | 2.4858 | 0.015217
26/08/2009 | 3.891 | 0.021998 | 3.891 | 0.021998
26/07/2009 | 0.028384 | 0.00039423 | 0.028384 | 0.00039423
26/06/2009 | 1.0278 | 0.013049 | 1.0278 | 0.013049
26/05/2009 | 1.3045 | 0.034968 | 1.3045 | 0.034968
24/09/2009 | 0.20985 | 0.0051644 | 0.20985 | 0.0051644
26/03/2010 | 0.20058 | 0.00047307 | 0.20058 | 0.00047307
28/02/2010 | 0.71722 | 0.00615 | 0.71722 | 0.00615
25/11/2009 | 0.042104 | 0.00047307 | 0.042104 | 0.00047307
25/09/2009 | 0.10676 | 0.0021288 | 0.10676 | 0.0021288
25/08/2009 | 1.1519 | 0.0090673 | 1.1519 | 0.0090673
25/07/2009 | 0.02527 | 0.00059134 | 0.02527 | 0.00059134
25/06/2009 | 0.63171 | 0.0054798 | 0.63171 | 0.0054798
25/05/2009 | 0.10037 | 0.0030356 | 0.10037 | 0.0030356
25/04/2009 | 0.031183 | 0.00027596 | 0.031183 | 0.00027596
25/03/2010 | 0.10163 | 0.00043365 | 0.10163 | 0.00043365
25/02/2010 | 0.13617 | 0.0091461 | 0.13617 | 0.0091461
25/01/2010 | 1.6548 | 0.0067413 | 1.6548 | 0.0067413
24/12/2009 | 1.5848 | 0.0047307 | 1.5848 | 0.0047307
16/09/2009 | 1.2166 | 0.028345 | 1.2166 | 0.028345
26/04/2009 | 0.056769 | 0.0011827 | 0.056769 | 0.0011827
29/12/2009 | 0.096113 | 0.0093432 | 0.096113 | 0.0093432
31/07/2009 | 0.10226 | 0.0033509 | 0.10226 | 0.0033509
31/05/2009 | 0.87278 | 0.0036269 | 0.87278 | 0.0036269
31/03/2010 | 0.0093038 | 0.00015769 | 0.0093038 | 0.00015769
31/01/2010 | 3.667 | 0.0088307 | 3.667 | 0.0088307
30/11/2009 | 2.8494 | 0.17843 | 2.8494 | 0.17843
30/10/2009 | 1.0984 | 0.028779 | 1.0984 | 0.028779
30/09/2009 | 0.13632 | 0.007175 | 0.13632 | 0.007175
30/08/2009 | 1.1378 | 0.006623 | 1.1378 | 0.006623
30/07/2009 | 1.0307 | 0.027083 | 1.0307 | 0.027083
30/06/2009 | 0.14157 | 0.0028384 | 0.14157 | 0.0028384
30/05/2009 | 0.48565 | 0.003824 | 0.48565 | 0.003824
30/04/2009 | 0.18213 | 0.0019711 | 0.18213 | 0.0019711
27/12/2009 | 0.028384 | 0.00023654 | 0.028384 | 0.00023654
30/01/2010 | 8.2642 | 0.015848 | 8.2642 | 0.015848
28/01/2010 | 0.069542 | 0.00082788 | 0.069542 | 0.00082788
29/10/2009 | 7.0427 | 0.09221 | 7.0427 | 0.09221
29/09/2009 | 0.4793 | 0.0048884 | 0.4793 | 0.0048884
29/07/2009 | 1.349 | 0.0052827 | 1.349 | 0.0052827
29/06/2009 | 1.247 | 0.018371 | 1.247 | 0.018371
29/05/2009 | 0.17709 | 0.0037057 | 0.17709 | 0.0037057
29/03/2010 | 0.4521 | 0.030119 | 0.4521 | 0.030119
29/01/2010 | 0.11969 | 0.00047307 | 0.11969 | 0.00047307
28/10/2009 | 0.4141 | 0.0029961 | 0.4141 | 0.0029961
28/09/2009 | 0.25672 | 0.005125 | 0.25672 | 0.005125
28/08/2009 | 0.12402 | 0.00094615 | 0.12402 | 0.00094615
28/05/2009 | 0.16463 | 0.00205 | 0.16463 | 0.00205
28/04/2009 | 0.037531 | 0.006899 | 0.037531 | 0.006899
24/08/2009 | 0.042577 | 0.00023654 | 0.042577 | 0.00023654
30/03/2010 | 0.27722 | 0.0022077 | 0.27722 | 0.0022077
18/06/2009 | 0.64953 | 0.011393 | 0.64953 | 0.011393
21/05/2009 | 1.5257 | 0.010605 | 1.5257 | 0.010605
21/04/2009 | 1.2716 | 0.020736 | 1.2716 | 0.020736
21/01/2010 | 0.93688 | 0.0044548 | 0.93688 | 0.0044548
20/10/2009 | 0.68387 | 0.0074903 | 0.68387 | 0.0074903
20/08/2009 | 0.92009 | 0.0087913 | 0.92009 | 0.0087913
20/07/2009 | 1.0241 | 0.0083182 | 1.0241 | 0.0083182
20/06/2009 | 0.13246 | 0.0012615 | 0.13246 | 0.0012615
20/04/2009 | 0.24221 | 0.0037846 | 0.24221 | 0.0037846
20/01/2010 | 0.2583 | 0.00055192 | 0.2583 | 0.00055192
19/11/2009 | 0.59844 | 0.0017346 | 0.59844 | 0.0017346
19/09/2009 | 1.6119 | 0.025861 | 1.6119 | 0.025861
19/08/2009 | 0.19554 | 0.00063077 | 0.19554 | 0.00063077
24/11/2009 | 0.052156 | 0.0019317 | 0.052156 | 0.0019317
18/08/2009 | 1.0243 | 0.0033509 | 1.0243 | 0.0033509
21/10/2009 | 0.4648 | 0.0081211 | 0.4648 | 0.0081211
18/05/2009 | 0.4724 | 0.0097769 | 0.4724 | 0.0097769
18/04/2009 | 0.17937 | 0.0029567 | 0.17937 | 0.0029567
18/03/2010 | 0.78152 | 0.00047307 | 0.78152 | 0.00047307
18/02/2010 | 0.17646 | 0.00047307 | 0.17646 | 0.00047307
18/01/2010 | 0.78215 | 0.0050461 | 0.78215 | 0.0050461
17/12/2009 | 0.77738 | 0.0097374 | 0.77738 | 0.0097374
17/11/2009 | 1.8644 | 0.073524 | 1.8644 | 0.073524
17/09/2009 | 1.62 | 0.016085 | 1.62 | 0.016085
17/08/2009 | 0.015178 | 0.00027596 | 0.015178 | 0.00027596
17/04/2009 | 0.18911 | 0.001301 | 0.18911 | 0.001301
17/03/2010 | 0.90105 | 0.0037452 | 0.90105 | 0.0037452
31/08/2009 | 10.1189 | 0.16317 | 10.1189 | 0.16317
19/07/2009 | 3.9483 | 0.013522 | 3.9483 | 0.013522
23/02/2010 | 1.156 | 0.0032721 | 1.156 | 0.0032721
24/07/2009 | 8.4694 | 0.045218 | 8.4694 | 0.045218
24/05/2009 | 0.073129 | 0.0050461 | 0.073129 | 0.0050461
24/04/2009 | 0.072538 | 0.0090673 | 0.072538 | 0.0090673
24/03/2010 | 0.80115 | 0.010013 | 0.80115 | 0.010013
23/12/2009 | 0.047307 | 0.00078846 | 0.047307 | 0.00078846
23/11/2009 | 0.19219 | 0.0025625 | 0.19219 | 0.0025625
23/10/2009 | 1.2598 | 0.11685 | 1.2598 | 0.11685
23/09/2009 | 1.9829 | 0.01364 | 1.9829 | 0.01364
23/08/2009 | 2.9804 | 0.017267 | 2.9804 | 0.017267
23/07/2009 | 13.2049 | 0.01983 | 13.2049 | 0.01983
23/06/2009 | 0.21714 | 0.00070961 | 0.21714 | 0.00070961
23/05/2009 | 1.8962 | 0.025309 | 1.8962 | 0.025309
21/07/2009 | 0.96468 | 0.013443 | 0.96468 | 0.013443
23/03/2010 | 1.4076 | 0.0094221 | 1.4076 | 0.0094221
21/09/2009 | 0.27545 | 0.0012221 | 0.27545 | 0.0012221
23/01/2010 | 0.32327 | 0.0012615 | 0.32327 | 0.0012615
22/12/2009 | 1.0918 | 0.011551 | 1.0918 | 0.011551
22/11/2009 | 2.5789 | 0.099188 | 2.5789 | 0.099188
22/10/2009 | 0.17543 | 0.00098557 | 0.17543 | 0.00098557
22/09/2009 | 0.89663 | 0.075219 | 0.89663 | 0.075219
22/08/2009 | 0.84085 | 0.0030356 | 0.84085 | 0.0030356
22/07/2009 | 0.49172 | 0.001025 | 0.49172 | 0.001025
22/06/2009 | 0.1336 | 0.0020106 | 0.1336 | 0.0020106
22/05/2009 | 1.317 | 0.10975 | 1.317 | 0.10975
22/03/2010 | 0.91177 | 0.0022077 | 0.91177 | 0.0022077
22/02/2010 | 0.0091067 | 0.00082788 | 0.0091067 | 0.00082788
22/01/2010 | 0.17823 | 0.00043365 | 0.17823 | 0.00043365
16/10/2009 | 0.045888 | 0.00047307 | 0.045888 | 0.00047307
23/04/2009 | 0.18923 | 0.0031538 | 0.18923 | 0.0031538

## 20092010Answer
SumOfSaidi | SumOfSafi | SumOfFixedSaidi | SumOfFixedSaifi
312.2629 | 3.4784 | 312.2629 | 3.4784