## D 1.
Post Acquisition quality data for assets acquired from Transpower for disclosure years 2007-02014
Assets acquired from Transpower were acquired on 31 March 2014 therefore there is no post acquisition outages up to 31 March 2014

## D 2.
Pre acquisition quality data for assets acquired from Transpower.
Year ended 31 March 2005
Average Customers in network for year |  |  |  |  | 14596
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request
2004-06-06 | 28 | 2072 |  | a | 0.14196 | 0.0019183 | Loss of Bulk | TPT CB 212 never cleared fault T1 tripped | HWB - OAM A & B Lines / Palmerston Substation | r
2004-06-06 | 887 | 63864 |  | a | 4.3754 | 0.06077 | Loss of Bulk | TPT CB 212 never cleared fault T1 tripped | HWB - OAM A & B Lines / Palmerston Substation | r
2004-06-06 | 1247 | 89784 |  | a | 6.1513 | 0.085434 | Loss of Bulk | TPT CB 212 never cleared fault T1 tripped | HWB - OAM A & B Lines / Palmerston Substation | r
2004-06-06 | 942 | 67824 |  | a | 4.6468 | 0.064538 | Loss of Bulk | TPT CB 212 never cleared fault T1 tripped | HWB - OAM A & B Lines / Palmerston Substation | r
2004-06-06 | 5 | 370 |  | a | 0.025349 | 0.00034256 | Loss of Bulk | TPT CB 212 never cleared fault T1 tripped | HWB - OAM A & B Lines / Palmerston Substation | r
2004-11-29 | 1247 | 28681 |  | a | 1.965 | 0.085434 | Lightning | Total loss of supply TPT | HWB - OAM A & B Lines / Palmerston Substation | r
2004-11-29 | 887 | 20401 |  | a | 1.3977 | 0.06077 | Lightning | Total loss of supply TPT | HWB - OAM A & B Lines / Palmerston Substation | r
2004-11-29 | 575 | 13225 |  | a | 0.90607 | 0.039394 | Lightning | Total loss of supply TPT | HWB - OAM A & B Lines / Palmerston Substation | r
Year ended 31 March 2006
Average Customers in network for year |  |  |  |  | 14463
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request
2005-12-21 | 3157 | 15785 |  | a | 1.0914 | 0.21828 | Loss of Bulk | Unknown | HWB - OAM A & B Lines / Palmerston Substation | r
2006-03-23 | 3151 | 15755 |  | a | 1.0893 | 0.21787 | Loss of Bulk | Unknown | HWB - OAM A & B Lines / Palmerston Substation | r
Year ended 31 March 2007
Average Customers in network for year |  |  |  |  | 14463
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request
2006-12-06 | 279 | 4743 | a |  | 0.32794 | 0.019291 | Planned | Transpower CB change at Palmerston | HWB - OAM A & B Lines / Palmerston Substation | r
2006-06-19 | 3098 | 178806 |  | a | 12.363 | 0.2142 | Loss of Bulk | Overload | HWB - OAM A & B Lines / Palmerston Substation | r
2007-01-25 | 3162 | 18972 |  | a | 1.3118 | 0.21863 | Loss of Bulk | Unknown | HWB - OAM A & B Lines / Palmerston Substation | r
2007-03-31 | 3166 | 9498 |  | a | 0.65671 | 0.2189 | Loss of Bulk | Unknown | HWB - OAM A & B Lines / Palmerston Substation | r
Year ended 31 March 2008
Average Customers in network for year |  |  |  |  | 14721
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request
Year ended 31 March 2009
Average Customers in network for year |  |  |  |  | 14754
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request
2009-01-03 | 3146 | 59774 |  | a | 4.0514 | 0.21323 | Loss of Bulk | Lightning | HWB - OAM A & B Lines / Palmerston Substation | r
Year ended 31 March 2010
Average Customers in network for year |  |  |  |  | 14767
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request
2009-04-29 | 3165 | 56970 |  | a | 3.8579 | 0.21433 | Loss of Bulk | Unknown | HWB - OAM A & B Lines / Palmerston Substation | r
2009-05-01 | 3166 | 56988 |  | a | 3.8591 | 0.2144 | Loss of Bulk | Unknown | HWB - OAM A & B Lines / Palmerston Substation | r
Year ended 31 March 2011
Average Customers in network for year |  |  |  |  | 14785
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request
Year ended 31 March 2012
Average Customers in network for year |  |  |  |  | 14813
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request
2012-03-25 | 3252 | 326904 |  | a | 22.0687 | 0.21954 | Loss of Bulk | Lightning | HWB - OAM A & B Lines / Palmerston Substation | r
Year ended 31 March 2013
Average Customers in network for year |  |  |  |  | 14818
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request
2013-01-25 | 3273 | 86510 |  | a | 5.8382 | 0.22088 | Loss of Bulk | Unknown | HWB - OAM A & B Lines / Palmerston Substation | r
Year ended 31 March 2014
Average Customers in network for year
Start Date | Customers interrupted | Customer Minutes | Planned | Unplanned | SAIDI | SAIFI | Cause | Reason | Asset | Recorded in previous s53ZD request