## (1a)_2005-09_incidents
2005-2009 datasets : Individual incident data
Outage Extra Records from Basix : 19 September 2014 |  |  | int(Interrupted) | [26 empty] | IF(Outage_Mins>0,Customers/Customer_Total,0)
NB: 2014 records have audited following the 53ZD information request.
Key | Description | Interrupted | calcByDate | Restored | Outage Status | Op Asset Local ID | Operated Asset Descript | Fault Asset | Segment | Asset Group | Service Level | Feeder | Zone Substation | Failed Component | Cause Category | Cause Group | Cause | Cause | Type Group | Outage Type | Category | Voltage | Voltage Value | Helicopter Used | Outage Mins | Customers | Customer Total | Customer Mins | SAIDI for Outage | calcSAIFI | Interrupted kVA | Load Losses | Financial Year | Month Year | Outage Month | Outage Year
6096 |  | 2004-04-01 09:01 | 2004-04-01 | 2004-04-01 13:28 | Calculated | O410E |  |  |  | Rangitoto 106-07 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 267 | 26 | 19353 | 6942 | 0.3587 | 0.0013435 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6097 |  | 2004-04-01 09:28 | 2004-04-01 | 2004-04-01 14:10 | Calculated | O410E | LF |  |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 2 | 19353 | 564 | 0.02914 | 0.00010334 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6098 |  | 2004-04-01 09:33 | 2004-04-01 | 2004-04-01 12:55 | Calculated | O410E | LF |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 202 | 1 | 19353 | 202 | 0.01044 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6099 |  | 2004-04-01 09:46 | 2004-04-01 | 2004-04-01 11:01 | Calculated | O410E | LF |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6100 |  | 2004-04-01 10:41 | 2004-04-01 | 2004-04-01 11:42 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 1 | 19353 | 61 | 0.00315 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6101 |  | 2004-04-02 09:28 | 2004-04-02 | 2004-04-02 10:00 | Calculated | O410E | LF |  |  | Mokauiti 115-05 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 32 | 1 | 19353 | 32 | 0.00165 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6102 |  | 2004-04-02 10:48 | 2004-04-02 | 2004-04-02 11:45 | Calculated | O410E | L744 | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 57 | 4 | 19353 | 228 | 0.01178 | 0.00020669 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6103 |  | 2004-04-02 11:22 | 2004-04-02 | 2004-04-02 15:21 | Calculated | O410E |  |  |  | Waihaha 426-02 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 239 | 101 | 19353 | 24139 | 1.2473 | 0.0052188 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6105 |  | 2004-04-06 07:53 | 2004-04-06 | 2004-04-06 12:17 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-06 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 264 | 1 | 19353 | 264 | 0.01364 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6106 |  | 2004-04-06 09:39 | 2004-04-06 | 2004-04-06 09:53 | Calculated | O410E | LF |  |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 2 | 19353 | 28 | 0.00145 | 0.00010334 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6107 |  | 2004-04-06 14:52 | 2004-04-06 | 2004-04-06 16:15 | Calculated | O410E | LF |  |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 83 | 1 | 19353 | 83 | 0.00429 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6109 |  | 2004-04-07 09:35 | 2004-04-07 | 2004-04-07 10:13 | Calculated | O410E | LF |  |  | Caves 101-07 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 38 | 2 | 19353 | 76 | 0.00393 | 0.00010334 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6110 |  | 2004-04-07 10:14 | 2004-04-07 | 2004-04-07 12:13 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 7 | 19353 | 833 | 0.04304 | 0.0003617 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6112 |  | 2004-04-08 09:00 | 2004-04-08 | 2004-04-08 15:01 | Calculated | O410E |  |  |  | Te Kuiti Town 105-01 | Remote Rural F | Te Kuiti Town | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 361 | 16 | 19353 | 5776 | 0.29846 | 0.00082675 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6113 |  | 2004-04-08 09:29 | 2004-04-08 | 2004-04-08 14:35 | Calculated | O410E |  |  |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 306 | 24 | 19353 | 7344 | 0.37948 | 0.0012401 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6114 |  | 2004-04-08 09:38 | 2004-04-08 | 2004-04-08 12:07 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 149 | 1 | 19353 | 149 | 0.0077 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6115 |  | 2004-04-08 12:00 | 2004-04-08 | 2004-04-08 13:17 | Calculated | O410E | C811 | Single Circuit |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 40 | 19353 | 3100 | 0.16018 | 0.0020669 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6116 |  | 2004-04-11 15:09 | 2004-04-11 | 2004-04-11 15:14 | Calculated | O410E |  | ABS |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Contacts | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 5 | 155 | 19353 | 775 | 0.04005 | 0.0080091 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6117 |  | 2004-04-12 09:45 | 2004-04-12 | 2004-04-12 12:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 149 | 1 | 19353 | 149 | 0.0077 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6118 |  | 2004-04-12 10:13 | 2004-04-12 | 2004-04-12 12:01 | Calculated | O410E | C1010 | ABS |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 108 | 498 | 19353 | 54182 | 2.7997 | 0.025732 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6120 |  | 2004-04-13 09:02 | 2004-04-13 | 2004-04-13 13:52 | Calculated | O410E | LF |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 290 | 7 | 19353 | 2030 | 0.10489 | 0.0003617 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6121 |  | 2004-04-13 12:05 | 2004-04-13 | 2004-04-13 14:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 123 | 1 | 19353 | 123 | 0.00636 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6124 |  | 2004-04-14 09:41 | 2004-04-14 | 2004-04-14 16:25 | Calculated | O410E | LF |  |  | Gravel Scoop 109-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 404 | 16 | 19353 | 6464 | 0.33401 | 0.00082675 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6123 |  | 2004-04-14 10:03 | 2004-04-14 | 2004-04-14 14:27 | Calculated | O410E |  |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 20 | 19353 | 5280 | 0.27283 | 0.0010334 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6125 |  | 2004-04-14 15:25 | 2004-04-14 | 2004-04-14 16:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 1 | 19353 | 94 | 0.00486 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6126 |  | 2004-04-15 02:22 | 2004-04-15 | 2004-04-15 03:16 | Calculated | O410E | C952 | Single Circuit |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 939 | 19353 | 50706 | 2.6201 | 0.04852 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6127 |  | 2004-04-15 09:01 | 2004-04-15 | 2004-04-15 13:53 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 49 | 19353 | 14345 | 0.74123 | 0.0025319 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6128 |  | 2004-04-15 09:03 | 2004-04-15 | 2004-04-15 15:03 | Calculated | O410E |  |  |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 24 | 19353 | 8640 | 0.44644 | 0.0012401 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6129 |  | 2004-04-15 13:40 | 2004-04-15 | 2004-04-15 15:44 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 124 | 2 | 19353 | 248 | 0.01281 | 0.00010334 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6130 |  | 2004-04-16 04:40 | 2004-04-16 | 2004-04-16 04:54 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 14 | 1 | 19353 | 14 | 0.00072 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6131 |  | 2004-04-16 09:03 | 2004-04-16 | 2004-04-16 14:33 | Calculated | O410E |  |  |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 4 | 19353 | 1320 | 0.06821 | 0.00020669 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6132 |  | 2004-04-16 09:35 | 2004-04-16 | 2004-04-16 10:16 | Calculated | O410E | LF |  |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 1 | 19353 | 41 | 0.00212 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6133 |  | 2004-04-16 11:55 | 2004-04-16 | 2004-04-16 13:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 83 | 5 | 19353 | 415 | 0.02144 | 0.00025836 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6134 |  | 2004-04-16 13:04 | 2004-04-16 | 2004-04-16 16:17 | Calculated | O410E | L1386 | Pole Mounted |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 4 | 19353 | 772 | 0.03989 | 0.00020669 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6135 |  | 2004-04-16 14:35 | 2004-04-16 | 2004-04-16 15:08 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 33 | 1 | 19353 | 33 | 0.00171 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6136 |  | 2004-04-17 14:33 | 2004-04-17 | 2004-04-17 14:40 | Calculated | O410E | C513 |  |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 409 | 19353 | 2863 | 0.14794 | 0.021134 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6137 |  | 2004-04-17 19:40 | 2004-04-17 | 2004-04-17 19:48 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1 | 19353 | 8 | 0.00041 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6138 |  | 2004-04-19 00:14 | 2004-04-19 | 2004-04-19 00:26 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 12 | 1 | 19353 | 12 | 0.00062 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6139 |  | 2004-04-19 09:07 | 2004-04-19 | 2004-04-19 14:27 | Calculated | O410E | LV |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 320 | 13 | 19353 | 4160 | 0.21495 | 0.00067173 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6140 |  | 2004-04-19 10:30 | 2004-04-19 | 2004-04-19 10:55 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 1 | 19353 | 25 | 0.00129 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6141 |  | 2004-04-20 09:38 | 2004-04-20 | 2004-04-20 11:38 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 29 | 19353 | 3487 | 0.18018 | 0.0014985 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6142 |  | 2004-04-21 08:00 | 2004-04-21 | 2004-04-21 09:40 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 100 | 14 | 19353 | 1400 | 0.07234 | 0.0007234 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6143 |  | 2004-04-21 13:04 | 2004-04-21 | 2004-04-21 15:46 | Calculated | O410E |  |  |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 162 | 7 | 19353 | 1134 | 0.0586 | 0.0003617 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6144 |  | 2004-04-22 08:00 | 2004-04-22 | 2004-04-22 09:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 101 | 1 | 19353 | 101 | 0.00522 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6145 |  | 2004-04-22 09:03 | 2004-04-22 | 2004-04-22 12:32 | Calculated | O410E |  |  |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 209 | 111 | 19353 | 23267 | 1.2022 | 0.0057355 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6146 |  | 2004-04-22 10:59 | 2004-04-22 | 2004-04-22 13:23 | Calculated | O410E |  | Single Circuit |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 1 | 19353 | 144 | 0.00744 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6147 |  | 2004-04-23 09:09 | 2004-04-23 | 2004-04-23 14:26 | Calculated | O410E | LV |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 317 | 9 | 19353 | 2853 | 0.14742 | 0.00046504 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6148 |  | 2004-04-23 10:15 | 2004-04-23 | 2004-04-23 10:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 35 | 9 | 19353 | 315 | 0.01628 | 0.00046504 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6149 |  | 2004-04-23 12:39 | 2004-04-23 | 2004-04-23 14:26 | Calculated | O410E |  |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 107 | 6 | 19353 | 642 | 0.03317 | 0.00031003 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6150 |  | 2004-04-24 06:44 | 2004-04-24 | 2004-04-24 08:14 | Calculated | O410E | C732 | ABS |  |  | Remote Rural F | Whakamaru 33 | Direct from Whakamaru Supply | Switchgear : Other | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 90 | 1840 | 19353 | 167286 | 8.6439 | 0.095076 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6151 |  | 2004-04-25 07:18 | 2004-04-25 | 2004-04-25 07:22 | Calculated | O410E | C732 |  |  |  | Remote Rural F | Whakamaru 33 | Direct from Whakamaru Supply |  | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 1840 | 19353 | 7360 | 0.3803 | 0.095076 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6152 |  | 2004-04-26 07:10 | 2004-04-26 | 2004-04-26 10:16 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 186 | 93 | 19353 | 17377 | 0.8979 | 0.0048055 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6154 |  | 2004-04-26 23:46 | 2004-04-26 | 2004-04-27 04:21 | Calculated | O410E | C114 | Single Circuit |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Conductor - Bare ACSR | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 275 | 239 | 19353 | 65812 | 3.4006 | 0.01235 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6155 |  | 2004-04-27 10:08 | 2004-04-27 | 2004-04-27 12:00 | Calculated | O410E |  |  |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 7 | 19353 | 788 | 0.04072 | 0.0003617 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6156 |  | 2004-04-27 13:44 | 2004-04-27 | 2004-04-27 14:35 | Calculated | O410E | LF |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 3 | 19353 | 153 | 0.00791 | 0.00015501 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6157 |  | 2004-04-28 09:38 | 2004-04-28 | 2004-04-28 10:49 | Calculated | O410E | LF |  |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 3 | 19353 | 213 | 0.01101 | 0.00015501 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6158 |  | 2004-04-28 20:46 | 2004-04-28 | 2004-04-28 20:54 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1 | 19353 | 8 | 0.00041 | 5.1672e-05 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6159 |  | 2004-04-29 10:05 | 2004-04-29 | 2004-04-29 17:02 | Calculated | O410E | LF | Pole Mounted |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 417 | 5 | 19353 | 2085 | 0.10774 | 0.00025836 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6160 |  | 2004-04-29 11:44 | 2004-04-29 | 2004-04-29 13:30 | Calculated | O410E | C536 | Single Circuit |  |  | Remote Rural F | Waihaha | Kuratau Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 6 | 19353 | 636 | 0.03286 | 0.00031003 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6161 |  | 2004-04-29 11:53 | 2004-04-29 | 2004-04-29 13:05 | Calculated | O410E | LF |  |  | Maihiihi 111-09 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 3 | 19353 | 216 | 0.01116 | 0.00015501 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6162 |  | 2004-04-29 13:02 | 2004-04-29 | 2004-04-29 14:33 | Calculated | O410E |  |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 3 | 19353 | 273 | 0.01411 | 0.00015501 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6163 |  | 2004-04-30 08:09 | 2004-04-30 | 2004-04-30 11:29 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 200 | 119 | 19353 | 23815 | 1.2306 | 0.0061489 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6164 |  | 2004-04-30 10:33 | 2004-04-30 | 2004-04-30 11:44 | Calculated | O410E |  |  |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 14 | 19353 | 994 | 0.05136 | 0.0007234 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6165 |  | 2004-04-30 13:02 | 2004-04-30 | 2004-04-30 15:01 | Calculated | O410E |  |  |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 4 | 19353 | 476 | 0.0246 | 0.00020669 | 0 | 0 | 2004/2005 | April-2004 | 4 | 2004
6166 |  | 2004-05-01 06:53 | 2004-05-01 | 2004-05-01 08:23 | Calculated | O410E | C112 | Single Circuit |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 206 | 19353 | 18550 | 0.95851 | 0.010644 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6167 |  | 2004-05-03 09:58 | 2004-05-03 | 2004-05-03 11:09 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 25 | 19353 | 1795 | 0.09275 | 0.0012918 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6168 |  | 2004-05-03 10:46 | 2004-05-03 | 2004-05-03 13:05 | Calculated | O410E |  |  |  |  | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 6 | 19353 | 834 | 0.04309 | 0.00031003 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6169 |  | 2004-05-04 06:21 | 2004-05-04 | 2004-05-04 07:05 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 44 | 1 | 19353 | 44 | 0.00227 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6170 |  | 2004-05-04 07:11 | 2004-05-04 | 2004-05-04 13:18 | Calculated | O410E | C1612 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 367 | 27 | 19353 | 9909 | 0.51201 | 0.0013951 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6173 |  | 2004-05-04 11:05 | 2004-05-04 | 2004-05-04 12:54 | Calculated | O410E | L1617 | Single Circuit |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 2 | 19353 | 219 | 0.01132 | 0.00010334 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6172 |  | 2004-05-04 13:13 | 2004-05-04 | 2004-05-04 14:02 | Calculated | O410E | LF |  |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 1 | 19353 | 49 | 0.00253 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6174 |  | 2004-05-04 15:35 | 2004-05-04 | 2004-05-04 16:56 | Calculated | O410E | LF | Outdoor - Ground Mounted |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation | Switchgear : Fuse Carriers | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 81 | 20 | 19353 | 1620 | 0.08371 | 0.0010334 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6175 |  | 2004-05-05 09:05 | 2004-05-05 | 2004-05-05 13:32 | Calculated | O410E | LV |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 267 | 29 | 19353 | 7743 | 0.40009 | 0.0014985 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6176 |  | 2004-05-05 10:09 | 2004-05-05 | 2004-05-05 10:36 | Calculated | O410E | LF |  |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 2 | 19353 | 54 | 0.00279 | 0.00010334 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6177 |  | 2004-05-05 11:48 | 2004-05-05 | 2004-05-05 14:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 190 | 1 | 19353 | 190 | 0.00982 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6178 |  | 2004-05-06 08:41 | 2004-05-06 | 2004-05-06 09:00 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 13 | 19353 | 247 | 0.01276 | 0.00067173 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6179 |  | 2004-05-06 14:32 | 2004-05-06 | 2004-05-06 14:53 | Calculated | O410E |  | Single Circuit |  | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 158 | 19353 | 3318 | 0.17145 | 0.0081641 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6180 |  | 2004-05-07 10:19 | 2004-05-07 | 2004-05-07 11:49 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 29 | 19353 | 2627 | 0.13574 | 0.0014985 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6182 |  | 2004-05-07 12:29 | 2004-05-07 | 2004-05-07 14:01 | Calculated | O410E | LF |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 2 | 19353 | 184 | 0.00951 | 0.00010334 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6183 |  | 2004-05-08 12:22 | 2004-05-08 | 2004-05-08 12:23 | Calculated | O410E | C222 | Outdoor - Ground Mounted |  |  | Remote Rural F | Te Waireka Rd 33 | Direct from Hangatiki Supply | Transformers : Other | Asset Related | Other |  | Condensation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | May-2004 | 5 | 2004
6184 |  | 2004-05-08 17:50 | 2004-05-08 | 2004-05-08 18:54 | Calculated | O410E | L1638 | Single Circuit |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 3 | 19353 | 192 | 0.00992 | 0.00015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6185 |  | 2004-05-10 10:28 | 2004-05-10 | 2004-05-10 12:01 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 93 | 29 | 19353 | 2713 | 0.14018 | 0.0014985 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6186 |  | 2004-05-11 09:00 | 2004-05-11 | 2004-05-11 13:02 | Calculated | O410E |  |  |  | Aria 114-03 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 242 | 39 | 19353 | 9438 | 0.48768 | 0.0020152 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6187 |  | 2004-05-11 09:13 | 2004-05-11 | 2004-05-11 11:07 | Calculated | O410E | LF |  |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 114 | 1 | 19353 | 114 | 0.00589 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6188 |  | 2004-05-11 09:14 | 2004-05-11 | 2004-05-11 11:07 | Calculated | O410E |  |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 3 | 19353 | 339 | 0.01752 | 0.00015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6189 |  | 2004-05-11 10:03 | 2004-05-11 | 2004-05-11 13:58 | Calculated | O410E | LF |  |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 235 | 2 | 19353 | 470 | 0.02429 | 0.00010334 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6190 |  | 2004-05-11 10:33 | 2004-05-11 | 2004-05-11 13:25 | Calculated | O410E |  |  |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 172 | 4 | 19353 | 688 | 0.03555 | 0.00020669 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6191 |  | 2004-05-11 10:37 | 2004-05-11 | 2004-05-11 11:51 | Calculated | O410E | L1638 | Single Circuit |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 3 | 19353 | 222 | 0.01147 | 0.00015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6192 |  | 2004-05-11 11:34 | 2004-05-11 | 2004-05-11 14:25 | Calculated | O410E | LF |  |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 171 | 1 | 19353 | 171 | 0.00884 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6193 |  | 2004-05-11 12:17 | 2004-05-11 | 2004-05-11 13:56 | Calculated | O410E |  |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 99 | 1 | 19353 | 99 | 0.00512 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6194 |  | 2004-05-11 22:23 | 2004-05-11 | 2004-05-11 22:33 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1 | 19353 | 10 | 0.00052 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6195 |  | 2004-05-12 09:28 | 2004-05-12 | 2004-05-12 13:53 | Calculated | O410E |  |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 265 | 3 | 19353 | 795 | 0.04108 | 0.00015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6197 |  | 2004-05-12 19:03 | 2004-05-12 | 2004-05-13 11:57 | Calculated | O410E | LF |  |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1014 | 4 | 19353 | 4056 | 0.20958 | 0.00020669 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6198 |  | 2004-05-13 07:00 | 2004-05-13 | 2004-05-13 09:19 | Calculated | O410E | L497 | Drop-Out Fuses |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 139 | 24 | 19353 | 3336 | 0.17238 | 0.0012401 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6199 |  | 2004-05-13 09:31 | 2004-05-13 | 2004-05-13 11:08 | Calculated | O410E |  |  |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 97 | 30 | 19353 | 2910 | 0.15036 | 0.0015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6200 |  | 2004-05-13 09:43 | 2004-05-13 | 2004-05-13 15:02 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 319 | 1 | 19353 | 319 | 0.01648 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6201 |  | 2004-05-13 10:17 | 2004-05-13 | 2004-05-13 12:46 | Calculated | O410E | LF |  |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 3 | 19353 | 447 | 0.0231 | 0.00015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6202 |  | 2004-05-13 10:45 | 2004-05-13 | 2004-05-13 11:19 | Calculated | O410E | LF | Drop-Out Fuses |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 34 | 7 | 19353 | 238 | 0.0123 | 0.0003617 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6203 |  | 2004-05-13 16:37 | 2004-05-13 | 2004-05-13 17:25 | Calculated | O410E | S678 | Single Circuit |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 84 | 19353 | 4032 | 0.20834 | 0.0043404 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6204 |  | 2004-05-14 07:19 | 2004-05-14 | 2004-05-14 08:22 | Calculated | O410E | L1648 | Single Circuit |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 40 | 19353 | 2520 | 0.13021 | 0.0020669 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6205 |  | 2004-05-14 10:05 | 2004-05-14 | 2004-05-14 10:19 | Calculated | O410E | LF |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 3 | 19353 | 42 | 0.00217 | 0.00015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6206 |  | 2004-05-14 10:24 | 2004-05-14 | 2004-05-14 11:17 | Calculated | O410E | LF |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 53 | 3 | 19353 | 159 | 0.00822 | 0.00015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6207 |  | 2004-05-14 10:31 | 2004-05-14 | 2004-05-14 14:14 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 223 | 21 | 19353 | 4683 | 0.24198 | 0.0010851 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6208 |  | 2004-05-14 10:44 | 2004-05-14 | 2004-05-14 11:39 | Calculated | O410E | LF |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 3 | 19353 | 165 | 0.00853 | 0.00015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6209 |  | 2004-05-14 12:23 | 2004-05-14 | 2004-05-14 13:17 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 84 | 19353 | 4586 | 0.23697 | 0.0043404 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6210 |  | 2004-05-14 20:30 | 2004-05-14 | 2004-05-14 20:38 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1 | 19353 | 8 | 0.00041 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6211 |  | 2004-05-16 19:15 | 2004-05-16 | 2004-05-16 20:29 | Calculated | O410E | C686 | Single Circuit |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 248 | 19353 | 18546 | 0.9583 | 0.012815 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6212 |  | 2004-05-17 09:32 | 2004-05-17 | 2004-05-17 09:51 | Calculated | O410E |  |  |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 19 | 21 | 19353 | 416 | 0.0215 | 0.0010851 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6213 |  | 2004-05-17 12:10 | 2004-05-17 | 2004-05-17 13:16 | Calculated | O410E | L1321 | Drop-Out Fuses |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 66 | 27 | 19353 | 1782 | 0.09208 | 0.0013951 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6214 |  | 2004-05-17 14:31 | 2004-05-17 | 2004-05-17 14:51 | Calculated | O410E |  |  |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 20 | 13 | 19353 | 260 | 0.01343 | 0.00067173 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6217 |  | 2004-05-18 10:44 | 2004-05-18 | 2004-05-18 14:12 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 208 | 15 | 19353 | 3120 | 0.16122 | 0.00077507 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6216 |  | 2004-05-18 11:33 | 2004-05-18 | 2004-05-18 13:14 | Calculated | O410E |  |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 101 | 6 | 19353 | 606 | 0.03131 | 0.00031003 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6219 |  | 2004-05-18 13:06 | 2004-05-18 | 2004-05-18 13:33 | Calculated | O410E | LF |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 27 | 5 | 19353 | 135 | 0.00698 | 0.00025836 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6221 |  | 2004-05-19 10:03 | 2004-05-19 | 2004-05-19 10:49 | Calculated | O410E |  |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 12 | 19353 | 552 | 0.02852 | 0.00062006 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6222 |  | 2004-05-19 14:02 | 2004-05-19 | 2004-05-19 15:44 | Calculated | O410E | LF |  |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 2 | 19353 | 204 | 0.01054 | 0.00010334 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6223 |  | 2004-05-19 18:35 | 2004-05-19 | 2004-05-19 19:13 | Calculated | O410E | L551 | Drop-Out Fuses |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 38 | 5 | 19353 | 190 | 0.00982 | 0.00025836 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6224 |  | 2004-05-19 22:01 | 2004-05-19 | 2004-05-19 22:04 | Calculated | O410E | C242 | Single Circuit |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply | OH Lines : Conductor - Bare ACSR | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 239 | 19353 | 717 | 0.03705 | 0.01235 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6225 |  | 2004-05-20 07:55 | 2004-05-20 | 2004-05-20 08:34 | Calculated | O410E | F855 |  |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 24 | 19353 | 936 | 0.04836 | 0.0012401 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6226 |  | 2004-05-20 09:17 | 2004-05-20 | 2004-05-20 10:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 46 | 3 | 19353 | 138 | 0.00713 | 0.00015501 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6227 |  | 2004-05-21 10:00 | 2004-05-21 | 2004-05-21 14:51 | Calculated | O410E | LF |  |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 291 | 4 | 19353 | 1164 | 0.06015 | 0.00020669 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6229 |  | 2004-05-21 15:03 | 2004-05-21 | 2004-05-21 16:51 | Calculated | O410E | C560 | Single Circuit |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 15 | 19353 | 1620 | 0.08371 | 0.00077507 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6230 |  | 2004-05-22 04:52 | 2004-05-22 | 2004-05-22 08:18 | Calculated | O410E | C113 | Single Circuit |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 206 | 16 | 19353 | 3296 | 0.17031 | 0.00082675 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6231 |  | 2004-05-23 00:48 | 2004-05-23 | 2004-05-23 00:49 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | May-2004 | 5 | 2004
6232 |  | 2004-05-23 10:30 | 2004-05-23 | 2004-05-23 12:40 | Calculated | O410E | LF | Single Circuit |  | Manunui 408-01 | Remote Rural F | Manunui | Manunui Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 27 | 19353 | 3510 | 0.18137 | 0.0013951 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6233 |  | 2004-05-24 04:50 | 2004-05-24 | 2004-05-24 07:46 | Calculated | O410E | C686 | Single Circuit |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 248 | 19353 | 43796 | 2.263 | 0.012815 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6235 |  | 2004-05-24 10:07 | 2004-05-24 | 2004-05-24 14:00 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 233 | 16 | 19353 | 3728 | 0.19263 | 0.00082675 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6237 |  | 2004-05-24 11:55 | 2004-05-24 | 2004-05-24 13:21 | Calculated | O410E | L1526 | Single Circuit |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 62 | 19353 | 5332 | 0.27551 | 0.0032036 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6238 |  | 2004-05-25 09:42 | 2004-05-25 | 2004-05-25 13:20 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 218 | 1 | 19353 | 218 | 0.01126 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6240 |  | 2004-05-25 10:22 | 2004-05-25 | 2004-05-25 10:31 | Calculated | O410E | LF |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 1 | 19353 | 9 | 0.00047 | 5.1672e-05 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6239 |  | 2004-05-25 10:23 | 2004-05-25 | 2004-05-25 10:45 | Calculated | O410E |  |  |  |  | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 22 | 96 | 19353 | 2128 | 0.10996 | 0.0049605 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6241 |  | 2004-05-25 13:01 | 2004-05-25 | 2004-05-25 15:11 | Calculated | O410E | LF |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 6 | 19353 | 780 | 0.0403 | 0.00031003 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6242 |  | 2004-05-26 06:03 | 2004-05-26 | 2004-05-26 08:05 | Calculated | O410E | C1530 |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 6 | 19353 | 732 | 0.03782 | 0.00031003 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6243 |  | 2004-05-26 09:05 | 2004-05-26 | 2004-05-26 15:11 | Calculated | O410E |  |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 366 | 11 | 19353 | 4026 | 0.20803 | 0.00056839 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6244 |  | 2004-05-26 11:00 | 2004-05-26 | 2004-05-26 13:29 | Calculated | O410E |  |  |  | Otorohanga 112-05 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 6 | 19353 | 894 | 0.04619 | 0.00031003 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6245 |  | 2004-05-27 08:30 | 2004-05-27 | 2004-05-27 15:35 | Calculated | O410E | LF |  |  | Manunui 408-01 | Remote Rural F | Manunui | Manunui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 425 | 27 | 19353 | 11475 | 0.59293 | 0.0013951 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6248 |  | 2004-05-28 08:30 | 2004-05-28 | 2004-05-28 15:21 | Calculated | O410E |  |  |  | Manunui 408-01 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 411 | 50 | 19353 | 20550 | 1.0618 | 0.0025836 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6249 |  | 2004-05-28 09:30 | 2004-05-28 | 2004-05-28 11:31 | Calculated | O410E |  |  |  | Caves 101-05 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 40 | 19353 | 4840 | 0.25009 | 0.0020669 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6252 |  | 2004-05-30 09:35 | 2004-05-30 | 2004-05-30 15:53 | Calculated | O410E | C560 | Single Circuit |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 378 | 15 | 19353 | 5670 | 0.29298 | 0.00077507 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6253 |  | 2004-05-31 08:03 | 2004-05-31 | 2004-05-31 10:53 | Calculated | O410E | C467 | Single Circuit |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 50 | 19353 | 8500 | 0.43921 | 0.0025836 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6254 |  | 2004-05-31 09:01 | 2004-05-31 | 2004-05-31 12:24 | Calculated | O410E |  |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 203 | 91 | 19353 | 18473 | 0.95453 | 0.0047021 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6255 |  | 2004-05-31 13:25 | 2004-05-31 | 2004-05-31 13:58 | Calculated | O410E | C446 | Single Circuit |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 103 | 19353 | 3399 | 0.17563 | 0.0053222 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6257 |  | 2004-05-31 14:58 | 2004-05-31 | 2004-05-31 16:45 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 107 | 4 | 19353 | 428 | 0.02212 | 0.00020669 | 0 | 0 | 2004/2005 | May-2004 | 5 | 2004
6258 |  | 2004-06-01 01:23 | 2004-06-01 | 2004-06-01 01:24 | Calculated | O410E | C262 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | June-2004 | 6 | 2004
6259 |  | 2004-06-01 09:34 | 2004-06-01 | 2004-06-01 12:21 | Calculated | O410E |  |  |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 167 | 28 | 19353 | 4676 | 0.24162 | 0.0014468 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6261 |  | 2004-06-01 11:01 | 2004-06-01 | 2004-06-01 13:15 | Calculated | O410E |  |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 134 | 51 | 19353 | 6834 | 0.35312 | 0.0026353 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6262 |  | 2004-06-01 12:21 | 2004-06-01 | 2004-06-01 13:48 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 87 | 4 | 19353 | 348 | 0.01798 | 0.00020669 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6263 |  | 2004-06-01 16:02 | 2004-06-01 | 2004-06-01 17:50 | Calculated | O410E | LF | Pole Mounted |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 1 | 19353 | 108 | 0.00558 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6264 |  | 2004-06-02 07:35 | 2004-06-02 | 2004-06-02 08:34 | Calculated | O410E | LF |  |  | Pureora 119-03 RETIRED | Remote Rural F | Pureora | Maraetai Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 1 | 19353 | 59 | 0.00305 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6265 |  | 2004-06-02 07:57 | 2004-06-02 | 2004-06-02 11:00 | Calculated | O410E | L689 | Drop-Out Fuses |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 183 | 19 | 19353 | 3477 | 0.17966 | 0.00098176 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6268 |  | 2004-06-02 14:04 | 2004-06-02 | 2004-06-02 14:47 | Calculated | O410E |  |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 46 | 19353 | 1978 | 0.10221 | 0.0023769 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6269 |  | 2004-06-02 18:30 | 2004-06-02 | 2004-06-02 19:44 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-03 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 74 | 1 | 19353 | 74 | 0.00382 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6270 |  | 2004-06-02 18:46 | 2004-06-02 | 2004-06-02 20:21 | Calculated | O410E | C113 | Single Circuit |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 84 | 19353 | 8043 | 0.41559 | 0.0043404 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6271 |  | 2004-06-03 05:48 | 2004-06-03 | 2004-06-03 07:45 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 67 | 19353 | 7839 | 0.40505 | 0.003462 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6275 |  | 2004-06-03 09:00 | 2004-06-03 | 2004-06-03 15:17 | Calculated | O410E | LF | Pole Mounted |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 377 | 1 | 19353 | 377 | 0.01948 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6272 |  | 2004-06-03 09:09 | 2004-06-03 | 2004-06-03 11:04 | Calculated | O410E |  |  |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 24 | 19353 | 2776 | 0.14344 | 0.0012401 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6273 |  | 2004-06-03 10:15 | 2004-06-03 | 2004-06-03 14:33 | Calculated | O410E |  |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 63 | 19353 | 16254 | 0.83987 | 0.0032553 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6274 |  | 2004-06-03 12:11 | 2004-06-03 | 2004-06-03 13:06 | Calculated | O410E | L265 | Single Circuit |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 9 | 19353 | 495 | 0.02558 | 0.00046504 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6278 |  | 2004-06-03 20:53 | 2004-06-03 | 2004-06-03 23:24 | Calculated | O410E | C113 | Single Circuit |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 51 | 19353 | 6921 | 0.35762 | 0.0026353 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6279 |  | 2004-06-04 00:53 | 2004-06-04 | 2004-06-04 00:54 | Calculated | O410E | C1102 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 1409 | 19353 | 2818 | 0.14561 | 0.072805 | 1 | 1 | 2004/2005 | June-2004 | 6 | 2004
6280 |  | 2004-06-04 13:28 | 2004-06-04 | 2004-06-04 14:13 | Calculated | O410E | L688 | Single Circuit |  | Kuratau 406-01 | Remote Rural F | Kuratau | Kuratau Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 1110 | 19353 | 50190 | 2.5934 | 0.057355 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6281 |  | 2004-06-04 13:37 | 2004-06-04 | 2004-06-04 15:11 | Calculated | O410E | C117 |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 97 | 19353 | 9150 | 0.47279 | 0.0050121 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6282 |  | 2004-06-04 14:41 | 2004-06-04 | 2004-06-04 15:21 | Calculated | O410E | C609 | Single Circuit |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 87 | 19353 | 3480 | 0.17982 | 0.0044954 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6283 |  | 2004-06-04 21:40 | 2004-06-04 | 2004-06-04 21:50 | Calculated | O410E | C127 | Single Circuit |  | Caves 101-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 338 | 19353 | 3380 | 0.17465 | 0.017465 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6284 |  | 2004-06-05 14:03 | 2004-06-05 | 2004-06-05 15:00 | Calculated | O410E | C547 | Single Circuit |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 182 | 19353 | 10449 | 0.53992 | 0.0094042 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6285 |  | 2004-06-06 04:25 | 2004-06-06 | 2004-06-06 04:38 | Calculated | O410E | C127 | Single Circuit |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 338 | 19353 | 4394 | 0.22704 | 0.017465 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6286 |  | 2004-06-06 08:13 | 2004-06-06 | 2004-06-06 08:29 | Calculated | O410E | C127 | Single Circuit |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 338 | 19353 | 5509 | 0.28466 | 0.017465 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6287 |  | 2004-06-06 10:04 | 2004-06-06 | 2004-06-06 12:06 | Calculated | O410E | C187 | Main Protection |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation | Miscellaneous : Overcurrent Relay - Inst | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 122 | 958 | 19353 | 117690 | 6.0812 | 0.049501 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6288 |  | 2004-06-06 10:06 | 2004-06-06 | 2004-06-06 11:40 | Calculated | O410E | S1619 | Single Circuit |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 381 | 19353 | 36099 | 1.8653 | 0.019687 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6289 |  | 2004-06-06 10:14 | 2004-06-06 | 2004-06-06 11:33 | Calculated | O410E | C107 | Single Circuit |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 327 | 19353 | 26121 | 1.3497 | 0.016897 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6290 |  | 2004-06-06 10:43 | 2004-06-06 | 2004-06-06 11:58 | Calculated | O410E | C534 | Single Circuit |  |  | Remote Rural F | Waihaha | Kuratau Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 12 | 19353 | 900 | 0.0465 | 0.00062006 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6291 |  | 2004-06-06 11:49 | 2004-06-06 | 2004-06-06 14:51 | Calculated | O410E | LF |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 182 | 26 | 19353 | 4741 | 0.24497 | 0.0013435 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6292 |  | 2004-06-06 12:05 | 2004-06-06 | 2004-06-06 12:58 | Calculated | O410E | L1.27 | Single Circuit |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | OH Lines : Jumper - Bare Copper | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 6 | 19353 | 318 | 0.01643 | 0.00031003 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6294 |  | 2004-06-08 07:13 | 2004-06-08 | 2004-06-08 08:39 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 86 | 119 | 19353 | 10235 | 0.52886 | 0.0061489 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6295 |  | 2004-06-08 08:13 | 2004-06-08 | 2004-06-08 10:05 | Calculated | O410E | LF |  |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 1 | 19353 | 112 | 0.00579 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6297 |  | 2004-06-08 12:45 | 2004-06-08 | 2004-06-08 13:01 | Calculated | O410E | LV |  |  | Piopio 116-02 | Remote Rural F | Piopio | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 44 | 19353 | 704 | 0.03638 | 0.0022735 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6299 |  | 2004-06-09 09:35 | 2004-06-09 | 2004-06-09 11:21 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 106 | 29 | 19353 | 3094 | 0.15987 | 0.0014985 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6301 |  | 2004-06-10 10:10 | 2004-06-10 | 2004-06-10 10:26 | Calculated | O410E |  |  |  |  | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 96 | 19353 | 1617 | 0.08355 | 0.0049605 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6302 |  | 2004-06-10 10:34 | 2004-06-10 | 2004-06-10 14:53 | Calculated | O410E |  |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 259 | 8 | 19353 | 2072 | 0.10706 | 0.00041337 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6305 |  | 2004-06-11 10:34 | 2004-06-11 | 2004-06-11 11:57 | Calculated | O410E |  |  |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 83 | 14 | 19353 | 1165 | 0.0602 | 0.0007234 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6307 |  | 2004-06-12 09:28 | 2004-06-12 | 2004-06-12 12:14 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 166 | 4 | 19353 | 664 | 0.03431 | 0.00020669 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6308 |  | 2004-06-12 09:51 | 2004-06-12 | 2004-06-12 11:34 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 103 | 2 | 19353 | 206 | 0.01064 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6309 |  | 2004-06-12 10:06 | 2004-06-12 | 2004-06-12 11:33 | Calculated | O410E | C1530 | Single Circuit |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 6 | 19353 | 522 | 0.02697 | 0.00031003 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6310 |  | 2004-06-14 10:05 | 2004-06-14 | 2004-06-14 10:21 | Calculated | O410E | LF |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 76 | 19353 | 1216 | 0.06283 | 0.003927 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6311 |  | 2004-06-14 12:33 | 2004-06-14 | 2004-06-14 13:07 | Calculated | O410E |  |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 34 | 9 | 19353 | 306 | 0.01581 | 0.00046504 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6312 |  | 2004-06-15 09:43 | 2004-06-15 | 2004-06-15 10:22 | Calculated | O410E |  |  |  | Tokaanu 420-01 | Remote Rural F | Tokaanu | Tokaanu Village Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 39 | 70 | 19353 | 2745 | 0.14184 | 0.003617 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6315 |  | 2004-06-15 15:33 | 2004-06-15 | 2004-06-15 15:39 | Calculated | O410E | C792 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 6 | 1567 | 19353 | 9402 | 0.48582 | 0.080969 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6317 |  | 2004-06-16 13:04 | 2004-06-16 | 2004-06-16 14:06 | Calculated | O410E | C5004 | Single Circuit |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Insulator - Kidney | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 416 | 19353 | 26041 | 1.3456 | 0.021495 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6319 |  | 2004-06-16 20:25 | 2004-06-16 | 2004-06-16 23:35 | Calculated | O410E | C378 | Single Circuit |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 36 | 19353 | 6871 | 0.35504 | 0.0018602 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6320 |  | 2004-06-17 14:32 | 2004-06-17 | 2004-06-17 15:02 | Calculated | O410E | LF |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 30 | 2 | 19353 | 60 | 0.0031 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6321 |  | 2004-06-17 21:14 | 2004-06-17 | 2004-06-17 21:23 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 1 | 19353 | 9 | 0.00047 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6322 |  | 2004-06-18 21:51 | 2004-06-18 | 2004-06-18 23:54 | Calculated | O410E | C797 |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 239 | 19353 | 29397 | 1.519 | 0.01235 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6324 |  | 2004-06-19 04:43 | 2004-06-19 | 2004-06-19 05:20 | Calculated | O410E | S518 | Single Circuit |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 238 | 19353 | 8806 | 0.45502 | 0.012298 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6323 |  | 2004-06-20 03:02 | 2004-06-20 | 2004-06-20 03:16 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 14 | 1 | 19353 | 14 | 0.00072 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6325 |  | 2004-06-20 13:58 | 2004-06-20 | 2004-06-20 14:09 | Calculated | O410E | C1354 | Single Circuit |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 42 | 19353 | 462 | 0.02387 | 0.0021702 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6326 |  | 2004-06-21 07:02 | 2004-06-21 | 2004-06-21 10:18 | Calculated | O410E | LF |  |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 1 | 19353 | 196 | 0.01013 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6327 |  | 2004-06-21 08:05 | 2004-06-21 | 2004-06-21 09:25 | Calculated | O410E | LF | Pole Mounted |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 1 | 19353 | 80 | 0.00413 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6328 |  | 2004-06-21 09:04 | 2004-06-21 | 2004-06-21 09:47 | Calculated | O410E | LF |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 2 | 19353 | 86 | 0.00444 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6329 |  | 2004-06-21 10:10 | 2004-06-21 | 2004-06-21 12:23 | Calculated | O410E | L677 | Drop-Out Fuses |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 133 | 8 | 19353 | 1064 | 0.05498 | 0.00041337 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6330 |  | 2004-06-22 02:13 | 2004-06-22 | 2004-06-22 02:27 | Calculated | O410E | C6007 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 14 | 83 | 19353 | 1162 | 0.06004 | 0.0042887 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6331 |  | 2004-06-22 06:47 | 2004-06-22 | 2004-06-22 06:59 | Calculated | O410E | C252 | Single Circuit |  |  | Remote Rural F | Gadsby Rd 33 | Direct from Hangatiki Supply | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 12 | 2234 | 19353 | 27068 | 1.3986 | 0.11543 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6332 |  | 2004-06-22 06:47 | 2004-06-22 | 2004-06-22 07:52 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 65 | 5 | 19353 | 325 | 0.01679 | 0.00025836 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6333 |  | 2004-06-22 07:25 | 2004-06-22 | 2004-06-22 09:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 145 | 2 | 19353 | 291 | 0.01504 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6334 |  | 2004-06-22 07:25 | 2004-06-22 | 2004-06-22 08:28 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 2 | 19353 | 126 | 0.00651 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6335 |  | 2004-06-22 08:09 | 2004-06-22 | 2004-06-22 08:55 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 46 | 6 | 19353 | 277 | 0.01431 | 0.00031003 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6336 |  | 2004-06-22 08:09 | 2004-06-22 | 2004-06-22 09:41 | Calculated | O410E | C110 |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 82 | 19353 | 7544 | 0.38981 | 0.0042371 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6338 |  | 2004-06-22 12:00 | 2004-06-22 | 2004-06-22 12:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 47 | 4 | 19353 | 188 | 0.00971 | 0.00020669 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6339 |  | 2004-06-22 14:02 | 2004-06-22 | 2004-06-22 18:01 | Calculated | O410E | C1107 | Single Circuit |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 65 | 19353 | 15535 | 0.80272 | 0.0033587 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6340 |  | 2004-06-22 14:27 | 2004-06-22 | 2004-06-22 18:07 | Calculated | O410E | L1297 | Drop-Out Fuses |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 220 | 46 | 19353 | 10120 | 0.52292 | 0.0023769 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6341 |  | 2004-06-22 15:35 | 2004-06-22 | 2004-06-22 17:14 | Calculated | O410E | L260 | Drop-Out Fuses |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 15 | 19353 | 1495 | 0.07725 | 0.00077507 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6342 |  | 2004-06-22 15:38 | 2004-06-22 | 2004-06-22 17:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 100 | 2 | 19353 | 200 | 0.01033 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6343 |  | 2004-06-22 15:58 | 2004-06-22 | 2004-06-22 17:22 | Calculated | O410E | C112 | Single Circuit |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 206 | 19353 | 17424 | 0.90033 | 0.010644 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6344 |  | 2004-06-22 17:08 | 2004-06-22 | 2004-06-22 17:09 | Calculated | O410E | C797 |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 61 | 240 | 19353 | 14160 | 0.73167 | 0.012401 | 1 | 1 | 2004/2005 | June-2004 | 6 | 2004
6345 |  | 2004-06-22 17:12 | 2004-06-22 | 2004-06-22 17:13 | Calculated | O410E | C262 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | June-2004 | 6 | 2004
6346 |  | 2004-06-22 17:18 | 2004-06-22 | 2004-06-22 18:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 101 | 2 | 19353 | 202 | 0.01044 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6347 |  | 2004-06-22 17:18 | 2004-06-22 | 2004-06-22 19:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 141 | 3 | 19353 | 425 | 0.02196 | 0.00015501 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6348 |  | 2004-06-22 17:18 | 2004-06-22 | 2004-06-22 19:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 143 | 1 | 19353 | 143 | 0.00739 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6349 |  | 2004-06-22 17:18 | 2004-06-22 | 2004-06-22 20:01 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 163 | 2 | 19353 | 326 | 0.01684 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6350 |  | 2004-06-22 17:18 | 2004-06-22 | 2004-06-22 20:02 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 164 | 2 | 19353 | 328 | 0.01695 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6351 |  | 2004-06-22 17:18 | 2004-06-22 | 2004-06-22 20:25 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 187 | 2 | 19353 | 374 | 0.01933 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6352 |  | 2004-06-22 21:42 | 2004-06-22 | 2004-06-22 21:44 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 | Outdoor Circuit Breaker - Ground Mounted | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 37 | 327 | 19353 | 12099 | 0.62517 | 0.016897 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
25028 | Faulty OCB 788 - Hangatiki | 2004-06-22 21:42 | 2004-06-22 | 2004-06-22 21:56 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 452 | 19353 | 911 | 0.04707 | 0.023356 | 5747.0672 | 11589 | 2004/2005 | June-2004 | 6 | 2004
25032 | Faulty OCB 788 - Hangatiki | 2004-06-23 03:44 | 2004-06-23 | 2004-06-23 03:47 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 19353 |  | 0 | 0 |  |  | 2004/2005 | June-2004 | 6 | 2004
25033 | Faulty OCB 788 - Hangatiki | 2004-06-23 03:44 | 2004-06-23 | 2004-06-23 05:36 | Calculated | 142 | 142 - (RC) Air Break Switch 142 |  | No Segment | 202-01 Piripiri | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 894 | 19353 | 11838 | 0.61169 | 0.046194 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6353 |  | 2004-06-23 07:58 | 2004-06-23 | 2004-06-23 08:24 | Calculated | O410E | S1310 | Single Circuit |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 12 | 19353 | 312 | 0.01612 | 0.00062006 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6354 |  | 2004-06-23 08:03 | 2004-06-23 | 2004-06-23 09:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 116 | 1 | 19353 | 116 | 0.00599 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6355 |  | 2004-06-23 08:05 | 2004-06-23 | 2004-06-23 11:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 180 | 2 | 19353 | 360 | 0.0186 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6356 |  | 2004-06-23 09:45 | 2004-06-23 | 2004-06-23 13:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 241 | 1 | 19353 | 241 | 0.01245 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6358 |  | 2004-06-23 12:27 | 2004-06-23 | 2004-06-23 13:27 | Calculated | O410E | S659 |  |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 22 | 19353 | 1320 | 0.06821 | 0.0011368 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6360 |  | 2004-06-23 16:14 | 2004-06-23 | 2004-06-23 18:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 118 | 2 | 19353 | 236 | 0.01219 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6361 |  | 2004-06-23 17:16 | 2004-06-23 | 2004-06-23 18:25 | Calculated | O410E | L1709 | Single Circuit |  | Mokauiti 115-02 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 3 | 19353 | 207 | 0.0107 | 0.00015501 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
25029 | Faulty OCB 788 - Hangatiki | 2004-06-23 21:42 | 2004-06-23 | 2004-06-23 21:56 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 19353 |  | 0 | 0 |  |  | 2004/2005 | June-2004 | 6 | 2004
6362 |  | 2004-06-24 08:15 | 2004-06-24 | 2004-06-24 11:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 173 | 1 | 19353 | 173 | 0.00894 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6363 |  | 2004-06-24 08:17 | 2004-06-24 | 2004-06-24 11:39 | Calculated | O410E | LF |  |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 1 | 19353 | 202 | 0.01044 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6364 |  | 2004-06-24 13:10 | 2004-06-24 | 2004-06-24 14:18 | Calculated | O410E | LF |  |  | National Park 411-02 | Remote Rural F | National Park | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 1 | 19353 | 68 | 0.00351 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6365 |  | 2004-06-25 10:52 | 2004-06-25 | 2004-06-25 10:59 | Calculated | O410E | C686 | Single Circuit |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 248 | 19353 | 1872 | 0.09673 | 0.012815 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6367 |  | 2004-06-27 15:20 | 2004-06-27 | 2004-06-27 16:26 | Calculated | O410E | C686 | Single Circuit |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 248 | 19353 | 16591 | 0.85728 | 0.012815 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6368 |  | 2004-06-28 05:40 | 2004-06-28 | 2004-06-28 14:21 | Calculated | O410E | C949 | PVC/Polythene - Laid Direct |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply | Cables : Cable Core - Phase | Weather | WOLD |  | Avalanche / Lahar | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 521 | 1 | 19353 | 521 | 0.02692 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6372 |  | 2004-06-29 09:33 | 2004-06-29 | 2004-06-29 11:01 | Calculated | O410E |  |  |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 17 | 19353 | 1499 | 0.07746 | 0.00087842 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6373 |  | 2004-06-29 10:03 | 2004-06-29 | 2004-06-29 13:52 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 229 | 1 | 19353 | 229 | 0.01183 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6374 |  | 2004-06-29 10:30 | 2004-06-29 | 2004-06-29 13:14 | Calculated | O410E |  |  |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 164 | 26 | 19353 | 4264 | 0.22033 | 0.0013435 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6376 |  | 2004-06-30 01:15 | 2004-06-30 | 2004-06-30 04:30 | Calculated | O410E | C5004 | Single Circuit |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 195 | 416 | 19353 | 81154 | 4.1934 | 0.021495 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6377 |  | 2004-06-30 07:44 | 2004-06-30 | 2004-06-30 09:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 2 | 19353 | 188 | 0.00971 | 0.00010334 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6378 |  | 2004-06-30 14:49 | 2004-06-30 | 2004-06-30 15:15 | Calculated | O410E | C687 | Single Circuit |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation | OH Lines : Insulator - Pin | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 159 | 19353 | 4237 | 0.21893 | 0.0082158 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6382 |  | 2004-06-30 18:26 | 2004-06-30 | 2004-06-30 23:40 | Calculated | O410E | C1717 | Single Circuit |  | Mokauiti 115-04 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 314 | 17 | 19353 | 5351 | 0.27649 | 0.00087842 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6380 |  | 2004-06-30 19:10 | 2004-06-30 | 2004-06-30 20:48 | Calculated | O410E | C462 | Single Circuit |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 88 | 19353 | 8624 | 0.44562 | 0.0045471 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6381 |  | 2004-06-30 20:35 | 2004-06-30 | 2004-06-30 20:53 | Calculated | O410E | C6143 | Single Circuit |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 18 | 1 | 19353 | 18 | 0.00093 | 5.1672e-05 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6383 |  | 2004-06-30 22:37 | 2004-06-30 | 2004-07-01 03:54 | Calculated | O410E | C427 | Single Circuit |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Crossarm - Wood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 317 | 52 | 19353 | 16484 | 0.85175 | 0.0026869 | 0 | 0 | 2004/2005 | June-2004 | 6 | 2004
6385 |  | 2004-07-01 04:02 | 2004-07-01 | 2004-07-01 08:39 | Calculated | O410E | L686 | Drop-Out Fuses |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 277 | 10 | 19353 | 2770 | 0.14313 | 0.00051672 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6384 |  | 2004-07-01 05:45 | 2004-07-01 | 2004-07-01 06:25 | Calculated | O410E | C446 | Single Circuit |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 104 | 19353 | 4160 | 0.21495 | 0.0053738 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6386 |  | 2004-07-01 07:16 | 2004-07-01 | 2004-07-01 15:41 | Calculated | O410E | C440 | Single Circuit |  | Southern 409-09 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 505 | 24 | 19353 | 12127 | 0.62662 | 0.0012401 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6387 |  | 2004-07-01 07:28 | 2004-07-01 | 2004-07-01 09:47 | Calculated | O410E | C705 | Single Circuit |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 22 | 19353 | 3058 | 0.15801 | 0.0011368 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6388 |  | 2004-07-01 08:06 | 2004-07-01 | 2004-07-01 09:34 | Calculated | O410E | L1386 | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 4 | 19353 | 352 | 0.01819 | 0.00020669 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6389 |  | 2004-07-01 09:08 | 2004-07-01 | 2004-07-01 10:11 | Calculated | O410E |  |  |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 65 | 19353 | 4095 | 0.2116 | 0.0033587 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6390 |  | 2004-07-01 10:05 | 2004-07-01 | 2004-07-01 13:01 | Calculated | O410E | C851 | Single Circuit |  | Ongarue 421-02 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 8 | 19353 | 1408 | 0.07275 | 0.00041337 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6391 |  | 2004-07-01 10:35 | 2004-07-01 | 2004-07-01 12:53 | Calculated | O410E |  |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 138 | 7 | 19353 | 966 | 0.04991 | 0.0003617 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6393 |  | 2004-07-01 11:23 | 2004-07-01 | 2004-07-01 12:40 | Calculated | O410E | L1725 | Single Circuit |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 6 | 19353 | 462 | 0.02387 | 0.00031003 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6394 |  | 2004-07-01 14:10 | 2004-07-01 | 2004-07-01 17:25 | Calculated | O410E | L1.27 | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 195 | 6 | 19353 | 1170 | 0.06046 | 0.00031003 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6395 |  | 2004-07-01 16:00 | 2004-07-01 | 2004-07-01 17:16 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 76 | 1 | 19353 | 76 | 0.00393 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6396 |  | 2004-07-01 17:30 | 2004-07-01 | 2004-07-01 18:40 | Calculated | O410E | C119 | Single Circuit |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Pole - Softwood | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 119 | 19353 | 8445 | 0.43637 | 0.0061489 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6397 |  | 2004-07-01 21:43 | 2004-07-01 | 2004-07-01 21:46 | Calculated | O410E | C242 | Outdoor Circuit Breaker - Pole Mounted |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply | Switchgear : Bushings (fixed Insulation) | Asset Related | Insulator |  | Insulator - Salt - Pollution Tracking | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 3 | 327 | 19353 | 981 | 0.05069 | 0.016897 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6398 |  | 2004-07-02 05:26 | 2004-07-02 | 2004-07-02 06:28 | Calculated | O410E | C799 | Single Circuit |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 14 | 19353 | 868 | 0.04485 | 0.0007234 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6399 |  | 2004-07-02 06:06 | 2004-07-02 | 2004-07-02 08:51 | Calculated | O410E | C156 | Outdoor - Ground Mounted |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation | Transformers : Other | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 165 | 69 | 19353 | 11448 | 0.59154 | 0.0035653 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6401 |  | 2004-07-03 16:30 | 2004-07-03 | 2004-07-03 18:56 | Calculated | O410E | C773 & 990 |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 48 | 19353 | 7008 | 0.36211 | 0.0024802 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6402 |  | 2004-07-03 17:53 | 2004-07-03 | 2004-07-03 18:15 | Calculated | O410E | C110 | Single Circuit |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 82 | 19353 | 1804 | 0.09322 | 0.0042371 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6403 |  | 2004-07-04 01:25 | 2004-07-04 | 2004-07-04 02:45 | Calculated | O410E | C5004 | Single Circuit |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 416 | 19353 | 33640 | 1.7382 | 0.021495 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6405 |  | 2004-07-04 10:35 | 2004-07-04 | 2004-07-04 13:31 | Calculated | O410E | LF | Pole Mounted |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 1 | 19353 | 176 | 0.00909 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6407 |  | 2004-07-04 17:06 | 2004-07-04 | 2004-07-04 18:29 | Calculated | O410E | C773 & 990 |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 48 | 19353 | 3984 | 0.20586 | 0.0024802 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6408 |  | 2004-07-05 07:35 | 2004-07-05 | 2004-07-05 08:43 | Calculated | O410E | LF |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 1 | 19353 | 68 | 0.00351 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6412 |  | 2004-07-06 00:19 | 2004-07-06 | 2004-07-06 00:54 | Calculated | O410E | C122 | Single Circuit |  | Gravel Scoop 109-01 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 438 | 19353 | 15402 | 0.79585 | 0.022632 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6413 |  | 2004-07-06 10:25 | 2004-07-06 | 2004-07-06 11:14 | Calculated | O410E | LF |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 1 | 19353 | 49 | 0.00253 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6414 |  | 2004-07-06 10:36 | 2004-07-06 | 2004-07-06 12:34 | Calculated | O410E | LF |  |  | Tihoi 124-02 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 3 | 19353 | 354 | 0.01829 | 0.00015501 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6415 |  | 2004-07-06 14:14 | 2004-07-06 | 2004-07-06 16:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 112 | 1 | 19353 | 112 | 0.00579 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6419 |  | 2004-07-07 14:00 | 2004-07-07 | 2004-07-07 14:42 | Calculated | O410E | C110 |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 82 | 19353 | 3444 | 0.17796 | 0.0042371 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6421 |  | 2004-07-08 07:35 | 2004-07-08 | 2004-07-08 09:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 135 | 3 | 19353 | 405 | 0.02093 | 0.00015501 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6422 |  | 2004-07-08 09:10 | 2004-07-08 | 2004-07-08 11:47 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 157 | 63 | 19353 | 9910 | 0.51207 | 0.0032553 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6423 |  | 2004-07-08 10:02 | 2004-07-08 | 2004-07-08 11:53 | Calculated | O410E |  |  |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 111 | 118 | 19353 | 13172 | 0.68062 | 0.0060972 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6424 |  | 2004-07-08 11:06 | 2004-07-08 | 2004-07-08 11:37 | Calculated | O410E | L717 | Single Circuit |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 5 | 19353 | 155 | 0.00801 | 0.00025836 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6426 |  | 2004-07-08 16:58 | 2004-07-08 | 2004-07-08 18:09 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 1 | 19353 | 71 | 0.00367 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6427 |  | 2004-07-09 09:20 | 2004-07-09 | 2004-07-09 11:36 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 136 | 93 | 19353 | 12655 | 0.6539 | 0.0048055 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6428 |  | 2004-07-09 09:21 | 2004-07-09 | 2004-07-09 11:10 | Calculated | O410E | C6007 | Single Circuit |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 109 | 83 | 19353 | 9118 | 0.47114 | 0.0042887 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6430 |  | 2004-07-09 11:01 | 2004-07-09 | 2004-07-09 13:31 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 150 | 239 | 19353 | 35877 | 1.8538 | 0.01235 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6431 |  | 2004-07-09 13:03 | 2004-07-09 | 2004-07-09 14:46 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 103 | 1 | 19353 | 103 | 0.00532 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6432 |  | 2004-07-09 16:54 | 2004-07-09 | 2004-07-09 17:25 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 31 | 1 | 19353 | 31 | 0.0016 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6434 |  | 2004-07-13 09:30 | 2004-07-13 | 2004-07-13 09:52 | Calculated | O410E |  |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 22 | 60 | 19353 | 1320 | 0.06821 | 0.0031003 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6435 |  | 2004-07-13 10:00 | 2004-07-13 | 2004-07-13 15:28 | Calculated | O410E |  |  |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 328 | 6 | 19353 | 1968 | 0.10169 | 0.00031003 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6436 |  | 2004-07-13 15:38 | 2004-07-13 | 2004-07-13 16:00 | Calculated | O410E | LF |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 5 | 19353 | 110 | 0.00568 | 0.00025836 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6437 |  | 2004-07-14 07:10 | 2004-07-14 | 2004-07-14 07:21 | Calculated | O410E |  | Single Circuit |  | Mokauiti 115-05 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 20 | 19353 | 228 | 0.01178 | 0.0010334 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6438 |  | 2004-07-14 10:15 | 2004-07-14 | 2004-07-14 15:24 | Calculated | O410E |  |  |  | Caves 101-02 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 309 | 13 | 19353 | 4017 | 0.20756 | 0.00067173 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6439 |  | 2004-07-14 10:46 | 2004-07-14 | 2004-07-14 14:34 | Calculated | O410E | LF |  |  | Caves 101-03 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 228 | 1 | 19353 | 228 | 0.01178 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6440 |  | 2004-07-15 14:37 | 2004-07-15 | 2004-07-15 16:08 | Calculated | O410E | L246 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 91 | 15 | 19353 | 1365 | 0.07053 | 0.00077507 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6441 |  | 2004-07-16 09:08 | 2004-07-16 | 2004-07-16 11:11 | Calculated | O410E |  |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 123 | 17 | 19353 | 2091 | 0.10805 | 0.00087842 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6442 |  | 2004-07-19 06:17 | 2004-07-19 | 2004-07-19 07:34 | Calculated | O410E | C5867 | Single Circuit |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Insulator - Disc | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 387 | 19353 | 30147 | 1.5577 | 0.019997 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6443 |  | 2004-07-19 07:23 | 2004-07-19 | 2004-07-19 09:24 | Calculated | O410E | C1724 | Single Circuit |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 13 | 19353 | 1573 | 0.08128 | 0.00067173 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6444 |  | 2004-07-19 08:45 | 2004-07-19 | 2004-07-19 10:15 | Calculated | O410E | LF |  |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 2 | 19353 | 180 | 0.0093 | 0.00010334 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6445 |  | 2004-07-19 09:12 | 2004-07-19 | 2004-07-19 15:05 | Calculated | O410E |  |  |  | Piopio 116-02 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 25 | 19353 | 8825 | 0.456 | 0.0012918 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6446 |  | 2004-07-19 10:08 | 2004-07-19 | 2004-07-19 13:40 | Calculated | O410E |  |  |  | Piopio 116-02 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 212 | 2 | 19353 | 424 | 0.02191 | 0.00010334 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6449 |  | 2004-07-19 13:03 | 2004-07-19 | 2004-07-19 15:41 | Calculated | O410E | LF |  |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 158 | 5 | 19353 | 790 | 0.04082 | 0.00025836 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6450 |  | 2004-07-20 05:25 | 2004-07-20 | 2004-07-20 09:06 | Calculated | O410E | C1631 |  |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 13 | 19353 | 2873 | 0.14845 | 0.00067173 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6451 |  | 2004-07-20 10:00 | 2004-07-20 | 2004-07-20 10:12 | Calculated | O410E |  |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 12 | 24 | 19353 | 288 | 0.01488 | 0.0012401 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6454 |  | 2004-07-20 14:39 | 2004-07-20 | 2004-07-20 15:46 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 1 | 19353 | 67 | 0.00346 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6456 |  | 2004-07-21 11:00 | 2004-07-21 | 2004-07-21 12:50 | Calculated | O410E | LF |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 110 | 40 | 19353 | 4400 | 0.22735 | 0.0020669 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6457 |  | 2004-07-22 07:00 | 2004-07-22 | 2004-07-22 10:19 | Calculated | O410E | C1631 | Single Circuit |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 13 | 19353 | 2591 | 0.13388 | 0.00067173 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6458 |  | 2004-07-22 09:00 | 2004-07-22 | 2004-07-22 12:00 | Calculated | O410E |  |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 180 | 63 | 19353 | 11340 | 0.58596 | 0.0032553 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6459 |  | 2004-07-22 09:00 | 2004-07-22 | 2004-07-22 11:30 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 150 | 5 | 19353 | 750 | 0.03875 | 0.00025836 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6460 |  | 2004-07-22 09:42 | 2004-07-22 | 2004-07-22 10:47 | Calculated | O410E | LF | Single Circuit |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Pole - Softwood | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 29 | 19353 | 1885 | 0.0974 | 0.0014985 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6462 |  | 2004-07-23 00:21 | 2004-07-23 | 2004-07-23 11:37 | Calculated | O410E | L689 | Single Circuit |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 676 | 19 | 19353 | 12847 | 0.66382 | 0.00098176 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6463 |  | 2004-07-23 01:20 | 2004-07-23 | 2004-07-23 04:46 | Calculated | O410E | C5004 | Single Circuit |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 206 | 409 | 19353 | 84485 | 4.3655 | 0.021134 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6464 |  | 2004-07-23 09:40 | 2004-07-23 | 2004-07-23 14:45 | Calculated | O410E |  |  |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 16 | 19353 | 4880 | 0.25216 | 0.00082675 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6467 |  | 2004-07-25 23:19 | 2004-07-25 | 2004-07-25 23:29 | Calculated | O410E | C513 |  |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 410 | 19353 | 4100 | 0.21185 | 0.021185 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6468 |  | 2004-07-26 09:09 | 2004-07-26 | 2004-07-26 13:21 | Calculated | O410E |  |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 252 | 27 | 19353 | 6804 | 0.35157 | 0.0013951 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6470 |  | 2004-07-26 15:26 | 2004-07-26 | 2004-07-26 16:11 | Calculated | O410E | LF |  |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 2 | 19353 | 90 | 0.00465 | 0.00010334 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6471 |  | 2004-07-26 15:28 | 2004-07-26 | 2004-07-26 16:47 | Calculated | O410E | LF |  |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 1 | 19353 | 79 | 0.00408 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6472 |  | 2004-07-26 15:47 | 2004-07-26 | 2004-07-26 15:48 | Calculated | O410E | C467 |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 50 | 19353 | 50 | 0.00258 | 0.0025836 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6473 |  | 2004-07-27 09:28 | 2004-07-27 | 2004-07-27 10:09 | Calculated | O410E |  |  |  | National Park 411-02 | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 8 | 19353 | 328 | 0.01695 | 0.00041337 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6475 |  | 2004-07-27 12:18 | 2004-07-27 | 2004-07-27 13:56 | Calculated | O410E |  | Single Circuit |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 12 | 19353 | 1176 | 0.06077 | 0.00062006 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6476 |  | 2004-07-27 13:11 | 2004-07-27 | 2004-07-27 13:30 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 19 | 1 | 19353 | 19 | 0.00098 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6477 |  | 2004-07-27 13:57 | 2004-07-27 | 2004-07-27 15:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 1 | 19353 | 96 | 0.00496 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6478 |  | 2004-07-27 15:33 | 2004-07-27 | 2004-07-27 15:50 | Calculated | O410E | C1272 | Single Circuit |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Wraplock Deadend | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 225 | 19353 | 3929 | 0.20302 | 0.011626 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6479 |  | 2004-07-28 07:05 | 2004-07-28 | 2004-07-28 08:45 | Calculated | O410E | LF |  |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 1 | 19353 | 100 | 0.00517 | 5.1672e-05 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6480 |  | 2004-07-28 10:31 | 2004-07-28 | 2004-07-28 11:54 | Calculated | O410E |  |  |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 83 | 7 | 19353 | 581 | 0.03002 | 0.0003617 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6481 |  | 2004-07-28 12:16 | 2004-07-28 | 2004-07-28 12:37 | Calculated | O410E |  |  |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 21 | 22 | 19353 | 462 | 0.02387 | 0.0011368 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6482 |  | 2004-07-28 15:10 | 2004-07-28 | 2004-07-28 16:02 | Calculated | O410E | LF |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 19353 | 104 | 0.00537 | 0.00010334 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6483 |  | 2004-07-29 08:40 | 2004-07-29 | 2004-07-29 09:56 | Calculated | O410E | C1728 | Single Circuit |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 28 | 19353 | 2145 | 0.11084 | 0.0014468 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6484 |  | 2004-07-29 09:57 | 2004-07-29 | 2004-07-29 10:57 | Calculated | O410E |  |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 87 | 19353 | 5220 | 0.26973 | 0.0044954 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6485 |  | 2004-07-29 12:13 | 2004-07-29 | 2004-07-29 12:16 | Calculated | O410E | C1 |  |  | Mokai 123-00 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 252 | 19353 | 756 | 0.03906 | 0.013021 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6486 |  | 2004-07-29 12:15 | 2004-07-29 | 2004-07-29 13:10 | Calculated | O410E | L433 | Single Circuit |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 9 | 19353 | 495 | 0.02558 | 0.00046504 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6488 |  | 2004-07-30 07:17 | 2004-07-30 | 2004-07-30 07:27 | Calculated | O410E | C798 |  |  |  | Remote Rural F | Wairere / Mahoenui 33 | Wairere Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 499 | 19353 | 4990 | 0.25784 | 0.025784 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6489 |  | 2004-07-30 09:31 | 2004-07-30 | 2004-07-30 10:29 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 28 | 19353 | 1624 | 0.08391 | 0.0014468 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6491 |  | 2004-07-30 11:12 | 2004-07-30 | 2004-07-30 14:09 | Calculated | O410E | LF | Pole Mounted |  | Southern 409-03 | Remote Rural F | Southern | Manunui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 4 | 19353 | 708 | 0.03658 | 0.00020669 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6493 |  | 2004-07-31 19:27 | 2004-07-31 | 2004-07-31 19:34 | Calculated | O410E | C513 | Single Circuit |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 410 | 19353 | 2870 | 0.1483 | 0.021185 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6494 |  | 2004-07-31 22:01 | 2004-07-31 | 2004-07-31 22:08 | Calculated | O410E | C104 | Single Circuit |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 619 | 19353 | 4333 | 0.22389 | 0.031985 | 0 | 0 | 2004/2005 | July-2004 | 7 | 2004
6495 |  | 2004-08-02 08:45 | 2004-08-02 | 2004-08-02 09:40 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 55 | 3 | 19353 | 165 | 0.00853 | 0.00015501 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6496 |  | 2004-08-02 09:50 | 2004-08-02 | 2004-08-02 12:33 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 163 | 72 | 19353 | 11772 | 0.60828 | 0.0037204 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6498 |  | 2004-08-02 10:00 | 2004-08-02 | 2004-08-02 14:06 | Calculated | O410E | LV |  |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 246 | 15 | 19353 | 3690 | 0.19067 | 0.00077507 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6497 |  | 2004-08-02 10:05 | 2004-08-02 | 2004-08-02 10:21 | Calculated | O410E | C187 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Other |  | Incorrect Protection Settings | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 16 | 959 | 19353 | 15344 | 0.79285 | 0.049553 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6499 |  | 2004-08-02 10:30 | 2004-08-02 | 2004-08-02 14:01 | Calculated | O410E | LF |  |  | Piopio 116-02 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 211 | 2 | 19353 | 422 | 0.02181 | 0.00010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6500 |  | 2004-08-03 07:01 | 2004-08-03 | 2004-08-03 07:16 | Calculated | O410E | C955 | Single Circuit |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 1042 | 19353 | 15630 | 0.80763 | 0.053842 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6501 |  | 2004-08-03 09:38 | 2004-08-03 | 2004-08-03 10:28 | Calculated | O410E |  |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 50 | 139 | 19353 | 6950 | 0.35912 | 0.0071823 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6503 |  | 2004-08-03 10:26 | 2004-08-03 | 2004-08-03 12:03 | Calculated | O410E | LF |  |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 97 | 3 | 19353 | 291 | 0.01504 | 0.00015501 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6504 |  | 2004-08-03 10:30 | 2004-08-03 | 2004-08-03 11:56 | Calculated | O410E | L663 | Single Circuit |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 5 | 19353 | 430 | 0.02222 | 0.00025836 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6505 |  | 2004-08-03 22:07 | 2004-08-03 | 2004-08-03 22:17 | Calculated | O410E | C684 | Single Circuit |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 184 | 19353 | 1840 | 0.09508 | 0.0095076 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6507 |  | 2004-08-05 10:32 | 2004-08-05 | 2004-08-05 13:28 | Calculated | O410E | LF |  |  | Gravel Scoop 109-10 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 176 | 18 | 19353 | 3168 | 0.1637 | 0.00093009 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6509 |  | 2004-08-06 01:37 | 2004-08-06 | 2004-08-06 02:08 | Calculated | O410E | C127 | Single Circuit |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 339 | 19353 | 10627 | 0.54911 | 0.017517 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6510 |  | 2004-08-07 10:56 | 2004-08-07 | 2004-08-07 11:05 | Calculated | O410E | C512 | Single Circuit |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Surge Diverters | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 831 | 19353 | 7686 | 0.39715 | 0.042939 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6511 |  | 2004-08-08 09:54 | 2004-08-08 | 2004-08-08 09:56 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 240 | 19353 | 480 | 0.0248 | 0.012401 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6512 |  | 2004-08-09 08:00 | 2004-08-09 | 2004-08-09 10:15 | Calculated | O410E | C506 | Drop-Out Fuses |  | Ohura 413-03 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 135 | 4 | 19353 | 541 | 0.02795 | 0.00020669 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6513 |  | 2004-08-09 09:00 | 2004-08-09 | 2004-08-09 12:27 | Calculated | O410E | L1611 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 207 | 30 | 19353 | 6210 | 0.32088 | 0.0015501 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6516 |  | 2004-08-10 10:07 | 2004-08-10 | 2004-08-10 12:31 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 144 | 16 | 19353 | 2304 | 0.11905 | 0.00082675 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6517 |  | 2004-08-10 10:58 | 2004-08-10 | 2004-08-10 11:05 | Calculated | O410E | LF |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 15 | 19353 | 105 | 0.00543 | 0.00077507 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6518 |  | 2004-08-10 11:29 | 2004-08-10 | 2004-08-10 12:04 | Calculated | O410E | LF |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 35 | 1 | 19353 | 35 | 0.00181 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6520 |  | 2004-08-10 13:06 | 2004-08-10 | 2004-08-10 13:47 | Calculated | O410E | C506 | Single Circuit |  | Ohura 413-03 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 4 | 19353 | 164 | 0.00847 | 0.00020669 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6521 |  | 2004-08-11 09:55 | 2004-08-11 | 2004-08-11 11:34 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 1 | 19353 | 99 | 0.00512 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6522 |  | 2004-08-11 10:10 | 2004-08-11 | 2004-08-11 12:34 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 144 | 1 | 19353 | 144 | 0.00744 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6523 |  | 2004-08-11 10:45 | 2004-08-11 | 2004-08-11 13:00 | Calculated | O410E | C506 | Drop-Out Fuses |  | Ohura 413-03 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 135 | 4 | 19353 | 541 | 0.02795 | 0.00020669 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6524 |  | 2004-08-11 12:08 | 2004-08-11 | 2004-08-11 13:05 | Calculated | O410E | LF |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 5 | 19353 | 285 | 0.01473 | 0.00025836 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6526 |  | 2004-08-11 13:17 | 2004-08-11 | 2004-08-11 14:51 | Calculated | O410E | C1321 | Drop-Out Fuses |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 27 | 19353 | 2556 | 0.13207 | 0.0013951 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6527 |  | 2004-08-12 08:05 | 2004-08-12 | 2004-08-12 10:12 | Calculated | O410E | LF |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 1 | 19353 | 127 | 0.00656 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6528 |  | 2004-08-12 10:30 | 2004-08-12 | 2004-08-12 11:12 | Calculated | O410E | LV |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 2 | 19353 | 84 | 0.00434 | 0.00010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6529 |  | 2004-08-12 18:02 | 2004-08-12 | 2004-08-13 06:15 | Calculated | O410E | C1042 | Single Circuit |  |  | Remote Rural F | Lake Taupo 33 | Direct from Tokaanu Supply | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 733 | 637 | 19353 | 467059 | 24.1337 | 0.032915 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6530 |  | 2004-08-13 10:07 | 2004-08-13 | 2004-08-13 14:16 | Calculated | O410E |  |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 249 | 181 | 19353 | 26953 | 1.3927 | 0.0093526 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6531 |  | 2004-08-15 01:05 | 2004-08-15 | 2004-08-15 01:07 | Calculated | O410E | C5200 |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 773 | 19353 | 1546 | 0.07988 | 0.039942 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6533 |  | 2004-08-16 09:09 | 2004-08-16 | 2004-08-16 14:20 | Calculated | O410E |  |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 311 | 17 | 19353 | 5287 | 0.27319 | 0.00087842 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6534 |  | 2004-08-16 09:34 | 2004-08-16 | 2004-08-16 12:00 | Calculated | O410E |  |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 146 | 27 | 19353 | 3942 | 0.20369 | 0.0013951 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6535 |  | 2004-08-16 10:08 | 2004-08-16 | 2004-08-16 11:23 | Calculated | O410E | LF | Pole Mounted |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 2 | 19353 | 150 | 0.00775 | 0.00010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6536 |  | 2004-08-16 11:00 | 2004-08-16 | 2004-08-16 15:07 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 247 | 2 | 19353 | 494 | 0.02553 | 0.00010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6538 |  | 2004-08-16 13:00 | 2004-08-16 | 2004-08-16 15:58 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 178 | 41 | 19353 | 7298 | 0.3771 | 0.0021185 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6539 |  | 2004-08-16 13:17 | 2004-08-16 | 2004-08-16 15:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 151 | 1 | 19353 | 151 | 0.0078 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6540 |  | 2004-08-16 14:00 | 2004-08-16 | 2004-08-16 15:04 | Calculated | O410E |  |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 64 | 9 | 19353 | 576 | 0.02976 | 0.00046504 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6541 |  | 2004-08-16 21:55 | 2004-08-16 | 2004-08-16 23:36 | Calculated | O410E | C164 | Single Circuit |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 443 | 19353 | 45149 | 2.3329 | 0.022891 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6542 |  | 2004-08-17 05:47 | 2004-08-17 | 2004-08-17 06:11 | Calculated | O410E | C119 |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 71 | 19353 | 1704 | 0.08805 | 0.0036687 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6543 |  | 2004-08-17 06:01 | 2004-08-17 | 2004-08-17 06:11 | Calculated | O410E | C122 | Single Circuit |  | Gravel Scoop 109-01 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 438 | 19353 | 4380 | 0.22632 | 0.022632 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6544 |  | 2004-08-17 09:11 | 2004-08-17 | 2004-08-17 14:44 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 333 | 6 | 19353 | 1998 | 0.10324 | 0.00031003 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6546 |  | 2004-08-17 09:37 | 2004-08-17 | 2004-08-17 11:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 108 | 1 | 19353 | 108 | 0.00558 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6547 |  | 2004-08-17 10:13 | 2004-08-17 | 2004-08-17 11:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 10 | 19353 | 950 | 0.04909 | 0.00051672 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6549 |  | 2004-08-17 11:32 | 2004-08-17 | 2004-08-17 12:00 | Calculated | O410E |  |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 28 | 31 | 19353 | 868 | 0.04485 | 0.0016018 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6551 |  | 2004-08-17 15:07 | 2004-08-17 | 2004-08-17 15:26 | Calculated | O410E | LF | Pole Mounted |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Transformers : Other | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 2 | 19353 | 38 | 0.00196 | 0.00010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6552 |  | 2004-08-17 22:17 | 2004-08-17 | 2004-08-17 22:27 | Calculated | O410E | C6007 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 83 | 19353 | 830 | 0.04289 | 0.0042887 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6554 |  | 2004-08-18 00:10 | 2004-08-18 | 2004-08-18 01:07 | Calculated | O410E | C2092 | Single Circuit |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 105 | 19353 | 5985 | 0.30925 | 0.0054255 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6556 |  | 2004-08-18 06:01 | 2004-08-18 | 2004-08-18 11:37 | Calculated | O410E | C961 | Single Circuit |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 336 | 106 | 19353 | 35665 | 1.8429 | 0.0054772 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6555 |  | 2004-08-18 06:02 | 2004-08-18 | 2004-08-18 06:10 | Calculated | O410E | C990 |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 13 | 19353 | 104 | 0.00537 | 0.00067173 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6557 |  | 2004-08-18 07:24 | 2004-08-18 | 2004-08-18 09:44 | Calculated | O410E | C701 |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 156 | 19353 | 21840 | 1.1285 | 0.0080608 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6558 |  | 2004-08-18 07:49 | 2004-08-18 | 2004-08-18 10:34 | Calculated | O410E | LF |  |  | McDonalds 110-02 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 10 | 19353 | 1650 | 0.08526 | 0.00051672 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6559 |  | 2004-08-18 09:07 | 2004-08-18 | 2004-08-18 13:47 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 280 | 6 | 19353 | 1680 | 0.08681 | 0.00031003 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6560 |  | 2004-08-18 09:11 | 2004-08-18 | 2004-08-18 10:46 | Calculated | O410E | L414 | Drop-Out Fuses |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 6 | 19353 | 570 | 0.02945 | 0.00031003 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6561 |  | 2004-08-18 10:58 | 2004-08-18 | 2004-08-18 12:33 | Calculated | O410E |  |  |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 11 | 19353 | 1045 | 0.054 | 0.00056839 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6562 |  | 2004-08-18 11:14 | 2004-08-18 | 2004-08-18 14:08 | Calculated | O410E | L705 | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 174 | 6 | 19353 | 1044 | 0.05395 | 0.00031003 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6565 |  | 2004-08-18 15:22 | 2004-08-18 | 2004-08-18 16:25 | Calculated | O410E | C1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 13 | 19353 | 824 | 0.04258 | 0.00067173 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6566 |  | 2004-08-18 18:25 | 2004-08-18 | 2004-08-18 19:12 | Calculated | O410E | L1617 | Single Circuit |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 2 | 19353 | 94 | 0.00486 | 0.00010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6567 |  | 2004-08-19 10:17 | 2004-08-19 | 2004-08-19 12:21 | Calculated | O410E |  |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 124 | 5 | 19353 | 620 | 0.03204 | 0.00025836 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6569 |  | 2004-08-19 16:42 | 2004-08-19 | 2004-08-20 07:14 | Calculated | O410E | C773 | PVC/Polythene - Laid Direct |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation | Cables : Cable Core - Phase | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 872 | 36 | 19353 | 31410 | 1.623 | 0.0018602 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
25069 | Restore Cable After Fault - Mt Ruapehu | 2004-08-20 16:34 | 2004-08-20 | 2004-08-20 16:57 | Calculated | 16N01 | 16N01 - 3ph 100kVA GMT |  | 419SEG5866-6338 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 23 | 28 | 19353 | 645 | 0.03333 | 0.0014468 | 965 | 22243 | 2004/2005 | August-2004 | 8 | 2004
6571 |  | 2004-08-21 18:58 | 2004-08-21 | 2004-08-21 20:37 | Calculated | O410E | C144 | Single Circuit |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 281 | 19353 | 27819 | 1.4374 | 0.01452 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6572 |  | 2004-08-22 00:55 | 2004-08-22 | 2004-08-22 01:06 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 1 | 19353 | 11 | 0.00057 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6573 |  | 2004-08-22 03:46 | 2004-08-22 | 2004-08-22 03:47 | Calculated | O410E | C262 | Single Circuit |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply | OH Lines : Insulator - Pin | Asset Related | Insulator |  | Insulator - Salt - Pollution Tracking | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | August-2004 | 8 | 2004
6574 |  | 2004-08-23 10:37 | 2004-08-23 | 2004-08-23 14:49 | Calculated | O410E |  |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 252 | 9 | 19353 | 2268 | 0.11719 | 0.00046504 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6575 |  | 2004-08-24 10:17 | 2004-08-24 | 2004-08-24 14:36 | Calculated | O410E |  |  |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 259 | 16 | 19353 | 4144 | 0.21413 | 0.00082675 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6576 |  | 2004-08-24 14:26 | 2004-08-24 | 2004-08-24 15:20 | Calculated | O410E |  | Single Circuit |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 7 | 19353 | 378 | 0.01953 | 0.0003617 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6578 |  | 2004-08-25 10:04 | 2004-08-25 | 2004-08-25 15:56 | Calculated | O410E |  |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 352 | 85 | 19353 | 29920 | 1.546 | 0.0043921 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6579 |  | 2004-08-25 15:09 | 2004-08-25 | 2004-08-25 16:21 | Calculated | O410E | LF |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 2 | 19353 | 144 | 0.00744 | 0.00010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6580 |  | 2004-08-25 15:30 | 2004-08-25 | 2004-08-25 16:24 | Calculated | O410E | LF | Drop-Out Fuses |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 54 | 20 | 19353 | 1080 | 0.05581 | 0.0010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6581 |  | 2004-08-25 16:51 | 2004-08-25 | 2004-08-25 16:59 | Calculated | O410E | LF |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 1 | 19353 | 8 | 0.00041 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6582 |  | 2004-08-26 10:07 | 2004-08-26 | 2004-08-26 10:54 | Calculated | O410E | LF |  |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 47 | 2 | 19353 | 94 | 0.00486 | 0.00010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6584 |  | 2004-08-27 09:46 | 2004-08-27 | 2004-08-27 11:07 | Calculated | O410E | LF |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 1 | 19353 | 81 | 0.00419 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6585 |  | 2004-08-27 10:09 | 2004-08-27 | 2004-08-27 11:01 | Calculated | O410E | LF |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 19353 | 104 | 0.00537 | 0.00010334 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6586 |  | 2004-08-28 08:09 | 2004-08-28 | 2004-08-28 09:17 | Calculated | O410E | C117 |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 97 | 19353 | 6670 | 0.34465 | 0.0050121 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6587 |  | 2004-08-30 11:30 | 2004-08-30 | 2004-08-30 14:18 | Calculated | O410E | LF |  |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 1 | 19353 | 168 | 0.00868 | 5.1672e-05 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6588 |  | 2004-08-30 14:24 | 2004-08-30 | 2004-08-30 14:56 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 4 | 19353 | 128 | 0.00661 | 0.00020669 | 0 | 0 | 2004/2005 | August-2004 | 8 | 2004
6590 |  | 2004-09-01 05:09 | 2004-09-01 | 2004-09-01 05:19 | Calculated | O410E | C513 | Single Circuit |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 410 | 19353 | 4332 | 0.22384 | 0.021185 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6591 |  | 2004-09-01 10:30 | 2004-09-01 | 2004-09-01 11:45 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6592 |  | 2004-09-01 10:35 | 2004-09-01 | 2004-09-01 11:20 | Calculated | O410E |  | ABS |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Bushings (fixed Insulation) | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 45 | 67 | 19353 | 3015 | 0.15579 | 0.003462 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6594 |  | 2004-09-02 11:43 | 2004-09-02 | 2004-09-02 11:58 | Calculated | O410E | C1052 | Single Circuit |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 258 | 19353 | 4024 | 0.20793 | 0.013331 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6597 |  | 2004-09-03 10:04 | 2004-09-03 | 2004-09-03 11:38 | Calculated | O410E | L693 |  |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 20 | 19353 | 1880 | 0.09714 | 0.0010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6598 |  | 2004-09-05 10:00 | 2004-09-05 | 2004-09-05 11:00 | Calculated | O410E | LV |  |  | Piopio 116-02 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 8 | 19353 | 480 | 0.0248 | 0.00041337 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6599 |  | 2004-09-06 09:03 | 2004-09-06 | 2004-09-06 15:15 | Calculated | O410E |  |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 372 | 83 | 19353 | 30876 | 1.5954 | 0.0042887 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6600 |  | 2004-09-06 15:50 | 2004-09-06 | 2004-09-06 16:57 | Calculated | O410E | C524 |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 4 | 19353 | 268 | 0.01385 | 0.00020669 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6601 |  | 2004-09-07 09:16 | 2004-09-07 | 2004-09-07 15:10 | Calculated | O410E |  |  |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 10 | 19353 | 3540 | 0.18292 | 0.00051672 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6602 |  | 2004-09-07 13:35 | 2004-09-07 | 2004-09-07 14:34 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-04 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 59 | 2 | 19353 | 118 | 0.0061 | 0.00010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6603 |  | 2004-09-08 07:58 | 2004-09-08 | 2004-09-08 09:36 | Calculated | O410E | LF | Single Circuit |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 1 | 19353 | 98 | 0.00506 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6604 |  | 2004-09-08 08:47 | 2004-09-08 | 2004-09-08 09:19 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-04 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 32 | 2 | 19353 | 64 | 0.00331 | 0.00010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6606 |  | 2004-09-08 09:56 | 2004-09-08 | 2004-09-08 11:44 | Calculated | O410E | L575 |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 31 | 19353 | 3348 | 0.173 | 0.0016018 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6607 |  | 2004-09-08 17:30 | 2004-09-08 | 2004-09-08 19:20 | Calculated | O410E | LF | Pole Mounted |  | McDonalds 110-04 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 2 | 19353 | 220 | 0.01137 | 0.00010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6608 |  | 2004-09-09 09:27 | 2004-09-09 | 2004-09-09 11:34 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 127 | 43 | 19353 | 5481 | 0.28321 | 0.0022219 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6609 |  | 2004-09-09 18:18 | 2004-09-09 | 2004-09-09 18:19 | Calculated | O410E | C222, 570, 125 | Main Protection |  |  | Remote Rural F | Te Waireka Rd 33 | Direct from Hangatiki Supply | Miscellaneous : Buchholz Relay | Asset Related | Other |  | Condensation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | September-2004 | 9 | 2004
6610 |  | 2004-09-10 10:04 | 2004-09-10 | 2004-09-10 13:13 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 189 | 67 | 19353 | 12663 | 0.65432 | 0.003462 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6611 |  | 2004-09-10 16:03 | 2004-09-10 | 2004-09-10 16:29 | Calculated | O410E | LF | Pole Mounted |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 1 | 19353 | 26 | 0.00134 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6612 |  | 2004-09-11 21:54 | 2004-09-11 | 2004-09-11 22:06 | Calculated | O410E | C1021 |  |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 233 | 19353 | 2796 | 0.14447 | 0.012039 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6614 |  | 2004-09-13 10:05 | 2004-09-13 | 2004-09-13 11:55 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 110 | 9 | 19353 | 990 | 0.05115 | 0.00046504 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6615 |  | 2004-09-13 10:32 | 2004-09-13 | 2004-09-13 11:56 | Calculated | O410E |  |  |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 27 | 19353 | 2288 | 0.11822 | 0.0013951 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6616 |  | 2004-09-14 04:48 | 2004-09-14 | 2004-09-14 07:45 | Calculated | O410E | L689 | Drop-Out Fuses |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 177 | 19 | 19353 | 3363 | 0.17377 | 0.00098176 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6618 |  | 2004-09-14 13:30 | 2004-09-14 | 2004-09-14 14:58 | Calculated | O410E | LF |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 1 | 19353 | 88 | 0.00455 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6619 |  | 2004-09-14 13:43 | 2004-09-14 | 2004-09-14 14:05 | Calculated | O410E | LF |  |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 22 | 1 | 19353 | 22 | 0.00114 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6620 |  | 2004-09-15 10:00 | 2004-09-15 | 2004-09-15 12:35 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 155 | 11 | 19353 | 1705 | 0.0881 | 0.00056839 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6621 |  | 2004-09-15 10:27 | 2004-09-15 | 2004-09-15 11:05 | Calculated | O410E |  |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 38 | 14 | 19353 | 532 | 0.02749 | 0.0007234 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6623 |  | 2004-09-16 09:27 | 2004-09-16 | 2004-09-16 10:15 | Calculated | O410E | L ??? | Single Circuit |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 5 | 19353 | 240 | 0.0124 | 0.00025836 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6624 |  | 2004-09-16 10:09 | 2004-09-16 | 2004-09-16 14:20 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 251 | 2 | 19353 | 502 | 0.02594 | 0.00010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6625 |  | 2004-09-16 10:30 | 2004-09-16 | 2004-09-16 14:22 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 15 | 19353 | 3480 | 0.17982 | 0.00077507 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6626 |  | 2004-09-16 13:10 | 2004-09-16 | 2004-09-16 13:45 | Calculated | O410E | LF |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 2 | 19353 | 70 | 0.00362 | 0.00010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6627 |  | 2004-09-17 09:39 | 2004-09-17 | 2004-09-17 15:13 | Calculated | O410E |  |  |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 334 | 4 | 19353 | 1336 | 0.06903 | 0.00020669 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6628 |  | 2004-09-17 09:41 | 2004-09-17 | 2004-09-17 10:37 | Calculated | O410E | L689 | Single Circuit |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 19 | 19353 | 1064 | 0.05498 | 0.00098176 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6629 |  | 2004-09-17 10:11 | 2004-09-17 | 2004-09-17 16:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 407 | 2 | 19353 | 814 | 0.04206 | 0.00010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6630 |  | 2004-09-17 10:13 | 2004-09-17 | 2004-09-17 11:31 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 78 | 2 | 19353 | 156 | 0.00806 | 0.00010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6631 |  | 2004-09-18 06:25 | 2004-09-18 | 2004-09-18 10:09 | Calculated | O410E | C687 | Single Circuit |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 224 | 160 | 19353 | 35922 | 1.8561 | 0.0082675 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6632 |  | 2004-09-18 09:02 | 2004-09-18 | 2004-09-18 09:31 | Calculated | O410E |  |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 29 | 5 | 19353 | 145 | 0.00749 | 0.00025836 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6633 |  | 2004-09-18 11:42 | 2004-09-18 | 2004-09-18 12:31 | Calculated | O410E | L165 & 627 | Single Circuit |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 12 | 19353 | 588 | 0.03038 | 0.00062006 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6634 |  | 2004-09-19 08:52 | 2004-09-19 | 2004-09-19 08:53 | Calculated | O410E | C262 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | September-2004 | 9 | 2004
6635 |  | 2004-09-19 13:11 | 2004-09-19 | 2004-09-19 15:38 | Calculated | O410E | L243 | Single Circuit |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 30 | 19353 | 4410 | 0.22787 | 0.0015501 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6636 |  | 2004-09-20 09:30 | 2004-09-20 | 2004-09-20 10:45 | Calculated | O410E |  |  |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 75 | 29 | 19353 | 2175 | 0.11239 | 0.0014985 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6637 |  | 2004-09-20 10:30 | 2004-09-20 | 2004-09-20 14:56 | Calculated | O410E | LF | Pole Mounted |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 266 | 1 | 19353 | 266 | 0.01374 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6638 |  | 2004-09-20 13:27 | 2004-09-20 | 2004-09-20 14:18 | Calculated | O410E | LF |  |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 1 | 19353 | 51 | 0.00264 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6639 |  | 2004-09-21 09:01 | 2004-09-21 | 2004-09-21 14:50 | Calculated | O410E |  |  |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 349 | 7 | 19353 | 2443 | 0.12623 | 0.0003617 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6640 |  | 2004-09-21 11:30 | 2004-09-21 | 2004-09-21 14:38 | Calculated | O410E |  |  |  | Maihiihi 111-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 188 | 19 | 19353 | 3572 | 0.18457 | 0.00098176 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6641 |  | 2004-09-22 09:38 | 2004-09-22 | 2004-09-22 11:11 | Calculated | O410E | LF |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 93 | 1 | 19353 | 93 | 0.00481 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6643 |  | 2004-09-22 11:21 | 2004-09-22 | 2004-09-22 11:21 | Calculated | O410E | L932 | Pole Mounted |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 10 | 19353 | 0 | 0 | 0.00051672 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6644 |  | 2004-09-22 13:31 | 2004-09-22 | 2004-09-22 14:13 | Calculated | O410E | LF |  |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 1 | 19353 | 42 | 0.00217 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6645 |  | 2004-09-22 13:35 | 2004-09-22 | 2004-09-22 14:25 | Calculated | O410E | L1.27 | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 50 | 6 | 19353 | 300 | 0.0155 | 0.00031003 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6646 |  | 2004-09-22 14:10 | 2004-09-22 | 2004-09-22 17:09 | Calculated | O410E | LF | Pole Mounted |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 3 | 19353 | 537 | 0.02775 | 0.00015501 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6647 |  | 2004-09-22 14:45 | 2004-09-22 | 2004-09-22 15:58 | Calculated | O410E | LF |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6648 |  | 2004-09-22 14:53 | 2004-09-22 | 2004-09-22 15:08 | Calculated | O410E | C6007 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 15 | 85 | 19353 | 1321 | 0.06826 | 0.0043921 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6649 |  | 2004-09-22 15:00 | 2004-09-22 | 2004-09-22 16:23 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 83 | 1 | 19353 | 83 | 0.00429 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6650 |  | 2004-09-22 15:51 | 2004-09-22 | 2004-09-22 19:27 | Calculated | O410E | S921 | Single Circuit |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 216 | 483 | 19353 | 104328 | 5.3908 | 0.024957 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6651 |  | 2004-09-22 16:34 | 2004-09-22 | 2004-09-22 19:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 149 | 2 | 19353 | 298 | 0.0154 | 0.00010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6653 |  | 2004-09-23 09:18 | 2004-09-23 | 2004-09-23 14:13 | Calculated | O410E |  |  |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 295 | 6 | 19353 | 1770 | 0.09146 | 0.00031003 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6656 |  | 2004-09-23 12:02 | 2004-09-23 | 2004-09-23 13:40 | Calculated | O410E | LF | Pole Mounted |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 1 | 19353 | 98 | 0.00506 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6657 |  | 2004-09-23 15:50 | 2004-09-23 | 2004-09-23 17:30 | Calculated | O410E | L705 | Drop-Out Fuses |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 100 | 16 | 19353 | 1600 | 0.08267 | 0.00082675 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6659 |  | 2004-09-24 00:11 | 2004-09-24 | 2004-09-24 00:19 | Calculated | O410E | C 180 & 6143 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 2 | 19353 | 17 | 0.00088 | 0.00010334 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6660 |  | 2004-09-24 09:25 | 2004-09-24 | 2004-09-24 09:43 | Calculated | O410E | LF |  |  | Benneydale 103-07 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 18 | 19 | 19353 | 342 | 0.01767 | 0.00098176 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6658 |  | 2004-09-24 23:34 | 2004-09-24 | 2004-09-24 23:35 | Calculated | O410E | C262 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | September-2004 | 9 | 2004
6661 |  | 2004-09-25 03:35 | 2004-09-25 | 2004-09-25 03:47 | Calculated | O410E | C594, 754 & 792 | Single Circuit |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 12 | 1571 | 19353 | 18852 | 0.97411 | 0.081176 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6662 |  | 2004-09-27 09:45 | 2004-09-27 | 2004-09-27 10:44 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 59 | 1 | 19353 | 59 | 0.00305 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6663 |  | 2004-09-27 12:30 | 2004-09-27 | 2004-09-27 15:23 | Calculated | O410E | LF |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 173 | 51 | 19353 | 8823 | 0.4559 | 0.0026353 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6664 |  | 2004-09-27 13:10 | 2004-09-27 | 2004-09-27 14:14 | Calculated | O410E | LF |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 64 | 1 | 19353 | 64 | 0.00331 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6665 |  | 2004-09-28 10:42 | 2004-09-28 | 2004-09-28 10:43 | Calculated | O410E |  |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 19 | 19353 | 19 | 0.00098 | 0.00098176 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6666 |  | 2004-09-28 11:09 | 2004-09-28 | 2004-09-28 15:45 | Calculated | O410E | C296 | Single Circuit |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 276 | 137 | 19353 | 37834 | 1.9549 | 0.007079 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6668 |  | 2004-09-28 12:39 | 2004-09-28 | 2004-09-28 14:05 | Calculated | O410E | C182 | Single Circuit |  |  | Remote Rural F | Nihoniho | Nihoniho Zone Substation | OH Lines : Crossarm - Wood | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 86 | 319 | 19353 | 27434 | 1.4176 | 0.016483 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6669 |  | 2004-09-28 13:08 | 2004-09-28 | 2004-09-28 14:12 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 64 | 1 | 19353 | 64 | 0.00331 | 5.1672e-05 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6670 |  | 2004-09-28 15:48 | 2004-09-28 | 2004-09-28 16:57 | Calculated | O410E | L362 | Drop-Out Fuses |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 69 | 11 | 19353 | 759 | 0.03922 | 0.00056839 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6671 |  | 2004-09-28 18:36 | 2004-09-28 | 2004-09-29 00:24 | Calculated | O410E | C1530 | Single Circuit |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 348 | 6 | 19353 | 2092 | 0.1081 | 0.00031003 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6672 |  | 2004-09-29 08:40 | 2004-09-29 | 2004-09-29 10:03 | Calculated | O410E | S1337 | Single Circuit |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 13 | 19353 | 1079 | 0.05575 | 0.00067173 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6673 |  | 2004-09-29 09:48 | 2004-09-29 | 2004-09-29 15:20 | Calculated | O410E |  |  |  | Caves 101-02 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 332 | 13 | 19353 | 4316 | 0.22301 | 0.00067173 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6674 |  | 2004-09-29 10:00 | 2004-09-29 | 2004-09-29 15:16 | Calculated | O410E | LV |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 316 | 14 | 19353 | 4424 | 0.2286 | 0.0007234 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6675 |  | 2004-09-30 09:37 | 2004-09-30 | 2004-09-30 13:23 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 226 | 11 | 19353 | 2486 | 0.12846 | 0.00056839 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6676 |  | 2004-09-30 10:00 | 2004-09-30 | 2004-09-30 14:56 | Calculated | O410E | LV |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 296 | 24 | 19353 | 7104 | 0.36707 | 0.0012401 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6677 |  | 2004-09-30 10:21 | 2004-09-30 | 2004-09-30 10:56 | Calculated | O410E |  |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 35 | 28 | 19353 | 1003 | 0.05183 | 0.0014468 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6678 |  | 2004-09-30 10:51 | 2004-09-30 | 2004-09-30 11:32 | Calculated | O410E | LV |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 56 | 19353 | 2296 | 0.11864 | 0.0028936 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6679 |  | 2004-09-30 11:38 | 2004-09-30 | 2004-09-30 13:06 | Calculated | O410E | LF |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 16 | 19353 | 1408 | 0.07275 | 0.00082675 | 0 | 0 | 2004/2005 | September-2004 | 9 | 2004
6680 |  | 2004-10-01 09:15 | 2004-10-01 | 2004-10-01 10:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 72 | 1 | 19353 | 72 | 0.00372 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6681 |  | 2004-10-01 10:10 | 2004-10-01 | 2004-10-01 12:02 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 112 | 2 | 19353 | 224 | 0.01157 | 0.00010334 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6682 |  | 2004-10-01 13:53 | 2004-10-01 | 2004-10-01 14:11 | Calculated | O410E | LF |  |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 18 | 2 | 19353 | 36 | 0.00186 | 0.00010334 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6683 |  | 2004-10-01 15:17 | 2004-10-01 | 2004-10-01 16:03 | Calculated | O410E | LF |  |  | Ohura 413-03 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 1 | 19353 | 46 | 0.00238 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6685 |  | 2004-10-04 09:58 | 2004-10-04 | 2004-10-04 10:23 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 117 | 19353 | 3022 | 0.15615 | 0.0060456 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6686 |  | 2004-10-04 13:08 | 2004-10-04 | 2004-10-04 15:03 | Calculated | O410E | C440 | Single Circuit |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 43 | 19353 | 4978 | 0.25722 | 0.0022219 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6687 |  | 2004-10-05 08:38 | 2004-10-05 | 2004-10-05 08:46 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 2 | 19353 | 17 | 0.00088 | 0.00010334 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6688 |  | 2004-10-05 10:03 | 2004-10-05 | 2004-10-05 11:46 | Calculated | O410E | C1343 | Single Circuit |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 83 | 19353 | 8549 | 0.44174 | 0.0042887 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6689 |  | 2004-10-06 09:00 | 2004-10-06 | 2004-10-06 12:31 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 211 | 1 | 19353 | 211 | 0.0109 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6691 |  | 2004-10-06 09:50 | 2004-10-06 | 2004-10-06 15:08 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 318 | 6 | 19353 | 1908 | 0.09859 | 0.00031003 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6692 |  | 2004-10-06 09:52 | 2004-10-06 | 2004-10-06 10:48 | Calculated | O410E |  |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 56 | 84 | 19353 | 4704 | 0.24306 | 0.0043404 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6694 |  | 2004-10-06 12:22 | 2004-10-06 | 2004-10-06 13:13 | Calculated | O410E | LF |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 2 | 19353 | 102 | 0.00527 | 0.00010334 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6695 |  | 2004-10-07 09:43 | 2004-10-07 | 2004-10-07 13:58 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 255 | 13 | 19353 | 3315 | 0.17129 | 0.00067173 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6697 |  | 2004-10-07 12:41 | 2004-10-07 | 2004-10-07 12:51 | Calculated | O410E | LF |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 10 | 2 | 19353 | 20 | 0.00103 | 0.00010334 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6698 |  | 2004-10-07 19:41 | 2004-10-07 | 2004-10-07 20:07 | Calculated | O410E | L368 | Drop-Out Fuses |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Switch Connections (O/H) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 26 | 24 | 19353 | 624 | 0.03224 | 0.0012401 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6699 |  | 2004-10-08 09:15 | 2004-10-08 | 2004-10-08 09:34 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-02 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 19 | 1 | 19353 | 19 | 0.00098 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6700 |  | 2004-10-08 09:30 | 2004-10-08 | 2004-10-08 12:10 | Calculated | O410E | LV |  |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 160 | 6 | 19353 | 960 | 0.0496 | 0.00031003 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6701 |  | 2004-10-08 09:41 | 2004-10-08 | 2004-10-08 11:16 | Calculated | O410E | LF |  |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 3 | 19353 | 287 | 0.01483 | 0.00015501 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6702 |  | 2004-10-08 09:59 | 2004-10-08 | 2004-10-08 10:34 | Calculated | O410E | C112 | Single Circuit |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 207 | 19353 | 7393 | 0.38201 | 0.010696 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6703 |  | 2004-10-08 10:31 | 2004-10-08 | 2004-10-08 13:42 | Calculated | O410E |  |  |  | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 191 | 13 | 19353 | 2483 | 0.1283 | 0.00067173 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6704 |  | 2004-10-08 22:21 | 2004-10-08 | 2004-10-09 00:13 | Calculated | O410E | C378 | Single Circuit |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 26 | 19353 | 2912 | 0.15047 | 0.0013435 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6705 |  | 2004-10-11 09:37 | 2004-10-11 | 2004-10-11 15:10 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 333 | 13 | 19353 | 4329 | 0.22369 | 0.00067173 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6706 |  | 2004-10-12 06:38 | 2004-10-12 | 2004-10-12 13:59 | Calculated | O410E | C1620 | Single Circuit |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 441 | 176 | 19353 | 77686 | 4.0142 | 0.0090942 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6707 |  | 2004-10-12 09:35 | 2004-10-12 | 2004-10-12 15:04 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 329 | 13 | 19353 | 4277 | 0.221 | 0.00067173 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6710 |  | 2004-10-13 10:33 | 2004-10-13 | 2004-10-13 11:29 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 56 | 3 | 19353 | 168 | 0.00868 | 0.00015501 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6711 |  | 2004-10-13 11:46 | 2004-10-13 | 2004-10-13 13:53 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 1 | 19353 | 127 | 0.00656 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6712 |  | 2004-10-13 13:00 | 2004-10-13 | 2004-10-13 13:25 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 7 | 19353 | 175 | 0.00904 | 0.0003617 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6713 |  | 2004-10-13 13:33 | 2004-10-13 | 2004-10-13 13:42 | Calculated | O410E | LF |  |  | Whakamaru 120-03 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 4 | 19353 | 36 | 0.00186 | 0.00020669 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6714 |  | 2004-10-14 07:30 | 2004-10-14 | 2004-10-14 08:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 56 | 1 | 19353 | 56 | 0.00289 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6715 |  | 2004-10-14 08:01 | 2004-10-14 | 2004-10-14 08:44 | Calculated | O410E | LF |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 4 | 19353 | 172 | 0.00889 | 0.00020669 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6716 |  | 2004-10-14 09:30 | 2004-10-14 | 2004-10-14 14:12 | Calculated | O410E |  |  |  | Caves 101-02 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 13 | 19353 | 3666 | 0.18943 | 0.00067173 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6718 |  | 2004-10-15 10:00 | 2004-10-15 | 2004-10-15 11:35 | Calculated | O410E |  |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 11 | 19353 | 1045 | 0.054 | 0.00056839 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6719 |  | 2004-10-15 10:30 | 2004-10-15 | 2004-10-15 13:10 | Calculated | O410E |  |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 160 | 17 | 19353 | 2720 | 0.14055 | 0.00087842 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6720 |  | 2004-10-16 23:25 | 2004-10-16 | 2004-10-17 02:59 | Calculated | O410E | C113 |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 42 | 19353 | 4718 | 0.24379 | 0.0021702 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6721 |  | 2004-10-17 12:57 | 2004-10-17 | 2004-10-17 17:02 | Calculated | O410E | LF | Pole Mounted |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 245 | 2 | 19353 | 490 | 0.02532 | 0.00010334 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6722 |  | 2004-10-18 05:13 | 2004-10-18 | 2004-10-18 05:57 | Calculated | O410E | C127 | Single Circuit |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Joint - Mechanical / Non-Tension | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 339 | 19353 | 15091 | 0.77978 | 0.017517 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6724 |  | 2004-10-18 14:00 | 2004-10-18 | 2004-10-18 16:42 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 162 | 1 | 19353 | 162 | 0.00837 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6723 |  | 2004-10-18 14:17 | 2004-10-18 | 2004-10-18 14:45 | Calculated | O410E | LF |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 28 | 1 | 19353 | 28 | 0.00145 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6725 |  | 2004-10-19 10:00 | 2004-10-19 | 2004-10-19 10:34 | Calculated | O410E |  |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 34 | 43 | 19353 | 1470 | 0.07596 | 0.0022219 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6726 |  | 2004-10-19 10:36 | 2004-10-19 | 2004-10-19 11:16 | Calculated | O410E | LF |  |  | Caves 101-07 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 40 | 2 | 19353 | 80 | 0.00413 | 0.00010334 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6728 |  | 2004-10-20 09:40 | 2004-10-20 | 2004-10-20 14:05 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 265 | 6 | 19353 | 1590 | 0.08216 | 0.00031003 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6729 |  | 2004-10-20 10:32 | 2004-10-20 | 2004-10-20 12:03 | Calculated | O410E | LF |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 1 | 19353 | 91 | 0.0047 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6730 |  | 2004-10-20 10:35 | 2004-10-20 | 2004-10-20 16:28 | Calculated | O410E |  |  |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 3 | 19353 | 1059 | 0.05472 | 0.00015501 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6731 |  | 2004-10-20 13:57 | 2004-10-20 | 2004-10-20 14:48 | Calculated | O410E | LF |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 1 | 19353 | 51 | 0.00264 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6732 |  | 2004-10-21 08:05 | 2004-10-21 | 2004-10-21 12:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 240 | 3 | 19353 | 720 | 0.0372 | 0.00015501 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6734 |  | 2004-10-21 09:43 | 2004-10-21 | 2004-10-21 10:48 | Calculated | O410E | L1623 | Single Circuit |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 10 | 19353 | 650 | 0.03359 | 0.00051672 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6735 |  | 2004-10-21 10:38 | 2004-10-21 | 2004-10-21 15:10 | Calculated | O410E |  |  |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 3 | 19353 | 816 | 0.04216 | 0.00015501 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6736 |  | 2004-10-22 09:49 | 2004-10-22 | 2004-10-22 15:01 | Calculated | O410E |  |  |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 312 | 16 | 19353 | 4992 | 0.25794 | 0.00082675 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6737 |  | 2004-10-22 10:23 | 2004-10-22 | 2004-10-22 15:28 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 43 | 19353 | 13115 | 0.67767 | 0.0022219 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6739 |  | 2004-10-23 19:18 | 2004-10-23 | 2004-10-23 19:31 | Calculated | O410E | C512 | Paper/Lead - Laid Direct |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Cables : Insulation | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 13 | 830 | 19353 | 11495 | 0.59396 | 0.042887 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6740 |  | 2004-10-24 19:29 | 2004-10-24 | 2004-10-24 19:32 | Calculated | O410E | C6125 | Drop-Out Fuses |  | Kuratau 406-01 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Fuse Carriers | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 3 | 1110 | 19353 | 3330 | 0.17207 | 0.057355 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6741 |  | 2004-10-26 09:39 | 2004-10-26 | 2004-10-26 14:43 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 304 | 15 | 19353 | 4560 | 0.23562 | 0.00077507 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6742 |  | 2004-10-26 11:52 | 2004-10-26 | 2004-10-26 16:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 252 | 1 | 19353 | 252 | 0.01302 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6743 |  | 2004-10-27 06:04 | 2004-10-27 | 2004-10-27 06:19 | Calculated | O410E | C754, 594 & 792 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 15 | 1572 | 19353 | 23580 | 1.2184 | 0.081228 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6745 |  | 2004-10-28 08:30 | 2004-10-28 | 2004-10-28 09:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 37 | 29 | 19353 | 1073 | 0.05544 | 0.0014985 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6746 |  | 2004-10-28 09:45 | 2004-10-28 | 2004-10-28 11:48 | Calculated | O410E |  |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 123 | 17 | 19353 | 2091 | 0.10805 | 0.00087842 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6747 |  | 2004-10-28 09:55 | 2004-10-28 | 2004-10-28 11:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-03 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 70 | 1 | 19353 | 70 | 0.00362 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6750 |  | 2004-10-28 16:10 | 2004-10-28 | 2004-10-28 17:18 | Calculated | O410E | C462 |  |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 88 | 19353 | 5984 | 0.3092 | 0.0045471 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6751 |  | 2004-10-29 09:34 | 2004-10-29 | 2004-10-29 11:57 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 143 | 29 | 19353 | 4170 | 0.21547 | 0.0014985 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6752 |  | 2004-10-29 09:55 | 2004-10-29 | 2004-10-29 11:10 | Calculated | O410E | LF |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 2 | 19353 | 150 | 0.00775 | 0.00010334 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6753 |  | 2004-10-29 10:17 | 2004-10-29 | 2004-10-29 14:38 | Calculated | O410E | LF | Pole Mounted |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 261 | 1 | 19353 | 261 | 0.01349 | 5.1672e-05 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6754 |  | 2004-10-30 09:30 | 2004-10-30 | 2004-10-30 12:00 | Calculated | O410E | LF |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 150 | 6 | 19353 | 900 | 0.0465 | 0.00031003 | 0 | 0 | 2004/2005 | October-2004 | 10 | 2004
6755 |  | 2004-11-01 08:30 | 2004-11-01 | 2004-11-01 12:50 | Calculated | O410E | LF |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 260 | 33 | 19353 | 8580 | 0.44334 | 0.0017052 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6756 |  | 2004-11-01 09:13 | 2004-11-01 | 2004-11-01 15:42 | Calculated | O410E |  |  |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 389 | 1 | 19353 | 389 | 0.0201 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6757 |  | 2004-11-01 09:25 | 2004-11-01 | 2004-11-01 09:41 | Calculated | O410E |  |  |  |  | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 136 | 19353 | 2259 | 0.11673 | 0.0070273 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6758 |  | 2004-11-01 09:52 | 2004-11-01 | 2004-11-01 14:00 | Calculated | O410E | LF |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 2 | 19353 | 496 | 0.02563 | 0.00010334 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6760 |  | 2004-11-01 14:29 | 2004-11-01 | 2004-11-01 14:51 | Calculated | O410E | LF | Single Circuit |  | Rangipo / Hautu 424-03 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 1 | 19353 | 22 | 0.00114 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6761 |  | 2004-11-02 09:35 | 2004-11-02 | 2004-11-02 13:19 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 224 | 6 | 19353 | 1344 | 0.06945 | 0.00031003 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6762 |  | 2004-11-02 12:40 | 2004-11-02 | 2004-11-02 13:10 | Calculated | O410E | LF |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 3 | 19353 | 90 | 0.00465 | 0.00015501 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6763 |  | 2004-11-03 07:10 | 2004-11-03 | 2004-11-03 10:56 | Calculated | O410E | LF |  |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 226 | 1 | 19353 | 226 | 0.01168 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6764 |  | 2004-11-03 08:03 | 2004-11-03 | 2004-11-03 11:54 | Calculated | O410E | L373 |  |  | National Park 411-02 | Remote Rural F | National Park | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 9 | 19353 | 2079 | 0.10743 | 0.00046504 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6765 |  | 2004-11-03 09:18 | 2004-11-03 | 2004-11-03 11:55 | Calculated | O410E |  |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 157 | 66 | 19353 | 10403 | 0.53754 | 0.0034103 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6766 |  | 2004-11-03 12:00 | 2004-11-03 | 2004-11-03 13:55 | Calculated | O410E | C1616 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 15 | 19353 | 1725 | 0.08913 | 0.00077507 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6767 |  | 2004-11-03 12:15 | 2004-11-03 | 2004-11-03 14:31 | Calculated | O410E | C961 |  |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 106 | 19353 | 14416 | 0.7449 | 0.0054772 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6770 |  | 2004-11-04 10:52 | 2004-11-04 | 2004-11-04 11:29 | Calculated | O410E | LF |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 3 | 19353 | 111 | 0.00574 | 0.00015501 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6771 |  | 2004-11-04 12:58 | 2004-11-04 | 2004-11-04 13:29 | Calculated | O410E | S437 | Drop-Out Fuses |  | Coast 125-05 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 31 | 108 | 19353 | 3414 | 0.17641 | 0.0055805 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6773 |  | 2004-11-05 09:42 | 2004-11-05 | 2004-11-05 15:12 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 18 | 19353 | 5940 | 0.30693 | 0.00093009 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6774 |  | 2004-11-05 11:43 | 2004-11-05 | 2004-11-05 11:57 | Calculated | O410E | LF |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 14 | 1 | 19353 | 14 | 0.00072 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6775 |  | 2004-11-05 12:55 | 2004-11-05 | 2004-11-05 15:52 | Calculated | O410E | LF | Pole Mounted |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 1 | 19353 | 177 | 0.00915 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6777 |  | 2004-11-08 09:34 | 2004-11-08 | 2004-11-08 14:51 | Calculated | O410E |  |  |  | Caves 101-05 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 317 | 9 | 19353 | 2853 | 0.14742 | 0.00046504 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6778 |  | 2004-11-08 12:14 | 2004-11-08 | 2004-11-08 13:46 | Calculated | O410E | LF |  |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 19353 | 92 | 0.00475 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6780 |  | 2004-11-09 08:49 | 2004-11-09 | 2004-11-09 15:18 | Calculated | O410E | LF | Pole Mounted |  | Caves 101-13 | Remote Rural F | Caves | Hangatiki Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 389 | 1 | 19353 | 389 | 0.0201 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6781 |  | 2004-11-09 09:32 | 2004-11-09 | 2004-11-09 14:49 | Calculated | O410E |  |  |  | Caves 101-05 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 317 | 9 | 19353 | 2853 | 0.14742 | 0.00046504 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6784 |  | 2004-11-10 08:10 | 2004-11-10 | 2004-11-10 10:32 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 142 | 1 | 19353 | 142 | 0.00734 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6786 |  | 2004-11-10 10:25 | 2004-11-10 | 2004-11-10 11:55 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 43 | 19353 | 3873 | 0.20012 | 0.0022219 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6787 |  | 2004-11-10 11:42 | 2004-11-10 | 2004-11-10 13:27 | Calculated | O410E | C1721 |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 16 | 19353 | 1688 | 0.08722 | 0.00082675 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6789 |  | 2004-11-11 08:58 | 2004-11-11 | 2004-11-11 13:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 275 | 1 | 19353 | 275 | 0.01421 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6790 |  | 2004-11-11 09:16 | 2004-11-11 | 2004-11-11 09:19 | Calculated | O410E |  |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 50 | 19353 | 150 | 0.00775 | 0.0025836 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6791 |  | 2004-11-11 09:37 | 2004-11-11 | 2004-11-11 16:49 | Calculated | O410E |  |  |  | Caves 101-05 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 432 | 13 | 19353 | 5616 | 0.29019 | 0.00067173 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6792 |  | 2004-11-11 10:14 | 2004-11-11 | 2004-11-11 14:39 | Calculated | O410E | C402 |  |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 265 | 16 | 19353 | 4253 | 0.21976 | 0.00082675 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6793 |  | 2004-11-12 09:00 | 2004-11-12 | 2004-11-12 14:43 | Calculated | O410E |  |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 343 | 562 | 19353 | 192766 | 9.9605 | 0.029039 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6794 |  | 2004-11-12 09:16 | 2004-11-12 | 2004-11-12 10:05 | Calculated | O410E |  |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 68 | 19353 | 3332 | 0.17217 | 0.0035137 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6795 |  | 2004-11-12 10:39 | 2004-11-12 | 2004-11-12 13:36 | Calculated | O410E |  |  |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 177 | 120 | 19353 | 21240 | 1.0975 | 0.0062006 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6796 |  | 2004-11-12 14:43 | 2004-11-12 | 2004-11-12 16:25 | Calculated | O410E | C108 | Sectionaliser |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Other | Asset Related | Other |  | Incorrect Protection Settings | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 102 | 28 | 19353 | 2856 | 0.14757 | 0.0014468 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6797 |  | 2004-11-12 17:31 | 2004-11-12 | 2004-11-12 18:20 | Calculated | O410E | C867 |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 387 | 19353 | 19253 | 0.99483 | 0.019997 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
25018 | Broken Pole 64 - Raurimu Feeder | 2004-11-14 05:55 | 2004-11-14 | 2004-11-14 07:46 | Calculated | 5543 | 5543 - Fused Link 5543 |  | 410SEG5543-5161 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 98 | 19353 | 10825 | 0.55934 | 0.0050638 | 600.8333 | 66372 | 2004/2005 | November-2004 | 11 | 2004
25020 | Broken Pole 64 - Raurimu Feeder | 2004-11-14 05:55 | 2004-11-14 | 2004-11-14 09:35 | Calculated | 5416 | 5416 - Fused Link 5416 |  | 410SEG5416-5490 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 74 | 19353 | 16240 | 0.83915 | 0.0038237 | 421.75 | 92560 | 2004/2005 | November-2004 | 11 | 2004
25021 | Broken Pole 64 - Raurimu Feeder | 2004-11-14 05:55 | 2004-11-14 | 2004-11-14 09:35 | Calculated | 5491 | 5491 - Fused Link 5491 |  | 410SEG5491-5494 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 51 | 19353 | 11192 | 0.57831 | 0.0026353 | 317.25 | 69625 | 2004/2005 | November-2004 | 11 | 2004
25022 | Broken Pole 64 - Raurimu Feeder | 2004-11-14 05:55 | 2004-11-14 | 2004-11-14 08:04 | Calculated | 5142 | 5142 - Circuit Breaker with Bypass 5142 |  | 410SEG6766-5141 | 501-01 National Park | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 333 | 19353 | 42779 | 2.2105 | 0.017207 | 2118.0833 | 272103 | 2004/2005 | November-2004 | 11 | 2004
25023 | Broken Pole 64 - Raurimu Feeder | 2004-11-14 05:55 | 2004-11-14 | 2004-11-14 13:10 | Calculated | 5141 | 5141 - Air Break Switch 5141 |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 434 | 323 | 19353 | 140332 | 7.2512 | 0.01669 | 2070.5833 | 899599 | 2004/2005 | November-2004 | 11 | 2004
6798 |  | 2004-11-14 11:23 | 2004-11-14 | 2004-11-14 13:07 | Calculated | O410E | C1345 | Single Circuit |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 25 | 19353 | 2612 | 0.13497 | 0.0012918 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6799 |  | 2004-11-14 18:36 | 2004-11-14 | 2004-11-15 12:36 | Calculated | O410E | C407 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1080 | 255 | 19353 | 88771 | 4.5869 | 0.013176 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6800 |  | 2004-11-14 23:00 | 2004-11-14 | 2004-11-15 06:50 | Calculated | O410E | C109 | Drop-Out Fuses |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 470 | 69 | 19353 | 32432 | 1.6758 | 0.0035653 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6801 |  | 2004-11-15 06:50 | 2004-11-15 | 2004-11-15 08:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-09 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6802 |  | 2004-11-15 06:52 | 2004-11-15 | 2004-11-15 09:44 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 172 | 10 | 19353 | 1722 | 0.08898 | 0.00051672 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6803 |  | 2004-11-15 08:52 | 2004-11-15 | 2004-11-15 10:21 | Calculated | O410E | LF |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 2 | 19353 | 178 | 0.0092 | 0.00010334 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6804 |  | 2004-11-15 11:51 | 2004-11-15 | 2004-11-15 14:32 | Calculated | O410E | C110 | Single Circuit |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Surge Diverters | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 84 | 19353 | 13571 | 0.70123 | 0.0043404 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6805 |  | 2004-11-15 19:37 | 2004-11-15 | 2004-11-16 14:26 | Calculated | O410E | L299 | Single Circuit |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1129 | 2 | 19353 | 2258 | 0.11667 | 0.00010334 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6806 |  | 2004-11-15 20:45 | 2004-11-15 | 2004-11-15 21:24 | Calculated | O410E | S217 | Single Circuit |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 26 | 19353 | 1014 | 0.05239 | 0.0013435 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6807 |  | 2004-11-15 22:25 | 2004-11-15 | 2004-11-16 09:18 | Calculated | O410E | S473 | Single Circuit |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Pole - Pre-Stressed Concrete | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 653 | 26 | 19353 | 16978 | 0.87728 | 0.0013435 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6809 |  | 2004-11-17 09:45 | 2004-11-17 | 2004-11-17 12:58 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 193 | 8 | 19353 | 1544 | 0.07978 | 0.00041337 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6810 |  | 2004-11-17 10:14 | 2004-11-17 | 2004-11-17 15:40 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 326 | 26 | 19353 | 8476 | 0.43797 | 0.0013435 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6811 |  | 2004-11-17 12:15 | 2004-11-17 | 2004-11-17 12:37 | Calculated | O410E | C955 | Auto-Recloser |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Switch Connections (O/H) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 22 | 1092 | 19353 | 24824 | 1.2827 | 0.056425 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6812 |  | 2004-11-18 10:42 | 2004-11-18 | 2004-11-18 11:46 | Calculated | O410E | C466 |  |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 45 | 19353 | 2880 | 0.14881 | 0.0023252 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6813 |  | 2004-11-18 23:31 | 2004-11-18 | 2004-11-18 23:40 | Calculated | O410E | C952 |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 939 | 19353 | 8451 | 0.43668 | 0.04852 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6814 |  | 2004-11-19 07:28 | 2004-11-19 | 2004-11-19 07:32 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 1 | 19353 | 4 | 0.00021 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6815 |  | 2004-11-19 10:00 | 2004-11-19 | 2004-11-19 14:14 | Calculated | O410E |  |  |  | Caves 101-02 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 254 | 51 | 19353 | 12954 | 0.66935 | 0.0026353 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6816 |  | 2004-11-19 22:55 | 2004-11-19 | 2004-11-19 23:36 | Calculated | O410E | L778 | Drop-Out Fuses |  | Southern 409-03 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 41 | 19 | 19353 | 779 | 0.04025 | 0.00098176 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6817 |  | 2004-11-20 03:48 | 2004-11-20 | 2004-11-20 05:24 | Calculated | O410E | C113 |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 42 | 19353 | 4045 | 0.20901 | 0.0021702 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6819 |  | 2004-11-22 09:12 | 2004-11-22 | 2004-11-22 11:24 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 132 | 50 | 19353 | 6600 | 0.34103 | 0.0025836 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6820 |  | 2004-11-22 09:42 | 2004-11-22 | 2004-11-22 14:24 | Calculated | O410E |  |  |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 7 | 19353 | 1974 | 0.102 | 0.0003617 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6822 |  | 2004-11-23 09:02 | 2004-11-23 | 2004-11-23 14:13 | Calculated | O410E |  |  |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 311 | 2 | 19353 | 622 | 0.03214 | 0.00010334 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6823 |  | 2004-11-23 09:41 | 2004-11-23 | 2004-11-23 11:00 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 79 | 50 | 19353 | 3953 | 0.20426 | 0.0025836 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6828 |  | 2004-11-24 09:02 | 2004-11-24 | 2004-11-24 14:14 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 312 | 33 | 19353 | 10296 | 0.53201 | 0.0017052 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6829 |  | 2004-11-24 09:32 | 2004-11-24 | 2004-11-24 13:04 | Calculated | O410E |  |  |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 212 | 7 | 19353 | 1484 | 0.07668 | 0.0003617 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6830 |  | 2004-11-24 09:34 | 2004-11-24 | 2004-11-24 11:53 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 69 | 19353 | 9641 | 0.49817 | 0.0035653 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6831 |  | 2004-11-24 10:00 | 2004-11-24 | 2004-11-24 11:50 | Calculated | O410E |  |  |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 110 | 3 | 19353 | 330 | 0.01705 | 0.00015501 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6832 |  | 2004-11-24 11:46 | 2004-11-24 | 2004-11-24 12:14 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 22 | 19353 | 616 | 0.03183 | 0.0011368 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6833 |  | 2004-11-24 12:47 | 2004-11-24 | 2004-11-24 14:17 | Calculated | O410E | S281 | Single Circuit |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 40 | 19353 | 3600 | 0.18602 | 0.0020669 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6834 |  | 2004-11-25 09:32 | 2004-11-25 | 2004-11-25 12:00 | Calculated | O410E |  |  |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 25 | 19353 | 3700 | 0.19118 | 0.0012918 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6835 |  | 2004-11-25 10:00 | 2004-11-25 | 2004-11-25 10:53 | Calculated | O410E | LF |  |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 53 | 1 | 19353 | 53 | 0.00274 | 5.1672e-05 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6836 |  | 2004-11-25 11:30 | 2004-11-25 | 2004-11-25 14:02 | Calculated | O410E |  |  |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 152 | 27 | 19353 | 4104 | 0.21206 | 0.0013951 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6837 |  | 2004-11-26 09:26 | 2004-11-26 | 2004-11-26 14:33 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 10 | 19353 | 3070 | 0.15863 | 0.00051672 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6838 |  | 2004-11-26 09:30 | 2004-11-26 | 2004-11-26 10:48 | Calculated | O410E | LF |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 78 | 4 | 19353 | 312 | 0.01612 | 0.00020669 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6840 |  | 2004-11-26 14:04 | 2004-11-26 | 2004-11-26 15:29 | Calculated | O410E | C1717 |  |  | Mokauiti 115-04 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 17 | 19353 | 1445 | 0.07467 | 0.00087842 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6841 |  | 2004-11-26 16:57 | 2004-11-26 | 2004-11-26 17:27 | Calculated | O410E | S1701 | Single Circuit |  | Mokauiti 115-02 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 131 | 19353 | 3930 | 0.20307 | 0.006769 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6842 |  | 2004-11-28 12:15 | 2004-11-28 | 2004-11-28 14:23 | Calculated | O410E | S634 | Single Circuit |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Crossarm - Wood | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 29 | 19353 | 3712 | 0.1918 | 0.0014985 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6843 |  | 2004-11-29 09:03 | 2004-11-29 | 2004-11-29 13:56 | Calculated | O410E |  |  |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 293 | 6 | 19353 | 1758 | 0.09084 | 0.00031003 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6845 |  | 2004-11-29 14:10 | 2004-11-29 | 2004-11-29 15:23 | Calculated | O410E | L602 | Single Circuit |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Stay Wire | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 8 | 19353 | 584 | 0.03018 | 0.00041337 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6846 |  | 2004-11-30 12:30 | 2004-11-30 | 2004-11-30 15:05 | Calculated | O410E |  |  |  | Ohura 413-01 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 155 | 273 | 19353 | 42315 | 2.1865 | 0.014106 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6847 |  | 2004-11-30 13:35 | 2004-11-30 | 2004-11-30 13:52 | Calculated | O410E | LF |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 5 | 19353 | 85 | 0.00439 | 0.00025836 | 0 | 0 | 2004/2005 | November-2004 | 11 | 2004
6849 |  | 2004-12-01 12:10 | 2004-12-01 | 2004-12-01 12:10 | Calculated | O410E | LF |  |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 1 | 19353 | 98 | 0.00506 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6850 |  | 2004-12-02 09:02 | 2004-12-02 | 2004-12-02 14:37 | Calculated | O410E |  |  |  | Southern 409-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 335 | 33 | 19353 | 11055 | 0.57123 | 0.0017052 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6852 |  | 2004-12-02 14:40 | 2004-12-02 | 2004-12-02 16:15 | Calculated | O410E |  |  |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 2 | 19353 | 190 | 0.00982 | 0.00010334 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6853 |  | 2004-12-03 12:30 | 2004-12-03 | 2004-12-03 15:30 | Calculated | O410E |  |  |  | Otorohanga 112-07 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 180 | 36 | 19353 | 6480 | 0.33483 | 0.0018602 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6854 |  | 2004-12-03 13:29 | 2004-12-03 | 2004-12-03 14:21 | Calculated | O410E | LF |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 3 | 19353 | 156 | 0.00806 | 0.00015501 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6856 |  | 2004-12-05 04:30 | 2004-12-05 | 2004-12-05 09:45 | Calculated | O410E | C584 | Single Circuit |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 315 | 66 | 19353 | 20790 | 1.0742 | 0.0034103 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6858 |  | 2004-12-05 14:55 | 2004-12-05 | 2004-12-05 15:05 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1 | 19353 | 10 | 0.00052 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6859 |  | 2004-12-05 15:05 | 2004-12-05 | 2004-12-05 15:06 | Calculated | O410E | C262 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | December-2004 | 12 | 2004
6860 |  | 2004-12-06 10:01 | 2004-12-06 | 2004-12-06 11:15 | Calculated | O410E | LF |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 74 | 1 | 19353 | 74 | 0.00382 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6862 |  | 2004-12-07 10:11 | 2004-12-07 | 2004-12-07 12:03 | Calculated | O410E |  |  |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 170 | 19353 | 19040 | 0.98383 | 0.0087842 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6863 |  | 2004-12-07 10:43 | 2004-12-07 | 2004-12-07 13:57 | Calculated | O410E | LF |  |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 194 | 4 | 19353 | 776 | 0.0401 | 0.00020669 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6869 |  | 2004-12-09 00:29 | 2004-12-09 | 2004-12-09 01:14 | Calculated | O410E | C296 | Single Circuit |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Jumper - Insulated ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 137 | 19353 | 6165 | 0.31856 | 0.007079 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6866 |  | 2004-12-09 09:00 | 2004-12-09 | 2004-12-09 15:40 | Calculated | O410E |  |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 400 | 486 | 19353 | 194400 | 10.045 | 0.025112 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6867 |  | 2004-12-09 09:33 | 2004-12-09 | 2004-12-09 10:24 | Calculated | O410E | LF |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 9 | 19353 | 459 | 0.02372 | 0.00046504 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
25015 | Jumper Off Tx 524 - Marakopa Rd | 2004-12-10 00:30 | 2004-12-10 | 2004-12-10 01:14 | Calculated | 296 | 296 - Recloser with Bypass 296 |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 169 | 19353 | 7537 | 0.38945 | 0.0087325 | 1185 | 52850 | 2004/2005 | December-2004 | 12 | 2004
6870 |  | 2004-12-10 09:06 | 2004-12-10 | 2004-12-10 09:08 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 240 | 19353 | 480 | 0.0248 | 0.012401 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6871 |  | 2004-12-10 10:11 | 2004-12-10 | 2004-12-10 14:31 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 260 | 1 | 19353 | 260 | 0.01343 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6872 |  | 2004-12-10 10:18 | 2004-12-10 | 2004-12-10 11:45 | Calculated | O410E | L616 | Drop-Out Fuses |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 87 | 100 | 19353 | 8700 | 0.44954 | 0.0051672 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6873 |  | 2004-12-11 08:59 | 2004-12-11 | 2004-12-11 09:07 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1 | 19353 | 8 | 0.00041 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6874 |  | 2004-12-11 15:10 | 2004-12-11 | 2004-12-11 15:12 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 240 | 19353 | 480 | 0.0248 | 0.012401 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6875 |  | 2004-12-12 00:03 | 2004-12-12 | 2004-12-12 01:03 | Calculated | O410E | S236 | Single Circuit |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 18 | 19353 | 1080 | 0.05581 | 0.00093009 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6877 |  | 2004-12-13 10:02 | 2004-12-13 | 2004-12-13 12:21 | Calculated | O410E |  |  |  | Caves 101-02 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 54 | 19353 | 7519 | 0.38852 | 0.0027903 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6878 |  | 2004-12-13 11:00 | 2004-12-13 | 2004-12-13 14:35 | Calculated | O410E | LF |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 215 | 1 | 19353 | 85 | 0.00439 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6880 |  | 2004-12-14 10:05 | 2004-12-14 | 2004-12-14 14:51 | Calculated | O410E |  |  |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 286 | 30 | 19353 | 8580 | 0.44334 | 0.0015501 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6881 |  | 2004-12-15 09:04 | 2004-12-15 | 2004-12-15 15:27 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 383 | 3 | 19353 | 1149 | 0.05937 | 0.00015501 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6882 |  | 2004-12-15 10:38 | 2004-12-15 | 2004-12-15 11:32 | Calculated | O410E | LF |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 3 | 19353 | 162 | 0.00837 | 0.00015501 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6883 |  | 2004-12-15 14:34 | 2004-12-15 | 2004-12-15 14:44 | Calculated | O410E | LF |  |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 10 | 2 | 19353 | 20 | 0.00103 | 0.00010334 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6884 |  | 2004-12-15 22:26 | 2004-12-15 | 2004-12-15 22:33 | Calculated | O410E | C120 |  |  | Gravel Scoop 109-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 329 | 19353 | 2303 | 0.119 | 0.017 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6885 |  | 2004-12-15 22:43 | 2004-12-15 | 2004-12-15 23:26 | Calculated | O410E | C107 | Single Circuit |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 342 | 19353 | 13102 | 0.677 | 0.017672 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6886 |  | 2004-12-16 00:37 | 2004-12-16 | 2004-12-16 01:39 | Calculated | O410E | S672 & 670 | All Others |  |  | Remote Rural F | Whakamaru 33 | Direct from Whakamaru Supply | Miscellaneous : SCADA Out Station | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 62 | 539 | 19353 | 33418 | 1.7268 | 0.027851 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6887 |  | 2004-12-16 05:26 | 2004-12-16 | 2004-12-16 07:21 | Calculated | O410E | L674 | Drop-Out Fuses |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 115 | 13 | 19353 | 1495 | 0.07725 | 0.00067173 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6888 |  | 2004-12-16 08:03 | 2004-12-16 | 2004-12-16 10:04 | Calculated | O410E | L499 | Drop-Out Fuses |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 121 | 6 | 19353 | 730 | 0.03772 | 0.00031003 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6889 |  | 2004-12-16 08:59 | 2004-12-16 | 2004-12-16 09:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 60 | 1 | 19353 | 60 | 0.0031 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6890 |  | 2004-12-16 10:10 | 2004-12-16 | 2004-12-16 10:44 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 34 | 1 | 19353 | 34 | 0.00176 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6891 |  | 2004-12-16 10:19 | 2004-12-16 | 2004-12-16 11:17 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 58 | 3 | 19353 | 174 | 0.00899 | 0.00015501 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6892 |  | 2004-12-16 11:05 | 2004-12-16 | 2004-12-16 13:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 3 | 19353 | 381 | 0.01969 | 0.00015501 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6893 |  | 2004-12-17 10:04 | 2004-12-17 | 2004-12-17 12:18 | Calculated | O410E | LV |  |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 134 | 48 | 19353 | 6432 | 0.33235 | 0.0024802 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6894 |  | 2004-12-17 12:34 | 2004-12-17 | 2004-12-17 12:56 | Calculated | O410E | L1533 |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 22 | 3 | 19353 | 66 | 0.00341 | 0.00015501 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6895 |  | 2004-12-17 13:41 | 2004-12-17 | 2004-12-17 15:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 129 | 1 | 19353 | 129 | 0.00667 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6896 |  | 2004-12-17 21:27 | 2004-12-17 | 2004-12-17 22:30 | Calculated | O410E | L170 | ABS |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 46 | 19353 | 2917 | 0.15073 | 0.0023769 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6898 |  | 2004-12-18 08:17 | 2004-12-18 | 2004-12-18 09:30 | Calculated | O410E | C222 | 11kv Under 33kv |  |  | Remote Rural F | Te Waireka Rd 33 | Direct from Hangatiki Supply | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6899 |  | 2004-12-18 14:00 | 2004-12-18 | 2004-12-18 14:59 | Calculated | O410E | C1108 | Single Circuit |  | Aria 114-03 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 39 | 19353 | 2301 | 0.1189 | 0.0020152 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6900 |  | 2004-12-18 14:49 | 2004-12-18 | 2004-12-18 14:50 | Calculated | O410E | C262 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | December-2004 | 12 | 2004
6901 |  | 2004-12-18 15:30 | 2004-12-18 | 2004-12-18 18:46 | Calculated | O410E | C560 | Sectionaliser |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Mechanism | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 196 | 15 | 19353 | 2940 | 0.15191 | 0.00077507 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6902 |  | 2004-12-19 01:40 | 2004-12-19 | 2004-12-19 10:28 | Calculated | O410E | C305 |  |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 528 | 15 | 19353 | 7930 | 0.40976 | 0.00077507 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6903 |  | 2004-12-19 17:06 | 2004-12-19 | 2004-12-19 17:16 | Calculated | O410E | C122 |  |  | Gravel Scoop 109-01 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 438 | 19353 | 4380 | 0.22632 | 0.022632 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6904 |  | 2004-12-19 17:47 | 2004-12-19 | 2004-12-19 17:49 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 327 | 19353 | 654 | 0.03379 | 0.016897 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6905 |  | 2004-12-20 07:39 | 2004-12-20 | 2004-12-20 17:30 | Calculated | O410E | LF | Pole Mounted |  | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 591 | 1 | 19353 | 591 | 0.03054 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6906 |  | 2004-12-20 10:59 | 2004-12-20 | 2004-12-20 13:10 | Calculated | O410E |  |  |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 131 | 148 | 19353 | 19388 | 1.0018 | 0.0076474 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6907 |  | 2004-12-21 09:40 | 2004-12-21 | 2004-12-21 11:28 | Calculated | O410E | LF | Drop-Out Fuses |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Bushings (fixed Insulation) | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 108 | 148 | 19353 | 16035 | 0.82855 | 0.0076474 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6908 |  | 2004-12-21 17:13 | 2004-12-21 | 2004-12-21 22:32 | Calculated | O410E | C564 | Sectionaliser |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Tank | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 319 | 12 | 19353 | 3828 | 0.1978 | 0.00062006 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6909 |  | 2004-12-22 05:05 | 2004-12-22 | 2004-12-22 06:08 | Calculated | O410E | C513 | Single Circuit |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 407 | 19353 | 25790 | 1.3326 | 0.02103 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6910 |  | 2004-12-22 09:18 | 2004-12-22 | 2004-12-22 14:06 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 288 | 3 | 19353 | 864 | 0.04464 | 0.00015501 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6911 |  | 2004-12-22 11:01 | 2004-12-22 | 2004-12-22 16:03 | Calculated | O410E |  | ABS |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply | Switchgear : Switch Connections (O/H) | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 33kV | 33000 |  | 302 | 76 | 19353 | 22952 | 1.186 | 0.003927 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6912 |  | 2004-12-22 13:40 | 2004-12-22 | 2004-12-23 11:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-01 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 1326 | 1 | 19353 | 1326 | 0.06852 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6913 |  | 2004-12-23 09:30 | 2004-12-23 | 2004-12-23 10:51 | Calculated | O410E | LF |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 32 | 19353 | 2592 | 0.13393 | 0.0016535 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6914 |  | 2004-12-27 15:51 | 2004-12-27 | 2004-12-27 16:23 | Calculated | O410E | S336 | Drop-Out Fuses |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 32 | 85 | 19353 | 2720 | 0.14055 | 0.0043921 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6915 |  | 2004-12-29 08:04 | 2004-12-29 | 2004-12-29 09:37 | Calculated | O410E | LF | Drop-Out Fuses |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 7 | 19353 | 651 | 0.03364 | 0.0003617 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6916 |  | 2004-12-29 08:05 | 2004-12-29 | 2004-12-29 10:31 | Calculated | O410E | LF | Single Circuit |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Surge Diverters | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 1 | 19353 | 146 | 0.00754 | 5.1672e-05 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6917 |  | 2004-12-29 14:37 | 2004-12-29 | 2004-12-29 15:30 | Calculated | O410E | LF |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 6 | 19353 | 318 | 0.01643 | 0.00031003 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6918 |  | 2004-12-29 17:30 | 2004-12-29 | 2004-12-29 17:45 | Calculated | O410E | L1297 | Drop-Out Fuses |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 15 | 47 | 19353 | 719 | 0.03715 | 0.0024286 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6919 |  | 2004-12-30 08:03 | 2004-12-30 | 2004-12-30 09:01 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 58 | 3 | 19353 | 174 | 0.00899 | 0.00015501 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6920 |  | 2004-12-30 09:25 | 2004-12-30 | 2004-12-30 10:21 | Calculated | O410E | C507 |  |  | Ohura 413-03 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 4 | 19353 | 224 | 0.01157 | 0.00020669 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6921 |  | 2004-12-31 09:41 | 2004-12-31 | 2004-12-31 10:48 | Calculated | O410E | LF |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 2 | 19353 | 134 | 0.00692 | 0.00010334 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6922 |  | 2004-12-31 18:49 | 2004-12-31 | 2004-12-31 20:53 | Calculated | O410E | C714 | ABS |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 124 | 49 | 19353 | 6106 | 0.31551 | 0.0025319 | 0 | 0 | 2004/2005 | December-2004 | 12 | 2004
6923 |  | 2005-01-03 21:30 | 2005-01-03 | 2005-01-04 01:19 | Calculated | O410E | LF | Pole Mounted |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 229 | 2 | 19353 | 458 | 0.02367 | 0.00010334 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6924 |  | 2005-01-05 14:31 | 2005-01-05 | 2005-01-05 14:45 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 6 | 19353 | 84 | 0.00434 | 0.00031003 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6925 |  | 2005-01-05 15:00 | 2005-01-05 | 2005-01-05 15:25 | Calculated | O410E | LF |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 27 | 19353 | 675 | 0.03488 | 0.0013951 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6926 |  | 2005-01-05 20:06 | 2005-01-05 | 2005-01-06 01:30 | Calculated | O410E | C1126 | Single Circuit |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Insulator - Pin | Weather | Lightning |  | Lightning Damage to Structure/Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 324 | 19 | 19353 | 6156 | 0.31809 | 0.00098176 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6927 |  | 2005-01-09 08:36 | 2005-01-09 | 2005-01-09 09:01 | Calculated | O410E | LF | Single Circuit |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 19 | 19353 | 475 | 0.02454 | 0.00098176 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6928 |  | 2005-01-10 09:30 | 2005-01-10 | 2005-01-10 10:49 | Calculated | O410E |  |  |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 79 | 147 | 19353 | 11733 | 0.60626 | 0.0075957 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6930 |  | 2005-01-10 15:21 | 2005-01-10 | 2005-01-10 18:45 | Calculated | O410E | C1716 & 1717 | Double Circuit |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 204 | 40 | 19353 | 8160 | 0.42164 | 0.0020669 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6931 |  | 2005-01-12 01:27 | 2005-01-12 | 2005-01-12 01:37 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 2 | 19353 | 20 | 0.00103 | 0.00010334 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6959 |  | 2005-01-12 08:29 | 2005-01-12 | 2005-01-12 08:30 | Calculated | O410E |  |  |  | Benneydale 103-01 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | January-2005 | 1 | 2005
6932 |  | 2005-01-12 10:00 | 2005-01-12 | 2005-01-12 11:13 | Calculated | O410E | LF |  |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 3 | 19353 | 219 | 0.01132 | 0.00015501 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6933 |  | 2005-01-13 09:09 | 2005-01-13 | 2005-01-13 09:33 | Calculated | O410E |  |  |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 24 | 26 | 19353 | 635 | 0.03281 | 0.0013435 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6934 |  | 2005-01-13 13:44 | 2005-01-13 | 2005-01-13 14:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 2 | 19353 | 126 | 0.00651 | 0.00010334 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6936 |  | 2005-01-17 10:05 | 2005-01-17 | 2005-01-17 13:44 | Calculated | O410E |  |  |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 219 | 5 | 19353 | 1095 | 0.05658 | 0.00025836 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6937 |  | 2005-01-17 10:55 | 2005-01-17 | 2005-01-17 14:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 188 | 1 | 19353 | 188 | 0.00971 | 5.1672e-05 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6939 |  | 2005-01-17 11:35 | 2005-01-17 | 2005-01-17 13:15 | Calculated | O410E | LF |  |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 1 | 19353 | 100 | 0.00517 | 5.1672e-05 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6940 |  | 2005-01-18 08:05 | 2005-01-18 | 2005-01-18 09:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 62 | 1 | 19353 | 62 | 0.0032 | 5.1672e-05 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6941 |  | 2005-01-18 17:40 | 2005-01-18 | 2005-01-18 18:33 | Calculated | O410E | C109 |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 70 | 19353 | 3766 | 0.1946 | 0.003617 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6942 |  | 2005-01-19 09:27 | 2005-01-19 | 2005-01-19 10:26 | Calculated | O410E | LF |  |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 59 | 2 | 19353 | 118 | 0.0061 | 0.00010334 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6943 |  | 2005-01-19 10:04 | 2005-01-19 | 2005-01-19 14:14 | Calculated | O410E |  |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 15 | 19353 | 3750 | 0.19377 | 0.00077507 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6944 |  | 2005-01-20 09:11 | 2005-01-20 | 2005-01-20 12:48 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 217 | 2 | 19353 | 434 | 0.02243 | 0.00010334 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6945 |  | 2005-01-20 09:21 | 2005-01-20 | 2005-01-20 12:56 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 215 | 1 | 19353 | 215 | 0.01111 | 5.1672e-05 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6946 |  | 2005-01-20 10:06 | 2005-01-20 | 2005-01-20 10:52 | Calculated | O410E | LF |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 8 | 19353 | 368 | 0.01902 | 0.00041337 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6948 |  | 2005-01-20 13:03 | 2005-01-20 | 2005-01-20 15:09 | Calculated | O410E | LF |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 126 | 5 | 19353 | 630 | 0.03255 | 0.00025836 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6949 |  | 2005-01-20 13:24 | 2005-01-20 | 2005-01-20 14:37 | Calculated | O410E | LF |  |  | Tihoi 124-02 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6950 |  | 2005-01-20 13:27 | 2005-01-20 | 2005-01-20 15:42 | Calculated | O410E | LF |  |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 135 | 3 | 19353 | 405 | 0.02093 | 0.00015501 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6951 |  | 2005-01-21 14:20 | 2005-01-21 | 2005-01-21 14:53 | Calculated | O410E | LF |  |  | Aria 114-03 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 33 | 2 | 19353 | 66 | 0.00341 | 0.00010334 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6952 |  | 2005-01-21 18:39 | 2005-01-21 | 2005-01-21 22:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 239 | 5 | 19353 | 1195 | 0.06175 | 0.00025836 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6953 |  | 2005-01-22 07:30 | 2005-01-22 | 2005-01-22 08:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Fuse Carriers | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 59 | 8 | 19353 | 478 | 0.0247 | 0.00041337 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6954 |  | 2005-01-22 22:49 | 2005-01-22 | 2005-01-22 22:56 | Calculated | O410E | C1020 |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 224 | 19353 | 1568 | 0.08102 | 0.011574 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6956 |  | 2005-01-24 10:16 | 2005-01-24 | 2005-01-24 11:09 | Calculated | O410E | LF |  |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 53 | 3 | 19353 | 159 | 0.00822 | 0.00015501 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6957 |  | 2005-01-24 11:01 | 2005-01-24 | 2005-01-24 11:57 | Calculated | O410E |  |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 56 | 3 | 19353 | 168 | 0.00868 | 0.00015501 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6958 |  | 2005-01-24 11:07 | 2005-01-24 | 2005-01-24 14:33 | Calculated | O410E |  |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 206 | 15 | 19353 | 3090 | 0.15967 | 0.00077507 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6960 |  | 2005-01-25 10:03 | 2005-01-25 | 2005-01-25 13:07 | Calculated | O410E |  |  |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 184 | 60 | 19353 | 11040 | 0.57045 | 0.0031003 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6961 |  | 2005-01-25 10:24 | 2005-01-25 | 2005-01-25 16:01 | Calculated | O410E |  |  |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 337 | 38 | 19353 | 12806 | 0.66171 | 0.0019635 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6962 |  | 2005-01-25 14:31 | 2005-01-25 | 2005-01-25 16:15 | Calculated | O410E | C1021 | Outdoor Circuit Breaker - Pole Mounted |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Mechanism | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 104 | 98 | 19353 | 10232 | 0.5287 | 0.0050638 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6963 |  | 2005-01-26 06:20 | 2005-01-26 | 2005-01-26 08:09 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 109 | 5 | 19353 | 546 | 0.02821 | 0.00025836 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6965 |  | 2005-01-27 09:35 | 2005-01-27 | 2005-01-27 14:59 | Calculated | O410E |  |  |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 416 | 19353 | 135137 | 6.9827 | 0.021495 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6966 |  | 2005-01-27 10:32 | 2005-01-27 | 2005-01-27 12:49 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 137 | 14 | 19353 | 1918 | 0.09911 | 0.0007234 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6967 |  | 2005-01-28 07:45 | 2005-01-28 | 2005-01-28 09:53 | Calculated | O410E | L764 | Drop-Out Fuses |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 128 | 8 | 19353 | 1024 | 0.05291 | 0.00041337 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6968 |  | 2005-01-28 09:01 | 2005-01-28 | 2005-01-28 13:44 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 283 | 1 | 19353 | 283 | 0.01462 | 5.1672e-05 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6969 |  | 2005-01-28 10:05 | 2005-01-28 | 2005-01-28 15:17 | Calculated | O410E |  |  |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 312 | 20 | 19353 | 6240 | 0.32243 | 0.0010334 | 0 | 0 | 2004/2005 | January-2005 | 1 | 2005
6971 |  | 2005-02-01 07:30 | 2005-02-01 | 2005-02-01 10:54 | Calculated | O410E | L499 | Drop-Out Fuses |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 204 | 5 | 19353 | 1020 | 0.05271 | 0.00025836 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6973 |  | 2005-02-01 12:10 | 2005-02-01 | 2005-02-01 13:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 80 | 3 | 19353 | 240 | 0.0124 | 0.00015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6974 |  | 2005-02-01 13:30 | 2005-02-01 | 2005-02-01 14:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 76 | 2 | 19353 | 152 | 0.00785 | 0.00010334 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6975 |  | 2005-02-01 17:23 | 2005-02-01 | 2005-02-01 17:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 23 | 1 | 19353 | 23 | 0.00119 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6976 |  | 2005-02-02 01:30 | 2005-02-02 | 2005-02-02 01:40 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 68 | 19353 | 680 | 0.03514 | 0.0035137 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6977 |  | 2005-02-02 09:24 | 2005-02-02 | 2005-02-02 09:28 | Calculated | O410E | C1102 | Catenary |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply | Cables : Other | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 4 | 1410 | 19353 | 5640 | 0.29143 | 0.072857 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6978 |  | 2005-02-02 09:31 | 2005-02-02 | 2005-02-02 11:42 | Calculated | O410E |  |  |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 131 | 97 | 19353 | 12765 | 0.65959 | 0.0050121 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6979 |  | 2005-02-03 06:49 | 2005-02-03 | 2005-02-03 08:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 110 | 2 | 19353 | 220 | 0.01137 | 0.00010334 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6980 |  | 2005-02-03 07:51 | 2005-02-03 | 2005-02-03 09:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 89 | 2 | 19353 | 178 | 0.0092 | 0.00010334 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6981 |  | 2005-02-03 09:00 | 2005-02-03 | 2005-02-03 14:10 | Calculated | O410E |  |  |  | Aria 114-03 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 310 | 39 | 19353 | 12090 | 0.62471 | 0.0020152 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6982 |  | 2005-02-03 09:01 | 2005-02-03 | 2005-02-03 12:57 | Calculated | O410E |  |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 236 | 142 | 19353 | 33613 | 1.7368 | 0.0073374 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
25024 | Pole & Arm Replacement - Aria | 2005-02-03 09:02 | 2005-02-03 | 2005-02-03 14:10 | Calculated | 1107 | 1107 - Recloser with Bypass 1107 |  | 114SEG1107-1116 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 308 | 93 | 19353 | 28650 | 1.4804 | 0.0048055 | 731.8333 | 225453 | 2004/2005 | February-2005 | 2 | 2005
25035 | Pole & Arm Replacement - Aria | 2005-02-03 09:06 | 2005-02-03 | 2005-02-03 13:48 | Calculated | 1109 | 1109 - Air Break Switch 1109 |  | 114SEG1109-1110 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 270 | 19353 | 76157 | 3.9352 | 0.013951 | 1958.1026 | 552315 | 2004/2005 | February-2005 | 2 | 2005
6983 |  | 2005-02-03 09:51 | 2005-02-03 | 2005-02-03 13:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 240 | 2 | 19353 | 480 | 0.0248 | 0.00010334 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6984 |  | 2005-02-03 10:00 | 2005-02-03 | 2005-02-03 10:29 | Calculated | O410E | LF |  |  | Piopio 116-02 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 29 | 22 | 19353 | 638 | 0.03297 | 0.0011368 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6985 |  | 2005-02-03 13:40 | 2005-02-03 | 2005-02-03 15:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-05 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 1 | 19353 | 88 | 0.00455 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6986 |  | 2005-02-03 13:40 | 2005-02-03 | 2005-02-03 16:45 | Calculated | O410E | L245 | Single Circuit |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 97 | 19353 | 17945 | 0.92725 | 0.0050121 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6987 |  | 2005-02-03 16:10 | 2005-02-03 | 2005-02-03 20:00 | Calculated | O410E | LF | Single Circuit |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Surge Diverters | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 230 | 1 | 19353 | 230 | 0.01188 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6988 |  | 2005-02-04 08:05 | 2005-02-04 | 2005-02-04 09:30 | Calculated | O410E | L261 | Drop-Out Fuses |  | Caves 101-02 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 29 | 19353 | 2465 | 0.12737 | 0.0014985 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6989 |  | 2005-02-04 10:14 | 2005-02-04 | 2005-02-04 12:56 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 162 | 1 | 19353 | 162 | 0.00837 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6990 |  | 2005-02-04 12:20 | 2005-02-04 | 2005-02-04 14:32 | Calculated | O410E |  |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 132 | 97 | 19353 | 12804 | 0.6616 | 0.0050121 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6991 |  | 2005-02-04 13:03 | 2005-02-04 | 2005-02-04 14:14 | Calculated | O410E | L663 |  |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 5 | 19353 | 355 | 0.01834 | 0.00025836 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6992 |  | 2005-02-04 13:36 | 2005-02-04 | 2005-02-04 14:30 | Calculated | O410E | LF |  |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 19353 | 54 | 0.00279 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6993 |  | 2005-02-04 14:35 | 2005-02-04 | 2005-02-04 15:02 | Calculated | O410E | LF |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 63 | 19353 | 1701 | 0.08789 | 0.0032553 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6994 |  | 2005-02-04 15:33 | 2005-02-04 | 2005-02-04 17:39 | Calculated | O410E | C296 | Single Circuit |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Insulator - Kidney | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 137 | 19353 | 17396 | 0.89888 | 0.007079 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6996 |  | 2005-02-07 08:45 | 2005-02-07 | 2005-02-07 11:08 | Calculated | O410E |  |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 143 | 145 | 19353 | 20836 | 1.0766 | 0.0074924 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6997 |  | 2005-02-07 12:10 | 2005-02-07 | 2005-02-07 12:59 | Calculated | O410E | C599 |  |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation |  | Asset Related | Other |  | Accidental Contact, Damage or Interference by TLC Staff | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 30 | 19353 | 1470 | 0.07596 | 0.0015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6998 |  | 2005-02-07 15:31 | 2005-02-07 | 2005-02-07 18:19 | Calculated | O410E | C407 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Incorrect Protection Settings | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 30 | 19353 | 5040 | 0.26042 | 0.0015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
6999 |  | 2005-02-07 18:39 | 2005-02-07 | 2005-02-07 19:06 | Calculated | O410E | C599 | Single Circuit |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 30 | 19353 | 810 | 0.04185 | 0.0015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7000 |  | 2005-02-07 19:43 | 2005-02-07 | 2005-02-07 23:20 | Calculated | O410E | C1530 | Single Circuit |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 6 | 19353 | 1302 | 0.06728 | 0.00031003 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7001 |  | 2005-02-08 07:34 | 2005-02-08 | 2005-02-08 09:08 | Calculated | O410E | C5536 |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 7 | 19353 | 658 | 0.034 | 0.0003617 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7002 |  | 2005-02-08 09:01 | 2005-02-08 | 2005-02-08 13:54 | Calculated | O410E |  |  |  | Tokaanu 420-01 | Remote Rural F | Tokaanu | Tokaanu Village Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 293 | 61 | 19353 | 17908 | 0.92533 | 0.003152 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7003 |  | 2005-02-08 10:00 | 2005-02-08 | 2005-02-08 14:05 | Calculated | O410E |  |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 24 | 19353 | 5880 | 0.30383 | 0.0012401 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7004 |  | 2005-02-08 10:10 | 2005-02-08 | 2005-02-08 11:42 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 1 | 19353 | 92 | 0.00475 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7006 |  | 2005-02-08 11:55 | 2005-02-08 | 2005-02-08 12:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 51 | 1 | 19353 | 51 | 0.00264 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7007 |  | 2005-02-08 13:32 | 2005-02-08 | 2005-02-08 14:14 | Calculated | O410E | L604 | Drop-Out Fuses |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 42 | 16 | 19353 | 672 | 0.03472 | 0.00082675 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7009 |  | 2005-02-08 16:15 | 2005-02-08 | 2005-02-08 19:35 | Calculated | O410E | C536 |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 200 | 7 | 19353 | 1400 | 0.07234 | 0.0003617 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7010 |  | 2005-02-09 06:45 | 2005-02-09 | 2005-02-09 06:46 | Calculated | O410E | C761 & 570 |  |  |  | Remote Rural F | Te Kawa St 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | February-2005 | 2 | 2005
7011 |  | 2005-02-09 08:44 | 2005-02-09 | 2005-02-09 09:36 | Calculated | O410E | L197 | Drop-Out Fuses |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 52 | 158 | 19353 | 8216 | 0.42453 | 0.0081641 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7012 |  | 2005-02-09 09:07 | 2005-02-09 | 2005-02-09 15:36 | Calculated | O410E |  |  |  | Benneydale 103-01 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 389 | 15 | 19353 | 5835 | 0.3015 | 0.00077507 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7013 |  | 2005-02-09 10:00 | 2005-02-09 | 2005-02-09 14:37 | Calculated | O410E |  |  |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 277 | 5 | 19353 | 1385 | 0.07157 | 0.00025836 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7014 |  | 2005-02-09 14:25 | 2005-02-09 | 2005-02-09 14:55 | Calculated | O410E | C1021 | Outdoor Circuit Breaker - Pole Mounted |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Mechanism | Asset Related | Other |  | Incorrect Protection Settings | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 30 | 48 | 19353 | 1440 | 0.07441 | 0.0024802 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7017 |  | 2005-02-09 22:47 | 2005-02-09 | 2005-02-09 22:59 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 68 | 19353 | 816 | 0.04216 | 0.0035137 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7018 |  | 2005-02-10 09:30 | 2005-02-10 | 2005-02-10 11:15 | Calculated | O410E | LV |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 105 | 31 | 19353 | 3255 | 0.16819 | 0.0016018 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7019 |  | 2005-02-10 09:44 | 2005-02-10 | 2005-02-10 14:50 | Calculated | O410E | C6560 |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 306 | 21 | 19353 | 6426 | 0.33204 | 0.0010851 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7020 |  | 2005-02-10 14:48 | 2005-02-10 | 2005-02-10 15:21 | Calculated | O410E | C107 |  |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Asset Related | Other |  | Incorrect Protection Settings | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 342 | 19353 | 11382 | 0.58813 | 0.017672 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7022 |  | 2005-02-11 13:09 | 2005-02-11 | 2005-02-11 14:10 | Calculated | O410E |  |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 61 | 327 | 19353 | 19947 | 1.0307 | 0.016897 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7023 |  | 2005-02-13 15:27 | 2005-02-13 | 2005-02-13 16:31 | Calculated | O410E | C114 | Single Circuit |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Crossarm - Wood | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 240 | 19353 | 15540 | 0.80298 | 0.012401 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7024 |  | 2005-02-13 18:00 | 2005-02-13 | 2005-02-13 19:43 | Calculated | O410E | C427 | Single Circuit |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 52 | 19353 | 5362 | 0.27706 | 0.0026869 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7025 |  | 2005-02-14 09:06 | 2005-02-14 | 2005-02-14 10:40 | Calculated | O410E | C290 |  |  | Ohura 413-01 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 273 | 19353 | 25662 | 1.326 | 0.014106 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7026 |  | 2005-02-14 10:00 | 2005-02-14 | 2005-02-14 12:51 | Calculated | O410E |  |  |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 171 | 46 | 19353 | 7867 | 0.4065 | 0.0023769 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7027 |  | 2005-02-14 10:01 | 2005-02-14 | 2005-02-14 15:00 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 299 | 8 | 19353 | 2392 | 0.1236 | 0.00041337 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7028 |  | 2005-02-15 08:30 | 2005-02-15 | 2005-02-15 10:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-05 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 119 | 1 | 19353 | 119 | 0.00615 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7030 |  | 2005-02-15 10:05 | 2005-02-15 | 2005-02-15 10:47 | Calculated | O410E |  |  |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 36 | 19353 | 1522 | 0.07864 | 0.0018602 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7031 |  | 2005-02-15 10:21 | 2005-02-15 | 2005-02-15 16:04 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 343 | 69 | 19353 | 23667 | 1.2229 | 0.0035653 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7032 |  | 2005-02-15 11:04 | 2005-02-15 | 2005-02-15 14:06 | Calculated | O410E | LF |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 182 | 19 | 19353 | 3458 | 0.17868 | 0.00098176 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7033 |  | 2005-02-15 12:32 | 2005-02-15 | 2005-02-15 14:08 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 96 | 3 | 19353 | 288 | 0.01488 | 0.00015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7034 |  | 2005-02-15 12:33 | 2005-02-15 | 2005-02-15 14:31 | Calculated | O410E |  |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 118 | 24 | 19353 | 2832 | 0.14633 | 0.0012401 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7035 |  | 2005-02-16 07:13 | 2005-02-16 | 2005-02-16 13:50 | Calculated | O410E | L466 | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 397 | 16 | 19353 | 6352 | 0.32822 | 0.00082675 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7036 |  | 2005-02-16 10:13 | 2005-02-16 | 2005-02-16 13:46 | Calculated | O410E |  |  |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 213 | 3 | 19353 | 639 | 0.03302 | 0.00015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7037 |  | 2005-02-16 10:30 | 2005-02-16 | 2005-02-16 15:35 | Calculated | O410E | LF |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 1 | 19353 | 305 | 0.01576 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7039 |  | 2005-02-17 10:07 | 2005-02-17 | 2005-02-17 15:11 | Calculated | O410E | LF |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 304 | 4 | 19353 | 1216 | 0.06283 | 0.00020669 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7038 |  | 2005-02-17 10:32 | 2005-02-17 | 2005-02-17 10:59 | Calculated | O410E |  |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 27 | 69 | 19353 | 1871 | 0.09668 | 0.0035653 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7040 |  | 2005-02-17 12:40 | 2005-02-17 | 2005-02-17 12:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | February-2005 | 2 | 2005
7041 |  | 2005-02-18 09:05 | 2005-02-18 | 2005-02-18 14:59 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 5 | 19353 | 1770 | 0.09146 | 0.00025836 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7044 |  | 2005-02-18 10:05 | 2005-02-18 | 2005-02-18 11:28 | Calculated | O410E |  |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 83 | 81 | 19353 | 6735 | 0.34801 | 0.0041854 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7043 |  | 2005-02-18 10:10 | 2005-02-18 | 2005-02-18 12:28 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 138 | 106 | 19353 | 14628 | 0.75585 | 0.0054772 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7045 |  | 2005-02-18 10:37 | 2005-02-18 | 2005-02-18 11:19 | Calculated | O410E | LF |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Weather | EART2 |  | Earthquake | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 62 | 19353 | 2604 | 0.13455 | 0.0032036 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7047 |  | 2005-02-18 14:37 | 2005-02-18 | 2005-02-18 14:47 | Calculated | O410E | LF |  |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 3 | 19353 | 30 | 0.00155 | 0.00015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7050 |  | 2005-02-21 09:09 | 2005-02-21 | 2005-02-21 10:09 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 62 | 19353 | 3742 | 0.19336 | 0.0032036 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7051 |  | 2005-02-21 10:01 | 2005-02-21 | 2005-02-21 12:51 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 170 | 10 | 19353 | 1700 | 0.08784 | 0.00051672 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7052 |  | 2005-02-21 17:24 | 2005-02-21 | 2005-02-21 17:58 | Calculated | O410E |  | Single Circuit |  | Waihaha 426-01 | Remote Rural F | Waihaha | Kuratau Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 229 | 19353 | 7816 | 0.40387 | 0.011833 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7053 |  | 2005-02-22 09:08 | 2005-02-22 | 2005-02-22 09:55 | Calculated | O410E |  |  |  | Caves 101-05 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 47 | 12 | 19353 | 564 | 0.02914 | 0.00062006 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7055 |  | 2005-02-22 10:05 | 2005-02-22 | 2005-02-22 14:00 | Calculated | O410E |  |  |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 235 | 3 | 19353 | 705 | 0.03643 | 0.00015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7056 |  | 2005-02-22 10:33 | 2005-02-22 | 2005-02-22 15:15 | Calculated | O410E |  |  |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 18 | 19353 | 5076 | 0.26228 | 0.00093009 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7057 |  | 2005-02-22 11:01 | 2005-02-22 | 2005-02-22 14:28 | Calculated | O410E |  |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 207 | 5 | 19353 | 1035 | 0.05348 | 0.00025836 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7059 |  | 2005-02-23 07:03 | 2005-02-23 | 2005-02-23 07:04 | Calculated | O410E | LF |  |  | McDonalds 110-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | February-2005 | 2 | 2005
7062 |  | 2005-02-23 10:39 | 2005-02-23 | 2005-02-23 13:45 | Calculated | O410E | LF | Drop-Out Fuses |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 186 | 1 | 19353 | 186 | 0.00961 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7063 |  | 2005-02-23 11:35 | 2005-02-23 | 2005-02-23 12:00 | Calculated | O410E | LF |  |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 1 | 19353 | 25 | 0.00129 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7064 |  | 2005-02-23 13:30 | 2005-02-23 | 2005-02-23 14:52 | Calculated | O410E | LF |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 1 | 19353 | 82 | 0.00424 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7068 |  | 2005-02-24 09:27 | 2005-02-24 | 2005-02-24 13:56 | Calculated | O410E |  |  |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 7 | 19353 | 1883 | 0.0973 | 0.0003617 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7071 |  | 2005-02-24 12:42 | 2005-02-24 | 2005-02-24 14:17 | Calculated | O410E | LF |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 4 | 19353 | 380 | 0.01964 | 0.00020669 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7072 |  | 2005-02-25 08:40 | 2005-02-25 | 2005-02-25 15:16 | Calculated | O410E | LF |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 396 | 1 | 19353 | 396 | 0.02046 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7073 |  | 2005-02-25 10:03 | 2005-02-25 | 2005-02-25 11:09 | Calculated | O410E |  |  |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 66 | 19 | 19353 | 1254 | 0.0648 | 0.00098176 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7074 |  | 2005-02-26 09:00 | 2005-02-26 | 2005-02-26 12:04 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 184 | 3 | 19353 | 552 | 0.02852 | 0.00015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7075 |  | 2005-02-28 04:50 | 2005-02-28 | 2005-02-28 05:02 | Calculated | O410E | C961 |  |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 106 | 19353 | 1272 | 0.06573 | 0.0054772 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7076 |  | 2005-02-28 09:07 | 2005-02-28 | 2005-02-28 10:03 | Calculated | O410E | LF |  |  | Caves 101-05 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 56 | 3 | 19353 | 168 | 0.00868 | 0.00015501 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7077 |  | 2005-02-28 10:27 | 2005-02-28 | 2005-02-28 13:53 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 206 | 1 | 19353 | 206 | 0.01064 | 5.1672e-05 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7078 |  | 2005-02-28 10:45 | 2005-02-28 | 2005-02-28 14:18 | Calculated | O410E | LF |  |  | Caves 101-02 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 213 | 9 | 19353 | 1917 | 0.09905 | 0.00046504 | 0 | 0 | 2004/2005 | February-2005 | 2 | 2005
7079 |  | 2005-03-01 09:35 | 2005-03-01 | 2005-03-01 15:44 | Calculated | O410E |  |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 369 | 24 | 19353 | 8856 | 0.4576 | 0.0012401 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7080 |  | 2005-03-01 10:12 | 2005-03-01 | 2005-03-01 11:17 | Calculated | O410E | L339 | Single Circuit |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 8 | 19353 | 520 | 0.02687 | 0.00041337 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7081 |  | 2005-03-01 22:56 | 2005-03-01 | 2005-03-01 23:07 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 2 | 19353 | 23 | 0.00119 | 0.00010334 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7082 |  | 2005-03-02 08:30 | 2005-03-02 | 2005-03-02 13:11 | Calculated | O410E |  |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 381 | 19353 | 107099 | 5.534 | 0.019687 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7083 |  | 2005-03-02 09:52 | 2005-03-02 | 2005-03-02 11:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 68 | 2 | 19353 | 136 | 0.00703 | 0.00010334 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7088 |  | 2005-03-03 04:10 | 2005-03-03 | 2005-03-03 04:21 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 1 | 19353 | 11 | 0.00057 | 5.1672e-05 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7084 |  | 2005-03-03 09:00 | 2005-03-03 | 2005-03-03 09:15 | Calculated | O410E |  |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 15 | 43 | 19353 | 645 | 0.03333 | 0.0022219 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7085 |  | 2005-03-03 10:34 | 2005-03-03 | 2005-03-03 12:25 | Calculated | O410E | LF |  |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 111 | 2 | 19353 | 222 | 0.01147 | 0.00010334 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7087 |  | 2005-03-03 13:14 | 2005-03-03 | 2005-03-03 14:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 97 | 1 | 19353 | 97 | 0.00501 | 5.1672e-05 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7089 |  | 2005-03-04 06:58 | 2005-03-04 | 2005-03-04 07:20 | Calculated | O410E | LF |  |  | McDonalds 110-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 22 | 2 | 19353 | 44 | 0.00227 | 0.00010334 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7090 |  | 2005-03-04 08:45 | 2005-03-04 | 2005-03-04 09:31 | Calculated | O410E | C519 |  |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 21 | 19353 | 966 | 0.04991 | 0.0010851 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7091 |  | 2005-03-04 10:36 | 2005-03-04 | 2005-03-04 11:57 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 16 | 19353 | 1296 | 0.06697 | 0.00082675 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7093 |  | 2005-03-06 22:36 | 2005-03-06 | 2005-03-06 22:39 | Calculated | O410E | C1102 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 1412 | 19353 | 4236 | 0.21888 | 0.07296 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7094 |  | 2005-03-07 06:03 | 2005-03-07 | 2005-03-07 06:14 | Calculated | O410E | C961 |  |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 106 | 19353 | 1166 | 0.06025 | 0.0054772 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7095 |  | 2005-03-07 11:09 | 2005-03-07 | 2005-03-07 12:28 | Calculated | O410E | LF |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 5 | 19353 | 395 | 0.02041 | 0.00025836 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7096 |  | 2005-03-07 13:32 | 2005-03-07 | 2005-03-07 14:30 | Calculated | O410E | LF |  |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 1 | 19353 | 58 | 0.003 | 5.1672e-05 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7098 |  | 2005-03-07 23:58 | 2005-03-07 | 2005-03-08 00:58 | Calculated | O410E | C513 | Single Circuit |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 411 | 19353 | 24742 | 1.2785 | 0.021237 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7099 |  | 2005-03-08 10:09 | 2005-03-08 | 2005-03-08 14:12 | Calculated | O410E |  |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 243 | 62 | 19353 | 15066 | 0.77848 | 0.0032036 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7100 |  | 2005-03-08 11:16 | 2005-03-08 | 2005-03-08 13:32 | Calculated | O410E | LF |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 136 | 5 | 19353 | 680 | 0.03514 | 0.00025836 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7101 |  | 2005-03-09 10:00 | 2005-03-09 | 2005-03-09 13:32 | Calculated | O410E |  |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 212 | 8 | 19353 | 1696 | 0.08763 | 0.00041337 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7102 |  | 2005-03-09 10:02 | 2005-03-09 | 2005-03-09 10:41 | Calculated | O410E |  |  |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 39 | 44 | 19353 | 1716 | 0.08867 | 0.0022735 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7104 |  | 2005-03-10 10:00 | 2005-03-10 | 2005-03-10 12:09 | Calculated | O410E |  |  |  | Western 403-03 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 129 | 38 | 19353 | 4902 | 0.25329 | 0.0019635 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7105 |  | 2005-03-10 10:02 | 2005-03-10 | 2005-03-10 11:23 | Calculated | O410E |  |  |  | Otorohanga 112-07 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 36 | 19353 | 2916 | 0.15067 | 0.0018602 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7106 |  | 2005-03-10 11:11 | 2005-03-10 | 2005-03-10 12:25 | Calculated | O410E |  |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 74 | 27 | 19353 | 1998 | 0.10324 | 0.0013951 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7107 |  | 2005-03-10 12:36 | 2005-03-10 | 2005-03-10 14:24 | Calculated | O410E |  |  |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 24 | 19353 | 2592 | 0.13393 | 0.0012401 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7108 |  | 2005-03-11 10:02 | 2005-03-11 | 2005-03-11 14:24 | Calculated | O410E |  |  |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 262 | 10 | 19353 | 2620 | 0.13538 | 0.00051672 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7109 |  | 2005-03-11 10:04 | 2005-03-11 | 2005-03-11 14:32 | Calculated | O410E |  |  |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 36 | 19353 | 9648 | 0.49853 | 0.0018602 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7110 |  | 2005-03-11 15:07 | 2005-03-11 | 2005-03-11 16:44 | Calculated | O410E | L139 |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 62 | 19353 | 6014 | 0.31075 | 0.0032036 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7111 |  | 2005-03-12 02:53 | 2005-03-12 | 2005-03-12 02:56 | Calculated | O410E | C1102 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 1412 | 19353 | 4236 | 0.21888 | 0.07296 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7112 |  | 2005-03-12 17:08 | 2005-03-12 | 2005-03-12 18:40 | Calculated | O410E | L656 | Drop-Out Fuses |  | Whakamaru 120-03 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 79 | 19353 | 7295 | 0.37694 | 0.0040821 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7113 |  | 2005-03-13 12:58 | 2005-03-13 | 2005-03-13 14:52 | Calculated | O410E | C109 | Pole Mounted |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 70 | 19353 | 8016 | 0.4142 | 0.003617 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7115 |  | 2005-03-14 02:50 | 2005-03-14 | 2005-03-14 02:53 | Calculated | O410E | C1102 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 1412 | 19353 | 4236 | 0.21888 | 0.07296 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7116 |  | 2005-03-14 07:49 | 2005-03-14 | 2005-03-14 09:34 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 105 | 2 | 19353 | 210 | 0.01085 | 0.00010334 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7117 |  | 2005-03-14 09:32 | 2005-03-14 | 2005-03-14 10:53 | Calculated | O410E |  |  |  | Aria 114-03 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 39 | 19353 | 3192 | 0.16494 | 0.0020152 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7118 |  | 2005-03-14 11:36 | 2005-03-14 | 2005-03-14 12:33 | Calculated | O410E | LF | Pole Mounted |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 1 | 19353 | 57 | 0.00295 | 5.1672e-05 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7120 |  | 2005-03-15 10:33 | 2005-03-15 | 2005-03-15 13:18 | Calculated | O410E | LF |  |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 165 | 4 | 19353 | 660 | 0.0341 | 0.00020669 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7121 |  | 2005-03-15 12:34 | 2005-03-15 | 2005-03-15 12:35 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | March-2005 | 3 | 2005
7122 |  | 2005-03-16 10:03 | 2005-03-16 | 2005-03-16 15:05 | Calculated | O410E |  |  |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 35 | 19353 | 10570 | 0.54617 | 0.0018085 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7125 |  | 2005-03-16 14:44 | 2005-03-16 | 2005-03-16 16:24 | Calculated | O410E | C5961 |  |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 106 | 19353 | 10617 | 0.5486 | 0.0054772 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7126 |  | 2005-03-16 18:50 | 2005-03-16 | 2005-03-17 00:05 | Calculated | O410E | C417 | Single Circuit |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 315 | 40 | 19353 | 12600 | 0.65106 | 0.0020669 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7128 |  | 2005-03-17 10:12 | 2005-03-17 | 2005-03-17 11:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 86 | 1 | 19353 | 86 | 0.00444 | 5.1672e-05 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7129 |  | 2005-03-17 10:20 | 2005-03-17 | 2005-03-17 11:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 60 | 159 | 19353 | 9630 | 0.4976 | 0.0082158 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7130 |  | 2005-03-17 16:51 | 2005-03-17 | 2005-03-17 17:46 | Calculated | O410E | C5961 | Single Circuit |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 106 | 19353 | 5930 | 0.30641 | 0.0054772 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7132 |  | 2005-03-18 09:25 | 2005-03-18 | 2005-03-18 11:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 98 | 3 | 19353 | 294 | 0.01519 | 0.00015501 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7131 |  | 2005-03-18 09:29 | 2005-03-18 | 2005-03-18 11:04 | Calculated | O410E |  |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 111 | 19353 | 10604 | 0.54793 | 0.0057355 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
3980 |  | 2005-03-20 | 2005-03-20 | 2005-03-20 05:24 | Calculated | O410E |  |  |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 32 | 19353 | 10368 | 0.53573 | 0.0016535 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7133 |  | 2005-03-21 07:31 | 2005-03-21 | 2005-03-21 09:23 | Calculated | O410E | L252 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 112 | 6 | 19353 | 673 | 0.03477 | 0.00031003 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7134 |  | 2005-03-21 10:03 | 2005-03-21 | 2005-03-21 14:24 | Calculated | O410E |  |  |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 261 | 7 | 19353 | 1827 | 0.0944 | 0.0003617 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7135 |  | 2005-03-21 10:48 | 2005-03-21 | 2005-03-21 12:13 | Calculated | O410E | LF | Drop-Out Fuses |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 1 | 19353 | 85 | 0.00439 | 5.1672e-05 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7136 |  | 2005-03-21 17:46 | 2005-03-21 | 2005-03-21 17:49 | Calculated | O410E | C594 & 754 | Single Circuit |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 1574 | 19353 | 4722 | 0.24399 | 0.081331 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7138 |  | 2005-03-22 10:30 | 2005-03-22 | 2005-03-22 16:30 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 69 | 19353 | 24840 | 1.2835 | 0.0035653 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7140 |  | 2005-03-22 10:37 | 2005-03-22 | 2005-03-22 12:18 | Calculated | O410E |  |  |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 101 | 12 | 19353 | 1212 | 0.06263 | 0.00062006 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7143 |  | 2005-03-22 11:57 | 2005-03-22 | 2005-03-22 13:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 70 | 6 | 19353 | 420 | 0.0217 | 0.00031003 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7144 |  | 2005-03-23 08:03 | 2005-03-23 | 2005-03-23 11:50 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 227 | 3 | 19353 | 681 | 0.03519 | 0.00015501 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7145 |  | 2005-03-23 09:28 | 2005-03-23 | 2005-03-23 12:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 158 | 1 | 19353 | 158 | 0.00816 | 5.1672e-05 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7146 |  | 2005-03-23 10:33 | 2005-03-23 | 2005-03-23 12:21 | Calculated | O410E |  |  |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 19 | 19353 | 2052 | 0.10603 | 0.00098176 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7147 |  | 2005-03-24 07:29 | 2005-03-24 | 2005-03-24 07:52 | Calculated | O410E | C252 | Outdoor - Ground Mounted |  |  | Remote Rural F | Gadsby Rd 33 | Direct from Hangatiki Supply | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 23 | 412 | 19353 | 9867 | 0.50984 | 0.021289 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7148 |  | 2005-03-24 08:36 | 2005-03-24 | 2005-03-24 10:08 | Calculated | O410E | C355 |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 12 | 19353 | 1104 | 0.05705 | 0.00062006 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7150 |  | 2005-03-26 01:05 | 2005-03-26 | 2005-03-26 02:18 | Calculated | O410E | C102 | Single Circuit |  | Te Kuiti Town 105-01 | Remote Rural F | Te Kuiti Town | Waitete Zone Substation | OH Lines : Joint - Compression / Non-Tension | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 536 | 19353 | 39538 | 2.043 | 0.027696 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7151 |  | 2005-03-26 04:17 | 2005-03-26 | 2005-03-26 04:19 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 1 | 19353 | 2 | 0.0001 | 5.1672e-05 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7152 |  | 2005-03-26 07:40 | 2005-03-26 | 2005-03-26 10:58 | Calculated | O410E | C422 |  |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 24 | 19353 | 4752 | 0.24554 | 0.0012401 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7153 |  | 2005-03-26 17:01 | 2005-03-26 | 2005-03-26 18:09 | Calculated | O410E | L429 | Single Circuit |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 15 | 19353 | 1020 | 0.05271 | 0.00077507 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7154 |  | 2005-03-28 13:15 | 2005-03-28 | 2005-03-28 14:35 | Calculated | O410E | LF | Single Circuit |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 11 | 19353 | 880 | 0.04547 | 0.00056839 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7156 |  | 2005-03-29 12:35 | 2005-03-29 | 2005-03-29 13:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 62 | 2 | 19353 | 124 | 0.00641 | 0.00010334 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7157 |  | 2005-03-29 19:44 | 2005-03-29 | 2005-03-29 20:06 | Calculated | O410E | C961 |  |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 106 | 19353 | 2332 | 0.1205 | 0.0054772 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7158 |  | 2005-03-30 06:47 | 2005-03-30 | 2005-03-30 06:48 | Calculated | O410E | C570 - 761 |  |  |  | Remote Rural F | Te Kawa St 33 | Direct from Hangatiki Supply |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2004/2005 | March-2005 | 3 | 2005
7159 |  | 2005-03-30 11:00 | 2005-03-30 | 2005-03-30 12:51 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 111 | 9 | 19353 | 999 | 0.05162 | 0.00046504 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7160 |  | 2005-03-30 14:51 | 2005-03-30 | 2005-03-30 16:30 | Calculated | O410E | L1648 | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 40 | 19353 | 3960 | 0.20462 | 0.0020669 | 0 | 0 | 2004/2005 | March-2005 | 3 | 2005
7165 |  | 2005-04-02 09:25 | 2005-04-02 | 2005-04-02 15:32 | Calculated | O410E | L719 | Drop-Out Fuses |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 367 | 6 | 19353 | 2202 | 0.11378 | 0.00031003 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7166 |  | 2005-04-02 18:02 | 2005-04-02 | 2005-04-02 21:19 | Calculated | O410E | C682 | Single Circuit |  |  | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Pole - Softwood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 136 | 19353 | 26871 | 1.3885 | 0.0070273 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7167 |  | 2005-04-03 07:40 | 2005-04-03 | 2005-04-03 07:41 | Calculated | O410E | C798 |  |  |  | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 499 | 19353 | 499 | 0.02578 | 0.025784 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7168 |  | 2005-04-04 10:12 | 2005-04-04 | 2005-04-04 12:26 | Calculated | O410E |  |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 134 | 49 | 19353 | 6588 | 0.34041 | 0.0025319 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7170 |  | 2005-04-05 12:40 | 2005-04-05 | 2005-04-05 13:41 | Calculated | O410E | LF |  |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 1 | 19353 | 61 | 0.00315 | 5.1672e-05 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7171 |  | 2005-04-06 | 2005-04-06 | 2005-04-06 00:10 | Calculated | O410E | C113 |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 42 | 19353 | 420 | 0.0217 | 0.0021702 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7175 |  | 2005-04-07 10:02 | 2005-04-07 | 2005-04-07 14:15 | Calculated | O410E |  |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 253 | 12 | 19353 | 3036 | 0.15687 | 0.00062006 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7176 |  | 2005-04-08 10:01 | 2005-04-08 | 2005-04-08 10:20 | Calculated | O410E |  |  |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 19 | 32 | 19353 | 628 | 0.03245 | 0.0016535 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7177 |  | 2005-04-08 10:32 | 2005-04-08 | 2005-04-08 14:52 | Calculated | O410E |  |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 260 | 27 | 19353 | 7020 | 0.36273 | 0.0013951 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7178 |  | 2005-04-08 13:30 | 2005-04-08 | 2005-04-08 14:02 | Calculated | O410E | LF | Drop-Out Fuses |  | Whakamaru 120-02 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 32 | 56 | 19353 | 1792 | 0.0926 | 0.0028936 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7179 |  | 2005-04-08 14:10 | 2005-04-08 | 2005-04-08 14:32 | Calculated | O410E | LF |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 22 | 3 | 19353 | 66 | 0.00341 | 0.00015501 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7180 |  | 2005-04-09 19:15 | 2005-04-09 | 2005-04-10 09:38 | Calculated | O410E | L1539 | Single Circuit |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 863 | 7 | 19353 | 6041 | 0.31215 | 0.0003617 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7181 |  | 2005-04-11 10:41 | 2005-04-11 | 2005-04-11 11:55 | Calculated | O410E |  |  |  | Mokauiti 115-02 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 74 | 91 | 19353 | 6755 | 0.34904 | 0.0047021 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7182 |  | 2005-04-11 10:58 | 2005-04-11 | 2005-04-11 11:57 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 59 | 2 | 19353 | 118 | 0.0061 | 0.00010334 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7183 |  | 2005-04-12 09:01 | 2005-04-12 | 2005-04-12 11:34 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 7 | 19353 | 1071 | 0.05534 | 0.0003617 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7186 |  | 2005-04-12 14:01 | 2005-04-12 | 2005-04-12 14:52 | Calculated | O410E |  |  |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 25 | 19353 | 1275 | 0.06588 | 0.0012918 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
3981 |  | 2005-04-13 | 2005-04-13 | 2005-04-13 04:21 | Calculated | O410E |  |  |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 261 | 4 | 19353 | 1044 | 0.05395 | 0.00020669 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7188 |  | 2005-04-13 05:53 | 2005-04-13 | 2005-04-13 07:10 | Calculated | O410E | C799 |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 14 | 19353 | 1078 | 0.0557 | 0.0007234 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7190 |  | 2005-04-13 12:59 | 2005-04-13 | 2005-04-13 14:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 69 | 1 | 19353 | 69 | 0.00357 | 5.1672e-05 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7191 |  | 2005-04-14 10:31 | 2005-04-14 | 2005-04-14 14:31 | Calculated | O410E |  |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 240 | 39 | 19353 | 9360 | 0.48365 | 0.0020152 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7193 |  | 2005-04-15 09:48 | 2005-04-15 | 2005-04-15 11:54 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 126 | 1 | 19353 | 126 | 0.00651 | 5.1672e-05 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7194 |  | 2005-04-16 06:47 | 2005-04-16 | 2005-04-16 06:48 | Calculated | O410E | C570-761 |  |  |  | Remote Rural F | Te Kawa St 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2005/2006 | April-2005 | 4 | 2005
7196 |  | 2005-04-16 22:03 | 2005-04-16 | 2005-04-16 22:11 | Calculated | O410E | C754-594 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1574 | 19353 | 12592 | 0.65065 | 0.081331 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7197 |  | 2005-04-18 07:15 | 2005-04-18 | 2005-04-18 08:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 5 | 19353 | 315 | 0.01628 | 0.00025836 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7198 |  | 2005-04-18 10:10 | 2005-04-18 | 2005-04-18 11:50 | Calculated | O410E |  |  |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 52 | 19353 | 5200 | 0.26869 | 0.0026869 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7199 |  | 2005-04-18 12:02 | 2005-04-18 | 2005-04-18 12:56 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 7 | 19353 | 378 | 0.01953 | 0.0003617 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7200 |  | 2005-04-18 16:07 | 2005-04-18 | 2005-04-18 16:32 | Calculated | O410E | LV |  |  | Tokaanu 420-01 | Remote Rural F | Tokaanu | Tokaanu Village Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 21 | 19353 | 525 | 0.02713 | 0.0010851 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7201 |  | 2005-04-18 19:01 | 2005-04-18 | 2005-04-18 19:56 | Calculated | O410E | C113 |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 42 | 19353 | 2310 | 0.11936 | 0.0021702 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7202 |  | 2005-04-19 10:02 | 2005-04-19 | 2005-04-19 12:13 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 131 | 134 | 19353 | 17554 | 0.90704 | 0.006924 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7205 |  | 2005-04-19 22:19 | 2005-04-19 | 2005-04-19 22:28 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 68 | 19353 | 612 | 0.03162 | 0.0035137 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7207 |  | 2005-04-20 15:58 | 2005-04-20 | 2005-04-20 16:55 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-04 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 57 | 2 | 19353 | 114 | 0.00589 | 0.00010334 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7209 |  | 2005-04-21 10:32 | 2005-04-21 | 2005-04-21 14:12 | Calculated | O410E |  |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 220 | 23 | 19353 | 5060 | 0.26146 | 0.0011884 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7210 |  | 2005-04-21 12:21 | 2005-04-21 | 2005-04-21 13:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 1 | 19353 | 77 | 0.00398 | 5.1672e-05 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7211 |  | 2005-04-21 13:20 | 2005-04-21 | 2005-04-21 14:46 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 86 | 69 | 19353 | 5934 | 0.30662 | 0.0035653 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7212 |  | 2005-04-22 09:00 | 2005-04-22 | 2005-04-22 11:14 | Calculated | O410E | C1626 |  |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 111 | 19353 | 14874 | 0.76856 | 0.0057355 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7213 |  | 2005-04-22 09:54 | 2005-04-22 | 2005-04-22 10:55 | Calculated | O410E | LF | Pole Mounted |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Windings | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 1 | 19353 | 61 | 0.00315 | 5.1672e-05 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7214 |  | 2005-04-22 10:00 | 2005-04-22 | 2005-04-22 11:52 | Calculated | O410E |  |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 201 | 19353 | 22572 | 1.1663 | 0.010386 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7215 |  | 2005-04-24 08:36 | 2005-04-24 | 2005-04-24 08:48 | Calculated | O410E | C242 & 262 | Double Circuit |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 12 | 240 | 19353 | 2900 | 0.14985 | 0.012401 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7217 |  | 2005-04-24 13:26 | 2005-04-24 | 2005-04-24 17:31 | Calculated | O410E | C1717 |  |  | Mokauiti 115-04 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 245 | 17 | 19353 | 4165 | 0.21521 | 0.00087842 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7218 |  | 2005-04-26 09:04 | 2005-04-26 | 2005-04-26 14:18 | Calculated | O410E | LV |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 314 | 38 | 19353 | 11932 | 0.61655 | 0.0019635 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7219 |  | 2005-04-26 17:40 | 2005-04-26 | 2005-04-26 20:13 | Calculated | O410E | C1345 | Drop-Out Fuses |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 153 | 25 | 19353 | 3825 | 0.19764 | 0.0012918 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7220 |  | 2005-04-26 21:13 | 2005-04-26 | 2005-04-26 23:37 | Calculated | O410E | C107 | ABS |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 144 | 339 | 19353 | 49143 | 2.5393 | 0.017517 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7221 |  | 2005-04-26 23:09 | 2005-04-26 | 2005-04-26 23:10 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 240 | 19353 | 240 | 0.0124 | 0.012401 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7222 |  | 2005-04-27 06:45 | 2005-04-27 | 2005-04-27 06:55 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 68 | 19353 | 680 | 0.03514 | 0.0035137 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7223 |  | 2005-04-27 07:40 | 2005-04-27 | 2005-04-27 09:40 | Calculated | O410E | C440 |  |  | Southern 409-09 | Remote Rural F | Southern | Manunui Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 24 | 19353 | 2880 | 0.14881 | 0.0012401 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7224 |  | 2005-04-27 20:43 | 2005-04-27 | 2005-04-27 22:52 | Calculated | O410E | C609 | Single Circuit |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation | OH Lines : Insulator - Pin | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 87 | 19353 | 11223 | 0.57991 | 0.0044954 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
25036 | Faulty Insulator - Taharoa | 2005-04-28 02:05 | 2005-04-28 | 2005-04-28 03:24 | Calculated | 609 | 609 - Circuit Breaker 609 (Rural Feeder) 609 | Single Circuit | No Segment | 201-01 Taharoa | Rural D | Rural | Taharoa Zone Substation | OH Lines : Insulator - Pin | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 87 | 19353 | 6873 | 0.35514 | 0.0044954 | 673 | 53166 | 2005/2006 | April-2005 | 4 | 2005
7225 |  | 2005-04-29 08:30 | 2005-04-29 | 2005-04-29 12:00 | Calculated | O410E |  |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 210 | 5 | 19353 | 1050 | 0.05426 | 0.00025836 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7226 |  | 2005-04-29 10:00 | 2005-04-29 | 2005-04-29 10:34 | Calculated | O410E |  |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 34 | 7 | 19353 | 238 | 0.0123 | 0.0003617 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7227 |  | 2005-04-30 14:30 | 2005-04-30 | 2005-04-30 14:50 | Calculated | O410E | C123 | Single Circuit |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 1012 | 19353 | 20999 | 1.0851 | 0.052292 | 0 | 0 | 2005/2006 | April-2005 | 4 | 2005
7228 |  | 2005-05-01 07:30 | 2005-05-01 | 2005-05-01 09:24 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 114 | 81 | 19353 | 9310 | 0.48106 | 0.0041854 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7229 |  | 2005-05-03 07:25 | 2005-05-03 | 2005-05-03 09:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 145 | 15 | 19353 | 2178 | 0.11254 | 0.00077507 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7230 |  | 2005-05-03 08:12 | 2005-05-03 | 2005-05-03 09:56 | Calculated | O410E | LF | Drop-Out Fuses |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 104 | 1 | 19353 | 104 | 0.00537 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7231 |  | 2005-05-04 09:35 | 2005-05-04 | 2005-05-04 10:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 52 | 1 | 19353 | 52 | 0.00269 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7232 |  | 2005-05-04 11:00 | 2005-05-04 | 2005-05-04 14:04 | Calculated | O410E |  |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 184 | 16 | 19353 | 2944 | 0.15212 | 0.00082675 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7233 |  | 2005-05-04 11:16 | 2005-05-04 | 2005-05-04 13:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 150 | 2 | 19353 | 300 | 0.0155 | 0.00010334 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7234 |  | 2005-05-04 11:19 | 2005-05-04 | 2005-05-04 12:35 | Calculated | O410E | LF |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 76 | 1 | 19353 | 76 | 0.00393 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7235 |  | 2005-05-05 05:21 | 2005-05-05 | 2005-05-05 06:23 | Calculated | O410E | C952 | Single Circuit |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 939 | 19353 | 58890 | 3.0429 | 0.04852 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7236 |  | 2005-05-05 09:04 | 2005-05-05 | 2005-05-05 09:51 | Calculated | O410E |  |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 47 | 70 | 19353 | 3315 | 0.17129 | 0.003617 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7237 |  | 2005-05-05 10:16 | 2005-05-05 | 2005-05-05 12:00 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 104 | 1 | 19353 | 104 | 0.00537 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7238 |  | 2005-05-05 10:28 | 2005-05-05 | 2005-05-05 15:20 | Calculated | O410E |  |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 9 | 19353 | 2628 | 0.13579 | 0.00046504 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7240 |  | 2005-05-06 10:31 | 2005-05-06 | 2005-05-06 12:02 | Calculated | O410E |  |  |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 144 | 19353 | 13128 | 0.67834 | 0.0074407 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7241 |  | 2005-05-08 08:13 | 2005-05-08 | 2005-05-08 08:22 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 1 | 19353 | 9 | 0.00047 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7242 |  | 2005-05-09 06:49 | 2005-05-09 | 2005-05-09 07:03 | Calculated | O410E | C549, 754 & 792 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 14 | 1574 | 19353 | 22036 | 1.1386 | 0.081331 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7243 |  | 2005-05-09 10:40 | 2005-05-09 | 2005-05-09 14:00 | Calculated | O410E |  |  |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 200 | 5 | 19353 | 1000 | 0.05167 | 0.00025836 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7244 |  | 2005-05-09 13:19 | 2005-05-09 | 2005-05-09 15:36 | Calculated | O410E | C5534 | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 137 | 12 | 19353 | 1644 | 0.08495 | 0.00062006 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7245 |  | 2005-05-09 14:10 | 2005-05-09 | 2005-05-09 14:46 | Calculated | O410E | LF |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 4 | 19353 | 144 | 0.00744 | 0.00020669 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7247 |  | 2005-05-09 19:29 | 2005-05-09 | 2005-05-09 20:27 | Calculated | O410E | C113 |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 42 | 19353 | 2451 | 0.12665 | 0.0021702 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7248 |  | 2005-05-10 10:42 | 2005-05-10 | 2005-05-10 11:19 | Calculated | O410E | LF |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 5 | 19353 | 185 | 0.00956 | 0.00025836 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7249 |  | 2005-05-10 13:05 | 2005-05-10 | 2005-05-10 14:48 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 103 | 1 | 19353 | 103 | 0.00532 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7250 |  | 2005-05-11 10:15 | 2005-05-11 | 2005-05-11 10:25 | Calculated | O410E |  | Control Equipment |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation | Miscellaneous : Battery Cells | Asset Related | Other |  | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1574 | 19353 | 15740 | 0.81331 | 0.081331 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7252 |  | 2005-05-12 10:37 | 2005-05-12 | 2005-05-12 12:21 | Calculated | O410E |  |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 104 | 6 | 19353 | 624 | 0.03224 | 0.00031003 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7253 |  | 2005-05-12 11:10 | 2005-05-12 | 2005-05-12 11:31 | Calculated | O410E | LF |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 4 | 19353 | 84 | 0.00434 | 0.00020669 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7255 |  | 2005-05-13 10:17 | 2005-05-13 | 2005-05-13 11:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 72 | 40 | 19353 | 2880 | 0.14881 | 0.0020669 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7257 |  | 2005-05-13 20:46 | 2005-05-13 | 2005-05-13 21:15 | Calculated | O410E | L550 | Drop-Out Fuses |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 29 | 11 | 19353 | 319 | 0.01648 | 0.00056839 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7258 |  | 2005-05-16 09:32 | 2005-05-16 | 2005-05-16 11:49 | Calculated | O410E |  |  |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 137 | 8 | 19353 | 1096 | 0.05663 | 0.00041337 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7259 |  | 2005-05-16 09:43 | 2005-05-16 | 2005-05-16 12:09 | Calculated | O410E |  |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 146 | 49 | 19353 | 7165 | 0.37023 | 0.0025319 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7260 |  | 2005-05-16 15:30 | 2005-05-16 | 2005-05-16 15:43 | Calculated | O410E | S337-344 | Single Circuit |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 49 | 19353 | 637 | 0.03291 | 0.0025319 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7261 |  | 2005-05-16 17:58 | 2005-05-16 | 2005-05-16 22:16 | Calculated | O410E | C1615 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 258 | 9 | 19353 | 2322 | 0.11998 | 0.00046504 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7262 |  | 2005-05-17 07:43 | 2005-05-17 | 2005-05-17 12:19 | Calculated | O410E | C1616 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 276 | 15 | 19353 | 4140 | 0.21392 | 0.00077507 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7263 |  | 2005-05-17 08:12 | 2005-05-17 | 2005-05-17 10:29 | Calculated | O410E | L368 | Drop-Out Fuses |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 137 | 24 | 19353 | 3288 | 0.1699 | 0.0012401 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7264 |  | 2005-05-17 09:00 | 2005-05-17 | 2005-05-17 10:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 16 | 19353 | 1008 | 0.05208 | 0.00082675 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7265 |  | 2005-05-17 09:05 | 2005-05-17 | 2005-05-17 10:23 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 78 | 1 | 19353 | 78 | 0.00403 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7268 |  | 2005-05-17 11:57 | 2005-05-17 | 2005-05-17 13:13 | Calculated | O410E | C355 |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 12 | 19353 | 912 | 0.04712 | 0.00062006 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7270 |  | 2005-05-18 14:45 | 2005-05-18 | 2005-05-18 14:47 | Calculated | O410E | LF |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 327 | 19353 | 654 | 0.03379 | 0.016897 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7271 |  | 2005-05-18 14:45 | 2005-05-18 | 2005-05-18 15:59 | Calculated | O410E | L362 | Drop-Out Fuses |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 74 | 11 | 19353 | 814 | 0.04206 | 0.00056839 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7272 |  | 2005-05-19 06:45 | 2005-05-19 | 2005-05-19 10:05 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-02 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 200 | 2 | 19353 | 400 | 0.02067 | 0.00010334 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7273 |  | 2005-05-19 06:52 | 2005-05-19 | 2005-05-19 10:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 246 | 2 | 19353 | 492 | 0.02542 | 0.00010334 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7274 |  | 2005-05-19 09:08 | 2005-05-19 | 2005-05-19 11:15 | Calculated | O410E | LF |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 127 | 62 | 19353 | 7874 | 0.40686 | 0.0032036 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7275 |  | 2005-05-19 10:31 | 2005-05-19 | 2005-05-19 14:01 | Calculated | O410E |  |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 210 | 15 | 19353 | 3150 | 0.16277 | 0.00077507 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7277 |  | 2005-05-19 12:07 | 2005-05-19 | 2005-05-19 15:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 180 | 1 | 19353 | 180 | 0.0093 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7278 |  | 2005-05-19 13:40 | 2005-05-19 | 2005-05-19 14:24 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 44 | 1 | 19353 | 44 | 0.00227 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7279 |  | 2005-05-20 12:20 | 2005-05-20 | 2005-05-20 13:38 | Calculated | O410E | C467 | Single Circuit |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 50 | 19353 | 3915 | 0.20229 | 0.0025836 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7280 |  | 2005-05-23 02:07 | 2005-05-23 | 2005-05-23 03:00 | Calculated | O410E | C955 | Single Circuit |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ground Subsidence | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 1092 | 19353 | 58385 | 3.0168 | 0.056425 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7281 |  | 2005-05-23 06:45 | 2005-05-23 | 2005-05-23 08:01 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-05 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 76 | 2 | 19353 | 152 | 0.00785 | 0.00010334 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7282 |  | 2005-05-23 08:12 | 2005-05-23 | 2005-05-23 10:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 134 | 1 | 19353 | 134 | 0.00692 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7283 |  | 2005-05-23 11:05 | 2005-05-23 | 2005-05-23 12:34 | Calculated | O410E |  |  |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 89 | 10 | 19353 | 890 | 0.04599 | 0.00051672 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7284 |  | 2005-05-23 11:12 | 2005-05-23 | 2005-05-23 13:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 141 | 3 | 19353 | 423 | 0.02186 | 0.00015501 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7285 |  | 2005-05-24 10:30 | 2005-05-24 | 2005-05-24 13:41 | Calculated | O410E |  |  |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 191 | 24 | 19353 | 4584 | 0.23686 | 0.0012401 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7286 |  | 2005-05-25 07:06 | 2005-05-25 | 2005-05-25 07:07 | Calculated | O410E | C232 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 153 | 19353 | 153 | 0.00791 | 0.0079058 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7287 |  | 2005-05-25 07:24 | 2005-05-25 | 2005-05-25 07:25 | Calculated | O410E | C761 & 570 |  |  |  | Remote Rural F | Te Kawa St 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 0 | 19353 | 0 | 0 | 0 | 1 | 0 | 2005/2006 | May-2005 | 5 | 2005
7288 |  | 2005-05-25 09:30 | 2005-05-25 | 2005-05-25 12:34 | Calculated | O410E |  |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 184 | 55 | 19353 | 10126 | 0.52323 | 0.0028419 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7289 |  | 2005-05-26 07:15 | 2005-05-26 | 2005-05-26 07:22 | Calculated | O410E | C963 |  |  | Rangipo / Hautu 424-03 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 22 | 19353 | 154 | 0.00796 | 0.0011368 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7290 |  | 2005-05-26 11:00 | 2005-05-26 | 2005-05-26 13:59 | Calculated | O410E |  |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 179 | 87 | 19353 | 15573 | 0.80468 | 0.0044954 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7292 |  | 2005-05-27 08:07 | 2005-05-27 | 2005-05-27 11:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 177 | 2 | 19353 | 354 | 0.01829 | 0.00010334 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7293 |  | 2005-05-27 12:43 | 2005-05-27 | 2005-05-27 14:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 2 | 19353 | 154 | 0.00796 | 0.00010334 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7295 |  | 2005-05-28 10:45 | 2005-05-28 | 2005-05-28 14:34 | Calculated | O410E | LF | Pole Mounted |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation | Transformers : Internal Connections | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 229 | 1 | 19353 | 229 | 0.01183 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7296 |  | 2005-05-29 07:47 | 2005-05-29 | 2005-05-29 10:42 | Calculated | O410E | C961 | Single Circuit |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 106 | 19353 | 18625 | 0.96238 | 0.0054772 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7297 |  | 2005-05-30 08:42 | 2005-05-30 | 2005-05-30 12:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 198 | 1 | 19353 | 198 | 0.01023 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7298 |  | 2005-05-30 09:06 | 2005-05-30 | 2005-05-30 11:58 | Calculated | O410E |  |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 172 | 97 | 19353 | 16684 | 0.86209 | 0.0050121 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7299 |  | 2005-05-30 10:17 | 2005-05-30 | 2005-05-30 10:57 | Calculated | O410E | LF |  |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 2 | 19353 | 80 | 0.00413 | 0.00010334 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7300 |  | 2005-05-30 10:25 | 2005-05-30 | 2005-05-30 12:53 | Calculated | O410E |  |  |  | Turoa 415-02 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 24 | 19353 | 3552 | 0.18354 | 0.0012401 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7301 |  | 2005-05-30 18:03 | 2005-05-30 | 2005-05-30 22:03 | Calculated | O410E | LF | Pole Mounted |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 240 | 4 | 19353 | 960 | 0.0496 | 0.00020669 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7302 |  | 2005-05-30 18:36 | 2005-05-30 | 2005-05-31 05:05 | Calculated | O410E | C1530 | Single Circuit |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 629 | 6 | 19353 | 3777 | 0.19516 | 0.00031003 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7303 |  | 2005-05-30 19:36 | 2005-05-30 | 2005-05-30 19:40 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 240 | 19353 | 960 | 0.0496 | 0.012401 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7304 |  | 2005-05-31 08:03 | 2005-05-31 | 2005-05-31 11:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 213 | 1 | 19353 | 213 | 0.01101 | 5.1672e-05 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7305 |  | 2005-05-31 10:41 | 2005-05-31 | 2005-05-31 11:02 | Calculated | O410E | S460 | Single Circuit |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 68 | 19353 | 1428 | 0.07379 | 0.0035137 | 0 | 0 | 2005/2006 | May-2005 | 5 | 2005
7306 |  | 2005-06-01 06:33 | 2005-06-01 | 2005-06-01 09:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 188 | 49 | 19353 | 9252 | 0.47807 | 0.0025319 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7307 |  | 2005-06-01 08:17 | 2005-06-01 | 2005-06-01 10:16 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 119 | 3 | 19353 | 357 | 0.01845 | 0.00015501 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7308 |  | 2005-06-01 08:54 | 2005-06-01 | 2005-06-01 12:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 222 | 3 | 19353 | 666 | 0.03441 | 0.00015501 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7310 |  | 2005-06-01 09:09 | 2005-06-01 | 2005-06-01 14:51 | Calculated | O410E |  |  |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 4 | 19353 | 1368 | 0.07069 | 0.00020669 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7311 |  | 2005-06-01 11:24 | 2005-06-01 | 2005-06-01 15:27 | Calculated | O410E | L246 | Single Circuit |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Pole - Softwood | Weather | Lightning |  | Lightning Damage to Structure/Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 243 | 17 | 19353 | 4142 | 0.21402 | 0.00087842 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7312 |  | 2005-06-02 08:32 | 2005-06-02 | 2005-06-02 10:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 126 | 1 | 19353 | 126 | 0.00651 | 5.1672e-05 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7313 |  | 2005-06-02 12:25 | 2005-06-02 | 2005-06-02 13:17 | Calculated | O410E |  | Single Circuit |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 214 | 19353 | 11281 | 0.58291 | 0.011058 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7315 |  | 2005-06-03 00:21 | 2005-06-03 | 2005-06-03 00:22 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 240 | 19353 | 240 | 0.0124 | 0.012401 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7316 |  | 2005-06-03 00:21 | 2005-06-03 | 2005-06-03 00:31 | Calculated | O410E | C792 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1574 | 19353 | 15740 | 0.81331 | 0.081331 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7317 |  | 2005-06-03 00:22 | 2005-06-03 | 2005-06-03 08:50 | Calculated | O410E |  |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 508 | 43 | 19353 | 21844 | 1.1287 | 0.0022219 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7318 |  | 2005-06-03 08:03 | 2005-06-03 | 2005-06-03 09:55 | Calculated | O410E | L892 |  |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 17 | 19353 | 1904 | 0.09838 | 0.00087842 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7319 |  | 2005-06-03 10:44 | 2005-06-03 | 2005-06-03 11:30 | Calculated | O410E | S454 | Drop-Out Fuses |  | Tihoi 124-03 (was Tihoi 124-06) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Fuse Carriers | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 46 | 13 | 19353 | 598 | 0.0309 | 0.00067173 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7320 |  | 2005-06-03 11:35 | 2005-06-03 | 2005-06-03 12:23 | Calculated | O410E | L1359 | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 48 | 7 | 19353 | 336 | 0.01736 | 0.0003617 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7322 |  | 2005-06-03 12:33 | 2005-06-03 | 2005-06-03 13:27 | Calculated | O410E | C119 | Single Circuit |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 119 | 19353 | 6521 | 0.33695 | 0.0061489 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7323 |  | 2005-06-03 12:51 | 2005-06-03 | 2005-06-03 12:53 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 240 | 19353 | 480 | 0.0248 | 0.012401 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7324 |  | 2005-06-03 13:08 | 2005-06-03 | 2005-06-04 04:02 | Calculated | O410E | C1620 | Single Circuit |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Pole - Hardwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 894 | 176 | 19353 | 157511 | 8.1388 | 0.0090942 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7325 |  | 2005-06-03 13:47 | 2005-06-03 | 2005-06-03 16:40 | Calculated | O410E | L565 | Drop-Out Fuses |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 173 | 4 | 19353 | 692 | 0.03576 | 0.00020669 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7326 |  | 2005-06-03 14:00 | 2005-06-03 | 2005-06-03 16:12 | Calculated | O410E | C642 | Single Circuit |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 64 | 19353 | 8485 | 0.43843 | 0.003307 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7327 |  | 2005-06-03 14:28 | 2005-06-03 | 2005-06-03 15:06 | Calculated | O410E | S753 | Single Circuit |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 22 | 19353 | 836 | 0.0432 | 0.0011368 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7329 |  | 2005-06-03 17:47 | 2005-06-03 | 2005-06-03 18:25 | Calculated | O410E | C1343 | Single Circuit |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 18 | 19353 | 684 | 0.03534 | 0.00093009 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7330 |  | 2005-06-03 18:25 | 2005-06-03 | 2005-06-03 19:21 | Calculated | O410E | L500 | Drop-Out Fuses |  | Caves 101-07 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 56 | 13 | 19353 | 728 | 0.03762 | 0.00067173 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7331 |  | 2005-06-04 09:23 | 2005-06-04 | 2005-06-04 13:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 264 | 2 | 19353 | 528 | 0.02728 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7332 |  | 2005-06-05 08:08 | 2005-06-05 | 2005-06-05 08:10 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 240 | 19353 | 480 | 0.0248 | 0.012401 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7333 |  | 2005-06-07 07:46 | 2005-06-07 | 2005-06-07 10:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 172 | 2 | 19353 | 344 | 0.01778 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7334 |  | 2005-06-07 09:06 | 2005-06-07 | 2005-06-07 12:39 | Calculated | O410E |  |  |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 213 | 4 | 19353 | 852 | 0.04402 | 0.00020669 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7335 |  | 2005-06-07 10:18 | 2005-06-07 | 2005-06-07 13:39 | Calculated | O410E |  |  |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 201 | 53 | 19353 | 10698 | 0.55278 | 0.0027386 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7338 |  | 2005-06-08 13:50 | 2005-06-08 | 2005-06-08 14:27 | Calculated | O410E | L633 | Single Circuit |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 13 | 19353 | 481 | 0.02485 | 0.00067173 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7339 |  | 2005-06-08 15:00 | 2005-06-08 | 2005-06-08 15:20 | Calculated | O410E | L940 |  |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 4 | 19353 | 80 | 0.00413 | 0.00020669 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7341 |  | 2005-06-09 10:30 | 2005-06-09 | 2005-06-09 13:22 | Calculated | O410E | L1613 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Crossarm - Wood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 25 | 19353 | 4300 | 0.22219 | 0.0012918 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7342 |  | 2005-06-10 02:13 | 2005-06-10 | 2005-06-10 02:23 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 42 | 19353 | 420 | 0.0217 | 0.0021702 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7343 |  | 2005-06-10 08:55 | 2005-06-10 | 2005-06-10 09:04 | Calculated | O410E | S4.8 |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 77 | 19353 | 693 | 0.03581 | 0.0039787 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7344 |  | 2005-06-10 08:56 | 2005-06-10 | 2005-06-10 11:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 128 | 1 | 19353 | 128 | 0.00661 | 5.1672e-05 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7345 |  | 2005-06-10 10:04 | 2005-06-10 | 2005-06-10 10:32 | Calculated | O410E |  |  |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 28 | 17 | 19353 | 476 | 0.0246 | 0.00087842 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7346 |  | 2005-06-10 10:33 | 2005-06-10 | 2005-06-10 12:10 | Calculated | O410E | LF |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 97 | 10 | 19353 | 970 | 0.05012 | 0.00051672 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7347 |  | 2005-06-10 10:38 | 2005-06-10 | 2005-06-10 13:46 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 188 | 39 | 19353 | 7332 | 0.37886 | 0.0020152 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7348 |  | 2005-06-10 13:30 | 2005-06-10 | 2005-06-10 13:41 | Calculated | O410E | LF |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 11 | 26 | 19353 | 286 | 0.01478 | 0.0013435 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7349 |  | 2005-06-11 11:19 | 2005-06-11 | 2005-06-11 15:02 | Calculated | O410E | LF | Pole Mounted |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 223 | 2 | 19353 | 446 | 0.02305 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7351 |  | 2005-06-13 08:42 | 2005-06-13 | 2005-06-13 11:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 167 | 2 | 19353 | 334 | 0.01726 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7353 |  | 2005-06-13 09:32 | 2005-06-13 | 2005-06-13 11:52 | Calculated | O410E |  |  |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 140 | 13 | 19353 | 1820 | 0.09404 | 0.00067173 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7355 |  | 2005-06-13 12:00 | 2005-06-13 | 2005-06-13 12:34 | Calculated | O410E | S672 | Drop-Out Fuses |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 34 | 24 | 19353 | 816 | 0.04216 | 0.0012401 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7356 |  | 2005-06-13 15:30 | 2005-06-13 | 2005-06-13 15:41 | Calculated | O410E | C952 |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 939 | 19353 | 10329 | 0.53372 | 0.04852 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7357 |  | 2005-06-14 10:18 | 2005-06-14 | 2005-06-14 17:08 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 410 | 8 | 19353 | 3280 | 0.16948 | 0.00041337 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7358 |  | 2005-06-14 10:30 | 2005-06-14 | 2005-06-14 14:18 | Calculated | O410E |  |  |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 228 | 20 | 19353 | 4560 | 0.23562 | 0.0010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7360 |  | 2005-06-15 08:02 | 2005-06-15 | 2005-06-15 08:49 | Calculated | O410E | L575 | Drop-Out Fuses |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 47 | 31 | 19353 | 1457 | 0.07529 | 0.0016018 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7361 |  | 2005-06-15 10:31 | 2005-06-15 | 2005-06-15 14:25 | Calculated | O410E |  |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 234 | 9 | 19353 | 2106 | 0.10882 | 0.00046504 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7362 |  | 2005-06-15 10:48 | 2005-06-15 | 2005-06-15 10:51 | Calculated | O410E | C144 |  |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 281 | 19353 | 843 | 0.04356 | 0.01452 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7365 |  | 2005-06-15 14:53 | 2005-06-15 | 2005-06-15 16:46 | Calculated | O410E | C1072 | Single Circuit |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 108 | 19353 | 12259 | 0.63344 | 0.0055805 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7366 |  | 2005-06-16 10:32 | 2005-06-16 | 2005-06-16 12:31 | Calculated | O410E | LF |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 2 | 19353 | 238 | 0.0123 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7367 |  | 2005-06-16 12:38 | 2005-06-16 | 2005-06-16 13:21 | Calculated | O410E | S305 | Single Circuit |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 86 | 19353 | 3698 | 0.19108 | 0.0044438 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7368 |  | 2005-06-17 10:19 | 2005-06-17 | 2005-06-17 11:42 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 83 | 240 | 19353 | 19992 | 1.033 | 0.012401 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7369 |  | 2005-06-17 11:47 | 2005-06-17 | 2005-06-17 13:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 48 | 19353 | 4224 | 0.21826 | 0.0024802 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7370 |  | 2005-06-19 13:04 | 2005-06-19 | 2005-06-19 16:13 | Calculated | O410E | L162 | Single Circuit |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 189 | 4 | 19353 | 756 | 0.03906 | 0.00020669 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7371 |  | 2005-06-20 09:30 | 2005-06-20 | 2005-06-20 12:22 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 172 | 2 | 19353 | 344 | 0.01778 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7373 |  | 2005-06-20 10:49 | 2005-06-20 | 2005-06-20 12:49 | Calculated | O410E | LF | Pole Mounted |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 2 | 19353 | 240 | 0.0124 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7374 |  | 2005-06-20 11:35 | 2005-06-20 | 2005-06-20 15:16 | Calculated | O410E | LF |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 2 | 19353 | 442 | 0.02284 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7375 |  | 2005-06-21 08:20 | 2005-06-21 | 2005-06-21 09:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 50 | 5 | 19353 | 250 | 0.01292 | 0.00025836 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7376 |  | 2005-06-21 08:34 | 2005-06-21 | 2005-06-21 08:36 | Calculated | O410E |  |  |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 16 | 19353 | 32 | 0.00165 | 0.00082675 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7377 |  | 2005-06-21 09:00 | 2005-06-21 | 2005-06-21 12:38 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 218 | 8 | 19353 | 1744 | 0.09012 | 0.00041337 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7378 |  | 2005-06-21 09:03 | 2005-06-21 | 2005-06-21 13:11 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 1 | 19353 | 248 | 0.01281 | 5.1672e-05 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7379 |  | 2005-06-21 09:47 | 2005-06-21 | 2005-06-21 11:20 | Calculated | O410E | LF |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 19353 | 186 | 0.00961 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7380 |  | 2005-06-21 11:00 | 2005-06-21 | 2005-06-21 11:39 | Calculated | O410E | L246 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 39 | 17 | 19353 | 663 | 0.03426 | 0.00087842 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7381 |  | 2005-06-21 11:15 | 2005-06-21 | 2005-06-21 14:43 | Calculated | O410E | L693 | Drop-Out Fuses |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 208 | 20 | 19353 | 4160 | 0.21495 | 0.0010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7382 |  | 2005-06-21 13:05 | 2005-06-21 | 2005-06-21 15:43 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 158 | 1 | 19353 | 158 | 0.00816 | 5.1672e-05 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7383 |  | 2005-06-22 08:04 | 2005-06-22 | 2005-06-22 11:02 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 178 | 4 | 19353 | 712 | 0.03679 | 0.00020669 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7384 |  | 2005-06-22 08:30 | 2005-06-22 | 2005-06-22 11:23 | Calculated | O410E | C396 |  |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 173 | 26 | 19353 | 4498 | 0.23242 | 0.0013435 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7385 |  | 2005-06-22 09:23 | 2005-06-22 | 2005-06-22 11:43 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 140 | 132 | 19353 | 18480 | 0.95489 | 0.0068206 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7387 |  | 2005-06-22 11:27 | 2005-06-22 | 2005-06-22 12:24 | Calculated | O410E | S396-397 | Single Circuit |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 24 | 19353 | 1368 | 0.07069 | 0.0012401 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7390 |  | 2005-06-23 14:33 | 2005-06-23 | 2005-06-23 15:41 | Calculated | O410E |  |  |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 68 | 15 | 19353 | 1020 | 0.05271 | 0.00077507 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7391 |  | 2005-06-23 15:46 | 2005-06-23 | 2005-06-23 15:55 | Calculated | O410E | C107 | Single Circuit |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 339 | 19353 | 3051 | 0.15765 | 0.017517 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7392 |  | 2005-06-24 07:34 | 2005-06-24 | 2005-06-24 07:35 | Calculated | O410E | C761-570 |  |  |  | Remote Rural F | Te Kawa St 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2005/2006 | June-2005 | 6 | 2005
7393 |  | 2005-06-24 08:40 | 2005-06-24 | 2005-06-24 10:37 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 132 | 19353 | 15444 | 0.79802 | 0.0068206 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7394 |  | 2005-06-24 11:01 | 2005-06-24 | 2005-06-24 11:51 | Calculated | O410E |  |  |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 50 | 25 | 19353 | 1250 | 0.06459 | 0.0012918 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7395 |  | 2005-06-24 14:04 | 2005-06-24 | 2005-06-24 15:02 | Calculated | O410E | LF |  |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 2 | 19353 | 116 | 0.00599 | 0.00010334 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7396 |  | 2005-06-26 13:00 | 2005-06-26 | 2005-06-26 14:07 | Calculated | O410E | L1714 | Single Circuit |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Conductor - Galvanised | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 10 | 19353 | 670 | 0.03462 | 0.00051672 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7397 |  | 2005-06-27 01:09 | 2005-06-27 | 2005-06-27 02:30 | Calculated | O410E | C104 | Single Circuit |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Conductor - Bare Copper | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 621 | 19353 | 50332 | 2.6007 | 0.032088 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7398 |  | 2005-06-27 09:53 | 2005-06-27 | 2005-06-27 11:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 1 | 19353 | 85 | 0.00439 | 5.1672e-05 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7399 |  | 2005-06-27 10:18 | 2005-06-27 | 2005-06-27 11:46 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 16 | 19353 | 1408 | 0.07275 | 0.00082675 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7400 |  | 2005-06-27 12:23 | 2005-06-27 | 2005-06-27 14:13 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 110 | 3 | 19353 | 330 | 0.01705 | 0.00015501 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7401 |  | 2005-06-27 13:45 | 2005-06-27 | 2005-06-27 13:52 | Calculated | O410E | C952 |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 939 | 19353 | 6573 | 0.33964 | 0.04852 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7402 |  | 2005-06-27 14:38 | 2005-06-27 | 2005-06-27 15:32 | Calculated | O410E | L292 | Single Circuit |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Jumper - Insulated ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 5 | 19353 | 270 | 0.01395 | 0.00025836 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7403 |  | 2005-06-28 00:53 | 2005-06-28 | 2005-06-28 04:37 | Calculated | O410E | C385 | Single Circuit |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 224 | 116 | 19353 | 26080 | 1.3476 | 0.0059939 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7404 |  | 2005-06-28 07:38 | 2005-06-28 | 2005-06-28 09:55 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 137 | 32 | 19353 | 4384 | 0.22653 | 0.0016535 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7405 |  | 2005-06-28 08:06 | 2005-06-28 | 2005-06-28 09:00 | Calculated | O410E | LF | Pole Mounted |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 19353 | 54 | 0.00279 | 5.1672e-05 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7406 |  | 2005-06-28 08:13 | 2005-06-28 | 2005-06-28 08:18 | Calculated | O410E | LV |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 57 | 19353 | 285 | 0.01473 | 0.0029453 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7409 |  | 2005-06-29 09:16 | 2005-06-29 | 2005-06-29 15:44 | Calculated | O410E |  |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 388 | 27 | 19353 | 10476 | 0.54131 | 0.0013951 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7410 |  | 2005-06-30 07:19 | 2005-06-30 | 2005-06-30 09:52 | Calculated | O410E | C1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 153 | 29 | 19353 | 4437 | 0.22927 | 0.0014985 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7412 |  | 2005-06-30 10:12 | 2005-06-30 | 2005-06-30 11:14 | Calculated | O410E |  |  |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 62 | 27 | 19353 | 1687 | 0.08717 | 0.0013951 | 0 | 0 | 2005/2006 | June-2005 | 6 | 2005
7414 |  | 2005-07-01 09:33 | 2005-07-01 | 2005-07-01 10:12 | Calculated | O410E |  |  |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 39 | 32 | 19353 | 1273 | 0.06578 | 0.0016535 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7415 |  | 2005-07-01 09:52 | 2005-07-01 | 2005-07-01 11:30 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 98 | 62 | 19353 | 6135 | 0.31701 | 0.0032036 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7416 |  | 2005-07-01 13:07 | 2005-07-01 | 2005-07-01 16:29 | Calculated | O410E | L519 | Single Circuit |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 14 | 19353 | 2828 | 0.14613 | 0.0007234 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7417 |  | 2005-07-02 09:00 | 2005-07-02 | 2005-07-02 15:23 | Calculated | O410E |  | Single Circuit |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation | OH Lines : Pole - Other | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 383 | 263 | 19353 | 100939 | 5.2157 | 0.01359 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7418 |  | 2005-07-04 06:00 | 2005-07-04 | 2005-07-04 09:51 | Calculated | O410E | LF | Drop-Out Fuses |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 231 | 12 | 19353 | 2772 | 0.14323 | 0.00062006 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7420 |  | 2005-07-05 09:03 | 2005-07-05 | 2005-07-05 11:37 | Calculated | O410E | LF |  |  | Caves 101-08 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 154 | 1 | 19353 | 154 | 0.00796 | 5.1672e-05 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7421 |  | 2005-07-05 11:47 | 2005-07-05 | 2005-07-05 13:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 79 | 1 | 19353 | 79 | 0.00408 | 5.1672e-05 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7423 |  | 2005-07-06 09:05 | 2005-07-06 | 2005-07-06 14:34 | Calculated | O410E |  |  |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 329 | 8 | 19353 | 2632 | 0.136 | 0.00041337 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7424 |  | 2005-07-06 10:00 | 2005-07-06 | 2005-07-06 12:19 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 69 | 19353 | 9591 | 0.49558 | 0.0035653 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7425 |  | 2005-07-06 10:20 | 2005-07-06 | 2005-07-06 11:18 | Calculated | O410E |  |  |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 38 | 19353 | 2204 | 0.11388 | 0.0019635 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7426 |  | 2005-07-06 10:31 | 2005-07-06 | 2005-07-06 13:26 | Calculated | O410E |  |  |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 175 | 23 | 19353 | 4025 | 0.20798 | 0.0011884 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7427 |  | 2005-07-06 12:17 | 2005-07-06 | 2005-07-06 13:45 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 3 | 19353 | 264 | 0.01364 | 0.00015501 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7429 |  | 2005-07-07 09:35 | 2005-07-07 | 2005-07-07 15:14 | Calculated | O410E |  |  |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 339 | 17 | 19353 | 5763 | 0.29778 | 0.00087842 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7430 |  | 2005-07-07 10:32 | 2005-07-07 | 2005-07-07 13:01 | Calculated | O410E |  |  |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 6 | 19353 | 894 | 0.04619 | 0.00031003 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7431 |  | 2005-07-07 18:43 | 2005-07-07 | 2005-07-07 22:01 | Calculated | O410E | LF | Pole Mounted |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 7 | 19353 | 1386 | 0.07162 | 0.0003617 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7432 |  | 2005-07-08 02:19 | 2005-07-08 | 2005-07-08 02:30 | Calculated | O410E | C1 |  |  | Mokai 123-00 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 256 | 19353 | 2816 | 0.14551 | 0.013228 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7434 |  | 2005-07-08 09:10 | 2005-07-08 | 2005-07-08 10:57 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 107 | 72 | 19353 | 7704 | 0.39808 | 0.0037204 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7433 |  | 2005-07-08 09:11 | 2005-07-08 | 2005-07-08 13:19 | Calculated | O410E |  |  |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 15 | 19353 | 3720 | 0.19222 | 0.00077507 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7435 |  | 2005-07-08 15:01 | 2005-07-08 | 2005-07-08 17:30 | Calculated | O410E | C1 | Single Circuit |  | Mokai 123-00 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 256 | 19353 | 38391 | 1.9837 | 0.013228 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7436 |  | 2005-07-11 10:48 | 2005-07-11 | 2005-07-11 14:03 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 195 | 7 | 19353 | 1367 | 0.07064 | 0.0003617 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7437 |  | 2005-07-11 14:40 | 2005-07-11 | 2005-07-11 15:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 28 | 4 | 19353 | 112 | 0.00579 | 0.00020669 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7439 |  | 2005-07-11 20:47 | 2005-07-11 | 2005-07-11 22:04 | Calculated | O410E | S1105 | Drop-Out Fuses |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 11 | 19353 | 847 | 0.04377 | 0.00056839 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7440 |  | 2005-07-12 10:01 | 2005-07-12 | 2005-07-12 13:36 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 215 | 7 | 19353 | 1505 | 0.07777 | 0.0003617 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7441 |  | 2005-07-12 10:33 | 2005-07-12 | 2005-07-12 15:05 | Calculated | O410E | LF |  |  | Otorohanga 112-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 26 | 19353 | 7072 | 0.36542 | 0.0013435 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7442 |  | 2005-07-12 11:15 | 2005-07-12 | 2005-07-12 12:57 | Calculated | O410E | C1072 | Single Circuit |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 108 | 19353 | 11113 | 0.57423 | 0.0055805 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7443 |  | 2005-07-12 14:19 | 2005-07-12 | 2005-07-12 15:50 | Calculated | O410E | C705 | Single Circuit |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 29 | 19353 | 2641 | 0.13646 | 0.0014985 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7446 |  | 2005-07-13 09:31 | 2005-07-13 | 2005-07-13 10:06 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 3 | 19353 | 105 | 0.00543 | 0.00015501 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7447 |  | 2005-07-13 10:12 | 2005-07-13 | 2005-07-13 11:53 | Calculated | O410E | C1549 |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 21 | 19353 | 2121 | 0.1096 | 0.0010851 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7448 |  | 2005-07-14 09:26 | 2005-07-14 | 2005-07-14 11:35 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 129 | 62 | 19353 | 7998 | 0.41327 | 0.0032036 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7449 |  | 2005-07-14 09:31 | 2005-07-14 | 2005-07-14 10:10 | Calculated | O410E | LF |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 39 | 38 | 19353 | 1482 | 0.07658 | 0.0019635 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7450 |  | 2005-07-14 10:07 | 2005-07-14 | 2005-07-14 11:13 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 66 | 2 | 19353 | 132 | 0.00682 | 0.00010334 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7451 |  | 2005-07-15 07:17 | 2005-07-15 | 2005-07-15 10:31 | Calculated | O410E | L239 | Single Circuit |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 194 | 20 | 19353 | 3888 | 0.2009 | 0.0010334 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7452 |  | 2005-07-15 08:07 | 2005-07-15 | 2005-07-15 09:16 | Calculated | O410E | C1272 | Single Circuit |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Pole - Softwood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 230 | 19353 | 16054 | 0.82954 | 0.011884 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7454 |  | 2005-07-17 09:11 | 2005-07-17 | 2005-07-17 14:50 | Calculated | O410E | C1616 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Surge Diverters | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 339 | 15 | 19353 | 5085 | 0.26275 | 0.00077507 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7455 |  | 2005-07-17 23:38 | 2005-07-17 | 2005-07-17 23:47 | Calculated | O410E | C990 |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 13 | 19353 | 117 | 0.00605 | 0.00067173 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7456 |  | 2005-07-18 09:12 | 2005-07-18 | 2005-07-18 15:01 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 349 | 30 | 19353 | 10470 | 0.541 | 0.0015501 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7457 |  | 2005-07-18 10:09 | 2005-07-18 | 2005-07-18 14:23 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 254 | 7 | 19353 | 1778 | 0.09187 | 0.0003617 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7459 |  | 2005-07-19 09:01 | 2005-07-19 | 2005-07-19 10:47 | Calculated | O410E |  |  |  | Western 403-04 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 106 | 16 | 19353 | 1696 | 0.08763 | 0.00082675 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7460 |  | 2005-07-19 10:00 | 2005-07-19 | 2005-07-19 13:36 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 216 | 7 | 19353 | 1516 | 0.07833 | 0.0003617 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7461 |  | 2005-07-19 14:56 | 2005-07-19 | 2005-07-19 14:59 | Calculated | O410E | C242 | Single Circuit |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply | OH Lines : Crossarm - Wood | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 240 | 19353 | 720 | 0.0372 | 0.012401 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7462 |  | 2005-07-20 10:00 | 2005-07-20 | 2005-07-20 11:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 78 | 1 | 19353 | 78 | 0.00403 | 5.1672e-05 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7463 |  | 2005-07-20 10:02 | 2005-07-20 | 2005-07-20 11:40 | Calculated | O410E |  |  |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 98 | 7 | 19353 | 686 | 0.03545 | 0.0003617 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7464 |  | 2005-07-20 11:39 | 2005-07-20 | 2005-07-20 14:04 | Calculated | O410E | C891 | Auto-Recloser |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Tank | Weather | WOLD |  | WOLR | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 145 | 46 | 19353 | 6670 | 0.34465 | 0.0023769 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7465 |  | 2005-07-20 12:15 | 2005-07-20 | 2005-07-20 13:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 72 | 9 | 19353 | 648 | 0.03348 | 0.00046504 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7467 |  | 2005-07-21 09:00 | 2005-07-21 | 2005-07-21 14:52 | Calculated | O410E |  |  |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 352 | 6 | 19353 | 2112 | 0.10913 | 0.00031003 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7468 |  | 2005-07-21 09:10 | 2005-07-21 | 2005-07-21 10:09 | Calculated | O410E | L162 | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 59 | 4 | 19353 | 236 | 0.01219 | 0.00020669 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7469 |  | 2005-07-21 09:34 | 2005-07-21 | 2005-07-21 15:01 | Calculated | O410E |  |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 36 | 19353 | 11772 | 0.60828 | 0.0018602 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7470 |  | 2005-07-21 11:49 | 2005-07-21 | 2005-07-21 13:01 | Calculated | O410E | LF |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 72 | 2 | 19353 | 144 | 0.00744 | 0.00010334 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7471 |  | 2005-07-22 09:06 | 2005-07-22 | 2005-07-22 16:15 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 429 | 62 | 19353 | 26598 | 1.3744 | 0.0032036 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7473 |  | 2005-07-22 15:49 | 2005-07-22 | 2005-07-22 16:02 | Calculated | O410E | C232 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error |  | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 13 | 1651 | 19353 | 21463 | 1.109 | 0.08531 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7472 |  | 2005-07-22 16:15 | 2005-07-22 | 2005-07-22 16:28 | Calculated | O410E | C952 & 880 |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 1176 | 19353 | 15366 | 0.79399 | 0.060766 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7474 |  | 2005-07-23 09:21 | 2005-07-23 | 2005-07-23 13:13 | Calculated | O410E |  |  |  | Hangatiki East 102-03 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 1 | 19353 | 232 | 0.01199 | 5.1672e-05 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7475 |  | 2005-07-25 09:34 | 2005-07-25 | 2005-07-25 10:03 | Calculated | O410E | LF |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 2 | 19353 | 58 | 0.003 | 0.00010334 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7476 |  | 2005-07-25 10:30 | 2005-07-25 | 2005-07-25 11:15 | Calculated | O410E |  |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 24 | 19353 | 1080 | 0.05581 | 0.0012401 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7477 |  | 2005-07-25 13:39 | 2005-07-25 | 2005-07-25 14:22 | Calculated | O410E | LF |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 1 | 19353 | 43 | 0.00222 | 5.1672e-05 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7478 |  | 2005-07-25 20:52 | 2005-07-25 | 2005-07-25 21:01 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 1 | 19353 | 9 | 0.00047 | 5.1672e-05 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7479 |  | 2005-07-26 08:30 | 2005-07-26 | 2005-07-26 09:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-04 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 45 | 24 | 19353 | 1080 | 0.05581 | 0.0012401 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7480 |  | 2005-07-26 09:15 | 2005-07-26 | 2005-07-26 11:26 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 131 | 132 | 19353 | 17292 | 0.8935 | 0.0068206 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7481 |  | 2005-07-26 11:46 | 2005-07-26 | 2005-07-26 18:58 | Calculated | O410E | L162 | Single Circuit |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 432 | 4 | 19353 | 1728 | 0.08929 | 0.00020669 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7484 |  | 2005-07-27 08:32 | 2005-07-27 | 2005-07-27 17:21 | Calculated | O410E | LF |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 529 | 65 | 19353 | 34385 | 1.7767 | 0.0033587 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7485 |  | 2005-07-27 23:35 | 2005-07-27 | 2005-07-27 23:43 | Calculated | O410E | C512 |  |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 833 | 19353 | 6664 | 0.34434 | 0.043042 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7486 |  | 2005-07-29 08:42 | 2005-07-29 | 2005-07-29 11:04 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 142 | 155 | 19353 | 22010 | 1.1373 | 0.0080091 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7487 |  | 2005-07-29 10:00 | 2005-07-29 | 2005-07-29 11:31 | Calculated | O410E |  |  |  | Gravel Scoop 109-01 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 30 | 19353 | 2742 | 0.14168 | 0.0015501 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7488 |  | 2005-07-29 14:12 | 2005-07-29 | 2005-07-29 15:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 14 | 19353 | 1316 | 0.068 | 0.0007234 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7489 |  | 2005-07-30 00:38 | 2005-07-30 | 2005-07-30 02:48 | Calculated | O410E | LF | Pole Mounted |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 2 | 19353 | 260 | 0.01343 | 0.00010334 | 0 | 0 | 2005/2006 | July-2005 | 7 | 2005
7490 |  | 2005-08-01 02:31 | 2005-08-01 | 2005-08-01 03:22 | Calculated | O410E | C512 | Single Circuit |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 833 | 19353 | 42871 | 2.2152 | 0.043042 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7491 |  | 2005-08-01 09:30 | 2005-08-01 | 2005-08-01 11:02 | Calculated | O410E | LF |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 3 | 19353 | 276 | 0.01426 | 0.00015501 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7492 |  | 2005-08-01 09:31 | 2005-08-01 | 2005-08-01 12:08 | Calculated | O410E |  |  |  | Maihiihi 111-09 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 157 | 20 | 19353 | 3140 | 0.16225 | 0.0010334 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7493 |  | 2005-08-02 09:30 | 2005-08-02 | 2005-08-02 10:14 | Calculated | O410E | LF |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 44 | 3 | 19353 | 132 | 0.00682 | 0.00015501 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7494 |  | 2005-08-02 12:05 | 2005-08-02 | 2005-08-02 13:51 | Calculated | O410E | L699 | Single Circuit |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Surge Diverters | Weather | Lightning |  | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 7 | 19353 | 742 | 0.03834 | 0.0003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7497 |  | 2005-08-03 13:20 | 2005-08-03 | 2005-08-03 14:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 65 | 2 | 19353 | 130 | 0.00672 | 0.00010334 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7499 |  | 2005-08-04 11:25 | 2005-08-04 | 2005-08-04 13:38 | Calculated | O410E | LF |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 133 | 4 | 19353 | 532 | 0.02749 | 0.00020669 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
25070 | Fuse Pulled Apart - SH 47 | 2005-08-05 09:23 | 2005-08-05 | 2005-08-05 14:32 | Calculated | 12P04 | 12P04 - 1 Phase : 50.00 kVA : POLEMNT |  | 418SEG5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 309 | 3 | 19353 | 927 | 0.0479 | 0.00015501 | 50 | 15452 | 2005/2006 | August-2005 | 8 | 2005
25071 | L/V Maintenance - Oio No.1 Rd | 2005-08-05 10:11 | 2005-08-05 | 2005-08-05 12:29 | Calculated | 11K04 | 11K04 - 1 Phase : 15.00 kVA : POLEMNT |  | 409SEG5440-5748 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 138 | 3 | 19353 | 414 | 0.02139 | 0.00015501 | 15 | 2070 | 2005/2006 | August-2005 | 8 | 2005
7503 |  | 2005-08-06 18:02 | 2005-08-06 | 2005-08-06 18:10 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1 | 19353 | 8 | 0.00041 | 5.1672e-05 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7504 |  | 2005-08-06 20:28 | 2005-08-06 | 2005-08-07 00:03 | Calculated | O410E | L842 | Drop-Out Fuses |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 215 | 13 | 19353 | 2795 | 0.14442 | 0.00067173 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7505 |  | 2005-08-07 03:45 | 2005-08-07 | 2005-08-07 07:22 | Calculated | O410E | C109 |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 70 | 19353 | 15198 | 0.7853 | 0.003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7506 |  | 2005-08-08 10:36 | 2005-08-08 | 2005-08-08 13:50 | Calculated | O410E |  |  |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 194 | 39 | 19353 | 7566 | 0.39095 | 0.0020152 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7507 |  | 2005-08-08 11:45 | 2005-08-08 | 2005-08-08 11:47 | Calculated | O410E |  |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 12 | 19353 | 24 | 0.00124 | 0.00062006 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7509 |  | 2005-08-10 10:35 | 2005-08-10 | 2005-08-10 11:17 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 239 | 19353 | 10038 | 0.51868 | 0.01235 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7510 |  | 2005-08-11 10:28 | 2005-08-11 | 2005-08-11 13:02 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 154 | 7 | 19353 | 1082 | 0.05591 | 0.0003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7511 |  | 2005-08-12 09:19 | 2005-08-12 | 2005-08-12 15:14 | Calculated | O410E |  |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 39 | 19353 | 13845 | 0.71539 | 0.0020152 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7512 |  | 2005-08-12 10:03 | 2005-08-12 | 2005-08-12 12:13 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 7 | 19353 | 910 | 0.04702 | 0.0003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7513 |  | 2005-08-12 20:39 | 2005-08-12 | 2005-08-12 20:42 | Calculated | O410E | C242 & 796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 240 | 19353 | 720 | 0.0372 | 0.012401 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7514 |  | 2005-08-13 19:05 | 2005-08-13 | 2005-08-13 23:35 | Calculated | O410E | LF | Pole Mounted |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 6 | 19353 | 1620 | 0.08371 | 0.00031003 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7516 |  | 2005-08-15 10:30 | 2005-08-15 | 2005-08-15 11:41 | Calculated | O410E |  |  |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 16 | 19353 | 1136 | 0.0587 | 0.00082675 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7520 |  | 2005-08-16 08:53 | 2005-08-16 | 2005-08-16 09:48 | Calculated | O410E | L763 | Drop-Out Fuses |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 55 | 1 | 19353 | 55 | 0.00284 | 5.1672e-05 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7519 |  | 2005-08-16 09:02 | 2005-08-16 | 2005-08-16 10:56 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 114 | 155 | 19353 | 17670 | 0.91304 | 0.0080091 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7522 |  | 2005-08-16 09:52 | 2005-08-16 | 2005-08-16 10:40 | Calculated | O410E | LF |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 48 | 2 | 19353 | 96 | 0.00496 | 0.00010334 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7523 |  | 2005-08-17 08:34 | 2005-08-17 | 2005-08-17 10:21 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 107 | 1 | 19353 | 107 | 0.00553 | 5.1672e-05 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7524 |  | 2005-08-18 07:53 | 2005-08-18 | 2005-08-18 09:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 82 | 1 | 19353 | 82 | 0.00424 | 5.1672e-05 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7528 |  | 2005-08-18 10:00 | 2005-08-18 | 2005-08-18 11:57 | Calculated | O410E | L5534 | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 117 | 12 | 19353 | 1404 | 0.07255 | 0.00062006 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7525 |  | 2005-08-18 10:02 | 2005-08-18 | 2005-08-18 13:38 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 216 | 6 | 19353 | 1296 | 0.06697 | 0.00031003 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7526 |  | 2005-08-18 10:07 | 2005-08-18 | 2005-08-18 12:25 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 138 | 7 | 19353 | 970 | 0.05012 | 0.0003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7527 |  | 2005-08-18 10:12 | 2005-08-18 | 2005-08-18 12:31 | Calculated | O410E | LF |  |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 33 | 19353 | 4587 | 0.23702 | 0.0017052 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7529 |  | 2005-08-19 10:00 | 2005-08-19 | 2005-08-19 12:22 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 142 | 7 | 19353 | 995 | 0.05141 | 0.0003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7530 |  | 2005-08-19 18:39 | 2005-08-19 | 2005-08-19 19:21 | Calculated | O410E | S1635 | Single Circuit |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 119 | 19353 | 5023 | 0.25955 | 0.0061489 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7531 |  | 2005-08-21 19:06 | 2005-08-21 | 2005-08-21 19:10 | Calculated | O410E | C1354 | Single Circuit |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 42 | 19353 | 168 | 0.00868 | 0.0021702 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7532 |  | 2005-08-22 06:50 | 2005-08-22 | 2005-08-22 10:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 190 | 2 | 19353 | 380 | 0.01964 | 0.00010334 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7533 |  | 2005-08-22 09:35 | 2005-08-22 | 2005-08-22 12:24 | Calculated | O410E |  |  |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 169 | 3 | 19353 | 507 | 0.0262 | 0.00015501 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7534 |  | 2005-08-22 10:31 | 2005-08-22 | 2005-08-22 15:38 | Calculated | O410E |  |  |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 1 | 19353 | 307 | 0.01586 | 5.1672e-05 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7535 |  | 2005-08-22 13:02 | 2005-08-22 | 2005-08-22 14:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 116 | 1 | 19353 | 116 | 0.00599 | 5.1672e-05 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7536 |  | 2005-08-23 09:38 | 2005-08-23 | 2005-08-23 11:12 | Calculated | O410E |  |  |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 43 | 19353 | 4052 | 0.20937 | 0.0022219 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7537 |  | 2005-08-23 10:31 | 2005-08-23 | 2005-08-23 12:03 | Calculated | O410E |  |  |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 7 | 19353 | 644 | 0.03328 | 0.0003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7539 |  | 2005-08-24 10:23 | 2005-08-24 | 2005-08-24 11:34 | Calculated | O410E | LF |  |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 1 | 19353 | 71 | 0.00367 | 5.1672e-05 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7540 |  | 2005-08-24 13:05 | 2005-08-24 | 2005-08-24 15:04 | Calculated | O410E | LF |  |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 3 | 19353 | 357 | 0.01845 | 0.00015501 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7542 |  | 2005-08-25 07:18 | 2005-08-25 | 2005-08-25 09:02 | Calculated | O410E | L500 | Drop-Out Fuses |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation | Switchgear : Supports or Foundations | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 104 | 70 | 19353 | 7336 | 0.37906 | 0.003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7543 |  | 2005-08-25 09:06 | 2005-08-25 | 2005-08-25 10:21 | Calculated | O410E | LF | Drop-Out Fuses |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 39 | 19353 | 2925 | 0.15114 | 0.0020152 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7544 |  | 2005-08-25 17:36 | 2005-08-25 | 2005-08-25 18:32 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 56 | 53 | 19353 | 2971 | 0.15352 | 0.0027386 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7545 |  | 2005-08-27 09:25 | 2005-08-27 | 2005-08-27 10:24 | Calculated | O410E | C109 | Single Circuit |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Surge Diverters | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 70 | 19353 | 4197 | 0.21687 | 0.003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7546 |  | 2005-08-28 08:46 | 2005-08-28 | 2005-08-28 11:11 | Calculated | O410E | S291 | Single Circuit |  | Caves 101-13 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 20 | 19353 | 2905 | 0.15011 | 0.0010334 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7547 |  | 2005-08-29 02:29 | 2005-08-29 | 2005-08-29 04:04 | Calculated | O410E | C109 | Single Circuit |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 70 | 19353 | 6701 | 0.34625 | 0.003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7548 |  | 2005-08-29 10:07 | 2005-08-29 | 2005-08-29 11:33 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 86 | 8 | 19353 | 688 | 0.03555 | 0.00041337 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7551 |  | 2005-08-30 08:34 | 2005-08-30 | 2005-08-30 10:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 1 | 19353 | 92 | 0.00475 | 5.1672e-05 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7550 |  | 2005-08-30 10:31 | 2005-08-30 | 2005-08-30 11:32 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 7 | 19353 | 432 | 0.02232 | 0.0003617 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7552 |  | 2005-08-30 13:02 | 2005-08-30 | 2005-08-30 13:42 | Calculated | O410E | C132 | Single Circuit |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 497 | 19353 | 20277 | 1.0477 | 0.025681 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7554 |  | 2005-08-31 09:41 | 2005-08-31 | 2005-08-31 10:35 | Calculated | O410E |  |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 49 | 19353 | 2666 | 0.13776 | 0.0025319 | 0 | 0 | 2005/2006 | August-2005 | 8 | 2005
7557 |  | 2005-09-02 08:30 | 2005-09-02 | 2005-09-02 09:22 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 52 | 2 | 19353 | 104 | 0.00537 | 0.00010334 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7558 |  | 2005-09-02 09:34 | 2005-09-02 | 2005-09-02 13:38 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 244 | 35 | 19353 | 8540 | 0.44128 | 0.0018085 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7559 |  | 2005-09-02 12:00 | 2005-09-02 | 2005-09-02 16:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 240 | 2 | 19353 | 480 | 0.0248 | 0.00010334 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7560 |  | 2005-09-02 13:25 | 2005-09-02 | 2005-09-02 14:08 | Calculated | O410E | L557 | Drop-Out Fuses |  | Tihoi 124-02 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 43 | 3 | 19353 | 129 | 0.00667 | 0.00015501 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7561 |  | 2005-09-02 15:47 | 2005-09-02 | 2005-09-02 17:03 | Calculated | O410E | L458 | Single Circuit |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 22 | 19353 | 1672 | 0.08639 | 0.0011368 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7562 |  | 2005-09-05 08:01 | 2005-09-05 | 2005-09-05 09:42 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 101 | 2 | 19353 | 202 | 0.01044 | 0.00010334 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7563 |  | 2005-09-05 08:20 | 2005-09-05 | 2005-09-05 09:54 | Calculated | O410E | LF | Drop-Out Fuses |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 7 | 19353 | 658 | 0.034 | 0.0003617 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7564 |  | 2005-09-05 09:30 | 2005-09-05 | 2005-09-05 12:36 | Calculated | O410E |  |  |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 186 | 21 | 19353 | 3918 | 0.20245 | 0.0010851 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7565 |  | 2005-09-05 12:12 | 2005-09-05 | 2005-09-05 12:20 | Calculated | O410E | LF |  |  | Tuhua 422-02 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 1 | 19353 | 8 | 0.00041 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7566 |  | 2005-09-05 13:02 | 2005-09-05 | 2005-09-05 13:09 | Calculated | O410E | LV |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 30 | 19353 | 210 | 0.01085 | 0.0015501 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7568 |  | 2005-09-06 08:10 | 2005-09-06 | 2005-09-06 15:08 | Calculated | O410E | L1529 | Pole Mounted |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 418 | 2 | 19353 | 836 | 0.0432 | 0.00010334 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7569 |  | 2005-09-06 09:06 | 2005-09-06 | 2005-09-06 13:54 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 288 | 13 | 19353 | 3744 | 0.19346 | 0.00067173 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
3983 |  | 2005-09-07 | 2005-09-07 | 2005-09-07 01:12 | Calculated | O410E | LF | Single Circuit |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Conductor - Bare ACSR | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 1 | 19353 | 72 | 0.00372 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7571 |  | 2005-09-07 03:10 | 2005-09-07 | 2005-09-07 03:20 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1 | 19353 | 10 | 0.00052 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7572 |  | 2005-09-07 06:02 | 2005-09-07 | 2005-09-07 11:38 | Calculated | O410E | C531 | Single Circuit |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 336 | 10 | 19353 | 3360 | 0.17362 | 0.00051672 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7575 |  | 2005-09-08 08:30 | 2005-09-08 | 2005-09-08 10:33 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 123 | 36 | 19353 | 4459 | 0.2304 | 0.0018602 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7577 |  | 2005-09-11 05:25 | 2005-09-11 | 2005-09-11 06:43 | Calculated | O410E | C222, 570, 761 & 120 | Double Circuit |  |  | Remote Rural F | Te Waireka Rd 33 | Direct from Hangatiki Supply | OH Lines : Conductor - Bare ACSR | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 78 | 2370 | 19353 | 186874 | 9.6561 | 0.12246 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7578 |  | 2005-09-11 12:00 | 2005-09-11 | 2005-09-11 15:10 | Calculated | O410E | C1262 | Single Circuit |  | Huirimu 121-04 | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 11 | 19353 | 2091 | 0.10805 | 0.00056839 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7579 |  | 2005-09-12 14:00 | 2005-09-12 | 2005-09-12 15:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 68 | 1 | 19353 | 68 | 0.00351 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7581 |  | 2005-09-13 13:00 | 2005-09-13 | 2005-09-13 13:21 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 21 | 3 | 19353 | 63 | 0.00326 | 0.00015501 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
25072 | Tree On Line - Gadsby Rd | 2005-09-14 07:03 | 2005-09-14 | 2005-09-14 08:52 | Calculated | 510 | 510 - Circuit Breaker Gadsby Rd 11 kV Incomer CB 510 |  | No Segment | 205-01 Gadsby Road | Urban A | No Feeder |  |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1424 | 19353 | 30723 | 1.5875 | 0.07358 | 12382.5 | 163629 | 2005/2006 | September-2005 | 9 | 2005
7583 |  | 2005-09-14 08:30 | 2005-09-14 | 2005-09-14 09:08 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 38 | 56 | 19353 | 2174 | 0.11233 | 0.0028936 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7584 |  | 2005-09-14 09:14 | 2005-09-14 | 2005-09-14 15:10 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 3 | 19353 | 1068 | 0.05519 | 0.00015501 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7586 |  | 2005-09-14 11:42 | 2005-09-14 | 2005-09-14 13:13 | Calculated | O410E | LF | Drop-Out Fuses |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 91 | 1 | 19353 | 91 | 0.0047 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7587 |  | 2005-09-14 13:54 | 2005-09-14 | 2005-09-14 14:30 | Calculated | O410E | LF |  |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 1 | 19353 | 36 | 0.00186 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7588 |  | 2005-09-14 15:03 | 2005-09-14 | 2005-09-14 16:09 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 66 | 1 | 19353 | 66 | 0.00341 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7589 |  | 2005-09-14 15:04 | 2005-09-14 | 2005-09-14 16:44 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 100 | 3 | 19353 | 300 | 0.0155 | 0.00015501 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7590 |  | 2005-09-15 06:13 | 2005-09-15 | 2005-09-15 09:13 | Calculated | O410E | C1627 | Single Circuit |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Spark Gaps | Weather | Lightning |  | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 6 | 19353 | 1080 | 0.05581 | 0.00031003 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7591 |  | 2005-09-15 08:04 | 2005-09-15 | 2005-09-15 11:53 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 229 | 1 | 19353 | 229 | 0.01183 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7592 |  | 2005-09-15 08:36 | 2005-09-15 | 2005-09-15 09:03 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 27 | 27 | 19353 | 731 | 0.03777 | 0.0013951 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7593 |  | 2005-09-15 09:33 | 2005-09-15 | 2005-09-15 09:50 | Calculated | O410E | LF |  |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 17 | 1 | 19353 | 17 | 0.00088 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7594 |  | 2005-09-15 10:42 | 2005-09-15 | 2005-09-15 11:41 | Calculated | O410E | LF |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 59 | 1 | 19353 | 59 | 0.00305 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7595 |  | 2005-09-16 12:45 | 2005-09-16 | 2005-09-16 13:06 | Calculated | O410E | L693 | Single Circuit |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 364 | 19353 | 7771 | 0.40154 | 0.018808 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7596 |  | 2005-09-16 15:00 | 2005-09-16 | 2005-09-16 16:54 | Calculated | O410E |  |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 114 | 6 | 19353 | 684 | 0.03534 | 0.00031003 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7597 |  | 2005-09-17 07:40 | 2005-09-17 | 2005-09-17 08:01 | Calculated | O410E | F376 & 377 | Single Circuit |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 68 | 19353 | 1428 | 0.07379 | 0.0035137 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7598 |  | 2005-09-18 16:32 | 2005-09-18 | 2005-09-18 17:06 | Calculated | O410E | C124 | Single Circuit |  | Maihiihi 111-00 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 589 | 19353 | 20261 | 1.0469 | 0.030435 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7599 |  | 2005-09-18 18:44 | 2005-09-18 | 2005-09-19 00:29 | Calculated | O410E | C465 | Single Circuit |  | Ongarue 421-02 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 345 | 25 | 19353 | 8645 | 0.4467 | 0.0012918 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7600 |  | 2005-09-19 13:56 | 2005-09-19 | 2005-09-19 15:11 | Calculated | O410E | LF | Pole Mounted |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | Transformers : External Bushings | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 2 | 19353 | 150 | 0.00775 | 0.00010334 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7601 |  | 2005-09-19 15:13 | 2005-09-19 | 2005-09-19 16:16 | Calculated | O410E | C429 | Drop-Out Fuses |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 24 | 19353 | 1512 | 0.07813 | 0.0012401 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7602 |  | 2005-09-20 08:56 | 2005-09-20 | 2005-09-20 15:52 | Calculated | O410E | LF | Single Circuit |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | OH Lines : Crossarm - Wood | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 416 | 3 | 19353 | 1248 | 0.06449 | 0.00015501 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7604 |  | 2005-09-20 09:27 | 2005-09-20 | 2005-09-20 09:58 | Calculated | O410E | LF |  |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 2 | 19353 | 62 | 0.0032 | 0.00010334 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7606 |  | 2005-09-21 08:52 | 2005-09-21 | 2005-09-21 08:57 | Calculated | O410E |  |  |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 41 | 19353 | 213 | 0.01101 | 0.0021185 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7607 |  | 2005-09-21 08:56 | 2005-09-21 | 2005-09-21 09:45 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 16 | 19353 | 789 | 0.04077 | 0.00082675 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7610 |  | 2005-09-22 10:32 | 2005-09-22 | 2005-09-22 14:11 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 219 | 15 | 19353 | 3285 | 0.16974 | 0.00077507 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7612 |  | 2005-09-22 14:25 | 2005-09-22 | 2005-09-22 16:19 | Calculated | O410E | C170 |  |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 17 | 19353 | 1938 | 0.10014 | 0.00087842 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7613 |  | 2005-09-22 16:47 | 2005-09-22 | 2005-09-22 18:20 | Calculated | O410E | RMS 973 |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 1 | 19353 | 93 | 0.00481 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7614 |  | 2005-09-23 06:59 | 2005-09-23 | 2005-09-23 08:52 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 113 | 4 | 19353 | 452 | 0.02336 | 0.00020669 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7615 |  | 2005-09-23 08:48 | 2005-09-23 | 2005-09-23 09:25 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 37 | 16 | 19353 | 597 | 0.03085 | 0.00082675 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7616 |  | 2005-09-23 10:33 | 2005-09-23 | 2005-09-23 14:19 | Calculated | O410E |  |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 226 | 15 | 19353 | 3390 | 0.17517 | 0.00077507 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7617 |  | 2005-09-23 13:45 | 2005-09-23 | 2005-09-23 15:19 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 1 | 19353 | 94 | 0.00486 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7618 |  | 2005-09-23 22:30 | 2005-09-23 | 2005-09-23 23:14 | Calculated | O410E | S925-964 | Outdoor - Ground Mounted |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply | Transformers : Other | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 198 | 19353 | 8830 | 0.45626 | 0.010231 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7619 |  | 2005-09-24 17:02 | 2005-09-24 | 2005-09-24 18:02 | Calculated | O410E | C949 | Fuse Switch |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 60 | 1 | 19353 | 60 | 0.0031 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7620 |  | 2005-09-25 08:50 | 2005-09-25 | 2005-09-25 10:06 | Calculated | O410E | L319 | Drop-Out Fuses |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 76 | 6 | 19353 | 456 | 0.02356 | 0.00031003 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7621 |  | 2005-09-25 09:31 | 2005-09-25 | 2005-09-25 15:20 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 349 | 206 | 19353 | 71894 | 3.7149 | 0.010644 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7622 |  | 2005-09-25 13:09 | 2005-09-25 | 2005-09-25 13:54 | Calculated | O410E | LV |  |  | Hakiaha 401-01 | Remote Rural F | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 50 | 19353 | 2250 | 0.11626 | 0.0025836 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7623 |  | 2005-09-26 00:45 | 2005-09-26 | 2005-09-26 00:47 | Calculated | O410E | C1102 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 1413 | 19353 | 2826 | 0.14602 | 0.073012 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7624 |  | 2005-09-26 09:10 | 2005-09-26 | 2005-09-26 09:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 49 | 1 | 19353 | 49 | 0.00253 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7625 |  | 2005-09-26 09:44 | 2005-09-26 | 2005-09-26 10:22 | Calculated | O410E | LF |  |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 3 | 19353 | 114 | 0.00589 | 0.00015501 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7626 |  | 2005-09-26 14:47 | 2005-09-26 | 2005-09-26 15:52 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 65 | 1 | 19353 | 65 | 0.00336 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7627 |  | 2005-09-28 09:10 | 2005-09-28 | 2005-09-28 13:39 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 3 | 19353 | 807 | 0.0417 | 0.00015501 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7628 |  | 2005-09-29 09:30 | 2005-09-29 | 2005-09-29 14:55 | Calculated | O410E |  |  |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 325 | 7 | 19353 | 2275 | 0.11755 | 0.0003617 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7629 |  | 2005-09-29 09:30 | 2005-09-29 | 2005-09-29 14:55 | Calculated | O410E |  |  |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 325 | 44 | 19353 | 14300 | 0.7389 | 0.0022735 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7630 |  | 2005-09-30 07:20 | 2005-09-30 | 2005-09-30 08:15 | Calculated | O410E | C949 |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 19353 | 55 | 0.00284 | 5.1672e-05 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7631 |  | 2005-09-30 15:00 | 2005-09-30 | 2005-09-30 17:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 87 | 19353 | 11049 | 0.57092 | 0.0044954 | 0 | 0 | 2005/2006 | September-2005 | 9 | 2005
7632 |  | 2005-10-03 08:01 | 2005-10-03 | 2005-10-03 09:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 59 | 1 | 19353 | 59 | 0.00305 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7633 |  | 2005-10-03 10:09 | 2005-10-03 | 2005-10-03 11:25 | Calculated | O410E |  |  |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 76 | 32 | 19353 | 2440 | 0.12608 | 0.0016535 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7634 |  | 2005-10-03 14:21 | 2005-10-03 | 2005-10-03 15:45 | Calculated | O410E | LF |  |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 2 | 19353 | 168 | 0.00868 | 0.00010334 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7635 |  | 2005-10-04 06:45 | 2005-10-04 | 2005-10-04 09:37 | Calculated | O410E | L584 | Drop-Out Fuses |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 172 | 66 | 19353 | 11352 | 0.58658 | 0.0034103 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7636 |  | 2005-10-04 10:32 | 2005-10-04 | 2005-10-04 12:52 | Calculated | O410E |  |  |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 140 | 33 | 19353 | 4620 | 0.23872 | 0.0017052 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7637 |  | 2005-10-04 12:21 | 2005-10-04 | 2005-10-04 16:21 | Calculated | O410E |  |  |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 240 | 9 | 19353 | 2160 | 0.11161 | 0.00046504 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7638 |  | 2005-10-04 14:01 | 2005-10-04 | 2005-10-04 14:48 | Calculated | O410E |  |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 47 | 3 | 19353 | 141 | 0.00729 | 0.00015501 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7639 |  | 2005-10-04 15:55 | 2005-10-04 | 2005-10-04 16:58 | Calculated | O410E | L697 | Drop-Out Fuses |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 4 | 19353 | 252 | 0.01302 | 0.00020669 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7640 |  | 2005-10-05 06:54 | 2005-10-05 | 2005-10-05 10:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 211 | 3 | 19353 | 633 | 0.03271 | 0.00015501 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7641 |  | 2005-10-05 09:21 | 2005-10-05 | 2005-10-05 12:10 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 169 | 106 | 19353 | 17977 | 0.9289 | 0.0054772 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7642 |  | 2005-10-05 09:25 | 2005-10-05 | 2005-10-05 16:45 | Calculated | O410E |  |  |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 440 | 9 | 19353 | 3960 | 0.20462 | 0.00046504 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7643 |  | 2005-10-05 19:26 | 2005-10-05 | 2005-10-06 09:35 | Calculated | O410E | C1616 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Spark Gaps | Weather | Lightning |  | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 849 | 15 | 19353 | 12735 | 0.65804 | 0.00077507 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7644 |  | 2005-10-06 06:50 | 2005-10-06 | 2005-10-06 08:54 | Calculated | O410E | C591 | Single Circuit |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation | OH Lines : Binder / Stirrup | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 44 | 19353 | 5456 | 0.28192 | 0.0022735 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7645 |  | 2005-10-06 09:33 | 2005-10-06 | 2005-10-06 12:03 | Calculated | O410E |  |  |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 150 | 66 | 19353 | 9911 | 0.51212 | 0.0034103 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7646 |  | 2005-10-06 10:56 | 2005-10-06 | 2005-10-06 14:21 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 205 | 7 | 19353 | 1435 | 0.07415 | 0.0003617 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7647 |  | 2005-10-06 20:07 | 2005-10-06 | 2005-10-06 20:45 | Calculated | O410E | L526 | Drop-Out Fuses |  | Caves 101-03 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 38 | 6 | 19353 | 228 | 0.01178 | 0.00031003 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7648 |  | 2005-10-06 23:43 | 2005-10-06 | 2005-10-07 05:40 | Calculated | O410E | C1519 | Single Circuit |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 357 | 19 | 19353 | 6791 | 0.3509 | 0.00098176 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7650 |  | 2005-10-08 03:14 | 2005-10-08 | 2005-10-08 05:30 | Calculated | O410E | C378 | Single Circuit |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Insulator - Pin | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 202 | 19353 | 27525 | 1.4223 | 0.010438 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7651 |  | 2005-10-08 07:50 | 2005-10-08 | 2005-10-08 08:41 | Calculated | O410E | ABS 140, 142 & 161 | Control Equipment |  |  | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Miscellaneous : SCADA Out Station | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 327 | 19353 | 16845 | 0.87041 | 0.016897 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7652 |  | 2005-10-08 08:13 | 2005-10-08 | 2005-10-08 10:42 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 149 | 6 | 19353 | 898 | 0.0464 | 0.00031003 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7653 |  | 2005-10-08 08:15 | 2005-10-08 | 2005-10-08 11:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-02 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 185 | 18 | 19353 | 3340 | 0.17258 | 0.00093009 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7654 |  | 2005-10-08 12:07 | 2005-10-08 | 2005-10-08 15:17 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 190 | 1 | 19353 | 190 | 0.00982 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7655 |  | 2005-10-08 12:27 | 2005-10-08 | 2005-10-08 13:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 74 | 17 | 19353 | 1267 | 0.06547 | 0.00087842 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7656 |  | 2005-10-08 14:37 | 2005-10-08 | 2005-10-08 15:26 | Calculated | O410E | C683 | Single Circuit |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 350 | 19353 | 17167 | 0.88705 | 0.018085 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7657 |  | 2005-10-08 15:23 | 2005-10-08 | 2005-10-08 17:50 | Calculated | O410E | C459 |  |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 17 | 19353 | 2499 | 0.12913 | 0.00087842 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7658 |  | 2005-10-08 15:42 | 2005-10-08 | 2005-10-08 18:51 | Calculated | O410E | LF | Single Circuit |  | Otorohanga 112-07 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 189 | 2 | 19353 | 378 | 0.01953 | 0.00010334 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7659 |  | 2005-10-08 16:19 | 2005-10-08 | 2005-10-08 18:51 | Calculated | O410E | LF | Pole Mounted |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 1 | 19353 | 152 | 0.00785 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7660 |  | 2005-10-08 16:42 | 2005-10-08 | 2005-10-08 17:46 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 64 | 4 | 19353 | 256 | 0.01323 | 0.00020669 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7661 |  | 2005-10-08 16:51 | 2005-10-08 | 2005-10-08 18:48 | Calculated | O410E | L368 | Drop-Out Fuses |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 117 | 24 | 19353 | 2808 | 0.14509 | 0.0012401 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7662 |  | 2005-10-09 10:55 | 2005-10-09 | 2005-10-09 12:10 | Calculated | O410E | LF | Pole Mounted |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7663 |  | 2005-10-10 06:24 | 2005-10-10 | 2005-10-10 09:43 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 199 | 10 | 19353 | 1994 | 0.10303 | 0.00051672 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7664 |  | 2005-10-10 06:54 | 2005-10-10 | 2005-10-10 09:56 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 182 | 4 | 19353 | 728 | 0.03762 | 0.00020669 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7665 |  | 2005-10-10 08:10 | 2005-10-10 | 2005-10-10 09:17 | Calculated | O410E | L1529 | Drop-Out Fuses |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 2 | 19353 | 134 | 0.00692 | 0.00010334 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7666 |  | 2005-10-10 09:50 | 2005-10-10 | 2005-10-10 11:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 120 | 1 | 19353 | 120 | 0.0062 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7667 |  | 2005-10-11 08:58 | 2005-10-11 | 2005-10-11 15:35 | Calculated | O410E |  |  |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 397 | 247 | 19353 | 98264 | 5.0775 | 0.012763 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7668 |  | 2005-10-11 09:03 | 2005-10-11 | 2005-10-11 10:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7669 |  | 2005-10-11 09:17 | 2005-10-11 | 2005-10-11 12:55 | Calculated | O410E | LF | Single Circuit |  | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare Copper | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 218 | 1 | 19353 | 218 | 0.01126 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7670 |  | 2005-10-11 14:02 | 2005-10-11 | 2005-10-11 15:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 84 | 2 | 19353 | 168 | 0.00868 | 0.00010334 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7671 |  | 2005-10-11 16:34 | 2005-10-11 | 2005-10-11 17:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 1 | 19353 | 77 | 0.00398 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7672 |  | 2005-10-12 10:01 | 2005-10-12 | 2005-10-12 11:38 | Calculated | O410E | LF |  |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 97 | 4 | 19353 | 388 | 0.02005 | 0.00020669 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7674 |  | 2005-10-12 13:10 | 2005-10-12 | 2005-10-12 14:23 | Calculated | O410E | LV |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 28 | 19353 | 2044 | 0.10562 | 0.0014468 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7675 |  | 2005-10-13 08:10 | 2005-10-13 | 2005-10-13 09:17 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 55 | 19353 | 3685 | 0.19041 | 0.0028419 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7677 |  | 2005-10-13 10:33 | 2005-10-13 | 2005-10-13 13:43 | Calculated | O410E |  |  |  | Aria 114-03 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 36 | 19353 | 6840 | 0.35343 | 0.0018602 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7678 |  | 2005-10-13 10:43 | 2005-10-13 | 2005-10-13 12:13 | Calculated | O410E | L & B RG 3 | Single Circuit |  | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 154 | 19353 | 13860 | 0.71617 | 0.0079574 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7679 |  | 2005-10-14 10:01 | 2005-10-14 | 2005-10-14 10:25 | Calculated | O410E |  |  |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 24 | 4 | 19353 | 96 | 0.00496 | 0.00020669 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7680 |  | 2005-10-14 10:34 | 2005-10-14 | 2005-10-14 12:42 | Calculated | O410E |  |  |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 128 | 7 | 19353 | 896 | 0.0463 | 0.0003617 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7681 |  | 2005-10-14 13:32 | 2005-10-14 | 2005-10-14 14:00 | Calculated | O410E | LF |  |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 5 | 19353 | 140 | 0.00723 | 0.00025836 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7682 |  | 2005-10-14 19:30 | 2005-10-14 | 2005-10-14 22:51 | Calculated | O410E | C806 | Single Circuit |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 201 | 81 | 19353 | 16302 | 0.84235 | 0.0041854 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7683 |  | 2005-10-17 09:18 | 2005-10-17 | 2005-10-17 10:53 | Calculated | O410E |  |  |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 101 | 19353 | 9674 | 0.49987 | 0.0052188 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7686 |  | 2005-10-18 09:32 | 2005-10-18 | 2005-10-18 11:27 | Calculated | O410E |  |  |  | Rangitoto 106-07 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 26 | 19353 | 3001 | 0.15507 | 0.0013435 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7687 |  | 2005-10-18 11:03 | 2005-10-18 | 2005-10-18 14:07 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 184 | 19 | 19353 | 3496 | 0.18064 | 0.00098176 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7689 |  | 2005-10-19 09:32 | 2005-10-19 | 2005-10-19 12:05 | Calculated | O410E |  |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 217 | 19353 | 33201 | 1.7155 | 0.011213 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7690 |  | 2005-10-19 10:35 | 2005-10-19 | 2005-10-19 11:45 | Calculated | O410E |  |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 70 | 36 | 19353 | 2520 | 0.13021 | 0.0018602 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7691 |  | 2005-10-19 12:07 | 2005-10-19 | 2005-10-19 12:40 | Calculated | O410E | LF |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 1 | 19353 | 33 | 0.00171 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7692 |  | 2005-10-19 13:17 | 2005-10-19 | 2005-10-19 14:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 76 | 1 | 19353 | 76 | 0.00393 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7693 |  | 2005-10-20 08:54 | 2005-10-20 | 2005-10-20 10:14 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 80 | 29 | 19353 | 2320 | 0.11988 | 0.0014985 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7694 |  | 2005-10-20 12:33 | 2005-10-20 | 2005-10-20 16:13 | Calculated | O410E | S528 | Single Circuit |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation | OH Lines : Pole - Pre-Stressed Concrete | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 220 | 217 | 19353 | 47740 | 2.4668 | 0.011213 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7695 |  | 2005-10-21 03:43 | 2005-10-21 | 2005-10-21 03:53 | Calculated | O410E | C120 |  |  | Gravel Scoop 109-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 258 | 19353 | 2580 | 0.13331 | 0.013331 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7696 |  | 2005-10-21 11:37 | 2005-10-21 | 2005-10-21 13:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 113 | 2 | 19353 | 227 | 0.01173 | 0.00010334 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7697 |  | 2005-10-21 11:58 | 2005-10-21 | 2005-10-21 13:30 | Calculated | O410E | L424 | Drop-Out Fuses |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 24 | 19353 | 2208 | 0.11409 | 0.0012401 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7698 |  | 2005-10-21 17:16 | 2005-10-21 | 2005-10-21 18:43 | Calculated | O410E | S320 | Single Circuit |  | McDonalds 110-02 | Remote Rural F | McDonalds | Te Waireka Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 71 | 19353 | 6177 | 0.31918 | 0.0036687 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7699 |  | 2005-10-21 18:07 | 2005-10-21 | 2005-10-21 19:44 | Calculated | O410E | C119 | Single Circuit |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 122 | 19353 | 11899 | 0.61484 | 0.0063039 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7701 |  | 2005-10-22 08:30 | 2005-10-22 | 2005-10-22 10:34 | Calculated | O410E | L480 | Single Circuit |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 14 | 19353 | 1736 | 0.0897 | 0.0007234 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7702 |  | 2005-10-22 19:24 | 2005-10-22 | 2005-10-22 20:59 | Calculated | O410E | LF | Pole Mounted |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 7 | 19353 | 665 | 0.03436 | 0.0003617 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7703 |  | 2005-10-25 12:45 | 2005-10-25 | 2005-10-25 14:52 | Calculated | O410E | LF | Drop-Out Fuses |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 1 | 19353 | 127 | 0.00656 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7704 |  | 2005-10-25 13:15 | 2005-10-25 | 2005-10-25 14:55 | Calculated | O410E | L455 | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 100 | 30 | 19353 | 3000 | 0.15501 | 0.0015501 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7705 |  | 2005-10-25 13:45 | 2005-10-25 | 2005-10-25 14:17 | Calculated | O410E | L443 |  |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 11 | 19353 | 352 | 0.01819 | 0.00056839 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7706 |  | 2005-10-25 18:19 | 2005-10-25 | 2005-10-25 19:40 | Calculated | O410E | L292 | Single Circuit |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Surge Diverters | Weather | Lightning |  | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 5 | 19353 | 405 | 0.02093 | 0.00025836 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7707 |  | 2005-10-26 09:40 | 2005-10-26 | 2005-10-26 10:11 | Calculated | O410E |  |  |  | Tihoi 124-03 (was Tihoi 124-06) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 31 | 52 | 19353 | 1654 | 0.08546 | 0.0026869 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7708 |  | 2005-10-26 10:33 | 2005-10-26 | 2005-10-26 14:38 | Calculated | O410E |  |  |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 33 | 19353 | 8085 | 0.41776 | 0.0017052 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7709 |  | 2005-10-26 10:33 | 2005-10-26 | 2005-10-26 11:19 | Calculated | O410E | LF |  |  | Gravel Scoop 109-01 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 26 | 19353 | 1218 | 0.06294 | 0.0013435 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7710 |  | 2005-10-26 12:47 | 2005-10-26 | 2005-10-26 20:30 | Calculated | O410E | LF | Paper/Lead - Laid Direct |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Cables : Cable Core - Phase | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 463 | 16 | 19353 | 7408 | 0.38278 | 0.00082675 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7711 |  | 2005-10-26 18:49 | 2005-10-26 | 2005-10-26 21:25 | Calculated | O410E | LF | Pole Mounted |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 156 | 1 | 19353 | 156 | 0.00806 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7712 |  | 2005-10-27 09:14 | 2005-10-27 | 2005-10-27 09:58 | Calculated | O410E |  |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 44 | 119 | 19353 | 5236 | 0.27055 | 0.0061489 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7713 |  | 2005-10-27 13:30 | 2005-10-27 | 2005-10-27 15:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 105 | 3 | 19353 | 315 | 0.01628 | 0.00015501 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7714 |  | 2005-10-27 17:46 | 2005-10-27 | 2005-10-27 18:05 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 16 | 19353 | 304 | 0.01571 | 0.00082675 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7715 |  | 2005-10-28 03:47 | 2005-10-28 | 2005-10-28 03:57 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1 | 19353 | 10 | 0.00052 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7716 |  | 2005-10-28 12:52 | 2005-10-28 | 2005-10-28 13:23 | Calculated | O410E | L606 | Single Circuit |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 6 | 19353 | 186 | 0.00961 | 0.00031003 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
3982 |  | 2005-10-30 | 2005-10-30 | 2005-10-30 03:10 | Calculated | O410E |  |  |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 2 | 19353 | 380 | 0.01964 | 0.00010334 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7717 |  | 2005-10-31 07:00 | 2005-10-31 | 2005-10-31 07:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 0 | 2 | 19353 | 0 | 0 | 0.00010334 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7718 |  | 2005-10-31 08:23 | 2005-10-31 | 2005-10-31 10:31 | Calculated | O410E | L431 | Drop-Out Fuses |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 128 | 5 | 19353 | 640 | 0.03307 | 0.00025836 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7719 |  | 2005-10-31 09:33 | 2005-10-31 | 2005-10-31 13:18 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 225 | 30 | 19353 | 6774 | 0.35002 | 0.0015501 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7721 |  | 2005-10-31 18:00 | 2005-10-31 | 2005-10-31 21:40 | Calculated | O410E | LF | Pole Mounted |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Transformers : Internal Connections | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 220 | 1 | 19353 | 220 | 0.01137 | 5.1672e-05 | 0 | 0 | 2005/2006 | October-2005 | 10 | 2005
7722 |  | 2005-11-01 09:30 | 2005-11-01 | 2005-11-01 11:23 | Calculated | O410E | L5534 | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 113 | 12 | 19353 | 1356 | 0.07007 | 0.00062006 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7723 |  | 2005-11-01 09:31 | 2005-11-01 | 2005-11-01 13:15 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 224 | 30 | 19353 | 6741 | 0.34832 | 0.0015501 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7724 |  | 2005-11-02 10:32 | 2005-11-02 | 2005-11-02 12:37 | Calculated | O410E |  |  |  | Otorohanga 112-07 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 125 | 10 | 19353 | 1250 | 0.06459 | 0.00051672 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7726 |  | 2005-11-02 10:37 | 2005-11-02 | 2005-11-02 12:26 | Calculated | O410E |  |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 109 | 2 | 19353 | 218 | 0.01126 | 0.00010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7728 |  | 2005-11-02 13:28 | 2005-11-02 | 2005-11-02 14:26 | Calculated | O410E | LF |  |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 2 | 19353 | 116 | 0.00599 | 0.00010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7729 |  | 2005-11-03 10:37 | 2005-11-03 | 2005-11-03 14:07 | Calculated | O410E | LF |  |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 210 | 1 | 19353 | 210 | 0.01085 | 5.1672e-05 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7730 |  | 2005-11-03 11:16 | 2005-11-03 | 2005-11-03 13:00 | Calculated | O410E | LF |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 104 | 4 | 19353 | 416 | 0.0215 | 0.00020669 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7731 |  | 2005-11-04 07:58 | 2005-11-04 | 2005-11-04 08:43 | Calculated | O410E | LF |  |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 2 | 19353 | 90 | 0.00465 | 0.00010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7733 |  | 2005-11-04 10:02 | 2005-11-04 | 2005-11-04 11:15 | Calculated | O410E | LF |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 7 | 19353 | 511 | 0.0264 | 0.0003617 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7734 |  | 2005-11-04 14:04 | 2005-11-04 | 2005-11-04 14:55 | Calculated | O410E |  |  |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 10 | 19353 | 510 | 0.02635 | 0.00051672 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7735 |  | 2005-11-06 13:00 | 2005-11-06 | 2005-11-06 14:32 | Calculated | O410E | LF | Pole Mounted |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 19353 | 92 | 0.00475 | 5.1672e-05 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7738 |  | 2005-11-08 10:11 | 2005-11-08 | 2005-11-08 13:37 | Calculated | O410E | LF |  |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 206 | 3 | 19353 | 618 | 0.03193 | 0.00015501 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7739 |  | 2005-11-08 10:32 | 2005-11-08 | 2005-11-08 10:33 | Calculated | O410E |  |  |  | Otorohanga 112-07 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2005/2006 | November-2005 | 11 | 2005
25074 | Replacing Structure Tx224 | 2005-11-08 10:33 | 2005-11-08 | 2005-11-08 14:45 | Calculated | 637 | 637 - Air Berak Switch 637 |  | 112SEG637-352 | Otorohanga 112-07 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 252 | 10 | 19353 | 2520 | 0.13021 | 0.00051672 | 130 | 32766 | 2005/2006 | November-2005 | 11 | 2005
7740 |  | 2005-11-09 09:33 | 2005-11-09 | 2005-11-09 11:32 | Calculated | O410E |  |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 29 | 19353 | 3477 | 0.17966 | 0.0014985 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7742 |  | 2005-11-09 13:38 | 2005-11-09 | 2005-11-09 16:04 | Calculated | O410E | C1042 |  |  |  | Remote Rural F | Lake Taupo 33 | Direct from Tokaanu Supply |  | Asset Related | Other |  | Accidental Contact, Damage or Interference by TLC Staff | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 146 | 598 | 19353 | 87308 | 4.5113 | 0.0309 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7743 |  | 2005-11-10 09:46 | 2005-11-10 | 2005-11-10 14:21 | Calculated | O410E | LF |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 275 | 1 | 19353 | 275 | 0.01421 | 5.1672e-05 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7744 |  | 2005-11-10 10:35 | 2005-11-10 | 2005-11-10 15:02 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 267 | 24 | 19353 | 6408 | 0.33111 | 0.0012401 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7746 |  | 2005-11-11 10:37 | 2005-11-11 | 2005-11-11 13:14 | Calculated | O410E |  |  |  | Te Kuiti Town 105-01 | Remote Rural F | Te Kuiti Town | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 157 | 16 | 19353 | 2512 | 0.1298 | 0.00082675 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7748 |  | 2005-11-13 11:01 | 2005-11-13 | 2005-11-13 16:28 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 227 | 19353 | 74229 | 3.8355 | 0.011729 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7751 |  | 2005-11-15 10:00 | 2005-11-15 | 2005-11-15 10:06 | Calculated | O410E | LV |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 6 | 8 | 19353 | 48 | 0.00248 | 0.00041337 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7752 |  | 2005-11-15 10:59 | 2005-11-15 | 2005-11-15 12:41 | Calculated | O410E | LF |  |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 2 | 19353 | 204 | 0.01054 | 0.00010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7753 |  | 2005-11-15 14:06 | 2005-11-15 | 2005-11-15 15:07 | Calculated | O410E |  |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 24 | 19353 | 1464 | 0.07565 | 0.0012401 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7754 |  | 2005-11-16 08:34 | 2005-11-16 | 2005-11-16 09:19 | Calculated | O410E | L502 | Single Circuit |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 2 | 19353 | 90 | 0.00465 | 0.00010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7755 |  | 2005-11-16 08:48 | 2005-11-16 | 2005-11-16 08:50 | Calculated | O410E | C1102 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 1415 | 19353 | 2830 | 0.14623 | 0.073115 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7756 |  | 2005-11-16 09:52 | 2005-11-16 | 2005-11-16 10:25 | Calculated | O410E | LF |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 2 | 19353 | 66 | 0.00341 | 0.00010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7757 |  | 2005-11-16 10:01 | 2005-11-16 | 2005-11-16 11:01 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 20 | 19353 | 1200 | 0.06201 | 0.0010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7760 |  | 2005-11-17 08:04 | 2005-11-17 | 2005-11-17 11:20 | Calculated | O410E |  |  |  | National Park 411-02 | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 196 | 6 | 19353 | 1176 | 0.06077 | 0.00031003 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7761 |  | 2005-11-17 09:18 | 2005-11-17 | 2005-11-17 09:51 | Calculated | O410E | C156 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 33 | 75 | 19353 | 2475 | 0.12789 | 0.0038754 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7762 |  | 2005-11-17 15:01 | 2005-11-17 | 2005-11-17 16:53 | Calculated | O410E | C2082 | PVC/Polythene - Laid Direct |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation | Cables : Pole Termination - Raychem | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 112 | 443 | 19353 | 49667 | 2.5664 | 0.022891 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7763 |  | 2005-11-18 07:15 | 2005-11-18 | 2005-11-18 08:54 | Calculated | O410E | L892 |  |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 17 | 19353 | 1683 | 0.08696 | 0.00087842 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7764 |  | 2005-11-18 08:15 | 2005-11-18 | 2005-11-18 10:52 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 157 | 17 | 19353 | 2669 | 0.13791 | 0.00087842 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7766 |  | 2005-11-19 08:01 | 2005-11-19 | 2005-11-19 08:10 | Calculated | O410E | C798 |  |  |  | Remote Rural F | Wairere / Mahoenui 33 | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 500 | 19353 | 4500 | 0.23252 | 0.025836 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7767 |  | 2005-11-20 12:00 | 2005-11-20 | 2005-11-20 13:43 | Calculated | O410E | L239 | Drop-Out Fuses |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 103 | 20 | 19353 | 2060 | 0.10644 | 0.0010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7768 |  | 2005-11-21 14:37 | 2005-11-21 | 2005-11-21 16:12 | Calculated | O410E | L654 | Drop-Out Fuses |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 3 | 19353 | 285 | 0.01473 | 0.00015501 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7769 |  | 2005-11-21 16:58 | 2005-11-21 | 2005-11-21 17:21 | Calculated | O410E | S996 |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 160 | 19353 | 3680 | 0.19015 | 0.0082675 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7770 |  | 2005-11-22 08:23 | 2005-11-22 | 2005-11-22 09:09 | Calculated | O410E | LF | Single Circuit |  | McDonalds 110-02 | Remote Rural F | McDonalds | Te Waireka Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 1 | 19353 | 46 | 0.00238 | 5.1672e-05 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7771 |  | 2005-11-22 10:24 | 2005-11-22 | 2005-11-22 12:24 | Calculated | O410E |  |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 52 | 19353 | 6243 | 0.32259 | 0.0026869 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7772 |  | 2005-11-23 09:59 | 2005-11-23 | 2005-11-23 12:44 | Calculated | O410E | LV |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 165 | 14 | 19353 | 2310 | 0.11936 | 0.0007234 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7773 |  | 2005-11-23 10:30 | 2005-11-23 | 2005-11-23 11:04 | Calculated | O410E | LF |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 34 | 2 | 19353 | 68 | 0.00351 | 0.00010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7775 |  | 2005-11-24 08:35 | 2005-11-24 | 2005-11-24 10:21 | Calculated | O410E |  |  |  | National Park 411-02 | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 106 | 3 | 19353 | 318 | 0.01643 | 0.00015501 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7776 |  | 2005-11-24 10:02 | 2005-11-24 | 2005-11-24 14:34 | Calculated | O410E |  |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 4 | 19353 | 1088 | 0.05622 | 0.00020669 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7779 |  | 2005-11-25 09:08 | 2005-11-25 | 2005-11-25 13:59 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 291 | 15 | 19353 | 4365 | 0.22555 | 0.00077507 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7780 |  | 2005-11-25 09:34 | 2005-11-25 | 2005-11-25 11:52 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 138 | 20 | 19353 | 2760 | 0.14261 | 0.0010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7782 |  | 2005-11-25 10:00 | 2005-11-25 | 2005-11-25 11:50 | Calculated | O410E | S290 | Single Circuit |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 7 | 19353 | 774 | 0.03999 | 0.0003617 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7781 |  | 2005-11-25 10:34 | 2005-11-25 | 2005-11-25 12:12 | Calculated | O410E |  |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 98 | 6 | 19353 | 588 | 0.03038 | 0.00031003 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7784 |  | 2005-11-26 00:31 | 2005-11-26 | 2005-11-26 00:32 | Calculated | O410E | C132 |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2005/2006 | November-2005 | 11 | 2005
7785 |  | 2005-11-27 19:41 | 2005-11-27 | 2005-11-27 22:05 | Calculated | O410E | C1072 | Single Circuit |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 108 | 19353 | 15638 | 0.80804 | 0.0055805 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7786 |  | 2005-11-28 01:30 | 2005-11-28 | 2005-11-28 01:40 | Calculated | O410E | C594 & 754 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1574 | 19353 | 15740 | 0.81331 | 0.081331 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7787 |  | 2005-11-28 08:00 | 2005-11-28 | 2005-11-28 08:40 | Calculated | O410E | L475 | Drop-Out Fuses |  | Tihoi 124-03 (was Tihoi 124-06) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 40 | 41 | 19353 | 1640 | 0.08474 | 0.0021185 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7788 |  | 2005-11-28 08:00 | 2005-11-28 | 2005-11-28 09:06 | Calculated | O410E | C5534 |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 12 | 19353 | 792 | 0.04092 | 0.00062006 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7789 |  | 2005-11-28 08:43 | 2005-11-28 | 2005-11-28 10:25 | Calculated | O410E | C811 |  |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 20 | 19353 | 2040 | 0.10541 | 0.0010334 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7790 |  | 2005-11-28 09:22 | 2005-11-28 | 2005-11-28 12:20 | Calculated | O410E | LF |  |  | Turoa 415-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 178 | 29 | 19353 | 5162 | 0.26673 | 0.0014985 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7791 |  | 2005-11-28 10:00 | 2005-11-28 | 2005-11-28 13:18 | Calculated | O410E |  |  |  | Caves 101-07 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 198 | 13 | 19353 | 2578 | 0.13321 | 0.00067173 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7792 |  | 2005-11-28 10:33 | 2005-11-28 | 2005-11-28 11:58 | Calculated | O410E |  |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 85 | 9 | 19353 | 765 | 0.03953 | 0.00046504 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7794 |  | 2005-11-28 12:33 | 2005-11-28 | 2005-11-28 15:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 162 | 7 | 19353 | 1134 | 0.0586 | 0.0003617 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7793 |  | 2005-11-28 14:13 | 2005-11-28 | 2005-11-28 15:34 | Calculated | O410E | C62 | Single Circuit |  |  | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 81 | 369 | 19353 | 30067 | 1.5536 | 0.019067 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7795 |  | 2005-11-28 15:59 | 2005-11-28 | 2005-11-28 16:54 | Calculated | O410E | C378 | Single Circuit |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 203 | 19353 | 11225 | 0.58001 | 0.010489 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7796 |  | 2005-11-28 16:04 | 2005-11-28 | 2005-11-28 18:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 174 | 1 | 19353 | 174 | 0.00899 | 5.1672e-05 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7797 |  | 2005-11-28 17:23 | 2005-11-28 | 2005-11-28 18:46 | Calculated | O410E | C429 | Single Circuit |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 78 | 19353 | 6490 | 0.33535 | 0.0040304 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7798 |  | 2005-11-29 09:05 | 2005-11-29 | 2005-11-29 16:11 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 426 | 1 | 19353 | 426 | 0.02201 | 5.1672e-05 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7800 |  | 2005-11-29 10:34 | 2005-11-29 | 2005-11-29 12:51 | Calculated | O410E |  |  |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 137 | 39 | 19353 | 5354 | 0.27665 | 0.0020152 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7802 |  | 2005-11-29 14:37 | 2005-11-29 | 2005-11-29 15:44 | Calculated | O410E | C379 |  |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 25 | 19353 | 1675 | 0.08655 | 0.0012918 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7803 |  | 2005-11-30 09:32 | 2005-11-30 | 2005-11-30 15:27 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 16 | 19353 | 5680 | 0.29349 | 0.00082675 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7804 |  | 2005-11-30 10:02 | 2005-11-30 | 2005-11-30 13:15 | Calculated | O410E |  |  |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 193 | 16 | 19353 | 3092 | 0.15977 | 0.00082675 | 0 | 0 | 2005/2006 | November-2005 | 11 | 2005
7805 |  | 2005-12-01 08:41 | 2005-12-01 | 2005-12-01 12:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 225 | 2 | 19353 | 450 | 0.02325 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7806 |  | 2005-12-01 09:12 | 2005-12-01 | 2005-12-01 13:01 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 229 | 1 | 19353 | 229 | 0.01183 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7807 |  | 2005-12-01 09:26 | 2005-12-01 | 2005-12-01 12:03 | Calculated | O410E | C6132 |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 577 | 19353 | 91156 | 4.7102 | 0.029814 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7808 |  | 2005-12-02 10:30 | 2005-12-02 | 2005-12-02 15:03 | Calculated | O410E |  |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 273 | 16 | 19353 | 4368 | 0.2257 | 0.00082675 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7811 |  | 2005-12-04 14:01 | 2005-12-04 | 2005-12-04 14:11 | Calculated | O410E | C2092 |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 105 | 19353 | 1050 | 0.05426 | 0.0054255 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7812 |  | 2005-12-05 05:23 | 2005-12-05 | 2005-12-05 08:37 | Calculated | O410E | C768 | Drop-Out Fuses |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Bushings (fixed Insulation) | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 194 | 43 | 19353 | 8380 | 0.43301 | 0.0022219 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7814 |  | 2005-12-05 06:12 | 2005-12-05 | 2005-12-05 06:55 | Calculated | O410E | C212 | Single Circuit |  |  | Remote Rural F | National Park 33 | Direct from National Park Supply | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 43 | 629 | 19353 | 27623 | 1.4273 | 0.032501 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7815 |  | 2005-12-05 10:40 | 2005-12-05 | 2005-12-05 12:21 | Calculated | O410E | LF |  |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 101 | 2 | 19353 | 202 | 0.01044 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7816 |  | 2005-12-06 09:00 | 2005-12-06 | 2005-12-06 13:05 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 15 | 19353 | 3675 | 0.18989 | 0.00077507 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7817 |  | 2005-12-06 09:51 | 2005-12-06 | 2005-12-06 11:13 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 240 | 19353 | 19784 | 1.0223 | 0.012401 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7818 |  | 2005-12-06 10:28 | 2005-12-06 | 2005-12-06 12:32 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 124 | 4 | 19353 | 496 | 0.02563 | 0.00020669 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7819 |  | 2005-12-06 10:28 | 2005-12-06 | 2005-12-06 12:29 | Calculated | O410E | C758 | Drop-Out Fuses |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 121 | 88 | 19353 | 10706 | 0.5532 | 0.0045471 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7834 |  | 2005-12-06 10:28 | 2005-12-06 | 2005-12-06 11:14 | Calculated | O410E | C1640 | Pole Mounted |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 480 | 19353 | 22120 | 1.143 | 0.024802 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7820 |  | 2005-12-06 10:58 | 2005-12-06 | 2005-12-06 13:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-04 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 170 | 6 | 19353 | 1023 | 0.05286 | 0.00031003 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7821 |  | 2005-12-06 11:12 | 2005-12-06 | 2005-12-06 12:48 | Calculated | O410E | L1539 | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 8 | 19353 | 772 | 0.03989 | 0.00041337 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7822 |  | 2005-12-06 11:19 | 2005-12-06 | 2005-12-06 12:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-04 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 78 | 51 | 19353 | 4003 | 0.20684 | 0.0026353 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7823 |  | 2005-12-06 11:21 | 2005-12-06 | 2005-12-06 13:53 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 152 | 13 | 19353 | 1976 | 0.1021 | 0.00067173 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7824 |  | 2005-12-06 12:00 | 2005-12-06 | 2005-12-06 13:27 | Calculated | O410E | L475 | Drop-Out Fuses |  | Tihoi 124-03 (was Tihoi 124-06) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 87 | 57 | 19353 | 5000 | 0.25836 | 0.0029453 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7825 |  | 2005-12-06 12:06 | 2005-12-06 | 2005-12-06 13:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 102 | 4 | 19353 | 410 | 0.02119 | 0.00020669 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7826 |  | 2005-12-06 12:08 | 2005-12-06 | 2005-12-06 14:17 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 129 | 2 | 19353 | 258 | 0.01333 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7827 |  | 2005-12-06 12:13 | 2005-12-06 | 2005-12-06 14:16 | Calculated | O410E | L674 | Drop-Out Fuses |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 123 | 18 | 19353 | 2224 | 0.11492 | 0.00093009 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7828 |  | 2005-12-06 12:28 | 2005-12-06 | 2005-12-06 14:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 151 | 2 | 19353 | 302 | 0.0156 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7829 |  | 2005-12-06 12:34 | 2005-12-06 | 2005-12-06 16:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 233 | 5 | 19353 | 1168 | 0.06035 | 0.00025836 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7830 |  | 2005-12-06 12:43 | 2005-12-06 | 2005-12-06 19:40 | Calculated | O410E | LF | Pole Mounted |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 417 | 1 | 19353 | 417 | 0.02155 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7831 |  | 2005-12-06 12:58 | 2005-12-06 | 2005-12-06 19:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 362 | 1 | 19353 | 362 | 0.01871 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7832 |  | 2005-12-06 13:01 | 2005-12-06 | 2005-12-06 18:39 | Calculated | O410E | LF | Pole Mounted |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 338 | 2 | 19353 | 676 | 0.03493 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7833 |  | 2005-12-06 14:23 | 2005-12-06 | 2005-12-06 18:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 276 | 1 | 19353 | 276 | 0.01426 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7835 |  | 2005-12-07 07:45 | 2005-12-07 | 2005-12-07 09:24 | Calculated | O410E | C1641 |  |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 8 | 19353 | 792 | 0.04092 | 0.00041337 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7836 |  | 2005-12-07 08:42 | 2005-12-07 | 2005-12-07 10:43 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-08 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 121 | 1 | 19353 | 121 | 0.00625 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7837 |  | 2005-12-07 09:31 | 2005-12-07 | 2005-12-07 14:33 | Calculated | O410E | LF | Pole Mounted |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | Transformers : Tank | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 302 | 1 | 19353 | 302 | 0.0156 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7838 |  | 2005-12-07 09:37 | 2005-12-07 | 2005-12-07 15:09 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 332 | 240 | 19353 | 79680 | 4.1172 | 0.012401 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7839 |  | 2005-12-07 11:58 | 2005-12-07 | 2005-12-07 13:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 1 | 19353 | 67 | 0.00346 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7840 |  | 2005-12-08 08:00 | 2005-12-08 | 2005-12-08 13:45 | Calculated | O410E | L1725 | Drop-Out Fuses |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 345 | 6 | 19353 | 2070 | 0.10696 | 0.00031003 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7841 |  | 2005-12-08 08:12 | 2005-12-08 | 2005-12-08 09:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 89 | 1 | 19353 | 89 | 0.0046 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7842 |  | 2005-12-08 08:17 | 2005-12-08 | 2005-12-08 10:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 161 | 1 | 19353 | 161 | 0.00832 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7843 |  | 2005-12-08 09:00 | 2005-12-08 | 2005-12-08 15:08 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 368 | 12 | 19353 | 4416 | 0.22818 | 0.00062006 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7845 |  | 2005-12-08 12:47 | 2005-12-08 | 2005-12-08 13:58 | Calculated | O410E | LF |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 1 | 19353 | 71 | 0.00367 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7846 |  | 2005-12-09 09:31 | 2005-12-09 | 2005-12-09 12:31 | Calculated | O410E |  |  |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 180 | 20 | 19353 | 3600 | 0.18602 | 0.0010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7847 |  | 2005-12-09 12:28 | 2005-12-09 | 2005-12-09 14:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 117 | 1 | 19353 | 117 | 0.00605 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7848 |  | 2005-12-09 12:47 | 2005-12-09 | 2005-12-09 15:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 137 | 2 | 19353 | 274 | 0.01416 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7849 |  | 2005-12-09 17:41 | 2005-12-09 | 2005-12-09 18:35 | Calculated | O410E | S709 | Drop-Out Fuses |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 54 | 35 | 19353 | 1890 | 0.09766 | 0.0018085 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7850 |  | 2005-12-09 18:22 | 2005-12-09 | 2005-12-09 21:28 | Calculated | O410E | L855 | Pole Mounted |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 24 | 19353 | 4464 | 0.23066 | 0.0012401 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7851 |  | 2005-12-09 18:33 | 2005-12-09 | 2005-12-09 20:16 | Calculated | O410E | L485 | Drop-Out Fuses |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 103 | 12 | 19353 | 1244 | 0.06428 | 0.00062006 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7852 |  | 2005-12-09 18:40 | 2005-12-09 | 2005-12-09 21:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 145 | 2 | 19353 | 290 | 0.01498 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7853 |  | 2005-12-10 02:17 | 2005-12-10 | 2005-12-10 03:26 | Calculated | O410E | C426 |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 78 | 19353 | 5443 | 0.28125 | 0.0040304 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7854 |  | 2005-12-10 05:49 | 2005-12-10 | 2005-12-10 08:10 | Calculated | O410E | L209 |  |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 32 | 19353 | 4512 | 0.23314 | 0.0016535 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7855 |  | 2005-12-11 15:40 | 2005-12-11 | 2005-12-11 17:25 | Calculated | O410E | L338 | Drop-Out Fuses |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 105 | 7 | 19353 | 738 | 0.03813 | 0.0003617 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7856 |  | 2005-12-11 16:08 | 2005-12-11 | 2005-12-11 17:33 | Calculated | O410E | L433 | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 68 | 19353 | 5787 | 0.29902 | 0.0035137 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7857 |  | 2005-12-11 16:46 | 2005-12-11 | 2005-12-11 17:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 61 | 74 | 19353 | 4520 | 0.23356 | 0.0038237 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7858 |  | 2005-12-11 21:27 | 2005-12-11 | 2005-12-11 23:31 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 124 | 2 | 19353 | 248 | 0.01281 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7859 |  | 2005-12-11 23:51 | 2005-12-11 | 2005-12-11 23:55 | Calculated | O410E | C242 & 796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 240 | 19353 | 960 | 0.0496 | 0.012401 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7860 |  | 2005-12-12 07:55 | 2005-12-12 | 2005-12-12 09:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 115 | 10 | 19353 | 1156 | 0.05973 | 0.00051672 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7861 |  | 2005-12-12 08:08 | 2005-12-12 | 2005-12-12 10:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 163 | 2 | 19353 | 326 | 0.01684 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7862 |  | 2005-12-12 08:13 | 2005-12-12 | 2005-12-12 09:44 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 91 | 1 | 19353 | 91 | 0.0047 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7864 |  | 2005-12-12 09:00 | 2005-12-12 | 2005-12-12 14:53 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 12 | 19353 | 4236 | 0.21888 | 0.00062006 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7863 |  | 2005-12-12 09:03 | 2005-12-12 | 2005-12-12 11:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 135 | 1 | 19353 | 135 | 0.00698 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7865 |  | 2005-12-12 12:05 | 2005-12-12 | 2005-12-12 17:05 | Calculated | O410E | LF | Pole Mounted |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 300 | 2 | 19353 | 600 | 0.031 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7866 |  | 2005-12-13 09:14 | 2005-12-13 | 2005-12-13 16:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Fuse Carriers | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 421 | 1 | 19353 | 421 | 0.02175 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7867 |  | 2005-12-13 10:38 | 2005-12-13 | 2005-12-13 12:48 | Calculated | O410E |  |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 14 | 19353 | 1820 | 0.09404 | 0.0007234 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7868 |  | 2005-12-13 12:03 | 2005-12-13 | 2005-12-13 13:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 87 | 3 | 19353 | 261 | 0.01349 | 0.00015501 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7869 |  | 2005-12-13 18:02 | 2005-12-13 | 2005-12-13 20:28 | Calculated | O410E | C440 |  |  | Southern 409-09 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 24 | 19353 | 3511 | 0.18142 | 0.0012401 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7870 |  | 2005-12-14 10:32 | 2005-12-14 | 2005-12-14 11:18 | Calculated | O410E |  |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 12 | 19353 | 552 | 0.02852 | 0.00062006 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7871 |  | 2005-12-14 11:42 | 2005-12-14 | 2005-12-14 13:55 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Fuse Carriers | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 133 | 1 | 19353 | 133 | 0.00687 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7872 |  | 2005-12-14 12:01 | 2005-12-14 | 2005-12-14 13:43 | Calculated | O410E |  |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 16 | 19353 | 1632 | 0.08433 | 0.00082675 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7873 |  | 2005-12-14 14:01 | 2005-12-14 | 2005-12-14 14:36 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 35 | 41 | 19353 | 1435 | 0.07415 | 0.0021185 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7874 |  | 2005-12-14 14:30 | 2005-12-14 | 2005-12-14 16:31 | Calculated | O410E | C1346 |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 6 | 19353 | 726 | 0.03751 | 0.00031003 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7875 |  | 2005-12-14 18:56 | 2005-12-14 | 2005-12-14 20:13 | Calculated | O410E | L456 | Drop-Out Fuses |  | Ohura 413-07 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 12 | 19353 | 926 | 0.04785 | 0.00062006 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7876 |  | 2005-12-14 19:27 | 2005-12-14 | 2005-12-14 21:28 | Calculated | O410E | C489 |  |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 24 | 19353 | 2904 | 0.15005 | 0.0012401 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7877 |  | 2005-12-15 06:17 | 2005-12-15 | 2005-12-15 07:45 | Calculated | O410E | C1626 |  |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 111 | 19353 | 9768 | 0.50473 | 0.0057355 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7879 |  | 2005-12-15 09:36 | 2005-12-15 | 2005-12-15 14:35 | Calculated | O410E |  |  |  | Caves 101-13 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 299 | 7 | 19353 | 2093 | 0.10815 | 0.0003617 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7880 |  | 2005-12-15 09:52 | 2005-12-15 | 2005-12-15 11:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 98 | 1 | 19353 | 98 | 0.00506 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7881 |  | 2005-12-15 12:00 | 2005-12-15 | 2005-12-15 13:01 | Calculated | O410E | L475 | Drop-Out Fuses |  | Tihoi 124-03 (was Tihoi 124-06) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 61 | 53 | 19353 | 3233 | 0.16705 | 0.0027386 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7882 |  | 2005-12-15 18:00 | 2005-12-15 | 2005-12-15 21:51 | Calculated | O410E | LF | Pole Mounted |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 2 | 19353 | 462 | 0.02387 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7883 |  | 2005-12-16 07:30 | 2005-12-16 | 2005-12-16 07:31 | Calculated | O410E | C761 & 570 |  |  |  | Remote Rural F | Te Kawa St 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2005/2006 | December-2005 | 12 | 2005
7884 |  | 2005-12-16 09:06 | 2005-12-16 | 2005-12-16 11:36 | Calculated | O410E | LF |  |  | Southern 409-04 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 150 | 7 | 19353 | 1050 | 0.05426 | 0.0003617 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7886 |  | 2005-12-16 12:01 | 2005-12-16 | 2005-12-16 13:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 89 | 1 | 19353 | 89 | 0.0046 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7887 |  | 2005-12-17 13:16 | 2005-12-17 | 2005-12-17 20:27 | Calculated | O410E | C529 | Single Circuit |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 431 | 42 | 19353 | 18102 | 0.93536 | 0.0021702 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7888 |  | 2005-12-17 16:00 | 2005-12-17 | 2005-12-17 19:32 | Calculated | O410E | C527 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 212 | 25 | 19353 | 5300 | 0.27386 | 0.0012918 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7889 |  | 2005-12-18 07:29 | 2005-12-18 | 2005-12-18 07:30 | Calculated | O410E | C761 & 570 |  |  |  | Remote Rural F | Te Kawa St 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 0 | 19353 | 0 | 0 | 0 | 1 | 0 | 2005/2006 | December-2005 | 12 | 2005
7890 |  | 2005-12-19 07:54 | 2005-12-19 | 2005-12-19 09:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 125 | 1 | 19353 | 125 | 0.00646 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7891 |  | 2005-12-19 09:31 | 2005-12-19 | 2005-12-19 11:11 | Calculated | O410E |  |  |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 112 | 19353 | 11280 | 0.58286 | 0.0057872 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7892 |  | 2005-12-20 09:25 | 2005-12-20 | 2005-12-20 10:03 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 38 | 238 | 19353 | 9044 | 0.46732 | 0.012298 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7893 |  | 2005-12-20 10:14 | 2005-12-20 | 2005-12-20 13:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Nihoniho 412-01 | Remote Rural F | Nihoniho | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 195 | 2 | 19353 | 390 | 0.02015 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7894 |  | 2005-12-20 10:15 | 2005-12-20 | 2005-12-20 13:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 195 | 9 | 19353 | 1757 | 0.09079 | 0.00046504 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7895 |  | 2005-12-20 13:02 | 2005-12-20 | 2005-12-20 15:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 126 | 1 | 19353 | 126 | 0.00651 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7896 |  | 2005-12-20 13:17 | 2005-12-20 | 2005-12-20 15:24 | Calculated | O410E | L433 | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 9 | 19353 | 1143 | 0.05906 | 0.00046504 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7898 |  | 2005-12-20 13:57 | 2005-12-20 | 2005-12-20 17:57 | Calculated | O410E | C1620 | Single Circuit |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 240 | 176 | 19353 | 42342 | 2.1879 | 0.0090942 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7899 |  | 2005-12-21 05:57 | 2005-12-21 | 2005-12-21 08:03 | Calculated | O410E | C5534 |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 12 | 19353 | 1512 | 0.07813 | 0.00062006 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7900 |  | 2005-12-21 10:33 | 2005-12-21 | 2005-12-21 14:08 | Calculated | O410E |  |  |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 215 | 40 | 19353 | 8600 | 0.44438 | 0.0020669 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7901 |  | 2005-12-21 12:09 | 2005-12-21 | 2005-12-21 16:35 | Calculated | O410E | LF | Drop-Out Fuses |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 266 | 2 | 19353 | 532 | 0.02749 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7902 |  | 2005-12-21 16:17 | 2005-12-21 | 2005-12-21 16:58 | Calculated | O410E | L488 | Drop-Out Fuses |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 41 | 1 | 19353 | 41 | 0.00212 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7903 |  | 2005-12-21 21:30 | 2005-12-21 | 2005-12-21 22:24 | Calculated | O410E | S410 | Drop-Out Fuses |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 54 | 21 | 19353 | 1134 | 0.0586 | 0.0010851 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7904 |  | 2005-12-22 02:26 | 2005-12-22 | 2005-12-22 03:19 | Calculated | O410E |  | ABS |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Bushings (fixed Insulation) | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 53 | 223 | 19353 | 11848 | 0.6122 | 0.011523 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7905 |  | 2005-12-22 11:15 | 2005-12-22 | 2005-12-22 13:41 | Calculated | O410E | LF | Pole Mounted |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation | Transformers : External Bushings | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 53 | 19353 | 7738 | 0.39983 | 0.0027386 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7907 |  | 2005-12-22 14:27 | 2005-12-22 | 2005-12-22 15:19 | Calculated | O410E | LF |  |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 3 | 19353 | 156 | 0.00806 | 0.00015501 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7908 |  | 2005-12-22 14:38 | 2005-12-22 | 2005-12-22 15:47 | Calculated | O410E | LF | Pole Mounted |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 19353 | 69 | 0.00357 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7909 |  | 2005-12-23 08:00 | 2005-12-23 | 2005-12-23 09:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 107 | 1 | 19353 | 107 | 0.00553 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7910 |  | 2005-12-23 08:12 | 2005-12-23 | 2005-12-23 10:47 | Calculated | O410E | C1616 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 15 | 19353 | 2325 | 0.12014 | 0.00077507 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7911 |  | 2005-12-23 10:37 | 2005-12-23 | 2005-12-23 12:23 | Calculated | O410E | LF | Drop-Out Fuses |  | Tuhua 422-02 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 106 | 1 | 19353 | 106 | 0.00548 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7912 |  | 2005-12-23 14:01 | 2005-12-23 | 2005-12-23 15:17 | Calculated | O410E | C1343 |  |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 83 | 19353 | 6308 | 0.32594 | 0.0042887 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7913 |  | 2005-12-23 14:11 | 2005-12-23 | 2005-12-23 14:25 | Calculated | O410E | LF |  |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 34 | 19353 | 476 | 0.0246 | 0.0017568 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7914 |  | 2005-12-23 23:28 | 2005-12-23 | 2005-12-24 03:32 | Calculated | O410E | C114 | Single Circuit |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Insulator - Kidney | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 244 | 241 | 19353 | 58984 | 3.0478 | 0.012453 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7915 |  | 2005-12-25 00:39 | 2005-12-25 | 2005-12-25 00:49 | Calculated | O410E | C 594-754 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1574 | 19353 | 15740 | 0.81331 | 0.081331 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7916 |  | 2005-12-26 05:34 | 2005-12-26 | 2005-12-26 05:42 | Calculated | O410E | C114 |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 241 | 19353 | 1928 | 0.09962 | 0.012453 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7917 |  | 2005-12-28 06:04 | 2005-12-28 | 2005-12-28 06:05 | Calculated | O410E | C262 - 788 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 0 | 19353 | 0 | 0 | 0 | 1 | 0 | 2005/2006 | December-2005 | 12 | 2005
7919 |  | 2005-12-28 06:15 | 2005-12-28 | 2005-12-28 11:25 | Calculated | O410E | C1530 |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 310 | 6 | 19353 | 1860 | 0.09611 | 0.00031003 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7918 |  | 2005-12-28 06:43 | 2005-12-28 | 2005-12-28 06:52 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 1 | 19353 | 9 | 0.00047 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7920 |  | 2005-12-28 10:35 | 2005-12-28 | 2005-12-28 13:35 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 180 | 17 | 19353 | 3060 | 0.15812 | 0.00087842 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7921 |  | 2005-12-28 14:45 | 2005-12-28 | 2005-12-28 15:34 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 49 | 2 | 19353 | 99 | 0.00512 | 0.00010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7922 |  | 2005-12-28 15:00 | 2005-12-28 | 2005-12-28 18:11 | Calculated | O410E | L542 | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 191 | 11 | 19353 | 2105 | 0.10877 | 0.00056839 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7923 |  | 2005-12-28 17:12 | 2005-12-28 | 2005-12-28 18:25 | Calculated | O410E | L579 | Drop-Out Fuses |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 73 | 6 | 19353 | 438 | 0.02263 | 0.00031003 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7924 |  | 2005-12-28 17:42 | 2005-12-28 | 2005-12-28 18:36 | Calculated | O410E | L433 | Single Circuit |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 9 | 19353 | 486 | 0.02511 | 0.00046504 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7926 |  | 2005-12-28 19:58 | 2005-12-28 | 2005-12-28 21:53 | Calculated | O410E | C379 | Pole Mounted |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation | Transformers : Internal Connections | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 25 | 19353 | 2891 | 0.14938 | 0.0012918 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7925 |  | 2005-12-28 20:05 | 2005-12-28 | 2005-12-28 22:03 | Calculated | O410E | LF | Pole Mounted |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Transformers : Supports / Structures / Foundations | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 1 | 19353 | 118 | 0.0061 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7930 |  | 2005-12-29 07:01 | 2005-12-29 | 2005-12-29 07:22 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 21 | 1 | 19353 | 21 | 0.00109 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7927 |  | 2005-12-29 09:45 | 2005-12-29 | 2005-12-29 12:22 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 157 | 1 | 19353 | 157 | 0.00811 | 5.1672e-05 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7928 |  | 2005-12-29 10:33 | 2005-12-29 | 2005-12-29 14:14 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 221 | 7 | 19353 | 1547 | 0.07994 | 0.0003617 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7932 |  | 2005-12-31 17:21 | 2005-12-31 | 2005-12-31 17:49 | Calculated | O410E | C811 |  |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 20 | 19353 | 560 | 0.02894 | 0.0010334 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7933 |  | 2005-12-31 18:02 | 2005-12-31 | 2005-12-31 19:27 | Calculated | O410E | C402 |  |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 16 | 19353 | 1360 | 0.07027 | 0.00082675 | 0 | 0 | 2005/2006 | December-2005 | 12 | 2005
7934 |  | 2006-01-02 14:42 | 2006-01-02 | 2006-01-02 17:58 | Calculated | O410E | C1335 | Single Circuit |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 13 | 19353 | 2553 | 0.13192 | 0.00067173 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7935 |  | 2006-01-02 15:00 | 2006-01-02 | 2006-01-02 19:01 | Calculated | O410E | L1645 | Single Circuit |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Pole - Softwood | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 241 | 24 | 19353 | 5784 | 0.29887 | 0.0012401 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7936 |  | 2006-01-03 07:01 | 2006-01-03 | 2006-01-03 09:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 144 | 2 | 19353 | 288 | 0.01488 | 0.00010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7937 |  | 2006-01-03 10:03 | 2006-01-03 | 2006-01-03 12:37 | Calculated | O410E | C1632 |  |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 9 | 19353 | 1386 | 0.07162 | 0.00046504 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7938 |  | 2006-01-04 07:02 | 2006-01-04 | 2006-01-04 08:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 1 | 19353 | 63 | 0.00326 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7939 |  | 2006-01-04 07:46 | 2006-01-04 | 2006-01-04 08:32 | Calculated | O410E | C127 |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 342 | 19353 | 15897 | 0.82142 | 0.017672 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7940 |  | 2006-01-04 11:37 | 2006-01-04 | 2006-01-04 13:07 | Calculated | O410E | S320-387 | Single Circuit |  | McDonalds 110-02 | Remote Rural F | McDonalds | Te Waireka Zone Substation | OH Lines : Crossarm - Wood | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 71 | 19353 | 6390 | 0.33018 | 0.0036687 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7941 |  | 2006-01-04 13:16 | 2006-01-04 | 2006-01-04 13:49 | Calculated | O410E | S336 | Drop-Out Fuses |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 33 | 85 | 19353 | 2805 | 0.14494 | 0.0043921 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7942 |  | 2006-01-04 14:02 | 2006-01-04 | 2006-01-04 15:54 | Calculated | O410E | C127 | Single Circuit |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 342 | 19353 | 38492 | 1.9889 | 0.017672 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7943 |  | 2006-01-04 14:47 | 2006-01-04 | 2006-01-04 17:58 | Calculated | O410E | C368 | Single Circuit |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Conductor - Bare Copper | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 7 | 19353 | 1339 | 0.06919 | 0.0003617 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7944 |  | 2006-01-04 14:49 | 2006-01-04 | 2006-01-04 15:42 | Calculated | O410E | L495 | Drop-Out Fuses |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 53 | 4 | 19353 | 212 | 0.01095 | 0.00020669 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7945 |  | 2006-01-04 14:58 | 2006-01-04 | 2006-01-04 16:20 | Calculated | O410E | L433 | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 82 | 9 | 19353 | 738 | 0.03813 | 0.00046504 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7946 |  | 2006-01-05 05:28 | 2006-01-05 | 2006-01-05 06:31 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 2 | 19353 | 126 | 0.00651 | 0.00010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7947 |  | 2006-01-05 05:42 | 2006-01-05 | 2006-01-05 06:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 3 | 19353 | 231 | 0.01194 | 0.00015501 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7949 |  | 2006-01-05 08:03 | 2006-01-05 | 2006-01-05 09:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 2 | 19353 | 190 | 0.00982 | 0.00010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7950 |  | 2006-01-05 08:20 | 2006-01-05 | 2006-01-05 09:34 | Calculated | O410E | C268 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 52 | 19353 | 3848 | 0.19883 | 0.0026869 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7951 |  | 2006-01-05 10:33 | 2006-01-05 | 2006-01-05 15:00 | Calculated | O410E |  |  |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 267 | 88 | 19353 | 23496 | 1.2141 | 0.0045471 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7952 |  | 2006-01-05 13:36 | 2006-01-05 | 2006-01-05 14:13 | Calculated | O410E | L230 |  |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 5 | 19353 | 185 | 0.00956 | 0.00025836 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7953 |  | 2006-01-05 13:43 | 2006-01-05 | 2006-01-05 16:01 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 138 | 1 | 19353 | 138 | 0.00713 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7954 |  | 2006-01-05 16:00 | 2006-01-05 | 2006-01-05 17:22 | Calculated | O410E | L475 | Drop-Out Fuses |  | Tihoi 124-03 (was Tihoi 124-06) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 82 | 53 | 19353 | 4346 | 0.22456 | 0.0027386 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7957 |  | 2006-01-06 13:07 | 2006-01-06 | 2006-01-06 13:09 | Calculated | O410E | C242 - 796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 241 | 19353 | 482 | 0.02491 | 0.012453 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7958 |  | 2006-01-07 20:14 | 2006-01-07 | 2006-01-07 21:28 | Calculated | O410E | L693 | Drop-Out Fuses |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 74 | 20 | 19353 | 1480 | 0.07647 | 0.0010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7959 |  | 2006-01-09 08:15 | 2006-01-09 | 2006-01-09 09:48 | Calculated | O410E | LF |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 19353 | 186 | 0.00961 | 0.00010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7961 |  | 2006-01-09 16:25 | 2006-01-09 | 2006-01-09 17:17 | Calculated | O410E | S652 | Drop-Out Fuses |  | Pureora 119-03 RETIRED | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Contacts | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 52 | 1 | 19353 | 52 | 0.00269 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7962 |  | 2006-01-10 09:32 | 2006-01-10 | 2006-01-10 10:45 | Calculated | O410E |  |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 19 | 19353 | 1395 | 0.07208 | 0.00098176 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7963 |  | 2006-01-10 09:55 | 2006-01-10 | 2006-01-10 11:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7964 |  | 2006-01-10 10:19 | 2006-01-10 | 2006-01-10 11:54 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-04 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 1 | 19353 | 95 | 0.00491 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7966 |  | 2006-01-10 18:48 | 2006-01-10 | 2006-01-10 19:24 | Calculated | O410E | C686 | ABS |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Switch Connections (O/H) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 36 | 19 | 19353 | 684 | 0.03534 | 0.00098176 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7967 |  | 2006-01-11 08:05 | 2006-01-11 | 2006-01-11 11:45 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 220 | 1 | 19353 | 220 | 0.01137 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7968 |  | 2006-01-11 09:00 | 2006-01-11 | 2006-01-11 10:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 1 | 19353 | 99 | 0.00512 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7969 |  | 2006-01-11 10:06 | 2006-01-11 | 2006-01-11 11:30 | Calculated | O410E | LF |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 34 | 19353 | 2856 | 0.14757 | 0.0017568 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7970 |  | 2006-01-11 10:32 | 2006-01-11 | 2006-01-11 14:15 | Calculated | O410E |  |  |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 223 | 22 | 19353 | 4906 | 0.2535 | 0.0011368 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
25075 | Clash - Rihia Rd | 2006-01-12 09:49 | 2006-01-12 | 2006-01-12 11:56 | Calculated | 10T01 | 10T01 - 1 Phase : 30.00 kVA : POLEMNT |  | 424SEGT4172-6560 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 6 | 19353 | 762 | 0.03937 | 0.00031003 | 30 | 3810 | 2005/2006 | January-2006 | 1 | 2006
7973 |  | 2006-01-12 10:05 | 2006-01-12 | 2006-01-12 12:45 | Calculated | O410E | LF |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 160 | 69 | 19353 | 11040 | 0.57045 | 0.0035653 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7975 |  | 2006-01-13 07:23 | 2006-01-13 | 2006-01-13 11:15 | Calculated | O410E | C5534 |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 232 | 12 | 19353 | 2784 | 0.14385 | 0.00062006 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7976 |  | 2006-01-13 08:05 | 2006-01-13 | 2006-01-13 08:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 25 | 2 | 19353 | 50 | 0.00258 | 0.00010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7978 |  | 2006-01-13 09:37 | 2006-01-13 | 2006-01-13 11:13 | Calculated | O410E | LF |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 96 | 2 | 19353 | 192 | 0.00992 | 0.00010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7979 |  | 2006-01-13 09:37 | 2006-01-13 | 2006-01-13 11:09 | Calculated | O410E |  |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 24 | 19353 | 2216 | 0.1145 | 0.0012401 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7980 |  | 2006-01-13 10:35 | 2006-01-13 | 2006-01-13 13:46 | Calculated | O410E |  |  |  | Caves 101-13 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 191 | 5 | 19353 | 955 | 0.04935 | 0.00025836 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7981 |  | 2006-01-13 11:07 | 2006-01-13 | 2006-01-13 12:54 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 107 | 1 | 19353 | 107 | 0.00553 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7982 |  | 2006-01-16 09:33 | 2006-01-16 | 2006-01-16 13:00 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 207 | 6 | 19353 | 1242 | 0.06418 | 0.00031003 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7983 |  | 2006-01-17 12:36 | 2006-01-17 | 2006-01-17 13:58 | Calculated | O410E |  |  |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 20 | 19353 | 1640 | 0.08474 | 0.0010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7984 |  | 2006-01-18 08:03 | 2006-01-18 | 2006-01-18 17:16 | Calculated | O410E | LF | Pole Mounted |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 553 | 1 | 19353 | 553 | 0.02857 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7985 |  | 2006-01-18 09:50 | 2006-01-18 | 2006-01-18 10:13 | Calculated | O410E |  |  |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 23 | 31 | 19353 | 713 | 0.03684 | 0.0016018 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7986 |  | 2006-01-18 10:01 | 2006-01-18 | 2006-01-18 13:01 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 180 | 238 | 19353 | 42895 | 2.2165 | 0.012298 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7987 |  | 2006-01-18 12:56 | 2006-01-18 | 2006-01-18 14:16 | Calculated | O410E | L431 | Drop-Out Fuses |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 80 | 5 | 19353 | 400 | 0.02067 | 0.00025836 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7988 |  | 2006-01-18 13:31 | 2006-01-18 | 2006-01-18 13:35 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 14 | 19353 | 56 | 0.00289 | 0.0007234 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7989 |  | 2006-01-18 18:56 | 2006-01-18 | 2006-01-18 21:37 | Calculated | O410E | C109 | Single Circuit |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 70 | 19353 | 11335 | 0.5857 | 0.003617 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7990 |  | 2006-01-18 22:55 | 2006-01-18 | 2006-01-19 00:01 | Calculated | O410E | S1635 | Single Circuit |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 118 | 19353 | 7788 | 0.40242 | 0.0060972 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7991 |  | 2006-01-19 08:37 | 2006-01-19 | 2006-01-19 10:23 | Calculated | O410E | LF | Drop-Out Fuses |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 106 | 2 | 19353 | 212 | 0.01095 | 0.00010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7992 |  | 2006-01-19 12:58 | 2006-01-19 | 2006-01-19 16:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 187 | 1 | 19353 | 187 | 0.00966 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7993 |  | 2006-01-20 09:30 | 2006-01-20 | 2006-01-20 09:55 | Calculated | O410E | LV |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 44 | 19353 | 1100 | 0.05684 | 0.0022735 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7994 |  | 2006-01-20 10:36 | 2006-01-20 | 2006-01-20 13:40 | Calculated | O410E |  |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 184 | 31 | 19353 | 5704 | 0.29473 | 0.0016018 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7995 |  | 2006-01-20 10:39 | 2006-01-20 | 2006-01-20 15:56 | Calculated | O410E | LF | PVC/Polythene - Ducted |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Cables : Pole Box - Compound Filled | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 317 | 1 | 19353 | 317 | 0.01638 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7996 |  | 2006-01-23 13:34 | 2006-01-23 | 2006-01-23 14:27 | Calculated | O410E |  |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 53 | 119 | 19353 | 6307 | 0.32589 | 0.0061489 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7997 |  | 2006-01-24 07:50 | 2006-01-24 | 2006-01-24 10:13 | Calculated | O410E | C277 |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 86 | 19353 | 12298 | 0.63546 | 0.0044438 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
7999 |  | 2006-01-24 13:38 | 2006-01-24 | 2006-01-24 15:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 1 | 19353 | 92 | 0.00475 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8000 |  | 2006-01-24 14:06 | 2006-01-24 | 2006-01-24 14:43 | Calculated | O410E | S583 | Single Circuit |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Binder / Stirrup | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 121 | 19353 | 4477 | 0.23133 | 0.0062523 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8001 |  | 2006-01-24 14:41 | 2006-01-24 | 2006-01-24 19:11 | Calculated | O410E | L369 | Drop-Out Fuses |  | Wharepapa 122-08 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 270 | 7 | 19353 | 1890 | 0.09766 | 0.0003617 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
25038 | Trees-Lines Down - Hangatiki | 2006-01-24 15:14 | 2006-01-24 | 2006-01-24 16:00 | Calculated | 1272 | 1272 - Circuit Breaker 1272 |  | No Segment | 204-01 Hangatiki | Urban A | Caves | Hangatiki Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 783 | 19353 | 36018 | 1.8611 | 0.040459 | 2873.5 | 132180 | 2005/2006 | January-2006 | 1 | 2006
25039 | Trees-Lines Down - Hangatiki | 2006-01-24 15:14 | 2006-01-24 | 2006-01-24 16:52 | Calculated | 239 | 239 - Fused Link 239 |  | 107SEG239-508 | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 20 | 19353 | 1960 | 0.10128 | 0.0010334 | 190 | 18619 | 2005/2006 | January-2006 | 1 | 2006
8003 |  | 2006-01-24 15:23 | 2006-01-24 | 2006-01-24 16:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-08 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 83 | 1 | 19353 | 83 | 0.00429 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8004 |  | 2006-01-24 16:42 | 2006-01-24 | 2006-01-24 17:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 69 | 3 | 19353 | 207 | 0.0107 | 0.00015501 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8005 |  | 2006-01-24 19:04 | 2006-01-24 | 2006-01-24 22:23 | Calculated | O410E | C426 | Single Circuit |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Conductor - Bare Copper | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 78 | 19353 | 15584 | 0.80525 | 0.0040304 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8006 |  | 2006-01-24 19:36 | 2006-01-24 | 2006-01-24 20:53 | Calculated | O410E | L1296 | Drop-Out Fuses |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 43 | 19353 | 3311 | 0.17108 | 0.0022219 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8007 |  | 2006-01-24 20:12 | 2006-01-24 | 2006-01-24 23:20 | Calculated | O410E | C1346 | Single Circuit |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Conductor - Bare Copper | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 6 | 19353 | 1128 | 0.05829 | 0.00031003 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8008 |  | 2006-01-24 21:25 | 2006-01-24 | 2006-01-24 22:25 | Calculated | O410E | C277 | Single Circuit |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 86 | 19353 | 5160 | 0.26663 | 0.0044438 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8009 |  | 2006-01-24 21:29 | 2006-01-24 | 2006-01-24 22:40 | Calculated | O410E | L775 | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 71 | 18 | 19353 | 1278 | 0.06604 | 0.00093009 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8010 |  | 2006-01-24 22:13 | 2006-01-24 | 2006-01-24 23:30 | Calculated | O410E | C489 |  |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 24 | 19353 | 1848 | 0.09549 | 0.0012401 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8011 |  | 2006-01-24 22:43 | 2006-01-24 | 2006-01-24 23:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 43 | 30 | 19353 | 1290 | 0.06666 | 0.0015501 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8012 |  | 2006-01-24 23:53 | 2006-01-24 | 2006-01-25 00:37 | Calculated | O410E | LF |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 68 | 19353 | 2992 | 0.1546 | 0.0035137 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8013 |  | 2006-01-25 01:10 | 2006-01-25 | 2006-01-25 02:22 | Calculated | O410E | S1339 | Single Circuit |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 65 | 19353 | 4680 | 0.24182 | 0.0033587 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8014 |  | 2006-01-25 07:15 | 2006-01-25 | 2006-01-25 08:47 | Calculated | O410E | L249 | Drop-Out Fuses |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 3 | 19353 | 276 | 0.01426 | 0.00015501 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8015 |  | 2006-01-25 09:26 | 2006-01-25 | 2006-01-25 10:17 | Calculated | O410E | LF |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 5 | 19353 | 255 | 0.01318 | 0.00025836 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8016 |  | 2006-01-25 09:58 | 2006-01-25 | 2006-01-25 11:00 | Calculated | O410E | LF |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 4 | 19353 | 248 | 0.01281 | 0.00020669 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8018 |  | 2006-01-25 10:12 | 2006-01-25 | 2006-01-25 12:53 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 161 | 9 | 19353 | 1449 | 0.07487 | 0.00046504 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8019 |  | 2006-01-25 10:35 | 2006-01-25 | 2006-01-25 13:00 | Calculated | O410E | LF | Pole Mounted |  | Wharepapa 122-08 | Remote Rural F | Wharepapa | Arohena Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 1 | 19353 | 145 | 0.00749 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8020 |  | 2006-01-25 11:19 | 2006-01-25 | 2006-01-25 12:02 | Calculated | O410E | C519 |  |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 20 | 19353 | 860 | 0.04444 | 0.0010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8021 |  | 2006-01-25 11:22 | 2006-01-25 | 2006-01-25 13:10 | Calculated | O410E | L310 | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 108 | 4 | 19353 | 432 | 0.02232 | 0.00020669 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8023 |  | 2006-01-26 07:42 | 2006-01-26 | 2006-01-26 09:50 | Calculated | O410E | C891 |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 46 | 19353 | 5888 | 0.30424 | 0.0023769 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8024 |  | 2006-01-26 09:21 | 2006-01-26 | 2006-01-26 10:44 | Calculated | O410E | LF |  |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 83 | 1 | 19353 | 83 | 0.00429 | 5.1672e-05 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8026 |  | 2006-01-26 12:22 | 2006-01-26 | 2006-01-26 13:57 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 2 | 19353 | 190 | 0.00982 | 0.00010334 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8028 |  | 2006-01-27 13:57 | 2006-01-27 | 2006-01-27 14:45 | Calculated | O410E | LF | Drop-Out Fuses |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 48 | 3 | 19353 | 144 | 0.00744 | 0.00015501 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8030 |  | 2006-01-28 15:00 | 2006-01-28 | 2006-01-28 17:23 | Calculated | O410E | C422 | Sectionaliser |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Other | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 143 | 24 | 19353 | 3432 | 0.17734 | 0.0012401 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8032 |  | 2006-01-30 08:57 | 2006-01-30 | 2006-01-30 11:31 | Calculated | O410E | LF | Single Circuit |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 6 | 19353 | 924 | 0.04774 | 0.00031003 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8031 |  | 2006-01-30 10:08 | 2006-01-30 | 2006-01-30 12:28 | Calculated | O410E | L476 | Drop-Out Fuses |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 140 | 57 | 19353 | 7980 | 0.41234 | 0.0029453 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8033 |  | 2006-01-30 20:56 | 2006-01-30 | 2006-01-30 21:04 | Calculated | O410E | C686 |  |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 242 | 19353 | 1936 | 0.10004 | 0.012505 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8034 |  | 2006-01-31 14:37 | 2006-01-31 | 2006-01-31 15:23 | Calculated | O410E | LF |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 3 | 19353 | 138 | 0.00713 | 0.00015501 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8035 |  | 2006-01-31 15:52 | 2006-01-31 | 2006-01-31 17:29 | Calculated | O410E | S1619 |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 381 | 19353 | 36957 | 1.9096 | 0.019687 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
25068 | OCB 792 Tripped - Wairere Sub | 2006-01-31 23:52 | 2006-01-31 | 2006-02-01 00:01 | Calculated | 792 | 792 - Circuit Breaker 792 |  | No Segment | 207-01 Wairere Falls | Rural D | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 1574 | 19353 | 14166 | 0.73198 | 0.081331 | 13921.5 | 121349 | 2005/2006 | January-2006 | 1 | 2006
8036 |  | 2006-01-31 23:55 | 2006-01-31 | 2006-02-01 00:01 | Calculated | O410E | C754 & 792 & 594 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 6 | 1574 | 19353 | 9444 | 0.48799 | 0.081331 | 0 | 0 | 2005/2006 | January-2006 | 1 | 2006
8037 |  | 2006-02-02 09:00 | 2006-02-02 | 2006-02-02 14:30 | Calculated | O410E |  |  |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 6 | 19353 | 1980 | 0.10231 | 0.00031003 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8038 |  | 2006-02-02 10:30 | 2006-02-02 | 2006-02-02 11:51 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 145 | 19353 | 11863 | 0.61298 | 0.0074924 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8039 |  | 2006-02-03 09:00 | 2006-02-03 | 2006-02-03 13:44 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 284 | 15 | 19353 | 4260 | 0.22012 | 0.00077507 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8040 |  | 2006-02-03 10:30 | 2006-02-03 | 2006-02-03 14:41 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 251 | 7 | 19353 | 1757 | 0.09079 | 0.0003617 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8041 |  | 2006-02-03 14:33 | 2006-02-03 | 2006-02-03 15:13 | Calculated | O410E | LF |  |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1 | 19353 | 40 | 0.00207 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8042 |  | 2006-02-04 17:21 | 2006-02-04 | 2006-02-05 00:19 | Calculated | O410E | C489 | Single Circuit |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 418 | 24 | 19353 | 10048 | 0.5192 | 0.0012401 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8043 |  | 2006-02-05 06:07 | 2006-02-05 | 2006-02-05 06:53 | Calculated | O410E | C955 | Single Circuit |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Joint - Compression / Tension | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 1096 | 19353 | 50580 | 2.6136 | 0.056632 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
3984 |  | 2006-02-06 | 2006-02-06 | 2006-02-06 01:31 | Calculated | O410E | LF | Single Circuit |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 4 | 19353 | 364 | 0.01881 | 0.00020669 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8044 |  | 2006-02-07 10:32 | 2006-02-07 | 2006-02-07 11:35 | Calculated | O410E |  |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 19 | 19353 | 1197 | 0.06185 | 0.00098176 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8045 |  | 2006-02-08 10:36 | 2006-02-08 | 2006-02-08 13:12 | Calculated | O410E |  |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 156 | 6 | 19353 | 936 | 0.04836 | 0.00031003 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8047 |  | 2006-02-08 12:14 | 2006-02-08 | 2006-02-08 14:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 106 | 1 | 19353 | 106 | 0.00548 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8048 |  | 2006-02-08 13:02 | 2006-02-08 | 2006-02-08 13:36 | Calculated | O410E | L209 | Single Circuit |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 32 | 19353 | 1088 | 0.05622 | 0.0016535 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8049 |  | 2006-02-08 13:56 | 2006-02-08 | 2006-02-08 16:19 | Calculated | O410E | L172 | Pole Mounted |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 11 | 19353 | 1579 | 0.08159 | 0.00056839 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8050 |  | 2006-02-08 15:42 | 2006-02-08 | 2006-02-08 17:52 | Calculated | O410E | C1321 |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 27 | 19353 | 3525 | 0.18214 | 0.0013951 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8051 |  | 2006-02-09 06:14 | 2006-02-09 | 2006-02-09 10:59 | Calculated | O410E | C511 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 285 | 19 | 19353 | 5415 | 0.2798 | 0.00098176 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8052 |  | 2006-02-09 09:07 | 2006-02-09 | 2006-02-09 13:56 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 289 | 2 | 19353 | 578 | 0.02987 | 0.00010334 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8053 |  | 2006-02-09 10:00 | 2006-02-09 | 2006-02-09 14:48 | Calculated | O410E |  |  |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 288 | 40 | 19353 | 11520 | 0.59526 | 0.0020669 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8055 |  | 2006-02-09 17:38 | 2006-02-09 | 2006-02-09 18:43 | Calculated | O410E | C268 | Auto-Recloser |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Tank | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 65 | 52 | 19353 | 3380 | 0.17465 | 0.0026869 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8056 |  | 2006-02-10 10:19 | 2006-02-10 | 2006-02-10 11:36 | Calculated | O410E | LF |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 77 | 15 | 19353 | 1155 | 0.05968 | 0.00077507 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8057 |  | 2006-02-10 10:33 | 2006-02-10 | 2006-02-10 14:49 | Calculated | O410E |  |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 256 | 13 | 19353 | 3328 | 0.17196 | 0.00067173 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8059 |  | 2006-02-10 13:00 | 2006-02-10 | 2006-02-10 14:03 | Calculated | O410E | LF |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 32 | 19353 | 2016 | 0.10417 | 0.0016535 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8060 |  | 2006-02-10 15:17 | 2006-02-10 | 2006-02-10 15:33 | Calculated | O410E | LF |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 2 | 19353 | 32 | 0.00165 | 0.00010334 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8061 |  | 2006-02-11 08:01 | 2006-02-11 | 2006-02-11 16:22 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 501 | 80 | 19353 | 40080 | 2.071 | 0.0041337 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8062 |  | 2006-02-12 08:01 | 2006-02-12 | 2006-02-12 15:30 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 449 | 2 | 19353 | 898 | 0.0464 | 0.00010334 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8063 |  | 2006-02-13 08:03 | 2006-02-13 | 2006-02-13 12:35 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 272 | 1 | 19353 | 272 | 0.01405 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8064 |  | 2006-02-13 08:55 | 2006-02-13 | 2006-02-13 09:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 43 | 1 | 19353 | 43 | 0.00222 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8065 |  | 2006-02-13 08:57 | 2006-02-13 | 2006-02-13 11:00 | Calculated | O410E | C509 |  |  | Ohura 413-03 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 4 | 19353 | 492 | 0.02542 | 0.00020669 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8066 |  | 2006-02-13 11:00 | 2006-02-13 | 2006-02-13 13:46 | Calculated | O410E |  |  |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 166 | 35 | 19353 | 5810 | 0.30021 | 0.0018085 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8067 |  | 2006-02-14 08:12 | 2006-02-14 | 2006-02-14 09:53 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 101 | 1 | 19353 | 101 | 0.00522 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8068 |  | 2006-02-14 09:32 | 2006-02-14 | 2006-02-14 13:29 | Calculated | O410E | LV |  |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 237 | 75 | 19353 | 17775 | 0.91846 | 0.0038754 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8069 |  | 2006-02-14 14:53 | 2006-02-14 | 2006-02-14 16:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-02 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 81 | 1 | 19353 | 81 | 0.00419 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8072 |  | 2006-02-16 09:03 | 2006-02-16 | 2006-02-16 13:02 | Calculated | O410E |  |  |  | Mokauiti 115-05 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 239 | 14 | 19353 | 3349 | 0.17305 | 0.0007234 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8073 |  | 2006-02-16 10:04 | 2006-02-16 | 2006-02-16 10:54 | Calculated | O410E | C730 |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 41 | 19353 | 2050 | 0.10593 | 0.0021185 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8074 |  | 2006-02-16 12:35 | 2006-02-16 | 2006-02-16 15:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 186 | 1 | 19353 | 186 | 0.00961 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8075 |  | 2006-02-16 13:37 | 2006-02-16 | 2006-02-16 13:39 | Calculated | O410E | C222 | ABS |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply | Switchgear : Switch Connections (O/H) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 2 | 711 | 19353 | 1741 | 0.08996 | 0.036738 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8076 |  | 2006-02-16 13:55 | 2006-02-16 | 2006-02-16 14:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 25 | 14 | 19353 | 350 | 0.01809 | 0.0007234 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8078 |  | 2006-02-17 08:12 | 2006-02-17 | 2006-02-17 10:16 | Calculated | O410E | C1530 |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 6 | 19353 | 744 | 0.03844 | 0.00031003 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8079 |  | 2006-02-17 08:58 | 2006-02-17 | 2006-02-17 13:21 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 263 | 12 | 19353 | 3156 | 0.16308 | 0.00062006 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8081 |  | 2006-02-17 16:10 | 2006-02-17 | 2006-02-17 16:46 | Calculated | O410E | LF |  |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 2 | 19353 | 72 | 0.00372 | 0.00010334 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8082 |  | 2006-02-18 19:50 | 2006-02-18 | 2006-02-18 21:25 | Calculated | O410E | L619 | Drop-Out Fuses |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 52 | 19353 | 4940 | 0.25526 | 0.0026869 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8083 |  | 2006-02-20 09:30 | 2006-02-20 | 2006-02-20 12:02 | Calculated | O410E |  |  |  |  | Remote Rural F | Lake Taupo 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 152 | 772 | 19353 | 118077 | 6.1012 | 0.03989 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8086 |  | 2006-02-20 15:23 | 2006-02-20 | 2006-02-20 16:16 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 53 | 5 | 19353 | 265 | 0.01369 | 0.00025836 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8087 |  | 2006-02-21 10:02 | 2006-02-21 | 2006-02-21 15:52 | Calculated | O410E |  |  |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 350 | 8 | 19353 | 2800 | 0.14468 | 0.00041337 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8088 |  | 2006-02-21 12:53 | 2006-02-21 | 2006-02-21 14:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 104 | 1 | 19353 | 104 | 0.00537 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8089 |  | 2006-02-21 13:08 | 2006-02-21 | 2006-02-21 15:05 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 7 | 19353 | 819 | 0.04232 | 0.0003617 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8091 |  | 2006-02-22 10:34 | 2006-02-22 | 2006-02-22 13:02 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 1 | 19353 | 148 | 0.00765 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8092 |  | 2006-02-23 11:07 | 2006-02-23 | 2006-02-23 14:34 | Calculated | O410E | C1322 |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 207 | 17 | 19353 | 3519 | 0.18183 | 0.00087842 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8094 |  | 2006-02-23 13:00 | 2006-02-23 | 2006-02-23 13:36 | Calculated | O410E |  |  |  | Maihiihi 111-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 9 | 19353 | 324 | 0.01674 | 0.00046504 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8097 |  | 2006-02-24 12:30 | 2006-02-24 | 2006-02-24 14:50 | Calculated | O410E |  |  |  |  | Remote Rural F | Lake Taupo 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 140 | 772 | 19353 | 108826 | 5.6232 | 0.03989 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8098 |  | 2006-02-24 15:47 | 2006-02-24 | 2006-02-24 16:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-02 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 61 | 5 | 19353 | 305 | 0.01576 | 0.00025836 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8099 |  | 2006-02-25 11:00 | 2006-02-25 | 2006-02-25 13:27 | Calculated | O410E | LF | Pole Mounted |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 1 | 19353 | 147 | 0.0076 | 5.1672e-05 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8100 |  | 2006-02-26 14:51 | 2006-02-26 | 2006-02-26 15:32 | Calculated | O410E | C1347 | Single Circuit |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 6 | 19353 | 246 | 0.01271 | 0.00031003 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8101 |  | 2006-02-26 15:09 | 2006-02-26 | 2006-02-26 18:43 | Calculated | O410E | C277 |  |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 9 | 19353 | 1926 | 0.09952 | 0.00046504 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8103 |  | 2006-02-28 08:40 | 2006-02-28 | 2006-02-28 09:47 | Calculated | O410E | C277 | Single Circuit |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 9 | 19353 | 603 | 0.03116 | 0.00046504 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8104 |  | 2006-02-28 11:03 | 2006-02-28 | 2006-02-28 13:00 | Calculated | O410E |  |  |  | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 153 | 19353 | 18008 | 0.9305 | 0.0079058 | 0 | 0 | 2005/2006 | February-2006 | 2 | 2006
8106 |  | 2006-03-02 09:48 | 2006-03-02 | 2006-03-02 14:00 | Calculated | O410E | LV |  |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 252 | 6 | 19353 | 1512 | 0.07813 | 0.00031003 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8107 |  | 2006-03-02 09:54 | 2006-03-02 | 2006-03-02 11:28 | Calculated | O410E | L172 | Drop-Out Fuses |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 11 | 19353 | 1035 | 0.05348 | 0.00056839 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8110 |  | 2006-03-02 13:03 | 2006-03-02 | 2006-03-02 14:14 | Calculated | O410E |  |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 51 | 19353 | 3621 | 0.1871 | 0.0026353 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8112 |  | 2006-03-03 08:15 | 2006-03-03 | 2006-03-03 10:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 111 | 1 | 19353 | 111 | 0.00574 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8113 |  | 2006-03-03 10:01 | 2006-03-03 | 2006-03-03 11:17 | Calculated | O410E |  |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 76 | 71 | 19353 | 5439 | 0.28104 | 0.0036687 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8115 |  | 2006-03-03 22:50 | 2006-03-03 | 2006-03-03 22:52 | Calculated | O410E | C232 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 159 | 19353 | 318 | 0.01643 | 0.0082158 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8116 |  | 2006-03-04 10:57 | 2006-03-04 | 2006-03-04 10:58 | Calculated | O410E | C232, 180 Or 6143 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 166 | 19353 | 177 | 0.00915 | 0.0085775 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8117 |  | 2006-03-05 09:11 | 2006-03-05 | 2006-03-05 13:00 | Calculated | O410E | S544 | Single Circuit |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply | OH Lines : Jumper - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 229 | 2 | 19353 | 458 | 0.02367 | 0.00010334 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8118 |  | 2006-03-05 19:48 | 2006-03-05 | 2006-03-05 19:55 | Calculated | O410E | C6007 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 7 | 84 | 19353 | 588 | 0.03038 | 0.0043404 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8120 |  | 2006-03-06 10:02 | 2006-03-06 | 2006-03-06 14:25 | Calculated | O410E |  |  |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 263 | 20 | 19353 | 5260 | 0.27179 | 0.0010334 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8121 |  | 2006-03-07 09:14 | 2006-03-07 | 2006-03-07 13:02 | Calculated | O410E |  |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 228 | 11 | 19353 | 2508 | 0.12959 | 0.00056839 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8122 |  | 2006-03-07 10:32 | 2006-03-07 | 2006-03-07 12:02 | Calculated | O410E |  |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 36 | 19353 | 3240 | 0.16742 | 0.0018602 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8123 |  | 2006-03-08 11:30 | 2006-03-08 | 2006-03-08 14:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 153 | 1 | 19353 | 153 | 0.00791 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8124 |  | 2006-03-08 12:27 | 2006-03-08 | 2006-03-08 14:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 129 | 6 | 19353 | 774 | 0.03999 | 0.00031003 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8125 |  | 2006-03-09 08:37 | 2006-03-09 | 2006-03-09 09:40 | Calculated | O410E | S1619 | Single Circuit |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 381 | 19353 | 24003 | 1.2403 | 0.019687 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8126 |  | 2006-03-09 09:16 | 2006-03-09 | 2006-03-09 09:40 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 24 | 1 | 19353 | 24 | 0.00124 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8127 |  | 2006-03-09 09:23 | 2006-03-09 | 2006-03-09 11:19 | Calculated | O410E | LF |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 116 | 1 | 19353 | 116 | 0.00599 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8128 |  | 2006-03-09 09:56 | 2006-03-09 | 2006-03-09 11:05 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 69 | 77 | 19353 | 5329 | 0.27536 | 0.0039787 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8129 |  | 2006-03-09 10:31 | 2006-03-09 | 2006-03-09 13:18 | Calculated | O410E |  |  |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 167 | 68 | 19353 | 11356 | 0.58678 | 0.0035137 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8130 |  | 2006-03-09 10:33 | 2006-03-09 | 2006-03-09 14:21 | Calculated | O410E | LV |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 228 | 9 | 19353 | 2052 | 0.10603 | 0.00046504 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8132 |  | 2006-03-10 16:00 | 2006-03-10 | 2006-03-10 16:28 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 28 | 3 | 19353 | 84 | 0.00434 | 0.00015501 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8133 |  | 2006-03-11 03:45 | 2006-03-11 | 2006-03-11 03:55 | Calculated | O410E | C754 & 594 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1574 | 19353 | 15740 | 0.81331 | 0.081331 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8134 |  | 2006-03-11 05:35 | 2006-03-11 | 2006-03-11 05:44 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 1 | 19353 | 9 | 0.00047 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8135 |  | 2006-03-11 14:25 | 2006-03-11 | 2006-03-11 14:42 | Calculated | O410E | S1710 | Single Circuit |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 112 | 19353 | 1904 | 0.09838 | 0.0057872 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8136 |  | 2006-03-12 10:07 | 2006-03-12 | 2006-03-12 11:07 | Calculated | O410E | L1528 | Drop-Out Fuses |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 60 | 7 | 19353 | 420 | 0.0217 | 0.0003617 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8137 |  | 2006-03-13 09:41 | 2006-03-13 | 2006-03-13 13:02 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 201 | 4 | 19353 | 804 | 0.04154 | 0.00020669 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8138 |  | 2006-03-13 10:31 | 2006-03-13 | 2006-03-13 12:19 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 15 | 19353 | 1620 | 0.08371 | 0.00077507 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8139 |  | 2006-03-13 10:33 | 2006-03-13 | 2006-03-13 14:29 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 236 | 4 | 19353 | 944 | 0.04878 | 0.00020669 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8140 |  | 2006-03-13 15:54 | 2006-03-13 | 2006-03-13 16:20 | Calculated | O410E | LF | Single Circuit |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation | OH Lines : Surge Diverters | Weather | Lightning |  | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 3 | 19353 | 78 | 0.00403 | 0.00015501 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8142 |  | 2006-03-14 09:01 | 2006-03-14 | 2006-03-14 12:01 | Calculated | O410E | LF |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 180 | 6 | 19353 | 1080 | 0.05581 | 0.00031003 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8143 |  | 2006-03-14 09:02 | 2006-03-14 | 2006-03-14 14:23 | Calculated | O410E | LF |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 2 | 19353 | 642 | 0.03317 | 0.00010334 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8145 |  | 2006-03-14 10:45 | 2006-03-14 | 2006-03-14 14:06 | Calculated | O410E | LF |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 201 | 1 | 19353 | 201 | 0.01039 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8150 |  | 2006-03-16 09:33 | 2006-03-16 | 2006-03-16 15:42 | Calculated | O410E |  |  |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 369 | 6 | 19353 | 2214 | 0.1144 | 0.00031003 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8151 |  | 2006-03-16 09:51 | 2006-03-16 | 2006-03-16 13:17 | Calculated | O410E |  |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 206 | 381 | 19353 | 78657 | 4.0643 | 0.019687 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8146 |  | 2006-03-17 09:37 | 2006-03-17 | 2006-03-17 11:05 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 30 | 19353 | 2655 | 0.13719 | 0.0015501 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8148 |  | 2006-03-17 12:08 | 2006-03-17 | 2006-03-17 13:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 1 | 19353 | 99 | 0.00512 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8152 |  | 2006-03-20 09:14 | 2006-03-20 | 2006-03-20 10:50 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 96 | 30 | 19353 | 2880 | 0.14881 | 0.0015501 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8153 |  | 2006-03-20 13:00 | 2006-03-20 | 2006-03-20 15:26 | Calculated | O410E | LV |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 146 | 8 | 19353 | 1168 | 0.06035 | 0.00041337 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8154 |  | 2006-03-21 08:51 | 2006-03-21 | 2006-03-21 10:09 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 78 | 30 | 19353 | 2340 | 0.12091 | 0.0015501 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8155 |  | 2006-03-22 09:08 | 2006-03-22 | 2006-03-22 14:06 | Calculated | O410E |  |  |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 298 | 4 | 19353 | 1192 | 0.06159 | 0.00020669 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8156 |  | 2006-03-22 10:34 | 2006-03-22 | 2006-03-22 14:36 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 242 | 8 | 19353 | 1936 | 0.10004 | 0.00041337 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8157 |  | 2006-03-23 10:30 | 2006-03-23 | 2006-03-23 12:33 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 123 | 20 | 19353 | 2460 | 0.12711 | 0.0010334 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8159 |  | 2006-03-23 10:31 | 2006-03-23 | 2006-03-23 12:22 | Calculated | O410E | LF | Pole Mounted |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | Transformers : Internal Connections | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 3 | 19353 | 335 | 0.01731 | 0.00015501 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8160 |  | 2006-03-24 03:52 | 2006-03-24 | 2006-03-24 12:31 | Calculated | O410E | C6125 | Single Circuit |  | Kuratau 406-01 | Remote Rural F | Kuratau | Kuratau Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 519 | 1048 | 19353 | 543912 | 28.1048 | 0.054152 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8162 |  | 2006-03-24 08:15 | 2006-03-24 | 2006-03-24 09:51 | Calculated | O410E | C411 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 52 | 19353 | 5003 | 0.25851 | 0.0026869 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8163 |  | 2006-03-24 11:43 | 2006-03-24 | 2006-03-24 14:35 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 172 | 1 | 19353 | 172 | 0.00889 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8164 |  | 2006-03-24 20:37 | 2006-03-24 | 2006-03-24 23:02 | Calculated | O410E | L414 | Drop-Out Fuses |  | Mokau 128-07 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 145 | 6 | 19353 | 870 | 0.04495 | 0.00031003 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8165 |  | 2006-03-26 09:07 | 2006-03-26 | 2006-03-26 11:09 | Calculated | O410E | LV |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 122 | 20 | 19353 | 2440 | 0.12608 | 0.0010334 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8167 |  | 2006-03-26 20:27 | 2006-03-26 | 2006-03-26 21:47 | Calculated | O410E | C1612 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 27 | 19353 | 2160 | 0.11161 | 0.0013951 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8168 |  | 2006-03-27 06:58 | 2006-03-27 | 2006-03-27 07:16 | Calculated | O410E | C952 |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 939 | 19353 | 16995 | 0.87816 | 0.04852 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8169 |  | 2006-03-27 07:23 | 2006-03-27 | 2006-03-27 08:31 | Calculated | O410E | C6560 |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 21 | 19353 | 1428 | 0.07379 | 0.0010851 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8170 |  | 2006-03-27 08:03 | 2006-03-27 | 2006-03-27 14:51 | Calculated | O410E | C1615 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 408 | 9 | 19353 | 3672 | 0.18974 | 0.00046504 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8171 |  | 2006-03-27 08:17 | 2006-03-27 | 2006-03-27 09:57 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 100 | 2 | 19353 | 200 | 0.01033 | 0.00010334 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8172 |  | 2006-03-27 09:53 | 2006-03-27 | 2006-03-27 10:38 | Calculated | O410E | LF |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 2 | 19353 | 90 | 0.00465 | 0.00010334 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8173 |  | 2006-03-27 10:34 | 2006-03-27 | 2006-03-27 11:12 | Calculated | O410E | L1614 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare Copper | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 16 | 19353 | 608 | 0.03142 | 0.00082675 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8174 |  | 2006-03-27 13:47 | 2006-03-27 | 2006-03-27 15:04 | Calculated | O410E | L519 | Single Circuit |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 14 | 19353 | 1078 | 0.0557 | 0.0007234 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8178 |  | 2006-03-29 08:07 | 2006-03-29 | 2006-03-29 09:17 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 70 | 4 | 19353 | 280 | 0.01447 | 0.00020669 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8179 |  | 2006-03-29 09:13 | 2006-03-29 | 2006-03-29 10:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 72 | 1 | 19353 | 72 | 0.00372 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8181 |  | 2006-03-29 14:59 | 2006-03-29 | 2006-03-29 15:56 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 57 | 1 | 19353 | 57 | 0.00295 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8182 |  | 2006-03-30 08:58 | 2006-03-30 | 2006-03-30 09:54 | Calculated | O410E | LF | Drop-Out Fuses |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 56 | 4 | 19353 | 224 | 0.01157 | 0.00020669 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8183 |  | 2006-03-30 09:30 | 2006-03-30 | 2006-03-30 11:12 | Calculated | O410E | LV |  |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 32 | 19353 | 3272 | 0.16907 | 0.0016535 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8185 |  | 2006-03-30 10:30 | 2006-03-30 | 2006-03-30 15:41 | Calculated | O410E |  |  |  | Rural 126-03 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 311 | 2 | 19353 | 622 | 0.03214 | 0.00010334 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8186 |  | 2006-03-30 10:55 | 2006-03-30 | 2006-03-30 14:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 212 | 3 | 19353 | 636 | 0.03286 | 0.00015501 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8187 |  | 2006-03-31 08:10 | 2006-03-31 | 2006-03-31 09:35 | Calculated | O410E | LF | Drop-Out Fuses |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 1 | 19353 | 85 | 0.00439 | 5.1672e-05 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8188 |  | 2006-03-31 09:30 | 2006-03-31 | 2006-03-31 10:25 | Calculated | O410E |  |  |  | Mokauiti 115-02 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 131 | 19353 | 7220 | 0.37307 | 0.006769 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8189 |  | 2006-03-31 10:25 | 2006-03-31 | 2006-03-31 11:33 | Calculated | O410E | C1721 |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 53 | 19353 | 3604 | 0.18622 | 0.0027386 | 0 | 0 | 2005/2006 | March-2006 | 3 | 2006
8192 |  | 2006-04-03 00:57 | 2006-04-03 | 2006-04-03 01:09 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 12 | 1 | 19353 | 12 | 0.00062 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8194 |  | 2006-04-03 08:45 | 2006-04-03 | 2006-04-03 10:51 | Calculated | O410E | C1347 |  |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 6 | 19353 | 756 | 0.03906 | 0.00031003 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8195 |  | 2006-04-03 10:30 | 2006-04-03 | 2006-04-03 11:00 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 30 | 5 | 19353 | 150 | 0.00775 | 0.00025836 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8196 |  | 2006-04-03 10:31 | 2006-04-03 | 2006-04-03 11:14 | Calculated | O410E |  |  |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 7 | 19353 | 301 | 0.01555 | 0.0003617 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8197 |  | 2006-04-03 11:14 | 2006-04-03 | 2006-04-03 12:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 84 | 1 | 19353 | 84 | 0.00434 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8198 |  | 2006-04-03 12:35 | 2006-04-03 | 2006-04-03 12:36 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8200 |  | 2006-04-04 10:31 | 2006-04-04 | 2006-04-04 13:22 | Calculated | O410E |  |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 171 | 25 | 19353 | 4275 | 0.2209 | 0.0012918 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8201 |  | 2006-04-04 12:00 | 2006-04-04 | 2006-04-04 13:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 65 | 3 | 19353 | 195 | 0.01008 | 0.00015501 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8202 |  | 2006-04-04 12:10 | 2006-04-04 | 2006-04-04 14:35 | Calculated | O410E | L800 | Drop-Out Fuses |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Supports or Foundations | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 145 | 16 | 19353 | 2332 | 0.1205 | 0.00082675 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8203 |  | 2006-04-04 13:10 | 2006-04-04 | 2006-04-04 15:49 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 159 | 1 | 19353 | 159 | 0.00822 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8204 |  | 2006-04-04 15:40 | 2006-04-04 | 2006-04-04 17:23 | Calculated | O410E | C1626 |  |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 111 | 19353 | 11433 | 0.59076 | 0.0057355 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8205 |  | 2006-04-04 23:26 | 2006-04-04 | 2006-04-05 01:34 | Calculated | O410E | C642 |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 64 | 19353 | 8236 | 0.42557 | 0.003307 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8206 |  | 2006-04-05 10:36 | 2006-04-05 | 2006-04-05 14:49 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 253 | 8 | 19353 | 2024 | 0.10458 | 0.00041337 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8207 |  | 2006-04-05 10:41 | 2006-04-05 | 2006-04-05 13:26 | Calculated | O410E | LV |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 165 | 62 | 19353 | 10230 | 0.5286 | 0.0032036 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8209 |  | 2006-04-06 17:35 | 2006-04-06 | 2006-04-06 19:19 | Calculated | O410E | C779 | Single Circuit |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 42 | 19353 | 4368 | 0.2257 | 0.0021702 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8210 |  | 2006-04-07 07:26 | 2006-04-07 | 2006-04-07 09:43 | Calculated | O410E | C5536 |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 7 | 19353 | 959 | 0.04955 | 0.0003617 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8211 |  | 2006-04-07 09:07 | 2006-04-07 | 2006-04-07 09:11 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 14 | 19353 | 56 | 0.00289 | 0.0007234 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8212 |  | 2006-04-07 10:30 | 2006-04-07 | 2006-04-07 12:18 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 31 | 19353 | 3351 | 0.17315 | 0.0016018 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8215 |  | 2006-04-07 13:03 | 2006-04-07 | 2006-04-07 14:58 | Calculated | O410E |  |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 9 | 19353 | 1035 | 0.05348 | 0.00046504 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8216 |  | 2006-04-07 14:17 | 2006-04-07 | 2006-04-07 14:37 | Calculated | O410E | LF |  |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 2 | 19353 | 40 | 0.00207 | 0.00010334 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8217 |  | 2006-04-08 08:52 | 2006-04-08 | 2006-04-08 13:20 | Calculated | O410E | LF |  |  | Pureora 119-03 RETIRED | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 1 | 19353 | 268 | 0.01385 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8218 |  | 2006-04-09 11:17 | 2006-04-09 | 2006-04-09 12:11 | Calculated | O410E | C955 | Single Circuit |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Pole - Hardwood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1096 | 19353 | 59622 | 3.0808 | 0.056632 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8219 |  | 2006-04-10 02:06 | 2006-04-10 | 2006-04-10 02:17 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 42 | 19353 | 462 | 0.02387 | 0.0021702 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8220 |  | 2006-04-10 06:53 | 2006-04-10 | 2006-04-10 08:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-07 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 87 | 1 | 19353 | 87 | 0.0045 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8221 |  | 2006-04-10 08:08 | 2006-04-10 | 2006-04-10 09:25 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 4 | 19353 | 310 | 0.01602 | 0.00020669 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8222 |  | 2006-04-10 08:12 | 2006-04-10 | 2006-04-10 09:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 1 | 19353 | 96 | 0.00496 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8223 |  | 2006-04-10 08:20 | 2006-04-10 | 2006-04-10 09:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 11 | 19353 | 968 | 0.05002 | 0.00056839 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8224 |  | 2006-04-10 10:56 | 2006-04-10 | 2006-04-10 11:40 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 44 | 2 | 19353 | 88 | 0.00455 | 0.00010334 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8225 |  | 2006-04-10 15:32 | 2006-04-10 | 2006-04-10 16:26 | Calculated | O410E | LF |  |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 2 | 19353 | 108 | 0.00558 | 0.00010334 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8226 |  | 2006-04-11 04:59 | 2006-04-11 | 2006-04-11 07:40 | Calculated | O410E | C1620 | Single Circuit |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 176 | 19353 | 28336 | 1.4642 | 0.0090942 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8228 |  | 2006-04-11 06:58 | 2006-04-11 | 2006-04-11 09:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-07 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 148 | 1 | 19353 | 148 | 0.00765 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8229 |  | 2006-04-11 09:02 | 2006-04-11 | 2006-04-11 14:20 | Calculated | O410E | LF |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 318 | 5 | 19353 | 1590 | 0.08216 | 0.00025836 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8232 |  | 2006-04-11 13:20 | 2006-04-11 | 2006-04-11 14:17 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 57 | 1 | 19353 | 57 | 0.00295 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8234 |  | 2006-04-12 09:05 | 2006-04-12 | 2006-04-12 14:14 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 309 | 9 | 19353 | 2781 | 0.1437 | 0.00046504 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8235 |  | 2006-04-12 09:40 | 2006-04-12 | 2006-04-12 10:22 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 42 | 1 | 19353 | 42 | 0.00217 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8236 |  | 2006-04-12 10:32 | 2006-04-12 | 2006-04-12 13:55 | Calculated | O410E |  |  |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 203 | 24 | 19353 | 4872 | 0.25174 | 0.0012401 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8237 |  | 2006-04-12 20:18 | 2006-04-12 | 2006-04-13 00:01 | Calculated | O410E | L665 | Pole Mounted |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 223 | 6 | 19353 | 1339 | 0.06919 | 0.00031003 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8238 |  | 2006-04-13 10:52 | 2006-04-13 | 2006-04-13 14:29 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 217 | 8 | 19353 | 1736 | 0.0897 | 0.00041337 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8239 |  | 2006-04-14 08:10 | 2006-04-14 | 2006-04-14 08:44 | Calculated | O410E | S373-399 | Single Circuit |  | Maihiihi 111-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 19 | 19353 | 646 | 0.03338 | 0.00098176 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8240 |  | 2006-04-18 09:46 | 2006-04-18 | 2006-04-18 09:51 | Calculated | O410E |  |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 13 | 19353 | 65 | 0.00336 | 0.00067173 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8242 |  | 2006-04-18 14:05 | 2006-04-18 | 2006-04-18 14:56 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 51 | 1 | 19353 | 51 | 0.00264 | 5.1672e-05 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8243 |  | 2006-04-19 10:13 | 2006-04-19 | 2006-04-19 14:06 | Calculated | O410E | LF |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 233 | 3 | 19353 | 699 | 0.03612 | 0.00015501 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8245 |  | 2006-04-19 10:37 | 2006-04-19 | 2006-04-19 10:38 | Calculated | O410E | C222 & 570 |  |  |  | Remote Rural F | Te Waireka Rd 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 0 | 19353 | 0 | 0 | 0 | 1 | 0 | 2006/2007 | April-2006 | 4 | 2006
8246 |  | 2006-04-19 22:04 | 2006-04-19 | 2006-04-19 22:05 | Calculated | O410E | C262 & 788 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2006/2007 | April-2006 | 4 | 2006
8247 |  | 2006-04-20 08:30 | 2006-04-20 | 2006-04-20 09:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 2 | 19353 | 154 | 0.00796 | 0.00010334 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8248 |  | 2006-04-20 10:27 | 2006-04-20 | 2006-04-20 10:48 | Calculated | O410E | LF |  |  | Aria 114-03 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 21 | 2 | 19353 | 42 | 0.00217 | 0.00010334 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8249 |  | 2006-04-21 10:34 | 2006-04-21 | 2006-04-21 14:25 | Calculated | O410E |  |  |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 231 | 8 | 19353 | 1848 | 0.09549 | 0.00041337 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8250 |  | 2006-04-21 11:20 | 2006-04-21 | 2006-04-21 15:24 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 244 | 3 | 19353 | 732 | 0.03782 | 0.00015501 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8251 |  | 2006-04-23 17:38 | 2006-04-23 | 2006-04-23 17:46 | Calculated | O410E | L1.16 | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 8 | 29 | 19353 | 232 | 0.01199 | 0.0014985 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8252 |  | 2006-04-24 09:38 | 2006-04-24 | 2006-04-24 11:30 | Calculated | O410E |  |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 37 | 19353 | 4144 | 0.21413 | 0.0019118 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8253 |  | 2006-04-24 22:36 | 2006-04-24 | 2006-04-24 22:52 | Calculated | O410E | C411 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 52 | 19353 | 832 | 0.04299 | 0.0026869 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8254 |  | 2006-04-25 09:19 | 2006-04-25 | 2006-04-25 10:56 | Calculated | O410E | C2102 | Single Circuit |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation | OH Lines : Pole - Hardwood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 420 | 19353 | 40810 | 2.1087 | 0.021702 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8255 |  | 2006-04-25 13:25 | 2006-04-25 | 2006-04-25 13:59 | Calculated | O410E | LV |  |  | Southern 409-04 | Remote Rural F | Southern | Manunui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 21 | 19353 | 714 | 0.03689 | 0.0010851 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8256 |  | 2006-04-25 16:25 | 2006-04-25 | 2006-04-25 17:40 | Calculated | O410E | C527 | Sectionaliser |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Mechanism | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 52 | 19353 | 3948 | 0.204 | 0.0026869 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8257 |  | 2006-04-27 09:02 | 2006-04-27 | 2006-04-27 11:13 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 131 | 43 | 19353 | 5639 | 0.29138 | 0.0022219 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8258 |  | 2006-04-27 09:10 | 2006-04-27 | 2006-04-27 15:59 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 409 | 300 | 19353 | 122700 | 6.3401 | 0.015501 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8259 |  | 2006-04-28 07:56 | 2006-04-28 | 2006-04-28 10:42 | Calculated | O410E | C1345 | Single Circuit |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Pole - Hardwood | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 25 | 19353 | 4155 | 0.2147 | 0.0012918 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8260 |  | 2006-04-28 11:26 | 2006-04-28 | 2006-04-28 14:56 | Calculated | O410E | LF |  |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 210 | 3 | 19353 | 630 | 0.03255 | 0.00015501 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8261 |  | 2006-04-30 08:48 | 2006-04-30 | 2006-04-30 09:45 | Calculated | O410E | C683 | Drop-Out Fuses |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 57 | 350 | 19353 | 20095 | 1.0383 | 0.018085 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8262 |  | 2006-04-30 19:10 | 2006-04-30 | 2006-04-30 19:14 | Calculated | O410E | C242 & 796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 241 | 19353 | 964 | 0.04981 | 0.012453 | 0 | 0 | 2006/2007 | April-2006 | 4 | 2006
8263 |  | 2006-05-01 09:10 | 2006-05-01 | 2006-05-01 11:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 120 | 1 | 19353 | 120 | 0.0062 | 5.1672e-05 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8264 |  | 2006-05-01 09:32 | 2006-05-01 | 2006-05-01 14:21 | Calculated | O410E |  |  |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 289 | 40 | 19353 | 11560 | 0.59732 | 0.0020669 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8266 |  | 2006-05-01 10:34 | 2006-05-01 | 2006-05-01 13:09 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 155 | 11 | 19353 | 1705 | 0.0881 | 0.00056839 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8267 |  | 2006-05-01 11:20 | 2006-05-01 | 2006-05-01 11:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 17 | 1 | 19353 | 17 | 0.00088 | 5.1672e-05 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8268 |  | 2006-05-01 19:00 | 2006-05-01 | 2006-05-01 21:41 | Calculated | O410E | L578 | Single Circuit |  | Rural 126-03 | Remote Rural F | Rural | Taharoa Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 2 | 19353 | 322 | 0.01664 | 0.00010334 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8270 |  | 2006-05-02 09:34 | 2006-05-02 | 2006-05-02 11:03 | Calculated | O410E |  |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 89 | 39 | 19353 | 3472 | 0.1794 | 0.0020152 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8272 |  | 2006-05-02 12:03 | 2006-05-02 | 2006-05-02 15:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 181 | 1 | 19353 | 181 | 0.00935 | 5.1672e-05 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8273 |  | 2006-05-03 10:38 | 2006-05-03 | 2006-05-03 15:22 | Calculated | O410E | LF |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 284 | 7 | 19353 | 1988 | 0.10272 | 0.0003617 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8274 |  | 2006-05-04 10:32 | 2006-05-04 | 2006-05-04 13:13 | Calculated | O410E |  |  |  | Whakamaru 120-03 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 161 | 8 | 19353 | 1288 | 0.06655 | 0.00041337 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8275 |  | 2006-05-04 10:33 | 2006-05-04 | 2006-05-04 12:02 | Calculated | O410E | LF |  |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 89 | 2 | 19353 | 178 | 0.0092 | 0.00010334 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8277 |  | 2006-05-06 14:05 | 2006-05-06 | 2006-05-06 14:36 | Calculated | O410E | L292 | Single Circuit |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 5 | 19353 | 155 | 0.00801 | 0.00025836 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8278 |  | 2006-05-07 09:42 | 2006-05-07 | 2006-05-07 11:43 | Calculated | O410E | L500 | Drop-Out Fuses |  | Caves 101-07 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 121 | 13 | 19353 | 1573 | 0.08128 | 0.00067173 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8279 |  | 2006-05-07 09:54 | 2006-05-07 | 2006-05-07 12:04 | Calculated | O410E | C268 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 52 | 19353 | 6775 | 0.35007 | 0.0026869 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8280 |  | 2006-05-09 09:22 | 2006-05-09 | 2006-05-09 11:39 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 137 | 27 | 19353 | 3718 | 0.19211 | 0.0013951 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8281 |  | 2006-05-09 11:00 | 2006-05-09 | 2006-05-09 12:09 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 69 | 40 | 19353 | 2760 | 0.14261 | 0.0020669 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8282 |  | 2006-05-10 08:08 | 2006-05-10 | 2006-05-10 08:23 | Calculated | O410E |  |  |  |  | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 15 | 58 | 19353 | 870 | 0.04495 | 0.002997 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8283 |  | 2006-05-10 10:03 | 2006-05-10 | 2006-05-10 14:01 | Calculated | O410E | LV |  |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 238 | 85 | 19353 | 20230 | 1.0453 | 0.0043921 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8284 |  | 2006-05-10 12:38 | 2006-05-10 | 2006-05-10 14:01 | Calculated | O410E | LF |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 4 | 19353 | 332 | 0.01715 | 0.00020669 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8285 |  | 2006-05-11 15:42 | 2006-05-11 | 2006-05-11 16:19 | Calculated | O410E | C683 |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 350 | 19353 | 13142 | 0.67907 | 0.018085 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8286 |  | 2006-05-11 20:21 | 2006-05-11 | 2006-05-11 21:16 | Calculated | O410E | S868-384-L390 | Drop-Out Fuses |  | Piopio 116-01 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 55 | 202 | 19353 | 11211 | 0.57929 | 0.010438 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8287 |  | 2006-05-11 20:37 | 2006-05-11 | 2006-05-11 22:16 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 3 | 19353 | 297 | 0.01535 | 0.00015501 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8288 |  | 2006-05-12 07:58 | 2006-05-12 | 2006-05-12 10:53 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 175 | 2 | 19353 | 350 | 0.01809 | 0.00010334 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8289 |  | 2006-05-12 08:01 | 2006-05-12 | 2006-05-12 10:55 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 174 | 5 | 19353 | 874 | 0.04516 | 0.00025836 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8290 |  | 2006-05-12 09:35 | 2006-05-12 | 2006-05-12 10:00 | Calculated | O410E | C683 | Single Circuit |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 63 | 19353 | 1578 | 0.08154 | 0.0032553 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8291 |  | 2006-05-12 09:42 | 2006-05-12 | 2006-05-12 11:43 | Calculated | O410E |  |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 5 | 19353 | 605 | 0.03126 | 0.00025836 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8292 |  | 2006-05-12 10:00 | 2006-05-12 | 2006-05-12 12:54 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 174 | 2 | 19353 | 348 | 0.01798 | 0.00010334 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8293 |  | 2006-05-12 10:07 | 2006-05-12 | 2006-05-12 13:56 | Calculated | O410E |  |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 229 | 97 | 19353 | 22213 | 1.1478 | 0.0050121 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8294 |  | 2006-05-12 10:17 | 2006-05-12 | 2006-05-12 13:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 167 | 1 | 19353 | 167 | 0.00863 | 5.1672e-05 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8295 |  | 2006-05-12 10:32 | 2006-05-12 | 2006-05-12 12:08 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 96 | 12 | 19353 | 1152 | 0.05953 | 0.00062006 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8296 |  | 2006-05-12 11:22 | 2006-05-12 | 2006-05-12 16:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-08 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 329 | 2 | 19353 | 658 | 0.034 | 0.00010334 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8297 |  | 2006-05-13 20:26 | 2006-05-13 | 2006-05-13 21:22 | Calculated | O410E | LF | Pole Mounted |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 3 | 19353 | 168 | 0.00868 | 0.00015501 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8298 |  | 2006-05-15 07:03 | 2006-05-15 | 2006-05-15 19:17 | Calculated | O410E | C806 | Single Circuit |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | OH Lines : Pole - Iron Rail | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 734 | 46 | 19353 | 33800 | 1.7465 | 0.0023769 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8299 |  | 2006-05-15 07:45 | 2006-05-15 | 2006-05-15 10:19 | Calculated | O410E | LV |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 4 | 19353 | 616 | 0.03183 | 0.00020669 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8300 |  | 2006-05-15 11:24 | 2006-05-15 | 2006-05-15 12:15 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 29 | 19353 | 1496 | 0.0773 | 0.0014985 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8302 |  | 2006-05-16 08:05 | 2006-05-16 | 2006-05-16 15:04 | Calculated | O410E | LF | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 419 | 1 | 19353 | 419 | 0.02165 | 5.1672e-05 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8304 |  | 2006-05-17 08:00 | 2006-05-17 | 2006-05-17 09:11 | Calculated | O410E | L500 | Drop-Out Fuses |  | Caves 101-07 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 71 | 13 | 19353 | 923 | 0.04769 | 0.00067173 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8305 |  | 2006-05-18 07:30 | 2006-05-18 | 2006-05-18 09:56 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 146 | 1 | 19353 | 146 | 0.00754 | 5.1672e-05 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8306 |  | 2006-05-18 09:15 | 2006-05-18 | 2006-05-18 11:07 | Calculated | O410E | C1725 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 6 | 19353 | 672 | 0.03472 | 0.00031003 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8307 |  | 2006-05-18 10:39 | 2006-05-18 | 2006-05-18 14:19 | Calculated | O410E |  |  |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 220 | 7 | 19353 | 1540 | 0.07957 | 0.0003617 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8308 |  | 2006-05-19 09:22 | 2006-05-19 | 2006-05-19 09:47 | Calculated | O410E |  |  |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 31 | 19353 | 775 | 0.04005 | 0.0016018 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8309 |  | 2006-05-19 09:40 | 2006-05-19 | 2006-05-19 11:34 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 114 | 1 | 19353 | 114 | 0.00589 | 5.1672e-05 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8311 |  | 2006-05-19 13:03 | 2006-05-19 | 2006-05-19 15:01 | Calculated | O410E |  |  |  | National Park 411-02 | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 118 | 9 | 19353 | 1062 | 0.05488 | 0.00046504 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8312 |  | 2006-05-19 14:32 | 2006-05-19 | 2006-05-19 16:01 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 89 | 41 | 19353 | 3649 | 0.18855 | 0.0021185 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8313 |  | 2006-05-22 09:06 | 2006-05-22 | 2006-05-22 12:04 | Calculated | O410E | LV |  |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 178 | 1 | 19353 | 178 | 0.0092 | 5.1672e-05 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8314 |  | 2006-05-22 10:04 | 2006-05-22 | 2006-05-22 11:57 | Calculated | O410E | LF |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 13 | 19353 | 1469 | 0.07591 | 0.00067173 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8315 |  | 2006-05-23 09:12 | 2006-05-23 | 2006-05-23 10:47 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 30 | 19353 | 2876 | 0.14861 | 0.0015501 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8316 |  | 2006-05-23 09:19 | 2006-05-23 | 2006-05-23 11:19 | Calculated | O410E | LF |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 3 | 19353 | 360 | 0.0186 | 0.00015501 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8317 |  | 2006-05-23 16:24 | 2006-05-23 | 2006-05-23 18:00 | Calculated | O410E | C362 |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 11 | 19353 | 1056 | 0.05457 | 0.00056839 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8318 |  | 2006-05-24 09:35 | 2006-05-24 | 2006-05-24 13:09 | Calculated | O410E |  |  |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 214 | 40 | 19353 | 8560 | 0.44231 | 0.0020669 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8319 |  | 2006-05-24 10:19 | 2006-05-24 | 2006-05-24 10:35 | Calculated | O410E | LF |  |  | Benneydale 103-07 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 45 | 19353 | 720 | 0.0372 | 0.0023252 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8321 |  | 2006-05-25 09:00 | 2006-05-25 | 2006-05-25 10:33 | Calculated | O410E | LF |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 1 | 19353 | 93 | 0.00481 | 5.1672e-05 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8320 |  | 2006-05-25 09:33 | 2006-05-25 | 2006-05-25 15:00 | Calculated | O410E |  |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 32 | 19353 | 10464 | 0.54069 | 0.0016535 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8322 |  | 2006-05-26 10:32 | 2006-05-26 | 2006-05-26 13:00 | Calculated | O410E |  |  |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 11 | 19353 | 1628 | 0.08412 | 0.00056839 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8325 |  | 2006-05-27 07:23 | 2006-05-27 | 2006-05-27 07:34 | Calculated | O410E | C132 |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 489 | 19353 | 5379 | 0.27794 | 0.025267 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8326 |  | 2006-05-28 11:33 | 2006-05-28 | 2006-05-28 12:17 | Calculated | O410E | L292 | Single Circuit |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 5 | 19353 | 220 | 0.01137 | 0.00025836 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8327 |  | 2006-05-28 13:09 | 2006-05-28 | 2006-05-28 16:31 | Calculated | O410E | C370 | Single Circuit |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 58 | 19353 | 11733 | 0.60626 | 0.002997 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8328 |  | 2006-05-30 09:03 | 2006-05-30 | 2006-05-30 12:28 | Calculated | O410E | LV |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 205 | 16 | 19353 | 3280 | 0.16948 | 0.00082675 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8329 |  | 2006-05-30 10:43 | 2006-05-30 | 2006-05-30 11:18 | Calculated | O410E | LF |  |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 4 | 19353 | 140 | 0.00723 | 0.00020669 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8330 |  | 2006-05-30 12:30 | 2006-05-30 | 2006-05-30 13:38 | Calculated | O410E | LF |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 16 | 19353 | 1088 | 0.05622 | 0.00082675 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8331 |  | 2006-05-31 10:30 | 2006-05-31 | 2006-05-31 13:52 | Calculated | O410E | LF |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 202 | 4 | 19353 | 808 | 0.04175 | 0.00020669 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8332 |  | 2006-05-31 12:45 | 2006-05-31 | 2006-05-31 14:00 | Calculated | O410E | LF |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 2 | 19353 | 150 | 0.00775 | 0.00010334 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8333 |  | 2006-05-31 23:10 | 2006-05-31 | 2006-06-01 01:13 | Calculated | O410E | C2092 |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 104 | 19353 | 12792 | 0.66098 | 0.0053738 | 0 | 0 | 2006/2007 | May-2006 | 5 | 2006
8334 |  | 2006-06-01 10:30 | 2006-06-01 | 2006-06-01 14:28 | Calculated | O410E |  |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 238 | 14 | 19353 | 3332 | 0.17217 | 0.0007234 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8335 |  | 2006-06-01 10:57 | 2006-06-01 | 2006-06-01 12:53 | Calculated | O410E | LF |  |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 116 | 1 | 19353 | 116 | 0.00599 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8336 |  | 2006-06-01 11:06 | 2006-06-01 | 2006-06-01 12:40 | Calculated | O410E | LF | Pole Mounted |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 1 | 19353 | 94 | 0.00486 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8337 |  | 2006-06-02 09:09 | 2006-06-02 | 2006-06-02 11:04 | Calculated | O410E | LF |  |  | Manunui 408-01 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 34 | 19353 | 3925 | 0.20281 | 0.0017568 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8338 |  | 2006-06-02 10:45 | 2006-06-02 | 2006-06-02 15:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 262 | 1 | 19353 | 262 | 0.01354 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8339 |  | 2006-06-03 07:41 | 2006-06-03 | 2006-06-03 07:50 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 42 | 19353 | 378 | 0.01953 | 0.0021702 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8340 |  | 2006-06-06 08:03 | 2006-06-06 | 2006-06-06 10:27 | Calculated | O410E | L466 | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 144 | 16 | 19353 | 2304 | 0.11905 | 0.00082675 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8341 |  | 2006-06-06 08:23 | 2006-06-06 | 2006-06-06 10:38 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 135 | 1 | 19353 | 135 | 0.00698 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8342 |  | 2006-06-06 09:17 | 2006-06-06 | 2006-06-06 09:40 | Calculated | O410E | LF |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 23 | 2 | 19353 | 46 | 0.00238 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8343 |  | 2006-06-06 09:34 | 2006-06-06 | 2006-06-06 11:31 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 30 | 19353 | 3516 | 0.18168 | 0.0015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8344 |  | 2006-06-06 12:48 | 2006-06-06 | 2006-06-06 13:45 | Calculated | O410E | L578 | Drop-Out Fuses |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 57 | 2 | 19353 | 114 | 0.00589 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8345 |  | 2006-06-06 14:21 | 2006-06-06 | 2006-06-06 15:56 | Calculated | O410E | LF |  |  | Southern 409-09 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 1 | 19353 | 95 | 0.00491 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8346 |  | 2006-06-07 09:12 | 2006-06-07 | 2006-06-07 10:45 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 93 | 30 | 19353 | 2811 | 0.14525 | 0.0015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8347 |  | 2006-06-07 09:38 | 2006-06-07 | 2006-06-07 15:05 | Calculated | O410E |  |  |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 15 | 19353 | 4905 | 0.25345 | 0.00077507 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8348 |  | 2006-06-07 10:31 | 2006-06-07 | 2006-06-07 13:37 | Calculated | O410E |  |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 186 | 7 | 19353 | 1302 | 0.06728 | 0.0003617 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8351 |  | 2006-06-08 11:00 | 2006-06-08 | 2006-06-08 14:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 205 | 6 | 19353 | 1230 | 0.06356 | 0.00031003 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8352 |  | 2006-06-08 13:04 | 2006-06-08 | 2006-06-08 14:03 | Calculated | O410E | S147 | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 59 | 27 | 19353 | 1593 | 0.08231 | 0.0013951 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8353 |  | 2006-06-09 09:03 | 2006-06-09 | 2006-06-09 11:05 | Calculated | O410E | LF |  |  | Manunui 408-01 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 122 | 34 | 19353 | 4153 | 0.21459 | 0.0017568 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8356 |  | 2006-06-09 12:24 | 2006-06-09 | 2006-06-09 13:13 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Bushings (fixed Insulation) | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 49 | 118 | 19353 | 5866 | 0.30311 | 0.0060972 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8357 |  | 2006-06-09 14:53 | 2006-06-09 | 2006-06-09 14:56 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 241 | 19353 | 723 | 0.03736 | 0.012453 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8358 |  | 2006-06-12 08:08 | 2006-06-12 | 2006-06-12 11:24 | Calculated | O410E | C1107 | Single Circuit |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Pole - Hardwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 65 | 19353 | 12740 | 0.6583 | 0.0033587 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8360 |  | 2006-06-12 08:20 | 2006-06-12 | 2006-06-13 08:44 | Calculated | O410E | C287 | Single Circuit |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Pole - Iron Rail | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1464 | 18 | 19353 | 26365 | 1.3623 | 0.00093009 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8359 |  | 2006-06-12 09:48 | 2006-06-12 | 2006-06-12 11:29 | Calculated | O410E | S695 | Drop-Out Fuses |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 101 | 126 | 19353 | 12726 | 0.65757 | 0.0065106 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8361 |  | 2006-06-12 09:48 | 2006-06-12 | 2006-06-12 16:15 | Calculated | O410E | C1354 | Single Circuit |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Pole - Pre-Stressed Concrete | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 387 | 42 | 19353 | 16275 | 0.84095 | 0.0021702 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8362 |  | 2006-06-12 10:00 | 2006-06-12 | 2006-06-12 15:31 | Calculated | O410E | C1010 | Single Circuit |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Insulator - Pin | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 331 | 499 | 19353 | 165169 | 8.5345 | 0.025784 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8363 |  | 2006-06-12 10:31 | 2006-06-12 | 2006-06-12 11:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 79 | 4 | 19353 | 316 | 0.01633 | 0.00020669 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8364 |  | 2006-06-12 10:46 | 2006-06-12 | 2006-06-13 04:52 | Calculated | O410E | C426 | Single Circuit |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1086 | 78 | 19353 | 84762 | 4.3798 | 0.0040304 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8365 |  | 2006-06-12 10:50 | 2006-06-12 | 2006-06-12 19:54 | Calculated | O410E | C109 | Single Circuit |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 544 | 70 | 19353 | 38137 | 1.9706 | 0.003617 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8396 |  | 2006-06-12 11:17 | 2006-06-12 | 2006-06-13 14:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 1615 | 3 | 19353 | 4845 | 0.25035 | 0.00015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8366 |  | 2006-06-12 11:28 | 2006-06-12 | 2006-06-12 22:12 | Calculated | O410E | C1 | Single Circuit |  | Mokai 123-00 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 644 | 259 | 19353 | 166830 | 8.6204 | 0.013383 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8368 |  | 2006-06-12 11:31 | 2006-06-12 | 2006-06-12 15:06 | Calculated | O410E | C6121 | Single Circuit |  | Waihaha 426-01 | Remote Rural F | Waihaha | Kuratau Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 215 | 236 | 19353 | 50858 | 2.6279 | 0.012194 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8367 |  | 2006-06-12 11:35 | 2006-06-12 | 2006-06-12 23:30 | Calculated | O410E | C1072 | Single Circuit |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 715 | 107 | 19353 | 76546 | 3.9552 | 0.0055289 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8369 |  | 2006-06-12 11:39 | 2006-06-12 | 2006-06-12 13:28 | Calculated | O410E | C2082 | Single Circuit |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation | OH Lines : Conductor - Bare Copper | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 443 | 19353 | 48626 | 2.5126 | 0.022891 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8370 |  | 2006-06-12 11:40 | 2006-06-12 | 2006-06-12 12:40 | Calculated | O410E | L246 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 60 | 17 | 19353 | 1020 | 0.05271 | 0.00087842 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8371 |  | 2006-06-12 11:43 | 2006-06-12 | 2006-06-12 13:16 | Calculated | O410E | C462 |  |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 87 | 19353 | 8091 | 0.41807 | 0.0044954 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8372 |  | 2006-06-12 12:17 | 2006-06-12 | 2006-06-12 15:20 | Calculated | O410E | L720 | Drop-Out Fuses |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 183 | 1 | 19353 | 183 | 0.00946 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8373 |  | 2006-06-12 12:31 | 2006-06-12 | 2006-06-12 13:16 | Calculated | O410E | C642 | Single Circuit |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 87 | 19353 | 3915 | 0.20229 | 0.0044954 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8374 |  | 2006-06-12 13:52 | 2006-06-12 | 2006-06-13 04:44 | Calculated | O410E | S314 | Single Circuit |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 892 | 10 | 19353 | 8926 | 0.46122 | 0.00051672 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8375 |  | 2006-06-12 13:55 | 2006-06-12 | 2006-06-12 15:52 | Calculated | O410E | C1322 | Single Circuit |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 17 | 19353 | 1989 | 0.10277 | 0.00087842 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8376 |  | 2006-06-12 13:59 | 2006-06-12 | 2006-06-13 15:12 | Calculated | O410E | C202 | Low Under High |  |  | Remote Rural F | Nihoniho | Nihoniho Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1513 | 321 | 19353 | 485903 | 25.1074 | 0.016587 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8377 |  | 2006-06-12 13:59 | 2006-06-12 | 2006-06-13 08:16 | Calculated | O410E | C824 | Low Under High |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1097 | 101 | 19353 | 110830 | 5.7268 | 0.0052188 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8378 |  | 2006-06-12 14:16 | 2006-06-12 | 2006-06-13 05:14 | Calculated | O410E | C440 | Single Circuit |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 898 | 43 | 19353 | 38622 | 1.9957 | 0.0022219 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8379 |  | 2006-06-12 14:34 | 2006-06-12 | 2006-06-12 16:25 | Calculated | O410E | C1272 | Single Circuit |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 150 | 19353 | 16780 | 0.86705 | 0.0077507 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8403 |  | 2006-06-12 15:32 | 2006-06-12 | 2006-06-13 17:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 1555 | 2 | 19353 | 3110 | 0.1607 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8380 |  | 2006-06-12 16:48 | 2006-06-12 | 2006-06-12 17:42 | Calculated | O410E | C1335 | Single Circuit |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 13 | 19353 | 702 | 0.03627 | 0.00067173 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8381 |  | 2006-06-12 16:53 | 2006-06-12 | 2006-06-12 19:24 | Calculated | O410E | C378 | Single Circuit |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 203 | 19353 | 30761 | 1.5895 | 0.010489 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8382 |  | 2006-06-12 17:13 | 2006-06-12 | 2006-06-12 19:47 | Calculated | O410E | L1539 | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 154 | 9 | 19353 | 1393 | 0.07198 | 0.00046504 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8383 |  | 2006-06-12 17:58 | 2006-06-12 | 2006-06-13 10:20 | Calculated | O410E | L239 | Single Circuit |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 982 | 20 | 19353 | 19640 | 1.0148 | 0.0010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8384 |  | 2006-06-12 18:52 | 2006-06-12 | 2006-06-12 19:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 23 | 1 | 19353 | 23 | 0.00119 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8385 |  | 2006-06-12 19:21 | 2006-06-12 | 2006-06-13 12:51 | Calculated | O410E | C1354 | Single Circuit |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Insulator - Pin | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1050 | 32 | 19353 | 33616 | 1.737 | 0.0016535 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8386 |  | 2006-06-12 19:54 | 2006-06-12 | 2006-06-12 22:26 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 152 | 3 | 19353 | 456 | 0.02356 | 0.00015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8387 |  | 2006-06-13 07:15 | 2006-06-13 | 2006-06-13 09:06 | Calculated | O410E | C378 | Single Circuit |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 203 | 19353 | 22637 | 1.1697 | 0.010489 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8388 |  | 2006-06-13 07:20 | 2006-06-13 | 2006-06-13 08:53 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 4 | 19353 | 372 | 0.01922 | 0.00020669 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8389 |  | 2006-06-13 07:23 | 2006-06-13 | 2006-06-13 09:52 | Calculated | O410E | L433 | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 149 | 9 | 19353 | 1341 | 0.06929 | 0.00046504 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8390 |  | 2006-06-13 08:09 | 2006-06-13 | 2006-06-13 14:17 | Calculated | O410E | L593 | Drop-Out Fuses |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 368 | 15 | 19353 | 5520 | 0.28523 | 0.00077507 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8391 |  | 2006-06-13 09:12 | 2006-06-13 | 2006-06-13 11:02 | Calculated | O410E | C811 |  |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 30 | 19353 | 3300 | 0.17052 | 0.0015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8392 |  | 2006-06-13 09:23 | 2006-06-13 | 2006-06-13 11:55 | Calculated | O410E | L677 | Drop-Out Fuses |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 152 | 8 | 19353 | 1216 | 0.06283 | 0.00041337 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8393 |  | 2006-06-13 09:27 | 2006-06-13 | 2006-06-13 11:39 | Calculated | O410E | L246 | Drop-Out Fuses |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 132 | 20 | 19353 | 2640 | 0.13641 | 0.0010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8394 |  | 2006-06-13 10:57 | 2006-06-13 | 2006-06-13 11:22 | Calculated | O410E | LF |  |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 2 | 19353 | 50 | 0.00258 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8395 |  | 2006-06-13 12:10 | 2006-06-13 | 2006-06-13 13:21 | Calculated | O410E | LF |  |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 1 | 19353 | 71 | 0.00367 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8397 |  | 2006-06-13 12:14 | 2006-06-13 | 2006-06-13 14:54 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 160 | 3 | 19353 | 480 | 0.0248 | 0.00015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8398 |  | 2006-06-13 12:32 | 2006-06-13 | 2006-06-13 14:56 | Calculated | O410E | L171 | Drop-Out Fuses |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 144 | 8 | 19353 | 1152 | 0.05953 | 0.00041337 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8399 |  | 2006-06-13 13:36 | 2006-06-13 | 2006-06-13 16:31 | Calculated | O410E | L633 | Single Circuit |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Pole - Hardwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 13 | 19353 | 2275 | 0.11755 | 0.00067173 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8400 |  | 2006-06-13 15:03 | 2006-06-13 | 2006-06-13 18:20 | Calculated | O410E | LF | Pole Mounted |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 2 | 19353 | 394 | 0.02036 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8401 |  | 2006-06-13 15:04 | 2006-06-13 | 2006-06-13 16:10 | Calculated | O410E | LF |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 15 | 19353 | 990 | 0.05115 | 0.00077507 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8402 |  | 2006-06-13 15:06 | 2006-06-13 | 2006-06-13 15:31 | Calculated | O410E | S491-462 | Drop-Out Fuses |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation | Switchgear : Mechanism | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 25 | 4 | 19353 | 100 | 0.00517 | 0.00020669 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8404 |  | 2006-06-13 15:14 | 2006-06-13 | 2006-06-13 17:12 | Calculated | O410E | L414 | Drop-Out Fuses |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 118 | 6 | 19353 | 708 | 0.03658 | 0.00031003 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8405 |  | 2006-06-13 17:27 | 2006-06-13 | 2006-06-13 17:53 | Calculated | O410E | LF |  |  | Caves 101-05 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 1 | 19353 | 26 | 0.00134 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8406 |  | 2006-06-14 08:04 | 2006-06-14 | 2006-06-14 10:09 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 125 | 1 | 19353 | 125 | 0.00646 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8407 |  | 2006-06-14 10:01 | 2006-06-14 | 2006-06-14 10:38 | Calculated | O410E | LF |  |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 1 | 19353 | 37 | 0.00191 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8408 |  | 2006-06-14 10:54 | 2006-06-14 | 2006-06-14 11:34 | Calculated | O410E | LF |  |  | Te Mapara 117-05 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1 | 19353 | 40 | 0.00207 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8409 |  | 2006-06-14 11:46 | 2006-06-14 | 2006-06-14 13:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 124 | 3 | 19353 | 372 | 0.01922 | 0.00015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8410 |  | 2006-06-14 12:30 | 2006-06-14 | 2006-06-14 12:58 | Calculated | O410E | LF |  |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 1 | 19353 | 28 | 0.00145 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8411 |  | 2006-06-14 12:32 | 2006-06-14 | 2006-06-14 13:50 | Calculated | O410E | L5537 | Single Circuit |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 25 | 19353 | 1950 | 0.10076 | 0.0012918 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8412 |  | 2006-06-14 14:03 | 2006-06-14 | 2006-06-14 14:46 | Calculated | O410E | L1621 |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 6 | 19353 | 258 | 0.01333 | 0.00031003 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8413 |  | 2006-06-14 15:11 | 2006-06-14 | 2006-06-14 16:37 | Calculated | O410E | C313 | Single Circuit |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 10 | 19353 | 860 | 0.04444 | 0.00051672 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8414 |  | 2006-06-14 16:04 | 2006-06-14 | 2006-06-14 17:56 | Calculated | O410E | S700-428-C426 |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 48 | 19353 | 5376 | 0.27779 | 0.0024802 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8415 |  | 2006-06-15 11:23 | 2006-06-15 | 2006-06-15 13:30 | Calculated | O410E |  | Single Circuit |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation | OH Lines : Crossarm - Wood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 80 | 19353 | 10160 | 0.52498 | 0.0041337 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8416 |  | 2006-06-15 11:44 | 2006-06-15 | 2006-06-15 15:06 | Calculated | O410E | S506 | Single Circuit |  | Caves 101-13 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 43 | 19353 | 8686 | 0.44882 | 0.0022219 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8417 |  | 2006-06-16 10:01 | 2006-06-16 | 2006-06-16 16:20 | Calculated | O410E | LF |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 379 | 32 | 19353 | 12128 | 0.62667 | 0.0016535 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8418 |  | 2006-06-16 11:29 | 2006-06-16 | 2006-06-16 13:45 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 136 | 2 | 19353 | 272 | 0.01405 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8419 |  | 2006-06-16 15:20 | 2006-06-16 | 2006-06-16 18:01 | Calculated | O410E | C475 |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 34 | 19353 | 5474 | 0.28285 | 0.0017568 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8420 |  | 2006-06-16 15:44 | 2006-06-16 | 2006-06-16 16:53 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 69 | 5 | 19353 | 347 | 0.01793 | 0.00025836 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8421 |  | 2006-06-16 15:45 | 2006-06-16 | 2006-06-16 16:55 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 70 | 6 | 19353 | 424 | 0.02191 | 0.00031003 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8422 |  | 2006-06-16 15:59 | 2006-06-16 | 2006-06-16 17:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 3 | 19353 | 227 | 0.01173 | 0.00015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8423 |  | 2006-06-16 16:07 | 2006-06-16 | 2006-06-16 18:22 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 135 | 4 | 19353 | 542 | 0.02801 | 0.00020669 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8424 |  | 2006-06-16 16:42 | 2006-06-16 | 2006-06-16 19:43 | Calculated | O410E | LF | Drop-Out Fuses |  | Rural 126-02 | Remote Rural F | Rural | Taharoa Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 181 | 8 | 19353 | 1454 | 0.07513 | 0.00041337 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8426 |  | 2006-06-18 11:05 | 2006-06-18 | 2006-06-18 11:55 | Calculated | O410E | L691 | Single Circuit |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 3 | 19353 | 150 | 0.00775 | 0.00015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8427 |  | 2006-06-19 10:27 | 2006-06-19 | 2006-06-20 08:41 | Calculated | O410E | L162 | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 1334 | 4 | 19353 | 5336 | 0.27572 | 0.00020669 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8428 |  | 2006-06-19 10:31 | 2006-06-19 | 2006-06-19 15:16 | Calculated | O410E |  |  |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 121 | 19353 | 34485 | 1.7819 | 0.0062523 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8429 |  | 2006-06-19 10:39 | 2006-06-19 | 2006-06-19 12:38 | Calculated | O410E | C641 | Single Circuit |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 267 | 19353 | 31799 | 1.6431 | 0.013796 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8430 |  | 2006-06-19 10:48 | 2006-06-19 | 2006-06-19 13:16 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 148 | 1 | 19353 | 148 | 0.00765 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8431 |  | 2006-06-19 11:36 | 2006-06-19 | 2006-06-19 13:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-05 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 123 | 1 | 19353 | 123 | 0.00636 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8432 |  | 2006-06-19 11:41 | 2006-06-19 | 2006-06-19 14:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 185 | 3 | 19353 | 555 | 0.02868 | 0.00015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8433 |  | 2006-06-19 12:07 | 2006-06-19 | 2006-06-19 14:15 | Calculated | O410E | L310 | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 128 | 4 | 19353 | 512 | 0.02646 | 0.00020669 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8434 |  | 2006-06-19 13:34 | 2006-06-19 | 2006-06-19 13:58 | Calculated | O410E | LF |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 15 | 19353 | 360 | 0.0186 | 0.00077507 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8435 |  | 2006-06-19 14:10 | 2006-06-19 | 2006-06-19 16:11 | Calculated | O410E | C268 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 52 | 19353 | 6292 | 0.32512 | 0.0026869 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8436 |  | 2006-06-19 16:03 | 2006-06-19 | 2006-06-19 18:18 | Calculated | O410E | C142 |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 273 | 19353 | 36855 | 1.9044 | 0.014106 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8437 |  | 2006-06-19 16:21 | 2006-06-19 | 2006-06-19 17:20 | Calculated | O410E | C824 | Single Circuit |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 101 | 19353 | 5959 | 0.30791 | 0.0052188 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8438 |  | 2006-06-19 16:31 | 2006-06-19 | 2006-06-19 18:56 | Calculated | O410E | C591 | Single Circuit |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 44 | 19353 | 6380 | 0.32966 | 0.0022735 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8439 |  | 2006-06-19 16:38 | 2006-06-19 | 2006-06-20 11:08 | Calculated | O410E | L590 | Single Circuit |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1110 | 5 | 19353 | 5550 | 0.28678 | 0.00025836 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8440 |  | 2006-06-19 16:41 | 2006-06-19 | 2006-06-19 22:00 | Calculated | O410E | C446 | Single Circuit |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 319 | 106 | 19353 | 33911 | 1.7522 | 0.0054772 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8441 |  | 2006-06-20 08:03 | 2006-06-20 | 2006-06-20 09:18 | Calculated | O410E | LF | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8442 |  | 2006-06-20 10:55 | 2006-06-20 | 2006-06-20 15:39 | Calculated | O410E |  |  |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 284 | 11 | 19353 | 3124 | 0.16142 | 0.00056839 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8443 |  | 2006-06-20 10:59 | 2006-06-20 | 2006-06-20 12:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-05 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 2 | 19353 | 134 | 0.00692 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8444 |  | 2006-06-20 14:43 | 2006-06-20 | 2006-06-20 16:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 2 | 19353 | 184 | 0.00951 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8445 |  | 2006-06-20 17:10 | 2006-06-20 | 2006-06-20 17:33 | Calculated | O410E | LF |  |  | McDonalds 110-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 23 | 1 | 19353 | 23 | 0.00119 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8446 |  | 2006-06-21 09:25 | 2006-06-21 | 2006-06-21 10:13 | Calculated | O410E | LF | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 48 | 1 | 19353 | 48 | 0.00248 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8447 |  | 2006-06-21 09:35 | 2006-06-21 | 2006-06-21 10:33 | Calculated | O410E | LF |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 16 | 19353 | 928 | 0.04795 | 0.00082675 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8448 |  | 2006-06-21 10:48 | 2006-06-21 | 2006-06-21 14:09 | Calculated | O410E | LF |  |  | Mokau 128-08 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 201 | 26 | 19353 | 5226 | 0.27004 | 0.0013435 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8449 |  | 2006-06-21 11:11 | 2006-06-21 | 2006-06-21 13:06 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 42 | 19353 | 4835 | 0.24983 | 0.0021702 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8450 |  | 2006-06-21 11:32 | 2006-06-21 | 2006-06-21 14:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 174 | 3 | 19353 | 522 | 0.02697 | 0.00015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8451 |  | 2006-06-22 08:45 | 2006-06-22 | 2006-06-22 09:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 51 | 1 | 19353 | 51 | 0.00264 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8452 |  | 2006-06-22 10:34 | 2006-06-22 | 2006-06-22 14:38 | Calculated | O410E |  |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 244 | 80 | 19353 | 19520 | 1.0086 | 0.0041337 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8454 |  | 2006-06-22 15:43 | 2006-06-22 | 2006-06-22 15:54 | Calculated | O410E | S667-681 | Single Circuit |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 149 | 19353 | 1698 | 0.08774 | 0.0076991 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8455 |  | 2006-06-22 16:47 | 2006-06-22 | 2006-06-22 19:13 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 146 | 2 | 19353 | 292 | 0.01509 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8456 |  | 2006-06-23 05:25 | 2006-06-23 | 2006-06-23 09:16 | Calculated | O410E | C949 |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 1 | 19353 | 231 | 0.01194 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8457 |  | 2006-06-23 09:03 | 2006-06-23 | 2006-06-23 11:40 | Calculated | O410E | L466 | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 157 | 16 | 19353 | 2512 | 0.1298 | 0.00082675 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8458 |  | 2006-06-23 09:20 | 2006-06-23 | 2006-06-23 10:37 | Calculated | O410E | S645 | Drop-Out Fuses |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 71 | 19353 | 5467 | 0.28249 | 0.0036687 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8459 |  | 2006-06-23 10:13 | 2006-06-23 | 2006-06-23 15:25 | Calculated | O410E |  |  |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 312 | 8 | 19353 | 2496 | 0.12897 | 0.00041337 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8460 |  | 2006-06-23 12:50 | 2006-06-23 | 2006-06-23 15:14 | Calculated | O410E | L442 | Single Circuit |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 16 | 19353 | 2304 | 0.11905 | 0.00082675 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8461 |  | 2006-06-23 14:05 | 2006-06-23 | 2006-06-23 15:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 70 | 2 | 19353 | 140 | 0.00723 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8462 |  | 2006-06-23 14:12 | 2006-06-23 | 2006-06-23 15:29 | Calculated | O410E | C1725 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 6 | 19353 | 462 | 0.02387 | 0.00031003 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8463 |  | 2006-06-24 08:30 | 2006-06-24 | 2006-06-24 09:11 | Calculated | O410E | LF | Pole Mounted |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 1 | 19353 | 41 | 0.00212 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8464 |  | 2006-06-24 08:47 | 2006-06-24 | 2006-06-24 10:11 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 84 | 1 | 19353 | 84 | 0.00434 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8465 |  | 2006-06-25 09:08 | 2006-06-25 | 2006-06-25 11:33 | Calculated | O410E | C2082 |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 443 | 19353 | 64330 | 3.324 | 0.022891 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8466 |  | 2006-06-25 11:59 | 2006-06-25 | 2006-06-25 12:03 | Calculated | O410E | C2092 |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 105 | 19353 | 420 | 0.0217 | 0.0054255 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8468 |  | 2006-06-26 12:36 | 2006-06-26 | 2006-06-26 13:14 | Calculated | O410E | LF |  |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 38 | 4 | 19353 | 152 | 0.00785 | 0.00020669 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8469 |  | 2006-06-26 15:24 | 2006-06-26 | 2006-06-26 17:16 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 112 | 1 | 19353 | 112 | 0.00579 | 5.1672e-05 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8470 |  | 2006-06-27 09:00 | 2006-06-27 | 2006-06-27 14:25 | Calculated | O410E |  |  |  | Manunui 408-01 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 325 | 50 | 19353 | 16250 | 0.83966 | 0.0025836 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8471 |  | 2006-06-27 09:19 | 2006-06-27 | 2006-06-27 09:59 | Calculated | O410E | LF |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 40 | 4 | 19353 | 160 | 0.00827 | 0.00020669 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8472 |  | 2006-06-27 09:31 | 2006-06-27 | 2006-06-27 15:58 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 387 | 29 | 19353 | 11223 | 0.57991 | 0.0014985 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8474 |  | 2006-06-27 10:30 | 2006-06-27 | 2006-06-27 14:27 | Calculated | O410E |  |  |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 237 | 32 | 19353 | 7584 | 0.39188 | 0.0016535 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8476 |  | 2006-06-27 10:30 | 2006-06-27 | 2006-06-27 11:16 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 46 | 63 | 19353 | 2898 | 0.14974 | 0.0032553 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8475 |  | 2006-06-27 10:31 | 2006-06-27 | 2006-06-27 14:04 | Calculated | O410E |  |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 213 | 33 | 19353 | 7029 | 0.3632 | 0.0017052 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8477 |  | 2006-06-27 11:43 | 2006-06-27 | 2006-06-27 12:08 | Calculated | O410E | LF |  |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 2 | 19353 | 50 | 0.00258 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8478 |  | 2006-06-27 12:30 | 2006-06-27 | 2006-06-27 17:59 | Calculated | O410E | LF | Pole Mounted |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 329 | 4 | 19353 | 1316 | 0.068 | 0.00020669 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8479 |  | 2006-06-27 17:09 | 2006-06-27 | 2006-06-27 17:40 | Calculated | O410E | S423-653 | Drop-Out Fuses |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 31 | 35 | 19353 | 1085 | 0.05606 | 0.0018085 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8480 |  | 2006-06-28 01:35 | 2006-06-28 | 2006-06-28 03:30 | Calculated | O410E | C880 | Other |  | Hakiaha 401-01 | Remote Rural F | Hakiaha | Borough Zone Substation | Cables : Cable Box - Dry (Raychem) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 115 | 237 | 19353 | 27393 | 1.4154 | 0.012246 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8481 |  | 2006-06-28 10:02 | 2006-06-28 | 2006-06-28 15:01 | Calculated | O410E | LV |  |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 299 | 30 | 19353 | 8970 | 0.46349 | 0.0015501 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8482 |  | 2006-06-28 12:00 | 2006-06-28 | 2006-06-28 13:33 | Calculated | O410E | L1529 | Drop-Out Fuses |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 2 | 19353 | 186 | 0.00961 | 0.00010334 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8483 |  | 2006-06-29 09:25 | 2006-06-29 | 2006-06-29 11:04 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 99 | 17 | 19353 | 1683 | 0.08696 | 0.00087842 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
8484 |  | 2006-06-29 16:00 | 2006-06-29 | 2006-06-29 16:49 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 49 | 48 | 19353 | 2352 | 0.12153 | 0.0024802 | 0 | 0 | 2006/2007 | June-2006 | 6 | 2006
11015 |  | 2006-07-02 10:35 | 2006-07-02 | 2006-07-02 12:11 | Calculated | o410e | LF13K13 | 38 |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 5 | 19353 | 480 | 0.0248 | 0.00025836 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8488 |  | 2006-07-03 21:54 | 2006-07-03 | 2006-07-03 22:02 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1 | 19353 | 8 | 0.00041 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8489 |  | 2006-07-04 09:49 | 2006-07-04 | 2006-07-04 10:27 | Calculated | O410E |  |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 38 | 65 | 19353 | 2525 | 0.13047 | 0.0033587 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8491 |  | 2006-07-04 10:57 | 2006-07-04 | 2006-07-04 12:19 | Calculated | O410E | L1730 | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 82 | 7 | 19353 | 574 | 0.02966 | 0.0003617 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8492 |  | 2006-07-05 11:04 | 2006-07-05 | 2006-07-05 14:09 | Calculated | O410E | LV |  |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 185 | 86 | 19353 | 15910 | 0.82209 | 0.0044438 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8496 |  | 2006-07-06 08:54 | 2006-07-06 | 2006-07-06 12:10 | Calculated | O410E | C296 | Single Circuit |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Conductor - Bare ACSR | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 138 | 19353 | 27103 | 1.4004 | 0.0071307 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8495 |  | 2006-07-06 09:00 | 2006-07-06 | 2006-07-06 10:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 97 | 8 | 19353 | 776 | 0.0401 | 0.00041337 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8497 |  | 2006-07-06 12:30 | 2006-07-06 | 2006-07-06 13:53 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 83 | 1 | 19353 | 83 | 0.00429 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8498 |  | 2006-07-06 14:01 | 2006-07-06 | 2006-07-06 16:11 | Calculated | O410E | C378 | Single Circuit |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 203 | 19353 | 26552 | 1.372 | 0.010489 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8500 |  | 2006-07-06 21:36 | 2006-07-06 | 2006-07-06 21:45 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 2 | 19353 | 18 | 0.00093 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8501 |  | 2006-07-06 23:11 | 2006-07-06 | 2006-07-07 02:00 | Calculated | O410E | C466 | Single Circuit |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Pole Fittings e.g OCB Hangers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 169 | 45 | 19353 | 7608 | 0.39312 | 0.0023252 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8502 |  | 2006-07-07 09:16 | 2006-07-07 | 2006-07-07 14:59 | Calculated | O410E |  |  |  | Manunui 408-01 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 343 | 190 | 19353 | 65170 | 3.3674 | 0.0098176 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8503 |  | 2006-07-07 10:24 | 2006-07-07 | 2006-07-07 11:34 | Calculated | O410E | LF |  |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 6 | 19353 | 420 | 0.0217 | 0.00031003 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8504 |  | 2006-07-08 05:26 | 2006-07-08 | 2006-07-08 08:52 | Calculated | O410E | S473 | Single Circuit |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 206 | 20 | 19353 | 4120 | 0.21289 | 0.0010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8505 |  | 2006-07-08 15:50 | 2006-07-08 | 2006-07-08 17:11 | Calculated | O410E | LF | Pole Mounted |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 1 | 19353 | 81 | 0.00419 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8506 |  | 2006-07-08 23:49 | 2006-07-08 | 2006-07-09 00:10 | Calculated | O410E | LV |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 61 | 19353 | 1281 | 0.06619 | 0.003152 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8507 |  | 2006-07-10 09:11 | 2006-07-10 | 2006-07-10 14:30 | Calculated | O410E | LF |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 319 | 1 | 19353 | 319 | 0.01648 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8508 |  | 2006-07-10 09:18 | 2006-07-10 | 2006-07-10 10:08 | Calculated | O410E | LF |  |  | Rangitoto 106-07 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 50 | 1 | 19353 | 50 | 0.00258 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8510 |  | 2006-07-10 10:47 | 2006-07-10 | 2006-07-10 14:18 | Calculated | O410E |  |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 211 | 6 | 19353 | 1266 | 0.06542 | 0.00031003 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8512 |  | 2006-07-10 13:18 | 2006-07-10 | 2006-07-10 14:15 | Calculated | O410E | LF |  |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 57 | 1 | 19353 | 57 | 0.00295 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8513 |  | 2006-07-10 14:44 | 2006-07-10 | 2006-07-10 16:06 | Calculated | O410E | LF |  |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 3 | 19353 | 246 | 0.01271 | 0.00015501 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8518 |  | 2006-07-11 13:32 | 2006-07-11 | 2006-07-11 14:52 | Calculated | O410E |  |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 80 | 22 | 19353 | 1760 | 0.09094 | 0.0011368 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8519 |  | 2006-07-11 16:17 | 2006-07-11 | 2006-07-11 17:09 | Calculated | O410E | LF |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 4 | 19353 | 208 | 0.01075 | 0.00020669 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8520 |  | 2006-07-12 03:52 | 2006-07-12 | 2006-07-12 04:07 | Calculated | O410E | C242 & 262 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 15 | 328 | 19353 | 4920 | 0.25422 | 0.016948 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8521 |  | 2006-07-12 03:52 | 2006-07-12 | 2006-07-12 11:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 433 | 10 | 19353 | 4336 | 0.22405 | 0.00051672 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8522 |  | 2006-07-12 03:52 | 2006-07-12 | 2006-07-12 13:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 563 | 45 | 19353 | 25363 | 1.3106 | 0.0023252 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8523 |  | 2006-07-12 04:07 | 2006-07-12 | 2006-07-12 08:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 247 | 4 | 19353 | 988 | 0.05105 | 0.00020669 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8524 |  | 2006-07-12 04:15 | 2006-07-12 | 2006-07-12 08:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 245 | 2 | 19353 | 490 | 0.02532 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8525 |  | 2006-07-12 11:00 | 2006-07-12 | 2006-07-12 11:45 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 45 | 20 | 19353 | 908 | 0.04692 | 0.0010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8526 |  | 2006-07-12 12:35 | 2006-07-12 | 2006-07-12 13:06 | Calculated | O410E | L578 | Single Circuit |  | Rural 126-03 | Remote Rural F | Rural | Taharoa Zone Substation | OH Lines : Surge Diverters | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 2 | 19353 | 62 | 0.0032 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8527 |  | 2006-07-12 13:32 | 2006-07-12 | 2006-07-12 15:11 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 10 | 19353 | 994 | 0.05136 | 0.00051672 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8528 |  | 2006-07-12 22:28 | 2006-07-12 | 2006-07-12 22:29 | Calculated | O410E | C262 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2006/2007 | July-2006 | 7 | 2006
8529 |  | 2006-07-12 22:34 | 2006-07-12 | 2006-07-13 01:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 204 | 1 | 19353 | 204 | 0.01054 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8530 |  | 2006-07-13 07:20 | 2006-07-13 | 2006-07-13 09:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 115 | 5 | 19353 | 579 | 0.02992 | 0.00025836 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8531 |  | 2006-07-13 08:11 | 2006-07-13 | 2006-07-13 10:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 117 | 1 | 19353 | 117 | 0.00605 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8532 |  | 2006-07-13 08:12 | 2006-07-13 | 2006-07-13 10:34 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 142 | 12 | 19353 | 1712 | 0.08846 | 0.00062006 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8533 |  | 2006-07-13 08:29 | 2006-07-13 | 2006-07-13 11:08 | Calculated | O410E | C170 |  |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 17 | 19353 | 2703 | 0.13967 | 0.00087842 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8535 |  | 2006-07-13 09:29 | 2006-07-13 | 2006-07-13 10:48 | Calculated | O410E | LF | Pole Mounted |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Transformers : Tank | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 2 | 19353 | 158 | 0.00816 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8536 |  | 2006-07-13 09:31 | 2006-07-13 | 2006-07-13 10:04 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 33 | 16 | 19353 | 533 | 0.02754 | 0.00082675 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8537 |  | 2006-07-13 09:33 | 2006-07-13 | 2006-07-13 11:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 137 | 4 | 19353 | 551 | 0.02847 | 0.00020669 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8538 |  | 2006-07-13 10:33 | 2006-07-13 | 2006-07-13 12:39 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 126 | 21 | 19353 | 2646 | 0.13672 | 0.0010851 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8539 |  | 2006-07-13 11:08 | 2006-07-13 | 2006-07-13 14:48 | Calculated | O410E | L688 | ABS |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 220 | 255 | 19353 | 56219 | 2.9049 | 0.013176 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8540 |  | 2006-07-13 12:51 | 2006-07-13 | 2006-07-13 14:25 | Calculated | O410E | C170 | Drop-Out Fuses |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Fuse Carriers | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 17 | 19353 | 1598 | 0.08257 | 0.00087842 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8542 |  | 2006-07-13 13:05 | 2006-07-13 | 2006-07-13 14:22 | Calculated | O410E | LF | Drop-Out Fuses |  | Rural 126-02 | Remote Rural F | Rural | Taharoa Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 11 | 19353 | 853 | 0.04408 | 0.00056839 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8543 |  | 2006-07-13 13:12 | 2006-07-13 | 2006-07-13 14:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 58 | 2 | 19353 | 116 | 0.00599 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8544 |  | 2006-07-13 13:12 | 2006-07-13 | 2006-07-13 14:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 58 | 2 | 19353 | 116 | 0.00599 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8545 |  | 2006-07-13 13:26 | 2006-07-13 | 2006-07-13 15:40 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 134 | 4 | 19353 | 537 | 0.02775 | 0.00020669 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8546 |  | 2006-07-13 13:30 | 2006-07-13 | 2006-07-13 15:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 138 | 1 | 19353 | 138 | 0.00713 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8547 |  | 2006-07-13 13:42 | 2006-07-13 | 2006-07-13 16:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 196 | 4 | 19353 | 786 | 0.04061 | 0.00020669 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8548 |  | 2006-07-14 10:05 | 2006-07-14 | 2006-07-14 14:23 | Calculated | O410E | LV |  |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 85 | 19353 | 21930 | 1.1332 | 0.0043921 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8549 |  | 2006-07-14 14:52 | 2006-07-14 | 2006-07-14 16:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 82 | 1 | 19353 | 82 | 0.00424 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8551 |  | 2006-07-15 22:01 | 2006-07-15 | 2006-07-15 22:54 | Calculated | O410E | C117 | Single Circuit |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 98 | 19353 | 5194 | 0.26838 | 0.0050638 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8552 |  | 2006-07-16 09:22 | 2006-07-16 | 2006-07-16 10:06 | Calculated | O410E | S522 | Single Circuit |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 33 | 19353 | 1452 | 0.07503 | 0.0017052 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8553 |  | 2006-07-16 21:36 | 2006-07-16 | 2006-07-16 21:41 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 5 | 241 | 19353 | 1205 | 0.06226 | 0.012453 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8554 |  | 2006-07-17 09:09 | 2006-07-17 | 2006-07-17 10:23 | Calculated | O410E | LF | Pole Mounted |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 1 | 19353 | 74 | 0.00382 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8556 |  | 2006-07-18 08:32 | 2006-07-18 | 2006-07-18 11:25 | Calculated | O410E | L1617 | Drop-Out Fuses |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 173 | 2 | 19353 | 346 | 0.01788 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8558 |  | 2006-07-18 13:46 | 2006-07-18 | 2006-07-18 17:09 | Calculated | O410E | LF | Pole Mounted |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 203 | 2 | 19353 | 406 | 0.02098 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8559 |  | 2006-07-18 22:05 | 2006-07-18 | 2006-07-18 22:12 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 7 | 1 | 19353 | 7 | 0.00036 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8560 |  | 2006-07-19 09:03 | 2006-07-19 | 2006-07-19 11:30 | Calculated | O410E | LF |  |  | Gravel Scoop 109-10 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 147 | 48 | 19353 | 7073 | 0.36547 | 0.0024802 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8561 |  | 2006-07-20 08:06 | 2006-07-20 | 2006-07-20 10:25 | Calculated | O410E | C1725 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 6 | 19353 | 834 | 0.04309 | 0.00031003 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8562 |  | 2006-07-20 11:37 | 2006-07-20 | 2006-07-20 13:44 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 113 | 19353 | 14351 | 0.74154 | 0.0058389 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8563 |  | 2006-07-21 11:37 | 2006-07-21 | 2006-07-21 13:35 | Calculated | O410E | C164 | Single Circuit |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 159 | 19353 | 18762 | 0.96946 | 0.0082158 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8564 |  | 2006-07-21 13:40 | 2006-07-21 | 2006-07-21 15:59 | Calculated | O410E | C429 | Single Circuit |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Jumper - Bare ACSR | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 24 | 19353 | 3336 | 0.17238 | 0.0012401 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8565 |  | 2006-07-23 16:35 | 2006-07-23 | 2006-07-23 17:14 | Calculated | O410E | L1617 | Single Circuit |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 2 | 19353 | 78 | 0.00403 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8566 |  | 2006-07-24 10:31 | 2006-07-24 | 2006-07-24 11:28 | Calculated | O410E |  |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 57 | 5 | 19353 | 285 | 0.01473 | 0.00025836 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8567 |  | 2006-07-24 10:33 | 2006-07-24 | 2006-07-24 14:15 | Calculated | O410E |  |  |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 222 | 15 | 19353 | 3330 | 0.17207 | 0.00077507 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8568 |  | 2006-07-24 10:35 | 2006-07-24 | 2006-07-24 12:12 | Calculated | O410E | LF |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 16 | 19353 | 1552 | 0.08019 | 0.00082675 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8570 |  | 2006-07-24 10:56 | 2006-07-24 | 2006-07-24 12:52 | Calculated | O410E | C1725 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 6 | 19353 | 696 | 0.03596 | 0.00031003 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8572 |  | 2006-07-25 10:34 | 2006-07-25 | 2006-07-25 14:17 | Calculated | O410E |  |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 223 | 13 | 19353 | 2899 | 0.1498 | 0.00067173 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8573 |  | 2006-07-25 11:09 | 2006-07-25 | 2006-07-25 11:39 | Calculated | O410E | LF |  |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 47 | 19353 | 1410 | 0.07286 | 0.0024286 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8574 |  | 2006-07-25 14:40 | 2006-07-25 | 2006-07-25 16:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 1 | 19353 | 88 | 0.00455 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
3985 |  | 2006-07-27 | 2006-07-27 | 2006-07-27 00:12 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 12 | 12 | 19353 | 144 | 0.00744 | 0.00062006 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8579 |  | 2006-07-28 00:38 | 2006-07-28 | 2006-07-28 02:47 | Calculated | O410E | C990 | Paper/Lead - Laid Direct |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation | Cables : Cable Box - Dry (Raychem) | Asset Related | Other |  | Condensation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 129 | 8 | 19353 | 1032 | 0.05333 | 0.00041337 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8582 |  | 2006-07-28 14:20 | 2006-07-28 | 2006-07-28 15:32 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 72 | 2 | 19353 | 144 | 0.00744 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8583 |  | 2006-07-30 23:31 | 2006-07-30 | 2006-07-30 23:42 | Calculated | O410E | C180 & 6143 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 2 | 19353 | 22 | 0.00114 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8584 |  | 2006-07-31 09:38 | 2006-07-31 | 2006-07-31 15:07 | Calculated | O410E | LF | Pole Mounted |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Transformers : Internal Connections | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 329 | 1 | 19353 | 329 | 0.017 | 5.1672e-05 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8586 |  | 2006-07-31 10:16 | 2006-07-31 | 2006-07-31 11:39 | Calculated | O410E | LF |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 2 | 19353 | 166 | 0.00858 | 0.00010334 | 0 | 0 | 2006/2007 | July-2006 | 7 | 2006
8591 |  | 2006-08-01 13:31 | 2006-08-01 | 2006-08-01 15:20 | Calculated | O410E | LF |  |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 109 | 1 | 19353 | 109 | 0.00563 | 5.1672e-05 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8593 |  | 2006-08-02 10:37 | 2006-08-02 | 2006-08-02 12:29 | Calculated | O410E |  |  |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 4 | 19353 | 448 | 0.02315 | 0.00020669 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8594 |  | 2006-08-03 08:13 | 2006-08-03 | 2006-08-03 10:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 1 | 19353 | 127 | 0.00656 | 5.1672e-05 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8595 |  | 2006-08-04 01:29 | 2006-08-04 | 2006-08-04 01:39 | Calculated | O410E | C180 & 6143 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 4 | 19353 | 40 | 0.00207 | 0.00020669 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8596 |  | 2006-08-04 10:19 | 2006-08-04 | 2006-08-04 12:35 | Calculated | O410E | LF |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 136 | 1 | 19353 | 136 | 0.00703 | 5.1672e-05 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8597 |  | 2006-08-04 10:33 | 2006-08-04 | 2006-08-04 14:49 | Calculated | O410E |  |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 256 | 87 | 19353 | 22272 | 1.1508 | 0.0044954 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8598 |  | 2006-08-05 07:46 | 2006-08-05 | 2006-08-05 07:47 | Calculated | O410E | S589-559-631 | 11kv Under 33kv |  | Gravel Scoop 109-10 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2006/2007 | August-2006 | 8 | 2006
8599 |  | 2006-08-05 09:36 | 2006-08-05 | 2006-08-05 09:44 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 3 | 19353 | 24 | 0.00124 | 0.00015501 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8600 |  | 2006-08-06 07:08 | 2006-08-06 | 2006-08-06 10:53 | Calculated | O410E | C440 |  |  | Southern 409-09 | Remote Rural F | Southern | Manunui Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 225 | 24 | 19353 | 5400 | 0.27903 | 0.0012401 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8602 |  | 2006-08-06 21:16 | 2006-08-06 | 2006-08-06 21:24 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 3 | 19353 | 24 | 0.00124 | 0.00015501 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8603 |  | 2006-08-07 04:21 | 2006-08-07 | 2006-08-07 06:51 | Calculated | O410E | C368 | Single Circuit |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 18 | 19353 | 2700 | 0.13951 | 0.00093009 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8604 |  | 2006-08-07 09:00 | 2006-08-07 | 2006-08-07 09:40 | Calculated | O410E | L249 | Drop-Out Fuses |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 40 | 3 | 19353 | 120 | 0.0062 | 0.00015501 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8605 |  | 2006-08-07 09:06 | 2006-08-07 | 2006-08-07 12:43 | Calculated | O410E | LV |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 16 | 19353 | 3472 | 0.1794 | 0.00082675 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8606 |  | 2006-08-07 09:16 | 2006-08-07 | 2006-08-07 10:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 71 | 1 | 19353 | 71 | 0.00367 | 5.1672e-05 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8607 |  | 2006-08-08 07:05 | 2006-08-08 | 2006-08-08 08:21 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 76 | 2 | 19353 | 152 | 0.00785 | 0.00010334 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8608 |  | 2006-08-08 08:10 | 2006-08-08 | 2006-08-08 09:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 1 | 19353 | 96 | 0.00496 | 5.1672e-05 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8609 |  | 2006-08-08 09:28 | 2006-08-08 | 2006-08-08 10:08 | Calculated | O410E | S522 | Single Circuit |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 33 | 19353 | 1320 | 0.06821 | 0.0017052 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8612 |  | 2006-08-09 10:18 | 2006-08-09 | 2006-08-09 11:22 | Calculated | O410E | LF |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 64 | 5 | 19353 | 320 | 0.01653 | 0.00025836 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8611 |  | 2006-08-09 10:30 | 2006-08-09 | 2006-08-09 12:01 | Calculated | O410E |  |  |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 31 | 19353 | 2821 | 0.14577 | 0.0016018 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8613 |  | 2006-08-09 16:15 | 2006-08-09 | 2006-08-09 16:42 | Calculated | O410E | LF | Drop-Out Fuses |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 27 | 7 | 19353 | 189 | 0.00977 | 0.0003617 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8614 |  | 2006-08-10 09:00 | 2006-08-10 | 2006-08-10 16:00 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 420 | 10 | 19353 | 4200 | 0.21702 | 0.00051672 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8615 |  | 2006-08-10 09:30 | 2006-08-10 | 2006-08-10 14:30 | Calculated | O410E |  |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 300 | 2 | 19353 | 600 | 0.031 | 0.00010334 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8616 |  | 2006-08-10 10:02 | 2006-08-10 | 2006-08-10 10:32 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 22 | 19353 | 660 | 0.0341 | 0.0011368 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8617 |  | 2006-08-10 10:33 | 2006-08-10 | 2006-08-10 15:19 | Calculated | O410E | LF |  |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 286 | 8 | 19353 | 2288 | 0.11822 | 0.00041337 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8618 |  | 2006-08-10 13:30 | 2006-08-10 | 2006-08-10 14:40 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 70 | 1 | 19353 | 70 | 0.00362 | 5.1672e-05 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8619 |  | 2006-08-11 09:00 | 2006-08-11 | 2006-08-11 15:51 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 411 | 10 | 19353 | 4110 | 0.21237 | 0.00051672 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8620 |  | 2006-08-11 10:00 | 2006-08-11 | 2006-08-11 13:40 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 220 | 20 | 19353 | 4400 | 0.22735 | 0.0010334 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8621 |  | 2006-08-11 10:00 | 2006-08-11 | 2006-08-11 11:45 | Calculated | O410E | LF |  |  | McDonalds 110-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 105 | 1 | 19353 | 105 | 0.00543 | 5.1672e-05 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8623 |  | 2006-08-13 11:35 | 2006-08-13 | 2006-08-13 15:20 | Calculated | O410E | C820 | Single Circuit |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 225 | 174 | 19353 | 39150 | 2.0229 | 0.0089909 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8624 |  | 2006-08-14 07:56 | 2006-08-14 | 2006-08-14 07:57 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 241 | 19353 | 241 | 0.01245 | 0.012453 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8625 |  | 2006-08-14 09:04 | 2006-08-14 | 2006-08-14 15:50 | Calculated | O410E | LF |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 406 | 18 | 19353 | 7308 | 0.37762 | 0.00093009 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8626 |  | 2006-08-14 15:45 | 2006-08-14 | 2006-08-14 17:10 | Calculated | O410E | LF |  |  | Caves 101-07 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 2 | 19353 | 170 | 0.00878 | 0.00010334 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8627 |  | 2006-08-15 05:58 | 2006-08-15 | 2006-08-15 09:16 | Calculated | O410E | L442 | Drop-Out Fuses |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 198 | 16 | 19353 | 3168 | 0.1637 | 0.00082675 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8628 |  | 2006-08-15 09:25 | 2006-08-15 | 2006-08-15 11:09 | Calculated | O410E | L1736 | Drop-Out Fuses |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 104 | 9 | 19353 | 936 | 0.04836 | 0.00046504 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8629 |  | 2006-08-15 10:01 | 2006-08-15 | 2006-08-15 14:03 | Calculated | O410E |  |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 242 | 38 | 19353 | 9221 | 0.47646 | 0.0019635 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8631 |  | 2006-08-16 10:30 | 2006-08-16 | 2006-08-16 14:25 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 235 | 16 | 19353 | 3760 | 0.19429 | 0.00082675 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8632 |  | 2006-08-16 10:38 | 2006-08-16 | 2006-08-16 11:05 | Calculated | O410E | LF |  |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 27 | 1 | 19353 | 27 | 0.0014 | 5.1672e-05 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8633 |  | 2006-08-16 15:12 | 2006-08-16 | 2006-08-16 15:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 27 | 36 | 19353 | 975 | 0.05038 | 0.0018602 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8634 |  | 2006-08-17 10:31 | 2006-08-17 | 2006-08-17 13:52 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 201 | 12 | 19353 | 2412 | 0.12463 | 0.00062006 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8635 |  | 2006-08-17 12:47 | 2006-08-17 | 2006-08-17 14:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 2 | 19353 | 176 | 0.00909 | 0.00010334 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8636 |  | 2006-08-17 16:06 | 2006-08-17 | 2006-08-17 16:39 | Calculated | O410E | LF | Pole Mounted |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 62 | 19353 | 2105 | 0.10877 | 0.0032036 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8640 |  | 2006-08-19 02:07 | 2006-08-19 | 2006-08-19 02:24 | Calculated | O410E | C104 |  |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 602 | 19353 | 10424 | 0.53862 | 0.031106 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8641 |  | 2006-08-19 08:12 | 2006-08-19 | 2006-08-19 09:32 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-03 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 80 | 1 | 19353 | 80 | 0.00413 | 5.1672e-05 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8642 |  | 2006-08-19 20:03 | 2006-08-19 | 2006-08-19 21:32 | Calculated | O410E | L693 | Drop-Out Fuses |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Fuse Carriers | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 89 | 19 | 19353 | 1691 | 0.08738 | 0.00098176 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8645 |  | 2006-08-22 12:35 | 2006-08-22 | 2006-08-22 14:14 | Calculated | O410E | L6003 | Drop-Out Fuses |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 26 | 19353 | 2574 | 0.133 | 0.0013435 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8647 |  | 2006-08-22 17:58 | 2006-08-22 | 2006-08-22 23:34 | Calculated | O410E | L468 | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 336 | 15 | 19353 | 5040 | 0.26042 | 0.00077507 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8648 |  | 2006-08-23 09:32 | 2006-08-23 | 2006-08-23 09:42 | Calculated | O410E | LF |  |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 10 | 41 | 19353 | 410 | 0.02119 | 0.0021185 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8652 |  | 2006-08-27 09:09 | 2006-08-27 | 2006-08-27 14:05 | Calculated | O410E | LF |  |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 296 | 4 | 19353 | 1184 | 0.06118 | 0.00020669 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8655 |  | 2006-08-29 14:12 | 2006-08-29 | 2006-08-29 15:55 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Fuse Carriers | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 103 | 3 | 19353 | 309 | 0.01597 | 0.00015501 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8656 |  | 2006-08-29 23:57 | 2006-08-29 | 2006-08-30 00:01 | Calculated | O410E | C1102 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 1940 | 19353 | 7760 | 0.40097 | 0.10024 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8657 |  | 2006-08-30 09:30 | 2006-08-30 | 2006-08-30 16:22 | Calculated | O410E |  |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 412 | 3 | 19353 | 1236 | 0.06387 | 0.00015501 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8658 |  | 2006-08-30 11:00 | 2006-08-30 | 2006-08-30 12:03 | Calculated | O410E | LV |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 76 | 19353 | 4788 | 0.2474 | 0.003927 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8660 |  | 2006-08-30 14:39 | 2006-08-30 | 2006-08-30 15:15 | Calculated | O410E | LF |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 3 | 19353 | 108 | 0.00558 | 0.00015501 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8661 |  | 2006-08-31 09:15 | 2006-08-31 | 2006-08-31 14:20 | Calculated | O410E | L490 | Drop-Out Fuses |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 305 | 5 | 19353 | 1525 | 0.0788 | 0.00025836 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8662 |  | 2006-08-31 09:17 | 2006-08-31 | 2006-08-31 14:28 | Calculated | O410E | LF |  |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 311 | 5 | 19353 | 1555 | 0.08035 | 0.00025836 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8663 |  | 2006-08-31 09:30 | 2006-08-31 | 2006-08-31 15:26 | Calculated | O410E |  |  |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 2 | 19353 | 712 | 0.03679 | 0.00010334 | 0 | 0 | 2006/2007 | August-2006 | 8 | 2006
8666 |  | 2006-09-01 04:35 | 2006-09-01 | 2006-09-01 07:55 | Calculated | O410E | C1620 | Single Circuit |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Wraplock Deadend | Asset Related | Insulator |  | Insulator - Salt - Pollution Tracking | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 200 | 176 | 19353 | 35364 | 1.8273 | 0.0090942 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8668 |  | 2006-09-01 09:30 | 2006-09-01 | 2006-09-01 14:59 | Calculated | O410E |  |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 329 | 23 | 19353 | 7567 | 0.391 | 0.0011884 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8669 |  | 2006-09-01 09:33 | 2006-09-01 | 2006-09-01 13:19 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 226 | 21 | 19353 | 4746 | 0.24523 | 0.0010851 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8671 |  | 2006-09-01 10:30 | 2006-09-01 | 2006-09-01 13:08 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 158 | 2 | 19353 | 316 | 0.01633 | 0.00010334 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8672 |  | 2006-09-01 11:20 | 2006-09-01 | 2006-09-01 12:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 2 | 19353 | 154 | 0.00796 | 0.00010334 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8673 |  | 2006-09-01 15:55 | 2006-09-01 | 2006-09-01 16:27 | Calculated | O410E | LF |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 4 | 19353 | 128 | 0.00661 | 0.00020669 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8674 |  | 2006-09-02 19:45 | 2006-09-02 | 2006-09-02 20:46 | Calculated | O410E | S692 | Drop-Out Fuses |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 61 | 102 | 19353 | 6222 | 0.3215 | 0.0052705 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8675 |  | 2006-09-03 09:00 | 2006-09-03 | 2006-09-03 11:00 | Calculated | O410E | LV |  |  | Hakiaha 401-01 | Remote Rural F | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 19 | 19353 | 2280 | 0.11781 | 0.00098176 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8677 |  | 2006-09-04 09:56 | 2006-09-04 | 2006-09-04 12:15 | Calculated | O410E |  |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 86 | 19353 | 11954 | 0.61768 | 0.0044438 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8678 |  | 2006-09-04 10:04 | 2006-09-04 | 2006-09-04 12:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 130 | 1 | 19353 | 130 | 0.00672 | 5.1672e-05 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8680 |  | 2006-09-05 09:00 | 2006-09-05 | 2006-09-05 13:19 | Calculated | O410E |  |  |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 259 | 36 | 19353 | 9324 | 0.48179 | 0.0018602 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8681 |  | 2006-09-05 10:15 | 2006-09-05 | 2006-09-05 10:22 | Calculated | O410E |  |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 7 | 86 | 19353 | 602 | 0.03111 | 0.0044438 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8682 |  | 2006-09-06 09:30 | 2006-09-06 | 2006-09-06 13:55 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 265 | 17 | 19353 | 4505 | 0.23278 | 0.00087842 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8683 |  | 2006-09-06 09:49 | 2006-09-06 | 2006-09-06 12:01 | Calculated | O410E | LF |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 132 | 1 | 19353 | 132 | 0.00682 | 5.1672e-05 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8684 |  | 2006-09-06 10:30 | 2006-09-06 | 2006-09-06 14:20 | Calculated | O410E |  |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 230 | 80 | 19353 | 18400 | 0.95076 | 0.0041337 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8685 |  | 2006-09-07 09:00 | 2006-09-07 | 2006-09-07 15:16 | Calculated | O410E |  |  |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 376 | 20 | 19353 | 7520 | 0.38857 | 0.0010334 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8686 |  | 2006-09-08 04:15 | 2006-09-08 | 2006-09-08 04:23 | Calculated | O410E | C104 | Single Circuit |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 602 | 19353 | 4816 | 0.24885 | 0.031106 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8687 |  | 2006-09-09 08:41 | 2006-09-09 | 2006-09-09 08:51 | Calculated | O410E | C880 |  |  | Hakiaha 401-01 | Remote Rural F | Hakiaha | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 237 | 19353 | 2370 | 0.12246 | 0.012246 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8688 |  | 2006-09-09 10:17 | 2006-09-09 | 2006-09-09 12:01 | Calculated | O410E | L1736 | Drop-Out Fuses |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 104 | 9 | 19353 | 936 | 0.04836 | 0.00046504 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8689 |  | 2006-09-10 11:51 | 2006-09-10 | 2006-09-10 12:24 | Calculated | O410E | C116 | Single Circuit |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Pole - Softwood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 95 | 19353 | 3142 | 0.16235 | 0.0049088 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8691 |  | 2006-09-11 12:11 | 2006-09-11 | 2006-09-11 12:53 | Calculated | O410E | LF |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 2 | 19353 | 84 | 0.00434 | 0.00010334 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8692 |  | 2006-09-13 09:31 | 2006-09-13 | 2006-09-13 10:22 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 130 | 19353 | 6649 | 0.34356 | 0.0067173 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8693 |  | 2006-09-13 10:04 | 2006-09-13 | 2006-09-13 13:09 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 185 | 10 | 19353 | 1850 | 0.09559 | 0.00051672 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8694 |  | 2006-09-14 08:55 | 2006-09-14 | 2006-09-14 14:05 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 310 | 3 | 19353 | 930 | 0.04805 | 0.00015501 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8695 |  | 2006-09-14 09:07 | 2006-09-14 | 2006-09-14 16:21 | Calculated | O410E |  |  |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 434 | 24 | 19353 | 10416 | 0.53821 | 0.0012401 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8696 |  | 2006-09-14 09:33 | 2006-09-14 | 2006-09-14 12:44 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 191 | 62 | 19353 | 11857 | 0.61267 | 0.0032036 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8697 |  | 2006-09-14 10:34 | 2006-09-14 | 2006-09-14 12:21 | Calculated | O410E |  |  |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 107 | 5 | 19353 | 535 | 0.02764 | 0.00025836 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8698 |  | 2006-09-14 10:57 | 2006-09-14 | 2006-09-14 12:31 | Calculated | O410E | C262 |  |  | Nihoniho 412-02 | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 27 | 19353 | 2561 | 0.13233 | 0.0013951 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8699 |  | 2006-09-15 07:40 | 2006-09-15 | 2006-09-15 08:31 | Calculated | O410E | C1020 | Drop-Out Fuses |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 51 | 6 | 19353 | 306 | 0.01581 | 0.00031003 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8700 |  | 2006-09-15 09:05 | 2006-09-15 | 2006-09-15 11:33 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 3 | 19353 | 444 | 0.02294 | 0.00015501 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8701 |  | 2006-09-15 09:32 | 2006-09-15 | 2006-09-15 12:01 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 62 | 19353 | 9255 | 0.47822 | 0.0032036 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8702 |  | 2006-09-15 14:03 | 2006-09-15 | 2006-09-15 15:21 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-07 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 78 | 2 | 19353 | 156 | 0.00806 | 0.00010334 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8703 |  | 2006-09-16 17:31 | 2006-09-16 | 2006-09-16 18:29 | Calculated | O410E | LF | Pole Mounted |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Accidental Contact, Damage or Interference by TLC Staff | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 6 | 19353 | 348 | 0.01798 | 0.00031003 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8704 |  | 2006-09-17 19:41 | 2006-09-17 | 2006-09-17 20:34 | Calculated | O410E | C927 | Drop-Out Fuses |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 53 | 321 | 19353 | 17013 | 0.87909 | 0.016587 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8707 |  | 2006-09-19 11:45 | 2006-09-19 | 2006-09-19 13:21 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 3 | 19353 | 288 | 0.01488 | 0.00015501 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8708 |  | 2006-09-19 14:45 | 2006-09-19 | 2006-09-19 16:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 79 | 1 | 19353 | 79 | 0.00408 | 5.1672e-05 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8709 |  | 2006-09-20 02:51 | 2006-09-20 | 2006-09-20 06:18 | Calculated | O410E | C547 | Pole Mounted |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | Transformers : Internal Connections | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 207 | 183 | 19353 | 38003 | 1.9637 | 0.0094559 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8710 |  | 2006-09-20 06:28 | 2006-09-20 | 2006-09-20 06:57 | Calculated | O410E | S724 | Drop-Out Fuses |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 29 | 86 | 19353 | 2494 | 0.12887 | 0.0044438 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8712 |  | 2006-09-20 19:45 | 2006-09-20 | 2006-09-20 22:30 | Calculated | O410E | LF |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 6 | 19353 | 990 | 0.05115 | 0.00031003 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8713 |  | 2006-09-21 07:03 | 2006-09-21 | 2006-09-21 08:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 2 | 19353 | 186 | 0.00961 | 0.00010334 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8714 |  | 2006-09-21 09:00 | 2006-09-21 | 2006-09-21 17:22 | Calculated | O410E |  |  |  |  | Remote Rural F | Lake Taupo 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 502 | 599 | 19353 | 299500 | 15.4756 | 0.030951 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8715 |  | 2006-09-21 09:09 | 2006-09-21 | 2006-09-21 14:38 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 329 | 9 | 19353 | 2961 | 0.153 | 0.00046504 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8717 |  | 2006-09-21 10:04 | 2006-09-21 | 2006-09-21 15:30 | Calculated | O410E |  |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 326 | 29 | 19353 | 9454 | 0.4885 | 0.0014985 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8719 |  | 2006-09-21 21:41 | 2006-09-21 | 2006-09-21 23:04 | Calculated | O410E | C467 |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 50 | 19353 | 4150 | 0.21444 | 0.0025836 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8721 |  | 2006-09-22 10:22 | 2006-09-22 | 2006-09-22 11:47 | Calculated | O410E | LF | Pole Mounted |  | Mahoenui 113-07 | Remote Rural F | Mahoenui | Wairere Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 2 | 19353 | 170 | 0.00878 | 0.00010334 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8722 |  | 2006-09-22 12:04 | 2006-09-22 | 2006-09-22 13:30 | Calculated | O410E | LF | Pole Mounted |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Transformers : External Bushings | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 6 | 19353 | 516 | 0.02666 | 0.00031003 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8724 |  | 2006-09-25 10:36 | 2006-09-25 | 2006-09-25 13:46 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 15 | 19353 | 2850 | 0.14726 | 0.00077507 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8728 |  | 2006-09-26 09:06 | 2006-09-26 | 2006-09-26 14:44 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 338 | 12 | 19353 | 4056 | 0.20958 | 0.00062006 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8729 |  | 2006-09-26 09:34 | 2006-09-26 | 2006-09-26 11:03 | Calculated | O410E |  |  |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 89 | 89 | 19353 | 7978 | 0.41224 | 0.0045988 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8732 |  | 2006-09-27 09:30 | 2006-09-27 | 2006-09-27 10:15 | Calculated | O410E | LF |  |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 3 | 19353 | 135 | 0.00698 | 0.00015501 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8733 |  | 2006-09-27 09:50 | 2006-09-27 | 2006-09-27 11:19 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 89 | 1 | 19353 | 89 | 0.0046 | 5.1672e-05 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8734 |  | 2006-09-27 13:17 | 2006-09-27 | 2006-09-27 14:34 | Calculated | O410E | LF |  |  | McDonalds 110-02 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 77 | 10 | 19353 | 770 | 0.03979 | 0.00051672 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8735 |  | 2006-09-27 19:20 | 2006-09-27 | 2006-09-27 21:06 | Calculated | O410E | L693 | Single Circuit |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 19 | 19353 | 2014 | 0.10407 | 0.00098176 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8736 |  | 2006-09-28 09:04 | 2006-09-28 | 2006-09-28 13:06 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 242 | 9 | 19353 | 2178 | 0.11254 | 0.00046504 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8737 |  | 2006-09-28 09:11 | 2006-09-28 | 2006-09-28 15:08 | Calculated | O410E |  |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 357 | 52 | 19353 | 18564 | 0.95923 | 0.0026869 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8738 |  | 2006-09-28 10:34 | 2006-09-28 | 2006-09-28 14:08 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 214 | 10 | 19353 | 2140 | 0.11058 | 0.00051672 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8740 |  | 2006-09-29 10:31 | 2006-09-29 | 2006-09-29 13:33 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 182 | 21 | 19353 | 3822 | 0.19749 | 0.0010851 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8741 |  | 2006-09-29 10:40 | 2006-09-29 | 2006-09-29 11:55 | Calculated | O410E |  |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 75 | 85 | 19353 | 6375 | 0.32941 | 0.0043921 | 0 | 0 | 2006/2007 | September-2006 | 9 | 2006
8742 |  | 2006-10-01 09:32 | 2006-10-01 | 2006-10-01 12:40 | Calculated | O410E |  |  |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 188 | 39 | 19353 | 7332 | 0.37886 | 0.0020152 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8745 |  | 2006-10-02 11:16 | 2006-10-02 | 2006-10-02 16:36 | Calculated | O410E | LF |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 320 | 4 | 19353 | 1280 | 0.06614 | 0.00020669 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8746 |  | 2006-10-02 12:49 | 2006-10-02 | 2006-10-02 12:59 | Calculated | O410E | C512 | Single Circuit |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 835 | 19353 | 8586 | 0.44365 | 0.043146 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8747 |  | 2006-10-02 13:49 | 2006-10-02 | 2006-10-02 14:03 | Calculated | O410E | C1616 | Single Circuit |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 15 | 19353 | 210 | 0.01085 | 0.00077507 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8748 |  | 2006-10-02 16:10 | 2006-10-02 | 2006-10-02 17:52 | Calculated | O410E | LF | Pole Mounted |  | Southern 409-03 | Remote Rural F | Southern | Manunui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 5 | 19353 | 510 | 0.02635 | 0.00025836 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8749 |  | 2006-10-03 05:16 | 2006-10-03 | 2006-10-03 06:58 | Calculated | O410E | C1636 | Single Circuit |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Spark Gaps | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 11 | 19353 | 1122 | 0.05798 | 0.00056839 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8750 |  | 2006-10-03 09:04 | 2006-10-03 | 2006-10-03 14:24 | Calculated | O410E | LV |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 320 | 76 | 19353 | 24320 | 1.2567 | 0.003927 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8751 |  | 2006-10-03 09:05 | 2006-10-03 | 2006-10-03 14:50 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 345 | 12 | 19353 | 4140 | 0.21392 | 0.00062006 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8753 |  | 2006-10-03 13:40 | 2006-10-03 | 2006-10-03 14:40 | Calculated | O410E | L1529 | Drop-Out Fuses |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 60 | 2 | 19353 | 120 | 0.0062 | 0.00010334 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8754 |  | 2006-10-04 09:39 | 2006-10-04 | 2006-10-04 09:45 | Calculated | O410E |  |  |  | Mokauiti 115-05 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 6 | 14 | 19353 | 84 | 0.00434 | 0.0007234 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8755 |  | 2006-10-04 09:47 | 2006-10-04 | 2006-10-04 10:33 | Calculated | O410E | LF |  |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 4 | 19353 | 184 | 0.00951 | 0.00020669 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8756 |  | 2006-10-04 10:04 | 2006-10-04 | 2006-10-04 13:50 | Calculated | O410E | LF |  |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 226 | 48 | 19353 | 10848 | 0.56053 | 0.0024802 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8757 |  | 2006-10-04 10:43 | 2006-10-04 | 2006-10-04 12:00 | Calculated | O410E | S583 | Drop-Out Fuses |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 77 | 121 | 19353 | 9317 | 0.48142 | 0.0062523 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8758 |  | 2006-10-04 13:59 | 2006-10-04 | 2006-10-04 15:39 | Calculated | O410E | S290 | Single Circuit |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 7 | 19353 | 700 | 0.03617 | 0.0003617 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8760 |  | 2006-10-05 09:03 | 2006-10-05 | 2006-10-05 13:55 | Calculated | O410E | LV |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 24 | 19353 | 7008 | 0.36211 | 0.0012401 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8759 |  | 2006-10-05 09:05 | 2006-10-05 | 2006-10-05 14:53 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 348 | 21 | 19353 | 7308 | 0.37762 | 0.0010851 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8761 |  | 2006-10-05 09:30 | 2006-10-05 | 2006-10-05 11:04 | Calculated | O410E |  | Sectionaliser |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Mechanism | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 94 | 30 | 19353 | 2823 | 0.14587 | 0.0015501 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8762 |  | 2006-10-05 11:00 | 2006-10-05 | 2006-10-05 15:13 | Calculated | O410E | C1724 & 1725 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 253 | 13 | 19353 | 3297 | 0.17036 | 0.00067173 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8763 |  | 2006-10-06 09:01 | 2006-10-06 | 2006-10-06 10:46 | Calculated | O410E | L1519 | Drop-Out Fuses |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 105 | 14 | 19353 | 1470 | 0.07596 | 0.0007234 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8764 |  | 2006-10-06 09:24 | 2006-10-06 | 2006-10-06 12:33 | Calculated | O410E | LV |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 189 | 64 | 19353 | 12096 | 0.62502 | 0.003307 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8765 |  | 2006-10-06 10:31 | 2006-10-06 | 2006-10-06 13:49 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 198 | 6 | 19353 | 1188 | 0.06139 | 0.00031003 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8766 |  | 2006-10-06 10:32 | 2006-10-06 | 2006-10-06 15:12 | Calculated | O410E |  |  |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 280 | 6 | 19353 | 1680 | 0.08681 | 0.00031003 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8767 |  | 2006-10-07 08:18 | 2006-10-07 | 2006-10-07 09:16 | Calculated | O410E | L1542 | Single Circuit |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 3 | 19353 | 174 | 0.00899 | 0.00015501 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8768 |  | 2006-10-07 09:00 | 2006-10-07 | 2006-10-07 10:11 | Calculated | O410E | RTE 5101 |  |  | Tokaanu 420-01 | Remote Rural F | Tokaanu | Tokaanu Village Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 30 | 19353 | 2130 | 0.11006 | 0.0015501 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8769 |  | 2006-10-07 14:51 | 2006-10-07 | 2006-10-07 15:25 | Calculated | O410E | L292 | Drop-Out Fuses |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 34 | 5 | 19353 | 170 | 0.00878 | 0.00025836 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8771 |  | 2006-10-09 10:33 | 2006-10-09 | 2006-10-09 12:42 | Calculated | O410E |  |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 129 | 33 | 19353 | 4257 | 0.21997 | 0.0017052 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8772 |  | 2006-10-09 11:35 | 2006-10-09 | 2006-10-09 11:36 | Calculated | O410E | C1102 | Drop-Out Fuses |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 1 | 1942 | 19353 | 2006 | 0.10365 | 0.10035 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8773 |  | 2006-10-09 15:00 | 2006-10-09 | 2006-10-09 19:30 | Calculated | O410E | C378 | Single Circuit |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 37 | 19353 | 10014 | 0.51744 | 0.0019118 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8774 |  | 2006-10-10 06:25 | 2006-10-10 | 2006-10-10 11:57 | Calculated | O410E | C1519 | Single Circuit |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 332 | 14 | 19353 | 4660 | 0.24079 | 0.0007234 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8775 |  | 2006-10-10 08:46 | 2006-10-10 | 2006-10-10 12:30 | Calculated | O410E | LF | Pole Mounted |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 224 | 28 | 19353 | 6274 | 0.32419 | 0.0014468 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8776 |  | 2006-10-10 09:04 | 2006-10-10 | 2006-10-10 11:17 | Calculated | O410E | L250 | Drop-Out Fuses |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 133 | 21 | 19353 | 2793 | 0.14432 | 0.0010851 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8777 |  | 2006-10-10 09:43 | 2006-10-10 | 2006-10-10 10:43 | Calculated | O410E | C961 | Single Circuit |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 108 | 19353 | 6496 | 0.33566 | 0.0055805 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8778 |  | 2006-10-10 10:02 | 2006-10-10 | 2006-10-10 10:52 | Calculated | O410E | C683 |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 350 | 19353 | 17686 | 0.91386 | 0.018085 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8779 |  | 2006-10-10 10:41 | 2006-10-10 | 2006-10-10 12:13 | Calculated | O410E | C687 | ABS |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 162 | 19353 | 14928 | 0.77135 | 0.0083708 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8783 |  | 2006-10-10 12:42 | 2006-10-10 | 2006-10-10 14:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 111 | 26 | 19353 | 2886 | 0.14912 | 0.0013435 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8784 |  | 2006-10-10 14:02 | 2006-10-10 | 2006-10-10 15:35 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 30 | 19353 | 2790 | 0.14416 | 0.0015501 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8786 |  | 2006-10-10 14:02 | 2006-10-10 | 2006-10-10 16:09 | Calculated | O410E | C1724 | Single Circuit |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Surge Diverters | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 13 | 19353 | 1657 | 0.08562 | 0.00067173 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8787 |  | 2006-10-10 14:27 | 2006-10-10 | 2006-10-10 16:51 | Calculated | O410E | L693 | Drop-Out Fuses |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 144 | 19 | 19353 | 2736 | 0.14137 | 0.00098176 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8788 |  | 2006-10-11 01:40 | 2006-10-11 | 2006-10-11 04:34 | Calculated | O410E | C164 | Single Circuit |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Surge Diverters | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 174 | 159 | 19353 | 27811 | 1.437 | 0.0082158 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8789 |  | 2006-10-11 08:32 | 2006-10-11 | 2006-10-11 10:17 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 105 | 1 | 19353 | 105 | 0.00543 | 5.1672e-05 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8791 |  | 2006-10-12 09:38 | 2006-10-12 | 2006-10-12 10:20 | Calculated | O410E | LF |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 10 | 19353 | 427 | 0.02206 | 0.00051672 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8792 |  | 2006-10-12 10:03 | 2006-10-12 | 2006-10-12 10:04 | Calculated | O410E | C222 & 570 |  |  |  | Remote Rural F | Te Waireka Rd 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2006/2007 | October-2006 | 10 | 2006
8793 |  | 2006-10-12 10:48 | 2006-10-12 | 2006-10-12 12:07 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 79 | 43 | 19353 | 3414 | 0.17641 | 0.0022219 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8794 |  | 2006-10-12 12:10 | 2006-10-12 | 2006-10-12 13:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 98 | 1 | 19353 | 98 | 0.00506 | 5.1672e-05 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8795 |  | 2006-10-12 23:42 | 2006-10-12 | 2006-10-13 00:45 | Calculated | O410E | LF |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 27 | 19353 | 1701 | 0.08789 | 0.0013951 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8797 |  | 2006-10-13 10:23 | 2006-10-13 | 2006-10-13 12:48 | Calculated | O410E |  |  |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 145 | 24 | 19353 | 3480 | 0.17982 | 0.0012401 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8800 |  | 2006-10-15 02:37 | 2006-10-15 | 2006-10-15 02:47 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 3 | 19353 | 30 | 0.00155 | 0.00015501 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8802 |  | 2006-10-16 08:10 | 2006-10-16 | 2006-10-16 10:05 | Calculated | O410E | L1529 | Drop-Out Fuses |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 115 | 2 | 19353 | 230 | 0.01188 | 0.00010334 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8803 |  | 2006-10-17 09:08 | 2006-10-17 | 2006-10-17 14:51 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 343 | 12 | 19353 | 4116 | 0.21268 | 0.00062006 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8804 |  | 2006-10-17 09:20 | 2006-10-17 | 2006-10-17 15:13 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 353 | 2 | 19353 | 706 | 0.03648 | 0.00010334 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8805 |  | 2006-10-17 09:51 | 2006-10-17 | 2006-10-17 11:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 81 | 48 | 19353 | 3888 | 0.2009 | 0.0024802 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8807 |  | 2006-10-18 10:06 | 2006-10-18 | 2006-10-18 10:58 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 52 | 71 | 19353 | 3709 | 0.19165 | 0.0036687 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8808 |  | 2006-10-18 10:33 | 2006-10-18 | 2006-10-18 14:34 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 241 | 15 | 19353 | 3615 | 0.18679 | 0.00077507 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8809 |  | 2006-10-19 09:20 | 2006-10-19 | 2006-10-19 14:51 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 331 | 19 | 19353 | 6289 | 0.32496 | 0.00098176 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8810 |  | 2006-10-19 09:30 | 2006-10-19 | 2006-10-19 10:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 45 | 1 | 19353 | 45 | 0.00233 | 5.1672e-05 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8811 |  | 2006-10-19 10:32 | 2006-10-19 | 2006-10-19 14:55 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 263 | 15 | 19353 | 3945 | 0.20384 | 0.00077507 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8812 |  | 2006-10-19 10:34 | 2006-10-19 | 2006-10-19 15:05 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 4 | 19353 | 1084 | 0.05601 | 0.00020669 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8814 |  | 2006-10-20 08:30 | 2006-10-20 | 2006-10-20 12:06 | Calculated | O410E | L476 | Single Circuit |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 216 | 59 | 19353 | 12767 | 0.65969 | 0.0030486 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8815 |  | 2006-10-20 10:30 | 2006-10-20 | 2006-10-20 11:35 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 65 | 15 | 19353 | 975 | 0.05038 | 0.00077507 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8816 |  | 2006-10-20 10:34 | 2006-10-20 | 2006-10-20 15:05 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 4 | 19353 | 1084 | 0.05601 | 0.00020669 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8817 |  | 2006-10-24 09:02 | 2006-10-24 | 2006-10-24 10:13 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 71 | 2 | 19353 | 142 | 0.00734 | 0.00010334 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8818 |  | 2006-10-24 09:33 | 2006-10-24 | 2006-10-24 10:27 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 8 | 19353 | 432 | 0.02232 | 0.00041337 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8819 |  | 2006-10-24 10:00 | 2006-10-24 | 2006-10-24 10:17 | Calculated | O410E |  |  |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 17 | 2 | 19353 | 34 | 0.00176 | 0.00010334 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8820 |  | 2006-10-24 18:14 | 2006-10-24 | 2006-10-24 18:21 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 7 | 2 | 19353 | 14 | 0.00072 | 0.00010334 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8821 |  | 2006-10-24 20:20 | 2006-10-24 | 2006-10-24 21:40 | Calculated | O410E | LF | Pole Mounted |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation | Transformers : Internal Connections | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 4 | 19353 | 320 | 0.01653 | 0.00020669 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8822 |  | 2006-10-25 10:39 | 2006-10-25 | 2006-10-25 14:50 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 251 | 25 | 19353 | 6275 | 0.32424 | 0.0012918 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8823 |  | 2006-10-26 09:13 | 2006-10-26 | 2006-10-26 14:34 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 21 | 19353 | 6741 | 0.34832 | 0.0010851 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8824 |  | 2006-10-26 10:06 | 2006-10-26 | 2006-10-26 11:06 | Calculated | O410E |  |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 6 | 19353 | 360 | 0.0186 | 0.00031003 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8825 |  | 2006-10-26 10:32 | 2006-10-26 | 2006-10-26 12:26 | Calculated | O410E | L733 | Drop-Out Fuses |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 114 | 1 | 19353 | 114 | 0.00589 | 5.1672e-05 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8826 |  | 2006-10-27 10:41 | 2006-10-27 | 2006-10-27 14:06 | Calculated | O410E | LF |  |  | Mahoenui 113-07 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 205 | 2 | 19353 | 410 | 0.02119 | 0.00010334 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8827 |  | 2006-10-27 13:56 | 2006-10-27 | 2006-10-27 15:01 | Calculated | O410E | LF |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 65 | 5 | 19353 | 325 | 0.01679 | 0.00025836 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8828 |  | 2006-10-27 20:02 | 2006-10-27 | 2006-10-27 21:14 | Calculated | O410E | L429 | Single Circuit |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Joint - Mechanical / Tension | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 15 | 19353 | 1080 | 0.05581 | 0.00077507 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8829 |  | 2006-10-28 07:14 | 2006-10-28 | 2006-10-28 07:16 | Calculated | O410E | C1102 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 1955 | 19353 | 3910 | 0.20204 | 0.10102 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8830 |  | 2006-10-29 13:42 | 2006-10-29 | 2006-10-29 16:25 | Calculated | O410E | L429 | Drop-Out Fuses |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 163 | 15 | 19353 | 2445 | 0.12634 | 0.00077507 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8832 |  | 2006-10-29 18:54 | 2006-10-29 | 2006-10-29 19:27 | Calculated | O410E | C2 | Single Circuit |  | Tihoi 124-00 | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 304 | 19353 | 10138 | 0.52385 | 0.015708 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8833 |  | 2006-10-29 21:14 | 2006-10-29 | 2006-10-30 00:49 | Calculated | O410E | S583 | Single Circuit |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 215 | 121 | 19353 | 26015 | 1.3442 | 0.0062523 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8834 |  | 2006-10-30 07:22 | 2006-10-30 | 2006-10-30 09:18 | Calculated | O410E | LF |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 6 | 19353 | 696 | 0.03596 | 0.00031003 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8835 |  | 2006-10-30 07:27 | 2006-10-30 | 2006-10-30 13:22 | Calculated | O410E | C1630 | Single Circuit |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 355 | 33 | 19353 | 11744 | 0.60683 | 0.0017052 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8836 |  | 2006-10-30 08:26 | 2006-10-30 | 2006-10-30 10:01 | Calculated | O410E | L427 | Drop-Out Fuses |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 24 | 19353 | 2280 | 0.11781 | 0.0012401 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8837 |  | 2006-10-30 08:37 | 2006-10-30 | 2006-10-30 10:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 129 | 1 | 19353 | 129 | 0.00667 | 5.1672e-05 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8838 |  | 2006-10-30 10:02 | 2006-10-30 | 2006-10-30 10:52 | Calculated | O410E | LF |  |  | Otorohanga 112-07 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 7 | 19353 | 350 | 0.01809 | 0.0003617 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8839 |  | 2006-10-30 10:17 | 2006-10-30 | 2006-10-30 10:22 | Calculated | O410E | C242 - 796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 5 | 241 | 19353 | 1205 | 0.06226 | 0.012453 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8840 |  | 2006-10-30 10:48 | 2006-10-30 | 2006-10-30 11:31 | Calculated | O410E | LF | Pole Mounted |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation | Transformers : Other | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 1 | 19353 | 43 | 0.00222 | 5.1672e-05 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8841 |  | 2006-10-30 11:07 | 2006-10-30 | 2006-10-30 16:02 | Calculated | O410E | C455 | Single Circuit |  | Ohura 413-07 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 295 | 15 | 19353 | 4437 | 0.22927 | 0.00077507 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8842 |  | 2006-10-31 09:33 | 2006-10-31 | 2006-10-31 14:08 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 275 | 12 | 19353 | 3300 | 0.17052 | 0.00062006 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8843 |  | 2006-10-31 09:36 | 2006-10-31 | 2006-10-31 11:10 | Calculated | O410E | LV |  |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 12 | 19353 | 1128 | 0.05829 | 0.00062006 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8844 |  | 2006-10-31 09:37 | 2006-10-31 | 2006-10-31 11:12 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 43 | 19353 | 4107 | 0.21222 | 0.0022219 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8845 |  | 2006-10-31 10:27 | 2006-10-31 | 2006-10-31 10:51 | Calculated | O410E | LF |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 1 | 19353 | 24 | 0.00124 | 5.1672e-05 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8846 |  | 2006-10-31 16:42 | 2006-10-31 | 2006-10-31 21:10 | Calculated | O410E | C378 | Single Circuit |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 268 | 37 | 19353 | 9916 | 0.51238 | 0.0019118 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8847 |  | 2006-10-31 18:20 | 2006-10-31 | 2006-10-31 18:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 26 | 11 | 19353 | 286 | 0.01478 | 0.00056839 | 0 | 0 | 2006/2007 | October-2006 | 10 | 2006
8848 |  | 2006-11-01 10:03 | 2006-11-01 | 2006-11-01 11:27 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 43 | 19353 | 3615 | 0.18679 | 0.0022219 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8849 |  | 2006-11-02 09:30 | 2006-11-02 | 2006-11-02 14:12 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 12 | 19353 | 3384 | 0.17486 | 0.00062006 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8850 |  | 2006-11-02 10:27 | 2006-11-02 | 2006-11-02 13:25 | Calculated | O410E |  |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 178 | 21 | 19353 | 3740 | 0.19325 | 0.0010851 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8851 |  | 2006-11-03 09:04 | 2006-11-03 | 2006-11-03 09:58 | Calculated | O410E | LF |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 12 | 19353 | 648 | 0.03348 | 0.00062006 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8852 |  | 2006-11-03 13:12 | 2006-11-03 | 2006-11-03 15:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Manunui 407-01 (was Affco) | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 128 | 1 | 19353 | 128 | 0.00661 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8853 |  | 2006-11-06 10:29 | 2006-11-06 | 2006-11-06 12:04 | Calculated | O410E |  |  |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 4 | 19353 | 380 | 0.01964 | 0.00020669 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8854 |  | 2006-11-06 16:03 | 2006-11-06 | 2006-11-06 17:14 | Calculated | O410E | L705 | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 71 | 6 | 19353 | 426 | 0.02201 | 0.00031003 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8857 |  | 2006-11-07 08:00 | 2006-11-07 | 2006-11-07 10:47 | Calculated | O410E | C1616 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 15 | 19353 | 2505 | 0.12944 | 0.00077507 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8855 |  | 2006-11-07 10:00 | 2006-11-07 | 2006-11-07 14:58 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 298 | 4 | 19353 | 1192 | 0.06159 | 0.00020669 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8856 |  | 2006-11-07 10:00 | 2006-11-07 | 2006-11-07 13:52 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 15 | 19353 | 3480 | 0.17982 | 0.00077507 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8858 |  | 2006-11-07 12:00 | 2006-11-07 | 2006-11-07 13:57 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 117 | 1 | 19353 | 117 | 0.00605 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8859 |  | 2006-11-08 03:13 | 2006-11-08 | 2006-11-08 03:23 | Calculated | O410E | C116 |  |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 95 | 19353 | 950 | 0.04909 | 0.0049088 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8860 |  | 2006-11-08 03:46 | 2006-11-08 | 2006-11-08 04:46 | Calculated | O410E | C212 |  |  |  | Remote Rural F | Tuhua 33 | Direct from Ongarue Supply |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 60 | 266 | 19353 | 16057 | 0.82969 | 0.013745 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8861 |  | 2006-11-08 07:00 | 2006-11-08 | 2006-11-08 08:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 1 | 19353 | 67 | 0.00346 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8863 |  | 2006-11-08 08:30 | 2006-11-08 | 2006-11-08 10:22 | Calculated | O410E | C1716 | Single Circuit |  | Mokauiti 115-04 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 23 | 19353 | 2579 | 0.13326 | 0.0011884 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8862 |  | 2006-11-08 09:00 | 2006-11-08 | 2006-11-08 15:00 | Calculated | O410E |  |  |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 24 | 19353 | 8640 | 0.44644 | 0.0012401 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8864 |  | 2006-11-08 12:00 | 2006-11-08 | 2006-11-08 13:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 86 | 2 | 19353 | 172 | 0.00889 | 0.00010334 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8865 |  | 2006-11-08 20:40 | 2006-11-08 | 2006-11-08 22:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 80 | 6 | 19353 | 480 | 0.0248 | 0.00031003 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8866 |  | 2006-11-09 08:32 | 2006-11-09 | 2006-11-09 14:55 | Calculated | O410E | C314 | Single Circuit |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 383 | 11 | 19353 | 4213 | 0.21769 | 0.00056839 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8867 |  | 2006-11-09 11:15 | 2006-11-09 | 2006-11-09 11:21 | Calculated | O410E | C242 & 262 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 6 | 241 | 19353 | 1446 | 0.07472 | 0.012453 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8868 |  | 2006-11-09 11:28 | 2006-11-09 | 2006-11-09 14:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 179 | 2 | 19353 | 358 | 0.0185 | 0.00010334 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8869 |  | 2006-11-09 14:28 | 2006-11-09 | 2006-11-09 16:37 | Calculated | O410E | L499 | Drop-Out Fuses |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 129 | 5 | 19353 | 645 | 0.03333 | 0.00025836 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8870 |  | 2006-11-10 09:03 | 2006-11-10 | 2006-11-10 12:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 215 | 4 | 19353 | 860 | 0.04444 | 0.00020669 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8871 |  | 2006-11-10 11:00 | 2006-11-10 | 2006-11-10 14:17 | Calculated | O410E | LF |  |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 197 | 4 | 19353 | 788 | 0.04072 | 0.00020669 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8872 |  | 2006-11-10 15:04 | 2006-11-10 | 2006-11-10 19:02 | Calculated | O410E | LF | Pole Mounted |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | Transformers : Internal Connections | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 238 | 2 | 19353 | 476 | 0.0246 | 0.00010334 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8873 |  | 2006-11-12 12:27 | 2006-11-12 | 2006-11-12 12:31 | Calculated | O410E | C112 |  |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 190 | 19353 | 760 | 0.03927 | 0.0098176 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8874 |  | 2006-11-13 09:49 | 2006-11-13 | 2006-11-13 14:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 298 | 1 | 19353 | 298 | 0.0154 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8875 |  | 2006-11-13 10:03 | 2006-11-13 | 2006-11-13 12:46 | Calculated | O410E | LF |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 163 | 3 | 19353 | 489 | 0.02527 | 0.00015501 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8876 |  | 2006-11-13 10:47 | 2006-11-13 | 2006-11-13 11:56 | Calculated | O410E |  |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 69 | 59 | 19353 | 4078 | 0.21072 | 0.0030486 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8878 |  | 2006-11-13 12:37 | 2006-11-13 | 2006-11-13 13:34 | Calculated | O410E | LF |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 1 | 19353 | 57 | 0.00295 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8879 |  | 2006-11-13 14:00 | 2006-11-13 | 2006-11-13 14:32 | Calculated | O410E | LF |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 2 | 19353 | 64 | 0.00331 | 0.00010334 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8881 |  | 2006-11-13 15:39 | 2006-11-13 | 2006-11-13 16:20 | Calculated | O410E | LF |  |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 2 | 19353 | 82 | 0.00424 | 0.00010334 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8882 |  | 2006-11-14 09:21 | 2006-11-14 | 2006-11-14 09:54 | Calculated | O410E | LF |  |  | Otorohanga 112-07 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 7 | 19353 | 231 | 0.01194 | 0.0003617 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8884 |  | 2006-11-15 09:01 | 2006-11-15 | 2006-11-15 10:38 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 97 | 43 | 19353 | 4197 | 0.21687 | 0.0022219 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8885 |  | 2006-11-16 08:00 | 2006-11-16 | 2006-11-16 12:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 254 | 1 | 19353 | 254 | 0.01312 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8886 |  | 2006-11-16 09:38 | 2006-11-16 | 2006-11-16 13:00 | Calculated | O410E |  |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 202 | 11 | 19353 | 2222 | 0.11481 | 0.00056839 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8887 |  | 2006-11-16 09:47 | 2006-11-16 | 2006-11-16 11:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 87 | 1 | 19353 | 87 | 0.0045 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8888 |  | 2006-11-16 10:52 | 2006-11-16 | 2006-11-16 11:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 49 | 4 | 19353 | 196 | 0.01013 | 0.00020669 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8889 |  | 2006-11-16 19:13 | 2006-11-16 | 2006-11-16 21:10 | Calculated | O410E | L509 | Drop-Out Fuses |  | Rural 126-02 | Remote Rural F | Rural | Taharoa Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 117 | 6 | 19353 | 706 | 0.03648 | 0.00031003 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8891 |  | 2006-11-17 07:47 | 2006-11-17 | 2006-11-17 07:56 | Calculated | O410E | LF |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 3 | 19353 | 27 | 0.0014 | 0.00015501 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8892 |  | 2006-11-17 08:17 | 2006-11-17 | 2006-11-17 10:46 | Calculated | O410E | C368 | Single Circuit |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 18 | 19353 | 2685 | 0.13874 | 0.00093009 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8893 |  | 2006-11-17 09:44 | 2006-11-17 | 2006-11-17 12:40 | Calculated | O410E | L649 | Paper/Lead - Laid Direct |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Cables : Cable Box - Compound Filled | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 176 | 194 | 19353 | 34302 | 1.7724 | 0.010024 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8896 |  | 2006-11-17 11:23 | 2006-11-17 | 2006-11-17 12:46 | Calculated | O410E | LF |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 83 | 1 | 19353 | 83 | 0.00429 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8897 |  | 2006-11-17 13:42 | 2006-11-17 | 2006-11-17 16:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 156 | 1 | 19353 | 156 | 0.00806 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8898 |  | 2006-11-18 10:53 | 2006-11-18 | 2006-11-18 11:49 | Calculated | O410E | L1730 | Single Circuit |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 7 | 19353 | 392 | 0.02026 | 0.0003617 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8899 |  | 2006-11-20 09:14 | 2006-11-20 | 2006-11-20 10:34 | Calculated | O410E | L763 | Drop-Out Fuses |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 80 | 1 | 19353 | 80 | 0.00413 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8900 |  | 2006-11-20 09:47 | 2006-11-20 | 2006-11-20 11:20 | Calculated | O410E | L1529 | Drop-Out Fuses |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 2 | 19353 | 186 | 0.00961 | 0.00010334 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8901 |  | 2006-11-20 10:22 | 2006-11-20 | 2006-11-20 11:02 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 11 | 19353 | 440 | 0.02274 | 0.00056839 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8904 |  | 2006-11-21 10:05 | 2006-11-21 | 2006-11-21 12:32 | Calculated | O410E |  |  |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 147 | 22 | 19353 | 3234 | 0.16711 | 0.0011368 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8905 |  | 2006-11-21 12:56 | 2006-11-21 | 2006-11-21 12:57 | Calculated | O410E | C242 | Single Circuit |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2006/2007 | November-2006 | 11 | 2006
8906 |  | 2006-11-21 13:53 | 2006-11-21 | 2006-11-21 14:54 | Calculated | O410E | C465 | Single Circuit |  | Ongarue 421-02 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 25 | 19353 | 1525 | 0.0788 | 0.0012918 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8909 |  | 2006-11-22 09:36 | 2006-11-22 | 2006-11-22 12:01 | Calculated | O410E |  | Drop-Out Fuses |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Bushings (fixed Insulation) | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 145 | 72 | 19353 | 10454 | 0.54017 | 0.0037204 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8907 |  | 2006-11-22 10:01 | 2006-11-22 | 2006-11-22 14:34 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 273 | 9 | 19353 | 2457 | 0.12696 | 0.00046504 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8910 |  | 2006-11-22 14:13 | 2006-11-22 | 2006-11-22 14:15 | Calculated | O410E | C107 |  |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 341 | 19353 | 682 | 0.03524 | 0.01762 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8911 |  | 2006-11-23 07:47 | 2006-11-23 | 2006-11-23 09:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 109 | 1 | 19353 | 109 | 0.00563 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8912 |  | 2006-11-23 09:33 | 2006-11-23 | 2006-11-23 10:27 | Calculated | O410E |  |  |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 70 | 19353 | 3795 | 0.19609 | 0.003617 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8913 |  | 2006-11-23 10:16 | 2006-11-23 | 2006-11-23 11:27 | Calculated | O410E | S544 | Single Circuit |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 20 | 19353 | 1420 | 0.07337 | 0.0010334 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8915 |  | 2006-11-24 09:38 | 2006-11-24 | 2006-11-24 13:09 | Calculated | O410E | LF |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 211 | 4 | 19353 | 844 | 0.04361 | 0.00020669 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8916 |  | 2006-11-24 10:01 | 2006-11-24 | 2006-11-24 13:49 | Calculated | O410E |  |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 228 | 4 | 19353 | 912 | 0.04712 | 0.00020669 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8918 |  | 2006-11-24 11:07 | 2006-11-24 | 2006-11-24 11:37 | Calculated | O410E | LF |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 3 | 19353 | 90 | 0.00465 | 0.00015501 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8919 |  | 2006-11-24 14:15 | 2006-11-24 | 2006-11-24 14:51 | Calculated | O410E | C127 |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 344 | 19353 | 12475 | 0.6446 | 0.017775 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8920 |  | 2006-11-24 17:10 | 2006-11-24 | 2006-11-24 19:42 | Calculated | O410E | L1.27 | Single Circuit |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 6 | 19353 | 912 | 0.04712 | 0.00031003 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8921 |  | 2006-11-24 18:51 | 2006-11-24 | 2006-11-24 20:17 | Calculated | O410E | L246 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 86 | 17 | 19353 | 1469 | 0.07591 | 0.00087842 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8922 |  | 2006-11-24 20:37 | 2006-11-24 | 2006-11-24 20:49 | Calculated | O410E | LF |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 2 | 19353 | 24 | 0.00124 | 0.00010334 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8923 |  | 2006-11-24 20:43 | 2006-11-24 | 2006-11-24 22:04 | Calculated | O410E | LF |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 5 | 19353 | 405 | 0.02093 | 0.00025836 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8924 |  | 2006-11-27 03:03 | 2006-11-27 | 2006-11-27 05:35 | Calculated | O410E | C1 | Single Circuit |  | Mokai 123-00 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Pole - Hardwood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 546 | 19353 | 83328 | 4.3057 | 0.028213 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8925 |  | 2006-11-27 08:42 | 2006-11-27 | 2006-11-27 09:51 | Calculated | O410E | L717 | Drop-Out Fuses |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 69 | 2 | 19353 | 138 | 0.00713 | 0.00010334 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8926 |  | 2006-11-27 10:04 | 2006-11-27 | 2006-11-27 11:58 | Calculated | O410E |  |  |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 114 | 17 | 19353 | 1940 | 0.10024 | 0.00087842 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8928 |  | 2006-11-27 14:17 | 2006-11-27 | 2006-11-27 14:46 | Calculated | O410E | C1107 | Single Circuit |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 65 | 19353 | 1885 | 0.0974 | 0.0033587 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8930 |  | 2006-11-28 09:48 | 2006-11-28 | 2006-11-28 13:12 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 204 | 1 | 19353 | 204 | 0.01054 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8931 |  | 2006-11-28 11:07 | 2006-11-28 | 2006-11-28 13:26 | Calculated | O410E |  |  |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 3 | 19353 | 417 | 0.02155 | 0.00015501 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8934 |  | 2006-11-29 09:31 | 2006-11-29 | 2006-11-29 10:43 | Calculated | O410E | C268 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 52 | 19353 | 3744 | 0.19346 | 0.0026869 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8935 |  | 2006-11-29 10:36 | 2006-11-29 | 2006-11-29 14:46 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 19 | 19353 | 4750 | 0.24544 | 0.00098176 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8936 |  | 2006-11-30 06:25 | 2006-11-30 | 2006-11-30 06:36 | Calculated | O410E | C242 | Single Circuit |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply | OH Lines : Crossarm - Wood | Weather | Lightning |  | Lightning Damage to Structure/Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 241 | 19353 | 2651 | 0.13698 | 0.012453 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8937 |  | 2006-11-30 06:31 | 2006-11-30 | 2006-11-30 07:22 | Calculated | O410E | C465 |  |  | Ongarue 421-02 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 25 | 19353 | 1275 | 0.06588 | 0.0012918 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8938 |  | 2006-11-30 06:58 | 2006-11-30 | 2006-11-30 08:26 | Calculated | O410E | C682 |  |  |  | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 136 | 19353 | 12088 | 0.62461 | 0.0070273 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8939 |  | 2006-11-30 08:03 | 2006-11-30 | 2006-11-30 10:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 164 | 13 | 19353 | 2134 | 0.11027 | 0.00067173 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8940 |  | 2006-11-30 08:07 | 2006-11-30 | 2006-11-30 11:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 193 | 6 | 19353 | 1162 | 0.06004 | 0.00031003 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8941 |  | 2006-11-30 08:23 | 2006-11-30 | 2006-11-30 11:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 198 | 1 | 19353 | 198 | 0.01023 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8942 |  | 2006-11-30 09:58 | 2006-11-30 | 2006-11-30 10:39 | Calculated | O410E | L272 | Drop-Out Fuses |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 41 | 8 | 19353 | 328 | 0.01695 | 0.00041337 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8944 |  | 2006-11-30 11:39 | 2006-11-30 | 2006-11-30 13:37 | Calculated | O410E | C1262 |  |  | Huirimu 121-04 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 11 | 19353 | 1302 | 0.06728 | 0.00056839 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8943 |  | 2006-11-30 11:40 | 2006-11-30 | 2006-11-30 12:34 | Calculated | O410E | S1548 | Drop-Out Fuses |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 54 | 90 | 19353 | 4860 | 0.25112 | 0.0046504 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8945 |  | 2006-11-30 11:54 | 2006-11-30 | 2006-11-30 15:03 | Calculated | O410E | C142 | Single Circuit |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation | OH Lines : Insulator - Pin | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 189 | 273 | 19353 | 51783 | 2.6757 | 0.014106 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8946 |  | 2006-11-30 12:19 | 2006-11-30 | 2006-11-30 16:17 | Calculated | O410E | C426 | Single Circuit |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 238 | 78 | 19353 | 18597 | 0.96094 | 0.0040304 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8947 |  | 2006-11-30 12:28 | 2006-11-30 | 2006-11-30 16:51 | Calculated | O410E | C446 | Single Circuit |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 263 | 106 | 19353 | 27957 | 1.4446 | 0.0054772 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8948 |  | 2006-11-30 12:32 | 2006-11-30 | 2006-11-30 14:23 | Calculated | O410E | C1728 | Single Circuit |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 21 | 19353 | 2331 | 0.12045 | 0.0010851 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8949 |  | 2006-11-30 13:57 | 2006-11-30 | 2006-11-30 14:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 42 | 1 | 19353 | 42 | 0.00217 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8950 |  | 2006-11-30 14:09 | 2006-11-30 | 2006-11-30 15:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 98 | 1 | 19353 | 98 | 0.00506 | 5.1672e-05 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8951 |  | 2006-11-30 21:04 | 2006-11-30 | 2006-11-30 21:56 | Calculated | O410E | S1339 | Single Circuit |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 65 | 19353 | 3380 | 0.17465 | 0.0033587 | 0 | 0 | 2006/2007 | November-2006 | 11 | 2006
8952 |  | 2006-12-01 07:26 | 2006-12-01 | 2006-12-01 08:22 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 56 | 2 | 19353 | 112 | 0.00579 | 0.00010334 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8953 |  | 2006-12-01 09:08 | 2006-12-01 | 2006-12-01 13:40 | Calculated | O410E |  |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 3 | 19353 | 816 | 0.04216 | 0.00015501 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8954 |  | 2006-12-01 09:34 | 2006-12-01 | 2006-12-01 11:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 1 | 19353 | 92 | 0.00475 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8955 |  | 2006-12-03 03:47 | 2006-12-03 | 2006-12-03 04:01 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 14 | 3 | 19353 | 42 | 0.00217 | 0.00015501 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8956 |  | 2006-12-04 09:33 | 2006-12-04 | 2006-12-04 12:00 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 147 | 6 | 19353 | 882 | 0.04557 | 0.00031003 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8957 |  | 2006-12-04 10:31 | 2006-12-04 | 2006-12-04 12:13 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 47 | 19353 | 4805 | 0.24828 | 0.0024286 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8959 |  | 2006-12-04 11:49 | 2006-12-04 | 2006-12-04 15:41 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 232 | 3 | 19353 | 698 | 0.03607 | 0.00015501 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8960 |  | 2006-12-05 10:04 | 2006-12-05 | 2006-12-05 14:52 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 288 | 15 | 19353 | 4320 | 0.22322 | 0.00077507 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8961 |  | 2006-12-05 10:35 | 2006-12-05 | 2006-12-05 15:06 | Calculated | O410E |  |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 51 | 19353 | 13821 | 0.71415 | 0.0026353 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8962 |  | 2006-12-05 11:08 | 2006-12-05 | 2006-12-05 18:30 | Calculated | O410E | LF | Pole Mounted |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 442 | 2 | 19353 | 884 | 0.04568 | 0.00010334 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8963 |  | 2006-12-05 14:15 | 2006-12-05 | 2006-12-05 14:33 | Calculated | O410E | LF |  |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 1 | 19353 | 18 | 0.00093 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8964 |  | 2006-12-05 19:33 | 2006-12-05 | 2006-12-05 20:10 | Calculated | O410E | L1118 | Single Circuit |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 2 | 19353 | 74 | 0.00382 | 0.00010334 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8965 |  | 2006-12-06 10:24 | 2006-12-06 | 2006-12-06 12:04 | Calculated | O410E | LF |  |  | Maihiihi 111-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 1 | 19353 | 100 | 0.00517 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8966 |  | 2006-12-06 10:41 | 2006-12-06 | 2006-12-06 12:09 | Calculated | O410E | C250 | Drop-Out Fuses |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 10 | 19353 | 880 | 0.04547 | 0.00051672 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8968 |  | 2006-12-07 08:58 | 2006-12-07 | 2006-12-07 10:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 65 | 2 | 19353 | 130 | 0.00672 | 0.00010334 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8969 |  | 2006-12-07 09:50 | 2006-12-07 | 2006-12-07 10:29 | Calculated | O410E |  |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 39 | 86 | 19353 | 3354 | 0.17331 | 0.0044438 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8970 |  | 2006-12-07 10:07 | 2006-12-07 | 2006-12-07 11:53 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 106 | 1 | 19353 | 106 | 0.00548 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8971 |  | 2006-12-07 10:32 | 2006-12-07 | 2006-12-07 13:21 | Calculated | O410E | C1615 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 169 | 9 | 19353 | 1521 | 0.07859 | 0.00046504 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8972 |  | 2006-12-08 09:10 | 2006-12-08 | 2006-12-08 14:00 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 290 | 4 | 19353 | 1160 | 0.05994 | 0.00020669 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8973 |  | 2006-12-08 10:18 | 2006-12-08 | 2006-12-08 14:04 | Calculated | O410E |  |  |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 226 | 5 | 19353 | 1130 | 0.05839 | 0.00025836 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8974 |  | 2006-12-08 10:35 | 2006-12-08 | 2006-12-08 12:25 | Calculated | O410E |  |  |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 110 | 1 | 19353 | 110 | 0.00568 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8975 |  | 2006-12-08 13:13 | 2006-12-08 | 2006-12-08 13:47 | Calculated | O410E |  |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 34 | 86 | 19353 | 2924 | 0.15109 | 0.0044438 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8976 |  | 2006-12-09 07:00 | 2006-12-09 | 2006-12-09 09:44 | Calculated | O410E | C268 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 52 | 19353 | 8535 | 0.44102 | 0.0026869 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8977 |  | 2006-12-10 02:20 | 2006-12-10 | 2006-12-10 02:24 | Calculated | O410E | C242 & 262 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 328 | 19353 | 1312 | 0.06779 | 0.016948 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8978 |  | 2006-12-10 09:26 | 2006-12-10 | 2006-12-10 10:28 | Calculated | O410E | C112 | Single Circuit |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Pole - Hardwood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 190 | 19353 | 11932 | 0.61655 | 0.0098176 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8979 |  | 2006-12-11 10:04 | 2006-12-11 | 2006-12-11 11:17 | Calculated | O410E |  |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 86 | 19353 | 6299 | 0.32548 | 0.0044438 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8980 |  | 2006-12-11 18:30 | 2006-12-11 | 2006-12-11 19:48 | Calculated | O410E | LF |  |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 4 | 19353 | 312 | 0.01612 | 0.00020669 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8981 |  | 2006-12-11 19:48 | 2006-12-11 | 2006-12-11 21:19 | Calculated | O410E | C5536 | Sectionaliser |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Mechanism | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 91 | 7 | 19353 | 637 | 0.03291 | 0.0003617 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8982 |  | 2006-12-12 09:14 | 2006-12-12 | 2006-12-12 12:49 | Calculated | O410E |  |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 215 | 70 | 19353 | 15059 | 0.77812 | 0.003617 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8983 |  | 2006-12-12 13:02 | 2006-12-12 | 2006-12-12 13:43 | Calculated | O410E |  |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 182 | 19353 | 7462 | 0.38557 | 0.0094042 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8985 |  | 2006-12-13 09:19 | 2006-12-13 | 2006-12-13 09:41 | Calculated | O410E |  |  |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 22 | 20 | 19353 | 440 | 0.02274 | 0.0010334 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8986 |  | 2006-12-13 09:22 | 2006-12-13 | 2006-12-13 14:40 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 318 | 10 | 19353 | 3180 | 0.16432 | 0.00051672 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8988 |  | 2006-12-14 08:09 | 2006-12-14 | 2006-12-14 12:37 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 106 | 19353 | 28450 | 1.4701 | 0.0054772 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8989 |  | 2006-12-14 09:21 | 2006-12-14 | 2006-12-14 10:10 | Calculated | O410E | LF |  |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 1 | 19353 | 49 | 0.00253 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8990 |  | 2006-12-14 09:23 | 2006-12-14 | 2006-12-14 13:37 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 254 | 10 | 19353 | 2540 | 0.13125 | 0.00051672 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8991 |  | 2006-12-14 10:33 | 2006-12-14 | 2006-12-14 14:30 | Calculated | O410E |  |  |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 237 | 35 | 19353 | 8295 | 0.42862 | 0.0018085 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8992 |  | 2006-12-14 14:12 | 2006-12-14 | 2006-12-14 14:44 | Calculated | O410E | S659 |  |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 23 | 19353 | 736 | 0.03803 | 0.0011884 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8993 |  | 2006-12-14 20:00 | 2006-12-14 | 2006-12-14 21:37 | Calculated | O410E | C466 | Pole Mounted |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 59 | 19353 | 5723 | 0.29572 | 0.0030486 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8994 |  | 2006-12-15 09:30 | 2006-12-15 | 2006-12-15 10:48 | Calculated | O410E | LF | Pole Mounted |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 1 | 19353 | 78 | 0.00403 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8995 |  | 2006-12-15 09:39 | 2006-12-15 | 2006-12-15 09:55 | Calculated | O410E |  |  |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 7 | 19353 | 112 | 0.00579 | 0.0003617 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8996 |  | 2006-12-15 10:05 | 2006-12-15 | 2006-12-15 11:29 | Calculated | O410E | LF |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 1 | 19353 | 84 | 0.00434 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8997 |  | 2006-12-15 10:31 | 2006-12-15 | 2006-12-15 15:23 | Calculated | O410E |  |  |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 11 | 19353 | 3212 | 0.16597 | 0.00056839 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
8998 |  | 2006-12-15 10:32 | 2006-12-15 | 2006-12-15 14:43 | Calculated | O410E |  |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 251 | 51 | 19353 | 12801 | 0.66145 | 0.0026353 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9000 |  | 2006-12-17 09:15 | 2006-12-17 | 2006-12-17 11:04 | Calculated | O410E | C623 | Single Circuit |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 10 | 19353 | 1090 | 0.05632 | 0.00051672 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9001 |  | 2006-12-18 10:26 | 2006-12-18 | 2006-12-18 12:04 | Calculated | O410E | L679 | Single Circuit |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Insulated ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 3 | 19353 | 294 | 0.01519 | 0.00015501 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9002 |  | 2006-12-18 10:35 | 2006-12-18 | 2006-12-18 14:52 | Calculated | O410E |  |  |  | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 257 | 158 | 19353 | 40692 | 2.1026 | 0.0081641 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9003 |  | 2006-12-18 13:27 | 2006-12-18 | 2006-12-18 15:23 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangipo / Hautu 424-03 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 116 | 4 | 19353 | 464 | 0.02398 | 0.00020669 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9004 |  | 2006-12-19 08:57 | 2006-12-19 | 2006-12-19 09:26 | Calculated | O410E | LF |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 29 | 3 | 19353 | 87 | 0.0045 | 0.00015501 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9006 |  | 2006-12-19 12:00 | 2006-12-19 | 2006-12-19 12:20 | Calculated | O410E |  |  |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 20 | 8 | 19353 | 160 | 0.00827 | 0.00041337 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9007 |  | 2006-12-19 16:29 | 2006-12-19 | 2006-12-19 17:23 | Calculated | O410E | L6176 - RMU701 | Drop-Out Fuses |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 54 | 156 | 19353 | 8424 | 0.43528 | 0.0080608 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9008 |  | 2006-12-20 03:50 | 2006-12-20 | 2006-12-20 04:01 | Calculated | O410E | C952 |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 939 | 19353 | 10329 | 0.53372 | 0.04852 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9009 |  | 2006-12-20 07:42 | 2006-12-20 | 2006-12-20 10:30 | Calculated | O410E | L368 | Drop-Out Fuses |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 168 | 24 | 19353 | 4032 | 0.20834 | 0.0012401 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9011 |  | 2006-12-20 09:52 | 2006-12-20 | 2006-12-20 11:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9012 |  | 2006-12-20 09:56 | 2006-12-20 | 2006-12-20 11:12 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 76 | 43 | 19353 | 3276 | 0.16928 | 0.0022219 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9013 |  | 2006-12-20 10:07 | 2006-12-20 | 2006-12-20 14:50 | Calculated | O410E | LV |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 283 | 5 | 19353 | 1415 | 0.07312 | 0.00025836 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9014 |  | 2006-12-20 10:21 | 2006-12-20 | 2006-12-20 12:14 | Calculated | O410E | LF |  |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 2 | 19353 | 226 | 0.01168 | 0.00010334 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9016 |  | 2006-12-20 12:46 | 2006-12-20 | 2006-12-20 12:47 | Calculated | O410E | C242 & 796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 241 | 19353 | 241 | 0.01245 | 0.012453 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9017 |  | 2006-12-20 12:53 | 2006-12-20 | 2006-12-20 13:46 | Calculated | O410E | LF | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 53 | 2 | 19353 | 106 | 0.00548 | 0.00010334 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9018 |  | 2006-12-20 13:32 | 2006-12-20 | 2006-12-20 14:15 | Calculated | O410E |  |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 33 | 19353 | 1419 | 0.07332 | 0.0017052 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9019 |  | 2006-12-20 13:34 | 2006-12-20 | 2006-12-20 16:02 | Calculated | O410E |  |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 5 | 19353 | 740 | 0.03824 | 0.00025836 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9020 |  | 2006-12-21 09:14 | 2006-12-21 | 2006-12-21 15:08 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 3 | 19353 | 1062 | 0.05488 | 0.00015501 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9021 |  | 2006-12-21 10:00 | 2006-12-21 | 2006-12-21 15:10 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 310 | 78 | 19353 | 24219 | 1.2514 | 0.0040304 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9022 |  | 2006-12-21 10:32 | 2006-12-21 | 2006-12-21 11:45 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 39 | 19353 | 2865 | 0.14804 | 0.0020152 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9023 |  | 2006-12-21 10:37 | 2006-12-21 | 2006-12-21 14:14 | Calculated | O410E |  |  |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 217 | 8 | 19353 | 1736 | 0.0897 | 0.00041337 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9025 |  | 2006-12-21 19:39 | 2006-12-21 | 2006-12-21 20:19 | Calculated | O410E | S583 | Single Circuit |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 121 | 19353 | 4840 | 0.25009 | 0.0062523 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9026 |  | 2006-12-22 07:11 | 2006-12-22 | 2006-12-22 08:02 | Calculated | O410E | LF | Single Circuit |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 1 | 19353 | 51 | 0.00264 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9027 |  | 2006-12-22 09:44 | 2006-12-22 | 2006-12-22 10:42 | Calculated | O410E |  |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 3 | 19353 | 174 | 0.00899 | 0.00015501 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9030 |  | 2006-12-22 18:30 | 2006-12-22 | 2006-12-22 20:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 100 | 1 | 19353 | 100 | 0.00517 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9029 |  | 2006-12-22 19:11 | 2006-12-22 | 2006-12-22 20:02 | Calculated | O410E | Link 654 | Single Circuit |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 3 | 19353 | 153 | 0.00791 | 0.00015501 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9032 |  | 2006-12-28 01:36 | 2006-12-28 | 2006-12-28 01:46 | Calculated | O410E | OCB 118 | Single Circuit |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 259 | 19353 | 2590 | 0.13383 | 0.013383 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9033 |  | 2006-12-28 09:25 | 2006-12-28 | 2006-12-28 16:13 | Calculated | O410E | Sect 1541 |  |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 408 | 5 | 19353 | 2040 | 0.10541 | 0.00025836 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9034 |  | 2006-12-28 13:35 | 2006-12-28 | 2006-12-28 14:52 | Calculated | O410E | LF | Single Circuit |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 1 | 19353 | 77 | 0.00398 | 5.1672e-05 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9035 |  | 2006-12-29 06:48 | 2006-12-29 | 2006-12-29 07:55 | Calculated | O410E | Rec 375 | Single Circuit |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 31 | 19353 | 2077 | 0.10732 | 0.0016018 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9036 |  | 2006-12-29 10:02 | 2006-12-29 | 2006-12-29 11:39 | Calculated | O410E | LF |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 7 | 19353 | 679 | 0.03508 | 0.0003617 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9037 |  | 2006-12-29 10:36 | 2006-12-29 | 2006-12-29 14:21 | Calculated | O410E | LF |  |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 225 | 2 | 19353 | 450 | 0.02325 | 0.00010334 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9038 |  | 2006-12-31 13:10 | 2006-12-31 | 2006-12-31 14:41 | Calculated | O410E | Sect 5536 | Single Circuit |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 7 | 19353 | 637 | 0.03291 | 0.0003617 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9039 |  | 2006-12-31 13:15 | 2006-12-31 | 2006-12-31 13:30 | Calculated | O410E | LF |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 53 | 19353 | 795 | 0.04108 | 0.0027386 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9040 |  | 2006-12-31 18:18 | 2006-12-31 | 2006-12-31 18:22 | Calculated | O410E | OCB 202 | Single Circuit |  |  | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 321 | 19353 | 1284 | 0.06635 | 0.016587 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9041 |  | 2006-12-31 18:21 | 2006-12-31 | 2006-12-31 20:28 | Calculated | O410E | LF |  |  | Ongarue 421-02 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 2 | 19353 | 254 | 0.01312 | 0.00010334 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9042 |  | 2006-12-31 18:42 | 2006-12-31 | 2006-12-31 20:52 | Calculated | O410E | LF |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 9 | 19353 | 1170 | 0.06046 | 0.00046504 | 0 | 0 | 2006/2007 | December-2006 | 12 | 2006
9043 |  | 2007-01-01 06:55 | 2007-01-01 | 2007-01-01 07:04 | Calculated | O410E | OCB 180 | Single Circuit |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 3 | 19353 | 27 | 0.0014 | 0.00015501 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9044 |  | 2007-01-01 20:57 | 2007-01-01 | 2007-01-01 22:39 | Calculated | O410E | L913 | Drop-Out Fuses |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 102 | 162 | 19353 | 16524 | 0.85382 | 0.0083708 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9045 |  | 2007-01-02 13:37 | 2007-01-02 | 2007-01-02 13:38 | Calculated | O410E | S607-890 |  |  |  | Remote Rural F | Nihoniho | Nihoniho Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2006/2007 | January-2007 | 1 | 2007
9046 |  | 2007-01-02 18:48 | 2007-01-02 | 2007-01-02 20:13 | Calculated | O410E | LF | Pole Mounted |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | Transformers : Internal Connections | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 2 | 19353 | 170 | 0.00878 | 0.00010334 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9047 |  | 2007-01-02 21:01 | 2007-01-02 | 2007-01-02 22:20 | Calculated | O410E | L341 & 587 | Drop-Out Fuses |  | Gravel Scoop 109-05 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 79 | 27 | 19353 | 2157 | 0.11146 | 0.0013951 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9048 |  | 2007-01-03 09:39 | 2007-01-03 | 2007-01-03 10:48 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 69 | 39 | 19353 | 2712 | 0.14013 | 0.0020152 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9049 |  | 2007-01-03 10:10 | 2007-01-03 | 2007-01-03 10:55 | Calculated | O410E | LF | Pole Mounted |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 1 | 19353 | 45 | 0.00233 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9050 |  | 2007-01-03 10:37 | 2007-01-03 | 2007-01-03 16:10 | Calculated | O410E | C505 | Single Circuit |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 333 | 22 | 19353 | 7334 | 0.37896 | 0.0011368 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9051 |  | 2007-01-04 10:35 | 2007-01-04 | 2007-01-04 11:37 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 62 | 39 | 19353 | 2420 | 0.12505 | 0.0020152 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9052 |  | 2007-01-05 09:27 | 2007-01-05 | 2007-01-05 13:54 | Calculated | O410E | LF | Pole Mounted |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 267 | 2 | 19353 | 534 | 0.02759 | 0.00010334 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9053 |  | 2007-01-05 10:38 | 2007-01-05 | 2007-01-05 13:57 | Calculated | O410E |  |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 199 | 25 | 19353 | 4975 | 0.25707 | 0.0012918 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9054 |  | 2007-01-05 12:57 | 2007-01-05 | 2007-01-05 14:03 | Calculated | O410E | LF | Single Circuit |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Stay Pole or Strut | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 2 | 19353 | 132 | 0.00682 | 0.00010334 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9055 |  | 2007-01-05 23:09 | 2007-01-05 | 2007-01-05 23:16 | Calculated | O410E | C1010 |  |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 499 | 19353 | 3493 | 0.18049 | 0.025784 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9056 |  | 2007-01-07 07:03 | 2007-01-07 | 2007-01-07 08:18 | Calculated | O410E | C277 |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 86 | 19353 | 6450 | 0.33328 | 0.0044438 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9057 |  | 2007-01-07 10:01 | 2007-01-07 | 2007-01-07 12:08 | Calculated | O410E | S345 & 348 | Single Circuit |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 23 | 19353 | 2935 | 0.15166 | 0.0011884 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9058 |  | 2007-01-08 08:21 | 2007-01-08 | 2007-01-08 10:46 | Calculated | O410E | S983-704-714 | Single Circuit |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 39 | 19353 | 5655 | 0.2922 | 0.0020152 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9059 |  | 2007-01-08 09:09 | 2007-01-08 | 2007-01-08 11:28 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 72 | 19353 | 10059 | 0.51976 | 0.0037204 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9060 |  | 2007-01-08 11:00 | 2007-01-08 | 2007-01-08 12:22 | Calculated | O410E | LF |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 1 | 19353 | 82 | 0.00424 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9062 |  | 2007-01-08 13:48 | 2007-01-08 | 2007-01-08 14:37 | Calculated | O410E | LF |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 1 | 19353 | 49 | 0.00253 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9063 |  | 2007-01-08 16:52 | 2007-01-08 | 2007-01-08 17:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-02 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 38 | 2 | 19353 | 76 | 0.00393 | 0.00010334 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9064 |  | 2007-01-09 08:55 | 2007-01-09 | 2007-01-09 15:23 | Calculated | O410E | LF | Pole Mounted |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 388 | 1 | 19353 | 388 | 0.02005 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9065 |  | 2007-01-09 08:57 | 2007-01-09 | 2007-01-09 12:09 | Calculated | O410E | LF |  |  | Benneydale 103-03 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 192 | 1 | 19353 | 192 | 0.00992 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9067 |  | 2007-01-09 09:35 | 2007-01-09 | 2007-01-09 10:34 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 59 | 39 | 19353 | 2310 | 0.11936 | 0.0020152 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9066 |  | 2007-01-09 09:47 | 2007-01-09 | 2007-01-09 11:01 | Calculated | O410E | LF | Drop-Out Fuses |  | National Park 411-02 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 74 | 1 | 19353 | 74 | 0.00382 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9068 |  | 2007-01-09 10:02 | 2007-01-09 | 2007-01-09 11:42 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 73 | 19353 | 7308 | 0.37762 | 0.003772 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9069 |  | 2007-01-10 09:36 | 2007-01-10 | 2007-01-10 13:54 | Calculated | O410E | LF |  |  | Western 403-01 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 35 | 19353 | 9053 | 0.46778 | 0.0018085 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9070 |  | 2007-01-11 10:32 | 2007-01-11 | 2007-01-11 13:59 | Calculated | O410E |  |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 207 | 38 | 19353 | 7880 | 0.40717 | 0.0019635 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9071 |  | 2007-01-11 11:32 | 2007-01-11 | 2007-01-11 12:13 | Calculated | O410E | C952 | Paper/Lead - Ducted |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Cables : Cable Core - Phase | Asset Related | TLC Operator & Authorised Contractor Error |  | Control Operator Error | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 41 | 1176 | 19353 | 48941 | 2.5289 | 0.060766 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9072 |  | 2007-01-11 15:07 | 2007-01-11 | 2007-01-11 16:29 | Calculated | O410E | C6560 |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 21 | 19353 | 1722 | 0.08898 | 0.0010851 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9073 |  | 2007-01-11 15:23 | 2007-01-11 | 2007-01-11 16:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9074 |  | 2007-01-12 10:34 | 2007-01-12 | 2007-01-12 13:21 | Calculated | O410E |  |  |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 167 | 9 | 19353 | 1503 | 0.07766 | 0.00046504 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9075 |  | 2007-01-12 10:39 | 2007-01-12 | 2007-01-12 11:47 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 68 | 1 | 19353 | 68 | 0.00351 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9076 |  | 2007-01-12 11:02 | 2007-01-12 | 2007-01-12 12:57 | Calculated | O410E | S915-RMU1-48-LB2 |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error |  | Control Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 70 | 19353 | 8050 | 0.41596 | 0.003617 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9077 |  | 2007-01-13 09:37 | 2007-01-13 | 2007-01-13 11:58 | Calculated | O410E | C385 | Single Circuit |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 116 | 19353 | 16450 | 0.85 | 0.0059939 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9078 |  | 2007-01-14 05:10 | 2007-01-14 | 2007-01-14 08:15 | Calculated | O410E | C446 | Single Circuit |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 106 | 19353 | 19694 | 1.0176 | 0.0054772 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9080 |  | 2007-01-15 02:33 | 2007-01-15 | 2007-01-15 02:40 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 7 | 3 | 19353 | 21 | 0.00109 | 0.00015501 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9081 |  | 2007-01-15 09:27 | 2007-01-15 | 2007-01-15 11:24 | Calculated | O410E | LF | Drop-Out Fuses |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 117 | 1 | 19353 | 117 | 0.00605 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9082 |  | 2007-01-15 10:18 | 2007-01-15 | 2007-01-15 11:21 | Calculated | O410E | LF |  |  | Otorohanga 112-06 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 1 | 19353 | 63 | 0.00326 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9083 |  | 2007-01-15 13:01 | 2007-01-15 | 2007-01-15 14:34 | Calculated | O410E |  |  |  | Caves 101-05 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 93 | 12 | 19353 | 1116 | 0.05767 | 0.00062006 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9084 |  | 2007-01-16 10:01 | 2007-01-16 | 2007-01-16 11:42 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 101 | 62 | 19353 | 6262 | 0.32357 | 0.0032036 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9085 |  | 2007-01-16 13:00 | 2007-01-16 | 2007-01-16 14:59 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 28 | 19353 | 3332 | 0.17217 | 0.0014468 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9088 |  | 2007-01-17 09:02 | 2007-01-17 | 2007-01-17 15:00 | Calculated | O410E |  |  |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 358 | 32 | 19353 | 11456 | 0.59195 | 0.0016535 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9089 |  | 2007-01-17 10:03 | 2007-01-17 | 2007-01-17 13:59 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 236 | 8 | 19353 | 1888 | 0.09756 | 0.00041337 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9090 |  | 2007-01-17 10:33 | 2007-01-17 | 2007-01-17 11:41 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 68 | 39 | 19353 | 2656 | 0.13724 | 0.0020152 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9091 |  | 2007-01-17 15:10 | 2007-01-17 | 2007-01-17 16:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 58 | 1 | 19353 | 58 | 0.003 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9092 |  | 2007-01-17 22:14 | 2007-01-17 | 2007-01-17 23:36 | Calculated | O410E | LF | Pole Mounted |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 1 | 19353 | 82 | 0.00424 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9093 |  | 2007-01-18 01:21 | 2007-01-18 | 2007-01-18 01:30 | Calculated | O410E | C6143 & C180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 3 | 19353 | 27 | 0.0014 | 0.00015501 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9096 |  | 2007-01-19 13:29 | 2007-01-19 | 2007-01-19 14:22 | Calculated | O410E | LF |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 53 | 1 | 19353 | 53 | 0.00274 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9097 |  | 2007-01-19 15:11 | 2007-01-19 | 2007-01-19 15:48 | Calculated | O410E | LF | Single Circuit |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 1 | 19353 | 37 | 0.00191 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9098 |  | 2007-01-21 00:50 | 2007-01-21 | 2007-01-21 01:45 | Calculated | O410E | C1272-S523-257 | Single Circuit |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Joint - Compression / Non-Tension | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 8 | 19353 | 440 | 0.02274 | 0.00041337 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9099 |  | 2007-01-21 06:51 | 2007-01-21 | 2007-01-21 09:45 | Calculated | O410E | C446 | Single Circuit |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 174 | 106 | 19353 | 18488 | 0.9553 | 0.0054772 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9100 |  | 2007-01-24 08:21 | 2007-01-24 | 2007-01-24 13:26 | Calculated | O410E | LV |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 8 | 19353 | 2440 | 0.12608 | 0.00041337 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9101 |  | 2007-01-24 10:03 | 2007-01-24 | 2007-01-24 11:43 | Calculated | O410E |  |  |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 5 | 19353 | 500 | 0.02584 | 0.00025836 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9102 |  | 2007-01-24 14:11 | 2007-01-24 | 2007-01-24 16:27 | Calculated | O410E | LF |  |  | Southern 409-04 | Remote Rural F | Southern | Manunui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 19 | 19353 | 2584 | 0.13352 | 0.00098176 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9103 |  | 2007-01-25 08:13 | 2007-01-25 | 2007-01-25 14:53 | Calculated | O410E | LF |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 400 | 3 | 19353 | 1200 | 0.06201 | 0.00015501 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9105 |  | 2007-01-25 10:19 | 2007-01-25 | 2007-01-25 11:57 | Calculated | O410E |  |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 98 | 30 | 19353 | 2940 | 0.15191 | 0.0015501 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9106 |  | 2007-01-25 12:00 | 2007-01-25 | 2007-01-25 13:05 | Calculated | O410E |  |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 65 | 201 | 19353 | 13075 | 0.67561 | 0.010386 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9107 |  | 2007-01-25 15:45 | 2007-01-25 | 2007-01-25 16:35 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 50 | 1 | 19353 | 50 | 0.00258 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9108 |  | 2007-01-26 10:35 | 2007-01-26 | 2007-01-26 14:59 | Calculated | O410E |  |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 33 | 19353 | 8712 | 0.45016 | 0.0017052 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9109 |  | 2007-01-26 12:11 | 2007-01-26 | 2007-01-26 13:23 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 72 | 1 | 19353 | 72 | 0.00372 | 5.1672e-05 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9110 |  | 2007-01-26 13:07 | 2007-01-26 | 2007-01-26 15:35 | Calculated | O410E | L145 |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 4 | 19353 | 592 | 0.03059 | 0.00020669 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9111 |  | 2007-01-27 09:43 | 2007-01-27 | 2007-01-27 10:43 | Calculated | O410E | S709 | Drop-Out Fuses |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 60 | 35 | 19353 | 2100 | 0.10851 | 0.0018085 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9112 |  | 2007-01-28 05:14 | 2007-01-28 | 2007-01-28 05:22 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 3 | 19353 | 24 | 0.00124 | 0.00015501 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9114 |  | 2007-01-30 11:21 | 2007-01-30 | 2007-01-30 12:56 | Calculated | O410E | L726 | Single Circuit |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 14 | 19353 | 1330 | 0.06872 | 0.0007234 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9116 |  | 2007-01-31 10:01 | 2007-01-31 | 2007-01-31 11:36 | Calculated | O410E | C296 |  |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 138 | 19353 | 13110 | 0.67741 | 0.0071307 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9117 |  | 2007-01-31 10:55 | 2007-01-31 | 2007-01-31 13:28 | Calculated | O410E | C5534 |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 153 | 12 | 19353 | 1836 | 0.09487 | 0.00062006 | 0 | 0 | 2006/2007 | January-2007 | 1 | 2007
9123 |  | 2007-02-01 09:50 | 2007-02-01 | 2007-02-01 12:10 | Calculated | O410E | L5536 | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 140 | 7 | 19353 | 980 | 0.05064 | 0.0003617 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9125 |  | 2007-02-01 12:41 | 2007-02-01 | 2007-02-01 13:50 | Calculated | O410E | L449 | Single Circuit |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Wraplock Deadend | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 35 | 19353 | 2432 | 0.12567 | 0.0018085 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9126 |  | 2007-02-01 13:04 | 2007-02-01 | 2007-02-01 13:42 | Calculated | O410E | S227 - 586 | Single Circuit |  | Rangitoto 106-02 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 5 | 19353 | 190 | 0.00982 | 0.00025836 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9127 |  | 2007-02-01 13:39 | 2007-02-01 | 2007-02-01 14:28 | Calculated | O410E | LF | Single Circuit |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation | OH Lines : Stay Wire | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 3 | 19353 | 147 | 0.0076 | 0.00015501 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9128 |  | 2007-02-01 15:42 | 2007-02-01 | 2007-02-01 16:14 | Calculated | O410E | LF |  |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 6 | 19353 | 192 | 0.00992 | 0.00031003 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9131 |  | 2007-02-02 21:32 | 2007-02-02 | 2007-02-02 22:57 | Calculated | O410E | C836 |  |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 72 | 19353 | 6120 | 0.31623 | 0.0037204 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9133 |  | 2007-02-04 18:58 | 2007-02-04 | 2007-02-04 21:11 | Calculated | O410E | C1 | Single Circuit |  | Mokai 123-00 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Crossarm - Wood | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 259 | 19353 | 34485 | 1.7819 | 0.013383 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9135 |  | 2007-02-05 11:19 | 2007-02-05 | 2007-02-05 14:21 | Calculated | O410E | S460 |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 182 | 71 | 19353 | 12940 | 0.66863 | 0.0036687 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9136 |  | 2007-02-06 22:43 | 2007-02-06 | 2007-02-07 00:38 | Calculated | O410E | C378 | Single Circuit |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 203 | 19353 | 23487 | 1.2136 | 0.010489 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9137 |  | 2007-02-07 08:03 | 2007-02-07 | 2007-02-07 10:39 | Calculated | O410E | C1616 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 156 | 15 | 19353 | 2340 | 0.12091 | 0.00077507 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9139 |  | 2007-02-07 10:17 | 2007-02-07 | 2007-02-07 14:22 | Calculated | O410E |  |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 4 | 19353 | 980 | 0.05064 | 0.00020669 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9140 |  | 2007-02-07 10:21 | 2007-02-07 | 2007-02-07 11:23 | Calculated | O410E |  |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 62 | 25 | 19353 | 1550 | 0.08009 | 0.0012918 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9141 |  | 2007-02-07 15:07 | 2007-02-07 | 2007-02-07 16:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 71 | 1 | 19353 | 71 | 0.00367 | 5.1672e-05 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9144 |  | 2007-02-08 18:26 | 2007-02-08 | 2007-02-09 03:10 | Calculated | O410E | C740 |  |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 524 | 14 | 19353 | 7343 | 0.37942 | 0.0007234 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9145 |  | 2007-02-09 06:44 | 2007-02-09 | 2007-02-09 10:42 | Calculated | O410E | L1533 |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 238 | 3 | 19353 | 714 | 0.03689 | 0.00015501 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9147 |  | 2007-02-09 10:33 | 2007-02-09 | 2007-02-09 13:01 | Calculated | O410E |  |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 24 | 19353 | 3552 | 0.18354 | 0.0012401 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9148 |  | 2007-02-09 12:06 | 2007-02-09 | 2007-02-09 12:37 | Calculated | O410E | LF |  |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 3 | 19353 | 93 | 0.00481 | 0.00015501 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9149 |  | 2007-02-09 12:47 | 2007-02-09 | 2007-02-09 14:01 | Calculated | O410E | C5534 |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 12 | 19353 | 888 | 0.04588 | 0.00062006 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9152 |  | 2007-02-09 15:47 | 2007-02-09 | 2007-02-09 16:43 | Calculated | O410E | LV |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 35 | 19353 | 1960 | 0.10128 | 0.0018085 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9153 |  | 2007-02-09 15:52 | 2007-02-09 | 2007-02-09 17:03 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 71 | 1 | 19353 | 71 | 0.00367 | 5.1672e-05 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9154 |  | 2007-02-09 23:05 | 2007-02-09 | 2007-02-10 00:49 | Calculated | O410E | C1272 | Single Circuit |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Conductor - Bare ACSR | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 230 | 19353 | 24119 | 1.2463 | 0.011884 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9155 |  | 2007-02-12 10:53 | 2007-02-12 | 2007-02-12 11:23 | Calculated | O410E |  |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 30 | 30 | 19353 | 900 | 0.0465 | 0.0015501 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9157 |  | 2007-02-12 13:20 | 2007-02-12 | 2007-02-12 16:59 | Calculated | O410E | C591 |  |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 48 | 19353 | 10538 | 0.54452 | 0.0024802 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9158 |  | 2007-02-12 14:40 | 2007-02-12 | 2007-02-12 15:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 32 | 3 | 19353 | 96 | 0.00496 | 0.00015501 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9159 |  | 2007-02-12 18:20 | 2007-02-12 | 2007-02-12 20:29 | Calculated | O410E |  |  |  | Rangitoto 106-02 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 129 | 5 | 19353 | 645 | 0.03333 | 0.00025836 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9160 |  | 2007-02-12 21:07 | 2007-02-12 | 2007-02-12 21:25 | Calculated | O410E | C641 |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 267 | 19353 | 4806 | 0.24833 | 0.013796 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9161 |  | 2007-02-13 13:44 | 2007-02-13 | 2007-02-13 14:33 | Calculated | O410E | LF |  |  | Gravel Scoop 109-05 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 2 | 19353 | 98 | 0.00506 | 0.00010334 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9162 |  | 2007-02-13 14:46 | 2007-02-13 | 2007-02-13 16:21 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 1 | 19353 | 95 | 0.00491 | 5.1672e-05 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9163 |  | 2007-02-14 07:37 | 2007-02-14 | 2007-02-14 07:38 | Calculated | O410E | C798 |  |  |  | Remote Rural F | Wairere / Mahoenui 33 | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 499 | 19353 | 499 | 0.02578 | 0.025784 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9164 |  | 2007-02-14 07:51 | 2007-02-14 | 2007-02-14 08:32 | Calculated | O410E | L341 | Single Circuit |  | Gravel Scoop 109-05 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 27 | 19353 | 1111 | 0.05741 | 0.0013951 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9165 |  | 2007-02-14 09:27 | 2007-02-14 | 2007-02-14 10:44 | Calculated | O410E | C5849 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 26 | 19353 | 2002 | 0.10345 | 0.0013435 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9166 |  | 2007-02-14 10:32 | 2007-02-14 | 2007-02-14 14:12 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 220 | 59 | 19353 | 12980 | 0.6707 | 0.0030486 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9167 |  | 2007-02-14 10:57 | 2007-02-14 | 2007-02-14 13:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 156 | 2 | 19353 | 312 | 0.01612 | 0.00010334 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9168 |  | 2007-02-14 12:47 | 2007-02-14 | 2007-02-14 13:41 | Calculated | O410E | LV |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 44 | 19353 | 2376 | 0.12277 | 0.0022735 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9169 |  | 2007-02-15 00:37 | 2007-02-15 | 2007-02-15 00:47 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 3 | 19353 | 30 | 0.00155 | 0.00015501 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9170 |  | 2007-02-15 09:07 | 2007-02-15 | 2007-02-15 15:27 | Calculated | O410E |  |  |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 380 | 5 | 19353 | 1900 | 0.09818 | 0.00025836 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9172 |  | 2007-02-15 10:39 | 2007-02-15 | 2007-02-15 15:08 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 59 | 19353 | 15871 | 0.82008 | 0.0030486 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9173 |  | 2007-02-15 10:43 | 2007-02-15 | 2007-02-15 11:07 | Calculated | O410E | LF |  |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 24 | 1 | 19353 | 24 | 0.00124 | 5.1672e-05 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9175 |  | 2007-02-16 09:05 | 2007-02-16 | 2007-02-16 12:47 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 222 | 9 | 19353 | 1998 | 0.10324 | 0.00046504 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9177 |  | 2007-02-16 10:07 | 2007-02-16 | 2007-02-16 17:05 | Calculated | O410E | C564 | Single Circuit |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 418 | 19 | 19353 | 7942 | 0.41038 | 0.00098176 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9176 |  | 2007-02-16 10:41 | 2007-02-16 | 2007-02-16 13:22 | Calculated | O410E |  |  |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 161 | 8 | 19353 | 1288 | 0.06655 | 0.00041337 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9178 |  | 2007-02-19 09:38 | 2007-02-19 | 2007-02-19 11:58 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 140 | 105 | 19353 | 14700 | 0.75957 | 0.0054255 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9179 |  | 2007-02-20 07:14 | 2007-02-20 | 2007-02-20 08:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 54 | 1 | 19353 | 54 | 0.00279 | 5.1672e-05 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9180 |  | 2007-02-20 09:06 | 2007-02-20 | 2007-02-20 13:30 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 9 | 19353 | 2376 | 0.12277 | 0.00046504 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9181 |  | 2007-02-20 09:22 | 2007-02-20 | 2007-02-20 15:36 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 28 | 19353 | 10472 | 0.5411 | 0.0014468 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9182 |  | 2007-02-20 09:58 | 2007-02-20 | 2007-02-20 17:50 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 472 | 37 | 19353 | 17464 | 0.90239 | 0.0019118 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9184 |  | 2007-02-22 09:31 | 2007-02-22 | 2007-02-22 12:30 | Calculated | O410E |  |  |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 179 | 39 | 19353 | 6981 | 0.36072 | 0.0020152 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9352 |  | 2007-02-23 08:50 | 2007-02-23 | 2007-02-23 10:43 | Calculated | O410E | LF |  |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 2 | 19353 | 226 | 0.01168 | 0.00010334 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9187 |  | 2007-02-23 09:39 | 2007-02-23 | 2007-02-23 14:43 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 304 | 5 | 19353 | 1520 | 0.07854 | 0.00025836 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9190 |  | 2007-02-26 10:00 | 2007-02-26 | 2007-02-26 12:32 | Calculated | O410E |  |  |  | Ongarue 421-02 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 152 | 23 | 19353 | 3496 | 0.18064 | 0.0011884 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9191 |  | 2007-02-26 13:00 | 2007-02-26 | 2007-02-26 14:40 | Calculated | O410E |  |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 493 | 19353 | 49300 | 2.5474 | 0.025474 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9192 |  | 2007-02-26 14:00 | 2007-02-26 | 2007-02-26 15:01 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 61 | 1 | 19353 | 61 | 0.00315 | 5.1672e-05 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9193 |  | 2007-02-26 16:05 | 2007-02-26 | 2007-02-26 16:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 24 | 8 | 19353 | 192 | 0.00992 | 0.00041337 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9194 |  | 2007-02-27 09:03 | 2007-02-27 | 2007-02-27 15:16 | Calculated | O410E |  |  |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 373 | 26 | 19353 | 9698 | 0.50111 | 0.0013435 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9195 |  | 2007-02-27 09:37 | 2007-02-27 | 2007-02-27 12:05 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 48 | 19353 | 7104 | 0.36707 | 0.0024802 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9196 |  | 2007-02-27 13:01 | 2007-02-27 | 2007-02-27 14:40 | Calculated | O410E | LF |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 99 | 4 | 19353 | 396 | 0.02046 | 0.00020669 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9197 |  | 2007-02-27 13:15 | 2007-02-27 | 2007-02-27 13:57 | Calculated | O410E | S630 |  |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 20 | 19353 | 840 | 0.0434 | 0.0010334 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9198 |  | 2007-02-27 15:12 | 2007-02-27 | 2007-02-27 16:22 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 70 | 5 | 19353 | 350 | 0.01809 | 0.00025836 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9199 |  | 2007-02-28 05:20 | 2007-02-28 | 2007-02-28 05:22 | Calculated | O410E | C1102 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 1905 | 19353 | 3810 | 0.19687 | 0.098434 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9200 |  | 2007-02-28 09:01 | 2007-02-28 | 2007-02-28 09:47 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 67 | 19353 | 3087 | 0.15951 | 0.003462 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9201 |  | 2007-02-28 09:15 | 2007-02-28 | 2007-02-28 11:35 | Calculated | O410E | L374 | Drop-Out Fuses |  |  | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 140 | 27 | 19353 | 3780 | 0.19532 | 0.0013951 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9202 |  | 2007-02-28 11:08 | 2007-02-28 | 2007-02-28 12:33 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 85 | 1 | 19353 | 85 | 0.00439 | 5.1672e-05 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9204 |  | 2007-02-28 20:55 | 2007-02-28 | 2007-03-01 00:24 | Calculated | O410E | C641 | ABS |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 209 | 267 | 19353 | 55803 | 2.8834 | 0.013796 | 0 | 0 | 2006/2007 | February-2007 | 2 | 2007
9205 |  | 2007-03-01 10:27 | 2007-03-01 | 2007-03-01 12:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 97 | 1 | 19353 | 97 | 0.00501 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9206 |  | 2007-03-02 09:02 | 2007-03-02 | 2007-03-02 13:39 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 277 | 21 | 19353 | 5817 | 0.30057 | 0.0010851 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9207 |  | 2007-03-02 09:04 | 2007-03-02 | 2007-03-02 14:22 | Calculated | O410E |  |  |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 318 | 5 | 19353 | 1590 | 0.08216 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9208 |  | 2007-03-02 10:35 | 2007-03-02 | 2007-03-02 15:11 | Calculated | O410E |  |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 276 | 4 | 19353 | 1104 | 0.05705 | 0.00020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9209 |  | 2007-03-03 21:25 | 2007-03-03 | 2007-03-03 21:34 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 3 | 19353 | 27 | 0.0014 | 0.00015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9210 |  | 2007-03-05 13:00 | 2007-03-05 | 2007-03-05 14:35 | Calculated | O410E |  |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 493 | 19353 | 46835 | 2.42 | 0.025474 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9211 |  | 2007-03-05 18:57 | 2007-03-05 | 2007-03-05 19:05 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 8 | 30 | 19353 | 264 | 0.01364 | 0.0015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9213 |  | 2007-03-06 09:32 | 2007-03-06 | 2007-03-06 14:37 | Calculated | O410E |  |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 9 | 19353 | 2745 | 0.14184 | 0.00046504 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9215 |  | 2007-03-07 06:27 | 2007-03-07 | 2007-03-07 06:40 | Calculated | O410E | C513 |  |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 411 | 19353 | 5343 | 0.27608 | 0.021237 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9216 |  | 2007-03-07 07:48 | 2007-03-07 | 2007-03-07 09:16 | Calculated | O410E | S182 | Single Circuit |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | OH Lines : Jumper - Bare Copper | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 31 | 19353 | 2728 | 0.14096 | 0.0016018 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9217 |  | 2007-03-07 09:18 | 2007-03-07 | 2007-03-07 10:30 | Calculated | O410E | LF | Pole Mounted |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 4 | 19353 | 288 | 0.01488 | 0.00020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9218 |  | 2007-03-08 07:03 | 2007-03-08 | 2007-03-08 09:11 | Calculated | O410E | LF | Single Circuit |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 1 | 19353 | 128 | 0.00661 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9220 |  | 2007-03-08 12:34 | 2007-03-08 | 2007-03-08 14:13 | Calculated | O410E | S630 | Single Circuit |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 20 | 19353 | 1980 | 0.10231 | 0.0010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9221 |  | 2007-03-09 09:03 | 2007-03-09 | 2007-03-09 10:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 72 | 1 | 19353 | 72 | 0.00372 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9224 |  | 2007-03-09 12:05 | 2007-03-09 | 2007-03-09 13:12 | Calculated | O410E | L1714 | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 10 | 19353 | 670 | 0.03462 | 0.00051672 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9225 |  | 2007-03-09 12:57 | 2007-03-09 | 2007-03-09 13:40 | Calculated | O410E | L663 | Drop-Out Fuses |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 43 | 7 | 19353 | 301 | 0.01555 | 0.0003617 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9226 |  | 2007-03-11 07:51 | 2007-03-11 | 2007-03-11 09:50 | Calculated | O410E | C1 | Single Circuit |  | Mokai 123-00 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 259 | 19353 | 31071 | 1.6055 | 0.013383 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9227 |  | 2007-03-12 09:32 | 2007-03-12 | 2007-03-12 11:28 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 116 | 47 | 19353 | 5469 | 0.28259 | 0.0024286 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9228 |  | 2007-03-12 10:38 | 2007-03-12 | 2007-03-12 13:02 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 144 | 68 | 19353 | 9792 | 0.50597 | 0.0035137 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9229 |  | 2007-03-12 13:46 | 2007-03-12 | 2007-03-12 15:12 | Calculated | O410E | L1547 |  |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 9 | 19353 | 774 | 0.03999 | 0.00046504 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9230 |  | 2007-03-13 04:30 | 2007-03-13 | 2007-03-13 06:15 | Calculated | O410E | L677 | Drop-Out Fuses |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 105 | 8 | 19353 | 840 | 0.0434 | 0.00041337 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9231 |  | 2007-03-13 07:32 | 2007-03-13 | 2007-03-13 08:03 | Calculated | O410E | LV |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 44 | 19353 | 1364 | 0.07048 | 0.0022735 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9232 |  | 2007-03-13 08:02 | 2007-03-13 | 2007-03-13 09:40 | Calculated | O410E | L1709 | Drop-Out Fuses |  | Mokauiti 115-02 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 98 | 3 | 19353 | 294 | 0.01519 | 0.00015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9233 |  | 2007-03-13 10:42 | 2007-03-13 | 2007-03-13 12:26 | Calculated | O410E |  |  |  | Whakamaru 120-03 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 104 | 102 | 19353 | 10662 | 0.55092 | 0.0052705 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9235 |  | 2007-03-13 11:10 | 2007-03-13 | 2007-03-13 15:05 | Calculated | O410E | LF |  |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 235 | 1 | 19353 | 235 | 0.01214 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9236 |  | 2007-03-13 11:18 | 2007-03-13 | 2007-03-13 13:13 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 11 | 19353 | 1265 | 0.06536 | 0.00056839 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9237 |  | 2007-03-13 16:00 | 2007-03-13 | 2007-03-13 16:24 | Calculated | O410E | LV |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 24 | 35 | 19353 | 840 | 0.0434 | 0.0018085 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9238 |  | 2007-03-13 16:48 | 2007-03-13 | 2007-03-13 17:13 | Calculated | O410E | C2102 |  |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 472 | 19353 | 11925 | 0.61618 | 0.024389 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9239 |  | 2007-03-14 07:02 | 2007-03-14 | 2007-03-14 08:15 | Calculated | O410E | L1539 | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 73 | 7 | 19353 | 511 | 0.0264 | 0.0003617 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9240 |  | 2007-03-14 08:38 | 2007-03-14 | 2007-03-14 10:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 108 | 1 | 19353 | 108 | 0.00558 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9242 |  | 2007-03-14 09:58 | 2007-03-14 | 2007-03-14 15:44 | Calculated | O410E | C758 | Drop-Out Fuses |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 346 | 85 | 19353 | 29419 | 1.5201 | 0.0043921 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9243 |  | 2007-03-14 10:00 | 2007-03-14 | 2007-03-14 12:52 | Calculated | O410E | L280 | Single Circuit |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 8 | 19353 | 1376 | 0.0711 | 0.00041337 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9245 |  | 2007-03-14 12:41 | 2007-03-14 | 2007-03-14 15:16 | Calculated | O410E |  |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 155 | 31 | 19353 | 4805 | 0.24828 | 0.0016018 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9244 |  | 2007-03-14 12:45 | 2007-03-14 | 2007-03-14 13:58 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 18 | 19353 | 1314 | 0.0679 | 0.00093009 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9246 |  | 2007-03-14 14:04 | 2007-03-14 | 2007-03-14 14:45 | Calculated | O410E | S1339-1511 | Single Circuit |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Jumper - Bare Copper | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 7 | 19353 | 287 | 0.01483 | 0.0003617 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9247 |  | 2007-03-14 14:05 | 2007-03-14 | 2007-03-14 14:08 | Calculated | O410E | C124 |  |  | Maihiihi 111-00 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 592 | 19353 | 1776 | 0.09177 | 0.03059 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9248 |  | 2007-03-14 14:30 | 2007-03-14 | 2007-03-14 14:49 | Calculated | O410E | C127 | Single Circuit |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 592 | 19353 | 11287 | 0.58322 | 0.03059 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9249 |  | 2007-03-14 15:09 | 2007-03-14 | 2007-03-14 20:33 | Calculated | O410E | C609 | Single Circuit |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation | OH Lines : Surge Diverters | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 324 | 104 | 19353 | 33696 | 1.7411 | 0.0053738 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9250 |  | 2007-03-14 15:12 | 2007-03-14 | 2007-03-14 16:17 | Calculated | O410E | L433 | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 65 | 9 | 19353 | 585 | 0.03023 | 0.00046504 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9251 |  | 2007-03-14 15:17 | 2007-03-14 | 2007-03-14 16:48 | Calculated | O410E | L332 | Drop-Out Fuses |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 91 | 2 | 19353 | 182 | 0.0094 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9269 |  | 2007-03-14 15:19 | 2007-03-14 | 2007-03-14 19:55 | Calculated | O410E | C277 |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 276 | 86 | 19353 | 23736 | 1.2265 | 0.0044438 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9253 |  | 2007-03-14 15:35 | 2007-03-14 | 2007-03-14 16:27 | Calculated | O410E | C124 | Single Circuit |  | Maihiihi 111-00 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 615 | 19353 | 32338 | 1.671 | 0.031778 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9254 |  | 2007-03-14 15:38 | 2007-03-14 | 2007-03-14 17:18 | Calculated | O410E | C120 | Single Circuit |  | McDonalds 110-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 548 | 19353 | 55211 | 2.8528 | 0.028316 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9255 |  | 2007-03-14 16:06 | 2007-03-14 | 2007-03-14 17:37 | Calculated | O410E | L1638 | Drop-Out Fuses |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 91 | 3 | 19353 | 273 | 0.01411 | 0.00015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9256 |  | 2007-03-14 16:12 | 2007-03-14 | 2007-03-14 21:40 | Calculated | O410E | C119 | Single Circuit |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 328 | 122 | 19353 | 40048 | 2.0693 | 0.0063039 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9258 |  | 2007-03-14 16:39 | 2007-03-14 | 2007-03-14 18:07 | Calculated | O410E | C2102 | Single Circuit |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 543 | 19353 | 47811 | 2.4705 | 0.028058 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9257 |  | 2007-03-14 16:43 | 2007-03-14 | 2007-03-14 19:29 | Calculated | O410E | C2 | Single Circuit |  | Tihoi 124-00 | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 287 | 19353 | 47732 | 2.4664 | 0.01483 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9259 |  | 2007-03-14 16:47 | 2007-03-14 | 2007-03-14 18:11 | Calculated | O410E | S307-314 | Single Circuit |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 348 | 19353 | 29226 | 1.5102 | 0.017982 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9261 |  | 2007-03-14 16:52 | 2007-03-14 | 2007-03-15 15:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 1355 | 2 | 19353 | 2710 | 0.14003 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9263 |  | 2007-03-14 16:57 | 2007-03-14 | 2007-03-14 17:27 | Calculated | O410E | C683 |  |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 350 | 19353 | 10657 | 0.55066 | 0.018085 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9262 |  | 2007-03-14 16:58 | 2007-03-14 | 2007-03-14 19:30 | Calculated | O410E | S281 | Single Circuit |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 40 | 19353 | 6080 | 0.31416 | 0.0020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9264 |  | 2007-03-14 17:01 | 2007-03-14 | 2007-03-14 19:06 | Calculated | O410E | L372 | Drop-Out Fuses |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 125 | 14 | 19353 | 1750 | 0.09043 | 0.0007234 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9265 |  | 2007-03-14 18:26 | 2007-03-14 | 2007-03-14 21:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 168 | 1 | 19353 | 168 | 0.00868 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9266 |  | 2007-03-14 18:50 | 2007-03-14 | 2007-03-14 22:27 | Calculated | O410E | C378 | Single Circuit |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 203 | 19353 | 44162 | 2.2819 | 0.010489 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9267 |  | 2007-03-14 19:00 | 2007-03-14 | 2007-03-15 10:19 | Calculated | O410E | L1.8 | Single Circuit |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 919 | 36 | 19353 | 33084 | 1.7095 | 0.0018602 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9268 |  | 2007-03-14 19:05 | 2007-03-14 | 2007-03-14 19:10 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 5 | 241 | 19353 | 1205 | 0.06226 | 0.012453 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9270 |  | 2007-03-14 20:30 | 2007-03-14 | 2007-03-14 21:16 | Calculated | O410E | C202 | Drop-Out Fuses |  |  | Remote Rural F | Nihoniho | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 46 | 321 | 19353 | 15060 | 0.77817 | 0.016587 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9271 |  | 2007-03-14 20:38 | 2007-03-14 | 2007-03-14 21:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 32 | 3 | 19353 | 96 | 0.00496 | 0.00015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9272 |  | 2007-03-14 21:04 | 2007-03-14 | 2007-03-14 21:09 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 5 | 241 | 19353 | 1205 | 0.06226 | 0.012453 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9273 |  | 2007-03-15 01:23 | 2007-03-15 | 2007-03-15 08:00 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 397 | 3 | 19353 | 1191 | 0.06154 | 0.00015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9274 |  | 2007-03-15 08:02 | 2007-03-15 | 2007-03-15 09:28 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 86 | 1 | 19353 | 86 | 0.00444 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9275 |  | 2007-03-15 08:47 | 2007-03-15 | 2007-03-15 10:10 | Calculated | O410E | LV |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 20 | 19353 | 1660 | 0.08577 | 0.0010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9276 |  | 2007-03-15 09:32 | 2007-03-15 | 2007-03-15 12:10 | Calculated | O410E | C1530 |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 6 | 19353 | 948 | 0.04898 | 0.00031003 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9277 |  | 2007-03-15 09:57 | 2007-03-15 | 2007-03-15 12:12 | Calculated | O410E | L518 | Drop-Out Fuses |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 135 | 31 | 19353 | 4185 | 0.21625 | 0.0016018 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9278 |  | 2007-03-15 10:13 | 2007-03-15 | 2007-03-15 12:20 | Calculated | O410E | L275 | Drop-Out Fuses |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 52 | 19353 | 6604 | 0.34124 | 0.0026869 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9279 |  | 2007-03-15 10:17 | 2007-03-15 | 2007-03-15 13:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 171 | 4 | 19353 | 684 | 0.03534 | 0.00020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9280 |  | 2007-03-15 10:23 | 2007-03-15 | 2007-03-15 13:16 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 173 | 2 | 19353 | 346 | 0.01788 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9281 |  | 2007-03-15 10:42 | 2007-03-15 | 2007-03-15 13:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 167 | 2 | 19353 | 334 | 0.01726 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9282 |  | 2007-03-15 10:51 | 2007-03-15 | 2007-03-15 13:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 158 | 2 | 19353 | 316 | 0.01633 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9284 |  | 2007-03-15 11:29 | 2007-03-15 | 2007-03-15 13:14 | Calculated | O410E | L372 | Single Circuit |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 70 | 19353 | 7350 | 0.37979 | 0.003617 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9283 |  | 2007-03-15 11:35 | 2007-03-15 | 2007-03-15 13:05 | Calculated | O410E | C1271-S175-340 | Single Circuit |  | Hangatiki East 102-01 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 14 | 19353 | 1260 | 0.06511 | 0.0007234 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9285 |  | 2007-03-15 12:11 | 2007-03-15 | 2007-03-15 13:36 | Calculated | O410E | S281 |  |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 40 | 19353 | 3400 | 0.17568 | 0.0020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9286 |  | 2007-03-15 12:18 | 2007-03-15 | 2007-03-15 14:24 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 126 | 1 | 19353 | 126 | 0.00651 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9287 |  | 2007-03-15 12:37 | 2007-03-15 | 2007-03-15 15:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 150 | 1 | 19353 | 150 | 0.00775 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9288 |  | 2007-03-15 12:41 | 2007-03-15 | 2007-03-15 15:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 166 | 2 | 19353 | 332 | 0.01715 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9289 |  | 2007-03-15 12:46 | 2007-03-15 | 2007-03-15 15:28 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 162 | 2 | 19353 | 324 | 0.01674 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9290 |  | 2007-03-15 13:02 | 2007-03-15 | 2007-03-15 16:09 | Calculated | O410E | L1538 | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 187 | 2 | 19353 | 374 | 0.01933 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9291 |  | 2007-03-15 13:25 | 2007-03-15 | 2007-03-15 16:04 | Calculated | O410E | C1636 | Single Circuit |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 11 | 19353 | 1749 | 0.09037 | 0.00056839 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9292 |  | 2007-03-15 13:47 | 2007-03-15 | 2007-03-15 16:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 172 | 1 | 19353 | 172 | 0.00889 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9293 |  | 2007-03-15 13:59 | 2007-03-15 | 2007-03-15 16:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 133 | 1 | 19353 | 133 | 0.00687 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9294 |  | 2007-03-15 14:06 | 2007-03-15 | 2007-03-15 14:34 | Calculated | O410E | LV |  |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 3 | 19353 | 84 | 0.00434 | 0.00015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9295 |  | 2007-03-15 14:42 | 2007-03-15 | 2007-03-15 15:10 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 28 | 241 | 19353 | 6748 | 0.34868 | 0.012453 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9296 |  | 2007-03-15 15:39 | 2007-03-15 | 2007-03-15 16:44 | Calculated | O410E | C560 |  |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 15 | 19353 | 975 | 0.05038 | 0.00077507 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9297 |  | 2007-03-15 15:58 | 2007-03-15 | 2007-03-15 16:31 | Calculated | O410E | LV |  |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 2 | 19353 | 66 | 0.00341 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9298 |  | 2007-03-15 16:02 | 2007-03-15 | 2007-03-15 18:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 133 | 1 | 19353 | 133 | 0.00687 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9299 |  | 2007-03-15 16:06 | 2007-03-15 | 2007-03-15 17:13 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 2 | 19353 | 134 | 0.00692 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9300 |  | 2007-03-15 16:09 | 2007-03-15 | 2007-03-15 17:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 55 | 1 | 19353 | 55 | 0.00284 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9301 |  | 2007-03-15 16:22 | 2007-03-15 | 2007-03-15 17:41 | Calculated | O410E | L1539 | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 79 | 7 | 19353 | 553 | 0.02857 | 0.0003617 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9302 |  | 2007-03-15 17:51 | 2007-03-15 | 2007-03-15 18:11 | Calculated | O410E | L179 |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 11 | 19353 | 220 | 0.01137 | 0.00056839 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9303 |  | 2007-03-15 19:10 | 2007-03-15 | 2007-03-15 19:34 | Calculated | O410E | LF |  |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 2 | 19353 | 48 | 0.00248 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9304 |  | 2007-03-15 20:03 | 2007-03-15 | 2007-03-15 20:41 | Calculated | O410E | S550-545 | Single Circuit |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 18 | 19353 | 684 | 0.03534 | 0.00093009 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9305 |  | 2007-03-16 09:06 | 2007-03-16 | 2007-03-16 09:44 | Calculated | O410E | L754 | Drop-Out Fuses |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 38 | 23 | 19353 | 874 | 0.04516 | 0.0011884 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9306 |  | 2007-03-16 09:31 | 2007-03-16 | 2007-03-16 11:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 101 | 6 | 19353 | 606 | 0.03131 | 0.00031003 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9307 |  | 2007-03-16 10:13 | 2007-03-16 | 2007-03-16 11:10 | Calculated | O410E | LF |  |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 3 | 19353 | 171 | 0.00884 | 0.00015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9308 |  | 2007-03-16 10:45 | 2007-03-16 | 2007-03-16 12:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 100 | 3 | 19353 | 300 | 0.0155 | 0.00015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9309 |  | 2007-03-16 11:18 | 2007-03-16 | 2007-03-16 11:37 | Calculated | O410E | LF |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 4 | 19353 | 76 | 0.00393 | 0.00020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9310 |  | 2007-03-16 12:10 | 2007-03-16 | 2007-03-16 17:03 | Calculated | O410E | LF | Pole Mounted |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 293 | 1 | 19353 | 293 | 0.01514 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9311 |  | 2007-03-16 12:17 | 2007-03-16 | 2007-03-16 16:42 | Calculated | O410E | L252 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 265 | 6 | 19353 | 1590 | 0.08216 | 0.00031003 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9312 |  | 2007-03-16 13:05 | 2007-03-16 | 2007-03-16 14:28 | Calculated | O410E | L732 | Drop-Out Fuses |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 83 | 5 | 19353 | 415 | 0.02144 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9313 |  | 2007-03-16 13:46 | 2007-03-16 | 2007-03-16 14:53 | Calculated | O410E | L647 | Single Circuit |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Crossarm - Wood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 13 | 19353 | 871 | 0.04501 | 0.00067173 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9314 |  | 2007-03-16 14:27 | 2007-03-16 | 2007-03-16 15:07 | Calculated | O410E | L1317 | Single Circuit |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 6 | 19353 | 240 | 0.0124 | 0.00031003 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9315 |  | 2007-03-16 14:27 | 2007-03-16 | 2007-03-16 16:32 | Calculated | O410E | C378-S376-619 | Single Circuit |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 28 | 19353 | 3500 | 0.18085 | 0.0014468 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9316 |  | 2007-03-16 14:37 | 2007-03-16 | 2007-03-16 16:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 1 | 19353 | 88 | 0.00455 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9317 |  | 2007-03-16 14:59 | 2007-03-16 | 2007-03-16 15:22 | Calculated | O410E | S331 | Single Circuit |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Jumper - Bare Copper | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 15 | 19353 | 345 | 0.01783 | 0.00077507 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9318 |  | 2007-03-16 15:20 | 2007-03-16 | 2007-03-16 16:03 | Calculated | O410E | S293 | Single Circuit |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Jumper - Bare Copper | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 83 | 19353 | 3569 | 0.18442 | 0.0042887 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9319 |  | 2007-03-16 16:50 | 2007-03-16 | 2007-03-16 17:25 | Calculated | O410E | LF |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 1 | 19353 | 35 | 0.00181 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9320 |  | 2007-03-16 17:49 | 2007-03-16 | 2007-03-16 18:07 | Calculated | O410E | LF |  |  | McDonalds 110-02 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 10 | 19353 | 180 | 0.0093 | 0.00051672 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9321 |  | 2007-03-17 11:03 | 2007-03-17 | 2007-03-17 12:49 | Calculated | O410E | L1617 | Drop-Out Fuses |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 106 | 2 | 19353 | 212 | 0.01095 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9322 |  | 2007-03-17 11:16 | 2007-03-17 | 2007-03-17 12:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 83 | 1 | 19353 | 83 | 0.00429 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9323 |  | 2007-03-17 11:47 | 2007-03-17 | 2007-03-17 13:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 112 | 1 | 19353 | 112 | 0.00579 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9324 |  | 2007-03-18 09:06 | 2007-03-18 | 2007-03-18 09:47 | Calculated | O410E | C609 |  |  | Rural 126-03 | Remote Rural F | Rural | Taharoa Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 104 | 19353 | 4264 | 0.22033 | 0.0053738 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9325 |  | 2007-03-18 10:38 | 2007-03-18 | 2007-03-18 12:25 | Calculated | O410E | C455 | Drop-Out Fuses |  | Ohura 413-07 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 107 | 15 | 19353 | 1614 | 0.0834 | 0.00077507 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9326 |  | 2007-03-19 08:37 | 2007-03-19 | 2007-03-19 11:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 179 | 1 | 19353 | 179 | 0.00925 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9327 |  | 2007-03-19 09:42 | 2007-03-19 | 2007-03-19 11:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 83 | 1 | 19353 | 83 | 0.00429 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9328 |  | 2007-03-19 10:07 | 2007-03-19 | 2007-03-19 14:13 | Calculated | O410E | LF |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 246 | 4 | 19353 | 984 | 0.05084 | 0.00020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9330 |  | 2007-03-19 10:49 | 2007-03-19 | 2007-03-19 13:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 141 | 1 | 19353 | 141 | 0.00729 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9331 |  | 2007-03-19 12:35 | 2007-03-19 | 2007-03-19 12:38 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 241 | 19353 | 723 | 0.03736 | 0.012453 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9332 |  | 2007-03-19 13:53 | 2007-03-19 | 2007-03-19 14:56 | Calculated | O410E | C1541 |  |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 5 | 19353 | 315 | 0.01628 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9333 |  | 2007-03-19 14:58 | 2007-03-19 | 2007-03-19 16:20 | Calculated | O410E | LF |  |  | Gravel Scoop 109-10 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 18 | 19353 | 1476 | 0.07627 | 0.00093009 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9334 |  | 2007-03-19 17:15 | 2007-03-19 | 2007-03-19 18:44 | Calculated | O410E | S644-759 | Pole Mounted |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 34 | 19353 | 3026 | 0.15636 | 0.0017568 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9335 |  | 2007-03-20 04:05 | 2007-03-20 | 2007-03-20 04:15 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 435 | 19353 | 4350 | 0.22477 | 0.022477 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9336 |  | 2007-03-20 07:42 | 2007-03-20 | 2007-03-20 14:40 | Calculated | O410E | C490 | Single Circuit |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation | OH Lines : Binder / Stirrup | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 418 | 47 | 19353 | 19656 | 1.0157 | 0.0024286 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9338 |  | 2007-03-20 11:05 | 2007-03-20 | 2007-03-20 11:31 | Calculated | O410E | LF |  |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 4 | 19353 | 104 | 0.00537 | 0.00020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9339 |  | 2007-03-20 11:10 | 2007-03-20 | 2007-03-20 15:22 | Calculated | O410E |  |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 252 | 5 | 19353 | 1260 | 0.06511 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9340 |  | 2007-03-20 12:23 | 2007-03-20 | 2007-03-20 14:47 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 144 | 1 | 19353 | 144 | 0.00744 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9341 |  | 2007-03-20 17:32 | 2007-03-20 | 2007-03-20 17:50 | Calculated | O410E | LF |  |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 4 | 19353 | 72 | 0.00372 | 0.00020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9342 |  | 2007-03-20 18:07 | 2007-03-20 | 2007-03-20 18:58 | Calculated | O410E | LV |  |  | Hakiaha 401-01 | Remote Rural F | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 18 | 19353 | 918 | 0.04743 | 0.00093009 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9343 |  | 2007-03-21 09:30 | 2007-03-21 | 2007-03-21 13:08 | Calculated | O410E | LF |  |  | Turoa 415-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 218 | 29 | 19353 | 6322 | 0.32667 | 0.0014985 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9344 |  | 2007-03-21 09:42 | 2007-03-21 | 2007-03-21 14:59 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 317 | 5 | 19353 | 1585 | 0.0819 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9345 |  | 2007-03-21 10:12 | 2007-03-21 | 2007-03-21 15:06 | Calculated | O410E | LF |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 149 | 19353 | 43806 | 2.2635 | 0.0076991 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9346 |  | 2007-03-21 10:30 | 2007-03-21 | 2007-03-21 12:05 | Calculated | O410E |  |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 112 | 19353 | 10669 | 0.55128 | 0.0057872 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9347 |  | 2007-03-21 14:09 | 2007-03-21 | 2007-03-21 14:57 | Calculated | O410E | S632 | Drop-Out Fuses |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 48 | 9 | 19353 | 432 | 0.02232 | 0.00046504 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9349 |  | 2007-03-22 09:42 | 2007-03-22 | 2007-03-22 14:59 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 317 | 5 | 19353 | 1585 | 0.0819 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9351 |  | 2007-03-22 19:51 | 2007-03-22 | 2007-03-22 20:08 | Calculated | O410E | C594-754-792 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 17 | 1575 | 19353 | 26775 | 1.3835 | 0.081383 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9354 |  | 2007-03-23 09:33 | 2007-03-23 | 2007-03-23 14:58 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 325 | 5 | 19353 | 1625 | 0.08397 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9353 |  | 2007-03-23 09:37 | 2007-03-23 | 2007-03-23 14:01 | Calculated | O410E |  |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 1 | 19353 | 264 | 0.01364 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9355 |  | 2007-03-23 09:58 | 2007-03-23 | 2007-03-23 15:06 | Calculated | O410E | LF |  |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 308 | 5 | 19353 | 1540 | 0.07957 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9356 |  | 2007-03-23 10:25 | 2007-03-23 | 2007-03-23 14:45 | Calculated | O410E |  |  |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 260 | 5 | 19353 | 1300 | 0.06717 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9358 |  | 2007-03-23 22:12 | 2007-03-23 | 2007-03-23 22:20 | Calculated | O410E | C180-6143 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 4 | 19353 | 32 | 0.00165 | 0.00020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9359 |  | 2007-03-25 09:59 | 2007-03-25 | 2007-03-25 14:55 | Calculated | O410E |  |  |  | Gravel Scoop 109-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 296 | 17 | 19353 | 5032 | 0.26001 | 0.00087842 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9360 |  | 2007-03-26 09:32 | 2007-03-26 | 2007-03-26 10:53 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 39 | 19353 | 3169 | 0.16375 | 0.0020152 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9364 |  | 2007-03-26 16:46 | 2007-03-26 | 2007-03-26 18:25 | Calculated | O410E | C836 | Drop-Out Fuses |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 72 | 19353 | 7128 | 0.36831 | 0.0037204 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9365 |  | 2007-03-26 17:02 | 2007-03-26 | 2007-03-26 18:14 | Calculated | O410E | L1504 | Single Circuit |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 4 | 19353 | 288 | 0.01488 | 0.00020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9366 |  | 2007-03-27 09:34 | 2007-03-27 | 2007-03-27 13:54 | Calculated | O410E | LF |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 260 | 149 | 19353 | 38740 | 2.0018 | 0.0076991 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9367 |  | 2007-03-27 10:30 | 2007-03-27 | 2007-03-27 12:12 | Calculated | O410E | LF |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 2 | 19353 | 204 | 0.01054 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9368 |  | 2007-03-28 08:10 | 2007-03-28 | 2007-03-28 10:08 | Calculated | O410E | C117 | Single Circuit |  | Maihiihi 111-09 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 98 | 19353 | 11617 | 0.60027 | 0.0050638 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9369 |  | 2007-03-28 10:06 | 2007-03-28 | 2007-03-28 12:20 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 134 | 105 | 19353 | 14070 | 0.72702 | 0.0054255 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9370 |  | 2007-03-28 10:06 | 2007-03-28 | 2007-03-28 16:13 | Calculated | O410E | C417 |  |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 367 | 40 | 19353 | 14680 | 0.75854 | 0.0020669 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9372 |  | 2007-03-29 08:53 | 2007-03-29 | 2007-03-29 14:37 | Calculated | O410E |  |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 344 | 302 | 19353 | 103888 | 5.3681 | 0.015605 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9373 |  | 2007-03-29 09:12 | 2007-03-29 | 2007-03-29 10:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 2 | 19353 | 170 | 0.00878 | 0.00010334 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9374 |  | 2007-03-29 09:48 | 2007-03-29 | 2007-03-29 10:30 | Calculated | O410E | LV |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 44 | 19353 | 1848 | 0.09549 | 0.0022735 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9375 |  | 2007-03-29 10:01 | 2007-03-29 | 2007-03-29 11:41 | Calculated | O410E |  |  |  | Southern 409-09 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 100 | 24 | 19353 | 2400 | 0.12401 | 0.0012401 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9376 |  | 2007-03-29 10:07 | 2007-03-29 | 2007-03-29 13:21 | Calculated | O410E |  |  |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 194 | 5 | 19353 | 970 | 0.05012 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9377 |  | 2007-03-29 12:24 | 2007-03-29 | 2007-03-29 13:20 | Calculated | O410E | LF |  |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 3 | 19353 | 168 | 0.00868 | 0.00015501 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9380 |  | 2007-03-29 15:37 | 2007-03-29 | 2007-03-29 16:08 | Calculated | O410E | L677 | Drop-Out Fuses |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 31 | 8 | 19353 | 248 | 0.01281 | 0.00041337 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9381 |  | 2007-03-29 17:39 | 2007-03-29 | 2007-03-29 18:32 | Calculated | O410E | C118 | Single Circuit |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 259 | 19353 | 13960 | 0.72134 | 0.013383 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9382 |  | 2007-03-29 19:14 | 2007-03-29 | 2007-03-29 19:30 | Calculated | O410E | S193 |  |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 7 | 19353 | 112 | 0.00579 | 0.0003617 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9384 |  | 2007-03-30 06:12 | 2007-03-30 | 2007-03-30 11:13 | Calculated | O410E | C277 | Single Circuit |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 301 | 9 | 19353 | 2709 | 0.13998 | 0.00046504 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9386 |  | 2007-03-30 10:41 | 2007-03-30 | 2007-03-30 15:19 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 278 | 5 | 19353 | 1390 | 0.07182 | 0.00025836 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9387 |  | 2007-03-30 11:09 | 2007-03-30 | 2007-03-30 11:46 | Calculated | O410E | LF | Single Circuit |  |  | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 1 | 19353 | 37 | 0.00191 | 5.1672e-05 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9389 |  | 2007-03-31 07:07 | 2007-03-31 | 2007-03-31 11:52 | Calculated | O410E | C281 |  |  | Ohura 413-03 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 285 | 15 | 19353 | 4275 | 0.2209 | 0.00077507 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9390 |  | 2007-03-31 08:05 | 2007-03-31 | 2007-03-31 11:21 | Calculated | O410E | L579 | Single Circuit |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 13 | 19353 | 2548 | 0.13166 | 0.00067173 | 0 | 0 | 2006/2007 | March-2007 | 3 | 2007
9393 |  | 2007-04-02 15:22 | 2007-04-02 | 2007-04-02 17:41 | Calculated | O410E | L254 | Single Circuit |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 2 | 19353 | 278 | 0.01436 | 0.00010334 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9394 |  | 2007-04-02 16:34 | 2007-04-02 | 2007-04-02 19:40 | Calculated | O410E | L568 | Single Circuit |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 7 | 19353 | 1302 | 0.06728 | 0.0003617 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9396 |  | 2007-04-03 09:30 | 2007-04-03 | 2007-04-03 10:54 | Calculated | O410E | LV |  |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 7 | 19353 | 588 | 0.03038 | 0.0003617 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9397 |  | 2007-04-03 09:39 | 2007-04-03 | 2007-04-03 11:02 | Calculated | O410E |  |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 83 | 39 | 19353 | 3237 | 0.16726 | 0.0020152 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9398 |  | 2007-04-03 10:55 | 2007-04-03 | 2007-04-03 14:00 | Calculated | O410E | LF |  |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 185 | 9 | 19353 | 1665 | 0.08603 | 0.00046504 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9400 |  | 2007-04-05 06:13 | 2007-04-05 | 2007-04-05 08:28 | Calculated | O410E | L356 |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 5 | 19353 | 675 | 0.03488 | 0.00025836 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9401 |  | 2007-04-05 09:42 | 2007-04-05 | 2007-04-05 10:13 | Calculated | O410E | LV |  |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 45 | 19353 | 1395 | 0.07208 | 0.0023252 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9402 |  | 2007-04-05 10:03 | 2007-04-05 | 2007-04-05 14:01 | Calculated | O410E |  |  |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 238 | 15 | 19353 | 3570 | 0.18447 | 0.00077507 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9404 |  | 2007-04-06 10:22 | 2007-04-06 | 2007-04-06 11:36 | Calculated | O410E | L935 | Drop-Out Fuses |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 74 | 33 | 19353 | 2468 | 0.12753 | 0.0017052 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9405 |  | 2007-04-08 19:50 | 2007-04-08 | 2007-04-08 20:35 | Calculated | O410E | L349 | Single Circuit |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 15 | 19353 | 675 | 0.03488 | 0.00077507 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9406 |  | 2007-04-08 20:33 | 2007-04-08 | 2007-04-08 20:40 | Calculated | O410E | LF |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 69 | 19353 | 483 | 0.02496 | 0.0035653 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9408 |  | 2007-04-10 10:20 | 2007-04-10 | 2007-04-10 12:29 | Calculated | O410E | C379 |  |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 25 | 19353 | 3225 | 0.16664 | 0.0012918 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9409 |  | 2007-04-10 12:40 | 2007-04-10 | 2007-04-10 14:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 128 | 2 | 19353 | 256 | 0.01323 | 0.00010334 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9410 |  | 2007-04-11 10:33 | 2007-04-11 | 2007-04-11 13:44 | Calculated | O410E |  |  |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 191 | 10 | 19353 | 1910 | 0.09869 | 0.00051672 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9414 |  | 2007-04-12 09:30 | 2007-04-12 | 2007-04-12 11:12 | Calculated | O410E | C352 |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 25 | 19353 | 2550 | 0.13176 | 0.0012918 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9415 |  | 2007-04-12 09:45 | 2007-04-12 | 2007-04-12 10:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 2 | 19353 | 126 | 0.00651 | 0.00010334 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9416 |  | 2007-04-12 13:49 | 2007-04-12 | 2007-04-12 14:35 | Calculated | O410E | LF | Single Circuit |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 1 | 19353 | 46 | 0.00238 | 5.1672e-05 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9417 |  | 2007-04-12 17:56 | 2007-04-12 | 2007-04-12 18:42 | Calculated | O410E | C352 |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 25 | 19353 | 1150 | 0.05942 | 0.0012918 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9418 |  | 2007-04-12 20:34 | 2007-04-12 | 2007-04-12 20:44 | Calculated | O410E | C2062 |  |  |  | Remote Rural F | Whakamaru 33 | Direct from Whakamaru Supply |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 968 | 19353 | 9680 | 0.50018 | 0.050018 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9419 |  | 2007-04-13 08:27 | 2007-04-13 | 2007-04-13 08:28 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 241 | 19353 | 241 | 0.01245 | 0.012453 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9420 |  | 2007-04-13 10:01 | 2007-04-13 | 2007-04-13 11:49 | Calculated | O410E | C1052 | Single Circuit |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 261 | 19353 | 28422 | 1.4686 | 0.013486 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9421 |  | 2007-04-13 10:10 | 2007-04-13 | 2007-04-13 12:52 | Calculated | O410E | LF |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 162 | 36 | 19353 | 5832 | 0.30135 | 0.0018602 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9423 |  | 2007-04-13 13:34 | 2007-04-13 | 2007-04-13 13:35 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 241 | 19353 | 241 | 0.01245 | 0.012453 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9424 |  | 2007-04-13 13:40 | 2007-04-13 | 2007-04-13 16:07 | Calculated | O410E | C446 | Single Circuit |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 106 | 19353 | 15650 | 0.80866 | 0.0054772 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9425 |  | 2007-04-13 14:50 | 2007-04-13 | 2007-04-13 17:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 159 | 1 | 19353 | 159 | 0.00822 | 5.1672e-05 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9426 |  | 2007-04-13 15:15 | 2007-04-13 | 2007-04-13 19:19 | Calculated | O410E | L455 | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 244 | 30 | 19353 | 7320 | 0.37824 | 0.0015501 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9427 |  | 2007-04-13 18:45 | 2007-04-13 | 2007-04-13 18:46 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 241 | 19353 | 241 | 0.01245 | 0.012453 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9428 |  | 2007-04-15 08:25 | 2007-04-15 | 2007-04-15 11:17 | Calculated | O410E | LV |  |  | Hakiaha 401-01 | Remote Rural F | Hakiaha | Borough Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 19 | 19353 | 3268 | 0.16886 | 0.00098176 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9429 |  | 2007-04-16 10:02 | 2007-04-16 | 2007-04-16 14:11 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 249 | 59 | 19353 | 14691 | 0.75911 | 0.0030486 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9430 |  | 2007-04-16 10:33 | 2007-04-16 | 2007-04-16 15:05 | Calculated | O410E |  |  |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 18 | 19353 | 4896 | 0.25298 | 0.00093009 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9432 |  | 2007-04-17 07:30 | 2007-04-17 | 2007-04-17 10:05 | Calculated | O410E | C379 |  |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 25 | 19353 | 3890 | 0.201 | 0.0012918 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9434 |  | 2007-04-17 12:11 | 2007-04-17 | 2007-04-17 13:19 | Calculated | O410E | L578 | Single Circuit |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 2 | 19353 | 136 | 0.00703 | 0.00010334 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9435 |  | 2007-04-17 16:05 | 2007-04-17 | 2007-04-17 17:48 | Calculated | O410E | C494 |  |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 35 | 19353 | 3605 | 0.18628 | 0.0018085 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9436 |  | 2007-04-18 08:40 | 2007-04-18 | 2007-04-18 10:44 | Calculated | O410E | L1617 | Drop-Out Fuses |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 124 | 2 | 19353 | 248 | 0.01281 | 0.00010334 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9437 |  | 2007-04-18 09:11 | 2007-04-18 | 2007-04-18 10:53 | Calculated | O410E | LF |  |  | Turoa 415-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 29 | 19353 | 2958 | 0.15284 | 0.0014985 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9439 |  | 2007-04-19 05:57 | 2007-04-19 | 2007-04-19 06:45 | Calculated | O410E | L811 |  |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Asset Related | Other |  | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 20 | 19353 | 960 | 0.0496 | 0.0010334 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9440 |  | 2007-04-19 08:49 | 2007-04-19 | 2007-04-19 15:26 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 397 | 1 | 19353 | 397 | 0.02051 | 5.1672e-05 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9441 |  | 2007-04-19 11:30 | 2007-04-19 | 2007-04-19 11:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 28 | 32 | 19353 | 896 | 0.0463 | 0.0016535 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9442 |  | 2007-04-19 12:53 | 2007-04-19 | 2007-04-19 13:53 | Calculated | O410E | LF |  |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 2 | 19353 | 120 | 0.0062 | 0.00010334 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9445 |  | 2007-04-20 10:38 | 2007-04-20 | 2007-04-20 14:20 | Calculated | O410E |  |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 222 | 33 | 19353 | 7326 | 0.37855 | 0.0017052 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9446 |  | 2007-04-20 11:40 | 2007-04-20 | 2007-04-20 13:04 | Calculated | O410E | S351-647 | Drop-Out Fuses |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 84 | 36 | 19353 | 3024 | 0.15625 | 0.0018602 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9447 |  | 2007-04-22 01:37 | 2007-04-22 | 2007-04-22 01:47 | Calculated | O410E | C510 |  |  |  | Remote Rural F | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 673 | 19353 | 6730 | 0.34775 | 0.034775 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9448 |  | 2007-04-23 08:20 | 2007-04-23 | 2007-04-23 13:00 | Calculated | O410E | L726 | Drop-Out Fuses |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 280 | 14 | 19353 | 3920 | 0.20255 | 0.0007234 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9449 |  | 2007-04-23 09:40 | 2007-04-23 | 2007-04-23 10:09 | Calculated | O410E | L557 - C218 | Drop-Out Fuses |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 29 | 70 | 19353 | 2065 | 0.1067 | 0.003617 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9450 |  | 2007-04-23 09:50 | 2007-04-23 | 2007-04-23 11:45 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 115 | 6 | 19353 | 694 | 0.03586 | 0.00031003 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9451 |  | 2007-04-23 10:08 | 2007-04-23 | 2007-04-23 12:37 | Calculated | O410E | LF |  |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 3 | 19353 | 447 | 0.0231 | 0.00015501 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9452 |  | 2007-04-23 11:14 | 2007-04-23 | 2007-04-23 11:38 | Calculated | O410E | LF |  |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 1 | 19353 | 24 | 0.00124 | 5.1672e-05 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9453 |  | 2007-04-24 09:44 | 2007-04-24 | 2007-04-24 11:58 | Calculated | O410E | LF |  |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 134 | 3 | 19353 | 402 | 0.02077 | 0.00015501 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9455 |  | 2007-04-24 22:44 | 2007-04-24 | 2007-04-24 22:53 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 3 | 19353 | 27 | 0.0014 | 0.00015501 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9456 |  | 2007-04-26 10:00 | 2007-04-26 | 2007-04-26 14:32 | Calculated | O410E | LF |  |  | Maihiihi 111-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 5 | 19353 | 1360 | 0.07027 | 0.00025836 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9458 |  | 2007-04-26 19:40 | 2007-04-26 | 2007-04-26 23:12 | Calculated | O410E | C494 |  |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 212 | 35 | 19353 | 7444 | 0.38464 | 0.0018085 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9459 |  | 2007-04-27 08:12 | 2007-04-27 | 2007-04-27 09:15 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 3 | 19353 | 189 | 0.00977 | 0.00015501 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9460 |  | 2007-04-27 14:07 | 2007-04-27 | 2007-04-27 15:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-07 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 78 | 3 | 19353 | 234 | 0.01209 | 0.00015501 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9461 |  | 2007-04-27 17:17 | 2007-04-27 | 2007-04-27 18:46 | Calculated | O410E | L686 | Single Circuit |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 10 | 19353 | 890 | 0.04599 | 0.00051672 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9462 |  | 2007-04-28 04:14 | 2007-04-28 | 2007-04-28 12:00 | Calculated | O410E | C594 |  |  | Western 403-04 | Remote Rural F | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 466 | 22 | 19353 | 10252 | 0.52974 | 0.0011368 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9463 |  | 2007-04-28 08:12 | 2007-04-28 | 2007-04-28 09:20 | Calculated | O410E | L936 | Drop-Out Fuses |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 68 | 27 | 19353 | 1836 | 0.09487 | 0.0013951 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9464 |  | 2007-04-28 16:17 | 2007-04-28 | 2007-04-28 17:38 | Calculated | O410E | C429 | Single Circuit |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 24 | 19353 | 1962 | 0.10138 | 0.0012401 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9465 |  | 2007-04-29 19:36 | 2007-04-29 | 2007-04-29 19:44 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 3 | 19353 | 24 | 0.00124 | 0.00015501 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9466 |  | 2007-04-30 10:11 | 2007-04-30 | 2007-04-30 12:44 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 8 | 19353 | 1224 | 0.06325 | 0.00041337 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9467 |  | 2007-04-30 10:50 | 2007-04-30 | 2007-04-30 11:51 | Calculated | O410E | LF |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 2 | 19353 | 122 | 0.0063 | 0.00010334 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9469 |  | 2007-04-30 13:15 | 2007-04-30 | 2007-04-30 17:13 | Calculated | O410E | C490 |  |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 238 | 47 | 19353 | 11223 | 0.57991 | 0.0024286 | 0 | 0 | 2007/2008 | April-2007 | 4 | 2007
9470 |  | 2007-05-01 12:08 | 2007-05-01 | 2007-05-01 12:58 | Calculated | O410E | C127-S339 | Single Circuit |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 85 | 19353 | 4250 | 0.2196 | 0.0043921 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9471 |  | 2007-05-02 11:14 | 2007-05-02 | 2007-05-02 13:11 | Calculated | O410E | LF |  |  | Te Mapara 117-05 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 3 | 19353 | 351 | 0.01814 | 0.00015501 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9472 |  | 2007-05-02 12:18 | 2007-05-02 | 2007-05-02 13:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 69 | 32 | 19353 | 2208 | 0.11409 | 0.0016535 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9474 |  | 2007-05-02 22:41 | 2007-05-02 | 2007-05-02 23:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 27 | 38 | 19353 | 1026 | 0.05302 | 0.0019635 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9475 |  | 2007-05-03 02:53 | 2007-05-03 | 2007-05-03 03:03 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1 | 19353 | 10 | 0.00052 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9476 |  | 2007-05-03 07:02 | 2007-05-03 | 2007-05-03 07:37 | Calculated | O410E | LF |  |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 35 | 5 | 19353 | 175 | 0.00904 | 0.00025836 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9478 |  | 2007-05-03 10:35 | 2007-05-03 | 2007-05-03 14:25 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 230 | 16 | 19353 | 3680 | 0.19015 | 0.00082675 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9479 |  | 2007-05-03 13:50 | 2007-05-03 | 2007-05-03 14:42 | Calculated | O410E | LF | Drop-Out Fuses |  | Manunui 408-01 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 52 | 45 | 19353 | 2340 | 0.12091 | 0.0023252 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9481 |  | 2007-05-04 09:01 | 2007-05-04 | 2007-05-04 09:52 | Calculated | O410E | LF |  |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 1 | 19353 | 51 | 0.00264 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9482 |  | 2007-05-04 09:31 | 2007-05-04 | 2007-05-04 10:56 | Calculated | O410E |  |  |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 85 | 34 | 19353 | 2890 | 0.14933 | 0.0017568 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9483 |  | 2007-05-04 13:48 | 2007-05-04 | 2007-05-04 14:36 | Calculated | O410E | C1126 | Single Circuit |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 19 | 19353 | 912 | 0.04712 | 0.00098176 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9484 |  | 2007-05-06 08:04 | 2007-05-06 | 2007-05-06 09:31 | Calculated | O410E | C415 |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 25 | 19353 | 2175 | 0.11239 | 0.0012918 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9485 |  | 2007-05-06 19:12 | 2007-05-06 | 2007-05-06 20:42 | Calculated | O410E | LF | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 90 | 41 | 19353 | 3690 | 0.19067 | 0.0021185 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9486 |  | 2007-05-07 10:10 | 2007-05-07 | 2007-05-07 14:41 | Calculated | O410E |  |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 17 | 19353 | 4607 | 0.23805 | 0.00087842 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9488 |  | 2007-05-07 10:30 | 2007-05-07 | 2007-05-07 13:13 | Calculated | O410E |  |  |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 163 | 18 | 19353 | 2934 | 0.1516 | 0.00093009 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9489 |  | 2007-05-07 14:08 | 2007-05-07 | 2007-05-07 15:00 | Calculated | O410E | LF |  |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 19353 | 104 | 0.00537 | 0.00010334 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9491 |  | 2007-05-08 10:06 | 2007-05-08 | 2007-05-08 11:22 | Calculated | O410E | LF | Single Circuit |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | OH Lines : Surge Diverters | Weather | Lightning |  | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 1 | 19353 | 76 | 0.00393 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9492 |  | 2007-05-08 13:34 | 2007-05-08 | 2007-05-08 14:29 | Calculated | O410E |  |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 9 | 19353 | 495 | 0.02558 | 0.00046504 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9493 |  | 2007-05-09 09:05 | 2007-05-09 | 2007-05-09 09:41 | Calculated | O410E |  |  |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 17 | 19353 | 612 | 0.03162 | 0.00087842 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9494 |  | 2007-05-09 09:07 | 2007-05-09 | 2007-05-09 11:35 | Calculated | O410E |  |  |  | Caves 101-11 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 17 | 19353 | 2516 | 0.13001 | 0.00087842 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9496 |  | 2007-05-09 10:11 | 2007-05-09 | 2007-05-09 10:34 | Calculated | O410E | LF |  |  | Southern 409-09 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 23 | 1 | 19353 | 23 | 0.00119 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9499 |  | 2007-05-10 10:07 | 2007-05-10 | 2007-05-10 15:09 | Calculated | O410E | LF |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 19 | 19353 | 5738 | 0.29649 | 0.00098176 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9501 |  | 2007-05-10 16:12 | 2007-05-10 | 2007-05-10 17:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 81 | 1 | 19353 | 81 | 0.00419 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9502 |  | 2007-05-10 18:50 | 2007-05-10 | 2007-05-10 19:22 | Calculated | O410E | C103 | Main Protection |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Miscellaneous : Battery Cells | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 1119 | 19353 | 36162 | 1.8685 | 0.05782 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9503 |  | 2007-05-11 10:18 | 2007-05-11 | 2007-05-11 13:00 | Calculated | O410E |  |  |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 162 | 15 | 19353 | 2430 | 0.12556 | 0.00077507 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9504 |  | 2007-05-11 14:05 | 2007-05-11 | 2007-05-11 14:53 | Calculated | O410E | LF | Pole Mounted |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 2 | 19353 | 96 | 0.00496 | 0.00010334 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9505 |  | 2007-05-12 08:56 | 2007-05-12 | 2007-05-12 09:58 | Calculated | O410E | C212 | Single Circuit |  |  | Remote Rural F | National Park | National Park Zone Substation | OH Lines : Conductor - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 554 | 19353 | 34384 | 1.7767 | 0.028626 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9506 |  | 2007-05-12 18:33 | 2007-05-12 | 2007-05-12 19:22 | Calculated | O410E | S306 - 322 | Drop-Out Fuses |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 49 | 101 | 19353 | 4949 | 0.25572 | 0.0052188 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9507 |  | 2007-05-14 14:10 | 2007-05-14 | 2007-05-14 16:27 | Calculated | O410E | L586 | Drop-Out Fuses |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 137 | 1 | 19353 | 137 | 0.00708 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9508 |  | 2007-05-14 23:27 | 2007-05-14 | 2007-05-14 23:44 | Calculated | O410E | C1102 | Single Circuit |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply | OH Lines : Pole - Softwood | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 17 | 1931 | 19353 | 33309 | 1.7211 | 0.099778 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9509 |  | 2007-05-15 09:34 | 2007-05-15 | 2007-05-15 15:21 | Calculated | O410E |  |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 347 | 11 | 19353 | 3817 | 0.19723 | 0.00056839 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9510 |  | 2007-05-15 10:02 | 2007-05-15 | 2007-05-15 13:28 | Calculated | O410E |  |  |  | Tihoi 124-02 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 206 | 18 | 19353 | 3708 | 0.1916 | 0.00093009 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9512 |  | 2007-05-16 08:35 | 2007-05-16 | 2007-05-16 12:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 242 | 2 | 19353 | 484 | 0.02501 | 0.00010334 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9513 |  | 2007-05-16 09:02 | 2007-05-16 | 2007-05-16 09:47 | Calculated | O410E | LF |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 2 | 19353 | 90 | 0.00465 | 0.00010334 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9514 |  | 2007-05-16 09:30 | 2007-05-16 | 2007-05-16 12:07 | Calculated | O410E |  |  |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 157 | 106 | 19353 | 16733 | 0.86462 | 0.0054772 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9515 |  | 2007-05-16 10:53 | 2007-05-16 | 2007-05-16 14:09 | Calculated | O410E | C779 | Single Circuit |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 42 | 19353 | 8253 | 0.42645 | 0.0021702 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9516 |  | 2007-05-16 12:57 | 2007-05-16 | 2007-05-16 13:52 | Calculated | O410E | C147 | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 55 | 27 | 19353 | 1485 | 0.07673 | 0.0013951 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9517 |  | 2007-05-17 07:45 | 2007-05-17 | 2007-05-17 09:43 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 118 | 1 | 19353 | 118 | 0.0061 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9518 |  | 2007-05-17 10:01 | 2007-05-17 | 2007-05-17 14:37 | Calculated | O410E |  |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 276 | 11 | 19353 | 3036 | 0.15687 | 0.00056839 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9519 |  | 2007-05-17 10:12 | 2007-05-17 | 2007-05-17 10:40 | Calculated | O410E | LF |  |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 2 | 19353 | 56 | 0.00289 | 0.00010334 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9520 |  | 2007-05-18 10:03 | 2007-05-18 | 2007-05-18 14:45 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 4 | 19353 | 1128 | 0.05829 | 0.00020669 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9521 |  | 2007-05-18 11:36 | 2007-05-18 | 2007-05-18 13:55 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 1 | 19353 | 139 | 0.00718 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9522 |  | 2007-05-20 14:09 | 2007-05-20 | 2007-05-20 16:15 | Calculated | O410E | LF | Pole Mounted |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Transformers : Internal Connections | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 2 | 19353 | 252 | 0.01302 | 0.00010334 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9523 |  | 2007-05-21 02:31 | 2007-05-21 | 2007-05-21 05:35 | Calculated | O410E | C1620 | Single Circuit |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Stay Wire | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 176 | 19353 | 32460 | 1.6773 | 0.0090942 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9524 |  | 2007-05-21 09:30 | 2007-05-21 | 2007-05-21 16:04 | Calculated | O410E |  |  |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 394 | 3 | 19353 | 1182 | 0.06108 | 0.00015501 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9525 |  | 2007-05-21 15:12 | 2007-05-21 | 2007-05-21 16:33 | Calculated | O410E | L744 | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 81 | 4 | 19353 | 324 | 0.01674 | 0.00020669 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9526 |  | 2007-05-22 10:18 | 2007-05-22 | 2007-05-22 14:22 | Calculated | O410E |  |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 244 | 21 | 19353 | 5124 | 0.26477 | 0.0010851 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9527 |  | 2007-05-22 11:40 | 2007-05-22 | 2007-05-22 14:43 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 183 | 1 | 19353 | 183 | 0.00946 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9528 |  | 2007-05-22 14:00 | 2007-05-22 | 2007-05-22 15:34 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 1 | 19353 | 94 | 0.00486 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9529 |  | 2007-05-23 09:02 | 2007-05-23 | 2007-05-23 12:15 | Calculated | O410E |  |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 193 | 25 | 19353 | 4825 | 0.24932 | 0.0012918 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9530 |  | 2007-05-23 09:32 | 2007-05-23 | 2007-05-23 12:22 | Calculated | O410E | LF |  |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 170 | 3 | 19353 | 510 | 0.02635 | 0.00015501 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9531 |  | 2007-05-23 10:25 | 2007-05-23 | 2007-05-23 13:21 | Calculated | O410E | LF | Drop-Out Fuses |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 176 | 1 | 19353 | 176 | 0.00909 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9532 |  | 2007-05-23 20:12 | 2007-05-23 | 2007-05-23 20:57 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-04 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 45 | 1 | 19353 | 45 | 0.00233 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9533 |  | 2007-05-24 09:37 | 2007-05-24 | 2007-05-24 15:33 | Calculated | O410E |  |  |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 5 | 19353 | 1780 | 0.09198 | 0.00025836 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9535 |  | 2007-05-24 15:10 | 2007-05-24 | 2007-05-24 16:11 | Calculated | O410E | LF |  |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 1 | 19353 | 61 | 0.00315 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9536 |  | 2007-05-24 20:17 | 2007-05-24 | 2007-05-24 21:44 | Calculated | O410E | L232 | Drop-Out Fuses |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 87 | 1 | 19353 | 87 | 0.0045 | 5.1672e-05 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9537 |  | 2007-05-25 09:37 | 2007-05-25 | 2007-05-25 15:11 | Calculated | O410E |  |  |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 334 | 5 | 19353 | 1670 | 0.08629 | 0.00025836 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9539 |  | 2007-05-25 16:14 | 2007-05-25 | 2007-05-25 17:52 | Calculated | O410E | L332 | Single Circuit |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Crossarm - Wood | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 2 | 19353 | 196 | 0.01013 | 0.00010334 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9540 |  | 2007-05-26 21:20 | 2007-05-26 | 2007-05-26 21:28 | Calculated | O410E | C2092 |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 105 | 19353 | 840 | 0.0434 | 0.0054255 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9542 |  | 2007-05-28 09:05 | 2007-05-28 | 2007-05-28 12:55 | Calculated | O410E | LV |  |  | Hakiaha 401-01 | Remote Rural F | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 230 | 3 | 19353 | 690 | 0.03565 | 0.00015501 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9544 |  | 2007-05-28 19:20 | 2007-05-28 | 2007-05-28 20:53 | Calculated | O410E | L764 | Drop-Out Fuses |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 8 | 19353 | 744 | 0.03844 | 0.00041337 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9545 |  | 2007-05-29 10:03 | 2007-05-29 | 2007-05-29 14:00 | Calculated | O410E |  |  |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 237 | 17 | 19353 | 4029 | 0.20818 | 0.00087842 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9546 |  | 2007-05-29 10:03 | 2007-05-29 | 2007-05-29 14:29 | Calculated | O410E |  |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 266 | 13 | 19353 | 3458 | 0.17868 | 0.00067173 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9547 |  | 2007-05-29 10:57 | 2007-05-29 | 2007-05-29 15:03 | Calculated | O410E | LV |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 246 | 2 | 19353 | 492 | 0.02542 | 0.00010334 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9548 |  | 2007-05-30 09:33 | 2007-05-30 | 2007-05-30 14:51 | Calculated | O410E |  |  |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 318 | 6 | 19353 | 1908 | 0.09859 | 0.00031003 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9549 |  | 2007-05-30 10:01 | 2007-05-30 | 2007-05-30 12:40 | Calculated | O410E | LV |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 159 | 37 | 19353 | 5883 | 0.30398 | 0.0019118 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9553 |  | 2007-05-31 13:19 | 2007-05-31 | 2007-05-31 13:20 | Calculated | O410E |  |  |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 3 | 19353 | 3 | 0.00016 | 0.00015501 | 1 | 3 | 2007/2008 | May-2007 | 5 | 2007
9554 |  | 2007-05-31 17:41 | 2007-05-31 | 2007-05-31 17:47 | Calculated | O410E | C2092 |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 105 | 19353 | 630 | 0.03255 | 0.0054255 | 0 | 0 | 2007/2008 | May-2007 | 5 | 2007
9555 |  | 2007-06-01 09:16 | 2007-06-01 | 2007-06-01 14:52 | Calculated | O410E | LV |  |  | Southern 409-04 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 336 | 65 | 19353 | 21840 | 1.1285 | 0.0033587 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9556 |  | 2007-06-01 09:34 | 2007-06-01 | 2007-06-01 15:05 | Calculated | O410E |  |  |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 331 | 6 | 19353 | 1986 | 0.10262 | 0.00031003 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9557 |  | 2007-06-01 10:10 | 2007-06-01 | 2007-06-01 11:12 | Calculated | O410E | LF |  |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 62 | 4 | 19353 | 248 | 0.01281 | 0.00020669 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9559 |  | 2007-06-04 01:14 | 2007-06-04 | 2007-06-04 03:10 | Calculated | O410E | L252 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 116 | 6 | 19353 | 696 | 0.03596 | 0.00031003 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9558 |  | 2007-06-04 03:40 | 2007-06-04 | 2007-06-04 08:33 | Calculated | O410E | C949 |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 293 | 1 | 19353 | 293 | 0.01514 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9562 |  | 2007-06-05 08:50 | 2007-06-05 | 2007-06-05 09:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 36 | 1 | 19353 | 36 | 0.00186 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9560 |  | 2007-06-05 09:17 | 2007-06-05 | 2007-06-05 10:41 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 20 | 19353 | 1680 | 0.08681 | 0.0010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9561 |  | 2007-06-05 09:24 | 2007-06-05 | 2007-06-05 10:05 | Calculated | O410E |  |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 20 | 19353 | 820 | 0.04237 | 0.0010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9563 |  | 2007-06-05 10:15 | 2007-06-05 | 2007-06-05 11:53 | Calculated | O410E | LF |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 98 | 4 | 19353 | 392 | 0.02026 | 0.00020669 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9564 |  | 2007-06-05 14:58 | 2007-06-05 | 2007-06-05 17:05 | Calculated | O410E | L256 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 5 | 19353 | 635 | 0.03281 | 0.00025836 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9565 |  | 2007-06-05 21:09 | 2007-06-05 | 2007-06-05 21:28 | Calculated | O410E | C1512 |  |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 140 | 19353 | 2660 | 0.13745 | 0.007234 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9566 |  | 2007-06-05 21:24 | 2007-06-05 | 2007-06-05 22:06 | Calculated | O410E | LF |  |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 2 | 19353 | 84 | 0.00434 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9567 |  | 2007-06-06 07:30 | 2007-06-06 | 2007-06-06 11:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Hangatiki East 102-03 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 218 | 2 | 19353 | 436 | 0.02253 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9569 |  | 2007-06-07 08:41 | 2007-06-07 | 2007-06-07 09:16 | Calculated | O410E | LF |  |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 35 | 1 | 19353 | 35 | 0.00181 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9570 |  | 2007-06-07 10:00 | 2007-06-07 | 2007-06-07 14:02 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 242 | 25 | 19353 | 6050 | 0.31261 | 0.0012918 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9571 |  | 2007-06-07 10:01 | 2007-06-07 | 2007-06-07 10:17 | Calculated | O410E | S408-465-489 | Single Circuit |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation | OH Lines : Other | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 8 | 19353 | 128 | 0.00661 | 0.00041337 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9573 |  | 2007-06-07 11:12 | 2007-06-07 | 2007-06-07 12:44 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 16 | 19353 | 1472 | 0.07606 | 0.00082675 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9574 |  | 2007-06-07 11:56 | 2007-06-07 | 2007-06-07 13:43 | Calculated | O410E | L1526 | Single Circuit |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 62 | 19353 | 6634 | 0.34279 | 0.0032036 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9575 |  | 2007-06-07 12:06 | 2007-06-07 | 2007-06-07 12:08 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 241 | 19353 | 482 | 0.02491 | 0.012453 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9578 |  | 2007-06-08 09:34 | 2007-06-08 | 2007-06-08 14:32 | Calculated | O410E |  |  |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 298 | 5 | 19353 | 1490 | 0.07699 | 0.00025836 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9577 |  | 2007-06-08 09:36 | 2007-06-08 | 2007-06-08 10:18 | Calculated | O410E |  |  |  | Nihoniho 412-02 | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 12 | 19353 | 504 | 0.02604 | 0.00062006 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9581 |  | 2007-06-08 13:35 | 2007-06-08 | 2007-06-08 15:33 | Calculated | O410E | S1516 | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 118 | 118 | 19353 | 13924 | 0.71948 | 0.0060972 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9582 |  | 2007-06-08 15:01 | 2007-06-08 | 2007-06-08 15:31 | Calculated | O410E | LF |  |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 3 | 19353 | 90 | 0.00465 | 0.00015501 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9584 |  | 2007-06-09 18:00 | 2007-06-09 | 2007-06-09 20:04 | Calculated | O410E | C949 |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 1 | 19353 | 124 | 0.00641 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9588 |  | 2007-06-10 09:29 | 2007-06-10 | 2007-06-10 11:17 | Calculated | O410E | C571 | Sectionaliser |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Mechanism | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 108 | 6 | 19353 | 648 | 0.03348 | 0.00031003 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9587 |  | 2007-06-10 09:56 | 2007-06-10 | 2007-06-10 10:41 | Calculated | O410E | C949 |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 1 | 19353 | 45 | 0.00233 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9590 |  | 2007-06-11 11:06 | 2007-06-11 | 2007-06-11 15:09 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 243 | 105 | 19353 | 25515 | 1.3184 | 0.0054255 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9591 |  | 2007-06-12 09:24 | 2007-06-12 | 2007-06-12 15:36 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 372 | 93 | 19353 | 34596 | 1.7876 | 0.0048055 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9592 |  | 2007-06-12 09:32 | 2007-06-12 | 2007-06-12 14:46 | Calculated | O410E |  |  |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 314 | 121 | 19353 | 38096 | 1.9685 | 0.0062523 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9594 |  | 2007-06-12 13:30 | 2007-06-12 | 2007-06-12 15:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 116 | 1 | 19353 | 116 | 0.00599 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9593 |  | 2007-06-12 14:49 | 2007-06-12 | 2007-06-12 15:04 | Calculated | O410E | LF |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 4 | 19353 | 60 | 0.0031 | 0.00020669 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9595 |  | 2007-06-12 18:03 | 2007-06-12 | 2007-06-12 19:00 | Calculated | O410E | C949 |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 1 | 19353 | 57 | 0.00295 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9596 |  | 2007-06-13 09:01 | 2007-06-13 | 2007-06-13 10:16 | Calculated | O410E | LF |  |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9597 |  | 2007-06-13 11:00 | 2007-06-13 | 2007-06-13 12:29 | Calculated | O410E |  |  |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 89 | 24 | 19353 | 2136 | 0.11037 | 0.0012401 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9598 |  | 2007-06-14 09:02 | 2007-06-14 | 2007-06-14 16:17 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 435 | 69 | 19353 | 30015 | 1.5509 | 0.0035653 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9600 |  | 2007-06-14 10:00 | 2007-06-14 | 2007-06-14 14:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 245 | 5 | 19353 | 1225 | 0.0633 | 0.00025836 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9599 |  | 2007-06-14 10:03 | 2007-06-14 | 2007-06-14 14:57 | Calculated | O410E |  |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 5 | 19353 | 1470 | 0.07596 | 0.00025836 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9601 |  | 2007-06-14 14:30 | 2007-06-14 | 2007-06-14 15:00 | Calculated | O410E | L1.27 | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 30 | 5 | 19353 | 150 | 0.00775 | 0.00025836 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9602 |  | 2007-06-15 09:46 | 2007-06-15 | 2007-06-15 13:27 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 5 | 19353 | 1105 | 0.0571 | 0.00025836 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9604 |  | 2007-06-15 10:32 | 2007-06-15 | 2007-06-15 11:56 | Calculated | O410E | LF | Pole Mounted |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 1 | 19353 | 84 | 0.00434 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9605 |  | 2007-06-15 16:59 | 2007-06-15 | 2007-06-15 17:53 | Calculated | O410E | C949 |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 19353 | 54 | 0.00279 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9607 |  | 2007-06-17 16:14 | 2007-06-17 | 2007-06-17 16:42 | Calculated | O410E | L499 | Drop-Out Fuses |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 28 | 5 | 19353 | 140 | 0.00723 | 0.00025836 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9609 |  | 2007-06-19 14:22 | 2007-06-19 | 2007-06-19 15:24 | Calculated | O410E | L655 | Drop-Out Fuses |  | Piopio 116-02 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 62 | 1 | 19353 | 62 | 0.0032 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9610 |  | 2007-06-20 12:36 | 2007-06-20 | 2007-06-20 13:08 | Calculated | O410E | C513 | Single Circuit |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | OH Lines : Joint - Compression / Tension | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 411 | 19353 | 13425 | 0.69369 | 0.021237 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9611 |  | 2007-06-20 13:15 | 2007-06-20 | 2007-06-20 16:26 | Calculated | O410E | L1539 | Drop-Out Fuses |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 191 | 7 | 19353 | 1337 | 0.06908 | 0.0003617 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9612 |  | 2007-06-20 15:25 | 2007-06-20 | 2007-06-20 16:40 | Calculated | O410E | L1.27 | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 6 | 19353 | 450 | 0.02325 | 0.00031003 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9613 |  | 2007-06-20 16:15 | 2007-06-20 | 2007-06-20 17:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 2 | 19353 | 192 | 0.00992 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9614 |  | 2007-06-20 17:14 | 2007-06-20 | 2007-06-20 17:16 | Calculated | O410E | C5200 |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 765 | 19353 | 1734 | 0.0896 | 0.039529 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9615 |  | 2007-06-20 19:29 | 2007-06-20 | 2007-06-20 20:21 | Calculated | O410E | L775 | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 52 | 18 | 19353 | 936 | 0.04836 | 0.00093009 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9616 |  | 2007-06-21 10:02 | 2007-06-21 | 2007-06-21 14:18 | Calculated | O410E |  |  |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 256 | 6 | 19353 | 1536 | 0.07937 | 0.00031003 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9617 |  | 2007-06-21 10:54 | 2007-06-21 | 2007-06-21 12:45 | Calculated | O410E | LF |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 111 | 2 | 19353 | 222 | 0.01147 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9618 |  | 2007-06-21 15:31 | 2007-06-21 | 2007-06-21 22:40 | Calculated | O410E | C287 |  |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 429 | 31 | 19353 | 13320 | 0.68827 | 0.0016018 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9619 |  | 2007-06-21 17:12 | 2007-06-21 | 2007-06-21 18:52 | Calculated | O410E | L319 | Drop-Out Fuses |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 100 | 6 | 19353 | 600 | 0.031 | 0.00031003 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9622 |  | 2007-06-21 19:35 | 2007-06-21 | 2007-06-22 07:40 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 725 | 3 | 19353 | 2175 | 0.11239 | 0.00015501 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9623 |  | 2007-06-22 06:32 | 2007-06-22 | 2007-06-22 08:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 138 | 1 | 19353 | 138 | 0.00713 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9624 |  | 2007-06-22 08:16 | 2007-06-22 | 2007-06-22 09:59 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 103 | 4 | 19353 | 412 | 0.02129 | 0.00020669 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9625 |  | 2007-06-22 08:21 | 2007-06-22 | 2007-06-22 10:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 113 | 2 | 19353 | 226 | 0.01168 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9626 |  | 2007-06-22 08:37 | 2007-06-22 | 2007-06-22 11:35 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 178 | 1 | 19353 | 178 | 0.0092 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9627 |  | 2007-06-22 09:07 | 2007-06-22 | 2007-06-22 12:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 185 | 1 | 19353 | 185 | 0.00956 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9628 |  | 2007-06-22 09:46 | 2007-06-22 | 2007-06-22 13:39 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 233 | 2 | 19353 | 467 | 0.02413 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9629 |  | 2007-06-22 10:14 | 2007-06-22 | 2007-06-22 13:57 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-01 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 223 | 1 | 19353 | 223 | 0.01152 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9630 |  | 2007-06-22 10:23 | 2007-06-22 | 2007-06-22 14:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 235 | 2 | 19353 | 470 | 0.02429 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9631 |  | 2007-06-22 12:50 | 2007-06-22 | 2007-06-22 12:51 | Calculated | O410E | C798 & 1010 | Single Circuit |  |  | Remote Rural F | Wairere / Mahoenui 33 | Wairere Zone Substation | OH Lines : Pole - Hardwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2007/2008 | June-2007 | 6 | 2007
9632 |  | 2007-06-22 22:06 | 2007-06-22 | 2007-06-22 22:15 | Calculated | O410E | C202 | Drop-Out Fuses |  |  | Remote Rural F | Nihoniho | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 9 | 321 | 19353 | 2889 | 0.14928 | 0.016587 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9633 |  | 2007-06-22 23:19 | 2007-06-22 | 2007-06-23 05:56 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 397 | 3 | 19353 | 1191 | 0.06154 | 0.00015501 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9634 |  | 2007-06-22 23:22 | 2007-06-22 | 2007-06-22 23:29 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 42 | 19353 | 294 | 0.01519 | 0.0021702 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9635 |  | 2007-06-23 08:22 | 2007-06-23 | 2007-06-23 11:19 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 177 | 1 | 19353 | 177 | 0.00915 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9636 |  | 2007-06-23 09:11 | 2007-06-23 | 2007-06-23 11:32 | Calculated | O410E | L1.27 | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 141 | 6 | 19353 | 846 | 0.04371 | 0.00031003 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9637 |  | 2007-06-23 12:07 | 2007-06-23 | 2007-06-23 15:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 199 | 2 | 19353 | 398 | 0.02057 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9638 |  | 2007-06-23 12:18 | 2007-06-23 | 2007-06-23 16:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 225 | 2 | 19353 | 450 | 0.02325 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9639 |  | 2007-06-23 12:37 | 2007-06-23 | 2007-06-23 16:59 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 262 | 1 | 19353 | 262 | 0.01354 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9640 |  | 2007-06-23 12:49 | 2007-06-23 | 2007-06-23 15:33 | Calculated | O410E | C714 & 411 | Single Circuit |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Insulator - Pin | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 101 | 19353 | 16607 | 0.85811 | 0.0052188 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9641 |  | 2007-06-23 14:02 | 2007-06-23 | 2007-06-23 16:27 | Calculated | O410E | L478 | Drop-Out Fuses |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 145 | 9 | 19353 | 1305 | 0.06743 | 0.00046504 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9642 |  | 2007-06-23 20:25 | 2007-06-23 | 2007-06-23 20:35 | Calculated | O410E | C5200 |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 765 | 19353 | 7650 | 0.39529 | 0.039529 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9643 |  | 2007-06-25 14:58 | 2007-06-25 | 2007-06-25 16:42 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 104 | 1 | 19353 | 104 | 0.00537 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9644 |  | 2007-06-26 10:01 | 2007-06-26 | 2007-06-26 14:21 | Calculated | O410E |  |  |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 260 | 8 | 19353 | 2080 | 0.10748 | 0.00041337 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9646 |  | 2007-06-26 11:12 | 2007-06-26 | 2007-06-26 11:28 | Calculated | O410E | LF |  |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 3 | 19353 | 48 | 0.00248 | 0.00015501 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9647 |  | 2007-06-26 11:50 | 2007-06-26 | 2007-06-26 12:55 | Calculated | O410E | LF |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 4 | 19353 | 260 | 0.01343 | 0.00020669 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9648 |  | 2007-06-26 14:59 | 2007-06-26 | 2007-06-26 16:19 | Calculated | O410E | S1313 | Drop-Out Fuses |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 80 | 17 | 19353 | 1360 | 0.07027 | 0.00087842 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9650 |  | 2007-06-27 10:02 | 2007-06-27 | 2007-06-27 14:20 | Calculated | O410E |  |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 33 | 19353 | 8514 | 0.43993 | 0.0017052 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9653 |  | 2007-06-28 10:03 | 2007-06-28 | 2007-06-28 13:05 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 182 | 20 | 19353 | 3640 | 0.18808 | 0.0010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9654 |  | 2007-06-29 10:00 | 2007-06-29 | 2007-06-29 11:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 111 | 1 | 19353 | 111 | 0.00574 | 5.1672e-05 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9655 |  | 2007-06-29 13:00 | 2007-06-29 | 2007-06-29 14:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 2 | 19353 | 192 | 0.00992 | 0.00010334 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9656 |  | 2007-06-29 16:25 | 2007-06-29 | 2007-06-30 10:24 | Calculated | O410E | C591 | Single Circuit |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation | OH Lines : Surge Diverters | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1079 | 48 | 19353 | 51792 | 2.6762 | 0.0024802 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9657 |  | 2007-06-30 11:30 | 2007-06-30 | 2007-06-30 14:57 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 207 | 4 | 19353 | 828 | 0.04278 | 0.00020669 | 0 | 0 | 2007/2008 | June-2007 | 6 | 2007
9658 |  | 2007-07-02 10:06 | 2007-07-02 | 2007-07-02 10:52 | Calculated | O410E | LF |  |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 1 | 19353 | 46 | 0.00238 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9659 |  | 2007-07-02 13:00 | 2007-07-02 | 2007-07-02 13:57 | Calculated | O410E | C963 | Single Circuit |  | Rangipo / Hautu 424-03 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 22 | 19353 | 1254 | 0.0648 | 0.0011368 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9660 |  | 2007-07-03 09:34 | 2007-07-03 | 2007-07-03 15:24 | Calculated | O410E |  |  |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 350 | 5 | 19353 | 1750 | 0.09043 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9661 |  | 2007-07-03 12:00 | 2007-07-03 | 2007-07-03 13:23 | Calculated | O410E | L256 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 83 | 5 | 19353 | 415 | 0.02144 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9662 |  | 2007-07-03 15:11 | 2007-07-03 | 2007-07-03 15:21 | Calculated | O410E | C118 |  |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 259 | 19353 | 2590 | 0.13383 | 0.013383 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9663 |  | 2007-07-04 09:33 | 2007-07-04 | 2007-07-04 11:57 | Calculated | O410E |  |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 144 | 23 | 19353 | 3323 | 0.1717 | 0.0011884 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9664 |  | 2007-07-04 09:49 | 2007-07-04 | 2007-07-04 11:37 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 121 | 19353 | 13068 | 0.67524 | 0.0062523 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9665 |  | 2007-07-05 10:03 | 2007-07-05 | 2007-07-05 13:17 | Calculated | O410E |  |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 194 | 1 | 19353 | 194 | 0.01002 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9666 |  | 2007-07-05 11:55 | 2007-07-05 | 2007-07-05 14:36 | Calculated | O410E | C1343 |  |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 83 | 19353 | 13439 | 0.69441 | 0.0042887 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9668 |  | 2007-07-05 20:15 | 2007-07-05 | 2007-07-06 01:36 | Calculated | O410E | C494 | Single Circuit |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 321 | 35 | 19353 | 11268 | 0.58224 | 0.0018085 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9669 |  | 2007-07-05 20:27 | 2007-07-05 | 2007-07-06 03:20 | Calculated | O410E | C237 | Single Circuit |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation | OH Lines : Insulator - Pin | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 413 | 22 | 19353 | 9086 | 0.46949 | 0.0011368 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9670 |  | 2007-07-05 21:00 | 2007-07-05 | 2007-07-06 | Calculated | O410E | L433 | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 180 | 9 | 19353 | 1620 | 0.08371 | 0.00046504 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9671 |  | 2007-07-06 | 2007-07-06 | 2007-07-06 07:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 478 | 1 | 19353 | 478 | 0.0247 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9672 |  | 2007-07-06 07:55 | 2007-07-06 | 2007-07-06 12:54 | Calculated | O410E | C1626 |  |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 299 | 111 | 19353 | 33189 | 1.7149 | 0.0057355 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9673 |  | 2007-07-06 08:00 | 2007-07-06 | 2007-07-06 09:57 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 117 | 1 | 19353 | 117 | 0.00605 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9674 |  | 2007-07-06 08:32 | 2007-07-06 | 2007-07-06 13:35 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-07 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 303 | 3 | 19353 | 911 | 0.04707 | 0.00015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9675 |  | 2007-07-06 08:37 | 2007-07-06 | 2007-07-06 13:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 301 | 6 | 19353 | 1806 | 0.09332 | 0.00031003 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9676 |  | 2007-07-06 08:49 | 2007-07-06 | 2007-07-06 15:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 401 | 9 | 19353 | 3609 | 0.18648 | 0.00046504 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9677 |  | 2007-07-06 08:49 | 2007-07-06 | 2007-07-06 15:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 401 | 1 | 19353 | 401 | 0.02072 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9678 |  | 2007-07-06 09:47 | 2007-07-06 | 2007-07-06 11:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-04 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 78 | 2 | 19353 | 156 | 0.00806 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9679 |  | 2007-07-06 15:12 | 2007-07-06 | 2007-07-06 15:54 | Calculated | O410E | LF |  |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 20 | 19353 | 840 | 0.0434 | 0.0010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9680 |  | 2007-07-06 15:19 | 2007-07-06 | 2007-07-06 18:11 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 172 | 1 | 19353 | 172 | 0.00889 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9681 |  | 2007-07-06 16:27 | 2007-07-06 | 2007-07-06 18:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 103 | 5 | 19353 | 515 | 0.02661 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9683 |  | 2007-07-07 14:34 | 2007-07-07 | 2007-07-07 16:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 104 | 1 | 19353 | 104 | 0.00537 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9684 |  | 2007-07-07 20:32 | 2007-07-07 | 2007-07-07 20:34 | Calculated | O410E | C242 & 262 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 241 | 19353 | 482 | 0.02491 | 0.012453 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9685 |  | 2007-07-09 08:05 | 2007-07-09 | 2007-07-09 12:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 255 | 1 | 19353 | 255 | 0.01318 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9686 |  | 2007-07-09 10:27 | 2007-07-09 | 2007-07-09 11:11 | Calculated | O410E | LF | Pole Mounted |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation | Transformers : Internal Connections | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 1 | 19353 | 44 | 0.00227 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9687 |  | 2007-07-09 12:35 | 2007-07-09 | 2007-07-09 14:04 | Calculated | O410E | LF | Drop-Out Fuses |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 89 | 1 | 19353 | 89 | 0.0046 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9688 |  | 2007-07-09 13:40 | 2007-07-09 | 2007-07-09 14:53 | Calculated | O410E | L705 | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 73 | 6 | 19353 | 438 | 0.02263 | 0.00031003 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9689 |  | 2007-07-09 13:46 | 2007-07-09 | 2007-07-09 16:14 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 148 | 1 | 19353 | 148 | 0.00765 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9691 |  | 2007-07-09 17:05 | 2007-07-09 | 2007-07-09 19:53 | Calculated | O410E | C531 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 10 | 19353 | 1680 | 0.08681 | 0.00051672 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9692 |  | 2007-07-10 08:17 | 2007-07-10 | 2007-07-10 10:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 154 | 1 | 19353 | 154 | 0.00796 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9693 |  | 2007-07-10 09:42 | 2007-07-10 | 2007-07-10 10:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 68 | 2 | 19353 | 136 | 0.00703 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9695 |  | 2007-07-10 10:17 | 2007-07-10 | 2007-07-10 14:59 | Calculated | O410E |  |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 85 | 19353 | 23970 | 1.2386 | 0.0043921 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9697 |  | 2007-07-10 11:13 | 2007-07-10 | 2007-07-10 12:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 1 | 19353 | 95 | 0.00491 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9698 |  | 2007-07-10 12:37 | 2007-07-10 | 2007-07-10 14:54 | Calculated | O410E | L170 | Drop-Out Fuses |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 137 | 18 | 19353 | 2466 | 0.12742 | 0.00093009 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9699 |  | 2007-07-10 13:16 | 2007-07-10 | 2007-07-10 14:27 | Calculated | O410E | S336 | Drop-Out Fuses |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 71 | 85 | 19353 | 6035 | 0.31184 | 0.0043921 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9700 |  | 2007-07-10 15:32 | 2007-07-10 | 2007-07-10 20:24 | Calculated | O410E | L1517 | Drop-Out Fuses |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 292 | 3 | 19353 | 876 | 0.04526 | 0.00015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9701 |  | 2007-07-10 16:35 | 2007-07-10 | 2007-07-10 17:38 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 63 | 1 | 19353 | 63 | 0.00326 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9702 |  | 2007-07-10 16:39 | 2007-07-10 | 2007-07-10 17:52 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 73 | 30 | 19353 | 2190 | 0.11316 | 0.0015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9704 |  | 2007-07-10 17:09 | 2007-07-10 | 2007-07-11 10:26 | Calculated | O410E | C1262 | Single Circuit |  | Huirimu 121-04 | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1037 | 11 | 19353 | 11407 | 0.58942 | 0.00056839 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9703 |  | 2007-07-10 17:22 | 2007-07-10 | 2007-07-10 19:55 | Calculated | O410E | L1547 | Drop-Out Fuses |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 153 | 9 | 19353 | 1377 | 0.07115 | 0.00046504 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9705 |  | 2007-07-10 19:06 | 2007-07-10 | 2007-07-10 23:37 | Calculated | O410E | C378 |  |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 271 | 203 | 19353 | 55144 | 2.8494 | 0.010489 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9706 |  | 2007-07-10 19:39 | 2007-07-10 | 2007-07-11 06:18 | Calculated | O410E | C117 |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 639 | 98 | 19353 | 62657 | 3.2376 | 0.0050638 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9707 |  | 2007-07-10 19:59 | 2007-07-10 | 2007-07-10 22:54 | Calculated | O410E | C127 | Single Circuit |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 246 | 19353 | 43066 | 2.2253 | 0.012711 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9708 |  | 2007-07-10 20:02 | 2007-07-10 | 2007-07-10 21:49 | Calculated | O410E | C2102 | Single Circuit |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 420 | 19353 | 45164 | 2.3337 | 0.021702 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9709 |  | 2007-07-10 20:50 | 2007-07-10 | 2007-07-10 21:13 | Calculated | O410E | C512 | Single Circuit |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 835 | 19353 | 19984 | 1.0326 | 0.043146 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9710 |  | 2007-07-10 20:55 | 2007-07-10 | 2007-07-10 23:51 | Calculated | O410E | C2092 | Single Circuit |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | OH Lines : Pole - Hardwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 105 | 19353 | 18550 | 0.95851 | 0.0054255 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9711 |  | 2007-07-10 21:00 | 2007-07-10 | 2007-07-11 12:20 | Calculated | O410E | C714 |  |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 920 | 49 | 19353 | 45097 | 2.3302 | 0.0025319 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9712 |  | 2007-07-10 21:07 | 2007-07-10 | 2007-07-10 23:00 | Calculated | O410E | C466 | Single Circuit |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 62 | 19353 | 7040 | 0.36377 | 0.0032036 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9713 |  | 2007-07-10 21:16 | 2007-07-10 | 2007-07-10 22:21 | Calculated | O410E | C1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 13 | 19353 | 845 | 0.04366 | 0.00067173 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9714 |  | 2007-07-10 21:19 | 2007-07-10 | 2007-07-11 05:43 | Calculated | O410E | C1716 |  |  | Mokauiti 115-04 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 504 | 23 | 19353 | 11602 | 0.59949 | 0.0011884 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9715 |  | 2007-07-10 21:33 | 2007-07-10 | 2007-07-11 09:48 | Calculated | O410E | C116 | Single Circuit |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 735 | 95 | 19353 | 40663 | 2.1011 | 0.0049088 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9716 |  | 2007-07-10 23:48 | 2007-07-10 | 2007-07-11 01:13 | Calculated | O410E | S175 | Single Circuit |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 30 | 19353 | 2550 | 0.13176 | 0.0015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9717 |  | 2007-07-11 06:10 | 2007-07-11 | 2007-07-12 17:50 | Calculated | O410E | S290 | Single Circuit |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2140 | 7 | 19353 | 14980 | 0.77404 | 0.0003617 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9719 |  | 2007-07-11 06:34 | 2007-07-11 | 2007-07-11 09:32 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 178 | 1 | 19353 | 178 | 0.0092 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9720 |  | 2007-07-11 06:37 | 2007-07-11 | 2007-07-11 09:42 | Calculated | O410E | L1517 | Drop-Out Fuses |  | Piopio 116-03 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 185 | 3 | 19353 | 555 | 0.02868 | 0.00015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9721 |  | 2007-07-11 07:00 | 2007-07-11 | 2007-07-11 14:04 | Calculated | O410E | C1728 | Single Circuit |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 424 | 28 | 19353 | 11875 | 0.6136 | 0.0014468 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9722 |  | 2007-07-11 07:10 | 2007-07-11 | 2007-07-11 14:29 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 439 | 2 | 19353 | 878 | 0.04537 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9723 |  | 2007-07-11 07:12 | 2007-07-11 | 2007-07-11 14:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 445 | 1 | 19353 | 445 | 0.02299 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9724 |  | 2007-07-11 07:25 | 2007-07-11 | 2007-07-11 15:48 | Calculated | O410E | L431 | Drop-Out Fuses |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 503 | 5 | 19353 | 2515 | 0.12995 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9725 |  | 2007-07-11 08:00 | 2007-07-11 | 2007-07-11 15:02 | Calculated | O410E | L298 | Drop-Out Fuses |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 422 | 5 | 19353 | 2110 | 0.10903 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9726 |  | 2007-07-11 08:25 | 2007-07-11 | 2007-07-11 10:04 | Calculated | O410E | LV |  |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 58 | 19353 | 5742 | 0.2967 | 0.002997 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9727 |  | 2007-07-11 08:32 | 2007-07-11 | 2007-07-11 12:24 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 232 | 2 | 19353 | 464 | 0.02398 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9728 |  | 2007-07-11 08:36 | 2007-07-11 | 2007-07-11 12:34 | Calculated | O410E | LF | Drop-Out Fuses |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 238 | 1 | 19353 | 238 | 0.0123 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9729 |  | 2007-07-11 08:39 | 2007-07-11 | 2007-07-11 12:43 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 244 | 1 | 19353 | 244 | 0.01261 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9731 |  | 2007-07-11 09:19 | 2007-07-11 | 2007-07-11 18:25 | Calculated | O410E | L245 | Single Circuit |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | OH Lines : Pole - Softwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 546 | 5 | 19353 | 2730 | 0.14106 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9732 |  | 2007-07-11 10:16 | 2007-07-11 | 2007-07-11 11:03 | Calculated | O410E | L691 | Single Circuit |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Jumper - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 3 | 19353 | 141 | 0.00729 | 0.00015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9733 |  | 2007-07-11 10:37 | 2007-07-11 | 2007-07-11 15:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 269 | 1 | 19353 | 269 | 0.0139 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9734 |  | 2007-07-11 10:54 | 2007-07-11 | 2007-07-11 16:32 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-09 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 338 | 2 | 19353 | 676 | 0.03493 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9735 |  | 2007-07-11 11:33 | 2007-07-11 | 2007-07-11 11:58 | Calculated | O410E | LF |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 2 | 19353 | 50 | 0.00258 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9736 |  | 2007-07-11 11:34 | 2007-07-11 | 2007-07-11 12:07 | Calculated | O410E | LF |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 5 | 19353 | 165 | 0.00853 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9737 |  | 2007-07-11 12:06 | 2007-07-11 | 2007-07-11 13:10 | Calculated | O410E | L449 |  |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 3 | 19353 | 192 | 0.00992 | 0.00015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9738 |  | 2007-07-11 14:33 | 2007-07-11 | 2007-07-11 15:08 | Calculated | O410E | LF |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 2 | 19353 | 70 | 0.00362 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9740 |  | 2007-07-11 15:02 | 2007-07-11 | 2007-07-11 17:27 | Calculated | O410E | L364 | Drop-Out Fuses |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 145 | 30 | 19353 | 4350 | 0.22477 | 0.0015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9741 |  | 2007-07-11 15:14 | 2007-07-11 | 2007-07-11 17:34 | Calculated | O410E | L424 | Drop-Out Fuses |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 140 | 10 | 19353 | 1400 | 0.07234 | 0.00051672 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9742 |  | 2007-07-11 15:23 | 2007-07-11 | 2007-07-11 17:54 | Calculated | O410E | C1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 13 | 19353 | 1963 | 0.10143 | 0.00067173 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9743 |  | 2007-07-11 15:31 | 2007-07-11 | 2007-07-11 22:41 | Calculated | O410E | L679 | Drop-Out Fuses |  | Wharepapa 122-08 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 430 | 7 | 19353 | 3015 | 0.15579 | 0.0003617 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9744 |  | 2007-07-11 15:59 | 2007-07-11 | 2007-07-11 16:39 | Calculated | O410E | LF |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 2 | 19353 | 80 | 0.00413 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9745 |  | 2007-07-11 16:17 | 2007-07-11 | 2007-07-12 01:04 | Calculated | O410E | C1721 |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 527 | 17 | 19353 | 8972 | 0.4636 | 0.00087842 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9746 |  | 2007-07-11 16:41 | 2007-07-11 | 2007-07-11 18:44 | Calculated | O410E | L443 | Drop-Out Fuses |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 123 | 11 | 19353 | 1353 | 0.06991 | 0.00056839 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9747 |  | 2007-07-11 16:45 | 2007-07-11 | 2007-07-11 17:32 | Calculated | O410E | L407 | Drop-Out Fuses |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 47 | 9 | 19353 | 423 | 0.02186 | 0.00046504 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9748 |  | 2007-07-11 18:35 | 2007-07-11 | 2007-07-11 18:45 | Calculated | O410E | C1052 |  |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 261 | 19353 | 2610 | 0.13486 | 0.013486 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9749 |  | 2007-07-12 08:00 | 2007-07-12 | 2007-07-12 09:00 | Calculated | O410E | C5847 |  |  |  | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 26 | 19353 | 1560 | 0.08061 | 0.0013435 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9750 |  | 2007-07-12 08:02 | 2007-07-12 | 2007-07-12 09:34 | Calculated | O410E | L677 | Drop-Out Fuses |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 8 | 19353 | 736 | 0.03803 | 0.00041337 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9751 |  | 2007-07-12 08:03 | 2007-07-12 | 2007-07-12 10:12 | Calculated | O410E | L289 | Drop-Out Fuses |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 129 | 4 | 19353 | 516 | 0.02666 | 0.00020669 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9752 |  | 2007-07-12 08:05 | 2007-07-12 | 2007-07-12 10:50 | Calculated | O410E | L256 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 165 | 5 | 19353 | 825 | 0.04263 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9753 |  | 2007-07-12 08:12 | 2007-07-12 | 2007-07-12 11:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 198 | 1 | 19353 | 198 | 0.01023 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9754 |  | 2007-07-12 10:04 | 2007-07-12 | 2007-07-12 14:08 | Calculated | O410E |  |  |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 244 | 22 | 19353 | 5368 | 0.27737 | 0.0011368 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9755 |  | 2007-07-12 11:51 | 2007-07-12 | 2007-07-12 12:15 | Calculated | O410E | L342 | Single Circuit |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 17 | 19353 | 408 | 0.02108 | 0.00087842 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9756 |  | 2007-07-12 14:02 | 2007-07-12 | 2007-07-12 15:28 | Calculated | O410E | LF |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 5 | 19353 | 430 | 0.02222 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9757 |  | 2007-07-13 00:07 | 2007-07-13 | 2007-07-13 07:51 | Calculated | O410E | C154 | PVC/Polythene - Laid Direct |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation | Cables : Cable Core - Phase | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 464 | 78 | 19353 | 36192 | 1.8701 | 0.0040304 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9844 |  | 2007-07-13 09:34 | 2007-07-13 | 2007-07-13 11:49 | Calculated | O410E | L777 | Single Circuit |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 8 | 19353 | 1080 | 0.05581 | 0.00041337 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9758 |  | 2007-07-13 11:50 | 2007-07-13 | 2007-07-13 12:57 | Calculated | O410E | S423 - 432 | Single Circuit |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation | OH Lines : Pole - Hardwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 18 | 19353 | 1206 | 0.06232 | 0.00093009 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9759 |  | 2007-07-13 12:51 | 2007-07-13 | 2007-07-13 18:10 | Calculated | O410E | L1547 | Single Circuit |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | OH Lines : Pole - Hardwood | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 319 | 9 | 19353 | 2871 | 0.14835 | 0.00046504 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9761 |  | 2007-07-15 12:00 | 2007-07-15 | 2007-07-15 14:10 | Calculated | O410E | C409 |  |  |  | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 27 | 19353 | 3510 | 0.18137 | 0.0013951 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9762 |  | 2007-07-16 09:58 | 2007-07-16 | 2007-07-16 10:30 | Calculated | O410E | LF |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 2 | 19353 | 64 | 0.00331 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9764 |  | 2007-07-16 11:46 | 2007-07-16 | 2007-07-16 13:18 | Calculated | O410E | LF |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 2 | 19353 | 184 | 0.00951 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9765 |  | 2007-07-16 12:30 | 2007-07-16 | 2007-07-16 14:24 | Calculated | O410E | C371 |  |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 25 | 19353 | 2850 | 0.14726 | 0.0012918 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9766 |  | 2007-07-16 14:00 | 2007-07-16 | 2007-07-16 15:18 | Calculated | O410E | L364 | Drop-Out Fuses |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 78 | 30 | 19353 | 2340 | 0.12091 | 0.0015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9767 |  | 2007-07-16 16:43 | 2007-07-16 | 2007-07-16 17:05 | Calculated | O410E | LF |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 2 | 19353 | 44 | 0.00227 | 0.00010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9768 |  | 2007-07-17 08:50 | 2007-07-17 | 2007-07-17 09:12 | Calculated | O410E | C5847 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 26 | 19353 | 572 | 0.02956 | 0.0013435 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9769 |  | 2007-07-17 10:47 | 2007-07-17 | 2007-07-17 11:58 | Calculated | O410E | LF |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 1 | 19353 | 71 | 0.00367 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9771 |  | 2007-07-18 09:14 | 2007-07-18 | 2007-07-18 11:48 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 154 | 1 | 19353 | 154 | 0.00796 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9772 |  | 2007-07-18 10:04 | 2007-07-18 | 2007-07-18 14:09 | Calculated | O410E | LF |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 245 | 4 | 19353 | 980 | 0.05064 | 0.00020669 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9773 |  | 2007-07-18 11:10 | 2007-07-18 | 2007-07-18 15:32 | Calculated | O410E | LV |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 262 | 52 | 19353 | 13624 | 0.70397 | 0.0026869 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9774 |  | 2007-07-18 13:58 | 2007-07-18 | 2007-07-18 16:04 | Calculated | O410E | LF |  |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 3 | 19353 | 378 | 0.01953 | 0.00015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9775 |  | 2007-07-19 08:30 | 2007-07-19 | 2007-07-19 15:08 | Calculated | O410E |  |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 398 | 198 | 19353 | 78804 | 4.0719 | 0.010231 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9776 |  | 2007-07-19 09:03 | 2007-07-19 | 2007-07-19 14:58 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 8 | 19353 | 2840 | 0.14675 | 0.00041337 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9777 |  | 2007-07-19 09:25 | 2007-07-19 | 2007-07-19 12:13 | Calculated | O410E | C1615 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 9 | 19353 | 1519 | 0.07849 | 0.00046504 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9778 |  | 2007-07-19 11:03 | 2007-07-19 | 2007-07-19 13:43 | Calculated | O410E | S290 |  |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 7 | 19353 | 1120 | 0.05787 | 0.0003617 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9781 |  | 2007-07-20 22:00 | 2007-07-20 | 2007-07-20 23:50 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 28 | 19353 | 3080 | 0.15915 | 0.0014468 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9783 |  | 2007-07-22 07:21 | 2007-07-22 | 2007-07-22 09:08 | Calculated | O410E | L275 |  |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 52 | 19353 | 5564 | 0.2875 | 0.0026869 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9785 |  | 2007-07-23 08:03 | 2007-07-23 | 2007-07-23 09:37 | Calculated | O410E | L764 | Drop-Out Fuses |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 8 | 19353 | 752 | 0.03886 | 0.00041337 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9786 |  | 2007-07-23 10:12 | 2007-07-23 | 2007-07-23 11:18 | Calculated | O410E | C811 |  |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 20 | 19353 | 1320 | 0.06821 | 0.0010334 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9788 |  | 2007-07-24 08:00 | 2007-07-24 | 2007-07-24 10:05 | Calculated | O410E | L364 | Drop-Out Fuses |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 125 | 30 | 19353 | 3750 | 0.19377 | 0.0015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9789 |  | 2007-07-24 09:30 | 2007-07-24 | 2007-07-24 15:51 | Calculated | O410E |  |  |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 381 | 27 | 19353 | 10287 | 0.53155 | 0.0013951 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9790 |  | 2007-07-24 14:21 | 2007-07-24 | 2007-07-24 16:40 | Calculated | O410E |  |  |  | Rangitoto 106-02 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 5 | 19353 | 695 | 0.03591 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9791 |  | 2007-07-24 17:02 | 2007-07-24 | 2007-07-24 17:13 | Calculated | O410E | LF |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 3 | 19353 | 33 | 0.00171 | 0.00015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9792 |  | 2007-07-25 01:00 | 2007-07-25 | 2007-07-25 01:10 | Calculated | O410E | C2092 |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 105 | 19353 | 1050 | 0.05426 | 0.0054255 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9793 |  | 2007-07-25 09:12 | 2007-07-25 | 2007-07-25 09:57 | Calculated | O410E |  |  |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 23 | 19353 | 1035 | 0.05348 | 0.0011884 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9794 |  | 2007-07-25 10:02 | 2007-07-25 | 2007-07-25 14:02 | Calculated | O410E |  |  |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 240 | 5 | 19353 | 1200 | 0.06201 | 0.00025836 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9795 |  | 2007-07-25 10:30 | 2007-07-25 | 2007-07-25 11:56 | Calculated | O410E | LV |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 28 | 19353 | 2408 | 0.12443 | 0.0014468 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9796 |  | 2007-07-25 11:03 | 2007-07-25 | 2007-07-25 13:28 | Calculated | O410E |  |  |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 145 | 17 | 19353 | 2465 | 0.12737 | 0.00087842 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9797 |  | 2007-07-25 12:00 | 2007-07-25 | 2007-07-25 14:43 | Calculated | O410E |  |  |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 163 | 37 | 19353 | 6031 | 0.31163 | 0.0019118 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9799 |  | 2007-07-27 10:00 | 2007-07-27 | 2007-07-27 11:30 | Calculated | O410E | L1715 | Drop-Out Fuses |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 90 | 17 | 19353 | 1530 | 0.07906 | 0.00087842 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9800 |  | 2007-07-27 10:31 | 2007-07-27 | 2007-07-27 13:26 | Calculated | O410E |  |  |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 175 | 14 | 19353 | 2450 | 0.1266 | 0.0007234 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9801 |  | 2007-07-29 15:38 | 2007-07-29 | 2007-07-29 17:03 | Calculated | O410E | S236 & 731 | Drop-Out Fuses |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 18 | 19353 | 1530 | 0.07906 | 0.00093009 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9802 |  | 2007-07-30 13:52 | 2007-07-30 | 2007-07-30 15:41 | Calculated | O410E | LF |  |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 3 | 19353 | 327 | 0.0169 | 0.00015501 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9803 |  | 2007-07-30 15:44 | 2007-07-30 | 2007-07-30 19:43 | Calculated | O410E |  |  |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 239 | 1 | 19353 | 239 | 0.01235 | 5.1672e-05 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9804 |  | 2007-07-31 15:12 | 2007-07-31 | 2007-07-31 16:39 | Calculated | O410E | L433 | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 87 | 9 | 19353 | 783 | 0.04046 | 0.00046504 | 0 | 0 | 2007/2008 | July-2007 | 7 | 2007
9805 |  | 2007-08-01 10:06 | 2007-08-01 | 2007-08-01 11:21 | Calculated | O410E | LF | Single Circuit |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation | OH Lines : Surge Diverters | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9806 |  | 2007-08-01 10:57 | 2007-08-01 | 2007-08-01 12:05 | Calculated | O410E | LF |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 3 | 19353 | 204 | 0.01054 | 0.00015501 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9807 |  | 2007-08-01 10:57 | 2007-08-01 | 2007-08-01 10:59 | Calculated | O410E | C1354 |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 42 | 19353 | 84 | 0.00434 | 0.0021702 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9808 |  | 2007-08-01 11:22 | 2007-08-01 | 2007-08-01 14:18 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-07 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 176 | 4 | 19353 | 704 | 0.03638 | 0.00020669 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9810 |  | 2007-08-02 08:45 | 2007-08-02 | 2007-08-02 13:54 | Calculated | O410E | LF |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 309 | 2 | 19353 | 618 | 0.03193 | 0.00010334 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9811 |  | 2007-08-02 10:07 | 2007-08-02 | 2007-08-02 12:26 | Calculated | O410E | LF |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 3 | 19353 | 417 | 0.02155 | 0.00015501 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9812 |  | 2007-08-02 11:30 | 2007-08-02 | 2007-08-02 13:11 | Calculated | O410E | L256 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 101 | 5 | 19353 | 505 | 0.02609 | 0.00025836 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9813 |  | 2007-08-03 01:26 | 2007-08-03 | 2007-08-03 05:49 | Calculated | O410E | C820 | Single Circuit |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation | OH Lines : Insulator - Disc | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 263 | 174 | 19353 | 45762 | 2.3646 | 0.0089909 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9814 |  | 2007-08-03 09:08 | 2007-08-03 | 2007-08-03 13:21 | Calculated | O410E |  |  |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 253 | 24 | 19353 | 6072 | 0.31375 | 0.0012401 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9815 |  | 2007-08-03 09:16 | 2007-08-03 | 2007-08-03 13:45 | Calculated | O410E | L844 | Drop-Out Fuses |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 269 | 25 | 19353 | 6725 | 0.34749 | 0.0012918 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9817 |  | 2007-08-03 11:10 | 2007-08-03 | 2007-08-03 11:46 | Calculated | O410E | S1313 | Single Circuit |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Stay Wire | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 17 | 19353 | 612 | 0.03162 | 0.00087842 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9818 |  | 2007-08-05 13:36 | 2007-08-05 | 2007-08-05 15:25 | Calculated | O410E | L289 | Drop-Out Fuses |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 109 | 11 | 19353 | 1199 | 0.06195 | 0.00056839 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9819 |  | 2007-08-06 09:23 | 2007-08-06 | 2007-08-06 11:10 | Calculated | O410E |  |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 107 | 52 | 19353 | 5564 | 0.2875 | 0.0026869 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9820 |  | 2007-08-06 09:50 | 2007-08-06 | 2007-08-06 16:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 396 | 1 | 19353 | 396 | 0.02046 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9821 |  | 2007-08-06 10:50 | 2007-08-06 | 2007-08-06 16:14 | Calculated | O410E | L292 | Drop-Out Fuses |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 324 | 5 | 19353 | 1620 | 0.08371 | 0.00025836 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9822 |  | 2007-08-06 11:46 | 2007-08-06 | 2007-08-06 13:03 | Calculated | O410E | S552 | Single Circuit |  | Caves 101-12 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Insulator - Polymer | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 10 | 19353 | 770 | 0.03979 | 0.00051672 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9823 |  | 2007-08-07 07:56 | 2007-08-07 | 2007-08-07 15:38 | Calculated | O410E | LF | Drop-Out Fuses |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 462 | 1 | 19353 | 462 | 0.02387 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9825 |  | 2007-08-07 10:00 | 2007-08-07 | 2007-08-07 12:11 | Calculated | O410E | C564 |  |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 13 | 19353 | 1703 | 0.088 | 0.00067173 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9826 |  | 2007-08-07 10:02 | 2007-08-07 | 2007-08-07 13:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 211 | 1 | 19353 | 211 | 0.0109 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9828 |  | 2007-08-07 11:42 | 2007-08-07 | 2007-08-07 11:44 | Calculated | O410E | C792 & 594 & 754 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 1574 | 19353 | 3148 | 0.16266 | 0.081331 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9829 |  | 2007-08-07 18:30 | 2007-08-07 | 2007-08-07 18:31 | Calculated | O410E | C169 |  |  |  | Remote Rural F | Te Waireka Rd 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2007/2008 | August-2007 | 8 | 2007
9830 |  | 2007-08-08 10:23 | 2007-08-08 | 2007-08-08 14:12 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 229 | 94 | 19353 | 21526 | 1.1123 | 0.0048571 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9831 |  | 2007-08-09 09:30 | 2007-08-09 | 2007-08-09 10:19 | Calculated | O410E |  |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 86 | 19353 | 4214 | 0.21774 | 0.0044438 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9832 |  | 2007-08-09 09:47 | 2007-08-09 | 2007-08-09 11:04 | Calculated | O410E | LF |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 2 | 19353 | 154 | 0.00796 | 0.00010334 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9835 |  | 2007-08-09 17:05 | 2007-08-09 | 2007-08-09 18:21 | Calculated | O410E | LF | Drop-Out Fuses |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 76 | 3 | 19353 | 228 | 0.01178 | 0.00015501 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9834 |  | 2007-08-09 18:01 | 2007-08-09 | 2007-08-09 18:59 | Calculated | O410E | LF |  |  | McDonalds 110-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 1 | 19353 | 58 | 0.003 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9836 |  | 2007-08-10 19:47 | 2007-08-10 | 2007-08-10 19:54 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 7 | 3 | 19353 | 21 | 0.00109 | 0.00015501 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9837 |  | 2007-08-11 12:01 | 2007-08-11 | 2007-08-11 13:17 | Calculated | O410E | C446 |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 29 | 19353 | 2204 | 0.11388 | 0.0014985 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9838 |  | 2007-08-11 14:47 | 2007-08-11 | 2007-08-11 17:02 | Calculated | O410E | C467 |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 50 | 19353 | 6777 | 0.35018 | 0.0025836 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9839 |  | 2007-08-11 15:21 | 2007-08-11 | 2007-08-11 18:19 | Calculated | O410E | C144 | Single Circuit |  | National Park 411-01 | Remote Rural F | National Park | National Park Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 178 | 267 | 19353 | 47663 | 2.4628 | 0.013796 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9840 |  | 2007-08-11 21:05 | 2007-08-11 | 2007-08-11 21:40 | Calculated | O410E | L663 | Drop-Out Fuses |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 35 | 7 | 19353 | 245 | 0.01266 | 0.0003617 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9841 |  | 2007-08-11 23:49 | 2007-08-11 | 2007-08-11 23:58 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 1 | 19353 | 9 | 0.00047 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9842 |  | 2007-08-12 08:44 | 2007-08-12 | 2007-08-12 09:54 | Calculated | O410E | C117 | Single Circuit |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 98 | 19353 | 6918 | 0.35746 | 0.0050638 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9843 |  | 2007-08-13 08:40 | 2007-08-13 | 2007-08-13 09:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 53 | 1 | 19353 | 53 | 0.00274 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9845 |  | 2007-08-13 10:05 | 2007-08-13 | 2007-08-13 12:50 | Calculated | O410E |  |  |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 165 | 4 | 19353 | 660 | 0.0341 | 0.00020669 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9846 |  | 2007-08-14 09:37 | 2007-08-14 | 2007-08-14 15:12 | Calculated | O410E |  |  |  | Benneydale 103-08 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 335 | 9 | 19353 | 3015 | 0.15579 | 0.00046504 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9847 |  | 2007-08-14 17:36 | 2007-08-14 | 2007-08-14 18:53 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 77 | 1 | 19353 | 77 | 0.00398 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9848 |  | 2007-08-15 09:35 | 2007-08-15 | 2007-08-15 14:25 | Calculated | O410E |  |  |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 290 | 35 | 19353 | 10150 | 0.52447 | 0.0018085 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9849 |  | 2007-08-15 11:02 | 2007-08-15 | 2007-08-15 13:47 | Calculated | O410E | LF |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 165 | 1 | 19353 | 165 | 0.00853 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9850 |  | 2007-08-15 11:44 | 2007-08-15 | 2007-08-15 11:54 | Calculated | O410E | LV |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 35 | 19353 | 350 | 0.01809 | 0.0018085 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9851 |  | 2007-08-15 12:02 | 2007-08-15 | 2007-08-15 12:28 | Calculated | O410E | C6576 |  |  |  | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Asset Related | Other |  | Fault on Adjacent Circuit | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 26 | 1323 | 19353 | 34398 | 1.7774 | 0.068361 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9852 |  | 2007-08-16 09:01 | 2007-08-16 | 2007-08-16 13:25 | Calculated | O410E |  |  |  | Hangatiki East 102-01 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 2 | 19353 | 528 | 0.02728 | 0.00010334 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9853 |  | 2007-08-16 09:40 | 2007-08-16 | 2007-08-16 10:23 | Calculated | O410E |  |  |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 3 | 19353 | 129 | 0.00667 | 0.00015501 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9854 |  | 2007-08-17 07:07 | 2007-08-17 | 2007-08-17 09:54 | Calculated | O410E | C806 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 46 | 19353 | 7682 | 0.39694 | 0.0023769 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9855 |  | 2007-08-17 07:23 | 2007-08-17 | 2007-08-17 08:55 | Calculated | O410E | L429 | Drop-Out Fuses |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 16 | 19353 | 1472 | 0.07606 | 0.00082675 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9856 |  | 2007-08-17 08:04 | 2007-08-17 | 2007-08-17 13:50 | Calculated | O410E | L687 | Single Circuit |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 346 | 2 | 19353 | 692 | 0.03576 | 0.00010334 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9857 |  | 2007-08-17 08:12 | 2007-08-17 | 2007-08-17 09:26 | Calculated | O410E | L555 | Single Circuit |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Binder / Stirrup | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 27 | 19353 | 2017 | 0.10422 | 0.0013951 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9858 |  | 2007-08-17 09:09 | 2007-08-17 | 2007-08-17 12:44 | Calculated | O410E |  |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 215 | 52 | 19353 | 11180 | 0.57769 | 0.0026869 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9859 |  | 2007-08-18 10:12 | 2007-08-18 | 2007-08-18 12:24 | Calculated | O410E | L260 | Single Circuit |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Conductor - Bare Copper | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 14 | 19353 | 1848 | 0.09549 | 0.0007234 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9860 |  | 2007-08-18 12:42 | 2007-08-18 | 2007-08-18 15:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 143 | 1 | 19353 | 143 | 0.00739 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9861 |  | 2007-08-19 12:07 | 2007-08-19 | 2007-08-19 13:35 | Calculated | O410E | LF | Drop-Out Fuses |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 86 | 19353 | 7568 | 0.39105 | 0.0044438 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9863 |  | 2007-08-20 07:34 | 2007-08-20 | 2007-08-20 11:56 | Calculated | O410E | L478 | Drop-Out Fuses |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 262 | 9 | 19353 | 2358 | 0.12184 | 0.00046504 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9865 |  | 2007-08-20 13:40 | 2007-08-20 | 2007-08-20 14:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 32 | 1 | 19353 | 32 | 0.00165 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9866 |  | 2007-08-21 09:00 | 2007-08-21 | 2007-08-21 14:36 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 336 | 16 | 19353 | 5376 | 0.27779 | 0.00082675 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9867 |  | 2007-08-21 10:04 | 2007-08-21 | 2007-08-21 13:56 | Calculated | O410E |  |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 6 | 19353 | 1392 | 0.07193 | 0.00031003 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9870 |  | 2007-08-22 10:02 | 2007-08-22 | 2007-08-22 12:57 | Calculated | O410E |  |  |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 175 | 5 | 19353 | 875 | 0.04521 | 0.00025836 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9869 |  | 2007-08-22 10:03 | 2007-08-22 | 2007-08-22 13:47 | Calculated | O410E |  |  |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 224 | 32 | 19353 | 7168 | 0.37038 | 0.0016535 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9872 |  | 2007-08-23 10:13 | 2007-08-23 | 2007-08-23 13:05 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 172 | 21 | 19353 | 3612 | 0.18664 | 0.0010851 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9875 |  | 2007-08-25 20:19 | 2007-08-25 | 2007-08-26 06:43 | Calculated | O410E | C287 |  |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 624 | 18 | 19353 | 11232 | 0.58038 | 0.00093009 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9876 |  | 2007-08-27 10:34 | 2007-08-27 | 2007-08-27 14:43 | Calculated | O410E |  |  |  | Rural 126-02 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 249 | 6 | 19353 | 1494 | 0.0772 | 0.00031003 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9877 |  | 2007-08-27 14:41 | 2007-08-27 | 2007-08-27 16:13 | Calculated | O410E | C505 |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 22 | 19353 | 2024 | 0.10458 | 0.0011368 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9878 |  | 2007-08-28 10:07 | 2007-08-28 | 2007-08-28 11:56 | Calculated | O410E |  |  |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 109 | 8 | 19353 | 872 | 0.04506 | 0.00041337 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9879 |  | 2007-08-28 12:30 | 2007-08-28 | 2007-08-28 14:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 117 | 1 | 19353 | 117 | 0.00605 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9880 |  | 2007-08-28 18:07 | 2007-08-28 | 2007-08-28 19:50 | Calculated | O410E | C378 | Single Circuit |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Binder / Stirrup | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 203 | 19353 | 20993 | 1.0847 | 0.010489 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9881 |  | 2007-08-28 19:05 | 2007-08-28 | 2007-08-28 20:00 | Calculated | O410E | L499 | Single Circuit |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Jumper - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 5 | 19353 | 275 | 0.01421 | 0.00025836 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9882 |  | 2007-08-28 20:39 | 2007-08-28 | 2007-08-28 21:20 | Calculated | O410E | LF |  |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 82 | 19353 | 3362 | 0.17372 | 0.0042371 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9883 |  | 2007-08-28 21:48 | 2007-08-28 | 2007-08-28 23:38 | Calculated | O410E | L525 | Single Circuit |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation | OH Lines : Pole - Softwood | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 76 | 19353 | 8415 | 0.43482 | 0.003927 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9884 |  | 2007-08-29 01:41 | 2007-08-29 | 2007-08-29 06:14 | Calculated | O410E | C1072 | Single Circuit |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Pole - Hardwood | Asset Related | Other |  | Ground Subsidence | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 273 | 108 | 19353 | 29484 | 1.5235 | 0.0055805 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9885 |  | 2007-08-29 13:19 | 2007-08-29 | 2007-08-29 14:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 99 | 1 | 19353 | 99 | 0.00512 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9887 |  | 2007-08-30 10:01 | 2007-08-30 | 2007-08-30 13:39 | Calculated | O410E | LF |  |  | Turoa 415-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 218 | 37 | 19353 | 8066 | 0.41678 | 0.0019118 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9888 |  | 2007-08-30 10:35 | 2007-08-30 | 2007-08-30 12:06 | Calculated | O410E | LF |  |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 4 | 19353 | 364 | 0.01881 | 0.00020669 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9889 |  | 2007-08-31 07:50 | 2007-08-31 | 2007-08-31 11:01 | Calculated | O410E | LF | Pole Mounted |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 1 | 19353 | 191 | 0.00987 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9890 |  | 2007-08-31 09:18 | 2007-08-31 | 2007-08-31 14:23 | Calculated | O410E | LF |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 1 | 19353 | 305 | 0.01576 | 5.1672e-05 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9891 |  | 2007-08-31 09:30 | 2007-08-31 | 2007-08-31 14:53 | Calculated | O410E | LV |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 323 | 21 | 19353 | 6783 | 0.35049 | 0.0010851 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9892 |  | 2007-08-31 10:35 | 2007-08-31 | 2007-08-31 13:22 | Calculated | O410E | LF |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 167 | 4 | 19353 | 668 | 0.03452 | 0.00020669 | 0 | 0 | 2007/2008 | August-2007 | 8 | 2007
9895 |  | 2007-09-01 13:33 | 2007-09-01 | 2007-09-01 14:07 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 3 | 19353 | 102 | 0.00527 | 0.00015501 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9896 |  | 2007-09-02 12:33 | 2007-09-02 | 2007-09-02 12:40 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 7 | 4 | 19353 | 31 | 0.0016 | 0.00020669 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9897 |  | 2007-09-03 08:51 | 2007-09-03 | 2007-09-03 09:03 | Calculated | O410E |  |  |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 12 | 52 | 19353 | 624 | 0.03224 | 0.0026869 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9900 |  | 2007-09-04 09:01 | 2007-09-04 | 2007-09-04 14:34 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 333 | 10 | 19353 | 3330 | 0.17207 | 0.00051672 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9902 |  | 2007-09-05 05:04 | 2007-09-05 | 2007-09-05 06:32 | Calculated | O410E |  |  |  | Caves 101-08 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 98 | 19353 | 8679 | 0.44846 | 0.0050638 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9903 |  | 2007-09-05 08:47 | 2007-09-05 | 2007-09-05 09:27 | Calculated | O410E | LF |  |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 5 | 19353 | 200 | 0.01033 | 0.00025836 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9904 |  | 2007-09-05 10:32 | 2007-09-05 | 2007-09-05 13:16 | Calculated | O410E |  |  |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 164 | 60 | 19353 | 9840 | 0.50845 | 0.0031003 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9905 |  | 2007-09-05 11:32 | 2007-09-05 | 2007-09-05 15:34 | Calculated | O410E | LV |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 242 | 22 | 19353 | 5324 | 0.2751 | 0.0011368 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9907 |  | 2007-09-06 09:01 | 2007-09-06 | 2007-09-06 15:40 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 399 | 16 | 19353 | 6384 | 0.32987 | 0.00082675 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9909 |  | 2007-09-06 14:09 | 2007-09-06 | 2007-09-06 14:38 | Calculated | O410E | LF |  |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 1 | 19353 | 29 | 0.0015 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9910 |  | 2007-09-07 09:00 | 2007-09-07 | 2007-09-07 14:50 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 350 | 16 | 19353 | 5600 | 0.28936 | 0.00082675 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9911 |  | 2007-09-07 11:14 | 2007-09-07 | 2007-09-07 13:10 | Calculated | O410E | LF |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 116 | 1 | 19353 | 116 | 0.00599 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9912 |  | 2007-09-10 06:43 | 2007-09-10 | 2007-09-10 06:51 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 4 | 19353 | 32 | 0.00165 | 0.00020669 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9913 |  | 2007-09-10 10:00 | 2007-09-10 | 2007-09-10 11:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 1 | 19353 | 85 | 0.00439 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9914 |  | 2007-09-10 12:05 | 2007-09-10 | 2007-09-10 13:11 | Calculated | O410E | LF |  |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 2 | 19353 | 132 | 0.00682 | 0.00010334 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9915 |  | 2007-09-11 10:11 | 2007-09-11 | 2007-09-11 12:08 | Calculated | O410E |  |  |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 9 | 19353 | 1059 | 0.05472 | 0.00046504 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9916 |  | 2007-09-11 19:42 | 2007-09-11 | 2007-09-11 20:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 54 | 3 | 19353 | 162 | 0.00837 | 0.00015501 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9917 |  | 2007-09-12 09:01 | 2007-09-12 | 2007-09-12 15:15 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 10 | 19353 | 3740 | 0.19325 | 0.00051672 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9918 |  | 2007-09-12 09:15 | 2007-09-12 | 2007-09-12 11:33 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 138 | 5 | 19353 | 690 | 0.03565 | 0.00025836 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9921 |  | 2007-09-13 09:01 | 2007-09-13 | 2007-09-13 13:53 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 16 | 19353 | 4672 | 0.24141 | 0.00082675 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9923 |  | 2007-09-13 20:56 | 2007-09-13 | 2007-09-13 20:58 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Other |  | Condensation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 4 | 19353 | 8 | 0.00041 | 0.00020669 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9924 |  | 2007-09-14 08:04 | 2007-09-14 | 2007-09-14 09:28 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 84 | 1 | 19353 | 84 | 0.00434 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9925 |  | 2007-09-14 09:35 | 2007-09-14 | 2007-09-14 13:45 | Calculated | O410E |  |  |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 6 | 19353 | 1500 | 0.07751 | 0.00031003 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9928 |  | 2007-09-15 11:51 | 2007-09-15 | 2007-09-15 13:50 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 119 | 2 | 19353 | 238 | 0.0123 | 0.00010334 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9929 |  | 2007-09-16 18:31 | 2007-09-16 | 2007-09-16 22:37 | Calculated | O410E | C360 |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 246 | 6 | 19353 | 1476 | 0.07627 | 0.00031003 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9930 |  | 2007-09-17 11:01 | 2007-09-17 | 2007-09-17 12:13 | Calculated | O410E | L265 | Drop-Out Fuses |  | Nihoniho 412-02 | Remote Rural F | Nihoniho | Nihoniho Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 72 | 21 | 19353 | 1512 | 0.07813 | 0.0010851 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9931 |  | 2007-09-17 13:01 | 2007-09-17 | 2007-09-17 14:47 | Calculated | O410E |  |  |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 106 | 18 | 19353 | 1908 | 0.09859 | 0.00093009 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9932 |  | 2007-09-17 14:02 | 2007-09-17 | 2007-09-17 14:56 | Calculated | O410E | LF |  |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 3 | 19353 | 162 | 0.00837 | 0.00015501 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9933 |  | 2007-09-18 13:36 | 2007-09-18 | 2007-09-18 14:46 | Calculated | O410E |  |  |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 70 | 17 | 19353 | 1190 | 0.06149 | 0.00087842 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9934 |  | 2007-09-19 11:00 | 2007-09-19 | 2007-09-19 12:46 | Calculated | O410E | LF |  |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 106 | 1 | 19353 | 106 | 0.00548 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9936 |  | 2007-09-20 19:42 | 2007-09-20 | 2007-09-20 21:08 | Calculated | O410E | L1122 | Drop-Out Fuses |  | Aria 114-05 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 86 | 5 | 19353 | 430 | 0.02222 | 0.00025836 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9938 |  | 2007-09-22 16:55 | 2007-09-22 | 2007-09-22 17:58 | Calculated | O410E | L500 |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Other |  | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 26 | 19353 | 1638 | 0.08464 | 0.0013435 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9939 |  | 2007-09-24 09:00 | 2007-09-24 | 2007-09-24 14:13 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 313 | 10 | 19353 | 3130 | 0.16173 | 0.00051672 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9940 |  | 2007-09-24 09:33 | 2007-09-24 | 2007-09-24 14:17 | Calculated | O410E |  |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 284 | 26 | 19353 | 7384 | 0.38154 | 0.0013435 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9941 |  | 2007-09-24 09:55 | 2007-09-24 | 2007-09-24 12:24 | Calculated | O410E | L726 | Drop-Out Fuses |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 149 | 14 | 19353 | 2086 | 0.10779 | 0.0007234 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9942 |  | 2007-09-24 13:40 | 2007-09-24 | 2007-09-24 15:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 90 | 3 | 19353 | 270 | 0.01395 | 0.00015501 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9944 |  | 2007-09-24 14:10 | 2007-09-24 | 2007-09-24 16:38 | Calculated | O410E | L443 | Drop-Out Fuses |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 148 | 11 | 19353 | 1628 | 0.08412 | 0.00056839 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9945 |  | 2007-09-24 14:55 | 2007-09-24 | 2007-09-24 16:31 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 6 | 19353 | 577 | 0.02981 | 0.00031003 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9946 |  | 2007-09-25 09:00 | 2007-09-25 | 2007-09-25 14:42 | Calculated | O410E |  |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 21 | 19353 | 7182 | 0.37111 | 0.0010851 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9947 |  | 2007-09-25 09:05 | 2007-09-25 | 2007-09-25 11:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 122 | 1 | 19353 | 122 | 0.0063 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9948 |  | 2007-09-25 10:52 | 2007-09-25 | 2007-09-25 16:45 | Calculated | O410E |  |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 3 | 19353 | 1059 | 0.05472 | 0.00015501 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9949 |  | 2007-09-25 12:45 | 2007-09-25 | 2007-09-25 14:13 | Calculated | O410E | L256 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 5 | 19353 | 440 | 0.02274 | 0.00025836 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9952 |  | 2007-09-25 19:06 | 2007-09-25 | 2007-09-25 22:45 | Calculated | O410E | L256 | Drop-Out Fuses |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 219 | 5 | 19353 | 1095 | 0.05658 | 0.00025836 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9953 |  | 2007-09-26 08:06 | 2007-09-26 | 2007-09-26 09:31 | Calculated | O410E | LF | Drop-Out Fuses |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 1 | 19353 | 85 | 0.00439 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9954 |  | 2007-09-26 09:00 | 2007-09-26 | 2007-09-26 15:00 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 9 | 19353 | 3240 | 0.16742 | 0.00046504 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9955 |  | 2007-09-26 09:03 | 2007-09-26 | 2007-09-26 14:19 | Calculated | O410E | LF | Pole Mounted |  | Huirimu 121-04 | Remote Rural F | Huirimu | Arohena Zone Substation | Transformers : Internal Connections | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 316 | 2 | 19353 | 632 | 0.03266 | 0.00010334 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9956 |  | 2007-09-26 09:07 | 2007-09-26 | 2007-09-26 12:03 | Calculated | O410E | LF | Drop-Out Fuses |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 176 | 2 | 19353 | 352 | 0.01819 | 0.00010334 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9957 |  | 2007-09-26 09:22 | 2007-09-26 | 2007-09-26 14:51 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 329 | 1 | 19353 | 329 | 0.017 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9958 |  | 2007-09-27 09:02 | 2007-09-27 | 2007-09-27 12:49 | Calculated | O410E |  |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 227 | 6 | 19353 | 1362 | 0.07038 | 0.00031003 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9961 |  | 2007-09-27 10:20 | 2007-09-27 | 2007-09-28 12:31 | Calculated | O410E | LF | Pole Mounted |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Transformers : Internal Connections | Weather | Lightning |  | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1571 | 1 | 19353 | 1571 | 0.08118 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9959 |  | 2007-09-27 10:35 | 2007-09-27 | 2007-09-27 14:22 | Calculated | O410E |  |  |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 227 | 26 | 19353 | 5902 | 0.30497 | 0.0013435 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9960 |  | 2007-09-27 13:01 | 2007-09-27 | 2007-09-27 14:23 | Calculated | O410E | LF |  |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 82 | 19353 | 6724 | 0.34744 | 0.0042371 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9962 |  | 2007-09-28 10:04 | 2007-09-28 | 2007-09-28 12:09 | Calculated | O410E | LF | Drop-Out Fuses |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 125 | 1 | 19353 | 125 | 0.00646 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9963 |  | 2007-09-28 11:00 | 2007-09-28 | 2007-09-28 15:59 | Calculated | O410E | LV |  |  | Southern 409-03 | Remote Rural F | Southern | Manunui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 299 | 10 | 19353 | 2990 | 0.1545 | 0.00051672 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9964 |  | 2007-09-30 15:02 | 2007-09-30 | 2007-09-30 15:53 | Calculated | O410E | L332 | Drop-Out Fuses |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 51 | 2 | 19353 | 102 | 0.00527 | 0.00010334 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9965 |  | 2007-09-30 15:56 | 2007-09-30 | 2007-09-30 18:02 | Calculated | O410E | C806 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 46 | 19353 | 5796 | 0.29949 | 0.0023769 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9966 |  | 2007-09-30 17:22 | 2007-09-30 | 2007-09-30 21:52 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 270 | 1 | 19353 | 270 | 0.01395 | 5.1672e-05 | 0 | 0 | 2007/2008 | September-2007 | 9 | 2007
9967 |  | 2007-10-01 09:54 | 2007-10-01 | 2007-10-01 15:50 | Calculated | O410E | LV |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 21 | 19353 | 7476 | 0.3863 | 0.0010851 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9968 |  | 2007-10-01 10:25 | 2007-10-01 | 2007-10-01 11:40 | Calculated | O410E | L261 | Single Circuit |  | Caves 101-02 | Remote Rural F | Caves | Hangatiki Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 31 | 19353 | 2325 | 0.12014 | 0.0016018 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9969 |  | 2007-10-01 13:10 | 2007-10-01 | 2007-10-01 14:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 60 | 1 | 19353 | 60 | 0.0031 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9970 |  | 2007-10-01 23:27 | 2007-10-01 | 2007-10-01 23:36 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 3 | 19353 | 27 | 0.0014 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9971 |  | 2007-10-02 01:25 | 2007-10-02 | 2007-10-02 01:29 | Calculated | O410E | C242 & 796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 243 | 19353 | 972 | 0.05022 | 0.012556 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9972 |  | 2007-10-02 07:43 | 2007-10-02 | 2007-10-02 10:01 | Calculated | O410E | C1641 |  |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 8 | 19353 | 1104 | 0.05705 | 0.00041337 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9973 |  | 2007-10-02 09:29 | 2007-10-02 | 2007-10-02 10:08 | Calculated | O410E | S573 | Single Circuit |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 35 | 19353 | 1365 | 0.07053 | 0.0018085 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9974 |  | 2007-10-02 10:57 | 2007-10-02 | 2007-10-02 11:00 | Calculated | O410E | C242 & 796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 243 | 19353 | 729 | 0.03767 | 0.012556 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9977 |  | 2007-10-02 18:34 | 2007-10-02 | 2007-10-02 19:54 | Calculated | O410E | C429 |  |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 24 | 19353 | 1920 | 0.09921 | 0.0012401 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9976 |  | 2007-10-02 18:57 | 2007-10-02 | 2007-10-02 19:05 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 3 | 19353 | 24 | 0.00124 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9978 |  | 2007-10-02 20:58 | 2007-10-02 | 2007-10-02 21:43 | Calculated | O410E | C446 |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 29 | 19353 | 1305 | 0.06743 | 0.0014985 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9979 |  | 2007-10-03 06:52 | 2007-10-03 | 2007-10-03 08:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9980 |  | 2007-10-03 08:14 | 2007-10-03 | 2007-10-03 10:18 | Calculated | O410E | C1536 |  |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning |  | Lightning Damage to Conductor | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 7 | 19353 | 868 | 0.04485 | 0.0003617 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9981 |  | 2007-10-03 08:17 | 2007-10-03 | 2007-10-03 10:35 | Calculated | O410E | LF | Drop-Out Fuses |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 138 | 3 | 19353 | 414 | 0.02139 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9982 |  | 2007-10-03 09:33 | 2007-10-03 | 2007-10-03 11:04 | Calculated | O410E |  |  |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 22 | 19353 | 2002 | 0.10345 | 0.0011368 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9983 |  | 2007-10-03 10:21 | 2007-10-03 | 2007-10-03 12:32 | Calculated | O410E | L1621 | Drop-Out Fuses |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 131 | 6 | 19353 | 786 | 0.04061 | 0.00031003 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9984 |  | 2007-10-03 12:45 | 2007-10-03 | 2007-10-03 13:40 | Calculated | O410E | C1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 13 | 19353 | 715 | 0.03695 | 0.00067173 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9985 |  | 2007-10-03 12:57 | 2007-10-03 | 2007-10-03 14:16 | Calculated | O410E | C1335 |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 13 | 19353 | 1027 | 0.05307 | 0.00067173 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9986 |  | 2007-10-03 13:15 | 2007-10-03 | 2007-10-03 14:51 | Calculated | O410E | L677 | Drop-Out Fuses |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 96 | 8 | 19353 | 768 | 0.03968 | 0.00041337 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9988 |  | 2007-10-03 17:00 | 2007-10-03 | 2007-10-03 17:05 | Calculated | O410E | S501 | Single Circuit |  | Waitomo 108-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 249 | 19353 | 1245 | 0.06433 | 0.012866 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9989 |  | 2007-10-04 08:30 | 2007-10-04 | 2007-10-04 11:54 | Calculated | O410E | C368 |  |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 204 | 18 | 19353 | 3672 | 0.18974 | 0.00093009 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9991 |  | 2007-10-05 02:14 | 2007-10-05 | 2007-10-05 07:20 | Calculated | O410E | Links On Pole 269 | Pole Mounted |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 306 | 5 | 19353 | 1533 | 0.07921 | 0.00025836 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9992 |  | 2007-10-05 05:46 | 2007-10-05 | 2007-10-05 06:13 | Calculated | O410E | L332 | Drop-Out Fuses |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 27 | 2 | 19353 | 54 | 0.00279 | 0.00010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9994 |  | 2007-10-05 08:17 | 2007-10-05 | 2007-10-05 10:24 | Calculated | O410E | LF | Drop-Out Fuses |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 3 | 19353 | 381 | 0.01969 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9995 |  | 2007-10-05 08:25 | 2007-10-05 | 2007-10-05 11:56 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 211 | 2 | 19353 | 422 | 0.02181 | 0.00010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9996 |  | 2007-10-05 11:30 | 2007-10-05 | 2007-10-05 13:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 116 | 25 | 19353 | 2900 | 0.14985 | 0.0012918 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9997 |  | 2007-10-05 12:02 | 2007-10-05 | 2007-10-05 13:17 | Calculated | O410E |  |  |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 75 | 6 | 19353 | 450 | 0.02325 | 0.00031003 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
9998 |  | 2007-10-05 12:16 | 2007-10-05 | 2007-10-05 14:12 | Calculated | O410E | C296 | Single Circuit |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Wraplock Deadend | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 139 | 19353 | 16124 | 0.83315 | 0.0071823 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10000 |  | 2007-10-08 08:40 | 2007-10-08 | 2007-10-08 09:24 | Calculated | O410E | LF | Drop-Out Fuses |  | Caves 101-06 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 44 | 1 | 19353 | 44 | 0.00227 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10001 |  | 2007-10-08 10:06 | 2007-10-08 | 2007-10-08 15:41 | Calculated | O410E |  |  |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 335 | 6 | 19353 | 2010 | 0.10386 | 0.00031003 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10002 |  | 2007-10-08 10:21 | 2007-10-08 | 2007-10-08 12:06 | Calculated | O410E | C684 |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 37 | 19353 | 3920 | 0.20255 | 0.0019118 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10003 |  | 2007-10-09 09:01 | 2007-10-09 | 2007-10-09 14:50 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 349 | 4 | 19353 | 1396 | 0.07213 | 0.00020669 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10005 |  | 2007-10-10 10:04 | 2007-10-10 | 2007-10-10 11:59 | Calculated | O410E |  |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 18 | 19353 | 2070 | 0.10696 | 0.00093009 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10008 |  | 2007-10-11 09:00 | 2007-10-11 | 2007-10-11 12:29 | Calculated | O410E |  |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 209 | 4 | 19353 | 836 | 0.0432 | 0.00020669 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10010 |  | 2007-10-11 10:46 | 2007-10-11 | 2007-10-11 11:33 | Calculated | O410E | LF | Pole Mounted |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 1 | 19353 | 47 | 0.00243 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10013 |  | 2007-10-12 08:01 | 2007-10-12 | 2007-10-12 09:00 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 59 | 2 | 19353 | 118 | 0.0061 | 0.00010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10016 |  | 2007-10-12 10:13 | 2007-10-12 | 2007-10-12 11:26 | Calculated | O410E | C296 | Single Circuit |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning |  | Lightning Damage to Structure/Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 139 | 19353 | 10147 | 0.52431 | 0.0071823 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10018 |  | 2007-10-12 11:11 | 2007-10-12 | 2007-10-12 11:15 | Calculated | O410E | C242 & 796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 243 | 19353 | 972 | 0.05022 | 0.012556 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10020 |  | 2007-10-14 02:55 | 2007-10-14 | 2007-10-14 05:52 | Calculated | O410E | C758 |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 83 | 19353 | 14691 | 0.75911 | 0.0042887 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10021 |  | 2007-10-14 03:50 | 2007-10-14 | 2007-10-14 08:49 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 299 | 3 | 19353 | 897 | 0.04635 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10022 |  | 2007-10-14 10:11 | 2007-10-14 | 2007-10-14 14:42 | Calculated | O410E | C758 | Single Circuit |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Conductor - Bare Copper | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 271 | 83 | 19353 | 22493 | 1.1623 | 0.0042887 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10023 |  | 2007-10-14 10:14 | 2007-10-14 | 2007-10-14 13:48 | Calculated | O410E | C1627 | Single Circuit |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare Copper | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 6 | 19353 | 1284 | 0.06635 | 0.00031003 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10025 |  | 2007-10-14 10:33 | 2007-10-14 | 2007-10-14 18:04 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 451 | 102 | 19353 | 46002 | 2.377 | 0.0052705 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10026 |  | 2007-10-14 16:41 | 2007-10-14 | 2007-10-14 17:37 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 56 | 3 | 19353 | 168 | 0.00868 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10027 |  | 2007-10-14 17:24 | 2007-10-14 | 2007-10-14 22:40 | Calculated | O410E | C378 |  |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 316 | 37 | 19353 | 11722 | 0.60569 | 0.0019118 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10028 |  | 2007-10-15 06:21 | 2007-10-15 | 2007-10-15 08:15 | Calculated | O410E | C880 |  |  | Hakiaha 401-01 | Remote Rural F | Hakiaha | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 219 | 19353 | 25053 | 1.2945 | 0.011316 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10030 |  | 2007-10-15 11:09 | 2007-10-15 | 2007-10-15 12:20 | Calculated | O410E | L601 | Drop-Out Fuses |  | Western 403-04 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 71 | 16 | 19353 | 1136 | 0.0587 | 0.00082675 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10031 |  | 2007-10-15 11:13 | 2007-10-15 | 2007-10-15 13:11 | Calculated | O410E | L471 | Drop-Out Fuses |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 118 | 5 | 19353 | 590 | 0.03049 | 0.00025836 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10032 |  | 2007-10-15 12:12 | 2007-10-15 | 2007-10-15 12:55 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 43 | 3 | 19353 | 129 | 0.00667 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10033 |  | 2007-10-15 12:47 | 2007-10-15 | 2007-10-15 15:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 140 | 3 | 19353 | 420 | 0.0217 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10034 |  | 2007-10-15 16:26 | 2007-10-15 | 2007-10-15 16:33 | Calculated | O410E | C218 |  |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 52 | 19353 | 364 | 0.01881 | 0.0026869 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10035 |  | 2007-10-15 19:42 | 2007-10-15 | 2007-10-15 21:40 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 118 | 1 | 19353 | 118 | 0.0061 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10036 |  | 2007-10-16 07:02 | 2007-10-16 | 2007-10-16 08:20 | Calculated | O410E | LF | Drop-Out Fuses |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 78 | 2 | 19353 | 156 | 0.00806 | 0.00010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10037 |  | 2007-10-16 08:00 | 2007-10-16 | 2007-10-16 09:07 | Calculated | O410E | LF | Drop-Out Fuses |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 2 | 19353 | 134 | 0.00692 | 0.00010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10038 |  | 2007-10-16 11:35 | 2007-10-16 | 2007-10-16 12:06 | Calculated | O410E | LF |  |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 3 | 19353 | 93 | 0.00481 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10039 |  | 2007-10-16 11:56 | 2007-10-16 | 2007-10-16 12:34 | Calculated | O410E | L436 |  |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 3 | 19353 | 114 | 0.00589 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10040 |  | 2007-10-16 13:47 | 2007-10-16 | 2007-10-16 15:02 | Calculated | O410E | LF | Drop-Out Fuses |  | Waihaha 426-02 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10041 |  | 2007-10-17 08:03 | 2007-10-17 | 2007-10-17 09:17 | Calculated | O410E | L1297 | Drop-Out Fuses |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 74 | 47 | 19353 | 3478 | 0.17971 | 0.0024286 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10042 |  | 2007-10-17 09:37 | 2007-10-17 | 2007-10-17 11:24 | Calculated | O410E | L980 | Drop-Out Fuses |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 107 | 6 | 19353 | 642 | 0.03317 | 0.00031003 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10043 |  | 2007-10-17 09:41 | 2007-10-17 | 2007-10-17 12:47 | Calculated | O410E | C511 | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 186 | 20 | 19353 | 3723 | 0.19237 | 0.0010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10044 |  | 2007-10-17 13:29 | 2007-10-17 | 2007-10-17 13:31 | Calculated | O410E | C192 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 3569 | 19353 | 7138 | 0.36883 | 0.18442 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10045 |  | 2007-10-17 13:42 | 2007-10-17 | 2007-10-17 14:20 | Calculated | O410E | C316 |  |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 18 | 19353 | 684 | 0.03534 | 0.00093009 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10046 |  | 2007-10-17 13:57 | 2007-10-17 | 2007-10-17 13:58 | Calculated | O410E | C202 |  |  |  | Remote Rural F | Nihoniho 33 | Direct from Ongarue Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 321 | 19353 | 321 | 0.01659 | 0.016587 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10047 |  | 2007-10-17 13:59 | 2007-10-17 | 2007-10-17 16:08 | Calculated | O410E | LF | Drop-Out Fuses |  | Nihoniho 412-01 | Remote Rural F | Nihoniho | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 129 | 2 | 19353 | 258 | 0.01333 | 0.00010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10048 |  | 2007-10-17 14:02 | 2007-10-17 | 2007-10-17 14:51 | Calculated | O410E | C429 |  |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 24 | 19353 | 1176 | 0.06077 | 0.0012401 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10049 |  | 2007-10-17 14:09 | 2007-10-17 | 2007-10-17 17:24 | Calculated | O410E | LF | Pole Mounted |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation | Transformers : Internal Connections | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 195 | 19 | 19353 | 3705 | 0.19144 | 0.00098176 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10050 |  | 2007-10-17 14:33 | 2007-10-17 | 2007-10-17 15:30 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 57 | 1 | 19353 | 57 | 0.00295 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10052 |  | 2007-10-17 15:11 | 2007-10-17 | 2007-10-17 17:53 | Calculated | O410E | C560 |  |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 15 | 19353 | 2430 | 0.12556 | 0.00077507 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10053 |  | 2007-10-17 15:46 | 2007-10-17 | 2007-10-17 18:01 | Calculated | O410E | LF | Drop-Out Fuses |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 135 | 1 | 19353 | 135 | 0.00698 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10054 |  | 2007-10-17 16:18 | 2007-10-17 | 2007-10-17 17:22 | Calculated | O410E | L677 | Drop-Out Fuses |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 64 | 8 | 19353 | 512 | 0.02646 | 0.00041337 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10055 |  | 2007-10-17 17:51 | 2007-10-17 | 2007-10-17 17:55 | Calculated | O410E | C180 & 6143 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 4 | 19353 | 16 | 0.00083 | 0.00020669 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10056 |  | 2007-10-17 20:47 | 2007-10-17 | 2007-10-17 22:36 | Calculated | O410E | LF | Drop-Out Fuses |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 109 | 3 | 19353 | 329 | 0.017 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10057 |  | 2007-10-18 07:00 | 2007-10-18 | 2007-10-18 07:58 | Calculated | O410E | LF | Drop-Out Fuses |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 58 | 1 | 19353 | 58 | 0.003 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10058 |  | 2007-10-18 08:00 | 2007-10-18 | 2007-10-18 09:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 66 | 1 | 19353 | 66 | 0.00341 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10059 |  | 2007-10-18 08:00 | 2007-10-18 | 2007-10-18 09:27 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 87 | 2 | 19353 | 174 | 0.00899 | 0.00010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10061 |  | 2007-10-18 10:01 | 2007-10-18 | 2007-10-18 14:11 | Calculated | O410E |  |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 3 | 19353 | 750 | 0.03875 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10062 |  | 2007-10-18 10:14 | 2007-10-18 | 2007-10-18 15:05 | Calculated | O410E | LF |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 291 | 88 | 19353 | 25615 | 1.3236 | 0.0045471 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10064 |  | 2007-10-18 12:00 | 2007-10-18 | 2007-10-18 13:25 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 3 | 19353 | 257 | 0.01328 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10065 |  | 2007-10-18 13:30 | 2007-10-18 | 2007-10-18 14:27 | Calculated | O410E | LF | Single Circuit |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 57 | 25 | 19353 | 1436 | 0.0742 | 0.0012918 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10066 |  | 2007-10-18 15:30 | 2007-10-18 | 2007-10-18 16:56 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 86 | 1 | 19353 | 86 | 0.00444 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10067 |  | 2007-10-18 15:45 | 2007-10-18 | 2007-10-18 16:48 | Calculated | O410E | LF | Drop-Out Fuses |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 63 | 1 | 19353 | 63 | 0.00326 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10068 |  | 2007-10-18 16:15 | 2007-10-18 | 2007-10-18 17:10 | Calculated | O410E | LF | Drop-Out Fuses |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 55 | 1 | 19353 | 55 | 0.00284 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10070 |  | 2007-10-21 08:14 | 2007-10-21 | 2007-10-21 08:24 | Calculated | O410E | C992 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 4 | 19353 | 40 | 0.00207 | 0.00020669 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10071 |  | 2007-10-21 13:10 | 2007-10-21 | 2007-10-21 17:46 | Calculated | O410E | C1335 | Single Circuit |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Insulator - Disc | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 276 | 13 | 19353 | 3588 | 0.1854 | 0.00067173 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10072 |  | 2007-10-21 13:39 | 2007-10-21 | 2007-10-21 16:42 | Calculated | O410E | C1512 |  |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 139 | 19353 | 25548 | 1.3201 | 0.0071823 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10073 |  | 2007-10-21 14:15 | 2007-10-21 | 2007-10-21 15:05 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-09 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 50 | 1 | 19353 | 50 | 0.00258 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10074 |  | 2007-10-21 19:50 | 2007-10-21 | 2007-10-21 20:26 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 36 | 3 | 19353 | 108 | 0.00558 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10075 |  | 2007-10-22 00:19 | 2007-10-22 | 2007-10-22 07:57 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 458 | 3 | 19353 | 1374 | 0.071 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10076 |  | 2007-10-22 11:37 | 2007-10-22 | 2007-10-22 13:09 | Calculated | O410E | C108 |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 30 | 19353 | 2760 | 0.14261 | 0.0015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10077 |  | 2007-10-23 09:34 | 2007-10-23 | 2007-10-23 10:15 | Calculated | O410E |  |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 25 | 19353 | 1047 | 0.0541 | 0.0012918 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10078 |  | 2007-10-23 10:21 | 2007-10-23 | 2007-10-23 11:21 | Calculated | O410E | LF |  |  | Caves 101-10 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 3 | 19353 | 180 | 0.0093 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10079 |  | 2007-10-23 11:47 | 2007-10-23 | 2007-10-23 13:32 | Calculated | O410E | LF | Drop-Out Fuses |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 105 | 1 | 19353 | 105 | 0.00543 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10080 |  | 2007-10-23 14:19 | 2007-10-23 | 2007-10-23 14:55 | Calculated | O410E | LF |  |  | Caves 101-10 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 3 | 19353 | 108 | 0.00558 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10082 |  | 2007-10-24 09:35 | 2007-10-24 | 2007-10-24 12:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 157 | 1 | 19353 | 157 | 0.00811 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10084 |  | 2007-10-24 10:11 | 2007-10-24 | 2007-10-24 13:35 | Calculated | O410E | LF |  |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 204 | 26 | 19353 | 5304 | 0.27407 | 0.0013435 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10085 |  | 2007-10-24 23:04 | 2007-10-24 | 2007-10-24 23:08 | Calculated | O410E | C242 & 796 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 243 | 19353 | 972 | 0.05022 | 0.012556 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10087 |  | 2007-10-25 10:35 | 2007-10-25 | 2007-10-25 15:40 | Calculated | O410E | LF |  |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 2 | 19353 | 610 | 0.03152 | 0.00010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10088 |  | 2007-10-26 09:31 | 2007-10-26 | 2007-10-26 15:57 | Calculated | O410E |  |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 386 | 5 | 19353 | 1931 | 0.09978 | 0.00025836 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10089 |  | 2007-10-26 13:14 | 2007-10-26 | 2007-10-26 14:38 | Calculated | O410E | L1617 | Single Circuit |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 2 | 19353 | 168 | 0.00868 | 0.00010334 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10092 |  | 2007-10-27 09:12 | 2007-10-27 | 2007-10-27 15:54 | Calculated | O410E | LF |  |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 402 | 1 | 19353 | 402 | 0.02077 | 5.1672e-05 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10093 |  | 2007-10-29 09:17 | 2007-10-29 | 2007-10-29 10:28 | Calculated | O410E |  |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 54 | 19353 | 3881 | 0.20054 | 0.0027903 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10095 |  | 2007-10-29 11:26 | 2007-10-29 | 2007-10-29 13:00 | Calculated | O410E | S331 | Drop-Out Fuses |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 17 | 19353 | 1598 | 0.08257 | 0.00087842 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10097 |  | 2007-10-30 09:00 | 2007-10-30 | 2007-10-30 13:30 | Calculated | O410E |  |  |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 270 | 16 | 19353 | 4320 | 0.22322 | 0.00082675 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10098 |  | 2007-10-30 09:57 | 2007-10-30 | 2007-10-30 11:21 | Calculated | O410E | LV |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 3 | 19353 | 252 | 0.01302 | 0.00015501 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10099 |  | 2007-10-31 08:03 | 2007-10-31 | 2007-10-31 10:36 | Calculated | O410E | L298 | Drop-Out Fuses |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 153 | 5 | 19353 | 765 | 0.03953 | 0.00025836 | 0 | 0 | 2007/2008 | October-2007 | 10 | 2007
10101 |  | 2007-11-01 06:30 | 2007-11-01 | 2007-11-01 06:39 | Calculated | O410E | C992 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 961 | 19353 | 8649 | 0.44691 | 0.049656 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10102 |  | 2007-11-01 08:13 | 2007-11-01 | 2007-11-01 09:43 | Calculated | O410E | LF | Drop-Out Fuses |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 90 | 2 | 19353 | 180 | 0.0093 | 0.00010334 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10103 |  | 2007-11-01 11:48 | 2007-11-01 | 2007-11-01 12:59 | Calculated | O410E | LF |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 2 | 19353 | 142 | 0.00734 | 0.00010334 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10104 |  | 2007-11-01 15:39 | 2007-11-01 | 2007-11-01 17:06 | Calculated | O410E | C107 | Single Circuit |  | Benneydale 103-04 | Remote Rural F | Benneydale | Waitete Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 341 | 19353 | 29820 | 1.5409 | 0.01762 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10105 |  | 2007-11-02 08:30 | 2007-11-02 | 2007-11-02 12:25 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 235 | 54 | 19353 | 12727 | 0.65762 | 0.0027903 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10106 |  | 2007-11-02 16:31 | 2007-11-02 | 2007-11-02 17:52 | Calculated | O410E | L919 | Drop-Out Fuses |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 81 | 6 | 19353 | 486 | 0.02511 | 0.00031003 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10108 |  | 2007-11-05 09:42 | 2007-11-05 | 2007-11-05 15:02 | Calculated | O410E |  |  |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 320 | 35 | 19353 | 11200 | 0.57872 | 0.0018085 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10109 |  | 2007-11-05 10:00 | 2007-11-05 | 2007-11-05 11:10 | Calculated | O410E | L509 | Drop-Out Fuses |  | Rural 126-02 | Remote Rural F | Rural | Taharoa Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 70 | 7 | 19353 | 490 | 0.02532 | 0.0003617 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10110 |  | 2007-11-05 11:15 | 2007-11-05 | 2007-11-05 11:56 | Calculated | O410E | L581 | Single Circuit |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 34 | 19353 | 1413 | 0.07301 | 0.0017568 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10111 |  | 2007-11-06 08:27 | 2007-11-06 | 2007-11-06 10:31 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 124 | 1 | 19353 | 124 | 0.00641 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10112 |  | 2007-11-06 08:46 | 2007-11-06 | 2007-11-06 10:43 | Calculated | O410E |  |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 10 | 19353 | 1179 | 0.06092 | 0.00051672 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10113 |  | 2007-11-06 09:41 | 2007-11-06 | 2007-11-06 14:01 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 260 | 17 | 19353 | 4420 | 0.22839 | 0.00087842 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10114 |  | 2007-11-06 12:30 | 2007-11-06 | 2007-11-06 16:46 | Calculated | O410E |  |  |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 256 | 416 | 19353 | 106496 | 5.5028 | 0.021495 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10115 |  | 2007-11-07 09:31 | 2007-11-07 | 2007-11-07 14:30 | Calculated | O410E |  |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 299 | 17 | 19353 | 5083 | 0.26265 | 0.00087842 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10117 |  | 2007-11-07 10:01 | 2007-11-07 | 2007-11-07 13:04 | Calculated | O410E |  |  |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 183 | 21 | 19353 | 3843 | 0.19857 | 0.0010851 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10118 |  | 2007-11-07 10:56 | 2007-11-07 | 2007-11-07 12:35 | Calculated | O410E | L354 | Single Circuit |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 3 | 19353 | 297 | 0.01535 | 0.00015501 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10116 |  | 2007-11-08 09:58 | 2007-11-08 | 2007-11-08 11:25 | Calculated | O410E | S193 | Single Circuit |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 17 | 19353 | 1479 | 0.07642 | 0.00087842 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10119 |  | 2007-11-08 10:05 | 2007-11-08 | 2007-11-08 14:42 | Calculated | O410E |  |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 277 | 5 | 19353 | 1385 | 0.07157 | 0.00025836 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10121 |  | 2007-11-08 13:06 | 2007-11-08 | 2007-11-08 13:59 | Calculated | O410E | S247 | Drop-Out Fuses |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 53 | 36 | 19353 | 1908 | 0.09859 | 0.0018602 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10122 |  | 2007-11-09 09:12 | 2007-11-09 | 2007-11-09 16:07 | Calculated | O410E |  |  |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 415 | 1 | 19353 | 415 | 0.02144 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10124 |  | 2007-11-09 10:04 | 2007-11-09 | 2007-11-09 13:26 | Calculated | O410E |  |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 202 | 5 | 19353 | 1010 | 0.05219 | 0.00025836 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10125 |  | 2007-11-09 12:21 | 2007-11-09 | 2007-11-09 14:58 | Calculated | O410E | LF |  |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 2 | 19353 | 314 | 0.01622 | 0.00010334 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10126 |  | 2007-11-09 16:17 | 2007-11-09 | 2007-11-09 16:23 | Calculated | O410E | S175 | ABS |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation | Switchgear : Contacts | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 6 | 30 | 19353 | 180 | 0.0093 | 0.0015501 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10127 |  | 2007-11-11 09:49 | 2007-11-11 | 2007-11-11 13:28 | Calculated | O410E | C1612 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 27 | 19353 | 5913 | 0.30553 | 0.0013951 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10129 |  | 2007-11-12 13:38 | 2007-11-12 | 2007-11-12 15:31 | Calculated | O410E | LV |  |  | Turoa 415-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 37 | 19353 | 4181 | 0.21604 | 0.0019118 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10130 |  | 2007-11-12 23:25 | 2007-11-12 | 2007-11-12 23:34 | Calculated | O410E | C6143 & 180 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 4 | 19353 | 39 | 0.00202 | 0.00020669 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10131 |  | 2007-11-13 09:12 | 2007-11-13 | 2007-11-13 11:17 | Calculated | O410E | LF | Drop-Out Fuses |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 125 | 1 | 19353 | 125 | 0.00646 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10132 |  | 2007-11-13 19:10 | 2007-11-13 | 2007-11-13 19:25 | Calculated | O410E | C798 | Single Circuit |  |  | Remote Rural F | Wairere / Mahoenui 33 | Wairere Zone Substation | OH Lines : Insulator - Pin | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 15 | 499 | 19353 | 7485 | 0.38676 | 0.025784 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10133 |  | 2007-11-14 00:36 | 2007-11-14 | 2007-11-14 00:45 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 3 | 19353 | 27 | 0.0014 | 0.00015501 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10134 |  | 2007-11-14 10:40 | 2007-11-14 | 2007-11-14 11:51 | Calculated | O410E | C5867 | Single Circuit |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 382 | 19353 | 27376 | 1.4146 | 0.019739 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10135 |  | 2007-11-14 11:27 | 2007-11-14 | 2007-11-14 12:22 | Calculated | O410E | L674 | Single Circuit |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 13 | 19353 | 715 | 0.03695 | 0.00067173 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10139 |  | 2007-11-14 14:00 | 2007-11-14 | 2007-11-14 15:37 | Calculated | O410E | LF | Drop-Out Fuses |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 97 | 22 | 19353 | 2134 | 0.11027 | 0.0011368 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10140 |  | 2007-11-14 14:12 | 2007-11-14 | 2007-11-14 19:06 | Calculated | O410E | C1321 | Single Circuit |  | Te Mapara 117-05 | Remote Rural F | Te Mapara | Wairere Zone Substation | OH Lines : Pole - Iron Rail | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 294 | 27 | 19353 | 7946 | 0.41058 | 0.0013951 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10141 |  | 2007-11-14 15:00 | 2007-11-14 | 2007-11-14 16:12 | Calculated | O410E | L1.27 | Drop-Out Fuses |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 72 | 6 | 19353 | 432 | 0.02232 | 0.00031003 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10142 |  | 2007-11-14 15:08 | 2007-11-14 | 2007-11-14 15:57 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 49 | 3 | 19353 | 147 | 0.0076 | 0.00015501 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10143 |  | 2007-11-14 15:50 | 2007-11-14 | 2007-11-14 17:51 | Calculated | O410E | L429 | Drop-Out Fuses |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 121 | 17 | 19353 | 2057 | 0.10629 | 0.00087842 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10144 |  | 2007-11-14 15:58 | 2007-11-14 | 2007-11-14 17:12 | Calculated | O410E | LF | Drop-Out Fuses |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 74 | 1 | 19353 | 74 | 0.00382 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10145 |  | 2007-11-14 20:27 | 2007-11-14 | 2007-11-14 21:48 | Calculated | O410E | L697 | Drop-Out Fuses |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 81 | 4 | 19353 | 324 | 0.01674 | 0.00020669 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10146 |  | 2007-11-15 09:07 | 2007-11-15 | 2007-11-15 14:46 | Calculated | O410E | LV |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 339 | 27 | 19353 | 9153 | 0.47295 | 0.0013951 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10147 |  | 2007-11-15 09:15 | 2007-11-15 | 2007-11-15 16:06 | Calculated | O410E | LF | Drop-Out Fuses |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 411 | 3 | 19353 | 1233 | 0.06371 | 0.00015501 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10148 |  | 2007-11-15 09:40 | 2007-11-15 | 2007-11-15 10:38 | Calculated | O410E |  |  |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 33 | 19353 | 1934 | 0.09993 | 0.0017052 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10150 |  | 2007-11-16 07:54 | 2007-11-16 | 2007-11-16 14:24 | Calculated | O410E | C1630 | 11 |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 390 | 33 | 19353 | 12884 | 0.66574 | 0.0017052 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10151 |  | 2007-11-16 08:04 | 2007-11-16 | 2007-11-16 09:25 | Calculated | O410E | L162 | 38 |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 81 | 4 | 19353 | 324 | 0.01674 | 0.00020669 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10152 |  | 2007-11-16 08:17 | 2007-11-16 | 2007-11-16 10:03 | Calculated | O410E | LF | 38 |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 106 | 1 | 19353 | 106 | 0.00548 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10153 |  | 2007-11-16 09:02 | 2007-11-16 | 2007-11-16 14:04 | Calculated | O410E |  |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 6 | 19353 | 1812 | 0.09363 | 0.00031003 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10154 |  | 2007-11-17 08:45 | 2007-11-17 | 2007-11-17 11:56 | Calculated | O410E | C1335 |  |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 13 | 19353 | 2483 | 0.1283 | 0.00067173 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10155 |  | 2007-11-18 13:17 | 2007-11-18 | 2007-11-18 14:25 | Calculated | O410E | C1632 |  |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 9 | 19353 | 612 | 0.03162 | 0.00046504 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10156 |  | 2007-11-19 08:03 | 2007-11-19 | 2007-11-19 09:08 | Calculated | O410E | LF | 38 |  |  | Remote Rural F | Lake Taupo 33 | Direct from Tokaanu Supply | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 65 | 1 | 19353 | 65 | 0.00336 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10157 |  | 2007-11-19 10:01 | 2007-11-19 | 2007-11-19 11:57 | Calculated | O410E |  |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 116 | 69 | 19353 | 8004 | 0.41358 | 0.0035653 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10158 |  | 2007-11-19 10:05 | 2007-11-19 | 2007-11-19 14:49 | Calculated | O410E |  |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 284 | 19 | 19353 | 5396 | 0.27882 | 0.00098176 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10160 |  | 2007-11-20 09:03 | 2007-11-20 | 2007-11-20 13:16 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 253 | 54 | 19353 | 13691 | 0.70744 | 0.0027903 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10161 |  | 2007-11-20 10:01 | 2007-11-20 | 2007-11-20 15:03 | Calculated | O410E |  |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 1 | 19353 | 302 | 0.0156 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10162 |  | 2007-11-21 08:59 | 2007-11-21 | 2007-11-21 17:04 | Calculated | O410E |  |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 485 | 17 | 19353 | 8245 | 0.42603 | 0.00087842 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10163 |  | 2007-11-21 11:38 | 2007-11-21 | 2007-11-21 11:56 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 3 | 19353 | 54 | 0.00279 | 0.00015501 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10164 |  | 2007-11-22 09:00 | 2007-11-22 | 2007-11-22 14:34 | Calculated | O410E |  |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 334 | 160 | 19353 | 53440 | 2.7613 | 0.0082675 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10165 |  | 2007-11-22 09:01 | 2007-11-22 | 2007-11-22 14:45 | Calculated | O410E |  |  |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 344 | 20 | 19353 | 6880 | 0.3555 | 0.0010334 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10166 |  | 2007-11-22 10:03 | 2007-11-22 | 2007-11-22 14:45 | Calculated | O410E |  |  |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 9 | 19353 | 2538 | 0.13114 | 0.00046504 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10168 |  | 2007-11-22 10:45 | 2007-11-22 | 2007-11-22 12:00 | Calculated | O410E | LF | 38 |  | Benneydale 103-03 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10167 |  | 2007-11-22 11:11 | 2007-11-22 | 2007-11-22 11:17 | Calculated | O410E | LF |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 3 | 19353 | 18 | 0.00093 | 0.00015501 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10169 |  | 2007-11-22 23:28 | 2007-11-22 | 2007-11-22 23:37 | Calculated | O410E | C180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 3 | 19353 | 27 | 0.0014 | 0.00015501 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10170 |  | 2007-11-23 07:35 | 2007-11-23 | 2007-11-23 11:55 | Calculated | O410E | L694 | 38 |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 260 | 6 | 19353 | 1560 | 0.08061 | 0.00031003 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10171 |  | 2007-11-23 09:57 | 2007-11-23 | 2007-11-23 14:10 | Calculated | O410E | LF |  |  | Turoa 415-02 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 253 | 1 | 19353 | 253 | 0.01307 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10172 |  | 2007-11-23 14:35 | 2007-11-23 | 2007-11-23 16:10 | Calculated | O410E | LF | 38 |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 46 | 19353 | 4370 | 0.2258 | 0.0023769 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10174 |  | 2007-11-26 10:01 | 2007-11-26 | 2007-11-26 13:35 | Calculated | O410E |  |  |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 214 | 19 | 19353 | 4066 | 0.2101 | 0.00098176 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10175 |  | 2007-11-26 13:52 | 2007-11-26 | 2007-11-26 15:14 | Calculated | O410E | LF |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 2 | 19353 | 164 | 0.00847 | 0.00010334 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10176 |  | 2007-11-26 18:43 | 2007-11-26 | 2007-11-26 19:14 | Calculated | O410E | LF |  |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 31 | 1 | 19353 | 31 | 0.0016 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10177 |  | 2007-11-26 20:56 | 2007-11-26 | 2007-11-27 12:48 | Calculated | O410E | LF | 43 |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 952 | 1 | 19353 | 952 | 0.04919 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10178 |  | 2007-11-27 06:21 | 2007-11-27 | 2007-11-27 07:52 | Calculated | O410E | LF | 38 |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 91 | 1 | 19353 | 91 | 0.0047 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10179 |  | 2007-11-27 09:13 | 2007-11-27 | 2007-11-27 11:49 | Calculated | O410E |  |  |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 156 | 4 | 19353 | 624 | 0.03224 | 0.00020669 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
21124 | Sandel Road | 2007-11-28 06:42 | 2007-11-28 | 2007-11-28 09:58 | Calculated | T1133 | T1133 - 3ph 15kVA POLEMNT | TF1133 - Transformer Fuse: TF1133 | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 2 | 19353 | 392 | 0.02026 | 0.00010334 | 16 | 3136 | 2007/2008 | November-2007 | 11 | 2007
10180 |  | 2007-11-28 09:00 | 2007-11-28 | 2007-11-28 17:00 | Calculated | O410E |  |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 480 | 160 | 19353 | 76800 | 3.9684 | 0.0082675 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10181 |  | 2007-11-28 11:45 | 2007-11-28 | 2007-11-28 14:00 | Calculated | O410E | LF | 38 |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 135 | 1 | 19353 | 135 | 0.00698 | 5.1672e-05 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10182 |  | 2007-11-29 09:00 | 2007-11-29 | 2007-11-29 16:55 | Calculated | O410E |  |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 475 | 11 | 19353 | 5225 | 0.26998 | 0.00056839 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10183 |  | 2007-11-30 10:02 | 2007-11-30 | 2007-11-30 12:23 | Calculated | O410E |  |  |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 141 | 33 | 19353 | 4653 | 0.24043 | 0.0017052 | 0 | 0 | 2007/2008 | November-2007 | 11 | 2007
10184 |  | 2007-12-01 09:00 | 2007-12-01 | 2007-12-01 14:46 | Calculated | O410E |  |  |  | Hangatiki East 102-01 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 346 | 3 | 19353 | 1038 | 0.05364 | 0.00015501 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10185 |  | 2007-12-03 08:03 | 2007-12-03 | 2007-12-03 09:10 | Calculated | O410E | L592 | 38 |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 20 | 19353 | 1340 | 0.06924 | 0.0010334 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10186 |  | 2007-12-03 08:32 | 2007-12-03 | 2007-12-03 10:41 | Calculated | O410E | LF | 38 |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 129 | 1 | 19353 | 129 | 0.00667 | 5.1672e-05 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10187 |  | 2007-12-04 07:21 | 2007-12-04 | 2007-12-04 08:35 | Calculated | O410E | LF | 38 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 74 | 2 | 19353 | 148 | 0.00765 | 0.00010334 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10188 |  | 2007-12-04 09:33 | 2007-12-04 | 2007-12-04 15:45 | Calculated | O410E |  |  |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 372 | 36 | 19353 | 13392 | 0.69199 | 0.0018602 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10189 |  | 2007-12-04 10:39 | 2007-12-04 | 2007-12-04 14:08 | Calculated | O410E |  |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 209 | 9 | 19353 | 1881 | 0.09719 | 0.00046504 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10190 |  | 2007-12-04 12:05 | 2007-12-04 | 2007-12-04 15:21 | Calculated | O410E |  |  |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 196 | 9 | 19353 | 1764 | 0.09115 | 0.00046504 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10192 |  | 2007-12-05 10:39 | 2007-12-05 | 2007-12-05 12:48 | Calculated | O410E | LF |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 129 | 2 | 19353 | 258 | 0.01333 | 0.00010334 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10193 |  | 2007-12-06 04:20 | 2007-12-06 | 2007-12-06 04:41 | Calculated | O410E | C262 | 11 |  | Nihoniho 412-02 | Remote Rural F | Nihoniho | Nihoniho Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 336 | 19353 | 7252 | 0.37472 | 0.017362 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10194 |  | 2007-12-06 09:04 | 2007-12-06 | 2007-12-06 14:33 | Calculated | O410E |  |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 329 | 13 | 19353 | 4277 | 0.221 | 0.00067173 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10195 |  | 2007-12-06 09:47 | 2007-12-06 | 2007-12-06 11:27 | Calculated | O410E | C440 |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 43 | 19353 | 4315 | 0.22296 | 0.0022219 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10197 |  | 2007-12-06 13:40 | 2007-12-06 | 2007-12-06 15:35 | Calculated | O410E | L284 | 38 |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 115 | 10 | 19353 | 1150 | 0.05942 | 0.00051672 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10198 |  | 2007-12-06 14:25 | 2007-12-06 | 2007-12-06 17:33 | Calculated | O410E | L638 | 38 |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 188 | 17 | 19353 | 3196 | 0.16514 | 0.00087842 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10200 |  | 2007-12-06 20:42 | 2007-12-06 | 2007-12-06 21:50 | Calculated | O410E | C2092 | 11 |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 108 | 19353 | 7367 | 0.38066 | 0.0055805 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10202 |  | 2007-12-06 20:47 | 2007-12-06 | 2007-12-07 01:01 | Calculated | O410E | L363 | 38 |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 254 | 4 | 19353 | 1016 | 0.0525 | 0.00020669 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10203 |  | 2007-12-06 21:58 | 2007-12-06 | 2007-12-06 22:40 | Calculated | O410E | LF | 38 |  | Maihiihi 111-09 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 42 | 3 | 19353 | 126 | 0.00651 | 0.00015501 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10201 |  | 2007-12-06 23:03 | 2007-12-06 | 2007-12-07 00:46 | Calculated | O410E | C714 |  |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 101 | 19353 | 10403 | 0.53754 | 0.0052188 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10204 |  | 2007-12-07 07:28 | 2007-12-07 | 2007-12-07 07:57 | Calculated | O410E | LF | 38 |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 29 | 3 | 19353 | 87 | 0.0045 | 0.00015501 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10205 |  | 2007-12-07 10:19 | 2007-12-07 | 2007-12-07 10:46 | Calculated | O410E | C876 | 11 |  | Manunui 407-01 (was Affco) | Remote Rural F | Manunui | Manunui Zone Substation | OH Lines : Insulator - Pin | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 465 | 19353 | 12562 | 0.6491 | 0.024027 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10207 |  | 2007-12-07 11:25 | 2007-12-07 | 2007-12-07 11:54 | Calculated | O410E | LF |  |  | Maihiihi 111-09 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 3 | 19353 | 87 | 0.0045 | 0.00015501 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10208 |  | 2007-12-07 11:37 | 2007-12-07 | 2007-12-07 12:14 | Calculated | O410E | L363 | 38 |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 37 | 4 | 19353 | 148 | 0.00765 | 0.00020669 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10209 |  | 2007-12-07 13:40 | 2007-12-07 | 2007-12-07 15:17 | Calculated | O410E | S360 - 395 | 11 |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 52 | 19353 | 5044 | 0.26063 | 0.0026869 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10210 |  | 2007-12-07 23:06 | 2007-12-07 | 2007-12-07 23:07 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 243 | 19353 | 243 | 0.01256 | 0.012556 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10211 |  | 2007-12-08 07:44 | 2007-12-08 | 2007-12-08 09:50 | Calculated | O410E | L1386 | 38 |  | Mahoenui 113-05 | Remote Rural F | Piopio | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 126 | 4 | 19353 | 504 | 0.02604 | 0.00020669 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10212 |  | 2007-12-08 09:00 | 2007-12-08 | 2007-12-08 12:27 | Calculated | O410E | LF |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 207 | 3 | 19353 | 621 | 0.03209 | 0.00015501 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10213 |  | 2007-12-08 14:15 | 2007-12-08 | 2007-12-08 14:56 | Calculated | O410E | LF | 38 |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 41 | 46 | 19353 | 1886 | 0.09745 | 0.0023769 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10214 |  | 2007-12-08 15:55 | 2007-12-08 | 2007-12-08 16:40 | Calculated | O410E | LF | 38 |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 45 | 57 | 19353 | 2565 | 0.13254 | 0.0029453 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10215 |  | 2007-12-09 05:21 | 2007-12-09 | 2007-12-09 08:06 | Calculated | O410E | C417 | 11 |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 40 | 19353 | 6612 | 0.34165 | 0.0020669 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10216 |  | 2007-12-09 14:41 | 2007-12-09 | 2007-12-09 18:21 | Calculated | O410E | C806 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 220 | 46 | 19353 | 10120 | 0.52292 | 0.0023769 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10217 |  | 2007-12-10 02:12 | 2007-12-10 | 2007-12-10 02:15 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 243 | 19353 | 729 | 0.03767 | 0.012556 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10218 |  | 2007-12-10 07:42 | 2007-12-10 | 2007-12-10 10:26 | Calculated | O410E | LF | 38 |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 164 | 1 | 19353 | 164 | 0.00847 | 5.1672e-05 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10219 |  | 2007-12-10 09:06 | 2007-12-10 | 2007-12-10 11:31 | Calculated | O410E |  |  |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 145 | 34 | 19353 | 4930 | 0.25474 | 0.0017568 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10220 |  | 2007-12-10 09:23 | 2007-12-10 | 2007-12-10 16:01 | Calculated | O410E |  |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 398 | 2 | 19353 | 796 | 0.04113 | 0.00010334 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10221 |  | 2007-12-10 10:15 | 2007-12-10 | 2007-12-10 11:37 | Calculated | O410E | C806 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 46 | 19353 | 3772 | 0.19491 | 0.0023769 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10223 |  | 2007-12-10 15:54 | 2007-12-10 | 2007-12-10 16:46 | Calculated | O410E | S1327 - 1355 | 11 |  | Piopio 116-01 | Remote Rural F | Piopio | Wairere Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 17 | 19353 | 884 | 0.04568 | 0.00087842 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10224 |  | 2007-12-11 09:07 | 2007-12-11 | 2007-12-11 12:19 | Calculated | O410E |  |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 192 | 255 | 19353 | 48960 | 2.5298 | 0.013176 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10225 |  | 2007-12-11 09:33 | 2007-12-11 | 2007-12-11 15:31 | Calculated | O410E |  |  |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 358 | 5 | 19353 | 1790 | 0.09249 | 0.00025836 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10226 |  | 2007-12-11 10:02 | 2007-12-11 | 2007-12-11 14:20 | Calculated | O410E |  |  |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 39 | 19353 | 10062 | 0.51992 | 0.0020152 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10227 |  | 2007-12-12 09:35 | 2007-12-12 | 2007-12-12 16:13 | Calculated | O410E |  |  |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 398 | 5 | 19353 | 1990 | 0.10283 | 0.00025836 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10229 |  | 2007-12-13 08:45 | 2007-12-13 | 2007-12-13 11:06 | Calculated | O410E | LF | 38 |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 141 | 2 | 19353 | 282 | 0.01457 | 0.00010334 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10230 |  | 2007-12-13 09:08 | 2007-12-13 | 2007-12-13 10:27 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 79 | 10 | 19353 | 790 | 0.04082 | 0.00051672 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10231 |  | 2007-12-13 09:34 | 2007-12-13 | 2007-12-13 13:53 | Calculated | O410E |  |  |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 259 | 5 | 19353 | 1295 | 0.06691 | 0.00025836 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10232 |  | 2007-12-13 09:49 | 2007-12-13 | 2007-12-13 14:51 | Calculated | O410E |  |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 7 | 19353 | 2114 | 0.10923 | 0.0003617 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10019 |  | 2007-12-13 21:51 | 2007-12-13 | 2007-12-13 23:15 | Calculated | O410E | C316 |  |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 18 | 19353 | 1512 | 0.07813 | 0.00093009 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10233 |  | 2007-12-14 09:12 | 2007-12-14 | 2007-12-14 14:46 | Calculated | O410E |  |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 334 | 255 | 19353 | 85170 | 4.4009 | 0.013176 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10235 |  | 2007-12-14 15:10 | 2007-12-14 | 2007-12-14 16:44 | Calculated | O410E | L848 | 38 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 94 | 59 | 19353 | 5546 | 0.28657 | 0.0030486 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10236 |  | 2007-12-16 19:43 | 2007-12-16 | 2007-12-16 22:20 | Calculated | O410E | C417 |  |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 40 | 19353 | 6280 | 0.3245 | 0.0020669 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10237 |  | 2007-12-17 09:00 | 2007-12-17 | 2007-12-17 15:19 | Calculated | O410E |  |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 379 | 45 | 19353 | 17073 | 0.88219 | 0.0023252 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10238 |  | 2007-12-17 10:30 | 2007-12-17 | 2007-12-17 12:41 | Calculated | O410E | LF | 38 |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 131 | 4 | 19353 | 524 | 0.02708 | 0.00020669 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10241 |  | 2007-12-18 09:02 | 2007-12-18 | 2007-12-18 15:47 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 405 | 6 | 19353 | 2430 | 0.12556 | 0.00031003 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10242 |  | 2007-12-18 09:45 | 2007-12-18 | 2007-12-18 14:32 | Calculated | O410E |  |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 287 | 7 | 19353 | 2009 | 0.10381 | 0.0003617 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10243 |  | 2007-12-18 11:00 | 2007-12-18 | 2007-12-18 11:35 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 4 | 19353 | 140 | 0.00723 | 0.00020669 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10245 |  | 2007-12-18 12:15 | 2007-12-18 | 2007-12-18 14:14 | Calculated | O410E | C417 |  |  | Ohura 413-08 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 67 | 19353 | 7990 | 0.41286 | 0.003462 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10246 |  | 2007-12-18 15:00 | 2007-12-18 | 2007-12-18 15:44 | Calculated | O410E | S549 | 38 |  | Southern 409-02 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Bushings (fixed Insulation) | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 44 | 10 | 19353 | 440 | 0.02274 | 0.00051672 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10247 |  | 2007-12-19 09:30 | 2007-12-19 | 2007-12-19 10:26 | Calculated | O410E | LF | 38 |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 56 | 2 | 19353 | 112 | 0.00579 | 0.00010334 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10248 |  | 2007-12-19 10:00 | 2007-12-19 | 2007-12-19 11:27 | Calculated | O410E | LF | 38 |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Bushings (fixed Insulation) | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 87 | 9 | 19353 | 789 | 0.04077 | 0.00046504 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10249 |  | 2007-12-19 19:45 | 2007-12-19 | 2007-12-20 00:04 | Calculated | O410E | LF | 43 |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 259 | 12 | 19353 | 3108 | 0.1606 | 0.00062006 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10250 |  | 2007-12-20 01:00 | 2007-12-20 | 2007-12-20 01:00 | Calculated | O410E | C792 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 2 | 19353 | 0 | 0 | 0.00010334 | 2 | 0 | 2007/2008 | December-2007 | 12 | 2007
10251 |  | 2007-12-20 02:51 | 2007-12-20 | 2007-12-20 03:01 | Calculated | O410E | C6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 4 | 19353 | 40 | 0.00207 | 0.00020669 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10252 |  | 2007-12-20 09:12 | 2007-12-20 | 2007-12-20 11:37 | Calculated | O410E |  |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 145 | 137 | 19353 | 19874 | 1.0269 | 0.007079 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10253 |  | 2007-12-20 09:40 | 2007-12-20 | 2007-12-20 10:33 | Calculated | O410E |  |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 53 | 63 | 19353 | 3340 | 0.17258 | 0.0032553 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10254 |  | 2007-12-20 10:15 | 2007-12-20 | 2007-12-20 13:47 | Calculated | O410E |  |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 212 | 35 | 19353 | 7420 | 0.3834 | 0.0018085 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10255 |  | 2007-12-20 10:19 | 2007-12-20 | 2007-12-20 11:44 | Calculated | O410E | L1529 | 38 |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 85 | 2 | 19353 | 170 | 0.00878 | 0.00010334 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10256 |  | 2007-12-20 10:27 | 2007-12-20 | 2007-12-20 11:56 | Calculated | O410E | LF | 38 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 89 | 1 | 19353 | 89 | 0.0046 | 5.1672e-05 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10257 |  | 2007-12-20 17:06 | 2007-12-20 | 2007-12-20 17:18 | Calculated | O410E | LF |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 1 | 19353 | 12 | 0.00062 | 5.1672e-05 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10258 |  | 2007-12-23 17:01 | 2007-12-23 | 2007-12-23 17:08 | Calculated | O410E | C798 |  |  |  | Remote Rural F | Wairere / Mahoenui 33 | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 7 | 512 | 19353 | 3584 | 0.18519 | 0.026456 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10259 |  | 2007-12-24 09:30 | 2007-12-24 | 2007-12-24 10:37 | Calculated | O410E | LF | 11 |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | OH Lines : Surge Diverters | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 1 | 19353 | 67 | 0.00346 | 5.1672e-05 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10260 |  | 2007-12-26 07:18 | 2007-12-26 | 2007-12-26 08:44 | Calculated | O410E | C867 | 11 |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 382 | 19353 | 33106 | 1.7106 | 0.019739 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10261 |  | 2007-12-26 13:15 | 2007-12-26 | 2007-12-26 14:24 | Calculated | O410E | L1648 | 38 |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 69 | 40 | 19353 | 2760 | 0.14261 | 0.0020669 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10265 |  | 2007-12-26 16:37 | 2007-12-26 | 2007-12-26 22:22 | Calculated | O410E | C779 | 35 |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Mechanism | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 345 | 42 | 19353 | 14497 | 0.74908 | 0.0021702 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10262 |  | 2007-12-26 17:30 | 2007-12-26 | 2007-12-26 18:58 | Calculated | O410E | L1538 | 38 |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 88 | 2 | 19353 | 176 | 0.00909 | 0.00010334 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10263 |  | 2007-12-26 18:59 | 2007-12-26 | 2007-12-26 20:30 | Calculated | O410E | LF | 38 |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 91 | 1 | 19353 | 91 | 0.0047 | 5.1672e-05 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10264 |  | 2007-12-26 20:46 | 2007-12-26 | 2007-12-26 22:27 | Calculated | O410E | L424 | 11 |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation | OH Lines : Pole - Softwood | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 10 | 19353 | 1010 | 0.05219 | 0.00051672 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10266 |  | 2007-12-27 06:41 | 2007-12-27 | 2007-12-27 09:48 | Calculated | O410E | LF | 38 |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 187 | 3 | 19353 | 561 | 0.02899 | 0.00015501 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10267 |  | 2007-12-27 06:55 | 2007-12-27 | 2007-12-27 10:30 | Calculated | O410E | C1612 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 215 | 27 | 19353 | 5805 | 0.29995 | 0.0013951 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10268 |  | 2007-12-27 13:35 | 2007-12-27 | 2007-12-27 15:18 | Calculated | O410E | LF | 38 |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 103 | 1 | 19353 | 103 | 0.00532 | 5.1672e-05 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10269 |  | 2007-12-28 10:10 | 2007-12-28 | 2007-12-28 10:55 | Calculated | O410E | LF | 38 |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 45 | 3 | 19353 | 135 | 0.00698 | 0.00015501 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10270 |  | 2007-12-28 11:27 | 2007-12-28 | 2007-12-28 13:00 | Calculated | O410E | LF | 38 |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 93 | 2 | 19353 | 186 | 0.00961 | 0.00010334 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10271 |  | 2007-12-30 13:39 | 2007-12-30 | 2007-12-30 14:26 | Calculated | O410E | C262 | 38 |  | Nihoniho 412-02 | Remote Rural F | Nihoniho | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 47 | 27 | 19353 | 1269 | 0.06557 | 0.0013951 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10272 |  | 2007-12-31 09:00 | 2007-12-31 | 2007-12-31 10:10 | Calculated | O410E | C623 |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 10 | 19353 | 700 | 0.03617 | 0.00051672 | 0 | 0 | 2007/2008 | December-2007 | 12 | 2007
10273 |  | 2008-01-03 09:26 | 2008-01-03 | 2008-01-03 10:40 | Calculated | O410E | LF |  |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 74 | 2 | 19353 | 148 | 0.00765 | 0.00010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10274 |  | 2008-01-03 13:57 | 2008-01-03 | 2008-01-03 15:13 | Calculated | O410E | LF |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 76 | 1 | 19353 | 76 | 0.00393 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10275 |  | 2008-01-04 09:04 | 2008-01-04 | 2008-01-04 14:14 | Calculated | O410E |  |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 310 | 11 | 19353 | 3410 | 0.1762 | 0.00056839 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10276 |  | 2008-01-04 11:15 | 2008-01-04 | 2008-01-04 12:28 | Calculated | O410E | LF | 43 |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10277 |  | 2008-01-04 12:37 | 2008-01-04 | 2008-01-04 13:39 | Calculated | O410E | LF |  |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 3 | 19353 | 186 | 0.00961 | 0.00015501 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10278 |  | 2008-01-05 09:18 | 2008-01-05 | 2008-01-05 11:26 | Calculated | O410E |  |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 128 | 3 | 19353 | 384 | 0.01984 | 0.00015501 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10279 |  | 2008-01-07 10:45 | 2008-01-07 | 2008-01-07 14:18 | Calculated | O410E | LF | 38 |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 213 | 1 | 19353 | 213 | 0.01101 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10280 |  | 2008-01-07 14:45 | 2008-01-07 | 2008-01-07 16:47 | Calculated | O410E | LF |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 2 | 19353 | 244 | 0.01261 | 0.00010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10281 |  | 2008-01-08 02:47 | 2008-01-08 | 2008-01-08 07:36 | Calculated | O410E | C218 |  |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 289 | 52 | 19353 | 15075 | 0.77895 | 0.0026869 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10282 |  | 2008-01-08 09:00 | 2008-01-08 | 2008-01-08 14:40 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 340 | 28 | 19353 | 9520 | 0.49191 | 0.0014468 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10283 |  | 2008-01-08 09:28 | 2008-01-08 | 2008-01-08 10:27 | Calculated | O410E | LF | 43 |  | Wharepapa 122-04 | Remote Rural F | Wharepapa | Arohena Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 1 | 19353 | 59 | 0.00305 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10285 |  | 2008-01-09 09:09 | 2008-01-09 | 2008-01-09 09:40 | Calculated | O410E | LF |  |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 3 | 19353 | 93 | 0.00481 | 0.00015501 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10287 |  | 2008-01-10 08:56 | 2008-01-10 | 2008-01-10 12:23 | Calculated | O410E | LF |  |  | Hangatiki East 102-01 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 207 | 3 | 19353 | 621 | 0.03209 | 0.00015501 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10288 |  | 2008-01-10 09:00 | 2008-01-10 | 2008-01-10 15:19 | Calculated | O410E |  |  |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 379 | 17 | 19353 | 6443 | 0.33292 | 0.00087842 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10289 |  | 2008-01-10 11:38 | 2008-01-10 | 2008-01-10 13:10 | Calculated | O410E | LF |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 1 | 19353 | 92 | 0.00475 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10290 |  | 2008-01-11 09:07 | 2008-01-11 | 2008-01-11 12:44 | Calculated | O410E | LF |  |  | Hangatiki East 102-01 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 217 | 1 | 19353 | 217 | 0.01121 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10291 |  | 2008-01-11 10:00 | 2008-01-11 | 2008-01-11 16:03 | Calculated | O410E | LF |  |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 363 | 2 | 19353 | 726 | 0.03751 | 0.00010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10292 |  | 2008-01-13 06:11 | 2008-01-13 | 2008-01-13 09:16 | Calculated | O410E | C287 |  |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 18 | 19353 | 3330 | 0.17207 | 0.00093009 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10293 |  | 2008-01-13 09:00 | 2008-01-13 | 2008-01-13 14:15 | Calculated | O410E |  |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 315 | 6 | 19353 | 1890 | 0.09766 | 0.00031003 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10294 |  | 2008-01-14 09:30 | 2008-01-14 | 2008-01-14 11:48 | Calculated | O410E |  | 38 |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 138 | 5 | 19353 | 690 | 0.03565 | 0.00025836 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10295 |  | 2008-01-14 10:00 | 2008-01-14 | 2008-01-14 11:31 | Calculated | O410E | LV |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 32 | 19353 | 2912 | 0.15047 | 0.0016535 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10296 |  | 2008-01-14 10:17 | 2008-01-14 | 2008-01-14 12:11 | Calculated | O410E | LF | 38 |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 114 | 1 | 19353 | 114 | 0.00589 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10297 |  | 2008-01-15 07:50 | 2008-01-15 | 2008-01-15 09:35 | Calculated | O410E | C287 |  |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 18 | 19353 | 1890 | 0.09766 | 0.00093009 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10298 |  | 2008-01-15 09:01 | 2008-01-15 | 2008-01-15 15:18 | Calculated | O410E |  |  |  | Whakamaru 120-03 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 377 | 102 | 19353 | 38454 | 1.987 | 0.0052705 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10299 |  | 2008-01-15 09:33 | 2008-01-15 | 2008-01-15 10:15 | Calculated | O410E |  |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 19 | 19353 | 800 | 0.04134 | 0.00098176 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10300 |  | 2008-01-15 10:03 | 2008-01-15 | 2008-01-15 14:11 | Calculated | O410E |  |  |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 5 | 19353 | 1240 | 0.06407 | 0.00025836 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10301 |  | 2008-01-16 08:15 | 2008-01-16 | 2008-01-16 11:44 | Calculated | O410E | L6584 | 39 |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 209 | 173 | 19353 | 36157 | 1.8683 | 0.0089392 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10302 |  | 2008-01-16 13:35 | 2008-01-16 | 2008-01-16 15:16 | Calculated | O410E | C5847 | 38 |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 101 | 26 | 19353 | 2648 | 0.13683 | 0.0013435 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10303 |  | 2008-01-16 20:37 | 2008-01-16 | 2008-01-17 01:14 | Calculated | O410E | LF | 21 |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Cables : Cable Box - Compound Filled | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 277 | 1 | 19353 | 277 | 0.01431 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10240 |  | 2008-01-17 01:14 | 2008-01-17 | 2008-01-17 01:14 | Calculated | O410E |  |  |  |  | Remote Rural F |  |  |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 2 | 19353 | 0 | 0 | 0.00010334 | 2 | 0 | 2007/2008 | January-2008 | 1 | 2008
10304 |  | 2008-01-17 09:02 | 2008-01-17 | 2008-01-17 15:31 | Calculated | O410E |  |  |  | Whakamaru 120-03 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 389 | 9 | 19353 | 3501 | 0.1809 | 0.00046504 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10305 |  | 2008-01-17 09:30 | 2008-01-17 | 2008-01-17 14:32 | Calculated | O410E |  |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 15 | 19353 | 4530 | 0.23407 | 0.00077507 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10306 |  | 2008-01-17 09:53 | 2008-01-17 | 2008-01-17 11:23 | Calculated | O410E | LF |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 3 | 19353 | 270 | 0.01395 | 0.00015501 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10307 |  | 2008-01-17 11:32 | 2008-01-17 | 2008-01-17 12:59 | Calculated | O410E | LF | 43 |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation | Transformers : Internal Connections | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 1 | 19353 | 87 | 0.0045 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10308 |  | 2008-01-17 12:36 | 2008-01-17 | 2008-01-17 13:32 | Calculated | O410E | LF |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 56 | 1 | 19353 | 56 | 0.00289 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10309 |  | 2008-01-17 14:19 | 2008-01-17 | 2008-01-17 17:23 | Calculated | O410E | C773 |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Asset Related | Other |  | Ground Subsidence | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 34 | 19353 | 6256 | 0.32326 | 0.0017568 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10310 |  | 2008-01-18 00:45 | 2008-01-18 | 2008-01-18 00:57 | Calculated | O410E | C513 |  |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 411 | 19353 | 4932 | 0.25484 | 0.021237 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10312 |  | 2008-01-18 09:35 | 2008-01-18 | 2008-01-18 10:07 | Calculated | O410E |  |  |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 32 | 43 | 19353 | 1411 | 0.07291 | 0.0022219 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10314 |  | 2008-01-18 11:15 | 2008-01-18 | 2008-01-18 11:42 | Calculated | O410E | L917 | 38 |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 27 | 20 | 19353 | 540 | 0.0279 | 0.0010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10315 |  | 2008-01-18 11:30 | 2008-01-18 | 2008-01-18 13:30 | Calculated | O410E | C1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 13 | 19353 | 1560 | 0.08061 | 0.00067173 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10313 |  | 2008-01-18 12:14 | 2008-01-18 | 2008-01-18 12:16 | Calculated | O410E |  |  |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 25 | 19353 | 50 | 0.00258 | 0.0012918 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10316 |  | 2008-01-19 09:27 | 2008-01-19 | 2008-01-19 11:25 | Calculated | O410E | C5847 | 38 |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 118 | 26 | 19353 | 3085 | 0.15941 | 0.0013435 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10317 |  | 2008-01-19 11:56 | 2008-01-19 | 2008-01-19 13:44 | Calculated | O410E | L364 | 38 |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 108 | 30 | 19353 | 3240 | 0.16742 | 0.0015501 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10318 |  | 2008-01-19 14:45 | 2008-01-19 | 2008-01-19 15:16 | Calculated | O410E | LF |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 1 | 19353 | 31 | 0.0016 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10319 |  | 2008-01-20 09:30 | 2008-01-20 | 2008-01-20 10:41 | Calculated | O410E |  |  |  | Hangatiki East 102-02 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 6 | 19353 | 426 | 0.02201 | 0.00031003 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10320 |  | 2008-01-20 10:40 | 2008-01-20 | 2008-01-20 15:44 | Calculated | O410E | L372 | 11 |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 304 | 14 | 19353 | 4256 | 0.21991 | 0.0007234 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10321 |  | 2008-01-20 18:30 | 2008-01-20 | 2008-01-20 20:12 | Calculated | O410E | C187 | 11 |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation | OH Lines : Conductor - Bare Copper | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 102 | 976 | 19353 | 99958 | 5.165 | 0.050431 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10322 |  | 2008-01-21 03:24 | 2008-01-21 | 2008-01-21 04:06 | Calculated | O410E | L592 | 38 |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 42 | 20 | 19353 | 840 | 0.0434 | 0.0010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10323 |  | 2008-01-21 07:24 | 2008-01-21 | 2008-01-21 07:24 | Calculated | O410E | L234 | 38 |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 0 | 26 | 19353 | 0 | 0 | 0.0013435 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10324 |  | 2008-01-21 07:51 | 2008-01-21 | 2008-01-21 10:21 | Calculated | O410E | LF | 38 |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 150 | 2 | 19353 | 300 | 0.0155 | 0.00010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10325 |  | 2008-01-21 09:00 | 2008-01-21 | 2008-01-21 11:15 | Calculated | O410E |  |  |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 135 | 52 | 19353 | 7020 | 0.36273 | 0.0026869 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10326 |  | 2008-01-21 09:20 | 2008-01-21 | 2008-01-21 17:48 | Calculated | O410E | C806 | 11 |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 508 | 46 | 19353 | 23391 | 1.2087 | 0.0023769 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10327 |  | 2008-01-21 10:02 | 2008-01-21 | 2008-01-21 11:12 | Calculated | O410E | LF |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 70 | 3 | 19353 | 210 | 0.01085 | 0.00015501 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10328 |  | 2008-01-21 14:11 | 2008-01-21 | 2008-01-21 15:21 | Calculated | O410E | LF |  |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 70 | 1 | 19353 | 70 | 0.00362 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10329 |  | 2008-01-21 14:25 | 2008-01-21 | 2008-01-21 16:32 | Calculated | O410E | C1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 13 | 19353 | 1651 | 0.08531 | 0.00067173 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10330 |  | 2008-01-21 21:00 | 2008-01-21 | 2008-01-22 02:17 | Calculated | O410E | C440 | 11 |  |  | Remote Rural F | Tihoi | Marotiri Zone Substation | OH Lines : Surge Diverters | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 317 | 43 | 19353 | 13667 | 0.7062 | 0.0022219 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10331 |  | 2008-01-22 08:54 | 2008-01-22 | 2008-01-22 08:56 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 243 | 19353 | 486 | 0.02511 | 0.012556 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10332 |  | 2008-01-22 09:15 | 2008-01-22 | 2008-01-22 12:43 | Calculated | O410E | C806 | 11 |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | OH Lines : Binder / Stirrup | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 208 | 46 | 19353 | 9601 | 0.4961 | 0.0023769 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10333 |  | 2008-01-22 09:36 | 2008-01-22 | 2008-01-22 11:00 | Calculated | O410E |  |  |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 20 | 19353 | 1680 | 0.08681 | 0.0010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10334 |  | 2008-01-22 10:42 | 2008-01-22 | 2008-01-22 11:40 | Calculated | O410E | LF | 38 |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 58 | 61 | 19353 | 3538 | 0.18281 | 0.003152 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10337 |  | 2008-01-22 10:55 | 2008-01-22 | 2008-01-22 13:07 | Calculated | O410E | L677 | 38 |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 132 | 8 | 19353 | 1056 | 0.05457 | 0.00041337 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10339 |  | 2008-01-22 11:12 | 2008-01-22 | 2008-01-22 13:58 | Calculated | O410E | L332 | 38 |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 166 | 2 | 19353 | 332 | 0.01715 | 0.00010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10335 |  | 2008-01-22 11:40 | 2008-01-22 | 2008-01-22 16:40 | Calculated | O410E | L433 | 38 |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 300 | 9 | 19353 | 2700 | 0.13951 | 0.00046504 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10336 |  | 2008-01-22 12:24 | 2008-01-22 | 2008-01-22 12:30 | Calculated | O410E | C242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 6 | 243 | 19353 | 1458 | 0.07534 | 0.012556 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10338 |  | 2008-01-22 12:35 | 2008-01-22 | 2008-01-22 14:05 | Calculated | O410E | LF | 38 |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 90 | 2 | 19353 | 180 | 0.0093 | 0.00010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10341 |  | 2008-01-22 14:10 | 2008-01-22 | 2008-01-22 16:44 | Calculated | O410E | C961 & 5004 | 11 |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | OH Lines : Conductor - Bare ACSR | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 438 | 19353 | 67744 | 3.5004 | 0.022632 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10343 |  | 2008-01-22 16:34 | 2008-01-22 | 2008-01-22 17:21 | Calculated | O410E | LF |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 2 | 19353 | 94 | 0.00486 | 0.00010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10344 |  | 2008-01-22 19:38 | 2008-01-22 | 2008-01-22 21:14 | Calculated | O410E | LF |  |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 3 | 19353 | 288 | 0.01488 | 0.00015501 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10345 |  | 2008-01-23 07:22 | 2008-01-23 | 2008-01-23 11:03 | Calculated | O410E | L693 | 38 |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 221 | 19 | 19353 | 4199 | 0.21697 | 0.00098176 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10346 |  | 2008-01-23 08:55 | 2008-01-23 | 2008-01-23 10:03 | Calculated | O410E | LF | 38 |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 68 | 1 | 19353 | 68 | 0.00351 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10347 |  | 2008-01-23 09:00 | 2008-01-23 | 2008-01-23 12:59 | Calculated | O410E |  |  |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 239 | 16 | 19353 | 3824 | 0.19759 | 0.00082675 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10348 |  | 2008-01-23 09:29 | 2008-01-23 | 2008-01-23 17:02 | Calculated | O410E |  |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 453 | 92 | 19353 | 41676 | 2.1535 | 0.0047538 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10349 |  | 2008-01-23 11:15 | 2008-01-23 | 2008-01-23 12:36 | Calculated | O410E | L917 | 38 |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 81 | 20 | 19353 | 1620 | 0.08371 | 0.0010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10350 |  | 2008-01-23 18:00 | 2008-01-23 | 2008-01-23 18:05 | Calculated | O410E | C792 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 5 | 1575 | 19353 | 7875 | 0.40691 | 0.081383 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10352 |  | 2008-01-24 06:37 | 2008-01-24 | 2008-01-24 09:49 | Calculated | O410E | LF | 38 |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 192 | 1 | 19353 | 192 | 0.00992 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10351 |  | 2008-01-24 07:00 | 2008-01-24 | 2008-01-24 08:44 | Calculated | O410E | C5005 | 42 |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply | Transformers : Internal Connections | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 648 | 19353 | 67435 | 3.4845 | 0.033483 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10353 |  | 2008-01-24 07:19 | 2008-01-24 | 2008-01-24 10:15 | Calculated | O410E | LF | 38 |  | Whakamaru 120-02 | Remote Rural F | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 176 | 56 | 19353 | 9856 | 0.50928 | 0.0028936 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10354 |  | 2008-01-24 09:18 | 2008-01-24 | 2008-01-24 12:16 | Calculated | O410E |  |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 178 | 5 | 19353 | 890 | 0.04599 | 0.00025836 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10355 |  | 2008-01-24 10:32 | 2008-01-24 | 2008-01-24 11:17 | Calculated | O410E | LF |  |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 41 | 19353 | 1845 | 0.09533 | 0.0021185 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10356 |  | 2008-01-24 12:30 | 2008-01-24 | 2008-01-24 13:33 | Calculated | O410E | LF |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 6 | 19353 | 381 | 0.01969 | 0.00031003 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10357 |  | 2008-01-24 15:40 | 2008-01-24 | 2008-01-24 16:03 | Calculated | O410E | C1549 |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 20 | 19353 | 460 | 0.02377 | 0.0010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10358 |  | 2008-01-25 10:57 | 2008-01-25 | 2008-01-25 11:55 | Calculated | O410E | LF |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 2 | 19353 | 116 | 0.00599 | 0.00010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10359 |  | 2008-01-26 08:39 | 2008-01-26 | 2008-01-26 11:34 | Calculated | O410E |  |  |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 175 | 13 | 19353 | 2283 | 0.11797 | 0.00067173 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10360 |  | 2008-01-27 00:31 | 2008-01-27 | 2008-01-27 04:40 | Calculated | O410E | C609 | 11 |  | Rural 126-03 | Remote Rural F | Rural | Taharoa Zone Substation | OH Lines : Conductor - Bare ACSR | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 249 | 105 | 19353 | 26145 | 1.351 | 0.0054255 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10361 |  | 2008-01-27 20:05 | 2008-01-27 | 2008-01-27 20:13 | Calculated | O410E | C792 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1575 | 19353 | 12600 | 0.65106 | 0.081383 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10362 |  | 2008-01-28 09:23 | 2008-01-28 | 2008-01-28 11:31 | Calculated | O410E | S215-517-582 | 11 |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation | OH Lines : Jumper - Bare ACSR | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 164 | 19353 | 20992 | 1.0847 | 0.0084741 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10363 |  | 2008-01-28 20:01 | 2008-01-28 | 2008-01-28 20:09 | Calculated | O410E | C792 |  |  |  | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1575 | 19353 | 12600 | 0.65106 | 0.081383 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10364 |  | 2008-01-29 09:00 | 2008-01-29 | 2008-01-29 13:22 | Calculated | O410E |  |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 262 | 12 | 19353 | 3144 | 0.16246 | 0.00062006 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10365 |  | 2008-01-29 09:53 | 2008-01-29 | 2008-01-29 12:36 | Calculated | O410E | LF |  |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 5 | 19353 | 815 | 0.04211 | 0.00025836 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10367 |  | 2008-01-30 05:00 | 2008-01-30 | 2008-01-30 11:52 | Calculated | O410E | LF | 38 |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 412 | 1 | 19353 | 412 | 0.02129 | 5.1672e-05 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10368 |  | 2008-01-30 09:01 | 2008-01-30 | 2008-01-30 15:21 | Calculated | O410E |  |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 380 | 72 | 19353 | 27360 | 1.4137 | 0.0037204 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10369 |  | 2008-01-30 09:31 | 2008-01-30 | 2008-01-30 14:45 | Calculated | O410E |  |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 314 | 15 | 19353 | 4710 | 0.24337 | 0.00077507 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10370 |  | 2008-01-30 12:28 | 2008-01-30 | 2008-01-30 13:26 | Calculated | O410E | LF |  |  | Hangatiki East 102-03 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 2 | 19353 | 116 | 0.00599 | 0.00010334 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10372 |  | 2008-01-31 09:44 | 2008-01-31 | 2008-01-31 15:37 | Calculated | O410E |  |  |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 8 | 19353 | 2824 | 0.14592 | 0.00041337 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10373 |  | 2008-01-31 10:00 | 2008-01-31 | 2008-01-31 15:26 | Calculated | O410E | LV |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 326 | 86 | 19353 | 28036 | 1.4487 | 0.0044438 | 0 | 0 | 2007/2008 | January-2008 | 1 | 2008
10375 |  | 2008-02-01 | 2008-02-01 | 2008-02-01 12:01 | Calculated | O410E |  |  |  |  | Remote Rural F | Matapuna | Borough Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2007/2008 | February-2008 | 2 | 2008
10376 |  | 2008-02-01 08:36 | 2008-02-01 | 2008-02-01 09:33 | Calculated | O410E | link 1.8 |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 57 | 36 | 19353 | 2052 | 0.10603 | 0.0018602 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10379 |  | 2008-02-01 08:47 | 2008-02-01 | 2008-02-01 14:53 | Calculated | O410E | Tx 8R25 |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 366 | 1 | 19353 | 366 | 0.01891 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10377 |  | 2008-02-01 09:22 | 2008-02-01 | 2008-02-01 15:57 | Calculated | O410E | RMS1.7-ABS 915-Link 1.8 |  |  | Hakiaha 401-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 395 | 36 | 19353 | 14220 | 0.73477 | 0.0018602 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10380 |  | 2008-02-01 09:59 | 2008-02-01 | 2008-02-01 15:29 | Calculated | O410E | LV fuses @ Tx 8R6 |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 86 | 19353 | 28380 | 1.4664 | 0.0044438 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10381 |  | 2008-02-01 14:40 | 2008-02-01 | 2008-02-01 14:41 | Calculated | O410E | Link 695 | 299 |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 3 | 19353 | 3 | 0.00016 | 0.00015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10378 |  | 2008-02-01 15:37 | 2008-02-01 | 2008-02-01 15:57 | Calculated | O410E | Link 1.8 |  |  | Hakiaha 401-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 20 | 36 | 19353 | 720 | 0.0372 | 0.0018602 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10382 |  | 2008-02-01 16:37 | 2008-02-01 | 2008-02-01 18:45 | Calculated | O410E | Tx 1529 | 999 |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 1 | 19353 | 128 | 0.00661 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10383 |  | 2008-02-01 18:29 | 2008-02-01 | 2008-02-01 18:29 | Calculated | O410E | Tx 9P1 | 299 |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation | Switchgear : Other | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 0 | 2 | 19353 | 1 | 5e-05 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
11248 |  | 2008-02-02 08:57 | 2008-02-02 | 2008-02-02 11:21 | Calculated | o410e | ABS 420 | 0 |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 144 | 19353 | 432 | 0.02232 | 0.0074407 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
11249 |  | 2008-02-02 19:30 | 2008-02-02 | 2008-02-02 19:38 | Calculated | o410e | OCB 798 | 0 |  |  | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 512 | 8 | 19353 | 4096 | 0.21165 | 0.00041337 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10384 |  | 2008-02-04 09:02 | 2008-02-04 | 2008-02-04 13:02 | Calculated | O410E | Link 6563 |  |  |  | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 240 | 33 | 19353 | 7920 | 0.40924 | 0.0017052 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10385 |  | 2008-02-04 09:31 | 2008-02-04 | 2008-02-04 14:37 | Calculated | O410E | L/L/B &Pole 104-113 |  |  | Oparure 107-04 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 306 | 5 | 19353 | 1530 | 0.07906 | 0.00025836 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10386 |  | 2008-02-04 10:05 | 2008-02-04 | 2008-02-04 11:12 | Calculated | O410E | Tx 385 |  |  | Gravel Scoop 109-05 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 1 | 19353 | 67 | 0.00346 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10387 |  | 2008-02-04 14:23 | 2008-02-04 | 2008-02-04 15:02 | Calculated | O410E | Recloser 1107 | 532 |  | Gravel Scoop 109-05 | Remote Rural F | Aria | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 65 | 19353 | 2535 | 0.13099 | 0.0033587 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10388 |  | 2008-02-05 09:31 | 2008-02-05 | 2008-02-05 10:22 | Calculated | O410E | Tx 14I1 |  |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 1 | 19353 | 51 | 0.00264 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10390 |  | 2008-02-05 09:40 | 2008-02-05 | 2008-02-05 12:02 | Calculated | O410E | Tx 2781 | 38 |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 142 | 1 | 19353 | 142 | 0.00734 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10389 |  | 2008-02-05 10:00 | 2008-02-05 | 2008-02-05 11:12 | Calculated | O410E | Link447 |  |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 72 | 23 | 19353 | 1656 | 0.08557 | 0.0011884 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10391 |  | 2008-02-05 11:51 | 2008-02-05 | 2008-02-05 12:09 | Calculated | O410E | Tx 1494 | 38 |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 18 | 1 | 19353 | 18 | 0.00093 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10392 |  | 2008-02-05 12:15 | 2008-02-05 | 2008-02-05 14:40 | Calculated | O410E | Tx 13L4 |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 145 | 3 | 19353 | 435 | 0.02248 | 0.00015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10393 |  | 2008-02-05 12:50 | 2008-02-05 | 2008-02-05 14:40 | Calculated | O410E | Tx 1117 | 38 |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 110 | 2 | 19353 | 220 | 0.01137 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10394 |  | 2008-02-05 15:19 | 2008-02-05 | 2008-02-05 16:56 | Calculated | O410E | Tx 869 | 38 |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 97 | 1 | 19353 | 97 | 0.00501 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10395 |  | 2008-02-05 17:20 | 2008-02-05 | 2008-02-05 17:38 | Calculated | O410E | OCB 180 |  |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 18 | 3 | 19353 | 54 | 0.00279 | 0.00015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10397 |  | 2008-02-06 00:44 | 2008-02-06 | 2008-02-06 00:50 | Calculated | O410E | OCB 242 &796 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 6 | 243 | 19353 | 1458 | 0.07534 | 0.012556 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10396 |  | 2008-02-06 18:02 | 2008-02-06 | 2008-02-06 23:59 | Calculated | O410E | Tx 7D17 |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 357 | 1 | 19353 | 357 | 0.01845 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10398 |  | 2008-02-07 11:00 | 2008-02-07 | 2008-02-07 13:12 | Calculated | O410E | Sectionaliser 277 |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 132 | 87 | 19353 | 11484 | 0.5934 | 0.0044954 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10400 |  | 2008-02-07 11:45 | 2008-02-07 | 2008-02-07 14:29 | Calculated | O410E | Tx 177 | 38 |  | Hangatiki East 102-01 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 164 | 3 | 19353 | 492 | 0.02542 | 0.00015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10399 |  | 2008-02-07 13:08 | 2008-02-07 | 2008-02-07 14:30 | Calculated | O410E | Tx 1409 | 64 |  | Rural 126-02 | Remote Rural F | Rural | Taharoa Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 2 | 19353 | 164 | 0.00847 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10401 |  | 2008-02-08 06:21 | 2008-02-08 | 2008-02-08 08:23 | Calculated | O410E | TX 2683 | 38 |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 122 | 1 | 19353 | 122 | 0.0063 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10402 |  | 2008-02-08 09:01 | 2008-02-08 | 2008-02-08 14:23 | Calculated | O410E | Link 292 |  |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 322 | 6 | 19353 | 1932 | 0.09983 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10403 |  | 2008-02-08 09:30 | 2008-02-08 | 2008-02-08 13:36 | Calculated | O410E | Link 1317 |  |  |  | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 246 | 6 | 19353 | 1476 | 0.07627 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10404 |  | 2008-02-08 09:30 | 2008-02-08 | 2008-02-08 14:56 | Calculated | O410E | Temp ABS#104-Jumpers |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 326 | 6 | 19353 | 1956 | 0.10107 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10405 |  | 2008-02-08 09:30 | 2008-02-08 | 2008-02-08 09:51 | Calculated | O410E | ABS399-Jumpers |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 8 | 19353 | 168 | 0.00868 | 0.00041337 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10407 |  | 2008-02-08 10:02 | 2008-02-08 | 2008-02-08 11:15 | Calculated | O410E | Tx 2455 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 2 | 19353 | 146 | 0.00754 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10408 |  | 2008-02-08 10:03 | 2008-02-08 | 2008-02-08 11:30 | Calculated | O410E | Tx 504 |  |  | McDonalds 110-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 27 | 19353 | 2349 | 0.12138 | 0.0013951 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10409 |  | 2008-02-08 13:00 | 2008-02-08 | 2008-02-08 13:40 | Calculated | O410E | ABS 161- 543 |  |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 63 | 19353 | 2520 | 0.13021 | 0.0032553 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10406 |  | 2008-02-08 14:30 | 2008-02-08 | 2008-02-08 14:56 | Calculated | O410E | ABS 399-Jumpers |  |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 6 | 19353 | 156 | 0.00806 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10410 |  | 2008-02-09 09:00 | 2008-02-09 | 2008-02-09 12:34 | Calculated | O410E | Link 710 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 4 | 19353 | 856 | 0.04423 | 0.00020669 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10411 |  | 2008-02-09 11:56 | 2008-02-09 | 2008-02-09 12:34 | Calculated | O410E | Sectionaliser 1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 4 | 19353 | 152 | 0.00785 | 0.00020669 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10412 |  | 2008-02-10 03:43 | 2008-02-10 | 2008-02-10 08:12 | Calculated | O410E | Sectionaliser 296-ABS 583 | 11 |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 269 | 17 | 19353 | 4573 | 0.23629 | 0.00087842 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10415 |  | 2008-02-10 03:43 | 2008-02-10 | 2008-02-10 10:46 | Calculated | O410E | ABS 583 | 11 |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 423 | 122 | 19353 | 51606 | 2.6666 | 0.0063039 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10413 |  | 2008-02-10 07:44 | 2008-02-10 | 2008-02-10 07:54 | Calculated | O410E | OCB 114-Sect 296 | 11 |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 104 | 19353 | 1040 | 0.05374 | 0.0053738 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10414 |  | 2008-02-10 08:49 | 2008-02-10 | 2008-02-10 09:02 | Calculated | O410E | Sect 296-ABS 583 | 11 |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 17 | 19353 | 221 | 0.01142 | 0.00087842 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10416 |  | 2008-02-10 09:00 | 2008-02-10 | 2008-02-10 11:42 | Calculated | O410E | Link 414 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 162 | 6 | 19353 | 972 | 0.05022 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10417 |  | 2008-02-10 14:17 | 2008-02-10 | 2008-02-10 15:46 | Calculated | O410E | Sectionaliser 296 | 35 |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Mechanism | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 89 | 138 | 19353 | 12282 | 0.63463 | 0.0071307 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10418 |  | 2008-02-10 14:17 | 2008-02-10 | 2008-02-10 17:26 | Calculated | O410E | Tx 2822 | 35 |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Mechanism | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 189 | 1 | 19353 | 189 | 0.00977 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10419 |  | 2008-02-10 21:28 | 2008-02-10 | 2008-02-10 23:59 | Calculated | O410E | Sectionaliser 296-ABS 583 | 11 |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Insulator - Disc | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 139 | 19353 | 20989 | 1.0845 | 0.0071823 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10420 |  | 2008-02-11 08:23 | 2008-02-11 | 2008-02-11 10:36 | Calculated | O410E | ABS 947 |  |  | Turoa 415-02 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 133 | 24 | 19353 | 3192 | 0.16494 | 0.0012401 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10421 |  | 2008-02-11 10:45 | 2008-02-11 | 2008-02-11 15:57 | Calculated | O410E | Link402 |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 312 | 19 | 19353 | 5928 | 0.30631 | 0.00098176 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10427 |  | 2008-02-12 05:40 | 2008-02-12 | 2008-02-12 07:41 | Calculated | O410E | Sect 379 |  |  |  | Remote Rural F | Manunui | Manunui Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 25 | 19353 | 3025 | 0.15631 | 0.0012918 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10422 |  | 2008-02-12 09:06 | 2008-02-12 | 2008-02-12 11:15 | Calculated | O410E | Magnafix 6187-6192 |  |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 129 | 123 | 19353 | 15867 | 0.81987 | 0.0063556 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10423 |  | 2008-02-12 09:35 | 2008-02-12 | 2008-02-12 16:17 | Calculated | O410E | Link 431 |  |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 402 | 5 | 19353 | 2010 | 0.10386 | 0.00025836 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10424 |  | 2008-02-12 10:59 | 2008-02-12 | 2008-02-12 12:34 | Calculated | O410E | Link 456 | 38 |  | Ohura 413-07 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 95 | 12 | 19353 | 1140 | 0.05891 | 0.00062006 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10425 |  | 2008-02-12 15:14 | 2008-02-12 | 2008-02-12 16:35 | Calculated | O410E | Recloser 455-Link456 |  |  | Ohura 413-07 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 3 | 19353 | 243 | 0.01256 | 0.00015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10426 |  | 2008-02-12 15:14 | 2008-02-12 | 2008-02-12 16:52 | Calculated | O410E | Link 456 |  |  | Ohura 413-07 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 12 | 19353 | 1176 | 0.06077 | 0.00062006 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10428 |  | 2008-02-13 08:02 | 2008-02-13 | 2008-02-13 10:29 | Calculated | O410E | Sect 379-Link916 | 11 |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation | OH Lines : Pole Fittings e.g OCB Hangers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 11 | 19353 | 1617 | 0.08355 | 0.00056839 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10430 |  | 2008-02-13 08:02 | 2008-02-13 | 2008-02-13 13:40 | Calculated | O410E | Link 5916 | 121 |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation | OH Lines : Pole Fittings e.g OCB Hangers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 338 | 14 | 19353 | 4732 | 0.24451 | 0.0007234 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10431 |  | 2008-02-13 08:15 | 2008-02-13 | 2008-02-13 09:14 | Calculated | O410E | TX 11 | 142 |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 47 | 19353 | 2773 | 0.14329 | 0.0024286 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10429 |  | 2008-02-13 09:03 | 2008-02-13 | 2008-02-13 09:17 | Calculated | O410E | Recloser 218-Sect379 | 11 |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation | OH Lines : Pole Fittings e.g OCB Hangers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 27 | 19353 | 378 | 0.01953 | 0.0013951 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10433 |  | 2008-02-13 09:32 | 2008-02-13 | 2008-02-13 15:25 | Calculated | O410E | ABS585 |  |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 33 | 19353 | 11649 | 0.60192 | 0.0017052 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10434 |  | 2008-02-13 10:11 | 2008-02-13 | 2008-02-13 10:54 | Calculated | O410E | Tx248 |  |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 2 | 19353 | 86 | 0.00444 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10435 |  | 2008-02-13 11:20 | 2008-02-13 | 2008-02-13 13:49 | Calculated | O410E | L1730 |  |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 7 | 19353 | 1043 | 0.05389 | 0.0003617 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10436 |  | 2008-02-13 13:00 | 2008-02-13 | 2008-02-13 18:37 | Calculated | O410E | 6187 |  |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 337 | 123 | 19353 | 41451 | 2.1418 | 0.0063556 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10437 |  | 2008-02-14 10:02 | 2008-02-14 | 2008-02-14 12:25 | Calculated | O410E | tx 20L64 |  |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 1 | 19353 | 143 | 0.00739 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10438 |  | 2008-02-14 10:15 | 2008-02-14 | 2008-02-14 10:59 | Calculated | O410E |  |  |  | Otorohanga 112-07 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 44 | 3 | 19353 | 132 | 0.00682 | 0.00015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10439 |  | 2008-02-14 13:19 | 2008-02-14 | 2008-02-14 14:18 | Calculated | O410E | tx1585 |  |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 32 | 19353 | 1888 | 0.09756 | 0.0016535 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10440 |  | 2008-02-14 14:12 | 2008-02-14 | 2008-02-14 14:49 | Calculated | O410E | tx438 |  |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 46 | 19353 | 1702 | 0.08795 | 0.0023769 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10441 |  | 2008-02-15 05:48 | 2008-02-15 | 2008-02-15 08:24 | Calculated | O410E | S505 |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 156 | 22 | 19353 | 3432 | 0.17734 | 0.0011368 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10442 |  | 2008-02-15 09:08 | 2008-02-15 | 2008-02-15 14:43 | Calculated | O410E | ABS967 |  |  | Hakiaha 401-02 | Remote Rural F | Hakiaha | Borough Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 335 | 13 | 19353 | 4355 | 0.22503 | 0.00067173 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10443 |  | 2008-02-15 09:27 | 2008-02-15 | 2008-02-15 14:17 | Calculated | O410E | TX2684 |  |  | Tihoi 124-02 (was Tihoi 124-05) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 290 | 5 | 19353 | 1450 | 0.07492 | 0.00025836 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10444 |  | 2008-02-15 10:27 | 2008-02-15 | 2008-02-15 12:34 | Calculated | O410E | 13G03 |  |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 1 | 19353 | 127 | 0.00656 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10445 |  | 2008-02-15 14:10 | 2008-02-15 | 2008-02-15 17:08 | Calculated | O410E | Sec 1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 178 | 13 | 19353 | 2314 | 0.11957 | 0.00067173 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10446 |  | 2008-02-15 15:12 | 2008-02-15 | 2008-02-15 15:49 | Calculated | O410E | tx 1313 |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 2 | 19353 | 74 | 0.00382 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10447 |  | 2008-02-15 17:16 | 2008-02-15 | 2008-02-15 17:39 | Calculated | O410E | Link 716 |  |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 93 | 19353 | 2139 | 0.11053 | 0.0048055 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10448 |  | 2008-02-15 19:56 | 2008-02-15 | 2008-02-15 21:20 | Calculated | O410E | Sec 1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 13 | 19353 | 1092 | 0.05643 | 0.00067173 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10449 |  | 2008-02-16 09:00 | 2008-02-16 | 2008-02-16 11:40 | Calculated | O410E | Link 414 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 6 | 19353 | 960 | 0.0496 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10450 |  | 2008-02-16 14:07 | 2008-02-16 | 2008-02-16 15:48 | Calculated | O410E | Sec 1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 13 | 19353 | 1313 | 0.06784 | 0.00067173 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10451 |  | 2008-02-17 09:00 | 2008-02-17 | 2008-02-17 11:41 | Calculated | O410E | Link 414 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 6 | 19353 | 966 | 0.04991 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10452 |  | 2008-02-17 12:08 | 2008-02-17 | 2008-02-17 13:45 | Calculated | O410E | Sec 1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 13 | 19353 | 1261 | 0.06516 | 0.00067173 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10311 |  | 2008-02-18 06:41 | 2008-02-18 | 2008-02-18 09:09 | Calculated | O410E | C511 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 19 | 19353 | 2812 | 0.1453 | 0.00098176 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10453 |  | 2008-02-18 08:10 | 2008-02-18 | 2008-02-18 10:01 | Calculated | O410E | Tx 2263 |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 2 | 19353 | 222 | 0.01147 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10454 |  | 2008-02-18 08:10 | 2008-02-18 | 2008-02-18 11:40 | Calculated | O410E | t1605 |  |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 210 | 1 | 19353 | 210 | 0.01085 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10455 |  | 2008-02-18 09:30 | 2008-02-18 | 2008-02-18 13:09 | Calculated | O410E | ABS 339 |  |  | Mokauiti 115-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 14 | 19353 | 3066 | 0.15843 | 0.0007234 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10456 |  | 2008-02-18 09:40 | 2008-02-18 | 2008-02-18 10:11 | Calculated | O410E | Tx1255 |  |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 3 | 19353 | 93 | 0.00481 | 0.00015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10457 |  | 2008-02-18 09:55 | 2008-02-18 | 2008-02-18 15:50 | Calculated | O410E | Tx1360 |  |  | Maihiihi 111-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 1 | 19353 | 355 | 0.01834 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10458 |  | 2008-02-18 17:41 | 2008-02-18 | 2008-02-18 18:39 | Calculated | O410E | ABS347 |  |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 25 | 19353 | 1450 | 0.07492 | 0.0012918 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10459 |  | 2008-02-18 17:41 | 2008-02-18 | 2008-02-18 18:39 | Calculated | O410E | ABS 367-394 - Rec 371 |  |  | Wharepapa 122-08 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 10 | 19353 | 580 | 0.02997 | 0.00051672 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10460 |  | 2008-02-19 08:21 | 2008-02-19 | 2008-02-19 11:58 | Calculated | O410E | Sec 1724 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 13 | 19353 | 2821 | 0.14577 | 0.00067173 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10461 |  | 2008-02-19 09:30 | 2008-02-19 | 2008-02-19 16:36 | Calculated | O410E | abs 504 |  |  | Rural 126-01 | Remote Rural F | Rural | Taharoa Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 426 | 97 | 19353 | 41322 | 2.1352 | 0.0050121 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10462 |  | 2008-02-20 10:35 | 2008-02-20 | 2008-02-20 12:28 | Calculated | O410E | tx 01m04 |  |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 2 | 19353 | 226 | 0.01168 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10463 |  | 2008-02-20 10:44 | 2008-02-20 | 2008-02-20 12:06 | Calculated | O410E | Link 1725 |  |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 6 | 19353 | 492 | 0.02542 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10610 |  | 2008-02-21 06:57 | 2008-02-21 | 2008-02-21 07:42 | Calculated | O410E | Fuse 497 |  |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 24 | 19353 | 1080 | 0.05581 | 0.0012401 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10464 |  | 2008-02-21 08:55 | 2008-02-21 | 2008-02-21 09:37 | Calculated | O410E | tx4024 |  |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 1 | 19353 | 42 | 0.00217 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10465 |  | 2008-02-21 09:01 | 2008-02-21 | 2008-02-21 14:18 | Calculated | O410E | RMS 1.7 - ABS 915 |  |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 317 | 72 | 19353 | 22824 | 1.1793 | 0.0037204 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10609 |  | 2008-02-21 09:50 | 2008-02-21 | 2008-02-21 14:31 | Calculated | O410E | ABS 748- 418 |  |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 281 | 8 | 19353 | 2248 | 0.11616 | 0.00041337 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10466 |  | 2008-02-22 10:01 | 2008-02-22 | 2008-02-22 14:47 | Calculated | O410E | tx853 |  |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 286 | 3 | 19353 | 858 | 0.04433 | 0.00015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10467 |  | 2008-02-22 11:05 | 2008-02-22 | 2008-02-22 13:41 | Calculated | O410E | Rec 806 - Link 431 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 156 | 6 | 19353 | 936 | 0.04836 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10468 |  | 2008-02-22 11:05 | 2008-02-22 | 2008-02-22 14:24 | Calculated | O410E | Link 431 - Sect 407 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 10 | 19353 | 1990 | 0.10283 | 0.00051672 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10469 |  | 2008-02-22 11:05 | 2008-02-22 | 2008-02-22 15:28 | Calculated | O410E | Sect 407 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 263 | 30 | 19353 | 7890 | 0.40769 | 0.0015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10470 |  | 2008-02-22 11:15 | 2008-02-22 | 2008-02-22 17:13 | Calculated | O410E | Sect 313 |  |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 358 | 10 | 19353 | 3580 | 0.18498 | 0.00051672 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
11250 |  | 2008-02-22 12:55 | 2008-02-22 | 2008-02-22 16:57 | Calculated | o410e | Link 239 | 0 |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 242 | 19353 | 968 | 0.05002 | 0.012505 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
11251 |  | 2008-02-22 15:30 | 2008-02-22 | 2008-02-22 16:18 | Calculated | o410e | Tx 330 | 0 |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 48 | 19353 | 1968 | 0.10169 | 0.0024802 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
11252 |  | 2008-02-22 15:50 | 2008-02-22 | 2008-02-22 16:54 | Calculated | o410e | OCB 117 | 0 |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 65 | 19353 | 10400 | 0.53738 | 0.0033587 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
11253 |  | 2008-02-22 16:02 | 2008-02-22 | 2008-02-22 17:06 | Calculated | o410e | Tx 81 | 0 |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 64 | 19353 | 384 | 0.01984 | 0.003307 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
11254 |  | 2008-02-22 17:54 | 2008-02-22 | 2008-02-22 21:01 | Calculated | o410e | Link 514 | 0 |  | Caves 101-11 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 187 | 19353 | 3179 | 0.16426 | 0.0096626 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10471 |  | 2008-02-23 09:00 | 2008-02-23 | 2008-02-23 11:50 | Calculated | O410E | ABS 427 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 170 | 10 | 19353 | 1700 | 0.08784 | 0.00051672 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10472 |  | 2008-02-23 10:10 | 2008-02-23 | 2008-02-24 11:03 | Calculated | O410E | Tx 81 |  |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1493 | 6 | 19353 | 8958 | 0.46287 | 0.00031003 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10473 |  | 2008-02-23 15:18 | 2008-02-23 | 2008-02-23 17:15 | Calculated | O410E | Link 509 |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 4 | 19353 | 468 | 0.02418 | 0.00020669 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10474 |  | 2008-02-24 08:25 | 2008-02-24 | 2008-02-24 08:28 | Calculated | O410E | OCB 798 |  |  |  | Remote Rural F | Wairere / Mahoenui 33 | Wairere Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 512 | 19353 | 1536 | 0.07937 | 0.026456 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10475 |  | 2008-02-24 23:55 | 2008-02-24 | 2008-02-25 07:10 | Calculated | O410E | Sec 296 |  |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 435 | 139 | 19353 | 60465 | 3.1243 | 0.0071823 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10476 |  | 2008-02-25 07:39 | 2008-02-25 | 2008-02-25 11:50 | Calculated | O410E | TX 2974 |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 251 | 1 | 19353 | 251 | 0.01297 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10477 |  | 2008-02-25 07:50 | 2008-02-25 | 2008-02-25 12:40 | Calculated | O410E | tx 1139 |  |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 290 | 2 | 19353 | 580 | 0.02997 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10478 |  | 2008-02-25 14:59 | 2008-02-25 | 2008-02-25 15:45 | Calculated | O410E | Tx 1794 |  |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 2 | 19353 | 92 | 0.00475 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10479 |  | 2008-02-25 15:50 | 2008-02-25 | 2008-02-25 16:54 | Calculated | O410E | tx 2723 |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 1 | 19353 | 64 | 0.00331 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10480 |  | 2008-02-26 09:22 | 2008-02-26 | 2008-02-26 15:53 | Calculated | O410E | Fuse 6320 |  |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 391 | 37 | 19353 | 14467 | 0.74753 | 0.0019118 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10481 |  | 2008-02-26 10:04 | 2008-02-26 | 2008-02-26 10:24 | Calculated | O410E | OCB 262 |  |  | Nihoniho 412-02 | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 20 | 27 | 19353 | 540 | 0.0279 | 0.0013951 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10482 |  | 2008-02-26 10:33 | 2008-02-26 | 2008-02-26 14:44 | Calculated | O410E | OCB 254 -262 - Links 445 |  |  | Nihoniho 412-01 | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 251 | 12 | 19353 | 3012 | 0.15563 | 0.00062006 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10483 |  | 2008-02-26 15:03 | 2008-02-26 | 2008-02-26 15:15 | Calculated | O410E | OCB 262 |  |  | Nihoniho 412-02 | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 12 | 27 | 19353 | 324 | 0.01674 | 0.0013951 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10484 |  | 2008-02-26 19:18 | 2008-02-26 | 2008-02-26 19:21 | Calculated | O410E | OCB 513 |  |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 411 | 19353 | 1233 | 0.06371 | 0.021237 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10485 |  | 2008-02-27 09:32 | 2008-02-27 | 2008-02-27 12:48 | Calculated | O410E | ABS 427 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 10 | 19353 | 1960 | 0.10128 | 0.00051672 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10486 |  | 2008-02-27 10:03 | 2008-02-27 | 2008-02-27 12:01 | Calculated | O410E | HV Fuses Tx 08R19 & 08R17 |  |  | Ongarue 421-01 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 50 | 19353 | 5900 | 0.30486 | 0.0025836 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10494 |  | 2008-02-28 10:08 | 2008-02-28 | 2008-02-28 12:12 | Calculated | O410E | Link 1533 |  |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 124 | 3 | 19353 | 372 | 0.01922 | 0.00015501 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10495 |  | 2008-02-28 10:50 | 2008-02-28 | 2008-02-28 17:10 | Calculated | O410E | Sect 251 |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 380 | 2 | 19353 | 760 | 0.03927 | 0.00010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10496 |  | 2008-02-28 15:00 | 2008-02-28 | 2008-02-28 16:14 | Calculated | O410E | Rec 268 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 9 | 19353 | 666 | 0.03441 | 0.00046504 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10497 |  | 2008-02-29 02:47 | 2008-02-29 | 2008-02-29 09:08 | Calculated | O410E | Sec 296 |  |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 381 | 139 | 19353 | 52959 | 2.7365 | 0.0071823 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10498 |  | 2008-02-29 06:54 | 2008-02-29 | 2008-02-29 08:04 | Calculated | O410E | REC 371 |  |  | Tuhua 422-02 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 20 | 19353 | 1400 | 0.07234 | 0.0010334 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10499 |  | 2008-02-29 08:08 | 2008-02-29 | 2008-02-29 11:32 | Calculated | O410E | TX 869 |  |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 204 | 1 | 19353 | 204 | 0.01054 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10500 |  | 2008-02-29 10:18 | 2008-02-29 | 2008-02-29 14:08 | Calculated | O410E | ABS 147-504, 537,538 |  |  |  | Remote Rural F | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 230 | 1 | 19353 | 230 | 0.01188 | 5.1672e-05 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10501 |  | 2008-02-29 10:30 | 2008-02-29 | 2008-02-29 11:40 | Calculated | O410E | Link 909 |  |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 127 | 19353 | 8890 | 0.45936 | 0.0065623 | 0 | 0 | 2007/2008 | February-2008 | 2 | 2008
10518 |  | 2008-03-01 04:09 | 2008-03-01 | 2008-03-01 04:17 | Calculated | O410E | REC 961 |  |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 109 | 19353 | 872 | 0.04506 | 0.0056322 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10519 |  | 2008-03-01 06:01 | 2008-03-01 | 2008-03-01 08:14 | Calculated | O410E | LINK 332 |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 2 | 19353 | 266 | 0.01374 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10502 |  | 2008-03-01 09:00 | 2008-03-01 | 2008-03-01 12:10 | Calculated | O410E | ABS 423-432 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 18 | 19353 | 3420 | 0.17672 | 0.00093009 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10503 |  | 2008-03-01 18:42 | 2008-03-01 | 2008-03-01 18:43 | Calculated | O410E | OCB242 |  |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 1 | 19353 | 1 | 5e-05 | 5.1672e-05 | 1 | 1 | 2007/2008 | March-2008 | 3 | 2008
10504 |  | 2008-03-01 20:08 | 2008-03-01 | 2008-03-01 20:14 | Calculated | O410E | OCB 124 |  |  | Maihiihi 111-00 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 661 | 19353 | 3966 | 0.20493 | 0.034155 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10510 |  | 2008-03-01 20:15 | 2008-03-01 | 2008-03-01 21:10 | Calculated | O410E | REC 884 |  |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 19 | 19353 | 1045 | 0.054 | 0.00098176 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10505 |  | 2008-03-01 20:23 | 2008-03-01 | 2008-03-01 21:24 | Calculated | O410E | ocb 109 to abs 506 |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 27 | 19353 | 1647 | 0.0851 | 0.0013951 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10507 |  | 2008-03-01 20:23 | 2008-03-01 | 2008-03-01 21:54 | Calculated | O410E | ABS 506 - 291 |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 23 | 19353 | 2093 | 0.10815 | 0.0011884 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10509 |  | 2008-03-01 20:23 | 2008-03-01 | 2008-03-01 22:23 | Calculated | O410E | ABS 291 |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 10 | 19353 | 1200 | 0.06201 | 0.00051672 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10511 |  | 2008-03-01 20:45 | 2008-03-01 | 2008-03-01 23:53 | Calculated | O410E | FUSE 936 - 557 |  |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 9 | 19353 | 1692 | 0.08743 | 0.00046504 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10512 |  | 2008-03-01 20:45 | 2008-03-01 | 2008-03-02 00:02 | Calculated | O410E | LINK 557-585 |  |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 8 | 19353 | 1576 | 0.08143 | 0.00041337 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10513 |  | 2008-03-01 20:45 | 2008-03-01 | 2008-03-02 00:39 | Calculated | O410E | LINK 585 - 406 |  |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 234 | 3 | 19353 | 702 | 0.03627 | 0.00015501 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10514 |  | 2008-03-01 20:45 | 2008-03-01 | 2008-03-02 09:39 | Calculated | O410E | LINK 406 |  |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 774 | 7 | 19353 | 5418 | 0.27996 | 0.0003617 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10515 |  | 2008-03-01 21:05 | 2008-03-01 | 2008-03-02 02:02 | Calculated | O410E | VCB 682 |  |  |  | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 297 | 35 | 19353 | 10395 | 0.53713 | 0.0018085 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10516 |  | 2008-03-01 21:05 | 2008-03-01 | 2008-03-02 11:56 | Calculated | O410E | ABS 1705 |  |  |  | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 891 | 61 | 19353 | 54351 | 2.8084 | 0.003152 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10517 |  | 2008-03-01 21:05 | 2008-03-01 | 2008-03-02 03:11 | Calculated | O410E | LINK 1718- 1648 |  |  |  | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 366 | 40 | 19353 | 14640 | 0.75647 | 0.0020669 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10506 |  | 2008-03-01 21:40 | 2008-03-01 | 2008-03-01 21:43 | Calculated | O410E | OCB 109-ABS 506 |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 27 | 19353 | 81 | 0.00419 | 0.0013951 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10508 |  | 2008-03-01 22:23 | 2008-03-01 | 2008-03-01 22:24 | Calculated | O410E | OCB 109-291 |  |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 50 | 19353 | 50 | 0.00258 | 0.0025836 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10520 |  | 2008-03-02 04:09 | 2008-03-02 | 2008-03-02 10:41 | Calculated | O410E | TX 21N08 |  |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 392 | 2 | 19353 | 784 | 0.04051 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10522 |  | 2008-03-02 09:35 | 2008-03-02 | 2008-03-02 10:32 | Calculated | O410E | LINK 412 |  |  | Huirimu 121-04 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 4 | 19353 | 228 | 0.01178 | 0.00020669 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10523 |  | 2008-03-02 10:32 | 2008-03-02 | 2008-03-02 12:43 | Calculated | O410E | LINK 429 |  |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 17 | 19353 | 2227 | 0.11507 | 0.00087842 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10524 |  | 2008-03-02 14:28 | 2008-03-02 | 2008-03-02 17:56 | Calculated | O410E | LINK 1539 |  |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 208 | 7 | 19353 | 1456 | 0.07523 | 0.0003617 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10525 |  | 2008-03-02 17:05 | 2008-03-02 | 2008-03-02 17:45 | Calculated | O410E | ABS 198 |  |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 6 | 19353 | 240 | 0.0124 | 0.00031003 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10531 |  | 2008-03-03 06:08 | 2008-03-03 | 2008-03-03 07:27 | Calculated | O410E | LINK 383 |  |  | McDonalds 110-02 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 10 | 19353 | 790 | 0.04082 | 0.00051672 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10527 |  | 2008-03-03 09:24 | 2008-03-03 | 2008-03-03 10:13 | Calculated | O410E | SEC 251 |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 2 | 19353 | 98 | 0.00506 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10528 |  | 2008-03-03 10:16 | 2008-03-03 | 2008-03-03 11:21 | Calculated | O410E | 08R06 |  |  | Kuratau 406-03 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 65 | 86 | 19353 | 5590 | 0.28884 | 0.0044438 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10529 |  | 2008-03-03 13:22 | 2008-03-03 | 2008-03-03 13:40 | Calculated | O410E | T2139 |  |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 4 | 19353 | 72 | 0.00372 | 0.00020669 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10530 |  | 2008-03-03 16:03 | 2008-03-03 | 2008-03-03 16:55 | Calculated | O410E | T13J03 |  |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 19353 | 104 | 0.00537 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10532 |  | 2008-03-04 10:56 | 2008-03-04 | 2008-03-04 11:37 | Calculated | O410E | TX 2082 |  |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 1 | 19353 | 41 | 0.00212 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10533 |  | 2008-03-04 15:12 | 2008-03-04 | 2008-03-04 15:32 | Calculated | O410E | TX 363 |  |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 2 | 19353 | 40 | 0.00207 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10534 |  | 2008-03-04 16:10 | 2008-03-04 | 2008-03-04 18:06 | Calculated | O410E | LINK 170 |  |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 18 | 19353 | 2088 | 0.10789 | 0.00093009 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10535 |  | 2008-03-05 09:04 | 2008-03-05 | 2008-03-05 12:06 | Calculated | O410E | TX 904 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 182 | 2 | 19353 | 364 | 0.01881 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10536 |  | 2008-03-05 09:32 | 2008-03-05 | 2008-03-05 15:14 | Calculated | O410E | ABS 322 |  |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 61 | 19353 | 20862 | 1.078 | 0.003152 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10537 |  | 2008-03-05 09:45 | 2008-03-05 | 2008-03-05 15:09 | Calculated | O410E | ABS 351 |  |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 37 | 19353 | 11988 | 0.61944 | 0.0019118 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10538 |  | 2008-03-05 14:45 | 2008-03-05 | 2008-03-05 16:26 | Calculated | O410E | REC 529 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 42 | 19353 | 4242 | 0.21919 | 0.0021702 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10539 |  | 2008-03-05 19:20 | 2008-03-05 | 2008-03-05 21:58 | Calculated | O410E | LINK 495 |  |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 4 | 19353 | 632 | 0.03266 | 0.00020669 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10540 |  | 2008-03-06 09:03 | 2008-03-06 | 2008-03-06 15:40 | Calculated | O410E | ABS 153 |  |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 397 | 89 | 19353 | 35333 | 1.8257 | 0.0045988 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10541 |  | 2008-03-06 12:00 | 2008-03-06 | 2008-03-06 14:56 | Calculated | O410E | TX 2538 |  |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 1 | 19353 | 176 | 0.00909 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10542 |  | 2008-03-07 09:00 | 2008-03-07 | 2008-03-07 10:54 | Calculated | O410E | LINK 443 |  |  | Western 403-05 | Remote Rural F | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 5 | 19353 | 570 | 0.02945 | 0.00025836 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10544 |  | 2008-03-07 09:45 | 2008-03-07 | 2008-03-07 12:20 | Calculated | O410E | LINK 252 |  |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 6 | 19353 | 930 | 0.04805 | 0.00031003 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10543 |  | 2008-03-07 10:00 | 2008-03-07 | 2008-03-07 14:09 | Calculated | O410E | LINK 332 |  |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 249 | 2 | 19353 | 498 | 0.02573 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10545 |  | 2008-03-07 13:08 | 2008-03-07 | 2008-03-07 14:16 | Calculated | O410E | LINK 677 |  |  | Oparure 107-01 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 8 | 19353 | 544 | 0.02811 | 0.00041337 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10547 |  | 2008-03-08 08:10 | 2008-03-08 | 2008-03-08 10:55 | Calculated | O410E | LINK 1386 |  |  | Mahoenui 113-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 4 | 19353 | 660 | 0.0341 | 0.00020669 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10546 |  | 2008-03-08 09:00 | 2008-03-08 | 2008-03-08 14:00 | Calculated | O410E | ABS 417 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 300 | 9 | 19353 | 2700 | 0.13951 | 0.00046504 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10548 |  | 2008-03-08 09:55 | 2008-03-08 | 2008-03-08 10:55 | Calculated | O410E | ABS 1310 |  |  | Mahoenui 113-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 16 | 19353 | 960 | 0.0496 | 0.00082675 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10549 |  | 2008-03-10 09:00 | 2008-03-10 | 2008-03-10 11:49 | Calculated | O410E | ABS 417 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 169 | 9 | 19353 | 1521 | 0.07859 | 0.00046504 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10550 |  | 2008-03-10 18:20 | 2008-03-10 | 2008-03-10 19:50 | Calculated | O410E | TX 4060 |  |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 1 | 19353 | 90 | 0.00465 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10551 |  | 2008-03-10 22:56 | 2008-03-10 | 2008-03-10 23:04 | Calculated | O410E | OCB 6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 4 | 19353 | 32 | 0.00165 | 0.00020669 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10552 |  | 2008-03-11 09:15 | 2008-03-11 | 2008-03-11 11:19 | Calculated | O410E | TX 2723 |  |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 1 | 19353 | 124 | 0.00641 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10553 |  | 2008-03-11 12:22 | 2008-03-11 | 2008-03-11 15:05 | Calculated | O410E | TX 941 |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 163 | 1 | 19353 | 163 | 0.00842 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10555 |  | 2008-03-11 21:35 | 2008-03-11 | 2008-03-11 22:52 | Calculated | O410E | FUSE 284 |  |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 10 | 19353 | 770 | 0.03979 | 0.00051672 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10556 |  | 2008-03-12 08:33 | 2008-03-12 | 2008-03-12 09:38 | Calculated | O410E | LINK 402 |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 13 | 19353 | 845 | 0.04366 | 0.00067173 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10557 |  | 2008-03-12 08:33 | 2008-03-12 | 2008-03-12 15:58 | Calculated | O410E | TX 1439 |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 445 | 2 | 19353 | 890 | 0.04599 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10558 |  | 2008-03-12 13:04 | 2008-03-12 | 2008-03-12 13:58 | Calculated | O410E | ABS 550 |  |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 20 | 19353 | 1080 | 0.05581 | 0.0010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10559 |  | 2008-03-12 13:32 | 2008-03-12 | 2008-03-12 15:58 | Calculated | O410E | LINK 402 |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 13 | 19353 | 1898 | 0.09807 | 0.00067173 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10560 |  | 2008-03-13 09:25 | 2008-03-13 | 2008-03-13 11:24 | Calculated | O410E | TX 2503 |  |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 1 | 19353 | 119 | 0.00615 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10562 |  | 2008-03-13 09:57 | 2008-03-13 | 2008-03-13 16:01 | Calculated | O410E | tx 1439 |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 2 | 19353 | 728 | 0.03762 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10563 |  | 2008-03-13 10:30 | 2008-03-13 | 2008-03-13 14:25 | Calculated | O410E | ABS 1318 |  |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 235 | 22 | 19353 | 5170 | 0.26714 | 0.0011368 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10561 |  | 2008-03-13 10:47 | 2008-03-13 | 2008-03-13 12:02 | Calculated | O410E | ABS 150 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 44 | 19353 | 3300 | 0.17052 | 0.0022735 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10564 |  | 2008-03-13 13:00 | 2008-03-13 | 2008-03-13 13:56 | Calculated | O410E | Tx 873 |  |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 2 | 19353 | 112 | 0.00579 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10565 |  | 2008-03-13 16:10 | 2008-03-13 | 2008-03-13 16:56 | Calculated | O410E | Link 592 |  |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 20 | 19353 | 920 | 0.04754 | 0.0010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10566 |  | 2008-03-14 10:40 | 2008-03-14 | 2008-03-14 13:15 | Calculated | O410E | Link 438-442-597 |  |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 47 | 19353 | 7285 | 0.37643 | 0.0024286 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10567 |  | 2008-03-14 11:05 | 2008-03-14 | 2008-03-14 12:00 | Calculated | O410E | tx 1668 |  |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 1 | 19353 | 55 | 0.00284 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10568 |  | 2008-03-14 11:10 | 2008-03-14 | 2008-03-14 12:40 | Calculated | O410E | Tx 2933 |  |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 1 | 19353 | 90 | 0.00465 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10569 |  | 2008-03-14 21:50 | 2008-03-14 | 2008-03-14 22:51 | Calculated | O410E | Tx 1048 |  |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 2 | 19353 | 122 | 0.0063 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10570 |  | 2008-03-15 09:00 | 2008-03-15 | 2008-03-15 14:24 | Calculated | O410E | ABS 417 |  |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 324 | 9 | 19353 | 2916 | 0.15067 | 0.00046504 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10571 |  | 2008-03-15 18:16 | 2008-03-15 | 2008-03-15 19:52 | Calculated | O410E | TX 07D23 |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 7 | 19353 | 672 | 0.03472 | 0.0003617 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10572 |  | 2008-03-16 09:00 | 2008-03-16 | 2008-03-16 13:57 | Calculated | O410E | ABS 653-432 |  |  | Pureora 119-03 RETIRED | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 297 | 16 | 19353 | 4752 | 0.24554 | 0.00082675 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10573 |  | 2008-03-16 10:57 | 2008-03-16 | 2008-03-16 14:19 | Calculated | O410E | Link 5895 |  |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 2 | 19353 | 404 | 0.02088 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10574 |  | 2008-03-16 10:57 | 2008-03-16 | 2008-03-16 16:15 | Calculated | O410E | Tx 2665 |  |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 318 | 1 | 19353 | 318 | 0.01643 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10575 |  | 2008-03-17 05:09 | 2008-03-17 | 2008-03-17 05:18 | Calculated | O410E | OCB 6143 |  |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 4 | 19353 | 36 | 0.00186 | 0.00020669 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10576 |  | 2008-03-18 08:20 | 2008-03-18 | 2008-03-18 09:49 | Calculated | O410E | Tx 381 |  |  | Hangatiki East 102-03 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 1 | 19353 | 89 | 0.0046 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10577 |  | 2008-03-18 08:59 | 2008-03-18 | 2008-03-18 15:10 | Calculated | O410E | ABS 549 |  |  | Southern 409-02 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 371 | 10 | 19353 | 3710 | 0.1917 | 0.00051672 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10578 |  | 2008-03-18 10:08 | 2008-03-18 | 2008-03-18 11:52 | Calculated | O410E | ABS 460 |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 68 | 19353 | 7072 | 0.36542 | 0.0035137 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10579 |  | 2008-03-18 19:20 | 2008-03-18 | 2008-03-18 19:42 | Calculated | O410E | Tx 09K26 |  |  | Southern 409-02 | Remote Rural F | Southern | Manunui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 1 | 19353 | 22 | 0.00114 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10580 |  | 2008-03-19 04:38 | 2008-03-19 | 2008-03-19 09:54 | Calculated | O410E | Sec 1536 |  |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 316 | 7 | 19353 | 2212 | 0.1143 | 0.0003617 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10581 |  | 2008-03-19 07:40 | 2008-03-19 | 2008-03-19 09:37 | Calculated | O410E | Rec 564 - Sec 1536 |  |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 6 | 19353 | 702 | 0.03627 | 0.00031003 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10582 |  | 2008-03-19 11:24 | 2008-03-19 | 2008-03-19 12:37 | Calculated | O410E | Tx 941 |  |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10583 |  | 2008-03-20 11:50 | 2008-03-20 | 2008-03-20 12:11 | Calculated | O410E | Tx 404 |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 1 | 19353 | 21 | 0.00109 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10584 |  | 2008-03-20 12:19 | 2008-03-20 | 2008-03-20 13:42 | Calculated | O410E | Tx 740 |  |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 3 | 19353 | 249 | 0.01287 | 0.00015501 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10585 |  | 2008-03-21 18:22 | 2008-03-21 | 2008-03-21 21:32 | Calculated | O410E | Tx 2117 |  |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 3 | 19353 | 570 | 0.02945 | 0.00015501 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10586 |  | 2008-03-21 21:00 | 2008-03-21 | 2008-03-21 21:43 | Calculated | O410E | Link 1539 |  |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 7 | 19353 | 301 | 0.01555 | 0.0003617 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10587 |  | 2008-03-23 14:29 | 2008-03-23 | 2008-03-23 15:57 | Calculated | O410E | OCB797 |  |  |  | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 243 | 19353 | 21384 | 1.1049 | 0.012556 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10588 |  | 2008-03-25 09:05 | 2008-03-25 | 2008-03-25 09:45 | Calculated | O410E | Tx 2337 |  |  | Piopio 116-02 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 40 | 8 | 19353 | 320 | 0.01653 | 0.00041337 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10589 |  | 2008-03-25 15:27 | 2008-03-25 | 2008-03-25 16:09 | Calculated | O410E | Tx 2337 |  |  | Piopio 116-02 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 42 | 8 | 19353 | 336 | 0.01736 | 0.00041337 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10590 |  | 2008-03-26 09:05 | 2008-03-26 | 2008-03-26 15:10 | Calculated | O410E | LLB @ Poles 19-23 |  |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 365 | 12 | 19353 | 4380 | 0.22632 | 0.00062006 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10591 |  | 2008-03-26 09:06 | 2008-03-26 | 2008-03-26 14:58 | Calculated | O410E | Link 789 |  |  | Southern 409-03 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 352 | 34 | 19353 | 11968 | 0.61841 | 0.0017568 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10592 |  | 2008-03-26 09:32 | 2008-03-26 | 2008-03-26 13:58 | Calculated | O410E | Tx 1240 |  |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 266 | 2 | 19353 | 532 | 0.02749 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10593 |  | 2008-03-26 09:36 | 2008-03-26 | 2008-03-26 14:25 | Calculated | O410E | ABS 1524 |  |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 289 | 14 | 19353 | 4046 | 0.20906 | 0.0007234 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10594 |  | 2008-03-27 09:13 | 2008-03-27 | 2008-03-27 15:21 | Calculated | O410E | ABS 135-136 |  |  | Southern 409-04 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 368 | 125 | 19353 | 46000 | 2.3769 | 0.0064589 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10595 |  | 2008-03-27 10:35 | 2008-03-27 | 2008-03-27 15:48 | Calculated | O410E | Link 246 |  |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 313 | 17 | 19353 | 5321 | 0.27494 | 0.00087842 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10596 |  | 2008-03-27 11:01 | 2008-03-27 | 2008-03-27 15:57 | Calculated | O410E | Tx 07E03 |  |  | Ohura 413-01 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 296 | 1 | 19353 | 296 | 0.01529 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10597 |  | 2008-03-27 13:31 | 2008-03-27 | 2008-03-27 15:05 | Calculated | O410E | Lv Fuses @ 08I05 |  |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 7 | 19353 | 658 | 0.034 | 0.0003617 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10598 |  | 2008-03-28 09:08 | 2008-03-28 | 2008-03-28 14:52 | Calculated | O410E | Link 6564 |  |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 344 | 28 | 19353 | 9632 | 0.4977 | 0.0014468 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10599 |  | 2008-03-28 09:35 | 2008-03-28 | 2008-03-28 13:36 | Calculated | O410E | Link 374 |  |  | Maihiihi 111-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 241 | 10 | 19353 | 2410 | 0.12453 | 0.00051672 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10600 |  | 2008-03-28 10:48 | 2008-03-28 | 2008-03-28 14:38 | Calculated | O410E | Tx 1875 |  |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 230 | 1 | 19353 | 230 | 0.01188 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10601 |  | 2008-03-28 11:42 | 2008-03-28 | 2008-03-29 01:00 | Calculated | O410E | Tx 12J04 |  |  | Southern 409-09 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 798 | 1 | 19353 | 798 | 0.04123 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10602 |  | 2008-03-29 10:08 | 2008-03-29 | 2008-03-29 11:39 | Calculated | O410E | Link 781 |  |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 5 | 19353 | 455 | 0.02351 | 0.00025836 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10603 |  | 2008-03-29 16:12 | 2008-03-29 | 2008-03-29 17:34 | Calculated | O410E | Tx 1853 |  |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 1 | 19353 | 82 | 0.00424 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10604 |  | 2008-03-31 08:10 | 2008-03-31 | 2008-03-31 10:33 | Calculated | O410E | Tx 4007 |  |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 1 | 19353 | 143 | 0.00739 | 5.1672e-05 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10605 |  | 2008-03-31 09:14 | 2008-03-31 | 2008-03-31 14:44 | Calculated | O410E | Links 452 |  |  | Southern 409-03 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 330 | 59 | 19353 | 19470 | 1.0061 | 0.0030486 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10606 |  | 2008-03-31 09:40 | 2008-03-31 | 2008-03-31 12:23 | Calculated | O410E | Tx 07D02 |  |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 2 | 19353 | 326 | 0.01684 | 0.00010334 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10607 |  | 2008-03-31 10:34 | 2008-03-31 | 2008-03-31 13:15 | Calculated | O410E | Sect 407 |  |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 30 | 19353 | 4830 | 0.24957 | 0.0015501 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
10608 |  | 2008-03-31 22:38 | 2008-03-31 | 2008-04-01 00:26 | Calculated | O410E | Fuse 207 |  |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 41 | 19353 | 4428 | 0.2288 | 0.0021185 | 0 | 0 | 2007/2008 | March-2008 | 3 | 2008
20009 | Check not doubled up | 2008-04-01 08:55 | 2008-04-01 | 2008-04-01 13:50 | Calculated | 20L53 | 20L53 - no label |  | No Segment | No Asset Group | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 295 | 1 | 19353 | 295 | 0.01524 | 5.1672e-05 | 8 | 2360 | 2008/2009 | April-2008 | 4 | 2008
20010 | Check not doubled up | 2008-04-01 09:00 | 2008-04-01 | 2008-04-01 15:00 | Calculated | 5902 | 5902 - DROP OUT FUSE |  | No Segment | No Asset Group | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 44 | 19353 | 15840 | 0.81848 | 0.0022735 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
20012 | Check not doubled up | 2008-04-01 09:45 | 2008-04-01 | 2008-04-01 11:28 | Calculated | 03Q10 | 03Q10 - 1ph 15kVA polemount |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 1 | 19353 | 103 | 0.00532 | 5.1672e-05 | 8 | 824 | 2008/2009 | April-2008 | 4 | 2008
20013 | Check not doubled up | 2008-04-01 10:15 | 2008-04-01 | 2008-04-01 12:02 | Calculated | 5362 | 5362 - RECLOSER WITH BYPASS |  | No Segment | No Asset Group | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 15 | 19353 | 1605 | 0.08293 | 0.00077507 | 120 | 12840 | 2008/2009 | April-2008 | 4 | 2008
10611 |  | 2008-04-01 22:30 | 2008-04-01 | 2008-04-02 09:20 | Calculated | o410e | C268 | 0 |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 650 | 9 | 19353 | 5850 | 0.30228 | 0.00046504 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10620 |  | 2008-04-02 09:03 | 2008-04-02 | 2008-04-02 15:10 | Calculated | o410e | L904 | 0 |  | Southern 409-04 | Remote Rural F | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 367 | 40 | 19353 | 14680 | 0.75854 | 0.0020669 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10621 |  | 2008-04-02 09:39 | 2008-04-02 | 2008-04-02 15:46 | Calculated | o410e | S322-LLB | 0 |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 367 | 73 | 19353 | 26791 | 1.3843 | 0.003772 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10622 |  | 2008-04-02 10:33 | 2008-04-02 | 2008-04-02 11:54 | Calculated | o410e | C268 | 11 |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation | OH Lines : Surge Diverters | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 9 | 19353 | 729 | 0.03767 | 0.00046504 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10624 |  | 2008-04-02 12:23 | 2008-04-02 | 2008-04-02 13:16 | Calculated | o410e | S281 | 38 |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 53 | 40 | 19353 | 2120 | 0.10954 | 0.0020669 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10625 |  | 2008-04-03 09:45 | 2008-04-03 | 2008-04-03 15:07 | Calculated | o410e | LF375 | 0 |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 322 | 3 | 19353 | 966 | 0.04991 | 0.00015501 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10627 |  | 2008-04-04 09:00 | 2008-04-04 | 2008-04-04 09:05 | Calculated | o410e | LF 227 | 0 |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 313 | 40 | 19353 | 5050 | 0.26094 | 0.0020669 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10630 |  | 2008-04-04 10:46 | 2008-04-04 | 2008-04-04 12:34 | Calculated | o410e | S416 | 0 |  | Whakamaru 120-04 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 12 | 19353 | 1296 | 0.06697 | 0.00062006 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10631 |  | 2008-04-04 12:45 | 2008-04-04 | 2008-04-04 15:18 | Calculated | o410e | LF5E4 | 38 |  | Nihoniho 412-02 | Remote Rural F | Nihoniho | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 153 | 1 | 19353 | 153 | 0.00791 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10632 |  | 2008-04-04 22:06 | 2008-04-04 | 2008-04-04 23:25 | Calculated | o410e | LV10S43 | 0 |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 36 | 19353 | 2844 | 0.14695 | 0.0018602 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10633 |  | 2008-04-07 06:49 | 2008-04-07 | 2008-04-07 09:01 | Calculated | o410e | LF3R1 | 38 |  | No Asset Group | Remote Rural F | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 132 | 1 | 19353 | 132 | 0.00682 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10634 |  | 2008-04-07 08:03 | 2008-04-07 | 2008-04-07 11:17 | Calculated | o410e | L1538 | 38 |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 194 | 2 | 19353 | 388 | 0.02005 | 0.00010334 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10636 |  | 2008-04-07 09:10 | 2008-04-07 | 2008-04-07 10:24 | Calculated | o410e | LF604 | 0 |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 1 | 19353 | 74 | 0.00382 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10635 |  | 2008-04-07 09:34 | 2008-04-07 | 2008-04-07 13:06 | Calculated | o410e | LF1685 | 0 |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 212 | 1 | 19353 | 212 | 0.01095 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10637 |  | 2008-04-07 17:26 | 2008-04-07 | 2008-04-07 18:30 | Calculated | o410e | LF7I49 | 0 |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 1 | 19353 | 64 | 0.00331 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10639 |  | 2008-04-08 07:09 | 2008-04-08 | 2008-04-08 09:33 | Calculated | o410e | LF1581 | 0 |  | Te Mapara 117-05 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 1 | 19353 | 144 | 0.00744 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
23466 | Planned Shutdown Tangiwai Feeder - Timber Mill (Left out of old system) | 2008-04-08 10:33 | 2008-04-08 | 2008-04-08 13:34 | Calculated | 5780 | 5780 - Fused Link 5780 |  | 416SEG5780-6608 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 181 | 12 | 19353 | 2172 | 0.11223 | 0.00062006 | 220 | 39820 | 2008/2009 | April-2008 | 4 | 2008
10640 |  | 2008-04-08 12:54 | 2008-04-08 | 2008-04-08 13:34 | Calculated | o410e | S709 | 38 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Fuse Carriers | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 40 | 1 | 19353 | 40 | 0.00207 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10641 |  | 2008-04-09 08:36 | 2008-04-09 | 2008-04-09 10:32 | Calculated | o410e | LF1067 | 0 |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 116 | 1 | 19353 | 116 | 0.00599 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10642 |  | 2008-04-09 14:45 | 2008-04-09 | 2008-04-09 16:10 | Calculated | o410e | LF2723 | 0 |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 2 | 19353 | 170 | 0.00878 | 0.00010334 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10643 |  | 2008-04-10 09:01 | 2008-04-10 | 2008-04-10 12:45 | Calculated | o410e | L609 | 0 |  | Ohura 413-01 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 224 | 4 | 19353 | 896 | 0.0463 | 0.00020669 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10645 |  | 2008-04-10 20:41 | 2008-04-10 | 2008-04-10 21:04 | Calculated | o410e | LF567 | 0 |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 42 | 19353 | 966 | 0.04991 | 0.0021702 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10646 |  | 2008-04-11 07:43 | 2008-04-11 | 2008-04-11 09:46 | Calculated | o410e | LF4007 | 0 |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 1 | 19353 | 123 | 0.00636 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10647 |  | 2008-04-11 09:30 | 2008-04-11 | 2008-04-11 13:22 | Calculated | o410e | S339 | 0 |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 14 | 19353 | 3248 | 0.16783 | 0.0007234 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10648 |  | 2008-04-11 10:00 | 2008-04-11 | 2008-04-11 12:07 | Calculated | o410e | L451 | 0 |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 127 | 6 | 19353 | 762 | 0.03937 | 0.00031003 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10649 |  | 2008-04-11 13:00 | 2008-04-11 | 2008-04-11 13:52 | Calculated | o410e | S405 | 0 |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 52 | 13 | 19353 | 676 | 0.03493 | 0.00067173 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10650 |  | 2008-04-14 09:58 | 2008-04-14 | 2008-04-14 16:05 | Calculated | o410e | L272 | 0 |  | Piopio 116-04 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 367 | 8 | 19353 | 2936 | 0.15171 | 0.00041337 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10651 |  | 2008-04-14 11:43 | 2008-04-14 | 2008-04-14 12:13 | Calculated | o410e | C296 | 0 |  | No Asset Group | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 139 | 19353 | 4170 | 0.21547 | 0.0071823 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10652 |  | 2008-04-14 15:40 | 2008-04-14 | 2008-04-14 17:35 | Calculated | o410e | LF4161 | 0 |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 1 | 19353 | 115 | 0.00594 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10653 |  | 2008-04-15 06:55 | 2008-04-15 | 2008-04-15 12:28 | Calculated | o410e | LF2212 | 0 |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 333 | 2 | 19353 | 666 | 0.03441 | 0.00010334 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10654 |  | 2008-04-15 07:11 | 2008-04-15 | 2008-04-15 09:27 | Calculated | o410e | C296 | 0 |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 139 | 19353 | 18904 | 0.9768 | 0.0071823 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10655 |  | 2008-04-15 07:44 | 2008-04-15 | 2008-04-15 11:09 | Calculated | o410e | LF2469 | 0 |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 205 | 1 | 19353 | 205 | 0.01059 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10656 |  | 2008-04-15 09:15 | 2008-04-15 | 2008-04-15 12:59 | Calculated | o410e | LF62 | 0 |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 224 | 1 | 19353 | 224 | 0.01157 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10657 |  | 2008-04-15 09:15 | 2008-04-15 | 2008-04-15 13:07 | Calculated | o410e | LF398 | 0 |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 232 | 1 | 19353 | 232 | 0.01199 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10658 |  | 2008-04-15 10:45 | 2008-04-15 | 2008-04-15 13:35 | Calculated | o410e | LF771 | 0 |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 170 | 2 | 19353 | 340 | 0.01757 | 0.00010334 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10659 |  | 2008-04-15 12:10 | 2008-04-15 | 2008-04-15 14:59 | Calculated | o410e | LF10O3 | 0 |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 169 | 1 | 19353 | 169 | 0.00873 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10660 |  | 2008-04-15 12:53 | 2008-04-15 | 2008-04-15 13:26 | Calculated | o410e | LF317 | 0 |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 3 | 19353 | 99 | 0.00512 | 0.00015501 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10668 |  | 2008-04-15 14:22 | 2008-04-15 | 2008-04-15 16:03 | Calculated | o410e | L187 | 0 |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 7 | 19353 | 707 | 0.03653 | 0.0003617 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10669 |  | 2008-04-15 16:20 | 2008-04-15 | 2008-04-15 16:49 | Calculated | o410e | L156 | 0 |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 5 | 19353 | 145 | 0.00749 | 0.00025836 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10670 |  | 2008-04-15 18:01 | 2008-04-15 | 2008-04-15 20:51 | Calculated | o410e | LF2259 | 0 |  | Benneydale 103-07 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 8 | 19353 | 1360 | 0.07027 | 0.00041337 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10671 |  | 2008-04-16 09:35 | 2008-04-16 | 2008-04-16 10:22 | Calculated | o410e | L403 | 0 |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 47 | 19 | 19353 | 893 | 0.04614 | 0.00098176 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10672 |  | 2008-04-17 09:04 | 2008-04-17 | 2008-04-17 11:40 | Calculated | o410e | L2066 | 0 |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 156 | 27 | 19353 | 4212 | 0.21764 | 0.0013951 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10673 |  | 2008-04-17 11:35 | 2008-04-17 | 2008-04-17 13:06 | Calculated | o410e | LF1484 | 0 |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 1 | 19353 | 91 | 0.0047 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10674 |  | 2008-04-17 11:55 | 2008-04-17 | 2008-04-17 14:26 | Calculated | o410e | LF12N3 | 0 |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 1 | 19353 | 151 | 0.0078 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10675 |  | 2008-04-17 11:57 | 2008-04-17 | 2008-04-17 14:00 | Calculated | o410e | S434 | 0 |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 3 | 19353 | 369 | 0.01907 | 0.00015501 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10678 |  | 2008-04-17 13:00 | 2008-04-17 | 2008-04-17 14:02 | Calculated | o410e | LF2405 | 0 |  | Te Mapara 117-05 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 1 | 19353 | 62 | 0.0032 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10679 |  | 2008-04-18 01:20 | 2008-04-18 | 2008-04-18 01:33 | Calculated | o410e | C792 | 0 |  | No Asset Group | Remote Rural F | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 13 | 1573 | 19353 | 20449 | 1.0566 | 0.081279 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10680 |  | 2008-04-18 07:29 | 2008-04-18 | 2008-04-18 10:10 | Calculated | o410e | LF2731 &1504 | 0 |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 3 | 19353 | 483 | 0.02496 | 0.00015501 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10681 |  | 2008-04-18 09:31 | 2008-04-18 | 2008-04-18 14:04 | Calculated | o410e | LF441 | 0 |  | Oparure 107-03 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 273 | 4 | 19353 | 1092 | 0.05643 | 0.00020669 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10682 |  | 2008-04-18 10:34 | 2008-04-18 | 2008-04-18 11:02 | Calculated | o410e | LF2154 | 0 |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 28 | 46 | 19353 | 1288 | 0.06655 | 0.0023769 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10683 |  | 2008-04-18 11:50 | 2008-04-18 | 2008-04-18 12:48 | Calculated | o410e | C1724 | 0 |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 13 | 19353 | 754 | 0.03896 | 0.00067173 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10684 |  | 2008-04-18 13:06 | 2008-04-18 | 2008-04-18 14:31 | Calculated | o410e | L6561 | 0 |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 85 | 4 | 19353 | 340 | 0.01757 | 0.00020669 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10685 |  | 2008-04-19 08:00 | 2008-04-19 | 2008-04-19 11:46 | Calculated | o410e | LF11S25 | 0 |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 226 | 28 | 19353 | 6328 | 0.32698 | 0.0014468 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10686 |  | 2008-04-19 09:04 | 2008-04-19 | 2008-04-19 12:00 | Calculated | o410e | S417 | 0 |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 176 | 28 | 19353 | 4928 | 0.25464 | 0.0014468 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10687 |  | 2008-04-19 09:04 | 2008-04-19 | 2008-04-19 15:09 | Calculated | o410e | C411 | 0 |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 365 | 9 | 19353 | 3285 | 0.16974 | 0.00046504 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10688 |  | 2008-04-19 22:12 | 2008-04-19 | 2008-04-19 23:34 | Calculated | o410e | L497 | 0 |  | Motuoapa 425-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 24 | 19353 | 1968 | 0.10169 | 0.0012401 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
23468 | Ranginui Road - By McCaughans (Originally left out) | 2008-04-20 09:00 | 2008-04-20 | 2008-04-20 13:52 | Calculated | 411 | 411 - Recloser with Bypass & Links 411 |  | No Segment | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 9 | 19353 | 2628 | 0.13579 | 0.00046504 | 1388 | 405296 | 2008/2009 | April-2008 | 4 | 2008
23469 | Tongaporutu - North of Rapanui Street (Left out of old system) | 2008-04-20 12:35 | 2008-04-20 | 2008-04-20 13:51 | Calculated | 1635 | 1635 - Air Break Switch 1635 | T2193 - 3ph 100kVA POLEMNT | 128SEG1635-1626 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Joint - Mechanical / Tension | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 118 | 19353 | 8968 | 0.46339 | 0.0060972 | 853.5 | 64866 | 2008/2009 | April-2008 | 4 | 2008
10689 |  | 2008-04-21 09:49 | 2008-04-21 | 2008-04-21 15:10 | Calculated | o410e | L6619 | 0 |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 6 | 19353 | 1926 | 0.09952 | 0.00031003 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10690 |  | 2008-04-21 10:07 | 2008-04-21 | 2008-04-21 14:59 | Calculated | o410e | LF3194 | 0 |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 1 | 19353 | 292 | 0.01509 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10691 |  | 2008-04-21 10:41 | 2008-04-21 | 2008-04-21 14:24 | Calculated | o410e | L1532 | 0 |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 223 | 2 | 19353 | 446 | 0.02305 | 0.00010334 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10692 |  | 2008-04-21 10:46 | 2008-04-21 | 2008-04-21 13:09 | Calculated | o410e | L402 | 0 |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 143 | 15 | 19353 | 2145 | 0.11084 | 0.00077507 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10693 |  | 2008-04-22 05:06 | 2008-04-22 | 2008-04-22 06:41 | Calculated | o410e | C198 | 0 |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 1292 | 19353 | 144056 | 7.4436 | 0.06676 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10697 |  | 2008-04-22 09:02 | 2008-04-22 | 2008-04-22 14:19 | Calculated | o410e | L358 | 0 |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 317 | 7 | 19353 | 2219 | 0.11466 | 0.0003617 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10698 |  | 2008-04-22 09:31 | 2008-04-22 | 2008-04-22 13:01 | Calculated | o410e | L6619 | 0 |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 210 | 6 | 19353 | 1260 | 0.06511 | 0.00031003 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10699 |  | 2008-04-22 10:00 | 2008-04-22 | 2008-04-22 11:22 | Calculated | o410e | LF1937 | 0 |  | Aria 114-01 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 1 | 19353 | 82 | 0.00424 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10700 |  | 2008-04-22 11:22 | 2008-04-22 | 2008-04-22 12:54 | Calculated | o410e | LF3082 | 0 |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 1 | 19353 | 92 | 0.00475 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10701 |  | 2008-04-22 12:55 | 2008-04-22 | 2008-04-22 19:45 | Calculated | o410e | LF20L49 | 0 |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 410 | 37 | 19353 | 15170 | 0.78386 | 0.0019118 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10702 |  | 2008-04-22 12:59 | 2008-04-22 | 2008-04-22 14:26 | Calculated | o410e | C1335 | 0 |  | Benneydale 103-10 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 13 | 19353 | 1131 | 0.05844 | 0.00067173 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10703 |  | 2008-04-23 08:38 | 2008-04-23 | 2008-04-23 08:54 | Calculated | o410e | S865 | 0 |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 520 | 19353 | 43742 | 2.2602 | 0.026869 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10708 |  | 2008-04-23 09:03 | 2008-04-23 | 2008-04-23 13:46 | Calculated | o410e | L354 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 283 | 6 | 19353 | 1698 | 0.08774 | 0.00031003 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10709 |  | 2008-04-23 09:32 | 2008-04-23 | 2008-04-23 15:16 | Calculated | o410e | L6619 | 0 |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 344 | 6 | 19353 | 2064 | 0.10665 | 0.00031003 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10710 |  | 2008-04-23 10:18 | 2008-04-23 | 2008-04-23 10:47 | Calculated | o410e | LF2396 | 0 |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 29 | 1 | 19353 | 29 | 0.0015 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10711 |  | 2008-04-23 10:50 | 2008-04-23 | 2008-04-23 11:40 | Calculated | o410e | LF1184 | 0 |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 50 | 1 | 19353 | 50 | 0.00258 | 5.1672e-05 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10717 |  | 2008-04-24 08:00 | 2008-04-24 | 2008-04-24 11:42 | Calculated | o410e | LF4034 | 0 |  | Manunui 407-01 (was Affco) | Remote Rural F | Manunui | Manunui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 222 | 6 | 19353 | 1332 | 0.06883 | 0.00031003 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10712 |  | 2008-04-24 08:30 | 2008-04-24 | 2008-04-24 08:58 | Calculated | o410e | C641 | 0 |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 28 | 542 | 19353 | 11427 | 0.59045 | 0.028006 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10715 |  | 2008-04-24 09:00 | 2008-04-24 | 2008-04-24 13:32 | Calculated | o410e | L637 | 0 |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 15 | 19353 | 4080 | 0.21082 | 0.00077507 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10716 |  | 2008-04-24 10:00 | 2008-04-24 | 2008-04-24 13:15 | Calculated | o410e | L443 | 0 |  | Wharepapa 122-01 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 195 | 11 | 19353 | 2145 | 0.11084 | 0.00056839 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10718 |  | 2008-04-24 10:50 | 2008-04-24 | 2008-04-24 16:55 | Calculated | o410e | LF304 | 0 |  | Wharepapa 122-06 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 365 | 5 | 19353 | 1825 | 0.0943 | 0.00025836 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10719 |  | 2008-04-24 22:04 | 2008-04-24 | 2008-04-25 00:01 | Calculated | o410e | LF2346 | 0 |  | Te Mapara 117-01 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 6 | 19353 | 342 | 0.01767 | 0.00031003 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10721 |  | 2008-04-25 19:03 | 2008-04-25 | 2008-04-25 21:11 | Calculated | o410e | C1717 | 0 |  | Mokauiti 115-04 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 17 | 19353 | 2176 | 0.11244 | 0.00087842 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10722 |  | 2008-04-25 21:28 | 2008-04-25 | 2008-04-25 22:37 | Calculated | o410e | C144 | 0 |  | National Park 411-02 | Remote Rural F | National Park | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 282 | 19353 | 23844 | 1.2321 | 0.014571 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10726 |  | 2008-04-27 20:58 | 2008-04-27 | 2008-04-28 05:26 | Calculated | o410e | LF5F27 | 0 |  | Nihoniho 412-01 | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 508 | 2 | 19353 | 1016 | 0.0525 | 0.00010334 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10727 |  | 2008-04-28 08:30 | 2008-04-28 | 2008-04-28 10:17 | Calculated | o410e | L2063 | 0 |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 6 | 19353 | 642 | 0.03317 | 0.00031003 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10728 |  | 2008-04-28 08:40 | 2008-04-28 | 2008-04-28 08:45 | Calculated | o410e | S865 | 0 |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 495 | 19353 | 25800 | 1.3331 | 0.025577 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10733 |  | 2008-04-28 14:10 | 2008-04-28 | 2008-04-28 15:02 | Calculated | o410e | C 1728 | 0 |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 28 | 19353 | 1456 | 0.07523 | 0.0014468 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10734 |  | 2008-04-29 08:35 | 2008-04-29 | 2008-04-29 09:48 | Calculated | o410e | S 496 | 0 |  | Mangakino 118-01 | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 568 | 19353 | 55308 | 2.8579 | 0.029349 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10738 |  | 2008-04-29 08:39 | 2008-04-29 | 2008-04-29 08:46 | Calculated | o410e | C 641 | 0 |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 7 | 542 | 19353 | 10690 | 0.55237 | 0.028006 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10741 |  | 2008-04-29 09:20 | 2008-04-29 | 2008-04-29 09:40 | Calculated | o410e | LF217 | 38 |  | Maihiihi 111-08 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 2 | 19353 | 40 | 0.00207 | 0.00010334 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10742 |  | 2008-04-29 12:30 | 2008-04-29 | 2008-04-29 14:09 | Calculated | o410e | L1708 | 0 |  | Mokauiti 115-02 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 13 | 19353 | 2405 | 0.12427 | 0.00067173 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10743 |  | 2008-04-29 13:47 | 2008-04-29 | 2008-04-29 15:35 | Calculated | o410e | LF1539 | 0 |  | Coast 125-03 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 2 | 19353 | 216 | 0.01116 | 0.00010334 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10744 |  | 2008-04-29 17:28 | 2008-04-29 | 2008-04-29 18:43 | Calculated | o410e | S 418 | 0 |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 38 | 19353 | 2850 | 0.14726 | 0.0019635 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10745 |  | 2008-04-30 03:18 | 2008-04-30 | 2008-04-30 06:53 | Calculated | o410e | C806 | 0 |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 215 | 46 | 19353 | 14577 | 0.75322 | 0.0023769 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10751 |  | 2008-04-30 09:00 | 2008-04-30 | 2008-04-30 12:09 | Calculated | o410e | LF7D24 | 0 |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 189 | 32 | 19353 | 6048 | 0.31251 | 0.0016535 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10750 |  | 2008-04-30 09:02 | 2008-04-30 | 2008-04-30 09:35 | Calculated | o410e | C 992 & 180 | 0 |  | No Asset Group | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 33 | 981 | 19353 | 32373 | 1.6728 | 0.05069 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10752 |  | 2008-04-30 09:05 | 2008-04-30 | 2008-04-30 14:43 | Calculated | o410e | C352 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 338 | 26 | 19353 | 8788 | 0.45409 | 0.0013435 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10753 |  | 2008-04-30 09:32 | 2008-04-30 | 2008-04-30 13:00 | Calculated | o410e | LF9K46 | 0 |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 208 | 3 | 19353 | 624 | 0.03224 | 0.00015501 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10754 |  | 2008-04-30 09:35 | 2008-04-30 | 2008-04-30 14:56 | Calculated | o410e | L6563 | 0 |  | Tangiwai 416-02 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 318 | 33 | 19353 | 10494 | 0.54224 | 0.0017052 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10755 |  | 2008-04-30 09:51 | 2008-04-30 | 2008-04-30 10:35 | Calculated | o410e | LF3G1 | 0 |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 2 | 19353 | 88 | 0.00455 | 0.00010334 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10756 |  | 2008-04-30 10:02 | 2008-04-30 | 2008-04-30 11:12 | Calculated | o410e | L674 | 0 |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 70 | 13 | 19353 | 910 | 0.04702 | 0.00067173 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10757 |  | 2008-04-30 10:04 | 2008-04-30 | 2008-04-30 13:57 | Calculated | o410e | L1532 | 0 |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 233 | 3 | 19353 | 699 | 0.03612 | 0.00015501 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10758 |  | 2008-04-30 10:06 | 2008-04-30 | 2008-04-30 11:32 | Calculated | o410e | L5017 | 0 |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 86 | 67 | 19353 | 9662 | 0.49925 | 0.003462 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10760 |  | 2008-04-30 10:08 | 2008-04-30 | 2008-04-30 11:33 | Calculated | o410e | L333 | 0 |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 24 | 19353 | 2040 | 0.10541 | 0.0012401 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10761 |  | 2008-04-30 12:14 | 2008-04-30 | 2008-04-30 13:31 | Calculated | o410e | S463 | 0 |  | No Asset Group | Remote Rural F | Mangakino | Maraetai Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 123 | 19353 | 9471 | 0.48938 | 0.0063556 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10762 |  | 2008-04-30 13:31 | 2008-04-30 | 2008-04-30 16:33 | Calculated | o410e | L6619 | 0 |  | No Asset Group | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 182 | 6 | 19353 | 1092 | 0.05643 | 0.00031003 | 0 | 0 | 2008/2009 | April-2008 | 4 | 2008
10763 |  | 2008-05-01 08:18 | 2008-05-01 | 2008-05-01 09:49 | Calculated | o410e | LF13K2 | 0 |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 13 | 19353 | 1183 | 0.06113 | 0.00067173 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10764 |  | 2008-05-01 10:30 | 2008-05-01 | 2008-05-01 14:12 | Calculated | o410e | L179 | 0 |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 222 | 12 | 19353 | 2664 | 0.13765 | 0.00062006 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10765 |  | 2008-05-01 13:14 | 2008-05-01 | 2008-05-01 13:50 | Calculated | o410e | LF9R3 | 0 |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 2 | 19353 | 72 | 0.00372 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10766 |  | 2008-05-01 17:56 | 2008-05-01 | 2008-05-01 19:57 | Calculated | o410e | LF10S14 | 0 |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 97 | 19353 | 11737 | 0.60647 | 0.0050121 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10767 |  | 2008-05-02 09:00 | 2008-05-02 | 2008-05-02 13:53 | Calculated | o410e | L 360 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 293 | 10 | 19353 | 2930 | 0.1514 | 0.00051672 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10768 |  | 2008-05-02 09:00 | 2008-05-02 | 2008-05-02 09:03 | Calculated | o410e | S454 | 0 |  | Tihoi 124-03 (was Tihoi 124-06) | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 3 | 109 | 19353 | 15979 | 0.82566 | 0.0056322 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10770 |  | 2008-05-02 09:15 | 2008-05-02 | 2008-05-02 09:33 | Calculated | o410e | L663 | 0 |  | Maihiihi 111-01 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 7 | 19353 | 126 | 0.00651 | 0.0003617 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10771 |  | 2008-05-02 14:11 | 2008-05-02 | 2008-05-02 15:20 | Calculated | o410e | C1724 | 0 |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 52 | 19353 | 4979 | 0.25727 | 0.0026869 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10775 |  | 2008-05-04 20:59 | 2008-05-04 | 2008-05-04 21:25 | Calculated | o410e | C 6143 | 0 |  | No Asset Group | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 26 | 4 | 19353 | 104 | 0.00537 | 0.00020669 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10776 |  | 2008-05-05 04:58 | 2008-05-05 | 2008-05-05 07:07 | Calculated | o410e | C 316 | 0 |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 18 | 19353 | 2322 | 0.11998 | 0.00093009 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10777 |  | 2008-05-05 06:24 | 2008-05-05 | 2008-05-05 07:23 | Calculated | o410e | C 218 | 0 |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 52 | 19353 | 13493 | 0.6972 | 0.0026869 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10779 |  | 2008-05-05 08:05 | 2008-05-05 | 2008-05-05 12:07 | Calculated | o410e | C 368 | 0 |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 242 | 7 | 19353 | 2934 | 0.1516 | 0.0003617 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10781 |  | 2008-05-05 09:30 | 2008-05-05 | 2008-05-05 10:50 | Calculated | o410e | S339 | 0 |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 80 | 27 | 19353 | 2160 | 0.11161 | 0.0013951 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10782 |  | 2008-05-05 15:56 | 2008-05-05 | 2008-05-05 16:58 | Calculated | o410e | S711 | 0 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 31 | 19353 | 1922 | 0.09931 | 0.0016018 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10783 |  | 2008-05-06 10:05 | 2008-05-06 | 2008-05-06 10:58 | Calculated | o410e | C 5847 | 0 |  | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 53 | 26 | 19353 | 1378 | 0.0712 | 0.0013435 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10784 |  | 2008-05-06 11:56 | 2008-05-06 | 2008-05-06 12:22 | Calculated | o410e | LF1006 | 0 |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 1 | 19353 | 26 | 0.00134 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10785 |  | 2008-05-07 07:05 | 2008-05-07 | 2008-05-07 07:36 | Calculated | o410e | S314 | 0 |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 31 | 12 | 19353 | 372 | 0.01922 | 0.00062006 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10787 |  | 2008-05-07 09:02 | 2008-05-07 | 2008-05-07 09:34 | Calculated | o410e | S320 | 0 |  | McDonalds 110-02 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 32 | 131 | 19353 | 9408 | 0.48613 | 0.006769 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10790 |  | 2008-05-07 09:35 | 2008-05-07 | 2008-05-07 11:55 | Calculated | o410e | L1528 | 0 |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 140 | 7 | 19353 | 980 | 0.05064 | 0.0003617 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10791 |  | 2008-05-07 13:00 | 2008-05-07 | 2008-05-07 15:34 | Calculated | o410e | LF20L34 | 0 |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 154 | 64 | 19353 | 9856 | 0.50928 | 0.003307 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10786 |  | 2008-05-07 15:42 | 2008-05-07 | 2008-05-07 16:23 | Calculated | o410e | S314 | 0 |  | Otorohanga 112-02 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 12 | 19353 | 492 | 0.02542 | 0.00062006 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10792 |  | 2008-05-07 17:44 | 2008-05-07 | 2008-05-07 19:26 | Calculated | o410e | LF616 | 0 |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 2 | 19353 | 204 | 0.01054 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10793 |  | 2008-05-07 19:30 | 2008-05-07 | 2008-05-07 20:30 | Calculated | o410e | LF404 | 0 |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 1 | 19353 | 60 | 0.0031 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10794 |  | 2008-05-08 09:45 | 2008-05-08 | 2008-05-08 11:23 | Calculated | o410e | L596 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 23 | 19353 | 2254 | 0.11647 | 0.0011884 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10795 |  | 2008-05-08 09:50 | 2008-05-08 | 2008-05-08 11:32 | Calculated | o410e | LF2191 | 0 |  | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 2 | 19353 | 204 | 0.01054 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10796 |  | 2008-05-08 11:00 | 2008-05-08 | 2008-05-08 13:48 | Calculated | o410e | L1529 | 0 |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 2 | 19353 | 336 | 0.01736 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10797 |  | 2008-05-08 11:27 | 2008-05-08 | 2008-05-08 12:34 | Calculated | o410e | LF4254 | 0 |  | No Asset Group | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 67 | 1 | 19353 | 67 | 0.00346 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10798 |  | 2008-05-08 12:06 | 2008-05-08 | 2008-05-08 14:36 | Calculated | o410e | LF3023 | 0 |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 150 | 1 | 19353 | 150 | 0.00775 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10799 |  | 2008-05-08 13:00 | 2008-05-08 | 2008-05-08 14:00 | Calculated | o410e | LF10S39 | 0 |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 38 | 19353 | 2280 | 0.11781 | 0.0019635 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10800 |  | 2008-05-08 13:33 | 2008-05-08 | 2008-05-08 14:40 | Calculated | o410e | LF2566 | 0 |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 35 | 19353 | 2345 | 0.12117 | 0.0018085 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10801 |  | 2008-05-09 09:27 | 2008-05-09 | 2008-05-09 09:28 | Calculated | o410e | C242 | 0 |  | No Asset Group | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 243 | 19353 | 243 | 0.01256 | 0.012556 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10802 |  | 2008-05-09 10:10 | 2008-05-09 | 2008-05-09 12:26 | Calculated | o410e | LF216 | 0 |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 2 | 19353 | 272 | 0.01405 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10803 |  | 2008-05-09 10:12 | 2008-05-09 | 2008-05-09 11:47 | Calculated | o410e | L780 | 0 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 12 | 19353 | 1140 | 0.05891 | 0.00062006 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10804 |  | 2008-05-09 11:41 | 2008-05-09 | 2008-05-09 13:58 | Calculated | o410e | C758 | 0 |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 83 | 19353 | 11371 | 0.58756 | 0.0042887 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10805 |  | 2008-05-09 12:30 | 2008-05-09 | 2008-05-09 13:27 | Calculated | o410e | LF1044 | 0 |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 2 | 19353 | 114 | 0.00589 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10806 |  | 2008-05-11 07:15 | 2008-05-11 | 2008-05-11 09:14 | Calculated | o410e | C316 | 0 |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 18 | 19353 | 2858 | 0.14768 | 0.00093009 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10809 |  | 2008-05-12 09:02 | 2008-05-12 | 2008-05-12 12:05 | Calculated | o410e | S1318 | 0 |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 183 | 22 | 19353 | 4026 | 0.20803 | 0.0011368 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10810 |  | 2008-05-12 10:50 | 2008-05-12 | 2008-05-12 14:44 | Calculated | o410e | LF1674 | 0 |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 234 | 1 | 19353 | 234 | 0.01209 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10811 |  | 2008-05-12 14:48 | 2008-05-12 | 2008-05-12 15:35 | Calculated | o410e | LF2280 | 0 |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 2 | 19353 | 94 | 0.00486 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10812 |  | 2008-05-13 17:02 | 2008-05-13 | 2008-05-13 18:36 | Calculated | o410e | S6193 | 0 |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 3 | 19353 | 282 | 0.01457 | 0.00015501 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10813 |  | 2008-05-14 09:00 | 2008-05-14 | 2008-05-14 11:54 | Calculated | o410e | LF408 | 0 |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 174 | 5 | 19353 | 870 | 0.04495 | 0.00025836 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10814 |  | 2008-05-14 09:10 | 2008-05-14 | 2008-05-14 10:54 | Calculated | o410e | LF8M4 | 0 |  | Manunui 408-05 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 104 | 2 | 19353 | 208 | 0.01075 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10815 |  | 2008-05-14 09:16 | 2008-05-14 | 2008-05-14 11:17 | Calculated | o410e | L115 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 6 | 19353 | 726 | 0.03751 | 0.00031003 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10816 |  | 2008-05-14 12:49 | 2008-05-14 | 2008-05-14 14:19 | Calculated | o410e | LF8K5 | 0 |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 2 | 19353 | 180 | 0.0093 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10817 |  | 2008-05-15 08:30 | 2008-05-15 | 2008-05-15 08:55 | Calculated | o410e | S103 | 0 |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 115 | 19353 | 11521 | 0.59531 | 0.0059422 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10819 |  | 2008-05-15 09:00 | 2008-05-15 | 2008-05-15 10:37 | Calculated | o410e | LF8K15 | 0 |  | Manunui 408-04 | Remote Rural F | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 97 | 1 | 19353 | 97 | 0.00501 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10820 |  | 2008-05-15 12:04 | 2008-05-15 | 2008-05-15 12:55 | Calculated | o410e | L886 | 0 |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 3 | 19353 | 153 | 0.00791 | 0.00015501 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10821 |  | 2008-05-15 13:00 | 2008-05-15 | 2008-05-15 14:36 | Calculated | o410e | LF10J3 | 0 |  | Southern 409-01 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 96 | 1 | 19353 | 96 | 0.00496 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10822 |  | 2008-05-16 09:00 | 2008-05-16 | 2008-05-16 10:18 | Calculated | o410e | LF5I10 | 0 |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 78 | 1 | 19353 | 78 | 0.00403 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10823 |  | 2008-05-16 09:08 | 2008-05-16 | 2008-05-16 16:21 | Calculated | o410e | S786 | 0 |  | Mokai 123-02 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 433 | 3 | 19353 | 1299 | 0.06712 | 0.00015501 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10824 |  | 2008-05-16 09:40 | 2008-05-16 | 2008-05-16 14:17 | Calculated | o410e | L1637 | 0 |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 277 | 3 | 19353 | 831 | 0.04294 | 0.00015501 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10825 |  | 2008-05-16 09:54 | 2008-05-16 | 2008-05-16 14:05 | Calculated | o410e | LF6J12 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 251 | 5 | 19353 | 1255 | 0.06485 | 0.00025836 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10826 |  | 2008-05-18 16:37 | 2008-05-18 | 2008-05-18 19:22 | Calculated | o410e | S1336 | 0 |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 13 | 19353 | 2145 | 0.11084 | 0.00067173 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10827 |  | 2008-05-18 16:37 | 2008-05-18 | 2008-05-18 20:24 | Calculated | o410e | S1339 | 0 |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 227 | 39 | 19353 | 8853 | 0.45745 | 0.0020152 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10828 |  | 2008-05-19 09:35 | 2008-05-19 | 2008-05-19 09:37 | Calculated | o410e | C170 | 0 |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 64 | 19353 | 3232 | 0.167 | 0.003307 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10831 |  | 2008-05-19 13:00 | 2008-05-19 | 2008-05-19 14:28 | Calculated | o410e | LF10S41 | 0 |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 58 | 19353 | 5104 | 0.26373 | 0.002997 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10832 |  | 2008-05-20 10:11 | 2008-05-20 | 2008-05-20 13:37 | Calculated | o410e | LF772 | 0 |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 206 | 4 | 19353 | 824 | 0.04258 | 0.00020669 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10833 |  | 2008-05-21 09:01 | 2008-05-21 | 2008-05-21 14:07 | Calculated | o410e | L450 | 0 |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 306 | 17 | 19353 | 5202 | 0.2688 | 0.00087842 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10834 |  | 2008-05-21 10:30 | 2008-05-21 | 2008-05-21 11:37 | Calculated | o410e | LF9R3 | 0 |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 67 | 2 | 19353 | 134 | 0.00692 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10835 |  | 2008-05-21 11:27 | 2008-05-21 | 2008-05-21 11:35 | Calculated | o410e | LF12P1 | 0 |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 9 | 19353 | 72 | 0.00372 | 0.00046504 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10836 |  | 2008-05-21 13:00 | 2008-05-21 | 2008-05-21 13:36 | Calculated | o410e | LF9R8 | 0 |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 2 | 19353 | 72 | 0.00372 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10837 |  | 2008-05-21 15:13 | 2008-05-21 | 2008-05-21 15:26 | Calculated | o410e | S311 | 0 |  | Otorohanga 112-01 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 120 | 19353 | 1560 | 0.08061 | 0.0062006 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10838 |  | 2008-05-22 09:03 | 2008-05-22 | 2008-05-22 14:32 | Calculated | o410e | L450 | 0 |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 329 | 17 | 19353 | 5593 | 0.289 | 0.00087842 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10839 |  | 2008-05-22 09:32 | 2008-05-22 | 2008-05-22 11:19 | Calculated | o410e | S439 | 0 |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 107 | 15 | 19353 | 1605 | 0.08293 | 0.00077507 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10840 |  | 2008-05-22 09:50 | 2008-05-22 | 2008-05-22 11:56 | Calculated | o410e | L705 | 0 |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 6 | 19353 | 756 | 0.03906 | 0.00031003 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10841 |  | 2008-05-22 10:03 | 2008-05-22 | 2008-05-22 10:58 | Calculated | o410e | L617 | 0 |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 20 | 19353 | 1100 | 0.05684 | 0.0010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10842 |  | 2008-05-22 10:08 | 2008-05-22 | 2008-05-22 14:34 | Calculated | o410e | L699 | 0 |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 266 | 11 | 19353 | 2926 | 0.15119 | 0.00056839 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10843 |  | 2008-05-23 09:00 | 2008-05-23 | 2008-05-23 14:52 | Calculated | o410e | L450 | 0 |  | Mokai 123-02 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 352 | 17 | 19353 | 5984 | 0.3092 | 0.00087842 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10844 |  | 2008-05-23 09:06 | 2008-05-23 | 2008-05-23 09:26 | Calculated | o410e | LINK1317 | 0 |  | Te Mapara 117-06 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 20 | 6 | 19353 | 120 | 0.0062 | 0.00031003 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10845 |  | 2008-05-23 09:12 | 2008-05-23 | 2008-05-23 13:40 | Calculated | o410e | S523 | 0 |  | Te Kuiti South 104-01 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 8 | 19353 | 2144 | 0.11078 | 0.00041337 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10846 |  | 2008-05-23 09:28 | 2008-05-23 | 2008-05-23 15:42 | Calculated | o410e | LF703 | 0 |  | Otorohanga 112-05 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 374 | 1 | 19353 | 374 | 0.01933 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10847 |  | 2008-05-23 12:44 | 2008-05-23 | 2008-05-23 14:10 | Calculated | o410e | LF469 | 0 |  | Maihiihi 111-13 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 106 | 3 | 19353 | 318 | 0.01643 | 0.00015501 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10848 |  | 2008-05-23 13:15 | 2008-05-23 | 2008-05-23 13:18 | Calculated | o410e | C992 | 0 |  | No Asset Group | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 981 | 19353 | 2943 | 0.15207 | 0.05069 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10849 |  | 2008-05-24 01:09 | 2008-05-24 | 2008-05-24 01:18 | Calculated | o410e | C754 | 0 |  | No Asset Group | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 1573 | 19353 | 14157 | 0.73151 | 0.081279 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10851 |  | 2008-05-26 10:02 | 2008-05-26 | 2008-05-26 14:20 | Calculated | o410e | C1530 | 0 |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 2 | 19353 | 516 | 0.02666 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10852 |  | 2008-05-26 10:11 | 2008-05-26 | 2008-05-26 11:01 | Calculated | o410e | L6176 | 0 |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 50 | 105 | 19353 | 5250 | 0.27128 | 0.0054255 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10853 |  | 2008-05-26 10:27 | 2008-05-26 | 2008-05-26 11:24 | Calculated | o410e | LF20L57 | 0 |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 57 | 17 | 19353 | 969 | 0.05007 | 0.00087842 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10854 |  | 2008-05-26 10:40 | 2008-05-26 | 2008-05-26 13:11 | Calculated | o410e | LF272 | 0 |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 151 | 1 | 19353 | 151 | 0.0078 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10855 |  | 2008-05-26 13:01 | 2008-05-26 | 2008-05-26 15:48 | Calculated | o410e | L596 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 167 | 23 | 19353 | 3841 | 0.19847 | 0.0011884 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10856 |  | 2008-05-27 10:05 | 2008-05-27 | 2008-05-27 14:07 | Calculated | o410e | L563 | 0 |  | Tuhua 422-02 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 242 | 1 | 19353 | 242 | 0.0125 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10857 |  | 2008-05-27 13:09 | 2008-05-27 | 2008-05-27 14:21 | Calculated | o410e | LF8J12 | 0 |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 72 | 9 | 19353 | 648 | 0.03348 | 0.00046504 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10858 |  | 2008-05-27 14:41 | 2008-05-27 | 2008-05-27 16:16 | Calculated | o410e | C758 | 0 |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 83 | 19353 | 7885 | 0.40743 | 0.0042887 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10860 |  | 2008-05-28 10:40 | 2008-05-28 | 2008-05-28 14:43 | Calculated | o410e | LF7Q8 | 0 |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 243 | 1 | 19353 | 243 | 0.01256 | 5.1672e-05 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10859 |  | 2008-05-28 11:00 | 2008-05-28 | 2008-05-28 13:22 | Calculated | o410e | S425 | 0 |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 142 | 20 | 19353 | 2840 | 0.14675 | 0.0010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10861 |  | 2008-05-29 06:55 | 2008-05-29 | 2008-05-29 07:56 | Calculated | o410e | C127 | 0 |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 465 | 19353 | 28085 | 1.4512 | 0.024027 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10867 |  | 2008-05-29 09:19 | 2008-05-29 | 2008-05-29 13:59 | Calculated | o410e | LF9R5 | 0 |  | No Asset Group | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 280 | 2 | 19353 | 560 | 0.02894 | 0.00010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10868 |  | 2008-05-30 10:00 | 2008-05-30 | 2008-05-30 14:21 | Calculated | o410e | L780 | 0 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 261 | 12 | 19353 | 3132 | 0.16184 | 0.00062006 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10869 |  | 2008-05-30 10:00 | 2008-05-30 | 2008-05-30 12:48 | Calculated | o410e | L357 | 0 |  | Maihiihi 111-07 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 168 | 20 | 19353 | 3792 | 0.19594 | 0.0010334 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10871 |  | 2008-05-30 10:00 | 2008-05-30 | 2008-05-30 14:05 | Calculated | o410e | L777 | 0 |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 8 | 19353 | 1960 | 0.10128 | 0.00041337 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10872 |  | 2008-05-30 21:15 | 2008-05-30 | 2008-05-30 21:45 | Calculated | o410e | LF1143 | 0 |  | Whakamaru 120-02 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 47 | 19353 | 1410 | 0.07286 | 0.0024286 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10873 | te Waireka Road | 2008-05-31 07:17 | 2008-05-31 | 2008-05-31 07:27 | Calculated | o410e | C121 | 0 |  | No Asset Group | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | Incorrect Protection Settings | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 2397 | 19353 | 23970 | 1.2386 | 0.12386 | 0 | 0 | 2008/2009 | May-2008 | 5 | 2008
10874 |  | 2008-06-01 06:54 | 2008-06-01 | 2008-06-01 07:44 | Calculated | o410e | LF11S1 | 0 |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 2 | 19353 | 100 | 0.00517 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10875 |  | 2008-06-01 21:06 | 2008-06-01 | 2008-06-01 21:13 | Calculated | o410e | C142 | 0 |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 278 | 19353 | 1946 | 0.10055 | 0.014365 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10876 |  | 2008-06-02 10:25 | 2008-06-02 | 2008-06-02 10:50 | Calculated | o410e | C2092 | 0 |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 109 | 19353 | 2725 | 0.14081 | 0.0056322 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10877 |  | 2008-06-03 09:06 | 2008-06-03 | 2008-06-03 14:38 | Calculated | o410e | S324 | 0 |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 332 | 40 | 19353 | 13280 | 0.6862 | 0.0020669 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10878 |  | 2008-06-03 09:41 | 2008-06-03 | 2008-06-03 09:44 | Calculated | o410e | C313 | 0 |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 3 | 44 | 19353 | 4488 | 0.2319 | 0.0022735 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10881 |  | 2008-06-04 06:53 | 2008-06-04 | 2008-06-04 07:48 | Calculated | o410e | C1724 | 0 |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 13 | 19353 | 715 | 0.03695 | 0.00067173 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10882 |  | 2008-06-04 10:00 | 2008-06-04 | 2008-06-04 11:57 | Calculated | o410e | C378 | 0 |  | Wharepapa 122-03 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 28 | 19353 | 3276 | 0.16928 | 0.0014468 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10883 |  | 2008-06-04 11:03 | 2008-06-04 | 2008-06-04 12:44 | Calculated | o410e | L1127 | 0 |  | Aria 114-04 | Remote Rural F | Aria | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 8 | 19353 | 808 | 0.04175 | 0.00041337 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10885 |  | 2008-06-05 09:38 | 2008-06-05 | 2008-06-05 13:26 | Calculated | o410e | LF7I8 | 0 |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 228 | 3 | 19353 | 684 | 0.03534 | 0.00015501 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10886 |  | 2008-06-05 10:02 | 2008-06-05 | 2008-06-05 14:17 | Calculated | o410e | S192 | 0 |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 255 | 28 | 19353 | 7140 | 0.36894 | 0.0014468 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10887 |  | 2008-06-05 10:52 | 2008-06-05 | 2008-06-05 12:07 | Calculated | o410e | S629 | 0 |  | McDonalds 110-01 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other |  | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 36 | 19353 | 2700 | 0.13951 | 0.0018602 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10888 |  | 2008-06-05 13:33 | 2008-06-05 | 2008-06-05 15:16 | Calculated | o410e | LF242 | 0 |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 103 | 3 | 19353 | 309 | 0.01597 | 0.00015501 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10889 |  | 2008-06-06 09:50 | 2008-06-06 | 2008-06-06 13:42 | Calculated | o410e | L369 | 0 |  | Wharepapa 122-08 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 7 | 19353 | 1624 | 0.08391 | 0.0003617 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10891 |  | 2008-06-06 18:05 | 2008-06-06 | 2008-06-06 21:55 | Calculated | o410e | LF15N2 | 0 |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 230 | 2 | 19353 | 460 | 0.02377 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10892 |  | 2008-06-07 09:56 | 2008-06-07 | 2008-06-07 10:48 | Calculated | o410e | LF20M1 | 0 |  | Turoa 415-04 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 1 | 19353 | 52 | 0.00269 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10893 |  | 2008-06-07 21:48 | 2008-06-07 | 2008-06-07 23:04 | Calculated | o410e | C799 | 0 |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 26 | 19353 | 1976 | 0.1021 | 0.0013435 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10894 |  | 2008-06-07 22:05 | 2008-06-07 | 2008-06-07 22:14 | Calculated | o410e | C1512 | 0 |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 139 | 19353 | 1251 | 0.06464 | 0.0071823 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10895 |  | 2008-06-07 22:24 | 2008-06-07 | 2008-06-07 22:32 | Calculated | o410e | C6143 | 0 |  | No Asset Group | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 4 | 19353 | 32 | 0.00165 | 0.00020669 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10896 |  | 2008-06-07 22:37 | 2008-06-07 | 2008-06-08 04:00 | Calculated | o410e | L1736 | 0 |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 323 | 9 | 19353 | 2907 | 0.15021 | 0.00046504 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10897 |  | 2008-06-08 06:21 | 2008-06-08 | 2008-06-08 08:12 | Calculated | o410e | C5107 | 0 |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 44 | 19353 | 4884 | 0.25236 | 0.0022735 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10898 |  | 2008-06-08 08:26 | 2008-06-08 | 2008-06-08 10:10 | Calculated | o410e | C820 | 0 |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 246 | 19353 | 22500 | 1.1626 | 0.012711 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10899 |  | 2008-06-09 10:06 | 2008-06-09 | 2008-06-09 14:04 | Calculated | o410e | L509 | 0 |  | Rural 126-02 | Remote Rural F | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 238 | 7 | 19353 | 1666 | 0.08608 | 0.0003617 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10900 |  | 2008-06-09 10:07 | 2008-06-09 | 2008-06-09 12:03 | Calculated | o410e | L548 | 0 |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 23 | 19353 | 2691 | 0.13905 | 0.0011884 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10901 |  | 2008-06-09 13:07 | 2008-06-09 | 2008-06-09 15:19 | Calculated | o410e | LF10S37 | 0 |  | Turangi 423-01 | Remote Rural F | Turangi | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 132 | 72 | 19353 | 9504 | 0.49109 | 0.0037204 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10902 |  | 2008-06-10 09:45 | 2008-06-10 | 2008-06-10 11:39 | Calculated | o410e | LF15L5 | 0 |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 1 | 19353 | 114 | 0.00589 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10903 |  | 2008-06-10 10:30 | 2008-06-10 | 2008-06-10 13:11 | Calculated | o410e | LF6Q9 | 0 |  | Waihaha 426-04 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 1 | 19353 | 161 | 0.00832 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10904 |  | 2008-06-10 13:03 | 2008-06-10 | 2008-06-10 16:35 | Calculated | o410e | LF1048 | 0 |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 212 | 2 | 19353 | 424 | 0.02191 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10905 |  | 2008-06-10 14:29 | 2008-06-10 | 2008-06-10 15:54 | Calculated | o410e | S573 | 0 |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 35 | 19353 | 2975 | 0.15372 | 0.0018085 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10906 |  | 2008-06-11 09:43 | 2008-06-11 | 2008-06-11 13:33 | Calculated | o410e | LF1203 | 0 |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 230 | 2 | 19353 | 460 | 0.02377 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10907 |  | 2008-06-11 10:20 | 2008-06-11 | 2008-06-11 11:34 | Calculated | o410e | LF3187 | 0 |  | No Asset Group | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 74 | 1 | 19353 | 74 | 0.00382 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10908 |  | 2008-06-11 11:55 | 2008-06-11 | 2008-06-11 14:18 | Calculated | o410e | L1617 | 0 |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 2 | 19353 | 286 | 0.01478 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10909 |  | 2008-06-12 10:08 | 2008-06-12 | 2008-06-12 12:34 | Calculated | o410e | C371 | 0 |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 25 | 19353 | 3650 | 0.1886 | 0.0012918 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10910 |  | 2008-06-13 10:02 | 2008-06-13 | 2008-06-13 12:08 | Calculated | o410e | C884 | 0 |  | Southern 409-08 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 126 | 19 | 19353 | 2394 | 0.1237 | 0.00098176 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10911 |  | 2008-06-13 10:35 | 2008-06-13 | 2008-06-13 15:13 | Calculated | o410e | LF1988 | 0 |  | Aria 114-06 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 278 | 2 | 19353 | 556 | 0.02873 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10913 |  | 2008-06-15 20:28 | 2008-06-15 | 2008-06-15 20:47 | Calculated | o410e | C955 | 0 |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 1083 | 19353 | 84840 | 4.3838 | 0.05596 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10915 |  | 2008-06-16 10:13 | 2008-06-16 | 2008-06-16 12:31 | Calculated | o410e | S1313 | 0 |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 138 | 17 | 19353 | 2346 | 0.12122 | 0.00087842 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10916 |  | 2008-06-16 11:56 | 2008-06-16 | 2008-06-16 13:43 | Calculated | o410e | C5107 | 0 |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 44 | 19353 | 4708 | 0.24327 | 0.0022735 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10917 |  | 2008-06-17 08:32 | 2008-06-17 | 2008-06-17 08:36 | Calculated | o410e | C108 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 35 | 19353 | 449 | 0.0232 | 0.0018085 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10918 |  | 2008-06-17 09:50 | 2008-06-17 | 2008-06-17 11:16 | Calculated | o410e | L231 | 0 |  | Oparure 107-06 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 4 | 19353 | 344 | 0.01778 | 0.00020669 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10919 |  | 2008-06-17 09:51 | 2008-06-17 | 2008-06-17 12:26 | Calculated | o410e | S1606 | 0 |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 12 | 19353 | 1860 | 0.09611 | 0.00062006 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10920 |  | 2008-06-17 11:25 | 2008-06-17 | 2008-06-17 12:00 | Calculated | o410e | LF1242 | 0 |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 1 | 19353 | 35 | 0.00181 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10921 |  | 2008-06-17 12:04 | 2008-06-17 | 2008-06-17 13:37 | Calculated | o410e | LF1290 | 0 |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 93 | 1 | 19353 | 93 | 0.00481 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10922 |  | 2008-06-17 16:55 | 2008-06-17 | 2008-06-17 18:03 | Calculated | o410e | C277 | 0 |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 9 | 19353 | 612 | 0.03162 | 0.00046504 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10923 |  | 2008-06-18 08:39 | 2008-06-18 | 2008-06-18 08:40 | Calculated | o410e | C108 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 16 | 19353 | 16 | 0.00083 | 0.00082675 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10924 |  | 2008-06-18 09:01 | 2008-06-18 | 2008-06-18 14:21 | Calculated | o410e | L1298 | 0 |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 320 | 8 | 19353 | 2560 | 0.13228 | 0.00041337 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10925 |  | 2008-06-18 09:17 | 2008-06-18 | 2008-06-18 14:25 | Calculated | o410e | LF1210 | 0 |  | Maihiihi 111-05 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 308 | 1 | 19353 | 308 | 0.01591 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10926 |  | 2008-06-18 10:56 | 2008-06-18 | 2008-06-18 11:50 | Calculated | o410e | S6160 | 0 |  | Ohakune Town 414-01 | Remote Rural F | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 2 | 19353 | 108 | 0.00558 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10928 |  | 2008-06-19 09:35 | 2008-06-19 | 2008-06-19 21:01 | Calculated | o410e | S321 | 0 |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 686 | 4 | 19353 | 2744 | 0.14179 | 0.00020669 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10929 |  | 2008-06-19 10:05 | 2008-06-19 | 2008-06-19 11:47 | Calculated | o410e | S408 | 0 |  | Waihaha 426-02 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 103 | 19353 | 10506 | 0.54286 | 0.0053222 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10930 |  | 2008-06-19 20:23 | 2008-06-19 | 2008-06-19 22:26 | Calculated | o410e | L364 | 0 |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 30 | 19353 | 3690 | 0.19067 | 0.0015501 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10931 |  | 2008-06-20 07:00 | 2008-06-20 | 2008-06-20 11:57 | Calculated | o410e | LF673 | 0 |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Animals |  | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 297 | 2 | 19353 | 594 | 0.03069 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10932 |  | 2008-06-20 07:01 | 2008-06-20 | 2008-06-20 08:41 | Calculated | o410e | LF357 | 0 |  | Maihiihi 111-14 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 1 | 19353 | 100 | 0.00517 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10933 |  | 2008-06-20 09:00 | 2008-06-20 | 2008-06-20 13:08 | Calculated | o410e | L1298 | 0 |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 8 | 19353 | 1984 | 0.10252 | 0.00041337 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10934 |  | 2008-06-20 09:26 | 2008-06-20 | 2008-06-20 13:06 | Calculated | o410e | LF8I13 | 0 |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 220 | 3 | 19353 | 660 | 0.0341 | 0.00015501 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10935 |  | 2008-06-20 09:27 | 2008-06-20 | 2008-06-20 13:52 | Calculated | o410e | LF464 | 0 |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 265 | 7 | 19353 | 1855 | 0.09585 | 0.0003617 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10936 |  | 2008-06-20 14:02 | 2008-06-20 | 2008-06-20 14:40 | Calculated | o410e | LF369 | 0 |  | Gravel Scoop 109-06 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 3 | 19353 | 114 | 0.00589 | 0.00015501 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10937 |  | 2008-06-21 20:33 | 2008-06-21 | 2008-06-21 22:34 | Calculated | o410e | C296 | 0 |  | Coast 125-04 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 139 | 19353 | 16819 | 0.86906 | 0.0071823 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10938 |  | 2008-06-22 09:23 | 2008-06-22 | 2008-06-22 10:16 | Calculated | o410e | S399 | 0 |  | Maihiihi 111-13 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 39 | 19353 | 2067 | 0.10681 | 0.0020152 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10939 |  | 2008-06-22 09:25 | 2008-06-22 | 2008-06-22 11:36 | Calculated | o410e | L1736 | 0 |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 9 | 19353 | 1179 | 0.06092 | 0.00046504 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10941 |  | 2008-06-23 14:15 | 2008-06-23 | 2008-06-23 15:32 | Calculated | o410e | C1724 | 0 |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 13 | 19353 | 1001 | 0.05172 | 0.00067173 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10940 |  | 2008-06-23 15:41 | 2008-06-23 | 2008-06-23 15:43 | Calculated | o410e | C242 | 0 |  | No Asset Group | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 243 | 19353 | 486 | 0.02511 | 0.012556 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10942 |  | 2008-06-23 19:03 | 2008-06-23 | 2008-06-23 20:18 | Calculated | o410e | L1263 | 0 |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 19353 | 75 | 0.00388 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10943 |  | 2008-06-24 08:35 | 2008-06-24 | 2008-06-25 15:42 | Calculated | o410e | LF1836 | 0 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1867 | 1 | 19353 | 1867 | 0.09647 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10944 |  | 2008-06-24 10:15 | 2008-06-24 | 2008-06-24 13:13 | Calculated | o410e | C1630 | 0 |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 178 | 31 | 19353 | 6607 | 0.34139 | 0.0016018 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10945 |  | 2008-06-24 14:58 | 2008-06-24 | 2008-06-24 16:50 | Calculated | o410e | C1724 | 0 |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 20 | 19353 | 7700 | 0.39787 | 0.0010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10946 |  | 2008-06-25 07:17 | 2008-06-25 | 2008-06-25 11:58 | Calculated | o410e | LF1836 | 0 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 281 | 1 | 19353 | 281 | 0.01452 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10947 |  | 2008-06-25 08:18 | 2008-06-25 | 2008-06-25 09:31 | Calculated | o410e | C961 | 0 |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 109 | 19353 | 8040 | 0.41544 | 0.0056322 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10948 |  | 2008-06-25 09:05 | 2008-06-25 | 2008-06-25 11:43 | Calculated | o410e | LF2928 | 0 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 1 | 19353 | 158 | 0.00816 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10949 |  | 2008-06-25 09:35 | 2008-06-25 | 2008-06-25 14:03 | Calculated | o410e | L424 | 0 |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 10 | 19353 | 2680 | 0.13848 | 0.00051672 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10950 |  | 2008-06-25 10:27 | 2008-06-25 | 2008-06-25 11:49 | Calculated | o410e | LF196 | 0 |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 2 | 19353 | 164 | 0.00847 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10951 |  | 2008-06-25 14:17 | 2008-06-25 | 2008-06-25 14:49 | Calculated | o410e | L1726 | 0 |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 6 | 19353 | 192 | 0.00992 | 0.00031003 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10952 |  | 2008-06-25 14:34 | 2008-06-25 | 2008-06-25 15:05 | Calculated | o410e | C1536 | 0 |  | Coast 125-06 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 7 | 19353 | 217 | 0.01121 | 0.0003617 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10953 |  | 2008-06-25 15:37 | 2008-06-25 | 2008-06-25 18:18 | Calculated | o410e | LF416 | 0 |  | Maihiihi 111-13 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 2 | 19353 | 322 | 0.01664 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10954 |  | 2008-06-25 16:27 | 2008-06-25 | 2008-06-25 21:30 | Calculated | o410e | L509 | 0 |  | Rural 126-02 | Remote Rural F | Rural | Taharoa Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 303 | 7 | 19353 | 2121 | 0.1096 | 0.0003617 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10955 |  | 2008-06-25 18:29 | 2008-06-25 | 2008-06-25 19:10 | Calculated | o410e | L1725 | 0 |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Asset Related | Other |  | Operational or Safety Restriction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 6 | 19353 | 246 | 0.01271 | 0.00031003 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10956 |  | 2008-06-25 21:56 | 2008-06-25 | 2008-06-25 21:57 | Calculated | o410e | C6143 | 0 |  | No Asset Group | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 4 | 19353 | 4 | 0.00021 | 0.00020669 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10957 |  | 2008-06-26 00:47 | 2008-06-26 | 2008-06-26 09:00 | Calculated | o410e | LF1889 | 0 |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 493 | 1 | 19353 | 493 | 0.02547 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10958 |  | 2008-06-26 06:33 | 2008-06-26 | 2008-06-26 09:42 | Calculated | o410e | LF1876 | 0 |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 189 | 1 | 19353 | 189 | 0.00977 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10959 |  | 2008-06-26 07:34 | 2008-06-26 | 2008-06-26 10:15 | Calculated | o410e | LF13I11 | 0 |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 1 | 19353 | 161 | 0.00832 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10960 |  | 2008-06-26 07:42 | 2008-06-26 | 2008-06-26 10:28 | Calculated | o410e | LF4I16 | 0 |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 1 | 19353 | 166 | 0.00858 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10961 |  | 2008-06-26 07:51 | 2008-06-26 | 2008-06-26 12:43 | Calculated | o410e | LF45 | 0 |  | Hakiaha 401-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 292 | 2 | 19353 | 584 | 0.03018 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10962 |  | 2008-06-26 08:05 | 2008-06-26 | 2008-06-26 11:36 | Calculated | o410e | LF13K7 | 0 |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 211 | 4 | 19353 | 844 | 0.04361 | 0.00020669 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10963 |  | 2008-06-26 08:10 | 2008-06-26 | 2008-06-26 10:50 | Calculated | o410e | C396 | 0 |  | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 26 | 19353 | 4160 | 0.21495 | 0.0013435 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10964 |  | 2008-06-26 09:10 | 2008-06-26 | 2008-06-26 13:06 | Calculated | o410e | LF2053 | 0 |  | Mokauiti 115-04 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 236 | 1 | 19353 | 236 | 0.01219 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10965 |  | 2008-06-26 09:20 | 2008-06-26 | 2008-06-26 15:36 | Calculated | o410e | LF576 | 0 |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 376 | 2 | 19353 | 752 | 0.03886 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10966 |  | 2008-06-26 10:00 | 2008-06-26 | 2008-06-26 12:24 | Calculated | o410e | LF1954 | 0 |  | Aria 114-03 | Remote Rural F | Aria | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 1 | 19353 | 144 | 0.00744 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10967 |  | 2008-06-26 10:04 | 2008-06-26 | 2008-06-26 13:24 | Calculated | o410e | L451 | 0 |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 200 | 6 | 19353 | 1200 | 0.06201 | 0.00031003 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10968 |  | 2008-06-26 10:05 | 2008-06-26 | 2008-06-26 13:16 | Calculated | o410e | S161 | 0 |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 191 | 10 | 19353 | 1910 | 0.09869 | 0.00051672 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10970 |  | 2008-06-26 10:27 | 2008-06-26 | 2008-06-26 13:14 | Calculated | o410e | LF | 0 |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 3 | 19353 | 501 | 0.02589 | 0.00015501 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10971 |  | 2008-06-26 13:00 | 2008-06-26 | 2008-06-26 16:15 | Calculated | o410e | LF13K4 | 0 |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 195 | 1 | 19353 | 195 | 0.01008 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10972 |  | 2008-06-26 14:13 | 2008-06-26 | 2008-06-26 14:47 | Calculated | o410e | L1645 | 0 |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 24 | 19353 | 816 | 0.04216 | 0.0012401 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10973 |  | 2008-06-26 15:21 | 2008-06-26 | 2008-06-26 16:35 | Calculated | o410e | L1725 | 0 |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 6 | 19353 | 444 | 0.02294 | 0.00031003 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10974 |  | 2008-06-26 16:35 | 2008-06-26 | 2008-06-26 21:02 | Calculated | o410e | L1645 | 0 |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 267 | 24 | 19353 | 6408 | 0.33111 | 0.0012401 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10975 |  | 2008-06-26 19:00 | 2008-06-26 | 2008-06-26 19:04 | Calculated | o410e | C1022 | 0 |  | No Asset Group | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 1872 | 19353 | 7488 | 0.38692 | 0.096729 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10977 |  | 2008-06-27 07:00 | 2008-06-27 | 2008-06-27 11:21 | Calculated | o410e | L1529 | 0 |  | Mahoenui 113-06 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 261 | 2 | 19353 | 522 | 0.02697 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10978 |  | 2008-06-27 07:40 | 2008-06-27 | 2008-06-27 15:52 | Calculated | o410e | C1610 | 0 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 492 | 5 | 19353 | 2460 | 0.12711 | 0.00025836 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10979 |  | 2008-06-27 07:56 | 2008-06-27 | 2008-06-27 12:40 | Calculated | o410e | LF2976 | 0 |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 284 | 1 | 19353 | 284 | 0.01467 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10980 |  | 2008-06-27 08:10 | 2008-06-27 | 2008-06-27 11:22 | Calculated | o410e | L355 | 0 |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 192 | 8 | 19353 | 1536 | 0.07937 | 0.00041337 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10981 |  | 2008-06-27 08:24 | 2008-06-27 | 2008-06-27 10:07 | Calculated | o410e | LF101 | 0 |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 4 | 19353 | 412 | 0.02129 | 0.00020669 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10982 |  | 2008-06-27 08:40 | 2008-06-27 | 2008-06-27 09:40 | Calculated | o410e | LF464 | 0 |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 26 | 19353 | 1560 | 0.08061 | 0.0013435 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10983 |  | 2008-06-27 08:40 | 2008-06-27 | 2008-06-27 10:37 | Calculated | o410e | LF959 | 0 |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 1 | 19353 | 117 | 0.00605 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10984 |  | 2008-06-27 08:40 | 2008-06-27 | 2008-06-27 10:06 | Calculated | o410e | L232 | 0 |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 1 | 19353 | 86 | 0.00444 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10985 |  | 2008-06-27 08:55 | 2008-06-27 | 2008-06-27 12:13 | Calculated | o410e | LF356 | 0 |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 2 | 19353 | 234 | 0.01209 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10986 |  | 2008-06-27 09:12 | 2008-06-27 | 2008-06-27 10:52 | Calculated | o410e | LF852 | 0 |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 2 | 19353 | 200 | 0.01033 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10987 |  | 2008-06-27 09:30 | 2008-06-27 | 2008-06-27 12:46 | Calculated | o410e | LF2831 | 0 |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 2 | 19353 | 392 | 0.02026 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10988 |  | 2008-06-27 09:50 | 2008-06-27 | 2008-06-27 13:09 | Calculated | o410e | LF1591 | 0 |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 1 | 19353 | 199 | 0.01028 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10989 |  | 2008-06-27 11:20 | 2008-06-27 | 2008-06-27 11:43 | Calculated | o410e | C112 | 0 |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 192 | 19353 | 4588 | 0.23707 | 0.0099209 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10990 |  | 2008-06-27 11:22 | 2008-06-27 | 2008-06-27 11:52 | Calculated | o410e | L1725 | 0 |  | Mokauiti 115-06 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 6 | 19353 | 180 | 0.0093 | 0.00031003 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10991 |  | 2008-06-27 11:25 | 2008-06-27 | 2008-06-27 12:09 | Calculated | o410e | LF1364 | 0 |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 1 | 19353 | 44 | 0.00227 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10992 |  | 2008-06-27 11:35 | 2008-06-27 | 2008-06-27 12:38 | Calculated | o410e | LF7L17 | 0 |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 2 | 19353 | 126 | 0.00651 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10993 |  | 2008-06-27 13:00 | 2008-06-27 | 2008-06-27 15:04 | Calculated | o410e | C277 | 0 |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 9 | 19353 | 1116 | 0.05767 | 0.00046504 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10994 |  | 2008-06-27 13:15 | 2008-06-27 | 2008-06-27 14:07 | Calculated | o410e | L246 | 0 |  | Rangitoto 106-05 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 17 | 19353 | 884 | 0.04568 | 0.00087842 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10995 |  | 2008-06-27 15:05 | 2008-06-27 | 2008-06-27 17:30 | Calculated | o410e | L429 | 0 |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 17 | 19353 | 2465 | 0.12737 | 0.00087842 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10996 |  | 2008-06-27 15:36 | 2008-06-27 | 2008-06-27 18:01 | Calculated | o410e | LF11H1 | 0 |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 2 | 19353 | 290 | 0.01498 | 0.00010334 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10997 |  | 2008-06-27 16:00 | 2008-06-27 | 2008-06-27 16:55 | Calculated | o410e | LF2798 | 0 |  | Caves 101-13 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 19353 | 55 | 0.00284 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10998 |  | 2008-06-27 16:15 | 2008-06-27 | 2008-06-27 17:13 | Calculated | o410e | LF7L3 | 0 |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 3 | 19353 | 174 | 0.00899 | 0.00015501 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10976 |  | 2008-06-28 00:53 | 2008-06-28 | 2008-06-28 02:54 | Calculated | o410e | C114 | 0 |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 17 | 19353 | 2057 | 0.10629 | 0.00087842 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
10999 |  | 2008-06-28 09:54 | 2008-06-28 | 2008-06-28 11:16 | Calculated | o410e | LF2976 | 0 |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 1 | 19353 | 82 | 0.00424 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
11000 |  | 2008-06-28 10:27 | 2008-06-28 | 2008-06-28 15:53 | Calculated | o410e | LF2970 | 0 |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 326 | 1 | 19353 | 326 | 0.01684 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
11001 |  | 2008-06-28 15:34 | 2008-06-28 | 2008-06-28 15:58 | Calculated | o410e | C1610 | 0 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 32 | 19353 | 768 | 0.03968 | 0.0016535 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
11002 |  | 2008-06-29 11:37 | 2008-06-29 | 2008-06-29 12:41 | Calculated | o410e | C1612 | 0 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 27 | 19353 | 1728 | 0.08929 | 0.0013951 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
11003 |  | 2008-06-29 14:03 | 2008-06-29 | 2008-06-29 16:12 | Calculated | o410e | LF7C1 | 0 |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 1 | 19353 | 129 | 0.00667 | 5.1672e-05 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
11005 |  | 2008-06-30 09:14 | 2008-06-30 | 2008-06-30 14:10 | Calculated | o410e | LF607 | 0 |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 296 | 5 | 19353 | 1480 | 0.07647 | 0.00025836 | 0 | 0 | 2008/2009 | June-2008 | 6 | 2008
11006 |  | 2008-07-01 07:07 | 2008-07-01 | 2008-07-01 13:30 | Calculated | o410e | S394 | 11 |  | Wharepapa 122-07 | Remote Rural F | Wharepapa | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 383 | 12 | 19353 | 4596 | 0.23748 | 0.00062006 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11007 |  | 2008-07-01 09:36 | 2008-07-01 | 2008-07-01 14:42 | Calculated | o410e | C5536 | 0 |  | No Asset Group | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 306 | 7 | 19353 | 2142 | 0.11068 | 0.0003617 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11008 |  | 2008-07-01 09:37 | 2008-07-01 | 2008-07-01 15:41 | Calculated | o410e | S329 | 0 |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 14 | 19353 | 5096 | 0.26332 | 0.0007234 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11009 |  | 2008-07-01 09:46 | 2008-07-01 | 2008-07-01 11:35 | Calculated | o410e | LF7D5 | 38 |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 109 | 1 | 19353 | 109 | 0.00563 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11010 |  | 2008-07-01 13:01 | 2008-07-01 | 2008-07-01 15:30 | Calculated | o410e | LF572 | 38 |  | Caves 101-04 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 149 | 2 | 19353 | 298 | 0.0154 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11011 |  | 2008-07-02 07:42 | 2008-07-02 | 2008-07-02 07:47 | Calculated | o410e | C2092 | 0 |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 110 | 19353 | 550 | 0.02842 | 0.0056839 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11012 |  | 2008-07-02 09:22 | 2008-07-02 | 2008-07-02 09:29 | Calculated | o410e | C219 | 0 |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 78 | 19353 | 546 | 0.02821 | 0.0040304 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11013 |  | 2008-07-02 09:30 | 2008-07-02 | 2008-07-02 14:34 | Calculated | o410e | LF372 | 0 |  | Maihiihi 111-11 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 304 | 1 | 19353 | 304 | 0.01571 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11014 |  | 2008-07-02 10:28 | 2008-07-02 | 2008-07-02 16:41 | Calculated | o410e | LF8D3 | 0 |  | Ohura 413-06 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 373 | 2 | 19353 | 746 | 0.03855 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11016 |  | 2008-07-02 10:54 | 2008-07-02 | 2008-07-02 13:10 | Calculated | o410e | LF639 | 0 |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 136 | 2 | 19353 | 272 | 0.01405 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11017 |  | 2008-07-02 12:50 | 2008-07-02 | 2008-07-02 14:22 | Calculated | o410e | LF2212 | 38 |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 92 | 2 | 19353 | 184 | 0.00951 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11019 |  | 2008-07-02 16:56 | 2008-07-02 | 2008-07-02 17:51 | Calculated | o410e | C277 | 0 |  | Tuhua 422-03 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 9 | 19353 | 495 | 0.02558 | 0.00046504 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11020 |  | 2008-07-02 17:47 | 2008-07-02 | 2008-07-02 20:09 | Calculated | o410e | C368 | 0 |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 7 | 19353 | 994 | 0.05136 | 0.0003617 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11021 |  | 2008-07-03 12:46 | 2008-07-03 | 2008-07-03 12:47 | Calculated | o410e | C252 | 0 |  | No Asset Group | Remote Rural F | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 745 | 19353 | 2235 | 0.11549 | 0.038495 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11022 |  | 2008-07-03 12:46 | 2008-07-03 | 2008-07-03 12:49 | Calculated | o410e | C792 | 0 |  | No Asset Group | Remote Rural F | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 |  | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 1573 | 19353 | 4719 | 0.24384 | 0.081279 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11023 |  | 2008-07-03 12:50 | 2008-07-03 | 2008-07-03 14:03 | Calculated | o410e | LF21N17 | 38 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 73 | 4 | 19353 | 292 | 0.01509 | 0.00020669 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11024 |  | 2008-07-03 13:12 | 2008-07-03 | 2008-07-03 14:27 | Calculated | o410e | L1539 | 38 |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 75 | 7 | 19353 | 525 | 0.02713 | 0.0003617 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11032 |  | 2008-07-04 04:39 | 2008-07-04 | 2008-07-04 06:56 | Calculated | o410e | C1 | 0 |  | Mokai 123-00 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 265 | 19353 | 36441 | 1.883 | 0.013693 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11025 |  | 2008-07-04 08:29 | 2008-07-04 | 2008-07-04 09:21 | Calculated | o410e | LF22O7 | 38 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 52 | 1 | 19353 | 52 | 0.00269 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11026 |  | 2008-07-04 10:11 | 2008-07-04 | 2008-07-04 10:58 | Calculated | o410e | LF106 | 38 |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 47 | 1 | 19353 | 47 | 0.00243 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11027 |  | 2008-07-04 10:18 | 2008-07-04 | 2008-07-04 12:12 | Calculated | o410e | L402 | 0 |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 114 | 15 | 19353 | 1710 | 0.08836 | 0.00077507 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11028 |  | 2008-07-04 10:37 | 2008-07-04 | 2008-07-04 12:02 | Calculated | o410e | LF2933 | 0 |  | Coast 125-05 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 85 | 1 | 19353 | 85 | 0.00439 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11029 |  | 2008-07-04 10:58 | 2008-07-04 | 2008-07-04 11:21 | Calculated | o410e | LF9K49 | 38 |  | Southern 409-02 | Remote Rural F | Southern | Manunui Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Overload |  | Overload | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 23 | 2 | 19353 | 46 | 0.00238 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11030 |  | 2008-07-04 12:30 | 2008-07-04 | 2008-07-04 14:24 | Calculated | o410e | S218 | 0 |  | Oparure 107-02 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 114 | 65 | 19353 | 7410 | 0.38289 | 0.0033587 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11031 |  | 2008-07-04 22:35 | 2008-07-04 | 2008-07-04 22:42 | Calculated | o410e | C6143 | 0 |  | No Asset Group | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 7 | 4 | 19353 | 28 | 0.00145 | 0.00020669 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11033 |  | 2008-07-05 04:00 | 2008-07-05 | 2008-07-05 12:44 | Calculated | o410e | C305 | 0 |  | Ohura 413-04 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 524 | 15 | 19353 | 7863 | 0.40629 | 0.00077507 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11035 |  | 2008-07-05 07:18 | 2008-07-05 | 2008-07-05 15:57 | Calculated | o410e | L1532 | 0 |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 519 | 5 | 19353 | 2599 | 0.13429 | 0.00025836 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11034 |  | 2008-07-05 09:00 | 2008-07-05 | 2008-07-05 10:07 | Calculated | o410e | LF8I71 | 38 |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 1 | 19353 | 67 | 0.00346 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11037 |  | 2008-07-06 02:31 | 2008-07-06 | 2008-07-06 04:08 | Calculated | o410e | C5004 | 0 |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 445 | 19353 | 43276 | 2.2361 | 0.022994 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11038 |  | 2008-07-06 05:19 | 2008-07-06 | 2008-07-06 06:21 | Calculated | o410e | C5003 | 0 |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 382 | 19353 | 23836 | 1.2316 | 0.019739 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11039 |  | 2008-07-06 05:25 | 2008-07-06 | 2008-07-06 10:41 | Calculated | o410e | C961 | 0 |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 316 | 109 | 19353 | 34547 | 1.7851 | 0.0056322 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11041 |  | 2008-07-06 12:31 | 2008-07-06 | 2008-07-06 12:58 | Calculated | o410e | LF21N8 | 38 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply | Switchgear : Main Circuit Fuses | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 27 | 2 | 19353 | 54 | 0.00279 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11042 |  | 2008-07-06 20:16 | 2008-07-06 | 2008-07-06 20:38 | Calculated | o410e | C1512 | 0 |  | Mahoenui 113-05 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 139 | 19353 | 3058 | 0.15801 | 0.0071823 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11043 |  | 2008-07-07 08:31 | 2008-07-07 | 2008-07-07 11:29 | Calculated | o410e | L1.27 | 0 |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 178 | 6 | 19353 | 1068 | 0.05519 | 0.00031003 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11044 |  | 2008-07-07 09:21 | 2008-07-07 | 2008-07-07 10:07 | Calculated | o410e | S460 | 0 |  | Mokai 123-04 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 136 | 19353 | 6256 | 0.32326 | 0.0070273 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11046 |  | 2008-07-07 12:10 | 2008-07-07 | 2008-07-07 13:57 | Calculated | o410e | L1736 | 0 |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 9 | 19353 | 963 | 0.04976 | 0.00046504 | 52.5 | 5617 | 2008/2009 | July-2008 | 7 | 2008
11047 |  | 2008-07-07 12:12 | 2008-07-07 | 2008-07-07 13:15 | Calculated | o410e | L492 | 0 |  | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 11 | 19353 | 693 | 0.03581 | 0.00056839 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11048 |  | 2008-07-07 14:50 | 2008-07-07 | 2008-07-07 16:00 | Calculated | o410e | L1523 | 0 |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 4 | 19353 | 280 | 0.01447 | 0.00020669 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11049 |  | 2008-07-08 09:05 | 2008-07-08 | 2008-07-08 13:59 | Calculated | o410e | S 1299 | 0 |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 5 | 19353 | 1470 | 0.07596 | 0.00025836 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11050 |  | 2008-07-08 09:31 | 2008-07-08 | 2008-07-08 14:45 | Calculated | o410e | L451 | 0 |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 314 | 10 | 19353 | 3148 | 0.16266 | 0.00051672 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11051 |  | 2008-07-08 09:50 | 2008-07-08 | 2008-07-08 10:59 | Calculated | o410e | LF2137 | 0 |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 5 | 19353 | 345 | 0.01783 | 0.00025836 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11052 |  | 2008-07-08 10:23 | 2008-07-08 | 2008-07-08 12:24 | Calculated | o410e | LF16 | 0 |  | Benneydale 103-03 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 1 | 19353 | 121 | 0.00625 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11053 |  | 2008-07-08 11:17 | 2008-07-08 | 2008-07-08 14:30 | Calculated | o410e | LF3023 | 0 |  | Aria 114-02 | Remote Rural F | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 193 | 1 | 19353 | 193 | 0.00997 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11054 |  | 2008-07-08 14:32 | 2008-07-08 | 2008-07-08 15:47 | Calculated | o410e | C758 | 0 |  | Ohura 413-02 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 83 | 19353 | 6225 | 0.32166 | 0.0042887 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11055 |  | 2008-07-08 15:05 | 2008-07-08 | 2008-07-08 16:00 | Calculated | o410e | LF695 | 0 |  | Rangitoto 106-03 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 19353 | 55 | 0.00284 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11056 |  | 2008-07-09 07:26 | 2008-07-09 | 2008-07-09 11:25 | Calculated | o410e | L746 | 0 |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 46 | 19353 | 11010 | 0.5689 | 0.0023769 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11057 |  | 2008-07-09 09:00 | 2008-07-09 | 2008-07-09 12:35 | Calculated | o410e | L940 | 0 |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 215 | 3 | 19353 | 645 | 0.03333 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11058 |  | 2008-07-09 10:07 | 2008-07-09 | 2008-07-09 11:09 | Calculated | o410e | LF3031 | 0 |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 1 | 19353 | 62 | 0.0032 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11061 |  | 2008-07-10 08:48 | 2008-07-10 | 2008-07-10 09:37 | Calculated | o410e | LF2J23 | 0 |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 2 | 19353 | 98 | 0.00506 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11060 |  | 2008-07-10 09:02 | 2008-07-10 | 2008-07-10 14:16 | Calculated | o410e | S1299 | 0 |  | Te Mapara 117-02 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 314 | 5 | 19353 | 1570 | 0.08112 | 0.00025836 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11062 |  | 2008-07-10 23:02 | 2008-07-10 | 2008-07-10 23:11 | Calculated | o410e | C798 | 0 |  | No Asset Group | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 512 | 19353 | 4608 | 0.2381 | 0.026456 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11063 |  | 2008-07-11 09:55 | 2008-07-11 | 2008-07-11 12:00 | Calculated | o410e | L940 | 0 |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 125 | 3 | 19353 | 375 | 0.01938 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11064 |  | 2008-07-11 11:12 | 2008-07-11 | 2008-07-11 11:50 | Calculated | o410e | L1605 | 0 |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 34 | 19353 | 1292 | 0.06676 | 0.0017568 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11065 |  | 2008-07-11 11:40 | 2008-07-11 | 2008-07-11 12:26 | Calculated | o410e | LF10K21 | 0 |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 4 | 19353 | 184 | 0.00951 | 0.00020669 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11066 |  | 2008-07-11 12:52 | 2008-07-11 | 2008-07-11 13:29 | Calculated | o410e | LF2118 | 0 |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 1 | 19353 | 37 | 0.00191 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11067 |  | 2008-07-12 01:15 | 2008-07-12 | 2008-07-12 01:24 | Calculated | o410e | C474 | 0 |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 142 | 19353 | 1278 | 0.06604 | 0.0073374 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11068 |  | 2008-07-12 08:56 | 2008-07-12 | 2008-07-12 15:05 | Calculated | o410e | S1524 | 0 |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 369 | 498 | 19353 | 188244 | 9.7269 | 0.025732 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11069 |  | 2008-07-12 10:07 | 2008-07-12 | 2008-07-12 12:54 | Calculated | o410e | C368 | 0 |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 7 | 19353 | 1171 | 0.06051 | 0.0003617 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11070 |  | 2008-07-12 15:02 | 2008-07-12 | 2008-07-12 15:47 | Calculated | o410e | S987 | 0 |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 469 | 19353 | 21550 | 1.1135 | 0.024234 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11071 |  | 2008-07-13 23:10 | 2008-07-13 | 2008-07-14 04:27 | Calculated | o410e | C1010 | 0 |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Third Party (includeds unauthorised contractors) | Fire |  | Fire (Not Electrical) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 288 | 484 | 19353 | 158752 | 8.203 | 0.025009 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11072 |  | 2008-07-14 20:33 | 2008-07-14 | 2008-07-14 21:40 | Calculated | o410e | C949 | 0 |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 1 | 19353 | 67 | 0.00346 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11073 |  | 2008-07-15 08:30 | 2008-07-15 | 2008-07-15 09:10 | Calculated | o410e | LF20L12 | 0 |  | Turoa 415-01 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 2 | 19353 | 80 | 0.00413 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11074 |  | 2008-07-15 09:00 | 2008-07-15 | 2008-07-15 15:00 | Calculated | o410e | S481 | 0 |  | Tihoi 124-02 RETIRED | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 19 | 19353 | 6840 | 0.35343 | 0.00098176 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11075 |  | 2008-07-15 09:46 | 2008-07-15 | 2008-07-15 14:51 | Calculated | o410e | L1726 | 0 |  | Benneydale 103-11 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 3 | 19353 | 915 | 0.04728 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11076 |  | 2008-07-15 09:57 | 2008-07-15 | 2008-07-15 14:52 | Calculated | o410e | LF316 | 0 |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 295 | 3 | 19353 | 885 | 0.04573 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11077 |  | 2008-07-16 08:57 | 2008-07-16 | 2008-07-16 10:26 | Calculated | o410e | LF1022 | 0 |  | Oparure 107-05 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 1 | 19353 | 89 | 0.0046 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11078 |  | 2008-07-16 09:23 | 2008-07-16 | 2008-07-16 11:22 | Calculated | o410e | LF2592 | 0 |  | Tihoi 124-02 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 2 | 19353 | 238 | 0.0123 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11079 |  | 2008-07-16 12:51 | 2008-07-16 | 2008-07-16 15:02 | Calculated | 1523 | L1523 | 0 |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 131 | 4 | 19353 | 524 | 0.02708 | 0.00020669 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11080 |  | 2008-07-16 13:15 | 2008-07-16 | 2008-07-16 14:25 | Calculated | o410e | LF30 | 0 |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 1 | 19353 | 70 | 0.00362 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11082 |  | 2008-07-17 09:02 | 2008-07-17 | 2008-07-17 15:27 | Calculated | o410e | S422 | 0 |  | Tihoi 124-02 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 385 | 19 | 19353 | 7315 | 0.37798 | 0.00098176 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11083 |  | 2008-07-17 09:30 | 2008-07-17 | 2008-07-17 12:17 | Calculated | o410e | L1501 | 0 |  | Mahoenui 113-08 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 167 | 4 | 19353 | 668 | 0.03452 | 0.00020669 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11084 |  | 2008-07-17 12:17 | 2008-07-17 | 2008-07-17 12:48 | Calculated | o410e | LF21O8 | 167 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 3 | 19353 | 93 | 0.00481 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11085 |  | 2008-07-17 12:20 | 2008-07-17 | 2008-07-17 13:35 | Calculated | o410e | LF9R28 | 0 |  | No Asset Group | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 2 | 19353 | 150 | 0.00775 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11086 |  | 2008-07-18 09:05 | 2008-07-18 | 2008-07-18 09:47 | Calculated | o410e | L228 | 38 |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 42 | 2 | 19353 | 84 | 0.00434 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11087 |  | 2008-07-18 09:44 | 2008-07-18 | 2008-07-18 14:06 | Calculated | o410e | LF 316 | 0 |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 262 | 3 | 19353 | 786 | 0.04061 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11088 |  | 2008-07-19 11:25 | 2008-07-19 | 2008-07-19 14:07 | Calculated | o410e | L1.27 | 11 |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation | OH Lines : Surge Diverters | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 6 | 19353 | 972 | 0.05022 | 0.00031003 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11089 |  | 2008-07-21 02:13 | 2008-07-21 | 2008-07-21 02:15 | Calculated | o410e | C242 | 0 |  | No Asset Group | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 243 | 19353 | 486 | 0.02511 | 0.012556 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11090 |  | 2008-07-21 07:43 | 2008-07-21 | 2008-07-21 10:30 | Calculated | o410e | LF 1863 | 38 |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 167 | 2 | 19353 | 334 | 0.01726 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11091 |  | 2008-07-21 08:16 | 2008-07-21 | 2008-07-21 12:18 | Calculated | o410e | LF 2928 | 38 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 242 | 1 | 19353 | 242 | 0.0125 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11092 |  | 2008-07-21 10:00 | 2008-07-21 | 2008-07-21 14:33 | Calculated | o410e | L451 | 0 |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 273 | 6 | 19353 | 1638 | 0.08464 | 0.00031003 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11093 |  | 2008-07-22 10:03 | 2008-07-22 | 2008-07-22 13:16 | Calculated | o410e | L451 | 0 |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 193 | 6 | 19353 | 1158 | 0.05984 | 0.00031003 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11094 |  | 2008-07-22 10:35 | 2008-07-22 | 2008-07-22 11:22 | Calculated | o410e | L1539 | 38 |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 47 | 7 | 19353 | 329 | 0.017 | 0.0003617 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11095 |  | 2008-07-22 14:04 | 2008-07-22 | 2008-07-22 14:44 | Calculated | o410e | LF475 | 0 |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 3 | 19353 | 120 | 0.0062 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11096 |  | 2008-07-22 21:57 | 2008-07-22 | 2008-07-22 23:43 | Calculated | o410e | C949 | 0 |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 1 | 19353 | 106 | 0.00548 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11099 |  | 2008-07-23 06:45 | 2008-07-23 | 2008-07-23 09:03 | Calculated | o410e | L1621 | 0 |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 6 | 19353 | 828 | 0.04278 | 0.00031003 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11100 |  | 2008-07-23 06:47 | 2008-07-23 | 2008-07-23 10:03 | Calculated | o410e | Lf2953 | 38 |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 196 | 1 | 19353 | 196 | 0.01013 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11101 |  | 2008-07-23 06:48 | 2008-07-23 | 2008-07-23 10:27 | Calculated | o410e | LF 30 | 38 |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 219 | 1 | 19353 | 219 | 0.01132 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11102 |  | 2008-07-23 07:28 | 2008-07-23 | 2008-07-23 11:07 | Calculated | o410e | LF 513 | 38 |  | Caves 101-13 | Remote Rural F | Caves | Hangatiki Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 219 | 2 | 19353 | 438 | 0.02263 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11103 |  | 2008-07-23 07:32 | 2008-07-23 | 2008-07-23 09:45 | Calculated | o410e | LF2785 | 38 |  | Waitomo 108-01 | Remote Rural F | Waitomo | Gadsby Road Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 133 | 1 | 19353 | 133 | 0.00687 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11104 |  | 2008-07-23 08:08 | 2008-07-23 | 2008-07-23 12:38 | Calculated | o410e | LF1889 | 38 |  | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 270 | 1 | 19353 | 270 | 0.01395 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11105 |  | 2008-07-23 08:10 | 2008-07-23 | 2008-07-23 13:56 | Calculated | o410e | LF1863 | 38 |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 346 | 2 | 19353 | 692 | 0.03576 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11106 |  | 2008-07-23 09:00 | 2008-07-23 | 2008-07-23 11:00 | Calculated | o410e | L940 | 0 |  | Hirangi 405-01 | Remote Rural F | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 3 | 19353 | 360 | 0.0186 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11107 |  | 2008-07-23 09:40 | 2008-07-23 | 2008-07-23 11:52 | Calculated | o410e | LF2300 | 38 |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 132 | 1 | 19353 | 132 | 0.00682 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11108 |  | 2008-07-23 10:00 | 2008-07-23 | 2008-07-23 11:24 | Calculated | o410e | S724 | 0 |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 20 | 19353 | 1680 | 0.08681 | 0.0010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11109 |  | 2008-07-23 13:10 | 2008-07-23 | 2008-07-23 14:17 | Calculated | o410e | LF 5F10 | 38 |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 67 | 11 | 19353 | 737 | 0.03808 | 0.00056839 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11110 |  | 2008-07-23 13:36 | 2008-07-23 | 2008-07-23 13:38 | Calculated | o410e | C 180 | 0 |  | No Asset Group | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 3 | 19353 | 6 | 0.00031 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11112 |  | 2008-07-23 22:58 | 2008-07-23 | 2008-07-24 00:07 | Calculated | o410e | C 375 | 0 |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 31 | 19353 | 2162 | 0.11171 | 0.0016018 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11114 |  | 2008-07-24 09:35 | 2008-07-24 | 2008-07-24 14:04 | Calculated | o410e | S539 | 0 |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 6 | 19353 | 1614 | 0.0834 | 0.00031003 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11115 |  | 2008-07-24 10:55 | 2008-07-24 | 2008-07-24 14:08 | Calculated | o410e | LF9J4 | 0 |  | Southern 409-06 | Remote Rural F | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 193 | 2 | 19353 | 386 | 0.01995 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11116 |  | 2008-07-24 15:10 | 2008-07-24 | 2008-07-24 19:00 | Calculated | o410e | LF2752 | 38 |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 230 | 1 | 19353 | 230 | 0.01188 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11117 |  | 2008-07-25 09:30 | 2008-07-25 | 2008-07-25 12:31 | Calculated | o410e | LF2549 | 0 |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 1 | 19353 | 181 | 0.00935 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11118 |  | 2008-07-25 09:31 | 2008-07-25 | 2008-07-25 10:16 | Calculated | o410e | S194 | 0 |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 85 | 19353 | 3825 | 0.19764 | 0.0043921 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11119 |  | 2008-07-25 10:07 | 2008-07-25 | 2008-07-25 10:25 | Calculated | o410e | L 330 | 0 |  | Chateau 419-01 | Remote Rural F | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 18 | 26 | 19353 | 462 | 0.02387 | 0.0013435 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11120 |  | 2008-07-25 10:29 | 2008-07-25 | 2008-07-25 15:01 | Calculated | o410e | S 711 | 0 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 31 | 19353 | 8432 | 0.43569 | 0.0016018 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11121 |  | 2008-07-25 10:50 | 2008-07-25 | 2008-07-25 13:59 | Calculated | o410e | LF 5E4 | 0 |  | Nihoniho 412-02 | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 189 | 1 | 19353 | 189 | 0.00977 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11122 |  | 2008-07-25 14:49 | 2008-07-25 | 2008-07-25 16:16 | Calculated | o410e | C475 | 0 |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 35 | 19353 | 3045 | 0.15734 | 0.0018085 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11124 |  | 2008-07-26 14:30 | 2008-07-26 | 2008-07-26 15:22 | Calculated | o410e | LF 12K5 | 0 |  | Southern 409-05 | Remote Rural F | Southern | Manunui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 1 | 19353 | 52 | 0.00269 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11125 |  | 2008-07-26 14:53 | 2008-07-26 | 2008-07-26 16:09 | Calculated | o410e | C6143 | 0 |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 76 | 4 | 19353 | 304 | 0.01571 | 0.00020669 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11126 |  | 2008-07-26 15:06 | 2008-07-26 | 2008-07-26 19:09 | Calculated | o410e | C112 | 0 |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 244 | 229 | 19353 | 55876 | 2.8872 | 0.011833 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11128 |  | 2008-07-26 17:10 | 2008-07-26 | 2008-07-26 20:49 | Calculated | o410e | C1616 | 0 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 15 | 19353 | 3290 | 0.17 | 0.00077507 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11129 |  | 2008-07-26 17:12 | 2008-07-26 | 2008-07-26 23:36 | Calculated | o410e | C 117 | 0 |  | Maihiihi 111-10 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 385 | 101 | 19353 | 38885 | 2.0093 | 0.0052188 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11130 |  | 2008-07-26 17:12 | 2008-07-26 | 2008-07-27 15:37 | Calculated | o410e | L551 | 0 |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1345 | 5 | 19353 | 6725 | 0.34749 | 0.00025836 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11131 |  | 2008-07-26 17:14 | 2008-07-26 | 2008-07-26 18:33 | Calculated | o410e | LF4015 | 0 |  | Kuratau 406-02 | Remote Rural F | Kuratau | Kuratau Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 1 | 19353 | 79 | 0.00408 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11132 |  | 2008-07-26 17:15 | 2008-07-26 | 2008-07-26 18:34 | Calculated | o410e | LF7I3 | 0 |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 17 | 19353 | 1343 | 0.06939 | 0.00087842 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11133 |  | 2008-07-26 17:34 | 2008-07-26 | 2008-07-27 08:13 | Calculated | o410e | C117 | 0 |  | Maihiihi 111-10 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 913 | 141 | 19353 | 128733 | 6.6518 | 0.0072857 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11134 |  | 2008-07-26 17:50 | 2008-07-26 | 2008-07-26 19:31 | Calculated | o410e | C118 | 0 |  | Gravel Scoop 109-02 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 91 | 19353 | 101192 | 5.2287 | 0.0047021 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11136 |  | 2008-07-26 18:44 | 2008-07-26 | 2008-07-26 22:26 | Calculated | o410e | C112 | 0 |  | Rangitoto 106-04 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 222 | 216 | 19353 | 47952 | 2.4778 | 0.011161 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11137 |  | 2008-07-26 18:55 | 2008-07-26 | 2008-07-27 04:36 | Calculated | o410e | C334 | 0 |  | Gravel Scoop 109-11 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 582 | 107 | 19353 | 62274 | 3.2178 | 0.0055289 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11138 |  | 2008-07-26 18:58 | 2008-07-26 | 2008-07-26 19:41 | Calculated | o410e | C121 | 0 |  |  | Remote Rural F | Te Waireka Rd 33 | Direct from Hangatiki Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 43 | 2166 | 19353 | 93138 | 4.8126 | 0.11192 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11139 |  | 2008-07-26 19:24 | 2008-07-26 | 2008-07-26 19:50 | Calculated | o410e | L909 | 0 |  |  | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 127 | 19353 | 3302 | 0.17062 | 0.0065623 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11140 |  | 2008-07-26 19:52 | 2008-07-26 | 2008-07-26 21:54 | Calculated | o410e | C5004 | 0 |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 445 | 19353 | 54735 | 2.8282 | 0.022994 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11141 |  | 2008-07-26 20:39 | 2008-07-26 | 2008-07-26 21:38 | Calculated | o410e | S669 | 0 |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 279 | 19353 | 16740 | 0.86498 | 0.014416 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11142 |  | 2008-07-26 20:41 | 2008-07-26 | 2008-07-27 07:23 | Calculated | o410e | C385 | 0 |  | Manunui 408-02 | Remote Rural F | Manunui | Manunui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 642 | 117 | 19353 | 75114 | 3.8813 | 0.0060456 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11143 |  | 2008-07-26 20:47 | 2008-07-26 | 2008-07-26 23:09 | Calculated | o410e | C820 | 0 |  | Ongarue 421-01 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 377 | 19353 | 53534 | 2.7662 | 0.01948 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11144 |  | 2008-07-26 21:50 | 2008-07-26 | 2008-07-26 23:20 | Calculated | o410e | C2092 | 0 |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 110 | 19353 | 9900 | 0.51155 | 0.0056839 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11145 |  | 2008-07-26 22:10 | 2008-07-26 | 2008-07-26 22:51 | Calculated | o410e | LF717 | 0 |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 2 | 19353 | 82 | 0.00424 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11146 |  | 2008-07-27 00:05 | 2008-07-27 | 2008-07-27 00:45 | Calculated | o410e | LF81 | 0 |  | Caves 101-01 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 6 | 19353 | 240 | 0.0124 | 0.00031003 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11147 |  | 2008-07-27 00:17 | 2008-07-27 | 2008-07-27 16:36 | Calculated | o410e | C180 | 0 |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 979 | 3 | 19353 | 2937 | 0.15176 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11148 |  | 2008-07-27 01:10 | 2008-07-27 | 2008-07-27 13:26 | Calculated | o410e | LF3065 | 0 |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 736 | 1 | 19353 | 736 | 0.03803 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11149 |  | 2008-07-27 03:08 | 2008-07-27 | 2008-07-27 04:18 | Calculated | o410e | C2092 | 0 |  | Pureora 119-01 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 66 | 19353 | 4620 | 0.23872 | 0.0034103 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11150 |  | 2008-07-27 03:08 | 2008-07-27 | 2008-07-27 06:35 | Calculated | o410e | C714 | 0 |  | Benneydale 103-09 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 207 | 50 | 19353 | 10350 | 0.5348 | 0.0025836 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11151 |  | 2008-07-27 03:08 | 2008-07-27 | 2008-07-27 11:57 | Calculated | o410e | S417 | 0 |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 529 | 43 | 19353 | 22747 | 1.1754 | 0.0022219 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11152 |  | 2008-07-28 08:05 | 2008-07-28 | 2008-07-28 10:23 | Calculated | o410e | L170 | 0 |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 18 | 19353 | 2484 | 0.12835 | 0.00093009 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11153 |  | 2008-07-28 08:20 | 2008-07-28 | 2008-07-28 16:19 | Calculated | o410e | C642 | 0 |  | McDonalds 110-05 | Remote Rural F | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 479 | 65 | 19353 | 31125 | 1.6083 | 0.0033587 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11154 |  | 2008-07-28 09:03 | 2008-07-28 | 2008-07-28 15:48 | Calculated | o410e | LF247 | 0 |  | Gravel Scoop 109-14 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 405 | 2 | 19353 | 810 | 0.04185 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11155 |  | 2008-07-28 10:00 | 2008-07-28 | 2008-07-28 11:46 | Calculated | o410e | S709 | 0 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 13 | 19353 | 1378 | 0.0712 | 0.00067173 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11157 |  | 2008-07-28 10:04 | 2008-07-28 | 2008-07-28 12:18 | Calculated | o410e | Lf6J10 | 0 |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 3 | 19353 | 402 | 0.02077 | 0.00015501 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11159 |  | 2008-07-28 10:36 | 2008-07-28 | 2008-07-28 13:46 | Calculated | o410e | LF32 | 0 |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 1 | 19353 | 190 | 0.00982 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11160 |  | 2008-07-28 11:40 | 2008-07-28 | 2008-07-28 12:33 | Calculated | o410e | LF1288 | 0 |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 2 | 19353 | 106 | 0.00548 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11161 |  | 2008-07-28 12:04 | 2008-07-28 | 2008-07-28 13:31 | Calculated | o410e | S636 | 0 |  | Benneydale 103-06 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 41 | 19353 | 3567 | 0.18431 | 0.0021185 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11162 |  | 2008-07-28 13:15 | 2008-07-28 | 2008-07-28 13:57 | Calculated | o410e | L302 | 0 |  | Gravel Scoop 109-03 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 6 | 19353 | 252 | 0.01302 | 0.00031003 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11163 |  | 2008-07-28 14:20 | 2008-07-28 | 2008-07-28 15:01 | Calculated | o410e | LF357 | 0 |  | Maihiihi 111-14 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 1 | 19353 | 41 | 0.00212 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11164 |  | 2008-07-28 15:25 | 2008-07-28 | 2008-07-28 16:01 | Calculated | o410e | LF1085 | 0 |  | Te Kuiti South 104-02 | Remote Rural F | Te Kuiti South | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 2 | 19353 | 72 | 0.00372 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11165 |  | 2008-07-28 16:22 | 2008-07-28 | 2008-07-28 16:44 | Calculated | o410e | LF2419 | 0 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 1 | 19353 | 22 | 0.00114 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11166 |  | 2008-07-28 17:15 | 2008-07-28 | 2008-07-28 18:21 | Calculated | o410e | L327 | 0 |  | Hangatiki East 102-03 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 2 | 19353 | 132 | 0.00682 | 0.00010334 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11167 |  | 2008-07-28 19:25 | 2008-07-28 | 2008-07-28 20:45 | Calculated | o410e | L721 | 0 |  | Tihoi 124-03 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 1 | 19353 | 80 | 0.00413 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11168 |  | 2008-07-29 06:28 | 2008-07-29 | 2008-07-29 07:50 | Calculated | o410e | LF11S18 | 0 |  | Rangipo / Hautu 424-01 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 11 | 19353 | 902 | 0.04661 | 0.00056839 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11169 |  | 2008-07-29 09:30 | 2008-07-29 | 2008-07-29 10:54 | Calculated | o410e | L674 | 0 |  | Otorohanga 112-03 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 22 | 19353 | 1848 | 0.09549 | 0.0011368 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11170 |  | 2008-07-29 10:05 | 2008-07-29 | 2008-07-29 13:36 | Calculated | o410e | LF2518 | 0 |  | Mahoenui 113-03 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 211 | 1 | 19353 | 211 | 0.0109 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11171 |  | 2008-07-29 10:12 | 2008-07-29 | 2008-07-29 13:13 | Calculated | o410e | LF664 | 0 |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 1 | 19353 | 181 | 0.00935 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11174 |  | 2008-07-29 11:09 | 2008-07-29 | 2008-07-29 12:12 | Calculated | o410e | S399 | 0 |  | Maihiihi 111-13 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 39 | 19353 | 3237 | 0.16726 | 0.0020152 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11175 |  | 2008-07-29 12:25 | 2008-07-29 | 2008-07-29 13:20 | Calculated | o410e | LF21N11 | 0 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 19353 | 55 | 0.00284 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11176 |  | 2008-07-29 16:39 | 2008-07-29 | 2008-07-29 17:00 | Calculated | o410e | LF5F1 | 0 |  | Tuhua 422-01 | Remote Rural F | Tuhua | Tuhua Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 7 | 19353 | 21 | 0.00109 | 0.0003617 | 1 | 21 | 2008/2009 | July-2008 | 7 | 2008
11177 |  | 2008-07-29 20:32 | 2008-07-29 | 2008-07-29 21:45 | Calculated | o410e | LF12N8 | 0 |  | Otukou 418-01 | Remote Rural F | Otukou | Otukou Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 1 | 19353 | 73 | 0.00377 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11180 |  | 2008-07-30 04:00 | 2008-07-30 | 2008-07-30 19:16 | Calculated | o410e | LF15L4 | 0 |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 916 | 1 | 19353 | 916 | 0.04733 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11178 |  | 2008-07-30 06:37 | 2008-07-30 | 2008-07-30 07:00 | Calculated | o410e | C5004 | 0 |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 445 | 19353 | 10235 | 0.52886 | 0.022994 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11181 |  | 2008-07-30 06:37 | 2008-07-30 | 2008-07-30 15:44 | Calculated | o410e | S677 | 0 |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 547 | 34 | 19353 | 18598 | 0.96099 | 0.0017568 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11182 |  | 2008-07-30 06:45 | 2008-07-30 | 2008-07-30 11:58 | Calculated | o410e | 11 | 0 |  | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 313 | 12 | 19353 | 3756 | 0.19408 | 0.00062006 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11183 |  | 2008-07-30 06:55 | 2008-07-30 | 2008-07-30 09:20 | Calculated | o410e | C370 | 0 |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 145 | 19353 | 7685 | 0.3971 | 0.0074924 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11184 |  | 2008-07-30 07:03 | 2008-07-30 | 2008-07-30 10:59 | Calculated | o410e | LF2142 | 0 |  | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 236 | 19353 | 236 | 0.01219 | 0.012194 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11185 |  | 2008-07-30 07:20 | 2008-07-30 | 2008-07-30 08:31 | Calculated | o410e | L333 | 0 |  | Gravel Scoop 109-04 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 71 | 19353 | 1704 | 0.08805 | 0.0036687 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11179 |  | 2008-07-30 07:33 | 2008-07-30 | 2008-07-30 08:50 | Calculated | o410e | L1.27 | 0 |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 6 | 19353 | 462 | 0.02387 | 0.00031003 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11186 |  | 2008-07-30 07:50 | 2008-07-30 | 2008-07-30 11:01 | Calculated | o410e | C446 | 0 |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 191 | 19353 | 4011 | 0.20725 | 0.0098693 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11187 |  | 2008-07-30 08:00 | 2008-07-30 | 2008-07-30 11:11 | Calculated | o410e | LF9K16 | 0 |  | Southern 409-03 | Remote Rural F | Southern | Manunui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 191 | 19353 | 573 | 0.02961 | 0.0098693 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11188 |  | 2008-07-30 08:14 | 2008-07-30 | 2008-07-30 11:15 | Calculated | o410e | C529 | 0 |  | Waihaha 426-03 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 181 | 19353 | 7602 | 0.39281 | 0.0093526 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11189 |  | 2008-07-30 08:17 | 2008-07-30 | 2008-07-30 10:57 | Calculated | o410e | L170 | 0 |  | Gravel Scoop 109-07 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 160 | 19353 | 2880 | 0.14881 | 0.0082675 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11190 |  | 2008-07-30 08:55 | 2008-07-30 | 2008-07-30 10:41 | Calculated | o410e | L245 | 0 |  | Oruatua 417-01 | Remote Rural F | Oruatua | Kiko Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 106 | 19353 | 10282 | 0.53129 | 0.0054772 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11191 |  | 2008-07-30 08:55 | 2008-07-30 | 2008-07-30 09:24 | Calculated | o410e | LF573 | 0 |  | Hangatiki East 102-01 | Remote Rural F | Hangatiki East | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 29 | 19353 | 87 | 0.0045 | 0.0014985 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11192 |  | 2008-07-30 09:04 | 2008-07-30 | 2008-07-30 10:02 | Calculated | o410e | C961 | 0 |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 58 | 19353 | 6322 | 0.32667 | 0.002997 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11193 |  | 2008-07-30 09:26 | 2008-07-30 | 2008-07-30 15:10 | Calculated | o410e | LF2057 | 0 |  | Mokauiti 115-05 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 344 | 19353 | 688 | 0.03555 | 0.017775 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11194 |  | 2008-07-30 09:35 | 2008-07-30 | 2008-07-30 10:00 | Calculated | o410e | S422 | 0 |  | Tihoi 124-02 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 25 | 19353 | 475 | 0.02454 | 0.0012918 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11195 |  | 2008-07-30 10:01 | 2008-07-30 | 2008-07-30 10:02 | Calculated | o410e | C6143 | 0 |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 4 | 1 | 19353 | 4 | 0.00021 | 5.1672e-05 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11197 |  | 2008-07-30 10:04 | 2008-07-30 | 2008-07-30 13:05 | Calculated | o410e | C547 | 11 |  | Western 403-02 | Remote Rural F | Western | Borough Zone Substation | OH Lines : Surge Diverters | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 181 | 19353 | 26542 | 1.3715 | 0.0093526 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11196 |  | 2008-07-30 10:13 | 2008-07-30 | 2008-07-30 15:52 | Calculated | o410e | L162 | 0 |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 339 | 19353 | 1356 | 0.07007 | 0.017517 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11201 |  | 2008-07-30 10:40 | 2008-07-30 | 2008-07-30 17:29 | Calculated | o410e | L703 | 0 |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 409 | 19353 | 21268 | 1.099 | 0.021134 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11198 |  | 2008-07-30 11:39 | 2008-07-30 | 2008-07-30 11:57 | Calculated | o410e | LF587 | 0 |  | Maihiihi 111-12 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 18 | 19353 | 54 | 0.00279 | 0.00093009 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11199 |  | 2008-07-30 11:40 | 2008-07-30 | 2008-07-30 13:38 | Calculated | o410e | L1713 | 0 |  | Mokauiti 115-03 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 118 | 19353 | 708 | 0.03658 | 0.0060972 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11200 |  | 2008-07-30 12:06 | 2008-07-30 | 2008-07-30 12:43 | Calculated | o410e | LF1139 | 0 |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 37 | 19353 | 74 | 0.00382 | 0.0019118 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11203 |  | 2008-07-30 16:42 | 2008-07-30 | 2008-07-30 16:50 | Calculated | o410e | C6174 | 0 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 8 | 19353 | 240 | 0.0124 | 0.00041337 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11204 |  | 2008-07-30 17:06 | 2008-07-30 | 2008-07-30 17:28 | Calculated | o410e | C127 | 0 |  | Maihiihi 111-03 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 352 | 22 | 19353 | 7744 | 0.40014 | 0.0011368 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11207 |  | 2008-07-30 17:20 | 2008-07-30 | 2008-07-30 21:47 | Calculated | o410e | L730 | 0 |  | Tangiwai 416-01 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 267 | 19353 | 2136 | 0.11037 | 0.013796 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11205 |  | 2008-07-30 17:26 | 2008-07-30 | 2008-07-30 18:13 | Calculated | o410e | LF22M7 | 0 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 47 | 19353 | 94 | 0.00486 | 0.0024286 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11208 |  | 2008-07-30 17:40 | 2008-07-30 | 2008-07-30 22:03 | Calculated | o410e | LF481 | 0 |  | Maihiihi 111-13 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 263 | 19353 | 263 | 0.01359 | 0.01359 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11206 |  | 2008-07-30 20:30 | 2008-07-30 | 2008-07-30 21:38 | Calculated | o410e | LF10K11 | 0 |  | Southern 409-07 | Remote Rural F | Southern | Manunui Zone Substation |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 68 | 19353 | 68 | 0.00351 | 0.0035137 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11209 |  | 2008-07-31 00:19 | 2008-07-31 | 2008-07-31 03:51 | Calculated | o410e | C52 | 0 |  |  | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 498 | 213 | 19353 | 106074 | 5.481 | 0.011006 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11210 |  | 2008-07-31 03:15 | 2008-07-31 | 2008-07-31 10:52 | Calculated | o410e | C1620 | 0 |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 457 | 19353 | 80432 | 4.156 | 0.023614 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11211 |  | 2008-07-31 07:00 | 2008-07-31 | 2008-07-31 09:44 | Calculated | o410e | L355 | 0 |  | Otorohanga 112-04 | Remote Rural F | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 164 | 19353 | 1312 | 0.06779 | 0.0084741 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11212 |  | 2008-07-31 07:26 | 2008-07-31 | 2008-07-31 09:43 | Calculated | o410e | L1297 | 0 |  | Te Mapara 117-03 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 137 | 19353 | 6439 | 0.33271 | 0.007079 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11213 |  | 2008-07-31 07:30 | 2008-07-31 | 2008-07-31 10:48 | Calculated | o410e | L292 | 0 |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 198 | 19353 | 1188 | 0.06139 | 0.010231 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11214 |  | 2008-07-31 07:51 | 2008-07-31 | 2008-07-31 09:23 | Calculated | o410e | LF2512 | 0 |  | Caves 101-11 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 92 | 19353 | 92 | 0.00475 | 0.0047538 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11215 |  | 2008-07-31 07:51 | 2008-07-31 | 2008-07-31 11:04 | Calculated | o410e | T3J5 | 0 |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 193 | 19353 | 193 | 0.00997 | 0.0099726 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11216 |  | 2008-07-31 07:54 | 2008-07-31 | 2008-07-31 10:27 | Calculated | o410e | LF13K12 | 0 |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 153 | 19353 | 153 | 0.00791 | 0.0079058 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11217 |  | 2008-07-31 08:10 | 2008-07-31 | 2008-07-31 13:27 | Calculated | o410e | C1721 | 0 |  | Te Mapara 117-04 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 307 | 9 | 19353 | 2853 | 0.14742 | 0.00046504 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11218 |  | 2008-07-31 09:37 | 2008-07-31 | 2008-07-31 14:54 | Calculated | o410e | L1539 | 0 |  | Mahoenui 113-02 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 317 | 19353 | 2219 | 0.11466 | 0.01638 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11219 |  | 2008-07-31 10:20 | 2008-07-31 | 2008-07-31 12:29 | Calculated | o410e | L1.27 | 0 |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 129 | 19353 | 774 | 0.03999 | 0.0066656 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11220 |  | 2008-07-31 10:42 | 2008-07-31 | 2008-07-31 13:50 | Calculated | o410e | C669 | 0 |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 279 | 188 | 19353 | 52452 | 2.7103 | 0.0097143 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11221 |  | 2008-07-31 10:45 | 2008-07-31 | 2008-07-31 11:27 | Calculated | o410e | LF1048 | 0 |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 42 | 19353 | 84 | 0.00434 | 0.0021702 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11222 |  | 2008-07-31 11:20 | 2008-07-31 | 2008-07-31 11:43 | Calculated | o410e | TF228 | 0 |  | Maihiihi 111-02 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 23 | 19353 | 184 | 0.00951 | 0.0011884 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11223 |  | 2008-07-31 12:55 | 2008-07-31 | 2008-08-01 09:35 | Calculated | o410e | C1610 | 0 |  | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 1241 | 19353 | 23674 | 1.2233 | 0.064124 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11225 |  | 2008-07-31 13:29 | 2008-07-31 | 2008-07-31 14:10 | Calculated | o410e | L1719 | 0 |  | Mokauiti 115-05 | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 41 | 19353 | 246 | 0.01271 | 0.0021185 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11226 |  | 2008-07-31 15:25 | 2008-07-31 | 2008-07-31 15:51 | Calculated | o410e | C52 | 0 |  |  | Remote Rural F | Whakamaru 33 | Direct from Whakamaru Supply |  | Asset Related | Other |  | Condensation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 498 | 27 | 19353 | 13446 | 0.69478 | 0.0013951 | 0 | 0 | 2008/2009 | July-2008 | 7 | 2008
11228 |  | 2008-08-01 11:19 | 2008-08-01 | 2008-08-01 12:03 | Calculated | o410e | S247 | 0 |  | Rangitoto 106-06 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Birds & Animals | Animals |  | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 44 | 20359 | 1144 | 0.05619 | 0.0021612 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11229 |  | 2008-08-01 23:38 | 2008-08-01 | 2008-08-02 00:34 | Calculated | o410e | LF406 | 0 |  | Waitomo 108-03 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 56 | 20359 | 1176 | 0.05776 | 0.0027506 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11230 |  | 2008-08-02 08:19 | 2008-08-02 | 2008-08-02 11:00 | Calculated | o410e | L292 | 0 |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 161 | 20359 | 966 | 0.04745 | 0.0079081 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11231 |  | 2008-08-02 11:04 | 2008-08-02 | 2008-08-02 12:44 | Calculated | o410e | L467 | 0 |  | Mokai 123-03 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 100 | 20359 | 800 | 0.03929 | 0.0049118 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11232 |  | 2008-08-02 12:11 | 2008-08-02 | 2008-08-02 12:30 | Calculated | o410e | Rec474 | 0 |  | Mokai 123-01 | Remote Rural F | Mokai | Marotiri Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 19 | 20359 | 589 | 0.02893 | 0.00093325 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11233 |  | 2008-08-02 13:32 | 2008-08-02 | 2008-08-02 14:23 | Calculated | o410e | OCB121 | 0 |  |  | Remote Rural F | Te Waireka Rd 33 | Direct from Hangatiki Supply |  | Asset Related | Other |  | Condensation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2398 | 52 | 20359 | 124696 | 6.1249 | 0.0025542 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11234 |  | 2008-08-02 14:27 | 2008-08-02 | 2008-08-02 15:41 | Calculated | o410e | Rec 466 | 0 |  | Ongarue 421-03 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 74 | 20359 | 4366 | 0.21445 | 0.0036348 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11235 |  | 2008-08-02 19:52 | 2008-08-02 | 2008-08-02 20:47 | Calculated | o410e | OCB 1072 | 38 |  | Huirimu 121-01 | Remote Rural F | Huirimu | Arohena Zone Substation | Switchgear : Main Circuit Fuses | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 127 | 56 | 20359 | 7112 | 0.34933 | 0.0027506 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11236 |  | 2008-08-03 05:03 | 2008-08-03 | 2008-08-03 05:06 | Calculated | o410e | OCB242 | 0 |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 243 | 3 | 20359 | 729 | 0.03581 | 0.00014735 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11237 |  | 2008-08-03 08:31 | 2008-08-03 | 2008-08-03 09:27 | Calculated | o410e | T515 | 0 |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 56 | 20359 | 56 | 0.00275 | 0.0027506 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11238 |  | 2008-08-03 11:14 | 2008-08-03 | 2008-08-03 16:25 | Calculated | o410e | L 1.27 | 0 |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 311 | 20359 | 1866 | 0.09165 | 0.015276 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11239 |  | 2008-08-03 11:56 | 2008-08-03 | 2008-08-03 11:59 | Calculated | o410e | OCB 6143 | 38 |  |  | Remote Rural F | Taumarunui / Kuratau 33 | Borough Zone Substation | Switchgear : Main Circuit Fuses | Weather | Wind |  | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 4 | 3 | 20359 | 12 | 0.00059 | 0.00014735 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11240 |  | 2008-08-03 14:10 | 2008-08-03 | 2008-08-03 15:31 | Calculated | o410e | ABS 748 | 0 |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 81 | 20359 | 729 | 0.03581 | 0.0039786 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11241 |  | 2008-08-03 14:32 | 2008-08-03 | 2008-08-03 17:08 | Calculated | o410e | T7I24 | 0 |  | Northern 402-02 | Remote Rural F | Northern | Borough Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 156 | 20359 | 156 | 0.00766 | 0.0076625 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11242 |  | 2008-08-04 05:03 | 2008-08-04 | 2008-08-04 05:13 | Calculated | o410e | OCB 796 | 38 |  |  | Remote Rural F | Taharoa A 33 | Direct from Hangatiki Supply | Switchgear : Main Circuit Fuses | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Underground | 33kV | 33000 |  | 1 | 10 | 20359 | 10 | 0.00049 | 0.00049118 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11243 |  | 2008-08-04 13:36 | 2008-08-04 | 2008-08-04 14:35 | Calculated | o410e | T 05I07 | 0 |  | Northern 402-05 | Remote Rural F | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 59 | 20359 | 177 | 0.00869 | 0.002898 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11244 |  | 2008-08-04 15:23 | 2008-08-04 | 2008-08-04 16:18 | Calculated | o410e | T 08I13 | 0 |  | Western 403-03 | Remote Rural F | Western | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 55 | 20359 | 165 | 0.0081 | 0.0027015 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11245 |  | 2008-08-05 08:04 | 2008-08-05 | 2008-08-05 10:11 | Calculated | o410e | T 2549 | 0 |  | Coast 125-02 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 127 | 20359 | 127 | 0.00624 | 0.006238 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11246 |  | 2008-08-05 10:36 | 2008-08-05 | 2008-08-05 12:57 | Calculated | o410e | T 1027 | 0 |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 141 | 20359 | 141 | 0.00693 | 0.0069257 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11247 |  | 2008-08-05 16:37 | 2008-08-05 | 2008-08-05 18:50 | Calculated | o410e | T 08I34 | 0 |  | Northern 402-01 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 133 | 20359 | 4123 | 0.20251 | 0.0065327 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11256 |  | 2008-08-06 11:39 | 2008-08-06 | 2008-08-06 13:57 | Calculated | o410e | T807 | 0 |  | Pureora 119-02 | Remote Rural F | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 3 | 138 | 20359 | 414 | 0.02033 | 0.0067783 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11257 |  | 2008-08-06 15:09 | 2008-08-06 | 2008-08-06 15:32 | Calculated | o410e | T2380 | 0 |  | Huirimu 121-02 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 23 | 20359 | 23 | 0.00113 | 0.0011297 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11258 |  | 2008-08-07 07:56 | 2008-08-07 | 2008-08-07 09:40 | Calculated | o410e | T4160 | 0 |  |  | Remote Rural F | Lake Taupo 33 | Direct from Tokaanu Supply |  | Birds & Animals | FODU1 |  | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 104 | 20359 | 104 | 0.00511 | 0.0051083 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11260 |  | 2008-08-08 10:30 | 2008-08-08 | 2008-08-08 10:54 | Calculated | o410e | T4127 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 24 | 20359 | 24 | 0.00118 | 0.0011788 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11261 |  | 2008-08-08 11:30 | 2008-08-08 | 2008-08-08 12:08 | Calculated | o410e | T1504 | 38 |  | McDonalds 110-03 | Remote Rural F | McDonalds | Te Waireka Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 2 | 38 | 20359 | 76 | 0.00373 | 0.0018665 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11262 |  | 2008-08-08 12:38 | 2008-08-08 | 2008-08-08 13:54 | Calculated | o410e | ABS 544 | 0 |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 76 | 20359 | 1520 | 0.07466 | 0.003733 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11263 |  | 2008-08-08 13:50 | 2008-08-08 | 2008-08-08 15:19 | Calculated | o410e | T1674 | 0 |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 89 | 20359 | 89 | 0.00437 | 0.0043715 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11264 |  | 2008-08-11 06:55 | 2008-08-11 | 2008-08-11 10:03 | Calculated | o410e | T1511 | 0 |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 188 | 20359 | 376 | 0.01847 | 0.0092342 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11265 |  | 2008-08-11 09:24 | 2008-08-11 | 2008-08-11 13:08 | Calculated | o410e | ABS709 | 0 |  | Tangiwai 416-04 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 13 | 224 | 20359 | 2912 | 0.14303 | 0.011003 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11266 |  | 2008-08-11 09:30 | 2008-08-11 | 2008-08-11 15:56 | Calculated | o410e | L634 | 0 |  | Tihoi 124-04 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 386 | 20359 | 1544 | 0.07584 | 0.01896 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11267 |  | 2008-08-11 16:37 | 2008-08-11 | 2008-08-11 17:19 | Calculated | o410e | VCB 6147 | 0 |  | Turoa 415-03 | Remote Rural F | Turoa | Direct from Ohakune Supply |  | Asset Related | Conductor - Overhead |  | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 42 | 20359 | 84 | 0.00413 | 0.002063 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11268 |  | 2008-08-12 09:50 | 2008-08-12 | 2008-08-12 12:39 | Calculated | o410e | L509 | 0 |  | Rural 126-02 | Remote Rural F | Rural | Taharoa Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 169 | 20359 | 1183 | 0.05811 | 0.008301 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11269 |  | 2008-08-12 12:22 | 2008-08-12 | 2008-08-12 13:54 | Calculated | o410e | ABS544 | 0 |  |  | Remote Rural F | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 2 | 92 | 20359 | 184 | 0.00904 | 0.0045189 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11270 |  | 2008-08-13 05:21 | 2008-08-13 | 2008-08-13 08:44 | Calculated | o410e | Sect 407 | 0 |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 203 | 20359 | 6090 | 0.29913 | 0.009971 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11272 |  | 2008-08-13 11:35 | 2008-08-13 | 2008-08-13 12:54 | Calculated | o410e | T5 | 0 |  | Rangitoto 106-01 | Remote Rural F | Rangitoto | Waitete Zone Substation |  | Birds & Animals | Animals |  | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 79 | 20359 | 395 | 0.0194 | 0.0038803 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11273 |  | 2008-08-13 12:38 | 2008-08-13 | 2008-08-13 16:12 | Calculated | o410e | T876 | 0 |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 214 | 20359 | 214 | 0.01051 | 0.010511 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11274 |  | 2008-08-14 07:02 | 2008-08-14 | 2008-08-14 13:43 | Calculated | o410e | T357 | 0 |  | Maihiihi 111-14 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 401 | 20359 | 401 | 0.0197 | 0.019696 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11275 |  | 2008-08-14 08:01 | 2008-08-14 | 2008-08-14 13:50 | Calculated | o410e | T1674 | 0 |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 349 | 20359 | 349 | 0.01714 | 0.017142 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11276 |  | 2008-08-14 08:03 | 2008-08-14 | 2008-08-14 08:06 | Calculated | o410e | REC 164 | 0 |  | Northern 402-03 | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related | Other |  | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 3 | 20359 | 447 | 0.02196 | 0.00014735 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11277 |  | 2008-08-14 08:15 | 2008-08-14 | 2008-08-14 16:02 | Calculated | o410e | L942 | 0 |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 467 | 20359 | 467 | 0.02294 | 0.022938 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11279 |  | 2008-08-14 09:40 | 2008-08-14 | 2008-08-14 10:53 | Calculated | o410e | T6K4 | 0 |  | Northern 402-04 | Remote Rural F | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 73 | 20359 | 73 | 0.00359 | 0.0035856 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11280 |  | 2008-08-14 09:50 | 2008-08-14 | 2008-08-14 11:13 | Calculated | o410e | T1748 | 0 |  | Te Mapara 117-05 | Remote Rural F | Te Mapara | Wairere Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 83 | 20359 | 166 | 0.00815 | 0.0040768 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11281 |  | 2008-08-14 10:28 | 2008-08-14 | 2008-08-14 14:01 | Calculated | o410e | ABS 408 | 0 |  | Waihaha 426-02 | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 213 | 20359 | 21939 | 1.0776 | 0.010462 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11282 |  | 2008-08-14 14:31 | 2008-08-14 | 2008-08-14 15:50 | Calculated | o410e | ABS 380 | 0 |  | Wharepapa 122-05 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 79 | 20359 | 4661 | 0.22894 | 0.0038803 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11283 |  | 2008-08-14 22:16 | 2008-08-14 | 2008-08-15 00:52 | Calculated | o410e | T124 | 0 |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 156 | 20359 | 312 | 0.01532 | 0.0076625 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11285 |  | 2008-08-15 05:31 | 2008-08-15 | 2008-08-15 14:30 | Calculated | o410e | T124 | 0 |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 539 | 20359 | 1617 | 0.07942 | 0.026475 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11286 |  | 2008-08-15 06:30 | 2008-08-15 | 2008-08-15 08:27 | Calculated | o410e | REC 1627 | 0 |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 117 | 20359 | 702 | 0.03448 | 0.0057468 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11287 |  | 2008-08-15 06:51 | 2008-08-15 | 2008-08-15 15:29 | Calculated | o410e | L942 | 0 |  | Rangipo / Hautu 424-02 | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 518 | 20359 | 518 | 0.02544 | 0.025443 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11288 |  | 2008-08-15 06:56 | 2008-08-15 | 2008-08-15 11:25 | Calculated | o410e | T285 | 0 |  | Maihiihi 111-13 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 269 | 20359 | 538 | 0.02643 | 0.013213 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11289 |  | 2008-08-15 07:11 | 2008-08-15 | 2008-08-15 11:51 | Calculated | o410e | T576 | 0 |  | Oparure 107-08 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 280 | 20359 | 560 | 0.02751 | 0.013753 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11290 |  | 2008-08-15 07:30 | 2008-08-15 | 2008-08-15 10:58 | Calculated | o410e | T655 | 0 |  | Coast 125-01 | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 208 | 20359 | 416 | 0.02043 | 0.010217 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11291 |  | 2008-08-15 08:10 | 2008-08-15 | 2008-08-15 09:07 | Calculated | o410e | T8F2 | 0 |  | Ohura 413-05 | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 57 | 20359 | 57 | 0.0028 | 0.0027997 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11292 |  | 2008-08-15 08:42 | 2008-08-15 | 2008-08-15 10:52 | Calculated | o410e | L 1.27 | 0 |  | Matapuna 404-01 | Remote Rural F | Matapuna | Borough Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 130 | 20359 | 780 | 0.03831 | 0.0063854 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11293 |  | 2008-08-15 09:00 | 2008-08-15 | 2008-08-15 10:48 | Calculated | o410e | T1863 | 0 |  | Mahoenui 113-04 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 108 | 20359 | 216 | 0.01061 | 0.0053048 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11294 |  | 2008-08-15 09:02 | 2008-08-15 | 2008-08-15 14:30 | Calculated | o410e | ABS 481 | 0 |  | Tihoi 124-01 | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 18 | 328 | 20359 | 5904 | 0.28999 | 0.016111 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11296 |  | 2008-08-15 10:30 | 2008-08-15 | 2008-08-15 12:41 | Calculated | o410e | REC 1627 | 0 |  | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 132 | 20359 | 792 | 0.0389 | 0.0064836 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11297 |  | 2008-08-15 10:40 | 2008-08-15 | 2008-08-15 15:53 | Calculated | o410e | OCB 262 | 0 |  |  | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 313 | 20359 | 8451 | 0.4151 | 0.015374 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11284 |  | 2008-08-15 21:45 | 2008-08-15 | 2008-08-16 10:53 | Calculated | o410e | T321 | 0 |  | Oparure 107-07 | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 788 | 20359 | 788 | 0.03871 | 0.038705 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11300 |  | 2008-08-16 06:50 | 2008-08-16 | 2008-08-16 18:49 | Calculated | o410e | SEC 314 | 0 |  | Western 403-07 | Remote Rural F | Western | Borough Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 719 | 20359 | 7909 | 0.38848 | 0.035316 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11299 |  | 2008-08-16 08:13 | 2008-08-16 | 2008-08-16 09:22 | Calculated | o410e | ABS669 | 0 |  | Benneydale 103-05 | Remote Rural F | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation |  | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 280 | 69 | 20359 | 19320 | 0.94897 | 0.0033892 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11302 |  | 2008-08-16 13:17 | 2008-08-16 | 2008-08-16 17:02 | Calculated | o410e | T16L1 | 0 |  | National Park 411-03 | Remote Rural F | National Park | National Park Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 225 | 20359 | 6075 | 0.29839 | 0.011052 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11301 |  | 2008-08-16 13:33 | 2008-08-16 | 2008-08-16 18:01 | Calculated | o410e | T1441 | 0 |  | Huirimu 121-03 | Remote Rural F | Huirimu | Arohena Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 268 | 20359 | 1340 | 0.06582 | 0.013164 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11303 |  | 2008-08-16 13:48 | 2008-08-16 | 2008-08-16 14:22 | Calculated | o410e | ABS 348 | 0 |  | Gravel Scoop 109-13 | Remote Rural F | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 34 | 20359 | 816 | 0.04008 | 0.00167 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11304 |  | 2008-08-16 14:05 | 2008-08-16 | 2008-08-16 22:26 | Calculated | o410e | T2304 | 0 |  | Whakamaru 120-01 | Remote Rural F | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 502 | 20359 | 4016 | 0.19726 | 0.024657 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11305 |  | 2008-08-16 21:17 | 2008-08-16 | 2008-08-17 15:47 | Calculated | o410e | T2239 | 0 |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1110 | 20359 | 1110 | 0.05452 | 0.054521 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11306 |  | 2008-08-17 06:45 | 2008-08-17 | 2008-08-17 08:18 | Calculated | o410e | T1666 | 0 |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 93 | 20359 | 1581 | 0.07766 | 0.004568 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11307 |  | 2008-08-17 08:31 | 2008-08-17 | 2008-08-17 19:59 | Calculated | o410e | T585 | 0 |  | Maihiihi 111-06 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 688 | 20359 | 688 | 0.03379 | 0.033793 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11308 |  | 2008-08-17 11:26 | 2008-08-17 | 2008-08-17 18:09 | Calculated | o410e | T13K3 | 0 |  | Raurimu 410-01 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD |  | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 403 | 20359 | 403 | 0.01979 | 0.019795 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11309 |  | 2008-08-17 12:07 | 2008-08-17 | 2008-08-17 13:15 | Calculated | o410e | T2129 | 0 |  | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 68 | 20359 | 816 | 0.04008 | 0.00334 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11310 |  | 2008-08-17 18:00 | 2008-08-17 | 2008-08-18 14:38 | Calculated | o410e | T2752 | 0 |  | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1238 | 20359 | 1238 | 0.06081 | 0.060808 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11311 |  | 2008-08-17 20:07 | 2008-08-17 | 2008-08-18 09:58 | Calculated | o410e | L764 | 0 |  | Waitomo 108-02 | Remote Rural F | Waitomo | Gadsby Road Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 831 | 20359 | 6648 | 0.32654 | 0.040817 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11312 |  | 2008-08-18 07:50 | 2008-08-18 | 2008-08-18 12:54 | Calculated | o410e | T458 | 0 |  | Maihiihi 111-04 | Remote Rural F | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 304 | 20359 | 608 | 0.02986 | 0.014932 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11313 |  | 2008-08-18 08:03 | 2008-08-18 | 2008-08-18 09:39 | Calculated | o410e | T1660 | 0 |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 96 | 20359 | 96 | 0.00472 | 0.0047154 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11314 |  | 2008-08-18 08:30 | 2008-08-18 | 2008-08-18 11:22 | Calculated | o410e | T16J1 | 0 |  | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 172 | 20359 | 172 | 0.00845 | 0.0084484 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11316 |  | 2008-08-18 09:13 | 2008-08-18 | 2008-08-18 14:48 | Calculated | o410e | ABS 422 | 0 |  | Tihoi 124-02 RETIRED | Remote Rural F | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 335 | 20359 | 5360 | 0.26327 | 0.016455 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11318 |  | 2008-08-18 13:34 | 2008-08-18 | 2008-08-18 14:26 | Calculated | o410e | SEC 1631 | 0 |  | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 52 | 20359 | 884 | 0.04342 | 0.0025542 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11319 |  | 2008-08-19 09:03 | 2008-08-19 | 2008-08-19 10:06 | Calculated | o410e | Sec 368 | 0 |  | Western 403-06 | Remote Rural F | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 7 | 63 | 20359 | 441 | 0.02166 | 0.0030945 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11320 |  | 2008-08-19 09:36 | 2008-08-19 | 2008-08-19 13:56 | Calculated | o410e | TF 679 | 0 |  | Tangiwai 416-03 | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 3 | 260 | 20359 | 780 | 0.03831 | 0.012771 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11321 |  | 2008-08-19 15:09 | 2008-08-19 | 2008-08-19 16:28 | Calculated | o410e | T1415 | 0 |  | Wharepapa 122-02 | Remote Rural F | Wharepapa | Arohena Zone Substation |  | Weather | Lightning |  | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 79 | 20359 | 79 | 0.00388 | 0.0038803 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
11322 |  | 2008-08-19 19:56 | 2008-08-19 | 2008-08-19 19:59 | Calculated | o410e | T505 | 0 |  | Caves 101-09 | Remote Rural F | Caves | Hangatiki Zone Substation |  | Asset Related | Other |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 3 | 20359 | 9 | 0.00044 | 0.00014735 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
20019 |  | 2008-08-20 09:32 | 2008-08-20 | 2008-08-20 12:46 | Calculated | TF679 | TF679 - Transformer Fuse | TF679 - Transformer Fuse | No Segment | Tangiwai 416-03 | Rural D | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 194 | 1 | 20359 | 194 | 0.00953 | 4.9118e-05 | 8 | 1552 | 2008/2009 | August-2008 | 8 | 2008
20020 | ABS 748-418 | 2008-08-20 10:31 | 2008-08-20 | 2008-08-20 11:49 | Calculated | 748 | 748 - ABS 748 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 78 | 81 | 20359 | 6318 | 0.31033 | 0.0039786 | 648 | 50544 | 2008/2009 | August-2008 | 8 | 2008
20021 | TX620 | 2008-08-20 11:15 | 2008-08-20 | 2008-08-20 12:15 | Calculated | T620 | T620 - 3ph 100kVA POL |  | 103SEG1230 | Benneydale 103-07 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 26 | 20359 | 1560 | 0.07662 | 0.0012771 | 208 | 12480 | 2008/2009 | August-2008 | 8 | 2008
20022 | TX 2294 | 2008-08-21 08:01 | 2008-08-21 | 2008-08-21 10:32 | Calculated | T2294 | T2294 - 1ph 5kVA polemnt | T2294 - 1ph 5kVA polemnt | 121SEG425-748 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation | Transformers : Other | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 1 | 20359 | 151 | 0.00742 | 4.9118e-05 | 8 | 1208 | 2008/2009 | August-2008 | 8 | 2008
20023 | SECT 314 | 2008-08-21 10:30 | 2008-08-21 | 2008-08-21 14:15 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | No Segment | Western 403-07 | Remote Rural E | Western | Borough Zone Substation | Unknown (All Categories) | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 15 | 20359 | 2250 | 0.11052 | 0.00073677 | 120 | 18000 | 2008/2009 | August-2008 | 8 | 2008
20026 |  | 2008-08-22 08:30 | 2008-08-22 | 2008-08-22 09:31 | Calculated | T1030 | T1030 - 3ph 10kVA POL |  | No Segment | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation | Transformers : Other | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 1 | 20359 | 61 | 0.003 | 4.9118e-05 | 8 | 488 | 2008/2009 | August-2008 | 8 | 2008
20025 | ABS 483-182-LLL POLE 126 | 2008-08-22 09:04 | 2008-08-22 | 2008-08-22 15:41 | Calculated | 483 | 483 - ABS 483 |  | No Segment | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 397 | 19 | 20359 | 7543 | 0.3705 | 0.00093325 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
20027 | LINK 5354 | 2008-08-22 09:25 | 2008-08-22 | 2008-08-22 11:33 | Calculated | 5354 | 5354 - Earth Working Link 5354 |  | No Segment | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 128 | 8 | 20359 | 1024 | 0.0503 | 0.00039295 | 64 | 8192 | 2008/2009 | August-2008 | 8 | 2008
20028 | LINK 1533-1534 | 2008-08-22 10:32 | 2008-08-22 | 2008-08-22 13:35 | Calculated | 1533 | 1533 - Earth Working Link 1533 |  | 113SEG1533-1534 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage |  |  | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 183 | 3 | 20359 | 549 | 0.02697 | 0.00014735 | 24 | 4392 | 2008/2009 | August-2008 | 8 | 2008
20037 |  | 2008-08-24 12:42 | 2008-08-24 | 2008-08-24 14:30 | Calculated | 5402X | 5402X - Outgoing Link 5402X |  | 409SEG5884-5403 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation | Miscellaneous : Other Miscellaneous | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 211 | 14 | 20359 | 2954 | 0.1451 | 0.00068766 | 112 | 23632 | 2008/2009 | August-2008 | 8 | 2008
20038 | ocb 232-754 | 2008-08-24 12:49 | 2008-08-24 | 2008-08-24 13:01 | Calculated | 754 | 754 - 33kV Oil Circuit Breaker 754 | 754 - 33kV Oil Circuit Breaker 754 | No Segment | 206-01 Waitete | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 1575 | 20359 | 18900 | 0.92834 | 0.077361 | 0 | 0 | 2008/2009 | August-2008 | 8 | 2008
20039 |  | 2008-08-24 14:00 | 2008-08-24 | 2008-08-24 14:31 | Calculated | 5316 | 5316 - Sectionaliser with Bypass 5316 |  | No Segment | Western 403-06 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1310 | 7 | 20359 | 9170 | 0.45042 | 0.00034383 | 56 | 73360 | 2008/2009 | August-2008 | 8 | 2008
20040 |  | 2008-08-24 16:51 | 2008-08-24 | 2008-08-24 20:33 | Calculated | 5407 | 5407 - Sectionaliser with Bypass 5407 | 5407 - Sectionaliser with Bypass 5407 | 410SEG5407-5433 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 222 | 45 | 20359 | 9990 | 0.49069 | 0.0022103 | 360 | 79920 | 2008/2009 | August-2008 | 8 | 2008
20041 |  | 2008-08-24 21:00 | 2008-08-24 | 2008-08-24 21:59 | Calculated | 1112 | 1112 - Link 1112 |  | 114SEG1112 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 10 | 20359 | 590 | 0.02898 | 0.00049118 | 71 | 4189 | 2008/2009 | August-2008 | 8 | 2008
20042 |  | 2008-08-24 21:36 | 2008-08-24 | 2008-08-25 06:55 | Calculated | 642 | 642 - CIRCUIT BREAKER with Bypass 642 |  | No Segment | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 559 | 101 | 20359 | 56459 | 2.7732 | 0.004961 | 808 | 451672 | 2008/2009 | August-2008 | 8 | 2008
20043 |  | 2008-08-25 05:16 | 2008-08-25 | 2008-08-25 07:00 | Calculated | 09K06 | 09K06 - 3ph 30kVA POLEMNT |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation | Transformers : Other | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 5 | 20359 | 520 | 0.02554 | 0.00024559 | 40 | 4160 | 2008/2009 | August-2008 | 8 | 2008
20506 |  | 2008-08-26 10:00 | 2008-08-26 | 2008-08-26 12:01 | Calculated | 07D01 | 07D01 - 2ph 15kVA POLEMNT |  | 413SEG5509 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation | Switchgear : Main Circuit Fuses | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 3 | 20359 | 360 | 0.01768 | 0.00014735 | 24 | 2883 | 2008/2009 | August-2008 | 8 | 2008
20505 |  | 2008-08-26 10:01 | 2008-08-26 | 2008-08-26 12:01 | Calculated | 355 | 355 - Fused Link 355 |  | No Segment | No Asset Group | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 9 | 20359 | 1075 | 0.0528 | 0.00044206 | 72 | 8606 | 2008/2009 | August-2008 | 8 | 2008
20512 | Waitete Road | 2008-08-27 11:01 | 2008-08-27 | 2008-08-27 11:01 | Calculated | 200 | 200 - ABS 200 |  | No Segment | Benneydale 103-01 | Urban A | Benneydale | Waitete Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUO1 | Control Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 448 | 20359 | 0 | 0 | 0.022005 | 3584 | 298 | 2008/2009 | August-2008 | 8 | 2008
20514 |  | 2008-08-28 09:00 | 2008-08-28 | 2008-08-28 10:01 | Calculated | X5940 | X5940 - Earth Working Link 5940 |  | No Segment | No Asset Group |  | Hirangi | Awamate Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  |  |  | 20359 |  | 0 | 0 |  |  | 2008/2009 | August-2008 | 8 | 2008
20516 |  | 2008-08-28 09:56 | 2008-08-28 | 2008-08-28 11:18 | Calculated | T1276 | T1276 - 1ph 10kVA POLEMNT |  | 123SEG469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 1 | 20359 | 82 | 0.00403 | 4.9118e-05 | 8 | 656 | 2008/2009 | August-2008 | 8 | 2008
20517 |  | 2008-08-28 10:06 | 2008-08-28 | 2008-08-28 13:29 | Calculated | 468 | 468 - Fused Link 468 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 203 | 24 | 20359 | 4872 | 0.2393 | 0.0011788 | 192 | 38976 | 2008/2009 | August-2008 | 8 | 2008
20518 |  | 2008-08-28 10:47 | 2008-08-28 | 2008-08-28 13:42 | Calculated | T2875 | T2875 - 1ph 10kVA POL |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 2 | 20359 | 350 | 0.01719 | 9.8237e-05 | 16 | 2800 | 2008/2009 | August-2008 | 8 | 2008
20520 | Tiohi Rd | 2008-08-29 09:52 | 2008-08-29 | 2008-08-29 14:27 | Calculated | 667 | 667 - Fused Link 667 |  | No Segment | Tihoi 124-02 RETIRED | Rural D | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 275 | 3 | 20359 | 825 | 0.04052 | 0.00014735 | 24 | 6600 | 2008/2009 | August-2008 | 8 | 2008
20523 | Mt Ruapehu | 2008-08-29 10:17 | 2008-08-29 | 2008-08-29 10:18 | Calculated | 5773 | 5773 - CIRCUIT BREAKER 5773 |  | 419SEG5773-5998 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 1 | 40 | 20359 | 40 | 0.00196 | 0.0019647 | 320 | 320 | 2008/2009 | August-2008 | 8 | 2008
20526 | waikawau | 2008-08-29 10:30 | 2008-08-29 | 2008-08-29 14:52 | Calculated | 1624 | 1624 - Fused Link 1624 |  | 128SEG1615-1624 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 262 | 7 | 20359 | 1834 | 0.09008 | 0.00034383 | 56 | 14672 | 2008/2009 | August-2008 | 8 | 2008
20522 | Tirohanga Road | 2008-08-29 10:36 | 2008-08-29 | 2008-08-29 13:46 | Calculated | T3103 | T3103 - 3ph 100kVA POLEMNT |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 1 | 20359 | 190 | 0.00933 | 4.9118e-05 | 8 | 1520 | 2008/2009 | August-2008 | 8 | 2008
20527 |  | 2008-08-29 21:03 | 2008-08-29 | 2008-08-30 00:25 | Calculated | 5758 | 5758 - Sectionaliser 5758 |  | 413SEG5996-5758 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  |  |  | 20359 |  | 0 | 0 |  |  | 2008/2009 | August-2008 | 8 | 2008
20530 | Western Bay Road. For kAKAH | 2008-09-01 00:07 | 2008-09-01 | 2008-09-01 02:14 | Calculated | 478 | 478 - Fused Link 478 |  | No Segment | No Asset Group | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WOLR | WOLR | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 12 | 20359 | 1524 | 0.07486 | 0.00058942 | 96 | 12192 | 2008/2009 | September-2008 | 9 | 2008
20529 | Kiritihere- Last road Crossing | 2008-09-01 06:48 | 2008-09-01 | 2008-09-01 11:07 | Calculated | 1536X | 1536X - Outgoing Link 1536X | 1536X - Outgoing Link 1536X | No Segment | No Asset Group | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 259 | 8 | 20359 | 2072 | 0.10177 | 0.00039295 | 64 | 16576 | 2008/2009 | September-2008 | 9 | 2008
20531 | Mangarino Road | 2008-09-02 08:45 | 2008-09-02 | 2008-09-02 09:06 | Calculated | T1032 | T1032 - 3ph 30kVA POLEMNT |  | 106SEG224-361 | Rangitoto 106-07 | Rural C | Rangitoto | Waitete Zone Substation | Unknown (All Categories) | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 6 | 20359 | 126 | 0.00619 | 0.00029471 | 48 | 1008 | 2008/2009 | September-2008 | 9 | 2008
20532 | Hirnagi Sub. Connect Gen set | 2008-09-02 09:11 | 2008-09-02 | 2008-09-02 09:47 | Calculated | 5519J | 5519J - Incoming Link 5519J |  | No Segment | Lake Taupo 606-01 | Rural C | Lake Taupo 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 21 | 20359 | 756 | 0.03713 | 0.0010315 | 168 | 6048 | 2008/2009 | September-2008 | 9 | 2008
20533 | Gold Finch Street | 2008-09-02 09:36 | 2008-09-02 | 2008-09-02 16:41 | Calculated | 20L54GMT | 20L54GMT - 3ph 200kVA GMT |  | No Segment | No Asset Group |  | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Pole |  | PTRN1 | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 425 | 11 | 20359 | 4675 | 0.22963 | 0.0005403 | 0 | 0 | 2008/2009 | September-2008 | 9 | 2008
20534 | Whenuakura Road | 2008-09-02 09:36 | 2008-09-02 | 2008-09-02 09:40 | Calculated | 5270 | 5270 - Earth Working Link 5270 |  | No Segment | No Asset Group | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related |  |  | PTRN1 | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 136 | 58 | 20359 | 6800 | 0.334 | 0.0028489 | 464 | 54400 | 2008/2009 | September-2008 | 9 | 2008
20535 | Kohua Road Before Ngatama | 2008-09-02 10:06 | 2008-09-02 | 2008-09-02 14:52 | Calculated | 1738 | 1738 - Solid Link 1738 |  | 115SEG1738-1709 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 286 | 14 | 20359 | 4004 | 0.19667 | 0.00068766 | 112 | 32032 | 2008/2009 | September-2008 | 9 | 2008
20536 | Mahoenui | 2008-09-02 11:09 | 2008-09-02 | 2008-09-02 11:14 | Calculated | 1010 | 1010 - Mahoenui Oil Circuit Breaker 1010 |  | No Segment | 209-01 Mahoenui | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause |  |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  |  |  | 20359 |  | 0 | 0 |  |  | 2008/2009 | September-2008 | 9 | 2008
20537 | SH3 Rauputu's Spur | 2008-09-02 13:59 | 2008-09-02 | 2008-09-02 14:50 | Calculated | 1504 | 1504 - Fused Link 1504 |  | 113SEG1504 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related |  |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 6 | 20359 | 306 | 0.01503 | 0.00029471 | 48 | 2448 | 2008/2009 | September-2008 | 9 | 2008
20538 | Pokuru Road | 2008-09-02 14:43 | 2008-09-02 | 2008-09-02 17:33 | Calculated | 124T918 | 124T918 - 3ph 15kVA polemount |  | No Segment | Tihoi 124-04 RETIRED |  | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause |  |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 1 | 20359 | 170 | 0.00835 | 4.9118e-05 | 8 | 1360 | 2008/2009 | September-2008 | 9 | 2008
20539 | Sandel Road | 2008-09-02 18:45 | 2008-09-02 | 2008-09-02 19:59 | Calculated | 484 | 484 - ABS 484 |  | 120SEG484-483 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 102 | 20359 | 7446 | 0.36574 | 0.0050101 | 0 | 0 | 2008/2009 | September-2008 | 9 | 2008
20556 |  | 2008-09-04 09:34 | 2008-09-04 | 2008-09-04 10:53 | Calculated | 5850 | 5850 - ABS 5850 |  | 407SEG5850-5838 | Manunui 407-01 (was Affco) | Rural B | Manunui / AFFCO Retired | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 79 | 1 | 20359 | 79 | 0.00388 | 4.9118e-05 | 8 | 632 | 2008/2009 | September-2008 | 9 | 2008
20558 | Pamotumotu road | 2008-09-04 11:50 | 2008-09-04 | 2008-09-04 17:14 | Calculated | T639 | T639 - 3ph 30kVA polemnt |  | 5ZA7Q2 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation | Transformers : Other | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 324 | 4 | 20359 | 1296 | 0.06366 | 0.00019647 | 32 | 10368 | 2008/2009 | September-2008 | 9 | 2008
20559 | Otunui North Road | 2008-09-04 13:09 | 2008-09-04 | 2008-09-04 14:34 | Calculated | 5546 | 5546 - Earth Working Link 5546 | 5546 - Earth Working Link 5546 | No Segment | Western 403-05 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 13 | 20359 | 1105 | 0.05428 | 0.00063854 | 104 | 8840 | 2008/2009 | September-2008 | 9 | 2008
20561 | Te anga Road | 2008-09-05 09:53 | 2008-09-05 | 2008-09-05 10:56 | Calculated | T518 | T518 - 1ph 10kVA POL |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 2 | 20359 | 126 | 0.00619 | 9.8237e-05 | 16 | 1008 | 2008/2009 | September-2008 | 9 | 2008
20562 | Taupo Road | 2008-09-05 15:40 | 2008-09-05 | 2008-09-05 16:11 | Calculated | 5742 | 5742 - Fused Link 5742 |  | 404SEG5742 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 31 | 2 | 20359 | 62 | 0.00305 | 9.8237e-05 | 16 | 496 | 2008/2009 | September-2008 | 9 | 2008
20563 | SH 3 Mokau | 2008-09-08 07:32 | 2008-09-08 | 2008-09-08 10:08 | Calculated | T2174 | T2174 - 1ph 25kVA POLEMNT |  | 128SEG1634-REG3 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 156 | 2 | 20359 | 312 | 0.01532 | 9.8237e-05 | 16 | 2496 | 2008/2009 | September-2008 | 9 | 2008
20565 | Miro Street | 2008-09-08 09:25 | 2008-09-08 | 2008-09-08 11:06 | Calculated | 5868 | 5868 - ABS 5868 |  | No Segment | No Asset Group | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  |  |  | 20359 |  | 0 | 0 |  |  | 2008/2009 | September-2008 | 9 | 2008
20564 | Waitomo valley Road | 2008-09-08 10:34 | 2008-09-08 | 2008-09-08 12:54 | Calculated | 545 | 545 - ABS 545 |  | 112SEG545-326 | Otorohanga 112-05 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 140 | 19 | 20359 | 2660 | 0.13065 | 0.00093325 | 152 | 21280 | 2008/2009 | September-2008 | 9 | 2008
20588 | SH 40 | 2008-09-09 06:47 | 2008-09-09 | 2008-09-09 08:32 | Calculated | 06E13 | 06E13 - 2ph 15kVA POLEMNT |  | No Segment | No Asset Group | Rural D | Nihoniho | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 2 | 20359 | 210 | 0.01031 | 9.8237e-05 | 16 | 1680 | 2008/2009 | September-2008 | 9 | 2008
20589 | Old te Kuiti road | 2008-09-09 08:43 | 2008-09-09 | 2008-09-09 11:00 | Calculated | T208 | T208 - 3ph 25kVA POLEMNT |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 3 | 20359 | 411 | 0.02019 | 0.00014735 | 24 | 3288 | 2008/2009 | September-2008 | 9 | 2008
20590 | Old Te Kuiti road | 2008-09-09 08:43 | 2008-09-09 | 2008-09-09 11:13 | Calculated | T1042 | T1042 - 3ph 50kVA POLEMNT |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 3 | 20359 | 450 | 0.0221 | 0.00014735 | 24 | 3600 | 2008/2009 | September-2008 | 9 | 2008
20591 | Old Te Kuiti Road | 2008-09-09 08:43 | 2008-09-09 | 2008-09-09 11:34 | Calculated | T389 | T389 - 1ph 15kVA POLEMNT |  | No Segment | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 1 | 20359 | 171 | 0.0084 | 4.9118e-05 | 8 | 1368 | 2008/2009 | September-2008 | 9 | 2008
20568 | Tutunui Street | 2008-09-09 08:46 | 2008-09-09 | 2008-09-09 12:32 | Calculated | T351 | T351 - 3ph 200kVA GNDPAD |  | No Segment | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 226 | 57 | 20359 | 12882 | 0.63274 | 0.0027997 | 0 | 0 | 2008/2009 | September-2008 | 9 | 2008
20569 | Maihiihi Road | 2008-09-09 08:52 | 2008-09-09 | 2008-09-09 11:36 | Calculated | T1098 | T1098 - 2ph 15kVA polemnt |  | 111SEG665 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 3 | 20359 | 492 | 0.02417 | 0.00014735 | 24 | 3936 | 2008/2009 | September-2008 | 9 | 2008
20570 | Tauraroa Rd | 2008-09-09 08:52 | 2008-09-09 | 2008-09-09 11:57 | Calculated | T359 | T359 - 1ph 10kVA POLEMNT |  | 111SEG374-783 | Maihiihi 111-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 2 | 20359 | 370 | 0.01817 | 9.8237e-05 | 16 | 2960 | 2008/2009 | September-2008 | 9 | 2008
20571 | Mangaorongo Road | 2008-09-09 08:52 | 2008-09-09 | 2008-09-09 14:47 | Calculated | T232 | T232 - 3ph 25kVA polemnt |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 355 | 3 | 20359 | 1065 | 0.05231 | 0.00014735 | 24 | 8520 | 2008/2009 | September-2008 | 9 | 2008
20572 | Mangaorongo Road | 2008-09-09 08:52 | 2008-09-09 | 2008-09-09 15:10 | Calculated | T1286 | T1286 - 1ph 25kVA polemnt |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 378 | 2 | 20359 | 756 | 0.03713 | 9.8237e-05 | 16 | 6048 | 2008/2009 | September-2008 | 9 | 2008
20592 | Otewa Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 11:38 | Calculated | T399 | T399 - 1ph 15kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 2 | 20359 | 298 | 0.01464 | 9.8237e-05 | 16 | 2384 | 2008/2009 | September-2008 | 9 | 2008
20593 | Otewa Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 11:42 | Calculated | T261 | T261 - 3ph 15kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 153 | 1 | 20359 | 153 | 0.00752 | 4.9118e-05 | 8 | 1224 | 2008/2009 | September-2008 | 9 | 2008
20594 | Otewa Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 11:59 | Calculated | T1160 | T1160 - 1ph 10kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 2 | 20359 | 340 | 0.0167 | 9.8237e-05 | 16 | 2720 | 2008/2009 | September-2008 | 9 | 2008
20597 | otewa Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 14:23 | Calculated | T2833 | T2833 - 3ph 30kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 314 | 3 | 20359 | 942 | 0.04627 | 0.00014735 | 24 | 7536 | 2008/2009 | September-2008 | 9 | 2008
20598 | Irvine Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 12:29 | Calculated | T1300 | T1300 - 1ph 25kVA POLEMNT |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 200 | 2 | 20359 | 400 | 0.01965 | 9.8237e-05 | 16 | 3200 | 2008/2009 | September-2008 | 9 | 2008
20599 | Otewa Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 12:44 | Calculated | T643 | T643 - 3ph 25kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 215 | 3 | 20359 | 645 | 0.03168 | 0.00014735 | 24 | 5160 | 2008/2009 | September-2008 | 9 | 2008
20600 | Veale Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 12:40 | Calculated | T467 | T467 - 3ph 10kVA POLEMNT |  | No Segment | No Asset Group | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 211 | 1 | 20359 | 211 | 0.01036 | 4.9118e-05 | 8 | 1688 | 2008/2009 | September-2008 | 9 | 2008
20601 | Otewa Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 13:02 | Calculated | T196 | T196 - 3ph 15kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 233 | 4 | 20359 | 932 | 0.04578 | 0.00019647 | 32 | 7456 | 2008/2009 | September-2008 | 9 | 2008
20602 | Tahaia Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 13:12 | Calculated | 341 | 341 - Fused Link 341 |  | No Segment | No Asset Group | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 243 | 39 | 20359 | 9477 | 0.46549 | 0.0019156 | 312 | 75816 | 2008/2009 | September-2008 | 9 | 2008
20603 | otewa Road | 2008-09-09 09:09 | 2008-09-09 | 2008-09-09 13:31 | Calculated | T2280 | T2280 - 3ph 25kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 262 | 3 | 20359 | 786 | 0.03861 | 0.00014735 | 24 | 6288 | 2008/2009 | September-2008 | 9 | 2008
20573 | Mangatutu road | 2008-09-09 09:16 | 2008-09-09 | 2008-09-09 13:14 | Calculated | T2583 | T2583 - 1ph 10kVA polemnt |  | 111SEG395-549 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 238 | 1 | 20359 | 238 | 0.01169 | 4.9118e-05 | 8 | 1904 | 2008/2009 | September-2008 | 9 | 2008
20574 | Mangatutu road | 2008-09-09 09:16 | 2008-09-09 | 2008-09-09 13:27 | Calculated | T2582 | T2582 - 3ph 25kVA polemnt |  | 111SEG395-551RET | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 251 | 1 | 20359 | 251 | 0.01233 | 4.9118e-05 | 8 | 2008 | 2008/2009 | September-2008 | 9 | 2008
20575 | Maihiihi road | 2008-09-09 09:16 | 2008-09-09 | 2008-09-10 17:25 | Calculated | 662 | 662 - Fused Link 662 |  | 111SEG662 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1929 | 4 | 20359 | 7716 | 0.379 | 0.00019647 | 32 | 61728 | 2008/2009 | September-2008 | 9 | 2008
20576 | Chindie road | 2008-09-09 09:17 | 2008-09-09 | 2008-09-09 14:16 | Calculated | T2899 | T2899 - 1ph 10kVA POLEMNT |  | 111SEG399-374 | Maihiihi 111-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 299 | 1 | 20359 | 299 | 0.01469 | 4.9118e-05 | 8 | 2392 | 2008/2009 | September-2008 | 9 | 2008
20577 | Rangiatea road | 2008-09-09 09:17 | 2008-09-09 | 2008-09-09 14:41 | Calculated | T254 | T254 - 3ph 25kVA POLEMNT |  | 109SEG396-397 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 324 | 4 | 20359 | 1296 | 0.06366 | 0.00019647 | 32 | 10368 | 2008/2009 | September-2008 | 9 | 2008
20578 | Rangiatea Road | 2008-09-09 09:17 | 2008-09-09 | 2008-09-09 14:54 | Calculated | T581 | T581 - 3ph 25kVA POLEMNT |  | 109SEG396-397 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 337 | 2 | 20359 | 674 | 0.03311 | 9.8237e-05 | 16 | 5392 | 2008/2009 | September-2008 | 9 | 2008
20579 | Rangiatea Road | 2008-09-09 09:17 | 2008-09-09 | 2008-09-09 15:09 | Calculated | T435 | T435 - 3ph 30kVA POLEMNT |  | 109SEG397-345 | Gravel Scoop 109-12 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 352 | 4 | 20359 | 1408 | 0.06916 | 0.00019647 | 32 | 11264 | 2008/2009 | September-2008 | 9 | 2008
20580 | McRae road | 2008-09-09 09:17 | 2008-09-09 | 2008-09-09 15:48 | Calculated | T333 | T333 - 3ph 25kVA POLEMNT |  | 109SEG622 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 391 | 4 | 20359 | 1564 | 0.07682 | 0.00019647 | 32 | 12512 | 2008/2009 | September-2008 | 9 | 2008
20581 | Waimahora Road | 2008-09-09 09:28 | 2008-09-09 | 2008-09-09 13:32 | Calculated | 170J | 170J - Incoming Link 170J |  | 109SEG529-1727 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 326 | 28 | 20359 | 7406 | 0.36377 | 0.0013753 | 224 | 59248 | 2008/2009 | September-2008 | 9 | 2008
20582 | Ngapeke road | 2008-09-09 09:28 | 2008-09-09 | 2008-09-09 14:08 | Calculated | T566 | T566 - 3ph 25kVA POLEMNT |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 280 | 3 | 20359 | 840 | 0.04126 | 0.00014735 | 24 | 6720 | 2008/2009 | September-2008 | 9 | 2008
20583 | Waimahora Road | 2008-09-09 09:28 | 2008-09-09 | 2008-09-09 15:14 | Calculated | T2371 | T2371 - 1ph 10kVA POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 346 | 1 | 20359 | 346 | 0.01699 | 4.9118e-05 | 8 | 2768 | 2008/2009 | September-2008 | 9 | 2008
20584 | Waimahora Road | 2008-09-09 09:28 | 2008-09-09 | 2008-09-09 15:14 | Calculated | T1288 | T1288 - 1ph 10kVA POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 346 | 1 | 20359 | 346 | 0.01699 | 4.9118e-05 | 8 | 2768 | 2008/2009 | September-2008 | 9 | 2008
20604 | Potaka Road | 2008-09-09 09:30 | 2008-09-09 | 2008-09-09 09:48 | Calculated | T1944 | T1944 - 1ph 15kVA POLEMNT |  | 114SEG1106-1105 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 2 | 20359 | 36 | 0.00177 | 9.8237e-05 | 16 | 288 | 2008/2009 | September-2008 | 9 | 2008
20585 | Duncan Road | 2008-09-09 09:38 | 2008-09-09 | 2008-09-09 13:51 | Calculated | T419 | T419 - 1ph 25kVA POLEMNT |  | 122SEG678-768 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 253 | 2 | 20359 | 506 | 0.02485 | 9.8237e-05 | 16 | 4048 | 2008/2009 | September-2008 | 9 | 2008
20566 | Miro Street | 2008-09-09 09:43 | 2008-09-09 | 2008-09-09 11:00 | Calculated | 5390 | 5390 - Fused Link 5390 |  | No Segment | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 162 | 20359 | 12474 | 0.6127 | 0.0079572 | 1296 | 99792 | 2008/2009 | September-2008 | 9 | 2008
20605 | Ohura Road | 2008-09-09 10:19 | 2008-09-09 | 2008-09-09 10:49 | Calculated | T1983 | T1983 - 1ph 15kVA POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 30 | 3 | 20359 | 90 | 0.00442 | 0.00014735 | 24 | 720 | 2008/2009 | September-2008 | 9 | 2008
20606 | Orangi road | 2008-09-09 10:40 | 2008-09-09 | 2008-09-09 11:48 | Calculated | 08K03 | 08K03 - 1ph 15kVA POLEMNT |  | No Segment | No Asset Group | Rural B | Manunui | Manunui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 5 | 20359 | 340 | 0.0167 | 0.00024559 | 40 | 2720 | 2008/2009 | September-2008 | 9 | 2008
20607 | Upper Retaruke | 2008-09-09 10:55 | 2008-09-09 | 2008-09-09 13:02 | Calculated | 5744 | 5744 - Sectionaliser with Bypass 5744 |  | 410SEG5744-5631 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 12 | 20359 | 1524 | 0.07486 | 0.00058942 | 96 | 12192 | 2008/2009 | September-2008 | 9 | 2008
20608 | Mangawhio Road | 2008-09-09 11:25 | 2008-09-09 | 2008-09-09 13:23 | Calculated | T1441 | T1441 - 1ph 15kVA polemnt |  | No Segment | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 2 | 20359 | 236 | 0.01159 | 9.8237e-05 | 16 | 1888 | 2008/2009 | September-2008 | 9 | 2008
20609 | Allens Road | 2008-09-09 11:35 | 2008-09-09 | 2008-09-09 13:46 | Calculated | 449 | 449 - ABS 449 |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 5 | 20359 | 655 | 0.03217 | 0.00024559 | 40 | 5240 | 2008/2009 | September-2008 | 9 | 2008
20611 | Owaewenga Road | 2008-09-10 07:37 | 2008-09-10 | 2008-09-10 10:11 | Calculated | T1594 | T1594 - 1ph 10kVA POLEMNT |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 2 | 20359 | 308 | 0.01513 | 9.8237e-05 | 16 | 2464 | 2008/2009 | September-2008 | 9 | 2008
20612 | Lurman road | 2008-09-10 07:37 | 2008-09-10 | 2008-09-10 09:57 | Calculated | T2894 | T2894 - 3ph 25kVA POLEMNT |  | 109SEG188 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 1 | 20359 | 140 | 0.00688 | 4.9118e-05 | 8 | 1120 | 2008/2009 | September-2008 | 9 | 2008
20613 | Owaewenga Road | 2008-09-10 07:37 | 2008-09-10 | 2008-09-10 10:33 | Calculated | T2377 | T2377 - 1ph 10kVA POLEMNT |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 2 | 20359 | 352 | 0.01729 | 9.8237e-05 | 16 | 2816 | 2008/2009 | September-2008 | 9 | 2008
20614 | Tahaia Bush Road | 2008-09-10 07:37 | 2008-09-10 | 2008-09-10 11:58 | Calculated | T1448 | T1448 - 1ph 10kVA POLEMNT |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 261 | 1 | 20359 | 261 | 0.01282 | 4.9118e-05 | 8 | 2088 | 2008/2009 | September-2008 | 9 | 2008
20615 | Lower Retaruke Sub | 2008-09-10 09:47 | 2008-09-10 | 2008-09-10 15:10 | Calculated | 5490 | 5490 - Recloser with Bypass 5490 |  | 410SEG5490-5438 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 348 | 50 | 20359 | 17400 | 0.85466 | 0.0024559 | 400 | 139200 | 2008/2009 | September-2008 | 9 | 2008
20616 | Marakopa Road | 2008-09-10 10:05 | 2008-09-10 | 2008-09-10 14:16 | Calculated | 187 | 187 - Fused Link 187 |  | 125SEG187 | Coast 125-04 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 251 | 12 | 20359 | 3012 | 0.14794 | 0.00058942 | 96 | 24096 | 2008/2009 | September-2008 | 9 | 2008
20617 | Tihoi Road | 2008-09-10 11:13 | 2008-09-10 | 2008-09-10 12:16 | Calculated | T979 | T979 - 3ph 15kVA POLEMNT |  | No Segment | Tihoi 124-02 RETIRED | Rural D | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 1 | 20359 | 63 | 0.00309 | 4.9118e-05 | 8 | 504 | 2008/2009 | September-2008 | 9 | 2008
20618 | Kopaki road | 2008-09-10 12:10 | 2008-09-10 | 2008-09-10 13:10 | Calculated | T1833 | T1833 - 1ph 10kVA POL |  | 103SEG705-1736 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 2 | 20359 | 120 | 0.00589 | 9.8237e-05 | 16 | 960 | 2008/2009 | September-2008 | 9 | 2008
20619 | Tolley Road | 2008-09-10 12:45 | 2008-09-10 | 2008-09-10 15:07 | Calculated | T840 | T840 - 1ph 25kVA polemnt |  | No Segment | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 3 | 20359 | 426 | 0.02092 | 0.00014735 | 24 | 3408 | 2008/2009 | September-2008 | 9 | 2008
20620 | Moana Cres | 2008-09-10 13:40 | 2008-09-10 | 2008-09-10 14:03 | Calculated | T709 | T709 - 3ph 200kVA GNDPAD |  | 118SEG496-1741 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 46 | 20359 | 1058 | 0.05197 | 0.0022594 | 368 | 8464 | 2008/2009 | September-2008 | 9 | 2008
20621 | Kirikau Valley | 2008-09-11 06:15 | 2008-09-11 | 2008-09-11 10:19 | Calculated | 5314J | 5314J - Incoming Link 5314J |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 244 | 15 | 20359 | 3660 | 0.17977 | 0.00073677 | 120 | 29280 | 2008/2009 | September-2008 | 9 | 2008
20622 | Tolley Road | 2008-09-11 08:11 | 2008-09-11 | 2008-09-11 10:47 | Calculated | T2552 | T2552 - ph 3kVA polemnt |  | 121SEG425-748 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 156 | 1 | 20359 | 156 | 0.00766 | 4.9118e-05 | 8 | 1248 | 2008/2009 | September-2008 | 9 | 2008
20623 | Okahukura Back road | 2008-09-11 10:04 | 2008-09-11 | 2008-09-11 14:04 | Calculated | 5521 | 5521 - Fused Link 5521 |  | No Segment | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 240 | 4 | 20359 | 960 | 0.04715 | 0.00019647 | 32 | 7680 | 2008/2009 | September-2008 | 9 | 2008
20624 | Waitete Road | 2008-09-11 13:43 | 2008-09-11 | 2008-09-11 14:57 | Calculated | T2585 | T2585 - 1ph 10kVA POL |  | 103SEG107-REG7 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 74 | 1 | 20359 | 74 | 0.00363 | 4.9118e-05 | 8 | 592 | 2008/2009 | September-2008 | 9 | 2008
20625 | Haurua Road | 2008-09-11 14:40 | 2008-09-11 | 2008-09-11 17:10 | Calculated | 519 | 519 - Fused Link 519 |  | No Segment | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 20 | 20359 | 3000 | 0.14735 | 0.00098237 | 160 | 24000 | 2008/2009 | September-2008 | 9 | 2008
20626 | Tolley Road | 2008-09-12 08:02 | 2008-09-12 | 2008-09-12 10:55 | Calculated | T1006 | T1006 - 1ph 10kVA polemnt |  | No Segment | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 173 | 1 | 20359 | 173 | 0.0085 | 4.9118e-05 | 8 | 1384 | 2008/2009 | September-2008 | 9 | 2008
20628 | SH 4 | 2008-09-12 10:40 | 2008-09-12 | 2008-09-12 12:12 | Calculated | 06H09 | 06H09 - 1ph 15kVA POLEMNT |  | 402SEG5776 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 3 | 20359 | 276 | 0.01356 | 0.00014735 | 24 | 2208 | 2008/2009 | September-2008 | 9 | 2008
20629 | Ford Road | 2008-09-12 10:50 | 2008-09-12 | 2008-09-12 11:31 | Calculated | T3194 | T3194 - 3ph 15kVA POLEMNT |  | 119SEG785 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 1 | 20359 | 41 | 0.00201 | 4.9118e-05 | 8 | 328 | 2008/2009 | September-2008 | 9 | 2008
20630 | Kakara Road | 2008-09-12 11:36 | 2008-09-12 | 2008-09-12 12:42 | Calculated | 1730 | 1730 - Fused Link 1730 |  | No Segment | No Asset Group | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 8 | 20359 | 528 | 0.02593 | 0.00039295 | 64 | 4224 | 2008/2009 | September-2008 | 9 | 2008
20631 | Waimahora Road | 2008-09-12 13:36 | 2008-09-12 | 2008-09-12 15:57 | Calculated | T1547 | T1547 - 1ph 30kVA POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 1 | 20359 | 141 | 0.00693 | 4.9118e-05 | 8 | 1128 | 2008/2009 | September-2008 | 9 | 2008
20632 | Paparoa Road | 2008-09-12 14:53 | 2008-09-12 | 2008-09-12 15:49 | Calculated | 5368 | 5368 - Sectionaliser with Bypass & Links 5368 |  | 403SEG5622-5368 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 12 | 20359 | 945 | 0.04642 | 0.00058942 | 96 | 7560 | 2008/2009 | September-2008 | 9 | 2008
20634 | Retaruke road | 2008-09-13 17:41 | 2008-09-13 | 2008-09-13 18:53 | Calculated | 5611 | 5611 - Earth Working Link 5611 |  | No Segment | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 8 | 20359 | 576 | 0.02829 | 0.00039295 | 64 | 4608 | 2008/2009 | September-2008 | 9 | 2008
20635 | SH 30 Cnr Pureora Road | 2008-09-14 13:57 | 2008-09-14 | 2008-09-14 14:56 | Calculated | 432 | 432 - ABS 432 |  | No Segment | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 18 | 20359 | 1062 | 0.05216 | 0.00088413 | 144 | 8496 | 2008/2009 | September-2008 | 9 | 2008
20637 | Mokauiti Road E/W Sub | 2008-09-15 10:05 | 2008-09-15 | 2008-09-15 14:46 | Calculated | 1648 | 1648 - Earth Working Link 1648 |  | No Segment | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 5 | 20359 | 1405 | 0.06901 | 0.00024559 | 0 | 0 | 2008/2009 | September-2008 | 9 | 2008
20638 | SH3 Tongaporutu | 2008-09-15 10:13 | 2008-09-15 | 2008-09-15 12:27 | Calculated | T2204 | T2204 - 3ph 25kVA POLEMNT |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 5 | 20359 | 670 | 0.03291 | 0.00024559 | 40 | 5360 | 2008/2009 | September-2008 | 9 | 2008
20639 | Piwari Street | 2008-09-15 10:21 | 2008-09-15 | 2008-09-15 11:11 | Calculated | 20L39 | 20L39 - 5677-5681ph 50kVA POLEMNT |  | 416SEG5677-5681 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 50 | 3 | 20359 | 150 | 0.00737 | 0.00014735 | 24 | 1200 | 2008/2009 | September-2008 | 9 | 2008
20640 | Waimahora Road | 2008-09-15 12:23 | 2008-09-15 | 2008-09-15 15:22 | Calculated | T1289 | T1289 - 1ph 15kVA POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 1 | 20359 | 179 | 0.00879 | 4.9118e-05 | 8 | 1432 | 2008/2009 | September-2008 | 9 | 2008
20641 | Tauraroa Road | 2008-09-15 13:17 | 2008-09-15 | 2008-09-15 15:48 | Calculated | T474 | T474 - 1ph 5kVA POLEMNT |  | 109SEG529-1727 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 1 | 20359 | 151 | 0.00742 | 4.9118e-05 | 8 | 1208 | 2008/2009 | September-2008 | 9 | 2008
20642 | Taipairu Road | 2008-09-16 10:02 | 2008-09-16 | 2008-09-16 14:02 | Calculated | 247 | 247 - ABS 247 |  | No Segment | No Asset Group | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 240 | 36 | 20359 | 8640 | 0.42438 | 0.0017683 | 0 | 0 | 2008/2009 | September-2008 | 9 | 2008
20648 | Manunui Sub | 2008-09-17 06:44 | 2008-09-17 | 2008-09-17 06:53 | Calculated | 6143J | 6143J - Incoming Link 6143J |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  |  |  | 20359 |  | 0 | 0 |  |  | 2008/2009 | September-2008 | 9 | 2008
20646 | Otewa Road | 2008-09-17 10:07 | 2008-09-17 | 2008-09-17 13:45 | Calculated | 329 | 329 - ABS 329 |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 218 | 207 | 20359 | 45126 | 2.2165 | 0.010167 | 1656 | 361008 | 2008/2009 | September-2008 | 9 | 2008
20650 | Western Bay Road | 2008-09-18 07:10 | 2008-09-18 | 2008-09-18 08:30 | Calculated | T1572 | T1572 - 3ph 15kVA polemount |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 2 | 20359 | 160 | 0.00786 | 9.8237e-05 | 16 | 1280 | 2008/2009 | September-2008 | 9 | 2008
20652 | Forestry Road | 2008-09-18 07:59 | 2008-09-18 | 2008-09-18 08:35 | Calculated | 22N01 | 22N01 - 5687ph 15kVA POLEMNT |  | 416SEG5687 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 3 | 20359 | 108 | 0.0053 | 0.00014735 | 24 | 864 | 2008/2009 | September-2008 | 9 | 2008
20653 | Otewa Road | 2008-09-18 08:58 | 2008-09-18 | 2008-09-18 12:48 | Calculated | T614 | T614 - 3ph 15kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 230 | 4 | 20359 | 920 | 0.04519 | 0.00019647 | 32 | 7360 | 2008/2009 | September-2008 | 9 | 2008
20655 | Main South Road | 2008-09-18 09:30 | 2008-09-18 | 2008-09-18 12:13 | Calculated | 10K09 | 10K09 - 1ph 15kVA POLEMNT |  | 409SEG5411-5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 10 | 20359 | 1262 | 0.06199 | 0.00049118 | 80 | 10096 | 2008/2009 | September-2008 | 9 | 2008
20656 | Tauraroa Road | 2008-09-18 14:57 | 2008-09-18 | 2008-09-18 16:01 | Calculated | T137 | T137 - 3ph 30kVA POLEMNT |  | 109SEG529-1727 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 3 | 20359 | 192 | 0.00943 | 0.00014735 | 24 | 1536 | 2008/2009 | September-2008 | 9 | 2008
20647 | SH 30 Benneydale | 2008-09-18 15:03 | 2008-09-18 | 2008-09-18 15:14 | Calculated | T620 | T620 - 3ph 100kVA POL |  | 103SEG1230 | Benneydale 103-07 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 26 | 20359 | 286 | 0.01405 | 0.0012771 | 208 | 2288 | 2008/2009 | September-2008 | 9 | 2008
20657 | Tirohanga Road | 2008-09-18 17:07 | 2008-09-18 | 2008-09-18 18:00 | Calculated | T2761 | T2761 - 3ph 30kVA polemount |  | No Segment | Tihoi 124-04 RETIRED | Rural C | Tihoi | Marotiri Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 4 | 20359 | 212 | 0.01041 | 0.00019647 | 32 | 1696 | 2008/2009 | September-2008 | 9 | 2008
20658 | Scown Road | 2008-09-19 09:39 | 2008-09-19 | 2008-09-19 11:43 | Calculated | T1040 | T1040 - 3ph 15kVA polemnt |  | 111SEG342-544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 124 | 3 | 20359 | 372 | 0.01827 | 0.00014735 | 24 | 2976 | 2008/2009 | September-2008 | 9 | 2008
20660 | Troopers Road | 2008-09-19 12:53 | 2008-09-19 | 2008-09-19 14:42 | Calculated | T1995 | T1995 - 3ph 50kVA POL |  | No Segment | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 109 | 1 | 20359 | 109 | 0.00535 | 4.9118e-05 | 8 | 872 | 2008/2009 | September-2008 | 9 | 2008
20661 | Mangaiti road | 2008-09-19 13:40 | 2008-09-19 | 2008-09-19 16:18 | Calculated | T2769 | T2769 - 1ph 3kVA POL |  | No Segment | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 1 | 20359 | 158 | 0.00776 | 4.9118e-05 | 8 | 1264 | 2008/2009 | September-2008 | 9 | 2008
20662 | Main South Raod | 2008-09-19 16:03 | 2008-09-19 | 2008-09-19 16:21 | Calculated | 10K09 | 10K09 - 1ph 15kVA POLEMNT |  | 409SEG5411-5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 2 | 20359 | 36 | 0.00177 | 9.8237e-05 | 16 | 288 | 2008/2009 | September-2008 | 9 | 2008
20663 | Tawata Road | 2008-09-21 22:37 | 2008-09-21 | 2008-09-22 03:00 | Calculated | 12F02 | 12F02 - 1ph 15kVA POLEMNT |  | 403SEG5313-5541 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 263 | 3 | 20359 | 789 | 0.03875 | 0.00014735 | 24 | 6312 | 2008/2009 | September-2008 | 9 | 2008
20664 | Hohotaka Road | 2008-09-22 09:05 | 2008-09-22 | 2008-09-22 13:47 | Calculated | 5916 | 5916 - Earth Working Link 5916 |  | No Segment | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 22 | 20359 | 6204 | 0.30473 | 0.0010806 | 176 | 49632 | 2008/2009 | September-2008 | 9 | 2008
20666 | Rangitoto road | 2008-09-22 10:06 | 2008-09-22 | 2008-09-22 13:05 | Calculated | 585 | 585 - ABS 585 |  | No Segment | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 179 | 2 | 20359 | 358 | 0.01758 | 9.8237e-05 | 0 | 0 | 2008/2009 | September-2008 | 9 | 2008
20667 | Bayley Road | 2008-09-22 14:40 | 2008-09-22 | 2008-09-22 15:42 | Calculated | T2278 | T2278 - 3ph 30kVA POLEMNT |  | 122SEG616 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 3 | 20359 | 186 | 0.00914 | 0.00014735 | 24 | 1488 | 2008/2009 | September-2008 | 9 | 2008
20668 | Blackman Street | 2008-09-23 05:10 | 2008-09-23 | 2008-09-23 05:53 | Calculated | T1226 | T1226 - 3ph 200kVA GNDPAD |  | 106SEG543-224 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 27 | 20359 | 1161 | 0.05703 | 0.0013262 | 216 | 9288 | 2008/2009 | September-2008 | 9 | 2008
20671 | Opp Chateau turnoff | 2008-09-23 10:16 | 2008-09-23 | 2008-09-23 13:15 | Calculated | 5158 | 5158 - ABS 3 Phase 5158 |  | No Segment | National Park / Kuratau 609-01 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  |  |  | 20359 |  | 0 | 0 |  |  | 2008/2009 | September-2008 | 9 | 2008
20673 | Honikiwi road | 2008-09-23 14:34 | 2008-09-23 | 2008-09-23 15:31 | Calculated | T1239 | T1239 - 1ph 15kVA POLEMNT |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | ETRE2 | 3PAR:ETRE2:ETRE1 | Tree Clearing/Trimming Activities | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 4 | 20359 | 228 | 0.0112 | 0.00019647 | 32 | 1824 | 2008/2009 | September-2008 | 9 | 2008
20676 | Main south Road | 2008-09-24 01:09 | 2008-09-24 | 2008-09-24 15:55 | Calculated | 10K09 | 10K09 - 1ph 15kVA POLEMNT |  | 409SEG5411-5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 886 | 2 | 20359 | 1772 | 0.08704 | 9.8237e-05 | 16 | 14176 | 2008/2009 | September-2008 | 9 | 2008
20677 | Manunui | 2008-09-24 02:10 | 2008-09-24 | 2008-09-24 02:25 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  |  |  | 20359 |  | 0 | 0 |  |  | 2008/2009 | September-2008 | 9 | 2008
20670 | Main south road Otorohanga | 2008-09-24 09:33 | 2008-09-24 | 2008-09-24 15:09 | Calculated | T376 | T376 - 3ph 25kVA POLEMNT |  | 110SEG323-644 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 336 | 5 | 20359 | 1680 | 0.08252 | 0.00024559 | 40 | 13440 | 2008/2009 | September-2008 | 9 | 2008
20681 | Manunui Sub | 2008-09-27 00:27 | 2008-09-27 | 2008-09-27 00:36 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  |  |  | 20359 |  | 0 | 0 |  |  | 2008/2009 | September-2008 | 9 | 2008
20682 | Turakina Valley Road | 2008-09-27 17:46 | 2008-09-27 | 2008-09-27 20:45 | Calculated | 6174 | 6174 - Recloser 6174 |  | 416SEG5711-6174 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 179 | 32 | 20359 | 5728 | 0.28135 | 0.0015718 | 256 | 45824 | 2008/2009 | September-2008 | 9 | 2008
20683 | Turakina Valley road | 2008-09-27 21:14 | 2008-09-27 | 2008-09-27 23:48 | Calculated | 6174 | 6174 - Recloser 6174 |  | 416SEG5711-6174 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 154 | 32 | 20359 | 4928 | 0.24206 | 0.0015718 | 256 | 39424 | 2008/2009 | September-2008 | 9 | 2008
20684 | Kirikau Sub | 2008-09-29 03:05 | 2008-09-29 | 2008-09-29 09:27 | Calculated | 5378 | 5378 - Recloser with Bypass & Links 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 382 | 37 | 20359 | 14134 | 0.69424 | 0.0018174 | 0 | 0 | 2008/2009 | September-2008 | 9 | 2008
20689 | Mangaohutu Road | 2008-10-01 08:32 | 2008-10-01 | 2008-10-01 11:11 | Calculated | 11F02 | 11F02 - 1ph 15kVA POLEMNT |  | 403SEG5313-5541 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related |  |  | Ageing or Wear of Equipment | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 159 | 2 | 20330 | 318 | 0.01564 | 9.8377e-05 | 16 | 2544 | 2008/2009 | October-2008 | 10 | 2008
20688 | Rangiatea - By Wolver's | 2008-10-01 10:55 | 2008-10-01 | 2008-10-01 13:16 | Calculated | 348 | 348 - ABS 348 |  | No Segment | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 147 | 61 | 20330 | 8913 | 0.43842 | 0.0030005 | 488 | 71304 | 2008/2009 | October-2008 | 10 | 2008
20692 | Tahaia road | 2008-10-02 10:05 | 2008-10-02 | 2008-10-02 10:11 | Calculated | 341 | 341 - Fused Link 341 |  | No Segment | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 27 | 20330 | 6340 | 0.31185 | 0.0013281 | 0 | 0 | 2008/2009 | October-2008 | 10 | 2008
20696 | Tihoi Road | 2008-10-05 07:40 | 2008-10-05 | 2008-10-05 10:37 | Calculated | T2644 | T2644 - 3ph 25kVA polemount |  | No Segment | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause |  |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 1 | 20330 | 177 | 0.00871 | 4.9188e-05 | 8 | 1416 | 2008/2009 | October-2008 | 10 | 2008
20697 | Ongarue Village Road | 2008-10-05 10:52 | 2008-10-05 | 2008-10-05 12:10 | Calculated | 5669 | 5669 - Earth Working Link 5669 |  | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 44 | 20330 | 3432 | 0.16881 | 0.0021643 | 352 | 27456 | 2008/2009 | October-2008 | 10 | 2008
20698 | Kirtons Road | 2008-10-05 11:43 | 2008-10-05 | 2008-10-05 11:55 | Calculated | 5284 | 5284 - Fused Link 5284 |  | No Segment | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related |  |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 11 | 20330 | 132 | 0.00649 | 0.00054107 | 88 | 1056 | 2008/2009 | October-2008 | 10 | 2008
20699 | Taharoa on sand | 2008-10-06 07:27 | 2008-10-06 | 2008-10-06 12:36 | Calculated | 509 | 509 - Fused Link 509 |  | No Segment | Rural 126-02 | Rural D | Rural | Taharoa Zone Substation |  | Asset Related |  |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 309 | 9 | 20330 | 2781 | 0.13679 | 0.0004427 | 72 | 22248 | 2008/2009 | October-2008 | 10 | 2008
20700 | Otunui Sub | 2008-10-06 09:04 | 2008-10-06 | 2008-10-06 09:06 | Calculated | 5375 | 5375 - Recloser with Bypass & Links 5375 |  | 403SEG5375-5887 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 69 | 20330 | 6832 | 0.33606 | 0.003394 | 0 | 0 | 2008/2009 | October-2008 | 10 | 2008
20702 | SH 40 | 2008-10-06 14:15 | 2008-10-06 | 2008-10-06 17:56 | Calculated | 5574 | 5574 - Fused Link 5574 |  | 421SEG5574 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related |  |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 5 | 20330 | 1105 | 0.05435 | 0.00024594 | 40 | 8840 | 2008/2009 | October-2008 | 10 | 2008
20703 | Karangahape Road ISO Sub | 2008-10-06 17:03 | 2008-10-06 | 2008-10-06 18:31 | Calculated | 5847 | 5847 - FusedLink 5847 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause |  |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1818 | 49 | 20330 | 6707 | 0.32991 | 0.0024102 | 0 | 0 | 2008/2009 | October-2008 | 10 | 2008
20716 | MANGATEITEI ROAD | 2008-10-07 09:35 | 2008-10-07 | 2008-10-07 10:32 | Calculated | 5693 | 5693 - Fused Link 5693 |  | No Segment | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 29 | 20330 | 1653 | 0.08131 | 0.0014265 | 232 | 13224 | 2008/2009 | October-2008 | 10 | 2008
20717 | MANUNUI SUB | 2008-10-07 10:07 | 2008-10-07 | 2008-10-07 12:03 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | Taumarunui / Kuratau 608-01 | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 116 | 389 | 20330 | 55195 | 2.7149 | 0.019134 | 2082.5 | 324557 | 2008/2009 | October-2008 | 10 | 2008
20719 | SH3 bY 22KV SUBSTATION | 2008-10-07 13:23 | 2008-10-07 | 2008-10-07 15:07 | Calculated | 1524 | 1524 - ABS 1524 |  | No Segment | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 597 | 20330 | 62088 | 3.054 | 0.029365 | 4776 | 496704 | 2008/2009 | October-2008 | 10 | 2008
20720 | SH 3 Pastoral Holdings | 2008-10-07 13:42 | 2008-10-07 | 2008-10-07 14:36 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 6 | 20330 | 324 | 0.01594 | 0.00029513 | 48 | 2592 | 2008/2009 | October-2008 | 10 | 2008
20721 | Owne's Road | 2008-10-07 13:47 | 2008-10-07 | 2008-10-07 14:53 | Calculated | 1708 | 1708 - Fused Link 1708 |  | No Segment | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 18 | 20330 | 1188 | 0.05844 | 0.00088539 | 144 | 9504 | 2008/2009 | October-2008 | 10 | 2008
20705 | Taumatatotoro West | 2008-10-07 13:50 | 2008-10-07 | 2008-10-07 23:21 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 571 | 8 | 20330 | 4568 | 0.22469 | 0.00039351 | 64 | 36544 | 2008/2009 | October-2008 | 10 | 2008
20722 | Smiths road | 2008-10-07 14:08 | 2008-10-07 | 2008-10-07 15:54 | Calculated | T2238 | T2238 - 3ph 25kVA POLEMNT |  | 110SEG642-343 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 2 | 20330 | 212 | 0.01043 | 9.8377e-05 | 16 | 1696 | 2008/2009 | October-2008 | 10 | 2008
20707 |  | 2008-10-07 14:15 | 2008-10-07 | 2008-10-07 20:04 | Calculated | 42101N01 | 42101N01 - 1ph 15kVA POLEMNT |  | 421SEG5933 | Ongarue 421-04 |  | Ongarue | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 349 | 3 | 20330 | 1047 | 0.0515 | 0.00014757 | 24 | 8376 | 2008/2009 | October-2008 | 10 | 2008
20723 | Spicers Road | 2008-10-07 15:05 | 2008-10-07 | 2008-10-07 16:49 | Calculated | 1344 | 1344 - Fused Link 1344 |  | No Segment | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 7 | 20330 | 728 | 0.03581 | 0.00034432 | 56 | 5824 | 2008/2009 | October-2008 | 10 | 2008
20724 | Tumutumu road | 2008-10-07 15:10 | 2008-10-07 | 2008-10-07 16:17 | Calculated | 109 | 109 - Recloser with bypass 109 |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1022 | 310 | 20330 | 42735 | 2.1021 | 0.015248 | 2480 | 341880 | 2008/2009 | October-2008 | 10 | 2008
20728 | Te Raumauku Road | 2008-10-07 15:40 | 2008-10-07 | 2008-10-07 17:52 | Calculated | 355 | 355 - Fused Link 355 |  | No Segment | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 9 | 20330 | 1188 | 0.05844 | 0.0004427 | 72 | 9504 | 2008/2009 | October-2008 | 10 | 2008
20725 | SH# Pastoral Holdings | 2008-10-07 15:57 | 2008-10-07 | 2008-10-07 17:13 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 6 | 20330 | 456 | 0.02243 | 0.00029513 | 48 | 3648 | 2008/2009 | October-2008 | 10 | 2008
20730 | Piri Piri Substation | 2008-10-07 16:52 | 2008-10-07 | 2008-10-07 18:19 | Calculated | 114 | 114 - 11kV Oil Circuit Breaker with Bypass 114 |  | No Segment | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2926 | 313 | 20330 | 44410 | 2.1845 | 0.015396 | 2504 | 355280 | 2008/2009 | October-2008 | 10 | 2008
20708 | Mapara South road | 2008-10-07 17:25 | 2008-10-07 | 2008-10-08 14:21 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | EENF2 | WEAT:EENF2:EENF1 | Flood / Washout | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1256 | 13 | 20330 | 16328 | 0.80315 | 0.00063945 | 0 | 0 | 2008/2009 | October-2008 | 10 | 2008
20709 | aotearoa Road | 2008-10-07 17:32 | 2008-10-07 | 2008-10-08 00:07 | Calculated | 378 | 378 - Recloser with Bypass & Links 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 252 | 20330 | 7588 | 0.37324 | 0.012395 | 2016 | 60704 | 2008/2009 | October-2008 | 10 | 2008
20735 | River road | 2008-10-08 11:18 | 2008-10-08 | 2008-10-08 11:58 | Calculated | 09E14 | 09E14 - 1ph 30kVA POLEMNT |  | No Segment | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  |  |  | 20330 |  | 0 | 0 |  |  | 2008/2009 | October-2008 | 10 | 2008
20711 | Lees block Road | 2008-10-08 17:40 | 2008-10-08 | 2008-10-08 22:29 | Calculated | T78 | T78 - 1ph 25kVA POL |  | No Segment | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 289 | 5 | 20330 | 1445 | 0.07108 | 0.00024594 | 40 | 11560 | 2008/2009 | October-2008 | 10 | 2008
20712 | MAPARA ROAD | 2008-10-09 01:51 | 2008-10-09 | 2008-10-09 03:00 | Calculated | 11S18 | 11S18 - 3ph 300kVA GNDPAD |  | No Segment | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 12 | 20330 | 828 | 0.04073 | 0.00059026 | 96 | 6624 | 2008/2009 | October-2008 | 10 | 2008
20714 | MAHOENUI | 2008-10-09 04:19 | 2008-10-09 | 2008-10-09 06:36 | Calculated | 1010 | 1010 - Mahoenui Oil Circuit Breaker 1010 |  | No Segment | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDI | Conductor Failure - Insulated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 203 | 519 | 20330 | 102225 | 5.0283 | 0.025529 | 0 | 0 | 2008/2009 | October-2008 | 10 | 2008
20738 | Ngapaenga Road | 2008-10-09 06:55 | 2008-10-09 | 2008-10-09 07:45 | Calculated | T576 | T576 - 1ph 10kVA POLEMNT |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 2 | 20330 | 100 | 0.00492 | 9.8377e-05 | 16 | 800 | 2008/2009 | October-2008 | 10 | 2008
20743 | Hirangi Sub | 2008-10-10 11:45 | 2008-10-10 | 2008-10-10 12:43 | Calculated | 5519 | 5519 - Circuit Breaker with Bypass & Links 5519 |  | No Segment | Hirangi 405-01 | Urban A | Hirangi | Awamate Zone Substation (Containerised) |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 21 | 20330 | 1218 | 0.05991 | 0.001033 | 168 | 9744 | 2008/2009 | October-2008 | 10 | 2008
20746 | SH 40 Mangakara | 2008-10-13 17:05 | 2008-10-13 | 2008-10-13 18:41 | Calculated | 5304 | 5304 - Sectionaliser with Bypass & Links 5304 |  | 413SEG5420-5305 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 5 | 20330 | 480 | 0.02361 | 0.00024594 | 40 | 3840 | 2008/2009 | October-2008 | 10 | 2008
20747 | River Road | 2008-10-14 09:36 | 2008-10-14 | 2008-10-14 09:45 | Calculated | 09E14 | 09E14 - 1ph 30kVA POLEMNT |  | No Segment | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  |  |  | 20330 |  | 0 | 0 |  |  | 2008/2009 | October-2008 | 10 | 2008
20749 | SH 47 | 2008-10-15 11:50 | 2008-10-15 | 2008-10-15 13:03 | Calculated | 14M03 | 14M03 - 3ph 100kVA gndpad |  | No Segment | National Park 411-02 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 3 | 20330 | 219 | 0.01077 | 0.00014757 | 24 | 1752 | 2008/2009 | October-2008 | 10 | 2008
20752 | SH 40 MANGAKARA | 2008-10-15 15:50 | 2008-10-15 | 2008-10-15 17:10 | Calculated | 5304 | 5304 - Sectionaliser with Bypass & Links 5304 |  | 413SEG5420-5305 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 5 | 20330 | 400 | 0.01968 | 0.00024594 | 40 | 3200 | 2008/2009 | October-2008 | 10 | 2008
20753 | SH 40 MANGAKARA | 2008-10-16 06:47 | 2008-10-16 | 2008-10-16 08:48 | Calculated | 5304 | 5304 - Sectionaliser with Bypass & Links 5304 |  | 413SEG5420-5305 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 10 | 20330 | 830 | 0.04083 | 0.00049188 | 80 | 6640 | 2008/2009 | October-2008 | 10 | 2008
20755 | Te puke Road | 2008-10-16 10:25 | 2008-10-16 | 2008-10-16 11:19 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 2 | 20330 | 108 | 0.00531 | 9.8377e-05 | 16 | 864 | 2008/2009 | October-2008 | 10 | 2008
20757 | Barbers road | 2008-10-16 17:15 | 2008-10-16 | 2008-10-16 18:30 | Calculated | T2795 | T2795 - 3ph 30kVA POLEMNT |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 20330 | 75 | 0.00369 | 4.9188e-05 | 8 | 600 | 2008/2009 | October-2008 | 10 | 2008
20759 | Okau E/W/ Sub | 2008-10-17 16:00 | 2008-10-17 | 2008-10-17 19:11 | Calculated | 1630 | 1630 - Recloser with Bypass & Links 1630 |  | No Segment | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 39 | 20330 | 7449 | 0.3664 | 0.0019183 | 312 | 59592 | 2008/2009 | October-2008 | 10 | 2008
20760 | Haurua road | 2008-10-18 07:47 | 2008-10-18 | 2008-10-18 08:10 | Calculated | T1029 | T1029 - 3ph 25kVA POL |  | No Segment | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 3 | 20330 | 69 | 0.00339 | 0.00014757 | 24 | 552 | 2008/2009 | October-2008 | 10 | 2008
20761 | Waimiha | 2008-10-18 08:10 | 2008-10-18 | 2008-10-18 10:49 | Calculated | 5355 | 5355 - Sectionaliser with Bypass & Links 5355 |  | 421SEG5355-5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 753 | 51 | 20330 | 8848 | 0.43522 | 0.0025086 | 408 | 70784 | 2008/2009 | October-2008 | 10 | 2008
20764 | Whangamata road | 2008-10-18 19:05 | 2008-10-18 | 2008-10-18 20:26 | Calculated | 469 | 469 - Fused Link 469 |  | No Segment | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 9 | 20330 | 729 | 0.03586 | 0.0004427 | 72 | 5832 | 2008/2009 | October-2008 | 10 | 2008
20765 | Otuni / Kirikau sub | 2008-10-19 11:15 | 2008-10-19 | 2008-10-19 11:56 | Calculated | 5316 | 5316 - Sectionaliser with Bypass & Links 5316 |  | 403SEG5377-5378 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 26 | 20330 | 1066 | 0.05243 | 0.0012789 | 208 | 8528 | 2008/2009 | October-2008 | 10 | 2008
20782 | Kutai Street | 2008-10-20 09:35 | 2008-10-20 | 2008-10-20 12:06 | Calculated | 11S20 | 11S20 - 3ph 200kVA GNDPAD |  | No Segment | No Asset Group | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 151 | 29 | 20330 | 4379 | 0.2154 | 0.0014265 | 232 | 35032 | 2008/2009 | October-2008 | 10 | 2008
20783 | Otewa Road | 2008-10-20 10:00 | 2008-10-20 | 2008-10-20 10:30 | Calculated | T399 | T399 - 1ph 15kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 30 | 2 | 20330 | 60 | 0.00295 | 9.8377e-05 | 16 | 480 | 2008/2009 | October-2008 | 10 | 2008
20784 | Otunui Sub | 2008-10-21 09:02 | 2008-10-21 | 2008-10-21 09:04 | Calculated | 5375X | 5375X - Outgoing Link 5375X |  | 403SEG5375-5887 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 301 | 69 | 20330 | 20905 | 1.0283 | 0.003394 | 0 | 0 | 2008/2009 | October-2008 | 10 | 2008
20786 | Waitanguru | 2008-10-21 10:03 | 2008-10-21 | 2008-10-21 11:55 | Calculated | 1531 | 1531 - Sectionaliser 1531 |  | 113SEG1531-1501 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 17 | 20330 | 1904 | 0.09365 | 0.0008362 | 136 | 15232 | 2008/2009 | October-2008 | 10 | 2008
20995 | Kirikau Valley | 2008-10-22 09:50 | 2008-10-22 | 2008-10-22 15:17 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 15 | 20330 | 4905 | 0.24127 | 0.00073783 | 120 | 39240 | 2008/2009 | October-2008 | 10 | 2008
20996 | Maraetai substation | 2008-10-23 03:45 | 2008-10-23 | 2008-10-23 03:55 | Calculated | 2082 | 2082 - Maraetai Sub Feeder CB 2082 | Mangakino | No Segment | 210-01 Maraetai | Rural D | Mangakino | Maraetai Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 443 | 20330 | 30920 | 1.5209 | 0.02179 | 0 | 0 | 2008/2009 | October-2008 | 10 | 2008
20998 | Mangakahu Valley | 2008-10-23 09:52 | 2008-10-23 | 2008-10-23 09:54 | Calculated | 5342 | 5342 - Earth Working Link 5342 | Ongarue | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 439 | 27 | 20330 | 4101 | 0.20172 | 0.0013281 | 216 | 32808 | 2008/2009 | October-2008 | 10 | 2008
21000 | Kuku Street | 2008-10-24 22:04 | 2008-10-24 | 2008-10-24 22:13 | Calculated | 1354 | 1354 - Circuit Breaker with Bypass & Links 1354 | earthing fault | 116SEG1341-1354 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 67 | 20330 | 603 | 0.02966 | 0.0032956 | 536 | 4824 | 2008/2009 | October-2008 | 10 | 2008
20999 | Arahori Street | 2008-10-25 | 2008-10-25 | 2008-10-25 13:04 | Calculated | 10S16 | 10S16 - 3ph 200kVA CONC-MNT | TF10S16 - Transformer Fuse: TF10S16 | No Segment | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Fuse Carriers | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 784 | 14 | 20330 | 896 | 0.04407 | 0.00068864 | 0 | 0 | 2008/2009 | October-2008 | 10 | 2008
21001 | S.H. 47 | 2008-10-25 08:10 | 2008-10-25 | 2008-10-25 10:30 | Calculated | 14M03 | 14M03 - 3ph 100kVA gndpad | TF14M3 - Transformer Fuse: TF14M3 | No Segment | National Park 411-02 | Rural D | National Park | National Park Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 3 | 20330 | 420 | 0.02066 | 0.00014757 | 24 | 3360 | 2008/2009 | October-2008 | 10 | 2008
21002 | Aria Road | 2008-10-25 11:00 | 2008-10-25 | 2008-10-25 12:10 | Calculated | T2250 | T2250 - 1ph 10kVA POLEMNT | t2250 | 116SEG1355-1327 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 4 | 20330 | 280 | 0.01377 | 0.00019675 | 32 | 2240 | 2008/2009 | October-2008 | 10 | 2008
21003 | Oio Road | 2008-10-25 17:15 | 2008-10-25 | 2008-10-26 18:35 | Calculated | 12J02 | 12J02 - 1ph 15kVA POLEMNT | TF12J2 - Transformer Fuse: TF12J2 | 409SEG5748-5743 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1520 | 4 | 20330 | 6080 | 0.29907 | 0.00019675 | 32 | 48640 | 2008/2009 | October-2008 | 10 | 2008
21004 | Poihipi Road | 2008-10-26 00:09 | 2008-10-26 | 2008-10-26 01:13 | Calculated | 471 | 471 - Fused Link 471 | lightening arrester | No Segment | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 10 | 20330 | 640 | 0.03148 | 0.00049188 | 80 | 5120 | 2008/2009 | October-2008 | 10 | 2008
21005 | Waverley Road | 2008-10-26 09:36 | 2008-10-26 | 2008-10-26 10:20 | Calculated | T2239 | T2239 - 3ph 30kVA polemnt | LV Line down | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 2 | 20330 | 88 | 0.00433 | 9.8377e-05 | 16 | 704 | 2008/2009 | October-2008 | 10 | 2008
21006 | Echolands - Water Treatment | 2008-10-26 15:30 | 2008-10-26 | 2008-10-26 16:10 | Calculated | 1.27 | 1.27 - Fused Link 1.27 |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 6 | 20330 | 240 | 0.01181 | 0.00029513 | 48 | 1920 | 2008/2009 | October-2008 | 10 | 2008
21007 | Te Waireka Road | 2008-10-26 17:38 | 2008-10-26 | 2008-10-26 17:46 | Calculated | 124 | 124 - Oil Circuit Breaker 124 | Over currant | No Segment | 203-01 Te Waireka Road | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 1550 | 20330 | 10850 | 0.53369 | 0.076242 | 12400 | 86800 | 2008/2009 | October-2008 | 10 | 2008
21008 | Opp Chateau Turn off | 2008-10-28 09:33 | 2008-10-28 | 2008-10-28 15:49 | Calculated | 5158 | 5158 - ABS 3 Phase 5158 |  | No Segment | National Park / Kuratau 609-01 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  |  |  | 20330 |  | 0 | 0 |  |  | 2008/2009 | October-2008 | 10 | 2008
21009 | Paerata Road | 2008-10-28 10:03 | 2008-10-28 | 2008-10-28 14:54 | Calculated | 1407 | 1407 - Fused Link 1407 |  | No Segment | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 291 |  | 20330 |  | 0 | 0 | 0 |  | 2008/2009 | October-2008 | 10 | 2008
21010 | Near tunnel - By telecom R | 2008-10-29 10:05 | 2008-10-29 | 2008-10-29 10:11 | Calculated | 1603 | 1603 - Circuit Breaker 1603 |  | No Segment | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 6 | 1164 | 20330 | 5820 | 0.28628 | 0.057255 | 9312 | 46560 | 2008/2009 | October-2008 | 10 | 2008
21012 | Poihipi road | 2008-10-29 11:05 | 2008-10-29 | 2008-10-29 13:28 | Calculated | T1159 | T1159 - 1ph 15kVA POLEMNT |  | 123SEG699-1267 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 143 | 3 | 20330 | 429 | 0.0211 | 0.00014757 | 24 | 3432 | 2008/2009 | October-2008 | 10 | 2008
21016 | Kutai street | 2008-10-31 09:30 | 2008-10-31 | 2008-10-31 14:38 | Calculated | 11S20 | 11S20 - 3ph 200kVA GNDPAD |  | No Segment | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 308 | 30 | 20330 | 9240 | 0.4545 | 0.0014757 | 240 | 73920 | 2008/2009 | October-2008 | 10 | 2008
21017 | Poihipi Road | 2008-10-31 10:03 | 2008-10-31 | 2008-10-31 14:21 | Calculated | T1159 | T1159 - 1ph 15kVA POLEMNT |  | 123SEG699-1267 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 3 | 20330 | 774 | 0.03807 | 0.00014757 | 24 | 6192 | 2008/2009 | October-2008 | 10 | 2008
21018 | Scown Road | 2008-10-31 11:05 | 2008-10-31 | 2008-10-31 13:40 | Calculated | T1005 | T1005 - 3ph 25kVA polemnt |  | 5ZADPW | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 155 | 1 | 20330 | 155 | 0.00762 | 4.9188e-05 | 8 | 1240 | 2008/2009 | October-2008 | 10 | 2008
21020 | Haurua road | 2008-11-02 04:10 | 2008-11-02 | 2008-11-02 05:12 | Calculated | 519 | 519 - Fused Link 519 | 519 - Fused Link 519 | No Segment | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 20 | 24153 | 1240 | 0.05134 | 0.00082805 | 160 | 9920 | 2008/2009 | November-2008 | 11 | 2008
21025 | Aira Road | 2008-11-03 08:35 | 2008-11-03 | 2008-11-03 09:17 | Calculated | T1726 | T1726 - 2ph 25kVA POLEMNT | TF1726 - Transformer Fuse: TF1726 | 116SEG1327-1340 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 2 | 24153 | 84 | 0.00348 | 8.2805e-05 | 16 | 672 | 2008/2009 | November-2008 | 11 | 2008
21026 | barbers Road | 2008-11-03 09:55 | 2008-11-03 | 2008-11-03 11:16 | Calculated | T2795 | T2795 - 3ph 30kVA POLEMNT |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 1 | 24153 | 81 | 0.00335 | 4.1403e-05 | 8 | 648 | 2008/2009 | November-2008 | 11 | 2008
21027 | Rangitoto Road | 2008-11-03 09:56 | 2008-11-03 | 2008-11-03 16:13 | Calculated | 1757 | 1757 - Fused Link 1757 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 377 | 2 | 24153 | 754 | 0.03122 | 8.2805e-05 | 16 | 6032 | 2008/2009 | November-2008 | 11 | 2008
21029 | Otukou Sub | 2008-11-03 10:45 | 2008-11-03 | 2008-11-03 13:11 | Calculated | 5589 | 5589 - Fused Link 5589 |  | 418SEG5589-5584 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 146 | 73 | 24153 | 10658 | 0.44127 | 0.0030224 | 584 | 85264 | 2008/2009 | November-2008 | 11 | 2008
21030 | Waitomo Valley Road | 2008-11-04 08:15 | 2008-11-04 | 2008-11-04 09:20 | Calculated | T256 | T256 - 3ph 15kVA POLEMNT | TF256 | 112SEG326-288 | Otorohanga 112-06 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 3 | 24153 | 195 | 0.00807 | 0.00012421 | 24 | 1560 | 2008/2009 | November-2008 | 11 | 2008
21035 | Sircombe Road | 2008-11-05 10:00 | 2008-11-05 | 2008-11-05 10:28 | Calculated | 522 | 522 - ABS 522 | jumper off pole | No Segment | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Bare ACSR | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 52 | 24153 | 1456 | 0.06028 | 0.0021529 | 416 | 11648 | 2008/2009 | November-2008 | 11 | 2008
21040 | Taharoa Road | 2008-11-05 10:15 | 2008-11-05 | 2008-11-05 11:43 | Calculated | T533 | T533 - 1ph 25kVA POL | TF 533 | 125SEG277-268 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 3 | 24153 | 264 | 0.01093 | 0.00012421 | 24 | 2112 | 2008/2009 | November-2008 | 11 | 2008
21038 | Hangatiki | 2008-11-05 10:46 | 2008-11-05 | 2008-11-05 10:48 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  |  |  | 24153 |  | 0 | 0 |  |  | 2008/2009 | November-2008 | 11 | 2008
21041 | Aotearoa Road | 2008-11-05 11:48 | 2008-11-05 | 2008-11-05 11:51 | Calculated | 378 | 378 - Recloser with Bypass & Links 378 | 380 - ABS 380 | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 220 | 204 | 24153 | 11013 | 0.45597 | 0.0084462 | 0 | 0 | 2008/2009 | November-2008 | 11 | 2008
21042 | Cottles Road | 2008-11-05 14:30 | 2008-11-05 | 2008-11-05 16:00 | Calculated | T271 | T271 - 3ph 30kVA polemnt | TF271 | 113SEG1336-1337 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 3 | 24153 | 270 | 0.01118 | 0.00012421 | 24 | 2160 | 2008/2009 | November-2008 | 11 | 2008
21043 | Paparoa Road | 2008-11-05 15:40 | 2008-11-05 | 2008-11-05 19:28 | Calculated | 5368 | 5368 - Sectionaliser with Bypass & Links 5368 | FED403 - Western | 403SEG5622-5368 | Western 403-06 | Rural D | Western | Borough Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 228 | 12 | 24153 | 2736 | 0.11328 | 0.00049683 | 96 | 21888 | 2008/2009 | November-2008 | 11 | 2008
21044 | SH 46 | 2008-11-05 16:45 | 2008-11-05 | 2008-11-05 18:58 | Calculated | 12P03 | 12P03 - 1ph 15kVA POLEMNT | TF12P03 | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 4 | 24153 | 532 | 0.02203 | 0.00016561 | 32 | 4256 | 2008/2009 | November-2008 | 11 | 2008
21045 | Manunui Sub | 2008-11-05 22:53 | 2008-11-05 | 2008-11-05 23:04 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  |  |  | 24153 |  | 0 | 0 |  |  | 2008/2009 | November-2008 | 11 | 2008
21046 | Tihoi Road | 2008-11-05 22:57 | 2008-11-05 | 2008-11-06 00:29 | Calculated | 2102 | 2102 - Mareatai 11 kV feeder 2102 |  | No Segment | 210-01 Maraetai | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 309 | 24153 | 37128 | 1.5372 | 0.012793 | 1632 | 297024 | 2008/2009 | November-2008 | 11 | 2008
21047 | Maihiihi Road | 2008-11-06 05:30 | 2008-11-06 | 2008-11-06 06:45 | Calculated | T349 | T349 - 3ph 25kVA polemnt |  | 111SEG346-REG6 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 2 | 24153 | 150 | 0.00621 | 8.2805e-05 | 16 | 1200 | 2008/2009 | November-2008 | 11 | 2008
21048 | Hikumutu Road | 2008-11-06 07:18 | 2008-11-06 | 2008-11-06 07:56 | Calculated | 01A72 | 01A72 - 3ph 50kVA POLEMNT |  | No Segment | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BCMS | Bird Contact Mid-span / Wire Clash | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 3 | 24153 | 114 | 0.00472 | 0.00012421 | 24 | 912 | 2008/2009 | November-2008 | 11 | 2008
21050 | Poihipi Road | 2008-11-06 10:00 | 2008-11-06 | 2008-11-06 16:12 | Calculated | 699 | 699 - Solid Link 699 |  | 123SEG699-1267 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 372 | 13 | 24153 | 4836 | 0.20022 | 0.00053824 | 104 | 38688 | 2008/2009 | November-2008 | 11 | 2008
21052 | Ranginui Road | 2008-11-06 10:31 | 2008-11-06 | 2008-11-06 14:15 | Calculated | 487 | 487 - ABS 487 |  | No Segment | Huirimu 121-04 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 224 | 7 | 24153 | 1568 | 0.06492 | 0.00028982 | 56 | 12544 | 2008/2009 | November-2008 | 11 | 2008
21054 | Marakopa Road | 2008-11-07 00:45 | 2008-11-07 | 2008-11-07 04:40 | Calculated | 187 | 187 - Fused Link 187 | broken DDO | 125SEG187 | Coast 125-04 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 235 | 168 | 24153 | 13110 | 0.54279 | 0.0069557 | 1344 | 104880 | 2008/2009 | November-2008 | 11 | 2008
21055 | Borough Sub | 2008-11-07 06:31 | 2008-11-07 | 2008-11-07 06:42 | Calculated | 5992 | 5992 - 33kV Oil Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 980 | 24153 | 10780 | 0.44632 | 0.040575 | 0 | 0 | 2008/2009 | November-2008 | 11 | 2008
21056 | Lees Block Road | 2008-11-07 10:17 | 2008-11-07 | 2008-11-07 11:12 | Calculated | T78 | T78 - 1ph 25kVA POL |  | 101SEG248 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 5 | 24153 | 275 | 0.01139 | 0.00020701 | 40 | 2200 | 2008/2009 | November-2008 | 11 | 2008
21057 | Ohura Road | 2008-11-07 12:30 | 2008-11-07 | 2008-11-07 13:45 | Calculated | 05F15 | 05F15 - 1ph 10kVA POLEMNT | TF5F15 - Transformer Fuse: TF5F15 | 422SEG5618-5272 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 24153 | 75 | 0.00311 | 4.1403e-05 | 8 | 600 | 2008/2009 | November-2008 | 11 | 2008
21058 | Waihora road | 2008-11-10 08:30 | 2008-11-10 | 2008-11-10 11:30 | Calculated | 436 | 436 - Solid Link 436 | 436 - Solid Link 436 | 123SEG436 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 4 | 24153 | 720 | 0.02981 | 0.00016561 | 32 | 5760 | 2008/2009 | November-2008 | 11 | 2008
21064 | Pihanga Saddle Road | 2008-11-11 07:21 | 2008-11-11 | 2008-11-11 10:01 | Calculated | 5590 | 5590 - Earth Working Link 5590 | 12P04 - 1ph 25kVA POLEMNT | 418SEG5590-5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 8 | 24153 | 1280 | 0.053 | 0.00033122 | 64 | 10240 | 2008/2009 | November-2008 | 11 | 2008
21067 | Otewa Road | 2008-11-11 10:00 | 2008-11-11 | 2008-11-11 13:42 | Calculated | 118 | 118 - Circuit Breaker with Bypass & Links 118 |  | 109SEG118-329 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 222 | 43 | 24153 | 9546 | 0.39523 | 0.0017803 | 0 | 0 | 2008/2009 | November-2008 | 11 | 2008
21068 | Mokauiti Road | 2008-11-11 10:17 | 2008-11-11 | 2008-11-11 14:01 | Calculated | 1648 | 1648 - Earth Working Link 1648 |  | 115SEG1648-1716 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 224 | 56 | 24153 | 12544 | 0.51936 | 0.0023186 | 448 | 100352 | 2008/2009 | November-2008 | 11 | 2008
21069 | Waikino Road | 2008-11-12 08:40 | 2008-11-12 | 2008-11-12 10:07 | Calculated | 426 | 426 - Sectionaliser with Bypass & Links 426 |  | 129SEG434-426 | Tihoi 124-03 RETIRED | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 79 | 24153 | 6873 | 0.28456 | 0.0032708 | 0 | 0 | 2008/2009 | November-2008 | 11 | 2008
21074 | Forest Road | 2008-11-12 12:10 | 2008-11-12 | 2008-11-12 17:11 | Calculated | T2695 | T2695 - 3ph 15kVA POLEMNT | t2695 | 123SEG695RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 301 | 1 | 24153 | 301 | 0.01246 | 4.1403e-05 | 8 | 2408 | 2008/2009 | November-2008 | 11 | 2008
21076 | Marotiri Sub | 2008-11-12 14:10 | 2008-11-12 | 2008-11-12 14:48 | Calculated | 700 | 700 - ABS 700 | faulty LA | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation | Transformers : Other | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 271 | 24153 | 9921 | 0.41076 | 0.01122 | 2168 | 79368 | 2008/2009 | November-2008 | 11 | 2008
21078 | Hakiaha street | 2008-11-12 23:12 | 2008-11-12 | 2008-11-13 01:47 | Calculated | 5007 | 5007 - FUSE SWITCH |  | No Segment | Hakiaha 401-01 | Urban A | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 155 | 22 | 24153 | 3410 | 0.14118 | 0.00091086 | 176 | 27280 | 2008/2009 | November-2008 | 11 | 2008
21079 | Otewa Road | 2008-11-14 10:00 | 2008-11-14 | 2008-11-14 14:51 | Calculated | T1208 | T1208 - 3ph 15kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 291 | 6 | 24153 | 1650 | 0.06831 | 0.00024842 | 0 | 0 | 2008/2009 | November-2008 | 11 | 2008
21080 | Te Kura Road | 2008-11-14 20:08 | 2008-11-14 | 2008-11-14 20:50 | Calculated | 383 | 383 - Fused Link 383 | TF993 - Transformer Fuse: TF993 | 110SEG383 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 14 | 24153 | 588 | 0.02434 | 0.00057964 | 112 | 4704 | 2008/2009 | November-2008 | 11 | 2008
21082 | Kaimanawa Street | 2008-11-17 06:20 | 2008-11-17 | 2008-11-17 11:27 | Calculated | 5913 | 5913 - Solid Link 5913 | 08R18 - 3ph 200kVA GNDPAD | 406SEG5913-6599 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 326 | 369 | 24153 | 62269 | 2.5781 | 0.015278 | 2952 | 498152 | 2008/2009 | November-2008 | 11 | 2008
21085 | Tahaia Road | 2008-11-18 03:18 | 2008-11-18 | 2008-11-18 04:30 | Calculated | 341 | 341 - Fused Link 341 |  | 109SEG341-587 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 39 | 24153 | 2808 | 0.11626 | 0.0016147 | 312 | 22464 | 2008/2009 | November-2008 | 11 | 2008
21086 | Kinohaku. Harbour road | 2008-11-18 10:05 | 2008-11-18 | 2008-11-18 14:09 | Calculated | 561 | 561 - ABS 561 |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 244 | 15 | 24153 | 3660 | 0.15153 | 0.00062104 | 120 | 29280 | 2008/2009 | November-2008 | 11 | 2008
21091 | Kopaki Road | 2008-11-19 23:08 | 2008-11-19 | 2008-11-19 23:11 | Calculated | 669 | 669 - Recloser with Bypass & Links 669 | ABS 669 | 103SEG731-REG14 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation | Switchgear : Mechanism | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 251 | 24153 | 1004 | 0.04157 | 0.010392 | 2008 | 8032 | 2008/2009 | November-2008 | 11 | 2008
21093 | Mahoenui Substation - Outside | 2008-11-20 10:00 | 2008-11-20 | 2008-11-20 14:25 | Calculated | 1358 | 1358 - ABS1358 |  | 128SEG1358-1602 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 582 | 24153 | 1164 | 0.04819 | 0.024096 | 4656 | 9312 | 2008/2009 | November-2008 | 11 | 2008
21095 | Waitete | 2008-11-21 05:55 | 2008-11-21 | 2008-11-21 06:31 | Calculated | 104 | 104 - Waitete CB Rangitoto 104 |  | No Segment | 206-01 Waitete | Urban A | Rangitoto | Waitete Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 606 | 24153 | 21816 | 0.90324 | 0.02509 | 0 | 0 | 2008/2009 | November-2008 | 11 | 2008
21096 | Tongariro Street | 2008-11-21 09:12 | 2008-11-21 | 2008-11-21 15:23 | Calculated | 11S14 | 11S14 - 3ph 200kVA GROUNDMNT |  | No Segment | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 371 | 72 | 24153 | 26712 | 1.1059 | 0.002981 | 0 | 0 | 2008/2009 | November-2008 | 11 | 2008
21097 | Esplanade - Sth End Te Kuiti | 2008-11-21 09:33 | 2008-11-21 | 2008-11-21 09:36 | Calculated | 203 | 203 - ABS 203 |  | 106SEG203-205 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 198 | 24153 | 594 | 0.02459 | 0.0081977 | 1588 | 4764 | 2008/2009 | November-2008 | 11 | 2008
21099 | By Omori Boat Ramp | 2008-11-21 09:54 | 2008-11-21 | 2008-11-21 10:33 | Calculated | 5921 | 5921 - ABS 5921 |  | 406SEG6558-5921 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation | OH Lines : Jumper - Insulated Copper | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  |  |  | 24153 |  | 0 | 0 |  |  | 2008/2009 | November-2008 | 11 | 2008
21098 | Honikiwi Road | 2008-11-21 10:01 | 2008-11-21 | 2008-11-21 14:00 | Calculated | 209 | 209 - Fused Link 209 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 239 | 50 | 24153 | 11950 | 0.49476 | 0.0020701 | 400 | 95600 | 2008/2009 | November-2008 | 11 | 2008
21100 | Hikumutu Road | 2008-11-21 12:39 | 2008-11-21 | 2008-11-21 13:47 | Calculated | 01A74 | 01A74 - 3ph 25kVA POLEMNT |  | 404SEGL1.10 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 6 | 24153 | 408 | 0.01689 | 0.00024842 | 48 | 3264 | 2008/2009 | November-2008 | 11 | 2008
21102 | Tihoi Road | 2008-11-22 19:22 | 2008-11-22 | 2008-11-22 19:37 | Calculated | T2816 | T2816 - 1ph 15kVA polemount |  | No Segment | No Asset Group | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 1 | 24153 | 15 | 0.00062 | 4.1403e-05 | 8 | 120 | 2008/2009 | November-2008 | 11 | 2008
21103 | Main Road North of Salom Lodge | 2008-11-23 05:12 | 2008-11-23 | 2008-11-23 06:46 | Calculated | 5139 | 5139 - Fused Link 5139 |  | 410SEG5543-5161 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 79 | 24153 | 7426 | 0.30746 | 0.0032708 | 632 | 59408 | 2008/2009 | November-2008 | 11 | 2008
21104 | Pito Street | 2008-11-23 08:20 | 2008-11-23 | 2008-11-23 10:07 | Calculated | 13K05 | 13K05 - 3ph 50kVA POLEMNT |  | No Segment | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24153 | 107 | 0.00443 | 4.1403e-05 | 8 | 856 | 2008/2009 | November-2008 | 11 | 2008
21105 | Piri Piri Substation | 2008-11-24 12:12 | 2008-11-24 | 2008-11-24 13:24 | Calculated | 114 | 114 - 11kV Oil Circuit Breaker with Bypass 114 |  | No Segment | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 264 | 309 | 24153 | 52953 | 2.1924 | 0.012793 | 2472 | 423624 | 2008/2009 | November-2008 | 11 | 2008
21106 | Mangatea Road | 2008-11-24 15:00 | 2008-11-24 | 2008-11-24 16:37 | Calculated | T42 | T42 - 1ph 15kVA POL |  | 104SEG235 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 5 | 24153 | 485 | 0.02008 | 0.00020701 | 40 | 3880 | 2008/2009 | November-2008 | 11 | 2008
21107 | Kururau Road | 2008-11-25 06:45 | 2008-11-25 | 2008-11-25 07:58 | Calculated | 08H04 | 08H04 - 1ph 25kVA POLEMNT | TF8H4 - Transformer Fuse: TF8H4 | 403SEG5754-5766 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 5 | 24153 | 365 | 0.01511 | 0.00020701 | 40 | 2920 | 2008/2009 | November-2008 | 11 | 2008
21108 | Temaire Valley Road | 2008-11-25 09:34 | 2008-11-25 | 2008-11-25 10:17 | Calculated | 5230 | 5230 - Earth Working Link 5230 |  | 403SEG5230 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 7 | 24153 | 301 | 0.01246 | 0.00028982 | 56 | 2408 | 2008/2009 | November-2008 | 11 | 2008
21111 | Waipa River Road | 2008-11-25 16:53 | 2008-11-25 | 2008-11-25 19:23 | Calculated | 529 | 529 - ABS 529 |  | 109SEG529-1727 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Pole Fittings e.g OCB Hangers | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 35 | 24153 | 5250 | 0.21736 | 0.0014491 | 280 | 42000 | 2008/2009 | November-2008 | 11 | 2008
21112 | Mairoa Road | 2008-11-26 08:15 | 2008-11-26 | 2008-11-26 10:19 | Calculated | 265 | 265 - Sectionaliser with Bypass & Links 265 |  | 107SEG262-176 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 13 | 24153 | 1612 | 0.06674 | 0.00053824 | 104 | 12896 | 2008/2009 | November-2008 | 11 | 2008
21113 | Okahukura Back Road | 2008-11-26 12:12 | 2008-11-26 | 2008-11-26 13:45 | Calculated | 5553 | 5553 - Earth Working Link 5553 |  | 402SEG5553 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 24153 | 186 | 0.0077 | 8.2805e-05 | 16 | 1488 | 2008/2009 | November-2008 | 11 | 2008
21114 | Hohotaka Road | 2008-11-27 08:10 | 2008-11-27 | 2008-11-27 09:00 | Calculated | 08M03 | 08M03 - 1ph 5kVA POLEMNT |  | 408SEG5379-5654 | Manunui 408-05 | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 4 | 24153 | 200 | 0.00828 | 0.00016561 | 32 | 1600 | 2008/2009 | November-2008 | 11 | 2008
21115 | Taupehi Road | 2008-11-27 09:06 | 2008-11-27 | 2008-11-27 15:12 | Calculated | 10S01 | 10S01 - 3ph 300kVA GNDPAD | TF10S1 - Transformer Fuse: TF10S1 | 424SEG5942 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 366 | 58 | 24153 | 21228 | 0.8789 | 0.0024014 | 464 | 169824 | 2008/2009 | November-2008 | 11 | 2008
21116 | Tauraroa Road | 2008-11-27 09:49 | 2008-11-27 | 2008-11-27 11:23 | Calculated | T2796 | T2796 - 3ph 50kVA POLEMNT |  | 109SEG529-1727 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 1 | 24153 | 94 | 0.00389 | 4.1403e-05 | 8 | 752 | 2008/2009 | November-2008 | 11 | 2008
21117 | Otunui Sub | 2008-11-27 17:10 | 2008-11-27 | 2008-11-27 18:50 | Calculated | 5375 | 5375 - Recloser with Bypass & Links 5375 | 5316 - Sectionaliser with Bypass & Links 5316 | 403SEG5375-5887 | Western 403-06 | Rural D | Western | Borough Zone Substation | Switchgear : Other | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 45 | 24153 | 4500 | 0.18631 | 0.0018631 | 360 | 36000 | 2008/2009 | November-2008 | 11 | 2008
21118 | Poihipi Road | 2008-11-27 20:10 | 2008-11-27 | 2008-11-27 21:49 | Calculated | T933 | T933 - 1ph 15kVA POLEMNT | TF933 - Transformer Fuse: TF933 | No Segment | Tihoi 124-03 RETIRED | Rural C | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 3 | 24153 | 297 | 0.0123 | 0.00012421 | 24 | 2376 | 2008/2009 | November-2008 | 11 | 2008
21119 | Kaahu Road | 2008-11-27 20:10 | 2008-11-27 | 2008-11-27 22:07 | Calculated | T2821 | T2821 - 3ph 15kVA polemount |  | No Segment | Tihoi 124-03 RETIRED | Rural C | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 2 | 24153 | 234 | 0.00969 | 8.2805e-05 | 16 | 1872 | 2008/2009 | November-2008 | 11 | 2008
21120 | Sandel Road | 2008-11-27 20:37 | 2008-11-27 | 2008-11-27 22:51 | Calculated | T732 | T732 - 3ph 25kVA POLEMNT | TF732 - Transformer Fuse: TF732 | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 4 | 24153 | 536 | 0.02219 | 0.00016561 | 32 | 4288 | 2008/2009 | November-2008 | 11 | 2008
21121 | Kaahu road | 2008-11-27 21:40 | 2008-11-27 | 2008-11-27 22:23 | Calculated | T2544 | T2544 - 1ph 15kVA polemount | TF2544 - Transformer Fuse: TF2544 | No Segment | Tihoi 124-03 RETIRED | Rural C | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 2 | 24153 | 86 | 0.00356 | 8.2805e-05 | 16 | 688 | 2008/2009 | November-2008 | 11 | 2008
21122 | Sandel Road | 2008-11-27 21:52 | 2008-11-27 | 2008-11-27 23:19 | Calculated | T963 | T963 - 3ph 10kVA POLEMNT | TF963 - Transformer Fuse: TF963 | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 1 | 24153 | 87 | 0.0036 | 4.1403e-05 | 8 | 696 | 2008/2009 | November-2008 | 11 | 2008
21123 | Kaahu Road | 2008-11-28 06:33 | 2008-11-28 | 2008-11-28 09:07 | Calculated | T2844 | T2844 - 3ph 15kVA polemount | TF2844 - Transformer Fuse: TF2844 | 129SEG1749-2204 | Tihoi 124-03 RETIRED | Rural C | Tihoi | Marotiri Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 3 | 24153 | 462 | 0.01913 | 0.00012421 | 24 | 3696 | 2008/2009 | November-2008 | 11 | 2008
21125 | Manunui - Freezing works | 2008-11-28 09:05 | 2008-11-28 | 2008-11-28 16:26 | Calculated | 5850 | 5850 - ABS 5850 |  | 407SEG5850-5838 | Manunui 407-01 (was Affco) | Rural B | Manunui / AFFCO Retired | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 441 | 1 | 24153 | 441 | 0.01826 | 4.1403e-05 | 8 | 3528 | 2008/2009 | November-2008 | 11 | 2008
21126 | Ranginui Road | 2008-11-28 09:35 | 2008-11-28 | 2008-11-28 10:21 | Calculated | T802 | T802 - 1ph 10kVA POLEMNT | TF802 - Transformer Fuse: TF802 | 119SEG411-417 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation | Switchgear : Main Circuit Fuses | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 1 | 24153 | 46 | 0.0019 | 4.1403e-05 | 8 | 368 | 2008/2009 | November-2008 | 11 | 2008
21128 | Mapara road | 2008-11-29 14:43 | 2008-11-29 | 2008-11-29 17:24 | Calculated | 1298 | 1298 - 1DROP OUT FUSE |  | 117SEG1298-810 | Te Mapara 117-02 | Rural D | Te Mapara | Wairere Zone Substation | Switchgear : Other | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 11 | 24153 | 1771 | 0.07332 | 0.00045543 | 88 | 14168 | 2008/2009 | November-2008 | 11 | 2008
21130 | Pungarehu Road | 2008-11-30 07:35 | 2008-11-30 | 2008-11-30 10:15 | Calculated | 1529 | 1529 - Earth Working Link 1529 |  | No Segment | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 2 | 24153 | 320 | 0.01325 | 8.2805e-05 | 16 | 2560 | 2008/2009 | November-2008 | 11 | 2008
21132 | Mangaiti Road | 2008-12-01 07:55 | 2008-12-01 | 2008-12-01 11:26 | Calculated | T2244 | T2244 - 1ph 10kVA POLEMNT | TF2244 - Transformer Fuse: TF2244 | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation | Switchgear : Fuse Carriers | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 211 | 2 | 24142 | 422 | 0.01748 | 8.2843e-05 | 16 | 3376 | 2008/2009 | December-2008 | 12 | 2008
21133 | Mangapara Road | 2008-12-01 12:45 | 2008-12-01 | 2008-12-01 15:41 | Calculated | 07D05 | 07D05 - 2ph 10kVA POLEMNT | TF7D5 - Transformer Fuse: TF7D5 | 413SEG5299 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation | Switchgear : Fuse Carriers | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 1 | 24142 | 176 | 0.00729 | 4.1422e-05 | 8 | 1408 | 2008/2009 | December-2008 | 12 | 2008
21135 | Kohua Road | 2008-12-01 18:40 | 2008-12-01 | 2008-12-01 21:04 | Calculated | T2004 | T2004 - 1ph 5kVA POLEMNT | TF2004 - Transformer Fuse: TF2004 | No Segment | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other | FAIL:FOLD:FOLA | Accidental Contact, Damage or Interference by TLC Staff | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 1 | 24142 | 144 | 0.00596 | 4.1422e-05 | 8 | 1152 | 2008/2009 | December-2008 | 12 | 2008
21136 | Manunui - Tokaanu Highway | 2008-12-01 20:15 | 2008-12-01 | 2008-12-01 21:16 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 36 | 24142 | 2196 | 0.09096 | 0.0014912 | 288 | 17568 | 2008/2009 | December-2008 | 12 | 2008
21138 | SH1 | 2008-12-02 08:10 | 2008-12-02 | 2008-12-02 09:48 | Calculated | 08V01 | 08V01 - 1ph 50kVA POLEMNT | TF8V1 - Transformer Fuse: TF8V1 | No Segment | Motuoapa 425-01 | Rural D | Oruatua | Kiko Road Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 21 | 24142 | 2058 | 0.08525 | 0.00086985 | 168 | 16464 | 2008/2009 | December-2008 | 12 | 2008
21140 | Sandel Road | 2008-12-02 10:00 | 2008-12-02 | 2008-12-02 16:32 | Calculated | T1419 | T1419 - 3ph 15kVA POLEMNT |  | No Segment | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 392 | 2 | 24142 | 784 | 0.03247 | 8.2843e-05 | 16 | 6272 | 2008/2009 | December-2008 | 12 | 2008
21141 | Otewa Road | 2008-12-02 10:02 | 2008-12-02 | 2008-12-02 14:41 | Calculated | 539 | 539 - ABS 539 |  | 109SEG539-337 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 279 | 22 | 24142 | 6138 | 0.25425 | 0.00091127 | 0 | 0 | 2008/2009 | December-2008 | 12 | 2008
21142 | Mangapara Road | 2008-12-02 13:56 | 2008-12-02 | 2008-12-02 15:52 | Calculated | 07D05 | 07D05 - 2ph 10kVA POLEMNT |  | 413SEG5299 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 1 | 24142 | 116 | 0.0048 | 4.1422e-05 | 8 | 928 | 2008/2009 | December-2008 | 12 | 2008
21151 | Mangarino Road | 2008-12-03 05:51 | 2008-12-03 | 2008-12-03 07:32 | Calculated | T1218 | T1218 - 3ph 200kVA GNDPAD |  | 106SEG590 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation | OH Lines : Pole - Other | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 32 | 24142 | 3232 | 0.13387 | 0.0013255 | 256 | 25856 | 2008/2009 | December-2008 | 12 | 2008
21143 | Miro Street | 2008-12-03 09:20 | 2008-12-03 | 2008-12-03 10:05 | Calculated | 5390 | 5390 - Fused Link 5390 |  | 408SEG5390-5621 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation | Switchgear : Other | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 163 | 24142 | 7335 | 0.30383 | 0.0067517 | 1304 | 58680 | 2008/2009 | December-2008 | 12 | 2008
21144 | Ongarue stream Raod | 2008-12-03 09:41 | 2008-12-03 | 2008-12-03 11:11 | Calculated | 01J01 | 01J01 - 1ph 15kVA POLEMNT |  | 421SEG5732 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 4 | 24142 | 360 | 0.01491 | 0.00016569 | 32 | 2880 | 2008/2009 | December-2008 | 12 | 2008
21146 | kairimu Road | 2008-12-03 10:24 | 2008-12-03 | 2008-12-03 13:12 | Calculated | 516 | 516 - Fused Link 516 |  | 125SEG516-740 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLG | Ground Subsidence | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 4 | 24142 | 672 | 0.02784 | 0.00016569 | 32 | 5376 | 2008/2009 | December-2008 | 12 | 2008
21147 | Waimiha Valley Road | 2008-12-03 11:50 | 2008-12-03 | 2008-12-03 12:42 | Calculated | 01K04 | 01K04 - 1ph 15kVA POLEMNT |  | 421SEG5732 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 52 | 2 | 24142 | 104 | 0.00431 | 8.2843e-05 | 16 | 832 | 2008/2009 | December-2008 | 12 | 2008
21152 | Mangakahu Valley Road | 2008-12-04 09:12 | 2008-12-04 | 2008-12-04 09:14 | Calculated | 5342 | 5342 - Earth Working Link 5342 |  | 421SEG5342-5792 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 96 | 24142 | 11170 | 0.46268 | 0.0039765 | 768 | 89360 | 2008/2009 | December-2008 | 12 | 2008
21153 | Kokomiko Road | 2008-12-04 09:36 | 2008-12-04 | 2008-12-04 10:34 | Calculated | 02K04 | 02K04 - 1ph 10kVA POLEMNT |  | 421SEG5504-5219 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 2 | 24142 | 116 | 0.0048 | 8.2843e-05 | 16 | 928 | 2008/2009 | December-2008 | 12 | 2008
21154 | Hauturu West Road | 2008-12-04 10:02 | 2008-12-04 | 2008-12-04 10:07 | Calculated | 291 | 291 - ABS 291 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 280 | 44 | 24142 | 2029 | 0.08404 | 0.0018225 | 0 | 0 | 2008/2009 | December-2008 | 12 | 2008
21155 | Waione Road | 2008-12-04 12:09 | 2008-12-04 | 2008-12-04 12:24 | Calculated | 02K07 | 02K07 - 1ph 15kVA POLEMNT |  | 421SEG5355-5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 15 | 4 | 24142 | 60 | 0.00249 | 0.00016569 | 32 | 480 | 2008/2009 | December-2008 | 12 | 2008
21157 | Taupehi Road | 2008-12-05 09:03 | 2008-12-05 | 2008-12-05 16:30 | Calculated | 10S01 | 10S01 - 3ph 300kVA GNDPAD |  | 424SEG5942 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 447 | 58 | 24142 | 24585 | 1.0184 | 0.0024025 | 0 | 0 | 2008/2009 | December-2008 | 12 | 2008
21158 | Waimiha Road | 2008-12-05 09:32 | 2008-12-05 | 2008-12-05 10:37 | Calculated | 02J04 | 02J04 - 1ph 15kVA POLEMNT |  | 421SEG5468 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 65 | 4 | 24142 | 260 | 0.01077 | 0.00016569 | 32 | 2080 | 2008/2009 | December-2008 | 12 | 2008
21159 | Ruakuri Road | 2008-12-05 10:08 | 2008-12-05 | 2008-12-05 14:26 | Calculated | 110A | 110A - Earth Working Link 110A |  | 101SEG110-109 | Caves 101-08 |  | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 17 | 24142 | 4386 | 0.18168 | 0.00070417 | 0 | 0 | 2008/2009 | December-2008 | 12 | 2008
21160 | Ongarue Stream Road | 2008-12-05 12:03 | 2008-12-05 | 2008-12-05 12:48 | Calculated | 02K14 | 02K14 - 1ph 15kVA POLEMNT |  | 421SEG5505-5349 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 2 | 24142 | 90 | 0.00373 | 8.2843e-05 | 16 | 720 | 2008/2009 | December-2008 | 12 | 2008
21161 | Waurere /Road | 2008-12-05 14:11 | 2008-12-05 | 2008-12-05 15:02 | Calculated | 1355 | 1355 - ABS 1355 |  | 116SEG1355-1327 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 17 | 24142 | 867 | 0.03591 | 0.00070417 | 0 | 0 | 2008/2009 | December-2008 | 12 | 2008
21162 | Mangatutu Road | 2008-12-06 08:11 | 2008-12-06 | 2008-12-06 10:25 | Calculated | T1202 | T1202 - 3ph 25kVA polemnt | TF1202 - Transformer Fuse: TF1202 | 111SEG362 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 3 | 24142 | 402 | 0.01665 | 0.00012426 | 24 | 3216 | 2008/2009 | December-2008 | 12 | 2008
21163 | Waipa river Road | 2008-12-06 09:16 | 2008-12-06 | 2008-12-06 10:15 | Calculated | T370 | T370 - 1ph 15kVA POLEMNT |  | 109SEG119-2107 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 2 | 24142 | 118 | 0.00489 | 8.2843e-05 | 16 | 944 | 2008/2009 | December-2008 | 12 | 2008
21164 | Waituhi Road | 2008-12-06 13:16 | 2008-12-06 | 2008-12-06 18:38 | Calculated | 07K10 | 07K10 - 1ph 15kVA POLEMNT | 07K10 - 1ph 15kVA POLEMNT | 402SEG5930-5756 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 322 | 1 | 24142 | 322 | 0.01334 | 4.1422e-05 | 8 | 2576 | 2008/2009 | December-2008 | 12 | 2008
21165 | SH31 | 2008-12-06 14:45 | 2008-12-06 | 2008-12-06 15:50 | Calculated | T3070 | T3070 - 3ph 30kVA POLEMNT | TF3070 - Transformer Fuse: TF3070 | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 1 | 24142 | 65 | 0.00269 | 4.1422e-05 | 8 | 520 | 2008/2009 | December-2008 | 12 | 2008
21166 | Tongaporutu | 2008-12-07 07:30 | 2008-12-07 | 2008-12-07 09:43 | Calculated | T2204 | T2204 - 3ph 25kVA POLEMNT |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 5 | 24142 | 665 | 0.02755 | 0.00020711 | 40 | 5320 | 2008/2009 | December-2008 | 12 | 2008
21169 | Ngapuke Sub | 2008-12-08 10:32 | 2008-12-08 | 2008-12-08 10:38 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 76 | 285 | 24142 | 5110 | 0.21166 | 0.011805 | 2280 | 40880 | 2008/2009 | December-2008 | 12 | 2008
21171 | hAUTURU wEST ROAD | 2008-12-08 16:45 | 2008-12-08 | 2008-12-08 18:50 | Calculated | 286 | 286 - ABS 286 |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 10 | 24142 | 1250 | 0.05178 | 0.00041422 | 80 | 10000 | 2008/2009 | December-2008 | 12 | 2008
21172 | SH 4 Aramatai | 2008-12-09 07:25 | 2008-12-09 | 2008-12-09 08:45 | Calculated | T2082 | T2082 - 1ph 15kVA POLEMNT | TF2082 - Transformer Fuse: TF2082 | No Segment | No Asset Group | Rural D | Te Mapara | Wairere Zone Substation | Miscellaneous : Meter Wiring / Fuses | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 2 | 24142 | 160 | 0.00663 | 8.2843e-05 | 16 | 1280 | 2008/2009 | December-2008 | 12 | 2008
21178 | Behind Whakapapa Tavern | 2008-12-10 08:00 | 2008-12-10 | 2008-12-10 17:18 | Calculated | 5271 | 5271 - Fused Link 5271 |  | 419SEG5271-6697 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 558 | 44 | 24142 | 24552 | 1.017 | 0.0018225 | 351 | 195858 | 2008/2009 | December-2008 | 12 | 2008
21180 | Mokau River Road | 2008-12-10 10:06 | 2008-12-10 | 2008-12-10 14:10 | Calculated | 1621 | 1621 - Fused Link 1621 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 244 | 18 | 24142 | 4392 | 0.18192 | 0.00074559 | 144 | 35136 | 2008/2009 | December-2008 | 12 | 2008
21183 | Ngaroma - For tolley's road | 2008-12-11 10:17 | 2008-12-11 | 2008-12-11 10:35 | Calculated | 424 | 424 - Fused Link 424 |  | 121SEG424-799 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 18 | 15 | 24142 | 270 | 0.01118 | 0.00062132 | 120 | 2160 | 2008/2009 | December-2008 | 12 | 2008
21186 | Awakino Road | 2008-12-11 15:27 | 2008-12-11 | 2008-12-11 16:19 | Calculated | 730 | 730 - Recloser with Bypass & Links 730 |  | 104SEG217-730 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 52 | 24142 | 2704 | 0.112 | 0.0021539 | 416 | 21632 | 2008/2009 | December-2008 | 12 | 2008
21189 | Tongaporutu | 2008-12-12 14:27 | 2008-12-12 | 2008-12-12 15:49 | Calculated | 1635 | 1635 - ABS 1635 | T2193 - 3ph 100kVA POLEMNT | 128SEG1635-1626 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 135 | 24142 | 11070 | 0.45854 | 0.0055919 | 1080 | 88560 | 2008/2009 | December-2008 | 12 | 2008
21191 | Borough Sub | 2008-12-13 06:05 | 2008-12-13 | 2008-12-13 06:15 | Calculated | 5992 | 5992 - 33kV Oil Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 981 | 24142 | 9810 | 0.40635 | 0.040635 | 0 | 0 | 2008/2009 | December-2008 | 12 | 2008
21192 | Puketawai road | 2008-12-14 17:51 | 2008-12-14 | 2008-12-14 18:33 | Calculated | 189 | 189 - Fused Link 189 |  | 110SEG189 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 5 | 24142 | 210 | 0.0087 | 0.00020711 | 40 | 1680 | 2008/2009 | December-2008 | 12 | 2008
21195 | Kirikau Valley Road | 2008-12-15 05:46 | 2008-12-15 | 2008-12-15 07:04 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 15 | 24142 | 1170 | 0.04846 | 0.00062132 | 120 | 9360 | 2008/2009 | December-2008 | 12 | 2008
21194 | Gadsby road | 2008-12-15 13:48 | 2008-12-15 | 2008-12-15 14:27 | Calculated | 512 | 512 - Gadsby Rd 11 kV Feeder512 |  | No Segment | Oparure 107-01 | Urban A | Oparure | Gadsby Road Zone Substation | OH Lines : Insulator - Disc | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 318 | 24142 | 27981 | 1.159 | 0.013172 | 2544 | 223848 | 2008/2009 | December-2008 | 12 | 2008
21200 | SH 49 - Cnr Fields Track | 2008-12-16 05:55 | 2008-12-16 | 2008-12-16 06:03 | Calculated | 5684 | 5684 - Recloser 5684 |  | 416SEG5721-5684 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 63 | 24142 | 504 | 0.02088 | 0.0026096 | 504 | 4032 | 2008/2009 | December-2008 | 12 | 2008
21199 | Kirikau Valley Road | 2008-12-16 14:43 | 2008-12-16 | 2008-12-16 15:29 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 15 | 24142 | 690 | 0.02858 | 0.00062132 | 120 | 5520 | 2008/2009 | December-2008 | 12 | 2008
21201 | Mokauiti road | 2008-12-17 08:00 | 2008-12-17 | 2008-12-17 10:27 | Calculated | T1973 | T1973 - 1ph 10kVA POLEMNT | TF1973 - Transformer Fuse: TF1973 | 114SEG1112 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation | Switchgear : Main Circuit Fuses | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 2 | 24142 | 294 | 0.01218 | 8.2843e-05 | 16 | 2352 | 2008/2009 | December-2008 | 12 | 2008
21202 | Pokuru road | 2008-12-17 10:02 | 2008-12-17 | 2008-12-17 11:15 | Calculated | T3242 | T3242 - 3ph 50kVA polemount | TF3242 - Transformer Fuse: TF3242 | 129SEG442-2238 | Tihoi 124-04 RETIRED | Rural C | Tihoi | Marotiri Zone Substation | Transformers : Other | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  |  |  | 24142 |  | 0 | 0 |  |  | 2008/2009 | December-2008 | 12 | 2008
21203 | Waitete | 2008-12-17 11:20 | 2008-12-17 | 2008-12-17 11:59 | Calculated | 103 | 103 - Waitete Circuit Breaker Te Kuiti South 103 |  | No Segment | 206-01 Waitete | Urban A | Te Kuiti South | Waitete Zone Substation | OH Lines : Insulator - Pin | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 1032 | 24142 | 21198 | 0.87805 | 0.042747 | 8256 | 169584 | 2008/2009 | December-2008 | 12 | 2008
21205 | Waikino road | 2008-12-18 15:51 | 2008-12-18 | 2008-12-18 15:53 | Calculated | 426 | 426 - Sectionaliser with Bypass & Links 426 |  | 129SEG434-426 | Tihoi 124-03 RETIRED | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 199 | 24142 | 398 | 0.01649 | 0.0082429 | 1592 | 3184 | 2008/2009 | December-2008 | 12 | 2008
21206 | Ngamoki Road | 2008-12-19 08:32 | 2008-12-19 | 2008-12-19 09:37 | Calculated | 5716 | 5716 - Fused Link 5716 | 41621171 - 11 Straight Thru | 416SEG5716 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply | OH Lines : Crossarm - Wood | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 8 | 24142 | 520 | 0.02154 | 0.00033137 | 64 | 4160 | 2008/2009 | December-2008 | 12 | 2008
21209 | Paekaka Road | 2008-12-20 15:21 | 2008-12-20 | 2008-12-20 15:31 | Calculated | 1512 | 1512 - Recloser with Bypass & Links 1512 |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 154 | 24142 | 1540 | 0.06379 | 0.0063789 | 1232 | 12320 | 2008/2009 | December-2008 | 12 | 2008
21211 | Ranginui road | 2008-12-20 19:18 | 2008-12-20 | 2008-12-20 20:11 | Calculated | 412 | 412 - Fused Link 412 |  | 121SEG412 | Huirimu 121-04 | Rural D | Huirimu | Arohena Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 5 | 24142 | 265 | 0.01098 | 0.00020711 | 40 | 2120 | 2008/2009 | December-2008 | 12 | 2008
21212 | Hangatiki | 2008-12-21 08:36 | 2008-12-21 | 2008-12-21 08:50 | Calculated | TPHangatiki CB222 | TPHangatiki CB222 - 33kV Minimum Oil Circuit Breaker TP222 |  | No Segment | 213-01 Transpower Hangatiki |  | Te Waireka Rd 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  |  |  | 24142 |  | 0 | 0 |  |  | 2008/2009 | December-2008 | 12 | 2008
21214 | Napinapi road | 2008-12-22 09:30 | 2008-12-22 | 2008-12-22 11:17 | Calculated | T1766 | T1766 - 1ph 15kVA POLEMNT |  | 117SEG1299-1329 | Te Mapara 117-02 | Rural D | Te Mapara | Wairere Zone Substation | Switchgear : Fuse Carriers | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 2 | 24142 | 214 | 0.00886 | 8.2843e-05 | 16 | 1712 | 2008/2009 | December-2008 | 12 | 2008
21215 | Mangaotaki Road | 2008-12-22 09:55 | 2008-12-22 | 2008-12-22 12:24 | Calculated | T1625 | T1625 - 1ph 10kVA POLEMNT |  | 113SEG1548-1526 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 1 | 24142 | 149 | 0.00617 | 4.1422e-05 | 8 | 1192 | 2008/2009 | December-2008 | 12 | 2008
21216 | Waipuna road | 2008-12-23 09:23 | 2008-12-23 | 2008-12-23 13:32 | Calculated | 286 | 286 - ABS 286 |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 249 | 10 | 24142 | 2490 | 0.10314 | 0.00041422 | 80 | 19920 | 2008/2009 | December-2008 | 12 | 2008
21217 | Whangamata Road | 2008-12-23 10:24 | 2008-12-23 | 2008-12-23 12:00 | Calculated | 467 | 467 - Fused Link 467 |  | 123SEG467 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 96 | 10 | 24142 | 960 | 0.03976 | 0.00041422 | 80 | 7680 | 2008/2009 | December-2008 | 12 | 2008
21218 | Waihaha sub | 2008-12-23 12:12 | 2008-12-23 | 2008-12-23 12:38 | Calculated | 5409 | 5409 - Recloser with Bypass 5409 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 35 | 24142 | 910 | 0.03769 | 0.0014498 | 280 | 7280 | 2008/2009 | December-2008 | 12 | 2008
21220 | Manunui Sub | 2008-12-24 19:02 | 2008-12-24 | 2008-12-24 19:18 | Calculated | 132 | 132 - ABS 132 |  | No Segment | 207-01 Wairere Falls | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Protection |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  |  |  | 24142 |  | 0 | 0 |  |  | 2008/2009 | December-2008 | 12 | 2008
21221 | Ngatamahine road | 2008-12-25 16:20 | 2008-12-25 | 2008-12-26 11:34 | Calculated | 1709 | 1709 - Fused Link 1709 |  | 115SEG1709 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 14 | 24142 | 364 | 0.01508 | 0.0005799 | 112 | 2912 | 2008/2009 | December-2008 | 12 | 2008
21222 | Wairoma road | 2008-12-26 12:10 | 2008-12-26 | 2008-12-26 13:34 | Calculated | 1118 | 1118 - Link 1118 | 1118 - Link 1118 | 114SEG1118 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 3 | 24142 | 252 | 0.01044 | 0.00012426 | 24 | 2016 | 2008/2009 | December-2008 | 12 | 2008
21223 | Borough Sub | 2008-12-28 07:56 | 2008-12-28 | 2008-12-28 08:05 | Calculated | 5992 | 5992 - 33kV Oil Breaker 5992 | 5992 - 33kV Oil Breaker 5992 | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 981 | 24142 | 8829 | 0.36571 | 0.040635 | 0 | 0 | 2008/2009 | December-2008 | 12 | 2008
21224 | Karangahape road | 2008-12-29 08:05 | 2008-12-29 | 2008-12-29 11:30 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 205 | 39 | 24142 | 7995 | 0.33117 | 0.0016154 | 312 | 63960 | 2008/2009 | December-2008 | 12 | 2008
21225 | Kokakoroa road | 2008-12-29 08:30 | 2008-12-29 | 2008-12-29 10:57 | Calculated | 755 | 755 - Fused Link 755 | TF1185 - Transformer Fuse: TF1185 | 101SEG755 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation | Switchgear : Fuse Carriers | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 6 | 24142 | 882 | 0.03653 | 0.00024853 | 48 | 7056 | 2008/2009 | December-2008 | 12 | 2008
21228 | Te Kumi Station Road | 2008-12-31 07:40 | 2008-12-31 | 2008-12-31 09:47 | Calculated | 763 | 763 - Fused Link 763 |  | 108SEG763-2140 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 2 | 24142 | 254 | 0.01052 | 8.2843e-05 | 16 | 2032 | 2008/2009 | December-2008 | 12 | 2008
21232 | Karangahape Road | 2009-01-03 07:14 | 2009-01-03 | 2009-01-03 10:30 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 39 | 24163 | 7644 | 0.31635 | 0.001614 | 348.5 | 68305 | 2008/2009 | January-2009 | 1 | 2009
21233 | Opatu Sub | 2009-01-03 08:40 | 2009-01-03 | 2009-01-03 11:06 | Calculated | 5417 | 5417 - Recloser 5417 |  | 413SEG5418-5417 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 61 | 24163 | 8906 | 0.36858 | 0.0025245 | 413 | 60297 | 2008/2009 | January-2009 | 1 | 2009
21235 | Mangaorongo road | 2009-01-05 10:20 | 2009-01-05 | 2009-01-05 11:32 | Calculated | T664 | T664 - 3ph 7.5kVA polemnt |  | 111SEG342-544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 72 | 2 | 24163 | 144 | 0.00596 | 8.2771e-05 | 50 | 3600 | 2008/2009 | January-2009 | 1 | 2009
21238 | Harpers Ave | 2009-01-06 07:50 | 2009-01-06 | 2009-01-06 10:08 | Calculated | 663 | 663 - Fused Link 663 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BCMS | Bird Contact Mid-span / Wire Clash | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 6 | 24163 | 828 | 0.03427 | 0.00024831 | 90 | 12420 | 2008/2009 | January-2009 | 1 | 2009
21240 | Aotearoa Road | 2009-01-06 13:42 | 2009-01-06 | 2009-01-06 13:51 | Calculated | 378 | 378 - Recloser with Bypass & Links 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 205 | 24163 | 14670 | 0.60713 | 0.008484 | 0 | 0 | 2008/2009 | January-2009 | 1 | 2009
21243 | Mokauiti Road | 2009-01-08 01:40 | 2009-01-08 | 2009-01-08 03:03 | Calculated | 1107 | 1107 - Recloser with Bypass 1107 |  | 114SEG1107-1116 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 89 | 24163 | 10352 | 0.42842 | 0.0036833 | 676 | 85758 | 2008/2009 | January-2009 | 1 | 2009
21244 | Ahititi Before School | 2009-01-08 10:10 | 2009-01-08 | 2009-01-08 12:39 | Calculated | 1642 | 1642 - Fused Link 1642 |  | 128SEG1642-1630 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 43 | 24163 | 6407 | 0.26516 | 0.0017796 | 425 | 63325 | 2008/2009 | January-2009 | 1 | 2009
21245 | Mokauiti road - By Aria Post Office | 2009-01-08 10:41 | 2009-01-08 | 2009-01-08 12:56 | Calculated | 1107 | 1107 - Recloser with Bypass 1107 |  | 114SEG1107-1116 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 89 | 24163 | 12015 | 0.49725 | 0.0036833 | 676 | 91259 | 2008/2009 | January-2009 | 1 | 2009
21246 | Arohena Sub | 2009-01-08 16:02 | 2009-01-08 | 2009-01-08 16:05 | Calculated | 62 | 62 - Oil Breaker with Bypass & Links 62 | 62 - Oil Breaker with Bypass & Links 62 | 310SEG62-64 | 211-01 Arohena | Rural D | No Feeder |  |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 501 | 24163 | 1503 | 0.0622 | 0.020734 | 4582 | 13745 | 2008/2009 | January-2009 | 1 | 2009
21247 | Wairere | 2009-01-08 17:49 | 2009-01-08 | 2009-01-08 17:50 | Calculated | 792 | 792 - 33kV Circuit Breaker 792 |  | No Segment | 207-01 Wairere Falls | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 623 | 24163 | 3115 | 0.12892 | 0.025783 | 3862 | 19309 | 2008/2009 | January-2009 | 1 | 2009
21248 | Waikura Terrace | 2009-01-09 08:47 | 2009-01-09 | 2009-01-09 13:14 | Calculated | T4026 | T4026 - 3ph 100kVA POLEMNT |  | 408SEG5129-5882 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 267 | 29 | 24163 | 7743 | 0.32045 | 0.0012002 | 100 | 26699 | 2008/2009 | January-2009 | 1 | 2009
21249 | SH3 Tongaporutu | 2009-01-09 09:38 | 2009-01-09 | 2009-01-09 15:42 | Calculated | T2206 | T2206 - 1ph 10kVA POLEMNT |  | 128SEG1642-1630 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 2 | 24163 | 728 | 0.03013 | 8.2771e-05 | 30 | 10920 | 2008/2009 | January-2009 | 1 | 2009
21250 | soldiers Road | 2009-01-09 11:01 | 2009-01-09 | 2009-01-09 12:33 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24163 |  | 0 | 0 |  |  | 2008/2009 | January-2009 | 1 | 2009
21251 | Taharoa | 2009-01-09 12:32 | 2009-01-09 | 2009-01-09 14:06 | Calculated | 609 | 609 - 11kV Oil Circuit Breaker 609 (Rural Feeder) 609 | T1405 - 3ph 15kVA POLEMNT | No Segment | 201-01 Taharoa | Rural D | Rural | Taharoa Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 106 | 24163 | 9964 | 0.41237 | 0.0043869 | 648 | 60911 | 2008/2009 | January-2009 | 1 | 2009
21253 | Waitanguru | 2009-01-10 09:00 | 2009-01-10 | 2009-01-10 10:52 | Calculated | 1531 | 1531 - Sectionaliser 1531 | 1531J - Incoming Link 1531J | 113SEG1531-1501 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 17 | 24163 | 1904 | 0.0788 | 0.00070356 | 115 | 12879 | 2008/2009 | January-2009 | 1 | 2009
21255 | Benneydale - Tapuwae road | 2009-01-12 09:32 | 2009-01-12 | 2009-01-12 12:52 | Calculated | 1651 | 1651 - Fused Link 1651 |  | 103SEG1651-2227 | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 200 | 16 | 24163 | 3200 | 0.13243 | 0.00066217 | 90 | 18000 | 2008/2009 | January-2009 | 1 | 2009
21256 | Arohena substation | 2009-01-12 17:05 | 2009-01-12 | 2009-01-12 17:12 | Calculated | 1072 | 1072 - SF6 Breaker 1072 Huirimu |  | 121SEG1072-753 | 211-01 Arohena | Rural D | Huirimu | Arohena Zone Substation | Transformers : Other | Asset Related | Protection |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 108 | 24163 | 756 | 0.03129 | 0.0044696 | 0 | 0 | 2008/2009 | January-2009 | 1 | 2009
21257 | hangatiki | 2009-01-12 22:27 | 2009-01-12 | 2009-01-12 22:29 | Calculated | 242 | 242 - ABS 242 |  | 107SEG213-242 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 168 | 24163 | 13104 | 0.54232 | 0.0069528 | 1175 | 91649 | 2008/2009 | January-2009 | 1 | 2009
21258 | Borough Sub | 2009-01-13 00:53 | 2009-01-13 | 2009-01-13 01:00 | Calculated | 5992 | 5992 - 33kV Oil Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 7 | 1214 | 24163 | 8498 | 0.35169 | 0.050242 | 9214.5 | 64501 | 2008/2009 | January-2009 | 1 | 2009
21259 | Hangatiki | 2009-01-13 03:08 | 2009-01-13 | 2009-01-13 03:18 | Calculated | 242 | 242 - ABS 242 |  | 107SEG213-242 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 168 | 24163 | 12432 | 0.51451 | 0.0069528 | 1175 | 86949 | 2008/2009 | January-2009 | 1 | 2009
21260 | Pihanga Saddle road | 2009-01-13 08:02 | 2009-01-13 | 2009-01-13 10:11 | Calculated | 5590 | 5590 - Earth Working Link 5590 | 5590 - Earth Working Link 5590 | 418SEG5590-5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 8 | 24163 | 1032 | 0.04271 | 0.00033108 | 68 | 8772 | 2008/2009 | January-2009 | 1 | 2009
21262 | SH43 | 2009-01-14 08:45 | 2009-01-14 | 2009-01-14 08:52 | Calculated | 5622 | 5622 - Earth Working Link 5622 |  | 403SEG5622-5368 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 7 | 45 | 24163 | 5687 | 0.23536 | 0.0018624 | 270 | 34124 | 2008/2009 | January-2009 | 1 | 2009
21263 | Tihoi Road | 2009-01-14 09:45 | 2009-01-14 | 2009-01-14 12:18 | Calculated | 440 | 440 - Recloser with Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 50 | 24163 | 7650 | 0.3166 | 0.0020693 | 353.5 | 54085 | 2008/2009 | January-2009 | 1 | 2009
21264 | Raurimu Road | 2009-01-14 09:50 | 2009-01-14 | 2009-01-14 11:50 | Calculated | 13J03 | 13J03 - 1ph 10kVA POLEMNT | TF13J03 - Transformer Fuse: TF13J03 | No Segment | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 2 | 24163 | 240 | 0.00993 | 8.2771e-05 | 10 | 1200 | 2008/2009 | January-2009 | 1 | 2009
21265 | Sircombe Rd | 2009-01-14 10:02 | 2009-01-14 | 2009-01-14 14:55 | Calculated | 522 | 522 - ABS 522 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 293 | 53 | 24163 | 15529 | 0.64268 | 0.0021934 | 590 | 172869 | 2008/2009 | January-2009 | 1 | 2009
21266 | Waihora Road | 2009-01-14 10:03 | 2009-01-14 | 2009-01-14 14:16 | Calculated | 446 | 446 - Recloser with Bypass & Links 446 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 253 | 31 | 24163 | 7843 | 0.32459 | 0.001283 | 0 | 0 | 2008/2009 | January-2009 | 1 | 2009
21267 | Raurimu Road | 2009-01-14 17:05 | 2009-01-14 | 2009-01-14 18:26 | Calculated | T4000 | T4000 - 2ph 10kVA POLEMNT | TF4000 - Transformer Fuse: TF4000 | No Segment | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 1 | 24163 | 81 | 0.00335 | 4.1386e-05 | 10 | 810 | 2008/2009 | January-2009 | 1 | 2009
21268 | McLean Road | 2009-01-15 08:02 | 2009-01-15 | 2009-01-15 09:53 | Calculated | T2995 | T2995 - 1ph 5kVA POLEMNT |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 1 | 24163 | 111 | 0.00459 | 4.1386e-05 | 10 | 1110 | 2008/2009 | January-2009 | 1 | 2009
21269 | Mangaorongo Road | 2009-01-15 10:11 | 2009-01-15 | 2009-01-15 10:58 | Calculated | 335 | 335 - ABS 335 | TF1452 - Transformer Fuse: TF1452 | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation | Switchgear : Fuse Carriers | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 31 | 24163 | 1457 | 0.0603 | 0.001283 | 260 | 12219 | 2008/2009 | January-2009 | 1 | 2009
21270 | korohe road | 2009-01-15 15:50 | 2009-01-15 | 2009-01-15 16:27 | Calculated | 5917 | 5917 - Earth Working Link 5917 |  | 424SEG5917 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 23 | 24163 | 851 | 0.03522 | 0.00095187 | 100 | 3699 | 2008/2009 | January-2009 | 1 | 2009
21271 | Harvey Road | 2009-01-15 18:38 | 2009-01-15 | 2009-01-15 22:26 | Calculated | 494 | 494 - Fused Link 494 | T2243 - 3ph 30kVA POLEMNT | 119SEG494 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation | Transformers : Other | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 228 | 1 | 24163 | 228 | 0.00944 | 4.1386e-05 | 15 | 3420 | 2008/2009 | January-2009 | 1 | 2009
21272 | Waipuna Road | 2009-01-16 10:02 | 2009-01-16 | 2009-01-16 11:54 | Calculated | 291 | 291 - ABS 291 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 29 | 24163 | 3248 | 0.13442 | 0.0012002 | 248 | 27775 | 2008/2009 | January-2009 | 1 | 2009
21274 | Mangaorongo Road | 2009-01-16 23:07 | 2009-01-16 | 2009-01-17 00:53 | Calculated | 1519 | 1519 - Recloser 1519 | T1859 - 1ph 10kVA POLEMNT | 113SEG1519-1541 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation | OH Lines : Jumper - Insulated Copper | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 22 | 24163 | 2332 | 0.09651 | 0.00091048 | 138 | 14628 | 2008/2009 | January-2009 | 1 | 2009
21275 | National Park North | 2009-01-17 05:14 | 2009-01-17 | 2009-01-17 06:17 | Calculated | 5144 | 5144 - 11kV Oil Breaker with Bypass 5144 | 411-01 - National Park411-01 | 411SEG5144-5769 | 501-01 National Park | Rural D | National Park | National Park Zone Substation | OH Lines : Conductor - Insulated Copper | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 249 | 282 | 24163 | 64080 | 2.652 | 0.011671 | 0 | 0 | 2008/2009 | January-2009 | 1 | 2009
21278 | Waitaanga Sub | 2009-01-18 05:25 | 2009-01-18 | 2009-01-18 07:07 | Calculated | 5422 | 5422 - Recloser with Bypass & Links 5422 |  | 413SEG5636-5422 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 36 | 24163 | 3672 | 0.15197 | 0.0014899 | 233 | 23765 | 2008/2009 | January-2009 | 1 | 2009
21276 | Te Waitere Road | 2009-01-18 10:11 | 2009-01-18 | 2009-01-18 12:11 | Calculated | T547 | T547 - 3ph 300kVA GMT |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 19 | 24163 | 2280 | 0.09436 | 0.00078633 | 300 | 35999 | 2008/2009 | January-2009 | 1 | 2009
21281 | SH40 Mangakara | 2009-01-19 10:36 | 2009-01-19 | 2009-01-19 12:52 | Calculated | 5304 | 5304 - Sectionaliser with Bypass & Links 5304 | 06C04 - 1ph 7.5kVA POLEMNT | 413SEG5420-5305 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation | OH Lines : Jumper - Insulated Copper | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 5 | 24163 | 680 | 0.02814 | 0.00020693 | 32.5 | 4420 | 2008/2009 | January-2009 | 1 | 2009
21282 | Rangiatea Road | 2009-01-19 13:49 | 2009-01-19 | 2009-01-19 14:46 | Calculated | 345 | 345 - ABS 345 | T251 - 3ph 25kVA POLEMNT | 109SEG345-348 | Gravel Scoop 109-12 | Urban A | Gravel Scoop | Te Waireka Zone Substation | OH Lines : Jumper - Insulated Copper | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 103 | 24163 | 5871 | 0.24297 | 0.0042627 | 1033 | 58880 | 2008/2009 | January-2009 | 1 | 2009
21284 | Parerohi Grove | 2009-01-20 08:35 | 2009-01-20 | 2009-01-20 09:54 | Calculated | 09R32 | 09R32 - 1ph 15kVA POLEMNT |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation | Unknown (All Categories) | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 2 | 24163 | 158 | 0.00654 | 8.2771e-05 | 15 | 1185 | 2008/2009 | January-2009 | 1 | 2009
21285 | Kawhia Road | 2009-01-20 10:02 | 2009-01-20 | 2009-01-20 10:56 | Calculated | 317 | 317 - ABS 317 |  | 112SEG317-209 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 69 | 24163 | 3726 | 0.1542 | 0.0028556 | 775 | 41849 | 2008/2009 | January-2009 | 1 | 2009
21286 | Albatross point | 2009-01-20 10:24 | 2009-01-20 | 2009-01-20 12:45 | Calculated | T2496 | T2496 - 3ph 3kVA POLEMNT |  | No Segment | Rural 126-02 | Rural D | Rural | Taharoa Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 1 | 24163 | 141 | 0.00584 | 4.1386e-05 | 3 | 423 | 2008/2009 | January-2009 | 1 | 2009
21287 | SH 32 | 2009-01-21 06:40 | 2009-01-21 | 2009-01-21 10:07 | Calculated | 5737 | 5737 - Air Break Switch 5737 | 5737 - Air Break Switch 5737 | 426SEG5737-5374 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 207 | 35 | 24163 | 7245 | 0.29984 | 0.0014485 | 272.5 | 56407 | 2008/2009 | January-2009 | 1 | 2009
21288 | Waitete Road | 2009-01-22 09:01 | 2009-01-22 | 2009-01-22 14:17 | Calculated | T2981 | T2981 - 3ph 30kVA POL |  | No Segment | Benneydale 103-01 | Urban A | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 316 | 3 | 24163 | 948 | 0.03923 | 0.00012416 | 30 | 9480 | 2008/2009 | January-2009 | 1 | 2009
21291 | Paraheka Sub | 2009-01-22 10:04 | 2009-01-22 | 2009-01-22 12:16 | Calculated | 1126 | 1126 - Recloser with Incoming Link 1126 |  | 114SEG1126-1127 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 132 | 30 | 24163 | 3960 | 0.16389 | 0.0012416 | 210 | 27719 | 2008/2009 | January-2009 | 1 | 2009
21292 | Waihaha Sub | 2009-01-22 11:27 | 2009-01-22 | 2009-01-22 11:42 | Calculated | 5374 | 5374 - Fused Link 5374 | 5374 - Fused Link 5374 | 426SEG5374-04Q06 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 35 | 24163 | 525 | 0.02173 | 0.0014485 | 272.5 | 4087 | 2008/2009 | January-2009 | 1 | 2009
21293 | Atiamuri | 2009-01-22 22:44 | 2009-01-22 | 2009-01-22 22:45 | Calculated | 732 | 732 - CB Atiamuri 33 kV Supply 732 |  | No Segment | 215-01 Atiamuri | Rural C | No Feeder |  |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24163 |  | 0 | 0 |  |  | 2008/2009 | January-2009 | 1 | 2009
21294 | Karangahape Road | 2009-01-23 07:35 | 2009-01-23 | 2009-01-23 09:17 | Calculated | 07Q08 | 07Q08 - 1ph 10kVA POLEMNT |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds |  | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 2 | 24163 | 204 | 0.00844 | 8.2771e-05 | 10 | 1020 | 2008/2009 | January-2009 | 1 | 2009
21295 | Main South Road - Te Kuiti | 2009-01-23 09:00 | 2009-01-23 | 2009-01-23 09:57 | Calculated | T638 | T638 - 3ph 50kVA POL |  | No Segment | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 1 | 24163 | 57 | 0.00236 | 4.1386e-05 | 50 | 2850 | 2008/2009 | January-2009 | 1 | 2009
21300 | Rangitoto Road | 2009-01-23 12:24 | 2009-01-23 | 2009-01-23 17:21 | Calculated | T1150 | T1150 - 3ph 500kVA GNDPAD | T1150 - 3ph 500kVA GNDPAD | 106SEG227-586 | Rangitoto 106-02 |  | Rangitoto | Waitete Zone Substation | Transformers : Other | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 297 | 2 | 24163 | 594 | 0.02458 | 8.2771e-05 | 750 | 222750 | 2008/2009 | January-2009 | 1 | 2009
21302 | Western Bay Road | 2009-01-23 16:01 | 2009-01-23 | 2009-01-23 16:27 | Calculated | 475 | 475 - Fused Link 475 |  | 124SEG475-440 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Protection | FAIL:EHUO2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 60 | 24163 | 1560 | 0.06456 | 0.0024831 | 508.5 | 13220 | 2008/2009 | January-2009 | 1 | 2009
21305 | Pihanga Saddle Road | 2009-01-26 08:10 | 2009-01-26 | 2009-01-26 08:52 | Calculated | 5590 | 5590 - Earth Working Link 5590 |  | 418SEG5590-5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation | OH Lines : Other | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 8 | 24163 | 336 | 0.01391 | 0.00033108 | 68 | 2856 | 2008/2009 | January-2009 | 1 | 2009
21306 | Rangitoto road | 2009-01-26 08:30 | 2009-01-26 | 2009-01-26 11:01 | Calculated | T1150 | T1150 - 3ph 500kVA GNDPAD |  | 106SEG227-586 | Rangitoto 106-02 |  | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 151 | 2 | 24163 | 302 | 0.0125 | 8.2771e-05 | 750 | 113250 | 2008/2009 | January-2009 | 1 | 2009
21307 | SH 40 | 2009-01-26 08:40 | 2009-01-26 | 2009-01-26 09:54 | Calculated | 05F10 | 05F10 - 3ph 100kVA POLEMNT |  | No Segment | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 20 | 24163 | 1480 | 0.06125 | 0.00082771 | 100 | 7400 | 2008/2009 | January-2009 | 1 | 2009
21310 | Karangahape Road | 2009-01-27 08:10 | 2009-01-27 | 2009-01-27 10:12 | Calculated | 07Q08 | 07Q08 - 1ph 10kVA POLEMNT |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 2 | 24163 | 244 | 0.0101 | 8.2771e-05 | 10 | 1220 | 2008/2009 | January-2009 | 1 | 2009
21309 | Tauranga - Taupo | 2009-01-27 10:01 | 2009-01-27 | 2009-01-27 11:39 | Calculated | T4087 | T4087 - 1ph 50kVA POLEMNT |  | 417SEG5297-5245 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 98 | 1 | 24163 | 98 | 0.00406 | 4.1386e-05 | 15 | 1470 | 2008/2009 | January-2009 | 1 | 2009
21311 | Miro St & Prk Avenue | 2009-01-27 10:30 | 2009-01-27 | 2009-01-27 11:09 | Calculated | 6320 | 6320 - Fuse Link 6320 |  | 414SEG6173-5014 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 39 | 46 | 24163 | 1794 | 0.07425 | 0.0019037 | 400 | 15599 | 2008/2009 | January-2009 | 1 | 2009
21312 | Happy Valley Road | 2009-01-27 11:55 | 2009-01-27 | 2009-01-27 13:35 | Calculated | T270 | T270 - 3ph 25kVA polemnt |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation | Miscellaneous : Other Miscellaneous | Asset Related | Insulator |  | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 3 | 24163 | 300 | 0.01242 | 0.00012416 | 25 | 2499 | 2008/2009 | January-2009 | 1 | 2009
21313 | SH 32 | 2009-01-27 13:50 | 2009-01-27 | 2009-01-27 15:51 | Calculated | 04Q13 | 04Q13 - 1ph 15kVA POLEMNT |  | No Segment | No Asset Group | Remote Rural E | Waihaha | Kuratau Zone Substation | OH Lines : Other | Asset Related |  |  | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 1 | 24163 | 121 | 0.00501 | 4.1386e-05 | 15 | 1815 | 2008/2009 | January-2009 | 1 | 2009
21314 | Hangatiki | 2009-01-27 18:58 | 2009-01-27 | 2009-01-27 19:22 | Calculated | 1272 | 1272 - Vacuum Circuit Breaker 1272 |  | No Segment | 204-01 Hangatiki | Urban A | Caves | Hangatiki Zone Substation | Cables : Other | Asset Related |  |  |  | Unplanned | Unplanned - TLC : Class C | Underground | 11kV | 11000 |  | 24 | 378 | 24163 | 9640 | 0.39896 | 0.015644 | 4473.5 | 121283 | 2008/2009 | January-2009 | 1 | 2009
21322 | Marokopa Road | 2009-01-28 09:25 | 2009-01-28 | 2009-01-28 12:53 | Calculated | T1307 | T1307 - 1ph 15kVA POL |  | 125SEG296-583 | Coast 125-04 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 208 | 1 | 24163 | 208 | 0.00861 | 4.1386e-05 | 5 | 1040 | 2008/2009 | January-2009 | 1 | 2009
21320 | Moore Street | 2009-01-28 09:39 | 2009-01-28 | 2009-01-28 20:06 | Calculated | 20K10 | 20K10 - 3ph 100kVA POL |  | 415SEG5704-REG28 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 627 | 49 | 24163 | 30723 | 1.2715 | 0.0020279 | 0 | 0 | 2008/2009 | January-2009 | 1 | 2009
21321 | Paerata road | 2009-01-28 10:00 | 2009-01-28 | 2009-01-28 12:24 | Calculated | 455 | 455 - Fused Link 455 |  | 129SEG455-402 | BHRFHF | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 144 | 44 | 24163 | 6336 | 0.26222 | 0.001821 | 395 | 56879 | 2008/2009 | January-2009 | 1 | 2009
21323 | Waitanguru | 2009-01-29 10:04 | 2009-01-29 | 2009-01-29 11:52 | Calculated | 1549 | 1549 - Recloser 1549 |  | 113SEG1549-1530 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 27 | 24163 | 2916 | 0.12068 | 0.0011174 | 192.5 | 20789 | 2008/2009 | January-2009 | 1 | 2009
21326 | Korohe Road | 2009-01-29 14:40 | 2009-01-29 | 2009-01-29 15:30 | Calculated | T4172 | T4172 - 1ph 100kVA POLEMNT | tf4172 | No Segment | No Asset Group | Rural C | Rangipo / Hautu | Turangi Zone Substation | Switchgear : Fuse Carriers | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 24 | 24163 | 1200 | 0.04966 | 0.00099325 | 150 | 7499 | 2008/2009 | January-2009 | 1 | 2009
21327 | SH3 Soler's Spur | 2009-01-30 08:40 | 2009-01-30 | 2009-01-30 11:01 | Calculated | 1523 | 1523 - ABS 1523 |  | 128SEG1523 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 6 | 24163 | 846 | 0.03501 | 0.00024831 | 28 | 3948 | 2008/2009 | January-2009 | 1 | 2009
21328 | Main Rd South | 2009-02-01 10:45 | 2009-02-01 | 2009-02-01 11:47 | Calculated | 10K06 | 10K06 - 1ph 15kVA POLEMNT |  | 409SEG5403-5662RET | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 2 | 24176 | 124 | 0.00513 | 8.2727e-05 | 15 | 930 | 2008/2009 | February-2009 | 2 | 2009
21329 | Waitete Road | 2009-02-01 12:20 | 2009-02-01 | 2009-02-01 12:43 | Calculated | T445 | T445 - 3ph 200kVA POL |  | 105SEG204-202 | Te Kuiti Town 105-01 | Urban A | Te Kuiti Town | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 21 | 24176 | 483 | 0.01998 | 0.00086863 | 200 | 4599 | 2008/2009 | February-2009 | 2 | 2009
21330 | Karangahape Road | 2009-02-01 13:21 | 2009-02-01 | 2009-02-01 15:10 | Calculated | 07Q04 | 07Q04 - 1ph 10kVA POLEMNT |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 1 | 24176 | 109 | 0.00451 | 4.1363e-05 | 10 | 1090 | 2008/2009 | February-2009 | 2 | 2009
21331 | Tokaanu | 2009-02-01 20:23 | 2009-02-01 | 2009-02-01 21:47 | Calculated | 5979 | 5979 - ABS 3 Phase 5979 |  | No Segment | Tokaanu / Kuratau 607-01 | Urban A | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24176 |  | 0 | 0 |  |  | 2008/2009 | February-2009 | 2 | 2009
21332 | Cnr SH4 & Tangitu Road | 2009-02-02 13:45 | 2009-02-02 | 2009-02-02 16:50 | Calculated | 1356 | 1356 - Earth Working Link 1356 |  | 115SEG1356-1725 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 9 | 24176 | 1665 | 0.06887 | 0.00037227 | 105 | 19425 | 2008/2009 | February-2009 | 2 | 2009
21333 | Hingarae Road | 2009-02-02 19:30 | 2009-02-02 | 2009-02-02 22:25 | Calculated | 03R02 | 03R02 - 2ph 15kVA polemount |  | 124SEG5536 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 2 | 24176 | 350 | 0.01448 | 8.2727e-05 | 15 | 2625 | 2008/2009 | February-2009 | 2 | 2009
21334 | Thames Street | 2009-02-03 10:10 | 2009-02-03 | 2009-02-03 15:35 | Calculated | 20L55 | 20L55 - 1ph 15kVA POL |  | 415SEG5699-5695 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 325 | 3 | 24176 | 975 | 0.04033 | 0.00012409 | 15 | 4875 | 2008/2009 | February-2009 | 2 | 2009
21337 | Te Waitere Road | 2009-02-04 08:47 | 2009-02-04 | 2009-02-04 11:11 | Calculated | T547 | T547 - 3ph 300kVA GMT | TF547 - Transformer Fuse: TF547 | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 19 | 24176 | 2736 | 0.11317 | 0.0007859 | 300 | 43199 | 2008/2009 | February-2009 | 2 | 2009
21340 | Te Waitere Road | 2009-02-05 08:18 | 2009-02-05 | 2009-02-05 13:42 | Calculated | T1474 | T1474 - 3ph 25kVA POLEMNT |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 6 | 24176 | 1944 | 0.08041 | 0.00024818 | 25 | 8099 | 2008/2009 | February-2009 | 2 | 2009
21343 | Old Horopito Road | 2009-02-05 10:04 | 2009-02-05 | 2009-02-05 12:31 | Calculated | 5980 | 5980 - Fused Link 5980 |  | 415SEG5980 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 147 | 5 | 24176 | 735 | 0.0304 | 0.00020682 | 20 | 2939 | 2008/2009 | February-2009 | 2 | 2009
21344 | Marakopa Road | 2009-02-05 23:31 | 2009-02-05 | 2009-02-06 01:15 | Calculated | 296 | 296 - Sectionaliser with Bypass 296 |  | No Segment | No Asset Group | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 139 | 24176 | 14456 | 0.59795 | 0.0057495 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21345 | Marotiri Road | 2009-02-07 20:45 | 2009-02-07 | 2009-02-07 23:07 | Calculated | T2851 | T2851 - 3ph 15kVA POLEMNT |  | No Segment | No Asset Group | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 3 | 24176 | 426 | 0.01762 | 0.00012409 | 15 | 2130 | 2008/2009 | February-2009 | 2 | 2009
21346 | Body's Road | 2009-02-08 12:50 | 2009-02-08 | 2009-02-08 18:08 | Calculated | 5935 | 5935 - FUSE SWITCH |  | 408SEG5935-5936 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 318 | 48 | 24176 | 13176 | 0.545 | 0.0019854 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21349 | Coutts Road | 2009-02-09 18:08 | 2009-02-09 | 2009-02-09 21:38 | Calculated | 296 | 296 - Sectionaliser with Bypass 296 |  | No Segment | No Asset Group | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 210 | 139 | 24176 | 31300 | 1.2947 | 0.0057495 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21350 | Mangaorongo road | 2009-02-10 06:15 | 2009-02-10 | 2009-02-10 09:27 | Calculated | 1519 | 1519 - Recloser 1519 |  | 113SEG1519-1541 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation | OH Lines : Conductor - Insulated Copper | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 192 | 22 | 24176 | 5753 | 0.23796 | 0.00090999 | 138 | 34736 | 2008/2009 | February-2009 | 2 | 2009
21351 | Marotiri Road | 2009-02-10 08:32 | 2009-02-10 | 2009-02-10 09:44 | Calculated | 474 | 474 - Recloser with Bypass & Links 474 |  | 123SEG441-474 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 55 | 24176 | 5958 | 0.24644 | 0.002275 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21353 | Pukehou road | 2009-02-10 09:50 | 2009-02-10 | 2009-02-10 13:49 | Calculated | 09L06 | 09L06 - 1ph 10kVA POLEMNT |  | 407SEG5868-5126 | Manunui 407-01 (was Affco) | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 5 | 24176 | 1195 | 0.04943 | 0.00020682 | 10 | 2390 | 2008/2009 | February-2009 | 2 | 2009
21354 | Grace Road | 2009-02-10 10:35 | 2009-02-10 | 2009-02-10 12:05 | Calculated | 10S06 | 10S06 - 3ph 100kVA POLEMOUNT |  | No Segment | No Asset Group | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 9 | 24176 | 810 | 0.0335 | 0.00037227 | 100 | 8999 | 2008/2009 | February-2009 | 2 | 2009
21355 | Karangahape Road | 2009-02-10 12:10 | 2009-02-10 | 2009-02-10 13:46 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 39 | 24176 | 3744 | 0.15486 | 0.0016132 | 348.5 | 33455 | 2008/2009 | February-2009 | 2 | 2009
21356 | Oio No.2 Road | 2009-02-10 12:15 | 2009-02-10 | 2009-02-10 14:03 | Calculated | 12J10 | 12J10 - 1ph 25kVA POLEMNT |  | 409SEG5748-5743 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation | Switchgear : Fuse Carriers | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 1 | 24176 | 108 | 0.00447 | 4.1363e-05 | 25 | 2700 | 2008/2009 | February-2009 | 2 | 2009
21357 | Ohakune sub | 2009-02-10 13:22 | 2009-02-10 | 2009-02-10 13:35 | Calculated | 5004 | 5004 - Ohakune POS 11kV SF6 CB Tangiwai Feeder 5004 |  | No Segment | 517-01 Transpower Ohakune | Urban A | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 634 | 24176 | 8242 | 0.34092 | 0.026224 | 11340 | 147420 | 2008/2009 | February-2009 | 2 | 2009
21358 | Mangare Road | 2009-02-11 06:00 | 2009-02-11 | 2009-02-11 11:17 | Calculated | T1314 | T1314 - 3ph 30kVA polemnt |  | 121SEG435 | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 317 | 19 | 24176 | 1733 | 0.07168 | 0.0007859 | 220 | 13969 | 2008/2009 | February-2009 | 2 | 2009
21359 | Ngapuke Sub | 2009-02-11 09:06 | 2009-02-11 | 2009-02-11 09:13 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 7 | 74 | 24176 | 1702 | 0.0704 | 0.0030609 | 493 | 11338 | 2008/2009 | February-2009 | 2 | 2009
21360 | New River Road Sub | 2009-02-11 10:03 | 2009-02-11 | 2009-02-11 12:55 | Calculated | 5594 | 5594 - Sectionaliser with Bypass & Links 5594 |  | 403SEG5594-5601 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 172 | 35 | 24176 | 5760 | 0.23825 | 0.0014477 | 258 | 42295 | 2008/2009 | February-2009 | 2 | 2009
21361 | borough sub | 2009-02-12 04:38 | 2009-02-12 | 2009-02-12 04:48 | Calculated | 5992 | 5992 - 33kV Oil Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 1214 | 24176 | 12140 | 0.50215 | 0.050215 | 9214.5 | 92144 | 2008/2009 | February-2009 | 2 | 2009
21362 | Ohakune Sub | 2009-02-12 05:26 | 2009-02-12 | 2009-02-12 05:35 | Calculated | 5004 | 5004 - Ohakune POS 11kV SF6 CB Tangiwai Feeder 5004 |  | No Segment | 517-01 Transpower Ohakune | Urban A | Tangiwai | Direct from Ohakune Supply | OH Lines : Insulator - Pin | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 634 | 24176 | 54860 | 2.2692 | 0.026224 | 11340 | 1019480 | 2008/2009 | February-2009 | 2 | 2009
21363 | Pole 41 - Before McColl | 2009-02-12 07:50 | 2009-02-12 | 2009-02-12 12:30 | Calculated | 1632 | 1632 - Sectionaliser with Incoming Link1632 |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 280 | 10 | 24176 | 2800 | 0.11582 | 0.00041363 | 94.5 | 26460 | 2008/2009 | February-2009 | 2 | 2009
21365 | Poro-o-tarao By Pattersons's | 2009-02-12 09:04 | 2009-02-12 | 2009-02-12 09:13 | Calculated | 1737 | 1737 - Earth Working Link 1737 |  | 103SEG1346-1326 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 13 | 24176 | 3082 | 0.12748 | 0.00053772 | 62.5 | 14845 | 2008/2009 | February-2009 | 2 | 2009
21367 | Forest Road | 2009-02-12 10:21 | 2009-02-12 | 2009-02-12 15:28 | Calculated | 695 | 695 - ABS 695 |  | 123SEG473-695RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 5 | 24176 | 1535 | 0.06349 | 0.00020682 | 615 | 188805 | 2008/2009 | February-2009 | 2 | 2009
21368 | Whakamaru - Ataimuri Leg | 2009-02-12 15:40 | 2009-02-12 | 2009-02-12 15:49 | Calculated | 1720 | 1720 - 33kV Vacuum Circuit Breaker 1720 |  | 310SEG1025X-2196 | 214-01 Whakamaru | Rural D | Whakamaru 33 | Direct from Whakamaru Supply |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 704 | 24176 | 6336 | 0.26208 | 0.02912 | 7584 | 68255 | 2008/2009 | February-2009 | 2 | 2009
21369 | Ohakune sub | 2009-02-12 16:15 | 2009-02-12 | 2009-02-12 16:21 | Calculated | 5004 | 5004 - Ohakune POS 11kV SF6 CB Tangiwai Feeder 5004 |  | No Segment | 517-01 Transpower Ohakune | Urban A | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 445 | 24176 | 15416 | 0.63766 | 0.018407 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21372 | Taumatatotoro West | 2009-02-13 07:42 | 2009-02-13 | 2009-02-13 12:43 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 301 | 8 | 24176 | 2408 | 0.0996 | 0.00033091 | 58 | 17458 | 2008/2009 | February-2009 | 2 | 2009
21373 | Miro Stree & Willow Lane | 2009-02-13 09:05 | 2009-02-13 | 2009-02-13 13:49 | Calculated | 6321 | 6321 - Fuse Link 6321 |  | 103SEG453- Temp Link between Pole 544 & Pole 538 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 284 | 39 | 24176 | 11076 | 0.45814 | 0.0016132 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21374 | SH 3 - Paemako | 2009-02-13 15:05 | 2009-02-13 | 2009-02-13 16:48 | Calculated | T1850 | T1850 - 3ph 50kVA POLEMNT |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 3 | 24176 | 309 | 0.01278 | 0.00012409 | 50 | 5149 | 2008/2009 | February-2009 | 2 | 2009
21375 | Mt Ruapehu - By Water Tower | 2009-02-14 00:46 | 2009-02-14 | 2009-02-14 02:04 | Calculated | 5990 | 5990 - CIRCUIT BREAKER 5990 |  | 419SEG5990-5991 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Third Party (includeds unauthorised contractors) | Fire | 3PAR:EFIR:EFIB | Fire (Not Electrical) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 21 | 24176 | 9532 | 0.39428 | 0.00086863 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21376 | Te Kumi Road - By Paramount | 2009-02-14 06:11 | 2009-02-14 | 2009-02-14 06:28 | Calculated | 299 | 299 - ABS 299 |  | 107SEG299-218 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24176 |  | 0 | 0 |  |  | 2008/2009 | February-2009 | 2 | 2009
21377 | Makino road | 2009-02-16 08:00 | 2009-02-16 | 2009-02-16 10:09 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 28 | 24176 | 3612 | 0.1494 | 0.0011582 | 183.5 | 23671 | 2008/2009 | February-2009 | 2 | 2009
21379 | Denzil Drive | 2009-02-17 08:25 | 2009-02-17 | 2009-02-17 16:45 | Calculated | T4118 | T4118 - 3ph 30kVA POLEMNT |  | No Segment | No Asset Group | Rural D | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 500 | 3 | 24176 | 1500 | 0.06205 | 0.00012409 | 15 | 7500 | 2008/2009 | February-2009 | 2 | 2009
21380 | S.H.3 Near Tunnel | 2009-02-17 09:35 | 2009-02-17 | 2009-02-17 15:42 | Calculated | 1602 | 1602 - Earth Working Link 1602 |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 367 | 488 | 24176 | 1952 | 0.08074 | 0.020185 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21381 | Ongarue/Tapuwahine Sub | 2009-02-17 11:11 | 2009-02-17 | 2009-02-17 14:21 | Calculated | 5462 | 5462 - Sectionaliser with Bypass & Links 5462 |  | 421SEG6554-5462RET | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 88 | 24176 | 1492 | 0.06171 | 0.00364 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21383 | Owaewenga Road | 2009-02-17 14:20 | 2009-02-17 | 2009-02-17 15:11 | Calculated | T839 | T839 - 1ph 10kVA POLEMNT |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation | Miscellaneous : Other Miscellaneous | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 2 | 24176 | 102 | 0.00422 | 8.2727e-05 | 10 | 510 | 2008/2009 | February-2009 | 2 | 2009
21385 | Karangahape Road West | 2009-02-18 10:06 | 2009-02-18 | 2009-02-18 12:07 | Calculated | 5593 | 5593 - Solid Link 5593 |  | 426SEG5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 4 | 24176 | 484 | 0.02002 | 0.00016545 | 40 | 4840 | 2008/2009 | February-2009 | 2 | 2009
21387 | S.H. 41 - Tap Off to Omori | 2009-02-18 10:15 | 2009-02-18 | 2009-02-18 10:47 | Calculated | 5688 | 5688 - Solid Link 5688 |  | 406SEG6355-6353 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 323 | 24176 | 12331 | 0.51005 | 0.01336 | 1630 | 78759 | 2008/2009 | February-2009 | 2 | 2009
21388 | Taringamotu Road | 2009-02-19 12:34 | 2009-02-19 | 2009-02-19 13:54 | Calculated | 07I42 | 07I42 - 2ph 15kVA POLEMNT |  | 402SEG5923-5103 | Northern 402-05 | Rural C | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 80 | 3 | 24176 | 240 | 0.00993 | 0.00012409 | 15 | 1200 | 2008/2009 | February-2009 | 2 | 2009
21389 | Main North Road - Piopio | 2009-02-19 14:34 | 2009-02-19 | 2009-02-19 15:10 | Calculated | T1581 | T1581 - 1ph 15kVA POL |  | No Segment | No Asset Group | Rural C | Te Kuiti South | Waitete Zone Substation | Transformers : Other | Transpower | Transmission | TRAN:TFLT2:TFLT1 | Transpower Unplanned Outage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 2 | 24176 | 72 | 0.00298 | 8.2727e-05 | 15 | 540 | 2008/2009 | February-2009 | 2 | 2009
21390 | Mangahauhau Valley Road | 2009-02-20 07:15 | 2009-02-20 | 2009-02-20 09:29 | Calculated | 5717 | 5717 - Fused Link 5717 |  | 416SEG5717 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 5 | 24176 | 670 | 0.02771 | 0.00020682 | 45 | 6030 | 2008/2009 | February-2009 | 2 | 2009
21391 | Pureora Village | 2009-02-20 07:18 | 2009-02-20 | 2009-02-20 10:35 | Calculated | 456 | 456 - Fused Link 456 |  | 119SEG456 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 13 | 24176 | 2561 | 0.10593 | 0.00053772 | 60 | 11819 | 2008/2009 | February-2009 | 2 | 2009
21392 | Mangateitei Road | 2009-02-20 08:21 | 2009-02-20 | 2009-02-20 08:58 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply | OH Lines : Jumper - Bare ACSR | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 29 | 24176 | 1073 | 0.04438 | 0.0011995 | 285 | 10544 | 2008/2009 | February-2009 | 2 | 2009
21393 | Smiths Road | 2009-02-20 10:36 | 2009-02-20 | 2009-02-20 14:09 | Calculated | 390 | 390 - ABS 390 |  | 110SEG390-2144 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation | OH Lines : Pole - Softwood | Asset Related | Pole | FAIL:FPOL2:FPOR | Pole Down - Rotten | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 213 | 19 | 24176 | 4047 | 0.1674 | 0.0007859 | 185 | 39404 | 2008/2009 | February-2009 | 2 | 2009
21394 | Ongarue Road | 2009-02-20 13:35 | 2009-02-20 | 2009-02-21 13:46 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1451 | 11 | 24176 | 5027 | 0.20793 | 0.000455 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21395 | Hangatiki | 2009-02-20 15:16 | 2009-02-20 | 2009-02-20 15:18 | Calculated | 1271 | 1271 - Vacuum Circuit Breaker 1271 |  | No Segment | 204-01 Hangatiki | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 71 | 24176 | 142 | 0.00587 | 0.0029368 | 1740 | 3479 | 2008/2009 | February-2009 | 2 | 2009
21396 | Mangarino Road | 2009-02-20 16:32 | 2009-02-20 | 2009-02-20 16:46 | Calculated | 191 | 191 - ABS 191 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 3 | 24176 | 42 | 0.00174 | 0.00012409 | 1100 | 15400 | 2008/2009 | February-2009 | 2 | 2009
21397 | Gadsby Road | 2009-02-20 23:13 | 2009-02-20 | 2009-02-20 23:21 | Calculated | 594 | 594 - 33kV Oil Circuit Breaker 594 |  | No Segment | 205-01 Gadsby Road | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 1578 | 24176 | 12624 | 0.52217 | 0.065271 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21398 | Marakopa Road | 2009-02-21 02:17 | 2009-02-21 | 2009-02-21 08:45 | Calculated | 296 | 296 - Sectionaliser with Bypass 296 |  | No Segment | No Asset Group | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 388 | 88 | 24176 | 43560 | 1.8018 | 0.00364 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21399 | Waitete Road | 2009-02-21 15:36 | 2009-02-21 | 2009-02-21 15:45 | Calculated | 107 | 107 - Circuit Breaker with Bypass & Links 107 |  | 103SEG107-REG7 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 406 | 24176 | 6902 | 0.28549 | 0.016794 | 3099.5 | 52691 | 2008/2009 | February-2009 | 2 | 2009
21400 | Makino Road | 2009-02-23 06:00 | 2009-02-23 | 2009-02-23 20:27 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 867 | 46 | 24176 | 22683 | 0.93824 | 0.0019027 | 426.5 | 214984 | 2008/2009 | February-2009 | 2 | 2009
21404 | Ruatiti Sub | 2009-02-23 08:42 | 2009-02-23 | 2009-02-23 08:46 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 394 | 247 | 24176 | 9886 | 0.40892 | 0.010217 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21405 | Main North Road | 2009-02-23 10:50 | 2009-02-23 | 2009-02-23 13:28 | Calculated | T1581 | T1581 - 1ph 15kVA POL |  | No Segment | No Asset Group | Rural C | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 2 | 24176 | 316 | 0.01307 | 8.2727e-05 | 15 | 2370 | 2008/2009 | February-2009 | 2 | 2009
21406 | Taharoa Road | 2009-02-23 14:30 | 2009-02-23 | 2009-02-23 15:22 | Calculated | 268 | 268 - ABS 268 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) | OH Lines : Pole - Other | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 95 | 24176 | 4940 | 0.20433 | 0.0039295 | 750.5 | 39025 | 2008/2009 | February-2009 | 2 | 2009
21407 | S.H. 30 | 2009-02-24 09:48 | 2009-02-24 | 2009-02-24 11:09 | Calculated | REG1401 | REG1401 - Puketutu 1ph Voltage Regulator |  | No Segment | Benneydale 103-05 | Rural D | No Feeder |  |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 236 | 24176 | 19116 | 0.7907 | 0.0097617 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21408 | Near tunnel | 2009-02-24 10:57 | 2009-02-24 | 2009-02-24 15:28 | Calculated | 1603 | 1603 - Circuit Breaker 1603 |  | No Segment | No Asset Group | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 271 | 489 | 24176 | 1839 | 0.07607 | 0.020227 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21409 | Waitanguru | 2009-02-24 11:40 | 2009-02-24 | 2009-02-24 13:49 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 11 | 24176 | 1419 | 0.05869 | 0.000455 | 58 | 7482 | 2008/2009 | February-2009 | 2 | 2009
21410 | Manunui Sub | 2009-02-24 14:48 | 2009-02-24 | 2009-02-24 15:18 | Calculated | 5132 | 5132 - Manunui SF6 CB Southern Feeder 5132 |  | No Segment | 510-01 Manunui | Rural B | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 10 | 24176 | 640 | 0.02647 | 0.00041363 | 125 | 7999 | 2008/2009 | February-2009 | 2 | 2009
21411 | Near Tunnel | 2009-02-25 09:32 | 2009-02-25 | 2009-02-25 15:17 | Calculated | 1603 | 1603 - Circuit Breaker 1603 |  | No Segment | No Asset Group | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 345 | 489 | 24176 | 2354 | 0.09737 | 0.020227 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21412 | Pureora Village | 2009-02-25 16:40 | 2009-02-25 | 2009-02-25 19:04 | Calculated | 456 | 456 - Fused Link 456 |  | 119SEG456 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 13 | 24176 | 1872 | 0.07743 | 0.00053772 | 60 | 8639 | 2008/2009 | February-2009 | 2 | 2009
21413 | Near Tunnel | 2009-02-26 09:33 | 2009-02-26 | 2009-02-26 15:04 | Calculated | 1603 | 1603 - Circuit Breaker 1603 |  | No Segment | No Asset Group | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 93 | 484 | 24176 | 48118 | 1.9903 | 0.02002 | 3509 | 123745 | 2008/2009 | February-2009 | 2 | 2009
21414 | Waitete Road - Hardy's Hill | 2009-02-27 07:30 | 2009-02-27 | 2009-02-27 08:33 | Calculated | 107 | 107 - Circuit Breaker with Bypass & Links 107 |  | 103SEG107-REG7 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation | OH Lines : Pole Fittings e.g OCB Hangers | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 295 | 24176 | 18558 | 0.76762 | 0.012202 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21415 | Near Tunnel - By Telecom R | 2009-02-27 09:38 | 2009-02-27 | 2009-02-27 15:52 | Calculated | 1603 | 1603 - Circuit Breaker 1603 |  | No Segment | No Asset Group | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 489 | 24176 | 2354 | 0.09737 | 0.020227 | 3509.5 | 1316062 | 2008/2009 | February-2009 | 2 | 2009
21419 | Sandel Road | 2009-02-28 07:15 | 2009-02-28 | 2009-02-28 08:08 | Calculated | T2613 | T2613 - 3ph 25kVA POLEMNT |  | 120SEG410-632 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 1 | 24176 | 53 | 0.00219 | 4.1363e-05 | 25 | 1325 | 2008/2009 | February-2009 | 2 | 2009
21420 | Ruatiti Sub | 2009-02-28 08:33 | 2009-02-28 | 2009-02-28 14:55 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 382 | 46 | 24176 | 14950 | 0.61838 | 0.0019027 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21421 | Turn off to Raurimu Township | 2009-02-28 09:30 | 2009-02-28 | 2009-02-28 09:58 | Calculated | 5543 | 5543 - Fused Link 5543 |  | 410SEG5543-5161 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 124 | 24176 | 17690 | 0.73172 | 0.0051291 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21423 | Manunui - Tokaanu Highway | 2009-02-28 09:41 | 2009-02-28 | 2009-02-28 18:38 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 537 | 25 | 24176 | 13425 | 0.5553 | 0.0010341 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21425 | Matiere Road | 2009-02-28 09:53 | 2009-02-28 | 2009-02-28 11:31 | Calculated | T1980 | T1980 - 3ph 30kVA POLEMNT |  | 114SEG1116-1113 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 3 | 24176 | 294 | 0.01216 | 0.00012409 | 30 | 2940 | 2008/2009 | February-2009 | 2 | 2009
21434 | Mangakahu Road | 2009-02-28 10:05 | 2009-02-28 | 2009-02-28 20:48 | Calculated | 5108 | 5108 - Sectionaliser with Bypass 5108 |  | 402SEG5115-5108 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 643 | 22 | 24176 | 14146 | 0.58513 | 0.00090999 | 160 | 102880 | 2008/2009 | February-2009 | 2 | 2009
21427 | Ounga Valley Road | 2009-02-28 10:43 | 2009-02-28 | 2009-02-28 11:17 | Calculated | 5515 | 5515 - Earth Working Link 5515 |  | 408SEG5515 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 13 | 24176 | 442 | 0.01828 | 0.00053772 | 78 | 2652 | 2008/2009 | February-2009 | 2 | 2009
21428 | Waikawau - E/W Sub | 2009-02-28 11:00 | 2009-02-28 | 2009-02-28 12:38 | Calculated | 1610 | 1610 - Recloser 1610 | 1611 - Fused Link 1611 | No Segment | No Asset Group | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 49 | 24176 | 4802 | 0.19863 | 0.0020268 | 375.5 | 36799 | 2008/2009 | February-2009 | 2 | 2009
21429 | Echolands - Water Treatment | 2009-02-28 11:01 | 2009-02-28 | 2009-02-28 11:30 | Calculated | 1.27 | 1.27 - Fused Link 1.27 |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 6 | 24176 | 174 | 0.0072 | 0.00024818 | 25 | 725 | 2008/2009 | February-2009 | 2 | 2009
21430 | Owaewenga Road | 2009-02-28 12:12 | 2009-02-28 | 2009-02-28 16:05 | Calculated | 171 | 171 - Fused Link 171 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 233 | 7 | 24176 | 1631 | 0.06746 | 0.00028954 | 85 | 19805 | 2008/2009 | February-2009 | 2 | 2009
21431 | Owhango Road | 2009-02-28 12:19 | 2009-02-28 | 2009-02-28 15:38 | Calculated | TF10K13 | TF10K13 - Transformer Fuse: TF10K13 |  | No Segment | Southern 409-04 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 31 | 24176 | 6169 | 0.25517 | 0.0012823 | 200 | 39799 | 2008/2009 | February-2009 | 2 | 2009
21436 | Rata Street | 2009-02-28 13:28 | 2009-02-28 | 2009-02-28 16:11 | Calculated | 08J46 | 08J46 - 3ph 200kVA GNDPAD |  | 408SEG5390-5621 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 40 | 24176 | 6520 | 0.26969 | 0.0016545 | 250 | 40749 | 2008/2009 | February-2009 | 2 | 2009
21433 | Onaio road | 2009-02-28 14:26 | 2009-02-28 | 2009-02-28 15:45 | Calculated | T2047 | T2047 - 3ph 30kVA POLEMNT |  | 114SEG1114 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 3 | 24176 | 237 | 0.0098 | 0.00012409 | 30 | 2370 | 2008/2009 | February-2009 | 2 | 2009
21440 | Owhango road | 2009-02-28 16:57 | 2009-02-28 | 2009-02-28 19:20 | Calculated | 10K26 | 10K26 - 1ph 100kVA POLEMNT |  | 409SEG5413-5425 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 21 | 24176 | 3003 | 0.12421 | 0.00086863 | 100 | 14299 | 2008/2009 | February-2009 | 2 | 2009
21441 | Newman Road | 2009-02-28 17:10 | 2009-02-28 | 2009-02-28 17:23 | Calculated | T1364 | T1364 - 1ph 15kVA POLEMNT |  | 122SEG379 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 3 | 24176 | 39 | 0.00161 | 0.00012409 | 15 | 195 | 2008/2009 | February-2009 | 2 | 2009
21442 | by Makomiko Sub | 2009-02-28 19:21 | 2009-02-28 | 2009-02-28 19:33 | Calculated | 5867 | 5867 - Recloser with Bypass 5867 |  | 409SEG5761-5867 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 296 | 24176 | 30008 | 1.2412 | 0.012244 | 0 | 0 | 2008/2009 | February-2009 | 2 | 2009
21443 | Makokmiko Sub | 2009-03-01 06:30 | 2009-03-01 | 2009-03-01 11:47 | Calculated | 5518 | 5518 - Fused Link 5518 |  | 409SEG5518-5598 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 317 | 44 | 24186 | 13948 | 0.5767 | 0.0018192 | 303 | 96050 | 2008/2009 | March-2009 | 3 | 2009
21444 | SH3 Cnr Lees Block Road | 2009-03-01 10:05 | 2009-03-01 | 2009-03-01 11:08 | Calculated | 248 | 248 - Fused Link 248 |  | 101SEG248 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 12 | 24186 | 756 | 0.03126 | 0.00049615 | 60 | 3780 | 2008/2009 | March-2009 | 3 | 2009
21446 | Waikune Prison | 2009-03-01 14:50 | 2009-03-01 | 2009-03-01 15:25 | Calculated | 16L02 | 16L02 - 3ph 200kVA polemnt |  | 411SEG5775-5329 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 8 | 24186 | 280 | 0.01158 | 0.00033077 | 100 | 3500 | 2008/2009 | March-2009 | 3 | 2009
21447 | Karangahape Road ISO Sub | 2009-03-01 14:58 | 2009-03-01 | 2009-03-01 18:57 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 39 | 24186 | 9321 | 0.38539 | 0.0016125 | 348.5 | 83291 | 2008/2009 | March-2009 | 3 | 2009
21448 | Tihoi Road | 2009-03-01 15:35 | 2009-03-01 | 2009-03-01 17:20 | Calculated | T2770 | T2770 - 3ph 50kVA polemount |  | No Segment | No Asset Group | Rural D | Tihoi | Marotiri Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 1 | 24186 | 105 | 0.00434 | 4.1346e-05 | 50 | 5250 | 2008/2009 | March-2009 | 3 | 2009
21449 | kururau | 2009-03-02 09:40 | 2009-03-02 | 2009-03-02 15:31 | Calculated | 1603 | 1603 - Circuit Breaker 1603 |  | No Segment | No Asset Group | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 351 | 489 | 24186 | 2239 | 0.09257 | 0.020218 | 3509.5 | 1235344 | 2008/2009 | March-2009 | 3 | 2009
21451 | Bullians Road | 2009-03-02 12:50 | 2009-03-02 | 2009-03-02 14:16 | Calculated | 12K04 | 12K04 - 1ph 50kVA POLEMNT |  | 409SEG5335-5113 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 7 | 24186 | 602 | 0.02489 | 0.00028942 | 50 | 4299 | 2008/2009 | March-2009 | 3 | 2009
21452 | Kawautahi road | 2009-03-02 13:48 | 2009-03-02 | 2009-03-02 15:23 | Calculated | 5751 | 5751 - Earth Working Link 5751 |  | 409SEG5751-5401 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 7 | 24186 | 665 | 0.0275 | 0.00028942 | 58 | 5510 | 2008/2009 | March-2009 | 3 | 2009
21455 | SH 3 Near tunnel | 2009-03-04 09:32 | 2009-03-04 | 2009-03-04 16:37 | Calculated | 1602 | 1602 - Earth Working Link 1602 |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 425 | 488 | 24186 | 3152 | 0.13032 | 0.020177 | 3554.5 | 1521191 | 2008/2009 | March-2009 | 3 | 2009
21456 | Marotiri Sub | 2009-03-04 19:54 | 2009-03-04 | 2009-03-04 21:29 | Calculated | CB2 | CB2 - SF6 Tihoi Feeder Breaker CB2 |  | No Segment | Whakamaru-33 310-03 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 240 | 24186 | 51463 | 2.1278 | 0.0099231 | 0 | 0 | 2008/2009 | March-2009 | 3 | 2009
21457 | Tunakotekote road | 2009-03-05 07:45 | 2009-03-05 | 2009-03-05 09:18 | Calculated | 09I11 | 09I11 - 1ph 3kVA POLEMNT |  | 403SEG5811-5315 | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 1 | 24186 | 93 | 0.00385 | 4.1346e-05 | 3 | 279 | 2008/2009 | March-2009 | 3 | 2009
21458 | Paewhenua Road | 2009-03-05 08:43 | 2009-03-05 | 2009-03-05 10:56 | Calculated | T685 | T685 - 3ph 10kVA polemnt |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 1 | 24186 | 133 | 0.0055 | 4.1346e-05 | 10 | 1330 | 2008/2009 | March-2009 | 3 | 2009
21460 | SH 3 Near Tunnel | 2009-03-05 09:45 | 2009-03-05 | 2009-03-05 15:27 | Calculated | 1602 | 1602 - Earth Working Link 1602 |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 488 | 24186 | 1852 | 0.07657 | 0.020177 | 100 | 34255 | 2008/2009 | March-2009 | 3 | 2009
21461 | Flemngs Road | 2009-03-05 13:29 | 2009-03-05 | 2009-03-05 13:43 | Calculated | T186 | T186 - 3ph 50kVA POLEMNT |  | 110SEG390-2144 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 4 | 24186 | 56 | 0.00232 | 0.00016538 | 50 | 700 | 2008/2009 | March-2009 | 3 | 2009
21462 | Owaewenga Road | 2009-03-05 15:30 | 2009-03-05 | 2009-03-05 16:54 | Calculated | 171 | 171 - Fused Link 171 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 7 | 24186 | 588 | 0.02431 | 0.00028942 | 85 | 7140 | 2008/2009 | March-2009 | 3 | 2009
21464 | Poihipi Road | 2009-03-06 10:14 | 2009-03-06 | 2009-03-06 13:33 | Calculated | T1538 | T1538 - 1ph 10kVA POLEMNT |  | 123SEG472-698 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 199 | 1 | 24186 | 199 | 0.00823 | 4.1346e-05 | 15 | 2985 | 2008/2009 | March-2009 | 3 | 2009
21465 | Waimahora Road | 2009-03-06 11:30 | 2009-03-06 | 2009-03-06 14:00 | Calculated | T1290 | T1290 - 1ph 5kVA POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 4 | 24186 | 600 | 0.02481 | 0.00016538 | 55 | 8250 | 2008/2009 | March-2009 | 3 | 2009
21466 | Te Kumi Station road | 2009-03-07 10:40 | 2009-03-07 | 2009-03-07 11:18 | Calculated | 763 | 763 - Fused Link 763 |  | 108SEG763-2140 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 2 | 24186 | 76 | 0.00314 | 8.2692e-05 | 330 | 12540 | 2008/2009 | March-2009 | 3 | 2009
21467 | Burnanad road | 2009-03-07 13:59 | 2009-03-07 | 2009-03-07 14:50 | Calculated | 09K22 | 09K22 - 2ph 10kVA POLEMNT |  | 409SEG5549 | Southern 409-02 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 3 | 24186 | 153 | 0.00633 | 0.00012404 | 10 | 509 | 2008/2009 | March-2009 | 3 | 2009
21468 | Heuheu Parade | 2009-03-07 16:45 | 2009-03-07 | 2009-03-07 17:05 | Calculated | 09T03 | 09T03 - 3ph 200kVA POLEMNT |  | No Segment | No Asset Group | Rural D | Oruatua | Kiko Road Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 35 | 24186 | 700 | 0.02894 | 0.0014471 | 100 | 1999 | 2008/2009 | March-2009 | 3 | 2009
21469 | Meringa Road | 2009-03-09 09:02 | 2009-03-09 | 2009-03-09 10:24 | Calculated | 5736 | 5736 - Fused Link 5736 |  | 408SEG5736-5341 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 82 | 88 | 24186 | 7216 | 0.29835 | 0.0036385 | 613 | 50265 | 2008/2009 | March-2009 | 3 | 2009
21471 | Kahorekau Road | 2009-03-09 10:50 | 2009-03-09 | 2009-03-09 14:05 | Calculated | T870 | T870 - 3ph 25kVA POLEMNT |  | No Segment | No Asset Group | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 195 | 4 | 24186 | 780 | 0.03225 | 0.00016538 | 25 | 4875 | 2008/2009 | March-2009 | 3 | 2009
21472 | Tihoi Road | 2009-03-09 11:08 | 2009-03-09 | 2009-03-09 15:19 | Calculated | T2824 | T2824 - 3ph 50kVA POLEMNT |  | No Segment | No Asset Group | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 251 | 1 | 24186 | 251 | 0.01038 | 4.1346e-05 | 50 | 12550 | 2008/2009 | March-2009 | 3 | 2009
21473 | Otukou Sub | 2009-03-09 12:03 | 2009-03-09 | 2009-03-09 13:48 | Calculated | 5584 | 5584 - Recloser with Bypass & Links 5584 |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 73 | 24186 | 13177 | 0.54482 | 0.0030183 | 336 | 57327 | 2008/2009 | March-2009 | 3 | 2009
21470 | Ngapuke Sub | 2009-03-09 12:04 | 2009-03-09 | 2009-03-09 12:06 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 74 | 24186 | 148 | 0.00612 | 0.0030596 | 493 | 985 | 2008/2009 | March-2009 | 3 | 2009
21474 | Waimahora Road | 2009-03-09 12:45 | 2009-03-09 | 2009-03-09 15:25 | Calculated | T1290 | T1290 - 1ph 5kVA POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 4 | 24186 | 640 | 0.02646 | 0.00016538 | 55 | 8800 | 2008/2009 | March-2009 | 3 | 2009
21475 | Whittington Lane | 2009-03-09 23:01 | 2009-03-09 | 2009-03-09 23:46 | Calculated | T1086 | T1086 - 3ph 200kVA GNDPAD |  | No Segment | No Asset Group | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 20 | 24186 | 900 | 0.03721 | 0.00082692 | 200 | 9000 | 2008/2009 | March-2009 | 3 | 2009
21476 | Near Tunnel - By Telecom | 2009-03-10 09:37 | 2009-03-10 | 2009-03-10 15:10 | Calculated | 1603 | 1603 - Circuit Breaker 1603 |  | No Segment | No Asset Group | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 23 | 489 | 24186 | 2633 | 0.10886 | 0.020218 | 55 | 2475 | 2008/2009 | March-2009 | 3 | 2009
21478 | Tunakotekote Road | 2009-03-11 07:37 | 2009-03-11 | 2009-03-11 09:54 | Calculated | 09I11 | 09I11 - 1ph 3kVA POLEMNT |  | 403SEG5811-5315 | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 1 | 24186 | 137 | 0.00566 | 4.1346e-05 | 3 | 411 | 2008/2009 | March-2009 | 3 | 2009
21479 | SH 30 Pureora | 2009-03-11 08:40 | 2009-03-11 | 2009-03-11 10:53 | Calculated | T982 | T982 - 1ph 10kVA POLEMNT |  | 119SEG710 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 1 | 24186 | 133 | 0.0055 | 4.1346e-05 | 10 | 1330 | 2008/2009 | March-2009 | 3 | 2009
21480 | Owaewenga Road | 2009-03-11 09:05 | 2009-03-11 | 2009-03-11 10:58 | Calculated | 171 | 171 - Fused Link 171 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 7 | 24186 | 791 | 0.0327 | 0.00028942 | 85 | 9605 | 2008/2009 | March-2009 | 3 | 2009
21481 | Mahoenui Substation | 2009-03-11 09:34 | 2009-03-11 | 2009-03-11 15:31 | Calculated | 1358 | 1358 - ABS1358 |  | 128SEG1358-1602 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 357 | 498 | 24186 | 5522 | 0.22831 | 0.02059 | 428 | 153196 | 2008/2009 | March-2009 | 3 | 2009
21485 | Manunui - Tokaanu Highway | 2009-03-11 15:10 | 2009-03-11 | 2009-03-11 17:39 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 37 | 24186 | 6894 | 0.28504 | 0.0015298 | 227.5 | 42017 | 2008/2009 | March-2009 | 3 | 2009
21486 | Taumatatotoro West | 2009-03-11 16:10 | 2009-03-11 | 2009-03-11 19:15 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 8 | 24186 | 1480 | 0.06119 | 0.00033077 | 58 | 10730 | 2008/2009 | March-2009 | 3 | 2009
21487 | Marokopa Road | 2009-03-12 10:50 | 2009-03-12 | 2009-03-12 14:04 | Calculated | T1089 | T1089 - 1ph 15kVA POL |  | 125SEG296-583 | Coast 125-04 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 194 | 1 | 24186 | 194 | 0.00802 | 4.1346e-05 | 15 | 2910 | 2008/2009 | March-2009 | 3 | 2009
21489 | Hauhangaroa | 2009-03-12 16:20 | 2009-03-12 | 2009-03-12 18:38 | Calculated | 5177 | 5177 - ABS 5177 |  | 426SEG5177 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 1 | 24186 | 138 | 0.00571 | 4.1346e-05 | 5 | 690 | 2008/2009 | March-2009 | 3 | 2009
21490 | Owaewenga road | 2009-03-13 07:30 | 2009-03-13 | 2009-03-13 09:15 | Calculated | 171 | 171 - Fused Link 171 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 7 | 24186 | 4728 | 0.19548 | 0.00028942 | 85 | 57405 | 2008/2009 | March-2009 | 3 | 2009
21492 | Waikaka Road | 2009-03-13 14:25 | 2009-03-13 | 2009-03-13 14:55 | Calculated | 04E02 | 04E02 - 1ph 10kVA POLEMNT |  | No Segment | No Asset Group | Rural D | Tuhua | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 1 | 24186 | 30 | 0.00124 | 4.1346e-05 | 10 | 300 | 2008/2009 | March-2009 | 3 | 2009
21493 | Kururau Road | 2009-03-13 16:25 | 2009-03-13 | 2009-03-13 18:05 | Calculated | 5575 | 5575 - Earth Working Link 5575 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 1 | 24186 | 100 | 0.00413 | 4.1346e-05 | 15 | 1500 | 2008/2009 | March-2009 | 3 | 2009
21494 | Atirau road | 2009-03-14 09:04 | 2009-03-14 | 2009-03-14 16:30 | Calculated | 11S06 | 11S06 - 3ph 300kVA GNDPAD |  | No Segment | No Asset Group | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 446 | 8 | 24186 | 3568 | 0.14752 | 0.00033077 | 300 | 133800 | 2008/2009 | March-2009 | 3 | 2009
21495 | Waitanguru | 2009-03-15 08:45 | 2009-03-15 | 2009-03-15 11:12 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 11 | 24186 | 1617 | 0.06686 | 0.00045481 | 58 | 8526 | 2008/2009 | March-2009 | 3 | 2009
21496 | Whangaehu Valley Road | 2009-03-17 08:04 | 2009-03-17 | 2009-03-17 14:44 | Calculated | 5686 | 5686 - Fused Link 5686 |  | 416SEG5686 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 400 | 15 | 24186 | 6000 | 0.24808 | 0.00062019 | 130 | 51999 | 2008/2009 | March-2009 | 3 | 2009
21499 | Poihipi Road | 2009-03-18 11:01 | 2009-03-18 | 2009-03-18 13:02 | Calculated | 472 | 472 - ABS 472 |  | 123SEG472-698 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 29 | 24186 | 3509 | 0.14508 | 0.001199 | 480 | 58079 | 2008/2009 | March-2009 | 3 | 2009
21501 | National Park - behind service station | 2009-03-19 07:46 | 2009-03-19 | 2009-03-19 09:58 | Calculated | 5147 | 5147 - Circuit Breaker with Bypass 5147 |  | No Segment | No Asset Group | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | PTRN2 | POUT:PTRN2:PTRN1 | PTRN1 | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 132 | 37 | 24186 | 4884 | 0.20194 | 0.0015298 | 533 | 70355 | 2008/2009 | March-2009 | 3 | 2009
21502 | Mangatorota Stream Road | 2009-03-19 07:52 | 2009-03-19 | 2009-03-19 11:10 | Calculated | 08E02 | 08E02 - 1ph 10kVA POLEMNT |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 4 | 24186 | 792 | 0.03275 | 0.00016538 | 10 | 1980 | 2008/2009 | March-2009 | 3 | 2009
21508 | Waiparemo Cres | 2009-03-20 19:00 | 2009-03-20 | 2009-03-20 19:51 | Calculated | 09R35 | 09R35 - 3ph 300kVA GNDPAD |  | No Segment | No Asset Group | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 70 | 24186 | 3570 | 0.14761 | 0.0028942 | 300 | 15299 | 2008/2009 | March-2009 | 3 | 2009
21509 | Kawautahi road | 2009-03-22 14:05 | 2009-03-22 | 2009-03-22 15:00 | Calculated | 5884 | 5884 - Recloser 5884 |  | 409SEG5884-5403 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 29 | 24186 | 1595 | 0.06595 | 0.001199 | 225 | 12375 | 2008/2009 | March-2009 | 3 | 2009
21510 | Pioi Station | 2009-03-22 18:27 | 2009-03-22 | 2009-03-23 11:59 | Calculated | 1617 | 1617 - Fused Link 1617 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1052 | 2 | 24186 | 2104 | 0.08699 | 8.2692e-05 | 30 | 31560 | 2008/2009 | March-2009 | 3 | 2009
21511 | Manunui Sub | 2009-03-23 00:18 | 2009-03-23 | 2009-03-23 00:26 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 8 | 4 | 24186 | 32 | 0.00132 | 0.00016538 | 450 | 3600 | 2008/2009 | March-2009 | 3 | 2009
21512 | Princess Street | 2009-03-23 09:06 | 2009-03-23 | 2009-03-23 12:00 | Calculated | T1580 | T1580 - 3ph 300kVA POL |  | No Segment | No Asset Group | Urban A | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 174 | 1 | 24186 | 174 | 0.00719 | 4.1346e-05 | 300 | 52200 | 2008/2009 | March-2009 | 3 | 2009
21513 | SH3 Near tunnel | 2009-03-23 09:42 | 2009-03-23 | 2009-03-23 15:46 | Calculated | 1602 | 1602 - Earth Working Link 1602 |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 488 | 24186 | 3755 | 0.15526 | 0.020177 | 3554.5 | 39854 | 2008/2009 | March-2009 | 3 | 2009
21514 | Bayley road | 2009-03-23 14:00 | 2009-03-23 | 2009-03-23 23:58 | Calculated | T2343 | T2343 - 3ph 50kVA POLEMNT |  | 122SEG616 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 598 | 2 | 24186 | 1196 | 0.04945 | 8.2692e-05 | 50 | 29900 | 2008/2009 | March-2009 | 3 | 2009
21515 | Waikino Road | 2009-03-23 15:08 | 2009-03-23 | 2009-03-23 15:34 | Calculated | 426 | 426 - Sectionaliser with Bypass & Links 426 |  | 129SEG434-426 | Tihoi 124-03 RETIRED | Rural C | Tihoi | Marotiri Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 136 | 24186 | 13019 | 0.53829 | 0.0056231 | 0 | 0 | 2008/2009 | March-2009 | 3 | 2009
21516 | Benneydale - Tapuwae Road | 2009-03-24 08:31 | 2009-03-24 | 2009-03-24 09:47 | Calculated | T3280 | T3280 - 1ph 15kVA POLEMNT |  | 103SEG270RET | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 76 | 16 | 24186 | 7200 | 0.29769 | 0.00066154 | 90 | 36000 | 2008/2009 | March-2009 | 3 | 2009
21517 | SH# Near Tunnel | 2009-03-24 09:33 | 2009-03-24 | 2009-03-24 15:47 | Calculated | 1602 | 1602 - Earth Working Link 1602 |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 488 | 24186 | 3845 | 0.15898 | 0.020177 | 3554.5 | 1332837 | 2008/2009 | March-2009 | 3 | 2009
21518 | Sommerville road | 2009-03-24 10:03 | 2009-03-24 | 2009-03-24 13:33 | Calculated | 182 | 182 - ABS 182 |  | 108SEG182-505 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 210 | 38 | 24186 | 7980 | 0.32994 | 0.0015712 | 300 | 62999 | 2008/2009 | March-2009 | 3 | 2009
21519 | Manunui Sub | 2009-03-25 05:02 | 2009-03-25 | 2009-03-25 05:12 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 4 | 24186 | 40 | 0.00165 | 0.00016538 | 450 | 4500 | 2008/2009 | March-2009 | 3 | 2009
21521 | Benneydale - Tapuwae Road | 2009-03-25 08:31 | 2009-03-25 | 2009-03-25 08:37 | Calculated | T3280 | T3280 - no label |  | No Segment | No Asset Group | Rural D | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 6 | 16 | 24186 | 6979 | 0.28856 | 0.00066154 | 90 | 39265 | 2008/2009 | March-2009 | 3 | 2009
21522 | SH 3 Near Tunnel | 2009-03-25 09:36 | 2009-03-25 | 2009-03-25 15:52 | Calculated | 1602 | 1602 - Earth Working Link 1602 |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 376 | 488 | 24186 | 3863 | 0.15972 | 0.020177 | 3554.5 | 1339946 | 2008/2009 | March-2009 | 3 | 2009
21524 | Rangataua Road | 2009-03-25 15:55 | 2009-03-25 | 2009-03-25 16:18 | Calculated | 20L09 | 20L09 - 5677-5681ph 30kVA POLEMNT |  | 416SEG5677-5681 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 3 | 24186 | 69 | 0.00285 | 0.00012404 | 30 | 690 | 2008/2009 | March-2009 | 3 | 2009
21525 | Benneydale - Tapuwae Road | 2009-03-26 08:30 | 2009-03-26 | 2009-03-26 08:35 | Calculated | T3280 | T3280 - 1ph 15kVA POLEMNT |  | 103SEG270RET | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 16 | 24186 | 6900 | 0.28529 | 0.00066154 | 90 | 38820 | 2008/2009 | March-2009 | 3 | 2009
21526 | SH 3 NEAR TUNNEL | 2009-03-26 09:33 | 2009-03-26 | 2009-03-26 17:48 | Calculated | 1602 | 1602 - Earth Working Link 1602 |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 495 | 488 | 24186 | 2464 | 0.10188 | 0.020177 | 3554.5 | 1762987 | 2008/2009 | March-2009 | 3 | 2009
21528 | Marotiri sub | 2009-03-26 10:43 | 2009-03-26 | 2009-03-26 11:14 | Calculated | CB2 | CB2 - SF6 Tihoi Feeder Breaker CB2 |  | No Segment | 212-01 Marotiri | Rural C | Tihoi | Marotiri Zone Substation |  | Third Party (includeds unauthorised contractors) | ETRE2 | 3PAR:ETRE2:ETRE1 | Tree Clearing/Trimming Activities | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 296 | 24186 | 29803 | 1.2322 | 0.012238 | 0 | 0 | 2008/2009 | March-2009 | 3 | 2009
21529 | Gadsby Road | 2009-03-26 22:27 | 2009-03-26 | 2009-03-26 22:38 | Calculated | 594 | 594 - 33kV Oil Circuit Breaker 594 |  | No Segment | 205-01 Gadsby Road | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 1578 | 24186 | 17358 | 0.71769 | 0.065244 | 0 | 0 | 2008/2009 | March-2009 | 3 | 2009
21530 | Near Tunnel by SH3 | 2009-03-27 09:33 | 2009-03-27 | 2009-03-27 16:02 | Calculated | 1603 | 1603 - Circuit Breaker 1603 |  | No Segment | No Asset Group | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 389 | 484 | 24186 | 2424 | 0.10022 | 0.020012 | 3509.5 | 1372104 | 2008/2009 | March-2009 | 3 | 2009
21531 | Happy Valley Road - By Smith's | 2009-03-27 10:03 | 2009-03-27 | 2009-03-27 11:16 | Calculated | 357 | 357 - Fused Link 357 |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 29 | 24186 | 2665 | 0.11019 | 0.001199 | 315 | 25734 | 2008/2009 | March-2009 | 3 | 2009
21532 | Aratora Road - by Rail Yard | 2009-03-27 10:04 | 2009-03-27 | 2009-03-27 12:18 | Calculated | 641 | 641 - ABS 641 |  | 103SEG641-1350 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 45 | 24186 | 6030 | 0.24932 | 0.0018606 | 326 | 43683 | 2008/2009 | March-2009 | 3 | 2009
21534 | Gadsby Road | 2009-03-28 05:45 | 2009-03-28 | 2009-03-28 05:55 | Calculated | 594 | 594 - 33kV Oil Circuit Breaker 594 |  | No Segment | 205-01 Gadsby Road | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 1578 | 24186 | 15780 | 0.65244 | 0.065244 | 0 | 0 | 2008/2009 | March-2009 | 3 | 2009
21535 | No.3 Access road | 2009-03-28 09:21 | 2009-03-28 | 2009-03-28 12:03 | Calculated | 6544 | 6544 - Fused Link 6544 |  | 418SEG6544 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 1 | 24186 | 162 | 0.0067 | 4.1346e-05 | 25 | 4050 | 2008/2009 | March-2009 | 3 | 2009
21536 | Kawautahi Road | 2009-03-30 10:00 | 2009-03-30 | 2009-03-30 11:17 | Calculated | 11J04 | 11J04 - 1ph 7.5kVA POLEMNT |  | 409SEG5389-5751 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 1 | 24186 | 77 | 0.00318 | 4.1346e-05 | 7.5 | 577 | 2008/2009 | March-2009 | 3 | 2009
21538 | Benneydale - Tapuwae Road | 2009-03-31 08:36 | 2009-03-31 | 2009-03-31 08:41 | Calculated | T3280 | T3280 - 1ph 15kVA POLEMNT |  | 103SEG270RET | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 16 | 24186 | 5655 | 0.23381 | 0.00066154 | 90 | 31895 | 2008/2009 | March-2009 | 3 | 2009
21539 | Mahoenui substation | 2009-03-31 09:33 | 2009-03-31 | 2009-03-31 16:56 | Calculated | 1358 | 1358 - ABS1358 |  | 128SEG1358-1602 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 443 | 488 | 24186 | 8176 | 0.33805 | 0.020177 | 3862 | 1710866 | 2008/2009 | March-2009 | 3 | 2009
21540 | Stouts Road | 2009-03-31 13:00 | 2009-03-31 | 2009-03-31 14:53 | Calculated | 5555 | 5555 - Fused Link 5555 |  | 416SEG5555 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 5 | 24186 | 565 | 0.02336 | 0.00020673 | 55 | 6215 | 2008/2009 | March-2009 | 3 | 2009
1447.757
Formulas:
calcByDate = INT([Interrupted])

## (1b)_2005-09_dailyAggregates
2005-2009 daily aggregate data |  |  | Boundaries | SAIDI | SAIFI | IF(SAIDI_Actual>refSAIDI,refSAIDI,SAIDI_Actual)
Outage Extra Records from Basix : 19 September 2014 |  | int(Interrupted) |  | 21.6659 | 0.26757 | IF(SAIFI_Actual>refSAIFI,refSAIFI,SAIFI_Actual)
NB: 2014 records have audited following the 53ZD information request.
FinYear | Row Labels | SAIDI Actual | SAIFI Actual | SAIDI Normalised | SAIFI Normalised
2004/2005 | 2004-04-01 | 0.40531 | 0.0016018 | 0.40531 | 0.0016018
2004/2005 | 2004-04-02 | 1.2607 | 0.0054772 | 1.2607 | 0.0054772
2004/2005 | 2004-04-06 | 0.01938 | 0.00020669 | 0.01938 | 0.00020669
2004/2005 | 2004-04-07 | 0.04697 | 0.00046504 | 0.04697 | 0.00046504
2004/2005 | 2004-04-08 | 0.84582 | 0.0041854 | 0.84582 | 0.0041854
2004/2005 | 2004-04-11 | 0.04005 | 0.0080091 | 0.04005 | 0.0080091
2004/2005 | 2004-04-12 | 2.8074 | 0.025784 | 2.8074 | 0.025784
2004/2005 | 2004-04-13 | 0.11125 | 0.00041337 | 0.11125 | 0.00041337
2004/2005 | 2004-04-14 | 0.6117 | 0.0019118 | 0.6117 | 0.0019118
2004/2005 | 2004-04-15 | 3.8205 | 0.052395 | 3.8205 | 0.052395
2004/2005 | 2004-04-16 | 0.13409 | 0.00082675 | 0.13409 | 0.00082675
2004/2005 | 2004-04-17 | 0.14835 | 0.021185 | 0.14835 | 0.021185
2004/2005 | 2004-04-19 | 0.21686 | 0.00077507 | 0.21686 | 0.00077507
2004/2005 | 2004-04-20 | 0.18018 | 0.0014985 | 0.18018 | 0.0014985
2004/2005 | 2004-04-21 | 0.13094 | 0.0010851 | 0.13094 | 0.0010851
2004/2005 | 2004-04-22 | 1.2149 | 0.0058389 | 1.2149 | 0.0058389
2004/2005 | 2004-04-23 | 0.19687 | 0.0012401 | 0.19687 | 0.0012401
2004/2005 | 2004-04-24 | 8.6439 | 0.095076 | 8.6439 | 0.095076
2004/2005 | 2004-04-25 | 0.3803 | 0.095076 | 0.3803 | 0.095076
2004/2005 | 2004-04-26 | 4.2985 | 0.017155 | 4.2985 | 0.017155
2004/2005 | 2004-04-27 | 0.04863 | 0.00051672 | 0.04863 | 0.00051672
2004/2005 | 2004-04-28 | 0.01142 | 0.00020669 | 0.01142 | 0.00020669
2004/2005 | 2004-04-29 | 0.16587 | 0.00087842 | 0.16587 | 0.00087842
2004/2005 | 2004-04-30 | 1.3065 | 0.007079 | 1.3065 | 0.007079
2004/2005 | 2004-05-01 | 0.95851 | 0.010644 | 0.95851 | 0.010644
2004/2005 | 2004-05-03 | 0.13584 | 0.0016018 | 0.13584 | 0.0016018
2004/2005 | 2004-05-04 | 0.61184 | 0.0026353 | 0.61184 | 0.0026353
2004/2005 | 2004-05-05 | 0.4127 | 0.0016535 | 0.4127 | 0.0016535
2004/2005 | 2004-05-06 | 0.18421 | 0.0088358 | 0.18421 | 0.0088358
2004/2005 | 2004-05-07 | 0.14525 | 0.0016018 | 0.14525 | 0.0016018
2004/2005 | 2004-05-08 | 0.00997 | 0.00020669 | 0.00997 | 0.00020669
2004/2005 | 2004-05-10 | 0.14018 | 0.0014985 | 0.14018 | 0.0014985
2004/2005 | 2004-05-11 | 0.59688 | 0.0028419 | 0.59688 | 0.0028419
2004/2005 | 2004-05-12 | 0.25066 | 0.0003617 | 0.25066 | 0.0003617
2004/2005 | 2004-05-13 | 0.58296 | 0.0076991 | 0.58296 | 0.0076991
2004/2005 | 2004-05-14 | 0.62849 | 0.0080091 | 0.62849 | 0.0080091
2004/2005 | 2004-05-16 | 0.9583 | 0.012815 | 0.9583 | 0.012815
2004/2005 | 2004-05-17 | 0.12701 | 0.003152 | 0.12701 | 0.003152
2004/2005 | 2004-05-18 | 0.19951 | 0.0013435 | 0.19951 | 0.0013435
2004/2005 | 2004-05-19 | 0.08593 | 0.013331 | 0.08593 | 0.013331
2004/2005 | 2004-05-20 | 0.05549 | 0.0013951 | 0.05549 | 0.0013951
2004/2005 | 2004-05-21 | 0.14386 | 0.00098176 | 0.14386 | 0.00098176
2004/2005 | 2004-05-22 | 0.17031 | 0.00082675 | 0.17031 | 0.00082675
2004/2005 | 2004-05-23 | 0.18142 | 0.0014468 | 0.18142 | 0.0014468
2004/2005 | 2004-05-24 | 2.7311 | 0.016845 | 2.7311 | 0.016845
2004/2005 | 2004-05-25 | 0.16199 | 0.0053738 | 0.16199 | 0.0053738
2004/2005 | 2004-05-26 | 0.29204 | 0.0011884 | 0.29204 | 0.0011884
2004/2005 | 2004-05-27 | 0.59293 | 0.0013951 | 0.59293 | 0.0013951
2004/2005 | 2004-05-28 | 1.3119 | 0.0046504 | 1.3119 | 0.0046504
2004/2005 | 2004-05-30 | 0.29298 | 0.00077507 | 0.29298 | 0.00077507
2004/2005 | 2004-05-31 | 1.5915 | 0.012815 | 1.5915 | 0.012815
2004/2005 | 2004-06-01 | 0.61835 | 0.0043921 | 0.61835 | 0.0043921
2004/2005 | 2004-06-02 | 0.70433 | 0.0078024 | 0.70433 | 0.0078024
2004/2005 | 2004-06-03 | 1.791 | 0.011109 | 1.791 | 0.011109
2004/2005 | 2004-06-04 | 3.5663 | 0.15713 | 3.5663 | 0.15713
2004/2005 | 2004-06-05 | 0.53992 | 0.0094042 | 0.53992 | 0.0094042
2004/2005 | 2004-06-06 | 10.1158 | 0.12329 | 10.1158 | 0.12329
2004/2005 | 2004-06-08 | 0.57103 | 0.0084741 | 0.57103 | 0.0084741
2004/2005 | 2004-06-09 | 0.15987 | 0.0014985 | 0.15987 | 0.0014985
2004/2005 | 2004-06-10 | 0.19061 | 0.0053738 | 0.19061 | 0.0053738
2004/2005 | 2004-06-11 | 0.0602 | 0.0007234 | 0.0602 | 0.0007234
2004/2005 | 2004-06-12 | 0.07192 | 0.00062006 | 0.07192 | 0.00062006
2004/2005 | 2004-06-14 | 0.07864 | 0.0043921 | 0.07864 | 0.0043921
2004/2005 | 2004-06-15 | 0.62766 | 0.084586 | 0.62766 | 0.084586
2004/2005 | 2004-06-16 | 1.7006 | 0.023356 | 1.7006 | 0.023356
2004/2005 | 2004-06-17 | 0.00357 | 0.00015501 | 0.00357 | 0.00015501
2004/2005 | 2004-06-18 | 1.519 | 0.01235 | 1.519 | 0.01235
2004/2005 | 2004-06-19 | 0.45502 | 0.012298 | 0.45502 | 0.012298
2004/2005 | 2004-06-20 | 0.02459 | 0.0022219 | 0.02459 | 0.0022219
2004/2005 | 2004-06-21 | 0.07368 | 0.00062006 | 0.07368 | 0.00062006
2004/2005 | 2004-06-22 | 5.7213 | 0.19553 | 5.7213 | 0.19553
2004/2005 | 2004-06-23 | 0.75595 | 0.048416 | 0.75595 | 0.048416
2004/2005 | 2004-06-24 | 0.02289 | 0.00015501 | 0.02289 | 0.00015501
2004/2005 | 2004-06-25 | 0.09673 | 0.012815 | 0.09673 | 0.012815
2004/2005 | 2004-06-27 | 0.85728 | 0.012815 | 0.85728 | 0.012815
2004/2005 | 2004-06-28 | 0.02692 | 5.1672e-05 | 0.02692 | 5.1672e-05
2004/2005 | 2004-06-29 | 0.30962 | 0.0022735 | 0.30962 | 0.0022735
2004/2005 | 2004-06-30 | 5.9968 | 0.037979 | 5.9968 | 0.037979
2004/2005 | 2004-07-01 | 2.0705 | 0.036325 | 2.0705 | 0.036325
2004/2005 | 2004-07-02 | 0.63639 | 0.0042887 | 0.63639 | 0.0042887
2004/2005 | 2004-07-03 | 0.45533 | 0.0067173 | 0.45533 | 0.0067173
2004/2005 | 2004-07-04 | 1.9532 | 0.024027 | 1.9532 | 0.024027
2004/2005 | 2004-07-05 | 0.00351 | 5.1672e-05 | 0.00351 | 5.1672e-05
2004/2005 | 2004-07-06 | 0.82246 | 0.022891 | 0.82246 | 0.022891
2004/2005 | 2004-07-07 | 0.17796 | 0.0042371 | 0.17796 | 0.0042371
2004/2005 | 2004-07-08 | 1.2253 | 0.0098176 | 1.2253 | 0.0098176
2004/2005 | 2004-07-09 | 2.9858 | 0.021547 | 2.9858 | 0.021547
2004/2005 | 2004-07-13 | 0.17558 | 0.0036687 | 0.17558 | 0.0036687
2004/2005 | 2004-07-14 | 0.23112 | 0.0017568 | 0.23112 | 0.0017568
2004/2005 | 2004-07-15 | 0.07053 | 0.00077507 | 0.07053 | 0.00077507
2004/2005 | 2004-07-16 | 0.10805 | 0.00087842 | 0.10805 | 0.00087842
2004/2005 | 2004-07-19 | 2.1671 | 0.022425 | 2.1671 | 0.022425
2004/2005 | 2004-07-20 | 0.16679 | 0.0019635 | 0.16679 | 0.0019635
2004/2005 | 2004-07-21 | 0.22735 | 0.0020669 | 0.22735 | 0.0020669
2004/2005 | 2004-07-22 | 0.85599 | 0.0056839 | 0.85599 | 0.0056839
2004/2005 | 2004-07-23 | 5.2815 | 0.022942 | 5.2815 | 0.022942
2004/2005 | 2004-07-25 | 0.21185 | 0.021185 | 0.21185 | 0.021185
2004/2005 | 2004-07-26 | 0.36288 | 0.0041337 | 0.36288 | 0.0041337
2004/2005 | 2004-07-27 | 0.28668 | 0.012763 | 0.28668 | 0.012763
2004/2005 | 2004-07-28 | 0.06443 | 0.0016535 | 0.06443 | 0.0016535
2004/2005 | 2004-07-29 | 0.44521 | 0.019429 | 0.44521 | 0.019429
2004/2005 | 2004-07-30 | 0.37833 | 0.027438 | 0.37833 | 0.027438
2004/2005 | 2004-07-31 | 0.37219 | 0.05317 | 0.37219 | 0.05317
2004/2005 | 2004-08-02 | 1.6221 | 0.054307 | 1.6221 | 0.054307
2004/2005 | 2004-08-03 | 1.2991 | 0.070945 | 1.2991 | 0.070945
2004/2005 | 2004-08-05 | 0.1637 | 0.00093009 | 0.1637 | 0.00093009
2004/2005 | 2004-08-06 | 0.54911 | 0.017517 | 0.54911 | 0.017517
2004/2005 | 2004-08-07 | 0.39715 | 0.042939 | 0.39715 | 0.042939
2004/2005 | 2004-08-08 | 0.0248 | 0.012401 | 0.0248 | 0.012401
2004/2005 | 2004-08-09 | 0.34883 | 0.0017568 | 0.34883 | 0.0017568
2004/2005 | 2004-08-10 | 0.13476 | 0.0018602 | 0.13476 | 0.0018602
2004/2005 | 2004-08-11 | 0.18731 | 0.0019635 | 0.18731 | 0.0019635
2004/2005 | 2004-08-12 | 24.1446 | 0.03307 | 21.6659 | 0.03307
2004/2005 | 2004-08-13 | 1.3927 | 0.0093526 | 1.3927 | 0.0093526
2004/2005 | 2004-08-15 | 0.07988 | 0.039942 | 0.07988 | 0.039942
2004/2005 | 2004-08-16 | 3.2577 | 0.028006 | 3.2577 | 0.028006
2004/2005 | 2004-08-17 | 0.56198 | 0.033173 | 0.56198 | 0.033173
2004/2005 | 2004-08-18 | 3.6429 | 0.022425 | 3.6429 | 0.022425
2004/2005 | 2004-08-19 | 1.655 | 0.0021185 | 1.655 | 0.0021185
2004/2005 | 2004-08-20 | 0.03333 | 0.0014468 | 0.03333 | 0.0014468
2004/2005 | 2004-08-21 | 1.4374 | 0.01452 | 1.4374 | 0.01452
2004/2005 | 2004-08-22 | 0.00062 | 0.00010334 | 0.00062 | 0.00010334
2004/2005 | 2004-08-23 | 0.11719 | 0.00046504 | 0.11719 | 0.00046504
2004/2005 | 2004-08-24 | 0.23366 | 0.0011884 | 0.23366 | 0.0011884
2004/2005 | 2004-08-25 | 1.6097 | 0.0055805 | 1.6097 | 0.0055805
2004/2005 | 2004-08-26 | 0.00486 | 0.00010334 | 0.00486 | 0.00010334
2004/2005 | 2004-08-27 | 0.00956 | 0.00015501 | 0.00956 | 0.00015501
2004/2005 | 2004-08-28 | 0.34465 | 0.0050121 | 0.34465 | 0.0050121
2004/2005 | 2004-08-30 | 0.01529 | 0.00025836 | 0.01529 | 0.00025836
2004/2005 | 2004-09-01 | 0.38351 | 0.024699 | 0.38351 | 0.024699
2004/2005 | 2004-09-02 | 0.20793 | 0.013331 | 0.20793 | 0.013331
2004/2005 | 2004-09-03 | 0.09714 | 0.0010334 | 0.09714 | 0.0010334
2004/2005 | 2004-09-05 | 0.0248 | 0.00041337 | 0.0248 | 0.00041337
2004/2005 | 2004-09-06 | 1.6093 | 0.0044954 | 1.6093 | 0.0044954
2004/2005 | 2004-09-07 | 0.18902 | 0.00062006 | 0.18902 | 0.00062006
2004/2005 | 2004-09-08 | 0.19274 | 0.0018602 | 0.19274 | 0.0018602
2004/2005 | 2004-09-09 | 0.28326 | 0.0022735 | 0.28326 | 0.0022735
2004/2005 | 2004-09-10 | 0.65566 | 0.0035137 | 0.65566 | 0.0035137
2004/2005 | 2004-09-11 | 0.14447 | 0.012039 | 0.14447 | 0.012039
2004/2005 | 2004-09-13 | 0.16937 | 0.0018602 | 0.16937 | 0.0018602
2004/2005 | 2004-09-14 | 0.17946 | 0.0010851 | 0.17946 | 0.0010851
2004/2005 | 2004-09-15 | 0.11559 | 0.0012918 | 0.11559 | 0.0012918
2004/2005 | 2004-09-16 | 0.22178 | 0.0012401 | 0.22178 | 0.0012401
2004/2005 | 2004-09-17 | 0.17413 | 0.0013951 | 0.17413 | 0.0013951
2004/2005 | 2004-09-18 | 1.894 | 0.0091459 | 1.894 | 0.0091459
2004/2005 | 2004-09-19 | 0.22792 | 0.0016018 | 0.22792 | 0.0016018
2004/2005 | 2004-09-20 | 0.12877 | 0.0016018 | 0.12877 | 0.0016018
2004/2005 | 2004-09-21 | 0.3108 | 0.0013435 | 0.3108 | 0.0013435
2004/2005 | 2004-09-22 | 5.5327 | 0.030641 | 5.5327 | 0.030641
2004/2005 | 2004-09-23 | 0.17919 | 0.0011884 | 0.17919 | 0.0011884
2004/2005 | 2004-09-24 | 0.0186 | 0.0011368 | 0.0186 | 0.0011368
2004/2005 | 2004-09-25 | 0.97411 | 0.081176 | 0.97411 | 0.081176
2004/2005 | 2004-09-27 | 0.46226 | 0.0027386 | 0.46226 | 0.0027386
2004/2005 | 2004-09-28 | 3.5241 | 0.025474 | 3.5241 | 0.025474
2004/2005 | 2004-09-29 | 0.50736 | 0.0020669 | 0.50736 | 0.0020669
2004/2005 | 2004-09-30 | 0.73875 | 0.0069757 | 0.73875 | 0.0069757
2004/2005 | 2004-10-01 | 0.01953 | 0.00031003 | 0.01953 | 0.00031003
2004/2005 | 2004-10-04 | 0.41337 | 0.0082675 | 0.41337 | 0.0082675
2004/2005 | 2004-10-05 | 0.44262 | 0.0043921 | 0.44262 | 0.0043921
2004/2005 | 2004-10-06 | 0.35782 | 0.0048055 | 0.35782 | 0.0048055
2004/2005 | 2004-10-07 | 0.20456 | 0.0020152 | 0.20456 | 0.0020152
2004/2005 | 2004-10-08 | 0.72619 | 0.013228 | 0.72619 | 0.013228
2004/2005 | 2004-10-11 | 0.22369 | 0.00067173 | 0.22369 | 0.00067173
2004/2005 | 2004-10-12 | 4.2352 | 0.0097659 | 4.2352 | 0.0097659
2004/2005 | 2004-10-13 | 0.02614 | 0.00077507 | 0.02614 | 0.00077507
2004/2005 | 2004-10-14 | 0.20121 | 0.00093009 | 0.20121 | 0.00093009
2004/2005 | 2004-10-15 | 0.19455 | 0.0014468 | 0.19455 | 0.0014468
2004/2005 | 2004-10-16 | 0.24379 | 0.0021702 | 0.24379 | 0.0021702
2004/2005 | 2004-10-17 | 0.02532 | 0.00010334 | 0.02532 | 0.00010334
2004/2005 | 2004-10-18 | 0.7896 | 0.01762 | 0.7896 | 0.01762
2004/2005 | 2004-10-19 | 0.08009 | 0.0023252 | 0.08009 | 0.0023252
2004/2005 | 2004-10-20 | 0.14422 | 0.00056839 | 0.14422 | 0.00056839
2004/2005 | 2004-10-21 | 0.11295 | 0.00082675 | 0.11295 | 0.00082675
2004/2005 | 2004-10-22 | 0.93561 | 0.0030486 | 0.93561 | 0.0030486
2004/2005 | 2004-10-23 | 0.59396 | 0.042887 | 0.59396 | 0.042887
2004/2005 | 2004-10-24 | 0.17207 | 0.057355 | 0.17207 | 0.057355
2004/2005 | 2004-10-26 | 0.24864 | 0.00082675 | 0.24864 | 0.00082675
2004/2005 | 2004-10-27 | 1.2184 | 0.081228 | 1.2184 | 0.081228
2004/2005 | 2004-10-28 | 0.47631 | 0.0069757 | 0.47631 | 0.0069757
2004/2005 | 2004-10-29 | 0.23671 | 0.0016535 | 0.23671 | 0.0016535
2004/2005 | 2004-10-30 | 0.0465 | 0.00031003 | 0.0465 | 0.00031003
2004/2005 | 2004-11-01 | 0.60694 | 0.0089392 | 0.60694 | 0.0089392
2004/2005 | 2004-11-02 | 0.0741 | 0.00046504 | 0.0741 | 0.00046504
2004/2005 | 2004-11-03 | 1.4907 | 0.010179 | 1.4907 | 0.010179
2004/2005 | 2004-11-04 | 0.18215 | 0.0057355 | 0.18215 | 0.0057355
2004/2005 | 2004-11-05 | 0.3168 | 0.0010334 | 0.3168 | 0.0010334
2004/2005 | 2004-11-08 | 0.15217 | 0.00051672 | 0.15217 | 0.00051672
2004/2005 | 2004-11-09 | 0.16752 | 0.00051672 | 0.16752 | 0.00051672
2004/2005 | 2004-11-10 | 0.29468 | 0.0031003 | 0.29468 | 0.0031003
2004/2005 | 2004-11-11 | 0.53191 | 0.0041337 | 0.53191 | 0.0041337
2004/2005 | 2004-11-12 | 12.3726 | 0.060197 | 12.3726 | 0.060197
2004/2005 | 2004-11-14 | 17.8362 | 0.063453 | 17.8362 | 0.063453
2004/2005 | 2004-11-15 | 1.8495 | 0.0078024 | 1.8495 | 0.0078024
2004/2005 | 2004-11-17 | 1.8005 | 0.058182 | 1.8005 | 0.058182
2004/2005 | 2004-11-18 | 0.58549 | 0.050845 | 0.58549 | 0.050845
2004/2005 | 2004-11-19 | 0.70981 | 0.0036687 | 0.70981 | 0.0036687
2004/2005 | 2004-11-20 | 0.20901 | 0.0021702 | 0.20901 | 0.0021702
2004/2005 | 2004-11-22 | 0.44303 | 0.0029453 | 0.44303 | 0.0029453
2004/2005 | 2004-11-23 | 0.2364 | 0.0026869 | 0.2364 | 0.0026869
2004/2005 | 2004-11-24 | 1.3418 | 0.0089909 | 1.3418 | 0.0089909
2004/2005 | 2004-11-25 | 0.40598 | 0.0027386 | 0.40598 | 0.0027386
2004/2005 | 2004-11-26 | 0.45249 | 0.0083708 | 0.45249 | 0.0083708
2004/2005 | 2004-11-28 | 0.1918 | 0.0014985 | 0.1918 | 0.0014985
2004/2005 | 2004-11-29 | 0.12102 | 0.0007234 | 0.12102 | 0.0007234
2004/2005 | 2004-11-30 | 2.1909 | 0.014365 | 2.1909 | 0.014365
2004/2005 | 2004-12-01 | 0.00506 | 5.1672e-05 | 0.00506 | 5.1672e-05
2004/2005 | 2004-12-02 | 0.58105 | 0.0018085 | 0.58105 | 0.0018085
2004/2005 | 2004-12-03 | 0.34289 | 0.0020152 | 0.34289 | 0.0020152
2004/2005 | 2004-12-05 | 1.0748 | 0.0035137 | 1.0748 | 0.0035137
2004/2005 | 2004-12-06 | 0.00382 | 5.1672e-05 | 0.00382 | 5.1672e-05
2004/2005 | 2004-12-07 | 1.0239 | 0.0089909 | 1.0239 | 0.0089909
2004/2005 | 2004-12-09 | 10.3872 | 0.032656 | 10.3872 | 0.032656
2004/2005 | 2004-12-10 | 0.87722 | 0.026353 | 0.87722 | 0.026353
2004/2005 | 2004-12-11 | 0.02521 | 0.012453 | 0.02521 | 0.012453
2004/2005 | 2004-12-12 | 0.05581 | 0.00093009 | 0.05581 | 0.00093009
2004/2005 | 2004-12-13 | 0.39291 | 0.0028419 | 0.39291 | 0.0028419
2004/2005 | 2004-12-14 | 0.44334 | 0.0015501 | 0.44334 | 0.0015501
2004/2005 | 2004-12-15 | 0.86477 | 0.035085 | 0.86477 | 0.035085
2004/2005 | 2004-12-16 | 1.8753 | 0.029246 | 1.8753 | 0.029246
2004/2005 | 2004-12-17 | 0.49316 | 0.0050638 | 0.49316 | 0.0050638
2004/2005 | 2004-12-18 | 0.27463 | 0.0028936 | 0.27463 | 0.0028936
2004/2005 | 2004-12-19 | 0.66987 | 0.040304 | 0.66987 | 0.040304
2004/2005 | 2004-12-20 | 1.0324 | 0.0076991 | 1.0324 | 0.0076991
2004/2005 | 2004-12-21 | 1.0264 | 0.0082675 | 1.0264 | 0.0082675
2004/2005 | 2004-12-22 | 2.6317 | 0.025164 | 2.6317 | 0.025164
2004/2005 | 2004-12-23 | 0.13393 | 0.0016535 | 0.13393 | 0.0016535
2004/2005 | 2004-12-27 | 0.14055 | 0.0043921 | 0.14055 | 0.0043921
2004/2005 | 2004-12-29 | 0.09476 | 0.003152 | 0.09476 | 0.003152
2004/2005 | 2004-12-30 | 0.02056 | 0.0003617 | 0.02056 | 0.0003617
2004/2005 | 2004-12-31 | 0.32243 | 0.0026353 | 0.32243 | 0.0026353
2004/2005 | 2005-01-03 | 0.02367 | 0.00010334 | 0.02367 | 0.00010334
2004/2005 | 2005-01-05 | 0.35731 | 0.0026869 | 0.35731 | 0.0026869
2004/2005 | 2005-01-09 | 0.02454 | 0.00098176 | 0.02454 | 0.00098176
2004/2005 | 2005-01-10 | 1.0279 | 0.0096626 | 1.0279 | 0.0096626
2004/2005 | 2005-01-12 | 0.0124 | 0.00031003 | 0.0124 | 0.00031003
2004/2005 | 2005-01-13 | 0.03932 | 0.0014468 | 0.03932 | 0.0014468
2004/2005 | 2005-01-17 | 0.07146 | 0.0003617 | 0.07146 | 0.0003617
2004/2005 | 2005-01-18 | 0.1978 | 0.0036687 | 0.1978 | 0.0036687
2004/2005 | 2005-01-19 | 0.19987 | 0.00087842 | 0.19987 | 0.00087842
2004/2005 | 2005-01-20 | 0.10981 | 0.0010334 | 0.10981 | 0.0010334
2004/2005 | 2005-01-21 | 0.06516 | 0.0003617 | 0.06516 | 0.0003617
2004/2005 | 2005-01-22 | 0.10572 | 0.011988 | 0.10572 | 0.011988
2004/2005 | 2005-01-24 | 0.17657 | 0.0010851 | 0.17657 | 0.0010851
2004/2005 | 2005-01-25 | 1.7609 | 0.010128 | 1.7609 | 0.010128
2004/2005 | 2005-01-26 | 0.02821 | 0.00025836 | 0.02821 | 0.00025836
2004/2005 | 2005-01-27 | 7.0818 | 0.022219 | 7.0818 | 0.022219
2004/2005 | 2005-01-28 | 0.38996 | 0.0014985 | 0.38996 | 0.0014985
2004/2005 | 2005-02-01 | 0.07415 | 0.00056839 | 0.07415 | 0.00056839
2004/2005 | 2005-02-02 | 0.98616 | 0.081383 | 0.98616 | 0.081383
2004/2005 | 2005-02-03 | 8.7991 | 0.034672 | 8.7991 | 0.034672
2004/2005 | 2005-02-04 | 1.8052 | 0.017207 | 1.8052 | 0.017207
2004/2005 | 2005-02-07 | 1.5221 | 0.012453 | 1.5221 | 0.012453
2004/2005 | 2005-02-08 | 1.3776 | 0.0060456 | 1.3776 | 0.0060456
2004/2005 | 2005-02-09 | 0.91422 | 0.015243 | 0.91422 | 0.015243
2004/2005 | 2005-02-10 | 1.0884 | 0.020359 | 1.0884 | 0.020359
2004/2005 | 2005-02-11 | 1.0307 | 0.016897 | 1.0307 | 0.016897
2004/2005 | 2005-02-13 | 1.08 | 0.015088 | 1.08 | 0.015088
2004/2005 | 2005-02-14 | 1.8561 | 0.016897 | 1.8561 | 0.016897
2004/2005 | 2005-02-15 | 1.6476 | 0.0078541 | 1.6476 | 0.0078541
2004/2005 | 2005-02-16 | 0.377 | 0.0010334 | 0.377 | 0.0010334
2004/2005 | 2005-02-17 | 0.15956 | 0.0038237 | 0.15956 | 0.0038237
2004/2005 | 2005-02-18 | 1.3314 | 0.01328 | 1.3314 | 0.01328
2004/2005 | 2005-02-21 | 0.68507 | 0.015553 | 0.68507 | 0.015553
2004/2005 | 2005-02-22 | 0.38133 | 0.0019635 | 0.38133 | 0.0019635
2004/2005 | 2005-02-23 | 0.01519 | 0.00020669 | 0.01519 | 0.00020669
2004/2005 | 2005-02-24 | 0.11694 | 0.00056839 | 0.11694 | 0.00056839
2004/2005 | 2005-02-25 | 0.08526 | 0.0010334 | 0.08526 | 0.0010334
2004/2005 | 2005-02-26 | 0.02852 | 0.00015501 | 0.02852 | 0.00015501
2004/2005 | 2005-02-28 | 0.1841 | 0.0061489 | 0.1841 | 0.0061489
2004/2005 | 2005-03-01 | 0.48566 | 0.0017568 | 0.48566 | 0.0017568
2004/2005 | 2005-03-02 | 5.541 | 0.01979 | 5.541 | 0.01979
2004/2005 | 2005-03-03 | 0.05038 | 0.0024286 | 0.05038 | 0.0024286
2004/2005 | 2005-03-04 | 0.11915 | 0.0020152 | 0.11915 | 0.0020152
2004/2005 | 2005-03-06 | 0.21888 | 0.07296 | 0.21888 | 0.07296
2004/2005 | 2005-03-07 | 1.3621 | 0.027024 | 1.3621 | 0.027024
2004/2005 | 2005-03-08 | 0.81362 | 0.003462 | 0.81362 | 0.003462
2004/2005 | 2005-03-09 | 0.1763 | 0.0026869 | 0.1763 | 0.0026869
2004/2005 | 2005-03-10 | 0.64113 | 0.0064589 | 0.64113 | 0.0064589
2004/2005 | 2005-03-11 | 0.94466 | 0.0055805 | 0.94466 | 0.0055805
2004/2005 | 2005-03-12 | 0.59582 | 0.077042 | 0.59582 | 0.077042
2004/2005 | 2005-03-13 | 0.4142 | 0.003617 | 0.4142 | 0.003617
2004/2005 | 2005-03-14 | 0.39762 | 0.07513 | 0.39762 | 0.07513
2004/2005 | 2005-03-15 | 0.03415 | 0.00025836 | 0.03415 | 0.00025836
2004/2005 | 2005-03-16 | 1.7458 | 0.0093526 | 1.7458 | 0.0093526
2004/2005 | 2005-03-17 | 0.80845 | 0.013745 | 0.80845 | 0.013745
2004/2005 | 2005-03-18 | 0.56312 | 0.0058906 | 0.56312 | 0.0058906
2004/2005 | 2005-03-20 | 0.53573 | 0.0016535 | 0.53573 | 0.0016535
2004/2005 | 2005-03-21 | 0.37755 | 0.082054 | 0.37755 | 0.082054
2004/2005 | 2005-03-22 | 1.3679 | 0.0044954 | 1.3679 | 0.0044954
2004/2005 | 2005-03-23 | 0.14938 | 0.0011884 | 0.14938 | 0.0011884
2004/2005 | 2005-03-24 | 0.56689 | 0.021909 | 0.56689 | 0.021909
2004/2005 | 2005-03-26 | 2.3413 | 0.029763 | 2.3413 | 0.029763
2004/2005 | 2005-03-28 | 0.04547 | 0.00056839 | 0.04547 | 0.00056839
2004/2005 | 2005-03-29 | 0.12691 | 0.0055805 | 0.12691 | 0.0055805
2004/2005 | 2005-03-30 | 0.25629 | 0.0025836 | 0.25629 | 0.0025836
2005/2006 | 2005-04-02 | 1.5023 | 0.0073374 | 1.5023 | 0.0073374
2005/2006 | 2005-04-03 | 0.02578 | 0.025784 | 0.02578 | 0.025784
2005/2006 | 2005-04-04 | 0.34041 | 0.0025319 | 0.34041 | 0.0025319
2005/2006 | 2005-04-05 | 0.00315 | 5.1672e-05 | 0.00315 | 5.1672e-05
2005/2006 | 2005-04-06 | 0.0217 | 0.0021702 | 0.0217 | 0.0021702
2005/2006 | 2005-04-07 | 0.15687 | 0.00062006 | 0.15687 | 0.00062006
2005/2006 | 2005-04-08 | 0.49119 | 0.0060972 | 0.49119 | 0.0060972
2005/2006 | 2005-04-09 | 0.31215 | 0.0003617 | 0.31215 | 0.0003617
2005/2006 | 2005-04-11 | 0.35514 | 0.0048055 | 0.35514 | 0.0048055
2005/2006 | 2005-04-12 | 0.12122 | 0.0016535 | 0.12122 | 0.0016535
2005/2006 | 2005-04-13 | 0.11322 | 0.00098176 | 0.11322 | 0.00098176
2005/2006 | 2005-04-14 | 0.48365 | 0.0020152 | 0.48365 | 0.0020152
2005/2006 | 2005-04-15 | 0.00651 | 5.1672e-05 | 0.00651 | 5.1672e-05
2005/2006 | 2005-04-16 | 0.6507 | 0.081383 | 0.6507 | 0.081383
2005/2006 | 2005-04-18 | 0.45099 | 0.0065623 | 0.45099 | 0.0065623
2005/2006 | 2005-04-19 | 0.93866 | 0.010438 | 0.93866 | 0.010438
2005/2006 | 2005-04-20 | 0.00589 | 0.00010334 | 0.00589 | 0.00010334
2005/2006 | 2005-04-21 | 0.57206 | 0.0048055 | 0.57206 | 0.0048055
2005/2006 | 2005-04-22 | 1.938 | 0.016173 | 1.938 | 0.016173
2005/2006 | 2005-04-24 | 0.36506 | 0.01328 | 0.36506 | 0.01328
2005/2006 | 2005-04-26 | 3.3659 | 0.033173 | 3.3659 | 0.033173
2005/2006 | 2005-04-27 | 0.76386 | 0.0092492 | 0.76386 | 0.0092492
2005/2006 | 2005-04-28 | 0.35514 | 0.0044954 | 0.35514 | 0.0044954
2005/2006 | 2005-04-29 | 0.06656 | 0.00062006 | 0.06656 | 0.00062006
2005/2006 | 2005-04-30 | 1.0851 | 0.052292 | 1.0851 | 0.052292
2005/2006 | 2005-05-01 | 0.48106 | 0.0041854 | 0.48106 | 0.0041854
2005/2006 | 2005-05-03 | 0.11791 | 0.00082675 | 0.11791 | 0.00082675
2005/2006 | 2005-05-04 | 0.17424 | 0.0010334 | 0.17424 | 0.0010334
2005/2006 | 2005-05-05 | 3.3554 | 0.052653 | 3.3554 | 0.052653
2005/2006 | 2005-05-06 | 0.67834 | 0.0074407 | 0.67834 | 0.0074407
2005/2006 | 2005-05-08 | 0.00047 | 5.1672e-05 | 0.00047 | 5.1672e-05
2005/2006 | 2005-05-09 | 1.4093 | 0.084586 | 1.4093 | 0.084586
2005/2006 | 2005-05-10 | 0.01488 | 0.00031003 | 0.01488 | 0.00031003
2005/2006 | 2005-05-11 | 0.81331 | 0.081331 | 0.81331 | 0.081331
2005/2006 | 2005-05-12 | 0.03658 | 0.00051672 | 0.03658 | 0.00051672
2005/2006 | 2005-05-13 | 0.16529 | 0.0026353 | 0.16529 | 0.0026353
2005/2006 | 2005-05-16 | 0.57975 | 0.0059422 | 0.57975 | 0.0059422
2005/2006 | 2005-05-17 | 0.48705 | 0.0035137 | 0.48705 | 0.0035137
2005/2006 | 2005-05-18 | 0.07585 | 0.017465 | 0.07585 | 0.017465
2005/2006 | 2005-05-19 | 0.62729 | 0.0042887 | 0.62729 | 0.0042887
2005/2006 | 2005-05-20 | 0.20229 | 0.0025836 | 0.20229 | 0.0025836
2005/2006 | 2005-05-23 | 3.0995 | 0.057252 | 3.0995 | 0.057252
2005/2006 | 2005-05-24 | 0.23686 | 0.0012401 | 0.23686 | 0.0012401
2005/2006 | 2005-05-25 | 0.53114 | 0.010748 | 0.53114 | 0.010748
2005/2006 | 2005-05-26 | 0.81264 | 0.0056322 | 0.81264 | 0.0056322
2005/2006 | 2005-05-27 | 0.02625 | 0.00020669 | 0.02625 | 0.00020669
2005/2006 | 2005-05-28 | 0.01183 | 5.1672e-05 | 0.01183 | 5.1672e-05
2005/2006 | 2005-05-29 | 0.96238 | 0.0054772 | 0.96238 | 0.0054772
2005/2006 | 2005-05-30 | 1.3544 | 0.019325 | 1.3544 | 0.019325
2005/2006 | 2005-05-31 | 0.0848 | 0.0035653 | 0.0848 | 0.0035653
2005/2006 | 2005-06-01 | 0.81564 | 0.003927 | 0.81564 | 0.003927
2005/2006 | 2005-06-02 | 0.58942 | 0.011109 | 0.58942 | 0.011109
2005/2006 | 2005-06-03 | 11.192 | 0.13176 | 11.192 | 0.13176
2005/2006 | 2005-06-04 | 0.02728 | 0.00010334 | 0.02728 | 0.00010334
2005/2006 | 2005-06-05 | 0.0248 | 0.012401 | 0.0248 | 0.012401
2005/2006 | 2005-06-07 | 0.61458 | 0.0030486 | 0.61458 | 0.0030486
2005/2006 | 2005-06-08 | 0.02898 | 0.00087842 | 0.02898 | 0.00087842
2005/2006 | 2005-06-09 | 0.22219 | 0.0012918 | 0.22219 | 0.0012918
2005/2006 | 2005-06-10 | 0.53248 | 0.010954 | 0.53248 | 0.010954
2005/2006 | 2005-06-11 | 0.02305 | 0.00010334 | 0.02305 | 0.00010334
2005/2006 | 2005-06-13 | 0.68718 | 0.050535 | 0.68718 | 0.050535
2005/2006 | 2005-06-14 | 0.4051 | 0.0014468 | 0.4051 | 0.0014468
2005/2006 | 2005-06-15 | 0.86111 | 0.022167 | 0.86111 | 0.022167
2005/2006 | 2005-06-16 | 0.20338 | 0.0045471 | 0.20338 | 0.0045471
2005/2006 | 2005-06-17 | 1.2513 | 0.014881 | 1.2513 | 0.014881
2005/2006 | 2005-06-19 | 0.03906 | 0.00020669 | 0.03906 | 0.00020669
2005/2006 | 2005-06-20 | 0.05302 | 0.00031003 | 0.05302 | 0.00031003
2005/2006 | 2005-06-21 | 0.38448 | 0.003617 | 0.38448 | 0.003617
2005/2006 | 2005-06-22 | 1.2948 | 0.0096109 | 1.2948 | 0.0096109
2005/2006 | 2005-06-23 | 0.21036 | 0.018292 | 0.21036 | 0.018292
2005/2006 | 2005-06-24 | 0.86865 | 0.0082675 | 0.86865 | 0.0082675
2005/2006 | 2005-06-26 | 0.03462 | 0.00051672 | 0.03462 | 0.00051672
2005/2006 | 2005-06-27 | 3.0485 | 0.081899 | 3.0485 | 0.081899
2005/2006 | 2005-06-28 | 1.5916 | 0.010644 | 1.5916 | 0.010644
2005/2006 | 2005-06-29 | 0.54131 | 0.0013951 | 0.54131 | 0.0013951
2005/2006 | 2005-06-30 | 0.31644 | 0.0028936 | 0.31644 | 0.0028936
2005/2006 | 2005-07-01 | 0.52892 | 0.0055805 | 0.52892 | 0.0055805
2005/2006 | 2005-07-02 | 5.2157 | 0.01359 | 5.2157 | 0.01359
2005/2006 | 2005-07-04 | 0.14323 | 0.00062006 | 0.14323 | 0.00062006
2005/2006 | 2005-07-05 | 0.01204 | 0.00010334 | 0.01204 | 0.00010334
2005/2006 | 2005-07-06 | 0.96708 | 0.0072857 | 0.96708 | 0.0072857
2005/2006 | 2005-07-07 | 0.41559 | 0.0015501 | 0.41559 | 0.0015501
2005/2006 | 2005-07-08 | 2.7195 | 0.030951 | 2.7195 | 0.030951
2005/2006 | 2005-07-11 | 0.1202 | 0.0011368 | 0.1202 | 0.0011368
2005/2006 | 2005-07-12 | 1.1539 | 0.0087842 | 1.1539 | 0.0087842
2005/2006 | 2005-07-13 | 0.11503 | 0.0012401 | 0.11503 | 0.0012401
2005/2006 | 2005-07-14 | 0.49667 | 0.0052705 | 0.49667 | 0.0052705
2005/2006 | 2005-07-15 | 1.0304 | 0.012918 | 1.0304 | 0.012918
2005/2006 | 2005-07-17 | 0.2688 | 0.0014468 | 0.2688 | 0.0014468
2005/2006 | 2005-07-18 | 0.63287 | 0.0019118 | 0.63287 | 0.0019118
2005/2006 | 2005-07-19 | 0.20316 | 0.01359 | 0.20316 | 0.01359
2005/2006 | 2005-07-20 | 0.41761 | 0.0032553 | 0.41761 | 0.0032553
2005/2006 | 2005-07-21 | 0.73704 | 0.0024802 | 0.73704 | 0.0024802
2005/2006 | 2005-07-22 | 3.2774 | 0.14928 | 3.2774 | 0.14928
2005/2006 | 2005-07-23 | 0.01199 | 5.1672e-05 | 0.01199 | 5.1672e-05
2005/2006 | 2005-07-25 | 0.0615 | 0.0014468 | 0.0615 | 0.0014468
2005/2006 | 2005-07-26 | 1.0386 | 0.0082675 | 1.0386 | 0.0082675
2005/2006 | 2005-07-27 | 2.1211 | 0.046401 | 2.1211 | 0.046401
2005/2006 | 2005-07-29 | 1.347 | 0.010283 | 1.347 | 0.010283
2005/2006 | 2005-07-30 | 0.01343 | 0.00010334 | 0.01343 | 0.00010334
2005/2006 | 2005-08-01 | 2.3917 | 0.044231 | 2.3917 | 0.044231
2005/2006 | 2005-08-02 | 0.04516 | 0.00051672 | 0.04516 | 0.00051672
2005/2006 | 2005-08-03 | 0.00672 | 0.00010334 | 0.00672 | 0.00010334
2005/2006 | 2005-08-04 | 0.02749 | 0.00020669 | 0.02749 | 0.00020669
2005/2006 | 2005-08-05 | 0.06929 | 0.00031003 | 0.06929 | 0.00031003
2005/2006 | 2005-08-06 | 0.14483 | 0.0007234 | 0.14483 | 0.0007234
2005/2006 | 2005-08-07 | 0.7853 | 0.003617 | 0.7853 | 0.003617
2005/2006 | 2005-08-08 | 0.39219 | 0.0026353 | 0.39219 | 0.0026353
2005/2006 | 2005-08-10 | 0.51868 | 0.01235 | 0.51868 | 0.01235
2005/2006 | 2005-08-11 | 0.05591 | 0.0003617 | 0.05591 | 0.0003617
2005/2006 | 2005-08-12 | 0.79961 | 0.014778 | 0.79961 | 0.014778
2005/2006 | 2005-08-13 | 0.08371 | 0.00031003 | 0.08371 | 0.00031003
2005/2006 | 2005-08-15 | 0.0587 | 0.00082675 | 0.0587 | 0.00082675
2005/2006 | 2005-08-16 | 0.92084 | 0.0081641 | 0.92084 | 0.0081641
2005/2006 | 2005-08-17 | 0.00553 | 5.1672e-05 | 0.00553 | 5.1672e-05
2005/2006 | 2005-08-18 | 0.4309 | 0.0030486 | 0.4309 | 0.0030486
2005/2006 | 2005-08-19 | 0.31096 | 0.0065106 | 0.31096 | 0.0065106
2005/2006 | 2005-08-21 | 0.00868 | 0.0021702 | 0.00868 | 0.0021702
2005/2006 | 2005-08-22 | 0.06769 | 0.0003617 | 0.06769 | 0.0003617
2005/2006 | 2005-08-23 | 0.24265 | 0.0025836 | 0.24265 | 0.0025836
2005/2006 | 2005-08-24 | 0.02212 | 0.00020669 | 0.02212 | 0.00020669
2005/2006 | 2005-08-25 | 0.68372 | 0.0083708 | 0.68372 | 0.0083708
2005/2006 | 2005-08-27 | 0.21687 | 0.003617 | 0.21687 | 0.003617
2005/2006 | 2005-08-28 | 0.15011 | 0.0010334 | 0.15011 | 0.0010334
2005/2006 | 2005-08-29 | 0.3818 | 0.0040304 | 0.3818 | 0.0040304
2005/2006 | 2005-08-30 | 1.0748 | 0.026094 | 1.0748 | 0.026094
2005/2006 | 2005-08-31 | 0.13776 | 0.0025319 | 0.13776 | 0.0025319
2005/2006 | 2005-09-02 | 0.56451 | 0.003307 | 0.56451 | 0.003307
2005/2006 | 2005-09-05 | 0.25815 | 0.003152 | 0.25815 | 0.003152
2005/2006 | 2005-09-06 | 0.23666 | 0.00077507 | 0.23666 | 0.00077507
2005/2006 | 2005-09-07 | 0.17786 | 0.00062006 | 0.17786 | 0.00062006
2005/2006 | 2005-09-08 | 0.2304 | 0.0018602 | 0.2304 | 0.0018602
2005/2006 | 2005-09-11 | 9.7641 | 0.12303 | 9.7641 | 0.12303
2005/2006 | 2005-09-12 | 0.00351 | 5.1672e-05 | 0.00351 | 5.1672e-05
2005/2006 | 2005-09-13 | 0.00326 | 0.00015501 | 0.00326 | 0.00015501
2005/2006 | 2005-09-14 | 1.7805 | 0.076939 | 1.7805 | 0.076939
2005/2006 | 2005-09-15 | 0.10934 | 0.0018602 | 0.10934 | 0.0018602
2005/2006 | 2005-09-16 | 0.43688 | 0.019118 | 0.43688 | 0.019118
2005/2006 | 2005-09-17 | 0.07379 | 0.0035137 | 0.07379 | 0.0035137
2005/2006 | 2005-09-18 | 1.4936 | 0.031726 | 1.4936 | 0.031726
2005/2006 | 2005-09-19 | 0.08588 | 0.0013435 | 0.08588 | 0.0013435
2005/2006 | 2005-09-20 | 0.06769 | 0.00025836 | 0.06769 | 0.00025836
2005/2006 | 2005-09-21 | 0.05178 | 0.0029453 | 0.05178 | 0.0029453
2005/2006 | 2005-09-22 | 0.27469 | 0.0017052 | 0.27469 | 0.0017052
2005/2006 | 2005-09-23 | 0.6905 | 0.012091 | 0.6905 | 0.012091
2005/2006 | 2005-09-24 | 0.0031 | 5.1672e-05 | 0.0031 | 5.1672e-05
2005/2006 | 2005-09-25 | 3.8547 | 0.013538 | 3.8547 | 0.013538
2005/2006 | 2005-09-26 | 0.1578 | 0.07327 | 0.1578 | 0.07327
2005/2006 | 2005-09-28 | 0.0417 | 0.00015501 | 0.0417 | 0.00015501
2005/2006 | 2005-09-29 | 0.85645 | 0.0026353 | 0.85645 | 0.0026353
2005/2006 | 2005-09-30 | 0.57376 | 0.0045471 | 0.57376 | 0.0045471
2005/2006 | 2005-10-03 | 0.13781 | 0.0018085 | 0.13781 | 0.0018085
2005/2006 | 2005-10-04 | 0.95722 | 0.0059422 | 0.95722 | 0.0059422
2005/2006 | 2005-10-05 | 1.8243 | 0.0068723 | 1.8243 | 0.0068723
2005/2006 | 2005-10-06 | 1.2309 | 0.0073374 | 1.2309 | 0.0073374
2005/2006 | 2005-10-08 | 3.7888 | 0.05007 | 3.7888 | 0.05007
2005/2006 | 2005-10-09 | 0.00388 | 5.1672e-05 | 0.00388 | 5.1672e-05
2005/2006 | 2005-10-10 | 0.15377 | 0.00087842 | 0.15377 | 0.00087842
2005/2006 | 2005-10-11 | 5.1053 | 0.013021 | 5.1053 | 0.013021
2005/2006 | 2005-10-12 | 0.12567 | 0.0016535 | 0.12567 | 0.0016535
2005/2006 | 2005-10-13 | 1.26 | 0.01266 | 1.26 | 0.01266
2005/2006 | 2005-10-14 | 0.90084 | 0.0050121 | 0.90084 | 0.0050121
2005/2006 | 2005-10-17 | 0.49987 | 0.0052188 | 0.49987 | 0.0052188
2005/2006 | 2005-10-18 | 0.33571 | 0.0023252 | 0.33571 | 0.0023252
2005/2006 | 2005-10-19 | 1.8514 | 0.013176 | 1.8514 | 0.013176
2005/2006 | 2005-10-20 | 2.5867 | 0.012711 | 2.5867 | 0.012711
2005/2006 | 2005-10-21 | 1.1932 | 0.024647 | 1.1932 | 0.024647
2005/2006 | 2005-10-22 | 0.12406 | 0.0010851 | 0.12406 | 0.0010851
2005/2006 | 2005-10-25 | 0.20069 | 0.0024286 | 0.20069 | 0.0024286
2005/2006 | 2005-10-26 | 0.957 | 0.006614 | 0.957 | 0.006614
2005/2006 | 2005-10-27 | 0.30254 | 0.0071307 | 0.30254 | 0.0071307
2005/2006 | 2005-10-28 | 0.01013 | 0.0003617 | 0.01013 | 0.0003617
2005/2006 | 2005-10-30 | 0.01964 | 0.00010334 | 0.01964 | 0.00010334
2005/2006 | 2005-10-31 | 0.39446 | 0.0019635 | 0.39446 | 0.0019635
2005/2006 | 2005-11-01 | 0.41839 | 0.0021702 | 0.41839 | 0.0021702
2005/2006 | 2005-11-02 | 0.08184 | 0.0007234 | 0.08184 | 0.0007234
2005/2006 | 2005-11-03 | 0.03235 | 0.00025836 | 0.03235 | 0.00025836
2005/2006 | 2005-11-04 | 0.0574 | 0.00098176 | 0.0574 | 0.00098176
2005/2006 | 2005-11-06 | 0.00475 | 5.1672e-05 | 0.00475 | 5.1672e-05
2005/2006 | 2005-11-08 | 0.16219 | 0.0007234 | 0.16219 | 0.0007234
2005/2006 | 2005-11-09 | 4.691 | 0.032398 | 4.691 | 0.032398
2005/2006 | 2005-11-10 | 0.34532 | 0.0012918 | 0.34532 | 0.0012918
2005/2006 | 2005-11-11 | 0.1298 | 0.00082675 | 0.1298 | 0.00082675
2005/2006 | 2005-11-13 | 3.8355 | 0.011729 | 3.8355 | 0.011729
2005/2006 | 2005-11-15 | 0.08867 | 0.0017568 | 0.08867 | 0.0017568
2005/2006 | 2005-11-16 | 0.2163 | 0.074355 | 0.2163 | 0.074355
2005/2006 | 2005-11-17 | 2.755 | 0.027076 | 2.755 | 0.027076
2005/2006 | 2005-11-18 | 0.22487 | 0.0017568 | 0.22487 | 0.0017568
2005/2006 | 2005-11-19 | 0.23252 | 0.025836 | 0.23252 | 0.025836
2005/2006 | 2005-11-20 | 0.10644 | 0.0010334 | 0.10644 | 0.0010334
2005/2006 | 2005-11-21 | 0.20488 | 0.0084225 | 0.20488 | 0.0084225
2005/2006 | 2005-11-22 | 0.32497 | 0.0027386 | 0.32497 | 0.0027386
2005/2006 | 2005-11-23 | 0.12287 | 0.00082675 | 0.12287 | 0.00082675
2005/2006 | 2005-11-24 | 0.07265 | 0.0003617 | 0.07265 | 0.0003617
2005/2006 | 2005-11-25 | 0.43853 | 0.0024802 | 0.43853 | 0.0024802
2005/2006 | 2005-11-26 | 5e-05 | 5.1672e-05 | 5e-05 | 5.1672e-05
2005/2006 | 2005-11-27 | 0.80804 | 0.0055805 | 0.80804 | 0.0055805
2005/2006 | 2005-11-28 | 4.0204 | 0.12174 | 4.0204 | 0.12174
2005/2006 | 2005-11-29 | 0.38521 | 0.0033587 | 0.38521 | 0.0033587
2005/2006 | 2005-11-30 | 0.45326 | 0.0016535 | 0.45326 | 0.0016535
2005/2006 | 2005-12-01 | 4.7452 | 0.02997 | 4.7452 | 0.02997
2005/2006 | 2005-12-02 | 0.2257 | 0.00082675 | 0.2257 | 0.00082675
2005/2006 | 2005-12-04 | 0.05426 | 0.0054255 | 0.05426 | 0.0054255
2005/2006 | 2005-12-05 | 1.8708 | 0.034827 | 1.8708 | 0.034827
2005/2006 | 2005-12-06 | 3.9089 | 0.051568 | 3.9089 | 0.051568
2005/2006 | 2005-12-07 | 4.1834 | 0.01297 | 4.1834 | 0.01297
2005/2006 | 2005-12-08 | 0.35173 | 0.0010851 | 0.35173 | 0.0010851
2005/2006 | 2005-12-09 | 0.61381 | 0.0049605 | 0.61381 | 0.0049605
2005/2006 | 2005-12-10 | 0.51439 | 0.0056839 | 0.51439 | 0.0056839
2005/2006 | 2005-12-11 | 0.63312 | 0.020204 | 0.63312 | 0.020204
2005/2006 | 2005-12-12 | 0.33813 | 0.0014468 | 0.33813 | 0.0014468
2005/2006 | 2005-12-13 | 0.3107 | 0.0021702 | 0.3107 | 0.0021702
2005/2006 | 2005-12-14 | 0.42928 | 0.0057872 | 0.42928 | 0.0057872
2005/2006 | 2005-12-15 | 0.80886 | 0.0089909 | 0.80886 | 0.0089909
2005/2006 | 2005-12-16 | 0.05891 | 0.00046504 | 0.05891 | 0.00046504
2005/2006 | 2005-12-17 | 1.2092 | 0.003462 | 1.2092 | 0.003462
2005/2006 | 2005-12-18 | 0 | 0 | 0 | 0
2005/2006 | 2005-12-19 | 0.58932 | 0.0058389 | 0.58932 | 0.0058389
2005/2006 | 2005-12-20 | 2.8317 | 0.022477 | 2.8317 | 0.022477
2005/2006 | 2005-12-21 | 0.61072 | 0.003927 | 0.61072 | 0.003927
2005/2006 | 2005-12-22 | 1.0237 | 0.014468 | 1.0237 | 0.014468
2005/2006 | 2005-12-23 | 3.5295 | 0.019377 | 3.5295 | 0.019377
2005/2006 | 2005-12-25 | 0.81331 | 0.081331 | 0.81331 | 0.081331
2005/2006 | 2005-12-26 | 0.09962 | 0.012453 | 0.09962 | 0.012453
2005/2006 | 2005-12-28 | 0.57181 | 0.0040304 | 0.57181 | 0.0040304
2005/2006 | 2005-12-29 | 0.08914 | 0.00046504 | 0.08914 | 0.00046504
2005/2006 | 2005-12-31 | 0.09921 | 0.0018602 | 0.09921 | 0.0018602
2005/2006 | 2006-01-02 | 0.43079 | 0.0019118 | 0.43079 | 0.0019118
2005/2006 | 2006-01-03 | 0.0865 | 0.00056839 | 0.0865 | 0.00056839
2005/2006 | 2006-01-04 | 3.407 | 0.044489 | 3.407 | 0.044489
2005/2006 | 2006-01-05 | 1.6824 | 0.010644 | 1.6824 | 0.010644
2005/2006 | 2006-01-06 | 0.02491 | 0.012453 | 0.02491 | 0.012453
2005/2006 | 2006-01-07 | 0.07647 | 0.0010334 | 0.07647 | 0.0010334
2005/2006 | 2006-01-09 | 0.0123 | 0.00015501 | 0.0123 | 0.00015501
2005/2006 | 2006-01-10 | 0.11621 | 0.0020669 | 0.11621 | 0.0020669
2005/2006 | 2006-01-11 | 0.41756 | 0.002997 | 0.41756 | 0.002997
2005/2006 | 2006-01-12 | 0.60982 | 0.0038754 | 0.60982 | 0.0038754
2005/2006 | 2006-01-13 | 0.32573 | 0.0023769 | 0.32573 | 0.0023769
2005/2006 | 2006-01-16 | 0.06418 | 0.00031003 | 0.06418 | 0.00031003
2005/2006 | 2006-01-17 | 0.08474 | 0.0010334 | 0.08474 | 0.0010334
2005/2006 | 2006-01-18 | 3.2935 | 0.024647 | 3.2935 | 0.024647
2005/2006 | 2006-01-19 | 0.02061 | 0.00015501 | 0.02061 | 0.00015501
2005/2006 | 2006-01-20 | 0.36795 | 0.003927 | 0.36795 | 0.003927
2005/2006 | 2006-01-23 | 0.32589 | 0.0061489 | 0.32589 | 0.0061489
2005/2006 | 2006-01-24 | 4.6306 | 0.071048 | 4.6306 | 0.071048
2005/2006 | 2006-01-25 | 0.43119 | 0.0057355 | 0.43119 | 0.0057355
2005/2006 | 2006-01-26 | 0.31835 | 0.0025319 | 0.31835 | 0.0025319
2005/2006 | 2006-01-27 | 0.00744 | 0.00015501 | 0.00744 | 0.00015501
2005/2006 | 2006-01-28 | 0.17734 | 0.0012401 | 0.17734 | 0.0012401
2005/2006 | 2006-01-30 | 0.56012 | 0.01576 | 0.56012 | 0.01576
2005/2006 | 2006-01-31 | 3.1367 | 0.1825 | 3.1367 | 0.1825
2005/2006 | 2006-02-02 | 0.71529 | 0.0078024 | 0.71529 | 0.0078024
2005/2006 | 2006-02-03 | 0.31298 | 0.0011884 | 0.31298 | 0.0011884
2005/2006 | 2006-02-04 | 0.5192 | 0.0012401 | 0.5192 | 0.0012401
2005/2006 | 2006-02-05 | 2.6136 | 0.056632 | 2.6136 | 0.056632
2005/2006 | 2006-02-06 | 0.01881 | 0.00020669 | 0.01881 | 0.00020669
2005/2006 | 2006-02-07 | 0.06185 | 0.00098176 | 0.06185 | 0.00098176
2005/2006 | 2006-02-08 | 0.37379 | 0.0039787 | 0.37379 | 0.0039787
2005/2006 | 2006-02-09 | 1.0796 | 0.0058389 | 1.0796 | 0.0058389
2005/2006 | 2006-02-10 | 0.33746 | 0.0032036 | 0.33746 | 0.0032036
2005/2006 | 2006-02-11 | 2.071 | 0.0041337 | 2.071 | 0.0041337
2005/2006 | 2006-02-12 | 0.0464 | 0.00010334 | 0.0464 | 0.00010334
2005/2006 | 2006-02-13 | 0.3419 | 0.0021185 | 0.3419 | 0.0021185
2005/2006 | 2006-02-14 | 0.92787 | 0.0039787 | 0.92787 | 0.0039787
2005/2006 | 2006-02-16 | 0.39664 | 0.040356 | 0.39664 | 0.040356
2005/2006 | 2006-02-17 | 0.20524 | 0.0010334 | 0.20524 | 0.0010334
2005/2006 | 2006-02-18 | 0.25526 | 0.0026869 | 0.25526 | 0.0026869
2005/2006 | 2006-02-20 | 6.1149 | 0.040149 | 6.1149 | 0.040149
2005/2006 | 2006-02-21 | 0.19237 | 0.00082675 | 0.19237 | 0.00082675
2005/2006 | 2006-02-22 | 0.00765 | 5.1672e-05 | 0.00765 | 5.1672e-05
2005/2006 | 2006-02-23 | 0.19857 | 0.0013435 | 0.19857 | 0.0013435
2005/2006 | 2006-02-24 | 5.639 | 0.040149 | 5.639 | 0.040149
2005/2006 | 2006-02-25 | 0.0076 | 5.1672e-05 | 0.0076 | 5.1672e-05
2005/2006 | 2006-02-26 | 0.11223 | 0.00077507 | 0.11223 | 0.00077507
2005/2006 | 2006-02-28 | 0.96166 | 0.0083708 | 0.96166 | 0.0083708
2005/2006 | 2006-03-02 | 0.31871 | 0.0035137 | 0.31871 | 0.0035137
2005/2006 | 2006-03-03 | 0.30321 | 0.011936 | 0.30321 | 0.011936
2005/2006 | 2006-03-04 | 0.00915 | 0.0085775 | 0.00915 | 0.0085775
2005/2006 | 2006-03-05 | 0.05405 | 0.0044438 | 0.05405 | 0.0044438
2005/2006 | 2006-03-06 | 0.27179 | 0.0010334 | 0.27179 | 0.0010334
2005/2006 | 2006-03-07 | 0.29701 | 0.0024286 | 0.29701 | 0.0024286
2005/2006 | 2006-03-08 | 0.0479 | 0.0003617 | 0.0479 | 0.0003617
2005/2006 | 2006-03-09 | 2.2157 | 0.027748 | 2.2157 | 0.027748
2005/2006 | 2006-03-10 | 0.00434 | 0.00015501 | 0.00434 | 0.00015501
2005/2006 | 2006-03-11 | 0.91216 | 0.08717 | 0.91216 | 0.08717
2005/2006 | 2006-03-12 | 0.0217 | 0.0003617 | 0.0217 | 0.0003617
2005/2006 | 2006-03-13 | 0.17806 | 0.0013435 | 0.17806 | 0.0013435
2005/2006 | 2006-03-14 | 0.09937 | 0.00046504 | 0.09937 | 0.00046504
2005/2006 | 2006-03-16 | 4.1787 | 0.019997 | 4.1787 | 0.019997
2005/2006 | 2006-03-17 | 0.14231 | 0.0016018 | 0.14231 | 0.0016018
2005/2006 | 2006-03-20 | 0.20916 | 0.0019635 | 0.20916 | 0.0019635
2005/2006 | 2006-03-21 | 0.12091 | 0.0015501 | 0.12091 | 0.0015501
2005/2006 | 2006-03-22 | 0.16163 | 0.00062006 | 0.16163 | 0.00062006
2005/2006 | 2006-03-23 | 0.14442 | 0.0011884 | 0.14442 | 0.0011884
2005/2006 | 2006-03-24 | 28.4171 | 0.0572 | 21.6659 | 0.0572
2005/2006 | 2006-03-26 | 0.23769 | 0.0024286 | 0.23769 | 0.0024286
2005/2006 | 2006-03-27 | 1.2438 | 0.051827 | 1.2438 | 0.051827
2005/2006 | 2006-03-29 | 0.02114 | 0.00031003 | 0.02114 | 0.00031003
2005/2006 | 2006-03-30 | 0.24564 | 0.0021185 | 0.24564 | 0.0021185
2005/2006 | 2006-03-31 | 0.56368 | 0.0095592 | 0.56368 | 0.0095592
2006/2007 | 2006-04-03 | 0.06737 | 0.0010851 | 0.06737 | 0.0010851
2006/2007 | 2006-04-04 | 1.376 | 0.011368 | 1.376 | 0.011368
2006/2007 | 2006-04-05 | 0.63318 | 0.003617 | 0.63318 | 0.003617
2006/2007 | 2006-04-06 | 0.2257 | 0.0021702 | 0.2257 | 0.0021702
2006/2007 | 2006-04-07 | 0.28114 | 0.0032553 | 0.28114 | 0.0032553
2006/2007 | 2006-04-08 | 0.01385 | 5.1672e-05 | 0.01385 | 5.1672e-05
2006/2007 | 2006-04-09 | 3.0808 | 0.056632 | 3.0808 | 0.056632
2006/2007 | 2006-04-10 | 0.1095 | 0.0032553 | 0.1095 | 0.0032553
2006/2007 | 2006-04-11 | 1.5569 | 0.0094559 | 1.5569 | 0.0094559
2006/2007 | 2006-04-12 | 0.4668 | 0.0020669 | 0.4668 | 0.0020669
2006/2007 | 2006-04-13 | 0.0897 | 0.00041337 | 0.0897 | 0.00041337
2006/2007 | 2006-04-14 | 0.03338 | 0.00098176 | 0.03338 | 0.00098176
2006/2007 | 2006-04-18 | 0.006 | 0.0007234 | 0.006 | 0.0007234
2006/2007 | 2006-04-19 | 0.03617 | 0.00020669 | 0.03617 | 0.00020669
2006/2007 | 2006-04-20 | 0.01013 | 0.00020669 | 0.01013 | 0.00020669
2006/2007 | 2006-04-21 | 0.13331 | 0.00056839 | 0.13331 | 0.00056839
2006/2007 | 2006-04-23 | 0.01199 | 0.0014985 | 0.01199 | 0.0014985
2006/2007 | 2006-04-24 | 0.25712 | 0.0045988 | 0.25712 | 0.0045988
2006/2007 | 2006-04-25 | 2.3496 | 0.025474 | 2.3496 | 0.025474
2006/2007 | 2006-04-27 | 6.6315 | 0.017723 | 6.6315 | 0.017723
2006/2007 | 2006-04-28 | 0.24725 | 0.0014468 | 0.24725 | 0.0014468
2006/2007 | 2006-04-30 | 1.0881 | 0.030538 | 1.0881 | 0.030538
2006/2007 | 2006-05-01 | 0.70914 | 0.0028419 | 0.70914 | 0.0028419
2006/2007 | 2006-05-02 | 0.18875 | 0.0020669 | 0.18875 | 0.0020669
2006/2007 | 2006-05-03 | 0.10272 | 0.0003617 | 0.10272 | 0.0003617
2006/2007 | 2006-05-04 | 0.07575 | 0.00051672 | 0.07575 | 0.00051672
2006/2007 | 2006-05-06 | 0.00801 | 0.00025836 | 0.00801 | 0.00025836
2006/2007 | 2006-05-07 | 0.43135 | 0.0033587 | 0.43135 | 0.0033587
2006/2007 | 2006-05-09 | 0.33472 | 0.003462 | 0.33472 | 0.003462
2006/2007 | 2006-05-10 | 1.1074 | 0.0075957 | 1.1074 | 0.0075957
2006/2007 | 2006-05-11 | 1.2737 | 0.028678 | 1.2737 | 0.028678
2006/2007 | 2006-05-12 | 1.444 | 0.0097659 | 1.444 | 0.0097659
2006/2007 | 2006-05-13 | 0.00868 | 0.00015501 | 0.00868 | 0.00015501
2006/2007 | 2006-05-15 | 1.8556 | 0.0040821 | 1.8556 | 0.0040821
2006/2007 | 2006-05-16 | 0.02165 | 5.1672e-05 | 0.02165 | 5.1672e-05
2006/2007 | 2006-05-17 | 0.04769 | 0.00067173 | 0.04769 | 0.00067173
2006/2007 | 2006-05-18 | 0.12183 | 0.0007234 | 0.12183 | 0.0007234
2006/2007 | 2006-05-19 | 0.28937 | 0.0042371 | 0.28937 | 0.0042371
2006/2007 | 2006-05-22 | 0.08511 | 0.0007234 | 0.08511 | 0.0007234
2006/2007 | 2006-05-23 | 0.22178 | 0.0022735 | 0.22178 | 0.0022735
2006/2007 | 2006-05-24 | 0.47951 | 0.0043921 | 0.47951 | 0.0043921
2006/2007 | 2006-05-25 | 0.5455 | 0.0017052 | 0.5455 | 0.0017052
2006/2007 | 2006-05-26 | 0.08412 | 0.00056839 | 0.08412 | 0.00056839
2006/2007 | 2006-05-27 | 0.27794 | 0.025267 | 0.27794 | 0.025267
2006/2007 | 2006-05-28 | 0.61763 | 0.0032553 | 0.61763 | 0.0032553
2006/2007 | 2006-05-30 | 0.23293 | 0.0018602 | 0.23293 | 0.0018602
2006/2007 | 2006-05-31 | 0.71048 | 0.0056839 | 0.71048 | 0.0056839
2006/2007 | 2006-06-01 | 0.18302 | 0.00082675 | 0.18302 | 0.00082675
2006/2007 | 2006-06-02 | 0.21635 | 0.0018085 | 0.21635 | 0.0018085
2006/2007 | 2006-06-03 | 0.01953 | 0.0021702 | 0.01953 | 0.0021702
2006/2007 | 2006-06-06 | 0.32089 | 0.0026869 | 0.32089 | 0.0026869
2006/2007 | 2006-06-07 | 0.46598 | 0.0026869 | 0.46598 | 0.0026869
2006/2007 | 2006-06-08 | 0.14587 | 0.0017052 | 0.14587 | 0.0017052
2006/2007 | 2006-06-09 | 0.55506 | 0.020307 | 0.55506 | 0.020307
2006/2007 | 2006-06-12 | 75.9652 | 0.15848 | 21.6659 | 0.15848
2006/2007 | 2006-06-13 | 2.2359 | 0.017775 | 2.2359 | 0.017775
2006/2007 | 2006-06-14 | 0.46743 | 0.0049605 | 0.46743 | 0.0049605
2006/2007 | 2006-06-15 | 0.9738 | 0.0063556 | 0.9738 | 0.0063556
2006/2007 | 2006-06-16 | 1.0783 | 0.0048571 | 1.0783 | 0.0048571
2006/2007 | 2006-06-18 | 0.00775 | 0.00015501 | 0.00775 | 0.00015501
2006/2007 | 2006-06-19 | 8.6945 | 0.051517 | 8.6945 | 0.051517
2006/2007 | 2006-06-20 | 0.18292 | 0.00087842 | 0.18292 | 0.00087842
2006/2007 | 2006-06-21 | 0.59727 | 0.0045471 | 0.59727 | 0.0045471
2006/2007 | 2006-06-22 | 1.1141 | 0.011988 | 1.1141 | 0.011988
2006/2007 | 2006-06-23 | 0.70335 | 0.0062006 | 0.70335 | 0.0062006
2006/2007 | 2006-06-24 | 0.00646 | 0.00010334 | 0.00646 | 0.00010334
2006/2007 | 2006-06-25 | 3.3457 | 0.028316 | 3.3457 | 0.028316
2006/2007 | 2006-06-26 | 0.01364 | 0.00025836 | 0.01364 | 0.00025836
2006/2007 | 2006-06-27 | 2.4593 | 0.013021 | 2.4593 | 0.013021
2006/2007 | 2006-06-28 | 1.8885 | 0.0139 | 1.8885 | 0.0139
2006/2007 | 2006-06-29 | 0.20849 | 0.0033587 | 0.20849 | 0.0033587
2006/2007 | 2006-07-02 | 0.0248 | 0.00025836 | 0.0248 | 0.00025836
2006/2007 | 2006-07-03 | 0.00041 | 5.1672e-05 | 0.00041 | 5.1672e-05
2006/2007 | 2006-07-04 | 0.16013 | 0.0037204 | 0.16013 | 0.0037204
2006/2007 | 2006-07-05 | 0.82209 | 0.0044438 | 0.82209 | 0.0044438
2006/2007 | 2006-07-06 | 3.2109 | 0.020514 | 3.2109 | 0.020514
2006/2007 | 2006-07-07 | 3.3891 | 0.010128 | 3.3891 | 0.010128
2006/2007 | 2006-07-08 | 0.28327 | 0.0042371 | 0.28327 | 0.0042371
2006/2007 | 2006-07-10 | 0.10014 | 0.00062006 | 0.10014 | 0.00062006
2006/2007 | 2006-07-11 | 0.10169 | 0.0013435 | 0.10169 | 0.0013435
2006/2007 | 2006-07-12 | 1.9773 | 0.021857 | 1.9773 | 0.021857
2006/2007 | 2006-07-13 | 3.584 | 0.019325 | 3.584 | 0.019325
2006/2007 | 2006-07-14 | 1.1374 | 0.0044438 | 1.1374 | 0.0044438
2006/2007 | 2006-07-15 | 0.26838 | 0.0050638 | 0.26838 | 0.0050638
2006/2007 | 2006-07-16 | 0.13729 | 0.014158 | 0.13729 | 0.014158
2006/2007 | 2006-07-17 | 0.00382 | 5.1672e-05 | 0.00382 | 5.1672e-05
2006/2007 | 2006-07-18 | 0.03922 | 0.00025836 | 0.03922 | 0.00025836
2006/2007 | 2006-07-19 | 0.36547 | 0.0024802 | 0.36547 | 0.0024802
2006/2007 | 2006-07-20 | 0.78463 | 0.0061489 | 0.78463 | 0.0061489
2006/2007 | 2006-07-21 | 1.1418 | 0.0094559 | 1.1418 | 0.0094559
2006/2007 | 2006-07-23 | 0.00403 | 0.00010334 | 0.00403 | 0.00010334
2006/2007 | 2006-07-24 | 0.30295 | 0.0021702 | 0.30295 | 0.0021702
2006/2007 | 2006-07-25 | 0.22721 | 0.003152 | 0.22721 | 0.003152
2006/2007 | 2006-07-27 | 0.00744 | 0.00062006 | 0.00744 | 0.00062006
2006/2007 | 2006-07-28 | 0.06077 | 0.00051672 | 0.06077 | 0.00051672
2006/2007 | 2006-07-30 | 0.00114 | 0.00010334 | 0.00114 | 0.00010334
2006/2007 | 2006-07-31 | 0.02558 | 0.00015501 | 0.02558 | 0.00015501
2006/2007 | 2006-08-01 | 0.00563 | 5.1672e-05 | 0.00563 | 5.1672e-05
2006/2007 | 2006-08-02 | 0.02315 | 0.00020669 | 0.02315 | 0.00020669
2006/2007 | 2006-08-03 | 0.00656 | 5.1672e-05 | 0.00656 | 5.1672e-05
2006/2007 | 2006-08-04 | 1.1599 | 0.0047538 | 1.1599 | 0.0047538
2006/2007 | 2006-08-05 | 0.00129 | 0.00020669 | 0.00129 | 0.00020669
2006/2007 | 2006-08-06 | 0.28027 | 0.0013951 | 0.28027 | 0.0013951
2006/2007 | 2006-08-07 | 0.32878 | 0.0019635 | 0.32878 | 0.0019635
2006/2007 | 2006-08-08 | 0.08102 | 0.0018602 | 0.08102 | 0.0018602
2006/2007 | 2006-08-09 | 0.17207 | 0.0022219 | 0.17207 | 0.0022219
2006/2007 | 2006-08-10 | 0.40396 | 0.0022219 | 0.40396 | 0.0022219
2006/2007 | 2006-08-11 | 0.44515 | 0.0016018 | 0.44515 | 0.0016018
2006/2007 | 2006-08-13 | 2.0229 | 0.0089909 | 2.0229 | 0.0089909
2006/2007 | 2006-08-14 | 0.39885 | 0.013486 | 0.39885 | 0.013486
2006/2007 | 2006-08-15 | 0.68852 | 0.0032553 | 0.68852 | 0.0032553
2006/2007 | 2006-08-16 | 0.24607 | 0.0027386 | 0.24607 | 0.0027386
2006/2007 | 2006-08-17 | 0.24249 | 0.003927 | 0.24249 | 0.003927
2006/2007 | 2006-08-19 | 0.63013 | 0.03214 | 0.63013 | 0.03214
2006/2007 | 2006-08-22 | 0.39342 | 0.0021185 | 0.39342 | 0.0021185
2006/2007 | 2006-08-23 | 0.02119 | 0.0021185 | 0.02119 | 0.0021185
2006/2007 | 2006-08-27 | 0.06118 | 0.00020669 | 0.06118 | 0.00020669
2006/2007 | 2006-08-29 | 0.41694 | 0.1004 | 0.41694 | 0.1004
2006/2007 | 2006-08-30 | 0.31685 | 0.0042371 | 0.31685 | 0.0042371
2006/2007 | 2006-08-31 | 0.19594 | 0.00062006 | 0.19594 | 0.00062006
2006/2007 | 2006-09-01 | 2.4944 | 0.011781 | 2.4944 | 0.011781
2006/2007 | 2006-09-02 | 0.3215 | 0.0052705 | 0.3215 | 0.0052705
2006/2007 | 2006-09-03 | 0.11781 | 0.00098176 | 0.11781 | 0.00098176
2006/2007 | 2006-09-04 | 0.6244 | 0.0044954 | 0.6244 | 0.0044954
2006/2007 | 2006-09-05 | 0.5129 | 0.0063039 | 0.5129 | 0.0063039
2006/2007 | 2006-09-06 | 1.1904 | 0.0050638 | 1.1904 | 0.0050638
2006/2007 | 2006-09-07 | 0.38857 | 0.0010334 | 0.38857 | 0.0010334
2006/2007 | 2006-09-08 | 0.24885 | 0.031106 | 0.24885 | 0.031106
2006/2007 | 2006-09-09 | 0.17082 | 0.012711 | 0.17082 | 0.012711
2006/2007 | 2006-09-10 | 0.16235 | 0.0049088 | 0.16235 | 0.0049088
2006/2007 | 2006-09-11 | 0.00434 | 0.00010334 | 0.00434 | 0.00010334
2006/2007 | 2006-09-13 | 0.43915 | 0.007234 | 0.43915 | 0.007234
2006/2007 | 2006-09-14 | 1.3589 | 0.0062523 | 1.3589 | 0.0062523
2006/2007 | 2006-09-15 | 0.52503 | 0.003772 | 0.52503 | 0.003772
2006/2007 | 2006-09-16 | 0.01798 | 0.00031003 | 0.01798 | 0.00031003
2006/2007 | 2006-09-17 | 0.87909 | 0.016587 | 0.87909 | 0.016587
2006/2007 | 2006-09-19 | 0.01896 | 0.00020669 | 0.01896 | 0.00020669
2006/2007 | 2006-09-20 | 2.1437 | 0.01421 | 2.1437 | 0.01421
2006/2007 | 2006-09-21 | 16.3412 | 0.035602 | 16.3412 | 0.035602
2006/2007 | 2006-09-22 | 0.03544 | 0.00041337 | 0.03544 | 0.00041337
2006/2007 | 2006-09-25 | 0.14726 | 0.00077507 | 0.14726 | 0.00077507
2006/2007 | 2006-09-26 | 0.62182 | 0.0052188 | 0.62182 | 0.0052188
2006/2007 | 2006-09-27 | 0.15544 | 0.0017052 | 0.15544 | 0.0017052
2006/2007 | 2006-09-28 | 1.1824 | 0.0036687 | 1.1824 | 0.0036687
2006/2007 | 2006-09-29 | 0.5269 | 0.0054772 | 0.5269 | 0.0054772
2006/2007 | 2006-10-01 | 0.37886 | 0.0020152 | 0.37886 | 0.0020152
2006/2007 | 2006-10-02 | 0.54699 | 0.044386 | 0.54699 | 0.044386
2006/2007 | 2006-10-03 | 1.5348 | 0.0052188 | 1.5348 | 0.0052188
2006/2007 | 2006-10-04 | 1.092 | 0.010024 | 1.092 | 0.010024
2006/2007 | 2006-10-05 | 1.056 | 0.0045471 | 1.056 | 0.0045471
2006/2007 | 2006-10-06 | 0.84918 | 0.0046504 | 0.84918 | 0.0046504
2006/2007 | 2006-10-07 | 0.12783 | 0.0019635 | 0.12783 | 0.0019635
2006/2007 | 2006-10-09 | 0.84106 | 0.10396 | 0.84106 | 0.10396
2006/2007 | 2006-10-10 | 3.2504 | 0.039839 | 3.2504 | 0.039839
2006/2007 | 2006-10-11 | 1.4425 | 0.0082675 | 1.4425 | 0.0082675
2006/2007 | 2006-10-12 | 0.29147 | 0.0042371 | 0.29147 | 0.0042371
2006/2007 | 2006-10-13 | 0.17982 | 0.0012401 | 0.17982 | 0.0012401
2006/2007 | 2006-10-15 | 0.00155 | 0.00015501 | 0.00155 | 0.00015501
2006/2007 | 2006-10-16 | 0.01188 | 0.00010334 | 0.01188 | 0.00010334
2006/2007 | 2006-10-17 | 0.45006 | 0.0032036 | 0.45006 | 0.0032036
2006/2007 | 2006-10-18 | 0.37844 | 0.0044438 | 0.37844 | 0.0044438
2006/2007 | 2006-10-19 | 0.58714 | 0.0020152 | 0.58714 | 0.0020152
2006/2007 | 2006-10-20 | 0.76608 | 0.0040304 | 0.76608 | 0.0040304
2006/2007 | 2006-10-24 | 0.04867 | 0.00093009 | 0.04867 | 0.00093009
2006/2007 | 2006-10-25 | 0.32424 | 0.0012918 | 0.32424 | 0.0012918
2006/2007 | 2006-10-26 | 0.37281 | 0.0014468 | 0.37281 | 0.0014468
2006/2007 | 2006-10-27 | 0.09379 | 0.0011368 | 0.09379 | 0.0011368
2006/2007 | 2006-10-28 | 0.20204 | 0.10102 | 0.20204 | 0.10102
2006/2007 | 2006-10-29 | 1.9944 | 0.022735 | 1.9944 | 0.022735
2006/2007 | 2006-10-30 | 1.0791 | 0.016948 | 1.0791 | 0.016948
2006/2007 | 2006-10-31 | 0.96943 | 0.0059939 | 0.96943 | 0.0059939
2006/2007 | 2006-11-01 | 0.18679 | 0.0022219 | 0.18679 | 0.0022219
2006/2007 | 2006-11-02 | 0.36811 | 0.0017052 | 0.36811 | 0.0017052
2006/2007 | 2006-11-03 | 0.04009 | 0.00067173 | 0.04009 | 0.00067173
2006/2007 | 2006-11-06 | 0.04165 | 0.00051672 | 0.04165 | 0.00051672
2006/2007 | 2006-11-07 | 0.3769 | 0.0018085 | 0.3769 | 0.0018085
2006/2007 | 2006-11-08 | 1.4956 | 0.021547 | 1.4956 | 0.021547
2006/2007 | 2006-11-09 | 0.34424 | 0.013383 | 0.34424 | 0.013383
2006/2007 | 2006-11-10 | 0.10976 | 0.00051672 | 0.10976 | 0.00051672
2006/2007 | 2006-11-12 | 0.03927 | 0.0098176 | 0.03927 | 0.0098176
2006/2007 | 2006-11-13 | 0.26189 | 0.0035137 | 0.26189 | 0.0035137
2006/2007 | 2006-11-14 | 0.01194 | 0.0003617 | 0.01194 | 0.0003617
2006/2007 | 2006-11-15 | 0.21687 | 0.0022219 | 0.21687 | 0.0022219
2006/2007 | 2006-11-16 | 0.17904 | 0.0011884 | 0.17904 | 0.0011884
2006/2007 | 2006-11-17 | 1.9249 | 0.011213 | 1.9249 | 0.011213
2006/2007 | 2006-11-18 | 0.02026 | 0.0003617 | 0.02026 | 0.0003617
2006/2007 | 2006-11-20 | 0.03648 | 0.0007234 | 0.03648 | 0.0007234
2006/2007 | 2006-11-21 | 0.24596 | 0.0024802 | 0.24596 | 0.0024802
2006/2007 | 2006-11-22 | 0.70237 | 0.021805 | 0.70237 | 0.021805
2006/2007 | 2006-11-23 | 0.27509 | 0.0047021 | 0.27509 | 0.0047021
2006/2007 | 2006-11-24 | 0.88518 | 0.019894 | 0.88518 | 0.019894
2006/2007 | 2006-11-27 | 4.5105 | 0.032553 | 4.5105 | 0.032553
2006/2007 | 2006-11-28 | 0.03209 | 0.00020669 | 0.03209 | 0.00020669
2006/2007 | 2006-11-29 | 0.4389 | 0.0036687 | 0.4389 | 0.0036687
2006/2007 | 2006-11-30 | 6.7269 | 0.055599 | 6.7269 | 0.055599
2006/2007 | 2006-12-01 | 0.0527 | 0.00031003 | 0.0527 | 0.00031003
2006/2007 | 2006-12-03 | 0.00217 | 0.00015501 | 0.00217 | 0.00015501
2006/2007 | 2006-12-04 | 0.32992 | 0.0028936 | 0.32992 | 0.0028936
2006/2007 | 2006-12-05 | 0.9878 | 0.0036687 | 0.9878 | 0.0036687
2006/2007 | 2006-12-06 | 0.05064 | 0.00056839 | 0.05064 | 0.00056839
2006/2007 | 2006-12-07 | 0.2641 | 0.0050638 | 0.2641 | 0.0050638
2006/2007 | 2006-12-08 | 0.2751 | 0.0049605 | 0.2751 | 0.0049605
2006/2007 | 2006-12-09 | 0.44102 | 0.0026869 | 0.44102 | 0.0026869
2006/2007 | 2006-12-10 | 0.68434 | 0.026766 | 0.68434 | 0.026766
2006/2007 | 2006-12-11 | 0.37451 | 0.0050121 | 0.37451 | 0.0050121
2006/2007 | 2006-12-12 | 1.1637 | 0.013021 | 1.1637 | 0.013021
2006/2007 | 2006-12-13 | 0.18706 | 0.0015501 | 0.18706 | 0.0015501
2006/2007 | 2006-12-14 | 2.3662 | 0.012091 | 2.3662 | 0.012091
2006/2007 | 2006-12-15 | 0.84158 | 0.0036687 | 0.84158 | 0.0036687
2006/2007 | 2006-12-17 | 0.05632 | 0.00051672 | 0.05632 | 0.00051672
2006/2007 | 2006-12-18 | 2.1418 | 0.0085258 | 2.1418 | 0.0085258
2006/2007 | 2006-12-19 | 0.44805 | 0.0086292 | 0.44805 | 0.0086292
2006/2007 | 2006-12-20 | 1.1294 | 0.066915 | 1.1294 | 0.066915
2006/2007 | 2006-12-21 | 1.7941 | 0.012866 | 1.7941 | 0.012866
2006/2007 | 2006-12-22 | 0.02471 | 0.00041337 | 0.02471 | 0.00041337
2006/2007 | 2006-12-28 | 0.24322 | 0.013693 | 0.24322 | 0.013693
2006/2007 | 2006-12-29 | 0.16565 | 0.0020669 | 0.16565 | 0.0020669
2006/2007 | 2006-12-31 | 0.21392 | 0.020255 | 0.21392 | 0.020255
2006/2007 | 2007-01-01 | 0.85522 | 0.0085258 | 0.85522 | 0.0085258
2006/2007 | 2007-01-02 | 0.12029 | 0.0015501 | 0.12029 | 0.0015501
2006/2007 | 2007-01-03 | 0.52142 | 0.0032036 | 0.52142 | 0.0032036
2006/2007 | 2007-01-04 | 0.12505 | 0.0020152 | 0.12505 | 0.0020152
2006/2007 | 2007-01-05 | 0.47197 | 0.027283 | 0.47197 | 0.027283
2006/2007 | 2007-01-07 | 0.48494 | 0.0056322 | 0.48494 | 0.0056322
2006/2007 | 2007-01-08 | 0.82266 | 0.0059422 | 0.82266 | 0.0059422
2006/2007 | 2007-01-09 | 0.53077 | 0.0059422 | 0.53077 | 0.0059422
2006/2007 | 2007-01-10 | 0.46778 | 0.0018085 | 0.46778 | 0.0018085
2006/2007 | 2007-01-11 | 3.0288 | 0.063866 | 3.0288 | 0.063866
2006/2007 | 2007-01-12 | 0.49713 | 0.0041337 | 0.49713 | 0.0041337
2006/2007 | 2007-01-13 | 0.85 | 0.0059939 | 0.85 | 0.0059939
2006/2007 | 2007-01-14 | 1.0176 | 0.0054772 | 1.0176 | 0.0054772
2006/2007 | 2007-01-15 | 0.06807 | 0.00087842 | 0.06807 | 0.00087842
2006/2007 | 2007-01-16 | 0.49574 | 0.0046504 | 0.49574 | 0.0046504
2006/2007 | 2007-01-17 | 0.83399 | 0.0041854 | 0.83399 | 0.0041854
2006/2007 | 2007-01-18 | 0.0014 | 0.00015501 | 0.0014 | 0.00015501
2006/2007 | 2007-01-19 | 0.00465 | 0.00010334 | 0.00465 | 0.00010334
2006/2007 | 2007-01-21 | 0.97804 | 0.0058906 | 0.97804 | 0.0058906
2006/2007 | 2007-01-24 | 0.28544 | 0.0016535 | 0.28544 | 0.0016535
2006/2007 | 2007-01-25 | 0.89211 | 0.012143 | 0.89211 | 0.012143
2006/2007 | 2007-01-26 | 0.48447 | 0.0019635 | 0.48447 | 0.0019635
2006/2007 | 2007-01-27 | 0.10851 | 0.0018085 | 0.10851 | 0.0018085
2006/2007 | 2007-01-28 | 0.00124 | 0.00015501 | 0.00124 | 0.00015501
2006/2007 | 2007-01-30 | 0.06872 | 0.0007234 | 0.06872 | 0.0007234
2006/2007 | 2007-01-31 | 0.77228 | 0.0077507 | 0.77228 | 0.0077507
2006/2007 | 2007-02-01 | 0.20365 | 0.0028936 | 0.20365 | 0.0028936
2006/2007 | 2007-02-02 | 0.31623 | 0.0037204 | 0.31623 | 0.0037204
2006/2007 | 2007-02-04 | 1.7819 | 0.013383 | 1.7819 | 0.013383
2006/2007 | 2007-02-05 | 0.66863 | 0.0036687 | 0.66863 | 0.0036687
2006/2007 | 2007-02-06 | 1.2136 | 0.010489 | 1.2136 | 0.010489
2006/2007 | 2007-02-07 | 0.25531 | 0.0023252 | 0.25531 | 0.0023252
2006/2007 | 2007-02-08 | 0.37942 | 0.0007234 | 0.37942 | 0.0007234
2006/2007 | 2007-02-09 | 1.6223 | 0.015915 | 1.6223 | 0.015915
2006/2007 | 2007-02-12 | 0.87764 | 0.01824 | 0.87764 | 0.01824
2006/2007 | 2007-02-13 | 0.00997 | 0.00015501 | 0.00997 | 0.00015501
2006/2007 | 2007-02-14 | 0.99623 | 0.033948 | 0.99623 | 0.033948
2006/2007 | 2007-02-15 | 0.92105 | 0.0035137 | 0.92105 | 0.0035137
2006/2007 | 2007-02-16 | 0.58017 | 0.0018602 | 0.58017 | 0.0018602
2006/2007 | 2007-02-19 | 0.75957 | 0.0054255 | 0.75957 | 0.0054255
2006/2007 | 2007-02-20 | 1.5691 | 0.0038754 | 1.5691 | 0.0038754
2006/2007 | 2007-02-22 | 0.36072 | 0.0020152 | 0.36072 | 0.0020152
2006/2007 | 2007-02-23 | 0.09022 | 0.0003617 | 0.09022 | 0.0003617
2006/2007 | 2007-02-26 | 2.7411 | 0.027128 | 2.7411 | 0.027128
2006/2007 | 2007-02-27 | 0.95013 | 0.0053222 | 0.95013 | 0.0053222
2006/2007 | 2007-02-28 | 3.4395 | 0.11714 | 3.4395 | 0.11714
2006/2007 | 2007-03-01 | 0.00501 | 5.1672e-05 | 0.00501 | 5.1672e-05
2006/2007 | 2007-03-02 | 0.43978 | 0.0015501 | 0.43978 | 0.0015501
2006/2007 | 2007-03-03 | 0.0014 | 0.00015501 | 0.0014 | 0.00015501
2006/2007 | 2007-03-05 | 2.4337 | 0.027024 | 2.4337 | 0.027024
2006/2007 | 2007-03-06 | 0.14184 | 0.00046504 | 0.14184 | 0.00046504
2006/2007 | 2007-03-07 | 0.43192 | 0.023046 | 0.43192 | 0.023046
2006/2007 | 2007-03-08 | 0.10892 | 0.0010851 | 0.10892 | 0.0010851
2006/2007 | 2007-03-09 | 0.05389 | 0.00093009 | 0.05389 | 0.00093009
2006/2007 | 2007-03-11 | 1.6055 | 0.013383 | 1.6055 | 0.013383
2006/2007 | 2007-03-12 | 0.82855 | 0.0064073 | 0.82855 | 0.0064073
2006/2007 | 2007-03-13 | 1.4171 | 0.03493 | 1.4171 | 0.03493
2006/2007 | 2007-03-14 | 24.6937 | 0.28213 | 21.6659 | 0.26757
2006/2007 | 2007-03-15 | 2.1404 | 0.029504 | 2.1404 | 0.029504
2006/2007 | 2007-03-16 | 0.67965 | 0.010748 | 0.67965 | 0.010748
2006/2007 | 2007-03-17 | 0.02103 | 0.00020669 | 0.02103 | 0.00020669
2006/2007 | 2007-03-18 | 0.30373 | 0.0061489 | 0.30373 | 0.0061489
2006/2007 | 2007-03-19 | 0.35794 | 0.01576 | 0.35794 | 0.01576
2006/2007 | 2007-03-20 | 1.3695 | 0.026559 | 1.3695 | 0.026559
2006/2007 | 2007-03-21 | 3.2457 | 0.015708 | 3.2457 | 0.015708
2006/2007 | 2007-03-22 | 1.4654 | 0.081641 | 1.4654 | 0.081641
2006/2007 | 2007-03-23 | 0.246 | 0.0010334 | 0.246 | 0.0010334
2006/2007 | 2007-03-25 | 0.26001 | 0.00087842 | 0.26001 | 0.00087842
2006/2007 | 2007-03-26 | 0.54694 | 0.0059422 | 0.54694 | 0.0059422
2006/2007 | 2007-03-27 | 2.0123 | 0.0078024 | 2.0123 | 0.0078024
2006/2007 | 2007-03-28 | 2.0858 | 0.012556 | 2.0858 | 0.012556
2006/2007 | 2007-03-29 | 6.3951 | 0.033793 | 6.3951 | 0.033793
2006/2007 | 2007-03-30 | 0.21371 | 0.00077507 | 0.21371 | 0.00077507
2006/2007 | 2007-03-31 | 0.35256 | 0.0014468 | 0.35256 | 0.0014468
2007/2008 | 2007-04-02 | 0.08164 | 0.00046504 | 0.08164 | 0.00046504
2007/2008 | 2007-04-03 | 0.28367 | 0.0028419 | 0.28367 | 0.0028419
2007/2008 | 2007-04-05 | 0.29143 | 0.0033587 | 0.29143 | 0.0033587
2007/2008 | 2007-04-06 | 0.12753 | 0.0017052 | 0.12753 | 0.0017052
2007/2008 | 2007-04-08 | 0.05984 | 0.0043404 | 0.05984 | 0.0043404
2007/2008 | 2007-04-10 | 0.17987 | 0.0013951 | 0.17987 | 0.0013951
2007/2008 | 2007-04-11 | 0.09869 | 0.00051672 | 0.09869 | 0.00051672
2007/2008 | 2007-04-12 | 0.70025 | 0.052757 | 0.70025 | 0.052757
2007/2008 | 2007-04-13 | 3.0024 | 0.059784 | 3.0024 | 0.059784
2007/2008 | 2007-04-15 | 0.16886 | 0.00098176 | 0.16886 | 0.00098176
2007/2008 | 2007-04-16 | 1.0121 | 0.0039787 | 1.0121 | 0.0039787
2007/2008 | 2007-04-17 | 0.39431 | 0.0032036 | 0.39431 | 0.0032036
2007/2008 | 2007-04-18 | 0.16565 | 0.0016018 | 0.16565 | 0.0016018
2007/2008 | 2007-04-19 | 0.12261 | 0.0028419 | 0.12261 | 0.0028419
2007/2008 | 2007-04-20 | 0.5348 | 0.0035653 | 0.5348 | 0.0035653
2007/2008 | 2007-04-22 | 0.34775 | 0.034775 | 0.34775 | 0.034775
2007/2008 | 2007-04-23 | 0.36945 | 0.0048571 | 0.36945 | 0.0048571
2007/2008 | 2007-04-24 | 0.02217 | 0.00031003 | 0.02217 | 0.00031003
2007/2008 | 2007-04-26 | 0.45491 | 0.0020669 | 0.45491 | 0.0020669
2007/2008 | 2007-04-27 | 0.06785 | 0.00082675 | 0.06785 | 0.00082675
2007/2008 | 2007-04-28 | 0.72599 | 0.003772 | 0.72599 | 0.003772
2007/2008 | 2007-04-29 | 0.00124 | 0.00015501 | 0.00124 | 0.00015501
2007/2008 | 2007-04-30 | 0.64946 | 0.0029453 | 0.64946 | 0.0029453
2007/2008 | 2007-05-01 | 0.2196 | 0.0043921 | 0.2196 | 0.0043921
2007/2008 | 2007-05-02 | 0.18525 | 0.003772 | 0.18525 | 0.003772
2007/2008 | 2007-05-03 | 0.32062 | 0.003462 | 0.32062 | 0.003462
2007/2008 | 2007-05-04 | 0.19909 | 0.0027903 | 0.19909 | 0.0027903
2007/2008 | 2007-05-06 | 0.30306 | 0.0034103 | 0.30306 | 0.0034103
2007/2008 | 2007-05-07 | 0.39502 | 0.0019118 | 0.39502 | 0.0019118
2007/2008 | 2007-05-08 | 0.02951 | 0.00051672 | 0.02951 | 0.00051672
2007/2008 | 2007-05-09 | 0.16282 | 0.0018085 | 0.16282 | 0.0018085
2007/2008 | 2007-05-10 | 2.1692 | 0.058854 | 2.1692 | 0.058854
2007/2008 | 2007-05-11 | 0.13052 | 0.00087842 | 0.13052 | 0.00087842
2007/2008 | 2007-05-12 | 2.0324 | 0.033845 | 2.0324 | 0.033845
2007/2008 | 2007-05-14 | 1.7282 | 0.099829 | 1.7282 | 0.099829
2007/2008 | 2007-05-15 | 0.38883 | 0.0014985 | 0.38883 | 0.0014985
2007/2008 | 2007-05-16 | 1.3975 | 0.0092492 | 1.3975 | 0.0092492
2007/2008 | 2007-05-17 | 0.16586 | 0.0007234 | 0.16586 | 0.0007234
2007/2008 | 2007-05-18 | 0.06547 | 0.00025836 | 0.06547 | 0.00025836
2007/2008 | 2007-05-20 | 0.01302 | 0.00010334 | 0.01302 | 0.00010334
2007/2008 | 2007-05-21 | 1.7551 | 0.0094559 | 1.7551 | 0.0094559
2007/2008 | 2007-05-22 | 0.27909 | 0.0011884 | 0.27909 | 0.0011884
2007/2008 | 2007-05-23 | 0.28709 | 0.0015501 | 0.28709 | 0.0015501
2007/2008 | 2007-05-24 | 0.09963 | 0.0003617 | 0.09963 | 0.0003617
2007/2008 | 2007-05-25 | 0.09642 | 0.0003617 | 0.09642 | 0.0003617
2007/2008 | 2007-05-26 | 0.0434 | 0.0054255 | 0.0434 | 0.0054255
2007/2008 | 2007-05-28 | 0.07409 | 0.00056839 | 0.07409 | 0.00056839
2007/2008 | 2007-05-29 | 0.41228 | 0.0016535 | 0.41228 | 0.0016535
2007/2008 | 2007-05-30 | 0.40257 | 0.0022219 | 0.40257 | 0.0022219
2007/2008 | 2007-05-31 | 0.03271 | 0.0055805 | 0.03271 | 0.0055805
2007/2008 | 2007-06-01 | 1.2439 | 0.0038754 | 1.2439 | 0.0038754
2007/2008 | 2007-06-04 | 0.0511 | 0.0003617 | 0.0511 | 0.0003617
2007/2008 | 2007-06-05 | 0.3259 | 0.0099209 | 0.3259 | 0.0099209
2007/2008 | 2007-06-06 | 0.02253 | 0.00010334 | 0.02253 | 0.00010334
2007/2008 | 2007-06-07 | 0.76479 | 0.01824 | 0.76479 | 0.01824
2007/2008 | 2007-06-08 | 0.82716 | 0.0071307 | 0.82716 | 0.0071307
2007/2008 | 2007-06-09 | 0.00641 | 5.1672e-05 | 0.00641 | 5.1672e-05
2007/2008 | 2007-06-10 | 0.03581 | 0.0003617 | 0.03581 | 0.0003617
2007/2008 | 2007-06-11 | 1.3184 | 0.0054255 | 1.3184 | 0.0054255
2007/2008 | 2007-06-12 | 3.7681 | 0.011368 | 3.7681 | 0.011368
2007/2008 | 2007-06-13 | 0.11425 | 0.0012918 | 0.11425 | 0.0012918
2007/2008 | 2007-06-14 | 1.6979 | 0.0043404 | 1.6979 | 0.0043404
2007/2008 | 2007-06-15 | 0.06423 | 0.0003617 | 0.06423 | 0.0003617
2007/2008 | 2007-06-17 | 0.00723 | 0.00025836 | 0.00723 | 0.00025836
2007/2008 | 2007-06-19 | 0.0032 | 5.1672e-05 | 0.0032 | 5.1672e-05
2007/2008 | 2007-06-20 | 0.9339 | 0.062471 | 0.9339 | 0.062471
2007/2008 | 2007-06-21 | 0.9225 | 0.0024802 | 0.9225 | 0.0024802
2007/2008 | 2007-06-22 | 0.34486 | 0.019687 | 0.34486 | 0.019687
2007/2008 | 2007-06-23 | 1.431 | 0.045833 | 1.431 | 0.045833
2007/2008 | 2007-06-25 | 0.00537 | 5.1672e-05 | 0.00537 | 5.1672e-05
2007/2008 | 2007-06-26 | 0.19366 | 0.0016535 | 0.19366 | 0.0016535
2007/2008 | 2007-06-27 | 0.43993 | 0.0017052 | 0.43993 | 0.0017052
2007/2008 | 2007-06-28 | 0.18808 | 0.0010334 | 0.18808 | 0.0010334
2007/2008 | 2007-06-29 | 2.6918 | 0.0026353 | 2.6918 | 0.0026353
2007/2008 | 2007-06-30 | 0.04278 | 0.00020669 | 0.04278 | 0.00020669
2007/2008 | 2007-07-02 | 0.06718 | 0.0011884 | 0.06718 | 0.0011884
2007/2008 | 2007-07-03 | 0.2457 | 0.0139 | 0.2457 | 0.0139
2007/2008 | 2007-07-04 | 0.84694 | 0.0074407 | 0.84694 | 0.0074407
2007/2008 | 2007-07-05 | 1.8399 | 0.0077507 | 1.8399 | 0.0077507
2007/2008 | 2007-07-06 | 2.1802 | 0.0082675 | 2.1802 | 0.0082675
2007/2008 | 2007-07-07 | 0.03028 | 0.012505 | 0.03028 | 0.012505
2007/2008 | 2007-07-09 | 0.13714 | 0.0010334 | 0.13714 | 0.0010334
2007/2008 | 2007-07-10 | 20.7271 | 0.1253 | 20.7271 | 0.1253
2007/2008 | 2007-07-11 | 3.549 | 0.025681 | 3.549 | 0.025681
2007/2008 | 2007-07-12 | 0.51883 | 0.0045471 | 0.51883 | 0.0045471
2007/2008 | 2007-07-13 | 2.1366 | 0.0058389 | 2.1366 | 0.0058389
2007/2008 | 2007-07-15 | 0.18137 | 0.0013951 | 0.18137 | 0.0013951
2007/2008 | 2007-07-16 | 0.28326 | 0.003152 | 0.28326 | 0.003152
2007/2008 | 2007-07-17 | 0.03323 | 0.0013951 | 0.03323 | 0.0013951
2007/2008 | 2007-07-18 | 0.7821 | 0.0031003 | 0.7821 | 0.0031003
2007/2008 | 2007-07-19 | 4.355 | 0.011471 | 4.355 | 0.011471
2007/2008 | 2007-07-20 | 0.15915 | 0.0014468 | 0.15915 | 0.0014468
2007/2008 | 2007-07-22 | 0.2875 | 0.0026869 | 0.2875 | 0.0026869
2007/2008 | 2007-07-23 | 0.10707 | 0.0014468 | 0.10707 | 0.0014468
2007/2008 | 2007-07-24 | 0.76294 | 0.0033587 | 0.76294 | 0.0033587
2007/2008 | 2007-07-25 | 0.73318 | 0.011109 | 0.73318 | 0.011109
2007/2008 | 2007-07-27 | 0.20566 | 0.0016018 | 0.20566 | 0.0016018
2007/2008 | 2007-07-29 | 0.07906 | 0.00093009 | 0.07906 | 0.00093009
2007/2008 | 2007-07-30 | 0.02925 | 0.00020669 | 0.02925 | 0.00020669
2007/2008 | 2007-07-31 | 0.04046 | 0.00046504 | 0.04046 | 0.00046504
2007/2008 | 2007-08-01 | 0.05514 | 0.0025836 | 0.05514 | 0.0025836
2007/2008 | 2007-08-02 | 0.07957 | 0.00051672 | 0.07957 | 0.00051672
2007/2008 | 2007-08-03 | 3.0575 | 0.012401 | 3.0575 | 0.012401
2007/2008 | 2007-08-05 | 0.06195 | 0.00056839 | 0.06195 | 0.00056839
2007/2008 | 2007-08-06 | 0.43146 | 0.0035137 | 0.43146 | 0.0035137
2007/2008 | 2007-08-07 | 0.28548 | 0.082158 | 0.28548 | 0.082158
2007/2008 | 2007-08-08 | 1.1123 | 0.0048571 | 1.1123 | 0.0048571
2007/2008 | 2007-08-09 | 0.24048 | 0.0047538 | 0.24048 | 0.0047538
2007/2008 | 2007-08-10 | 0.00109 | 0.00015501 | 0.00109 | 0.00015501
2007/2008 | 2007-08-11 | 2.94 | 0.018292 | 2.94 | 0.018292
2007/2008 | 2007-08-12 | 0.35746 | 0.0050638 | 0.35746 | 0.0050638
2007/2008 | 2007-08-13 | 0.03684 | 0.00025836 | 0.03684 | 0.00025836
2007/2008 | 2007-08-14 | 0.15977 | 0.00051672 | 0.15977 | 0.00051672
2007/2008 | 2007-08-15 | 2.3285 | 0.07203 | 2.3285 | 0.07203
2007/2008 | 2007-08-16 | 0.03395 | 0.00025836 | 0.03395 | 0.00025836
2007/2008 | 2007-08-17 | 1.1907 | 0.007389 | 1.1907 | 0.007389
2007/2008 | 2007-08-18 | 0.10288 | 0.00077507 | 0.10288 | 0.00077507
2007/2008 | 2007-08-19 | 0.39105 | 0.0044438 | 0.39105 | 0.0044438
2007/2008 | 2007-08-20 | 0.12349 | 0.00051672 | 0.12349 | 0.00051672
2007/2008 | 2007-08-21 | 0.34972 | 0.0011368 | 0.34972 | 0.0011368
2007/2008 | 2007-08-22 | 0.41559 | 0.0019118 | 0.41559 | 0.0019118
2007/2008 | 2007-08-23 | 0.18664 | 0.0010851 | 0.18664 | 0.0010851
2007/2008 | 2007-08-25 | 0.58038 | 0.00093009 | 0.58038 | 0.00093009
2007/2008 | 2007-08-27 | 0.18178 | 0.0014468 | 0.18178 | 0.0014468
2007/2008 | 2007-08-28 | 1.7586 | 0.019377 | 1.7586 | 0.019377
2007/2008 | 2007-08-29 | 1.5286 | 0.0056322 | 1.5286 | 0.0056322
2007/2008 | 2007-08-30 | 0.43559 | 0.0021185 | 0.43559 | 0.0021185
2007/2008 | 2007-08-31 | 0.41064 | 0.0013951 | 0.41064 | 0.0013951
2007/2008 | 2007-09-01 | 0.00527 | 0.00015501 | 0.00527 | 0.00015501
2007/2008 | 2007-09-02 | 0.0016 | 0.00020669 | 0.0016 | 0.00020669
2007/2008 | 2007-09-03 | 0.03224 | 0.0026869 | 0.03224 | 0.0026869
2007/2008 | 2007-09-04 | 0.17207 | 0.00051672 | 0.17207 | 0.00051672
2007/2008 | 2007-09-05 | 1.2423 | 0.0095592 | 1.2423 | 0.0095592
2007/2008 | 2007-09-06 | 0.33137 | 0.00087842 | 0.33137 | 0.00087842
2007/2008 | 2007-09-07 | 0.29535 | 0.00087842 | 0.29535 | 0.00087842
2007/2008 | 2007-09-10 | 0.01286 | 0.0003617 | 0.01286 | 0.0003617
2007/2008 | 2007-09-11 | 0.06309 | 0.00062006 | 0.06309 | 0.00062006
2007/2008 | 2007-09-12 | 0.2289 | 0.00077507 | 0.2289 | 0.00077507
2007/2008 | 2007-09-13 | 0.24182 | 0.0010334 | 0.24182 | 0.0010334
2007/2008 | 2007-09-14 | 0.08185 | 0.0003617 | 0.08185 | 0.0003617
2007/2008 | 2007-09-15 | 0.0123 | 0.00010334 | 0.0123 | 0.00010334
2007/2008 | 2007-09-16 | 0.07627 | 0.00031003 | 0.07627 | 0.00031003
2007/2008 | 2007-09-17 | 0.18509 | 0.0021702 | 0.18509 | 0.0021702
2007/2008 | 2007-09-18 | 0.06149 | 0.00087842 | 0.06149 | 0.00087842
2007/2008 | 2007-09-19 | 0.00548 | 5.1672e-05 | 0.00548 | 5.1672e-05
2007/2008 | 2007-09-20 | 0.02222 | 0.00025836 | 0.02222 | 0.00025836
2007/2008 | 2007-09-22 | 0.08464 | 0.0013435 | 0.08464 | 0.0013435
2007/2008 | 2007-09-24 | 0.77894 | 0.003617 | 0.77894 | 0.003617
2007/2008 | 2007-09-25 | 0.51145 | 0.0018085 | 0.51145 | 0.0018085
2007/2008 | 2007-09-26 | 0.23966 | 0.00077507 | 0.23966 | 0.00077507
2007/2008 | 2007-09-27 | 0.80397 | 0.0059422 | 0.80397 | 0.0059422
2007/2008 | 2007-09-28 | 0.16096 | 0.00056839 | 0.16096 | 0.00056839
2007/2008 | 2007-09-30 | 0.31871 | 0.0025319 | 0.31871 | 0.0025319
2007/2008 | 2007-10-01 | 0.51094 | 0.0028936 | 0.51094 | 0.0028936
2007/2008 | 2007-10-02 | 0.38335 | 0.030228 | 0.38335 | 0.030228
2007/2008 | 2007-10-03 | 0.4081 | 0.016638 | 0.4081 | 0.016638
2007/2008 | 2007-10-04 | 0.18974 | 0.00093009 | 0.18974 | 0.00093009
2007/2008 | 2007-10-05 | 1.1298 | 0.0094042 | 1.1298 | 0.0094042
2007/2008 | 2007-10-08 | 0.30868 | 0.0022735 | 0.30868 | 0.0022735
2007/2008 | 2007-10-09 | 0.07213 | 0.00020669 | 0.07213 | 0.00020669
2007/2008 | 2007-10-10 | 0.10696 | 0.00093009 | 0.10696 | 0.00093009
2007/2008 | 2007-10-11 | 0.04563 | 0.00025836 | 0.04563 | 0.00025836
2007/2008 | 2007-10-12 | 0.58063 | 0.019842 | 0.58063 | 0.019842
2007/2008 | 2007-10-14 | 5.0254 | 0.01638 | 5.0254 | 0.01638
2007/2008 | 2007-10-15 | 1.437 | 0.01545 | 1.437 | 0.01545
2007/2008 | 2007-10-16 | 0.02956 | 0.00056839 | 0.02956 | 0.00056839
2007/2008 | 2007-10-17 | 1.2713 | 0.20968 | 1.2713 | 0.20968
2007/2008 | 2007-10-18 | 1.4757 | 0.0065106 | 1.4757 | 0.0065106
2007/2008 | 2007-10-21 | 1.5157 | 0.0082675 | 1.5157 | 0.0082675
2007/2008 | 2007-10-22 | 0.21361 | 0.0017052 | 0.21361 | 0.0017052
2007/2008 | 2007-10-23 | 0.07441 | 0.0016535 | 0.07441 | 0.0016535
2007/2008 | 2007-10-24 | 0.3324 | 0.013951 | 0.3324 | 0.013951
2007/2008 | 2007-10-25 | 0.03152 | 0.00010334 | 0.03152 | 0.00010334
2007/2008 | 2007-10-26 | 0.10846 | 0.0003617 | 0.10846 | 0.0003617
2007/2008 | 2007-10-27 | 0.02077 | 5.1672e-05 | 0.02077 | 5.1672e-05
2007/2008 | 2007-10-29 | 0.28311 | 0.0036687 | 0.28311 | 0.0036687
2007/2008 | 2007-10-30 | 0.23624 | 0.00098176 | 0.23624 | 0.00098176
2007/2008 | 2007-10-31 | 0.03953 | 0.00025836 | 0.03953 | 0.00025836
2007/2008 | 2007-11-01 | 2.0044 | 0.067483 | 2.0044 | 0.067483
2007/2008 | 2007-11-02 | 0.68273 | 0.0031003 | 0.68273 | 0.0031003
2007/2008 | 2007-11-05 | 0.67705 | 0.003927 | 0.67705 | 0.003927
2007/2008 | 2007-11-06 | 5.7985 | 0.022942 | 5.7985 | 0.022942
2007/2008 | 2007-11-07 | 0.47657 | 0.0021185 | 0.47657 | 0.0021185
2007/2008 | 2007-11-08 | 0.24658 | 0.002997 | 0.24658 | 0.002997
2007/2008 | 2007-11-09 | 0.09915 | 0.0019635 | 0.09915 | 0.0019635
2007/2008 | 2007-11-11 | 0.30553 | 0.0013951 | 0.30553 | 0.0013951
2007/2008 | 2007-11-12 | 0.21806 | 0.0021185 | 0.21806 | 0.0021185
2007/2008 | 2007-11-13 | 0.39322 | 0.025836 | 0.39322 | 0.025836
2007/2008 | 2007-11-14 | 2.1305 | 0.024699 | 2.1305 | 0.024699
2007/2008 | 2007-11-15 | 0.63659 | 0.0032553 | 0.63659 | 0.0032553
2007/2008 | 2007-11-16 | 0.78159 | 0.0022735 | 0.78159 | 0.0022735
2007/2008 | 2007-11-17 | 0.1283 | 0.00067173 | 0.1283 | 0.00067173
2007/2008 | 2007-11-18 | 0.03162 | 0.00046504 | 0.03162 | 0.00046504
2007/2008 | 2007-11-19 | 0.69576 | 0.0045988 | 0.69576 | 0.0045988
2007/2008 | 2007-11-20 | 0.72304 | 0.0028419 | 0.72304 | 0.0028419
2007/2008 | 2007-11-21 | 0.42882 | 0.0010334 | 0.42882 | 0.0010334
2007/2008 | 2007-11-22 | 3.2542 | 0.010128 | 3.2542 | 0.010128
2007/2008 | 2007-11-23 | 0.31948 | 0.0027386 | 0.31948 | 0.0027386
2007/2008 | 2007-11-26 | 0.26936 | 0.0011884 | 0.26936 | 0.0011884
2007/2008 | 2007-11-27 | 0.03694 | 0.00025836 | 0.03694 | 0.00025836
2007/2008 | 2007-11-28 | 3.9956 | 0.0084225 | 3.9956 | 0.0084225
2007/2008 | 2007-11-29 | 0.26998 | 0.00056839 | 0.26998 | 0.00056839
2007/2008 | 2007-11-30 | 0.24043 | 0.0017052 | 0.24043 | 0.0017052
2007/2008 | 2007-12-01 | 0.05364 | 0.00015501 | 0.05364 | 0.00015501
2007/2008 | 2007-12-03 | 0.07591 | 0.0010851 | 0.07591 | 0.0010851
2007/2008 | 2007-12-04 | 0.88798 | 0.0028936 | 0.88798 | 0.0028936
2007/2008 | 2007-12-05 | 0.01333 | 0.00010334 | 0.01333 | 0.00010334
2007/2008 | 2007-12-06 | 2.0205 | 0.032811 | 2.0205 | 0.032811
2007/2008 | 2007-12-07 | 0.93894 | 0.039787 | 0.93894 | 0.039787
2007/2008 | 2007-12-08 | 0.28812 | 0.0056839 | 0.28812 | 0.0056839
2007/2008 | 2007-12-09 | 0.86457 | 0.0044438 | 0.86457 | 0.0044438
2007/2008 | 2007-12-10 | 0.5826 | 0.017723 | 0.5826 | 0.017723
2007/2008 | 2007-12-11 | 3.1423 | 0.01545 | 3.1423 | 0.01545
2007/2008 | 2007-12-12 | 0.10283 | 0.00025836 | 0.10283 | 0.00025836
2007/2008 | 2007-12-13 | 0.30966 | 0.0021702 | 0.30966 | 0.0021702
2007/2008 | 2007-12-14 | 4.6874 | 0.016225 | 4.6874 | 0.016225
2007/2008 | 2007-12-16 | 0.3245 | 0.0020669 | 0.3245 | 0.0020669
2007/2008 | 2007-12-17 | 0.90927 | 0.0025319 | 0.90927 | 0.0025319
2007/2008 | 2007-12-18 | 0.6722 | 0.0048571 | 0.6722 | 0.0048571
2007/2008 | 2007-12-19 | 0.20716 | 0.0011884 | 0.20716 | 0.0011884
2007/2008 | 2007-12-20 | 1.599 | 0.01266 | 1.599 | 0.01266
2007/2008 | 2007-12-23 | 0.18519 | 0.026456 | 0.18519 | 0.026456
2007/2008 | 2007-12-24 | 0.00346 | 5.1672e-05 | 0.00346 | 5.1672e-05
2007/2008 | 2007-12-26 | 2.6683 | 0.024647 | 2.6683 | 0.024647
2007/2008 | 2007-12-27 | 0.33426 | 0.0016018 | 0.33426 | 0.0016018
2007/2008 | 2007-12-28 | 0.01659 | 0.00025836 | 0.01659 | 0.00025836
2007/2008 | 2007-12-30 | 0.06557 | 0.0013951 | 0.06557 | 0.0013951
2007/2008 | 2007-12-31 | 0.03617 | 0.00051672 | 0.03617 | 0.00051672
2007/2008 | 2008-01-03 | 0.01158 | 0.00015501 | 0.01158 | 0.00015501
2007/2008 | 2008-01-04 | 0.18958 | 0.00077507 | 0.18958 | 0.00077507
2007/2008 | 2008-01-05 | 0.01984 | 0.00015501 | 0.01984 | 0.00015501
2007/2008 | 2008-01-07 | 0.02362 | 0.00015501 | 0.02362 | 0.00015501
2007/2008 | 2008-01-08 | 1.2739 | 0.0041854 | 1.2739 | 0.0041854
2007/2008 | 2008-01-09 | 0.00481 | 0.00015501 | 0.00481 | 0.00015501
2007/2008 | 2008-01-10 | 0.36976 | 0.0010851 | 0.36976 | 0.0010851
2007/2008 | 2008-01-11 | 0.04872 | 0.00015501 | 0.04872 | 0.00015501
2007/2008 | 2008-01-13 | 0.26973 | 0.0012401 | 0.26973 | 0.0012401
2007/2008 | 2008-01-14 | 0.19201 | 0.0019635 | 0.19201 | 0.0019635
2007/2008 | 2008-01-15 | 2.19 | 0.0074407 | 2.19 | 0.0074407
2007/2008 | 2008-01-16 | 2.0194 | 0.010334 | 2.0194 | 0.010334
2007/2008 | 2008-01-17 | 0.75957 | 0.0033587 | 0.75957 | 0.0033587
2007/2008 | 2008-01-18 | 0.43884 | 0.026456 | 0.43884 | 0.026456
2007/2008 | 2008-01-19 | 0.32843 | 0.0029453 | 0.32843 | 0.0029453
2007/2008 | 2008-01-20 | 5.4069 | 0.051465 | 5.4069 | 0.051465
2007/2008 | 2008-01-21 | 2.4363 | 0.010644 | 2.4363 | 0.010644
2007/2008 | 2008-01-22 | 4.6069 | 0.05565 | 4.6069 | 0.05565
2007/2008 | 2008-01-23 | 3.0621 | 0.08903 | 3.0621 | 0.08903
2007/2008 | 2008-01-24 | 4.1884 | 0.040149 | 4.1884 | 0.040149
2007/2008 | 2008-01-25 | 0.00599 | 0.00010334 | 0.00599 | 0.00010334
2007/2008 | 2008-01-26 | 0.11797 | 0.00067173 | 0.11797 | 0.00067173
2007/2008 | 2008-01-27 | 2.002 | 0.086808 | 2.002 | 0.086808
2007/2008 | 2008-01-28 | 1.7357 | 0.089857 | 1.7357 | 0.089857
2007/2008 | 2008-01-29 | 0.20457 | 0.00087842 | 0.20457 | 0.00087842
2007/2008 | 2008-01-30 | 1.6844 | 0.0046504 | 1.6844 | 0.0046504
2007/2008 | 2008-01-31 | 1.5946 | 0.0048571 | 1.5946 | 0.0048571
2007/2008 | 2008-02-01 | 2.3702 | 0.010438 | 2.3702 | 0.010438
2007/2008 | 2008-02-02 | 0.23397 | 0.0078541 | 0.23397 | 0.0078541
2007/2008 | 2008-02-04 | 0.62275 | 0.0053738 | 0.62275 | 0.0053738
2007/2008 | 2008-02-05 | 0.13813 | 0.0018085 | 0.13813 | 0.0018085
2007/2008 | 2008-02-06 | 0.09379 | 0.012608 | 0.09379 | 0.012608
2007/2008 | 2008-02-07 | 0.62729 | 0.0047538 | 0.62729 | 0.0047538
2007/2008 | 2008-02-08 | 0.55934 | 0.0064589 | 0.55934 | 0.0064589
2007/2008 | 2008-02-09 | 0.05208 | 0.00041337 | 0.05208 | 0.00041337
2007/2008 | 2008-02-10 | 4.7472 | 0.028109 | 4.7472 | 0.028109
2007/2008 | 2008-02-11 | 0.47125 | 0.0022219 | 0.47125 | 0.0022219
2007/2008 | 2008-02-12 | 1.2123 | 0.0093009 | 1.2123 | 0.0093009
2007/2008 | 2008-02-13 | 3.293 | 0.013641 | 3.293 | 0.013641
2007/2008 | 2008-02-14 | 0.19972 | 0.0042371 | 0.19972 | 0.0042371
2007/2008 | 2008-02-15 | 0.7742 | 0.0083708 | 0.7742 | 0.0083708
2007/2008 | 2008-02-16 | 0.11744 | 0.00098176 | 0.11744 | 0.00098176
2007/2008 | 2008-02-17 | 0.11507 | 0.00098176 | 0.11507 | 0.00098176
2007/2008 | 2008-02-18 | 0.45409 | 0.0038754 | 0.45409 | 0.0038754
2007/2008 | 2008-02-19 | 2.2809 | 0.0056839 | 2.2809 | 0.0056839
2007/2008 | 2008-02-20 | 0.0371 | 0.00041337 | 0.0371 | 0.00041337
2007/2008 | 2008-02-21 | 1.3535 | 0.0054255 | 1.3535 | 0.0054255
2007/2008 | 2008-02-22 | 1.6614 | 0.034362 | 1.6614 | 0.034362
2007/2008 | 2008-02-23 | 0.57489 | 0.0010334 | 0.57489 | 0.0010334
2007/2008 | 2008-02-24 | 3.2037 | 0.033638 | 3.2037 | 0.033638
2007/2008 | 2008-02-25 | 0.051 | 0.00031003 | 0.051 | 0.00031003
2007/2008 | 2008-02-26 | 1.0115 | 0.026559 | 1.0115 | 0.026559
2007/2008 | 2008-02-27 | 0.40614 | 0.0031003 | 0.40614 | 0.0031003
2007/2008 | 2008-02-28 | 0.0929 | 0.0007234 | 0.0929 | 0.0007234
2007/2008 | 2008-02-29 | 3.2906 | 0.014881 | 3.2906 | 0.014881
2007/2008 | 2008-03-01 | 5.3436 | 0.057355 | 5.3436 | 0.057355
2007/2008 | 2008-03-02 | 0.25499 | 0.0018602 | 0.25499 | 0.0018602
2007/2008 | 2008-03-03 | 0.34381 | 0.0053738 | 0.34381 | 0.0053738
2007/2008 | 2008-03-04 | 0.11208 | 0.0010851 | 0.11208 | 0.0010851
2007/2008 | 2008-03-05 | 1.9681 | 0.0075441 | 1.9681 | 0.0075441
2007/2008 | 2008-03-06 | 1.8348 | 0.0046504 | 1.8348 | 0.0046504
2007/2008 | 2008-03-07 | 0.13134 | 0.0010851 | 0.13134 | 0.0010851
2007/2008 | 2008-03-08 | 0.22321 | 0.0014985 | 0.22321 | 0.0014985
2007/2008 | 2008-03-10 | 0.08489 | 0.0007234 | 0.08489 | 0.0007234
2007/2008 | 2008-03-11 | 0.05462 | 0.00062006 | 0.05462 | 0.00062006
2007/2008 | 2008-03-12 | 0.24353 | 0.0024802 | 0.24353 | 0.0024802
2007/2008 | 2008-03-13 | 0.53476 | 0.0047021 | 0.53476 | 0.0047021
2007/2008 | 2008-03-14 | 0.39022 | 0.0026353 | 0.39022 | 0.0026353
2007/2008 | 2008-03-15 | 0.18539 | 0.00082675 | 0.18539 | 0.00082675
2007/2008 | 2008-03-16 | 0.28285 | 0.00098176 | 0.28285 | 0.00098176
2007/2008 | 2008-03-17 | 0.00186 | 0.00020669 | 0.00186 | 0.00020669
2007/2008 | 2008-03-18 | 0.56286 | 0.0041337 | 0.56286 | 0.0041337
2007/2008 | 2008-03-19 | 0.15434 | 0.0007234 | 0.15434 | 0.0007234
2007/2008 | 2008-03-20 | 0.01396 | 0.00020669 | 0.01396 | 0.00020669
2007/2008 | 2008-03-21 | 0.045 | 0.00051672 | 0.045 | 0.00051672
2007/2008 | 2008-03-23 | 1.1049 | 0.012556 | 1.1049 | 0.012556
2007/2008 | 2008-03-25 | 0.03389 | 0.00082675 | 0.03389 | 0.00082675
2007/2008 | 2008-03-26 | 1.0813 | 0.0032036 | 1.0813 | 0.0032036
2007/2008 | 2008-03-27 | 2.7011 | 0.0077507 | 2.7011 | 0.0077507
2007/2008 | 2008-03-28 | 0.67534 | 0.0020669 | 0.67534 | 0.0020669
2007/2008 | 2008-03-29 | 0.02775 | 0.00031003 | 0.02775 | 0.00031003
2007/2008 | 2008-03-31 | 1.5087 | 0.0068723 | 1.5087 | 0.0068723
2008/2009 | 2008-04-01 | 1.2243 | 0.003617 | 1.2243 | 0.003617
2008/2009 | 2008-04-02 | 2.2901 | 0.0083708 | 2.2901 | 0.0083708
2008/2009 | 2008-04-03 | 0.04991 | 0.00015501 | 0.04991 | 0.00015501
2008/2009 | 2008-04-04 | 0.48277 | 0.0045988 | 0.48277 | 0.0045988
2008/2009 | 2008-04-07 | 0.04495 | 0.00031003 | 0.04495 | 0.00031003
2008/2009 | 2008-04-08 | 0.12174 | 0.0007234 | 0.12174 | 0.0007234
2008/2009 | 2008-04-09 | 0.01477 | 0.00015501 | 0.01477 | 0.00015501
2008/2009 | 2008-04-10 | 0.09621 | 0.0023769 | 0.09621 | 0.0023769
2008/2009 | 2008-04-11 | 0.24849 | 0.0017568 | 0.24849 | 0.0017568
2008/2009 | 2008-04-14 | 0.37312 | 0.0076474 | 0.37312 | 0.0076474
2008/2009 | 2008-04-15 | 1.1911 | 0.0087842 | 1.1911 | 0.0087842
2008/2009 | 2008-04-16 | 0.04614 | 0.00098176 | 0.04614 | 0.00098176
2008/2009 | 2008-04-17 | 0.25241 | 0.0017052 | 0.25241 | 0.0017052
2008/2009 | 2008-04-18 | 1.2611 | 0.084896 | 1.2611 | 0.084896
2008/2009 | 2008-04-19 | 0.85305 | 0.0045988 | 0.85305 | 0.0045988
2008/2009 | 2008-04-20 | 0.59918 | 0.0065623 | 0.59918 | 0.0065623
2008/2009 | 2008-04-21 | 0.2485 | 0.0012401 | 0.2485 | 0.0012401
2008/2009 | 2008-04-22 | 8.4747 | 0.070118 | 8.4747 | 0.070118
2008/2009 | 2008-04-23 | 2.4587 | 0.027593 | 2.4587 | 0.027593
2008/2009 | 2008-04-24 | 1.0929 | 0.030228 | 1.0929 | 0.030228
2008/2009 | 2008-04-25 | 1.3445 | 0.01545 | 1.3445 | 0.01545
2008/2009 | 2008-04-27 | 0.0525 | 0.00010334 | 0.0525 | 0.00010334
2008/2009 | 2008-04-28 | 1.4415 | 0.027334 | 1.4415 | 0.027334
2008/2009 | 2008-04-29 | 3.695 | 0.060197 | 3.695 | 0.060197
2008/2009 | 2008-04-30 | 5.0052 | 0.070222 | 5.0052 | 0.070222
2008/2009 | 2008-05-01 | 0.80897 | 0.0064073 | 0.80897 | 0.0064073
2008/2009 | 2008-05-02 | 1.2408 | 0.0091975 | 1.2408 | 0.0091975
2008/2009 | 2008-05-04 | 0.00537 | 0.00020669 | 0.00537 | 0.00020669
2008/2009 | 2008-05-05 | 1.1797 | 0.0069757 | 1.1797 | 0.0069757
2008/2009 | 2008-05-06 | 0.07254 | 0.0013951 | 0.07254 | 0.0013951
2008/2009 | 2008-05-07 | 1.1043 | 0.011833 | 1.1043 | 0.011833
2008/2009 | 2008-05-08 | 0.39456 | 0.0052705 | 0.39456 | 0.0052705
2008/2009 | 2008-05-09 | 0.67897 | 0.017672 | 0.67897 | 0.017672
2008/2009 | 2008-05-11 | 0.14768 | 0.00093009 | 0.14768 | 0.00093009
2008/2009 | 2008-05-12 | 0.22498 | 0.0012918 | 0.22498 | 0.0012918
2008/2009 | 2008-05-13 | 0.01457 | 0.00015501 | 0.01457 | 0.00015501
2008/2009 | 2008-05-14 | 0.10251 | 0.00077507 | 0.10251 | 0.00077507
2008/2009 | 2008-05-15 | 0.61319 | 0.0062006 | 0.61319 | 0.0062006
2008/2009 | 2008-05-16 | 0.17894 | 0.00062006 | 0.17894 | 0.00062006
2008/2009 | 2008-05-18 | 0.56829 | 0.0026869 | 0.56829 | 0.0026869
2008/2009 | 2008-05-19 | 0.43073 | 0.0063039 | 0.43073 | 0.0063039
2008/2009 | 2008-05-20 | 0.04258 | 0.00020669 | 0.04258 | 0.00020669
2008/2009 | 2008-05-21 | 0.36377 | 0.0077507 | 0.36377 | 0.0077507
2008/2009 | 2008-05-22 | 0.61902 | 0.0035653 | 0.61902 | 0.0035653
2008/2009 | 2008-05-23 | 0.61401 | 0.052498 | 0.61401 | 0.052498
2008/2009 | 2008-05-24 | 0.73151 | 0.081279 | 0.73151 | 0.081279
2008/2009 | 2008-05-26 | 0.55428 | 0.0076474 | 0.55428 | 0.0076474
2008/2009 | 2008-05-27 | 0.45341 | 0.0048055 | 0.45341 | 0.0048055
2008/2009 | 2008-05-28 | 0.15931 | 0.0010851 | 0.15931 | 0.0010851
2008/2009 | 2008-05-29 | 1.4801 | 0.024131 | 1.4801 | 0.024131
2008/2009 | 2008-05-30 | 0.53192 | 0.0044954 | 0.53192 | 0.0044954
2008/2009 | 2008-05-31 | 1.2386 | 0.12386 | 1.2386 | 0.12386
2008/2009 | 2008-06-01 | 0.10572 | 0.014468 | 0.10572 | 0.014468
2008/2009 | 2008-06-02 | 0.14081 | 0.0056322 | 0.14081 | 0.0056322
2008/2009 | 2008-06-03 | 0.9181 | 0.0043404 | 0.9181 | 0.0043404
2008/2009 | 2008-06-04 | 0.24798 | 0.0025319 | 0.24798 | 0.0025319
2008/2009 | 2008-06-05 | 0.55976 | 0.003617 | 0.55976 | 0.003617
2008/2009 | 2008-06-06 | 0.10768 | 0.00046504 | 0.10768 | 0.00046504
2008/2009 | 2008-06-07 | 0.32129 | 0.0092492 | 0.32129 | 0.0092492
2008/2009 | 2008-06-08 | 1.415 | 0.014985 | 1.415 | 0.014985
2008/2009 | 2008-06-09 | 0.71622 | 0.0052705 | 0.71622 | 0.0052705
2008/2009 | 2008-06-10 | 0.18984 | 0.0020152 | 0.18984 | 0.0020152
2008/2009 | 2008-06-11 | 0.04237 | 0.00025836 | 0.04237 | 0.00025836
2008/2009 | 2008-06-12 | 0.1886 | 0.0012918 | 0.1886 | 0.0012918
2008/2009 | 2008-06-13 | 0.15243 | 0.0010851 | 0.15243 | 0.0010851
2008/2009 | 2008-06-15 | 4.3838 | 0.05596 | 4.3838 | 0.05596
2008/2009 | 2008-06-16 | 0.36449 | 0.003152 | 0.36449 | 0.003152
2008/2009 | 2008-06-17 | 0.17533 | 0.0032036 | 0.17533 | 0.0032036
2008/2009 | 2008-06-18 | 0.1546 | 0.0013951 | 0.1546 | 0.0013951
2008/2009 | 2008-06-19 | 0.87532 | 0.007079 | 0.87532 | 0.007079
2008/2009 | 2008-06-20 | 0.27422 | 0.0012401 | 0.27422 | 0.0012401
2008/2009 | 2008-06-21 | 0.86906 | 0.0071823 | 0.86906 | 0.0071823
2008/2009 | 2008-06-22 | 0.16773 | 0.0024802 | 0.16773 | 0.0024802
2008/2009 | 2008-06-23 | 0.08071 | 0.01328 | 0.08071 | 0.01328
2008/2009 | 2008-06-24 | 0.83573 | 0.0026869 | 0.83573 | 0.0026869
2008/2009 | 2008-06-25 | 0.74536 | 0.0080091 | 0.74536 | 0.0080091
2008/2009 | 2008-06-26 | 1.3792 | 0.10262 | 1.3792 | 0.10262
2008/2009 | 2008-06-27 | 0.92615 | 0.01576 | 0.92615 | 0.01576
2008/2009 | 2008-06-28 | 0.16705 | 0.0026353 | 0.16705 | 0.0026353
2008/2009 | 2008-06-29 | 0.09596 | 0.0014468 | 0.09596 | 0.0014468
2008/2009 | 2008-06-30 | 0.07647 | 0.00025836 | 0.07647 | 0.00025836
2008/2009 | 2008-07-01 | 0.63251 | 0.0018602 | 0.63251 | 0.0018602
2008/2009 | 2008-07-02 | 0.21139 | 0.010903 | 0.21139 | 0.010903
2008/2009 | 2008-07-03 | 0.40155 | 0.12034 | 0.40155 | 0.12034
2008/2009 | 2008-07-04 | 2.3676 | 0.018292 | 2.3676 | 0.018292
2008/2009 | 2008-07-05 | 0.54404 | 0.0010851 | 0.54404 | 0.0010851
2008/2009 | 2008-07-06 | 5.4137 | 0.05565 | 5.4137 | 0.05565
2008/2009 | 2008-07-07 | 0.47849 | 0.0085775 | 0.47849 | 0.0085775
2008/2009 | 2008-07-08 | 0.59717 | 0.0054772 | 0.59717 | 0.0054772
2008/2009 | 2008-07-09 | 0.60543 | 0.0025836 | 0.60543 | 0.0025836
2008/2009 | 2008-07-10 | 0.32428 | 0.026818 | 0.32428 | 0.026818
2008/2009 | 2008-07-11 | 0.09756 | 0.0021702 | 0.09756 | 0.0021702
2008/2009 | 2008-07-12 | 10.9669 | 0.057665 | 10.9669 | 0.057665
2008/2009 | 2008-07-13 | 8.203 | 0.025009 | 8.203 | 0.025009
2008/2009 | 2008-07-14 | 0.00346 | 5.1672e-05 | 0.00346 | 5.1672e-05
2008/2009 | 2008-07-15 | 0.45057 | 0.0013951 | 0.45057 | 0.0013951
2008/2009 | 2008-07-16 | 0.0476 | 0.00041337 | 0.0476 | 0.00041337
2008/2009 | 2008-07-17 | 0.42506 | 0.0014468 | 0.42506 | 0.0014468
2008/2009 | 2008-07-18 | 0.04495 | 0.00025836 | 0.04495 | 0.00025836
2008/2009 | 2008-07-19 | 0.05022 | 0.00031003 | 0.05022 | 0.00031003
2008/2009 | 2008-07-21 | 0.13951 | 0.013021 | 0.13951 | 0.013021
2008/2009 | 2008-07-22 | 0.08852 | 0.00087842 | 0.08852 | 0.00087842
2008/2009 | 2008-07-23 | 0.40577 | 0.0042887 | 0.40577 | 0.0042887
2008/2009 | 2008-07-24 | 0.11523 | 0.00046504 | 0.11523 | 0.00046504
2008/2009 | 2008-07-25 | 0.83366 | 0.0092492 | 0.83366 | 0.0092492
2008/2009 | 2008-07-26 | 38.9216 | 0.23516 | 21.6659 | 0.23516
2008/2009 | 2008-07-27 | 2.1511 | 0.0087325 | 2.1511 | 0.0087325
2008/2009 | 2008-07-28 | 2.101 | 0.0081641 | 2.101 | 0.0081641
2008/2009 | 2008-07-29 | 0.33731 | 0.0042887 | 0.33731 | 0.0042887
2008/2009 | 2008-07-30 | 7.0823 | 0.20736 | 7.0823 | 0.20736
2008/2009 | 2008-07-31 | 15.0785 | 0.18726 | 15.0785 | 0.18726
2008/2009 | 2008-08-01 | 0.11395 | 0.0049118 | 0.11395 | 0.0049118
2008/2009 | 2008-08-02 | 6.8043 | 0.022693 | 6.8043 | 0.022693
2008/2009 | 2008-08-03 | 0.17427 | 0.029962 | 0.17427 | 0.029962
2008/2009 | 2008-08-04 | 0.01728 | 0.0060907 | 0.01728 | 0.0060907
2008/2009 | 2008-08-05 | 0.21568 | 0.019696 | 0.21568 | 0.019696
2008/2009 | 2008-08-06 | 0.02146 | 0.0079081 | 0.02146 | 0.0079081
2008/2009 | 2008-08-07 | 0.00511 | 0.0051083 | 0.00511 | 0.0051083
2008/2009 | 2008-08-08 | 0.08394 | 0.01115 | 0.08394 | 0.01115
2008/2009 | 2008-08-11 | 0.24147 | 0.041259 | 0.24147 | 0.041259
2008/2009 | 2008-08-12 | 0.06715 | 0.01282 | 0.06715 | 0.01282
2008/2009 | 2008-08-13 | 0.32904 | 0.024363 | 0.32904 | 0.024363
2008/2009 | 2008-08-14 | 1.4153 | 0.089592 | 1.4153 | 0.089592
2008/2009 | 2008-08-15 | 1.0481 | 0.18601 | 1.0481 | 0.18601
2008/2009 | 2008-08-16 | 1.9935 | 0.14377 | 1.9935 | 0.14377
2008/2009 | 2008-08-17 | 0.55867 | 0.16312 | 0.55867 | 0.16312
2008/2009 | 2008-08-18 | 0.34972 | 0.047104 | 0.34972 | 0.047104
2008/2009 | 2008-08-19 | 0.06429 | 0.019893 | 0.06429 | 0.019893
2008/2009 | 2008-08-20 | 0.39648 | 0.0053048 | 0.39648 | 0.0053048
2008/2009 | 2008-08-21 | 0.11794 | 0.00078589 | 0.11794 | 0.00078589
2008/2009 | 2008-08-22 | 0.45077 | 0.0015227 | 0.45077 | 0.0015227
2008/2009 | 2008-08-24 | 4.8167 | 0.086055 | 4.8167 | 0.086055
2008/2009 | 2008-08-25 | 0.02554 | 0.00024559 | 0.02554 | 0.00024559
2008/2009 | 2008-08-26 | 0.07048 | 0.00058942 | 0.07048 | 0.00058942
2008/2009 | 2008-08-27 | 0 | 0.022005 | 0 | 0.022005
2008/2009 | 2008-08-28 | 0.26052 | 0.0013262 | 0.26052 | 0.0013262
2008/2009 | 2008-08-29 | 0.14189 | 0.002505 | 0.14189 | 0.002505
2008/2009 | 2008-09-01 | 0.17663 | 0.00098237 | 0.17663 | 0.00098237
2008/2009 | 2008-09-02 | 1.1927 | 0.010757 | 1.1927 | 0.010757
2008/2009 | 2008-09-04 | 0.12182 | 0.00088413 | 0.12182 | 0.00088413
2008/2009 | 2008-09-05 | 0.00924 | 0.00019647 | 0.00924 | 0.00019647
2008/2009 | 2008-09-08 | 0.14597 | 0.0010315 | 0.14597 | 0.0010315
2008/2009 | 2008-09-09 | 3.4007 | 0.018812 | 3.4007 | 0.018812
2008/2009 | 2008-09-10 | 1.1366 | 0.0058942 | 1.1366 | 0.0058942
2008/2009 | 2008-09-11 | 0.38556 | 0.0020139 | 0.38556 | 0.0020139
2008/2009 | 2008-09-12 | 0.10335 | 0.0012771 | 0.10335 | 0.0012771
2008/2009 | 2008-09-13 | 0.02829 | 0.00039295 | 0.02829 | 0.00039295
2008/2009 | 2008-09-14 | 0.05216 | 0.00088413 | 0.05216 | 0.00088413
2008/2009 | 2008-09-15 | 0.1255 | 0.00073677 | 0.1255 | 0.00073677
2008/2009 | 2008-09-16 | 0.42438 | 0.0017683 | 0.42438 | 0.0017683
2008/2009 | 2008-09-17 | 2.2165 | 0.010167 | 2.2165 | 0.010167
2008/2009 | 2008-09-18 | 0.15423 | 0.0025542 | 0.15423 | 0.0025542
2008/2009 | 2008-09-19 | 0.03315 | 0.00034383 | 0.03315 | 0.00034383
2008/2009 | 2008-09-21 | 0.03875 | 0.00014735 | 0.03875 | 0.00014735
2008/2009 | 2008-09-22 | 0.33145 | 0.0013262 | 0.33145 | 0.0013262
2008/2009 | 2008-09-23 | 0.06823 | 0.0015227 | 0.06823 | 0.0015227
2008/2009 | 2008-09-24 | 0.16956 | 0.00034383 | 0.16956 | 0.00034383
2008/2009 | 2008-09-27 | 0.52341 | 0.0031436 | 0.52341 | 0.0031436
2008/2009 | 2008-09-29 | 0.69424 | 0.0018174 | 0.69424 | 0.0018174
2008/2009 | 2008-10-01 | 0.45406 | 0.0030989 | 0.45406 | 0.0030989
2008/2009 | 2008-10-02 | 0.31185 | 0.0013281 | 0.31185 | 0.0013281
2008/2009 | 2008-10-05 | 0.18401 | 0.0027545 | 0.18401 | 0.0027545
2008/2009 | 2008-10-06 | 0.85711 | 0.0064929 | 0.85711 | 0.0064929
2008/2009 | 2008-10-07 | 11.7909 | 0.096508 | 11.7909 | 0.096508
2008/2009 | 2008-10-08 | 0.07108 | 0.00024594 | 0.07108 | 0.00024594
2008/2009 | 2008-10-09 | 5.0739 | 0.026217 | 5.0739 | 0.026217
2008/2009 | 2008-10-10 | 0.05991 | 0.001033 | 0.05991 | 0.001033
2008/2009 | 2008-10-13 | 0.02361 | 0.00024594 | 0.02361 | 0.00024594
2008/2009 | 2008-10-14 | 0 | 0 | 0 | 0
2008/2009 | 2008-10-15 | 0.03045 | 0.00039351 | 0.03045 | 0.00039351
2008/2009 | 2008-10-16 | 0.04983 | 0.00063945 | 0.04983 | 0.00063945
2008/2009 | 2008-10-17 | 0.3664 | 0.0019183 | 0.3664 | 0.0019183
2008/2009 | 2008-10-18 | 0.47447 | 0.0030989 | 0.47447 | 0.0030989
2008/2009 | 2008-10-19 | 0.05243 | 0.0012789 | 0.05243 | 0.0012789
2008/2009 | 2008-10-20 | 0.21835 | 0.0015248 | 0.21835 | 0.0015248
2008/2009 | 2008-10-21 | 1.1219 | 0.0042302 | 1.1219 | 0.0042302
2008/2009 | 2008-10-22 | 0.24127 | 0.00073783 | 0.24127 | 0.00073783
2008/2009 | 2008-10-23 | 1.7226 | 0.023119 | 1.7226 | 0.023119
2008/2009 | 2008-10-24 | 0.02966 | 0.0032956 | 0.02966 | 0.0032956
2008/2009 | 2008-10-25 | 0.37757 | 0.0012297 | 0.37757 | 0.0012297
2008/2009 | 2008-10-26 | 0.58131 | 0.077127 | 0.58131 | 0.077127
2008/2009 | 2008-10-28 | 0 | 0 | 0 | 0
2008/2009 | 2008-10-29 | 0.30738 | 0.057403 | 0.30738 | 0.057403
2008/2009 | 2008-10-31 | 0.50019 | 0.0016724 | 0.50019 | 0.0016724
2008/2009 | 2008-11-02 | 0.05134 | 0.00082805 | 0.05134 | 0.00082805
2008/2009 | 2008-11-03 | 0.47932 | 0.0032294 | 0.47932 | 0.0032294
2008/2009 | 2008-11-04 | 0.00807 | 0.00012421 | 0.00807 | 0.00012421
2008/2009 | 2008-11-05 | 2.2109 | 0.024303 | 2.2109 | 0.024303
2008/2009 | 2008-11-06 | 0.27607 | 0.0010351 | 0.27607 | 0.0010351
2008/2009 | 2008-11-07 | 1.0036 | 0.047779 | 1.0036 | 0.047779
2008/2009 | 2008-11-10 | 0.02981 | 0.00016561 | 0.02981 | 0.00016561
2008/2009 | 2008-11-11 | 0.96759 | 0.0044301 | 0.96759 | 0.0044301
2008/2009 | 2008-11-12 | 0.84896 | 0.015443 | 0.84896 | 0.015443
2008/2009 | 2008-11-14 | 0.09265 | 0.00082805 | 0.09265 | 0.00082805
2008/2009 | 2008-11-17 | 2.5781 | 0.015278 | 2.5781 | 0.015278
2008/2009 | 2008-11-18 | 0.26779 | 0.0022357 | 0.26779 | 0.0022357
2008/2009 | 2008-11-19 | 0.04157 | 0.010392 | 0.04157 | 0.010392
2008/2009 | 2008-11-20 | 0.04819 | 0.024096 | 0.04819 | 0.024096
2008/2009 | 2008-11-21 | 2.5454 | 0.038587 | 2.5454 | 0.038587
2008/2009 | 2008-11-22 | 0.00062 | 4.1403e-05 | 0.00062 | 4.1403e-05
2008/2009 | 2008-11-23 | 0.31189 | 0.0033122 | 0.31189 | 0.0033122
2008/2009 | 2008-11-24 | 2.2125 | 0.013 | 2.2125 | 0.013
2008/2009 | 2008-11-25 | 0.24493 | 0.0019459 | 0.24493 | 0.0019459
2008/2009 | 2008-11-26 | 0.07444 | 0.00062104 | 0.07444 | 0.00062104
2008/2009 | 2008-11-27 | 1.1287 | 0.0049683 | 1.1287 | 0.0049683
2008/2009 | 2008-11-28 | 0.03929 | 0.00020701 | 0.03929 | 0.00020701
2008/2009 | 2008-11-29 | 0.07332 | 0.00045543 | 0.07332 | 0.00045543
2008/2009 | 2008-11-30 | 0.01325 | 8.2805e-05 | 0.01325 | 8.2805e-05
2008/2009 | 2008-12-01 | 0.12169 | 0.0016569 | 0.12169 | 0.0016569
2008/2009 | 2008-12-02 | 0.37677 | 0.0019054 | 0.37677 | 0.0019054
2008/2009 | 2008-12-03 | 0.48476 | 0.0084914 | 0.48476 | 0.0084914
2008/2009 | 2008-12-04 | 0.55401 | 0.0060476 | 0.55401 | 0.0060476
2008/2009 | 2008-12-05 | 1.2504 | 0.0040593 | 1.2504 | 0.0040593
2008/2009 | 2008-12-06 | 0.03757 | 0.00028995 | 0.03757 | 0.00028995
2008/2009 | 2008-12-07 | 0.02755 | 0.00020711 | 0.02755 | 0.00020711
2008/2009 | 2008-12-08 | 0.26344 | 0.012219 | 0.26344 | 0.012219
2008/2009 | 2008-12-09 | 0.00663 | 8.2843e-05 | 0.00663 | 8.2843e-05
2008/2009 | 2008-12-10 | 1.1989 | 0.0025681 | 1.1989 | 0.0025681
2008/2009 | 2008-12-11 | 0.12318 | 0.0027752 | 0.12318 | 0.0027752
2008/2009 | 2008-12-12 | 0.45854 | 0.0055919 | 0.45854 | 0.0055919
2008/2009 | 2008-12-13 | 0.40635 | 0.040635 | 0.40635 | 0.040635
2008/2009 | 2008-12-14 | 0.0087 | 0.00020711 | 0.0087 | 0.00020711
2008/2009 | 2008-12-15 | 1.2075 | 0.013793 | 1.2075 | 0.013793
2008/2009 | 2008-12-16 | 0.04946 | 0.0032309 | 0.04946 | 0.0032309
2008/2009 | 2008-12-17 | 0.89023 | 0.04283 | 0.89023 | 0.04283
2008/2009 | 2008-12-18 | 0.01649 | 0.0082429 | 0.01649 | 0.0082429
2008/2009 | 2008-12-19 | 0.02154 | 0.00033137 | 0.02154 | 0.00033137
2008/2009 | 2008-12-20 | 0.07477 | 0.006586 | 0.07477 | 0.006586
2008/2009 | 2008-12-21 | 0 | 0 | 0 | 0
2008/2009 | 2008-12-22 | 0.01503 | 0.00012426 | 0.01503 | 0.00012426
2008/2009 | 2008-12-23 | 0.18059 | 0.0022782 | 0.18059 | 0.0022782
2008/2009 | 2008-12-24 | 0 | 0 | 0 | 0
2008/2009 | 2008-12-25 | 0.01508 | 0.0005799 | 0.01508 | 0.0005799
2008/2009 | 2008-12-26 | 0.01044 | 0.00012426 | 0.01044 | 0.00012426
2008/2009 | 2008-12-28 | 0.36571 | 0.040635 | 0.36571 | 0.040635
2008/2009 | 2008-12-29 | 0.3677 | 0.001864 | 0.3677 | 0.001864
2008/2009 | 2008-12-31 | 0.01052 | 8.2843e-05 | 0.01052 | 8.2843e-05
2008/2009 | 2009-01-03 | 0.68493 | 0.0041386 | 0.68493 | 0.0041386
2008/2009 | 2009-01-05 | 0.00596 | 8.2771e-05 | 0.00596 | 8.2771e-05
2008/2009 | 2009-01-06 | 0.6414 | 0.0087324 | 0.6414 | 0.0087324
2008/2009 | 2009-01-08 | 1.382 | 0.055664 | 1.382 | 0.055664
2008/2009 | 2009-01-09 | 0.76295 | 0.0056698 | 0.76295 | 0.0056698
2008/2009 | 2009-01-10 | 0.0788 | 0.00070356 | 0.0788 | 0.00070356
2008/2009 | 2009-01-12 | 0.70604 | 0.012085 | 0.70604 | 0.012085
2008/2009 | 2009-01-13 | 0.90891 | 0.057526 | 0.90891 | 0.057526
2008/2009 | 2009-01-14 | 1.5325 | 0.0075322 | 1.5325 | 0.0075322
2008/2009 | 2009-01-15 | 0.10955 | 0.0023176 | 0.10955 | 0.0023176
2008/2009 | 2009-01-16 | 0.23093 | 0.0021107 | 0.23093 | 0.0021107
2008/2009 | 2009-01-17 | 2.652 | 0.011671 | 2.652 | 0.011671
2008/2009 | 2009-01-18 | 0.24633 | 0.0022762 | 0.24633 | 0.0022762
2008/2009 | 2009-01-19 | 0.27111 | 0.0044696 | 0.27111 | 0.0044696
2008/2009 | 2009-01-20 | 0.16658 | 0.0029798 | 0.16658 | 0.0029798
2008/2009 | 2009-01-21 | 0.29984 | 0.0014485 | 0.29984 | 0.0014485
2008/2009 | 2009-01-22 | 0.22485 | 0.0028142 | 0.22485 | 0.0028142
2008/2009 | 2009-01-23 | 0.09994 | 0.0026901 | 0.09994 | 0.0026901
2008/2009 | 2009-01-26 | 0.08766 | 0.0012416 | 0.08766 | 0.0012416
2008/2009 | 2009-01-27 | 0.5048 | 0.017837 | 0.5048 | 0.017837
2008/2009 | 2009-01-28 | 1.5423 | 0.0038902 | 1.5423 | 0.0038902
2008/2009 | 2009-01-29 | 0.17034 | 0.0021107 | 0.17034 | 0.0021107
2008/2009 | 2009-01-30 | 0.03501 | 0.00024831 | 0.03501 | 0.00024831
2008/2009 | 2009-02-01 | 0.02962 | 0.00099272 | 0.02962 | 0.00099272
2008/2009 | 2009-02-02 | 0.08335 | 0.000455 | 0.08335 | 0.000455
2008/2009 | 2009-02-03 | 0.04033 | 0.00012409 | 0.04033 | 0.00012409
2008/2009 | 2009-02-04 | 0.11317 | 0.0007859 | 0.11317 | 0.0007859
2008/2009 | 2009-02-05 | 0.70876 | 0.0062045 | 0.70876 | 0.0062045
2008/2009 | 2009-02-07 | 0.01762 | 0.00012409 | 0.01762 | 0.00012409
2008/2009 | 2009-02-08 | 0.545 | 0.0019854 | 0.545 | 0.0019854
2008/2009 | 2009-02-09 | 1.2947 | 0.0057495 | 1.2947 | 0.0057495
2008/2009 | 2009-02-10 | 1.0676 | 0.031643 | 1.0676 | 0.031643
2008/2009 | 2009-02-11 | 0.38033 | 0.0052945 | 0.38033 | 0.0052945
2008/2009 | 2009-02-12 | 3.9779 | 0.12512 | 3.9779 | 0.12512
2008/2009 | 2009-02-13 | 0.57052 | 0.0020682 | 0.57052 | 0.0020682
2008/2009 | 2009-02-14 | 0.39428 | 0.00086863 | 0.39428 | 0.00086863
2008/2009 | 2009-02-16 | 0.1494 | 0.0011582 | 0.1494 | 0.0011582
2008/2009 | 2009-02-17 | 0.20872 | 0.024032 | 0.20872 | 0.024032
2008/2009 | 2009-02-18 | 0.53007 | 0.013526 | 0.53007 | 0.013526
2008/2009 | 2009-02-19 | 0.01291 | 0.00020682 | 0.01291 | 0.00020682
2008/2009 | 2009-02-20 | 1.0831 | 0.071517 | 1.0831 | 0.071517
2008/2009 | 2009-02-21 | 2.0873 | 0.020433 | 2.0873 | 0.020433
2008/2009 | 2009-02-23 | 1.5646 | 0.016132 | 1.5646 | 0.016132
2008/2009 | 2009-02-24 | 0.95193 | 0.030857 | 0.95193 | 0.030857
2008/2009 | 2009-02-25 | 0.1748 | 0.020764 | 0.1748 | 0.020764
2008/2009 | 2009-02-26 | 1.9903 | 0.02002 | 1.9903 | 0.02002
2008/2009 | 2009-02-27 | 0.86499 | 0.032429 | 0.86499 | 0.032429
2008/2009 | 2009-02-28 | 4.6982 | 0.028541 | 4.6982 | 0.028541
2008/2009 | 2009-03-01 | 1.0093 | 0.0043 | 1.0093 | 0.0043
2008/2009 | 2009-03-02 | 0.14496 | 0.020797 | 0.14496 | 0.020797
2008/2009 | 2009-03-04 | 2.2581 | 0.0301 | 2.2581 | 0.0301
2008/2009 | 2009-03-05 | 0.11255 | 0.020714 | 0.11255 | 0.020714
2008/2009 | 2009-03-06 | 0.03304 | 0.00020673 | 0.03304 | 0.00020673
2008/2009 | 2009-03-07 | 0.03841 | 0.0016538 | 0.03841 | 0.0016538
2008/2009 | 2009-03-09 | 0.95559 | 0.010915 | 0.95559 | 0.010915
2008/2009 | 2009-03-10 | 0.10886 | 0.020218 | 0.10886 | 0.020218
2008/2009 | 2009-03-11 | 0.6184 | 0.022823 | 0.6184 | 0.022823
2008/2009 | 2009-03-12 | 0.01373 | 8.2692e-05 | 0.01373 | 8.2692e-05
2008/2009 | 2009-03-13 | 0.20085 | 0.00037212 | 0.20085 | 0.00037212
2008/2009 | 2009-03-14 | 0.14752 | 0.00033077 | 0.14752 | 0.00033077
2008/2009 | 2009-03-15 | 0.06686 | 0.00045481 | 0.06686 | 0.00045481
2008/2009 | 2009-03-17 | 0.24808 | 0.00062019 | 0.24808 | 0.00062019
2008/2009 | 2009-03-18 | 0.14508 | 0.001199 | 0.14508 | 0.001199
2008/2009 | 2009-03-19 | 0.23469 | 0.0016952 | 0.23469 | 0.0016952
2008/2009 | 2009-03-20 | 0.14761 | 0.0028942 | 0.14761 | 0.0028942
2008/2009 | 2009-03-22 | 0.15294 | 0.0012817 | 0.15294 | 0.0012817
2008/2009 | 2009-03-23 | 0.75151 | 0.026089 | 0.75151 | 0.026089
2008/2009 | 2009-03-24 | 0.78661 | 0.02241 | 0.78661 | 0.02241
2008/2009 | 2009-03-25 | 0.45278 | 0.021128 | 0.45278 | 0.021128
2008/2009 | 2009-03-26 | 2.3371 | 0.098321 | 2.3371 | 0.098321
2008/2009 | 2009-03-27 | 0.45973 | 0.023071 | 0.45973 | 0.023071
2008/2009 | 2009-03-28 | 0.65914 | 0.065286 | 0.65914 | 0.065286
2008/2009 | 2009-03-30 | 0.00318 | 4.1346e-05 | 0.00318 | 4.1346e-05
2008/2009 | 2009-03-31 | 0.59522 | 0.021045 | 0.59522 | 0.021045

## (1c) 2005-09_boundaries
Data extracted from Basix : Reliability Report : Outage Ref 09 | [7 empty] | Calculated Boundary Values: | Boundary Values |  | Reliability Limits |  |  | Check > System Settings: | Boundary Values |  | Reliability Limits
Standard Deviation | beta | 1.7497 |  | 0.90063 |  |  | 1.7797 |  | BSAIDI | 21.6659 | SAIDILIMIT | 307.6921 |  |  | BSAIDI | 21.6659 | SAIDILIMIT | 307.6921
Nat Log Average | alpha | -1.2985 |  |  |  |  | -5.7677 |  | BSAIFI | 0.26757 | SAIFILIMIT | 4.1546 |  |  | BSAIFI | 0.26757 | SAIFILIMIT | 4.1546
Interrupted | SAIDI Value | SAIDI Nat Log | Customers Interrupted | Count Interrupted | Customers Total | SAIFI Value | SAIFI Nat Log | Year | Month | Month Year | SAIDI Norm | SAIFI Norm | AssessYear
2004-04-01 | 0.40531 | -0.9031 | 31 | 5 | 19353 | 0.0016018 | -6.4366 | 2004 | 4 | April-2004 | 0.40531 | 0.001602 | 2005
2004-04-02 | 1.2607 | 0.23169 | 106 | 3 | 19353 | 0.0054772 | -5.2072 | 2004 | 4 | April-2004 | 1.2607 | 0.005477 | 2005
2004-04-06 | 0.019377 | -3.9437 | 4 | 3 | 19353 | 0.00020669 | -8.4843 | 2004 | 4 | April-2004 | 0.019377 | 0.000207 | 2005
2004-04-07 | 0.046969 | -3.0583 | 9 | 2 | 19353 | 0.00046504 | -7.6734 | 2004 | 4 | April-2004 | 0.046969 | 0.000465 | 2005
2004-04-08 | 0.84581 | -0.16746 | 81 | 4 | 19353 | 0.0041854 | -5.4762 | 2004 | 4 | April-2004 | 0.84581 | 0.004185 | 2005
2004-04-11 | 0.040045 | -3.2177 | 155 | 1 | 19353 | 0.0080091 | -4.8272 | 2004 | 4 | April-2004 | 0.040045 | 0.008009 | 2005
2004-04-12 | 2.8074 | 1.0322 | 499 | 2 | 19353 | 0.025784 | -3.658 | 2004 | 4 | April-2004 | 2.8074 | 0.025784 | 2005
2004-04-13 | 0.11125 | -2.196 | 8 | 2 | 19353 | 0.00041337 | -7.7912 | 2004 | 4 | April-2004 | 0.11125 | 0.000413 | 2005
2004-04-14 | 0.61169 | -0.49153 | 37 | 3 | 19353 | 0.0019118 | -6.2597 | 2004 | 4 | April-2004 | 0.61169 | 0.001912 | 2005
2004-04-15 | 3.8205 | 1.3404 | 1014 | 4 | 19353 | 0.052395 | -2.9489 | 2004 | 4 | April-2004 | 3.8205 | 0.052395 | 2005
2004-04-16 | 0.13409 | -2.0093 | 16 | 6 | 19353 | 0.00082675 | -7.098 | 2004 | 4 | April-2004 | 0.13409 | 0.000827 | 2005
2004-04-17 | 0.14835 | -1.9082 | 410 | 2 | 19353 | 0.021185 | -3.8544 | 2004 | 4 | April-2004 | 0.14835 | 0.021185 | 2005
2004-04-19 | 0.21687 | -1.5285 | 15 | 3 | 19353 | 0.00077507 | -7.1626 | 2004 | 4 | April-2004 | 0.21687 | 0.000775 | 2005
2004-04-20 | 0.18018 | -1.7138 | 29 | 1 | 19353 | 0.0014985 | -6.5033 | 2004 | 4 | April-2004 | 0.18018 | 0.001498 | 2005
2004-04-21 | 0.13094 | -2.033 | 21 | 2 | 19353 | 0.0010851 | -6.8261 | 2004 | 4 | April-2004 | 0.13094 | 0.001085 | 2005
2004-04-22 | 1.2149 | 0.19466 | 113 | 3 | 19353 | 0.0058389 | -5.1432 | 2004 | 4 | April-2004 | 1.2149 | 0.005839 | 2005
2004-04-23 | 0.19687 | -1.6252 | 24 | 3 | 19353 | 0.0012401 | -6.6925 | 2004 | 4 | April-2004 | 0.19687 | 0.00124 | 2005
2004-04-24 | 8.6439 | 2.1569 | 1840 | 1 | 19353 | 0.095076 | -2.3531 | 2004 | 4 | April-2004 | 8.6439 | 0.095076 | 2005
2004-04-25 | 0.3803 | -0.96679 | 1840 | 1 | 19353 | 0.095076 | -2.3531 | 2004 | 4 | April-2004 | 0.3803 | 0.095076 | 2005
2004-04-26 | 4.2985 | 1.4583 | 332 | 2 | 19353 | 0.017155 | -4.0655 | 2004 | 4 | April-2004 | 4.2985 | 0.017155 | 2005
2004-04-27 | 0.048623 | -3.0237 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2004 | 4 | April-2004 | 0.048623 | 0.000517 | 2005
2004-04-28 | 0.011419 | -4.4724 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2004 | 4 | April-2004 | 0.011419 | 0.000207 | 2005
2004-04-29 | 0.16587 | -1.7966 | 17 | 4 | 19353 | 0.00087842 | -7.0374 | 2004 | 4 | April-2004 | 0.16587 | 0.000878 | 2005
2004-04-30 | 1.3065 | 0.26736 | 137 | 3 | 19353 | 0.007079 | -4.9506 | 2004 | 4 | April-2004 | 1.3065 | 0.007079 | 2005
2004-05-01 | 0.95851 | -0.042378 | 206 | 1 | 19353 | 0.010644 | -4.5427 | 2004 | 5 | May-2004 | 0.95851 | 0.010644 | 2005
2004-05-03 | 0.13584 | -1.9962 | 31 | 2 | 19353 | 0.0016018 | -6.4366 | 2004 | 5 | May-2004 | 0.13584 | 0.001602 | 2005
2004-05-04 | 0.61184 | -0.49128 | 51 | 5 | 19353 | 0.0026353 | -5.9388 | 2004 | 5 | May-2004 | 0.61184 | 0.002635 | 2005
2004-05-05 | 0.4127 | -0.88503 | 32 | 3 | 19353 | 0.0016535 | -6.4049 | 2004 | 5 | May-2004 | 0.4127 | 0.001653 | 2005
2004-05-06 | 0.18421 | -1.6917 | 171 | 2 | 19353 | 0.0088358 | -4.7289 | 2004 | 5 | May-2004 | 0.18421 | 0.008836 | 2005
2004-05-07 | 0.14525 | -1.9293 | 31 | 2 | 19353 | 0.0016018 | -6.4366 | 2004 | 5 | May-2004 | 0.14525 | 0.001602 | 2005
2004-05-08 | 0.0099726 | -4.6079 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2004 | 5 | May-2004 | 0.009973 | 0.000207 | 2005
2004-05-10 | 0.14018 | -1.9648 | 29 | 1 | 19353 | 0.0014985 | -6.5033 | 2004 | 5 | May-2004 | 0.14019 | 0.001498 | 2005
2004-05-11 | 0.59686 | -0.51608 | 55 | 9 | 19353 | 0.0028419 | -5.8633 | 2004 | 5 | May-2004 | 0.59686 | 0.002842 | 2005
2004-05-12 | 0.25066 | -1.3837 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2004 | 5 | May-2004 | 0.25066 | 0.000362 | 2005
2004-05-13 | 0.58296 | -0.53964 | 149 | 6 | 19353 | 0.0076991 | -4.8667 | 2004 | 5 | May-2004 | 0.58296 | 0.007699 | 2005
2004-05-14 | 0.62848 | -0.46445 | 155 | 7 | 19353 | 0.0080091 | -4.8272 | 2004 | 5 | May-2004 | 0.62848 | 0.008009 | 2005
2004-05-16 | 0.9583 | -0.042593 | 248 | 1 | 19353 | 0.012815 | -4.3572 | 2004 | 5 | May-2004 | 0.9583 | 0.012815 | 2005
2004-05-17 | 0.12701 | -2.0635 | 61 | 3 | 19353 | 0.003152 | -5.7597 | 2004 | 5 | May-2004 | 0.12701 | 0.003152 | 2005
2004-05-18 | 0.1995 | -1.6119 | 26 | 3 | 19353 | 0.0013435 | -6.6125 | 2004 | 5 | May-2004 | 0.1995 | 0.001343 | 2005
2004-05-19 | 0.08593 | -2.4542 | 258 | 4 | 19353 | 0.013331 | -4.3176 | 2004 | 5 | May-2004 | 0.08593 | 0.013331 | 2005
2004-05-20 | 0.055495 | -2.8915 | 27 | 2 | 19353 | 0.0013951 | -6.5748 | 2004 | 5 | May-2004 | 0.055495 | 0.001395 | 2005
2004-05-21 | 0.14385 | -1.939 | 19 | 2 | 19353 | 0.00098176 | -6.9262 | 2004 | 5 | May-2004 | 0.14385 | 0.000982 | 2005
2004-05-22 | 0.17031 | -1.7701 | 16 | 1 | 19353 | 0.00082675 | -7.098 | 2004 | 5 | May-2004 | 0.17031 | 0.000827 | 2005
2004-05-23 | 0.18142 | -1.7069 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2004 | 5 | May-2004 | 0.18142 | 0.001447 | 2005
2004-05-24 | 2.7312 | 1.0047 | 326 | 3 | 19353 | 0.016845 | -4.0837 | 2004 | 5 | May-2004 | 2.7312 | 0.016845 | 2005
2004-05-25 | 0.16199 | -1.8202 | 104 | 4 | 19353 | 0.0053738 | -5.2262 | 2004 | 5 | May-2004 | 0.16199 | 0.005374 | 2005
2004-05-26 | 0.29205 | -1.2308 | 23 | 3 | 19353 | 0.0011884 | -6.7351 | 2004 | 5 | May-2004 | 0.29205 | 0.001188 | 2005
2004-05-27 | 0.59293 | -0.52268 | 27 | 1 | 19353 | 0.0013951 | -6.5748 | 2004 | 5 | May-2004 | 0.59293 | 0.001395 | 2005
2004-05-28 | 1.3119 | 0.27151 | 90 | 2 | 19353 | 0.0046504 | -5.3708 | 2004 | 5 | May-2004 | 1.3119 | 0.00465 | 2005
2004-05-30 | 0.29298 | -1.2277 | 15 | 1 | 19353 | 0.00077507 | -7.1626 | 2004 | 5 | May-2004 | 0.29298 | 0.000775 | 2005
2004-05-31 | 1.5915 | 0.46467 | 248 | 4 | 19353 | 0.012815 | -4.3572 | 2004 | 5 | May-2004 | 1.5915 | 0.012815 | 2005
2004-06-01 | 0.61835 | -0.48069 | 85 | 5 | 19353 | 0.0043921 | -5.428 | 2004 | 6 | June-2004 | 0.61835 | 0.004392 | 2005
2004-06-02 | 0.70434 | -0.3505 | 151 | 5 | 19353 | 0.0078024 | -4.8533 | 2004 | 6 | June-2004 | 0.70434 | 0.007802 | 2005
2004-06-03 | 1.4334 | 0.36006 | 164 | 5 | 19353 | 0.0084741 | -4.7707 | 2004 | 6 | June-2004 | 1.4334 | 0.008474 | 2005
2004-06-04 | 3.4207 | 1.2298 | 1632 | 4 | 19353 | 0.084328 | -2.473 | 2004 | 6 | June-2004 | 3.4207 | 0.084328 | 2005
2004-06-05 | 0.53992 | -0.61634 | 182 | 1 | 19353 | 0.0094042 | -4.6666 | 2004 | 6 | June-2004 | 0.53992 | 0.009404 | 2005
2004-06-06 | 10.1158 | 2.3141 | 2386 | 8 | 19353 | 0.12329 | -2.0932 | 2004 | 6 | June-2004 | 10.1158 | 0.12329 | 2005
2004-06-08 | 0.57102 | -0.56033 | 164 | 3 | 19353 | 0.0084741 | -4.7707 | 2004 | 6 | June-2004 | 0.57102 | 0.008474 | 2005
2004-06-09 | 0.15987 | -1.8334 | 29 | 1 | 19353 | 0.0014985 | -6.5033 | 2004 | 6 | June-2004 | 0.15987 | 0.001498 | 2005
2004-06-10 | 0.19062 | -1.6575 | 104 | 2 | 19353 | 0.0053738 | -5.2262 | 2004 | 6 | June-2004 | 0.19062 | 0.005374 | 2005
2004-06-11 | 0.060197 | -2.8101 | 14 | 1 | 19353 | 0.0007234 | -7.2315 | 2004 | 6 | June-2004 | 0.060197 | 0.000723 | 2005
2004-06-12 | 0.071927 | -2.6321 | 12 | 3 | 19353 | 0.00062006 | -7.3857 | 2004 | 6 | June-2004 | 0.071927 | 0.00062 | 2005
2004-06-14 | 0.078644 | -2.5428 | 85 | 2 | 19353 | 0.0043921 | -5.428 | 2004 | 6 | June-2004 | 0.078644 | 0.004392 | 2005
2004-06-15 | 0.62765 | -0.46577 | 1637 | 2 | 19353 | 0.084586 | -2.47 | 2004 | 6 | June-2004 | 0.62765 | 0.084586 | 2005
2004-06-16 | 1.7006 | 0.53099 | 452 | 2 | 19353 | 0.023356 | -3.7569 | 2004 | 6 | June-2004 | 1.7006 | 0.023356 | 2005
2004-06-17 | 0.0035653 | -5.6365 | 3 | 2 | 19353 | 0.00015501 | -8.772 | 2004 | 6 | June-2004 | 0.003565 | 0.000155 | 2005
2004-06-18 | 1.519 | 0.41805 | 239 | 1 | 19353 | 0.01235 | -4.3941 | 2004 | 6 | June-2004 | 1.519 | 0.01235 | 2005
2004-06-19 | 0.45502 | -0.78741 | 238 | 1 | 19353 | 0.012298 | -4.3983 | 2004 | 6 | June-2004 | 0.45502 | 0.012298 | 2005
2004-06-20 | 0.024596 | -3.7052 | 43 | 2 | 19353 | 0.0022219 | -6.1094 | 2004 | 6 | June-2004 | 0.024596 | 0.002222 | 2005
2004-06-21 | 0.073684 | -2.608 | 12 | 4 | 19353 | 0.00062006 | -7.3857 | 2004 | 6 | June-2004 | 0.073684 | 0.00062 | 2005
2004-06-22 | 4.3644 | 1.4735 | 3217 | 21 | 19353 | 0.16623 | -1.7944 | 2004 | 6 | June-2004 | 4.3644 | 0.16623 | 2005
2004-06-23 | 0.75596 | -0.27977 | 937 | 8 | 19353 | 0.048416 | -3.0279 | 2004 | 6 | June-2004 | 0.75596 | 0.048416 | 2005
2004-06-24 | 0.022891 | -3.777 | 3 | 3 | 19353 | 0.00015501 | -8.772 | 2004 | 6 | June-2004 | 0.022891 | 0.000155 | 2005
2004-06-25 | 0.096729 | -2.3358 | 248 | 1 | 19353 | 0.012815 | -4.3572 | 2004 | 6 | June-2004 | 0.096729 | 0.012815 | 2005
2004-06-27 | 0.85728 | -0.15399 | 248 | 1 | 19353 | 0.012815 | -4.3572 | 2004 | 6 | June-2004 | 0.85728 | 0.012815 | 2005
2004-06-28 | 0.026921 | -3.6149 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2004 | 6 | June-2004 | 0.026921 | 5.2e-05 | 2005
2004-06-29 | 0.30962 | -1.1724 | 44 | 3 | 19353 | 0.0022735 | -6.0864 | 2004 | 6 | June-2004 | 0.30962 | 0.002274 | 2005
2004-06-30 | 5.9968 | 1.7912 | 735 | 7 | 19353 | 0.037979 | -3.2707 | 2004 | 6 | June-2004 | 5.9968 | 0.037979 | 2005
2004-07-01 | 2.0705 | 0.72778 | 703 | 13 | 19353 | 0.036325 | -3.3152 | 2004 | 7 | July-2004 | 2.0705 | 0.036325 | 2005
2004-07-02 | 0.63639 | -0.45195 | 83 | 2 | 19353 | 0.0042887 | -5.4518 | 2004 | 7 | July-2004 | 0.63639 | 0.004289 | 2005
2004-07-03 | 0.45533 | -0.78673 | 130 | 2 | 19353 | 0.0067173 | -5.0031 | 2004 | 7 | July-2004 | 0.45533 | 0.006717 | 2005
2004-07-04 | 1.9532 | 0.66946 | 465 | 3 | 19353 | 0.024027 | -3.7286 | 2004 | 7 | July-2004 | 1.9532 | 0.024027 | 2005
2004-07-05 | 0.0035137 | -5.6511 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2004 | 7 | July-2004 | 0.003514 | 5.2e-05 | 2005
2004-07-06 | 0.82246 | -0.19546 | 443 | 4 | 19353 | 0.022891 | -3.777 | 2004 | 7 | July-2004 | 0.82246 | 0.022891 | 2005
2004-07-07 | 0.17796 | -1.7262 | 82 | 1 | 19353 | 0.0042371 | -5.4639 | 2004 | 7 | July-2004 | 0.17796 | 0.004237 | 2005
2004-07-08 | 1.2253 | 0.20318 | 190 | 5 | 19353 | 0.0098176 | -4.6236 | 2004 | 7 | July-2004 | 1.2253 | 0.009818 | 2005
2004-07-09 | 2.9858 | 1.0939 | 417 | 5 | 19353 | 0.021547 | -3.8375 | 2004 | 7 | July-2004 | 2.9858 | 0.021547 | 2005
2004-07-13 | 0.17558 | -1.7397 | 71 | 3 | 19353 | 0.0036687 | -5.6079 | 2004 | 7 | July-2004 | 0.17558 | 0.003669 | 2005
2004-07-14 | 0.23113 | -1.4648 | 34 | 3 | 19353 | 0.0017568 | -6.3442 | 2004 | 7 | July-2004 | 0.23113 | 0.001757 | 2005
2004-07-15 | 0.070532 | -2.6517 | 15 | 1 | 19353 | 0.00077507 | -7.1626 | 2004 | 7 | July-2004 | 0.070532 | 0.000775 | 2005
2004-07-16 | 0.10805 | -2.2252 | 17 | 1 | 19353 | 0.00087842 | -7.0374 | 2004 | 7 | July-2004 | 0.10805 | 0.000878 | 2005
2004-07-19 | 2.1671 | 0.77337 | 434 | 6 | 19353 | 0.022425 | -3.7976 | 2004 | 7 | July-2004 | 2.1671 | 0.022425 | 2005
2004-07-20 | 0.1668 | -1.791 | 38 | 3 | 19353 | 0.0019635 | -6.233 | 2004 | 7 | July-2004 | 0.1668 | 0.001964 | 2005
2004-07-21 | 0.22735 | -1.4812 | 40 | 1 | 19353 | 0.0020669 | -6.1817 | 2004 | 7 | July-2004 | 0.22736 | 0.002067 | 2005
2004-07-22 | 0.85599 | -0.1555 | 110 | 4 | 19353 | 0.0056839 | -5.1701 | 2004 | 7 | July-2004 | 0.85599 | 0.005684 | 2005
2004-07-23 | 5.2815 | 1.6642 | 444 | 3 | 19353 | 0.022942 | -3.7748 | 2004 | 7 | July-2004 | 5.2815 | 0.022942 | 2005
2004-07-25 | 0.21185 | -1.5519 | 410 | 1 | 19353 | 0.021185 | -3.8544 | 2004 | 7 | July-2004 | 0.21185 | 0.021185 | 2005
2004-07-26 | 0.36289 | -1.0137 | 80 | 4 | 19353 | 0.0041337 | -5.4886 | 2004 | 7 | July-2004 | 0.36289 | 0.004134 | 2005
2004-07-27 | 0.28667 | -1.2494 | 247 | 5 | 19353 | 0.012763 | -4.3612 | 2004 | 7 | July-2004 | 0.28667 | 0.012763 | 2005
2004-07-28 | 0.064434 | -2.7421 | 32 | 4 | 19353 | 0.0016535 | -6.4049 | 2004 | 7 | July-2004 | 0.064434 | 0.001653 | 2005
2004-07-29 | 0.4452 | -0.80923 | 376 | 4 | 19353 | 0.019429 | -3.941 | 2004 | 7 | July-2004 | 0.4452 | 0.019429 | 2005
2004-07-30 | 0.37834 | -0.97196 | 531 | 3 | 19353 | 0.027438 | -3.5958 | 2004 | 7 | July-2004 | 0.37834 | 0.027438 | 2005
2004-07-31 | 0.37219 | -0.98835 | 1029 | 2 | 19353 | 0.05317 | -2.9343 | 2004 | 7 | July-2004 | 0.37219 | 0.05317 | 2005
2004-08-02 | 1.6221 | 0.48374 | 1051 | 5 | 19353 | 0.054307 | -2.9131 | 2004 | 8 | August-2004 | 1.6221 | 0.054307 | 2005
2004-08-03 | 1.2991 | 0.26165 | 1373 | 5 | 19353 | 0.070945 | -2.6458 | 2004 | 8 | August-2004 | 1.2991 | 0.070945 | 2005
2004-08-05 | 0.1637 | -1.8097 | 18 | 1 | 19353 | 0.00093009 | -6.9802 | 2004 | 8 | August-2004 | 0.1637 | 0.00093 | 2005
2004-08-06 | 0.54911 | -0.59945 | 339 | 1 | 19353 | 0.017517 | -4.0446 | 2004 | 8 | August-2004 | 0.54911 | 0.017517 | 2005
2004-08-07 | 0.39715 | -0.92345 | 831 | 1 | 19353 | 0.042939 | -3.148 | 2004 | 8 | August-2004 | 0.39715 | 0.042939 | 2005
2004-08-08 | 0.024802 | -3.6968 | 240 | 1 | 19353 | 0.012401 | -4.39 | 2004 | 8 | August-2004 | 0.024802 | 0.012401 | 2005
2004-08-09 | 0.34883 | -1.0532 | 34 | 2 | 19353 | 0.0017568 | -6.3442 | 2004 | 8 | August-2004 | 0.34884 | 0.001757 | 2005
2004-08-10 | 0.13476 | -2.0043 | 36 | 4 | 19353 | 0.0018602 | -6.2871 | 2004 | 8 | August-2004 | 0.13476 | 0.00186 | 2005
2004-08-11 | 0.18731 | -1.675 | 38 | 5 | 19353 | 0.0019635 | -6.233 | 2004 | 8 | August-2004 | 0.18731 | 0.001964 | 2005
2004-08-12 | 24.1446 | 3.1841 | 640 | 3 | 19353 | 0.03307 | -3.4091 | 2004 | 8 | August-2004 | 21.6659 | 0.03307 | 2005
2004-08-15 | 0.079884 | -2.5272 | 773 | 1 | 19353 | 0.039942 | -3.2203 | 2004 | 8 | August-2004 | 0.079884 | 0.039942 | 2005
2004-08-16 | 3.2577 | 1.181 | 542 | 8 | 19353 | 0.028006 | -3.5753 | 2004 | 8 | August-2004 | 3.2577 | 0.028006 | 2005
2004-08-17 | 0.56198 | -0.57629 | 642 | 8 | 19353 | 0.033173 | -3.406 | 2004 | 8 | August-2004 | 0.56198 | 0.033173 | 2005
2004-08-18 | 3.6429 | 1.2928 | 434 | 11 | 19353 | 0.022425 | -3.7976 | 2004 | 8 | August-2004 | 3.6429 | 0.022425 | 2005
2004-08-19 | 1.655 | 0.50383 | 41 | 2 | 19353 | 0.0021185 | -6.157 | 2004 | 8 | August-2004 | 1.655 | 0.002119 | 2005
2004-08-20 | 0.033328 | -3.4014 | 28 | 1 | 19353 | 0.0014468 | -6.5384 | 2004 | 8 | August-2004 | 0.033328 | 0.001447 | 2005
2004-08-21 | 1.4375 | 0.36287 | 281 | 1 | 19353 | 0.01452 | -4.2322 | 2004 | 8 | August-2004 | 1.4375 | 0.01452 | 2005
2004-08-22 | 0.00062006 | -7.3857 | 2 | 2 | 19353 | 0.00010334 | -9.1775 | 2004 | 8 | August-2004 | 0.00062 | 0.000103 | 2005
2004-08-23 | 0.11719 | -2.1439 | 9 | 1 | 19353 | 0.00046504 | -7.6734 | 2004 | 8 | August-2004 | 0.11719 | 0.000465 | 2005
2004-08-24 | 0.23366 | -1.4539 | 23 | 2 | 19353 | 0.0011884 | -6.7351 | 2004 | 8 | August-2004 | 0.23366 | 0.001188 | 2005
2004-08-25 | 1.6097 | 0.47603 | 108 | 4 | 19353 | 0.0055805 | -5.1885 | 2004 | 8 | August-2004 | 1.6097 | 0.005581 | 2005
2004-08-26 | 0.0048571 | -5.3273 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2004 | 8 | August-2004 | 0.004857 | 0.000103 | 2005
2004-08-27 | 0.0095592 | -4.6502 | 3 | 2 | 19353 | 0.00015501 | -8.772 | 2004 | 8 | August-2004 | 0.009559 | 0.000155 | 2005
2004-08-28 | 0.34465 | -1.0652 | 97 | 1 | 19353 | 0.0050121 | -5.2959 | 2004 | 8 | August-2004 | 0.34465 | 0.005012 | 2005
2004-08-30 | 0.015295 | -4.1802 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2004 | 8 | August-2004 | 0.015295 | 0.000258 | 2005
2004-09-01 | 0.38351 | -0.9584 | 478 | 3 | 19353 | 0.024699 | -3.701 | 2004 | 9 | September-2004 | 0.38351 | 0.024699 | 2005
2004-09-02 | 0.20793 | -1.5706 | 258 | 1 | 19353 | 0.013331 | -4.3176 | 2004 | 9 | September-2004 | 0.20793 | 0.013331 | 2005
2004-09-03 | 0.097143 | -2.3316 | 20 | 1 | 19353 | 0.0010334 | -6.8749 | 2004 | 9 | September-2004 | 0.097143 | 0.001033 | 2005
2004-09-05 | 0.024802 | -3.6968 | 8 | 1 | 19353 | 0.00041337 | -7.7912 | 2004 | 9 | September-2004 | 0.024802 | 0.000413 | 2005
2004-09-06 | 1.6093 | 0.47577 | 87 | 2 | 19353 | 0.0044954 | -5.4047 | 2004 | 9 | September-2004 | 1.6093 | 0.004495 | 2005
2004-09-07 | 0.18901 | -1.6659 | 12 | 2 | 19353 | 0.00062006 | -7.3857 | 2004 | 9 | September-2004 | 0.18901 | 0.00062 | 2005
2004-09-08 | 0.19273 | -1.6464 | 36 | 4 | 19353 | 0.0018602 | -6.2871 | 2004 | 9 | September-2004 | 0.19273 | 0.00186 | 2005
2004-09-09 | 0.28326 | -1.2614 | 44 | 2 | 19353 | 0.0022735 | -6.0864 | 2004 | 9 | September-2004 | 0.28326 | 0.002274 | 2005
2004-09-10 | 0.65566 | -0.42211 | 68 | 2 | 19353 | 0.0035137 | -5.6511 | 2004 | 9 | September-2004 | 0.65566 | 0.003514 | 2005
2004-09-11 | 0.14447 | -1.9347 | 233 | 1 | 19353 | 0.012039 | -4.4196 | 2004 | 9 | September-2004 | 0.14447 | 0.012039 | 2005
2004-09-13 | 0.16938 | -1.7756 | 36 | 2 | 19353 | 0.0018602 | -6.2871 | 2004 | 9 | September-2004 | 0.16938 | 0.00186 | 2005
2004-09-14 | 0.17946 | -1.7178 | 21 | 3 | 19353 | 0.0010851 | -6.8261 | 2004 | 9 | September-2004 | 0.17946 | 0.001085 | 2005
2004-09-15 | 0.11559 | -2.1577 | 25 | 2 | 19353 | 0.0012918 | -6.6517 | 2004 | 9 | September-2004 | 0.11559 | 0.001292 | 2005
2004-09-16 | 0.22177 | -1.5061 | 24 | 4 | 19353 | 0.0012401 | -6.6925 | 2004 | 9 | September-2004 | 0.22177 | 0.00124 | 2005
2004-09-17 | 0.17413 | -1.7479 | 27 | 4 | 19353 | 0.0013951 | -6.5748 | 2004 | 9 | September-2004 | 0.17413 | 0.001395 | 2005
2004-09-18 | 1.894 | 0.6387 | 177 | 3 | 19353 | 0.0091459 | -4.6945 | 2004 | 9 | September-2004 | 1.894 | 0.009146 | 2005
2004-09-19 | 0.22792 | -1.4787 | 31 | 2 | 19353 | 0.0016018 | -6.4366 | 2004 | 9 | September-2004 | 0.22792 | 0.001602 | 2005
2004-09-20 | 0.12877 | -2.0498 | 31 | 3 | 19353 | 0.0016018 | -6.4366 | 2004 | 9 | September-2004 | 0.12877 | 0.001602 | 2005
2004-09-21 | 0.3108 | -1.1686 | 26 | 2 | 19353 | 0.0013435 | -6.6125 | 2004 | 9 | September-2004 | 0.3108 | 0.001343 | 2005
2004-09-22 | 5.5327 | 1.7107 | 583 | 9 | 19353 | 0.030125 | -3.5024 | 2004 | 9 | September-2004 | 5.5327 | 0.030125 | 2005
2004-09-23 | 0.1792 | -1.7193 | 23 | 3 | 19353 | 0.0011884 | -6.7351 | 2004 | 9 | September-2004 | 0.1792 | 0.001188 | 2005
2004-09-24 | 0.018602 | -3.9845 | 22 | 3 | 19353 | 0.0011368 | -6.7796 | 2004 | 9 | September-2004 | 0.018602 | 0.001137 | 2005
2004-09-25 | 0.97411 | -0.026228 | 1571 | 1 | 19353 | 0.081176 | -2.5111 | 2004 | 9 | September-2004 | 0.97411 | 0.081176 | 2005
2004-09-27 | 0.46225 | -0.77164 | 53 | 3 | 19353 | 0.0027386 | -5.9003 | 2004 | 9 | September-2004 | 0.46225 | 0.002739 | 2005
2004-09-28 | 3.5241 | 1.2596 | 493 | 6 | 19353 | 0.025474 | -3.6701 | 2004 | 9 | September-2004 | 3.5241 | 0.025474 | 2005
2004-09-29 | 0.50736 | -0.67853 | 40 | 3 | 19353 | 0.0020669 | -6.1817 | 2004 | 9 | September-2004 | 0.50736 | 0.002067 | 2005
2004-09-30 | 0.73875 | -0.3028 | 135 | 5 | 19353 | 0.0069757 | -4.9653 | 2004 | 9 | September-2004 | 0.73875 | 0.006976 | 2005
2004-10-01 | 0.019532 | -3.9357 | 6 | 4 | 19353 | 0.00031003 | -8.0788 | 2004 | 10 | October-2004 | 0.019532 | 0.00031 | 2005
2004-10-04 | 0.41337 | -0.88341 | 160 | 2 | 19353 | 0.0082675 | -4.7954 | 2004 | 10 | October-2004 | 0.41337 | 0.008267 | 2005
2004-10-05 | 0.44262 | -0.81505 | 85 | 2 | 19353 | 0.0043921 | -5.428 | 2004 | 10 | October-2004 | 0.44262 | 0.004392 | 2005
2004-10-06 | 0.35783 | -1.0277 | 93 | 4 | 19353 | 0.0048055 | -5.338 | 2004 | 10 | October-2004 | 0.35783 | 0.004805 | 2005
2004-10-07 | 0.20457 | -1.5869 | 39 | 3 | 19353 | 0.0020152 | -6.207 | 2004 | 10 | October-2004 | 0.20457 | 0.002015 | 2005
2004-10-08 | 0.72619 | -0.31994 | 256 | 6 | 19353 | 0.013228 | -4.3254 | 2004 | 10 | October-2004 | 0.72619 | 0.013228 | 2005
2004-10-11 | 0.22369 | -1.4975 | 13 | 1 | 19353 | 0.00067173 | -7.3057 | 2004 | 10 | October-2004 | 0.22369 | 0.000672 | 2005
2004-10-12 | 4.2352 | 1.4434 | 189 | 2 | 19353 | 0.0097659 | -4.6289 | 2004 | 10 | October-2004 | 4.2352 | 0.009766 | 2005
2004-10-13 | 0.026146 | -3.6441 | 15 | 4 | 19353 | 0.00077507 | -7.1626 | 2004 | 10 | October-2004 | 0.026146 | 0.000775 | 2005
2004-10-14 | 0.20121 | -1.6034 | 18 | 3 | 19353 | 0.00093009 | -6.9802 | 2004 | 10 | October-2004 | 0.20121 | 0.00093 | 2005
2004-10-15 | 0.19454 | -1.6371 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2004 | 10 | October-2004 | 0.19454 | 0.001447 | 2005
2004-10-17 | 0.025319 | -3.6762 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2004 | 10 | October-2004 | 0.025319 | 0.000103 | 2005
2004-10-18 | 0.78959 | -0.23624 | 341 | 3 | 19353 | 0.01762 | -4.0387 | 2004 | 10 | October-2004 | 0.78959 | 0.01762 | 2005
2004-10-19 | 0.080091 | -2.5246 | 45 | 2 | 19353 | 0.0023252 | -6.0639 | 2004 | 10 | October-2004 | 0.080091 | 0.002325 | 2005
2004-10-20 | 0.14422 | -1.9364 | 11 | 4 | 19353 | 0.00056839 | -7.4727 | 2004 | 10 | October-2004 | 0.14422 | 0.000568 | 2005
2004-10-21 | 0.11295 | -2.1808 | 16 | 3 | 19353 | 0.00082675 | -7.098 | 2004 | 10 | October-2004 | 0.11295 | 0.000827 | 2005
2004-10-22 | 0.93562 | -0.066549 | 59 | 2 | 19353 | 0.0030486 | -5.7931 | 2004 | 10 | October-2004 | 0.93562 | 0.003049 | 2005
2004-10-23 | 0.59396 | -0.52094 | 830 | 1 | 19353 | 0.042887 | -3.1492 | 2004 | 10 | October-2004 | 0.59396 | 0.042887 | 2005
2004-10-24 | 0.17207 | -1.7599 | 1110 | 1 | 19353 | 0.057355 | -2.8585 | 2004 | 10 | October-2004 | 0.17207 | 0.057355 | 2005
2004-10-26 | 0.24864 | -1.3917 | 16 | 2 | 19353 | 0.00082675 | -7.098 | 2004 | 10 | October-2004 | 0.24864 | 0.000827 | 2005
2004-10-27 | 1.2184 | 0.19755 | 1572 | 1 | 19353 | 0.081228 | -2.5105 | 2004 | 10 | October-2004 | 1.2184 | 0.081228 | 2005
2004-10-28 | 0.47631 | -0.74169 | 135 | 4 | 19353 | 0.0069757 | -4.9653 | 2004 | 10 | October-2004 | 0.47631 | 0.006976 | 2005
2004-10-29 | 0.23671 | -1.4409 | 32 | 3 | 19353 | 0.0016535 | -6.4049 | 2004 | 10 | October-2004 | 0.23671 | 0.001653 | 2005
2004-10-30 | 0.046504 | -3.0682 | 6 | 1 | 19353 | 0.00031003 | -8.0788 | 2004 | 10 | October-2004 | 0.046504 | 0.00031 | 2005
2004-11-01 | 0.60693 | -0.49933 | 173 | 5 | 19353 | 0.0089392 | -4.7173 | 2004 | 11 | November-2004 | 0.60693 | 0.008939 | 2005
2004-11-02 | 0.074097 | -2.6024 | 9 | 2 | 19353 | 0.00046504 | -7.6734 | 2004 | 11 | November-2004 | 0.074097 | 0.000465 | 2005
2004-11-03 | 1.4907 | 0.39923 | 197 | 5 | 19353 | 0.010179 | -4.5874 | 2004 | 11 | November-2004 | 1.4907 | 0.010179 | 2005
2004-11-04 | 0.18214 | -1.703 | 111 | 2 | 19353 | 0.0057355 | -5.1611 | 2004 | 11 | November-2004 | 0.18214 | 0.005736 | 2005
2004-11-05 | 0.3168 | -1.1495 | 20 | 3 | 19353 | 0.0010334 | -6.8749 | 2004 | 11 | November-2004 | 0.3168 | 0.001033 | 2005
2004-11-08 | 0.15217 | -1.8827 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2004 | 11 | November-2004 | 0.15217 | 0.000517 | 2005
2004-11-09 | 0.16752 | -1.7867 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2004 | 11 | November-2004 | 0.16752 | 0.000517 | 2005
2004-11-10 | 0.29468 | -1.2219 | 60 | 3 | 19353 | 0.0031003 | -5.7763 | 2004 | 11 | November-2004 | 0.29468 | 0.0031 | 2005
2004-11-11 | 0.53191 | -0.63129 | 80 | 4 | 19353 | 0.0041337 | -5.4886 | 2004 | 11 | November-2004 | 0.53191 | 0.004134 | 2005
2004-11-12 | 12.3726 | 2.5155 | 1165 | 5 | 19353 | 0.060197 | -2.8101 | 2004 | 11 | November-2004 | 12.3726 | 0.060197 | 2005
2004-11-14 | 9.062 | 2.2041 | 417 | 3 | 19353 | 0.021547 | -3.8375 | 2004 | 11 | November-2004 | 9.062 | 0.021547 | 2005
2004-11-15 | 1.8495 | 0.61493 | 151 | 7 | 19353 | 0.0078024 | -4.8533 | 2004 | 11 | November-2004 | 1.8495 | 0.007802 | 2005
2004-11-17 | 1.8004 | 0.58803 | 1126 | 3 | 19353 | 0.058182 | -2.8442 | 2004 | 11 | November-2004 | 1.8004 | 0.058182 | 2005
2004-11-18 | 0.58549 | -0.53531 | 984 | 2 | 19353 | 0.050845 | -2.979 | 2004 | 11 | November-2004 | 0.58549 | 0.050845 | 2005
2004-11-19 | 0.70981 | -0.34275 | 71 | 3 | 19353 | 0.0036687 | -5.6079 | 2004 | 11 | November-2004 | 0.70981 | 0.003669 | 2005
2004-11-20 | 0.20901 | -1.5654 | 42 | 1 | 19353 | 0.0021702 | -6.1329 | 2004 | 11 | November-2004 | 0.20901 | 0.00217 | 2005
2004-11-22 | 0.44303 | -0.81411 | 57 | 2 | 19353 | 0.0029453 | -5.8276 | 2004 | 11 | November-2004 | 0.44303 | 0.002945 | 2005
2004-11-23 | 0.2364 | -1.4422 | 52 | 2 | 19353 | 0.0026869 | -5.9194 | 2004 | 11 | November-2004 | 0.2364 | 0.002687 | 2005
2004-11-24 | 1.3418 | 0.29398 | 174 | 6 | 19353 | 0.0089909 | -4.7115 | 2004 | 11 | November-2004 | 1.3418 | 0.008991 | 2005
2004-11-25 | 0.40598 | -0.90144 | 53 | 3 | 19353 | 0.0027386 | -5.9003 | 2004 | 11 | November-2004 | 0.40598 | 0.002739 | 2005
2004-11-26 | 0.45249 | -0.79299 | 162 | 4 | 19353 | 0.0083708 | -4.783 | 2004 | 11 | November-2004 | 0.45249 | 0.008371 | 2005
2004-11-28 | 0.1918 | -1.6513 | 29 | 1 | 19353 | 0.0014985 | -6.5033 | 2004 | 11 | November-2004 | 0.19181 | 0.001498 | 2005
2004-11-29 | 0.12101 | -2.1118 | 14 | 2 | 19353 | 0.0007234 | -7.2315 | 2004 | 11 | November-2004 | 0.12101 | 0.000723 | 2005
2004-11-30 | 2.1909 | 0.7843 | 278 | 2 | 19353 | 0.014365 | -4.243 | 2004 | 11 | November-2004 | 2.1909 | 0.014365 | 2005
2004-12-02 | 0.58105 | -0.54292 | 35 | 2 | 19353 | 0.0018085 | -6.3153 | 2004 | 12 | December-2004 | 0.58105 | 0.001809 | 2005
2004-12-03 | 0.34289 | -1.0703 | 39 | 2 | 19353 | 0.0020152 | -6.207 | 2004 | 12 | December-2004 | 0.34289 | 0.002015 | 2005
2004-12-05 | 1.0748 | 0.072154 | 68 | 3 | 19353 | 0.0035137 | -5.6511 | 2004 | 12 | December-2004 | 1.0748 | 0.003514 | 2005
2004-12-06 | 0.0038237 | -5.5665 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2004 | 12 | December-2004 | 0.003824 | 5.2e-05 | 2005
2004-12-07 | 1.0239 | 0.023642 | 174 | 2 | 19353 | 0.0089909 | -4.7115 | 2004 | 12 | December-2004 | 1.0239 | 0.008991 | 2005
2004-12-09 | 10.3872 | 2.3406 | 632 | 3 | 19353 | 0.032656 | -3.4217 | 2004 | 12 | December-2004 | 10.3872 | 0.032656 | 2005
2004-12-10 | 0.87723 | -0.13099 | 510 | 4 | 19353 | 0.026353 | -3.6362 | 2004 | 12 | December-2004 | 0.87723 | 0.026353 | 2005
2004-12-11 | 0.025216 | -3.6803 | 241 | 2 | 19353 | 0.012453 | -4.3858 | 2004 | 12 | December-2004 | 0.025216 | 0.012453 | 2005
2004-12-12 | 0.055805 | -2.8859 | 18 | 1 | 19353 | 0.00093009 | -6.9802 | 2004 | 12 | December-2004 | 0.055805 | 0.00093 | 2005
2004-12-13 | 0.38852 | -0.94541 | 54 | 1 | 19353 | 0.0027903 | -5.8816 | 2004 | 12 | December-2004 | 0.38852 | 0.00279 | 2005
2004-12-14 | 0.44334 | -0.81341 | 30 | 1 | 19353 | 0.0015501 | -6.4694 | 2004 | 12 | December-2004 | 0.44334 | 0.00155 | 2005
2004-12-15 | 0.18777 | -1.6725 | 337 | 4 | 19353 | 0.017413 | -4.0505 | 2004 | 12 | December-2004 | 0.18777 | 0.017413 | 2005
2004-12-16 | 1.8753 | 0.62875 | 566 | 7 | 19353 | 0.029246 | -3.532 | 2004 | 12 | December-2004 | 1.8753 | 0.029246 | 2005
2004-12-17 | 0.49315 | -0.70693 | 98 | 4 | 19353 | 0.0050638 | -5.2856 | 2004 | 12 | December-2004 | 0.49315 | 0.005064 | 2005
2004-12-18 | 0.27463 | -1.2923 | 56 | 4 | 19353 | 0.0028936 | -5.8453 | 2004 | 12 | December-2004 | 0.27463 | 0.002894 | 2005
2004-12-19 | 0.66987 | -0.40067 | 780 | 3 | 19353 | 0.040304 | -3.2113 | 2004 | 12 | December-2004 | 0.66987 | 0.040304 | 2005
2004-12-20 | 1.0323 | 0.031834 | 149 | 2 | 19353 | 0.0076991 | -4.8667 | 2004 | 12 | December-2004 | 1.0323 | 0.007699 | 2005
2004-12-21 | 1.0264 | 0.026011 | 160 | 2 | 19353 | 0.0082675 | -4.7954 | 2004 | 12 | December-2004 | 1.0264 | 0.008267 | 2005
2004-12-22 | 2.6317 | 0.96764 | 487 | 4 | 19353 | 0.025164 | -3.6823 | 2004 | 12 | December-2004 | 2.6317 | 0.025164 | 2005
2004-12-23 | 0.13393 | -2.0104 | 32 | 1 | 19353 | 0.0016535 | -6.4049 | 2004 | 12 | December-2004 | 0.13393 | 0.001653 | 2005
2004-12-27 | 0.14055 | -1.9622 | 85 | 1 | 19353 | 0.0043921 | -5.428 | 2004 | 12 | December-2004 | 0.14055 | 0.004392 | 2005
2004-12-29 | 0.094766 | -2.3563 | 61 | 4 | 19353 | 0.003152 | -5.7597 | 2004 | 12 | December-2004 | 0.094766 | 0.003152 | 2005
2004-12-30 | 0.020565 | -3.8842 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2004 | 12 | December-2004 | 0.020565 | 0.000362 | 2005
2004-12-31 | 0.32243 | -1.1319 | 51 | 2 | 19353 | 0.0026353 | -5.9388 | 2004 | 12 | December-2004 | 0.32243 | 0.002635 | 2005
2005-01-03 | 0.023666 | -3.7437 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2005 | 1 | January-2005 | 0.023666 | 0.000103 | 2005
2005-01-05 | 0.35731 | -1.0292 | 52 | 3 | 19353 | 0.0026869 | -5.9194 | 2005 | 1 | January-2005 | 0.35731 | 0.002687 | 2005
2005-01-09 | 0.024544 | -3.7073 | 19 | 1 | 19353 | 0.00098176 | -6.9262 | 2005 | 1 | January-2005 | 0.024544 | 0.000982 | 2005
2005-01-10 | 1.0279 | 0.02752 | 187 | 2 | 19353 | 0.0096626 | -4.6395 | 2005 | 1 | January-2005 | 1.0279 | 0.009663 | 2005
2005-01-12 | 0.012401 | -4.39 | 6 | 3 | 19353 | 0.00031003 | -8.0788 | 2005 | 1 | January-2005 | 0.012401 | 0.00031 | 2005
2005-01-13 | 0.039322 | -3.236 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2005 | 1 | January-2005 | 0.039322 | 0.001447 | 2005
2005-01-17 | 0.071462 | -2.6386 | 7 | 3 | 19353 | 0.0003617 | -7.9247 | 2005 | 1 | January-2005 | 0.071462 | 0.000362 | 2005
2005-01-18 | 0.1978 | -1.6205 | 71 | 2 | 19353 | 0.0036687 | -5.6079 | 2005 | 1 | January-2005 | 0.1978 | 0.003669 | 2005
2005-01-19 | 0.19987 | -1.6101 | 17 | 2 | 19353 | 0.00087842 | -7.0374 | 2005 | 1 | January-2005 | 0.19987 | 0.000878 | 2005
2005-01-20 | 0.1098 | -2.2091 | 20 | 6 | 19353 | 0.0010334 | -6.8749 | 2005 | 1 | January-2005 | 0.1098 | 0.001033 | 2005
2005-01-21 | 0.065158 | -2.7309 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2005 | 1 | January-2005 | 0.065158 | 0.000362 | 2005
2005-01-22 | 0.10572 | -2.247 | 232 | 2 | 19353 | 0.011988 | -4.4239 | 2005 | 1 | January-2005 | 0.10572 | 0.011988 | 2005
2005-01-24 | 0.17656 | -1.7341 | 21 | 3 | 19353 | 0.0010851 | -6.8261 | 2005 | 1 | January-2005 | 0.17656 | 0.001085 | 2005
2005-01-25 | 1.7609 | 0.5658 | 196 | 3 | 19353 | 0.010128 | -4.5925 | 2005 | 1 | January-2005 | 1.7609 | 0.010128 | 2005
2005-01-26 | 0.028213 | -3.568 | 5 | 1 | 19353 | 0.00025836 | -8.2612 | 2005 | 1 | January-2005 | 0.028213 | 0.000258 | 2005
2005-01-27 | 7.0818 | 1.9575 | 430 | 2 | 19353 | 0.022219 | -3.8068 | 2005 | 1 | January-2005 | 7.0818 | 0.022219 | 2005
2005-01-28 | 0.38997 | -0.9417 | 29 | 3 | 19353 | 0.0014985 | -6.5033 | 2005 | 1 | January-2005 | 0.38997 | 0.001498 | 2005
2005-02-01 | 0.074149 | -2.6017 | 11 | 4 | 19353 | 0.00056839 | -7.4727 | 2005 | 2 | February-2005 | 0.074149 | 0.000568 | 2005
2005-02-02 | 0.98615 | -0.013945 | 1575 | 3 | 19353 | 0.081383 | -2.5086 | 2005 | 2 | February-2005 | 0.98615 | 0.081383 | 2005
2005-02-03 | 8.7991 | 2.1746 | 671 | 11 | 19353 | 0.034672 | -3.3618 | 2005 | 2 | February-2005 | 8.7991 | 0.034672 | 2005
2005-02-04 | 1.8052 | 0.5907 | 333 | 7 | 19353 | 0.017207 | -4.0625 | 2005 | 2 | February-2005 | 1.8053 | 0.017207 | 2005
2005-02-07 | 1.5221 | 0.42012 | 241 | 5 | 19353 | 0.012453 | -4.3858 | 2005 | 2 | February-2005 | 1.5221 | 0.012453 | 2005
2005-02-08 | 1.3776 | 0.32035 | 117 | 7 | 19353 | 0.0060456 | -5.1084 | 2005 | 2 | February-2005 | 1.3776 | 0.006046 | 2005
2005-02-09 | 0.91423 | -0.089678 | 295 | 6 | 19353 | 0.015243 | -4.1836 | 2005 | 2 | February-2005 | 0.91422 | 0.015243 | 2005
2005-02-10 | 1.0884 | 0.084671 | 394 | 3 | 19353 | 0.020359 | -3.8943 | 2005 | 2 | February-2005 | 1.0884 | 0.020359 | 2005
2005-02-11 | 1.0307 | 0.030231 | 327 | 1 | 19353 | 0.016897 | -4.0806 | 2005 | 2 | February-2005 | 1.0307 | 0.016897 | 2005
2005-02-13 | 1.08 | 0.076997 | 292 | 2 | 19353 | 0.015088 | -4.1938 | 2005 | 2 | February-2005 | 1.08 | 0.015088 | 2005
2005-02-14 | 1.8561 | 0.61847 | 327 | 3 | 19353 | 0.016897 | -4.0806 | 2005 | 2 | February-2005 | 1.8561 | 0.016897 | 2005
2005-02-15 | 1.6476 | 0.49932 | 152 | 6 | 19353 | 0.0078541 | -4.8467 | 2005 | 2 | February-2005 | 1.6476 | 0.007854 | 2005
2005-02-16 | 0.377 | -0.97552 | 20 | 3 | 19353 | 0.0010334 | -6.8749 | 2005 | 2 | February-2005 | 0.377 | 0.001033 | 2005
2005-02-17 | 0.15956 | -1.8353 | 74 | 3 | 19353 | 0.0038237 | -5.5665 | 2005 | 2 | February-2005 | 0.15956 | 0.003824 | 2005
2005-02-18 | 1.3314 | 0.28625 | 257 | 5 | 19353 | 0.01328 | -4.3215 | 2005 | 2 | February-2005 | 1.3314 | 0.01328 | 2005
2005-02-21 | 0.68506 | -0.37825 | 301 | 3 | 19353 | 0.015553 | -4.1635 | 2005 | 2 | February-2005 | 0.68506 | 0.015553 | 2005
2005-02-22 | 0.35219 | -1.0436 | 26 | 3 | 19353 | 0.0013435 | -6.6125 | 2005 | 2 | February-2005 | 0.35219 | 0.001343 | 2005
2005-02-23 | 0.0139 | -4.2759 | 3 | 3 | 19353 | 0.00015501 | -8.772 | 2005 | 2 | February-2005 | 0.0139 | 0.000155 | 2005
2005-02-24 | 0.11693 | -2.1462 | 11 | 2 | 19353 | 0.00056839 | -7.4727 | 2005 | 2 | February-2005 | 0.11693 | 0.000568 | 2005
2005-02-25 | 0.085258 | -2.4621 | 20 | 2 | 19353 | 0.0010334 | -6.8749 | 2005 | 2 | February-2005 | 0.085258 | 0.001033 | 2005
2005-02-26 | 0.028523 | -3.5571 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2005 | 2 | February-2005 | 0.028523 | 0.000155 | 2005
2005-02-28 | 0.18411 | -1.6922 | 119 | 4 | 19353 | 0.0061489 | -5.0915 | 2005 | 2 | February-2005 | 0.18411 | 0.006149 | 2005
2005-03-01 | 0.48566 | -0.72224 | 34 | 3 | 19353 | 0.0017568 | -6.3442 | 2005 | 3 | March-2005 | 0.48566 | 0.001757 | 2005
2005-03-02 | 5.541 | 1.7122 | 383 | 2 | 19353 | 0.01979 | -3.9226 | 2005 | 3 | March-2005 | 5.541 | 0.01979 | 2005
2005-03-03 | 0.05038 | -2.9882 | 47 | 4 | 19353 | 0.0024286 | -6.0205 | 2005 | 3 | March-2005 | 0.05038 | 0.002429 | 2005
2005-03-04 | 0.11915 | -2.1273 | 39 | 3 | 19353 | 0.0020152 | -6.207 | 2005 | 3 | March-2005 | 0.11915 | 0.002015 | 2005
2005-03-06 | 0.21888 | -1.5192 | 1412 | 1 | 19353 | 0.07296 | -2.6178 | 2005 | 3 | March-2005 | 0.21888 | 0.07296 | 2005
2005-03-07 | 1.3621 | 0.30904 | 523 | 4 | 19353 | 0.027024 | -3.611 | 2005 | 3 | March-2005 | 1.3621 | 0.027024 | 2005
2005-03-08 | 0.81362 | -0.20626 | 67 | 2 | 19353 | 0.003462 | -5.6659 | 2005 | 3 | March-2005 | 0.81362 | 0.003462 | 2005
2005-03-09 | 0.1763 | -1.7355 | 52 | 2 | 19353 | 0.0026869 | -5.9194 | 2005 | 3 | March-2005 | 0.1763 | 0.002687 | 2005
2005-03-10 | 0.64114 | -0.44451 | 125 | 4 | 19353 | 0.0064589 | -5.0423 | 2005 | 3 | March-2005 | 0.64114 | 0.006459 | 2005
2005-03-11 | 0.94466 | -0.05693 | 108 | 3 | 19353 | 0.0055805 | -5.1885 | 2005 | 3 | March-2005 | 0.94466 | 0.005581 | 2005
2005-03-12 | 0.59582 | -0.51781 | 1491 | 2 | 19353 | 0.077042 | -2.5634 | 2005 | 3 | March-2005 | 0.59583 | 0.077042 | 2005
2005-03-13 | 0.4142 | -0.88141 | 70 | 1 | 19353 | 0.003617 | -5.6221 | 2005 | 3 | March-2005 | 0.4142 | 0.003617 | 2005
2005-03-14 | 0.39761 | -0.92228 | 1454 | 4 | 19353 | 0.07513 | -2.5885 | 2005 | 3 | March-2005 | 0.39761 | 0.07513 | 2005
2005-03-15 | 0.034155 | -3.3768 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2005 | 3 | March-2005 | 0.034155 | 0.000258 | 2005
2005-03-16 | 1.7458 | 0.55723 | 181 | 3 | 19353 | 0.0093526 | -4.6721 | 2005 | 3 | March-2005 | 1.7458 | 0.009353 | 2005
2005-03-17 | 0.80845 | -0.21263 | 266 | 3 | 19353 | 0.013745 | -4.2871 | 2005 | 3 | March-2005 | 0.80845 | 0.013745 | 2005
2005-03-18 | 0.56312 | -0.57427 | 114 | 2 | 19353 | 0.0058906 | -5.1344 | 2005 | 3 | March-2005 | 0.56312 | 0.005891 | 2005
2005-03-20 | 0.53573 | -0.62412 | 32 | 1 | 19353 | 0.0016535 | -6.4049 | 2005 | 3 | March-2005 | 0.53573 | 0.001653 | 2005
2005-03-21 | 0.37756 | -0.97401 | 1588 | 4 | 19353 | 0.082054 | -2.5004 | 2005 | 3 | March-2005 | 0.37756 | 0.082054 | 2005
2005-03-22 | 1.3678 | 0.31324 | 87 | 3 | 19353 | 0.0044954 | -5.4047 | 2005 | 3 | March-2005 | 1.3679 | 0.004495 | 2005
2005-03-23 | 0.14938 | -1.9012 | 23 | 3 | 19353 | 0.0011884 | -6.7351 | 2005 | 3 | March-2005 | 0.14938 | 0.001188 | 2005
2005-03-24 | 0.56689 | -0.56759 | 424 | 2 | 19353 | 0.021909 | -3.8209 | 2005 | 3 | March-2005 | 0.56689 | 0.021909 | 2005
2005-03-26 | 2.3413 | 0.85072 | 576 | 4 | 19353 | 0.029763 | -3.5145 | 2005 | 3 | March-2005 | 2.3413 | 0.029763 | 2005
2005-03-28 | 0.045471 | -3.0907 | 11 | 1 | 19353 | 0.00056839 | -7.4727 | 2005 | 3 | March-2005 | 0.045471 | 0.000568 | 2005
2005-03-29 | 0.12691 | -2.0643 | 108 | 2 | 19353 | 0.0055805 | -5.1885 | 2005 | 3 | March-2005 | 0.1269 | 0.005581 | 2005
2005-03-30 | 0.25629 | -1.3614 | 50 | 3 | 19353 | 0.0025836 | -5.9586 | 2005 | 3 | March-2005 | 0.25629 | 0.002584 | 2005
2005-04-02 | 1.5022 | 0.40696 | 142 | 2 | 19353 | 0.0073374 | -4.9148 | 2005 | 4 | April-2005 | 1.5022 | 0.007337 | 2006
2005-04-03 | 0.025784 | -3.658 | 499 | 1 | 19353 | 0.025784 | -3.658 | 2005 | 4 | April-2005 | 0.025784 | 0.025784 | 2006
2005-04-04 | 0.34041 | -1.0776 | 49 | 1 | 19353 | 0.0025319 | -5.9788 | 2005 | 4 | April-2005 | 0.34041 | 0.002532 | 2006
2005-04-05 | 0.003152 | -5.7597 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 4 | April-2005 | 0.003152 | 5.2e-05 | 2006
2005-04-06 | 0.021702 | -3.8303 | 42 | 1 | 19353 | 0.0021702 | -6.1329 | 2005 | 4 | April-2005 | 0.021702 | 0.00217 | 2006
2005-04-07 | 0.15687 | -1.8523 | 12 | 1 | 19353 | 0.00062006 | -7.3857 | 2005 | 4 | April-2005 | 0.15687 | 0.00062 | 2006
2005-04-08 | 0.49119 | -0.71092 | 118 | 4 | 19353 | 0.0060972 | -5.0999 | 2005 | 4 | April-2005 | 0.49119 | 0.006097 | 2006
2005-04-09 | 0.31215 | -1.1643 | 7 | 1 | 19353 | 0.0003617 | -7.9247 | 2005 | 4 | April-2005 | 0.31215 | 0.000362 | 2006
2005-04-11 | 0.35514 | -1.0352 | 93 | 2 | 19353 | 0.0048055 | -5.338 | 2005 | 4 | April-2005 | 0.35514 | 0.004805 | 2006
2005-04-12 | 0.12122 | -2.1101 | 32 | 2 | 19353 | 0.0016535 | -6.4049 | 2005 | 4 | April-2005 | 0.12122 | 0.001653 | 2006
2005-04-13 | 0.11321 | -2.1785 | 19 | 3 | 19353 | 0.00098176 | -6.9262 | 2005 | 4 | April-2005 | 0.11321 | 0.000982 | 2006
2005-04-14 | 0.48365 | -0.7264 | 39 | 1 | 19353 | 0.0020152 | -6.207 | 2005 | 4 | April-2005 | 0.48365 | 0.002015 | 2006
2005-04-15 | 0.0065106 | -5.0343 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 4 | April-2005 | 0.006511 | 5.2e-05 | 2006
2005-04-16 | 0.6507 | -0.42971 | 1575 | 2 | 19353 | 0.081383 | -2.5086 | 2005 | 4 | April-2005 | 0.6507 | 0.081383 | 2006
2005-04-18 | 0.45099 | -0.79631 | 127 | 5 | 19353 | 0.0065623 | -5.0264 | 2005 | 4 | April-2005 | 0.45099 | 0.006562 | 2006
2005-04-19 | 0.93867 | -0.063296 | 202 | 2 | 19353 | 0.010438 | -4.5623 | 2005 | 4 | April-2005 | 0.93867 | 0.010438 | 2006
2005-04-20 | 0.0058906 | -5.1344 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2005 | 4 | April-2005 | 0.005891 | 0.000103 | 2006
2005-04-21 | 0.57206 | -0.55852 | 93 | 3 | 19353 | 0.0048055 | -5.338 | 2005 | 4 | April-2005 | 0.57206 | 0.004805 | 2006
2005-04-22 | 1.938 | 0.66168 | 313 | 3 | 19353 | 0.016173 | -4.1244 | 2005 | 4 | April-2005 | 1.938 | 0.016173 | 2006
2005-04-24 | 0.36506 | -1.0077 | 257 | 2 | 19353 | 0.01328 | -4.3215 | 2005 | 4 | April-2005 | 0.36506 | 0.01328 | 2006
2005-04-26 | 3.3659 | 1.2137 | 642 | 4 | 19353 | 0.033173 | -3.406 | 2005 | 4 | April-2005 | 3.3659 | 0.033173 | 2006
2005-04-27 | 0.76386 | -0.26937 | 179 | 3 | 19353 | 0.0092492 | -4.6832 | 2005 | 4 | April-2005 | 0.76386 | 0.009249 | 2006
2005-04-28 | 0.35514 | -1.0352 | 87 | 1 | 19353 | 0.0044954 | -5.4047 | 2005 | 4 | April-2005 | 0.35514 | 0.004495 | 2006
2005-04-29 | 0.066553 | -2.7098 | 12 | 2 | 19353 | 0.00062006 | -7.3857 | 2005 | 4 | April-2005 | 0.066553 | 0.00062 | 2006
2005-04-30 | 1.0851 | 0.081627 | 1012 | 1 | 19353 | 0.052292 | -2.9509 | 2005 | 4 | April-2005 | 1.0851 | 0.052292 | 2006
2005-05-01 | 0.48106 | -0.73176 | 81 | 1 | 19353 | 0.0041854 | -5.4762 | 2005 | 5 | May-2005 | 0.48106 | 0.004185 | 2006
2005-05-03 | 0.11791 | -2.1378 | 16 | 2 | 19353 | 0.00082675 | -7.098 | 2005 | 5 | May-2005 | 0.11792 | 0.000827 | 2006
2005-05-04 | 0.17424 | -1.7473 | 20 | 4 | 19353 | 0.0010334 | -6.8749 | 2005 | 5 | May-2005 | 0.17424 | 0.001033 | 2006
2005-05-05 | 3.3554 | 1.2106 | 1019 | 4 | 19353 | 0.052653 | -2.944 | 2005 | 5 | May-2005 | 3.3554 | 0.052653 | 2006
2005-05-06 | 0.67834 | -0.3881 | 144 | 1 | 19353 | 0.0074407 | -4.9008 | 2005 | 5 | May-2005 | 0.67834 | 0.007441 | 2006
2005-05-08 | 0.00046504 | -7.6734 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 5 | May-2005 | 0.000465 | 5.2e-05 | 2006
2005-05-09 | 1.4093 | 0.34312 | 1637 | 5 | 19353 | 0.084586 | -2.47 | 2005 | 5 | May-2005 | 1.4093 | 0.084586 | 2006
2005-05-10 | 0.014881 | -4.2076 | 6 | 2 | 19353 | 0.00031003 | -8.0788 | 2005 | 5 | May-2005 | 0.014881 | 0.00031 | 2006
2005-05-11 | 0.81331 | -0.20664 | 1574 | 1 | 19353 | 0.081331 | -2.5092 | 2005 | 5 | May-2005 | 0.81331 | 0.081331 | 2006
2005-05-12 | 0.036583 | -3.3082 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2005 | 5 | May-2005 | 0.036583 | 0.000517 | 2006
2005-05-13 | 0.1653 | -1.8 | 51 | 2 | 19353 | 0.0026353 | -5.9388 | 2005 | 5 | May-2005 | 0.1653 | 0.002635 | 2006
2005-05-16 | 0.57976 | -0.54515 | 115 | 4 | 19353 | 0.0059422 | -5.1257 | 2005 | 5 | May-2005 | 0.57976 | 0.005942 | 2006
2005-05-17 | 0.48706 | -0.71938 | 68 | 5 | 19353 | 0.0035137 | -5.6511 | 2005 | 5 | May-2005 | 0.48706 | 0.003514 | 2006
2005-05-18 | 0.075854 | -2.5789 | 338 | 2 | 19353 | 0.017465 | -4.0476 | 2005 | 5 | May-2005 | 0.075854 | 0.017465 | 2006
2005-05-19 | 0.62729 | -0.46634 | 83 | 6 | 19353 | 0.0042887 | -5.4518 | 2005 | 5 | May-2005 | 0.62729 | 0.004289 | 2006
2005-05-20 | 0.20229 | -1.598 | 50 | 1 | 19353 | 0.0025836 | -5.9586 | 2005 | 5 | May-2005 | 0.20229 | 0.002584 | 2006
2005-05-23 | 3.0995 | 1.1312 | 1108 | 5 | 19353 | 0.057252 | -2.8603 | 2005 | 5 | May-2005 | 3.0995 | 0.057252 | 2006
2005-05-24 | 0.23686 | -1.4403 | 24 | 1 | 19353 | 0.0012401 | -6.6925 | 2005 | 5 | May-2005 | 0.23686 | 0.00124 | 2006
2005-05-25 | 0.53113 | -0.63274 | 208 | 2 | 19353 | 0.010748 | -4.5331 | 2005 | 5 | May-2005 | 0.53113 | 0.010748 | 2006
2005-05-26 | 0.81264 | -0.20747 | 109 | 2 | 19353 | 0.0056322 | -5.1793 | 2005 | 5 | May-2005 | 0.81264 | 0.005632 | 2006
2005-05-27 | 0.026249 | -3.6401 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2005 | 5 | May-2005 | 0.026249 | 0.000207 | 2006
2005-05-28 | 0.011833 | -4.4369 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 5 | May-2005 | 0.011833 | 5.2e-05 | 2006
2005-05-29 | 0.96238 | -0.038343 | 106 | 1 | 19353 | 0.0054772 | -5.2072 | 2005 | 5 | May-2005 | 0.96238 | 0.005477 | 2006
2005-05-30 | 1.3544 | 0.30333 | 374 | 7 | 19353 | 0.019325 | -3.9463 | 2005 | 5 | May-2005 | 1.3544 | 0.019325 | 2006
2005-05-31 | 0.084793 | -2.4675 | 69 | 2 | 19353 | 0.0035653 | -5.6365 | 2005 | 5 | May-2005 | 0.084793 | 0.003565 | 2006
2005-06-01 | 0.81564 | -0.20379 | 76 | 5 | 19353 | 0.003927 | -5.5399 | 2005 | 6 | June-2005 | 0.81564 | 0.003927 | 2006
2005-06-02 | 0.58942 | -0.52862 | 215 | 2 | 19353 | 0.011109 | -4.5 | 2005 | 6 | June-2005 | 0.58942 | 0.011109 | 2006
2005-06-03 | 11.192 | 2.4152 | 2550 | 14 | 19353 | 0.13176 | -2.0268 | 2005 | 6 | June-2005 | 11.192 | 0.13176 | 2006
2005-06-04 | 0.027283 | -3.6015 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2005 | 6 | June-2005 | 0.027283 | 0.000103 | 2006
2005-06-05 | 0.024802 | -3.6968 | 240 | 1 | 19353 | 0.012401 | -4.39 | 2005 | 6 | June-2005 | 0.024802 | 0.012401 | 2006
2005-06-07 | 0.61458 | -0.48681 | 59 | 3 | 19353 | 0.0030486 | -5.7931 | 2005 | 6 | June-2005 | 0.61458 | 0.003049 | 2006
2005-06-08 | 0.028988 | -3.5409 | 17 | 2 | 19353 | 0.00087842 | -7.0374 | 2005 | 6 | June-2005 | 0.028988 | 0.000878 | 2006
2005-06-09 | 0.22219 | -1.5042 | 25 | 1 | 19353 | 0.0012918 | -6.6517 | 2005 | 6 | June-2005 | 0.22219 | 0.001292 | 2006
2005-06-10 | 0.53248 | -0.63022 | 212 | 7 | 19353 | 0.010954 | -4.514 | 2005 | 6 | June-2005 | 0.53248 | 0.010954 | 2006
2005-06-11 | 0.023046 | -3.7703 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2005 | 6 | June-2005 | 0.023046 | 0.000103 | 2006
2005-06-13 | 0.68718 | -0.37516 | 978 | 4 | 19353 | 0.050535 | -2.9851 | 2005 | 6 | June-2005 | 0.68718 | 0.050535 | 2006
2005-06-14 | 0.40511 | -0.90361 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2005 | 6 | June-2005 | 0.4051 | 0.001447 | 2006
2005-06-15 | 0.86111 | -0.14954 | 429 | 4 | 19353 | 0.022167 | -3.8091 | 2005 | 6 | June-2005 | 0.86111 | 0.022167 | 2006
2005-06-16 | 0.20338 | -1.5927 | 88 | 2 | 19353 | 0.0045471 | -5.3933 | 2005 | 6 | June-2005 | 0.20338 | 0.004547 | 2006
2005-06-17 | 1.2513 | 0.22417 | 288 | 2 | 19353 | 0.014881 | -4.2076 | 2005 | 6 | June-2005 | 1.2513 | 0.014881 | 2006
2005-06-19 | 0.039064 | -3.2426 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2005 | 6 | June-2005 | 0.039064 | 0.000207 | 2006
2005-06-20 | 0.053015 | -2.9372 | 6 | 3 | 19353 | 0.00031003 | -8.0788 | 2005 | 6 | June-2005 | 0.053015 | 0.00031 | 2006
2005-06-21 | 0.38449 | -0.95584 | 70 | 8 | 19353 | 0.003617 | -5.6221 | 2005 | 6 | June-2005 | 0.38449 | 0.003617 | 2006
2005-06-22 | 1.2948 | 0.25835 | 186 | 4 | 19353 | 0.0096109 | -4.6449 | 2005 | 6 | June-2005 | 1.2948 | 0.009611 | 2006
2005-06-23 | 0.21035 | -1.559 | 354 | 2 | 19353 | 0.018292 | -4.0013 | 2005 | 6 | June-2005 | 0.21035 | 0.018292 | 2006
2005-06-24 | 0.86865 | -0.14081 | 160 | 4 | 19353 | 0.0082675 | -4.7954 | 2005 | 6 | June-2005 | 0.86865 | 0.008267 | 2006
2005-06-26 | 0.03462 | -3.3633 | 10 | 1 | 19353 | 0.00051672 | -7.568 | 2005 | 6 | June-2005 | 0.03462 | 0.000517 | 2006
2005-06-27 | 3.0485 | 1.1147 | 1585 | 6 | 19353 | 0.081899 | -2.5023 | 2005 | 6 | June-2005 | 3.0485 | 0.081899 | 2006
2005-06-28 | 1.5916 | 0.46476 | 206 | 4 | 19353 | 0.010644 | -4.5427 | 2005 | 6 | June-2005 | 1.5916 | 0.010644 | 2006
2005-06-29 | 0.54131 | -0.61376 | 27 | 1 | 19353 | 0.0013951 | -6.5748 | 2005 | 6 | June-2005 | 0.54131 | 0.001395 | 2006
2005-06-30 | 0.31644 | -1.1506 | 56 | 2 | 19353 | 0.0028936 | -5.8453 | 2005 | 6 | June-2005 | 0.31644 | 0.002894 | 2006
2005-07-01 | 0.52891 | -0.63694 | 108 | 3 | 19353 | 0.0055805 | -5.1885 | 2005 | 7 | July-2005 | 0.52891 | 0.005581 | 2006
2005-07-02 | 5.2157 | 1.6517 | 263 | 1 | 19353 | 0.01359 | -4.2984 | 2005 | 7 | July-2005 | 5.2157 | 0.01359 | 2006
2005-07-04 | 0.14323 | -1.9433 | 12 | 1 | 19353 | 0.00062006 | -7.3857 | 2005 | 7 | July-2005 | 0.14323 | 0.00062 | 2006
2005-07-05 | 0.012039 | -4.4196 | 2 | 2 | 19353 | 0.00010334 | -9.1775 | 2005 | 7 | July-2005 | 0.012039 | 0.000103 | 2006
2005-07-06 | 0.96709 | -0.033469 | 141 | 5 | 19353 | 0.0072857 | -4.9218 | 2005 | 7 | July-2005 | 0.96708 | 0.007286 | 2006
2005-07-07 | 0.41559 | -0.87805 | 30 | 3 | 19353 | 0.0015501 | -6.4694 | 2005 | 7 | July-2005 | 0.41559 | 0.00155 | 2006
2005-07-08 | 2.7195 | 1.0005 | 599 | 4 | 19353 | 0.030951 | -3.4753 | 2005 | 7 | July-2005 | 2.7195 | 0.030951 | 2006
2005-07-11 | 0.12019 | -2.1187 | 22 | 3 | 19353 | 0.0011368 | -6.7796 | 2005 | 7 | July-2005 | 0.12019 | 0.001137 | 2006
2005-07-12 | 1.1539 | 0.14313 | 170 | 4 | 19353 | 0.0087842 | -4.7348 | 2005 | 7 | July-2005 | 1.1539 | 0.008784 | 2006
2005-07-13 | 0.11502 | -2.1626 | 24 | 2 | 19353 | 0.0012401 | -6.6925 | 2005 | 7 | July-2005 | 0.11502 | 0.00124 | 2006
2005-07-14 | 0.49667 | -0.69984 | 102 | 3 | 19353 | 0.0052705 | -5.2456 | 2005 | 7 | July-2005 | 0.49667 | 0.005271 | 2006
2005-07-15 | 1.0304 | 0.029981 | 250 | 2 | 19353 | 0.012918 | -4.3491 | 2005 | 7 | July-2005 | 1.0304 | 0.012918 | 2006
2005-07-17 | 0.2688 | -1.3138 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2005 | 7 | July-2005 | 0.2688 | 0.001447 | 2006
2005-07-18 | 0.63287 | -0.45748 | 37 | 2 | 19353 | 0.0019118 | -6.2597 | 2005 | 7 | July-2005 | 0.63287 | 0.001912 | 2006
2005-07-19 | 0.20317 | -1.5937 | 263 | 3 | 19353 | 0.01359 | -4.2984 | 2005 | 7 | July-2005 | 0.20317 | 0.01359 | 2006
2005-07-20 | 0.41761 | -0.87321 | 63 | 4 | 19353 | 0.0032553 | -5.7275 | 2005 | 7 | July-2005 | 0.41761 | 0.003255 | 2006
2005-07-21 | 0.73704 | -0.30511 | 48 | 4 | 19353 | 0.0024802 | -5.9994 | 2005 | 7 | July-2005 | 0.73704 | 0.00248 | 2006
2005-07-22 | 3.2774 | 1.187 | 2889 | 3 | 19353 | 0.14928 | -1.9019 | 2005 | 7 | July-2005 | 3.2774 | 0.14928 | 2006
2005-07-23 | 0.011988 | -4.4239 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 7 | July-2005 | 0.011988 | 5.2e-05 | 2006
2005-07-25 | 0.061489 | -2.7889 | 28 | 4 | 19353 | 0.0014468 | -6.5384 | 2005 | 7 | July-2005 | 0.061489 | 0.001447 | 2006
2005-07-26 | 1.0386 | 0.037872 | 160 | 3 | 19353 | 0.0082675 | -4.7954 | 2005 | 7 | July-2005 | 1.0386 | 0.008267 | 2006
2005-07-27 | 2.1211 | 0.75192 | 898 | 2 | 19353 | 0.046401 | -3.0704 | 2005 | 7 | July-2005 | 2.1211 | 0.046401 | 2006
2005-07-29 | 1.347 | 0.29786 | 199 | 3 | 19353 | 0.010283 | -4.5773 | 2005 | 7 | July-2005 | 1.347 | 0.010283 | 2006
2005-07-30 | 0.013435 | -4.3099 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2005 | 7 | July-2005 | 0.013435 | 0.000103 | 2006
2005-08-01 | 2.3917 | 0.87201 | 856 | 3 | 19353 | 0.044231 | -3.1183 | 2005 | 8 | August-2005 | 2.3917 | 0.044231 | 2006
2005-08-02 | 0.045161 | -3.0975 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2005 | 8 | August-2005 | 0.045161 | 0.000517 | 2006
2005-08-03 | 0.0067173 | -5.0031 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2005 | 8 | August-2005 | 0.006717 | 0.000103 | 2006
2005-08-04 | 0.027489 | -3.594 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2005 | 8 | August-2005 | 0.027489 | 0.000207 | 2006
2005-08-05 | 0.069292 | -2.6694 | 6 | 2 | 19353 | 0.00031003 | -8.0788 | 2005 | 8 | August-2005 | 0.069292 | 0.00031 | 2006
2005-08-06 | 0.14484 | -1.9322 | 14 | 2 | 19353 | 0.0007234 | -7.2315 | 2005 | 8 | August-2005 | 0.14483 | 0.000723 | 2006
2005-08-07 | 0.7853 | -0.24168 | 70 | 1 | 19353 | 0.003617 | -5.6221 | 2005 | 8 | August-2005 | 0.78531 | 0.003617 | 2006
2005-08-08 | 0.39219 | -0.93602 | 51 | 2 | 19353 | 0.0026353 | -5.9388 | 2005 | 8 | August-2005 | 0.39219 | 0.002635 | 2006
2005-08-10 | 0.51868 | -0.65647 | 239 | 1 | 19353 | 0.01235 | -4.3941 | 2005 | 8 | August-2005 | 0.51868 | 0.01235 | 2006
2005-08-11 | 0.055909 | -2.884 | 7 | 1 | 19353 | 0.0003617 | -7.9247 | 2005 | 8 | August-2005 | 0.055909 | 0.000362 | 2006
2005-08-12 | 0.79962 | -0.22362 | 286 | 3 | 19353 | 0.014778 | -4.2146 | 2005 | 8 | August-2005 | 0.79962 | 0.014778 | 2006
2005-08-13 | 0.083708 | -2.4804 | 6 | 1 | 19353 | 0.00031003 | -8.0788 | 2005 | 8 | August-2005 | 0.083708 | 0.00031 | 2006
2005-08-15 | 0.058699 | -2.8353 | 16 | 1 | 19353 | 0.00082675 | -7.098 | 2005 | 8 | August-2005 | 0.058699 | 0.000827 | 2006
2005-08-16 | 0.92084 | -0.08247 | 158 | 3 | 19353 | 0.0081641 | -4.808 | 2005 | 8 | August-2005 | 0.92084 | 0.008164 | 2006
2005-08-17 | 0.0055289 | -5.1978 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 8 | August-2005 | 0.005529 | 5.2e-05 | 2006
2005-08-18 | 0.43089 | -0.8419 | 59 | 5 | 19353 | 0.0030486 | -5.7931 | 2005 | 8 | August-2005 | 0.43089 | 0.003049 | 2006
2005-08-19 | 0.31096 | -1.1681 | 126 | 2 | 19353 | 0.0065106 | -5.0343 | 2005 | 8 | August-2005 | 0.31096 | 0.006511 | 2006
2005-08-21 | 0.0086808 | -4.7466 | 42 | 1 | 19353 | 0.0021702 | -6.1329 | 2005 | 8 | August-2005 | 0.008681 | 0.00217 | 2006
2005-08-22 | 0.06769 | -2.6928 | 7 | 4 | 19353 | 0.0003617 | -7.9247 | 2005 | 8 | August-2005 | 0.06769 | 0.000362 | 2006
2005-08-23 | 0.24265 | -1.4161 | 50 | 2 | 19353 | 0.0025836 | -5.9586 | 2005 | 8 | August-2005 | 0.24265 | 0.002584 | 2006
2005-08-24 | 0.022115 | -3.8115 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2005 | 8 | August-2005 | 0.022115 | 0.000207 | 2006
2005-08-25 | 0.68372 | -0.38021 | 162 | 3 | 19353 | 0.0083708 | -4.783 | 2005 | 8 | August-2005 | 0.68372 | 0.008371 | 2006
2005-08-27 | 0.21687 | -1.5285 | 70 | 1 | 19353 | 0.003617 | -5.6221 | 2005 | 8 | August-2005 | 0.21687 | 0.003617 | 2006
2005-08-28 | 0.15011 | -1.8964 | 20 | 1 | 19353 | 0.0010334 | -6.8749 | 2005 | 8 | August-2005 | 0.15011 | 0.001033 | 2006
2005-08-29 | 0.3818 | -0.96286 | 78 | 2 | 19353 | 0.0040304 | -5.5139 | 2005 | 8 | August-2005 | 0.3818 | 0.00403 | 2006
2005-08-30 | 1.0748 | 0.072154 | 505 | 3 | 19353 | 0.026094 | -3.646 | 2005 | 8 | August-2005 | 1.0748 | 0.026094 | 2006
2005-08-31 | 0.13776 | -1.9823 | 49 | 1 | 19353 | 0.0025319 | -5.9788 | 2005 | 8 | August-2005 | 0.13776 | 0.002532 | 2006
2005-09-02 | 0.56451 | -0.57179 | 64 | 5 | 19353 | 0.003307 | -5.7117 | 2005 | 9 | September-2005 | 0.56451 | 0.003307 | 2006
2005-09-05 | 0.25815 | -1.3542 | 61 | 5 | 19353 | 0.003152 | -5.7597 | 2005 | 9 | September-2005 | 0.25815 | 0.003152 | 2006
2005-09-06 | 0.23666 | -1.4411 | 15 | 2 | 19353 | 0.00077507 | -7.1626 | 2005 | 9 | September-2005 | 0.23666 | 0.000775 | 2006
2005-09-07 | 0.17785 | -1.7268 | 12 | 3 | 19353 | 0.00062006 | -7.3857 | 2005 | 9 | September-2005 | 0.17785 | 0.00062 | 2006
2005-09-08 | 0.2304 | -1.4679 | 36 | 1 | 19353 | 0.0018602 | -6.2871 | 2005 | 9 | September-2005 | 0.2304 | 0.00186 | 2006
2005-09-11 | 9.7641 | 2.2787 | 2381 | 2 | 19353 | 0.12303 | -2.0953 | 2005 | 9 | September-2005 | 9.7641 | 0.12303 | 2006
2005-09-12 | 0.0035137 | -5.6511 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 9 | September-2005 | 0.003514 | 5.2e-05 | 2006
2005-09-13 | 0.0032553 | -5.7275 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2005 | 9 | September-2005 | 0.003255 | 0.000155 | 2006
2005-09-14 | 1.7805 | 0.57689 | 1489 | 7 | 19353 | 0.076939 | -2.5647 | 2005 | 9 | September-2005 | 1.7805 | 0.076939 | 2006
2005-09-15 | 0.10934 | -2.2133 | 36 | 5 | 19353 | 0.0018602 | -6.2871 | 2005 | 9 | September-2005 | 0.10934 | 0.00186 | 2006
2005-09-16 | 0.43688 | -0.82809 | 370 | 2 | 19353 | 0.019118 | -3.9571 | 2005 | 9 | September-2005 | 0.43688 | 0.019118 | 2006
2005-09-17 | 0.073787 | -2.6066 | 68 | 1 | 19353 | 0.0035137 | -5.6511 | 2005 | 9 | September-2005 | 0.073787 | 0.003514 | 2006
2005-09-18 | 1.4936 | 0.4012 | 614 | 2 | 19353 | 0.031726 | -3.4506 | 2005 | 9 | September-2005 | 1.4936 | 0.031726 | 2006
2005-09-19 | 0.085878 | -2.4548 | 26 | 2 | 19353 | 0.0013435 | -6.6125 | 2005 | 9 | September-2005 | 0.085878 | 0.001343 | 2006
2005-09-20 | 0.06769 | -2.6928 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2005 | 9 | September-2005 | 0.06769 | 0.000258 | 2006
2005-09-21 | 0.051775 | -2.9608 | 57 | 2 | 19353 | 0.0029453 | -5.8276 | 2005 | 9 | September-2005 | 0.051775 | 0.002945 | 2006
2005-09-22 | 0.27469 | -1.2921 | 33 | 3 | 19353 | 0.0017052 | -6.3741 | 2005 | 9 | September-2005 | 0.27469 | 0.001705 | 2006
2005-09-23 | 0.69049 | -0.37036 | 234 | 5 | 19353 | 0.012091 | -4.4153 | 2005 | 9 | September-2005 | 0.69049 | 0.012091 | 2006
2005-09-24 | 0.0031003 | -5.7763 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 9 | September-2005 | 0.0031 | 5.2e-05 | 2006
2005-09-25 | 3.8547 | 1.3493 | 262 | 3 | 19353 | 0.013538 | -4.3023 | 2005 | 9 | September-2005 | 3.8547 | 0.013538 | 2006
2005-09-26 | 0.1578 | -1.8464 | 1418 | 4 | 19353 | 0.07327 | -2.6136 | 2005 | 9 | September-2005 | 0.15781 | 0.07327 | 2006
2005-09-28 | 0.041699 | -3.1773 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2005 | 9 | September-2005 | 0.041699 | 0.000155 | 2006
2005-09-29 | 0.85646 | -0.15495 | 51 | 2 | 19353 | 0.0026353 | -5.9388 | 2005 | 9 | September-2005 | 0.85646 | 0.002635 | 2006
2005-09-30 | 0.57376 | -0.55554 | 88 | 2 | 19353 | 0.0045471 | -5.3933 | 2005 | 9 | September-2005 | 0.57376 | 0.004547 | 2006
2005-10-03 | 0.13781 | -1.9819 | 35 | 3 | 19353 | 0.0018085 | -6.3153 | 2005 | 10 | October-2005 | 0.13781 | 0.001809 | 2006
2005-10-04 | 0.95722 | -0.043726 | 115 | 5 | 19353 | 0.0059422 | -5.1257 | 2005 | 10 | October-2005 | 0.95722 | 0.005942 | 2006
2005-10-05 | 1.8243 | 0.60118 | 133 | 4 | 19353 | 0.0068723 | -4.9803 | 2005 | 10 | October-2005 | 1.8243 | 0.006872 | 2006
2005-10-06 | 1.2309 | 0.20772 | 142 | 5 | 19353 | 0.0073374 | -4.9148 | 2005 | 10 | October-2005 | 1.2309 | 0.007337 | 2006
2005-10-08 | 3.7888 | 1.3321 | 969 | 12 | 19353 | 0.05007 | -2.9943 | 2005 | 10 | October-2005 | 3.7888 | 0.05007 | 2006
2005-10-09 | 0.0038754 | -5.5531 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 10 | October-2005 | 0.003875 | 5.2e-05 | 2006
2005-10-10 | 0.15377 | -1.8723 | 17 | 4 | 19353 | 0.00087842 | -7.0374 | 2005 | 10 | October-2005 | 0.15377 | 0.000878 | 2006
2005-10-11 | 5.1053 | 1.6303 | 252 | 5 | 19353 | 0.013021 | -4.3412 | 2005 | 10 | October-2005 | 5.1053 | 0.013021 | 2006
2005-10-12 | 0.12567 | -2.0741 | 32 | 2 | 19353 | 0.0016535 | -6.4049 | 2005 | 10 | October-2005 | 0.12566 | 0.001653 | 2006
2005-10-13 | 1.26 | 0.23112 | 245 | 3 | 19353 | 0.01266 | -4.3693 | 2005 | 10 | October-2005 | 1.26 | 0.01266 | 2006
2005-10-14 | 0.90084 | -0.10443 | 97 | 4 | 19353 | 0.0050121 | -5.2959 | 2005 | 10 | October-2005 | 0.90084 | 0.005012 | 2006
2005-10-17 | 0.49987 | -0.69341 | 101 | 1 | 19353 | 0.0052188 | -5.2555 | 2005 | 10 | October-2005 | 0.49987 | 0.005219 | 2006
2005-10-18 | 0.33571 | -1.0915 | 45 | 2 | 19353 | 0.0023252 | -6.0639 | 2005 | 10 | October-2005 | 0.33571 | 0.002325 | 2006
2005-10-19 | 1.8514 | 0.61594 | 255 | 4 | 19353 | 0.013176 | -4.3293 | 2005 | 10 | October-2005 | 1.8514 | 0.013176 | 2006
2005-10-20 | 2.5867 | 0.95037 | 246 | 2 | 19353 | 0.012711 | -4.3653 | 2005 | 10 | October-2005 | 2.5867 | 0.012711 | 2006
2005-10-21 | 1.1931 | 0.1766 | 477 | 5 | 19353 | 0.024647 | -3.7031 | 2005 | 10 | October-2005 | 1.1931 | 0.024647 | 2006
2005-10-22 | 0.12406 | -2.087 | 21 | 2 | 19353 | 0.0010851 | -6.8261 | 2005 | 10 | October-2005 | 0.12406 | 0.001085 | 2006
2005-10-25 | 0.20069 | -1.606 | 47 | 4 | 19353 | 0.0024286 | -6.0205 | 2005 | 10 | October-2005 | 0.20069 | 0.002429 | 2006
2005-10-26 | 0.95701 | -0.043942 | 128 | 5 | 19353 | 0.006614 | -5.0186 | 2005 | 10 | October-2005 | 0.95701 | 0.006614 | 2006
2005-10-27 | 0.30254 | -1.1956 | 138 | 3 | 19353 | 0.0071307 | -4.9433 | 2005 | 10 | October-2005 | 0.30254 | 0.007131 | 2006
2005-10-28 | 0.010128 | -4.5925 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2005 | 10 | October-2005 | 0.010128 | 0.000362 | 2006
2005-10-30 | 0.019635 | -3.9304 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2005 | 10 | October-2005 | 0.019635 | 0.000103 | 2006
2005-10-31 | 0.39446 | -0.93024 | 36 | 3 | 19353 | 0.0018602 | -6.2871 | 2005 | 10 | October-2005 | 0.39446 | 0.00186 | 2006
2005-11-01 | 0.41838 | -0.87135 | 42 | 2 | 19353 | 0.0021702 | -6.1329 | 2005 | 11 | November-2005 | 0.41839 | 0.00217 | 2006
2005-11-02 | 0.081848 | -2.5029 | 14 | 3 | 19353 | 0.0007234 | -7.2315 | 2005 | 11 | November-2005 | 0.081848 | 0.000723 | 2006
2005-11-03 | 0.032346 | -3.4313 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2005 | 11 | November-2005 | 0.032346 | 0.000258 | 2006
2005-11-04 | 0.057407 | -2.8576 | 19 | 3 | 19353 | 0.00098176 | -6.9262 | 2005 | 11 | November-2005 | 0.057407 | 0.000982 | 2006
2005-11-06 | 0.0047538 | -5.3488 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 11 | November-2005 | 0.004754 | 5.2e-05 | 2006
2005-11-08 | 0.1622 | -1.8189 | 14 | 3 | 19353 | 0.0007234 | -7.2315 | 2005 | 11 | November-2005 | 0.1622 | 0.000723 | 2006
2005-11-09 | 4.691 | 1.5456 | 627 | 2 | 19353 | 0.032398 | -3.4297 | 2005 | 11 | November-2005 | 4.691 | 0.032398 | 2006
2005-11-10 | 0.34532 | -1.0633 | 25 | 2 | 19353 | 0.0012918 | -6.6517 | 2005 | 11 | November-2005 | 0.34532 | 0.001292 | 2006
2005-11-11 | 0.1298 | -2.0418 | 16 | 1 | 19353 | 0.00082675 | -7.098 | 2005 | 11 | November-2005 | 0.1298 | 0.000827 | 2006
2005-11-13 | 3.8355 | 1.3443 | 227 | 1 | 19353 | 0.011729 | -4.4457 | 2005 | 11 | November-2005 | 3.8355 | 0.011729 | 2006
2005-11-15 | 0.088668 | -2.4229 | 34 | 3 | 19353 | 0.0017568 | -6.3442 | 2005 | 11 | November-2005 | 0.088668 | 0.001757 | 2006
2005-11-16 | 0.2163 | -1.5311 | 1439 | 4 | 19353 | 0.074355 | -2.5989 | 2005 | 11 | November-2005 | 0.2163 | 0.074355 | 2006
2005-11-17 | 2.755 | 1.0134 | 524 | 3 | 19353 | 0.027076 | -3.6091 | 2005 | 11 | November-2005 | 2.755 | 0.027076 | 2006
2005-11-18 | 0.22487 | -1.4922 | 34 | 2 | 19353 | 0.0017568 | -6.3442 | 2005 | 11 | November-2005 | 0.22487 | 0.001757 | 2006
2005-11-19 | 0.23252 | -1.4588 | 500 | 1 | 19353 | 0.025836 | -3.656 | 2005 | 11 | November-2005 | 0.23252 | 0.025836 | 2006
2005-11-20 | 0.10644 | -2.2401 | 20 | 1 | 19353 | 0.0010334 | -6.8749 | 2005 | 11 | November-2005 | 0.10644 | 0.001033 | 2006
2005-11-21 | 0.20488 | -1.5853 | 163 | 2 | 19353 | 0.0084225 | -4.7769 | 2005 | 11 | November-2005 | 0.20488 | 0.008422 | 2006
2005-11-22 | 0.32496 | -1.124 | 53 | 2 | 19353 | 0.0027386 | -5.9003 | 2005 | 11 | November-2005 | 0.32496 | 0.002739 | 2006
2005-11-23 | 0.12288 | -2.0966 | 16 | 2 | 19353 | 0.00082675 | -7.098 | 2005 | 11 | November-2005 | 0.12287 | 0.000827 | 2006
2005-11-24 | 0.07265 | -2.6221 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2005 | 11 | November-2005 | 0.07265 | 0.000362 | 2006
2005-11-25 | 0.43854 | -0.82431 | 48 | 4 | 19353 | 0.0024802 | -5.9994 | 2005 | 11 | November-2005 | 0.43854 | 0.00248 | 2006
2005-11-26 | 5.1672e-05 | -9.8706 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2005 | 11 | November-2005 | 5.2e-05 | 5.2e-05 | 2006
2005-11-27 | 0.80804 | -0.21314 | 108 | 1 | 19353 | 0.0055805 | -5.1885 | 2005 | 11 | November-2005 | 0.80804 | 0.005581 | 2006
2005-11-28 | 4.0204 | 1.3914 | 2356 | 12 | 19353 | 0.12174 | -2.1059 | 2005 | 11 | November-2005 | 4.0204 | 0.12174 | 2006
2005-11-29 | 0.38521 | -0.95396 | 65 | 3 | 19353 | 0.0033587 | -5.6962 | 2005 | 11 | November-2005 | 0.38521 | 0.003359 | 2006
2005-11-30 | 0.45326 | -0.79128 | 32 | 2 | 19353 | 0.0016535 | -6.4049 | 2005 | 11 | November-2005 | 0.45326 | 0.001653 | 2006
2005-12-01 | 4.7453 | 1.5571 | 580 | 3 | 19353 | 0.02997 | -3.5076 | 2005 | 12 | December-2005 | 4.7453 | 0.02997 | 2006
2005-12-02 | 0.2257 | -1.4885 | 16 | 1 | 19353 | 0.00082675 | -7.098 | 2005 | 12 | December-2005 | 0.2257 | 0.000827 | 2006
2005-12-04 | 0.054255 | -2.9141 | 105 | 1 | 19353 | 0.0054255 | -5.2166 | 2005 | 12 | December-2005 | 0.054255 | 0.005426 | 2006
2005-12-05 | 1.8708 | 0.62635 | 674 | 3 | 19353 | 0.034827 | -3.3574 | 2005 | 12 | December-2005 | 1.8708 | 0.034827 | 2006
2005-12-06 | 3.9089 | 1.3632 | 998 | 19 | 19353 | 0.051568 | -2.9648 | 2005 | 12 | December-2005 | 3.9089 | 0.051568 | 2006
2005-12-07 | 4.1834 | 1.4311 | 251 | 5 | 19353 | 0.01297 | -4.3451 | 2005 | 12 | December-2005 | 4.1834 | 0.01297 | 2006
2005-12-08 | 0.35173 | -1.0449 | 21 | 5 | 19353 | 0.0010851 | -6.8261 | 2005 | 12 | December-2005 | 0.35173 | 0.001085 | 2006
2005-12-09 | 0.61381 | -0.48808 | 96 | 7 | 19353 | 0.0049605 | -5.3063 | 2005 | 12 | December-2005 | 0.61381 | 0.00496 | 2006
2005-12-10 | 0.51439 | -0.66477 | 110 | 2 | 19353 | 0.0056839 | -5.1701 | 2005 | 12 | December-2005 | 0.51439 | 0.005684 | 2006
2005-12-11 | 0.63313 | -0.45708 | 391 | 5 | 19353 | 0.020204 | -3.9019 | 2005 | 12 | December-2005 | 0.63313 | 0.020204 | 2006
2005-12-12 | 0.33814 | -1.0843 | 28 | 6 | 19353 | 0.0014468 | -6.5384 | 2005 | 12 | December-2005 | 0.33814 | 0.001447 | 2006
2005-12-13 | 0.3107 | -1.1689 | 42 | 4 | 19353 | 0.0021702 | -6.1329 | 2005 | 12 | December-2005 | 0.3107 | 0.00217 | 2006
2005-12-14 | 0.42929 | -0.84563 | 112 | 7 | 19353 | 0.0057872 | -5.1521 | 2005 | 12 | December-2005 | 0.42929 | 0.005787 | 2006
2005-12-15 | 0.80887 | -0.21212 | 174 | 5 | 19353 | 0.0089909 | -4.7115 | 2005 | 12 | December-2005 | 0.80887 | 0.008991 | 2006
2005-12-16 | 0.058906 | -2.8318 | 9 | 3 | 19353 | 0.00046504 | -7.6734 | 2005 | 12 | December-2005 | 0.058906 | 0.000465 | 2006
2005-12-17 | 1.2092 | 0.18997 | 67 | 2 | 19353 | 0.003462 | -5.6659 | 2005 | 12 | December-2005 | 1.2092 | 0.003462 | 2006
2005-12-19 | 0.58931 | -0.5288 | 113 | 2 | 19353 | 0.0058389 | -5.1432 | 2005 | 12 | December-2005 | 0.58931 | 0.005839 | 2006
2005-12-20 | 2.8317 | 1.0409 | 435 | 6 | 19353 | 0.022477 | -3.7953 | 2005 | 12 | December-2005 | 2.8317 | 0.022477 | 2006
2005-12-21 | 0.61071 | -0.49314 | 76 | 5 | 19353 | 0.003927 | -5.5399 | 2005 | 12 | December-2005 | 0.61071 | 0.003927 | 2006
2005-12-22 | 1.0237 | 0.02339 | 280 | 4 | 19353 | 0.014468 | -4.2358 | 2005 | 12 | December-2005 | 1.0237 | 0.014468 | 2006
2005-12-23 | 3.5295 | 1.2612 | 375 | 6 | 19353 | 0.019377 | -3.9437 | 2005 | 12 | December-2005 | 3.5295 | 0.019377 | 2006
2005-12-25 | 0.81331 | -0.20664 | 1574 | 1 | 19353 | 0.081331 | -2.5092 | 2005 | 12 | December-2005 | 0.81331 | 0.081331 | 2006
2005-12-26 | 0.099623 | -2.3064 | 241 | 1 | 19353 | 0.012453 | -4.3858 | 2005 | 12 | December-2005 | 0.099623 | 0.012453 | 2006
2005-12-28 | 0.5718 | -0.55897 | 78 | 9 | 19353 | 0.0040304 | -5.5139 | 2005 | 12 | December-2005 | 0.5718 | 0.00403 | 2006
2005-12-29 | 0.089133 | -2.4176 | 9 | 3 | 19353 | 0.00046504 | -7.6734 | 2005 | 12 | December-2005 | 0.089133 | 0.000465 | 2006
2005-12-31 | 0.099209 | -2.3105 | 36 | 2 | 19353 | 0.0018602 | -6.2871 | 2005 | 12 | December-2005 | 0.099209 | 0.00186 | 2006
2006-01-02 | 0.43079 | -0.84214 | 37 | 2 | 19353 | 0.0019118 | -6.2597 | 2006 | 1 | January-2006 | 0.43079 | 0.001912 | 2006
2006-01-03 | 0.086498 | -2.4476 | 11 | 2 | 19353 | 0.00056839 | -7.4727 | 2006 | 1 | January-2006 | 0.086498 | 0.000568 | 2006
2006-01-04 | 3.407 | 1.2258 | 861 | 8 | 19353 | 0.044489 | -3.1125 | 2006 | 1 | January-2006 | 3.407 | 0.044489 | 2006
2006-01-05 | 1.6824 | 0.52024 | 206 | 8 | 19353 | 0.010644 | -4.5427 | 2006 | 1 | January-2006 | 1.6824 | 0.010644 | 2006
2006-01-06 | 0.024906 | -3.6927 | 241 | 1 | 19353 | 0.012453 | -4.3858 | 2006 | 1 | January-2006 | 0.024906 | 0.012453 | 2006
2006-01-07 | 0.076474 | -2.5708 | 20 | 1 | 19353 | 0.0010334 | -6.8749 | 2006 | 1 | January-2006 | 0.076474 | 0.001033 | 2006
2006-01-09 | 0.012298 | -4.3983 | 3 | 2 | 19353 | 0.00015501 | -8.772 | 2006 | 1 | January-2006 | 0.012298 | 0.000155 | 2006
2006-01-10 | 0.11621 | -2.1524 | 40 | 4 | 19353 | 0.0020669 | -6.1817 | 2006 | 1 | January-2006 | 0.11621 | 0.002067 | 2006
2006-01-11 | 0.41756 | -0.87333 | 58 | 4 | 19353 | 0.002997 | -5.8102 | 2006 | 1 | January-2006 | 0.41756 | 0.002997 | 2006
2006-01-12 | 0.60983 | -0.49458 | 75 | 2 | 19353 | 0.0038754 | -5.5531 | 2006 | 1 | January-2006 | 0.60983 | 0.003875 | 2006
2006-01-13 | 0.32574 | -1.1217 | 46 | 6 | 19353 | 0.0023769 | -6.042 | 2006 | 1 | January-2006 | 0.32574 | 0.002377 | 2006
2006-01-16 | 0.064176 | -2.7461 | 6 | 1 | 19353 | 0.00031003 | -8.0788 | 2006 | 1 | January-2006 | 0.064176 | 0.00031 | 2006
2006-01-17 | 0.084741 | -2.4682 | 20 | 1 | 19353 | 0.0010334 | -6.8749 | 2006 | 1 | January-2006 | 0.084741 | 0.001033 | 2006
2006-01-18 | 3.2935 | 1.192 | 477 | 7 | 19353 | 0.024647 | -3.7031 | 2006 | 1 | January-2006 | 3.2935 | 0.024647 | 2006
2006-01-19 | 0.020617 | -3.8816 | 3 | 2 | 19353 | 0.00015501 | -8.772 | 2006 | 1 | January-2006 | 0.020617 | 0.000155 | 2006
2006-01-20 | 0.36795 | -0.9998 | 76 | 3 | 19353 | 0.003927 | -5.5399 | 2006 | 1 | January-2006 | 0.36795 | 0.003927 | 2006
2006-01-23 | 0.32589 | -1.1212 | 119 | 1 | 19353 | 0.0061489 | -5.0915 | 2006 | 1 | January-2006 | 0.32589 | 0.006149 | 2006
2006-01-24 | 4.6306 | 1.5327 | 1375 | 16 | 19353 | 0.071048 | -2.6444 | 2006 | 1 | January-2006 | 4.6306 | 0.071048 | 2006
2006-01-25 | 0.4312 | -0.84118 | 111 | 8 | 19353 | 0.0057355 | -5.1611 | 2006 | 1 | January-2006 | 0.4312 | 0.005736 | 2006
2006-01-26 | 0.31835 | -1.1446 | 49 | 3 | 19353 | 0.0025319 | -5.9788 | 2006 | 1 | January-2006 | 0.31835 | 0.002532 | 2006
2006-01-27 | 0.0074407 | -4.9008 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2006 | 1 | January-2006 | 0.007441 | 0.000155 | 2006
2006-01-28 | 0.17734 | -1.7297 | 24 | 1 | 19353 | 0.0012401 | -6.6925 | 2006 | 1 | January-2006 | 0.17734 | 0.00124 | 2006
2006-01-30 | 0.56012 | -0.5796 | 305 | 3 | 19353 | 0.01576 | -4.1503 | 2006 | 1 | January-2006 | 0.56012 | 0.01576 | 2006
2006-01-31 | 3.1367 | 1.1432 | 3532 | 4 | 19353 | 0.1825 | -1.701 | 2006 | 1 | January-2006 | 3.1367 | 0.1825 | 2006
2006-02-02 | 0.71529 | -0.33507 | 151 | 2 | 19353 | 0.0078024 | -4.8533 | 2006 | 2 | February-2006 | 0.71529 | 0.007802 | 2006
2006-02-03 | 0.31297 | -1.1616 | 23 | 3 | 19353 | 0.0011884 | -6.7351 | 2006 | 2 | February-2006 | 0.31298 | 0.001188 | 2006
2006-02-04 | 0.5192 | -0.65547 | 24 | 1 | 19353 | 0.0012401 | -6.6925 | 2006 | 2 | February-2006 | 0.5192 | 0.00124 | 2006
2006-02-05 | 2.6135 | 0.96071 | 1096 | 1 | 19353 | 0.056632 | -2.8712 | 2006 | 2 | February-2006 | 2.6135 | 0.056632 | 2006
2006-02-06 | 0.018808 | -3.9734 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2006 | 2 | February-2006 | 0.018808 | 0.000207 | 2006
2006-02-07 | 0.061851 | -2.783 | 19 | 1 | 19353 | 0.00098176 | -6.9262 | 2006 | 2 | February-2006 | 0.061851 | 0.000982 | 2006
2006-02-08 | 0.37379 | -0.98406 | 77 | 5 | 19353 | 0.0039787 | -5.5268 | 2006 | 2 | February-2006 | 0.37379 | 0.003979 | 2006
2006-02-09 | 1.0796 | 0.076567 | 113 | 4 | 19353 | 0.0058389 | -5.1432 | 2006 | 2 | February-2006 | 1.0796 | 0.005839 | 2006
2006-02-10 | 0.33747 | -1.0863 | 62 | 4 | 19353 | 0.0032036 | -5.7435 | 2006 | 2 | February-2006 | 0.33747 | 0.003204 | 2006
2006-02-11 | 2.071 | 0.72803 | 80 | 1 | 19353 | 0.0041337 | -5.4886 | 2006 | 2 | February-2006 | 2.071 | 0.004134 | 2006
2006-02-12 | 0.046401 | -3.0704 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2006 | 2 | February-2006 | 0.046401 | 0.000103 | 2006
2006-02-13 | 0.34191 | -1.0732 | 41 | 4 | 19353 | 0.0021185 | -6.157 | 2006 | 2 | February-2006 | 0.34191 | 0.002119 | 2006
2006-02-14 | 0.92787 | -0.074867 | 77 | 3 | 19353 | 0.0039787 | -5.5268 | 2006 | 2 | February-2006 | 0.92787 | 0.003979 | 2006
2006-02-16 | 0.39663 | -0.92475 | 781 | 5 | 19353 | 0.040356 | -3.21 | 2006 | 2 | February-2006 | 0.39663 | 0.040356 | 2006
2006-02-17 | 0.20524 | -1.5836 | 20 | 3 | 19353 | 0.0010334 | -6.8749 | 2006 | 2 | February-2006 | 0.20524 | 0.001033 | 2006
2006-02-18 | 0.25526 | -1.3655 | 52 | 1 | 19353 | 0.0026869 | -5.9194 | 2006 | 2 | February-2006 | 0.25526 | 0.002687 | 2006
2006-02-20 | 6.1149 | 1.8107 | 777 | 2 | 19353 | 0.040149 | -3.2152 | 2006 | 2 | February-2006 | 6.1149 | 0.040149 | 2006
2006-02-21 | 0.19237 | -1.6483 | 16 | 3 | 19353 | 0.00082675 | -7.098 | 2006 | 2 | February-2006 | 0.19237 | 0.000827 | 2006
2006-02-22 | 0.0076474 | -4.8734 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2006 | 2 | February-2006 | 0.007647 | 5.2e-05 | 2006
2006-02-23 | 0.19857 | -1.6166 | 26 | 2 | 19353 | 0.0013435 | -6.6125 | 2006 | 2 | February-2006 | 0.19857 | 0.001343 | 2006
2006-02-24 | 5.639 | 1.7297 | 777 | 2 | 19353 | 0.040149 | -3.2152 | 2006 | 2 | February-2006 | 5.639 | 0.040149 | 2006
2006-02-25 | 0.0075957 | -4.8802 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2006 | 2 | February-2006 | 0.007596 | 5.2e-05 | 2006
2006-02-26 | 0.11223 | -2.1872 | 15 | 2 | 19353 | 0.00077507 | -7.1626 | 2006 | 2 | February-2006 | 0.11223 | 0.000775 | 2006
2006-02-28 | 0.96166 | -0.039095 | 162 | 2 | 19353 | 0.0083708 | -4.783 | 2006 | 2 | February-2006 | 0.96166 | 0.008371 | 2006
2006-03-02 | 0.31871 | -1.1435 | 68 | 3 | 19353 | 0.0035137 | -5.6511 | 2006 | 3 | March-2006 | 0.31871 | 0.003514 | 2006
2006-03-03 | 0.30321 | -1.1933 | 231 | 3 | 19353 | 0.011936 | -4.4282 | 2006 | 3 | March-2006 | 0.30321 | 0.011936 | 2006
2006-03-04 | 0.0091459 | -4.6945 | 166 | 1 | 19353 | 0.0085775 | -4.7586 | 2006 | 3 | March-2006 | 0.009146 | 0.008577 | 2006
2006-03-05 | 0.054048 | -2.9179 | 86 | 2 | 19353 | 0.0044438 | -5.4163 | 2006 | 3 | March-2006 | 0.054048 | 0.004444 | 2006
2006-03-06 | 0.27179 | -1.3027 | 20 | 1 | 19353 | 0.0010334 | -6.8749 | 2006 | 3 | March-2006 | 0.27179 | 0.001033 | 2006
2006-03-07 | 0.29701 | -1.214 | 47 | 2 | 19353 | 0.0024286 | -6.0205 | 2006 | 3 | March-2006 | 0.29701 | 0.002429 | 2006
2006-03-08 | 0.0479 | -3.0386 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2006 | 3 | March-2006 | 0.0479 | 0.000362 | 2006
2006-03-09 | 2.2157 | 0.79556 | 537 | 6 | 19353 | 0.027748 | -3.5846 | 2006 | 3 | March-2006 | 2.2157 | 0.027748 | 2006
2006-03-10 | 0.0043404 | -5.4398 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2006 | 3 | March-2006 | 0.00434 | 0.000155 | 2006
2006-03-11 | 0.91216 | -0.091942 | 1687 | 3 | 19353 | 0.08717 | -2.4399 | 2006 | 3 | March-2006 | 0.91216 | 0.08717 | 2006
2006-03-12 | 0.021702 | -3.8303 | 7 | 1 | 19353 | 0.0003617 | -7.9247 | 2006 | 3 | March-2006 | 0.021702 | 0.000362 | 2006
2006-03-13 | 0.17806 | -1.7256 | 26 | 4 | 19353 | 0.0013435 | -6.6125 | 2006 | 3 | March-2006 | 0.17806 | 0.001343 | 2006
2006-03-14 | 0.099364 | -2.309 | 9 | 3 | 19353 | 0.00046504 | -7.6734 | 2006 | 3 | March-2006 | 0.099364 | 0.000465 | 2006
2006-03-16 | 4.1787 | 1.43 | 387 | 2 | 19353 | 0.019997 | -3.9122 | 2006 | 3 | March-2006 | 4.1787 | 0.019997 | 2006
2006-03-17 | 0.1423 | -1.9498 | 31 | 2 | 19353 | 0.0016018 | -6.4366 | 2006 | 3 | March-2006 | 0.1423 | 0.001602 | 2006
2006-03-20 | 0.20917 | -1.5646 | 38 | 2 | 19353 | 0.0019635 | -6.233 | 2006 | 3 | March-2006 | 0.20917 | 0.001964 | 2006
2006-03-21 | 0.12091 | -2.1127 | 30 | 1 | 19353 | 0.0015501 | -6.4694 | 2006 | 3 | March-2006 | 0.12091 | 0.00155 | 2006
2006-03-22 | 0.16163 | -1.8225 | 12 | 2 | 19353 | 0.00062006 | -7.3857 | 2006 | 3 | March-2006 | 0.16163 | 0.00062 | 2006
2006-03-23 | 0.14442 | -1.935 | 23 | 2 | 19353 | 0.0011884 | -6.7351 | 2006 | 3 | March-2006 | 0.14442 | 0.001188 | 2006
2006-03-24 | 28.4171 | 3.347 | 1107 | 4 | 19353 | 0.0572 | -2.8612 | 2006 | 3 | March-2006 | 21.6659 | 0.0572 | 2006
2006-03-26 | 0.23769 | -1.4368 | 47 | 2 | 19353 | 0.0024286 | -6.0205 | 2006 | 3 | March-2006 | 0.23769 | 0.002429 | 2006
2006-03-27 | 1.2438 | 0.21816 | 1003 | 7 | 19353 | 0.051827 | -2.9599 | 2006 | 3 | March-2006 | 1.2438 | 0.051827 | 2006
2006-03-29 | 0.021134 | -3.8569 | 6 | 3 | 19353 | 0.00031003 | -8.0788 | 2006 | 3 | March-2006 | 0.021134 | 0.00031 | 2006
2006-03-30 | 0.24565 | -1.4039 | 41 | 4 | 19353 | 0.0021185 | -6.157 | 2006 | 3 | March-2006 | 0.24565 | 0.002119 | 2006
2006-03-31 | 0.56369 | -0.57326 | 185 | 3 | 19353 | 0.0095592 | -4.6502 | 2006 | 3 | March-2006 | 0.56368 | 0.009559 | 2006
2006-04-03 | 0.06738 | -2.6974 | 21 | 6 | 19353 | 0.0010851 | -6.8261 | 2006 | 4 | April-2006 | 0.06738 | 0.001085 | 2007
2006-04-04 | 1.376 | 0.31919 | 220 | 6 | 19353 | 0.011368 | -4.477 | 2006 | 4 | April-2006 | 1.376 | 0.011368 | 2007
2006-04-05 | 0.63318 | -0.457 | 70 | 2 | 19353 | 0.003617 | -5.6221 | 2006 | 4 | April-2006 | 0.63318 | 0.003617 | 2007
2006-04-06 | 0.2257 | -1.4885 | 42 | 1 | 19353 | 0.0021702 | -6.1329 | 2006 | 4 | April-2006 | 0.2257 | 0.00217 | 2007
2006-04-07 | 0.28115 | -1.2689 | 63 | 5 | 19353 | 0.0032553 | -5.7275 | 2006 | 4 | April-2006 | 0.28114 | 0.003255 | 2007
2006-04-08 | 0.013848 | -4.2796 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2006 | 4 | April-2006 | 0.013848 | 5.2e-05 | 2007
2006-04-09 | 3.0808 | 1.1252 | 1096 | 1 | 19353 | 0.056632 | -2.8712 | 2006 | 4 | April-2006 | 3.0808 | 0.056632 | 2007
2006-04-10 | 0.10949 | -2.2119 | 63 | 7 | 19353 | 0.0032553 | -5.7275 | 2006 | 4 | April-2006 | 0.10949 | 0.003255 | 2007
2006-04-11 | 1.5569 | 0.44271 | 183 | 4 | 19353 | 0.0094559 | -4.6611 | 2006 | 4 | April-2006 | 1.5569 | 0.009456 | 2007
2006-04-12 | 0.4668 | -0.76185 | 40 | 4 | 19353 | 0.0020669 | -6.1817 | 2006 | 4 | April-2006 | 0.4668 | 0.002067 | 2007
2006-04-13 | 0.089702 | -2.4113 | 8 | 1 | 19353 | 0.00041337 | -7.7912 | 2006 | 4 | April-2006 | 0.089702 | 0.000413 | 2007
2006-04-14 | 0.03338 | -3.3998 | 19 | 1 | 19353 | 0.00098176 | -6.9262 | 2006 | 4 | April-2006 | 0.03338 | 0.000982 | 2007
2006-04-18 | 0.0059939 | -5.117 | 14 | 2 | 19353 | 0.0007234 | -7.2315 | 2006 | 4 | April-2006 | 0.005994 | 0.000723 | 2007
2006-04-19 | 0.03617 | -3.3195 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2006 | 4 | April-2006 | 0.03617 | 0.000207 | 2007
2006-04-20 | 0.010128 | -4.5925 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2006 | 4 | April-2006 | 0.010128 | 0.000207 | 2007
2006-04-21 | 0.13331 | -2.0151 | 11 | 2 | 19353 | 0.00056839 | -7.4727 | 2006 | 4 | April-2006 | 0.13331 | 0.000568 | 2007
2006-04-23 | 0.011988 | -4.4239 | 29 | 1 | 19353 | 0.0014985 | -6.5033 | 2006 | 4 | April-2006 | 0.011988 | 0.001498 | 2007
2006-04-24 | 0.25712 | -1.3582 | 89 | 2 | 19353 | 0.0045988 | -5.382 | 2006 | 4 | April-2006 | 0.25712 | 0.004599 | 2007
2006-04-25 | 2.3496 | 0.85425 | 493 | 3 | 19353 | 0.025474 | -3.6701 | 2006 | 4 | April-2006 | 2.3496 | 0.025474 | 2007
2006-04-27 | 6.6315 | 1.8918 | 343 | 2 | 19353 | 0.017723 | -4.0329 | 2006 | 4 | April-2006 | 6.6315 | 0.017723 | 2007
2006-04-28 | 0.24725 | -1.3974 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2006 | 4 | April-2006 | 0.24725 | 0.001447 | 2007
2006-04-30 | 1.0882 | 0.084481 | 591 | 2 | 19353 | 0.030538 | -3.4888 | 2006 | 4 | April-2006 | 1.0882 | 0.030538 | 2007
2006-05-01 | 0.70914 | -0.3437 | 55 | 5 | 19353 | 0.0028419 | -5.8633 | 2006 | 5 | May-2006 | 0.70914 | 0.002842 | 2007
2006-05-02 | 0.18876 | -1.6673 | 40 | 2 | 19353 | 0.0020669 | -6.1817 | 2006 | 5 | May-2006 | 0.18876 | 0.002067 | 2007
2006-05-03 | 0.10272 | -2.2757 | 7 | 1 | 19353 | 0.0003617 | -7.9247 | 2006 | 5 | May-2006 | 0.10272 | 0.000362 | 2007
2006-05-04 | 0.075751 | -2.5803 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2006 | 5 | May-2006 | 0.075751 | 0.000517 | 2007
2006-05-06 | 0.0080091 | -4.8272 | 5 | 1 | 19353 | 0.00025836 | -8.2612 | 2006 | 5 | May-2006 | 0.008009 | 0.000258 | 2007
2006-05-07 | 0.43135 | -0.84083 | 65 | 2 | 19353 | 0.0033587 | -5.6962 | 2006 | 5 | May-2006 | 0.43135 | 0.003359 | 2007
2006-05-09 | 0.33473 | -1.0944 | 67 | 2 | 19353 | 0.003462 | -5.6659 | 2006 | 5 | May-2006 | 0.33473 | 0.003462 | 2007
2006-05-10 | 1.1074 | 0.10204 | 147 | 3 | 19353 | 0.0075957 | -4.8802 | 2006 | 5 | May-2006 | 1.1074 | 0.007596 | 2007
2006-05-11 | 1.2737 | 0.24193 | 555 | 3 | 19353 | 0.028678 | -3.5516 | 2006 | 5 | May-2006 | 1.2737 | 0.028678 | 2007
2006-05-12 | 1.444 | 0.36739 | 189 | 9 | 19353 | 0.0097659 | -4.6289 | 2006 | 5 | May-2006 | 1.444 | 0.009766 | 2007
2006-05-13 | 0.0086808 | -4.7466 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2006 | 5 | May-2006 | 0.008681 | 0.000155 | 2007
2006-05-15 | 1.8556 | 0.61822 | 79 | 3 | 19353 | 0.0040821 | -5.5012 | 2006 | 5 | May-2006 | 1.8556 | 0.004082 | 2007
2006-05-16 | 0.02165 | -3.8327 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2006 | 5 | May-2006 | 0.02165 | 5.2e-05 | 2007
2006-05-17 | 0.047693 | -3.043 | 13 | 1 | 19353 | 0.00067173 | -7.3057 | 2006 | 5 | May-2006 | 0.047693 | 0.000672 | 2007
2006-05-18 | 0.12184 | -2.105 | 14 | 3 | 19353 | 0.0007234 | -7.2315 | 2006 | 5 | May-2006 | 0.12184 | 0.000723 | 2007
2006-05-19 | 0.28936 | -1.2401 | 82 | 4 | 19353 | 0.0042371 | -5.4639 | 2006 | 5 | May-2006 | 0.28936 | 0.004237 | 2007
2006-05-22 | 0.085103 | -2.4639 | 14 | 2 | 19353 | 0.0007234 | -7.2315 | 2006 | 5 | May-2006 | 0.085103 | 0.000723 | 2007
2006-05-23 | 0.22177 | -1.5061 | 44 | 3 | 19353 | 0.0022735 | -6.0864 | 2006 | 5 | May-2006 | 0.22177 | 0.002274 | 2007
2006-05-24 | 0.47951 | -0.73499 | 85 | 2 | 19353 | 0.0043921 | -5.428 | 2006 | 5 | May-2006 | 0.47951 | 0.004392 | 2007
2006-05-25 | 0.5455 | -0.60606 | 33 | 2 | 19353 | 0.0017052 | -6.3741 | 2006 | 5 | May-2006 | 0.5455 | 0.001705 | 2007
2006-05-26 | 0.084121 | -2.4755 | 11 | 1 | 19353 | 0.00056839 | -7.4727 | 2006 | 5 | May-2006 | 0.084121 | 0.000568 | 2007
2006-05-27 | 0.27794 | -1.2803 | 489 | 1 | 19353 | 0.025267 | -3.6782 | 2006 | 5 | May-2006 | 0.27794 | 0.025267 | 2007
2006-05-28 | 0.61763 | -0.48187 | 63 | 2 | 19353 | 0.0032553 | -5.7275 | 2006 | 5 | May-2006 | 0.61763 | 0.003255 | 2007
2006-05-30 | 0.23294 | -1.457 | 36 | 3 | 19353 | 0.0018602 | -6.2871 | 2006 | 5 | May-2006 | 0.23294 | 0.00186 | 2007
2006-05-31 | 0.71048 | -0.34181 | 110 | 3 | 19353 | 0.0056839 | -5.1701 | 2006 | 5 | May-2006 | 0.71048 | 0.005684 | 2007
2006-06-01 | 0.18302 | -1.6982 | 16 | 3 | 19353 | 0.00082675 | -7.098 | 2006 | 6 | June-2006 | 0.18302 | 0.000827 | 2007
2006-06-02 | 0.21635 | -1.5309 | 35 | 2 | 19353 | 0.0018085 | -6.3153 | 2006 | 6 | June-2006 | 0.21635 | 0.001809 | 2007
2006-06-03 | 0.019532 | -3.9357 | 42 | 1 | 19353 | 0.0021702 | -6.1329 | 2006 | 6 | June-2006 | 0.019532 | 0.00217 | 2007
2006-06-06 | 0.32088 | -1.1367 | 52 | 6 | 19353 | 0.0026869 | -5.9194 | 2006 | 6 | June-2006 | 0.32088 | 0.002687 | 2007
2006-06-07 | 0.46597 | -0.76362 | 52 | 3 | 19353 | 0.0026869 | -5.9194 | 2006 | 6 | June-2006 | 0.46597 | 0.002687 | 2007
2006-06-08 | 0.14587 | -1.925 | 33 | 2 | 19353 | 0.0017052 | -6.3741 | 2006 | 6 | June-2006 | 0.14587 | 0.001705 | 2007
2006-06-09 | 0.55506 | -0.58869 | 393 | 3 | 19353 | 0.020307 | -3.8968 | 2006 | 6 | June-2006 | 0.55506 | 0.020307 | 2007
2006-06-12 | 75.9652 | 4.3303 | 3067 | 31 | 19353 | 0.15848 | -1.8421 | 2006 | 6 | June-2006 | 21.6659 | 0.15848 | 2007
2006-06-13 | 2.2359 | 0.80466 | 344 | 17 | 19353 | 0.017775 | -4.03 | 2006 | 6 | June-2006 | 2.2359 | 0.017775 | 2007
2006-06-14 | 0.46742 | -0.76052 | 96 | 9 | 19353 | 0.0049605 | -5.3063 | 2006 | 6 | June-2006 | 0.46742 | 0.00496 | 2007
2006-06-15 | 0.9738 | -0.026547 | 123 | 2 | 19353 | 0.0063556 | -5.0584 | 2006 | 6 | June-2006 | 0.9738 | 0.006356 | 2007
2006-06-16 | 1.0783 | 0.075369 | 94 | 8 | 19353 | 0.0048571 | -5.3273 | 2006 | 6 | June-2006 | 1.0783 | 0.004857 | 2007
2006-06-18 | 0.0077507 | -4.86 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2006 | 6 | June-2006 | 0.007751 | 0.000155 | 2007
2006-06-19 | 8.6945 | 2.1627 | 997 | 14 | 19353 | 0.051517 | -2.9659 | 2006 | 6 | June-2006 | 8.6945 | 0.051517 | 2007
2006-06-20 | 0.18292 | -1.6987 | 17 | 5 | 19353 | 0.00087842 | -7.0374 | 2006 | 6 | June-2006 | 0.18292 | 0.000878 | 2007
2006-06-21 | 0.59727 | -0.51538 | 88 | 5 | 19353 | 0.0045471 | -5.3933 | 2006 | 6 | June-2006 | 0.59727 | 0.004547 | 2007
2006-06-22 | 1.1141 | 0.10804 | 232 | 4 | 19353 | 0.011988 | -4.4239 | 2006 | 6 | June-2006 | 1.1141 | 0.011988 | 2007
2006-06-23 | 0.70335 | -0.3519 | 120 | 7 | 19353 | 0.0062006 | -5.0831 | 2006 | 6 | June-2006 | 0.70335 | 0.006201 | 2007
2006-06-24 | 0.0064589 | -5.0423 | 2 | 2 | 19353 | 0.00010334 | -9.1775 | 2006 | 6 | June-2006 | 0.006459 | 0.000103 | 2007
2006-06-25 | 3.3457 | 1.2077 | 548 | 2 | 19353 | 0.028316 | -3.5643 | 2006 | 6 | June-2006 | 3.3457 | 0.028316 | 2007
2006-06-26 | 0.013641 | -4.2947 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2006 | 6 | June-2006 | 0.013641 | 0.000258 | 2007
2006-06-27 | 2.4593 | 0.89988 | 252 | 9 | 19353 | 0.013021 | -4.3412 | 2006 | 6 | June-2006 | 2.4593 | 0.013021 | 2007
2006-06-28 | 1.8885 | 0.63581 | 269 | 3 | 19353 | 0.0139 | -4.2759 | 2006 | 6 | June-2006 | 1.8885 | 0.0139 | 2007
2006-06-29 | 0.20849 | -1.5678 | 65 | 2 | 19353 | 0.0033587 | -5.6962 | 2006 | 6 | June-2006 | 0.2085 | 0.003359 | 2007
2006-07-02 | 0.024802 | -3.6968 | 5 | 1 | 19353 | 0.00025836 | -8.2612 | 2006 | 7 | July-2006 | 0.024802 | 0.000258 | 2007
2006-07-03 | 0.00041337 | -7.7912 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2006 | 7 | July-2006 | 0.000413 | 5.2e-05 | 2007
2006-07-04 | 0.16013 | -1.8318 | 72 | 2 | 19353 | 0.0037204 | -5.5939 | 2006 | 7 | July-2006 | 0.16013 | 0.00372 | 2007
2006-07-05 | 0.82209 | -0.1959 | 86 | 1 | 19353 | 0.0044438 | -5.4163 | 2006 | 7 | July-2006 | 0.8221 | 0.004444 | 2007
2006-07-06 | 3.2109 | 1.1665 | 397 | 6 | 19353 | 0.020514 | -3.8867 | 2006 | 7 | July-2006 | 3.2109 | 0.020514 | 2007
2006-07-07 | 3.3891 | 1.2206 | 196 | 2 | 19353 | 0.010128 | -4.5925 | 2006 | 7 | July-2006 | 3.3891 | 0.010128 | 2007
2006-07-08 | 0.28326 | -1.2614 | 82 | 3 | 19353 | 0.0042371 | -5.4639 | 2006 | 7 | July-2006 | 0.28326 | 0.004237 | 2007
2006-07-10 | 0.10014 | -2.3012 | 12 | 5 | 19353 | 0.00062006 | -7.3857 | 2006 | 7 | July-2006 | 0.10014 | 0.00062 | 2007
2006-07-11 | 0.10169 | -2.2858 | 26 | 2 | 19353 | 0.0013435 | -6.6125 | 2006 | 7 | July-2006 | 0.10169 | 0.001343 | 2007
2006-07-12 | 1.9773 | 0.68171 | 423 | 10 | 19353 | 0.021857 | -3.8232 | 2006 | 7 | July-2006 | 1.9773 | 0.021857 | 2007
2006-07-13 | 3.584 | 1.2765 | 374 | 16 | 19353 | 0.019325 | -3.9463 | 2006 | 7 | July-2006 | 3.584 | 0.019325 | 2007
2006-07-14 | 1.1374 | 0.12874 | 86 | 2 | 19353 | 0.0044438 | -5.4163 | 2006 | 7 | July-2006 | 1.1374 | 0.004444 | 2007
2006-07-15 | 0.26838 | -1.3153 | 98 | 1 | 19353 | 0.0050638 | -5.2856 | 2006 | 7 | July-2006 | 0.26838 | 0.005064 | 2007
2006-07-16 | 0.13729 | -1.9856 | 274 | 2 | 19353 | 0.014158 | -4.2575 | 2006 | 7 | July-2006 | 0.13729 | 0.014158 | 2007
2006-07-17 | 0.0038237 | -5.5665 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2006 | 7 | July-2006 | 0.003824 | 5.2e-05 | 2007
2006-07-18 | 0.039219 | -3.2386 | 5 | 3 | 19353 | 0.00025836 | -8.2612 | 2006 | 7 | July-2006 | 0.039219 | 0.000258 | 2007
2006-07-19 | 0.36547 | -1.0066 | 48 | 1 | 19353 | 0.0024802 | -5.9994 | 2006 | 7 | July-2006 | 0.36547 | 0.00248 | 2007
2006-07-20 | 0.78463 | -0.24254 | 119 | 2 | 19353 | 0.0061489 | -5.0915 | 2006 | 7 | July-2006 | 0.78463 | 0.006149 | 2007
2006-07-21 | 1.1418 | 0.13264 | 183 | 2 | 19353 | 0.0094559 | -4.6611 | 2006 | 7 | July-2006 | 1.1418 | 0.009456 | 2007
2006-07-23 | 0.0040304 | -5.5139 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2006 | 7 | July-2006 | 0.00403 | 0.000103 | 2007
2006-07-24 | 0.30295 | -1.1942 | 42 | 4 | 19353 | 0.0021702 | -6.1329 | 2006 | 7 | July-2006 | 0.30295 | 0.00217 | 2007
2006-07-25 | 0.2272 | -1.4819 | 61 | 3 | 19353 | 0.003152 | -5.7597 | 2006 | 7 | July-2006 | 0.2272 | 0.003152 | 2007
2006-07-27 | 0.0074407 | -4.9008 | 12 | 1 | 19353 | 0.00062006 | -7.3857 | 2006 | 7 | July-2006 | 0.007441 | 0.00062 | 2007
2006-07-28 | 0.060766 | -2.8007 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2006 | 7 | July-2006 | 0.060766 | 0.000517 | 2007
2006-07-30 | 0.0011368 | -6.7796 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2006 | 7 | July-2006 | 0.001137 | 0.000103 | 2007
2006-07-31 | 0.025577 | -3.666 | 3 | 2 | 19353 | 0.00015501 | -8.772 | 2006 | 7 | July-2006 | 0.025577 | 0.000155 | 2007
2006-08-01 | 0.0056322 | -5.1793 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2006 | 8 | August-2006 | 0.005632 | 5.2e-05 | 2007
2006-08-02 | 0.023149 | -3.7658 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2006 | 8 | August-2006 | 0.023149 | 0.000207 | 2007
2006-08-03 | 0.0065623 | -5.0264 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2006 | 8 | August-2006 | 0.006562 | 5.2e-05 | 2007
2006-08-04 | 1.1599 | 0.14835 | 92 | 3 | 19353 | 0.0047538 | -5.3488 | 2006 | 8 | August-2006 | 1.1599 | 0.004754 | 2007
2006-08-05 | 0.0012918 | -6.6517 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2006 | 8 | August-2006 | 0.001292 | 0.000207 | 2007
2006-08-06 | 0.28027 | -1.272 | 27 | 2 | 19353 | 0.0013951 | -6.5748 | 2006 | 8 | August-2006 | 0.28027 | 0.001395 | 2007
2006-08-07 | 0.32879 | -1.1123 | 38 | 4 | 19353 | 0.0019635 | -6.233 | 2006 | 8 | August-2006 | 0.32879 | 0.001964 | 2007
2006-08-08 | 0.081021 | -2.513 | 36 | 3 | 19353 | 0.0018602 | -6.2871 | 2006 | 8 | August-2006 | 0.081021 | 0.00186 | 2007
2006-08-09 | 0.17207 | -1.7599 | 43 | 3 | 19353 | 0.0022219 | -6.1094 | 2006 | 8 | August-2006 | 0.17207 | 0.002222 | 2007
2006-08-10 | 0.40397 | -0.90642 | 43 | 5 | 19353 | 0.0022219 | -6.1094 | 2006 | 8 | August-2006 | 0.40397 | 0.002222 | 2007
2006-08-11 | 0.44515 | -0.80934 | 31 | 3 | 19353 | 0.0016018 | -6.4366 | 2006 | 8 | August-2006 | 0.44515 | 0.001602 | 2007
2006-08-13 | 2.0229 | 0.70455 | 174 | 1 | 19353 | 0.0089909 | -4.7115 | 2006 | 8 | August-2006 | 2.0229 | 0.008991 | 2007
2006-08-14 | 0.39885 | -0.91916 | 261 | 3 | 19353 | 0.013486 | -4.3061 | 2006 | 8 | August-2006 | 0.39885 | 0.013486 | 2007
2006-08-15 | 0.68852 | -0.37321 | 63 | 3 | 19353 | 0.0032553 | -5.7275 | 2006 | 8 | August-2006 | 0.68852 | 0.003255 | 2007
2006-08-16 | 0.24606 | -1.4022 | 53 | 3 | 19353 | 0.0027386 | -5.9003 | 2006 | 8 | August-2006 | 0.24606 | 0.002739 | 2007
2006-08-17 | 0.24249 | -1.4168 | 76 | 3 | 19353 | 0.003927 | -5.5399 | 2006 | 8 | August-2006 | 0.24249 | 0.003927 | 2007
2006-08-19 | 0.63013 | -0.46182 | 622 | 3 | 19353 | 0.03214 | -3.4377 | 2006 | 8 | August-2006 | 0.63014 | 0.03214 | 2007
2006-08-22 | 0.39343 | -0.93286 | 41 | 2 | 19353 | 0.0021185 | -6.157 | 2006 | 8 | August-2006 | 0.39343 | 0.002119 | 2007
2006-08-23 | 0.021185 | -3.8544 | 41 | 1 | 19353 | 0.0021185 | -6.157 | 2006 | 8 | August-2006 | 0.021185 | 0.002119 | 2007
2006-08-27 | 0.061179 | -2.7939 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2006 | 8 | August-2006 | 0.061179 | 0.000207 | 2007
2006-08-29 | 0.41694 | -0.87482 | 1943 | 2 | 19353 | 0.1004 | -2.2986 | 2006 | 8 | August-2006 | 0.41694 | 0.1004 | 2007
2006-08-30 | 0.31685 | -1.1493 | 82 | 3 | 19353 | 0.0042371 | -5.4639 | 2006 | 8 | August-2006 | 0.31685 | 0.004237 | 2007
2006-08-31 | 0.19594 | -1.63 | 12 | 3 | 19353 | 0.00062006 | -7.3857 | 2006 | 8 | August-2006 | 0.19594 | 0.00062 | 2007
2006-09-01 | 2.4944 | 0.91407 | 228 | 6 | 19353 | 0.011781 | -4.4413 | 2006 | 9 | September-2006 | 2.4944 | 0.011781 | 2007
2006-09-02 | 0.3215 | -1.1348 | 102 | 1 | 19353 | 0.0052705 | -5.2456 | 2006 | 9 | September-2006 | 0.3215 | 0.005271 | 2007
2006-09-03 | 0.11781 | -2.1387 | 19 | 1 | 19353 | 0.00098176 | -6.9262 | 2006 | 9 | September-2006 | 0.11781 | 0.000982 | 2007
2006-09-04 | 0.6244 | -0.47097 | 87 | 2 | 19353 | 0.0044954 | -5.4047 | 2006 | 9 | September-2006 | 0.6244 | 0.004495 | 2007
2006-09-05 | 0.51289 | -0.66769 | 122 | 2 | 19353 | 0.0063039 | -5.0666 | 2006 | 9 | September-2006 | 0.51289 | 0.006304 | 2007
2006-09-06 | 1.1904 | 0.17425 | 98 | 3 | 19353 | 0.0050638 | -5.2856 | 2006 | 9 | September-2006 | 1.1904 | 0.005064 | 2007
2006-09-07 | 0.38857 | -0.94528 | 20 | 1 | 19353 | 0.0010334 | -6.8749 | 2006 | 9 | September-2006 | 0.38857 | 0.001033 | 2007
2006-09-08 | 0.24885 | -1.3909 | 602 | 1 | 19353 | 0.031106 | -3.4703 | 2006 | 9 | September-2006 | 0.24885 | 0.031106 | 2007
2006-09-09 | 0.17083 | -1.7671 | 246 | 2 | 19353 | 0.012711 | -4.3653 | 2006 | 9 | September-2006 | 0.17083 | 0.012711 | 2007
2006-09-10 | 0.16235 | -1.818 | 95 | 1 | 19353 | 0.0049088 | -5.3167 | 2006 | 9 | September-2006 | 0.16235 | 0.004909 | 2007
2006-09-11 | 0.0043404 | -5.4398 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2006 | 9 | September-2006 | 0.00434 | 0.000103 | 2007
2006-09-13 | 0.43916 | -0.8229 | 140 | 2 | 19353 | 0.007234 | -4.929 | 2006 | 9 | September-2006 | 0.43916 | 0.007234 | 2007
2006-09-14 | 1.3589 | 0.30668 | 121 | 5 | 19353 | 0.0062523 | -5.0748 | 2006 | 9 | September-2006 | 1.3589 | 0.006252 | 2007
2006-09-15 | 0.52503 | -0.64429 | 73 | 4 | 19353 | 0.003772 | -5.5801 | 2006 | 9 | September-2006 | 0.52504 | 0.003772 | 2007
2006-09-16 | 0.017982 | -4.0184 | 6 | 1 | 19353 | 0.00031003 | -8.0788 | 2006 | 9 | September-2006 | 0.017982 | 0.00031 | 2007
2006-09-17 | 0.87909 | -0.12887 | 321 | 1 | 19353 | 0.016587 | -4.0992 | 2006 | 9 | September-2006 | 0.87909 | 0.016587 | 2007
2006-09-19 | 0.018963 | -3.9652 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2006 | 9 | September-2006 | 0.018963 | 0.000207 | 2007
2006-09-20 | 2.1437 | 0.76253 | 275 | 3 | 19353 | 0.01421 | -4.2538 | 2006 | 9 | September-2006 | 2.1437 | 0.01421 | 2007
2006-09-21 | 16.3412 | 2.7937 | 689 | 5 | 19353 | 0.035602 | -3.3354 | 2006 | 9 | September-2006 | 16.3412 | 0.035602 | 2007
2006-09-22 | 0.035447 | -3.3397 | 8 | 2 | 19353 | 0.00041337 | -7.7912 | 2006 | 9 | September-2006 | 0.035447 | 0.000413 | 2007
2006-09-25 | 0.14726 | -1.9155 | 15 | 1 | 19353 | 0.00077507 | -7.1626 | 2006 | 9 | September-2006 | 0.14726 | 0.000775 | 2007
2006-09-26 | 0.62182 | -0.47511 | 101 | 2 | 19353 | 0.0052188 | -5.2555 | 2006 | 9 | September-2006 | 0.62182 | 0.005219 | 2007
2006-09-27 | 0.15543 | -1.8616 | 33 | 4 | 19353 | 0.0017052 | -6.3741 | 2006 | 9 | September-2006 | 0.15543 | 0.001705 | 2007
2006-09-28 | 1.1823 | 0.1675 | 71 | 3 | 19353 | 0.0036687 | -5.6079 | 2006 | 9 | September-2006 | 1.1823 | 0.003669 | 2007
2006-09-29 | 0.5269 | -0.64075 | 106 | 2 | 19353 | 0.0054772 | -5.2072 | 2006 | 9 | September-2006 | 0.5269 | 0.005477 | 2007
2006-10-01 | 0.37886 | -0.9706 | 39 | 1 | 19353 | 0.0020152 | -6.207 | 2006 | 10 | October-2006 | 0.37886 | 0.002015 | 2007
2006-10-02 | 0.547 | -0.60332 | 859 | 4 | 19353 | 0.044386 | -3.1148 | 2006 | 10 | October-2006 | 0.547 | 0.044386 | 2007
2006-10-03 | 1.5347 | 0.42837 | 101 | 4 | 19353 | 0.0052188 | -5.2555 | 2006 | 10 | October-2006 | 1.5347 | 0.005219 | 2007
2006-10-04 | 1.092 | 0.087988 | 194 | 5 | 19353 | 0.010024 | -4.6027 | 2006 | 10 | October-2006 | 1.092 | 0.010024 | 2007
2006-10-05 | 1.056 | 0.054451 | 88 | 4 | 19353 | 0.0045471 | -5.3933 | 2006 | 10 | October-2006 | 1.056 | 0.004547 | 2007
2006-10-06 | 0.84917 | -0.1635 | 90 | 4 | 19353 | 0.0046504 | -5.3708 | 2006 | 10 | October-2006 | 0.84917 | 0.00465 | 2007
2006-10-07 | 0.12784 | -2.057 | 38 | 3 | 19353 | 0.0019635 | -6.233 | 2006 | 10 | October-2006 | 0.12784 | 0.001964 | 2007
2006-10-09 | 0.84106 | -0.17309 | 2012 | 3 | 19353 | 0.10396 | -2.2637 | 2006 | 10 | October-2006 | 0.84106 | 0.10396 | 2007
2006-10-10 | 3.2505 | 1.1788 | 771 | 10 | 19353 | 0.039839 | -3.2229 | 2006 | 10 | October-2006 | 3.2505 | 0.039839 | 2007
2006-10-11 | 1.4425 | 0.36635 | 160 | 2 | 19353 | 0.0082675 | -4.7954 | 2006 | 10 | October-2006 | 1.4425 | 0.008267 | 2007
2006-10-12 | 0.29148 | -1.2328 | 82 | 5 | 19353 | 0.0042371 | -5.4639 | 2006 | 10 | October-2006 | 0.29148 | 0.004237 | 2007
2006-10-13 | 0.17982 | -1.7158 | 24 | 1 | 19353 | 0.0012401 | -6.6925 | 2006 | 10 | October-2006 | 0.17982 | 0.00124 | 2007
2006-10-15 | 0.0015501 | -6.4694 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2006 | 10 | October-2006 | 0.00155 | 0.000155 | 2007
2006-10-16 | 0.011884 | -4.4325 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2006 | 10 | October-2006 | 0.011884 | 0.000103 | 2007
2006-10-17 | 0.45006 | -0.79838 | 62 | 3 | 19353 | 0.0032036 | -5.7435 | 2006 | 10 | October-2006 | 0.45006 | 0.003204 | 2007
2006-10-18 | 0.37844 | -0.97169 | 86 | 2 | 19353 | 0.0044438 | -5.4163 | 2006 | 10 | October-2006 | 0.37844 | 0.004444 | 2007
2006-10-19 | 0.58714 | -0.53248 | 39 | 4 | 19353 | 0.0020152 | -6.207 | 2006 | 10 | October-2006 | 0.58714 | 0.002015 | 2007
2006-10-20 | 0.76608 | -0.26647 | 78 | 3 | 19353 | 0.0040304 | -5.5139 | 2006 | 10 | October-2006 | 0.76608 | 0.00403 | 2007
2006-10-24 | 0.048675 | -3.0226 | 18 | 5 | 19353 | 0.00093009 | -6.9802 | 2006 | 10 | October-2006 | 0.048675 | 0.00093 | 2007
2006-10-25 | 0.32424 | -1.1263 | 25 | 1 | 19353 | 0.0012918 | -6.6517 | 2006 | 10 | October-2006 | 0.32424 | 0.001292 | 2007
2006-10-26 | 0.37281 | -0.98669 | 28 | 3 | 19353 | 0.0014468 | -6.5384 | 2006 | 10 | October-2006 | 0.37281 | 0.001447 | 2007
2006-10-27 | 0.093784 | -2.3668 | 22 | 3 | 19353 | 0.0011368 | -6.7796 | 2006 | 10 | October-2006 | 0.093784 | 0.001137 | 2007
2006-10-28 | 0.20204 | -1.5993 | 1955 | 1 | 19353 | 0.10102 | -2.2925 | 2006 | 10 | October-2006 | 0.20204 | 0.10102 | 2007
2006-10-29 | 1.9944 | 0.69035 | 440 | 3 | 19353 | 0.022735 | -3.7838 | 2006 | 10 | October-2006 | 1.9944 | 0.022735 | 2007
2006-10-30 | 1.0791 | 0.076136 | 328 | 8 | 19353 | 0.016948 | -4.0776 | 2006 | 10 | October-2006 | 1.0791 | 0.016948 | 2007
2006-10-31 | 0.96941 | -0.031067 | 116 | 6 | 19353 | 0.0059939 | -5.117 | 2006 | 10 | October-2006 | 0.96941 | 0.005994 | 2007
2006-11-01 | 0.18679 | -1.6778 | 43 | 1 | 19353 | 0.0022219 | -6.1094 | 2006 | 11 | November-2006 | 0.18679 | 0.002222 | 2007
2006-11-02 | 0.36811 | -0.99938 | 33 | 2 | 19353 | 0.0017052 | -6.3741 | 2006 | 11 | November-2006 | 0.36811 | 0.001705 | 2007
2006-11-03 | 0.040097 | -3.2165 | 13 | 2 | 19353 | 0.00067173 | -7.3057 | 2006 | 11 | November-2006 | 0.040097 | 0.000672 | 2007
2006-11-06 | 0.041647 | -3.1785 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2006 | 11 | November-2006 | 0.041647 | 0.000517 | 2007
2006-11-07 | 0.37689 | -0.9758 | 35 | 4 | 19353 | 0.0018085 | -6.3153 | 2006 | 11 | November-2006 | 0.37689 | 0.001809 | 2007
2006-11-08 | 1.4956 | 0.40255 | 417 | 7 | 19353 | 0.021547 | -3.8375 | 2006 | 11 | November-2006 | 1.4956 | 0.021547 | 2007
2006-11-09 | 0.34424 | -1.0664 | 259 | 4 | 19353 | 0.013383 | -4.3138 | 2006 | 11 | November-2006 | 0.34424 | 0.013383 | 2007
2006-11-10 | 0.10975 | -2.2095 | 10 | 3 | 19353 | 0.00051672 | -7.568 | 2006 | 11 | November-2006 | 0.10975 | 0.000517 | 2007
2006-11-12 | 0.03927 | -3.2373 | 190 | 1 | 19353 | 0.0098176 | -4.6236 | 2006 | 11 | November-2006 | 0.03927 | 0.009818 | 2007
2006-11-13 | 0.26187 | -1.3399 | 68 | 6 | 19353 | 0.0035137 | -5.6511 | 2006 | 11 | November-2006 | 0.26187 | 0.003514 | 2007
2006-11-14 | 0.011936 | -4.4282 | 7 | 1 | 19353 | 0.0003617 | -7.9247 | 2006 | 11 | November-2006 | 0.011936 | 0.000362 | 2007
2006-11-15 | 0.21687 | -1.5285 | 43 | 1 | 19353 | 0.0022219 | -6.1094 | 2006 | 11 | November-2006 | 0.21687 | 0.002222 | 2007
2006-11-16 | 0.17904 | -1.7201 | 23 | 5 | 19353 | 0.0011884 | -6.7351 | 2006 | 11 | November-2006 | 0.17904 | 0.001188 | 2007
2006-11-17 | 1.9249 | 0.65489 | 217 | 5 | 19353 | 0.011213 | -4.4907 | 2006 | 11 | November-2006 | 1.9249 | 0.011213 | 2007
2006-11-18 | 0.020255 | -3.8993 | 7 | 1 | 19353 | 0.0003617 | -7.9247 | 2006 | 11 | November-2006 | 0.020255 | 0.000362 | 2007
2006-11-20 | 0.03648 | -3.311 | 14 | 3 | 19353 | 0.0007234 | -7.2315 | 2006 | 11 | November-2006 | 0.03648 | 0.000723 | 2007
2006-11-21 | 0.24596 | -1.4026 | 48 | 3 | 19353 | 0.0024802 | -5.9994 | 2006 | 11 | November-2006 | 0.24596 | 0.00248 | 2007
2006-11-22 | 0.70237 | -0.35329 | 422 | 3 | 19353 | 0.021805 | -3.8256 | 2006 | 11 | November-2006 | 0.70237 | 0.021805 | 2007
2006-11-23 | 0.2751 | -1.2906 | 91 | 3 | 19353 | 0.0047021 | -5.3597 | 2006 | 11 | November-2006 | 0.2751 | 0.004702 | 2007
2006-11-24 | 0.88519 | -0.12196 | 385 | 8 | 19353 | 0.019894 | -3.9174 | 2006 | 11 | November-2006 | 0.88519 | 0.019894 | 2007
2006-11-27 | 4.5105 | 1.5064 | 630 | 4 | 19353 | 0.032553 | -3.4249 | 2006 | 11 | November-2006 | 4.5105 | 0.032553 | 2007
2006-11-28 | 0.032088 | -3.4393 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2006 | 11 | November-2006 | 0.032088 | 0.000207 | 2007
2006-11-29 | 0.4389 | -0.82349 | 71 | 2 | 19353 | 0.0036687 | -5.6079 | 2006 | 11 | November-2006 | 0.4389 | 0.003669 | 2007
2006-11-30 | 6.7269 | 1.9061 | 1076 | 16 | 19353 | 0.055599 | -2.8896 | 2006 | 11 | November-2006 | 6.7269 | 0.055599 | 2007
2006-12-01 | 0.052705 | -2.943 | 6 | 3 | 19353 | 0.00031003 | -8.0788 | 2006 | 12 | December-2006 | 0.052705 | 0.00031 | 2007
2006-12-03 | 0.0021702 | -6.1329 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2006 | 12 | December-2006 | 0.00217 | 0.000155 | 2007
2006-12-04 | 0.32992 | -1.1089 | 56 | 3 | 19353 | 0.0028936 | -5.8453 | 2006 | 12 | December-2006 | 0.32992 | 0.002894 | 2007
2006-12-05 | 0.98781 | -0.012269 | 71 | 5 | 19353 | 0.0036687 | -5.6079 | 2006 | 12 | December-2006 | 0.98781 | 0.003669 | 2007
2006-12-06 | 0.050638 | -2.9831 | 11 | 2 | 19353 | 0.00056839 | -7.4727 | 2006 | 12 | December-2006 | 0.050638 | 0.000568 | 2007
2006-12-07 | 0.26409 | -1.3315 | 98 | 4 | 19353 | 0.0050638 | -5.2856 | 2006 | 12 | December-2006 | 0.26409 | 0.005064 | 2007
2006-12-08 | 0.2751 | -1.2906 | 96 | 4 | 19353 | 0.0049605 | -5.3063 | 2006 | 12 | December-2006 | 0.2751 | 0.00496 | 2007
2006-12-09 | 0.44102 | -0.81867 | 52 | 1 | 19353 | 0.0026869 | -5.9194 | 2006 | 12 | December-2006 | 0.44102 | 0.002687 | 2007
2006-12-10 | 0.68434 | -0.3793 | 518 | 2 | 19353 | 0.026766 | -3.6206 | 2006 | 12 | December-2006 | 0.68434 | 0.026766 | 2007
2006-12-11 | 0.37452 | -0.98212 | 97 | 3 | 19353 | 0.0050121 | -5.2959 | 2006 | 12 | December-2006 | 0.37452 | 0.005012 | 2007
2006-12-12 | 1.1637 | 0.1516 | 252 | 2 | 19353 | 0.013021 | -4.3412 | 2006 | 12 | December-2006 | 1.1637 | 0.013021 | 2007
2006-12-13 | 0.18705 | -1.6764 | 30 | 2 | 19353 | 0.0015501 | -6.4694 | 2006 | 12 | December-2006 | 0.18705 | 0.00155 | 2007
2006-12-14 | 2.3662 | 0.86128 | 234 | 6 | 19353 | 0.012091 | -4.4153 | 2006 | 12 | December-2006 | 2.3662 | 0.012091 | 2007
2006-12-15 | 0.84157 | -0.17248 | 71 | 5 | 19353 | 0.0036687 | -5.6079 | 2006 | 12 | December-2006 | 0.84157 | 0.003669 | 2007
2006-12-17 | 0.056322 | -2.8767 | 10 | 1 | 19353 | 0.00051672 | -7.568 | 2006 | 12 | December-2006 | 0.056322 | 0.000517 | 2007
2006-12-18 | 2.1418 | 0.76164 | 165 | 3 | 19353 | 0.0085258 | -4.7647 | 2006 | 12 | December-2006 | 2.1418 | 0.008526 | 2007
2006-12-19 | 0.44804 | -0.80286 | 167 | 3 | 19353 | 0.0086292 | -4.7526 | 2006 | 12 | December-2006 | 0.44804 | 0.008629 | 2007
2006-12-20 | 1.1294 | 0.12167 | 1295 | 10 | 19353 | 0.066915 | -2.7043 | 2006 | 12 | December-2006 | 1.1294 | 0.066915 | 2007
2006-12-21 | 1.7941 | 0.58453 | 249 | 5 | 19353 | 0.012866 | -4.3531 | 2006 | 12 | December-2006 | 1.7941 | 0.012866 | 2007
2006-12-22 | 0.024699 | -3.701 | 8 | 4 | 19353 | 0.00041337 | -7.7912 | 2006 | 12 | December-2006 | 0.024699 | 0.000413 | 2007
2006-12-28 | 0.24322 | -1.4138 | 265 | 3 | 19353 | 0.013693 | -4.2909 | 2006 | 12 | December-2006 | 0.24322 | 0.013693 | 2007
2006-12-29 | 0.16566 | -1.7978 | 40 | 3 | 19353 | 0.0020669 | -6.1817 | 2006 | 12 | December-2006 | 0.16566 | 0.002067 | 2007
2006-12-31 | 0.21392 | -1.5422 | 392 | 5 | 19353 | 0.020255 | -3.8993 | 2006 | 12 | December-2006 | 0.21392 | 0.020255 | 2007
2007-01-01 | 0.85522 | -0.1564 | 165 | 2 | 19353 | 0.0085258 | -4.7647 | 2007 | 1 | January-2007 | 0.85522 | 0.008526 | 2007
2007-01-02 | 0.12029 | -2.1178 | 30 | 3 | 19353 | 0.0015501 | -6.4694 | 2007 | 1 | January-2007 | 0.12029 | 0.00155 | 2007
2007-01-03 | 0.52142 | -0.6512 | 62 | 3 | 19353 | 0.0032036 | -5.7435 | 2007 | 1 | January-2007 | 0.52142 | 0.003204 | 2007
2007-01-04 | 0.12505 | -2.0791 | 39 | 1 | 19353 | 0.0020152 | -6.207 | 2007 | 1 | January-2007 | 0.12504 | 0.002015 | 2007
2007-01-05 | 0.47197 | -0.75084 | 528 | 4 | 19353 | 0.027283 | -3.6015 | 2007 | 1 | January-2007 | 0.47197 | 0.027283 | 2007
2007-01-07 | 0.48494 | -0.72373 | 109 | 2 | 19353 | 0.0056322 | -5.1793 | 2007 | 1 | January-2007 | 0.48494 | 0.005632 | 2007
2007-01-08 | 0.82266 | -0.19521 | 115 | 5 | 19353 | 0.0059422 | -5.1257 | 2007 | 1 | January-2007 | 0.82266 | 0.005942 | 2007
2007-01-09 | 0.53077 | -0.63343 | 115 | 5 | 19353 | 0.0059422 | -5.1257 | 2007 | 1 | January-2007 | 0.53077 | 0.005942 | 2007
2007-01-10 | 0.46778 | -0.75975 | 35 | 1 | 19353 | 0.0018085 | -6.3153 | 2007 | 1 | January-2007 | 0.46778 | 0.001809 | 2007
2007-01-11 | 3.0288 | 1.1082 | 1236 | 4 | 19353 | 0.063866 | -2.751 | 2007 | 1 | January-2007 | 3.0288 | 0.063866 | 2007
2007-01-12 | 0.49713 | -0.6989 | 80 | 3 | 19353 | 0.0041337 | -5.4886 | 2007 | 1 | January-2007 | 0.49713 | 0.004134 | 2007
2007-01-13 | 0.85 | -0.16252 | 116 | 1 | 19353 | 0.0059939 | -5.117 | 2007 | 1 | January-2007 | 0.85 | 0.005994 | 2007
2007-01-14 | 1.0176 | 0.017467 | 106 | 1 | 19353 | 0.0054772 | -5.2072 | 2007 | 1 | January-2007 | 1.0176 | 0.005477 | 2007
2007-01-15 | 0.068051 | -2.6875 | 17 | 4 | 19353 | 0.00087842 | -7.0374 | 2007 | 1 | January-2007 | 0.068051 | 0.000878 | 2007
2007-01-16 | 0.49574 | -0.70171 | 90 | 2 | 19353 | 0.0046504 | -5.3708 | 2007 | 1 | January-2007 | 0.49574 | 0.00465 | 2007
2007-01-17 | 0.83398 | -0.18155 | 81 | 5 | 19353 | 0.0041854 | -5.4762 | 2007 | 1 | January-2007 | 0.83398 | 0.004185 | 2007
2007-01-18 | 0.0013951 | -6.5748 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2007 | 1 | January-2007 | 0.001395 | 0.000155 | 2007
2007-01-19 | 0.0046504 | -5.3708 | 2 | 2 | 19353 | 0.00010334 | -9.1775 | 2007 | 1 | January-2007 | 0.00465 | 0.000103 | 2007
2007-01-21 | 0.97804 | -0.022205 | 114 | 2 | 19353 | 0.0058906 | -5.1344 | 2007 | 1 | January-2007 | 0.97804 | 0.005891 | 2007
2007-01-24 | 0.28543 | -1.2537 | 32 | 3 | 19353 | 0.0016535 | -6.4049 | 2007 | 1 | January-2007 | 0.28543 | 0.001653 | 2007
2007-01-25 | 0.89211 | -0.11417 | 235 | 4 | 19353 | 0.012143 | -4.411 | 2007 | 1 | January-2007 | 0.89211 | 0.012143 | 2007
2007-01-26 | 0.48447 | -0.72469 | 38 | 3 | 19353 | 0.0019635 | -6.233 | 2007 | 1 | January-2007 | 0.48447 | 0.001964 | 2007
2007-01-27 | 0.10851 | -2.2209 | 35 | 1 | 19353 | 0.0018085 | -6.3153 | 2007 | 1 | January-2007 | 0.10851 | 0.001809 | 2007
2007-01-28 | 0.0012401 | -6.6925 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2007 | 1 | January-2007 | 0.00124 | 0.000155 | 2007
2007-01-30 | 0.068723 | -2.6777 | 14 | 1 | 19353 | 0.0007234 | -7.2315 | 2007 | 1 | January-2007 | 0.068723 | 0.000723 | 2007
2007-01-31 | 0.77228 | -0.2584 | 150 | 2 | 19353 | 0.0077507 | -4.86 | 2007 | 1 | January-2007 | 0.77228 | 0.007751 | 2007
2007-02-01 | 0.20364 | -1.5914 | 56 | 5 | 19353 | 0.0028936 | -5.8453 | 2007 | 2 | February-2007 | 0.20364 | 0.002894 | 2007
2007-02-02 | 0.31623 | -1.1513 | 72 | 1 | 19353 | 0.0037204 | -5.5939 | 2007 | 2 | February-2007 | 0.31623 | 0.00372 | 2007
2007-02-04 | 1.7819 | 0.57768 | 259 | 1 | 19353 | 0.013383 | -4.3138 | 2007 | 2 | February-2007 | 1.7819 | 0.013383 | 2007
2007-02-05 | 0.66863 | -0.40252 | 71 | 1 | 19353 | 0.0036687 | -5.6079 | 2007 | 2 | February-2007 | 0.66863 | 0.003669 | 2007
2007-02-06 | 1.2136 | 0.1936 | 203 | 1 | 19353 | 0.010489 | -4.5574 | 2007 | 2 | February-2007 | 1.2136 | 0.010489 | 2007
2007-02-07 | 0.25531 | -1.3653 | 45 | 4 | 19353 | 0.0023252 | -6.0639 | 2007 | 2 | February-2007 | 0.25531 | 0.002325 | 2007
2007-02-08 | 0.37942 | -0.9691 | 14 | 1 | 19353 | 0.0007234 | -7.2315 | 2007 | 2 | February-2007 | 0.37942 | 0.000723 | 2007
2007-02-09 | 1.6223 | 0.48386 | 308 | 7 | 19353 | 0.015915 | -4.1405 | 2007 | 2 | February-2007 | 1.6223 | 0.015915 | 2007
2007-02-12 | 0.87764 | -0.13052 | 353 | 5 | 19353 | 0.01824 | -4.0041 | 2007 | 2 | February-2007 | 0.87764 | 0.01824 | 2007
2007-02-13 | 0.0099726 | -4.6079 | 3 | 2 | 19353 | 0.00015501 | -8.772 | 2007 | 2 | February-2007 | 0.009973 | 0.000155 | 2007
2007-02-14 | 0.99623 | -0.0037792 | 657 | 6 | 19353 | 0.033948 | -3.3829 | 2007 | 2 | February-2007 | 0.99623 | 0.033948 | 2007
2007-02-15 | 0.92105 | -0.082245 | 68 | 4 | 19353 | 0.0035137 | -5.6511 | 2007 | 2 | February-2007 | 0.92105 | 0.003514 | 2007
2007-02-16 | 0.58017 | -0.54444 | 36 | 3 | 19353 | 0.0018602 | -6.2871 | 2007 | 2 | February-2007 | 0.58017 | 0.00186 | 2007
2007-02-19 | 0.75957 | -0.275 | 105 | 1 | 19353 | 0.0054255 | -5.2166 | 2007 | 2 | February-2007 | 0.75957 | 0.005426 | 2007
2007-02-20 | 1.5691 | 0.45048 | 75 | 4 | 19353 | 0.0038754 | -5.5531 | 2007 | 2 | February-2007 | 1.5691 | 0.003875 | 2007
2007-02-22 | 0.36072 | -1.0197 | 39 | 1 | 19353 | 0.0020152 | -6.207 | 2007 | 2 | February-2007 | 0.36072 | 0.002015 | 2007
2007-02-23 | 0.090219 | -2.4055 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2007 | 2 | February-2007 | 0.090219 | 0.000362 | 2007
2007-02-26 | 2.7411 | 1.0084 | 525 | 4 | 19353 | 0.027128 | -3.6072 | 2007 | 2 | February-2007 | 2.7411 | 0.027128 | 2007
2007-02-27 | 0.95014 | -0.051149 | 103 | 5 | 19353 | 0.0053222 | -5.2359 | 2007 | 2 | February-2007 | 0.95014 | 0.005322 | 2007
2007-02-28 | 3.4395 | 1.2353 | 2267 | 5 | 19353 | 0.11714 | -2.1444 | 2007 | 2 | February-2007 | 3.4395 | 0.11714 | 2007
2007-03-01 | 0.0050121 | -5.2959 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2007 | 3 | March-2007 | 0.005012 | 5.2e-05 | 2007
2007-03-02 | 0.43978 | -0.82149 | 30 | 3 | 19353 | 0.0015501 | -6.4694 | 2007 | 3 | March-2007 | 0.43978 | 0.00155 | 2007
2007-03-03 | 0.0013951 | -6.5748 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2007 | 3 | March-2007 | 0.001395 | 0.000155 | 2007
2007-03-05 | 2.4337 | 0.8894 | 523 | 2 | 19353 | 0.027024 | -3.611 | 2007 | 3 | March-2007 | 2.4337 | 0.027024 | 2007
2007-03-06 | 0.14184 | -1.9531 | 9 | 1 | 19353 | 0.00046504 | -7.6734 | 2007 | 3 | March-2007 | 0.14184 | 0.000465 | 2007
2007-03-07 | 0.43192 | -0.83951 | 446 | 3 | 19353 | 0.023046 | -3.7703 | 2007 | 3 | March-2007 | 0.43192 | 0.023046 | 2007
2007-03-08 | 0.10892 | -2.2171 | 21 | 2 | 19353 | 0.0010851 | -6.8261 | 2007 | 3 | March-2007 | 0.10892 | 0.001085 | 2007
2007-03-09 | 0.053893 | -2.9207 | 18 | 3 | 19353 | 0.00093009 | -6.9802 | 2007 | 3 | March-2007 | 0.053893 | 0.00093 | 2007
2007-03-11 | 1.6055 | 0.47343 | 259 | 1 | 19353 | 0.013383 | -4.3138 | 2007 | 3 | March-2007 | 1.6055 | 0.013383 | 2007
2007-03-12 | 0.82855 | -0.18807 | 124 | 3 | 19353 | 0.0064073 | -5.0503 | 2007 | 3 | March-2007 | 0.82855 | 0.006407 | 2007
2007-03-13 | 1.4171 | 0.34861 | 676 | 8 | 19353 | 0.03493 | -3.3544 | 2007 | 3 | March-2007 | 1.4171 | 0.03493 | 2007
2007-03-14 | 24.6937 | 3.2065 | 5460 | 31 | 19353 | 0.28213 | -1.2654 | 2007 | 3 | March-2007 | 21.6659 | 0.26757 | 2007
2007-03-15 | 2.1404 | 0.76101 | 571 | 32 | 19353 | 0.029504 | -3.5232 | 2007 | 3 | March-2007 | 2.1404 | 0.029504 | 2007
2007-03-16 | 0.67964 | -0.3862 | 208 | 16 | 19353 | 0.010748 | -4.5331 | 2007 | 3 | March-2007 | 0.67964 | 0.010748 | 2007
2007-03-17 | 0.02103 | -3.8618 | 4 | 3 | 19353 | 0.00020669 | -8.4843 | 2007 | 3 | March-2007 | 0.02103 | 0.000207 | 2007
2007-03-18 | 0.30373 | -1.1916 | 119 | 2 | 19353 | 0.0061489 | -5.0915 | 2007 | 3 | March-2007 | 0.30373 | 0.006149 | 2007
2007-03-19 | 0.35793 | -1.0274 | 305 | 8 | 19353 | 0.01576 | -4.1503 | 2007 | 3 | March-2007 | 0.35793 | 0.01576 | 2007
2007-03-20 | 1.3695 | 0.31445 | 514 | 7 | 19353 | 0.026559 | -3.6284 | 2007 | 3 | March-2007 | 1.3695 | 0.026559 | 2007
2007-03-21 | 3.2457 | 1.1773 | 304 | 5 | 19353 | 0.015708 | -4.1536 | 2007 | 3 | March-2007 | 3.2457 | 0.015708 | 2007
2007-03-22 | 1.4654 | 0.38213 | 1580 | 2 | 19353 | 0.081641 | -2.5054 | 2007 | 3 | March-2007 | 1.4654 | 0.081641 | 2007
2007-03-23 | 0.24601 | -1.4024 | 20 | 5 | 19353 | 0.0010334 | -6.8749 | 2007 | 3 | March-2007 | 0.24601 | 0.001033 | 2007
2007-03-25 | 0.26001 | -1.347 | 17 | 1 | 19353 | 0.00087842 | -7.0374 | 2007 | 3 | March-2007 | 0.26001 | 0.000878 | 2007
2007-03-26 | 0.54694 | -0.60341 | 115 | 3 | 19353 | 0.0059422 | -5.1257 | 2007 | 3 | March-2007 | 0.54694 | 0.005942 | 2007
2007-03-27 | 2.0123 | 0.69928 | 151 | 2 | 19353 | 0.0078024 | -4.8533 | 2007 | 3 | March-2007 | 2.0123 | 0.007802 | 2007
2007-03-28 | 2.0858 | 0.73517 | 243 | 3 | 19353 | 0.012556 | -4.3775 | 2007 | 3 | March-2007 | 2.0858 | 0.012556 | 2007
2007-03-29 | 6.3951 | 1.8555 | 654 | 9 | 19353 | 0.033793 | -3.3875 | 2007 | 3 | March-2007 | 6.3951 | 0.033793 | 2007
2007-03-30 | 0.21371 | -1.5431 | 15 | 3 | 19353 | 0.00077507 | -7.1626 | 2007 | 3 | March-2007 | 0.21371 | 0.000775 | 2007
2007-03-31 | 0.35256 | -1.0425 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2007 | 3 | March-2007 | 0.35256 | 0.001447 | 2007
2007-04-02 | 0.081641 | -2.5054 | 9 | 2 | 19353 | 0.00046504 | -7.6734 | 2007 | 4 | April-2007 | 0.081641 | 0.000465 | 2008
2007-04-03 | 0.28368 | -1.2599 | 55 | 3 | 19353 | 0.0028419 | -5.8633 | 2007 | 4 | April-2007 | 0.28368 | 0.002842 | 2008
2007-04-05 | 0.29143 | -1.233 | 65 | 3 | 19353 | 0.0033587 | -5.6962 | 2007 | 4 | April-2007 | 0.29143 | 0.003359 | 2008
2007-04-06 | 0.12753 | -2.0594 | 33 | 1 | 19353 | 0.0017052 | -6.3741 | 2007 | 4 | April-2007 | 0.12752 | 0.001705 | 2008
2007-04-08 | 0.059836 | -2.8162 | 84 | 2 | 19353 | 0.0043404 | -5.4398 | 2007 | 4 | April-2007 | 0.059836 | 0.00434 | 2008
2007-04-10 | 0.17987 | -1.7155 | 27 | 2 | 19353 | 0.0013951 | -6.5748 | 2007 | 4 | April-2007 | 0.17987 | 0.001395 | 2008
2007-04-11 | 0.098693 | -2.3157 | 10 | 1 | 19353 | 0.00051672 | -7.568 | 2007 | 4 | April-2007 | 0.098693 | 0.000517 | 2008
2007-04-12 | 0.70025 | -0.35631 | 1021 | 5 | 19353 | 0.052757 | -2.9421 | 2007 | 4 | April-2007 | 0.70025 | 0.052757 | 2008
2007-04-13 | 3.0024 | 1.0994 | 1157 | 8 | 19353 | 0.059784 | -2.817 | 2007 | 4 | April-2007 | 3.0024 | 0.059784 | 2008
2007-04-15 | 0.16886 | -1.7787 | 19 | 1 | 19353 | 0.00098176 | -6.9262 | 2007 | 4 | April-2007 | 0.16886 | 0.000982 | 2008
2007-04-16 | 1.0121 | 0.012019 | 77 | 2 | 19353 | 0.0039787 | -5.5268 | 2007 | 4 | April-2007 | 1.0121 | 0.003979 | 2008
2007-04-17 | 0.39431 | -0.93063 | 62 | 3 | 19353 | 0.0032036 | -5.7435 | 2007 | 4 | April-2007 | 0.39431 | 0.003204 | 2008
2007-04-18 | 0.16566 | -1.7978 | 31 | 2 | 19353 | 0.0016018 | -6.4366 | 2007 | 4 | April-2007 | 0.16566 | 0.001602 | 2008
2007-04-19 | 0.12262 | -2.0987 | 55 | 4 | 19353 | 0.0028419 | -5.8633 | 2007 | 4 | April-2007 | 0.12262 | 0.002842 | 2008
2007-04-20 | 0.5348 | -0.62586 | 69 | 2 | 19353 | 0.0035653 | -5.6365 | 2007 | 4 | April-2007 | 0.5348 | 0.003565 | 2008
2007-04-22 | 0.34775 | -1.0563 | 673 | 1 | 19353 | 0.034775 | -3.3589 | 2007 | 4 | April-2007 | 0.34775 | 0.034775 | 2008
2007-04-23 | 0.36945 | -0.99574 | 94 | 5 | 19353 | 0.0048571 | -5.3273 | 2007 | 4 | April-2007 | 0.36945 | 0.004857 | 2008
2007-04-24 | 0.022167 | -3.8091 | 6 | 2 | 19353 | 0.00031003 | -8.0788 | 2007 | 4 | April-2007 | 0.022167 | 0.00031 | 2008
2007-04-26 | 0.45492 | -0.78764 | 40 | 2 | 19353 | 0.0020669 | -6.1817 | 2007 | 4 | April-2007 | 0.45492 | 0.002067 | 2008
2007-04-27 | 0.067845 | -2.6905 | 16 | 3 | 19353 | 0.00082675 | -7.098 | 2007 | 4 | April-2007 | 0.067845 | 0.000827 | 2008
2007-04-28 | 0.72599 | -0.32023 | 73 | 3 | 19353 | 0.003772 | -5.5801 | 2007 | 4 | April-2007 | 0.72599 | 0.003772 | 2008
2007-04-29 | 0.0012401 | -6.6925 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2007 | 4 | April-2007 | 0.00124 | 0.000155 | 2008
2007-04-30 | 0.64946 | -0.43161 | 57 | 3 | 19353 | 0.0029453 | -5.8276 | 2007 | 4 | April-2007 | 0.64946 | 0.002945 | 2008
2007-05-01 | 0.2196 | -1.5159 | 85 | 1 | 19353 | 0.0043921 | -5.428 | 2007 | 5 | May-2007 | 0.2196 | 0.004392 | 2008
2007-05-02 | 0.18524 | -1.6861 | 73 | 3 | 19353 | 0.003772 | -5.5801 | 2007 | 5 | May-2007 | 0.18524 | 0.003772 | 2008
2007-05-03 | 0.32062 | -1.1375 | 67 | 4 | 19353 | 0.003462 | -5.6659 | 2007 | 5 | May-2007 | 0.32062 | 0.003462 | 2008
2007-05-04 | 0.19909 | -1.614 | 54 | 3 | 19353 | 0.0027903 | -5.8816 | 2007 | 5 | May-2007 | 0.19909 | 0.00279 | 2008
2007-05-06 | 0.30305 | -1.1938 | 66 | 2 | 19353 | 0.0034103 | -5.6809 | 2007 | 5 | May-2007 | 0.30305 | 0.00341 | 2008
2007-05-07 | 0.39503 | -0.9288 | 37 | 3 | 19353 | 0.0019118 | -6.2597 | 2007 | 5 | May-2007 | 0.39503 | 0.001912 | 2008
2007-05-08 | 0.029504 | -3.5232 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2007 | 5 | May-2007 | 0.029504 | 0.000517 | 2008
2007-05-09 | 0.16282 | -1.8151 | 35 | 3 | 19353 | 0.0018085 | -6.3153 | 2007 | 5 | May-2007 | 0.16282 | 0.001809 | 2008
2007-05-10 | 2.1692 | 0.77437 | 1139 | 3 | 19353 | 0.058854 | -2.8327 | 2007 | 5 | May-2007 | 2.1692 | 0.058854 | 2008
2007-05-11 | 0.13052 | -2.0362 | 17 | 2 | 19353 | 0.00087842 | -7.0374 | 2007 | 5 | May-2007 | 0.13052 | 0.000878 | 2008
2007-05-12 | 2.0324 | 0.70922 | 655 | 2 | 19353 | 0.033845 | -3.386 | 2007 | 5 | May-2007 | 2.0324 | 0.033845 | 2008
2007-05-14 | 1.7282 | 0.54708 | 1932 | 2 | 19353 | 0.099829 | -2.3043 | 2007 | 5 | May-2007 | 1.7282 | 0.099829 | 2008
2007-05-15 | 0.38883 | -0.94462 | 29 | 2 | 19353 | 0.0014985 | -6.5033 | 2007 | 5 | May-2007 | 0.38883 | 0.001498 | 2008
2007-05-16 | 1.3975 | 0.33465 | 179 | 5 | 19353 | 0.0092492 | -4.6832 | 2007 | 5 | May-2007 | 1.3975 | 0.009249 | 2008
2007-05-17 | 0.16587 | -1.7966 | 14 | 3 | 19353 | 0.0007234 | -7.2315 | 2007 | 5 | May-2007 | 0.16587 | 0.000723 | 2008
2007-05-18 | 0.065468 | -2.7262 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2007 | 5 | May-2007 | 0.065468 | 0.000258 | 2008
2007-05-20 | 0.013021 | -4.3412 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2007 | 5 | May-2007 | 0.013021 | 0.000103 | 2008
2007-05-21 | 1.7551 | 0.56251 | 183 | 3 | 19353 | 0.0094559 | -4.6611 | 2007 | 5 | May-2007 | 1.7551 | 0.009456 | 2008
2007-05-22 | 0.27908 | -1.2763 | 23 | 3 | 19353 | 0.0011884 | -6.7351 | 2007 | 5 | May-2007 | 0.27908 | 0.001188 | 2008
2007-05-23 | 0.28709 | -1.248 | 30 | 4 | 19353 | 0.0015501 | -6.4694 | 2007 | 5 | May-2007 | 0.28709 | 0.00155 | 2008
2007-05-24 | 0.099623 | -2.3064 | 7 | 3 | 19353 | 0.0003617 | -7.9247 | 2007 | 5 | May-2007 | 0.099623 | 0.000362 | 2008
2007-05-25 | 0.096419 | -2.3391 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2007 | 5 | May-2007 | 0.096419 | 0.000362 | 2008
2007-05-26 | 0.043404 | -3.1372 | 105 | 1 | 19353 | 0.0054255 | -5.2166 | 2007 | 5 | May-2007 | 0.043404 | 0.005426 | 2008
2007-05-28 | 0.074097 | -2.6024 | 11 | 2 | 19353 | 0.00056839 | -7.4727 | 2007 | 5 | May-2007 | 0.074097 | 0.000568 | 2008
2007-05-29 | 0.41229 | -0.88603 | 32 | 3 | 19353 | 0.0016535 | -6.4049 | 2007 | 5 | May-2007 | 0.41229 | 0.001653 | 2008
2007-05-30 | 0.40257 | -0.90988 | 43 | 2 | 19353 | 0.0022219 | -6.1094 | 2007 | 5 | May-2007 | 0.40257 | 0.002222 | 2008
2007-05-31 | 0.032708 | -3.4201 | 108 | 2 | 19353 | 0.0055805 | -5.1885 | 2007 | 5 | May-2007 | 0.032708 | 0.005581 | 2008
2007-06-01 | 1.2439 | 0.21828 | 75 | 3 | 19353 | 0.0038754 | -5.5531 | 2007 | 6 | June-2007 | 1.2439 | 0.003875 | 2008
2007-06-04 | 0.051103 | -2.9739 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2007 | 6 | June-2007 | 0.051103 | 0.000362 | 2008
2007-06-05 | 0.32589 | -1.1212 | 192 | 7 | 19353 | 0.0099209 | -4.6131 | 2007 | 6 | June-2007 | 0.32589 | 0.009921 | 2008
2007-06-06 | 0.022529 | -3.793 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2007 | 6 | June-2007 | 0.022529 | 0.000103 | 2008
2007-06-07 | 0.76479 | -0.26815 | 353 | 6 | 19353 | 0.01824 | -4.0041 | 2007 | 6 | June-2007 | 0.76479 | 0.01824 | 2008
2007-06-08 | 0.82716 | -0.18976 | 138 | 4 | 19353 | 0.0071307 | -4.9433 | 2007 | 6 | June-2007 | 0.82716 | 0.007131 | 2008
2007-06-09 | 0.0064073 | -5.0503 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2007 | 6 | June-2007 | 0.006407 | 5.2e-05 | 2008
2007-06-10 | 0.035808 | -3.3296 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2007 | 6 | June-2007 | 0.035808 | 0.000362 | 2008
2007-06-11 | 1.3184 | 0.27642 | 105 | 1 | 19353 | 0.0054255 | -5.2166 | 2007 | 6 | June-2007 | 1.3184 | 0.005426 | 2008
2007-06-12 | 3.7681 | 1.3266 | 220 | 5 | 19353 | 0.011368 | -4.477 | 2007 | 6 | June-2007 | 3.7681 | 0.011368 | 2008
2007-06-13 | 0.11425 | -2.1694 | 25 | 2 | 19353 | 0.0012918 | -6.6517 | 2007 | 6 | June-2007 | 0.11425 | 0.001292 | 2008
2007-06-14 | 1.6979 | 0.52941 | 84 | 4 | 19353 | 0.0043404 | -5.4398 | 2007 | 6 | June-2007 | 1.6979 | 0.00434 | 2008
2007-06-15 | 0.064228 | -2.7453 | 7 | 3 | 19353 | 0.0003617 | -7.9247 | 2007 | 6 | June-2007 | 0.064228 | 0.000362 | 2008
2007-06-17 | 0.007234 | -4.929 | 5 | 1 | 19353 | 0.00025836 | -8.2612 | 2007 | 6 | June-2007 | 0.007234 | 0.000258 | 2008
2007-06-19 | 0.0032036 | -5.7435 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2007 | 6 | June-2007 | 0.003204 | 5.2e-05 | 2008
2007-06-20 | 0.93391 | -0.068373 | 1209 | 6 | 19353 | 0.062471 | -2.7731 | 2007 | 6 | June-2007 | 0.93391 | 0.062471 | 2008
2007-06-21 | 0.92249 | -0.080676 | 48 | 5 | 19353 | 0.0024802 | -5.9994 | 2007 | 6 | June-2007 | 0.92249 | 0.00248 | 2008
2007-06-22 | 0.34486 | -1.0646 | 381 | 12 | 19353 | 0.019687 | -3.9278 | 2007 | 6 | June-2007 | 0.34486 | 0.019687 | 2008
2007-06-23 | 1.431 | 0.3584 | 887 | 8 | 19353 | 0.045833 | -3.0828 | 2007 | 6 | June-2007 | 1.431 | 0.045833 | 2008
2007-06-25 | 0.0053738 | -5.2262 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2007 | 6 | June-2007 | 0.005374 | 5.2e-05 | 2008
2007-06-26 | 0.19367 | -1.6416 | 32 | 4 | 19353 | 0.0016535 | -6.4049 | 2007 | 6 | June-2007 | 0.19367 | 0.001653 | 2008
2007-06-27 | 0.43993 | -0.82114 | 33 | 1 | 19353 | 0.0017052 | -6.3741 | 2007 | 6 | June-2007 | 0.43993 | 0.001705 | 2008
2007-06-28 | 0.18808 | -1.6709 | 20 | 1 | 19353 | 0.0010334 | -6.8749 | 2007 | 6 | June-2007 | 0.18809 | 0.001033 | 2008
2007-06-29 | 2.6918 | 0.99022 | 51 | 3 | 19353 | 0.0026353 | -5.9388 | 2007 | 6 | June-2007 | 2.6918 | 0.002635 | 2008
2007-06-30 | 0.042784 | -3.1516 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2007 | 6 | June-2007 | 0.042784 | 0.000207 | 2008
2007-07-02 | 0.067173 | -2.7005 | 23 | 2 | 19353 | 0.0011884 | -6.7351 | 2007 | 7 | July-2007 | 0.067173 | 0.001188 | 2008
2007-07-03 | 0.2457 | -1.4037 | 269 | 3 | 19353 | 0.0139 | -4.2759 | 2007 | 7 | July-2007 | 0.2457 | 0.0139 | 2008
2007-07-04 | 0.84695 | -0.16612 | 144 | 2 | 19353 | 0.0074407 | -4.9008 | 2007 | 7 | July-2007 | 0.84695 | 0.007441 | 2008
2007-07-05 | 1.8399 | 0.60969 | 150 | 5 | 19353 | 0.0077507 | -4.86 | 2007 | 7 | July-2007 | 1.8399 | 0.007751 | 2008
2007-07-06 | 2.1802 | 0.77943 | 160 | 11 | 19353 | 0.0082675 | -4.7954 | 2007 | 7 | July-2007 | 2.1802 | 0.008267 | 2008
2007-07-07 | 0.03028 | -3.4973 | 242 | 2 | 19353 | 0.012505 | -4.3817 | 2007 | 7 | July-2007 | 0.03028 | 0.012505 | 2008
2007-07-09 | 0.13714 | -1.9868 | 20 | 6 | 19353 | 0.0010334 | -6.8749 | 2007 | 7 | July-2007 | 0.13714 | 0.001033 | 2008
2007-07-10 | 20.7271 | 3.0314 | 2425 | 23 | 19353 | 0.1253 | -2.077 | 2007 | 7 | July-2007 | 20.7271 | 0.1253 | 2008
2007-07-11 | 3.549 | 1.2667 | 497 | 29 | 19353 | 0.025681 | -3.662 | 2007 | 7 | July-2007 | 3.549 | 0.025681 | 2008
2007-07-12 | 0.51883 | -0.65617 | 88 | 8 | 19353 | 0.0045471 | -5.3933 | 2007 | 7 | July-2007 | 0.51883 | 0.004547 | 2008
2007-07-13 | 2.1366 | 0.7592 | 113 | 4 | 19353 | 0.0058389 | -5.1432 | 2007 | 7 | July-2007 | 2.1366 | 0.005839 | 2008
2007-07-15 | 0.18137 | -1.7072 | 27 | 1 | 19353 | 0.0013951 | -6.5748 | 2007 | 7 | July-2007 | 0.18137 | 0.001395 | 2008
2007-07-16 | 0.28326 | -1.2614 | 61 | 5 | 19353 | 0.003152 | -5.7597 | 2007 | 7 | July-2007 | 0.28326 | 0.003152 | 2008
2007-07-17 | 0.033225 | -3.4045 | 27 | 2 | 19353 | 0.0013951 | -6.5748 | 2007 | 7 | July-2007 | 0.033225 | 0.001395 | 2008
2007-07-18 | 0.7821 | -0.24577 | 60 | 4 | 19353 | 0.0031003 | -5.7763 | 2007 | 7 | July-2007 | 0.7821 | 0.0031 | 2008
2007-07-19 | 4.355 | 1.4713 | 222 | 4 | 19353 | 0.011471 | -4.4679 | 2007 | 7 | July-2007 | 4.355 | 0.011471 | 2008
2007-07-20 | 0.15915 | -1.8379 | 28 | 1 | 19353 | 0.0014468 | -6.5384 | 2007 | 7 | July-2007 | 0.15915 | 0.001447 | 2008
2007-07-22 | 0.2875 | -1.2465 | 52 | 1 | 19353 | 0.0026869 | -5.9194 | 2007 | 7 | July-2007 | 0.2875 | 0.002687 | 2008
2007-07-23 | 0.10706 | -2.2343 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2007 | 7 | July-2007 | 0.10706 | 0.001447 | 2008
2007-07-24 | 0.76293 | -0.27059 | 65 | 4 | 19353 | 0.0033587 | -5.6962 | 2007 | 7 | July-2007 | 0.76293 | 0.003359 | 2008
2007-07-25 | 0.73317 | -0.31038 | 215 | 6 | 19353 | 0.011109 | -4.5 | 2007 | 7 | July-2007 | 0.73317 | 0.011109 | 2008
2007-07-27 | 0.20565 | -1.5816 | 31 | 2 | 19353 | 0.0016018 | -6.4366 | 2007 | 7 | July-2007 | 0.20565 | 0.001602 | 2008
2007-07-29 | 0.079058 | -2.5376 | 18 | 1 | 19353 | 0.00093009 | -6.9802 | 2007 | 7 | July-2007 | 0.079058 | 0.00093 | 2008
2007-07-30 | 0.029246 | -3.532 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2007 | 7 | July-2007 | 0.029246 | 0.000207 | 2008
2007-07-31 | 0.040459 | -3.2075 | 9 | 1 | 19353 | 0.00046504 | -7.6734 | 2007 | 7 | July-2007 | 0.040459 | 0.000465 | 2008
2007-08-01 | 0.055134 | -2.898 | 50 | 4 | 19353 | 0.0025836 | -5.9586 | 2007 | 8 | August-2007 | 0.055134 | 0.002584 | 2008
2007-08-02 | 0.079574 | -2.5311 | 10 | 3 | 19353 | 0.00051672 | -7.568 | 2007 | 8 | August-2007 | 0.079574 | 0.000517 | 2008
2007-08-03 | 3.0575 | 1.1176 | 240 | 4 | 19353 | 0.012401 | -4.39 | 2007 | 8 | August-2007 | 3.0575 | 0.012401 | 2008
2007-08-05 | 0.061954 | -2.7814 | 11 | 1 | 19353 | 0.00056839 | -7.4727 | 2007 | 8 | August-2007 | 0.061954 | 0.000568 | 2008
2007-08-06 | 0.43146 | -0.84059 | 68 | 4 | 19353 | 0.0035137 | -5.6511 | 2007 | 8 | August-2007 | 0.43146 | 0.003514 | 2008
2007-08-07 | 0.28549 | -1.2536 | 1590 | 5 | 19353 | 0.082158 | -2.4991 | 2007 | 8 | August-2007 | 0.28548 | 0.082158 | 2008
2007-08-08 | 1.1123 | 0.10641 | 94 | 1 | 19353 | 0.0048571 | -5.3273 | 2007 | 8 | August-2007 | 1.1123 | 0.004857 | 2008
2007-08-09 | 0.24048 | -1.4251 | 92 | 4 | 19353 | 0.0047538 | -5.3488 | 2007 | 8 | August-2007 | 0.24048 | 0.004754 | 2008
2007-08-10 | 0.0010851 | -6.8261 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2007 | 8 | August-2007 | 0.001085 | 0.000155 | 2008
2007-08-11 | 2.94 | 1.0784 | 354 | 5 | 19353 | 0.018292 | -4.0013 | 2007 | 8 | August-2007 | 2.94 | 0.018292 | 2008
2007-08-12 | 0.35746 | -1.0287 | 98 | 1 | 19353 | 0.0050638 | -5.2856 | 2007 | 8 | August-2007 | 0.35746 | 0.005064 | 2008
2007-08-13 | 0.036842 | -3.3011 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2007 | 8 | August-2007 | 0.036842 | 0.000258 | 2008
2007-08-14 | 0.15977 | -1.834 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2007 | 8 | August-2007 | 0.15977 | 0.000517 | 2008
2007-08-15 | 2.3285 | 0.84521 | 1394 | 4 | 19353 | 0.07203 | -2.6307 | 2007 | 8 | August-2007 | 2.3285 | 0.07203 | 2008
2007-08-16 | 0.033948 | -3.3829 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2007 | 8 | August-2007 | 0.033948 | 0.000258 | 2008
2007-08-17 | 1.1907 | 0.17451 | 143 | 5 | 19353 | 0.007389 | -4.9078 | 2007 | 8 | August-2007 | 1.1907 | 0.007389 | 2008
2007-08-18 | 0.10288 | -2.2742 | 15 | 2 | 19353 | 0.00077507 | -7.1626 | 2007 | 8 | August-2007 | 0.10288 | 0.000775 | 2008
2007-08-19 | 0.39105 | -0.93892 | 86 | 1 | 19353 | 0.0044438 | -5.4163 | 2007 | 8 | August-2007 | 0.39105 | 0.004444 | 2008
2007-08-20 | 0.1235 | -2.0916 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2007 | 8 | August-2007 | 0.12349 | 0.000517 | 2008
2007-08-21 | 0.34971 | -1.0506 | 22 | 2 | 19353 | 0.0011368 | -6.7796 | 2007 | 8 | August-2007 | 0.34971 | 0.001137 | 2008
2007-08-22 | 0.41559 | -0.87805 | 37 | 2 | 19353 | 0.0019118 | -6.2597 | 2007 | 8 | August-2007 | 0.41559 | 0.001912 | 2008
2007-08-23 | 0.18664 | -1.6786 | 21 | 1 | 19353 | 0.0010851 | -6.8261 | 2007 | 8 | August-2007 | 0.18664 | 0.001085 | 2008
2007-08-25 | 0.58038 | -0.54408 | 18 | 1 | 19353 | 0.00093009 | -6.9802 | 2007 | 8 | August-2007 | 0.58037 | 0.00093 | 2008
2007-08-27 | 0.18178 | -1.705 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2007 | 8 | August-2007 | 0.18178 | 0.001447 | 2008
2007-08-28 | 1.7586 | 0.56451 | 375 | 6 | 19353 | 0.019377 | -3.9437 | 2007 | 8 | August-2007 | 1.7586 | 0.019377 | 2008
2007-08-29 | 1.5286 | 0.42435 | 109 | 2 | 19353 | 0.0056322 | -5.1793 | 2007 | 8 | August-2007 | 1.5286 | 0.005632 | 2008
2007-08-30 | 0.43559 | -0.83105 | 41 | 2 | 19353 | 0.0021185 | -6.157 | 2007 | 8 | August-2007 | 0.43559 | 0.002119 | 2008
2007-08-31 | 0.41063 | -0.89005 | 27 | 4 | 19353 | 0.0013951 | -6.5748 | 2007 | 8 | August-2007 | 0.41063 | 0.001395 | 2008
2007-09-01 | 0.0052705 | -5.2456 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2007 | 9 | September-2007 | 0.005271 | 0.000155 | 2008
2007-09-02 | 0.0016018 | -6.4366 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2007 | 9 | September-2007 | 0.001602 | 0.000207 | 2008
2007-09-03 | 0.032243 | -3.4345 | 52 | 1 | 19353 | 0.0026869 | -5.9194 | 2007 | 9 | September-2007 | 0.032243 | 0.002687 | 2008
2007-09-04 | 0.17207 | -1.7599 | 10 | 1 | 19353 | 0.00051672 | -7.568 | 2007 | 9 | September-2007 | 0.17207 | 0.000517 | 2008
2007-09-05 | 1.2423 | 0.217 | 185 | 4 | 19353 | 0.0095592 | -4.6502 | 2007 | 9 | September-2007 | 1.2423 | 0.009559 | 2008
2007-09-06 | 0.33137 | -1.1045 | 17 | 2 | 19353 | 0.00087842 | -7.0374 | 2007 | 9 | September-2007 | 0.33137 | 0.000878 | 2008
2007-09-07 | 0.29535 | -1.2196 | 17 | 2 | 19353 | 0.00087842 | -7.0374 | 2007 | 9 | September-2007 | 0.29535 | 0.000878 | 2008
2007-09-10 | 0.012866 | -4.3531 | 7 | 3 | 19353 | 0.0003617 | -7.9247 | 2007 | 9 | September-2007 | 0.012866 | 0.000362 | 2008
2007-09-11 | 0.063091 | -2.7632 | 12 | 2 | 19353 | 0.00062006 | -7.3857 | 2007 | 9 | September-2007 | 0.063091 | 0.00062 | 2008
2007-09-12 | 0.22891 | -1.4744 | 15 | 2 | 19353 | 0.00077507 | -7.1626 | 2007 | 9 | September-2007 | 0.2289 | 0.000775 | 2008
2007-09-13 | 0.24182 | -1.4195 | 20 | 2 | 19353 | 0.0010334 | -6.8749 | 2007 | 9 | September-2007 | 0.24182 | 0.001033 | 2008
2007-09-14 | 0.081848 | -2.5029 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2007 | 9 | September-2007 | 0.081848 | 0.000362 | 2008
2007-09-15 | 0.012298 | -4.3983 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2007 | 9 | September-2007 | 0.012298 | 0.000103 | 2008
2007-09-16 | 0.076267 | -2.5735 | 6 | 1 | 19353 | 0.00031003 | -8.0788 | 2007 | 9 | September-2007 | 0.076267 | 0.00031 | 2008
2007-09-17 | 0.18509 | -1.6869 | 42 | 3 | 19353 | 0.0021702 | -6.1329 | 2007 | 9 | September-2007 | 0.18509 | 0.00217 | 2008
2007-09-18 | 0.061489 | -2.7889 | 17 | 1 | 19353 | 0.00087842 | -7.0374 | 2007 | 9 | September-2007 | 0.061489 | 0.000878 | 2008
2007-09-19 | 0.0054772 | -5.2072 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2007 | 9 | September-2007 | 0.005477 | 5.2e-05 | 2008
2007-09-20 | 0.022219 | -3.8068 | 5 | 1 | 19353 | 0.00025836 | -8.2612 | 2007 | 9 | September-2007 | 0.022219 | 0.000258 | 2008
2007-09-22 | 0.084638 | -2.4694 | 26 | 1 | 19353 | 0.0013435 | -6.6125 | 2007 | 9 | September-2007 | 0.084638 | 0.001343 | 2008
2007-09-24 | 0.77895 | -0.24981 | 70 | 6 | 19353 | 0.003617 | -5.6221 | 2007 | 9 | September-2007 | 0.77895 | 0.003617 | 2008
2007-09-25 | 0.51145 | -0.67051 | 35 | 5 | 19353 | 0.0018085 | -6.3153 | 2007 | 9 | September-2007 | 0.51145 | 0.001809 | 2008
2007-09-26 | 0.23965 | -1.4286 | 15 | 5 | 19353 | 0.00077507 | -7.1626 | 2007 | 9 | September-2007 | 0.23965 | 0.000775 | 2008
2007-09-27 | 0.80396 | -0.21821 | 115 | 4 | 19353 | 0.0059422 | -5.1257 | 2007 | 9 | September-2007 | 0.80396 | 0.005942 | 2008
2007-09-28 | 0.16096 | -1.8266 | 11 | 2 | 19353 | 0.00056839 | -7.4727 | 2007 | 9 | September-2007 | 0.16096 | 0.000568 | 2008
2007-09-30 | 0.31871 | -1.1435 | 49 | 3 | 19353 | 0.0025319 | -5.9788 | 2007 | 9 | September-2007 | 0.31871 | 0.002532 | 2008
2007-10-01 | 0.51093 | -0.67153 | 56 | 4 | 19353 | 0.0028936 | -5.8453 | 2007 | 10 | October-2007 | 0.51093 | 0.002894 | 2008
2007-10-02 | 0.38335 | -0.9588 | 585 | 7 | 19353 | 0.030228 | -3.499 | 2007 | 10 | October-2007 | 0.38335 | 0.030228 | 2008
2007-10-03 | 0.4081 | -0.89624 | 322 | 9 | 19353 | 0.016638 | -4.0961 | 2007 | 10 | October-2007 | 0.4081 | 0.016638 | 2008
2007-10-04 | 0.18974 | -1.6621 | 18 | 1 | 19353 | 0.00093009 | -6.9802 | 2007 | 10 | October-2007 | 0.18974 | 0.00093 | 2008
2007-10-05 | 1.1297 | 0.12199 | 182 | 7 | 19353 | 0.0094042 | -4.6666 | 2007 | 10 | October-2007 | 1.1297 | 0.009404 | 2008
2007-10-08 | 0.30869 | -1.1754 | 44 | 3 | 19353 | 0.0022735 | -6.0864 | 2007 | 10 | October-2007 | 0.30869 | 0.002274 | 2008
2007-10-09 | 0.072134 | -2.6292 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2007 | 10 | October-2007 | 0.072134 | 0.000207 | 2008
2007-10-10 | 0.10696 | -2.2353 | 18 | 1 | 19353 | 0.00093009 | -6.9802 | 2007 | 10 | October-2007 | 0.10696 | 0.00093 | 2008
2007-10-11 | 0.045626 | -3.0873 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2007 | 10 | October-2007 | 0.045626 | 0.000258 | 2008
2007-10-12 | 0.58063 | -0.54364 | 384 | 3 | 19353 | 0.019842 | -3.92 | 2007 | 10 | October-2007 | 0.58063 | 0.019842 | 2008
2007-10-14 | 5.0254 | 1.6145 | 317 | 7 | 19353 | 0.01638 | -4.1117 | 2007 | 10 | October-2007 | 5.0254 | 0.01638 | 2008
2007-10-15 | 1.437 | 0.36255 | 299 | 7 | 19353 | 0.01545 | -4.1702 | 2007 | 10 | October-2007 | 1.437 | 0.01545 | 2008
2007-10-16 | 0.029556 | -3.5215 | 11 | 5 | 19353 | 0.00056839 | -7.4727 | 2007 | 10 | October-2007 | 0.029556 | 0.000568 | 2008
2007-10-17 | 1.2713 | 0.24006 | 4058 | 15 | 19353 | 0.20968 | -1.5622 | 2007 | 10 | October-2007 | 1.2713 | 0.20968 | 2008
2007-10-18 | 1.4757 | 0.38916 | 126 | 10 | 19353 | 0.0065106 | -5.0343 | 2007 | 10 | October-2007 | 1.4757 | 0.006511 | 2008
2007-10-21 | 1.5157 | 0.4159 | 160 | 5 | 19353 | 0.0082675 | -4.7954 | 2007 | 10 | October-2007 | 1.5157 | 0.008267 | 2008
2007-10-22 | 0.21361 | -1.5436 | 33 | 2 | 19353 | 0.0017052 | -6.3741 | 2007 | 10 | October-2007 | 0.21361 | 0.001705 | 2008
2007-10-23 | 0.074407 | -2.5982 | 32 | 4 | 19353 | 0.0016535 | -6.4049 | 2007 | 10 | October-2007 | 0.074407 | 0.001653 | 2008
2007-10-24 | 0.3324 | -1.1014 | 270 | 3 | 19353 | 0.013951 | -4.2722 | 2007 | 10 | October-2007 | 0.3324 | 0.013951 | 2008
2007-10-25 | 0.03152 | -3.4571 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2007 | 10 | October-2007 | 0.03152 | 0.000103 | 2008
2007-10-26 | 0.10846 | -2.2214 | 7 | 2 | 19353 | 0.0003617 | -7.9247 | 2007 | 10 | October-2007 | 0.10846 | 0.000362 | 2008
2007-10-27 | 0.020772 | -3.8742 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2007 | 10 | October-2007 | 0.020772 | 5.2e-05 | 2008
2007-10-29 | 0.28311 | -1.2619 | 71 | 2 | 19353 | 0.0036687 | -5.6079 | 2007 | 10 | October-2007 | 0.28311 | 0.003669 | 2008
2007-10-30 | 0.23624 | -1.4429 | 19 | 2 | 19353 | 0.00098176 | -6.9262 | 2007 | 10 | October-2007 | 0.23624 | 0.000982 | 2008
2007-10-31 | 0.039529 | -3.2307 | 5 | 1 | 19353 | 0.00025836 | -8.2612 | 2007 | 10 | October-2007 | 0.039529 | 0.000258 | 2008
2007-11-01 | 2.0044 | 0.69534 | 1306 | 4 | 19353 | 0.067483 | -2.6959 | 2007 | 11 | November-2007 | 2.0044 | 0.067483 | 2008
2007-11-02 | 0.68274 | -0.38165 | 60 | 2 | 19353 | 0.0031003 | -5.7763 | 2007 | 11 | November-2007 | 0.68274 | 0.0031 | 2008
2007-11-05 | 0.67705 | -0.39001 | 76 | 3 | 19353 | 0.003927 | -5.5399 | 2007 | 11 | November-2007 | 0.67705 | 0.003927 | 2008
2007-11-06 | 5.7985 | 1.7576 | 444 | 4 | 19353 | 0.022942 | -3.7748 | 2007 | 11 | November-2007 | 5.7985 | 0.022942 | 2008
2007-11-07 | 0.47657 | -0.74115 | 41 | 3 | 19353 | 0.0021185 | -6.157 | 2007 | 11 | November-2007 | 0.47657 | 0.002119 | 2008
2007-11-08 | 0.24658 | -1.4001 | 58 | 3 | 19353 | 0.002997 | -5.8102 | 2007 | 11 | November-2007 | 0.24658 | 0.002997 | 2008
2007-11-09 | 0.099158 | -2.311 | 38 | 4 | 19353 | 0.0019635 | -6.233 | 2007 | 11 | November-2007 | 0.099158 | 0.001964 | 2008
2007-11-11 | 0.30553 | -1.1857 | 27 | 1 | 19353 | 0.0013951 | -6.5748 | 2007 | 11 | November-2007 | 0.30553 | 0.001395 | 2008
2007-11-12 | 0.21805 | -1.523 | 41 | 2 | 19353 | 0.0021185 | -6.157 | 2007 | 11 | November-2007 | 0.21805 | 0.002119 | 2008
2007-11-13 | 0.39322 | -0.93338 | 500 | 2 | 19353 | 0.025836 | -3.656 | 2007 | 11 | November-2007 | 0.39322 | 0.025836 | 2008
2007-11-14 | 2.1305 | 0.75637 | 478 | 10 | 19353 | 0.024699 | -3.701 | 2007 | 11 | November-2007 | 2.1305 | 0.024699 | 2008
2007-11-15 | 0.63659 | -0.45162 | 63 | 3 | 19353 | 0.0032553 | -5.7275 | 2007 | 11 | November-2007 | 0.63659 | 0.003255 | 2008
2007-11-16 | 0.78158 | -0.24643 | 44 | 4 | 19353 | 0.0022735 | -6.0864 | 2007 | 11 | November-2007 | 0.78158 | 0.002274 | 2008
2007-11-17 | 0.1283 | -2.0534 | 13 | 1 | 19353 | 0.00067173 | -7.3057 | 2007 | 11 | November-2007 | 0.1283 | 0.000672 | 2008
2007-11-18 | 0.031623 | -3.4539 | 9 | 1 | 19353 | 0.00046504 | -7.6734 | 2007 | 11 | November-2007 | 0.031623 | 0.000465 | 2008
2007-11-19 | 0.69576 | -0.36275 | 89 | 3 | 19353 | 0.0045988 | -5.382 | 2007 | 11 | November-2007 | 0.69576 | 0.004599 | 2008
2007-11-20 | 0.72304 | -0.32429 | 55 | 2 | 19353 | 0.0028419 | -5.8633 | 2007 | 11 | November-2007 | 0.72304 | 0.002842 | 2008
2007-11-21 | 0.42882 | -0.84671 | 20 | 2 | 19353 | 0.0010334 | -6.8749 | 2007 | 11 | November-2007 | 0.42882 | 0.001033 | 2008
2007-11-22 | 3.2542 | 1.1799 | 196 | 6 | 19353 | 0.010128 | -4.5925 | 2007 | 11 | November-2007 | 3.2542 | 0.010128 | 2008
2007-11-23 | 0.31949 | -1.141 | 53 | 3 | 19353 | 0.0027386 | -5.9003 | 2007 | 11 | November-2007 | 0.31949 | 0.002739 | 2008
2007-11-26 | 0.26936 | -1.3117 | 23 | 4 | 19353 | 0.0011884 | -6.7351 | 2007 | 11 | November-2007 | 0.26936 | 0.001188 | 2008
2007-11-27 | 0.036945 | -3.2983 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2007 | 11 | November-2007 | 0.036945 | 0.000258 | 2008
2007-11-28 | 3.9956 | 1.3852 | 163 | 3 | 19353 | 0.0084225 | -4.7769 | 2007 | 11 | November-2007 | 3.9956 | 0.008422 | 2008
2007-11-29 | 0.26998 | -1.3094 | 11 | 1 | 19353 | 0.00056839 | -7.4727 | 2007 | 11 | November-2007 | 0.26998 | 0.000568 | 2008
2007-11-30 | 0.24043 | -1.4253 | 33 | 1 | 19353 | 0.0017052 | -6.3741 | 2007 | 11 | November-2007 | 0.24043 | 0.001705 | 2008
2007-12-01 | 0.053635 | -2.9256 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2007 | 12 | December-2007 | 0.053635 | 0.000155 | 2008
2007-12-03 | 0.075906 | -2.5783 | 21 | 2 | 19353 | 0.0010851 | -6.8261 | 2007 | 12 | December-2007 | 0.075906 | 0.001085 | 2008
2007-12-04 | 0.88798 | -0.11881 | 56 | 4 | 19353 | 0.0028936 | -5.8453 | 2007 | 12 | December-2007 | 0.88798 | 0.002894 | 2008
2007-12-05 | 0.013331 | -4.3176 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2007 | 12 | December-2007 | 0.013331 | 0.000103 | 2008
2007-12-06 | 2.0205 | 0.70333 | 635 | 9 | 19353 | 0.032811 | -3.417 | 2007 | 12 | December-2007 | 2.0205 | 0.032811 | 2008
2007-12-07 | 0.93892 | -0.063021 | 770 | 6 | 19353 | 0.039787 | -3.2242 | 2007 | 12 | December-2007 | 0.93892 | 0.039787 | 2008
2007-12-08 | 0.28812 | -1.2444 | 110 | 4 | 19353 | 0.0056839 | -5.1701 | 2007 | 12 | December-2007 | 0.28812 | 0.005684 | 2008
2007-12-09 | 0.86457 | -0.14552 | 86 | 2 | 19353 | 0.0044438 | -5.4163 | 2007 | 12 | December-2007 | 0.86457 | 0.004444 | 2008
2007-12-10 | 0.5826 | -0.54026 | 343 | 6 | 19353 | 0.017723 | -4.0329 | 2007 | 12 | December-2007 | 0.5826 | 0.017723 | 2008
2007-12-11 | 3.1423 | 1.1449 | 299 | 3 | 19353 | 0.01545 | -4.1702 | 2007 | 12 | December-2007 | 3.1423 | 0.01545 | 2008
2007-12-12 | 0.10283 | -2.2747 | 5 | 1 | 19353 | 0.00025836 | -8.2612 | 2007 | 12 | December-2007 | 0.10283 | 0.000258 | 2008
2007-12-13 | 0.30967 | -1.1723 | 42 | 5 | 19353 | 0.0021702 | -6.1329 | 2007 | 12 | December-2007 | 0.30967 | 0.00217 | 2008
2007-12-14 | 4.6874 | 1.5449 | 314 | 2 | 19353 | 0.016225 | -4.1212 | 2007 | 12 | December-2007 | 4.6874 | 0.016225 | 2008
2007-12-16 | 0.3245 | -1.1255 | 40 | 1 | 19353 | 0.0020669 | -6.1817 | 2007 | 12 | December-2007 | 0.3245 | 0.002067 | 2008
2007-12-17 | 0.90926 | -0.095119 | 49 | 2 | 19353 | 0.0025319 | -5.9788 | 2007 | 12 | December-2007 | 0.90926 | 0.002532 | 2008
2007-12-18 | 0.6722 | -0.39721 | 94 | 5 | 19353 | 0.0048571 | -5.3273 | 2007 | 12 | December-2007 | 0.6722 | 0.004857 | 2008
2007-12-19 | 0.20715 | -1.5743 | 23 | 3 | 19353 | 0.0011884 | -6.7351 | 2007 | 12 | December-2007 | 0.20715 | 0.001188 | 2008
2007-12-20 | 1.599 | 0.46936 | 243 | 7 | 19353 | 0.012556 | -4.3775 | 2007 | 12 | December-2007 | 1.599 | 0.012556 | 2008
2007-12-23 | 0.18519 | -1.6864 | 512 | 1 | 19353 | 0.026456 | -3.6323 | 2007 | 12 | December-2007 | 0.18519 | 0.026456 | 2008
2007-12-24 | 0.003462 | -5.6659 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2007 | 12 | December-2007 | 0.003462 | 5.2e-05 | 2008
2007-12-26 | 2.6683 | 0.98145 | 477 | 6 | 19353 | 0.024647 | -3.7031 | 2007 | 12 | December-2007 | 2.6683 | 0.024647 | 2008
2007-12-27 | 0.33426 | -1.0958 | 31 | 3 | 19353 | 0.0016018 | -6.4366 | 2007 | 12 | December-2007 | 0.33426 | 0.001602 | 2008
2007-12-28 | 0.016587 | -4.0992 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2007 | 12 | December-2007 | 0.016587 | 0.000258 | 2008
2007-12-30 | 0.065571 | -2.7246 | 27 | 1 | 19353 | 0.0013951 | -6.5748 | 2007 | 12 | December-2007 | 0.065571 | 0.001395 | 2008
2007-12-31 | 0.03617 | -3.3195 | 10 | 1 | 19353 | 0.00051672 | -7.568 | 2007 | 12 | December-2007 | 0.03617 | 0.000517 | 2008
2008-01-03 | 0.011574 | -4.459 | 3 | 2 | 19353 | 0.00015501 | -8.772 | 2008 | 1 | January-2008 | 0.011574 | 0.000155 | 2008
2008-01-04 | 0.18958 | -1.6629 | 15 | 3 | 19353 | 0.00077507 | -7.1626 | 2008 | 1 | January-2008 | 0.18958 | 0.000775 | 2008
2008-01-05 | 0.019842 | -3.92 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2008 | 1 | January-2008 | 0.019842 | 0.000155 | 2008
2008-01-07 | 0.023614 | -3.7459 | 3 | 2 | 19353 | 0.00015501 | -8.772 | 2008 | 1 | January-2008 | 0.023614 | 0.000155 | 2008
2008-01-08 | 1.2739 | 0.24209 | 81 | 3 | 19353 | 0.0041854 | -5.4762 | 2008 | 1 | January-2008 | 1.2739 | 0.004185 | 2008
2008-01-09 | 0.0048055 | -5.338 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2008 | 1 | January-2008 | 0.004805 | 0.000155 | 2008
2008-01-10 | 0.36976 | -0.9949 | 21 | 3 | 19353 | 0.0010851 | -6.8261 | 2008 | 1 | January-2008 | 0.36976 | 0.001085 | 2008
2008-01-11 | 0.048726 | -3.0215 | 3 | 2 | 19353 | 0.00015501 | -8.772 | 2008 | 1 | January-2008 | 0.048726 | 0.000155 | 2008
2008-01-13 | 0.26973 | -1.3104 | 24 | 2 | 19353 | 0.0012401 | -6.6925 | 2008 | 1 | January-2008 | 0.26973 | 0.00124 | 2008
2008-01-14 | 0.19201 | -1.6502 | 38 | 3 | 19353 | 0.0019635 | -6.233 | 2008 | 1 | January-2008 | 0.19201 | 0.001964 | 2008
2008-01-15 | 2.19 | 0.78392 | 144 | 4 | 19353 | 0.0074407 | -4.9008 | 2008 | 1 | January-2008 | 2.19 | 0.007441 | 2008
2008-01-16 | 2.0194 | 0.70281 | 200 | 3 | 19353 | 0.010334 | -4.5723 | 2008 | 1 | January-2008 | 2.0194 | 0.010334 | 2008
2008-01-17 | 0.75957 | -0.275 | 63 | 6 | 19353 | 0.0032553 | -5.7275 | 2008 | 1 | January-2008 | 0.75957 | 0.003255 | 2008
2008-01-18 | 0.43885 | -0.82361 | 512 | 5 | 19353 | 0.026456 | -3.6323 | 2008 | 1 | January-2008 | 0.43885 | 0.026456 | 2008
2008-01-19 | 0.32842 | -1.1134 | 57 | 3 | 19353 | 0.0029453 | -5.8276 | 2008 | 1 | January-2008 | 0.32843 | 0.002945 | 2008
2008-01-20 | 5.4069 | 1.6877 | 996 | 3 | 19353 | 0.051465 | -2.9669 | 2008 | 1 | January-2008 | 5.4069 | 0.051465 | 2008
2008-01-21 | 2.4363 | 0.89047 | 180 | 8 | 19353 | 0.0093009 | -4.6776 | 2008 | 1 | January-2008 | 2.4363 | 0.009301 | 2008
2008-01-22 | 4.6069 | 1.5276 | 1077 | 12 | 19353 | 0.05565 | -2.8887 | 2008 | 1 | January-2008 | 4.6069 | 0.05565 | 2008
2008-01-23 | 3.0622 | 1.1191 | 1723 | 6 | 19353 | 0.08903 | -2.4188 | 2008 | 1 | January-2008 | 3.0622 | 0.08903 | 2008
2008-01-24 | 4.1884 | 1.4323 | 777 | 7 | 19353 | 0.040149 | -3.2152 | 2008 | 1 | January-2008 | 4.1884 | 0.040149 | 2008
2008-01-25 | 0.0059939 | -5.117 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2008 | 1 | January-2008 | 0.005994 | 0.000103 | 2008
2008-01-26 | 0.11797 | -2.1374 | 13 | 1 | 19353 | 0.00067173 | -7.3057 | 2008 | 1 | January-2008 | 0.11797 | 0.000672 | 2008
2008-01-27 | 2.002 | 0.69415 | 1680 | 2 | 19353 | 0.086808 | -2.4441 | 2008 | 1 | January-2008 | 2.002 | 0.086808 | 2008
2008-01-28 | 1.7358 | 0.55144 | 1739 | 2 | 19353 | 0.089857 | -2.4095 | 2008 | 1 | January-2008 | 1.7358 | 0.089857 | 2008
2008-01-29 | 0.20457 | -1.5869 | 17 | 2 | 19353 | 0.00087842 | -7.0374 | 2008 | 1 | January-2008 | 0.20457 | 0.000878 | 2008
2008-01-30 | 1.6844 | 0.5214 | 90 | 4 | 19353 | 0.0046504 | -5.3708 | 2008 | 1 | January-2008 | 1.6844 | 0.00465 | 2008
2008-01-31 | 1.5946 | 0.46661 | 94 | 2 | 19353 | 0.0048571 | -5.3273 | 2008 | 1 | January-2008 | 1.5946 | 0.004857 | 2008
2008-02-01 | 2.3701 | 0.86292 | 199 | 8 | 19353 | 0.010283 | -4.5773 | 2008 | 2 | February-2008 | 2.3701 | 0.010283 | 2008
2008-02-02 | 0.23397 | -1.4526 | 152 | 2 | 19353 | 0.0078541 | -4.8467 | 2008 | 2 | February-2008 | 0.23397 | 0.007854 | 2008
2008-02-04 | 0.62275 | -0.47362 | 104 | 4 | 19353 | 0.0053738 | -5.2262 | 2008 | 2 | February-2008 | 0.62275 | 0.005374 | 2008
2008-02-05 | 0.13812 | -1.9796 | 35 | 8 | 19353 | 0.0018085 | -6.3153 | 2008 | 2 | February-2008 | 0.13812 | 0.001809 | 2008
2008-02-06 | 0.093784 | -2.3668 | 244 | 2 | 19353 | 0.012608 | -4.3734 | 2008 | 2 | February-2008 | 0.093784 | 0.012608 | 2008
2008-02-07 | 0.62729 | -0.46634 | 92 | 3 | 19353 | 0.0047538 | -5.3488 | 2008 | 2 | February-2008 | 0.62729 | 0.004754 | 2008
2008-02-08 | 0.55934 | -0.58099 | 125 | 9 | 19353 | 0.0064589 | -5.0423 | 2008 | 2 | February-2008 | 0.55934 | 0.006459 | 2008
2008-02-09 | 0.052085 | -2.9549 | 8 | 2 | 19353 | 0.00041337 | -7.7912 | 2008 | 2 | February-2008 | 0.052085 | 0.000413 | 2008
2008-02-10 | 4.7472 | 1.5575 | 544 | 8 | 19353 | 0.028109 | -3.5717 | 2008 | 2 | February-2008 | 4.7472 | 0.028109 | 2008
2008-02-11 | 0.47124 | -0.75238 | 43 | 2 | 19353 | 0.0022219 | -6.1094 | 2008 | 2 | February-2008 | 0.47125 | 0.002222 | 2008
2008-02-12 | 1.2123 | 0.19249 | 180 | 6 | 19353 | 0.0093009 | -4.6776 | 2008 | 2 | February-2008 | 1.2123 | 0.009301 | 2008
2008-02-13 | 3.293 | 1.1918 | 264 | 8 | 19353 | 0.013641 | -4.2947 | 2008 | 2 | February-2008 | 3.293 | 0.013641 | 2008
2008-02-14 | 0.19971 | -1.6109 | 82 | 4 | 19353 | 0.0042371 | -5.4639 | 2008 | 2 | February-2008 | 0.19971 | 0.004237 | 2008
2008-02-15 | 0.7742 | -0.25593 | 162 | 8 | 19353 | 0.0083708 | -4.783 | 2008 | 2 | February-2008 | 0.77419 | 0.008371 | 2008
2008-02-16 | 0.11745 | -2.1417 | 19 | 2 | 19353 | 0.00098176 | -6.9262 | 2008 | 2 | February-2008 | 0.11745 | 0.000982 | 2008
2008-02-17 | 0.11507 | -2.1622 | 19 | 2 | 19353 | 0.00098176 | -6.9262 | 2008 | 2 | February-2008 | 0.11507 | 0.000982 | 2008
2008-02-18 | 0.45409 | -0.78946 | 75 | 8 | 19353 | 0.0038754 | -5.5531 | 2008 | 2 | February-2008 | 0.45409 | 0.003875 | 2008
2008-02-19 | 2.2809 | 0.82459 | 110 | 2 | 19353 | 0.0056839 | -5.1701 | 2008 | 2 | February-2008 | 2.2809 | 0.005684 | 2008
2008-02-20 | 0.0371 | -3.2941 | 8 | 2 | 19353 | 0.00041337 | -7.7912 | 2008 | 2 | February-2008 | 0.0371 | 0.000413 | 2008
2008-02-21 | 1.3535 | 0.30268 | 105 | 4 | 19353 | 0.0054255 | -5.2166 | 2008 | 2 | February-2008 | 1.3535 | 0.005426 | 2008
2008-02-22 | 1.6614 | 0.50766 | 665 | 10 | 19353 | 0.034362 | -3.3708 | 2008 | 2 | February-2008 | 1.6614 | 0.034362 | 2008
2008-02-23 | 0.5749 | -0.55356 | 20 | 3 | 19353 | 0.0010334 | -6.8749 | 2008 | 2 | February-2008 | 0.5749 | 0.001033 | 2008
2008-02-24 | 3.2037 | 1.1643 | 651 | 2 | 19353 | 0.033638 | -3.3921 | 2008 | 2 | February-2008 | 3.2037 | 0.033638 | 2008
2008-02-25 | 0.051 | -2.9759 | 6 | 4 | 19353 | 0.00031003 | -8.0788 | 2008 | 2 | February-2008 | 0.051 | 0.00031 | 2008
2008-02-26 | 1.0115 | 0.011457 | 514 | 5 | 19353 | 0.026559 | -3.6284 | 2008 | 2 | February-2008 | 1.0115 | 0.026559 | 2008
2008-02-27 | 0.40614 | -0.90106 | 60 | 2 | 19353 | 0.0031003 | -5.7763 | 2008 | 2 | February-2008 | 0.40614 | 0.0031 | 2008
2008-02-28 | 0.092905 | -2.3762 | 14 | 3 | 19353 | 0.0007234 | -7.2315 | 2008 | 2 | February-2008 | 0.092905 | 0.000723 | 2008
2008-02-29 | 3.2906 | 1.1911 | 288 | 5 | 19353 | 0.014881 | -4.2076 | 2008 | 2 | February-2008 | 3.2906 | 0.014881 | 2008
2008-03-01 | 5.3436 | 1.6759 | 1110 | 18 | 19353 | 0.057355 | -2.8585 | 2008 | 3 | March-2008 | 5.3436 | 0.057355 | 2008
2008-03-02 | 0.255 | -1.3665 | 36 | 5 | 19353 | 0.0018602 | -6.2871 | 2008 | 3 | March-2008 | 0.255 | 0.00186 | 2008
2008-03-03 | 0.34382 | -1.0676 | 104 | 5 | 19353 | 0.0053738 | -5.2262 | 2008 | 3 | March-2008 | 0.34382 | 0.005374 | 2008
2008-03-04 | 0.11208 | -2.1886 | 21 | 3 | 19353 | 0.0010851 | -6.8261 | 2008 | 3 | March-2008 | 0.11208 | 0.001085 | 2008
2008-03-05 | 1.9681 | 0.67705 | 146 | 5 | 19353 | 0.0075441 | -4.887 | 2008 | 3 | March-2008 | 1.9681 | 0.007544 | 2008
2008-03-06 | 1.8348 | 0.60694 | 90 | 2 | 19353 | 0.0046504 | -5.3708 | 2008 | 3 | March-2008 | 1.8348 | 0.00465 | 2008
2008-03-07 | 0.13135 | -2.0299 | 21 | 4 | 19353 | 0.0010851 | -6.8261 | 2008 | 3 | March-2008 | 0.13135 | 0.001085 | 2008
2008-03-08 | 0.22322 | -1.4996 | 29 | 3 | 19353 | 0.0014985 | -6.5033 | 2008 | 3 | March-2008 | 0.22322 | 0.001498 | 2008
2008-03-10 | 0.084896 | -2.4663 | 14 | 3 | 19353 | 0.0007234 | -7.2315 | 2008 | 3 | March-2008 | 0.084896 | 0.000723 | 2008
2008-03-11 | 0.054617 | -2.9074 | 12 | 3 | 19353 | 0.00062006 | -7.3857 | 2008 | 3 | March-2008 | 0.054617 | 0.00062 | 2008
2008-03-12 | 0.24353 | -1.4125 | 48 | 4 | 19353 | 0.0024802 | -5.9994 | 2008 | 3 | March-2008 | 0.24353 | 0.00248 | 2008
2008-03-13 | 0.53475 | -0.62596 | 91 | 6 | 19353 | 0.0047021 | -5.3597 | 2008 | 3 | March-2008 | 0.53475 | 0.004702 | 2008
2008-03-14 | 0.39022 | -0.94104 | 51 | 4 | 19353 | 0.0026353 | -5.9388 | 2008 | 3 | March-2008 | 0.39022 | 0.002635 | 2008
2008-03-15 | 0.1854 | -1.6853 | 16 | 2 | 19353 | 0.00082675 | -7.098 | 2008 | 3 | March-2008 | 0.1854 | 0.000827 | 2008
2008-03-16 | 0.28285 | -1.2628 | 19 | 3 | 19353 | 0.00098176 | -6.9262 | 2008 | 3 | March-2008 | 0.28285 | 0.000982 | 2008
2008-03-17 | 0.0018602 | -6.2871 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2008 | 3 | March-2008 | 0.00186 | 0.000207 | 2008
2008-03-18 | 0.56286 | -0.57473 | 80 | 4 | 19353 | 0.0041337 | -5.4886 | 2008 | 3 | March-2008 | 0.56286 | 0.004134 | 2008
2008-03-19 | 0.15434 | -1.8686 | 14 | 3 | 19353 | 0.0007234 | -7.2315 | 2008 | 3 | March-2008 | 0.15434 | 0.000723 | 2008
2008-03-20 | 0.013951 | -4.2722 | 4 | 2 | 19353 | 0.00020669 | -8.4843 | 2008 | 3 | March-2008 | 0.013951 | 0.000207 | 2008
2008-03-21 | 0.045006 | -3.101 | 10 | 2 | 19353 | 0.00051672 | -7.568 | 2008 | 3 | March-2008 | 0.045006 | 0.000517 | 2008
2008-03-23 | 1.1049 | 0.099796 | 243 | 1 | 19353 | 0.012556 | -4.3775 | 2008 | 3 | March-2008 | 1.1049 | 0.012556 | 2008
2008-03-25 | 0.033897 | -3.3844 | 16 | 2 | 19353 | 0.00082675 | -7.098 | 2008 | 3 | March-2008 | 0.033897 | 0.000827 | 2008
2008-03-26 | 1.0813 | 0.078145 | 62 | 4 | 19353 | 0.0032036 | -5.7435 | 2008 | 3 | March-2008 | 1.0813 | 0.003204 | 2008
2008-03-27 | 2.7011 | 0.99367 | 150 | 4 | 19353 | 0.0077507 | -4.86 | 2008 | 3 | March-2008 | 2.7011 | 0.007751 | 2008
2008-03-28 | 0.67535 | -0.39253 | 40 | 4 | 19353 | 0.0020669 | -6.1817 | 2008 | 3 | March-2008 | 0.67535 | 0.002067 | 2008
2008-03-29 | 0.027748 | -3.5846 | 6 | 2 | 19353 | 0.00031003 | -8.0788 | 2008 | 3 | March-2008 | 0.027748 | 0.00031 | 2008
2008-03-31 | 1.5087 | 0.41122 | 133 | 5 | 19353 | 0.0068723 | -4.9803 | 2008 | 3 | March-2008 | 1.5087 | 0.006872 | 2008
2008-04-01 | 1.2243 | 0.20233 | 70 | 5 | 19353 | 0.003617 | -5.6221 | 2008 | 4 | April-2008 | 1.2243 | 0.003617 | 2009
2008-04-02 | 2.2901 | 0.82859 | 162 | 4 | 19353 | 0.0083708 | -4.783 | 2008 | 4 | April-2008 | 2.2901 | 0.008371 | 2009
2008-04-03 | 0.049915 | -2.9974 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2008 | 4 | April-2008 | 0.049915 | 0.000155 | 2009
2008-04-04 | 0.48277 | -0.72822 | 89 | 4 | 19353 | 0.0045988 | -5.382 | 2008 | 4 | April-2008 | 0.48277 | 0.004599 | 2009
2008-04-07 | 0.044954 | -3.1021 | 6 | 5 | 19353 | 0.00031003 | -8.0788 | 2008 | 4 | April-2008 | 0.044954 | 0.00031 | 2009
2008-04-08 | 0.12174 | -2.1059 | 14 | 3 | 19353 | 0.0007234 | -7.2315 | 2008 | 4 | April-2008 | 0.12174 | 0.000723 | 2009
2008-04-09 | 0.0059939 | -5.117 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2008 | 4 | April-2008 | 0.005994 | 5.2e-05 | 2009
2008-04-10 | 0.096212 | -2.3412 | 46 | 2 | 19353 | 0.0023769 | -6.042 | 2008 | 4 | April-2008 | 0.096212 | 0.002377 | 2009
2008-04-11 | 0.24849 | -1.3924 | 34 | 4 | 19353 | 0.0017568 | -6.3442 | 2008 | 4 | April-2008 | 0.24849 | 0.001757 | 2009
2008-04-14 | 0.37312 | -0.98585 | 148 | 3 | 19353 | 0.0076474 | -4.8734 | 2008 | 4 | April-2008 | 0.37312 | 0.007647 | 2009
2008-04-15 | 1.1911 | 0.17486 | 170 | 11 | 19353 | 0.0087842 | -4.7348 | 2008 | 4 | April-2008 | 1.1911 | 0.008784 | 2009
2008-04-16 | 0.046143 | -3.076 | 19 | 1 | 19353 | 0.00098176 | -6.9262 | 2008 | 4 | April-2008 | 0.046143 | 0.000982 | 2009
2008-04-17 | 0.25242 | -1.3767 | 33 | 5 | 19353 | 0.0017052 | -6.3741 | 2008 | 4 | April-2008 | 0.25242 | 0.001705 | 2009
2008-04-18 | 1.2611 | 0.23198 | 1643 | 6 | 19353 | 0.084896 | -2.4663 | 2008 | 4 | April-2008 | 1.2611 | 0.084896 | 2009
2008-04-19 | 0.85305 | -0.15894 | 89 | 4 | 19353 | 0.0045988 | -5.382 | 2008 | 4 | April-2008 | 0.85305 | 0.004599 | 2009
2008-04-20 | 0.59918 | -0.51219 | 127 | 2 | 19353 | 0.0065623 | -5.0264 | 2008 | 4 | April-2008 | 0.59918 | 0.006562 | 2009
2008-04-21 | 0.24849 | -1.3924 | 24 | 4 | 19353 | 0.0012401 | -6.6925 | 2008 | 4 | April-2008 | 0.24849 | 0.00124 | 2009
2008-04-22 | 8.4747 | 2.1371 | 1357 | 7 | 19353 | 0.070118 | -2.6576 | 2008 | 4 | April-2008 | 8.4747 | 0.070118 | 2009
2008-04-23 | 2.4587 | 0.89963 | 534 | 5 | 19353 | 0.027593 | -3.5902 | 2008 | 4 | April-2008 | 2.4587 | 0.027593 | 2009
2008-04-24 | 1.0929 | 0.08884 | 585 | 6 | 19353 | 0.030228 | -3.499 | 2008 | 4 | April-2008 | 1.0929 | 0.030228 | 2009
2008-04-25 | 1.3445 | 0.29602 | 299 | 2 | 19353 | 0.01545 | -4.1702 | 2008 | 4 | April-2008 | 1.3445 | 0.01545 | 2009
2008-04-27 | 0.052498 | -2.947 | 2 | 1 | 19353 | 0.00010334 | -9.1775 | 2008 | 4 | April-2008 | 0.052498 | 0.000103 | 2009
2008-04-28 | 1.4415 | 0.36571 | 529 | 3 | 19353 | 0.027334 | -3.5996 | 2008 | 4 | April-2008 | 1.4415 | 0.027334 | 2009
2008-04-29 | 3.695 | 1.307 | 1165 | 6 | 19353 | 0.060197 | -2.8101 | 2008 | 4 | April-2008 | 3.695 | 0.060197 | 2009
2008-04-30 | 5.0052 | 1.6105 | 1359 | 13 | 19353 | 0.070222 | -2.6561 | 2008 | 4 | April-2008 | 5.0052 | 0.070222 | 2009
2008-05-01 | 0.80897 | -0.21199 | 124 | 4 | 19353 | 0.0064073 | -5.0503 | 2008 | 5 | May-2008 | 0.80897 | 0.006407 | 2009
2008-05-02 | 1.2408 | 0.21579 | 178 | 4 | 19353 | 0.0091975 | -4.6888 | 2008 | 5 | May-2008 | 1.2408 | 0.009198 | 2009
2008-05-04 | 0.0053738 | -5.2262 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2008 | 5 | May-2008 | 0.005374 | 0.000207 | 2009
2008-05-05 | 1.1797 | 0.16527 | 135 | 5 | 19353 | 0.0069757 | -4.9653 | 2008 | 5 | May-2008 | 1.1797 | 0.006976 | 2009
2008-05-06 | 0.072547 | -2.6235 | 27 | 2 | 19353 | 0.0013951 | -6.5748 | 2008 | 5 | May-2008 | 0.072547 | 0.001395 | 2009
2008-05-07 | 1.1043 | 0.099234 | 229 | 7 | 19353 | 0.011833 | -4.4369 | 2008 | 5 | May-2008 | 1.1043 | 0.011833 | 2009
2008-05-08 | 0.39456 | -0.92997 | 102 | 7 | 19353 | 0.0052705 | -5.2456 | 2008 | 5 | May-2008 | 0.39456 | 0.005271 | 2009
2008-05-09 | 0.67896 | -0.38719 | 342 | 5 | 19353 | 0.017672 | -4.0358 | 2008 | 5 | May-2008 | 0.67897 | 0.017672 | 2009
2008-05-11 | 0.14768 | -1.9127 | 18 | 1 | 19353 | 0.00093009 | -6.9802 | 2008 | 5 | May-2008 | 0.14768 | 0.00093 | 2009
2008-05-12 | 0.22498 | -1.4918 | 25 | 3 | 19353 | 0.0012918 | -6.6517 | 2008 | 5 | May-2008 | 0.22498 | 0.001292 | 2009
2008-05-13 | 0.014571 | -4.2287 | 3 | 1 | 19353 | 0.00015501 | -8.772 | 2008 | 5 | May-2008 | 0.014571 | 0.000155 | 2009
2008-05-14 | 0.10252 | -2.2777 | 15 | 4 | 19353 | 0.00077507 | -7.1626 | 2008 | 5 | May-2008 | 0.10252 | 0.000775 | 2009
2008-05-15 | 0.61319 | -0.48909 | 120 | 4 | 19353 | 0.0062006 | -5.0831 | 2008 | 5 | May-2008 | 0.61319 | 0.006201 | 2009
2008-05-16 | 0.17894 | -1.7207 | 12 | 4 | 19353 | 0.00062006 | -7.3857 | 2008 | 5 | May-2008 | 0.17894 | 0.00062 | 2009
2008-05-18 | 0.56828 | -0.56513 | 52 | 2 | 19353 | 0.0026869 | -5.9194 | 2008 | 5 | May-2008 | 0.56828 | 0.002687 | 2009
2008-05-19 | 0.43073 | -0.84226 | 122 | 2 | 19353 | 0.0063039 | -5.0666 | 2008 | 5 | May-2008 | 0.43073 | 0.006304 | 2009
2008-05-20 | 0.042577 | -3.1564 | 4 | 1 | 19353 | 0.00020669 | -8.4843 | 2008 | 5 | May-2008 | 0.042577 | 0.000207 | 2009
2008-05-21 | 0.36377 | -1.0112 | 150 | 5 | 19353 | 0.0077507 | -4.86 | 2008 | 5 | May-2008 | 0.36377 | 0.007751 | 2009
2008-05-22 | 0.61903 | -0.47961 | 69 | 5 | 19353 | 0.0035653 | -5.6365 | 2008 | 5 | May-2008 | 0.61903 | 0.003565 | 2009
2008-05-23 | 0.61401 | -0.48774 | 1016 | 6 | 19353 | 0.052498 | -2.947 | 2008 | 5 | May-2008 | 0.61401 | 0.052498 | 2009
2008-05-24 | 0.73151 | -0.31264 | 1573 | 1 | 19353 | 0.081279 | -2.5099 | 2008 | 5 | May-2008 | 0.73151 | 0.081279 | 2009
2008-05-26 | 0.55428 | -0.59008 | 148 | 5 | 19353 | 0.0076474 | -4.8734 | 2008 | 5 | May-2008 | 0.55428 | 0.007647 | 2009
2008-05-27 | 0.45342 | -0.79094 | 93 | 3 | 19353 | 0.0048055 | -5.338 | 2008 | 5 | May-2008 | 0.45342 | 0.004805 | 2009
2008-05-28 | 0.1593 | -1.8369 | 21 | 2 | 19353 | 0.0010851 | -6.8261 | 2008 | 5 | May-2008 | 0.1593 | 0.001085 | 2009
2008-05-29 | 1.4801 | 0.39213 | 467 | 2 | 19353 | 0.024131 | -3.7243 | 2008 | 5 | May-2008 | 1.4801 | 0.024131 | 2009
2008-05-30 | 0.53191 | -0.63129 | 87 | 4 | 19353 | 0.0044954 | -5.4047 | 2008 | 5 | May-2008 | 0.53191 | 0.004495 | 2009
2008-05-31 | 1.2386 | 0.21396 | 2397 | 1 | 19353 | 0.12386 | -2.0886 | 2008 | 5 | May-2008 | 1.2386 | 0.12386 | 2009
2008-06-01 | 0.10572 | -2.247 | 280 | 2 | 19353 | 0.014468 | -4.2358 | 2008 | 6 | June-2008 | 0.10572 | 0.014468 | 2009
2008-06-02 | 0.14081 | -1.9604 | 109 | 1 | 19353 | 0.0056322 | -5.1793 | 2008 | 6 | June-2008 | 0.14081 | 0.005632 | 2009
2008-06-03 | 0.9181 | -0.085448 | 84 | 2 | 19353 | 0.0043404 | -5.4398 | 2008 | 6 | June-2008 | 0.9181 | 0.00434 | 2009
2008-06-04 | 0.24797 | -1.3944 | 49 | 3 | 19353 | 0.0025319 | -5.9788 | 2008 | 6 | June-2008 | 0.24797 | 0.002532 | 2009
2008-06-05 | 0.55976 | -0.58025 | 70 | 4 | 19353 | 0.003617 | -5.6221 | 2008 | 6 | June-2008 | 0.55976 | 0.003617 | 2009
2008-06-06 | 0.10768 | -2.2286 | 9 | 2 | 19353 | 0.00046504 | -7.6734 | 2008 | 6 | June-2008 | 0.10768 | 0.000465 | 2009
2008-06-07 | 0.32129 | -1.1354 | 179 | 5 | 19353 | 0.0092492 | -4.6832 | 2008 | 6 | June-2008 | 0.32129 | 0.009249 | 2009
2008-06-08 | 1.415 | 0.34711 | 290 | 2 | 19353 | 0.014985 | -4.2007 | 2008 | 6 | June-2008 | 1.415 | 0.014985 | 2009
2008-06-09 | 0.71622 | -0.33377 | 102 | 3 | 19353 | 0.0052705 | -5.2456 | 2008 | 6 | June-2008 | 0.71622 | 0.005271 | 2009
2008-06-10 | 0.18984 | -1.6616 | 39 | 4 | 19353 | 0.0020152 | -6.207 | 2008 | 6 | June-2008 | 0.18984 | 0.002015 | 2009
2008-06-11 | 0.042371 | -3.1613 | 5 | 3 | 19353 | 0.00025836 | -8.2612 | 2008 | 6 | June-2008 | 0.042371 | 0.000258 | 2009
2008-06-12 | 0.1886 | -1.6681 | 25 | 1 | 19353 | 0.0012918 | -6.6517 | 2008 | 6 | June-2008 | 0.1886 | 0.001292 | 2009
2008-06-13 | 0.15243 | -1.881 | 21 | 2 | 19353 | 0.0010851 | -6.8261 | 2008 | 6 | June-2008 | 0.15243 | 0.001085 | 2009
2008-06-15 | 4.3838 | 1.4779 | 1083 | 1 | 19353 | 0.05596 | -2.8831 | 2008 | 6 | June-2008 | 4.3838 | 0.05596 | 2009
2008-06-16 | 0.36449 | -1.0093 | 61 | 2 | 19353 | 0.003152 | -5.7597 | 2008 | 6 | June-2008 | 0.36449 | 0.003152 | 2009
2008-06-17 | 0.17532 | -1.7411 | 62 | 6 | 19353 | 0.0032036 | -5.7435 | 2008 | 6 | June-2008 | 0.17532 | 0.003204 | 2009
2008-06-18 | 0.1546 | -1.8669 | 27 | 4 | 19353 | 0.0013951 | -6.5748 | 2008 | 6 | June-2008 | 0.1546 | 0.001395 | 2009
2008-06-19 | 0.87532 | -0.13317 | 137 | 3 | 19353 | 0.007079 | -4.9506 | 2008 | 6 | June-2008 | 0.87532 | 0.007079 | 2009
2008-06-20 | 0.27422 | -1.2938 | 24 | 6 | 19353 | 0.0012401 | -6.6925 | 2008 | 6 | June-2008 | 0.27422 | 0.00124 | 2009
2008-06-21 | 0.86906 | -0.14034 | 139 | 1 | 19353 | 0.0071823 | -4.9361 | 2008 | 6 | June-2008 | 0.86906 | 0.007182 | 2009
2008-06-22 | 0.16773 | -1.7854 | 48 | 2 | 19353 | 0.0024802 | -5.9994 | 2008 | 6 | June-2008 | 0.16773 | 0.00248 | 2009
2008-06-23 | 0.080711 | -2.5169 | 257 | 3 | 19353 | 0.01328 | -4.3215 | 2008 | 6 | June-2008 | 0.080711 | 0.01328 | 2009
2008-06-24 | 0.83574 | -0.17944 | 52 | 3 | 19353 | 0.0026869 | -5.9194 | 2008 | 6 | June-2008 | 0.83574 | 0.002687 | 2009
2008-06-25 | 0.74536 | -0.29388 | 155 | 11 | 19353 | 0.0080091 | -4.8272 | 2008 | 6 | June-2008 | 0.74536 | 0.008009 | 2009
2008-06-26 | 1.3792 | 0.32148 | 1986 | 18 | 19353 | 0.10262 | -2.2767 | 2008 | 6 | June-2008 | 1.3792 | 0.10262 | 2009
2008-06-27 | 0.90591 | -0.09882 | 303 | 21 | 19353 | 0.015656 | -4.1569 | 2008 | 6 | June-2008 | 0.90591 | 0.015656 | 2009
2008-06-28 | 0.16705 | -1.7894 | 51 | 4 | 19353 | 0.0026353 | -5.9388 | 2008 | 6 | June-2008 | 0.16705 | 0.002635 | 2009
2008-06-29 | 0.095954 | -2.3439 | 28 | 2 | 19353 | 0.0014468 | -6.5384 | 2008 | 6 | June-2008 | 0.095954 | 0.001447 | 2009
2008-06-30 | 0.076474 | -2.5708 | 5 | 1 | 19353 | 0.00025836 | -8.2612 | 2008 | 6 | June-2008 | 0.076474 | 0.000258 | 2009
2008-07-01 | 0.63251 | -0.45806 | 36 | 5 | 19353 | 0.0018602 | -6.2871 | 2008 | 7 | July-2008 | 0.63251 | 0.00186 | 2009
2008-07-02 | 0.21139 | -1.5541 | 211 | 8 | 19353 | 0.010903 | -4.5187 | 2008 | 7 | July-2008 | 0.21139 | 0.010903 | 2009
2008-07-03 | 0.40154 | -0.91245 | 2329 | 4 | 19353 | 0.12034 | -2.1174 | 2008 | 7 | July-2008 | 0.40154 | 0.12034 | 2009
2008-07-04 | 2.3675 | 0.86185 | 354 | 8 | 19353 | 0.018292 | -4.0013 | 2008 | 7 | July-2008 | 2.3675 | 0.018292 | 2009
2008-07-05 | 0.54405 | -0.60871 | 21 | 3 | 19353 | 0.0010851 | -6.8261 | 2008 | 7 | July-2008 | 0.54405 | 0.001085 | 2009
2008-07-06 | 5.4137 | 1.6889 | 1077 | 5 | 19353 | 0.05565 | -2.8887 | 2008 | 7 | July-2008 | 5.4137 | 0.05565 | 2009
2008-07-07 | 0.47848 | -0.73714 | 166 | 5 | 19353 | 0.0085775 | -4.7586 | 2008 | 7 | July-2008 | 0.47848 | 0.008577 | 2009
2008-07-08 | 0.59717 | -0.51556 | 106 | 7 | 19353 | 0.0054772 | -5.2072 | 2008 | 7 | July-2008 | 0.59717 | 0.005477 | 2009
2008-07-09 | 0.60544 | -0.50181 | 50 | 3 | 19353 | 0.0025836 | -5.9586 | 2008 | 7 | July-2008 | 0.60544 | 0.002584 | 2009
2008-07-10 | 0.32429 | -1.1261 | 519 | 3 | 19353 | 0.026818 | -3.6187 | 2008 | 7 | July-2008 | 0.32429 | 0.026818 | 2009
2008-07-11 | 0.097556 | -2.3273 | 42 | 4 | 19353 | 0.0021702 | -6.1329 | 2008 | 7 | July-2008 | 0.097556 | 0.00217 | 2009
2008-07-12 | 10.9669 | 2.3949 | 1116 | 4 | 19353 | 0.057665 | -2.8531 | 2008 | 7 | July-2008 | 10.9669 | 0.057665 | 2009
2008-07-13 | 8.203 | 2.1045 | 484 | 1 | 19353 | 0.025009 | -3.6885 | 2008 | 7 | July-2008 | 8.203 | 0.025009 | 2009
2008-07-14 | 0.003462 | -5.6659 | 1 | 1 | 19353 | 5.1672e-05 | -9.8706 | 2008 | 7 | July-2008 | 0.003462 | 5.2e-05 | 2009
2008-07-15 | 0.45058 | -0.79723 | 27 | 4 | 19353 | 0.0013951 | -6.5748 | 2008 | 7 | July-2008 | 0.45058 | 0.001395 | 2009
2008-07-16 | 0.04759 | -3.0451 | 8 | 4 | 19353 | 0.00041337 | -7.7912 | 2008 | 7 | July-2008 | 0.04759 | 0.000413 | 2009
2008-07-17 | 0.42505 | -0.85555 | 28 | 4 | 19353 | 0.0014468 | -6.5384 | 2008 | 7 | July-2008 | 0.42505 | 0.001447 | 2009
2008-07-18 | 0.044954 | -3.1021 | 5 | 2 | 19353 | 0.00025836 | -8.2612 | 2008 | 7 | July-2008 | 0.044954 | 0.000258 | 2009
2008-07-19 | 0.050225 | -2.9912 | 6 | 1 | 19353 | 0.00031003 | -8.0788 | 2008 | 7 | July-2008 | 0.050225 | 0.00031 | 2009
2008-07-21 | 0.13951 | -1.9696 | 252 | 4 | 19353 | 0.013021 | -4.3412 | 2008 | 7 | July-2008 | 0.13951 | 0.013021 | 2009
2008-07-22 | 0.088513 | -2.4246 | 17 | 4 | 19353 | 0.00087842 | -7.0374 | 2008 | 7 | July-2008 | 0.088513 | 0.000878 | 2009
2008-07-23 | 0.40578 | -0.90195 | 83 | 13 | 19353 | 0.0042887 | -5.4518 | 2008 | 7 | July-2008 | 0.40578 | 0.004289 | 2009
2008-07-24 | 0.11523 | -2.1608 | 9 | 3 | 19353 | 0.00046504 | -7.6734 | 2008 | 7 | July-2008 | 0.11523 | 0.000465 | 2009
2008-07-25 | 0.83367 | -0.18192 | 179 | 6 | 19353 | 0.0092492 | -4.6832 | 2008 | 7 | July-2008 | 0.83367 | 0.009249 | 2009
2008-07-26 | 38.9216 | 3.6615 | 4551 | 20 | 19353 | 0.23516 | -1.4475 | 2008 | 7 | July-2008 | 21.6659 | 0.23516 | 2009
2008-07-27 | 2.1511 | 0.76597 | 169 | 6 | 19353 | 0.0087325 | -4.7407 | 2008 | 7 | July-2008 | 2.1511 | 0.008732 | 2009
2008-07-28 | 2.101 | 0.74242 | 158 | 14 | 19353 | 0.0081641 | -4.808 | 2008 | 7 | July-2008 | 2.101 | 0.008164 | 2009
2008-07-29 | 0.33731 | -1.0867 | 83 | 8 | 19353 | 0.0042887 | -5.4518 | 2008 | 7 | July-2008 | 0.33731 | 0.004289 | 2009
2008-07-30 | 7.0823 | 1.9576 | 4013 | 30 | 19353 | 0.20736 | -1.5733 | 2008 | 7 | July-2008 | 7.0823 | 0.20736 | 2009
2008-07-31 | 15.0785 | 2.7133 | 3624 | 17 | 19353 | 0.18726 | -1.6753 | 2008 | 7 | July-2008 | 15.0785 | 0.18726 | 2009
2008-08-01 | 0.11395 | -2.172 | 100 | 2 | 20359 | 0.0049118 | -5.3161 | 2008 | 8 | August-2008 | 0.11396 | 0.004912 | 2009
2008-08-02 | 6.8043 | 1.9176 | 462 | 6 | 20359 | 0.022693 | -3.7857 | 2008 | 8 | August-2008 | 6.8043 | 0.022693 | 2009
2008-08-03 | 0.17427 | -1.7471 | 610 | 6 | 20359 | 0.029962 | -3.5078 | 2008 | 8 | August-2008 | 0.17427 | 0.029962 | 2009
2008-08-04 | 0.01729 | -4.0576 | 124 | 3 | 20359 | 0.0060907 | -5.101 | 2008 | 8 | August-2008 | 0.01729 | 0.006091 | 2009
2008-08-05 | 0.21568 | -1.534 | 401 | 3 | 20359 | 0.019696 | -3.9273 | 2008 | 8 | August-2008 | 0.21568 | 0.019696 | 2009
2008-08-06 | 0.021465 | -3.8413 | 161 | 2 | 20359 | 0.0079081 | -4.8399 | 2008 | 8 | August-2008 | 0.021465 | 0.007908 | 2009
2008-08-07 | 0.0051083 | -5.2769 | 104 | 1 | 20359 | 0.0051083 | -5.2769 | 2008 | 8 | August-2008 | 0.005108 | 0.005108 | 2009
2008-08-08 | 0.083943 | -2.4776 | 227 | 4 | 20359 | 0.01115 | -4.4963 | 2008 | 8 | August-2008 | 0.083943 | 0.01115 | 2009
2008-08-11 | 0.24147 | -1.421 | 840 | 4 | 20359 | 0.041259 | -3.1879 | 2008 | 8 | August-2008 | 0.24147 | 0.041259 | 2009
2008-08-12 | 0.067145 | -2.7009 | 261 | 2 | 20359 | 0.01282 | -4.3568 | 2008 | 8 | August-2008 | 0.067145 | 0.01282 | 2009
2008-08-13 | 0.32904 | -1.1116 | 496 | 3 | 20359 | 0.024363 | -3.7147 | 2008 | 8 | August-2008 | 0.32904 | 0.024363 | 2009
2008-08-14 | 1.4153 | 0.34737 | 1824 | 9 | 20359 | 0.089592 | -2.4125 | 2008 | 8 | August-2008 | 1.4153 | 0.089592 | 2009
2008-08-15 | 1.0481 | 0.047013 | 3787 | 13 | 20359 | 0.18601 | -1.6819 | 2008 | 8 | August-2008 | 1.0481 | 0.18601 | 2009
2008-08-16 | 1.9935 | 0.6899 | 2927 | 7 | 20359 | 0.14377 | -1.9395 | 2008 | 8 | August-2008 | 1.9935 | 0.14377 | 2009
2008-08-17 | 0.55867 | -0.58219 | 3321 | 6 | 20359 | 0.16312 | -1.8133 | 2008 | 8 | August-2008 | 0.55867 | 0.16312 | 2009
2008-08-18 | 0.34972 | -1.0506 | 959 | 5 | 20359 | 0.047104 | -3.0554 | 2008 | 8 | August-2008 | 0.34972 | 0.047104 | 2009
2008-08-19 | 0.064296 | -2.7443 | 405 | 4 | 20359 | 0.019893 | -3.9174 | 2008 | 8 | August-2008 | 0.064296 | 0.019893 | 2009
2008-08-20 | 0.39648 | -0.92512 | 108 | 3 | 20359 | 0.0053048 | -5.2391 | 2008 | 8 | August-2008 | 0.39648 | 0.005305 | 2009
2008-08-21 | 0.11793 | -2.1376 | 16 | 2 | 20359 | 0.00078589 | -7.1487 | 2008 | 8 | August-2008 | 0.11793 | 0.000786 | 2009
2008-08-22 | 0.45076 | -0.79682 | 31 | 4 | 20359 | 0.0015227 | -6.4873 | 2008 | 8 | August-2008 | 0.45076 | 0.001523 | 2009
2008-08-24 | 4.8167 | 1.5721 | 1752 | 6 | 20359 | 0.086055 | -2.4528 | 2008 | 8 | August-2008 | 4.8167 | 0.086055 | 2009
2008-08-25 | 0.025542 | -3.6674 | 5 | 1 | 20359 | 0.00024559 | -8.3118 | 2008 | 8 | August-2008 | 0.025542 | 0.000246 | 2009
2008-08-26 | 0.070485 | -2.6524 | 12 | 2 | 20359 | 0.00058942 | -7.4364 | 2008 | 8 | August-2008 | 0.070485 | 0.000589 | 2009
2008-08-27 | 0.0018174 | -6.3104 | 448 | 1 | 20359 | 0.022005 | -3.8165 | 2008 | 8 | August-2008 | 0.001817 | 0.022005 | 2009
2008-08-28 | 0.28027 | -1.272 | 30 | 4 | 20359 | 0.0014735 | -6.5201 | 2008 | 8 | August-2008 | 0.28027 | 0.001474 | 2009
2008-08-29 | 0.1419 | -1.9526 | 51 | 4 | 20359 | 0.002505 | -5.9895 | 2008 | 8 | August-2008 | 0.1419 | 0.002505 | 2009
2008-09-01 | 0.17663 | -1.7337 | 20 | 2 | 20359 | 0.00098237 | -6.9255 | 2008 | 9 | September-2008 | 0.17663 | 0.000982 | 2009
2008-09-02 | 1.1927 | 0.17625 | 219 | 8 | 20359 | 0.010757 | -4.5322 | 2008 | 9 | September-2008 | 1.1927 | 0.010757 | 2009
2008-09-04 | 0.12181 | -2.1053 | 18 | 3 | 20359 | 0.00088413 | -7.0309 | 2008 | 9 | September-2008 | 0.12181 | 0.000884 | 2009
2008-09-05 | 0.0092342 | -4.6848 | 4 | 2 | 20359 | 0.00019647 | -8.535 | 2008 | 9 | September-2008 | 0.009234 | 0.000196 | 2009
2008-09-08 | 0.14598 | -1.9243 | 21 | 2 | 20359 | 0.0010315 | -6.8768 | 2008 | 9 | September-2008 | 0.14598 | 0.001031 | 2009
2008-09-09 | 3.4008 | 1.224 | 383 | 39 | 20359 | 0.018812 | -3.9732 | 2008 | 9 | September-2008 | 3.4008 | 0.018812 | 2009
2008-09-10 | 1.1366 | 0.12804 | 120 | 10 | 20359 | 0.0058942 | -5.1338 | 2008 | 9 | September-2008 | 1.1366 | 0.005894 | 2009
2008-09-11 | 0.38558 | -0.95301 | 41 | 5 | 20359 | 0.0020139 | -6.2077 | 2008 | 9 | September-2008 | 0.38558 | 0.002014 | 2009
2008-09-12 | 0.10334 | -2.2697 | 26 | 6 | 20359 | 0.0012771 | -6.6632 | 2008 | 9 | September-2008 | 0.10335 | 0.001277 | 2009
2008-09-13 | 0.028292 | -3.5652 | 8 | 1 | 20359 | 0.00039295 | -7.8418 | 2008 | 9 | September-2008 | 0.028292 | 0.000393 | 2009
2008-09-14 | 0.052164 | -2.9534 | 18 | 1 | 20359 | 0.00088413 | -7.0309 | 2008 | 9 | September-2008 | 0.052164 | 0.000884 | 2009
2008-09-15 | 0.1255 | -2.0755 | 15 | 5 | 20359 | 0.00073677 | -7.2132 | 2008 | 9 | September-2008 | 0.1255 | 0.000737 | 2009
2008-09-16 | 0.42438 | -0.85712 | 36 | 1 | 20359 | 0.0017683 | -6.3378 | 2008 | 9 | September-2008 | 0.42438 | 0.001768 | 2009
2008-09-17 | 2.2165 | 0.79594 | 207 | 1 | 20359 | 0.010167 | -4.5886 | 2008 | 9 | September-2008 | 2.2165 | 0.010167 | 2009
2008-09-18 | 0.15423 | -1.8693 | 52 | 7 | 20359 | 0.0025542 | -5.97 | 2008 | 9 | September-2008 | 0.15423 | 0.002554 | 2009
2008-09-19 | 0.033155 | -3.4066 | 7 | 4 | 20359 | 0.00034383 | -7.9754 | 2008 | 9 | September-2008 | 0.033155 | 0.000344 | 2009
2008-09-21 | 0.038754 | -3.2505 | 3 | 1 | 20359 | 0.00014735 | -8.8227 | 2008 | 9 | September-2008 | 0.038754 | 0.000147 | 2009
2008-09-22 | 0.33145 | -1.1043 | 27 | 3 | 20359 | 0.0013262 | -6.6254 | 2008 | 9 | September-2008 | 0.33145 | 0.001326 | 2009
2008-09-23 | 0.068225 | -2.6849 | 31 | 2 | 20359 | 0.0015227 | -6.4873 | 2008 | 9 | September-2008 | 0.068225 | 0.001523 | 2009
2008-09-24 | 0.16956 | -1.7746 | 7 | 2 | 20359 | 0.00034383 | -7.9754 | 2008 | 9 | September-2008 | 0.16956 | 0.000344 | 2009
2008-09-27 | 0.5234 | -0.6474 | 64 | 2 | 20359 | 0.0031436 | -5.7624 | 2008 | 9 | September-2008 | 0.52341 | 0.003144 | 2009
2008-09-29 | 0.69424 | -0.36494 | 37 | 1 | 20359 | 0.0018174 | -6.3104 | 2008 | 9 | September-2008 | 0.69424 | 0.001817 | 2009
2008-10-01 | 0.45406 | -0.78953 | 63 | 2 | 20330 | 0.0030989 | -5.7767 | 2008 | 10 | October-2008 | 0.45406 | 0.003099 | 2009
2008-10-02 | 0.31185 | -1.1652 | 27 | 1 | 20330 | 0.0013281 | -6.624 | 2008 | 10 | October-2008 | 0.31185 | 0.001328 | 2009
2008-10-05 | 0.18401 | -1.6927 | 56 | 3 | 20330 | 0.0027545 | -5.8945 | 2008 | 10 | October-2008 | 0.18401 | 0.002755 | 2009
2008-10-06 | 0.85711 | -0.15419 | 132 | 4 | 20330 | 0.0064929 | -5.0371 | 2008 | 10 | October-2008 | 0.85711 | 0.006493 | 2009
2008-10-07 | 11.7909 | 2.4673 | 1962 | 15 | 20330 | 0.096508 | -2.3381 | 2008 | 10 | October-2008 | 11.7909 | 0.096508 | 2009
2008-10-08 | 0.071077 | -2.644 | 5 | 1 | 20330 | 0.00024594 | -8.3104 | 2008 | 10 | October-2008 | 0.071077 | 0.000246 | 2009
2008-10-09 | 5.0739 | 1.6241 | 533 | 3 | 20330 | 0.026217 | -3.6413 | 2008 | 10 | October-2008 | 5.0739 | 0.026217 | 2009
2008-10-10 | 0.059911 | -2.8149 | 21 | 1 | 20330 | 0.001033 | -6.8753 | 2008 | 10 | October-2008 | 0.059911 | 0.001033 | 2009
2008-10-13 | 0.02361 | -3.7461 | 5 | 1 | 20330 | 0.00024594 | -8.3104 | 2008 | 10 | October-2008 | 0.02361 | 0.000246 | 2009
2008-10-15 | 0.030448 | -3.4917 | 8 | 2 | 20330 | 0.00039351 | -7.8404 | 2008 | 10 | October-2008 | 0.030448 | 0.000394 | 2009
2008-10-16 | 0.049828 | -2.9992 | 13 | 3 | 20330 | 0.00063945 | -7.3549 | 2008 | 10 | October-2008 | 0.049828 | 0.000639 | 2009
2008-10-17 | 0.3664 | -1.004 | 39 | 1 | 20330 | 0.0019183 | -6.2563 | 2008 | 10 | October-2008 | 0.3664 | 0.001918 | 2009
2008-10-18 | 0.47447 | -0.74555 | 63 | 3 | 20330 | 0.0030989 | -5.7767 | 2008 | 10 | October-2008 | 0.47447 | 0.003099 | 2009
2008-10-19 | 0.052435 | -2.9482 | 26 | 1 | 20330 | 0.0012789 | -6.6618 | 2008 | 10 | October-2008 | 0.052435 | 0.001279 | 2009
2008-10-20 | 0.21835 | -1.5217 | 31 | 2 | 20330 | 0.0015248 | -6.4859 | 2008 | 10 | October-2008 | 0.21835 | 0.001525 | 2009
2008-10-21 | 1.1219 | 0.11506 | 86 | 2 | 20330 | 0.0042302 | -5.4655 | 2008 | 10 | October-2008 | 1.1219 | 0.00423 | 2009
2008-10-22 | 0.24127 | -1.4218 | 15 | 1 | 20330 | 0.00073783 | -7.2118 | 2008 | 10 | October-2008 | 0.24127 | 0.000738 | 2009
2008-10-23 | 1.7226 | 0.54385 | 470 | 2 | 20330 | 0.023119 | -3.7671 | 2008 | 10 | October-2008 | 1.7226 | 0.023119 | 2009
2008-10-24 | 0.029661 | -3.5179 | 67 | 1 | 20330 | 0.0032956 | -5.7152 | 2008 | 10 | October-2008 | 0.029661 | 0.003296 | 2009
2008-10-25 | 0.37757 | -0.974 | 25 | 4 | 20330 | 0.0012297 | -6.701 | 2008 | 10 | October-2008 | 0.37757 | 0.00123 | 2009
2008-10-26 | 0.58131 | -0.54247 | 1568 | 4 | 20330 | 0.077127 | -2.5623 | 2008 | 10 | October-2008 | 0.58131 | 0.077127 | 2009
2008-10-29 | 0.30738 | -1.1797 | 1167 | 2 | 20330 | 0.057403 | -2.8577 | 2008 | 10 | October-2008 | 0.30738 | 0.057403 | 2009
2008-10-31 | 0.5002 | -0.69275 | 34 | 3 | 20330 | 0.0016724 | -6.3935 | 2008 | 10 | October-2008 | 0.5002 | 0.001672 | 2009
2008-11-02 | 0.051339 | -2.9693 | 20 | 1 | 24153 | 0.00082805 | -7.0964 | 2008 | 11 | November-2008 | 0.051339 | 0.000828 | 2009
2008-11-03 | 0.47932 | -0.73539 | 78 | 4 | 24153 | 0.0032294 | -5.7355 | 2008 | 11 | November-2008 | 0.47932 | 0.003229 | 2009
2008-11-04 | 0.0080735 | -4.8192 | 3 | 1 | 24153 | 0.00012421 | -8.9936 | 2008 | 11 | November-2008 | 0.008074 | 0.000124 | 2009
2008-11-05 | 2.2109 | 0.79338 | 587 | 7 | 24153 | 0.024303 | -3.7171 | 2008 | 11 | November-2008 | 2.2109 | 0.024303 | 2009
2008-11-06 | 0.27607 | -1.2871 | 25 | 4 | 24153 | 0.0010351 | -6.8733 | 2008 | 11 | November-2008 | 0.27607 | 0.001035 | 2009
2008-11-07 | 1.0036 | 0.0035956 | 1154 | 4 | 24153 | 0.047779 | -3.0412 | 2008 | 11 | November-2008 | 1.0036 | 0.047779 | 2009
2008-11-10 | 0.02981 | -3.5129 | 4 | 1 | 24153 | 0.00016561 | -8.7059 | 2008 | 11 | November-2008 | 0.02981 | 0.000166 | 2009
2008-11-11 | 0.96758 | -0.032955 | 107 | 3 | 24153 | 0.0044301 | -5.4193 | 2008 | 11 | November-2008 | 0.96758 | 0.00443 | 2009
2008-11-12 | 0.84896 | -0.16374 | 373 | 4 | 24153 | 0.015443 | -4.1706 | 2008 | 11 | November-2008 | 0.84896 | 0.015443 | 2009
2008-11-14 | 0.092659 | -2.3788 | 20 | 2 | 24153 | 0.00082805 | -7.0964 | 2008 | 11 | November-2008 | 0.092659 | 0.000828 | 2009
2008-11-17 | 2.5781 | 0.94706 | 369 | 1 | 24153 | 0.015278 | -4.1814 | 2008 | 11 | November-2008 | 2.5781 | 0.015278 | 2009
2008-11-18 | 0.26779 | -1.3175 | 54 | 2 | 24153 | 0.0022357 | -6.1032 | 2008 | 11 | November-2008 | 0.26779 | 0.002236 | 2009
2008-11-19 | 0.041568 | -3.1804 | 251 | 1 | 24153 | 0.010392 | -4.5667 | 2008 | 11 | November-2008 | 0.041568 | 0.010392 | 2009
2008-11-20 | 0.048193 | -3.0325 | 582 | 1 | 24153 | 0.024096 | -3.7257 | 2008 | 11 | November-2008 | 0.048193 | 0.024096 | 2009
2008-11-21 | 2.5454 | 0.9343 | 932 | 5 | 24153 | 0.038587 | -3.2548 | 2008 | 11 | November-2008 | 2.5454 | 0.038587 | 2009
2008-11-22 | 0.00062104 | -7.3841 | 1 | 1 | 24153 | 4.1403e-05 | -10.0922 | 2008 | 11 | November-2008 | 0.000621 | 4.1e-05 | 2009
2008-11-23 | 0.31189 | -1.1651 | 80 | 2 | 24153 | 0.0033122 | -5.7101 | 2008 | 11 | November-2008 | 0.31189 | 0.003312 | 2009
2008-11-24 | 2.2125 | 0.79411 | 314 | 2 | 24153 | 0.013 | -4.3428 | 2008 | 11 | November-2008 | 2.2125 | 0.013 | 2009
2008-11-25 | 0.24494 | -1.4067 | 47 | 3 | 24153 | 0.0019459 | -6.242 | 2008 | 11 | November-2008 | 0.24494 | 0.001946 | 2009
2008-11-26 | 0.074442 | -2.5977 | 15 | 2 | 24153 | 0.00062104 | -7.3841 | 2008 | 11 | November-2008 | 0.074442 | 0.000621 | 2009
2008-11-27 | 1.1287 | 0.12109 | 120 | 9 | 24153 | 0.0049683 | -5.3047 | 2008 | 11 | November-2008 | 1.1287 | 0.004968 | 2009
2008-11-28 | 0.039291 | -3.2368 | 5 | 3 | 24153 | 0.00020701 | -8.4827 | 2008 | 11 | November-2008 | 0.039291 | 0.000207 | 2009
2008-11-29 | 0.073324 | -2.6129 | 11 | 1 | 24153 | 0.00045543 | -7.6943 | 2008 | 11 | November-2008 | 0.073324 | 0.000455 | 2009
2008-11-30 | 0.013249 | -4.3238 | 2 | 1 | 24153 | 8.2805e-05 | -9.399 | 2008 | 11 | November-2008 | 0.013249 | 8.3e-05 | 2009
2008-12-01 | 0.1217 | -2.1062 | 40 | 4 | 24142 | 0.0016569 | -6.4028 | 2008 | 12 | December-2008 | 0.1217 | 0.001657 | 2009
2008-12-02 | 0.37677 | -0.97612 | 46 | 4 | 24142 | 0.0019054 | -6.2631 | 2008 | 12 | December-2008 | 0.37677 | 0.001905 | 2009
2008-12-03 | 0.48476 | -0.72411 | 205 | 5 | 24142 | 0.0084914 | -4.7687 | 2008 | 12 | December-2008 | 0.48476 | 0.008491 | 2009
2008-12-04 | 0.55401 | -0.59057 | 146 | 4 | 24142 | 0.0060476 | -5.1081 | 2008 | 12 | December-2008 | 0.55401 | 0.006048 | 2009
2008-12-05 | 1.2504 | 0.22349 | 98 | 5 | 24142 | 0.0040593 | -5.5067 | 2008 | 12 | December-2008 | 1.2504 | 0.004059 | 2009
2008-12-06 | 0.037569 | -3.2816 | 7 | 4 | 24142 | 0.00028995 | -8.1458 | 2008 | 12 | December-2008 | 0.037569 | 0.00029 | 2009
2008-12-07 | 0.027545 | -3.5919 | 5 | 1 | 24142 | 0.00020711 | -8.4823 | 2008 | 12 | December-2008 | 0.027545 | 0.000207 | 2009
2008-12-08 | 0.26344 | -1.3339 | 295 | 2 | 24142 | 0.012219 | -4.4047 | 2008 | 12 | December-2008 | 0.26344 | 0.012219 | 2009
2008-12-09 | 0.0066275 | -5.0165 | 2 | 1 | 24142 | 8.2843e-05 | -9.3986 | 2008 | 12 | December-2008 | 0.006627 | 8.3e-05 | 2009
2008-12-10 | 1.1989 | 0.18141 | 62 | 2 | 24142 | 0.0025681 | -5.9646 | 2008 | 12 | December-2008 | 1.1989 | 0.002568 | 2009
2008-12-11 | 0.12319 | -2.094 | 67 | 2 | 24142 | 0.0027752 | -5.887 | 2008 | 12 | December-2008 | 0.12319 | 0.002775 | 2009
2008-12-12 | 0.45854 | -0.77971 | 135 | 1 | 24142 | 0.0055919 | -5.1864 | 2008 | 12 | December-2008 | 0.45854 | 0.005592 | 2009
2008-12-13 | 0.40635 | -0.90055 | 981 | 1 | 24142 | 0.040635 | -3.2031 | 2008 | 12 | December-2008 | 0.40635 | 0.040635 | 2009
2008-12-14 | 0.0086985 | -4.7446 | 5 | 1 | 24142 | 0.00020711 | -8.4823 | 2008 | 12 | December-2008 | 0.008699 | 0.000207 | 2009
2008-12-15 | 1.2075 | 0.18854 | 333 | 2 | 24142 | 0.013793 | -4.2836 | 2008 | 12 | December-2008 | 1.2075 | 0.013793 | 2009
2008-12-16 | 0.049457 | -3.0066 | 78 | 2 | 24142 | 0.0032309 | -5.735 | 2008 | 12 | December-2008 | 0.049457 | 0.003231 | 2009
2008-12-17 | 0.89023 | -0.11627 | 1034 | 2 | 24142 | 0.04283 | -3.1505 | 2008 | 12 | December-2008 | 0.89023 | 0.04283 | 2009
2008-12-18 | 0.016486 | -4.1053 | 199 | 1 | 24142 | 0.0082429 | -4.7984 | 2008 | 12 | December-2008 | 0.016486 | 0.008243 | 2009
2008-12-19 | 0.021539 | -3.8379 | 8 | 1 | 24142 | 0.00033137 | -8.0123 | 2008 | 12 | December-2008 | 0.021539 | 0.000331 | 2009
2008-12-20 | 0.074766 | -2.5934 | 159 | 2 | 24142 | 0.006586 | -5.0228 | 2008 | 12 | December-2008 | 0.074766 | 0.006586 | 2009
2008-12-22 | 0.015036 | -4.1973 | 3 | 2 | 24142 | 0.00012426 | -8.9931 | 2008 | 12 | December-2008 | 0.015036 | 0.000124 | 2009
2008-12-23 | 0.1806 | -1.7115 | 55 | 3 | 24142 | 0.0022782 | -6.0844 | 2008 | 12 | December-2008 | 0.1806 | 0.002278 | 2009
2008-12-25 | 0.015077 | -4.1946 | 14 | 1 | 24142 | 0.0005799 | -7.4527 | 2008 | 12 | December-2008 | 0.015077 | 0.00058 | 2009
2008-12-26 | 0.010438 | -4.5623 | 3 | 1 | 24142 | 0.00012426 | -8.9931 | 2008 | 12 | December-2008 | 0.010438 | 0.000124 | 2009
2008-12-28 | 0.36571 | -1.0059 | 981 | 1 | 24142 | 0.040635 | -3.2031 | 2008 | 12 | December-2008 | 0.36571 | 0.040635 | 2009
2008-12-29 | 0.3677 | -1.0005 | 45 | 2 | 24142 | 0.001864 | -6.285 | 2008 | 12 | December-2008 | 0.3677 | 0.001864 | 2009
2008-12-31 | 0.010521 | -4.5544 | 2 | 1 | 24142 | 8.2843e-05 | -9.3986 | 2008 | 12 | December-2008 | 0.010521 | 8.3e-05 | 2009
2009-01-03 | 0.68493 | -0.37844 | 100 | 2 | 24163 | 0.0041386 | -5.4874 | 2009 | 1 | January-2009 | 0.68493 | 0.004139 | 2009
2009-01-05 | 0.0059595 | -5.1228 | 2 | 1 | 24163 | 8.2771e-05 | -9.3994 | 2009 | 1 | January-2009 | 0.00596 | 8.3e-05 | 2009
2009-01-06 | 0.64139 | -0.44411 | 211 | 2 | 24163 | 0.0087324 | -4.7407 | 2009 | 1 | January-2009 | 0.64139 | 0.008732 | 2009
2009-01-08 | 1.3819 | 0.32349 | 1345 | 5 | 24163 | 0.055664 | -2.8884 | 2009 | 1 | January-2009 | 1.3819 | 0.055664 | 2009
2009-01-09 | 0.76294 | -0.27057 | 137 | 3 | 24163 | 0.0056698 | -5.1726 | 2009 | 1 | January-2009 | 0.76294 | 0.00567 | 2009
2009-01-10 | 0.078798 | -2.5409 | 17 | 1 | 24163 | 0.00070356 | -7.2594 | 2009 | 1 | January-2009 | 0.078798 | 0.000704 | 2009
2009-01-12 | 0.70604 | -0.34809 | 292 | 3 | 24163 | 0.012085 | -4.4158 | 2009 | 1 | January-2009 | 0.70604 | 0.012085 | 2009
2009-01-13 | 0.90891 | -0.095509 | 1390 | 3 | 24163 | 0.057526 | -2.8555 | 2009 | 1 | January-2009 | 0.90891 | 0.057526 | 2009
2009-01-14 | 1.5325 | 0.42691 | 182 | 6 | 24163 | 0.0075322 | -4.8886 | 2009 | 1 | January-2009 | 1.5325 | 0.007532 | 2009
2009-01-15 | 0.10955 | -2.2114 | 56 | 4 | 24163 | 0.0023176 | -6.0672 | 2009 | 1 | January-2009 | 0.10955 | 0.002318 | 2009
2009-01-16 | 0.23093 | -1.4656 | 51 | 2 | 24163 | 0.0021107 | -6.1608 | 2009 | 1 | January-2009 | 0.23093 | 0.002111 | 2009
2009-01-17 | 2.652 | 0.97531 | 282 | 1 | 24163 | 0.011671 | -4.4507 | 2009 | 1 | January-2009 | 2.652 | 0.011671 | 2009
2009-01-18 | 0.24633 | -1.4011 | 55 | 2 | 24163 | 0.0022762 | -6.0852 | 2009 | 1 | January-2009 | 0.24633 | 0.002276 | 2009
2009-01-19 | 0.27112 | -1.3052 | 108 | 2 | 24163 | 0.0044696 | -5.4104 | 2009 | 1 | January-2009 | 0.27112 | 0.00447 | 2009
2009-01-20 | 0.16658 | -1.7923 | 72 | 3 | 24163 | 0.0029798 | -5.8159 | 2009 | 1 | January-2009 | 0.16658 | 0.00298 | 2009
2009-01-21 | 0.29984 | -1.2045 | 35 | 1 | 24163 | 0.0014485 | -6.5372 | 2009 | 1 | January-2009 | 0.29984 | 0.001448 | 2009
2009-01-22 | 0.22485 | -1.4923 | 68 | 3 | 24163 | 0.0028142 | -5.8731 | 2009 | 1 | January-2009 | 0.22485 | 0.002814 | 2009
2009-01-23 | 0.099946 | -2.3031 | 65 | 4 | 24163 | 0.0026901 | -5.9182 | 2009 | 1 | January-2009 | 0.099946 | 0.00269 | 2009
2009-01-26 | 0.087655 | -2.4344 | 30 | 3 | 24163 | 0.0012416 | -6.6914 | 2009 | 1 | January-2009 | 0.087655 | 0.001242 | 2009
2009-01-27 | 0.50478 | -0.68363 | 431 | 6 | 24163 | 0.017837 | -4.0265 | 2009 | 1 | January-2009 | 0.50478 | 0.017837 | 2009
2009-01-28 | 1.5423 | 0.43329 | 94 | 3 | 24163 | 0.0038902 | -5.5493 | 2009 | 1 | January-2009 | 1.5423 | 0.00389 | 2009
2009-01-29 | 0.17034 | -1.7699 | 51 | 2 | 24163 | 0.0021107 | -6.1608 | 2009 | 1 | January-2009 | 0.17034 | 0.002111 | 2009
2009-01-30 | 0.035012 | -3.3521 | 6 | 1 | 24163 | 0.00024831 | -8.3008 | 2009 | 1 | January-2009 | 0.035012 | 0.000248 | 2009
2009-02-01 | 0.029616 | -3.5194 | 24 | 3 | 24176 | 0.00099272 | -6.9151 | 2009 | 2 | February-2009 | 0.029616 | 0.000993 | 2009
2009-02-02 | 0.083347 | -2.4847 | 11 | 2 | 24176 | 0.000455 | -7.6952 | 2009 | 2 | February-2009 | 0.083347 | 0.000455 | 2009
2009-02-03 | 0.040329 | -3.2107 | 3 | 1 | 24176 | 0.00012409 | -8.9945 | 2009 | 2 | February-2009 | 0.040329 | 0.000124 | 2009
2009-02-04 | 0.11317 | -2.1789 | 19 | 1 | 24176 | 0.0007859 | -7.1487 | 2009 | 2 | February-2009 | 0.11317 | 0.000786 | 2009
2009-02-05 | 0.70876 | -0.34424 | 150 | 3 | 24176 | 0.0062045 | -5.0825 | 2009 | 2 | February-2009 | 0.70876 | 0.006205 | 2009
2009-02-07 | 0.017621 | -4.0387 | 3 | 1 | 24176 | 0.00012409 | -8.9945 | 2009 | 2 | February-2009 | 0.017621 | 0.000124 | 2009
2009-02-08 | 0.545 | -0.60696 | 48 | 1 | 24176 | 0.0019854 | -6.2219 | 2009 | 2 | February-2009 | 0.545 | 0.001985 | 2009
2009-02-09 | 1.2947 | 0.25826 | 139 | 1 | 24176 | 0.0057495 | -5.1586 | 2009 | 2 | February-2009 | 1.2947 | 0.00575 | 2009
2009-02-10 | 1.0676 | 0.065402 | 765 | 7 | 24176 | 0.031643 | -3.4532 | 2009 | 2 | February-2009 | 1.0676 | 0.031643 | 2009
2009-02-11 | 0.38034 | -0.9667 | 128 | 3 | 24176 | 0.0052945 | -5.2411 | 2009 | 2 | February-2009 | 0.38034 | 0.005295 | 2009
2009-02-12 | 3.9779 | 1.3807 | 3025 | 7 | 24176 | 0.12512 | -2.0784 | 2009 | 2 | February-2009 | 3.9779 | 0.12512 | 2009
2009-02-13 | 0.57052 | -0.5612 | 50 | 3 | 24176 | 0.0020682 | -6.1811 | 2009 | 2 | February-2009 | 0.57052 | 0.002068 | 2009
2009-02-14 | 0.39428 | -0.93071 | 21 | 1 | 24176 | 0.00086863 | -7.0486 | 2009 | 2 | February-2009 | 0.39427 | 0.000869 | 2009
2009-02-16 | 0.1494 | -1.9011 | 28 | 1 | 24176 | 0.0011582 | -6.7609 | 2009 | 2 | February-2009 | 0.1494 | 0.001158 | 2009
2009-02-17 | 0.20872 | -1.5668 | 581 | 4 | 24176 | 0.024032 | -3.7284 | 2009 | 2 | February-2009 | 0.20872 | 0.024032 | 2009
2009-02-18 | 0.53007 | -0.63474 | 327 | 2 | 24176 | 0.013526 | -4.3032 | 2009 | 2 | February-2009 | 0.53007 | 0.013526 | 2009
2009-02-19 | 0.012905 | -4.3501 | 5 | 2 | 24176 | 0.00020682 | -8.4837 | 2009 | 2 | February-2009 | 0.012905 | 0.000207 | 2009
2009-02-20 | 1.0831 | 0.079865 | 1729 | 8 | 24176 | 0.071517 | -2.6378 | 2009 | 2 | February-2009 | 1.0831 | 0.071517 | 2009
2009-02-21 | 2.0873 | 0.73586 | 494 | 2 | 24176 | 0.020433 | -3.8906 | 2009 | 2 | February-2009 | 2.0873 | 0.020433 | 2009
2009-02-23 | 1.5646 | 0.44761 | 390 | 4 | 24176 | 0.016132 | -4.127 | 2009 | 2 | February-2009 | 1.5646 | 0.016132 | 2009
2009-02-24 | 0.95194 | -0.049258 | 746 | 4 | 24176 | 0.030857 | -3.4784 | 2009 | 2 | February-2009 | 0.95194 | 0.030857 | 2009
2009-02-25 | 0.1748 | -1.7441 | 502 | 2 | 24176 | 0.020764 | -3.8745 | 2009 | 2 | February-2009 | 0.1748 | 0.020764 | 2009
2009-02-26 | 1.9903 | 0.6883 | 484 | 1 | 24176 | 0.02002 | -3.911 | 2009 | 2 | February-2009 | 1.9903 | 0.02002 | 2009
2009-02-27 | 0.86499 | -0.14504 | 784 | 2 | 24176 | 0.032429 | -3.4287 | 2009 | 2 | February-2009 | 0.86499 | 0.032429 | 2009
2009-02-28 | 4.6982 | 1.5472 | 690 | 16 | 24176 | 0.028541 | -3.5564 | 2009 | 2 | February-2009 | 4.6982 | 0.028541 | 2009
2009-03-01 | 1.0093 | 0.0092189 | 104 | 5 | 24186 | 0.0043 | -5.4491 | 2009 | 3 | March-2009 | 1.0093 | 0.0043 | 2009
2009-03-02 | 0.14496 | -1.9313 | 503 | 3 | 24186 | 0.020797 | -3.8729 | 2009 | 3 | March-2009 | 0.14496 | 0.020797 | 2009
2009-03-04 | 2.2581 | 0.81453 | 728 | 2 | 24186 | 0.0301 | -3.5032 | 2009 | 3 | March-2009 | 2.2581 | 0.0301 | 2009
2009-03-05 | 0.11254 | -2.1844 | 501 | 5 | 24186 | 0.020714 | -3.8769 | 2009 | 3 | March-2009 | 0.11254 | 0.020714 | 2009
2009-03-06 | 0.033036 | -3.4102 | 5 | 2 | 24186 | 0.00020673 | -8.4841 | 2009 | 3 | March-2009 | 0.033036 | 0.000207 | 2009
2009-03-07 | 0.038411 | -3.2594 | 40 | 3 | 24186 | 0.0016538 | -6.4046 | 2009 | 3 | March-2009 | 0.038411 | 0.001654 | 2009
2009-03-09 | 0.95559 | -0.045422 | 264 | 7 | 24186 | 0.010915 | -4.5176 | 2009 | 3 | March-2009 | 0.95559 | 0.010915 | 2009
2009-03-10 | 0.10886 | -2.2177 | 489 | 1 | 24186 | 0.020218 | -3.9012 | 2009 | 3 | March-2009 | 0.10887 | 0.020218 | 2009
2009-03-11 | 0.61842 | -0.48059 | 552 | 6 | 24186 | 0.022823 | -3.78 | 2009 | 3 | March-2009 | 0.61842 | 0.022823 | 2009
2009-03-12 | 0.013727 | -4.2884 | 2 | 2 | 24186 | 8.2692e-05 | -9.4004 | 2009 | 3 | March-2009 | 0.013727 | 8.3e-05 | 2009
2009-03-13 | 0.20086 | -1.6051 | 9 | 3 | 24186 | 0.00037212 | -7.8963 | 2009 | 3 | March-2009 | 0.20086 | 0.000372 | 2009
2009-03-14 | 0.14752 | -1.9138 | 8 | 1 | 24186 | 0.00033077 | -8.0141 | 2009 | 3 | March-2009 | 0.14752 | 0.000331 | 2009
2009-03-15 | 0.066857 | -2.7052 | 11 | 1 | 24186 | 0.00045481 | -7.6956 | 2009 | 3 | March-2009 | 0.066857 | 0.000455 | 2009
2009-03-17 | 0.24808 | -1.394 | 15 | 1 | 24186 | 0.00062019 | -7.3855 | 2009 | 3 | March-2009 | 0.24808 | 0.00062 | 2009
2009-03-18 | 0.14508 | -1.9304 | 29 | 1 | 24186 | 0.001199 | -6.7262 | 2009 | 3 | March-2009 | 0.14508 | 0.001199 | 2009
2009-03-19 | 0.23468 | -1.4495 | 41 | 2 | 24186 | 0.0016952 | -6.38 | 2009 | 3 | March-2009 | 0.23468 | 0.001695 | 2009
2009-03-20 | 0.14761 | -1.9132 | 70 | 1 | 24186 | 0.0028942 | -5.845 | 2009 | 3 | March-2009 | 0.14761 | 0.002894 | 2009
2009-03-22 | 0.15294 | -1.8777 | 31 | 2 | 24186 | 0.0012817 | -6.6595 | 2009 | 3 | March-2009 | 0.15294 | 0.001282 | 2009
2009-03-23 | 0.75151 | -0.28567 | 631 | 5 | 24186 | 0.026089 | -3.6462 | 2009 | 3 | March-2009 | 0.75151 | 0.026089 | 2009
2009-03-24 | 0.78661 | -0.24002 | 542 | 3 | 24186 | 0.02241 | -3.7983 | 2009 | 3 | March-2009 | 0.78661 | 0.02241 | 2009
2009-03-25 | 0.45278 | -0.79234 | 511 | 4 | 24186 | 0.021128 | -3.8572 | 2009 | 3 | March-2009 | 0.45278 | 0.021128 | 2009
2009-03-26 | 2.3371 | 0.84891 | 2378 | 4 | 24186 | 0.098321 | -2.3195 | 2009 | 3 | March-2009 | 2.3371 | 0.098321 | 2009
2009-03-27 | 0.45973 | -0.77712 | 558 | 3 | 24186 | 0.023071 | -3.7692 | 2009 | 3 | March-2009 | 0.45973 | 0.023071 | 2009
2009-03-28 | 0.65914 | -0.41682 | 1579 | 2 | 24186 | 0.065286 | -2.729 | 2009 | 3 | March-2009 | 0.65914 | 0.065286 | 2009
2009-03-30 | 0.0031837 | -5.7497 | 1 | 1 | 24186 | 4.1346e-05 | -10.0935 | 2009 | 3 | March-2009 | 0.003184 | 4.1e-05 | 2009
2009-03-31 | 0.59522 | -0.51882 | 509 | 3 | 24186 | 0.021045 | -3.8611 | 2009 | 3 | March-2009 | 0.59522 | 0.021045 | 2009

## (1d)_2005-09_StDev_buffer
Summary Data
(based on pivot of MasterDataset)
Year | Total Actual SAIDI | SAIDI Norm | Total Actual SAIFI | SAIFI Norm
2005 | 288.0467 | 285.568 | 3.7301 | 3.7301
2006 | 270.7943 | 264.0431 | 3.7167 | 3.7167
2007 | 330.1244 | 272.7971 | 3.0841 | 3.0695
2008 | 252.6152 | 252.6152 | 2.8542 | 2.8542
2009 | 293.1812 | 275.9254 | 4.9902 | 4.9902
| µSAIDI | 270.1898 | µSAIFI | 3.6722
| σSAIDI | 37.5023 | σSAIFI | 0.48248
| SAIDILIMIT | 307.6921 | SAIFILIMIT | 4.1546

## (1e)_2005-09_SummaryNorm
2005-2009 Summary Sheet with Normalised
SAIDI (Interruption Duration)
| Disclosed Actuals by Class |  |  |  | TLC 2005-09 Dataset Actuals by Class |  |  |  | Variance in Actuals by Class |  |  | SAIDI Normalised
Year | Class B | Class C | Total |  | Class B | Class C | Total SAIDI Actual |  | Class B | Class C | Total | TLC 2005-09 Dataset | Boundaries Dataset | Variance in Normalised
2005 | 92.61 | 171.93 | 264.54 |  | 112.5257 | 188.5086 | 301.0343 |  | -19.9157 | -16.5786 | -36.4943 | 298.5556 | 285.568 | 12.9876
2006 | 97.51 | 180.01 | 277.52 |  | 102.0353 | 168.759 | 270.7943 |  | -4.5253 | 11.251 | 6.7257 | 264.0431 | 264.0431 | -4.0175e-06
2007 | 101.24 | 232.6 | 333.84 |  | 109.6611 | 220.4633 | 330.1244 |  | -8.4211 | 12.1367 | 3.7156 | 272.7972 | 272.7971 | 6.6965e-05
2008 | 81.34 | 165.38 | 246.72 |  | 90.2223 | 162.3931 | 252.6154 |  | -8.8823 | 2.9869 | -5.8954 | 252.6154 | 252.6152 | 0.00019
2009 | 57.71 | 237.41 | 295.12 |  | 55.9484 | 237.2402 | 293.1886 |  | 1.7616 | 0.1698 | 1.9314 | 275.9328 | 275.9254 | 0.007346
SAIFI (Interruption Frequency)
| Disclosed Actuals by Class |  |  |  | TLC 2005-09 Dataset Actuals by Class |  |  |  | Variances in Actuals by Class |  |  | SAIFI Normalised
Year | Class B | Class C | Total |  | Class B | Class C | Total SAIFI Actual |  | Class B | Class C | Total | TLC 2005-09 Dataset | Boundaries Dataset | Variance in Normalised
2005 | 0.5 | 2.97 | 3.47 |  | 0.60399 | 3.3033 | 3.9072 |  | -0.10399 | -0.33326 | -0.43725 | 3.9072 | 3.7301 | 0.17713
2006 | 0.6 | 3.16 | 3.76 |  | 0.632 | 3.0848 | 3.7168 |  | -0.031995 | 0.075155 | 0.04316 | 3.7168 | 3.7167 | 0.00010477
2007 | 0.52 | 2.73 | 3.25 |  | 0.56978 | 2.5143 | 3.0841 |  | -0.049782 | 0.21571 | 0.16593 | 3.0695 | 3.0695 | -2.149e-06
2008 | 0.34 | 2.57 | 2.91 |  | 0.38103 | 2.4749 | 2.8559 |  | -0.041026 | 0.095087 | 0.05406 | 2.8559 | 2.8542 | 0.0017096
2009 | 0.81 | 3.88 | 4.69 |  | 0.87385 | 4.1164 | 4.9903 |  | -0.063847 | -0.23643 | -0.30027 | 4.9903 | 4.9902 | 6.6012e-05
Source = "(1a)_2005-09_incidents" | [6 empty] | Source = "(1b)_2005-09_dailyAggregates"
| SAIDI Actual | SAIDI Actual | SAIDI Actual | SAIFI Actual | SAIFI Actual | SAIFI Actual
Year | Class B | Class C | Total SAIDI Actual | Class B | Class C | Total SAIFI Actual | SAIDI Normalised | SAIFI Normalised | chk_SAIDI Actual | chk_SAIFI Actual
2004/2005 | 112.5257 | 188.5086 | 301.0343 | 0.60399 | 3.3033 | 3.9072 | 298.5556 | 3.9072 | 301.0343 | 3.9072
2005/2006 | 102.0353 | 168.759 | 270.7943 | 0.632 | 3.0848 | 3.7168 | 264.0431 | 3.7168 | 270.7943 | 3.7168
2006/2007 | 109.6611 | 220.4633 | 330.1244 | 0.56978 | 2.5143 | 3.0841 | 272.7972 | 3.0695 | 330.1244 | 3.0841
2007/2008 | 90.2223 | 162.3931 | 252.6154 | 0.38103 | 2.4749 | 2.8559 | 252.6154 | 2.8559 | 252.6154 | 2.8559
2008/2009 | 55.9484 | 237.2402 | 293.1886 | 0.87385 | 4.1164 | 4.9903 | 275.9328 | 4.9903 | 293.1886 | 4.9903
Column Labels
|  |  | Total Sum of SAIDI for Outage | Planned - TLC : Class B | Unplanned - TLC : Class C | Total Sum of calcSAIFI
Row Labels | Sum of SAIDI for Outage | Sum of SAIDI for Outage |  | Sum of calcSAIFI | Sum of calcSAIFI |  | Row Labels | Sum of SAIDI Normalised | Sum of SAIFI Normalised
2004/2005 | 112.5257 | 188.5086 | 301.0343 | 0.60399 | 3.3033 | 3.9072 | 2004/2005 | 298.5556 | 3.9072
2005/2006 | 102.0353 | 168.759 | 270.7943 | 0.632 | 3.0848 | 3.7168 | 2005/2006 | 264.0431 | 3.7168
2006/2007 | 109.6611 | 220.4633 | 330.1244 | 0.56978 | 2.5143 | 3.0841 | 2006/2007 | 272.7972 | 3.0695
2007/2008 | 90.2223 | 162.3931 | 252.6154 | 0.38103 | 2.4749 | 2.8559 | 2007/2008 | 252.6154 | 2.8559
2008/2009 | 55.9484 | 237.2402 | 293.1886 | 0.87385 | 4.1164 | 4.9903 | 2008/2009 | 275.9328 | 4.9903 | 0 | 0

## (1f)_2005-09_Customers
2005-09 DPP Quality Limits : average customers per annum
Year | Average Customers
2005 | 19353
2006 | 19353
2007 | 19353
2008 | 19353
2009 | 21542.3322

## (2a)_2010-14_incidents
2010-2014 datasets : Individual incident data
Outage Extra Records from Basix : 19 September 2014 |  |  | int(Interrupted)
NB: 2014 records have audited following the 53ZD information request.
Key | Description | Interrupted | calcByDate | Restored | Outage Status | Op Asset Local ID | Operated Asset Descript | Fault Asset | Segment | Asset Group | Service Level | Feeder | Zone Substation | Failed Component | Cause Category | Cause Group | Cause | Cause | Type Group | Outage Type | Category | Voltage | Voltage Value | Helicopter Used | Outage Mins | Customers | Customer Total | Customer Mins | SAIDI for Outage | calcSAIF | Interrupted kVA | Load Losses | Financial Year | Month Year | Outage Month | Outage Year
21541 | Benneydale - Tapuwae Road | 2009-04-01 08:38 | 2009-04-01 | 2009-04-01 16:05 | Calculated | T3280 | T3280 - 1ph 15kVA POLEMNT |  | 103SEG270RET | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 313 | 19 | 24229 | 5937 | 0.24504 | 0.00078418 | 90 | 28120 | 2009/2010 | April-2009 | 4 | 2009
21543 | Paerata Road | 2009-04-01 09:26 | 2009-04-01 | 2009-04-01 10:29 | Calculated | T3225 | T3225 - 3ph 100kVA POLEMNT |  | No Segment | BHRFHF | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24229 |  | 0 | 0 |  |  | 2009/2010 | April-2009 | 4 | 2009
21544 | Benneydale - Tapuwae Road | 2009-04-02 08:34 | 2009-04-02 | 2009-04-02 08:38 | Calculated | T3280 | T3280 - 1ph 15kVA POLEMNT |  | 103SEG270RET | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 19 | 24229 | 6308 | 0.26035 | 0.00078418 | 90 | 29875 | 2009/2010 | April-2009 | 4 | 2009
21548 | Tihoi Road | 2009-04-02 10:23 | 2009-04-02 | 2009-04-02 11:40 | Calculated | T2770 | T2770 - 3ph 50kVA polemount |  | No Segment | Tihoi 124-02 RETIRED | Rural D | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 77 | 1 | 24229 | 77 | 0.00318 | 4.1273e-05 | 50 | 3850 | 2009/2010 | April-2009 | 4 | 2009
21552 | Maihiihi Road | 2009-04-02 16:30 | 2009-04-02 | 2009-04-02 17:15 | Calculated | T604 | T604 - 3ph 5kVA polemnt |  | 111SEG346-REG6 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 1 | 24229 | 45 | 0.00186 | 4.1273e-05 | 5 | 225 | 2009/2010 | April-2009 | 4 | 2009
21553 | Mahoenui | 2009-04-03 09:42 | 2009-04-03 | 2009-04-03 15:25 | Calculated | 1010 | 1010 - Mahoenui Oil Circuit Breaker 1010 |  | No Segment | 209-01 Mahoenui | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 343 | 47 | 24229 | 16135 | 0.66594 | 0.0019398 | 428 | 146903 | 2009/2010 | April-2009 | 4 | 2009
21554 | Paerata Road | 2009-04-03 09:45 | 2009-04-03 | 2009-04-03 11:32 | Calculated | T3260 | T3260 - 3ph 75kVA POLEMNT |  | 129SEG455-402 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24229 |  | 0 | 0 |  |  | 2009/2010 | April-2009 | 4 | 2009
21555 | Mangakahu Road | 2009-04-03 13:25 | 2009-04-03 | 2009-04-03 14:05 | Calculated | T4039 | T4039 - 1ph 10kVA POLEMNT |  | 402SEG5115-5108 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1 | 24229 | 40 | 0.00165 | 4.1273e-05 | 10 | 400 | 2009/2010 | April-2009 | 4 | 2009
21557 | Manunui Sub | 2009-04-04 01:10 | 2009-04-04 | 2009-04-04 01:21 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 4 | 24229 | 44 | 0.00182 | 0.00016509 | 450 | 4950 | 2009/2010 | April-2009 | 4 | 2009
21558 | Fauchelle Road | 2009-04-06 09:11 | 2009-04-06 | 2009-04-06 12:03 | Calculated | 5277 | 5277 - Sectionaliser with Bypass & Links5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 172 | 16 | 24229 | 2752 | 0.11358 | 0.00066037 | 135 | 23220 | 2009/2010 | April-2009 | 4 | 2009
21559 | Benneydale - Tapuwae Road | 2009-04-07 09:00 | 2009-04-07 | 2009-04-07 13:52 | Calculated | 1651 | 1651 - Fused Link 1651 |  | 103SEG1651-2227 | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 16 | 24229 | 4672 | 0.19283 | 0.00066037 | 90 | 26280 | 2009/2010 | April-2009 | 4 | 2009
21560 | Taumatamaire | 2009-04-07 09:32 | 2009-04-07 | 2009-04-07 09:35 | Calculated | 1633 | 1633 - Fused Link 1633 |  | 128SEG1603-1633 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 3 | 484 | 24229 | 3656 | 0.15089 | 0.019976 | 0 | 0 | 2009/2010 | April-2009 | 4 | 2009
21561 | Oparure road | 2009-04-07 14:19 | 2009-04-07 | 2009-04-07 15:19 | Calculated | 388 | 388 - ABS 388 |  | 107SEG388-295 | Oparure 107-03 | Rural C | Oparure | Gadsby Road Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 30 | 24229 | 1800 | 0.07429 | 0.0012382 | 285 | 17099 | 2009/2010 | April-2009 | 4 | 2009
21562 | Manunui Sub | 2009-04-08 04:01 | 2009-04-08 | 2009-04-08 04:12 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24229 |  | 0 | 0 |  |  | 2009/2010 | April-2009 | 4 | 2009
21563 | MAHOE ROAD | 2009-04-08 07:18 | 2009-04-08 | 2009-04-08 09:16 | Calculated | 08K22 | 08K22 - 2ph 15kVA POLEMNT | TF8K22 - Transformer Fuse: TF8K22 | 408SEG5816-5912 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 3 | 24229 | 354 | 0.01461 | 0.00012382 | 15 | 1770 | 2009/2010 | April-2009 | 4 | 2009
21564 | Ruatiti Sub | 2009-04-08 08:15 | 2009-04-08 | 2009-04-08 14:48 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | 410SEG5806-5793 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 393 | 69 | 24229 | 39474 | 1.6292 | 0.0028478 | 426.5 | 234292 | 2009/2010 | April-2009 | 4 | 2009
21565 | Pokuru Road | 2009-04-08 15:25 | 2009-04-08 | 2009-04-08 17:18 | Calculated | 442 | 442 - Fused Link 442 |  | 129SEG442-2238 | Tihoi 124-04 RETIRED | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 25 | 24229 | 2825 | 0.1166 | 0.0010318 | 265 | 29945 | 2009/2010 | April-2009 | 4 | 2009
21566 | Upper Retaruke sub | 2009-04-08 17:33 | 2009-04-08 | 2009-04-08 18:22 | Calculated | 5494 | 5494 - Recloser with Bypass 5494 |  | 410SEG5494-5493 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 47 | 24229 | 2303 | 0.09505 | 0.0019398 | 290 | 14209 | 2009/2010 | April-2009 | 4 | 2009
21567 | SH 41 | 2009-04-08 19:07 | 2009-04-08 | 2009-04-08 20:29 | Calculated | 09R06 | 09R06 - 1ph 15kVA POLEMNT | TF9R6 - Transformer Fuse: TF9R6 | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 4 | 24229 | 328 | 0.01354 | 0.00016509 | 15 | 1230 | 2009/2010 | April-2009 | 4 | 2009
21568 | SH4 | 2009-04-09 01:11 | 2009-04-09 | 2009-04-09 07:46 | Calculated | 1724 | 1724 - Sectionaliser 1724 |  | No Segment | No Asset Group | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 395 | 15 | 24229 | 5925 | 0.24454 | 0.00061909 | 143 | 56485 | 2009/2010 | April-2009 | 4 | 2009
21569 | Manunui Sub | 2009-04-09 03:04 | 2009-04-09 | 2009-04-09 03:14 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 4 | 24229 | 40 | 0.00165 | 0.00016509 | 450 | 4500 | 2009/2010 | April-2009 | 4 | 2009
21570 | Ruatiti sub | 2009-04-09 06:18 | 2009-04-09 | 2009-04-09 08:03 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | 410SEG5806-5793 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 69 | 24229 | 7245 | 0.29902 | 0.0028478 | 426.5 | 44782 | 2009/2010 | April-2009 | 4 | 2009
21573 | Pa Hill | 2009-04-09 08:11 | 2009-04-09 | 2009-04-09 12:58 | Calculated | 5719 | 5719 - Fused Link 5719 |  | 416SEG5719-5720 | Tangiwai 416-05 RETIRED | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 287 | 14 | 24229 | 4018 | 0.16583 | 0.00057782 | 80 | 22960 | 2009/2010 | April-2009 | 4 | 2009
21574 | Kawautahi Road | 2009-04-09 09:34 | 2009-04-09 | 2009-04-09 14:19 | Calculated | 5884 | 5884 - Recloser 5884 |  | 409SEG5884-5403 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 29 | 24229 | 8265 | 0.34112 | 0.0011969 | 225 | 64125 | 2009/2010 | April-2009 | 4 | 2009
21580 | Taupehi Road | 2009-04-10 21:35 | 2009-04-10 | 2009-04-10 22:20 | Calculated | 10S01 | 10S01 - 3ph 300kVA POLE MNT |  | 424SEG5942 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 58 | 24229 | 2610 | 0.10772 | 0.0023938 | 200 | 8999 | 2009/2010 | April-2009 | 4 | 2009
21582 | SH 1 | 2009-04-12 18:10 | 2009-04-12 | 2009-04-12 19:14 | Calculated | 09U05 | 09U05 - 3ph 100kVA POLEMNT |  | No Segment | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 53 | 24229 | 3392 | 0.14 | 0.0021875 | 100 | 6399 | 2009/2010 | April-2009 | 4 | 2009
21584 | Tangiwai Railway Station | 2009-04-14 10:05 | 2009-04-14 | 2009-04-14 12:47 | Calculated | 5689 | 5689 - Fused Link 5689 |  | 416SEG5689-5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 162 | 28 | 24229 | 4536 | 0.18721 | 0.0011556 | 290 | 46979 | 2009/2010 | April-2009 | 4 | 2009
21585 | Awatane Road | 2009-04-14 10:16 | 2009-04-14 | 2009-04-14 15:58 | Calculated | 787 | 787 - ABS 787 |  | 123SEG460-787 | Tihoi 124-04 RETIRED | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24229 |  | 0 | 0 |  |  | 2009/2010 | April-2009 | 4 | 2009
21586 | Waihuka Road | 2009-04-14 10:30 | 2009-04-14 | 2009-04-14 12:51 | Calculated | 5364 | 5364 - ABS 5364 |  | 421SEG5364-5874 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 141 | 106 | 24229 | 15040 | 0.62074 | 0.0043749 | 765 | 108564 | 2009/2010 | April-2009 | 4 | 2009
21587 | SH 3 | 2009-04-15 09:34 | 2009-04-15 | 2009-04-15 15:54 | Calculated | 1602 | 1602 - Earth Working Link 1602 |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 380 | 591 | 24229 | 5320 | 0.21957 | 0.024392 | 3554.5 | 37999 | 2009/2010 | April-2009 | 4 | 2009
21588 | Waiparemo Cres | 2009-04-15 09:37 | 2009-04-15 | 2009-04-15 10:22 | Calculated | 09R35 | 09R35 - 3ph 300kVA GNDPAD |  | No Segment | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 70 | 24229 | 4270 | 0.17624 | 0.0028891 | 300 | 18299 | 2009/2010 | April-2009 | 4 | 2009
21589 | Kamanawa Street | 2009-04-15 09:49 | 2009-04-15 | 2009-04-15 10:40 | Calculated | 09R14 | 09R14 - 3ph 200kVA GNDPAD |  | No Segment | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 211 | 24229 | 48673 | 2.0089 | 0.0087086 | 800 | 184999 | 2009/2010 | April-2009 | 4 | 2009
21590 | Ailsa Street | 2009-04-15 09:54 | 2009-04-15 | 2009-04-15 15:20 | Calculated | T8 | T8 - 3ph 200kVA GNDPAD |  | No Segment | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 326 | 55 | 24229 | 17930 | 0.74002 | 0.00227 | 200 | 65199 | 2009/2010 | April-2009 | 4 | 2009
21591 | Pa Hill | 2009-04-16 08:06 | 2009-04-16 | 2009-04-16 12:55 | Calculated | 5719 | 5719 - Fused Link 5719 |  | 416SEG5719-5720 | Tangiwai 416-05 RETIRED | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 289 | 14 | 24229 | 4046 | 0.16699 | 0.00057782 | 80 | 23120 | 2009/2010 | April-2009 | 4 | 2009
21592 | Ohura Road | 2009-04-16 10:03 | 2009-04-16 | 2009-04-16 12:12 | Calculated | T825 | T825 - 3ph 25kVA POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 129 | 2 | 24229 | 258 | 0.01065 | 8.2546e-05 | 25 | 3225 | 2009/2010 | April-2009 | 4 | 2009
21593 | Arohena Road | 2009-04-16 10:08 | 2009-04-16 | 2009-04-16 14:26 | Calculated | 425 | 425 - ABS 425 |  | 121SEG425-748 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 97 | 24229 | 25026 | 1.0329 | 0.0040035 | 804 | 207431 | 2009/2010 | April-2009 | 4 | 2009
21594 | Tirohanga Road | 2009-04-16 10:17 | 2009-04-16 | 2009-04-16 12:44 | Calculated | 451 | 451 - ABS 451 |  | 129SEG451-787 | BHRFHF | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24229 |  | 0 | 0 |  |  | 2009/2010 | April-2009 | 4 | 2009
21595 | Pihanga road | 2009-04-16 10:20 | 2009-04-16 | 2009-04-16 11:54 | Calculated | 6584 | 6584 - Ring Main Unit 6584 |  | 406SEG6584-6585 | Huirimu 121-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 178 | 24229 | 16732 | 0.69058 | 0.0073466 | 700 | 65799 | 2009/2010 | April-2009 | 4 | 2009
21596 | Ngapuke - Ngakonui Road | 2009-04-16 10:35 | 2009-04-16 | 2009-04-16 13:44 | Calculated | 08K04 | 08K04 - 1ph 15kVA POLEMNT |  | 408SEG5233-5514 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 189 | 4 | 24229 | 756 | 0.0312 | 0.00016509 | 15 | 2835 | 2009/2010 | April-2009 | 4 | 2009
21597 | Te Wautere Road | 2009-04-16 11:30 | 2009-04-16 | 2009-04-16 12:51 | Calculated | T1474 | T1474 - 3ph 25kVA POLEMNT |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 6 | 24229 | 486 | 0.02006 | 0.00024764 | 25 | 2024 | 2009/2010 | April-2009 | 4 | 2009
21598 | Haurua road | 2009-04-17 06:55 | 2009-04-17 | 2009-04-17 08:11 | Calculated | 1359 | 1359 - Fused Link 1359 | T363 - 3ph 30kVA POLEMNT | 112SEG1359 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 4 | 24229 | 304 | 0.01255 | 0.00016509 | 45 | 3420 | 2009/2010 | April-2009 | 4 | 2009
21599 | Main North Road | 2009-04-17 09:02 | 2009-04-17 | 2009-04-17 15:58 | Calculated | 5482 | 5482 - Fused Link 5482 |  | 402SEG5984-5484 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 416 | 12 | 24229 | 4992 | 0.20603 | 0.00049527 | 68 | 28287 | 2009/2010 | April-2009 | 4 | 2009
21603 | Waipuna Road - by Morgans | 2009-04-17 09:33 | 2009-04-17 | 2009-04-17 09:58 | Calculated | 291 | 291 - ABS 291 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 29 | 24229 | 725 | 0.02992 | 0.0011969 | 248 | 6199 | 2009/2010 | April-2009 | 4 | 2009
21601 | Arohena Road | 2009-04-17 09:42 | 2009-04-17 | 2009-04-17 14:26 | Calculated | T3032 | T3032 - 1ph 15kVA POLEMNT |  | 121SEG724-425RET | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 284 | 25 | 24229 | 5896 | 0.24334 | 0.0010318 | 395 | 77909 | 2009/2010 | April-2009 | 4 | 2009
21606 | RIVER ROAD | 2009-04-19 18:25 | 2009-04-19 | 2009-04-19 20:19 | Calculated | 5547 | 5547 - Circuit Breaker 5547 |  | No Segment | No Asset Group | Remote Rural F | Western | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 262 | 24229 | 29868 | 1.2327 | 0.010813 | 1869 | 213065 | 2009/2010 | April-2009 | 4 | 2009
21607 | Taringamotu Road | 2009-04-19 20:15 | 2009-04-19 | 2009-04-19 20:37 | Calculated | 07J10 | 07J10 - 2ph 50kVA POLEMNT |  | 402SEG5103-5369 | Northern 402-05 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 6 | 24229 | 132 | 0.00545 | 0.00024764 | 50 | 1099 | 2009/2010 | April-2009 | 4 | 2009
21608 | Waipuna Road | 2009-04-20 10:05 | 2009-04-20 | 2009-04-20 15:28 | Calculated | 286 | 286 - ABS 286 |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 323 | 10 | 24229 | 3230 | 0.13331 | 0.00041273 | 103 | 33269 | 2009/2010 | April-2009 | 4 | 2009
21612 | Aotearoa Road | 2009-04-20 18:06 | 2009-04-20 | 2009-04-20 18:34 | Calculated | 378 | 378 - Recloser with Bypass & Links 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 252 | 24229 | 7056 | 0.29122 | 0.010401 | 2278 | 63783 | 2009/2010 | April-2009 | 4 | 2009
21613 | Whatauri Road | 2009-04-20 18:06 | 2009-04-20 | 2009-04-20 19:43 | Calculated | 619 | 619 - ABS 619 |  | 122SEG619-REG35 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 63 | 24229 | 6111 | 0.25222 | 0.0026002 | 580 | 56259 | 2009/2010 | April-2009 | 4 | 2009
21614 | Hingaia Road | 2009-04-20 18:06 | 2009-04-20 | 2009-04-21 13:00 | Calculated | 371 | 371 - Air Break Switch 371 |  | 122SEG371-633 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1134 | 49 | 24229 | 55141 | 2.2758 | 0.0020224 | 272.5 | 306889 | 2009/2010 | April-2009 | 4 | 2009
23314 | Faulty Insulator @ P125/96 - Hingaia Road | 2009-04-20 18:06 | 2009-04-20 | 2009-04-21 13:13 | Calculated | 633 | 633 - Fused Link 633 |  | 122SEG633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24229 |  | 0 | 0 |  |  | 2009/2010 | April-2009 | 4 | 2009
21615 | Kaahu South Road | 2009-04-20 20:20 | 2009-04-20 | 2009-04-20 23:21 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tihoi 124-03 RETIRED | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 26 | 24229 | 4706 | 0.19423 | 0.0010731 | 300 | 54300 | 2009/2010 | April-2009 | 4 | 2009
21617 | Kaahu south Road | 2009-04-21 07:15 | 2009-04-21 | 2009-04-21 14:31 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tihoi 124-03 RETIRED | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 436 | 26 | 24229 | 11336 | 0.46787 | 0.0010731 | 300 | 130800 | 2009/2010 | April-2009 | 4 | 2009
21616 | HAPPY VALLEY | 2009-04-21 21:55 | 2009-04-21 | 2009-04-22 00:09 | Calculated | 357 | 357 - Fused Link 357 |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 29 | 24229 | 3886 | 0.16039 | 0.0011969 | 315 | 42209 | 2009/2010 | April-2009 | 4 | 2009
21622 | Fullerton Road | 2009-04-22 05:35 | 2009-04-22 | 2009-04-22 06:28 | Calculated | T65 | T65 - 2ph 15kVA POLEMNT |  | 107SEG234 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 2 | 24229 | 106 | 0.00437 | 8.2546e-05 | 15 | 795 | 2009/2010 | April-2009 | 4 | 2009
21623 | Tongaporutu | 2009-04-22 08:15 | 2009-04-22 | 2009-04-22 10:30 | Calculated | 1626 | 1626 - Sectionaliser with Bypass & Links 1626 |  | 128SEG1635-1626 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 132 | 24229 | 17820 | 0.73548 | 0.005448 | 813 | 109755 | 2009/2010 | April-2009 | 4 | 2009
21625 | Waihaha Road | 2009-04-22 10:07 | 2009-04-22 | 2009-04-22 16:01 | Calculated | 5534 | 5534 - Sectionaliser 5534 |  | No Segment | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 14 | 24229 | 4956 | 0.20455 | 0.00057782 | 93 | 32922 | 2009/2010 | April-2009 | 4 | 2009
21626 | Tunakotekote road | 2009-04-22 11:35 | 2009-04-22 | 2009-04-22 14:00 | Calculated | 09I11 | 09I11 - 1ph 3kVA POLEMNT |  | 403SEG5811-5315 | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 1 | 24229 | 145 | 0.00598 | 4.1273e-05 | 3 | 435 | 2009/2010 | April-2009 | 4 | 2009
21627 | Waiotaka Valley Road | 2009-04-23 09:02 | 2009-04-23 | 2009-04-23 13:34 | Calculated | 6548 | 6548 - ABS 6548 |  | 427SEG6548-5392 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 7 | 24229 | 1904 | 0.07858 | 0.00028891 | 80 | 21760 | 2009/2010 | April-2009 | 4 | 2009
21628 | Ranginui Road | 2009-04-23 09:49 | 2009-04-23 | 2009-04-23 15:57 | Calculated | T2705 | T2705 - 3ph 30kVA POLEMNT |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 368 | 2 | 24229 | 736 | 0.03038 | 8.2546e-05 | 30 | 11040 | 2009/2010 | April-2009 | 4 | 2009
21631 | Aria Road | 2009-04-23 13:43 | 2009-04-23 | 2009-04-23 14:48 | Calculated | T1937 | T1937 - 1ph 15kVA POLEMNT |  | 114SEG1109-1110 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 2 | 24229 | 130 | 0.00537 | 8.2546e-05 | 15 | 975 | 2009/2010 | April-2009 | 4 | 2009
21632 | Pungapunga Valley Road | 2009-04-24 08:05 | 2009-04-24 | 2009-04-24 09:22 | Calculated | 08M02 | 08M02 - 1ph 15kVA POLEMNT |  | 408SEG5515 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 2 | 24229 | 154 | 0.00636 | 8.2546e-05 | 15 | 1155 | 2009/2010 | April-2009 | 4 | 2009
21634 | Ranginui Road | 2009-04-24 09:00 | 2009-04-24 | 2009-04-24 11:16 | Calculated | T801 | T801 - 1ph 25kVA POLEMNT |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 136 | 3 | 24229 | 408 | 0.01684 | 0.00012382 | 25 | 3399 | 2009/2010 | April-2009 | 4 | 2009
21636 | Lees Block Road | 2009-04-24 14:55 | 2009-04-24 | 2009-04-24 15:20 | Calculated | T78 | T78 - 1ph 25kVA POL |  | 101SEG248 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 5 | 24229 | 125 | 0.00516 | 0.00020636 | 25 | 625 | 2009/2010 | April-2009 | 4 | 2009
21637 | Bayley Road | 2009-04-25 15:20 | 2009-04-25 | 2009-04-25 17:45 | Calculated | T2343 | T2343 - 3ph 50kVA POLEMNT |  | 122SEG616 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 2 | 24229 | 290 | 0.01197 | 8.2546e-05 | 50 | 7250 | 2009/2010 | April-2009 | 4 | 2009
21639 | Kepa Road | 2009-04-26 11:30 | 2009-04-26 | 2009-04-26 13:39 | Calculated | 10T08 | 10T08 - 1ph 50kVA POLEMNT |  | No Segment | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 7 | 24229 | 903 | 0.03727 | 0.00028891 | 50 | 6449 | 2009/2010 | April-2009 | 4 | 2009
21640 | Relocate 11kV Line between TX 10s10 & 4032 | 2009-04-27 09:08 | 2009-04-27 | 2009-04-27 15:02 | Calculated | 6548 | 6548 - ABS 6548 |  | 427SEG6548-5392 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 7 | 24229 | 2478 | 0.10227 | 0.00028891 | 80 | 28320 | 2009/2010 | April-2009 | 4 | 2009
21642 | Bird | 2009-04-27 10:25 | 2009-04-27 | 2009-04-27 14:15 | Calculated | T1217 | T1217 - 1ph 15kVA POL | T1217 - 1ph 15kVA POL | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 230 | 2 | 24229 | 460 | 0.01899 | 8.2546e-05 | 15 | 3450 | 2009/2010 | April-2009 | 4 | 2009
21643 | TX 07k16 - thrush | 2009-04-27 12:02 | 2009-04-27 | 2009-04-27 15:01 | Calculated | 07K16 | 07K16 - 3ph 25kVA POLEMNT | 07K16 - 3ph 25kVA POLEMNT | No Segment | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 2 | 24229 | 358 | 0.01478 | 8.2546e-05 | 25 | 4475 | 2009/2010 | April-2009 | 4 | 2009
21644 | LV fault | 2009-04-27 15:00 | 2009-04-27 | 2009-04-27 16:15 | Calculated | 17H04 | 17H04 - 1ph 10kVA POLEMNT | 17H04 | 410SEG5510-5511 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 6 | 24229 | 450 | 0.01857 | 0.00024764 | 10 | 749 | 2009/2010 | April-2009 | 4 | 2009
23315 | Replace Red Tagged Pole 138 | 2009-04-29 09:31 | 2009-04-29 | 2009-04-29 14:38 | Calculated | 291 | 291 - Air Break Switch 291 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 59 | 24229 | 16576 | 0.68414 | 0.0024351 | 441 | 124362 | 2009/2010 | April-2009 | 4 | 2009
21655 | Branch on line, McDonald Road, Whakamaru | 2009-04-29 11:19 | 2009-04-29 | 2009-04-29 12:50 | Calculated | T721 | T721 - 3ph 25kVA POLEMNT | TF721 | 120SEG498-408 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation | Unknown (All Categories) | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 6 | 24229 | 546 | 0.02253 | 0.00024764 | 25 | 2274 | 2009/2010 | April-2009 | 4 | 2009
21656 | Replace Line 5895 | 2009-04-29 13:30 | 2009-04-29 | 2009-04-29 15:52 | Calculated | 5895 | 5895 - Earth Working Link 5895 | 5895 | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause |  | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 2 | 24229 | 284 | 0.01172 | 8.2546e-05 | 8 | 1136 | 2009/2010 | April-2009 | 4 | 2009
21657 | Replace HV fuse TX 46 - Cause unknown | 2009-04-30 07:30 | 2009-04-30 | 2009-04-30 09:05 | Calculated | T46 | T46 - 1 Phase : 15.00 kVA : POLEMNT | TF46 | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation | Miscellaneous : Other Miscellaneous | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 3 | 24229 | 285 | 0.01176 | 0.00012382 | 15 | 1425 | 2009/2010 | April-2009 | 4 | 2009
21658 | Planned work on Caves Feeder Replace redtaged pole 138 | 2009-04-30 09:31 | 2009-04-30 | 2009-04-30 09:40 | Calculated | 291 | 291 - ABS 291 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 9 | 30 | 24229 | 270 | 0.01114 | 0.0012382 | 233 | 2096 | 2009/2010 | April-2009 | 4 | 2009
23316 | Tree Cutting by Private Contractor | 2009-05-01 08:33 | 2009-05-01 | 2009-05-01 15:30 | Calculated | 5505 | 5505 - Sectionaliser with Bypass 5505 |  | 421SEG5502-5505 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 417 | 29 | 24249 | 12093 | 0.4987 | 0.0011959 | 227.5 | 94867 | 2009/2010 | May-2009 | 5 | 2009
21660 | Planned work - Western Feeder, Tree cutting | 2009-05-01 08:37 | 2009-05-01 | 2009-05-01 08:43 | Calculated | 5460 | 5460 - Earth Working Link 5460 |  | 403SEG5460-5812 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 6 | 31 | 24249 | 186 | 0.00767 | 0.0012784 | 220 | 1319 | 2009/2010 | May-2009 | 5 | 2009
21661 | Replace TX 1718, SH3, before Hunts Road | 2009-05-01 09:11 | 2009-05-01 | 2009-05-01 13:43 | Calculated | 1386 | 1386 - Fused Link 1386 |  |  | Piopio 116-05 | Remote Rural F | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 4 | 24249 | 1088 | 0.04487 | 0.00016496 | 17.5 | 4760 | 2009/2010 | May-2009 | 5 | 2009
23317 | Faulty L.A - Wharepapa Road | 2009-05-01 09:33 | 2009-05-01 | 2009-05-01 13:43 | Calculated | 375 | 375 - Fused Link 375 |  | 122SEG375 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 250 | 14 | 24249 | 3500 | 0.14434 | 0.00057734 | 95 | 23749 | 2009/2010 | May-2009 | 5 | 2009
21662 | Replace Pole 41 for Private Extension & fit links 768 | 2009-05-01 10:07 | 2009-05-01 | 2009-05-01 12:45 | Calculated | 678 | 678 - Fused Link 678 |  | 122SEG678-768 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 158 | 5 | 24249 | 790 | 0.03258 | 0.00020619 | 55 | 8690 | 2009/2010 | May-2009 | 5 | 2009
21663 | New River road Sub - Cause Unknown | 2009-05-01 13:17 | 2009-05-01 | 2009-05-01 15:32 | Calculated | 5594 | 5594 - Sectionaliser with Bypass & Links 5594 | 5594 | 403SEG5594-5601 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 25 | 24249 | 3375 | 0.13918 | 0.001031 | 178 | 24030 | 2009/2010 | May-2009 | 5 | 2009
23320 | Faulty Tx - SH3 Awakino | 2009-05-01 19:30 | 2009-05-01 | 2009-05-02 10:34 | Calculated | T2144 | T2144 - 3 Phase : 30.00 kVA : POLEMNT |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 904 | 4 | 24249 | 3616 | 0.14912 | 0.00016496 | 30 | 27120 | 2009/2010 | May-2009 | 5 | 2009
21665 | Earth Fault - Unknown Cause | 2009-05-01 22:55 | 2009-05-01 | 2009-05-01 22:59 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24249 |  | 0 | 0 |  |  | 2009/2010 | May-2009 | 5 | 2009
21666 | Unknown Cause | 2009-05-01 22:55 | 2009-05-01 | 2009-05-01 23:05 | Calculated | 788 | 788 - 33kV SF6 Circuit Breaker 788 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24249 |  | 0 | 0 |  |  | 2009/2010 | May-2009 | 5 | 2009
21667 | Change Pole and Fit new Vertical ABS 6639 | 2009-05-02 07:39 | 2009-05-02 | 2009-05-02 17:12 | Calculated | 5147 | 5147 - Circuit Breaker with Bypass 5147 |  | No Segment | No Asset Group | Remote Rural F | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 573 | 37 | 24249 | 21201 | 0.8743 | 0.0015258 | 533 | 305408 | 2009/2010 | May-2009 | 5 | 2009
21668 | Blown fuse at TX 05I06 | 2009-05-03 08:20 | 2009-05-03 | 2009-05-03 09:06 | Calculated | 05I06 | 05I06 - 1ph 3kVA POLEMNT |  | 402SEG5446-5797 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation | Switchgear : Other | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 1 | 24249 | 46 | 0.0019 | 4.1239e-05 | 3 | 138 | 2009/2010 | May-2009 | 5 | 2009
23363 | Tokaanu Village Sub Station Upgrade | 2009-05-05 08:03 | 2009-05-05 | 2009-05-05 08:30 | Calculated | T4187 | T4187 - 3ph 100kVA GROUNDMNT |  | 420SEG5185 | Tokaanu 420-01 | Rural C | Tokaanu | Tokaanu Village Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 27 | 46 | 24249 | 5488 | 0.22632 | 0.001897 | 450 | 51449 | 2009/2010 | May-2009 | 5 | 2009
21669 | Replace blown pole fuse - TX 12K13 | 2009-05-05 08:10 | 2009-05-05 | 2009-05-05 09:00 | Calculated | 12K13 | 12K13 - 1 Phase : 10.00 kVA : POLEMNT | TF12K13 - Transformer Fuse: TF12K13 | 409SEG5799-5335 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation | Switchgear : Other | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 2 | 24249 | 100 | 0.00412 | 8.2478e-05 | 10 | 500 | 2009/2010 | May-2009 | 5 | 2009
21671 | Sectionaliser 5594 opened - Cause unknown | 2009-05-05 15:40 | 2009-05-05 | 2009-05-05 16:20 | Calculated | 5594 | 5594 - Sectionaliser with Bypass & Links 5594 | 5594 | 403SEG5594-5601 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 25 | 24249 | 1000 | 0.04124 | 0.001031 | 178 | 7120 | 2009/2010 | May-2009 | 5 | 2009
21677 | lightning arrestor TX 1554 earth fault | 2009-05-06 01:39 | 2009-05-06 | 2009-05-06 04:30 | Calculated | 1620 | 1620 - Recloser with Bypass & Links 1620 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | Miscellaneous : Other Miscellaneous | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 228 | 24249 | 38988 | 1.6078 | 0.0094024 | 1533.5 | 262228 | 2009/2010 | May-2009 | 5 | 2009
21674 | Replace Pole 18 - TLC | 2009-05-06 10:08 | 2009-05-06 | 2009-05-06 13:39 | Calculated | 286 | 286 - ABS 286 |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 211 | 10 | 24249 | 2110 | 0.08701 | 0.00041239 | 88 | 18568 | 2009/2010 | May-2009 | 5 | 2009
21675 | Replace HV fuse - Cause Unknown | 2009-05-06 10:37 | 2009-05-06 | 2009-05-06 12:10 | Calculated | T3021 | T3021 - 1ph 3kVA POLEMNT | TF3021 - Transformer Fuse: TF3021 | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 1 | 24249 | 93 | 0.00384 | 4.1239e-05 | 3 | 279 | 2009/2010 | May-2009 | 5 | 2009
23364 | Tokaanu Village Sub Station Upgrade | 2009-05-06 16:29 | 2009-05-06 | 2009-05-06 17:39 | Calculated | T4187 | T4187 - 3ph 100kVA GROUNDMNT |  | 420SEG5185 | Tokaanu 420-01 | Rural C | Tokaanu | Tokaanu Village Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 70 | 47 | 24249 | 3290 | 0.13568 | 0.0019382 | 450 | 31499 | 2009/2010 | May-2009 | 5 | 2009
21676 | Tree burning on line - TX 08H03 | 2009-05-06 16:54 | 2009-05-06 | 2009-05-06 17:51 | Calculated | 5316 | 5316 - Sectionaliser with Bypass & Links 5316 |  | 403SEG5377-5378 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 26 | 24249 | 1482 | 0.06112 | 0.0010722 | 165 | 9404 | 2009/2010 | May-2009 | 5 | 2009
21678 | Tree cutting by private contractor | 2009-05-07 08:31 | 2009-05-07 | 2009-05-07 15:41 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 430 | 15 | 24249 | 6450 | 0.26599 | 0.00061858 | 112.5 | 48375 | 2009/2010 | May-2009 | 5 | 2009
21683 | TX 10S50 - Fuse pulled apart | 2009-05-07 11:30 | 2009-05-07 | 2009-05-07 12:41 | Calculated | TF10S50 | TF10S50 - Transformer Fuse: TF10S50 |  | No Segment | No Asset Group | Rural C | Rangipo / Hautu | Turangi Zone Substation | Transformers : Other | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 4 | 24249 | 284 | 0.01171 | 0.00016496 | 50 | 3550 | 2009/2010 | May-2009 | 5 | 2009
21685 | Lightning - Line 1298 | 2009-05-07 18:25 | 2009-05-07 | 2009-05-07 20:42 | Calculated | 1298 | 1298 - 1DROP OUT FUSE | 1298 | 117SEG1298-810 | Te Mapara 117-02 | Rural D | Te Mapara | Wairere Zone Substation | Switchgear : Other | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 11 | 24249 | 1507 | 0.06215 | 0.00045363 | 80 | 10959 | 2009/2010 | May-2009 | 5 | 2009
21688 | TX 2433 - Lightning | 2009-05-07 18:48 | 2009-05-07 | 2009-05-07 20:50 | Calculated | T2433 | T2433 - 1ph 10kVA POLEMNT | TF2433 - Transformer Fuse: TF2433 | 113SEG1514-1516 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation | Switchgear : Other | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 2 | 24249 | 244 | 0.01006 | 8.2478e-05 | 10 | 1220 | 2009/2010 | May-2009 | 5 | 2009
21686 | TX 1771 - Lightning | 2009-05-07 20:50 | 2009-05-07 | 2009-05-07 22:54 | Calculated | T1771 | T1771 - 1ph 10kVA POLEMNT | TF1771 - Transformer Fuse: TF1771 | 117SEG1298-810 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation | Switchgear : Other | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 1 | 24249 | 124 | 0.00511 | 4.1239e-05 | 10 | 1240 | 2009/2010 | May-2009 | 5 | 2009
21689 | TX 1693 - Lightning | 2009-05-07 20:53 | 2009-05-07 | 2009-05-07 21:47 | Calculated | T1693 | T1693 - 1ph 10kVA POLEMNT | TF1693 - Transformer Fuse: TF1693 | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation | Switchgear : Other | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 24249 | 54 | 0.00223 | 4.1239e-05 | 10 | 540 | 2009/2010 | May-2009 | 5 | 2009
21691 | TX 1774 - Lightning | 2009-05-08 07:00 | 2009-05-08 | 2009-05-08 09:29 | Calculated | T1774 | T1774 - 1ph 10kVA POLEMNT | TF1774 - Transformer Fuse: TF1774 | 117SEG1298-810 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation | Switchgear : Other | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 2 | 24249 | 298 | 0.01229 | 8.2478e-05 | 10 | 1490 | 2009/2010 | May-2009 | 5 | 2009
21692 | Change poles and xarms on Piopio Feeder - Line Renewal | 2009-05-08 09:03 | 2009-05-08 | 2009-05-08 15:14 | Calculated | 1319 | 1319 - ABS 1319 |  | 113SEG1319RET | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 371 | 10 | 24249 | 3710 | 0.153 | 0.00041239 | 72.5 | 26897 | 2009/2010 | May-2009 | 5 | 2009
21693 | Fuse pulled apart - TX 20K20 | 2009-05-08 10:15 | 2009-05-08 | 2009-05-08 11:25 | Calculated | 20K20 | 20K20 - 3ph 300kVA POL | TF20K20 - Transformer Fuse: TF20K20 | 415SEG5704-REG28 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply | Switchgear : Other | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 18 | 24249 | 1260 | 0.05196 | 0.0007423 | 300 | 20999 | 2009/2010 | May-2009 | 5 | 2009
21695 | TX 872 - Lightning | 2009-05-08 14:50 | 2009-05-08 | 2009-05-08 16:06 | Calculated | T872 | T872 - 3ph 15kVA POL | TF872 - Transformer Fuse: TF872 | 103SEG228-226 | Benneydale 103-03 | Urban A | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 1 | 24249 | 76 | 0.00313 | 4.1239e-05 | 15 | 1140 | 2009/2010 | May-2009 | 5 | 2009
21701 | Faulty insulator | 2009-05-09 07:10 | 2009-05-09 | 2009-05-09 07:53 | Calculated | 5594 | 5594 - Sectionaliser with Bypass & Links 5594 |  | 403SEG5594-5601 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 25 | 24249 | 1075 | 0.04433 | 0.001031 | 178 | 7654 | 2009/2010 | May-2009 | 5 | 2009
21696 | LV Maintenance - Corroded joint 11S04 | 2009-05-09 09:00 | 2009-05-09 | 2009-05-09 10:20 | Calculated | 11S04 | 11S04 - 3 Phase : 100.00 kVA : GNDPAD |  | 424SEG5207-6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 80 | 5 | 24249 | 400 | 0.0165 | 0.00020619 | 100 | 8000 | 2009/2010 | May-2009 | 5 | 2009
21697 | Burning xarm - Turoa Feeder | 2009-05-09 09:04 | 2009-05-09 | 2009-05-09 10:37 | Calculated | 20K09 | 20K09 - 3ph 75kVA POL |  | THUVVK | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 20 | 24249 | 1860 | 0.0767 | 0.00082478 | 75 | 6975 | 2009/2010 | May-2009 | 5 | 2009
21698 | TX 1769 - Burnt fuse holder | 2009-05-09 10:35 | 2009-05-09 | 2009-05-09 11:39 | Calculated | T1769 | T1769 - 1ph 15kVA POLEMNT | TF1769 - Transformer Fuse: TF1769 | 117SEG1299-1329 | Te Mapara 117-02 | Rural D | Te Mapara | Wairere Zone Substation | Switchgear : Fuse Carriers | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 2 | 24249 | 128 | 0.00528 | 8.2478e-05 | 15 | 960 | 2009/2010 | May-2009 | 5 | 2009
21699 | Broken crossarm - Mokauiti 136/1 | 2009-05-09 14:05 | 2009-05-09 | 2009-05-09 14:25 | Calculated | 1712 | 1712 - Fused Link 1712 | 1151110 - MOKAUITI/136/1 | 115SEG1712-1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 28 | 24249 | 560 | 0.02309 | 0.0011547 | 197.5 | 3950 | 2009/2010 | May-2009 | 5 | 2009
21702 | Faulty insulator | 2009-05-10 15:35 | 2009-05-10 | 2009-05-10 18:12 | Calculated | 5594 | 5594 - Sectionaliser with Bypass & Links 5594 |  | 403SEG5594-5601 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 25 | 24249 | 3925 | 0.16186 | 0.001031 | 178 | 27946 | 2009/2010 | May-2009 | 5 | 2009
21703 | Blown fuse - 10K13 | 2009-05-11 07:32 | 2009-05-11 | 2009-05-11 09:24 | Calculated | 10K13 | 10K13 - 3 Phase : 200.00 kVA : GNDPAD | TF10K13 - Transformer Fuse: TF10K13 | 409SEG5135-5136 | Southern 409-04 | Rural D | Southern | Manunui Zone Substation | Switchgear : Other | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 31 | 24249 | 3472 | 0.14318 | 0.0012784 | 200 | 22399 | 2009/2010 | May-2009 | 5 | 2009
21704 | LV line down , Awakino Road, | 2009-05-11 20:00 | 2009-05-11 | 2009-05-11 20:46 | Calculated | T11 | T11 - 3ph 100kVA POL | TF11 | 104SEG214-639 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation | OH Lines : Other | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 48 | 24249 | 2208 | 0.09106 | 0.0019795 | 100 | 4599 | 2009/2010 | May-2009 | 5 | 2009
21705 | Earth Test - 08F01 | 2009-05-12 09:53 | 2009-05-12 | 2009-05-12 10:25 | Calculated | 08F01 | 08F01 - 1 Phase : 15.00 kVA : POLEMNT | TF08F01 | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 32 | 7 | 24249 | 224 | 0.00924 | 0.00028867 | 15 | 479 | 2009/2010 | May-2009 | 5 | 2009
21706 | TX 2546 - Lightning | 2009-05-12 13:50 | 2009-05-12 | 2009-05-12 14:40 | Calculated | T2546 | T2546 - 1ph 10kVA POLEMNT | tf2546 | 102SEG521-505 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation | Switchgear : Other | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 1 | 24249 | 50 | 0.00206 | 4.1239e-05 | 10 | 500 | 2009/2010 | May-2009 | 5 | 2009
21707 | TX: 117 - Lightning Stikes | 2009-05-12 13:50 | 2009-05-12 | 2009-05-12 15:10 | Calculated | T117 | T117 - 3ph 15kVA POLEMNT | TF117 | 107SEG243-113 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation | Switchgear : Other | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 3 | 24249 | 240 | 0.0099 | 0.00012372 | 15 | 1200 | 2009/2010 | May-2009 | 5 | 2009
21708 | TX: 123 Lightning strikes | 2009-05-12 13:50 | 2009-05-12 | 2009-05-12 15:25 | Calculated | T123 | T123 - 1ph 10kVA POLEMNT | TF123 - Transformer Fuse: TF123 | 107SEG113-262 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 2 | 24249 | 190 | 0.00784 | 8.2478e-05 | 10 | 950 | 2009/2010 | May-2009 | 5 | 2009
21709 | TX 171 lightning strikes | 2009-05-12 13:50 | 2009-05-12 | 2009-05-12 16:01 | Calculated | T171 | T171 - 1ph 25kVA POLEMNT | TF171 - Transformer Fuse: TF171 | 114SEG1104 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 2 | 24249 | 262 | 0.0108 | 8.2478e-05 | 25 | 3275 | 2009/2010 | May-2009 | 5 | 2009
21710 | TX 1167 Lightning strikes | 2009-05-12 13:50 | 2009-05-12 | 2009-05-12 16:17 | Calculated | T1167 | T1167 - 3ph 25kVA POLEMNT | TF1167 - Transformer Fuse: TF1167 | 110SEG323-644 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 4 | 24249 | 588 | 0.02425 | 0.00016496 | 25 | 3675 | 2009/2010 | May-2009 | 5 | 2009
21711 | TX 174 - lightning strikes | 2009-05-12 13:50 | 2009-05-12 | 2009-05-12 16:21 | Calculated | T174 | T174 - 3ph 25kVA POLEMNT | TF174 - Transformer Fuse: TF174 | 110SEG1352 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 4 | 24249 | 604 | 0.02491 | 0.00016496 | 25 | 3775 | 2009/2010 | May-2009 | 5 | 2009
21712 | TX 376 - lightning strikes | 2009-05-12 13:50 | 2009-05-12 | 2009-05-12 16:21 | Calculated | T376 | T376 - 3ph 25kVA POLEMNT | TF376 - Transformer Fuse: TF376 | 110SEG323-644 | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 5 | 24249 | 755 | 0.03114 | 0.00020619 | 25 | 3775 | 2009/2010 | May-2009 | 5 | 2009
21713 | OCB 594 - Gadsby Rd | 2009-05-12 13:57 | 2009-05-12 | 2009-05-12 13:58 | Calculated | 594 | 594 - 33kV Oil Circuit Breaker 594 | 594 | No Segment | 205-01 Gadsby Road | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 2008 | 24249 | 2008 | 0.08281 | 0.082808 | 13722 | 13721 | 2009/2010 | May-2009 | 5 | 2009
21714 | tx 46 - Lightning strikes | 2009-05-12 14:15 | 2009-05-12 | 2009-05-12 15:10 | Calculated | T46 | T46 - 1 Phase : 15.00 kVA : POLEMNT | TF46 - Transformer Fuse: TF46 | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 3 | 24249 | 165 | 0.0068 | 0.00012372 | 15 | 825 | 2009/2010 | May-2009 | 5 | 2009
21715 | TX 47 lightning strikes | 2009-05-12 14:15 | 2009-05-12 | 2009-05-12 15:15 | Calculated | T47 | T47 - 1 Phase : 15.00 kVA : POLEMNT | TF47 - Transformer Fuse: TF47 | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 3 | 24249 | 180 | 0.00742 | 0.00012372 | 15 | 900 | 2009/2010 | May-2009 | 5 | 2009
21716 | tx 1776 Lightning strikes | 2009-05-12 14:15 | 2009-05-12 | 2009-05-12 15:25 | Calculated | T1776 | T1776 - 1ph 25kVA POL | TF1776 - Transformer Fuse: TF1776 | 117SEG1314-1324 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 3 | 24249 | 210 | 0.00866 | 0.00012372 | 25 | 1749 | 2009/2010 | May-2009 | 5 | 2009
21717 | tx 1698 - lightning strikes | 2009-05-12 14:15 | 2009-05-12 | 2009-05-12 16:30 | Calculated | T1698 | T1698 - 1ph 10kVA POLEMNT | TF1698 - Transformer Fuse: TF1698 | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 4 | 24249 | 540 | 0.02227 | 0.00016496 | 10 | 1350 | 2009/2010 | May-2009 | 5 | 2009
21719 | tx 1693 lightning strikes | 2009-05-12 14:15 | 2009-05-12 | 2009-05-12 16:55 | Calculated | T1693 | T1693 - 1ph 10kVA POLEMNT | TF1693 - Transformer Fuse: TF1693 | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 1 | 24249 | 160 | 0.0066 | 4.1239e-05 | 10 | 1600 | 2009/2010 | May-2009 | 5 | 2009
21720 | 10R11 - wont go back in | 2009-05-12 16:20 | 2009-05-12 | 2009-05-12 18:07 | Calculated | 10R11 | 10R11 - 1ph 50kVA POLEMNT | TF10R11 - Transformer Fuse: TF10R11 | 406SEG5247 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 8 | 24249 | 856 | 0.0353 | 0.00032991 | 50 | 5350 | 2009/2010 | May-2009 | 5 | 2009
21721 | TX 331 lightning strikes | 2009-05-12 17:34 | 2009-05-12 | 2009-05-12 19:30 | Calculated | T331 | T331 - 3ph 15kVA POLEMNT | TF331 - Transformer Fuse: TF331 | 112SEG545-326 | Otorohanga 112-05 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 1 | 24249 | 116 | 0.00478 | 4.1239e-05 | 15 | 1740 | 2009/2010 | May-2009 | 5 | 2009
21722 | Tx 331 - Lightning strike | 2009-05-12 17:37 | 2009-05-12 | 2009-05-12 18:07 | Calculated | 5247 | T331 - 3ph 15kVA POLEMNT | TF331 - Transformer Fuse: TF331 | 112SEG545-326 | Otorohanga 112-05 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 1 | 24249 | 116 | 0.00478 | 4.1239e-05 | 15 | 1740 | 2009/2010 | May-2009 | 5 | 2009
21729 | Taharoa A line - Earth fault overcurrent | 2009-05-13 02:44 | 2009-05-13 | 2009-05-13 02:47 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 317 | 24249 | 951 | 0.03922 | 0.013073 | 2383.5 | 7150 | 2009/2010 | May-2009 | 5 | 2009
21723 | TX 216 - lightning strikes | 2009-05-13 08:03 | 2009-05-13 | 2009-05-13 10:30 | Calculated | T216 | T216 - 1ph 10kVA POLEMNT | TF216 - Transformer Fuse: TF216 | 112SEG331-355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 2 | 24249 | 294 | 0.01212 | 8.2478e-05 | 10 | 1470 | 2009/2010 | May-2009 | 5 | 2009
21724 | Rangitoto Line Renewal - United Group | 2009-05-13 09:04 | 2009-05-13 | 2009-05-13 15:18 | Calculated | 192 | 192 - ABS 192 |  | 106SEG192-246 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 48 | 24249 | 17952 | 0.74032 | 0.0019795 | 297.5 | 111264 | 2009/2010 | May-2009 | 5 | 2009
21725 | Change TX structure 13F03 and LV pole - TLC | 2009-05-13 10:07 | 2009-05-13 | 2009-05-13 13:48 | Calculated | 5668 | 5668 - Fused Link 5668 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 221 | 14 | 24249 | 3094 | 0.12759 | 0.00057734 | 60 | 13260 | 2009/2010 | May-2009 | 5 | 2009
21726 | TX 744 - repair damaged earth | 2009-05-13 10:14 | 2009-05-13 | 2009-05-13 10:29 | Calculated | T744 | T744 - 1 Phase : 15.00 kVA : POLEMNT |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 3 | 24249 | 45 | 0.00186 | 0.00012372 | 15 | 225 | 2009/2010 | May-2009 | 5 | 2009
21727 | TX 1393 - lightning strike | 2009-05-13 11:05 | 2009-05-13 | 2009-05-13 14:57 | Calculated | T1393 | T1393 - 1ph 5kVA POLEMNT | TF1393 - Transformer Fuse: TF1393 | 102SEG521-505 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 232 | 1 | 24249 | 232 | 0.00957 | 4.1239e-05 | 5 | 1160 | 2009/2010 | May-2009 | 5 | 2009
21728 | TX 118 - lightning strikes | 2009-05-13 12:05 | 2009-05-13 | 2009-05-13 15:18 | Calculated | T118 | T118 - 3ph 15kVA POLEMNT | TF118 - Transformer Fuse: TF118 | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 3 | 24249 | 579 | 0.02388 | 0.00012372 | 15 | 2895 | 2009/2010 | May-2009 | 5 | 2009
21730 | Rangitoto Feeder line renewal -United Gooder | 2009-05-14 09:12 | 2009-05-14 | 2009-05-14 13:18 | Calculated | 548 | 548 - Solid Link 548 |  | 106SEG548-1550 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 246 | 26 | 24249 | 6396 | 0.26376 | 0.0010722 | 180 | 44280 | 2009/2010 | May-2009 | 5 | 2009
21731 | Upgrade complete structure - TX 2242 - TLC | 2009-05-14 10:02 | 2009-05-14 | 2009-05-14 14:20 | Calculated | 1621 | 1621 - Fused Link 1621 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 258 | 20 | 24249 | 5160 | 0.21279 | 0.00082478 | 145 | 37409 | 2009/2010 | May-2009 | 5 | 2009
21732 | Lower tap on transformer 620 | 2009-05-14 12:55 | 2009-05-14 | 2009-05-14 13:08 | Calculated | T620 | T620 - 3ph 100kVA POL |  | 103SEG1230 | Benneydale 103-07 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 26 | 24249 | 338 | 0.01394 | 0.0010722 | 100 | 1299 | 2009/2010 | May-2009 | 5 | 2009
21733 | Replace fuses TX 2488 | 2009-05-14 16:40 | 2009-05-14 | 2009-05-14 17:22 | Calculated | T2488 | T2488 - 3ph 15kVA POLEMNT | TF2488 - Transformer Fuse: TF2488 | 102SEG521-505 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 1 | 24249 | 42 | 0.00173 | 4.1239e-05 | 15 | 630 | 2009/2010 | May-2009 | 5 | 2009
21734 | Jumper off at TX 2026 | 2009-05-14 16:54 | 2009-05-14 | 2009-05-14 17:28 | Calculated | 1712 | 1712 - Fused Link 1712 |  | 115SEG1712-1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 28 | 24249 | 952 | 0.03926 | 0.0011547 | 197.5 | 6715 | 2009/2010 | May-2009 | 5 | 2009
21735 | Burnt out fuse carrier - TX 01A51 | 2009-05-14 17:15 | 2009-05-14 | 2009-05-14 18:12 | Calculated | 01A51 | 01A51 - 3 Phase : 200.00 kVA : GNDPAD |  | 402SEGA4.5-A4.6 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 23 | 24249 | 1311 | 0.05406 | 0.00094849 | 200 | 11399 | 2009/2010 | May-2009 | 5 | 2009
23322 | Upgrade Tx - Waitomo Caves Road | 2009-05-15 09:00 | 2009-05-15 | 2009-05-15 12:14 | Calculated | T1082 | T1082 - 3 Phase : 50.00 kVA : POLEMNT |  | 101SEG577-679 | Caves 101-05 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 194 | 1 | 24249 | 194 | 0.008 | 4.1239e-05 | 50 | 9700 | 2009/2010 | May-2009 | 5 | 2009
23323 | Rangitoto Feeder Line Renewal - Ahuroa Road | 2009-05-15 09:12 | 2009-05-15 | 2009-05-15 11:00 | Calculated | 196 | 196 - Air Break Switch 196 |  | 106SEG196-199 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 115 | 24249 | 12420 | 0.51219 | 0.0047425 | 997.5 | 107729 | 2009/2010 | May-2009 | 5 | 2009
21739 | Change poles and xarms - Piopio Feeder line renewal | 2009-05-15 09:14 | 2009-05-15 | 2009-05-15 12:42 | Calculated | T1722 | T1722 - 1ph 5kVA POLEMNT |  | 116SEG1310-1781 | Piopio 116-03 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 208 | 2 | 24249 | 416 | 0.01716 | 8.2478e-05 | 5 | 1040 | 2009/2010 | May-2009 | 5 | 2009
21736 | Replace pole 13/6 & install pole to lower line at end of airstrip - TLC | 2009-05-15 09:31 | 2009-05-15 | 2009-05-15 11:10 | Calculated | 5657 | 5657 - Earth Working Link 5657 |  | 421SEG5657-5473 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 99 | 11 | 24249 | 1089 | 0.04491 | 0.00045363 | 105 | 10395 | 2009/2010 | May-2009 | 5 | 2009
23324 | Replace Red Tagged Pole | 2009-05-15 09:31 | 2009-05-15 | 2009-05-15 13:34 | Calculated | 1519 | 1519 - Recloser 1519 |  | 113SEG1519-1541 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 243 | 22 | 24249 | 5346 | 0.22046 | 0.00090725 | 138 | 33534 | 2009/2010 | May-2009 | 5 | 2009
23325 | Replace Pole32/33 | 2009-05-15 09:32 | 2009-05-15 | 2009-05-15 11:59 | Calculated | 5892 | 5892 - Earth Working Link 5892 |  | 426SEG5892-5240 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 147 | 34 | 24249 | 4998 | 0.20611 | 0.0014021 | 182.5 | 26827 | 2009/2010 | May-2009 | 5 | 2009
21737 | Replace pole 13/6 & install pole to lower line at end of airstrip - TLC | 2009-05-15 12:05 | 2009-05-15 | 2009-05-15 13:57 | Calculated | 04J04 | 04J04 - 1ph 10kVA POLEMNT |  | 421SEG5656-5669 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 1 | 24249 | 112 | 0.00462 | 4.1239e-05 | 10 | 1120 | 2009/2010 | May-2009 | 5 | 2009
23326 | Broken Xarm - Marokopa Road | 2009-05-15 14:09 | 2009-05-15 | 2009-05-15 15:41 | Calculated | 583 | 583 - Air Break Switch 583 |  | 125SEG296-583 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 144 | 24249 | 13248 | 0.54633 | 0.0059384 | 970 | 89239 | 2009/2010 | May-2009 | 5 | 2009
23327 | Broken Xarm - Marokopa Road | 2009-05-15 14:09 | 2009-05-15 | 2009-05-15 17:15 | Calculated | 563 | 563 - Air Break Switch 563 |  | 125SEG563-569 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 25 | 24249 | 4650 | 0.19176 | 0.001031 | 225 | 41850 | 2009/2010 | May-2009 | 5 | 2009
21746 | Replace complete structure TX2093 | 2009-05-18 10:30 | 2009-05-18 | 2009-05-18 14:49 | Calculated | 1623 | 1623 - Fused Link 1623 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 259 | 13 | 24249 | 3367 | 0.13885 | 0.0005361 | 95 | 24605 | 2009/2010 | May-2009 | 5 | 2009
21741 | Replace TX fuse 1672 | 2009-05-18 12:55 | 2009-05-18 | 2009-05-18 14:00 | Calculated | T1672 | T1672 - 3ph 100kVA POLEMNT | TF1672 - Transformer Fuse: TF1672 | 116SEG1342-1312 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 34 | 24249 | 2210 | 0.09114 | 0.0014021 | 100 | 6499 | 2009/2010 | May-2009 | 5 | 2009
21749 | Upgrade TX 115 | 2009-05-19 08:45 | 2009-05-19 | 2009-05-19 09:40 | Calculated | TF115 | TF115 - Transformer Fuse: TF115 |  | 117SEG1297-1296 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 1 | 24249 | 55 | 0.00227 | 4.1239e-05 | 5 | 275 | 2009/2010 | May-2009 | 5 | 2009
21744 | Magpie - Raurimu Feeder | 2009-05-19 08:55 | 2009-05-19 | 2009-05-19 20:15 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | 410SEG5806-5793 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 380 | 69 | 24249 | 22194 | 0.91525 | 0.0028455 | 426.5 | 134360 | 2009/2010 | May-2009 | 5 | 2009
21754 | Upgrade TX 1779 - SH 4 - 8 Mile | 2009-05-19 10:14 | 2009-05-19 | 2009-05-19 11:00 | Calculated | T1779 | T1779 - 1 Phase : 25.00 kVA : POLEMNT |  | 117SEG1322 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 5 | 24249 | 230 | 0.00948 | 0.00020619 | 25 | 1150 | 2009/2010 | May-2009 | 5 | 2009
21748 | Tighten HV bushing and top up oil on TX 17N04 | 2009-05-19 12:31 | 2009-05-19 | 2009-05-19 12:46 | Calculated | 6587 | 6587 - Ring Main Unit 6587 |  | 415SEG6354-6586 | Turoa 415-03 | Rural B | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Underground | 11kV | 11000 |  | 0 | 0 | 24249 |  | 0 | 0 |  |  | 2009/2010 | May-2009 | 5 | 2009
21756 | Jumper off @ T1404 | 2009-05-19 20:46 | 2009-05-19 | 2009-05-19 21:30 | Calculated | 504 | 504 - ABS 504 | T1404 - 1ph 50kVA POLEMNT | 126SEG504-578 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 96 | 24249 | 4224 | 0.17419 | 0.0039589 | 590 | 25959 | 2009/2010 | May-2009 | 5 | 2009
21757 | Unknown fault on Tihoi Feeder - Overcurrent | 2009-05-19 23:29 | 2009-05-19 | 2009-05-19 23:38 | Calculated | 440 | 440 - Recloser with Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 50 | 24249 | 2116 | 0.08726 | 0.0020619 | 353.5 | 14248 | 2009/2010 | May-2009 | 5 | 2009
21758 | Rangitoto Feeder Line Renewal | 2009-05-20 08:03 | 2009-05-20 | 2009-05-20 16:02 | Calculated | 566 | 566 - ABS 566 |  | 106SEG247-2068 | Rangitoto 106-06 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 391 | 7 | 24249 | 2737 | 0.11287 | 0.00028867 | 65 | 25415 | 2009/2010 | May-2009 | 5 | 2009
21760 | Replace fuse 02J08 - Ongarue Stream Rd, Unknown Cause | 2009-05-21 07:45 | 2009-05-21 | 2009-05-21 10:05 | Calculated | 02J08 | 02J08 - 1ph 3kVA POLEMNT | TF2J8 - Transformer Fuse: TF2J8 | 421SEG5364-5874 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 1 | 24249 | 140 | 0.00577 | 4.1239e-05 | 15 | 2100 | 2009/2010 | May-2009 | 5 | 2009
21762 | Rangitoto feeder line renewal | 2009-05-21 08:24 | 2009-05-21 | 2009-05-21 14:59 | Calculated | 194 | 194 - ABS 194 |  | 106SEG199-247 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 256 | 32 | 24249 | 8192 | 0.33783 | 0.0013196 | 240 | 61440 | 2009/2010 | May-2009 | 5 | 2009
21761 | Install prop pole between poles 1/28 and 1/29 | 2009-05-21 09:43 | 2009-05-21 | 2009-05-21 12:16 | Calculated | 5408 | 5408 - Earth Working Link 5408 |  | 426SEG5408-5296 | Waihaha 426-02 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 144 | 24249 | 22032 | 0.90857 | 0.0059384 | 1115 | 170594 | 2009/2010 | May-2009 | 5 | 2009
21764 | Replace fuse TX 10K12 - Blown L/A | 2009-05-21 10:17 | 2009-05-21 | 2009-05-21 11:39 | Calculated | TF10K12 | TF10K12 - Transformer Fuse: TF10K12 | TF10K12 - Transformer Fuse: TF10K12 | No Segment | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 2 | 24249 | 164 | 0.00676 | 8.2478e-05 | 30 | 2460 | 2009/2010 | May-2009 | 5 | 2009
21766 | Faulty DDO fuse carrier - replace fuse | 2009-05-21 18:05 | 2009-05-21 | 2009-05-21 21:10 | Calculated | T504 | T504 - 3 Phase : 100.00 kVA : POLEMNT | TF504 - Transformer Fuse: TF504 | 110SEG312-629 | McDonalds 110-01 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 31 | 24249 | 5735 | 0.2365 | 0.0012784 | 100 | 18499 | 2009/2010 | May-2009 | 5 | 2009
21770 | Faulty transformer TX:13M04 | 2009-05-22 10:16 | 2009-05-22 | 2009-05-22 11:15 | Calculated | 13M04 | 13M04 - 1 Phase : 5.00 kVA : POLEMNT | 13M04 - 1 Phase : 5.00 kVA : POLEMNT | 411SEG5373-5387 | National Park 411-02 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 1 | 24249 | 59 | 0.00243 | 4.1239e-05 | 15 | 885 | 2009/2010 | May-2009 | 5 | 2009
21772 | Sectionalise 5740 opened - Cause unknown | 2009-05-22 12:35 | 2009-05-22 | 2009-05-22 13:34 | Calculated | 5740 | 5740 - Sectionaliser with Bypass & Links 5740 |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 24 | 24249 | 1416 | 0.05839 | 0.00098973 | 135 | 7964 | 2009/2010 | May-2009 | 5 | 2009
21775 | Replace Link 382 - Treescape vs Line (2 blown) | 2009-05-25 10:00 | 2009-05-25 | 2009-05-25 14:14 | Calculated | 382 | 382 - Fused Link 382 |  | 111SEG382 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 254 | 14 | 24249 | 3556 | 0.14665 | 0.00057734 | 125 | 31750 | 2009/2010 | May-2009 | 5 | 2009
21777 | Connect new line - TX 3294 | 2009-05-25 10:33 | 2009-05-25 | 2009-05-25 14:05 | Calculated | 633 | 633 - Fused Link 633 |  | 122SEG633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 143 | 25 | 24249 | 3575 | 0.14743 | 0.001031 | 142.5 | 20377 | 2009/2010 | May-2009 | 5 | 2009
21778 | Remove LV Fuses TX3019 - Faulty Pillar Box | 2009-05-25 13:03 | 2009-05-25 | 2009-05-25 13:29 | Calculated | TF3019 | TF3019 - Transformer Fuse: TF3019 |  | No Segment | Gravel Scoop 109-01 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 3 | 24249 | 78 | 0.00322 | 0.00012372 | 300 | 7800 | 2009/2010 | May-2009 | 5 | 2009
21779 | Replace HV fuse TX04G04 - Rat | 2009-05-25 13:50 | 2009-05-25 | 2009-05-25 14:57 | Calculated | TF4G4 | TF4G4 - Transformer Fuse: TF4G4 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AVER | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 2 | 24249 | 134 | 0.00553 | 8.2478e-05 | 30 | 2010 | 2009/2010 | May-2009 | 5 | 2009
21781 | Rangitoto Feeder Line Renewal | 2009-05-26 07:40 | 2009-05-26 | 2009-05-26 15:24 | Calculated | 566 | 566 - ABS 566 |  | 106SEG247-2068 | Rangitoto 106-06 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 350 | 15 | 24249 | 5205 | 0.21465 | 0.00061858 | 116 | 40375 | 2009/2010 | May-2009 | 5 | 2009
21782 | Piopio Feeder Line Renewal | 2009-05-26 09:01 | 2009-05-26 | 2009-05-26 14:39 | Calculated | 1319 | 1319 - ABS 1319 |  | 113SEG1319RET | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 331 | 10 | 24249 | 3310 | 0.1365 | 0.00041239 | 72.5 | 23997 | 2009/2010 | May-2009 | 5 | 2009
21784 | Earth fault on Taharoa A 33 | 2009-05-27 00:51 | 2009-05-27 | 2009-05-27 00:53 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 317 | 24249 | 634 | 0.02615 | 0.013073 | 2303.5 | 4606 | 2009/2010 | May-2009 | 5 | 2009
21783 | Replace HV fuses - TX 2130 2 blown - lightning | 2009-05-27 07:30 | 2009-05-27 | 2009-05-27 09:14 | Calculated | TF2130 | TF2130 - Transformer Fuse: TF2130 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 1 | 24249 | 104 | 0.00429 | 4.1239e-05 | 5 | 520 | 2009/2010 | May-2009 | 5 | 2009
21785 | Gadsby Wairere 33kV - Service CB 792 | 2009-05-27 08:47 | 2009-05-27 | 2009-05-27 15:49 | Calculated | 792 | 792 - 33kV Circuit Breaker 792 |  | No Segment | 207-01 Wairere Falls | Rural D | Waitete 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 420 | 52 | 24249 | 21840 | 0.90066 | 0.0021444 | 425 | 178500 | 2009/2010 | May-2009 | 5 | 2009
21789 | Piopio Feeder Line Renewal | 2009-05-28 09:01 | 2009-05-28 | 2009-05-28 14:36 | Calculated | 1319 | 1319 - ABS 1319 |  | 113SEG1319RET | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 335 | 10 | 24249 | 3350 | 0.13815 | 0.00041239 | 72.5 | 24287 | 2009/2010 | May-2009 | 5 | 2009
21788 | Rangitoto Feeder Line Renewal | 2009-05-28 09:04 | 2009-05-28 | 2009-05-28 15:09 | Calculated | 566 | 566 - ABS 566 |  | 106SEG247-2068 | Rangitoto 106-06 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 365 | 15 | 24249 | 5475 | 0.22578 | 0.00061858 | 116 | 42340 | 2009/2010 | May-2009 | 5 | 2009
21794 | Connect new earthmat - TX 08K24 | 2009-05-29 11:36 | 2009-05-29 | 2009-05-29 12:30 | Calculated | TF8K24 | TF8K24 - Transformer Fuse: TF8K24 |  | No Segment | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 3 | 24249 | 162 | 0.00668 | 0.00012372 | 15 | 810 | 2009/2010 | May-2009 | 5 | 2009
21795 | Replace Fuse TX2933 | 2009-05-29 11:40 | 2009-05-29 | 2009-05-29 14:03 | Calculated | TF2933 | TF2933 - Transformer Fuse: TF2933 |  | No Segment | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 2 | 24249 | 286 | 0.01179 | 8.2478e-05 | 15 | 2145 | 2009/2010 | May-2009 | 5 | 2009
21796 | Replace fuse - TX08E02 | 2009-05-29 12:45 | 2009-05-29 | 2009-05-29 14:36 | Calculated | TF8E2 | TF8E2 - Transformer Fuse: TF8E2 |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 4 | 24249 | 444 | 0.01831 | 0.00016496 | 10 | 1110 | 2009/2010 | May-2009 | 5 | 2009
21798 | Replace fuse TX 07Q08 | 2009-05-30 17:30 | 2009-05-30 | 2009-05-30 18:30 | Calculated | TF7Q8 | TF7Q8 - Transformer Fuse: TF7Q8 |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 2 | 24249 | 120 | 0.00495 | 8.2478e-05 | 10 | 600 | 2009/2010 | May-2009 | 5 | 2009
21799 | Tree through line - Kuratau/National Park 33kV | 2009-06-01 09:08 | 2009-06-01 | 2009-06-01 12:11 | Calculated | 5180 | 5180 - 33kV Minimum Oil Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 183 | 4 | 24256 | 732 | 0.03018 | 0.00016491 | 450 | 82350 | 2009/2010 | June-2009 | 6 | 2009
23333 |  | 2009-06-01 09:53 | 2009-06-01 | 2009-06-01 09:55 | Calculated | 5990 | 5990 - Circuit Breaker 5990 |  | 419SEG5990-5991 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24256 |  | 0 | 0 |  |  | 2009/2010 | June-2009 | 6 | 2009
23334 |  | 2009-06-01 11:00 | 2009-06-01 | 2009-06-01 13:18 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 25 | 24256 | 3450 | 0.14223 | 0.0010307 | 138.5 | 19112 | 2009/2010 | June-2009 | 6 | 2009
23335 | Stay Broken Pole - Kawhia Road | 2009-06-01 16:20 | 2009-06-01 | 2009-06-01 16:31 | Calculated | 317 | 317 - Air Break Switch 317 |  | 112SEG317-209 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 71 | 24256 | 781 | 0.0322 | 0.0029271 | 795 | 8744 | 2009/2010 | June-2009 | 6 | 2009
21801 | Replace fuse TX 2181 | 2009-06-02 08:55 | 2009-06-02 | 2009-06-02 10:52 | Calculated | TF2181 | TF2181 - Transformer Fuse: TF2181 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 4 | 24256 | 468 | 0.01929 | 0.00016491 | 15 | 1755 | 2009/2010 | June-2009 | 6 | 2009
21802 | Te Mapara Feeder Line Renewal | 2009-06-02 09:03 | 2009-06-02 | 2009-06-02 15:24 | Calculated | 1318 | 1318 - ABS 1318 |  | 117SEG1318-770 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 381 | 36 | 24256 | 13716 | 0.56547 | 0.0014842 | 308 | 117347 | 2009/2010 | June-2009 | 6 | 2009
21804 | TX 357 - Replace fuses | 2009-06-03 08:00 | 2009-06-03 | 2009-06-03 10:40 | Calculated | TF357 | TF357 - Transformer Fuse: TF357 |  | No Segment | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 2 | 24256 | 320 | 0.01319 | 8.2454e-05 | 25 | 4000 | 2009/2010 | June-2009 | 6 | 2009
21805 | TX 2181 - Replace 1 blown fuse | 2009-06-03 08:15 | 2009-06-03 | 2009-06-03 12:14 | Calculated | TF2181 | TF2181 - Transformer Fuse: TF2181 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 4 | 24256 | 956 | 0.03941 | 0.00016491 | 15 | 3585 | 2009/2010 | June-2009 | 6 | 2009
21803 | Te Mapara Feeder Line Renewal | 2009-06-03 09:02 | 2009-06-03 | 2009-06-03 15:16 | Calculated | 1318 | 1318 - Air Break Switch 1318 |  | 117SEG1318-770 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 374 | 36 | 24256 | 13464 | 0.55508 | 0.0014842 | 308 | 115191 | 2009/2010 | June-2009 | 6 | 2009
21808 | OCB 6143 Earth fault | 2009-06-04 09:27 | 2009-06-04 | 2009-06-04 09:28 | Calculated | 6143 | 6143 - Manunui 33kV CB Line Breaker with Links 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 4 | 24256 | 4 | 0.00016 | 0.00016491 | 450 | 450 | 2009/2010 | June-2009 | 6 | 2009
21809 | Upgrade SWER Sub - New pole and Tx 2363 | 2009-06-04 09:34 | 2009-06-04 | 2009-06-04 15:02 | Calculated | 1536 | 1536 - Sectionaliser 1536 |  | No Segment | No Asset Group | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 262 | 25 | 24256 | 4418 | 0.18214 | 0.0010307 | 225 | 41540 | 2009/2010 | June-2009 | 6 | 2009
21810 | TX 1724 - Change TX structure | 2009-06-04 10:01 | 2009-06-04 | 2009-06-04 14:14 | Calculated | TF1724 | TF1724 - Transformer Fuse: TF1724 |  | 116SEG1310-1781 | Piopio 116-03 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 253 | 4 | 24256 | 1012 | 0.04172 | 0.00016491 | 30 | 7590 | 2009/2010 | June-2009 | 6 | 2009
21811 | Close Sect 591 - Unknown fault | 2009-06-04 10:15 | 2009-06-04 | 2009-06-04 11:49 | Calculated | 5591 | 5591 - Sectionaliser with Bypass & Links 5591 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 52 | 24256 | 4888 | 0.20152 | 0.0021438 | 208 | 19551 | 2009/2010 | June-2009 | 6 | 2009
21815 | Faulty Insulator - Piopio Feeder | 2009-06-05 08:27 | 2009-06-05 | 2009-06-05 10:08 | Calculated | 683 | 683 - Vacuum Breaker 683 |  | No Segment | 207-01 Wairere Falls | Rural D | Piopio | Wairere Zone Substation | OH Lines : Insulator - Pin | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 462 | 24256 | 23342 | 0.96232 | 0.019047 | 2853.5 | 144255 | 2009/2010 | June-2009 | 6 | 2009
21816 | Te Mapara Feeder Line Renewal | 2009-06-05 09:04 | 2009-06-05 | 2009-06-05 15:40 | Calculated | 1318 | 1318 - Air Break Switch 1318 |  | 117SEG1318-770 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 396 | 36 | 24256 | 14256 | 0.58773 | 0.0014842 | 308 | 121967 | 2009/2010 | June-2009 | 6 | 2009
21818 | Broken Binder at P 51/82/1 | 2009-06-06 13:04 | 2009-06-06 | 2009-06-06 15:37 | Calculated | 280 | 280 - Fused Link 280 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 153 | 12 | 24256 | 1836 | 0.07569 | 0.00049472 | 98 | 14993 | 2009/2010 | June-2009 | 6 | 2009
21819 | Burnt Xarm | 2009-06-06 16:18 | 2009-06-06 | 2009-06-06 17:16 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 29 | 24256 | 1682 | 0.06934 | 0.0011956 | 285 | 16529 | 2009/2010 | June-2009 | 6 | 2009
21820 | TX 05F15 - Faulty TX | 2009-06-07 14:09 | 2009-06-07 | 2009-06-07 17:50 | Calculated | TF5F15 | TF5F15 - Transformer Fuse: TF5F15 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 1 | 24256 | 221 | 0.00911 | 4.1227e-05 | 10 | 2210 | 2009/2010 | June-2009 | 6 | 2009
21823 | 17N01 - Blown fuses | 2009-06-08 10:41 | 2009-06-08 | 2009-06-08 11:11 | Calculated | TF17N1 | TF17N1 - Transformer Fuse: TF17N1 | TF17N1 - Transformer Fuse: TF17N1 | 415SEG5949RET | Turoa 415-02 |  | Turoa | Direct from Ohakune Supply |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24256 |  | 0 | 0 |  |  | 2009/2010 | June-2009 | 6 | 2009
21828 | Scheduled maintenance on TX 08I26 | 2009-06-09 09:01 | 2009-06-09 | 2009-06-09 12:37 | Calculated | 08I26 | 08I26 - 1 Phase : 25.00 kVA : POLEMNT |  | 403SEG5845 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 216 | 6 | 24256 | 1296 | 0.05343 | 0.00024736 | 15 | 3240 | 2009/2010 | June-2009 | 6 | 2009
21829 | Planned maintenance to change TX1745 | 2009-06-09 10:01 | 2009-06-09 | 2009-06-09 11:21 | Calculated | T1745 | T1745 - 1ph 15kVA POL |  | 117SEG1318-770 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 80 | 5 | 24256 | 400 | 0.01649 | 0.00020613 | 15 | 1200 | 2009/2010 | June-2009 | 6 | 2009
21831 | Replace Link 5895 - cause of fault unknown | 2009-06-09 11:20 | 2009-06-09 | 2009-06-09 15:01 | Calculated | 5895 | 5895 - Earth Working Link 5895 | 5895 - Earth Working Link 5895 | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 2 | 24256 | 442 | 0.01822 | 8.2454e-05 | 8 | 1768 | 2009/2010 | June-2009 | 6 | 2009
21830 | Planned maintenance to change TX2405 | 2009-06-09 11:41 | 2009-06-09 | 2009-06-09 12:28 | Calculated | T2405 | T2405 - 1ph 10kVA POL |  | 117SEG1318-770 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 47 | 1 | 24256 | 47 | 0.00194 | 4.1227e-05 | 10 | 470 | 2009/2010 | June-2009 | 6 | 2009
21832 | Replace HV fuse - TX1316 - 1 fuse only, faulty transformer | 2009-06-09 17:02 | 2009-06-09 | 2009-06-09 18:32 | Calculated | TF1316 | TF1316 - Transformer Fuse: TF1316 | TF1316 - Transformer Fuse: TF1316 | No Segment | McDonalds 110-04 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 2 | 24256 | 180 | 0.00742 | 8.2454e-05 | 15 | 1350 | 2009/2010 | June-2009 | 6 | 2009
21833 | Line Renewal and Change ABS 1316 on Te Mapara Feeder | 2009-06-10 09:01 | 2009-06-10 | 2009-06-10 15:01 | Calculated | 444 | 444 - Air Break Switch 444 |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 360 | 64 | 24256 | 22440 | 0.92513 | 0.0026385 | 525 | 183999 | 2009/2010 | June-2009 | 6 | 2009
21834 | Upgrade TX 2941 | 2009-06-10 09:40 | 2009-06-10 | 2009-06-10 15:13 | Calculated | T2941 | T2941 - 3 Phase : 300.00 kVA : POLEMNT |  | 110SEG629-308 | McDonalds 110-01 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 333 | 2 | 24256 | 666 | 0.02746 | 8.2454e-05 | 300 | 99900 | 2009/2010 | June-2009 | 6 | 2009
21835 | Replace HV fuse T478 | 2009-06-10 13:10 | 2009-06-10 | 2009-06-10 14:19 | Calculated | TF478 | TF478 - Transformer Fuse: TF478 |  | No Segment | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 4 | 24256 | 276 | 0.01138 | 0.00016491 | 300 | 20700 | 2009/2010 | June-2009 | 6 | 2009
21840 | Cable termination blew up at TX 15N05 | 2009-06-11 03:15 | 2009-06-11 | 2009-06-11 05:24 | Calculated | 5330 | 5330 - Fused Link 5330 |  | 419SEG5330 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBT | Underground Cable Termination Failure - Other | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 30 | 24256 | 3870 | 0.15955 | 0.0012368 | 1525 | 196724 | 2009/2010 | June-2009 | 6 | 2009
21841 | Cable termination blew up at TX 15N05 | 2009-06-11 03:15 | 2009-06-11 | 2009-06-12 16:18 | Calculated | 15N05 | 15N05 - 3ph 25kVA GMT |  | 419SEG5330 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBJ | Underground Cable Joint Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2223 | 1 | 24256 | 2223 | 0.09165 | 4.1227e-05 | 25 | 55575 | 2009/2010 | June-2009 | 6 | 2009
21837 | Planned line renewal on Western Feeder | 2009-06-11 09:05 | 2009-06-11 | 2009-06-11 15:04 | Calculated | 5376 | 5376 - Fused Link 5376 |  | 403SEG5376-5375 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 329 | 114 | 24256 | 9898 | 0.40806 | 0.0046999 | 683 | 64088 | 2009/2010 | June-2009 | 6 | 2009
21838 | Te Mapara Feeder Line Renewal | 2009-06-11 09:34 | 2009-06-11 | 2009-06-11 15:47 | Calculated | 770 | 770 - Fused Link 770 |  | 117SEG770-1787 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 373 | 13 | 24256 | 4849 | 0.19991 | 0.00053595 | 98 | 36554 | 2009/2010 | June-2009 | 6 | 2009
21843 | Te Mapara Feeder Line Renewal | 2009-06-12 09:01 | 2009-06-12 | 2009-06-12 14:08 | Calculated | 1316 | 1316 - Air Break Switch 1316 |  | 117SEG1316-1314 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 150 | 24256 | 46050 | 1.8985 | 0.006184 | 1142 | 350593 | 2009/2010 | June-2009 | 6 | 2009
21842 | Benneydale Feeder: Change poles and xarms to upgrade to 3 phase for customer | 2009-06-12 09:34 | 2009-06-12 | 2009-06-12 14:44 | Calculated | 1651 | 1651 - Fused Link 1651 |  | 103SEG1651-2227 | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 310 | 16 | 24256 | 4960 | 0.20449 | 0.00065963 | 90 | 27900 | 2009/2010 | June-2009 | 6 | 2009
21845 | Broken DDO at TX 11G04 | 2009-06-14 14:38 | 2009-06-14 | 2009-06-14 17:12 | Calculated | TF11G4 | TF11G4 - Transformer Fuse: TF11G4 |  | 403SEG5313-5541 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 20 | 24256 | 2156 | 0.08889 | 0.00082454 | 120 | 11550 | 2009/2010 | June-2009 | 6 | 2009
21847 | Piopio Planned Line Renewal | 2009-06-16 09:01 | 2009-06-16 | 2009-06-16 11:45 | Calculated | 1310 | 1310 - Air Break Switch 1310 |  | 116SEG1310-1781 | Piopio 116-03 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 164 | 8 | 24256 | 1312 | 0.05409 | 0.00032982 | 50 | 8200 | 2009/2010 | June-2009 | 6 | 2009
21853 | Replace 1 blown link at 5228 | 2009-06-17 02:47 | 2009-06-17 | 2009-06-17 08:53 | Calculated | 5228 | 5228 - Fused Link 5228 | 5228 - Fused Link 5228 | 424SEG5228 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 366 | 2 | 24256 | 732 | 0.03018 | 8.2454e-05 | 207.5 | 75945 | 2009/2010 | June-2009 | 6 | 2009
21848 | Faulty DDO at TX 10T06 | 2009-06-17 08:00 | 2009-06-17 | 2009-06-17 10:29 | Calculated | TF10T6 | TF10T6 - Transformer Fuse: TF10T6 | TF10T6 - Transformer Fuse: TF10T6 | No Segment | Rangipo / Hautu 424-02 |  | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 1 | 24256 | 149 | 0.00614 | 4.1227e-05 | 10 | 1490 | 2009/2010 | June-2009 | 6 | 2009
21849 | Planned line renewal Western Feeder - Generator Used | 2009-06-17 08:53 | 2009-06-17 | 2009-06-17 15:38 | Calculated | 5795 | 5795 - Air Break Switch 5795 |  | 403SEG5795-5280 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 0 | 267 | 24256 | 17442 | 0.71908 | 0.011008 | 1249 | 0 | 2009/2010 | June-2009 | 6 | 2009
21850 | Gravel Scoop - Rework - Moving 2 angle poles and Changing 2 xarms | 2009-06-17 09:03 | 2009-06-17 | 2009-06-17 14:08 | Calculated | 373 | 373 - Air Break Switch 373 |  | 109SEG529-1727 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 207 | 24256 | 53553 | 2.2078 | 0.008534 | 1855.5 | 478990 | 2009/2010 | June-2009 | 6 | 2009
21851 | Replace xarms @ Pole 327 - Gravel Scoop | 2009-06-17 09:04 | 2009-06-17 | 2009-06-17 15:48 | Calculated | 171 | 171 - Fused Link 171 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 404 | 7 | 24256 | 2828 | 0.11659 | 0.00028859 | 85 | 34340 | 2009/2010 | June-2009 | 6 | 2009
21852 | Faulty DDO @ TX 10T06 | 2009-06-17 09:56 | 2009-06-17 | 2009-06-17 10:29 | Calculated | 10T06 | 10T06 - 1ph 10kVA POLEMNT | TF10T6 - Transformer Fuse: TF10T6 | 424SEGT4172-6560 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 1 | 24256 | 33 | 0.00136 | 4.1227e-05 | 10 | 330 | 2009/2010 | June-2009 | 6 | 2009
21856 | Te Mapara Feeder Line Renewal | 2009-06-18 09:10 | 2009-06-18 | 2009-06-18 14:24 | Calculated | 444 | 444 - Air Break Switch 444 |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 314 | 102 | 24256 | 31453 | 1.2967 | 0.0042051 | 734 | 226935 | 2009/2010 | June-2009 | 6 | 2009
21858 | Replace HV fuse TX 4039 | 2009-06-18 15:15 | 2009-06-18 | 2009-06-18 17:07 | Calculated | TF4039 | TF4039 - Transformer Fuse: TF4039 |  | 402SEG5115-5108 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 1 | 24256 | 112 | 0.00462 | 4.1227e-05 | 10 | 1120 | 2009/2010 | June-2009 | 6 | 2009
21855 | Western Feeder Line Renewal Work | 2009-06-19 08:38 | 2009-06-19 | 2009-06-19 16:25 | Calculated | 5375 | 5375 - Recloser with Bypass & Links 5375 |  | 403SEG5375-5887 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 92 | 192 | 24256 | 6176 | 0.25462 | 0.0079156 | 1259 | 43756 | 2009/2010 | June-2009 | 6 | 2009
21860 | Loose Cards in Recloser 642 | 2009-06-19 21:00 | 2009-06-19 | 2009-06-19 22:03 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 101 | 24256 | 6363 | 0.26233 | 0.0041639 | 953 | 60038 | 2009/2010 | June-2009 | 6 | 2009
21861 | Replace link 282 - fell out - vibration | 2009-06-21 09:15 | 2009-06-21 | 2009-06-21 10:30 | Calculated | 282 | 282 - Air Break Switch 282 | 282 - Air Break Switch 282 | 103SEG236-731 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 17 | 24256 | 1275 | 0.05256 | 0.00070086 | 90 | 6749 | 2009/2010 | June-2009 | 6 | 2009
21864 | TX 493 - Change transformer | 2009-06-22 13:00 | 2009-06-22 | 2009-06-22 14:11 | Calculated | T493 | T493 - 1ph 15kVA POLEMNT |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 71 | 2 | 24256 | 142 | 0.00585 | 8.2454e-05 | 15 | 1065 | 2009/2010 | June-2009 | 6 | 2009
21865 | Broken insulator | 2009-06-22 13:45 | 2009-06-22 | 2009-06-22 14:57 | Calculated | 5596 | 5596 - Fused Link 5596 |  | 402SEG5352-5596 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 31 | 24256 | 2232 | 0.09202 | 0.001278 | 242.5 | 17459 | 2009/2010 | June-2009 | 6 | 2009
21866 | Change Tx2256 | 2009-06-22 14:15 | 2009-06-22 | 2009-06-22 15:28 | Calculated | T2256 | T2256 - 1ph 15kVA POLEMNT |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 73 | 2 | 24256 | 146 | 0.00602 | 8.2454e-05 | 15 | 1095 | 2009/2010 | June-2009 | 6 | 2009
21862 | Western feeder planned line renewal | 2009-06-23 08:42 | 2009-06-23 | 2009-06-23 15:38 | Calculated | 5375 | 5375 - Recloser with Bypass & Links 5375 |  | 403SEG5375-5887 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 351 | 191 | 24256 | 36995 | 1.5252 | 0.0078743 | 1249 | 262596 | 2009/2010 | June-2009 | 6 | 2009
21867 | Change TX 349 | 2009-06-23 09:54 | 2009-06-23 | 2009-06-23 11:57 | Calculated | T349 | T349 - 3ph 25kVA polemnt |  | 111SEG346-REG6 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 123 | 2 | 24256 | 246 | 0.01014 | 8.2454e-05 | 25 | 3075 | 2009/2010 | June-2009 | 6 | 2009
21869 | Replace Complete structure - TX 273 | 2009-06-23 10:02 | 2009-06-23 | 2009-06-23 14:54 | Calculated | 579 | 579 - Fused Link 579 |  | 111SEG579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 10 | 24256 | 2920 | 0.12038 | 0.00041227 | 95 | 27740 | 2009/2010 | June-2009 | 6 | 2009
21870 | Replace 2 blown links at 341 | 2009-06-23 12:15 | 2009-06-23 | 2009-06-23 13:20 | Calculated | 341 | 341 - Fused Link 341 | 341 - Fused Link 341 | 109SEG341-587 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 39 | 24256 | 2535 | 0.10451 | 0.0016078 | 350 | 22749 | 2009/2010 | June-2009 | 6 | 2009
21871 | Replace HV Fuse 02J06 - Bird | 2009-06-23 12:20 | 2009-06-23 | 2009-06-23 14:10 | Calculated | 02J06 | 02J06 - 1ph 10kVA POLEMNT | TF2J6 - Transformer Fuse: TF2J6 | 421SEG5462-5364 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 2 | 24256 | 220 | 0.00907 | 8.2454e-05 | 10 | 1100 | 2009/2010 | June-2009 | 6 | 2009
21873 | Planned line renewal Piopio feeder | 2009-06-24 08:57 | 2009-06-24 | 2009-06-24 14:59 | Calculated | 1319 | 1319 - Air Break Switch 1319 |  | 113SEG1319RET | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 10 | 24256 | 3310 | 0.13646 | 0.00041227 | 72.5 | 23997 | 2009/2010 | June-2009 | 6 | 2009
21874 | Liveline Pole change - | 2009-06-24 09:02 | 2009-06-24 | 2009-06-24 13:40 | Calculated | TF8I48 | TF8I48 - Transformer Fuse: TF8I48 |  | No Segment | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 278 | 4 | 24256 | 1112 | 0.04584 | 0.00016491 | 40 | 11119 | 2009/2010 | June-2009 | 6 | 2009
21875 | Re sag 11kV line on Gravel Scoop feeder | 2009-06-24 10:02 | 2009-06-24 | 2009-06-24 11:58 | Calculated | 722 | 722 - Fused Link 722 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DICL | Conductor Low - Incorrect Clearances | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 116 | 5 | 24256 | 580 | 0.02391 | 0.00020613 | 75 | 8699 | 2009/2010 | June-2009 | 6 | 2009
21877 | Replace protection relay and test - Whakamaru 33kV | 2009-06-24 13:33 | 2009-06-24 | 2009-06-24 15:51 | Calculated | 51W | 51W - Bypass Switch 51W |  | 310SEG672-2132 | 212-01 Marotiri | Rural C | Whakamaru 33 | Direct from Whakamaru Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24256 |  | 0 | 0 |  |  | 2009/2010 | June-2009 | 6 | 2009
21879 | Replace fuse Tx 4039 | 2009-06-24 17:42 | 2009-06-24 | 2009-06-25 10:41 | Calculated | T4039 | T4039 - 1 Phase : 10.00 kVA : POLEMNT | T4039 - 1 Phase : 10.00 kVA : POLEMNT | 402SEG5115-5108 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1019 | 1 | 24256 | 1019 | 0.04201 | 4.1227e-05 | 10 | 10190 | 2009/2010 | June-2009 | 6 | 2009
21880 | Oto feeder - Change poles 30 & 31 | 2009-06-25 09:04 | 2009-06-25 | 2009-06-25 15:06 | Calculated | 674 | 674 - Fused Link 674 |  | 112SEG674RET | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 362 | 20 | 24256 | 7240 | 0.29848 | 0.00082454 | 130 | 47060 | 2009/2010 | June-2009 | 6 | 2009
21881 | Change faulty tx - Tx 4039 | 2009-06-25 09:29 | 2009-06-25 | 2009-06-25 10:41 | Calculated | T4039 | T4039 - 1 Phase : 10.00 kVA : POLEMNT | T4039 - 1 Phase : 10.00 kVA : POLEMNT | 402SEG5115-5108 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 1 | 24256 | 72 | 0.00297 | 4.1227e-05 | 10 | 720 | 2009/2010 | June-2009 | 6 | 2009
21883 | Replace fuses for TX 2824 | 2009-06-25 09:44 | 2009-06-25 | 2009-06-25 10:37 | Calculated | TF2824 | TF2824 - Transformer Fuse: TF2824 | TF2824 - Transformer Fuse: TF2824 | No Segment | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 1 | 24256 | 53 | 0.00219 | 4.1227e-05 | 50 | 2650 | 2009/2010 | June-2009 | 6 | 2009
21882 | Connect extension onto P/L for MRP | 2009-06-25 09:54 | 2009-06-25 | 2009-06-25 14:03 | Calculated | 765 | 765 - Air Break Switch 765 |  | 130SEG765-801 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24256 |  | 0 | 0 |  |  | 2009/2010 | June-2009 | 6 | 2009
21908 | Earthquake - Kuratau area | 2009-06-26 01:01 | 2009-06-26 | 2009-06-26 02:51 | Calculated | 6005 | 6005 - SF6 Breaker 6005 |  | 404SEGL1.10 | 509-01 Kuratau | Rural D | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Weather | EART2 | WEAT:EART2:EART1 | Earthquake | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 1579 | 24256 | 348959 | 14.3865 | 0.065097 | 8231.5 | 1819161 | 2009/2010 | June-2009 | 6 | 2009
21884 | Otorohanga line renewal | 2009-06-26 09:05 | 2009-06-26 | 2009-06-26 11:14 | Calculated | 674 | 674 - Fused Link 674 |  | 112SEG674RET | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 129 | 20 | 24256 | 2580 | 0.10637 | 0.00082454 | 130 | 16770 | 2009/2010 | June-2009 | 6 | 2009
21885 | replace fuse TX 10L05 - old age | 2009-06-26 12:10 | 2009-06-26 | 2009-06-26 13:10 | Calculated | TF10L5 | TF10L5 - Transformer Fuse: TF10L5 | TF10L5 - Transformer Fuse: TF10L5 | No Segment | Southern 409-07 |  | Southern | Manunui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 1 | 24256 | 60 | 0.00247 | 4.1227e-05 | 15 | 900 | 2009/2010 | June-2009 | 6 | 2009
21888 | Feeder Fault - Magpie on L/A at TX 821 | 2009-06-26 16:15 | 2009-06-26 | 2009-06-27 13:23 | Calculated | 1343 | 1343 - Recloser with bypass & Links 1343 |  | 113SEG1343-1339 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1268 | 91 | 24256 | 105733 | 4.359 | 0.0037516 | 738 | 848788 | 2009/2010 | June-2009 | 6 | 2009
23349 | Wind/Tree - King Country Lamb | 2009-06-28 00:15 | 2009-06-28 | 2009-06-28 00:43 | Calculated | 653 | 653 - Fuse Switch 653 |  | 119SEG653-652 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 1 | 24256 | 28 | 0.00115 | 4.1227e-05 | 500 | 14000 | 2009/2010 | June-2009 | 6 | 2009
23350 | Wind/Tree - Maraetai Substation | 2009-06-28 00:15 | 2009-06-28 | 2009-06-28 06:23 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 368 | 147 | 24256 | 54096 | 2.2302 | 0.0060604 | 2648 | 974463 | 2009/2010 | June-2009 | 6 | 2009
23352 | Wind/Tree - Scott Road | 2009-06-28 00:15 | 2009-06-28 | 2009-06-28 06:43 | Calculated | 403 | 403 - Air Break Switch 403 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 388 | 147 | 24256 | 57036 | 2.3514 | 0.0060604 | 2648 | 1027423 | 2009/2010 | June-2009 | 6 | 2009
23353 | Wind/Tree - Scott Road | 2009-06-28 00:15 | 2009-06-28 | 2009-06-28 06:55 | Calculated | 492 | 492 - Air Break Switch 492 |  | 119SEG492-406RET | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 400 | 117 | 24256 | 46800 | 1.9294 | 0.0048235 | 2143 | 857199 | 2009/2010 | June-2009 | 6 | 2009
23354 | Wind/Tree - McLean Road | 2009-06-28 00:15 | 2009-06-28 | 2009-06-28 07:01 | Calculated | 406 | 406 - Air Break Switch 406 |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 406 | 94 | 24256 | 38164 | 1.5734 | 0.0038753 | 1793 | 727957 | 2009/2010 | June-2009 | 6 | 2009
23355 | Wind/Tree - Ranginui Road | 2009-06-28 00:15 | 2009-06-28 | 2009-06-28 08:32 | Calculated | 411 | 411 - Recloser with Bypass & Links 411 |  | No Segment | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 497 | 69 | 24256 | 34293 | 1.4138 | 0.0028447 | 1388 | 689835 | 2009/2010 | June-2009 | 6 | 2009
23356 | Wind/Tree - SH30 | 2009-06-28 00:15 | 2009-06-28 | 2009-06-28 08:49 | Calculated | 423 | 423 - Air Break Switch 423 |  | 119SEG423-432 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 514 | 47 | 24256 | 24158 | 0.99596 | 0.0019377 | 1013 | 520681 | 2009/2010 | June-2009 | 6 | 2009
23357 | Wind/Tree - SH30 | 2009-06-28 00:15 | 2009-06-28 | 2009-06-28 17:10 | Calculated | 417 | 417 - Air Break Switch 417 |  | No Segment | No Asset Group | Remote Rural F | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1015 | 59 | 24256 | 59885 | 2.4689 | 0.0024324 | 1283 | 1302244 | 2009/2010 | June-2009 | 6 | 2009
23358 | Branch on Line - Ruapehu Road | 2009-06-28 00:22 | 2009-06-28 | 2009-06-28 03:02 | Calculated | 5677 | 5677 - Recloser with Bypass 5677 |  | 416SEG5677-5681 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 229 | 24256 | 36640 | 1.5106 | 0.009441 | 7770 | 1243199 | 2009/2010 | June-2009 | 6 | 2009
23359 | Branch on Line - SH49 | 2009-06-28 00:22 | 2009-06-28 | 2009-06-28 03:06 | Calculated | 5681 | 5681 - Air Break Switch 5681 |  | 416SEG5681-6118 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 185 | 24256 | 30340 | 1.2508 | 0.007627 | 7440 | 1220160 | 2009/2010 | June-2009 | 6 | 2009
23360 | Wind - Ruatiti Sub | 2009-06-28 01:32 | 2009-06-28 | 2009-06-28 03:14 | Calculated | 5703 | 5703 - Fused Link 5703 |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 73 | 24256 | 7446 | 0.30698 | 0.0030096 | 456.5 | 46562 | 2009/2010 | June-2009 | 6 | 2009
23351 | Wind/Tree - Maraetai Substation | 2009-06-28 06:31 | 2009-06-28 | 2009-06-28 06:43 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 147 | 24256 | 1764 | 0.07272 | 0.0060604 | 2648 | 31775 | 2009/2010 | June-2009 | 6 | 2009
23347 | Wind - Pukemapou Road | 2009-06-28 18:00 | 2009-06-28 | 2009-06-28 21:06 | Calculated | 364 | 364 - Fused Link 364 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 31 | 24256 | 5766 | 0.23771 | 0.001278 | 260 | 48359 | 2009/2010 | June-2009 | 6 | 2009
23348 | Jumper off - Kuku Street | 2009-06-28 18:25 | 2009-06-28 | 2009-06-29 12:12 | Calculated | 1354 | 1354 - Circuit Breaker with Bypass & Links 1354 |  | 116SEG1341-1354 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1067 | 70 | 24256 | 74690 | 3.0792 | 0.0028859 | 542.5 | 578847 | 2009/2010 | June-2009 | 6 | 2009
23361 | Wind - Whibleys Road | 2009-06-29 05:00 | 2009-06-29 | 2009-06-29 06:37 | Calculated | 638 | 638 - Fused Link 638 |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 26 | 24256 | 2522 | 0.10397 | 0.0010719 | 265 | 25704 | 2009/2010 | June-2009 | 6 | 2009
23362 | Wind - Maihiihi Road | 2009-06-29 05:07 | 2009-06-29 | 2009-06-29 08:01 | Calculated | 363 | 363 - Fused Link 363 |  | 111SEG363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 174 | 4 | 24256 | 696 | 0.02869 | 0.00016491 | 75 | 13050 | 2009/2010 | June-2009 | 6 | 2009
23338 | Unknown - Ongarue Sub | 2009-06-29 07:15 | 2009-06-29 | 2009-06-29 13:40 | Calculated | 5152 | 5152 - Circuit Breaker 5152 |  | No Segment | 514-01 Transpower Ongarue | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24256 |  | 0 | 0 |  |  | 2009/2010 | June-2009 | 6 | 2009
23339 | Wind/Clash - Maihiihi Road | 2009-06-29 08:03 | 2009-06-29 | 2009-06-29 11:10 | Calculated | 363 | 363 - Fused Link 363 |  | 111SEG363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 4 | 24256 | 748 | 0.03084 | 0.00016491 | 75 | 14025 | 2009/2010 | June-2009 | 6 | 2009
23340 | Wind - Whibleys Road | 2009-06-29 08:30 | 2009-06-29 | 2009-06-29 10:34 | Calculated | 638 | 638 - Fused Link 638 |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 26 | 24256 | 3224 | 0.13292 | 0.0010719 | 265 | 32859 | 2009/2010 | June-2009 | 6 | 2009
21899 | Close and lock ABS 461 | 2009-06-29 08:33 | 2009-06-29 | 2009-06-29 15:16 | Calculated | 461 | 461 - Air Break Switch 461 |  | 119SEG2092-403 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24256 |  | 0 | 0 |  |  | 2009/2010 | June-2009 | 6 | 2009
21900 | Open OCB 2092 - Just | 2009-06-29 08:39 | 2009-06-29 | 2009-06-29 09:20 | Calculated | 2092 | 2092 - Maraetai 11 kV feeder 2092 |  | No Segment | 210-01 Maraetai | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24256 |  | 0 | 0 |  |  | 2009/2010 | June-2009 | 6 | 2009
21903 | Rec 714 Tripped | 2009-06-29 10:14 | 2009-06-29 | 2009-06-29 10:53 | Calculated | 714 | 714 - Recloser with Bypass 714 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 61 | 24256 | 2379 | 0.09808 | 0.0025148 | 1028 | 40092 | 2009/2010 | June-2009 | 6 | 2009
23341 | Wind - SH30 | 2009-06-29 10:14 | 2009-06-29 | 2009-06-29 11:07 | Calculated | 423 | 423 - Air Break Switch 423 |  | 119SEG423-432 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 47 | 24256 | 2491 | 0.1027 | 0.0019377 | 1013 | 53688 | 2009/2010 | June-2009 | 6 | 2009
23342 | Wind/Trees - Whibleys Road | 2009-06-29 11:45 | 2009-06-29 | 2009-06-29 14:52 | Calculated | 638 | 638 - Fused Link 638 |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 26 | 24256 | 4862 | 0.20045 | 0.0010719 | 265 | 49554 | 2009/2010 | June-2009 | 6 | 2009
21904 | Line down | 2009-06-29 12:44 | 2009-06-29 | 2009-06-29 14:20 | Calculated | 522 | 522 - Air Break Switch 522 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 53 | 24256 | 5088 | 0.20976 | 0.002185 | 590 | 56639 | 2009/2010 | June-2009 | 6 | 2009
23343 | Cut Tree Clear of Lines - Maihiihi Road | 2009-06-29 15:06 | 2009-06-29 | 2009-06-29 15:26 | Calculated | 360 | 360 - Air Break Switch 360 |  | 111SEG360-395 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 107 | 24256 | 2140 | 0.08823 | 0.0044113 | 910 | 18199 | 2009/2010 | June-2009 | 6 | 2009
23344 | Faulty Tx - Barbers Road | 2009-06-29 16:25 | 2009-06-29 | 2009-06-30 11:14 | Calculated | T1305 | T1305 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1129 | 5 | 24256 | 5645 | 0.23273 | 0.00020613 | 15 | 16935 | 2009/2010 | June-2009 | 6 | 2009
23345 | Jumper off @ T1644 - Waitanguru | 2009-06-29 16:41 | 2009-06-29 | 2009-06-29 17:19 | Calculated | 1526 | 1526 - Fused Link 1526 |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 55 | 24256 | 2090 | 0.08616 | 0.0022675 | 365.5 | 13888 | 2009/2010 | June-2009 | 6 | 2009
21890 | Change H Structure Pole 61 - Nihoniho Feeder | 2009-06-30 08:56 | 2009-06-30 | 2009-06-30 15:12 | Calculated | 5254 | 5254 - 11kV Oil Nihoniho Feeder Breaker 5254 |  | No Segment | 503-01 Nihiniho | Rural D | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 13 | 63 | 24256 | 169 | 0.00697 | 0.0025973 | 358.5 | 844 | 2009/2010 | June-2009 | 6 | 2009
21894 | Resag line | 2009-06-30 09:57 | 2009-06-30 | 2009-06-30 14:07 | Calculated | 363 | 363 - Fused Link 363 |  | 111SEG363 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DICL | Conductor Low - Incorrect Clearances | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 4 | 24256 | 1000 | 0.04123 | 0.00016491 | 75 | 18750 | 2009/2010 | June-2009 | 6 | 2009
21898 | Fautly transformer - TX1305 | 2009-06-30 10:06 | 2009-06-30 | 2009-06-30 11:14 | Calculated | TF1305 | TF1305 - Transformer Fuse: TF1305 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 5 | 24256 | 340 | 0.01402 | 0.00020613 | 15 | 1020 | 2009/2010 | June-2009 | 6 | 2009
21896 | Replace HV fuse Tx 4018 - Rat | 2009-06-30 10:50 | 2009-06-30 | 2009-06-30 13:53 | Calculated | TF4018 | TF4018 - Transformer Fuse: TF4018 |  | No Segment | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AVER | Wild Animals or Vermin | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 1 | 24256 | 183 | 0.00754 | 4.1227e-05 | 7.5 | 1372 | 2009/2010 | June-2009 | 6 | 2009
21915 | Change Poles 69, 71 & 83 | 2009-07-02 08:55 | 2009-07-02 | 2009-07-02 15:36 | Calculated | 5496 | 5496 - Fused Link 5496 |  | 412SEG5496-5265 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 401 | 63 | 24187 | 24548 | 1.0149 | 0.0026047 | 358.5 | 140053 | 2009/2010 | July-2009 | 7 | 2009
21916 | SWER backfeed | 2009-07-02 15:35 | 2009-07-02 | 2009-07-02 15:36 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 34 | 24187 | 34 | 0.00141 | 0.0014057 | 208.5 | 208 | 2009/2010 | July-2009 | 7 | 2009
21914 | SWER backfeed | 2009-07-03 08:55 | 2009-07-03 | 2009-07-03 08:56 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 34 | 24187 | 34 | 0.00141 | 0.0014057 | 208.5 | 208 | 2009/2010 | July-2009 | 7 | 2009
21920 | SWER backfeed | 2009-07-03 09:01 | 2009-07-03 | 2009-07-03 09:04 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 3 | 34 | 24187 | 102 | 0.00422 | 0.0014057 | 208.5 | 625 | 2009/2010 | July-2009 | 7 | 2009
21921 | Planned work on Nihoniho Line - Cancelled due to incorrect application | 2009-07-03 09:13 | 2009-07-03 | 2009-07-03 10:54 | Calculated | 5496 | 5496 - Fused Link 5496 |  | 412SEG5496-5265 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 101 | 63 | 24187 | 7489 | 0.30963 | 0.0026047 | 358.5 | 42946 | 2009/2010 | July-2009 | 7 | 2009
21922 | SWER Backfeed | 2009-07-03 11:15 | 2009-07-03 | 2009-07-03 11:17 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 34 | 24187 | 68 | 0.00281 | 0.0014057 | 208.5 | 416 | 2009/2010 | July-2009 | 7 | 2009
21925 | Unknown - Taharoa Road for Taumatatotara | 2009-07-06 07:22 | 2009-07-06 | 2009-07-06 09:56 | Calculated | 280 | 280 - Fused Link 280 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 12 | 24187 | 1848 | 0.0764 | 0.00049613 | 98 | 15091 | 2009/2010 | July-2009 | 7 | 2009
21926 | Line Down @ Pole 5/8 - Te Puke Road | 2009-07-06 10:23 | 2009-07-06 | 2009-07-06 14:04 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 2 | 24187 | 442 | 0.01827 | 8.2689e-05 | 8 | 1768 | 2009/2010 | July-2009 | 7 | 2009
21927 | Change Poles 73 & 84 | 2009-07-07 08:43 | 2009-07-07 | 2009-07-07 09:44 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 61 | 63 | 24187 | 3234 | 0.13371 | 0.0026047 | 358.5 | 18718 | 2009/2010 | July-2009 | 7 | 2009
21928 | Replace Poles & Xarms - Perry Lime Shutdown for the Day | 2009-07-07 09:27 | 2009-07-07 | 2009-07-07 14:54 | Calculated | 191 | 191 - Air Break Switch 191 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 3 | 24187 | 981 | 0.04056 | 0.00012403 | 1100 | 359700 | 2009/2010 | July-2009 | 7 | 2009
21929 | Replace Pole 22/4/25 for new T4262 | 2009-07-07 10:32 | 2009-07-07 | 2009-07-07 13:54 | Calculated | 5930 | 5930 - Earth Working Link 5930 |  | 402SEG5930-5756 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 202 | 12 | 24187 | 2424 | 0.10022 | 0.00049613 | 100 | 20199 | 2009/2010 | July-2009 | 7 | 2009
21940 | Replace Red Tagged Pole 1100105 & Stub Pole 38A-Also Replace Complete Structure T389 | 2009-07-09 08:42 | 2009-07-09 | 2009-07-09 15:22 | Calculated | 361 | 361 - Air Break Switch 361 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOR | Pole Down - Rotten | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 329 | 97 | 24187 | 9319 | 0.38529 | 0.0040104 | 560 | 61259 | 2009/2010 | July-2009 | 7 | 2009
21941 | Replace Red Tagged Pole 264/2/2-Complete Structure T839 | 2009-07-09 09:31 | 2009-07-09 | 2009-07-09 14:51 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOR | Pole Down - Rotten | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 316 | 21 | 24187 | 6636 | 0.27436 | 0.00086824 | 168 | 53088 | 2009/2010 | July-2009 | 7 | 2009
21942 | Tree Cutting - T2567 | 2009-07-09 09:49 | 2009-07-09 | 2009-07-09 13:49 | Calculated | T2567 | T2567 - 1 Phase : 15.00 kVA : POLEMNT |  | 107SEG234 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 240 | 1 | 24187 | 240 | 0.00992 | 4.1345e-05 | 15 | 3600 | 2009/2010 | July-2009 | 7 | 2009
21946 | Unknown-SH43 T4105 | 2009-07-10 09:04 | 2009-07-10 | 2009-07-10 10:54 | Calculated | T4105 | T4105 - 1 Phase : 10.00 kVA : POLEMNT |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 1 | 24187 | 110 | 0.00455 | 4.1345e-05 | 10 | 1100 | 2009/2010 | July-2009 | 7 | 2009
21947 | Otorohanga Feeder Renewal Project | 2009-07-10 09:24 | 2009-07-10 | 2009-07-10 15:10 | Calculated | 209 | 209 - Fused Link 209 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 346 | 50 | 24187 | 17300 | 0.71526 | 0.0020672 | 530 | 183379 | 2009/2010 | July-2009 | 7 | 2009
21949 | Broken DDO @ 03Q08 | 2009-07-10 10:50 | 2009-07-10 | 2009-07-10 16:28 | Calculated | 03Q08 | 03Q08 - 1 Phase : 3.00 kVA : POLEMNT |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 338 | 1 | 24187 | 338 | 0.01397 | 4.1345e-05 | 3 | 1014 | 2009/2010 | July-2009 | 7 | 2009
21950 | Broken DDO @ 03Q08 | 2009-07-10 14:50 | 2009-07-10 | 2009-07-10 16:28 | Calculated | 5534 | 5534 - Sectionaliser 5534 |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 14 | 24187 | 1372 | 0.05672 | 0.00057882 | 93 | 9114 | 2009/2010 | July-2009 | 7 | 2009
21957 | Unknown - Oio Sub | 2009-07-12 04:00 | 2009-07-12 | 2009-07-12 05:08 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 24 | 24187 | 1632 | 0.06747 | 0.00099227 | 138.5 | 9417 | 2009/2010 | July-2009 | 7 | 2009
21952 | Lightning - Barbers Road | 2009-07-12 08:03 | 2009-07-12 | 2009-07-12 09:09 | Calculated | T1305 | T1305 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 5 | 24187 | 330 | 0.01364 | 0.00020672 | 15 | 990 | 2009/2010 | July-2009 | 7 | 2009
21953 | Trees-2x Broken Xarm - Pihanga Saddle Road | 2009-07-12 08:16 | 2009-07-12 | 2009-07-13 13:54 | Calculated | 5590 | 5590 - Fused Link 5590 |  | 418SEG5590-5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1778 | 8 | 24187 | 14224 | 0.58808 | 0.00033076 | 68 | 120904 | 2009/2010 | July-2009 | 7 | 2009
21954 | 3 Spans Down - No Access Otukou Sub | 2009-07-12 09:12 | 2009-07-12 | 2009-07-12 10:10 | Calculated | 5584 | 5584 - Recloser with Bypass & Links 5584 |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 73 | 24187 | 4234 | 0.17505 | 0.0030182 | 336 | 19487 | 2009/2010 | July-2009 | 7 | 2009
21955 | Wind - Tuararoa Road - At Dean's | 2009-07-12 09:43 | 2009-07-12 | 2009-07-12 10:24 | Calculated | 374 | 374 - Fused Link 374 |  | 111SEG374-783 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 20 | 24187 | 820 | 0.0339 | 0.00082689 | 335 | 13734 | 2009/2010 | July-2009 | 7 | 2009
21956 | Line Down to 12P05 by Te Roto School | 2009-07-12 16:05 | 2009-07-12 | 2009-07-12 18:42 | Calculated | 5591 | 5591 - Sectionaliser with Bypass & Links 5591 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 52 | 24187 | 8164 | 0.33754 | 0.0021499 | 208 | 32655 | 2009/2010 | July-2009 | 7 | 2009
21958 | Lightning - Aria Road | 2009-07-13 07:45 | 2009-07-13 | 2009-07-13 10:19 | Calculated | T1910 | T1910 - 3ph 30kVA POLEMNT |  | 116SEG1355-1327 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 3 | 24187 | 462 | 0.0191 | 0.00012403 | 30 | 4620 | 2009/2010 | July-2009 | 7 | 2009
21959 | Lightning - Aria Road | 2009-07-13 07:45 | 2009-07-13 | 2009-07-13 10:19 | Calculated | T3277 | T3277 - 3P 75kVA POLEMNT |  | 116SEG1355-1327 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24187 |  | 0 | 0 |  |  | 2009/2010 | July-2009 | 7 | 2009
21961 | Blown L/A - Otewa Road | 2009-07-13 08:20 | 2009-07-13 | 2009-07-13 09:26 | Calculated | T2708 | T2708 - 3ph 30kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 2 | 24187 | 132 | 0.00546 | 8.2689e-05 | 30 | 1980 | 2009/2010 | July-2009 | 7 | 2009
21962 | Feeder Renewal - Te Raumauku Road | 2009-07-13 09:02 | 2009-07-13 | 2009-07-13 13:47 | Calculated | 774 | 774 - Fused Link 774 |  | No Segment | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 7 | 24187 | 1995 | 0.08248 | 0.00028941 | 60 | 17100 | 2009/2010 | July-2009 | 7 | 2009
21965 | Broken LV Xarm - Rangitoto Road | 2009-07-13 13:51 | 2009-07-13 | 2009-07-13 15:50 | Calculated | T1124 | T1124 - 1 Phase : 30.00 kVA : POLEMNT |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 6 | 24187 | 714 | 0.02952 | 0.00024807 | 30 | 3570 | 2009/2010 | July-2009 | 7 | 2009
21966 | Unknown - Tauraroa Road | 2009-07-14 09:25 | 2009-07-14 | 2009-07-14 12:09 | Calculated | 783 | 783 - Fused Link 783 |  | 111SEG374-783 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 2 | 24187 | 328 | 0.01356 | 8.2689e-05 | 90 | 14760 | 2009/2010 | July-2009 | 7 | 2009
21969 | Replace Red Tagged Pole - Old Te Kuiti Road | 2009-07-14 09:29 | 2009-07-14 | 2009-07-14 14:43 | Calculated | T1120 | T1120 - 3 Phase : 30.00 kVA : POLEMNT |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 314 | 4 | 24187 | 1256 | 0.05193 | 0.00016538 | 30 | 9420 | 2009/2010 | July-2009 | 7 | 2009
21967 | Tree Cutting - Tate Road | 2009-07-14 09:31 | 2009-07-14 | 2009-07-14 16:56 | Calculated | T2565 | T2565 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG548-1550 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 445 | 4 | 24187 | 1780 | 0.07359 | 0.00016538 | 15 | 6675 | 2009/2010 | July-2009 | 7 | 2009
21968 | Private Line Burning Xarm -Paerata Road | 2009-07-14 09:35 | 2009-07-14 | 2009-07-14 11:01 | Calculated | 1407 | 1407 - Fused Link 1407 |  | 129SEG1407 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24187 |  | 0 | 0 |  |  | 2009/2010 | July-2009 | 7 | 2009
21972 | Urgent Pole Change T2181 | 2009-07-14 10:07 | 2009-07-14 | 2009-07-14 15:40 | Calculated | 1625 | 1625 - Recloser with Outgoing Link1625 |  | 128SEG1634-REG3 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 333 | 19 | 24187 | 6327 | 0.26159 | 0.00078555 | 107.5 | 35797 | 2009/2010 | July-2009 | 7 | 2009
21973 | Trees-Line Down @ P27 - Pihanga Saddle Road | 2009-07-14 10:17 | 2009-07-14 | 2009-07-14 15:30 | Calculated | 5590 | 5590 - Fused Link 5590 |  | 418SEG5590-5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 313 | 8 | 24187 | 2504 | 0.10353 | 0.00033076 | 68 | 21284 | 2009/2010 | July-2009 | 7 | 2009
21977 | Tree Cutting Ongarue/Tapuwahine Sub | 2009-07-16 10:05 | 2009-07-16 | 2009-07-16 14:25 | Calculated | 5462 | 5462 - Sectionaliser with Bypass & Links 5462 |  | 421SEG6554-5462RET | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 260 | 119 | 24187 | 30940 | 1.2792 | 0.00492 | 850 | 220999 | 2009/2010 | July-2009 | 7 | 2009
21978 | Fuse Pulled Apart - Whangeahu Valley Road | 2009-07-16 13:00 | 2009-07-16 | 2009-07-16 13:28 | Calculated | 22M19 | 22M19 - 1 Phase : 15.00 kVA : POLEMNT |  | 416SEG5686 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 2 | 24187 | 56 | 0.00232 | 8.2689e-05 | 15 | 420 | 2009/2010 | July-2009 | 7 | 2009
23297 | Faulty Kidney Strain @ P214 - Maihiihi Road | 2009-07-16 14:10 | 2009-07-16 | 2009-07-16 17:21 | Calculated | 117 | 117 - Circuit Breaker 117 |  | 111SEG647-117RET | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 231 | 24187 | 44121 | 1.8242 | 0.0095506 | 2247.5 | 429272 | 2009/2010 | July-2009 | 7 | 2009
21980 | Bypassed - Fault on CB - Otukou Sub | 2009-07-17 22:50 | 2009-07-17 | 2009-07-18 02:26 | Calculated | 5836 | 5836 - Circuit Breaker 5836 |  | No Segment | 512-01 Otukou | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 216 | 97 | 24187 | 20952 | 0.86625 | 0.0040104 | 761 | 164375 | 2009/2010 | July-2009 | 7 | 2009
21983 | Wind - Mahoenui | 2009-07-18 07:01 | 2009-07-18 | 2009-07-18 07:12 | Calculated | 1010 | 1010 - Circuit Breaker Mahoenui 1010 |  | No Segment | 209-01 Mahoenui | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 628 | 24187 | 6908 | 0.28561 | 0.025964 | 3882.5 | 42707 | 2009/2010 | July-2009 | 7 | 2009
21984 | Tree through line - Karangahape Road | 2009-07-19 05:25 | 2009-07-19 | 2009-07-19 10:15 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 290 | 39 | 24187 | 11310 | 0.46761 | 0.0016124 | 353.5 | 102514 | 2009/2010 | July-2009 | 7 | 2009
21985 | Wind - Maihihi Road (by school) | 2009-07-19 12:55 | 2009-07-19 | 2009-07-19 13:04 | Calculated | 117 | 117 - Circuit Breaker 117 |  | 111SEG647-117RET | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 232 | 24187 | 2088 | 0.08633 | 0.0095919 | 2242.5 | 20182 | 2009/2010 | July-2009 | 7 | 2009
21986 | Wind - Grice Road | 2009-07-19 17:48 | 2009-07-19 | 2009-07-19 20:43 | Calculated | T1344 | T1344 - 1 Phase : 15.00 kVA : POLEMNT |  | 111SEG625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 1 | 24187 | 175 | 0.00724 | 4.1345e-05 | 15 | 2625 | 2009/2010 | July-2009 | 7 | 2009
21987 | Wind - Waihuka Road | 2009-07-19 20:55 | 2009-07-19 | 2009-07-19 23:18 | Calculated | 03I02 | 03I02 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5462-5364 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 3 | 24187 | 429 | 0.01774 | 0.00012403 | 15 | 2145 | 2009/2010 | July-2009 | 7 | 2009
21988 | Western Feeder Renewal Project | 2009-07-20 08:35 | 2009-07-20 | 2009-07-20 16:47 | Calculated | 5378 | 5378 - Recloser with Bypass & Links 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 485 | 336 | 24187 | 63936 | 2.6434 | 0.013892 | 2169 | 500300 | 2009/2010 | July-2009 | 7 | 2009
21989 | Pole Down (P/73/27/42) Pokuru Road | 2009-07-20 14:18 | 2009-07-20 | 2009-07-20 17:39 | Calculated | 634 | 634 - Air Break Switch 634 |  | 129SEG634-2131 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 201 | 156 | 24187 | 31356 | 1.2964 | 0.0064497 | 1720 | 345719 | 2009/2010 | July-2009 | 7 | 2009
21993 | Connect new Earthmat - Mohakatino Road | 2009-07-22 12:16 | 2009-07-22 | 2009-07-22 14:10 | Calculated | T2181 | T2181 - U Phase : 15.00 kVA : Unk |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 114 | 4 | 24187 | 456 | 0.01885 | 0.00016538 | 0 | 0 | 2009/2010 | July-2009 | 7 | 2009
21995 | Faulty Tx - Karangahape Road | 2009-07-22 20:15 | 2009-07-22 | 2009-07-22 22:26 | Calculated | 07Q05 | 07Q05 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 1 | 24187 | 131 | 0.00542 | 4.1345e-05 | 15 | 1965 | 2009/2010 | July-2009 | 7 | 2009
21996 | Unknown - Taringamotu Road | 2009-07-23 10:55 | 2009-07-23 | 2009-07-23 11:22 | Calculated | T4094 | T4094 - 3 Phase : 15.00 kVA : POLEMNT |  | 402SEG5164-5923 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 1 | 24187 | 27 | 0.00112 | 4.1345e-05 | 15 | 405 | 2009/2010 | July-2009 | 7 | 2009
21997 | Jumper off @ T2481 - Mokauiti Road (by Aria Post Office) | 2009-07-23 17:10 | 2009-07-23 | 2009-07-23 17:43 | Calculated | 1107 | 1107 - Recloser with Bypass 1107 |  | 114SEG1107-1116 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 88 | 24187 | 2904 | 0.12006 | 0.0036383 | 676 | 22307 | 2009/2010 | July-2009 | 7 | 2009
21998 | Wind/Trees - SH3 Pastoral Holdings | 2009-07-23 18:12 | 2009-07-23 | 2009-07-23 19:42 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 6 | 24187 | 540 | 0.02233 | 0.00024807 | 90 | 8099 | 2009/2010 | July-2009 | 7 | 2009
21999 | Wind/Trees - Mahoenui | 2009-07-23 20:40 | 2009-07-23 | 2009-07-23 20:47 | Calculated | 1010 | 1010 - Circuit Breaker Mahoenui 1010 |  | No Segment | 209-01 Mahoenui | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 624 | 24187 | 4368 | 0.18059 | 0.025799 | 3882.5 | 27177 | 2009/2010 | July-2009 | 7 | 2009
22000 | Wind - Te Rauauku Road | 2009-07-23 21:30 | 2009-07-23 | 2009-07-23 22:49 | Calculated | 355 | 355 - Fused Link 355 |  | 112SEG355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 9 | 24187 | 711 | 0.0294 | 0.0003721 | 95 | 7504 | 2009/2010 | July-2009 | 7 | 2009
22001 | Wind - Kokomiko Sub | 2009-07-23 22:50 | 2009-07-23 | 2009-07-24 01:11 | Calculated | 5505 | 5505 - Sectionaliser with Bypass 5505 |  | 421SEG5502-5505 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 29 | 24187 | 4089 | 0.16906 | 0.001199 | 227.5 | 32077 | 2009/2010 | July-2009 | 7 | 2009
23311 | Trees Line Down - Ongarue Road | 2009-07-23 22:50 | 2009-07-23 | 2009-07-24 10:51 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 721 | 15 | 24187 | 10815 | 0.44714 | 0.00062017 | 112.5 | 81112 | 2009/2010 | July-2009 | 7 | 2009
23312 | Trees Line Down - Ongarue Stream Road | 2009-07-23 22:50 | 2009-07-23 | 2009-07-24 13:10 | Calculated | 5933 | 5933 - Earth Working Link 5933 |  | 421SEG5933 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 860 | 9 | 24187 | 7740 | 0.32001 | 0.0003721 | 60 | 51600 | 2009/2010 | July-2009 | 7 | 2009
23304 | Jumper Off @ T1187 - Waitomo Caves Road | 2009-07-24 09:22 | 2009-07-24 | 2009-07-24 09:45 | Calculated | 261 | 261 - Fused Link 261 |  | 101SEG261-519 | Caves 101-02 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 43 | 24187 | 989 | 0.04089 | 0.0017778 | 507.5 | 11672 | 2009/2010 | July-2009 | 7 | 2009
23303 | Trees Line Down - Ongarue Road | 2009-07-24 11:50 | 2009-07-24 | 2009-07-24 13:10 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 15 | 24187 | 1200 | 0.04961 | 0.00062017 | 112.5 | 9000 | 2009/2010 | July-2009 | 7 | 2009
23310 | Possum - Waitea Road | 2009-07-24 14:10 | 2009-07-24 | 2009-07-24 16:54 | Calculated | 09K05 | 09K05 - 2ph 15kVA POLEMNT |  | 409SEG5134 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 2 | 24187 | 328 | 0.01356 | 8.2689e-05 | 15 | 2460 | 2009/2010 | July-2009 | 7 | 2009
22099 | Wind - Hangatiki East Road | 2009-07-26 07:18 | 2009-07-26 | 2009-07-26 08:17 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 9 | 24187 | 531 | 0.02195 | 0.0003721 | 50 | 2949 | 2009/2010 | July-2009 | 7 | 2009
22003 | Unknown - Gadsby Road | 2009-07-26 17:40 | 2009-07-26 | 2009-07-26 17:51 | Calculated | 594 | 594 - Circuit Breaker 594 |  | No Segment | 205-01 Gadsby Road | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 11 | 2015 | 24187 | 22165 | 0.9164 | 0.083309 | 13837 | 152207 | 2009/2010 | July-2009 | 7 | 2009
22004 | Unknown - Hangatiki | 2009-07-26 17:40 | 2009-07-26 | 2009-07-26 18:54 | Calculated | 252 | 252 - Fused Link 252 |  | 106SEG252-803 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 10 | 24187 | 740 | 0.03059 | 0.00041345 | 50 | 3700 | 2009/2010 | July-2009 | 7 | 2009
22005 | Unknown - Gadsby Road Feeder | 2009-07-26 17:40 | 2009-07-26 | 2009-07-27 13:28 | Calculated | L126 | L126 - Air Break Switch L126 |  | 305SEG126-154 | Te Kawa Street 304-01 |  | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1345 | 24187 | 1345 | 0.05561 | 0.055608 | 9605 | 9604 | 2009/2010 | July-2009 | 7 | 2009
22009 | Line down broken Xarm - Otewa Road (by Subway) | 2009-07-27 03:13 | 2009-07-27 | 2009-07-27 03:46 | Calculated | 704 | 704 - Recloser with Bypass & Links 704 |  | 110SEG600-320 | McDonalds 110-01 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 185 | 24187 | 6105 | 0.25241 | 0.0076487 | 2400 | 79199 | 2009/2010 | July-2009 | 7 | 2009
22010 | Line down broken Xarm - Te Waireka Road | 2009-07-27 03:13 | 2009-07-27 | 2009-07-27 04:14 | Calculated | 120 | 120 - Circuit Breaker 120 |  | No Segment | 203-01 Te Waireka Road | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 457 | 24187 | 27877 | 1.1526 | 0.018894 | 5218 | 318297 | 2009/2010 | July-2009 | 7 | 2009
22011 | Line down broken Xarm - Old Te Kuiti Road | 2009-07-27 03:13 | 2009-07-27 | 2009-07-27 04:21 | Calculated | 387 | 387 - Air Break Switch 387 |  | 110SEG387-328 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 116 | 24187 | 7888 | 0.32613 | 0.004796 | 1823 | 123964 | 2009/2010 | July-2009 | 7 | 2009
22012 | Line down broken Xarm - Old Te Kuiti (by Saleyard) | 2009-07-27 03:13 | 2009-07-27 | 2009-07-27 08:26 | Calculated | 320 | 320 - Air Break Switch 320 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 313 | 213 | 24187 | 66669 | 2.7564 | 0.0088064 | 2383 | 745878 | 2009/2010 | July-2009 | 7 | 2009
22006 | Change poles 17/1/1 & 2 - Also 17/1/1/2 | 2009-07-27 08:39 | 2009-07-27 | 2009-07-27 08:44 | Calculated | 5863 | 5863 - Recloser with Bypass & Links 5863 |  | 403SEG5863-5862 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 5 | 69 | 24187 | 8388 | 0.3468 | 0.0028528 | 510 | 93930 | 2009/2010 | July-2009 | 7 | 2009
22016 | Unknown - Main Nth Road | 2009-07-28 07:00 | 2009-07-28 | 2009-07-28 07:47 | Calculated | 07I30 | 07I30 - 2 Phase : 50.00 kVA : POLEMNT |  | 402SEG5480 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 8 | 24187 | 376 | 0.01555 | 0.00033076 | 50 | 2350 | 2009/2010 | July-2009 | 7 | 2009
22013 | Otorohanga Feeder Renewal Project | 2009-07-28 09:39 | 2009-07-28 | 2009-07-28 09:40 | Calculated | 209 | 209 - Fused Link 209 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 69 | 24187 | 8188 | 0.33853 | 0.0028528 | 775 | 99959 | 2009/2010 | July-2009 | 7 | 2009
22015 | Branch on line - Mangarino Road (corner Esplanade) | 2009-07-28 15:01 | 2009-07-28 | 2009-07-28 15:14 | Calculated | 219 | 219 - Air Break Switch 219 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 339 | 24187 | 4407 | 0.18221 | 0.014016 | 2205 | 28664 | 2009/2010 | July-2009 | 7 | 2009
22120 | Line Clash - Marakopa | 2009-07-29 08:17 | 2009-07-29 | 2009-07-29 10:18 | Calculated | T2822 | T2822 - 3ph 15kVA POL |  | 125SEG1536-1535 | Coast 125-06 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 1 | 24187 | 121 | 0.005 | 4.1345e-05 | 15 | 1815 | 2009/2010 | July-2009 | 7 | 2009
23298 | Install L.A Earth - Kururau Road | 2009-07-30 09:00 | 2009-07-30 | 2009-07-30 09:46 | Calculated | 08I15 | 08I15 - 3ph 100kVA POLEMNT |  | 403SEG5404-5243 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 46 | 5 | 24187 | 230 | 0.00951 | 0.00020672 | 100 | 4600 | 2009/2010 | July-2009 | 7 | 2009
23300 | Conductor vs Stay - Waimiha Road | 2009-07-30 09:15 | 2009-07-30 | 2009-07-30 11:47 | Calculated | 02J04 | 02J04 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5468 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 4 | 24187 | 608 | 0.02514 | 0.00016538 | 15 | 2280 | 2009/2010 | July-2009 | 7 | 2009
22018 | Coast Feeder Renewal Project | 2009-07-31 09:32 | 2009-07-31 | 2009-07-31 14:03 | Calculated | 187 | 187 - Fused Link 187 |  | 125SEG187 | Coast 125-04 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 12 | 24187 | 3252 | 0.13445 | 0.00049613 | 95 | 25745 | 2009/2010 | July-2009 | 7 | 2009
22017 | Install new C/c Pole & DDO T/O link @ P28 - For 12P05 | 2009-07-31 10:03 | 2009-07-31 | 2009-07-31 12:31 | Calculated | 5591 | 5591 - Sectionaliser with Bypass & Links 5591 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 52 | 24187 | 7696 | 0.31819 | 0.0021499 | 208 | 30783 | 2009/2010 | July-2009 | 7 | 2009
22019 | Burnt out Fuse Carrier - SH3 Pastoral Holdings | 2009-08-01 12:15 | 2009-08-01 | 2009-08-01 15:43 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 208 | 6 | 24192 | 1248 | 0.05159 | 0.00024802 | 90 | 18719 | 2009/2010 | August-2009 | 8 | 2009
22020 | Jumper off @ Links 276 - Piripiri Sub | 2009-08-01 15:37 | 2009-08-01 | 2009-08-01 15:57 | Calculated | 114 | 114 - Circuit Breaker with Bypass 114 |  | No Segment | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 317 | 24192 | 6340 | 0.26207 | 0.013104 | 2383.5 | 47669 | 2009/2010 | August-2009 | 8 | 2009
22021 | Tree through line - Kirikau Valley Road | 2009-08-02 15:20 | 2009-08-02 | 2009-08-03 11:50 | Calculated | 5765 | 5765 - Fused Link 5765 |  | 403SEG5765-5653 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1230 | 6 | 24192 | 7380 | 0.30506 | 0.00024802 | 28 | 34440 | 2009/2010 | August-2009 | 8 | 2009
22022 | Lightning - SH3 Taumatamaire | 2009-08-02 19:30 | 2009-08-02 | 2009-08-02 21:42 | Calculated | T2169 | T2169 - 1 Phase : 10.00 kVA : POLEMNT |  | 128SEG1602-1603 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 4 | 24192 | 528 | 0.02183 | 0.00016534 | 10 | 1320 | 2009/2010 | August-2009 | 8 | 2009
22023 | Lightning - SH3 Taumatamaire | 2009-08-02 19:30 | 2009-08-02 | 2009-08-02 21:42 | Calculated | T2170 | T2170 - 1 Phase : 25.00 kVA : POLEMNT |  | 128SEG1601 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 3 | 24192 | 396 | 0.01637 | 0.00012401 | 25 | 3299 | 2009/2010 | August-2009 | 8 | 2009
22024 | Lightning - SH3 Taumatamaire | 2009-08-03 08:03 | 2009-08-03 | 2009-08-03 10:05 | Calculated | T2170 | T2170 - 1 Phase : 25.00 kVA : POLEMNT |  | 128SEG1601 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 3 | 24192 | 366 | 0.01513 | 0.00012401 | 25 | 3049 | 2009/2010 | August-2009 | 8 | 2009
22028 | Faulty DDO - Mairoa Road | 2009-08-04 17:15 | 2009-08-04 | 2009-08-04 18:32 | Calculated | T1687 | T1687 - 1 Phase : 15.00 kVA : POLEMNT |  | 116SEG1354-1334 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 2 | 24192 | 154 | 0.00637 | 8.2672e-05 | 15 | 1155 | 2009/2010 | August-2009 | 8 | 2009
22029 | Condensation - Mt Ruapehu (by water tower) | 2009-08-04 23:52 | 2009-08-04 | 2009-08-05 00:06 | Calculated | 5990 | 5990 - Circuit Breaker 5990 |  | 419SEG5990-5991 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24192 |  | 0 | 0 |  |  | 2009/2010 | August-2009 | 8 | 2009
22031 | Fuse Pulled Apart - Burn Street | 2009-08-05 07:50 | 2009-08-05 | 2009-08-05 08:40 | Calculated | 20K09 | 20K09 - 3ph 75kVA POL |  | THUVVK | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 20 | 24192 | 1000 | 0.04134 | 0.00082672 | 75 | 3750 | 2009/2010 | August-2009 | 8 | 2009
22032 | Faulty Fuse Carrier - Hangatiki Caves Road | 2009-08-05 07:55 | 2009-08-05 | 2009-08-05 08:59 | Calculated | T81 | T81 - 3ph 75kVA POL |  | 101SEG1272-257 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 11 | 24192 | 704 | 0.0291 | 0.0004547 | 75 | 4799 | 2009/2010 | August-2009 | 8 | 2009
22030 | Replace Pole 17/1/2 & Stay | 2009-08-05 08:34 | 2009-08-05 | 2009-08-05 08:37 | Calculated | 5863 | 5863 - Recloser with Bypass & Links 5863 |  | 403SEG5863-5862 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 0 | 49 | 24192 | 1482 | 0.06126 | 0.0020255 | 385 | 0 | 2009/2010 | August-2009 | 8 | 2009
22038 | Unknown - SH4 | 2009-08-06 14:43 | 2009-08-06 | 2009-08-06 14:44 | Calculated | T3293 | T3293 - 3 Phase : 75.00 kVA : POLEMNT |  | No Segment | No Asset Group | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24192 |  | 0 | 0 |  |  | 2009/2010 | August-2009 | 8 | 2009
22039 | RAL tripped while testing - BDS to Jumbo T Bar 17N05 | 2009-08-06 14:44 | 2009-08-06 | 2009-08-06 15:45 | Calculated | 6148 | 6148 - Circuit Breaker 6148 |  | 415SEG6598RET | Turoa 415-03 | Rural B | Turoa | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24192 |  | 0 | 0 |  |  | 2009/2010 | August-2009 | 8 | 2009
22040 | Unknown - Power Road | 2009-08-07 08:45 | 2009-08-07 | 2009-08-07 10:16 | Calculated | 15I01 | 15I01 - 1 Phase : 15.00 kVA : POLEMNT |  | 410SEG5431-5407 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 3 | 24192 | 273 | 0.01128 | 0.00012401 | 15 | 1365 | 2009/2010 | August-2009 | 8 | 2009
22041 | Coast Feeder Renewal Project | 2009-08-07 09:36 | 2009-08-07 | 2009-08-07 15:26 | Calculated | 280 | 280 - Fused Link 280 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 350 | 12 | 24192 | 4308 | 0.17808 | 0.00049603 | 118 | 42362 | 2009/2010 | August-2009 | 8 | 2009
22043 | Unknown - Whibleys Road | 2009-08-09 07:26 | 2009-08-09 | 2009-08-09 08:15 | Calculated | 638 | 638 - Fused Link 638 |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 26 | 24192 | 1274 | 0.05266 | 0.0010747 | 240 | 11759 | 2009/2010 | August-2009 | 8 | 2009
22046 | Replace Poles & Xarms | 2009-08-11 08:06 | 2009-08-11 | 2009-08-11 08:08 | Calculated | 787 | 787 - Air Break Switch 787 |  | 123SEG460-787 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 32 | 24192 | 12000 | 0.49603 | 0.0013228 | 280 | 104999 | 2009/2010 | August-2009 | 8 | 2009
22045 | Coast Feeder Renewal Project | 2009-08-11 09:06 | 2009-08-11 | 2009-08-11 09:20 | Calculated | T525 | T525 - 3ph 25kVA POL |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 169 | 24192 | 18875 | 0.78022 | 0.0069858 | 1185 | 131744 | 2009/2010 | August-2009 | 8 | 2009
22047 | Wrap HV Bushing 16N23 | 2009-08-11 16:28 | 2009-08-11 | 2009-08-11 17:45 | Calculated | 6331 | 6331 - Fused Link 6331 |  | 419SEG6331-6332 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24192 |  | 0 | 0 |  |  | 2009/2010 | August-2009 | 8 | 2009
22049 | Replace Poles & Xarms | 2009-08-12 08:13 | 2009-08-12 | 2009-08-12 15:42 | Calculated | 787 | 787 - Air Break Switch 787 |  | 123SEG460-787 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24192 |  | 0 | 0 |  |  | 2009/2010 | August-2009 | 8 | 2009
22050 | Coast Feeder Renewal Project | 2009-08-12 08:33 | 2009-08-12 | 2009-08-12 08:44 | Calculated | T525 | T525 - 3ph 25kVA POL |  | 125SEG583-563 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 11 | 28 | 24192 | 9304 | 0.38459 | 0.0011574 | 235 | 76930 | 2009/2010 | August-2009 | 8 | 2009
22054 | Fuse pulled apart - Turakina Valley Road | 2009-08-12 18:25 | 2009-08-12 | 2009-08-12 19:37 | Calculated | 22O05 | 22O05 - 1 Phase : 15.00 kVA : POLEMNT |  | 416SEG5689-5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 3 | 24192 | 216 | 0.00893 | 0.00012401 | 15 | 1080 | 2009/2010 | August-2009 | 8 | 2009
22056 | Replace Poles & Xarms | 2009-08-13 08:18 | 2009-08-13 | 2009-08-13 14:10 | Calculated | 787 | 787 - Air Break Switch 787 |  | 123SEG460-787 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24192 |  | 0 | 0 |  |  | 2009/2010 | August-2009 | 8 | 2009
22058 | Fuse Pulled Apart - Maihihi Road | 2009-08-13 16:10 | 2009-08-13 | 2009-08-13 17:42 | Calculated | T604 | T604 - 3ph 5kVA polemnt |  | 111SEG346-REG6 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 24192 | 92 | 0.0038 | 4.1336e-05 | 5 | 460 | 2009/2010 | August-2009 | 8 | 2009
22059 | Rotten Pole 32/16 | 2009-08-14 10:00 | 2009-08-14 | 2009-08-14 12:06 | Calculated | 5359 | 5359 - Fused Link 5359 |  | 426SEG5359-5237 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOR | Pole Down - Rotten | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 55 | 24192 | 6930 | 0.28646 | 0.0022735 | 317.5 | 40004 | 2009/2010 | August-2009 | 8 | 2009
22060 | Wind - McBeth Road | 2009-08-15 07:30 | 2009-08-15 | 2009-08-15 11:09 | Calculated | T2052 | T2052 - 1 Phase : 7.50 kVA : POLEMNT |  | 115SEG1717-1723 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24192 |  | 0 | 0 |  |  | 2009/2010 | August-2009 | 8 | 2009
22061 | Switchboard Fire - Waipa River Road | 2009-08-15 16:57 | 2009-08-15 | 2009-08-15 18:47 | Calculated | T369 | T369 - 3ph 30kVA POLEMNT |  | 109SEG119-2107 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 4 | 24192 | 440 | 0.01819 | 0.00016534 | 30 | 3300 | 2009/2010 | August-2009 | 8 | 2009
22062 | Unknown - Waihaha Road | 2009-08-17 08:00 | 2009-08-17 | 2009-08-17 14:37 | Calculated | 03Q08 | 03Q08 - 1 Phase : 3.00 kVA : POLEMNT |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 397 | 1 | 24192 | 397 | 0.01641 | 4.1336e-05 | 3 | 1191 | 2009/2010 | August-2009 | 8 | 2009
22063 | Move Tx Pole away from bank | 2009-08-17 09:32 | 2009-08-17 | 2009-08-17 12:46 | Calculated | 5749 | 5749 - Fused Link 5749 |  | 409SEG5749 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 194 | 6 | 24192 | 1164 | 0.04812 | 0.00024802 | 50 | 9700 | 2009/2010 | August-2009 | 8 | 2009
22064 | Upgrade Tx - Pukewhau Road | 2009-08-17 10:26 | 2009-08-17 | 2009-08-17 14:51 | Calculated | T2354 | T2354 - 3 Phase : 50.00 kVA : POLEMNT |  | 122SEG524-448 | Wharepapa 122-01 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 265 | 2 | 24192 | 530 | 0.02191 | 8.2672e-05 | 50 | 13250 | 2009/2010 | August-2009 | 8 | 2009
22066 | Waihaha Feeder Renewal Project | 2009-08-18 10:03 | 2009-08-18 | 2009-08-18 12:29 | Calculated | 5592 | 5592 - Fused Link 5592 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 146 | 32 | 24192 | 4672 | 0.19312 | 0.0013228 | 283.5 | 41390 | 2009/2010 | August-2009 | 8 | 2009
22069 | Unknown - Lairdvale Road | 2009-08-18 13:50 | 2009-08-18 | 2009-08-18 14:25 | Calculated | 08I34 | 08I34 - 3 Phase : 200.00 kVA : GNDPAD |  | 402SEG5351-5548 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 36 | 24192 | 1260 | 0.05208 | 0.0014881 | 200 | 6999 | 2009/2010 | August-2009 | 8 | 2009
22071 | Faulty DDO Fuse Carrier - Te Anga Road | 2009-08-19 11:20 | 2009-08-19 | 2009-08-19 12:13 | Calculated | T1057 | T1057 - 1 Phase : 10.00 kVA : POLEMNT |  | 101SEG514 | Caves 101-11 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 53 | 1 | 24192 | 53 | 0.00219 | 4.1336e-05 | 10 | 530 | 2009/2010 | August-2009 | 8 | 2009
22072 | Waihaha Feeder Renewal Project | 2009-08-20 08:11 | 2009-08-20 | 2009-08-20 08:13 | Calculated | 5409 | 5409 - Recloser with Bypass 5409 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 157 | 24192 | 23828 | 0.98495 | 0.0064897 | 1178.5 | 206008 | 2009/2010 | August-2009 | 8 | 2009
22075 | Unknown - Te Anga Road | 2009-08-21 08:40 | 2009-08-21 | 2009-08-21 09:53 | Calculated | T516 | T516 - 3ph 25kVA POL |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 5 | 24192 | 365 | 0.01509 | 0.00020668 | 25 | 1825 | 2009/2010 | August-2009 | 8 | 2009
22077 | Upgrade L/A - Oio No. 1 Road | 2009-08-21 09:11 | 2009-08-21 | 2009-08-21 09:36 | Calculated | 12J06 | 12J06 - 1 Phase : 10.00 kVA : POLEMNT |  | 409SEG5749 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 1 | 24192 | 25 | 0.00103 | 4.1336e-05 | 10 | 250 | 2009/2010 | August-2009 | 8 | 2009
22079 | Fit Stay - Old Te Kuiti Road | 2009-08-21 10:49 | 2009-08-21 | 2009-08-21 11:29 | Calculated | T1120 | T1120 - 3 Phase : 30.00 kVA : POLEMNT |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 40 | 4 | 24192 | 160 | 0.00661 | 0.00016534 | 30 | 1200 | 2009/2010 | August-2009 | 8 | 2009
22080 | Unknown - Te Waaka Tce | 2009-08-21 19:15 | 2009-08-21 | 2009-08-21 21:04 | Calculated | 08R17 | 08R17 - 3ph 200kVA GNDPAD |  | 406SEG6557-6580 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 62 | 24192 | 6758 | 0.27935 | 0.0025628 | 200 | 21800 | 2009/2010 | August-2009 | 8 | 2009
22081 | Unknown - Te Waaka Tce | 2009-08-21 19:15 | 2009-08-21 | 2009-08-21 21:04 | Calculated | 08R19 | 08R19 - 3ph 200kVA GNDPAD |  | 406SEG6557-6580 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 53 | 24192 | 5777 | 0.2388 | 0.0021908 | 200 | 21799 | 2009/2010 | August-2009 | 8 | 2009
22082 | Unknown - SH40 | 2009-08-22 13:50 | 2009-08-22 | 2009-08-22 14:32 | Calculated | 05H02 | 05H02 - 2ph 7.5kVA POLEMNT |  | 421SEG5573 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 2 | 24192 | 84 | 0.00347 | 8.2672e-05 | 7.5 | 315 | 2009/2010 | August-2009 | 8 | 2009
22227 | HV Cable Fault - Anzac Street | 2009-08-23 11:37 | 2009-08-23 | 2009-08-23 12:57 | Calculated | T1003 | T1003 - 3 Phase : 200.00 kVA : GNDPAD |  | 108SEG287 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 60 | 24192 | 19200 | 0.79365 | 0.0024802 | 200 | 63999 | 2009/2010 | August-2009 | 8 | 2009
22083 | Faulty Tx - Happy Valley Road | 2009-08-23 11:38 | 2009-08-23 | 2009-08-23 12:32 | Calculated | T270 | T270 - 3 Phase : 30.03 kVA : POLEMNT |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 3 | 24192 | 162 | 0.0067 | 0.00012401 | 30 | 1620 | 2009/2010 | August-2009 | 8 | 2009
22085 | Waihaha Feeder Renewal Project | 2009-08-24 09:52 | 2009-08-24 | 2009-08-24 14:28 | Calculated | 5324 | 5324 - Fused Link 5324 |  | 426SEG5324RET | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 266 | 34 | 24192 | 3605 | 0.14902 | 0.0014054 | 257.5 | 21874 | 2009/2010 | August-2009 | 8 | 2009
22089 | Fault Zone Extended - Manunui Sub | 2009-08-25 05:02 | 2009-08-25 | 2009-08-25 05:51 | Calculated | 5187 | 5187 - Circuit Breaker Manunui 33kV 5187 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 1210 | 24192 | 59290 | 2.4508 | 0.050017 | 8964.5 | 439260 | 2009/2010 | August-2009 | 8 | 2009
22091 | Broken DDO @ 09K24 - Manunui Sub | 2009-08-25 05:02 | 2009-08-25 | 2009-08-25 06:16 | Calculated | 5132 | 5132 - Circuit Breaker Manunui SF6 5132 |  | No Segment | 510-01 Manunui | Rural B | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24192 |  | 0 | 0 |  |  | 2009/2010 | August-2009 | 8 | 2009
22092 | Broken DDO @ 09K24 - Tunga Hill | 2009-08-25 05:02 | 2009-08-25 | 2009-08-25 06:50 | Calculated | 5757 | 5757 - Air Break Switch 5757 |  | 409SEG5757-5761 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 608 | 24192 | 65664 | 2.7143 | 0.025132 | 4525.5 | 488753 | 2009/2010 | August-2009 | 8 | 2009
22093 | Broken DDO @ 09K24 - Taitua Street | 2009-08-25 05:02 | 2009-08-25 | 2009-08-25 06:58 | Calculated | 5920 | 5920 - Air Break Switch 5920 |  | 409SEG5920-5383 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 77 | 24192 | 8932 | 0.36921 | 0.0031829 | 902.5 | 104689 | 2009/2010 | August-2009 | 8 | 2009
22094 | Broken DDO @ 09K24 - Tanoa Street Piriaka | 2009-08-25 05:02 | 2009-08-25 | 2009-08-25 08:54 | Calculated | 5383 | 5383 - Air Break Switch 5383 |  | 409SEG5920-5383 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 232 | 10 | 24192 | 2320 | 0.0959 | 0.00041336 | 125 | 28999 | 2009/2010 | August-2009 | 8 | 2009
22095 | Wind - Mangare Road | 2009-08-25 05:23 | 2009-08-25 | 2009-08-25 08:06 | Calculated | T852 | T852 - 1 Phase : 25.00 kVA : polemnt |  | 121SEG435 | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 2 | 24192 | 326 | 0.01348 | 8.2672e-05 | 25 | 4075 | 2009/2010 | August-2009 | 8 | 2009
22090 | Fault Zone Extended - Manunui Sub | 2009-08-25 05:52 | 2009-08-25 | 2009-08-25 05:58 | Calculated | 5187 | 5187 - Circuit Breaker Manunui 33kV 5187 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 1210 | 24192 | 7260 | 0.3001 | 0.050017 | 8964.5 | 53786 | 2009/2010 | August-2009 | 8 | 2009
22086 | Waihaha Feeder Renewal Project | 2009-08-25 08:18 | 2009-08-25 | 2009-08-27 15:38 | Calculated | 5409 | 5409 - Recloser with Bypass 5409 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 3297 | 47 | 24192 | 39725 | 1.6421 | 0.0019428 | 367.5 | 314457 | 2009/2010 | August-2009 | 8 | 2009
22087 | Check HV Cable for Damage - Anzac Street | 2009-08-25 15:02 | 2009-08-25 | 2009-08-25 15:41 | Calculated | T1003 | T1003 - 3 Phase : 200.00 kVA : GNDPAD |  | 108SEG287 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 60 | 24192 | 2340 | 0.09673 | 0.0024802 | 200 | 7799 | 2009/2010 | August-2009 | 8 | 2009
22088 | Wind - Whangaehu Valley Road | 2009-08-26 00:34 | 2009-08-26 | 2009-08-26 01:02 | Calculated | 5961 | 5961 - Recloser with Bypass 5961 |  | 416SEG5961-5683 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 166 | 24192 | 124168 | 5.1326 | 0.0068618 | 7315 | 5471619 | 2009/2010 | August-2009 | 8 | 2009
22096 | Ligthning -Mangare Road | 2009-08-26 05:23 | 2009-08-26 | 2009-08-26 08:27 | Calculated | T2664 | T2664 - 1 Phase : 50.00 kVA : polemnt |  | 121SEG435 | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 1 | 24192 | 184 | 0.00761 | 4.1336e-05 | 50 | 9200 | 2009/2010 | August-2009 | 8 | 2009
22097 | Ligthning -Mangare Road | 2009-08-26 05:23 | 2009-08-26 | 2009-08-26 09:10 | Calculated | T854 | T854 - 3ph 30kVA polemnt |  | 121SEG435 | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 227 | 3 | 24192 | 681 | 0.02815 | 0.00012401 | 30 | 6810 | 2009/2010 | August-2009 | 8 | 2009
22098 | Eyebolt let go (Pole 399) - Turakina Valley Road | 2009-08-26 06:55 | 2009-08-26 | 2009-08-26 10:06 | Calculated | 6174 | 6174 - Recloser 6174 |  | 416SEG5711-6174 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 37 | 24192 | 7067 | 0.29212 | 0.0015294 | 360 | 68759 | 2009/2010 | August-2009 | 8 | 2009
22100 | Lightning - SH47 | 2009-08-26 07:28 | 2009-08-26 | 2009-08-26 09:05 | Calculated | 12P05 | 12P05 - 1 Phase : 15.00 kVA : POLEMNT |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 1 | 24192 | 97 | 0.00401 | 4.1336e-05 | 15 | 1455 | 2009/2010 | August-2009 | 8 | 2009
22101 | Ducks - Mangahauhau Valley Road | 2009-08-26 07:35 | 2009-08-26 | 2009-08-26 11:00 | Calculated | 5717 | 5717 - Fused Link 5717 |  | 416SEG5717 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 205 | 5 | 24192 | 1025 | 0.04237 | 0.00020668 | 45 | 9225 | 2009/2010 | August-2009 | 8 | 2009
22102 | Magpie - Hirangi Road | 2009-08-26 08:55 | 2009-08-26 | 2009-08-26 10:22 | Calculated | 10R03 | 10R03 - 1 Phase : 10.00 kVA : POLEMNT |  | 405SEG5519-5488 | Hirangi 405-01 | Rural B | Hirangi | Awamate Zone Substation (Containerised) |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 4 | 24192 | 348 | 0.01438 | 0.00016534 | 10 | 870 | 2009/2010 | August-2009 | 8 | 2009
22104 | Burnt out LV Fuses - Otewa Road | 2009-08-26 15:56 | 2009-08-26 | 2009-08-26 16:59 | Calculated | T2708 | T2708 - 3ph 30kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 2 | 24192 | 126 | 0.00521 | 8.2672e-05 | 30 | 1890 | 2009/2010 | August-2009 | 8 | 2009
22105 | Lightning - Koporotuku Road | 2009-08-26 17:20 | 2009-08-26 | 2009-08-26 18:50 | Calculated | 5730 | 5730 - Fused Link 5730 |  | 416SEG5730-5676 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 14 | 24192 | 1260 | 0.05208 | 0.0005787 | 130 | 11700 | 2009/2010 | August-2009 | 8 | 2009
22106 | Lightning - SH46 | 2009-08-26 17:55 | 2009-08-26 | 2009-08-26 20:07 | Calculated | 12R01 | 12R01 - 1 Phase : 10.00 kVA : POLEMNT |  | 418SEG5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 2 | 24192 | 264 | 0.01091 | 8.2672e-05 | 10 | 1320 | 2009/2010 | August-2009 | 8 | 2009
22109 | Waihaha Feeder Renewal Project | 2009-08-27 08:24 | 2009-08-27 | 2009-08-27 13:30 | Calculated | 5583 | 5583 - Air Break Switch 5583 |  | 426SEG5532-5583 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 280 | 12 | 24192 | 3360 | 0.13889 | 0.00049603 | 95 | 26599 | 2009/2010 | August-2009 | 8 | 2009
22108 | Wind - Wall Road | 2009-08-27 08:30 | 2009-08-27 | 2009-08-27 11:47 | Calculated | T372 | T372 - 1 Phase : 5.00 kVA : POLEMNT |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 3 | 24192 | 591 | 0.02443 | 0.00012401 | 5 | 984 | 2009/2010 | August-2009 | 8 | 2009
22113 | Birds - Manuariki Marae | 2009-08-27 16:50 | 2009-08-27 | 2009-08-27 17:55 | Calculated | 06I07 | 06I07 - 3 Phase : 100.00 kVA : POLEMNT |  | 402SEG5645-5471 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 7 | 24192 | 455 | 0.01881 | 0.00028935 | 100 | 6499 | 2009/2010 | August-2009 | 8 | 2009
22114 | Unknown - Oio Sub | 2009-08-27 19:00 | 2009-08-27 | 2009-08-27 20:19 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 24 | 24192 | 1896 | 0.07837 | 0.00099206 | 138.5 | 10941 | 2009/2010 | August-2009 | 8 | 2009
22107 | Change Links & Pole to T1048 | 2009-08-28 08:34 | 2009-08-28 | 2009-08-28 12:03 | Calculated | 349 | 349 - Air Break Switch 349 |  | 109SEG348-522 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 135 | 39 | 24192 | 5265 | 0.21763 | 0.0016121 | 338 | 45629 | 2009/2010 | August-2009 | 8 | 2009
22116 | Waihaha Feeder Renewal Project | 2009-08-28 09:23 | 2009-08-28 | 2009-08-28 14:41 | Calculated | 5324 | 5324 - Fused Link 5324 |  | 426SEG5324RET | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 34 | 24192 | 3759 | 0.15538 | 0.0014054 | 257.5 | 23669 | 2009/2010 | August-2009 | 8 | 2009
22117 | Tree Cutting - SH3 Soler's Spur | 2009-08-28 09:34 | 2009-08-28 | 2009-08-28 15:00 | Calculated | 1523 | 1523 - Air Break Switch 1523 |  | 128SEG1523 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 326 | 6 | 24192 | 1956 | 0.08085 | 0.00024802 | 28 | 9128 | 2009/2010 | August-2009 | 8 | 2009
22118 | Unknown - Waihaha Road | 2009-08-28 12:20 | 2009-08-28 | 2009-08-28 15:53 | Calculated | 03Q08 | 03Q08 - 1 Phase : 3.00 kVA : POLEMNT |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 213 | 1 | 24192 | 213 | 0.0088 | 4.1336e-05 | 3 | 639 | 2009/2010 | August-2009 | 8 | 2009
22119 | Jumper Off - SH3 Mokau | 2009-08-28 14:19 | 2009-08-28 | 2009-08-28 15:03 | Calculated | T2061 | T2061 - 1 Phase : 30.00 kVA : POLEMNT |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 1 | 24192 | 44 | 0.00182 | 4.1336e-05 | 30 | 1320 | 2009/2010 | August-2009 | 8 | 2009
22126 | High Winds - Mahoenui | 2009-08-30 01:18 | 2009-08-30 | 2009-08-30 01:30 | Calculated | 1010 | 1010 - Circuit Breaker Mahoenui 1010 |  | No Segment | 209-01 Mahoenui | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 624 | 24192 | 7488 | 0.30952 | 0.025794 | 3882.5 | 46589 | 2009/2010 | August-2009 | 8 | 2009
22149 | Landslip (Pole down) - Ruakuri Road (by Woolshed) | 2009-08-30 01:21 | 2009-08-30 | 2009-08-31 11:34 | Calculated | 514 | 514 - Fused Link 514 |  | 101SEG514 | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLG | Ground Subsidence | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2053 | 23 | 24192 | 47219 | 1.9518 | 0.00095073 | 150 | 307950 | 2009/2010 | August-2009 | 8 | 2009
22150 | Landslip (Pole down) - Te Anga Road | 2009-08-30 01:21 | 2009-08-30 | 2009-09-01 16:57 | Calculated | T1373 | T1373 - 1 Phase : 30.00 kVA : POLEMNT |  | 101SEG514 | Caves 101-11 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLG | Ground Subsidence | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3816 | 3 | 24192 | 11448 | 0.47321 | 0.00012401 | 30 | 114480 | 2009/2010 | August-2009 | 8 | 2009
22128 | High Winds - Kuratau Sub | 2009-08-30 05:02 | 2009-08-30 | 2009-08-30 05:14 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 4 | 24192 | 48 | 0.00198 | 0.00016534 | 450 | 5400 | 2009/2010 | August-2009 | 8 | 2009
22121 | CT Metering - Phillips Ave | 2009-08-30 09:08 | 2009-08-30 | 2009-08-30 13:37 | Calculated | T1552 | T1552 - 3 Phase : 300.00 kVA : GNDPAD |  | 112SEG300-646 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 3 | 24192 | 807 | 0.03336 | 0.00012401 | 300 | 80700 | 2009/2010 | August-2009 | 8 | 2009
22122 | HV Cable Fault - Anzac Street | 2009-08-30 11:37 | 2009-08-30 | 2009-08-30 12:57 | Calculated | T1003 | T1003 - 3 Phase : 200.00 kVA : GNDPAD |  | 108SEG287 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 60 | 24192 | 4800 | 0.19841 | 0.0024802 | 200 | 15999 | 2009/2010 | August-2009 | 8 | 2009
22123 | HV Cable Fault - Anzac Street | 2009-08-30 11:37 | 2009-08-30 | 2009-08-30 14:58 | Calculated | T1003 | T1003 - 3 Phase : 200.00 kVA : GNDPAD |  | 108SEG287 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 201 | 60 | 24192 | 12060 | 0.49851 | 0.0024802 | 200 | 40199 | 2009/2010 | August-2009 | 8 | 2009
22124 | Connect LV Backfeed - Boddies Tce | 2009-08-30 12:28 | 2009-08-30 | 2009-08-30 12:57 | Calculated | T464 | T464 - 3ph 300kVA GNDPAD |  | 106SEG590 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 52 | 24192 | 1508 | 0.06233 | 0.0021495 | 300 | 8699 | 2009/2010 | August-2009 | 8 | 2009
22125 | Connect LV Backfeed - Sheridan Street | 2009-08-30 14:36 | 2009-08-30 | 2009-08-30 14:58 | Calculated | T634 | T634 - 3 Phase : 200.00 kVA : GNDPAD |  | 105SEG643-210 | Te Kuiti Town 105-01 | Urban A | Te Kuiti Town | Waitete Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 43 | 24192 | 946 | 0.0391 | 0.0017774 | 200 | 4399 | 2009/2010 | August-2009 | 8 | 2009
22127 | Road Slip (No Access) Tumutumu Road | 2009-08-31 01:21 | 2009-08-31 | 2009-08-31 11:00 | Calculated | 109 | 109 - Recloser with bypass 109 |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLG | Ground Subsidence | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 579 | 92 | 24192 | 53268 | 2.2019 | 0.0038029 | 726 | 420353 | 2009/2010 | August-2009 | 8 | 2009
22130 | Wind - Ahuroa Road (on right) | 2009-08-31 06:00 | 2009-08-31 | 2009-08-31 07:34 | Calculated | 252 | 252 - Fused Link 252 |  | 106SEG252-803 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 10 | 24192 | 940 | 0.03886 | 0.00041336 | 50 | 4700 | 2009/2010 | August-2009 | 8 | 2009
22131 | Wind - Te Raumauku Road | 2009-08-31 06:25 | 2009-08-31 | 2009-08-31 10:03 | Calculated | 355 | 355 - Fused Link 355 |  | 112SEG355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 218 | 9 | 24192 | 1962 | 0.0811 | 0.00037202 | 95 | 20709 | 2009/2010 | August-2009 | 8 | 2009
22132 | Faulty Recloser (Bypassed) - Lower Retruke Sub | 2009-08-31 06:35 | 2009-08-31 | 2009-08-31 10:30 | Calculated | 5490 | 5490 - Recloser with Bypass 5490 |  | 410SEG5490-5438 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 235 | 73 | 24192 | 17155 | 0.70912 | 0.0030175 | 406 | 95409 | 2009/2010 | August-2009 | 8 | 2009
22133 | Line Down - Lower Retaruke Road | 2009-08-31 06:35 | 2009-08-31 | 2009-08-31 13:08 | Calculated | 5396 | 5396 - Sectionaliser 5396 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 393 | 44 | 24192 | 17292 | 0.71478 | 0.0018188 | 180 | 70739 | 2009/2010 | August-2009 | 8 | 2009
22134 | Wind - River Road Tokirima | 2009-08-31 06:40 | 2009-08-31 | 2009-08-31 10:09 | Calculated | T4059 | T4059 - 3 Phase : 50.00 kVA : POLEMNT |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 209 | 1 | 24192 | 209 | 0.00864 | 4.1336e-05 | 50 | 10450 | 2009/2010 | August-2009 | 8 | 2009
22135 | Wind - Mangakara Road | 2009-08-31 07:15 | 2009-08-31 | 2009-08-31 11:25 | Calculated | 07C02 | 07C02 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5304 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 250 | 2 | 24192 | 500 | 0.02067 | 8.2672e-05 | 15 | 3750 | 2009/2010 | August-2009 | 8 | 2009
22136 | Wind - Te Anga Road | 2009-08-31 07:35 | 2009-08-31 | 2009-08-31 12:37 | Calculated | T519 | T519 - 3ph 50kVA POL |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 302 | 8 | 24192 | 2416 | 0.09987 | 0.00033069 | 50 | 15100 | 2009/2010 | August-2009 | 8 | 2009
22137 | Wind - Owens Road (opposite Houghton's) | 2009-08-31 08:30 | 2009-08-31 | 2009-08-31 12:52 | Calculated | 1708 | 1708 - Fused Link 1708 |  | 115SEG1708-1738 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 262 | 18 | 24192 | 4716 | 0.19494 | 0.00074405 | 100 | 26199 | 2009/2010 | August-2009 | 8 | 2009
22138 | Wind - Tihoi Road | 2009-08-31 08:50 | 2009-08-31 | 2009-08-31 10:49 | Calculated | T2645 | T2645 - 3 Phase : 15.00 kVA : POLEMNT |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 3 | 24192 | 357 | 0.01476 | 0.00012401 | 15 | 1785 | 2009/2010 | August-2009 | 8 | 2009
22139 | Wind - Tahae Road | 2009-08-31 09:15 | 2009-08-31 | 2009-08-31 10:33 | Calculated | T3290 | T3290 - 3 Phase : 30.00 kVA : POLEMNT |  | 119SEG241 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24192 | 156 | 0.00645 | 8.2672e-05 | 30 | 2340 | 2009/2010 | August-2009 | 8 | 2009
22140 | Jumper Off T1882 - SH3 (by 22kV Sub) | 2009-08-31 09:46 | 2009-08-31 | 2009-08-31 10:28 | Calculated | 1524 | 1524 - Air Break Switch 1524 |  | 128SEG1524-1261 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 21 | 24192 | 882 | 0.03646 | 0.00086806 | 245 | 10290 | 2009/2010 | August-2009 | 8 | 2009
22141 | Waihaha Feeder Renewal Project | 2009-08-31 10:26 | 2009-08-31 | 2009-08-31 12:17 | Calculated | 5324 | 5324 - Fused Link 5324 |  | 426SEG5324RET | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 111 | 34 | 24192 | 4600 | 0.19015 | 0.0014054 | 257.5 | 36137 | 2009/2010 | August-2009 | 8 | 2009
22144 | LV Fault - Waitepipi Road | 2009-08-31 12:53 | 2009-08-31 | 2009-08-31 13:04 | Calculated | T125 | T125 - 3ph 15kVA POLEMNT |  | 107SEG258 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 3 | 24192 | 33 | 0.00136 | 0.00012401 | 15 | 165 | 2009/2010 | August-2009 | 8 | 2009
22145 | Wind - Sandel Road | 2009-08-31 15:15 | 2009-08-31 | 2009-08-31 16:00 | Calculated | T1419 | T1419 - 3ph 15kVA POLEMNT |  | 120SEG697 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 2 | 24192 | 90 | 0.00372 | 8.2672e-05 | 15 | 675 | 2009/2010 | August-2009 | 8 | 2009
22147 | Faulty ABS192 - Rangitoto Road (Cnr Ahuroa) | 2009-08-31 21:20 | 2009-08-31 | 2009-08-31 22:00 | Calculated | 585 | 585 - Air Break Switch 585 |  | 106SEG585-196 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 161 | 24192 | 6440 | 0.2662 | 0.0066551 | 1330 | 53199 | 2009/2010 | August-2009 | 8 | 2009
22129 | Wind - SH3 Pastoral Holdings | 2009-08-31 21:50 | 2009-08-31 | 2009-09-01 07:45 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 595 | 6 | 24192 | 3570 | 0.14757 | 0.00024802 | 90 | 53549 | 2009/2010 | August-2009 | 8 | 2009
22148 | Wind - Manuariki Marae | 2009-08-31 22:30 | 2009-08-31 | 2009-09-01 07:35 | Calculated | 06I07 | 06I07 - 3 Phase : 100.00 kVA : POLEMNT |  | 402SEG5645-5471 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 545 | 7 | 24192 | 3815 | 0.1577 | 0.00028935 | 100 | 54499 | 2009/2010 | August-2009 | 8 | 2009
22151 | Wind - Taumatatotoro West | 2009-09-01 07:35 | 2009-09-01 | 2009-09-01 10:42 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 8 | 24207 | 1496 | 0.0618 | 0.00033048 | 73 | 13651 | 2009/2010 | September-2009 | 9 | 2009
22156 | Waihaha Feeder Renewal Project | 2009-09-01 09:56 | 2009-09-01 | 2009-09-01 14:48 | Calculated | 5324 | 5324 - Fused Link 5324 |  | 426SEG5324RET | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 21 | 24207 | 21 | 0.00087 | 0.00086752 | 180 | 179 | 2009/2010 | September-2009 | 9 | 2009
22152 | Wind - Waimiha Road | 2009-09-01 13:10 | 2009-09-01 | 2009-09-01 16:02 | Calculated | T2115 | T2115 - 1 Phase : 30.00 kVA : POLEMNT |  | 103SEG705-1736 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 2 | 24207 | 344 | 0.01421 | 8.2621e-05 | 30 | 5160 | 2009/2010 | September-2009 | 9 | 2009
22153 | Disconnect Genset - Anzac Street | 2009-09-01 15:36 | 2009-09-01 | 2009-09-01 15:54 | Calculated | T1003 | T1003 - 3 Phase : 200.00 kVA : GNDPAD |  | 108SEG287 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 60 | 24207 | 1080 | 0.04462 | 0.0024786 | 200 | 3599 | 2009/2010 | September-2009 | 9 | 2009
22154 | Wind - Kopaki Road | 2009-09-02 07:45 | 2009-09-02 | 2009-09-02 09:57 | Calculated | T1088 | T1088 - 1 Phase : 15.00 kVA : POLEMNT |  | 103SEG641-1350 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 7 | 24207 | 924 | 0.03817 | 0.00028917 | 15 | 1979 | 2009/2010 | September-2009 | 9 | 2009
22155 | Unknown - Hautu Rangipo Road | 2009-09-02 09:25 | 2009-09-02 | 2009-09-02 10:27 | Calculated | 11T03 | 11T03 - 3ph 50kVA POLEMNT |  | 427SEG5392-5642 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22158 | Jumper Off @ CB 5876 - Manunui Sub | 2009-09-02 10:42 | 2009-09-02 | 2009-09-02 11:30 | Calculated | 5126 | 5126 - Air Break Switch 5126 |  | 407SEG5126-5850 | Manunui 407-01 (was Affco) | Rural B | Manunui / AFFCO Retired | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 5 | 24207 | 240 | 0.00991 | 0.00020655 | 565 | 27120 | 2009/2010 | September-2009 | 9 | 2009
22161 | Unknown - Hautu Rangipo Road | 2009-09-03 08:00 | 2009-09-03 | 2009-09-03 13:29 | Calculated | 11T03 | 11T03 - 3ph 50kVA POLEMNT |  | 427SEG5392-5642 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22163 | Replace Tx - Hospital Road | 2009-09-03 09:33 | 2009-09-03 | 2009-09-03 11:04 | Calculated | T1339 | T1339 - 3ph 50kVA POLEMNT |  | 107SEG555 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 11 | 24207 | 1001 | 0.04135 | 0.00045441 | 50 | 4549 | 2009/2010 | September-2009 | 9 | 2009
22166 | Broken Xarm @T2032 - Mangateka Road Spur | 2009-09-03 10:17 | 2009-09-03 | 2009-09-03 13:36 | Calculated | 1712 | 1712 - Fused Link 1712 |  | 115SEG1712-1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 28 | 24207 | 5572 | 0.23018 | 0.0011567 | 197.5 | 39302 | 2009/2010 | September-2009 | 9 | 2009
22167 | Upgrade Tx - SH32 | 2009-09-03 10:39 | 2009-09-03 | 2009-09-03 13:00 | Calculated | 06Q07 | 06Q07 - 1 Phase : 10.00 kVA : POLEMNT |  | 426SEG5588-5583 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 141 | 2 | 24207 | 282 | 0.01165 | 8.2621e-05 | 10 | 1410 | 2009/2010 | September-2009 | 9 | 2009
22168 | Unknown - Otunui North Road | 2009-09-03 13:20 | 2009-09-03 | 2009-09-03 14:06 | Calculated | 08G07 | 08G07 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 2 | 24207 | 92 | 0.0038 | 8.2621e-05 | 15 | 690 | 2009/2010 | September-2009 | 9 | 2009
22169 | Unknown - Taharoa | 2009-09-03 22:44 | 2009-09-03 | 2009-09-03 22:54 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22170 | Unknown - Hautu Rangipo Road | 2009-09-04 08:00 | 2009-09-04 | 2009-09-04 10:52 | Calculated | 11T03 | 11T03 - 3ph 50kVA POLEMNT |  | 427SEG5392-5642 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22174 | Replace Red Tagged Poles - Ranginui Road | 2009-09-04 10:36 | 2009-09-04 | 2009-09-04 13:44 | Calculated | 411 | 411 - Recloser with Bypass & Links 411 |  | No Segment | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 188 | 5 | 24207 | 940 | 0.03883 | 0.00020655 | 55 | 10339 | 2009/2010 | September-2009 | 9 | 2009
22175 | Unknown - Manunui Sub | 2009-09-04 12:27 | 2009-09-04 | 2009-09-04 12:28 | Calculated | 5132 | 5132 - Circuit Breaker Manunui SF6 5132 |  | No Segment | 510-01 Manunui | Rural B | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22176 | Unknown - Waipapa Road | 2009-09-05 12:30 | 2009-09-05 | 2009-09-06 02:15 | Calculated | T949 | T949 - 1 Phase : 25.00 kVA : polemnt |  | 121SEG565 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 825 | 2 | 24207 | 1650 | 0.06816 | 8.2621e-05 | 25 | 20625 | 2009/2010 | September-2009 | 9 | 2009
22177 | Unknown - Main South Road | 2009-09-06 12:30 | 2009-09-06 | 2009-09-06 13:50 | Calculated | 12K01 | 12K01 - 2ph 15kVA POLEMNT |  | 410SEG5457 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 4 | 24207 | 320 | 0.01322 | 0.00016524 | 15 | 1200 | 2009/2010 | September-2009 | 9 | 2009
22178 | Unknown - Tongaporutu Street | 2009-09-06 17:15 | 2009-09-06 | 2009-09-06 18:25 | Calculated | 07D03 | 07D03 - 3ph 100kVA POLEMNT |  | 413SEG6543-5996 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 30 | 24207 | 2100 | 0.08675 | 0.0012393 | 100 | 6999 | 2009/2010 | September-2009 | 9 | 2009
22179 | Magpie vs Possum - Pungarehu Road | 2009-09-07 06:35 | 2009-09-07 | 2009-09-07 08:16 | Calculated | T1639 | T1639 - 1 Phase : 15.00 kVA : POLEMNT |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals |  | BANI |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 2 | 24207 | 202 | 0.00834 | 8.2621e-05 | 15 | 1515 | 2009/2010 | September-2009 | 9 | 2009
22180 | Faulty Insulator - Hautu Rangipo Road | 2009-09-07 08:35 | 2009-09-07 | 2009-09-07 12:30 | Calculated | 11T03 | 11T03 - 3ph 50kVA POLEMNT |  | 427SEG5392-5642 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22181 | Fuse Pulled Apart - Whakapapa Road | 2009-09-07 12:55 | 2009-09-07 | 2009-09-07 14:37 | Calculated | 09K38 | 09K38 - 3 Phase : 3.00 kVA : POLEMNT |  | 409SEG5114 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 2 | 24207 | 204 | 0.00843 | 8.2621e-05 | 3 | 306 | 2009/2010 | September-2009 | 9 | 2009
22187 | Coast Feeder Renewal Project | 2009-09-09 09:04 | 2009-09-09 | 2009-09-09 14:50 | Calculated | 280 | 280 - Fused Link 280 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 346 | 12 | 24207 | 4152 | 0.17152 | 0.00049572 | 113 | 39097 | 2009/2010 | September-2009 | 9 | 2009
22193 | Coast Feeder Renewal Project | 2009-09-10 08:39 | 2009-09-10 | 2009-09-10 09:06 | Calculated | T542 | T542 - 3 Phase : 30.00 kVA : POLEMNT |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 27 | 6 | 24207 | 162 | 0.00669 | 0.00024786 | 30 | 810 | 2009/2010 | September-2009 | 9 | 2009
22191 | LV Clash/Faulty Tx - Cottles Road | 2009-09-10 10:20 | 2009-09-10 | 2009-09-10 16:01 | Calculated | T272 | T272 - 3 Phase : 15.00 kVA : POLEMNT |  | 111SEG579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 341 | 3 | 24207 | 1023 | 0.04226 | 0.00012393 | 15 | 5115 | 2009/2010 | September-2009 | 9 | 2009
22194 | Unknown - Borough Sub | 2009-09-11 09:09 | 2009-09-11 | 2009-09-11 09:10 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22196 | Fix Leaking HV Bushing in T2416 | 2009-09-12 05:02 | 2009-09-12 | 2009-09-12 07:31 | Calculated | 668 | 668 - Fused Link 668 |  | 112SEG668-229 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 149 | 39 | 24207 | 5811 | 0.24005 | 0.0016111 | 400 | 59599 | 2009/2010 | September-2009 | 9 | 2009
22197 | Fuse Pulled Apart - Pehi Road | 2009-09-12 08:50 | 2009-09-12 | 2009-09-12 09:43 | Calculated | 15K06 | 15K06 - 1 Phase : 10.00 kVA : POLEMNT |  | 411SEG5162-5145 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22199 | Fuse Fell Out - Main North Road | 2009-09-13 18:20 | 2009-09-13 | 2009-09-13 20:10 | Calculated | T1173 | T1173 - 3ph 200kVA gndpad |  | 111SEG305-304 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 1 | 24207 | 110 | 0.00454 | 4.131e-05 | 200 | 22000 | 2009/2010 | September-2009 | 9 | 2009
22202 | Waihaha Feeder Renewal Project | 2009-09-14 10:35 | 2009-09-14 | 2009-09-14 14:43 | Calculated | 5531 | 5531 - Sectionaliser 5531 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 13 | 24207 | 3224 | 0.13318 | 0.00053703 | 125 | 30999 | 2009/2010 | September-2009 | 9 | 2009
22203 | Incorrect Fuse Size - Kaahu Road | 2009-09-14 12:10 | 2009-09-14 | 2009-09-14 13:21 | Calculated | T2717 | T2717 - 3 Phase : 50.00 kVA : POLEMNT |  | 120SEG482-480 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 1 | 24207 | 71 | 0.00293 | 4.131e-05 | 50 | 3550 | 2009/2010 | September-2009 | 9 | 2009
22204 | Fuse Pulled Apart - Transpower Local Service | 2009-09-14 13:00 | 2009-09-14 | 2009-09-14 13:48 | Calculated | 08J47 | 08J47 - 3 Phase : 200.00 kVA : GNDPAD |  | 408SEG5129-5882 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22205 | Unknown - Whangamata Road | 2009-09-14 14:35 | 2009-09-14 | 2009-09-14 15:47 | Calculated | T1269 | T1269 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG145-553 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 2 | 24207 | 144 | 0.00595 | 8.2621e-05 | 10 | 720 | 2009/2010 | September-2009 | 9 | 2009
22212 | Rangitoto Feeder Line Renewal | 2009-09-16 07:53 | 2009-09-16 | 2009-09-16 15:52 | Calculated | 566 | 566 - Air Break Switch 566 |  | 106SEG247-2068 | Rangitoto 106-06 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 479 | 116 | 24207 | 41316 | 1.7068 | 0.004792 | 1012.5 | 361127 | 2009/2010 | September-2009 | 9 | 2009
22215 | Upgrade Tx - Ngahape Road | 2009-09-16 09:06 | 2009-09-16 | 2009-09-16 16:07 | Calculated | T15 | T15 - 3ph 25kVA polemnt |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 421 | 4 | 24207 | 1684 | 0.06957 | 0.00016524 | 25 | 10525 | 2009/2010 | September-2009 | 9 | 2009
22219 | Rangitoto Feeder Line Renewal | 2009-09-17 07:52 | 2009-09-17 | 2009-09-17 14:15 | Calculated | 566 | 566 - Air Break Switch 566 |  | 106SEG247-2068 | Rangitoto 106-06 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 383 | 164 | 24207 | 46023 | 1.9012 | 0.0067749 | 1310 | 368344 | 2009/2010 | September-2009 | 9 | 2009
22218 | Replace Broken Xarm - Piopio Feeder | 2009-09-17 08:55 | 2009-09-17 | 2009-09-17 14:24 | Calculated | 1303 | 1303 - Air Break Switch 1303 |  | 117SEG1300-1311 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 276 | 25 | 24207 | 6900 | 0.28504 | 0.0010328 | 163 | 44987 | 2009/2010 | September-2009 | 9 | 2009
22220 | Upgrade Earth Bank - SH32 | 2009-09-17 10:13 | 2009-09-17 | 2009-09-17 15:03 | Calculated | 06Q07 | 06Q07 - 1 Phase : 10.00 kVA : POLEMNT |  | 426SEG5588-5583 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 290 | 2 | 24207 | 580 | 0.02396 | 8.2621e-05 | 10 | 2900 | 2009/2010 | September-2009 | 9 | 2009
22221 | Suspect Cable Fault - Mt Ruapehu (by Water Tower) | 2009-09-17 13:45 | 2009-09-17 | 2009-09-17 13:46 | Calculated | 5990 | 5990 - Circuit Breaker 5990 |  | 419SEG5990-5991 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22222 | Suspect Cable Fault - for 16N26 | 2009-09-17 13:45 | 2009-09-17 | 2009-09-17 13:46 | Calculated | 6343 | 6343 - Ring Main Unit 6343 |  | 419SEG6343 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22223 | Fit New Links for Private Line - Maihihi | 2009-09-18 10:06 | 2009-09-18 | 2009-09-18 13:43 | Calculated | 365 | 365 - Fused Link 365 |  | 109SEG365RET | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 217 | 4 | 24207 | 868 | 0.03586 | 0.00016524 | 40 | 8679 | 2009/2010 | September-2009 | 9 | 2009
22224 | Pole Burnt in Half - Before Mokau Bridge | 2009-09-19 10:08 | 2009-09-19 | 2009-09-19 12:09 | Calculated | 1620 | 1620 - Recloser 1620 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 229 | 24207 | 27709 | 1.1447 | 0.0094601 | 1544 | 186823 | 2009/2010 | September-2009 | 9 | 2009
22225 | Pole Burnt in Half - Mohakatino | 2009-09-19 10:08 | 2009-09-19 | 2009-09-19 16:51 | Calculated | REG03 | REG03 - Mohakatino 3ph Voltage Regulator |  | 128SEG1634-REG3 | Mokau 128-06 | Remote Rural F | Mahoenui | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 403 | 187 | 24207 | 75361 | 3.1132 | 0.007725 | 1201 | 484002 | 2009/2010 | September-2009 | 9 | 2009
22226 | Pole Burnt in Half - SH3 Mokau | 2009-09-19 10:08 | 2009-09-19 | 2009-09-20 15:35 | Calculated | T1554 | T1554 - 3 Phase : 10.00 kVA : POLEMNT |  | 128SEG1634-REG3 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1 | 24207 | 1 | 4e-05 | 4.131e-05 | 100 | 100 | 2009/2010 | September-2009 | 9 | 2009
22230 | Tangiwai Feeder Renewal Project | 2009-09-21 09:06 | 2009-09-21 | 2009-09-21 15:47 | Calculated | 5708 | 5708 - Air Break Switch 5708 |  | 416SEG5708-5700 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 316 | 8 | 24207 | 2528 | 0.10443 | 0.00033048 | 58 | 18327 | 2009/2010 | September-2009 | 9 | 2009
22232 | Change Taps - Rover Road Tokirima | 2009-09-21 12:43 | 2009-09-21 | 2009-09-21 13:30 | Calculated | T4059 | T4059 - 3 Phase : 50.00 kVA : POLEMNT |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | PTRN2 | POUT:PTRN2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 47 | 1 | 24207 | 47 | 0.00194 | 4.131e-05 | 50 | 2350 | 2009/2010 | September-2009 | 9 | 2009
22233 | Magpie 02K19 - Waimiha (Past E/W Sub) | 2009-09-22 05:50 | 2009-09-22 | 2009-09-22 07:55 | Calculated | 5355 | 5355 - Sectionaliser with Bypass & Links 5355 |  | 421SEG5355-5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 17 | 24207 | 2125 | 0.08778 | 0.00070228 | 120 | 15000 | 2009/2010 | September-2009 | 9 | 2009
22234 | Magpie 02K19 - Waione Road | 2009-09-22 05:50 | 2009-09-22 | 2009-09-22 11:52 | Calculated | 5763 | 5763 - Fused Link 5763 |  | 421SEG5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 362 | 9 | 24207 | 3258 | 0.13459 | 0.00037179 | 65 | 23530 | 2009/2010 | September-2009 | 9 | 2009
22235 | Birds - Troopers Road | 2009-09-22 06:00 | 2009-09-22 | 2009-09-22 07:00 | Calculated | 231 | 231 - Fused Link 231 |  | 107SEG244-575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 2 | 24207 | 120 | 0.00496 | 8.2621e-05 | 65 | 3900 | 2009/2010 | September-2009 | 9 | 2009
22236 | Tree Felling with Digger - Isolation Only | 2009-09-22 09:31 | 2009-09-22 | 2009-09-22 15:25 | Calculated | 514 | 514 - Fused Link 514 |  | 101SEG514 | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 23 | 24207 | 8142 | 0.33635 | 0.00095014 | 150 | 53100 | 2009/2010 | September-2009 | 9 | 2009
22237 | Fit Private Line T/O fuses & Remove Old DDO's from T1709 | 2009-09-22 09:41 | 2009-09-22 | 2009-09-22 12:08 | Calculated | 1650 | 1650 - Air Break Switch 1650 |  | 113SEG1337-1650 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 70 | 24207 | 9100 | 0.37592 | 0.0028917 | 518 | 67340 | 2009/2010 | September-2009 | 9 | 2009
22239 | CT Metering - Club Habitat | 2009-09-22 13:00 | 2009-09-22 | 2009-09-22 15:06 | Calculated | 10S49 | 10S49 - 3 Phase : 300.00 kVA : GNDPAD |  | 424SEG5200-5168RET | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 126 | 1 | 24207 | 126 | 0.00521 | 4.131e-05 | 300 | 37800 | 2009/2010 | September-2009 | 9 | 2009
22240 | Unknown - Mangakahu Road | 2009-09-22 15:00 | 2009-09-22 | 2009-09-22 16:29 | Calculated | 04J10 | 04J10 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5669-5342 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 3 | 24207 | 267 | 0.01103 | 0.00012393 | 15 | 1335 | 2009/2010 | September-2009 | 9 | 2009
22255 | Coast Feeder Renewal Project | 2009-09-23 08:37 | 2009-09-23 | 2009-09-23 15:51 | Calculated | T542 | T542 - 3 Phase : 30.00 kVA : POLEMNT |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 434 | 95 | 24207 | 2693 | 0.11125 | 0.0039245 | 750.5 | 13740 | 2009/2010 | September-2009 | 9 | 2009
22254 | Tangiwai Feeder Renewal Project | 2009-09-23 09:29 | 2009-09-23 | 2009-09-23 12:48 | Calculated | 5708 | 5708 - Air Break Switch 5708 |  | 416SEG5708-5700 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 199 | 36 | 24207 | 7164 | 0.29595 | 0.0014872 | 6233 | 1240367 | 2009/2010 | September-2009 | 9 | 2009
22257 | CT Metering - Rangiatea Road | 2009-09-23 10:22 | 2009-09-23 | 2009-09-23 14:39 | Calculated | T1007 | T1007 - 3 Phase : 300.00 kVA : GNDPAD |  | 109SEG303-334 | Gravel Scoop 109-10 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | PTRN2 | POUT:PTRN2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 257 | 30 | 24207 | 7710 | 0.3185 | 0.0012393 | 300 | 77100 | 2009/2010 | September-2009 | 9 | 2009
22258 | Broken Insulator - Kaahu Tee Zone Substation | 2009-09-23 12:13 | 2009-09-23 | 2009-09-23 12:15 | Calculated | 1748 | 1748 - Circuit Breaker 1748 |  | No Segment | 216-01 Kaahu Tee | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22259 | Unknown - Waihaha Road | 2009-09-23 14:55 | 2009-09-23 | 2009-09-23 16:42 | Calculated | 03Q08 | 03Q08 - 1 Phase : 3.00 kVA : POLEMNT |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24207 | 107 | 0.00442 | 4.131e-05 | 3 | 321 | 2009/2010 | September-2009 | 9 | 2009
22260 | Unknown - Mine Road | 2009-09-23 18:05 | 2009-09-23 | 2009-09-23 18:08 | Calculated | 714 | 714 - Recloser with Bypass 714 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 61 | 24207 | 183 | 0.00756 | 0.0025199 | 1028 | 3084 | 2009/2010 | September-2009 | 9 | 2009
22261 | Unknown - King Country Lamb | 2009-09-24 07:34 | 2009-09-24 | 2009-09-24 07:40 | Calculated | 651 | 651 - Fused Link 651 |  | 103SEG651-652 | Pureora 119-03 RETIRED | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 1 | 24207 | 6 | 0.00025 | 4.131e-05 | 500 | 3000 | 2009/2010 | September-2009 | 9 | 2009
22262 | Unknown - Mine Road | 2009-09-24 07:34 | 2009-09-24 | 2009-09-24 09:11 | Calculated | 714 | 714 - Recloser with Bypass 714 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 61 | 24207 | 5917 | 0.24443 | 0.0025199 | 1028 | 99715 | 2009/2010 | September-2009 | 9 | 2009
22263 | Unknown - Tiroa Road (off Waipa Valley Road) | 2009-09-24 07:34 | 2009-09-24 | 2009-09-24 10:12 | Calculated | 709 | 709 - Air Break Switch 709 |  | No Segment | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 47 | 24207 | 7426 | 0.30677 | 0.0019416 | 360.5 | 56958 | 2009/2010 | September-2009 | 9 | 2009
22264 | Faulty Insulator & Cut Trees - Allens Road (off Waipa Valley Road) | 2009-09-24 07:34 | 2009-09-24 | 2009-09-24 11:51 | Calculated | 449 | 449 - Air Break Switch 449 |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 257 | 5 | 24207 | 1285 | 0.05308 | 0.00020655 | 45 | 11564 | 2009/2010 | September-2009 | 9 | 2009
22265 | Faulty Insulator & Cut Trees - Allens Road (off Waipa Valley Road) | 2009-09-24 14:39 | 2009-09-24 | 2009-09-24 17:11 | Calculated | 449 | 449 - Air Break Switch 449 |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 5 | 24207 | 760 | 0.0314 | 0.00020655 | 45 | 6839 | 2009/2010 | September-2009 | 9 | 2009
22271 | Fuse Fell Out - Rata Street | 2009-09-25 18:30 | 2009-09-25 | 2009-09-25 19:02 | Calculated | 08J46 | 08J46 - 3ph 200kVA GNDPAD |  | 408SEG5390-5621 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 25 | 24207 | 800 | 0.03305 | 0.0010328 | 200 | 6400 | 2009/2010 | September-2009 | 9 | 2009
22272 | Clash - Arohena Road (by Barrett's) | 2009-09-25 20:20 | 2009-09-25 | 2009-09-25 22:12 | Calculated | 565 | 565 - Fused Link 565 |  | 121SEG565 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 6 | 24207 | 672 | 0.02776 | 0.00024786 | 40 | 4480 | 2009/2010 | September-2009 | 9 | 2009
22273 | Tree Felled Thru Line - Wairehi Road (past Graham's) | 2009-09-26 18:06 | 2009-09-26 | 2009-09-26 19:56 | Calculated | 748 | 748 - Air Break Switch 748 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 81 | 24207 | 8910 | 0.36808 | 0.0033461 | 719 | 79090 | 2009/2010 | September-2009 | 9 | 2009
22275 | Faulty L.A - Ranginui Road | 2009-09-27 23:44 | 2009-09-27 | 2009-09-27 23:54 | Calculated | 411 | 411 - Recloser with Bypass & Links 411 |  | No Segment | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Protection | FAIL:FPRO |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 69 | 24207 | 690 | 0.0285 | 0.0028504 | 1388 | 13879 | 2009/2010 | September-2009 | 9 | 2009
22276 | Faulty L.A - Maraetai Substation | 2009-09-27 23:44 | 2009-09-27 | 2009-09-28 01:32 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Protection | FAIL:FPRO |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 145 | 24207 | 15660 | 0.64692 | 0.00599 | 2633 | 284363 | 2009/2010 | September-2009 | 9 | 2009
22277 | Faulty L.A - McLean Road (east end) | 2009-09-27 23:44 | 2009-09-27 | 2009-09-28 11:04 | Calculated | 406 | 406 - Air Break Switch 406 |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Protection | FAIL:FPRO |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 680 | 122 | 24207 | 17494 | 0.72268 | 0.0050399 | 1793 | 1219240 | 2009/2010 | September-2009 | 9 | 2009
22286 | Faulty DDO @ 03Q08 - Waihaha Road | 2009-09-28 10:15 | 2009-09-28 | 2009-09-28 11:39 | Calculated | 5534 | 5534 - Sectionaliser 5534 |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 14 | 24207 | 1176 | 0.04858 | 0.00057835 | 93 | 7812 | 2009/2010 | September-2009 | 9 | 2009
22288 | Unknown - Manunui Sub | 2009-09-29 04:47 | 2009-09-29 | 2009-09-29 04:59 | Calculated | 6143 | 6143 - Circuit Breaker Manunui 33kV 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24207 |  | 0 | 0 |  |  | 2009/2010 | September-2009 | 9 | 2009
22291 | Replace pole for T/O - Ongarue Road | 2009-09-29 10:03 | 2009-09-29 | 2009-09-29 14:26 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 263 | 15 | 24207 | 3945 | 0.16297 | 0.00061966 | 112.5 | 29587 | 2009/2010 | September-2009 | 9 | 2009
22293 | Twist Sleeve Broke @ Pole - Aotearoa Road | 2009-09-29 17:20 | 2009-09-29 | 2009-09-29 17:31 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 252 | 24207 | 2772 | 0.11451 | 0.01041 | 2263 | 24892 | 2009/2010 | September-2009 | 9 | 2009
22294 | Twist Sleeve Broke @ Pole - Whatauri Road | 2009-09-29 17:20 | 2009-09-29 | 2009-09-29 18:21 | Calculated | 619 | 619 - Air Break Switch 619 |  | 122SEG619-REG35 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 62 | 24207 | 3782 | 0.15624 | 0.0025612 | 580 | 35379 | 2009/2010 | September-2009 | 9 | 2009
22295 | Twist Sleeve Broke @ Pole - Hingaia Road | 2009-09-29 17:20 | 2009-09-29 | 2009-09-29 18:35 | Calculated | 371 | 371 - Air Break Switch 371 |  | 122SEG371-633 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 44 | 24207 | 3300 | 0.13632 | 0.0018177 | 247.5 | 18562 | 2009/2010 | September-2009 | 9 | 2009
22296 | Twist Sleeve Broke @ Pole 125/162- Ngaroma Road | 2009-09-29 17:20 | 2009-09-29 | 2009-09-29 20:03 | Calculated | 633 | 633 - Fused Link 633 |  | 122SEG633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 25 | 24207 | 4075 | 0.16834 | 0.0010328 | 142.5 | 23227 | 2009/2010 | September-2009 | 9 | 2009
22302 | Unknown - Tangitu Road (for Pareketu Road) | 2009-09-30 18:40 | 2009-09-30 | 2009-10-01 15:45 | Calculated | 1263 | 1263 - Sectionaliser with Incoming Link 1263 |  | 115SEG1356-1725 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1265 | 1 | 24207 | 1265 | 0.05226 | 4.131e-05 | 15 | 18975 | 2009/2010 | September-2009 | 9 | 2009
22303 | Wind - Marakopa | 2009-10-01 20:07 | 2009-10-01 | 2009-10-02 10:40 | Calculated | T2822 | T2822 - 3ph 15kVA POL |  | 125SEG1536-1535 | Coast 125-06 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 873 | 1 | 24220 | 873 | 0.03604 | 4.1288e-05 | 15 | 13095 | 2009/2010 | October-2009 | 10 | 2009
22307 | Replace 'H' Tower Xarms on pole 72 | 2009-10-02 08:28 | 2009-10-02 | 2009-10-02 11:28 | Calculated | 1716 | 1716 - Recloser with Bypass1716 |  | No Segment | No Asset Group | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 154 | 24220 | 6236 | 0.25747 | 0.0063584 | 1118.5 | 47410 | 2009/2010 | October-2009 | 10 | 2009
22309 | Rebuild Structure @ T1053 | 2009-10-02 09:08 | 2009-10-02 | 2009-10-02 14:47 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 339 | 8 | 24220 | 2712 | 0.11197 | 0.00033031 | 73 | 24747 | 2009/2010 | October-2009 | 10 | 2009
22312 | Unknown - Waitomo Valley Road | 2009-10-02 15:10 | 2009-10-02 | 2009-10-02 15:38 | Calculated | T216 | T216 - 1 Phase : 10.00 kVA : POLEMNT |  | 112SEG331-355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 2 | 24220 | 56 | 0.00231 | 8.2576e-05 | 10 | 280 | 2009/2010 | October-2009 | 10 | 2009
22313 | Possum - Tumutumu Road | 2009-10-02 22:57 | 2009-10-02 | 2009-10-03 00:10 | Calculated | 109 | 109 - Recloser with bypass 109 |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 92 | 24220 | 6716 | 0.27729 | 0.0037985 | 726 | 52997 | 2009/2010 | October-2009 | 10 | 2009
22314 | Possum - Te Anga Road | 2009-10-02 22:57 | 2009-10-02 | 2009-10-03 00:27 | Calculated | 506 | 506 - Air Break Switch 506 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 58 | 24220 | 5220 | 0.21552 | 0.0023947 | 441 | 39689 | 2009/2010 | October-2009 | 10 | 2009
22316 | Possum - Waipuna Road | 2009-10-02 22:57 | 2009-10-02 | 2009-10-03 00:43 | Calculated | 291 | 291 - Air Break Switch 291 |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 29 | 24220 | 3074 | 0.12692 | 0.0011974 | 233 | 24697 | 2009/2010 | October-2009 | 10 | 2009
22317 | Possum - Mahoe Road (Putaki Spur) | 2009-10-02 22:57 | 2009-10-02 | 2009-10-03 03:03 | Calculated | 289 | 289 - Fused Link 289 |  | 101SEG289-552 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 246 | 14 | 24220 | 3444 | 0.1422 | 0.00057803 | 105 | 25829 | 2009/2010 | October-2009 | 10 | 2009
22318 | Possum - Mahoe Road (past Piggeries) | 2009-10-02 22:57 | 2009-10-02 | 2009-10-03 11:22 | Calculated | 552 | 552 - Air Break Switch 552 |  | 101SEG552-290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 745 | 13 | 24220 | 9685 | 0.39988 | 0.00053675 | 95 | 70774 | 2009/2010 | October-2009 | 10 | 2009
22315 | Possum - Tumutumu Road | 2009-10-03 00:33 | 2009-10-03 | 2009-10-03 00:36 | Calculated | 109 | 109 - Recloser with bypass 109 |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 92 | 24220 | 276 | 0.0114 | 0.0037985 | 726 | 2178 | 2009/2010 | October-2009 | 10 | 2009
22335 | Wind - Paewhenua Road | 2009-10-04 05:50 | 2009-10-04 | 2009-10-04 07:34 | Calculated | T278 | T278 - 3 Phase : 25.00 kVA : POLEMNT |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 7 | 24220 | 728 | 0.03006 | 0.00028902 | 25 | 2599 | 2009/2010 | October-2009 | 10 | 2009
22320 | Unknown - Herekiekie Street | 2009-10-04 09:55 | 2009-10-04 | 2009-10-04 14:14 | Calculated | 10S09 | 10S09 - 3 Phase : 100.00 kVA : GNDPAD |  | 424SEG6559 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 259 | 71 | 24220 | 18389 | 0.75925 | 0.0029315 | 100 | 25899 | 2009/2010 | October-2009 | 10 | 2009
22322 | Tree Through Line - SH49 Ohutu | 2009-10-04 14:58 | 2009-10-04 | 2009-10-04 17:40 | Calculated | 5681 | 5681 - Air Break Switch 5681 |  | 416SEG5681-6118 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 184 | 24220 | 29808 | 1.2307 | 0.007597 | 7690 | 1245779 | 2009/2010 | October-2009 | 10 | 2009
22323 | Line Down (snow) - Whangaehu Valley Road | 2009-10-04 14:58 | 2009-10-04 | 2009-10-05 13:31 | Calculated | 5961 | 5961 - Recloser with Bypass 5961 |  | 416SEG5961-5683 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1353 | 166 | 24220 | 224598 | 9.2733 | 0.0068538 | 7315 | 9897195 | 2009/2010 | October-2009 | 10 | 2009
22324 | Line Down (snow) - Winstones Pulp Mill | 2009-10-04 14:58 | 2009-10-04 | 2009-10-05 16:08 | Calculated | 5709 | 5709 - Air Break Switch 5709 |  | 416SEG5709-5796 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1510 | 28 | 24220 | 42280 | 1.7457 | 0.0011561 | 6425 | 9701750 | 2009/2010 | October-2009 | 10 | 2009
22336 | Tree Through Line - Ruapehu Road | 2009-10-04 14:58 | 2009-10-04 | 2009-10-05 12:56 | Calculated | 5677 | 5677 - Recloser with Bypass 5677 |  | 416SEG5677-5681 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1318 | 228 | 24220 | 300504 | 12.4073 | 0.0094137 | 8020 | 10570360 | 2009/2010 | October-2009 | 10 | 2009
22325 | Trees - Kuratau Sub | 2009-10-04 15:45 | 2009-10-04 | 2009-10-05 16:15 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24220 |  | 0 | 0 |  |  | 2009/2010 | October-2009 | 10 | 2009
22326 | Line Down (snow) - National Park North | 2009-10-04 19:59 | 2009-10-04 | 2009-10-04 20:46 | Calculated | 5144 | 5144 - Circuit Breaker with Bypass 5144 |  | 411SEG5144-5769 | 501-01 National Park | Rural D | National Park | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 420 | 24220 | 132552 | 5.4728 | 0.017341 | 3282 | 575896 | 2009/2010 | October-2009 | 10 | 2009
22327 | Line Down (snow) - SH4 | 2009-10-04 19:59 | 2009-10-04 | 2009-10-04 21:42 | Calculated | 5146 | 5146 - Air Break Switch 5146 |  | 411SEG5146-5148 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 90 | 24220 | 9270 | 0.38274 | 0.0037159 | 274 | 28221 | 2009/2010 | October-2009 | 10 | 2009
22328 | Line Down (snow/trees) - Ohakune Sub | 2009-10-04 20:21 | 2009-10-04 | 2009-10-04 21:06 | Calculated | 5003 | 5003 - Circuit Breaker 5003 |  | No Segment | 517-01 Transpower Ohakune | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 428 | 24220 | 19260 | 0.79521 | 0.017671 | 2808 | 126359 | 2009/2010 | October-2009 | 10 | 2009
22329 | Line Down (snow/trees) - Dreadnought Road | 2009-10-04 20:21 | 2009-10-04 | 2009-10-04 22:05 | Calculated | 5695 | 5695 - Air Break Switch 5695 |  | 415SEG5695-5692 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 182 | 24220 | 18928 | 0.7815 | 0.0075145 | 678 | 70511 | 2009/2010 | October-2009 | 10 | 2009
22331 | Line Down (snow/trees) - Mangateitei Road | 2009-10-04 20:21 | 2009-10-04 | 2009-10-05 12:34 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 973 | 29 | 24220 | 28217 | 1.165 | 0.0011974 | 285 | 277304 | 2009/2010 | October-2009 | 10 | 2009
22332 | Line Down (snow/trees) - SH49 Ohutu | 2009-10-04 20:21 | 2009-10-04 | 2009-10-05 13:06 | Calculated | 5681 | 5681 - Air Break Switch 5681 |  | 416SEG5681-6118 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1005 | 184 | 24220 | 184920 | 7.635 | 0.007597 | 7690 | 7728449 | 2009/2010 | October-2009 | 10 | 2009
22333 | Line Down (snow/trees) - Rangataua Township | 2009-10-04 20:21 | 2009-10-04 | 2009-10-05 13:45 | Calculated | 5712 | 5712 - Fused Link 5712 |  | 415SEG5712-6323 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24220 |  | 0 | 0 |  |  | 2009/2010 | October-2009 | 10 | 2009
22334 | Broken Pole (trees) - Tawahi Sub | 2009-10-04 20:58 | 2009-10-04 | 2009-10-05 12:35 | Calculated | 6007 | 6007 - Circuit Breaker 6007 |  | No Segment | 513-01 Tawhai | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 937 | 111 | 24220 | 104007 | 4.2943 | 0.004583 | 1106 | 1036321 | 2009/2010 | October-2009 | 10 | 2009
22330 | Line Down (snow/trees) - Ohakune Sub | 2009-10-04 22:18 | 2009-10-04 | 2009-10-04 22:26 | Calculated | 5003 | 5003 - Circuit Breaker 5003 |  | No Segment | 517-01 Transpower Ohakune | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 477 | 24220 | 38426 | 1.5865 | 0.019694 | 3308 | 266187 | 2009/2010 | October-2009 | 10 | 2009
22337 | Wind - Tauraroa Road | 2009-10-05 05:35 | 2009-10-05 | 2009-10-05 08:09 | Calculated | 374 | 374 - Fused Link 374 |  | 111SEG374-783 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 20 | 24220 | 3080 | 0.12717 | 0.00082576 | 335 | 51589 | 2009/2010 | October-2009 | 10 | 2009
22338 | Wind - Oio Sub | 2009-10-05 07:20 | 2009-10-05 | 2009-10-05 10:02 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 24 | 24220 | 3888 | 0.16053 | 0.00099092 | 138.5 | 22436 | 2009/2010 | October-2009 | 10 | 2009
22339 | Branch on Line - Whangaehu Valley Road | 2009-10-05 15:34 | 2009-10-05 | 2009-10-05 15:48 | Calculated | 5685 | 5685 - Fused Link 5685 |  | 416SEG5685-5716 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 18 | 24220 | 252 | 0.0104 | 0.00074319 | 135 | 1890 | 2009/2010 | October-2009 | 10 | 2009
22340 | Line Down - National Park North | 2009-10-05 19:09 | 2009-10-05 | 2009-10-05 19:59 | Calculated | 5144 | 5144 - Circuit Breaker with Bypass 5144 |  | 411SEG5144-5769 | 501-01 National Park | Rural D | National Park | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 420 | 24220 | 21000 | 0.86705 | 0.017341 | 3282 | 164099 | 2009/2010 | October-2009 | 10 | 2009
22341 | Line Down - Buddo Street | 2009-10-05 19:09 | 2009-10-05 | 2009-10-05 21:57 | Calculated | 5769 | 5769 - Air Break Switch 5769 |  | 411SEG5769-5147 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 317 | 24220 | 53256 | 2.1988 | 0.013088 | 2478 | 416303 | 2009/2010 | October-2009 | 10 | 2009
22342 | Unknown - Kururau Road | 2009-10-06 14:46 | 2009-10-06 | 2009-10-06 17:36 | Calculated | 08G03 | 08G03 - 1 Phase : 10.00 kVA : POLEMNT |  | 403SEG5812-5321 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 1 | 24220 | 170 | 0.00702 | 4.1288e-05 | 10 | 1700 | 2009/2010 | October-2009 | 10 | 2009
22343 | Fuse Fell Out (vibration) - Ararimu East Road | 2009-10-06 15:18 | 2009-10-06 | 2009-10-06 17:24 | Calculated | 06H05 | 06H05 - 1 Phase : 15.00 kVA : POLEMNT |  | 422SEG5538-5841 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 2 | 24220 | 252 | 0.0104 | 8.2576e-05 | 15 | 1890 | 2009/2010 | October-2009 | 10 | 2009
22344 | Clash - SH49 | 2009-10-06 15:25 | 2009-10-06 | 2009-10-06 16:01 | Calculated | T4082 | T4082 - 3 Phase : 15.00 kVA : POLEMNT |  | 415SEG5705 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24220 |  | 0 | 0 |  |  | 2009/2010 | October-2009 | 10 | 2009
22345 | Coast Feeder Renewal Project | 2009-10-07 09:01 | 2009-10-07 | 2009-10-07 09:05 | Calculated | T542 | T542 - 3 Phase : 30.00 kVA : POLEMNT |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 9 | 24220 | 1050 | 0.04335 | 0.00037159 | 55 | 8229 | 2009/2010 | October-2009 | 10 | 2009
22347 | Fuse Pulled Apart - Sunshine Drive | 2009-10-07 14:35 | 2009-10-07 | 2009-10-07 14:55 | Calculated | 08I58 | 08I58 - 3ph 50kVA POLEMNT |  | 404SEG5022-L1.10 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 10 | 24220 | 200 | 0.00826 | 0.00041288 | 50 | 1000 | 2009/2010 | October-2009 | 10 | 2009
22349 | Coast Feeder Renewal Project | 2009-10-08 08:58 | 2009-10-08 | 2009-10-08 09:18 | Calculated | T542 | T542 - 3 Phase : 30.00 kVA : POLEMNT |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 20 | 120 | 24220 | 41160 | 1.6994 | 0.0049546 | 958.5 | 334859 | 2009/2010 | October-2009 | 10 | 2009
22351 | Branch on Line - Ruapehu Road | 2009-10-08 18:23 | 2009-10-08 | 2009-10-08 18:27 | Calculated | 5677 | 5677 - Recloser with Bypass 5677 |  | 416SEG5677-5681 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 228 | 24220 | 912 | 0.03765 | 0.0094137 | 8020 | 32079 | 2009/2010 | October-2009 | 10 | 2009
22353 | Duck - Kawakawa Road | 2009-10-09 09:40 | 2009-10-09 | 2009-10-09 12:09 | Calculated | 822 | 822 - Fuse Link 822 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 1 | 24220 | 149 | 0.00615 | 4.1288e-05 | 15 | 2235 | 2009/2010 | October-2009 | 10 | 2009
22354 | CT Metering - Manu Ariki Marae | 2009-10-09 09:50 | 2009-10-09 | 2009-10-09 11:38 | Calculated | T4025 | T4025 - 3 Phase : 200.00 kVA : GNDPAD |  | 402SEG5645-5471 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 108 | 2 | 24220 | 216 | 0.00892 | 8.2576e-05 | 200 | 21600 | 2009/2010 | October-2009 | 10 | 2009
22355 | Magpie - Mokauiti Road | 2009-10-09 12:40 | 2009-10-09 | 2009-10-09 13:58 | Calculated | T2030 | T2030 - 1 Phase : 15.00 kVA : POLEMNT |  | 115SEG1707-1648 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 4 | 24220 | 312 | 0.01288 | 0.00016515 | 15 | 1170 | 2009/2010 | October-2009 | 10 | 2009
22356 | LV Fault - Waitomo Valley Road | 2009-10-09 19:20 | 2009-10-09 | 2009-10-09 19:58 | Calculated | T1399 | T1399 - 3ph 25kVA POLEMNT |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 3 | 24220 | 114 | 0.00471 | 0.00012386 | 25 | 949 | 2009/2010 | October-2009 | 10 | 2009
22357 | Suspension Arm Let Go - SH40 Mangakara | 2009-10-10 09:25 | 2009-10-10 | 2009-10-10 13:36 | Calculated | 5305 | 5305 - Sectionaliser with Bypass & Links 5305 |  | 413SEG5305-5306 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 251 | 25 | 24220 | 6275 | 0.25908 | 0.0010322 | 145 | 36394 | 2009/2010 | October-2009 | 10 | 2009
22358 | Suspension Arm Let Go - SH40 Mangakara | 2009-10-10 13:47 | 2009-10-10 | 2009-10-10 16:55 | Calculated | 5305 | 5305 - Sectionaliser with Bypass & Links 5305 |  | 413SEG5305-5306 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 25 | 24220 | 4700 | 0.19405 | 0.0010322 | 145 | 27259 | 2009/2010 | October-2009 | 10 | 2009
22360 | Faulty DDO - Otunui/Kirikau Sub | 2009-10-11 10:28 | 2009-10-11 | 2009-10-11 12:24 | Calculated | 5316 | 5316 - Sectionaliser with Bypass & Links 5316 |  | 403SEG5377-5378 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 26 | 24220 | 3016 | 0.12453 | 0.0010735 | 165 | 19139 | 2009/2010 | October-2009 | 10 | 2009
22375 | Replace Pole - Seafund Road | 2009-10-11 12:14 | 2009-10-11 | 2009-10-11 15:46 | Calculated | 372 | 372 - Fused Link 372 |  | 122SEG372 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 212 | 21 | 24220 | 4452 | 0.18382 | 0.00086705 | 133 | 28195 | 2009/2010 | October-2009 | 10 | 2009
22376 | Unknown - Main Sth Road Piopio | 2009-10-11 12:45 | 2009-10-11 | 2009-10-11 15:24 | Calculated | T1723 | T1723 - 1 Phase : 15.00 kVA : POLEMNT |  | 116SEG1310-1781 | Piopio 116-03 | Rural D | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 2 | 24220 | 318 | 0.01313 | 8.2576e-05 | 15 | 2385 | 2009/2010 | October-2009 | 10 | 2009
22365 | Clash - Tirohanga Road | 2009-10-11 14:05 | 2009-10-11 | 2009-10-11 15:22 | Calculated | T517 | T517 - 3ph 13kVA POLEMNT |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 1 | 24220 | 77 | 0.00318 | 4.1288e-05 | 13 | 1001 | 2009/2010 | October-2009 | 10 | 2009
22377 | Low SWER Line - Waimiha Sub | 2009-10-11 14:40 | 2009-10-11 | 2009-10-11 15:48 | Calculated | 5468 | 5468 - Fused Link 5468 |  | 421SEG5468 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DICL | Conductor Low - Incorrect Clearances | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 68 | 18 | 24220 | 1224 | 0.05054 | 0.00074319 | 120 | 8160 | 2009/2010 | October-2009 | 10 | 2009
22366 | Switching Error - Borough Sub | 2009-10-11 15:02 | 2009-10-11 | 2009-10-11 15:15 | Calculated | 880 | 880 - Circuit Breaker Hakiaha 880 |  | No Segment | 508-01 Borough |  | Hakiaha | Borough Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 298 | 24220 | 3874 | 0.15995 | 0.012304 | 3580 | 46539 | 2009/2010 | October-2009 | 10 | 2009
22379 | Replace 3 Pole Structure 4101039 | 2009-10-13 07:52 | 2009-10-13 | 2009-10-13 14:40 | Calculated | 5235 | 5235 - Air Break Switch 5235 |  | 409SEG5138-5235 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 361 | 217 | 24220 | 8784 | 0.36268 | 0.0089595 | 1470 | 99916 | 2009/2010 | October-2009 | 10 | 2009
22380 | Otorohanga Feeder Renewal Project | 2009-10-13 09:02 | 2009-10-13 | 2009-10-13 13:42 | Calculated | 771 | 771 - Fused Link 771 |  | 112SEG771 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 280 | 11 | 24220 | 3080 | 0.12717 | 0.00045417 | 60 | 16800 | 2009/2010 | October-2009 | 10 | 2009
22381 | Possum - Waitea Road | 2009-10-13 12:45 | 2009-10-13 | 2009-10-13 16:29 | Calculated | 09K05 | 09K05 - 2ph 15kVA POLEMNT |  | 409SEG5134 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 224 | 2 | 24220 | 448 | 0.0185 | 8.2576e-05 | 15 | 3360 | 2009/2010 | October-2009 | 10 | 2009
22382 | Tree Through Line - Kirikau Sub | 2009-10-14 06:25 | 2009-10-14 | 2009-10-14 07:21 | Calculated | 5378 | 5378 - Recloser with Bypass & Links 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 65 | 24220 | 3640 | 0.15029 | 0.0026837 | 383 | 21447 | 2009/2010 | October-2009 | 10 | 2009
22383 | Tree Through Line - Kirikau Valley Road | 2009-10-14 06:25 | 2009-10-14 | 2009-10-14 12:14 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 349 | 15 | 24220 | 5235 | 0.21614 | 0.00061932 | 98 | 34201 | 2009/2010 | October-2009 | 10 | 2009
22384 | Upgrade SWER Sub, Recloser & Earth Bank | 2009-10-14 09:33 | 2009-10-14 | 2009-10-14 15:04 | Calculated | 1102 | 1102 - Air Break Switch 1102 |  | 114SEG1102-1126RET | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 331 | 53 | 24220 | 17543 | 0.72432 | 0.0021883 | 368 | 121807 | 2009/2010 | October-2009 | 10 | 2009
22385 | Dig out & pull straight Pole 81/100 | 2009-10-14 10:05 | 2009-10-14 | 2009-10-14 11:00 | Calculated | 252 | 252 - Fused Link 252 |  | 106SEG252-803 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 55 | 10 | 24220 | 550 | 0.02271 | 0.00041288 | 50 | 2750 | 2009/2010 | October-2009 | 10 | 2009
22386 | Downgrade Tx 2573 - SH30 Waipa Valley | 2009-10-15 11:10 | 2009-10-15 | 2009-10-15 13:12 | Calculated | T2573 | T2573 - 3ph 100kVA POLEMNT |  | 119SEG432-653 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 122 | 3 | 24220 | 366 | 0.01511 | 0.00012386 | 100 | 12199 | 2009/2010 | October-2009 | 10 | 2009
22387 | Restore 100kVA Tx 2573 - SH30 Waipa Valley (see 22386) | 2009-10-15 16:24 | 2009-10-15 | 2009-10-15 17:45 | Calculated | T2573 | T2573 - 3ph 100kVA POLEMNT |  | 119SEG432-653 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 3 | 24220 | 243 | 0.01003 | 0.00012386 | 100 | 8099 | 2009/2010 | October-2009 | 10 | 2009
22390 | Broken Stay - Mangapapa Road | 2009-10-16 16:09 | 2009-10-16 | 2009-10-16 17:37 | Calculated | 04F08 | 04F08 - 1 Phase : 15.00 kVA : POLEMNT |  | 422SEG5274-5278 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 5 | 24220 | 440 | 0.01817 | 0.00020644 | 15 | 1320 | 2009/2010 | October-2009 | 10 | 2009
22391 | Lightning - SH4 (by Tuhua Road) | 2009-10-17 07:40 | 2009-10-17 | 2009-10-17 09:03 | Calculated | 1321 | 1321 - Recloser 1321 |  | 117SEG1314-1324 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 40 | 24220 | 3320 | 0.13708 | 0.0016515 | 228.5 | 18965 | 2009/2010 | October-2009 | 10 | 2009
22392 | Lightning - SH4 (by Tuhua Road) | 2009-10-17 11:45 | 2009-10-17 | 2009-10-17 13:08 | Calculated | 1321 | 1321 - Recloser 1321 |  | 117SEG1314-1324 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 40 | 24220 | 3320 | 0.13708 | 0.0016515 | 228.5 | 18965 | 2009/2010 | October-2009 | 10 | 2009
22393 | Unknown - SH4 Puketutu Spur | 2009-10-17 11:45 | 2009-10-17 | 2009-10-17 14:45 | Calculated | T1811 | T1811 - 1 Phase : 15.00 kVA : POLEMNT |  | 117SEG1322 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 5 | 24220 | 900 | 0.03716 | 0.00020644 | 45 | 8100 | 2009/2010 | October-2009 | 10 | 2009
22395 | Unknown - SH4 Puketutu Spur | 2009-10-17 11:45 | 2009-10-17 | 2009-10-17 16:56 | Calculated | T3010 | T3010 - 1 Phase : 7.50 kVA : POLEMNT |  | 117SEG1322 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 311 | 5 | 24220 | 1555 | 0.0642 | 0.00020644 | 20.5 | 6375 | 2009/2010 | October-2009 | 10 | 2009
22394 | Unknown - SH4 Puketutu Spur | 2009-10-17 16:34 | 2009-10-17 | 2009-10-17 16:56 | Calculated | T1811 | T1811 - 1 Phase : 15.00 kVA : POLEMNT |  | 117SEG1322 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 5 | 24220 | 110 | 0.00454 | 0.00020644 | 45 | 990 | 2009/2010 | October-2009 | 10 | 2009
22397 | Lightning - Raurimu Road | 2009-10-17 16:51 | 2009-10-17 | 2009-10-17 18:05 | Calculated | 13K04 | 13K04 - 1 Phase : 5.00 kVA : POLEMNT |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 1 | 24220 | 74 | 0.00306 | 4.1288e-05 | 5 | 370 | 2009/2010 | October-2009 | 10 | 2009
22398 | Lightning - Kaitieke Road | 2009-10-17 16:59 | 2009-10-17 | 2009-10-17 18:05 | Calculated | 13K07 | 13K07 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 2 | 24220 | 132 | 0.00545 | 8.2576e-05 | 10 | 660 | 2009/2010 | October-2009 | 10 | 2009
22396 | Unknown - SH4 Puketutu Spur | 2009-10-17 17:10 | 2009-10-17 | 2009-10-17 17:30 | Calculated | 1322 | 1322 - Sectionaliser 1322 |  | 117SEG1322 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 27 | 24220 | 540 | 0.0223 | 0.0011148 | 161 | 3219 | 2009/2010 | October-2009 | 10 | 2009
22399 | Faulty Tx558 (trees) - Oparure Road | 2009-10-17 17:55 | 2009-10-17 | 2009-10-17 19:47 | Calculated | 250 | 250 - Fused Link 250 |  | 107SEG250-254 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 15 | 24220 | 1680 | 0.06936 | 0.00061932 | 100 | 11200 | 2009/2010 | October-2009 | 10 | 2009
22400 | Faulty Tx558 (trees) - Waiapa Road | 2009-10-17 17:55 | 2009-10-17 | 2009-10-20 11:41 | Calculated | 254 | 254 - Fused Link 254 |  | 107SEG254 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3946 | 2 | 24220 | 7892 | 0.32585 | 8.2576e-05 | 10 | 39460 | 2009/2010 | October-2009 | 10 | 2009
22403 | Lightning - Okaihae Road | 2009-10-17 18:00 | 2009-10-17 | 2009-10-17 19:15 | Calculated | 07I34 | 07I34 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5781 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 24220 | 75 | 0.0031 | 4.1288e-05 | 15 | 1125 | 2009/2010 | October-2009 | 10 | 2009
22401 | Fault Zone Extended - Gadsby Road | 2009-10-17 18:37 | 2009-10-17 | 2009-10-17 18:49 | Calculated | 512 | 512 - Circuit Breaker Gadsby Rd 11 kV Feeder512 |  | No Segment | 205-01 Gadsby Road | Urban A | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 912 | 24220 | 10944 | 0.45186 | 0.037655 | 6175 | 74099 | 2009/2010 | October-2009 | 10 | 2009
22402 | Fault Zone Extended - Te Kumi Road | 2009-10-17 18:37 | 2009-10-17 | 2009-10-17 18:57 | Calculated | 1020 | 1020 - Circuit Breaker with Bypass & Links 1020 |  | 107SEG233-1020 | Oparure 107-03 | Rural C | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 269 | 24220 | 5380 | 0.22213 | 0.011107 | 2195 | 43899 | 2009/2010 | October-2009 | 10 | 2009
22404 | Branch on Line - Waipapa Road | 2009-10-17 19:39 | 2009-10-17 | 2009-10-17 19:56 | Calculated | T1014 | T1014 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG250-254 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 1 | 24220 | 17 | 0.0007 | 4.1288e-05 | 10 | 170 | 2009/2010 | October-2009 | 10 | 2009
22408 | Broken DDO - Marsack Road | 2009-10-18 14:05 | 2009-10-18 | 2009-10-18 15:04 | Calculated | 08J25 | 08J25 - 3ph 30kVA POLEMNT |  | 404SEG5915-5838 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 4 | 24220 | 236 | 0.00974 | 0.00016515 | 30 | 1770 | 2009/2010 | October-2009 | 10 | 2009
22409 | Unknown - Kaitieke Road | 2009-10-18 20:36 | 2009-10-18 | 2009-10-18 21:45 | Calculated | 13K15 | 13K15 - 2ph 15kVA POLEMNT |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24220 | 69 | 0.00285 | 4.1288e-05 | 15 | 1035 | 2009/2010 | October-2009 | 10 | 2009
22410 | Replace Red Tagged LV Pole - Maihihi Road | 2009-10-19 10:03 | 2009-10-19 | 2009-10-19 14:37 | Calculated | T277 | T277 - 1 Phase : 25.00 kVA : POLEMNT |  | 111SEG351-647 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 274 | 8 | 24220 | 2192 | 0.0905 | 0.00033031 | 25 | 6850 | 2009/2010 | October-2009 | 10 | 2009
22411 | Unknown - Taringamotu Road | 2009-10-19 17:50 | 2009-10-19 | 2009-10-19 19:18 | Calculated | 07I43 | 07I43 - 2 Phase : 15.00 kVA : POLEMNT |  | 402SEG5707 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 1 | 24220 | 88 | 0.00363 | 4.1288e-05 | 15 | 1320 | 2009/2010 | October-2009 | 10 | 2009
22414 | Fuse Pulled Apart - Erua Road | 2009-10-20 10:30 | 2009-10-20 | 2009-10-20 11:44 | Calculated | 16J01 | 16J01 - 1 Phase : 3.00 kVA : POLEMNT |  | 410SEG5631 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 2 | 24220 | 148 | 0.00611 | 8.2576e-05 | 3 | 222 | 2009/2010 | October-2009 | 10 | 2009
22422 | Replace Pole 36/10 Live Line - Honikiwi Road | 2009-10-22 09:03 | 2009-10-22 | 2009-10-22 13:13 | Calculated | 209 | 209 - Fused Link 209 |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 50 | 24220 | 12500 | 0.5161 | 0.0020644 | 530 | 132500 | 2009/2010 | October-2009 | 10 | 2009
22423 | Replace Pole 36/10 Live Line - Redlands Road | 2009-10-22 09:03 | 2009-10-22 | 2009-10-22 13:13 | Calculated | T2499 | T2499 - 1 Phase : 15.00 kVA : POLEMNT |  | 112SEG317-209 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 2 | 24220 | 500 | 0.02064 | 8.2576e-05 | 15 | 3750 | 2009/2010 | October-2009 | 10 | 2009
22425 | Magpie - Turakina Valley Road | 2009-10-22 16:40 | 2009-10-22 | 2009-10-22 17:31 | Calculated | 22O07 | 22O07 - 5689-5691ph 10kVA POLEMNT |  | 416SEG5689-5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 1 | 24220 | 51 | 0.00211 | 4.1288e-05 | 10 | 510 | 2009/2010 | October-2009 | 10 | 2009
22426 | Wind - Okau E/W Sub | 2009-10-22 21:40 | 2009-10-22 | 2009-10-22 23:31 | Calculated | 1630 | 1630 - Recloser 1630 |  | No Segment | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 46 | 24220 | 5106 | 0.21082 | 0.0018993 | 315.5 | 35020 | 2009/2010 | October-2009 | 10 | 2009
22429 | Replace Poles 109/12 & 13 | 2009-10-23 10:04 | 2009-10-23 | 2009-10-23 14:32 | Calculated | 5355 | 5355 - Sectionaliser with Bypass & Links 5355 |  | 421SEG5355-5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 268 | 17 | 24220 | 4556 | 0.18811 | 0.0007019 | 120 | 32160 | 2009/2010 | October-2009 | 10 | 2009
22431 | Lower 2 Taps - Paraheka Valley Road | 2009-10-23 13:35 | 2009-10-23 | 2009-10-23 13:50 | Calculated | T2836 | T2836 - 1 Phase : 15.00 kVA : POLEMNT |  | 114SEG1128 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 1 | 24220 | 15 | 0.00062 | 4.1288e-05 | 15 | 225 | 2009/2010 | October-2009 | 10 | 2009
22432 | Fuse Pulled Apart - Kowhai Road | 2009-10-23 19:18 | 2009-10-23 | 2009-10-23 20:48 | Calculated | T4180 | T4180 - 1 Phase : 15.00 kVA : POLEMNT |  | 406SEG5957RET | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 1 | 24220 | 90 | 0.00372 | 4.1288e-05 | 15 | 1350 | 2009/2010 | October-2009 | 10 | 2009
22437 | Fuse Pulled Apart - Pihanga Road | 2009-10-26 06:00 | 2009-10-26 | 2009-10-26 06:48 | Calculated | 10S48 | 10S48 - 3 Phase : 300.00 kVA : GNDPAD |  | 424SEG5200-5168RET | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 3 | 24220 | 144 | 0.00595 | 0.00012386 | 300 | 14400 | 2009/2010 | October-2009 | 10 | 2009
22438 | Unknown - Ngapuke Sub | 2009-10-27 07:20 | 2009-10-27 | 2009-10-27 07:58 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 74 | 24220 | 2812 | 0.1161 | 0.0030553 | 493 | 18733 | 2009/2010 | October-2009 | 10 | 2009
22439 | Otorohanga Feeder Renewal Project | 2009-10-27 09:02 | 2009-10-27 | 2009-10-27 14:46 | Calculated | 771 | 771 - Fused Link 771 |  | 112SEG771 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 344 | 11 | 24220 | 3784 | 0.15623 | 0.00045417 | 60 | 20640 | 2009/2010 | October-2009 | 10 | 2009
22440 | Connect 2 Pole Extension to Te Kuiti Gun Club | 2009-10-27 09:05 | 2009-10-27 | 2009-10-27 10:14 | Calculated | 248 | 248 - Fused Link 248 |  | 101SEG248 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 69 | 12 | 24220 | 828 | 0.03419 | 0.00049546 | 60 | 4140 | 2009/2010 | October-2009 | 10 | 2009
22441 | Unknown - Okahukura Back Road | 2009-10-27 10:00 | 2009-10-27 | 2009-10-27 11:40 | Calculated | 5345 | 5345 - Fused Link 5345 |  | 402SEG5345 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 6 | 24220 | 600 | 0.02477 | 0.00024773 | 30 | 3000 | 2009/2010 | October-2009 | 10 | 2009
22442 | Magpie - SH40 Mokau | 2009-10-27 10:10 | 2009-10-27 | 2009-10-27 11:49 | Calculated | T2212 | T2212 - 1 Phase : 3.00 kVA : POLEMNT |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 2 | 24220 | 198 | 0.00818 | 8.2576e-05 | 3 | 297 | 2009/2010 | October-2009 | 10 | 2009
22446 | Line Down - Borough Sub | 2009-10-28 12:05 | 2009-10-28 | 2009-10-28 12:32 | Calculated | 5955 | 5955 - Circuit Breaker Northern 5955 |  | No Segment | 508-01 Borough | Rural B | Northern | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 1235 | 24220 | 33345 | 1.3767 | 0.050991 | 7736.5 | 208885 | 2009/2010 | October-2009 | 10 | 2009
22447 | Line Down - Golf Road | 2009-10-28 12:05 | 2009-10-28 | 2009-10-28 13:45 | Calculated | 4.5 | 4.5 - Air Break Switch 4.5 |  | 402SEGA4.5-A4.6 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 414 | 24220 | 41400 | 1.7093 | 0.017093 | 1910 | 190999 | 2009/2010 | October-2009 | 10 | 2009
22449 | Broken DDO @ T221 - Te Raumauku Road | 2009-10-28 19:46 | 2009-10-28 | 2009-10-28 21:23 | Calculated | 355 | 355 - Fused Link 355 |  | 112SEG355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Protection | FAIL:FPRO |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 9 | 24220 | 873 | 0.03604 | 0.00037159 | 95 | 9214 | 2009/2010 | October-2009 | 10 | 2009
22450 | Replace "H" Tower Xarms on Pole 72 & Change Xarms @ T2009 | 2009-10-29 08:34 | 2009-10-29 | 2009-10-29 16:13 | Calculated | 1716 | 1716 - Recloser with Bypass1716 |  | 115SEG1716-1719 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 319 | 166 | 24220 | 12241 | 0.50541 | 0.0068538 | 1165.5 | 77716 | 2009/2010 | October-2009 | 10 | 2009
22451 | Change Tx - Omori Road | 2009-10-29 09:23 | 2009-10-29 | 2009-10-29 10:29 | Calculated | T4279 | T4279 - 1 Phase : 15.00 kVA : GNDPAD |  | 406SEG6353-5616 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24220 |  | 0 | 0 |  |  | 2009/2010 | October-2009 | 10 | 2009
22454 | Lift Iced Up - BDS to Jumbo T Bar 17N05 | 2009-10-30 14:00 | 2009-10-30 | 2009-10-30 14:16 | Calculated | 6148 | 6148 - Circuit Breaker 6148 |  | 415SEG6598RET | Turoa 415-03 | Rural B | Turoa | Direct from Ohakune Supply |  | Weather |  | WEAT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24220 |  | 0 | 0 |  |  | 2009/2010 | October-2009 | 10 | 2009
22456 | Burnt Fuse Carrier - Frethey Drive | 2009-10-30 14:05 | 2009-10-30 | 2009-10-30 15:00 | Calculated | 10T05 | 10T05 - 1 Phase : 50.00 kVA : POLEMNT |  | 424SEG5942 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 24220 | 55 | 0.00227 | 4.1288e-05 | 50 | 2750 | 2009/2010 | October-2009 | 10 | 2009
22455 | Lift Iced Up - BDS to Jumbo T Bar 17N05 | 2009-10-30 14:30 | 2009-10-30 | 2009-10-30 14:46 | Calculated | 6148 | 6148 - Circuit Breaker 6148 |  | 415SEG6598RET | Turoa 415-03 | Rural B | Turoa | Direct from Ohakune Supply |  | Weather |  | WEAT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24220 |  | 0 | 0 |  |  | 2009/2010 | October-2009 | 10 | 2009
22457 | Faulty Tx - Mahoe Road | 2009-11-01 18:45 | 2009-11-01 | 2009-11-01 21:50 | Calculated | 08K13 | 08K13 - 3ph 50kVA POLEMNT |  | 408SEG5116-5816 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 9 | 24280 | 1665 | 0.06857 | 0.00037068 | 50 | 9249 | 2009/2010 | November-2009 | 11 | 2009
22458 | Upgrade Earthing - Kururau Road | 2009-11-02 10:51 | 2009-11-02 | 2009-11-02 12:40 | Calculated | 08F01 | 08F01 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 109 | 7 | 24280 | 763 | 0.03143 | 0.0002883 | 15 | 1634 | 2009/2010 | November-2009 | 11 | 2009
22459 | Birds - Waitepipi Road | 2009-11-02 12:20 | 2009-11-02 | 2009-11-02 14:39 | Calculated | T126 | T126 - 3ph 30kVA POLEMNT |  | 107SEG258 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 4 | 24280 | 556 | 0.0229 | 0.00016474 | 30 | 4170 | 2009/2010 | November-2009 | 11 | 2009
22463 | Fuse Pulled Apart - Henderson Street | 2009-11-03 17:45 | 2009-11-03 | 2009-11-03 18:20 | Calculated | T656 | T656 - 3 Phase : 150.00 kVA : POLEMNT |  | 104SEG216 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 30 | 24280 | 1050 | 0.04325 | 0.0012356 | 150 | 5250 | 2009/2010 | November-2009 | 11 | 2009
22465 | Coast Feeder Renewal Project | 2009-11-04 08:47 | 2009-11-04 | 2009-11-04 08:49 | Calculated | T542 | T542 - 3 Phase : 30.00 kVA : POLEMNT |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 120 | 24280 | 31172 | 1.2839 | 0.0049423 | 958.5 | 252166 | 2009/2010 | November-2009 | 11 | 2009
22464 | Remove Ground Stay - Esplanade | 2009-11-04 09:31 | 2009-11-04 | 2009-11-04 09:49 | Calculated | T3301 | T3301 - 3 Phase : 100.00 kVA : GNDPAD |  | 108SEG181-219 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24280 |  | 0 | 0 |  |  | 2009/2010 | November-2009 | 11 | 2009
22467 | Duck - Nagahape Road | 2009-11-05 03:55 | 2009-11-05 | 2009-11-05 04:48 | Calculated | 359 | 359 - Fused Link 359 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 20 | 24280 | 1060 | 0.04366 | 0.00082372 | 235 | 12454 | 2009/2010 | November-2009 | 11 | 2009
22468 | Coast Feeder Renewal Project | 2009-11-05 08:44 | 2009-11-05 | 2009-11-05 09:00 | Calculated | T542 | T542 - 3 Phase : 30.00 kVA : POLEMNT |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 6 | 24280 | 96 | 0.00395 | 0.00024712 | 30 | 480 | 2009/2010 | November-2009 | 11 | 2009
22469 | Tree Cutting - Maihihi | 2009-11-05 09:35 | 2009-11-05 | 2009-11-05 12:43 | Calculated | 638 | 638 - Fused Link 638 |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 188 | 26 | 24280 | 4888 | 0.20132 | 0.0010708 | 240 | 45119 | 2009/2010 | November-2009 | 11 | 2009
22471 | Unknown - Raukura St North | 2009-11-05 10:15 | 2009-11-05 | 2009-11-05 11:23 | Calculated | 11S26 | 11S26 - 3 Phase : 200.00 kVA : GNDPAD |  | 424SEG5200-5168RET | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 68 | 67 | 24280 | 4556 | 0.18764 | 0.0027595 | 200 | 13599 | 2009/2010 | November-2009 | 11 | 2009
22473 | Unknown - Matiere Road | 2009-11-05 15:20 | 2009-11-05 | 2009-11-05 16:24 | Calculated | T2481 | T2481 - 3ph 15kVA POLEMNT |  | 114SEG1107-1116 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 1 | 24280 | 64 | 0.00264 | 4.1186e-05 | 15 | 960 | 2009/2010 | November-2009 | 11 | 2009
22474 | Wairere Ran As Island? - Waitete | 2009-11-05 21:44 | 2009-11-05 | 2009-11-05 21:53 | Calculated | 754 | 754 - Circuit Breaker 754 |  | No Segment | 206-01 Waitete | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Asset Related | Overload | FAIL:OOVL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24280 |  | 0 | 0 |  |  | 2009/2010 | November-2009 | 11 | 2009
22475 | Wairere Ran As Island? - Gadsby Road | 2009-11-05 21:44 | 2009-11-05 | 2009-11-05 21:54 | Calculated | 594 | 594 - Circuit Breaker 594 |  | No Segment | 205-01 Gadsby Road | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Asset Related | Overload | FAIL:OOVL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 2015 | 24280 | 20150 | 0.8299 | 0.08299 | 13837 | 138370 | 2009/2010 | November-2009 | 11 | 2009
22476 | Rat - Mangarino Road | 2009-11-06 05:20 | 2009-11-06 | 2009-11-06 07:22 | Calculated | T2367 | T2367 - 1 Phase : 10.00 kVA : POLEMNT |  | 106SEG224-361 | Rangitoto 106-07 | Rural C | Rangitoto | Waitete Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AOTH | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 1 | 24280 | 122 | 0.00502 | 4.1186e-05 | 10 | 1220 | 2009/2010 | November-2009 | 11 | 2009
22478 | Replace Pole 49/66/27/4 - Bulldozer Access Only | 2009-11-06 10:30 | 2009-11-06 | 2009-11-06 13:07 | Calculated | 1125 | 1125 - Fused Link 1125 |  | 114SEG1125-2160 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 157 | 16 | 24280 | 2512 | 0.10346 | 0.00065898 | 108 | 16955 | 2009/2010 | November-2009 | 11 | 2009
22479 | Unknown - Borough Sub | 2009-11-07 10:08 | 2009-11-07 | 2009-11-07 10:18 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24280 |  | 0 | 0 |  |  | 2009/2010 | November-2009 | 11 | 2009
22481 | Install Stays & Fit Private Line Links to Pole 261/9 | 2009-11-09 10:10 | 2009-11-09 | 2009-11-09 13:41 | Calculated | 5687 | 5687 - Fused Link 5687 |  | 416SEG5687 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 211 | 4 | 24280 | 844 | 0.03476 | 0.00016474 | 25 | 5275 | 2009/2010 | November-2009 | 11 | 2009
22482 | Waihaha Feeder Renwal Project | 2009-11-10 08:36 | 2009-11-10 | 2009-11-10 15:27 | Calculated | 5409 | 5409 - Recloser with Bypass 5409 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 391 | 47 | 24280 | 12444 | 0.51252 | 0.0019357 | 367.5 | 103354 | 2009/2010 | November-2009 | 11 | 2009
22483 | Replace DDO's Live Line - Main North Road | 2009-11-10 09:32 | 2009-11-10 | 2009-11-10 11:54 | Calculated | T471 | T471 - 3ph 200kVA gndpad |  | 111SEG306-322 | Maihiihi 111-02 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 142 | 29 | 24280 | 4118 | 0.1696 | 0.0011944 | 200 | 28399 | 2009/2010 | November-2009 | 11 | 2009
22486 | Possum @ T1673 - Kuratahi Street | 2009-11-11 02:00 | 2009-11-11 | 2009-11-11 03:30 | Calculated | 655 | 655 - Fused Link 655 |  | 116SEG655 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 2 | 24280 | 180 | 0.00741 | 8.2372e-05 | 65 | 5850 | 2009/2010 | November-2009 | 11 | 2009
22484 | Waihaha Feeder Renewal Project | 2009-11-11 08:55 | 2009-11-11 | 2009-11-11 15:28 | Calculated | 5324 | 5324 - Fused Link 5324 |  | 426SEG5324RET | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 0 | 0 | 24280 |  | 0 | 0 |  |  | 2009/2010 | November-2009 | 11 | 2009
22485 | Unknown - SH3 Arapae Spur | 2009-11-11 13:50 | 2009-11-11 | 2009-11-11 14:30 | Calculated | 1317 | 1317 - Fused Link 1317 |  | 117SEG1317 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 8 | 24280 | 320 | 0.01318 | 0.00032949 | 70 | 2799 | 2009/2010 | November-2009 | 11 | 2009
22488 | Change Tx Pole - SH49 | 2009-11-12 10:00 | 2009-11-12 | 2009-11-12 14:24 | Calculated | 21N14 | 21N14 - 5683-5523ph 50kVA POLEMNT |  | 416SEG5683-5523 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 5 | 24280 | 1320 | 0.05437 | 0.00020593 | 50 | 13200 | 2009/2010 | November-2009 | 11 | 2009
22489 | Replace Stay - Puratoke Rise | 2009-11-13 11:05 | 2009-11-13 | 2009-11-13 12:10 | Calculated | 09R30 | 09R30 - 1 Phase : 30.00 kVA : POLEMNT |  | 406SEG5896 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 65 | 7 | 24280 | 455 | 0.01874 | 0.0002883 | 30 | 1949 | 2009/2010 | November-2009 | 11 | 2009
22493 | Unknown - Whareroa Sub | 2009-11-14 10:30 | 2009-11-14 | 2009-11-14 11:40 | Calculated | 5619 | 5619 - Fused Link 5619 |  | 426SEGT07Q14-5268 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 81 | 24280 | 5670 | 0.23353 | 0.0033361 | 527.5 | 36924 | 2009/2010 | November-2009 | 11 | 2009
22494 | Unknown - Harpers Ave | 2009-11-14 21:25 | 2009-11-14 | 2009-11-14 23:50 | Calculated | 663 | 663 - Fused Link 663 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 6 | 24280 | 870 | 0.03583 | 0.00024712 | 90 | 13050 | 2009/2010 | November-2009 | 11 | 2009
22495 | Magpie - Kuratau | 2009-11-16 07:27 | 2009-11-16 | 2009-11-16 09:32 | Calculated | 5892 | 5892 - Earth Working Link 5892 |  | 426SEG5892-5240 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 34 | 24280 | 4250 | 0.17504 | 0.0014003 | 182.5 | 22812 | 2009/2010 | November-2009 | 11 | 2009
22496 | Wind - Pioi Station | 2009-11-16 10:00 | 2009-11-16 | 2009-11-16 12:30 | Calculated | 1617 | 1617 - Fused Link 1617 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 2 | 24280 | 300 | 0.01236 | 8.2372e-05 | 30 | 4500 | 2009/2010 | November-2009 | 11 | 2009
22497 | Deviate Line - Tongaporutu E/W Sub | 2009-11-16 10:30 | 2009-11-16 | 2009-11-16 15:16 | Calculated | 1638 | 1638 - Fused Link 1638 |  | 128SEG1638 | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 286 | 5 | 24280 | 1430 | 0.0589 | 0.00020593 | 45 | 12870 | 2009/2010 | November-2009 | 11 | 2009
22498 | Unknown - Ruatiti Sub | 2009-11-16 17:24 | 2009-11-16 | 2009-11-16 19:05 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | 410SEG5806-5793 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 69 | 24280 | 6969 | 0.28703 | 0.0028418 | 426.5 | 43076 | 2009/2010 | November-2009 | 11 | 2009
22499 | Lightning - Oio Road | 2009-11-16 19:30 | 2009-11-16 | 2009-11-16 21:30 | Calculated | 13I01 | 13I01 - 1 Phase : 15.00 kVA : POLEMNT |  | 410SEG5495-5499 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 2 | 24280 | 240 | 0.00988 | 8.2372e-05 | 15 | 1800 | 2009/2010 | November-2009 | 11 | 2009
22500 | Otorohanga Feeder Renewal Project | 2009-11-17 09:10 | 2009-11-17 | 2009-11-17 13:51 | Calculated | 771 | 771 - Fused Link 771 |  | 112SEG771 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 11 | 24280 | 3091 | 0.12731 | 0.00045305 | 60 | 16860 | 2009/2010 | November-2009 | 11 | 2009
22505 | Wind - Pao Road | 2009-11-17 20:00 | 2009-11-17 | 2009-11-17 22:30 | Calculated | T1986 | T1986 - 1 Phase : 15.00 kVA : POLEMNT |  | 114SEG1119 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 2 | 24280 | 300 | 0.01236 | 8.2372e-05 | 15 | 2250 | 2009/2010 | November-2009 | 11 | 2009
22506 | Wind - Ngakonui Road | 2009-11-17 20:25 | 2009-11-17 | 2009-11-17 21:24 | Calculated | 5354 | 5354 - Fused Link 5354 |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 8 | 24280 | 472 | 0.01944 | 0.00032949 | 67.5 | 3982 | 2009/2010 | November-2009 | 11 | 2009
22512 | Line Down (Wind) - Okau | 2009-11-18 07:39 | 2009-11-18 | 2009-11-18 14:09 | Calculated | 1641 | 1641 - Sectionaliser with Bypass & Links 1641 |  | 128SEGT2208-1645 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 390 | 11 | 24280 | 4290 | 0.17669 | 0.00045305 | 82.5 | 32175 | 2009/2010 | November-2009 | 11 | 2009
22513 | Faulty Insulator on Bypass - Maraetai | 2009-11-18 09:53 | 2009-11-18 | 2009-11-18 09:56 | Calculated | 1622 | 1622 - Circuit Breaker with Bypass & Links 1622 |  | 310SEG1622-62 | 211-01 Arohena | Rural D | Whakamaru 33 | Direct from Whakamaru Supply |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 502 | 24280 | 1506 | 0.06203 | 0.020675 | 4677 | 14030 | 2009/2010 | November-2009 | 11 | 2009
22514 | Faulty Insulator on Bypass - Arohena | 2009-11-18 10:19 | 2009-11-18 | 2009-11-18 10:22 | Calculated | 1052 | 1052 - Circuit Breaker 1052 Wharepapa |  | 122SEG1052-524 | 211-01 Arohena | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 351 | 24280 | 1053 | 0.04337 | 0.014456 | 3103 | 9308 | 2009/2010 | November-2009 | 11 | 2009
22515 | Faulty Insulator on Bypass - Arohena | 2009-11-18 10:19 | 2009-11-18 | 2009-11-18 10:52 | Calculated | 1072 | 1072 - Circuit Breaker 1072 Huirimu |  | 121SEG1072-753 | 211-01 Arohena | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 151 | 24280 | 4983 | 0.20523 | 0.0062191 | 1574 | 51941 | 2009/2010 | November-2009 | 11 | 2009
22516 | Scheduled Maintenance - Tirohanga Road | 2009-11-18 10:24 | 2009-11-18 | 2009-11-18 11:50 | Calculated | T3103 | T3103 - 3 Phase : 100.00 kVA : POLEMNT |  | 123SEG1751-765RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 86 | 1 | 24280 | 86 | 0.00354 | 4.1186e-05 | 100 | 8600 | 2009/2010 | November-2009 | 11 | 2009
22517 | Tree Through Lines - Turaki Street | 2009-11-18 15:32 | 2009-11-18 | 2009-11-18 15:49 | Calculated | 5166 | 5166 - Solid Link 5166 |  | 404SEG5166-A1.13 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 669 | 24280 | 11373 | 0.46841 | 0.027554 | 3000 | 50999 | 2009/2010 | November-2009 | 11 | 2009
22519 | Magpie - Piawa Road | 2009-11-19 08:30 | 2009-11-19 | 2009-11-19 10:38 | Calculated | 06J17 | 06J17 - 1 Phase : 7.50 kVA : POLEMNT |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 1 | 24280 | 128 | 0.00527 | 4.1186e-05 | 7.5 | 960 | 2009/2010 | November-2009 | 11 | 2009
22520 | Fit New Links 823 Live Line & Replace Red Tagged Pole | 2009-11-19 09:37 | 2009-11-19 | 2009-11-19 12:48 | Calculated | T102 | T102 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 191 | 7 | 24280 | 1589 | 0.06544 | 0.0002883 | 80 | 16540 | 2009/2010 | November-2009 | 11 | 2009
22524 | Replace Pole For New Extension to T4286 | 2009-11-20 10:00 | 2009-11-20 | 2009-11-20 14:39 | Calculated | 5403 | 5403 - Air Break Switch 5403 |  | 409SEG5403-5662RET | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24280 |  | 0 | 0 |  |  | 2009/2010 | November-2009 | 11 | 2009
22523 | Replace Poles 165/15 & 17 | 2009-11-20 10:07 | 2009-11-20 | 2009-11-20 14:54 | Calculated | 648 | 648 - Fused Link 648 |  | 111SEG648 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 287 | 8 | 24280 | 2296 | 0.09456 | 0.00032949 | 70 | 20090 | 2009/2010 | November-2009 | 11 | 2009
22527 | Magpie - Taumaranui Street | 2009-11-21 06:45 | 2009-11-21 | 2009-11-21 07:51 | Calculated | 01A58 | 01A58 - 3 Phase : 100.00 kVA : GNDPAD |  | 404SEGF1.36 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 42 | 24280 | 2772 | 0.11417 | 0.0017298 | 100 | 6599 | 2009/2010 | November-2009 | 11 | 2009
22528 | Unknown - Hangatiki | 2009-11-23 02:19 | 2009-11-23 | 2009-11-23 02:20 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24280 |  | 0 | 0 |  |  | 2009/2010 | November-2009 | 11 | 2009
22529 | Morepork - Waitete Road | 2009-11-23 06:30 | 2009-11-23 | 2009-11-23 07:48 | Calculated | T1488 | T1488 - 1 Phase : 30.00 kVA : POLEMNT |  | 103SEG236-731 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24280 | 156 | 0.00643 | 8.2372e-05 | 30 | 2340 | 2009/2010 | November-2009 | 11 | 2009
22530 | Possum - Main Sth Rd Piopio | 2009-11-23 08:00 | 2009-11-23 | 2009-11-23 15:06 | Calculated | T1710 | T1710 - 3ph 30kVA POLEMNT |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 426 | 2 | 24280 | 852 | 0.03509 | 8.2372e-05 | 30 | 12780 | 2009/2010 | November-2009 | 11 | 2009
22532 | Tangiwai Feeder Renewal Project | 2009-11-23 09:46 | 2009-11-23 | 2009-11-23 14:47 | Calculated | 5796 | 5796 - Air Break Switch 5796 |  | 416SEG5554-5711 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 274 | 12 | 24280 | 3288 | 0.13542 | 0.00049423 | 95 | 26030 | 2009/2010 | November-2009 | 11 | 2009
22535 | Fuse Pulled Apart - Pihanga Road | 2009-11-24 05:20 | 2009-11-24 | 2009-11-24 06:30 | Calculated | 10S48 | 10S48 - 3 Phase : 300.00 kVA : GNDPAD |  | 424SEG5200-5168RET | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 3 | 24280 | 210 | 0.00865 | 0.00012356 | 300 | 21000 | 2009/2010 | November-2009 | 11 | 2009
22536 | Possum - Main Sth Rd Piopio | 2009-11-24 08:10 | 2009-11-24 | 2009-11-24 10:19 | Calculated | T1715 | T1715 - 1 Phase : 15.00 kVA : POLEMNT |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 4 | 24280 | 516 | 0.02125 | 0.00016474 | 15 | 1935 | 2009/2010 | November-2009 | 11 | 2009
22537 | Unknown - Waitea Road | 2009-11-24 08:40 | 2009-11-24 | 2009-11-24 10:03 | Calculated | 09K51 | 09K51 - 3 Phase : 30.00 kVA : POLEMNT |  | 409SEG5332 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 1 | 24280 | 83 | 0.00342 | 4.1186e-05 | 30 | 2490 | 2009/2010 | November-2009 | 11 | 2009
22538 | Re-Sag Conductor | 2009-11-24 10:01 | 2009-11-24 | 2009-11-24 11:03 | Calculated | 5961 | 5961 - Recloser with Bypass 5961 |  | 416SEG5961-5683 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 100 | 24280 | 4952 | 0.20395 | 0.0041186 | 6779.5 | 362267 | 2009/2010 | November-2009 | 11 | 2009
22539 | Replace Red Tagged Pole 119/105/66/33 | 2009-11-24 10:49 | 2009-11-24 | 2009-11-24 14:30 | Calculated | 421 | 421 - Air Break Switch 421 |  | 121SEG421-424 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 221 | 50 | 24280 | 11050 | 0.45511 | 0.0020593 | 429 | 94808 | 2009/2010 | November-2009 | 11 | 2009
22540 | Jumper Off @ Pole 28 - Ahuroa Road | 2009-11-24 10:57 | 2009-11-24 | 2009-11-24 11:22 | Calculated | 586 | 586 - Air Break Switch 586 |  | 106SEG227-586 | Rangitoto 106-02 | Urban A | Rangitoto | Waitete Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 264 | 24280 | 6600 | 0.27183 | 0.010873 | 2047 | 51174 | 2009/2010 | November-2009 | 11 | 2009
22541 | Tangiwai Feeder Renewal Project | 2009-11-25 09:04 | 2009-11-25 | 2009-11-25 09:05 | Calculated | 5796 | 5796 - Air Break Switch 5796 |  | 416SEG5554-5711 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 1 | 24280 | 305 | 0.01256 | 4.1186e-05 | 6175 | 6175 | 2009/2010 | November-2009 | 11 | 2009
22542 | Isolate Section of 11kV Line for Crane Work | 2009-11-26 08:25 | 2009-11-26 | 2009-11-26 17:20 | Calculated | 766 | 766 - Solid Links 766 |  | No Segment | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 475 | 110 | 24280 | 52250 | 2.152 | 0.0045305 | 851 | 404224 | 2009/2010 | November-2009 | 11 | 2009
22543 | Install New Pole For New SWER Sub | 2009-11-26 10:05 | 2009-11-26 | 2009-11-26 13:25 | Calculated | 5957 | 5957 - Fused Link 5957 |  | 406SEG5957RET | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 200 | 16 | 24280 | 3200 | 0.1318 | 0.00065898 | 105 | 21000 | 2009/2010 | November-2009 | 11 | 2009
22544 | Coast Feeder Renewal Project | 2009-11-26 10:31 | 2009-11-26 | 2009-11-26 15:12 | Calculated | 280 | 280 - Fused Link 280 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 12 | 24280 | 3372 | 0.13888 | 0.00049423 | 113 | 31752 | 2009/2010 | November-2009 | 11 | 2009
22547 | Upgrade Earthing - Kururau Road | 2009-11-26 11:14 | 2009-11-26 | 2009-11-26 12:17 | Calculated | 08G01 | 08G01 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 2 | 24280 | 126 | 0.00519 | 8.2372e-05 | 15 | 945 | 2009/2010 | November-2009 | 11 | 2009
22548 | Unknown - Hautu Village | 2009-11-26 11:55 | 2009-11-26 | 2009-11-26 13:20 | Calculated | 5524 | 5524 - Sectionaliser 5524 |  | No Segment | No Asset Group | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 6 | 24280 | 510 | 0.021 | 0.00024712 | 50 | 4250 | 2009/2010 | November-2009 | 11 | 2009
22549 | Wind - Matiere/Aria Road | 2009-11-26 13:03 | 2009-11-26 | 2009-11-26 15:18 | Calculated | 05F04 | 05F04 - 1 Phase : 25.00 kVA : POLEMNT |  | 422SEG5618-5272 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 5 | 24280 | 675 | 0.0278 | 0.00020593 | 25 | 3375 | 2009/2010 | November-2009 | 11 | 2009
22550 | Wind - Main North Road | 2009-11-26 16:00 | 2009-11-26 | 2009-11-26 16:16 | Calculated | 07I30 | 07I30 - 2 Phase : 50.00 kVA : POLEMNT |  | 402SEG5480 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 8 | 24280 | 128 | 0.00527 | 0.00032949 | 50 | 800 | 2009/2010 | November-2009 | 11 | 2009
22551 | Wind - Hangatiki | 2009-11-26 20:22 | 2009-11-26 | 2009-11-26 20:24 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24280 |  | 0 | 0 |  |  | 2009/2010 | November-2009 | 11 | 2009
22552 | Fuse Pulled Apart - Ngakonui Road | 2009-11-27 07:45 | 2009-11-27 | 2009-11-27 08:05 | Calculated | 06J02 | 06J02 - 3 Phase : 50.00 kVA : POLEMNT |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 10 | 24280 | 200 | 0.00824 | 0.00041186 | 50 | 1000 | 2009/2010 | November-2009 | 11 | 2009
22554 | Replace & Re-Dig Pole 1/129 | 2009-11-27 10:02 | 2009-11-27 | 2009-11-27 12:26 | Calculated | 349 | 349 - Air Break Switch 349 |  | 109SEG348-522 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 40 | 24280 | 4080 | 0.16804 | 0.0016474 | 340 | 34679 | 2009/2010 | November-2009 | 11 | 2009
22556 | Connect Deep Driven Earth - Karangahape Road | 2009-11-27 10:52 | 2009-11-27 | 2009-11-27 11:17 | Calculated | 06S01 | 06S01 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 1 | 24280 | 25 | 0.00103 | 4.1186e-05 | 15 | 375 | 2009/2010 | November-2009 | 11 | 2009
22559 | Unknown - Okahukura Back Road | 2009-11-27 14:45 | 2009-11-27 | 2009-11-27 15:32 | Calculated | 07I33 | 07I33 - 1 Phase : 3.00 kVA : POLEMNT |  | 402SEG5112-5336 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 1 | 24280 | 47 | 0.00194 | 4.1186e-05 | 3 | 141 | 2009/2010 | November-2009 | 11 | 2009
22560 | Unknown - Western Bay Road | 2009-11-28 07:00 | 2009-11-28 | 2009-11-28 09:08 | Calculated | T2680 | T2680 - 3 Phase : 50.00 kVA : POLEMNT |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 1 | 24280 | 128 | 0.00527 | 4.1186e-05 | 50 | 6400 | 2009/2010 | November-2009 | 11 | 2009
22561 | Fuse Pulled Apart - Gradara Ave | 2009-11-29 06:46 | 2009-11-29 | 2009-11-29 08:01 | Calculated | T352 | T352 - 3ph 200kVA GNDPAD |  | 112SEG353-391 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 19 | 24280 | 1425 | 0.05869 | 0.00078254 | 200 | 14999 | 2009/2010 | November-2009 | 11 | 2009
22566 | Jumper Off @ T2748 - Tongaporutu | 2009-11-30 20:46 | 2009-11-30 | 2009-11-30 21:40 | Calculated | 1637 | 1637 - Fused Link 1637 |  | 128SEG1637 | Mokau 128-09 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 4 | 24280 | 216 | 0.0089 | 0.00016474 | 35 | 1890 | 2009/2010 | November-2009 | 11 | 2009
22567 | Magpie - Makomiko Road | 2009-12-01 11:05 | 2009-12-01 | 2009-12-01 13:34 | Calculated | T4056 | T4056 - 3 Phase : 5.00 kVA : POLEMNT |  | 409SEG5867-5135 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 1 | 24292 | 149 | 0.00613 | 4.1166e-05 | 5 | 745 | 2009/2010 | December-2009 | 12 | 2009
22568 | Unknown - Paerata Road | 2009-12-01 11:10 | 2009-12-01 | 2009-12-01 14:57 | Calculated | T2572 | T2572 - 3 Phase : 30.00 kVA : POLEMNT |  | 129SEG402-725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 227 | 1 | 24292 | 227 | 0.00934 | 4.1166e-05 | 30 | 6810 | 2009/2010 | December-2009 | 12 | 2009
22571 | Replace Xarm & Install Private Line Link @ 03k02 | 2009-12-02 09:04 | 2009-12-02 | 2009-12-02 12:13 | Calculated | 5763 | 5763 - Fused Link 5763 |  | 421SEG5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 189 | 9 | 24292 | 1701 | 0.07002 | 0.00037049 | 65 | 12285 | 2009/2010 | December-2009 | 12 | 2009
22573 | Install Private Line DDO's for 21N05 | 2009-12-02 09:27 | 2009-12-02 | 2009-12-02 12:36 | Calculated | 5796 | 5796 - Air Break Switch 5796 |  | 416SEG5554-5711 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 141 | 13 | 24292 | 1833 | 0.07546 | 0.00053516 | 71.5 | 10081 | 2009/2010 | December-2009 | 12 | 2009
22572 | Urgent Replacement of Red Tagged Pole 89 | 2009-12-02 09:49 | 2009-12-02 | 2009-12-02 13:08 | Calculated | 652 | 652 - Fuse Switch 652 |  | 119SEG653-652 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 174 | 380 | 24292 | 1566 | 0.06447 | 0.015643 | 2894.5 | 8700 | 2009/2010 | December-2009 | 12 | 2009
22575 | Replace DDO's for 21O17 & Pole | 2009-12-03 09:10 | 2009-12-03 | 2009-12-03 12:40 | Calculated | 5796 | 5796 - Air Break Switch 5796 |  | 416SEG5554-5711 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 152 | 16 | 24292 | 2432 | 0.10012 | 0.00065865 | 6175 | 974300 | 2009/2010 | December-2009 | 12 | 2009
22577 | Scheduled Maintenance - SH49 | 2009-12-04 10:02 | 2009-12-04 | 2009-12-04 11:27 | Calculated | 21O08 | 21O08 - 1 Phase : 25.00 kVA : POLEMNT |  | 416SEG5780-6608 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 85 | 5 | 24292 | 425 | 0.0175 | 0.00020583 | 25 | 2125 | 2009/2010 | December-2009 | 12 | 2009
22579 | Upgrade Tx - Universal Beef | 2009-12-05 07:10 | 2009-12-05 | 2009-12-05 12:07 | Calculated | T2789 | T2789 - 3 Phase : 500.00 kVA : GNDPAD |  | 103SEG723 | Benneydale 103-02 | Urban A | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24292 |  | 0 | 0 |  |  | 2009/2010 | December-2009 | 12 | 2009
22580 | Rusty Tx?? - Hikumutu Road | 2009-12-05 18:10 | 2009-12-05 | 2009-12-05 19:00 | Calculated | 10K11 | 10K11 - 1 Phase : 15.00 kVA : POLEMNT |  | 409SEG5403-5662RET | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 2 | 24292 | 100 | 0.00412 | 8.2332e-05 | 15 | 750 | 2009/2010 | December-2009 | 12 | 2009
22581 | Faulty Tx - Kopaki Road | 2009-12-06 13:06 | 2009-12-06 | 2009-12-06 14:08 | Calculated | T1088 | T1088 - 1 Phase : 15.00 kVA : POLEMNT |  | 103SEG641-1350 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 7 | 24292 | 434 | 0.01787 | 0.00028816 | 15 | 929 | 2009/2010 | December-2009 | 12 | 2009
22584 | Connect Deep Driven Earth - Kururau Road | 2009-12-07 09:04 | 2009-12-07 | 2009-12-07 09:36 | Calculated | 08G01 | 08G01 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 32 | 2 | 24292 | 64 | 0.00263 | 8.2332e-05 | 15 | 480 | 2009/2010 | December-2009 | 12 | 2009
22585 | Incorrect Isolation - SH41 Manunui | 2009-12-07 10:58 | 2009-12-07 | 2009-12-07 11:17 | Calculated | 08K16 | 08K16 - 1 Phase : 50.00 kVA : POLEMNT |  | 408SEG5935-5936 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 8 | 24292 | 152 | 0.00626 | 0.00032933 | 50 | 950 | 2009/2010 | December-2009 | 12 | 2009
22587 | Connect Deep Driven Earth - Otapouri Road | 2009-12-07 15:01 | 2009-12-07 | 2009-12-07 15:19 | Calculated | 10K29 | 10K29 - 1 Phase : 15.00 kVA : POLEMNT |  | 409SEG5403-5662RET | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 18 | 3 | 24292 | 54 | 0.00222 | 0.0001235 | 15 | 270 | 2009/2010 | December-2009 | 12 | 2009
22588 | Unknown - Borough Sub | 2009-12-08 06:04 | 2009-12-08 | 2009-12-08 06:17 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24292 |  | 0 | 0 |  |  | 2009/2010 | December-2009 | 12 | 2009
22589 | Fuse Pulled Apart - Haparua Road | 2009-12-08 13:30 | 2009-12-08 | 2009-12-08 15:32 | Calculated | 04E04 | 04E04 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5506 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 2 | 24292 | 244 | 0.01004 | 8.2332e-05 | 15 | 1830 | 2009/2010 | December-2009 | 12 | 2009
22590 | Disconnect Genset - Top Caves Road | 2009-12-08 15:02 | 2009-12-08 | 2009-12-08 15:10 | Calculated | 110 | 110 - Air Break Switch 110 |  | 101SEG110-109 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 8 | 111 | 24292 | 888 | 0.03656 | 0.0045694 | 851 | 6807 | 2009/2010 | December-2009 | 12 | 2009
22591 | Fuse Pulled Apart - Huirimu Road | 2009-12-09 10:30 | 2009-12-09 | 2009-12-09 12:08 | Calculated | T2369 | T2369 - 1 Phase : 15.00 kVA : polemnt |  | 121SEG724-425RET | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 1 | 24292 | 98 | 0.00403 | 4.1166e-05 | 15 | 1470 | 2009/2010 | December-2009 | 12 | 2009
22592 | Unknown - Paraheka Sub | 2009-12-09 20:34 | 2009-12-09 | 2009-12-09 22:04 | Calculated | 1126 | 1126 - Recloser with Bypass & Links 1126 |  | 114SEG1126-1127 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 30 | 24292 | 2700 | 0.11115 | 0.001235 | 210 | 18899 | 2009/2010 | December-2009 | 12 | 2009
22593 | Unknown - Ngatarawa Road | 2009-12-10 06:15 | 2009-12-10 | 2009-12-10 11:08 | Calculated | 1100 | 1100 - Sectionaliser with Incoming Link 1100 |  | 114SEG1128 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 293 | 13 | 24292 | 3809 | 0.1568 | 0.00053516 | 90 | 26369 | 2009/2010 | December-2009 | 12 | 2009
22595 | Ducks - Hangatiki East Road | 2009-12-10 06:45 | 2009-12-10 | 2009-12-10 09:08 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 9 | 24292 | 1287 | 0.05298 | 0.00037049 | 50 | 7149 | 2009/2010 | December-2009 | 12 | 2009
22596 | Replace Poles 30/6 & 10 - Replace 20L41 | 2009-12-10 10:06 | 2009-12-10 | 2009-12-10 14:41 | Calculated | 5643 | 5643 - Air Break Switch 5643 |  | 414SEG5715-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 275 | 94 | 24292 | 25780 | 1.0613 | 0.0038696 | 500 | 137199 | 2009/2010 | December-2009 | 12 | 2009
22597 | Cable Fault - Manunui Freezing Works | 2009-12-10 13:10 | 2009-12-10 | 2009-12-11 16:49 | Calculated | 5552 | 5552 - Fused Link 5552 |  | 407SEG5405 | Manunui 407-01 (was Affco) | Rural B | Manunui / AFFCO Retired | Manunui Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1659 | 2 | 24292 | 3318 | 0.13659 | 8.2332e-05 | 550 | 912450 | 2009/2010 | December-2009 | 12 | 2009
22598 | Fuse Pulled Apart - Fullerton Road | 2009-12-10 15:35 | 2009-12-10 | 2009-12-10 16:18 | Calculated | T944 | T944 - 1 Phase : 7.50 kVA : POLEMNT |  | 107SEG234 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 1 | 24292 | 43 | 0.00177 | 4.1166e-05 | 7.5 | 322 | 2009/2010 | December-2009 | 12 | 2009
22600 | Install New Pole 40 & Liven New Parerohi SWER Sub | 2009-12-11 10:01 | 2009-12-11 | 2009-12-11 13:46 | Calculated | 5481 | 5481 - Fused Link 5481 |  | 406SEG5481-5630RET | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 187 | 308 | 24292 | 57596 | 2.371 | 0.012679 | 1480 | 276759 | 2009/2010 | December-2009 | 12 | 2009
22602 | Magpie @ 07Q04 - Karangahape Road | 2009-12-11 10:55 | 2009-12-11 | 2009-12-11 14:01 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 39 | 24292 | 7254 | 0.29862 | 0.0016055 | 353.5 | 65750 | 2009/2010 | December-2009 | 12 | 2009
22603 | Unknown - Oio Sub | 2009-12-12 06:35 | 2009-12-12 | 2009-12-12 07:50 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 24 | 24292 | 1800 | 0.0741 | 0.00098798 | 138.5 | 10387 | 2009/2010 | December-2009 | 12 | 2009
22604 | Unknown - Te Anga Road | 2009-12-12 09:15 | 2009-12-12 | 2009-12-12 11:00 | Calculated | T516 | T516 - 3ph 25kVA POL |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 5 | 24292 | 525 | 0.02161 | 0.00020583 | 25 | 2625 | 2009/2010 | December-2009 | 12 | 2009
22605 | Jumper off @ Link 5539 | 2009-12-12 16:46 | 2009-12-12 | 2009-12-12 17:00 | Calculated | 5539 | 5539 - Fused Link 5539 |  | 422SEG5539 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 5 | 24292 | 70 | 0.00288 | 0.00020583 | 37.5 | 525 | 2009/2010 | December-2009 | 12 | 2009
22606 | Unknown - Puhanga Road | 2009-12-13 18:10 | 2009-12-13 | 2009-12-13 19:50 | Calculated | T2015 | T2015 - 2ph 25kVA POLEMNT |  | 115SEGTempABS1-1705 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 2 | 24292 | 200 | 0.00823 | 8.2332e-05 | 25 | 2500 | 2009/2010 | December-2009 | 12 | 2009
22607 | Faulty Insulator - Kiritihere (last Rd crossing) | 2009-12-14 06:13 | 2009-12-14 | 2009-12-14 22:45 | Calculated | 1536 | 1536 - Sectionaliser 1536 |  | No Segment | No Asset Group | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 992 | 8 | 24292 | 7936 | 0.32669 | 0.00032933 | 65 | 64480 | 2009/2010 | December-2009 | 12 | 2009
22609 | Change Rotation After Fault - Manunui Freezing Works | 2009-12-14 08:03 | 2009-12-14 | 2009-12-14 08:32 | Calculated | 5552 | 5552 - Fused Link 5552 |  | 407SEG5405 | Manunui 407-01 (was Affco) | Rural B | Manunui / AFFCO Retired | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 29 | 2 | 24292 | 58 | 0.00239 | 8.2332e-05 | 550 | 15950 | 2009/2010 | December-2009 | 12 | 2009
22610 | Rat - Main Nth Road | 2009-12-14 08:05 | 2009-12-14 | 2009-12-14 09:31 | Calculated | 06H15 | 06H15 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5339 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AOTH | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 86 | 1 | 24292 | 86 | 0.00354 | 4.1166e-05 | 15 | 1290 | 2009/2010 | December-2009 | 12 | 2009
22611 | Genset Failed to Hold Load - Top Caves Road | 2009-12-14 08:31 | 2009-12-14 | 2009-12-14 08:41 | Calculated | 110 | 110 - Air Break Switch 110 |  | 101SEG110-109 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 10 | 111 | 24292 | 1110 | 0.04569 | 0.0045694 | 851 | 8509 | 2009/2010 | December-2009 | 12 | 2009
22612 | Replace 3 Poles & Fit Pole Caps - Poles 71, 73, 76, 77, & 84 | 2009-12-14 09:04 | 2009-12-14 | 2009-12-14 15:08 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 63 | 24292 | 21714 | 0.89387 | 0.0025934 | 358.5 | 124193 | 2009/2010 | December-2009 | 12 | 2009
22614 | Replace Leaky Tx - Western Bay Road | 2009-12-14 13:11 | 2009-12-14 | 2009-12-14 14:36 | Calculated | T2680 | T2680 - 3 Phase : 50.00 kVA : POLEMNT |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 85 | 1 | 24292 | 85 | 0.0035 | 4.1166e-05 | 50 | 4250 | 2009/2010 | December-2009 | 12 | 2009
22608 | Faulty Insulator - Kiritihere (by Rd junction) | 2009-12-14 16:57 | 2009-12-14 | 2009-12-14 18:00 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 16 | 24292 | 1008 | 0.0415 | 0.00065865 | 135 | 8505 | 2009/2010 | December-2009 | 12 | 2009
22615 | Connect Genset - Top Caves Road | 2009-12-15 07:45 | 2009-12-15 | 2009-12-15 07:46 | Calculated | 110 | 110 - Air Break Switch 110 |  | 101SEG110-109 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 110 | 24292 | 110 | 0.00453 | 0.0045282 | 851 | 850 | 2009/2010 | December-2009 | 12 | 2009
22617 | Replace 2 Poles & 1 Xarm - Poles 67, 68, 69 | 2009-12-15 09:01 | 2009-12-15 | 2009-12-15 15:31 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 390 | 63 | 24292 | 23845 | 0.9816 | 0.0025934 | 358.5 | 136064 | 2009/2010 | December-2009 | 12 | 2009
22616 | Disconnect Genset - Top Caves Road | 2009-12-15 16:22 | 2009-12-15 | 2009-12-15 16:23 | Calculated | 110 | 110 - Air Break Switch 110 |  | 101SEG110-109 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 110 | 24292 | 110 | 0.00453 | 0.0045282 | 851 | 850 | 2009/2010 | December-2009 | 12 | 2009
22619 | Replace 2 Poles & Install 2 Sets of Links | 2009-12-16 09:02 | 2009-12-16 | 2009-12-16 14:53 | Calculated | 5257 | 5257 - Air Break Switch 5257 |  | 422SEG5727-5259 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 6 | 63 | 24292 | 78 | 0.00321 | 0.0025934 | 358.5 | 389 | 2009/2010 | December-2009 | 12 | 2009
22620 | Upgrade Tx - Lake Road | 2009-12-16 09:33 | 2009-12-16 | 2009-12-16 14:22 | Calculated | T2988 | T2988 - 3 Phase : 50.00 kVA : GNDPAD |  | 118SEG664-666 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 289 | 1 | 24292 | 289 | 0.0119 | 4.1166e-05 | 50 | 14450 | 2009/2010 | December-2009 | 12 | 2009
22621 | Replace 2 Poles & Install 2 Sets of Links | 2009-12-17 08:58 | 2009-12-17 | 2009-12-17 15:04 | Calculated | 5254 | 5254 - Circuit Breaker 5254 |  | No Segment | 503-01 Nihiniho | Rural D | Nihoniho | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 366 | 63 | 24292 | 18378 | 0.75655 | 0.0025934 | 358.5 | 107810 | 2009/2010 | December-2009 | 12 | 2009
22624 | Upgrade Speedies Rd to 3 Phase | 2009-12-17 09:08 | 2009-12-17 | 2009-12-17 15:59 | Calculated | 285 | 285 - Fused Link 285 |  | 125SEG285-1768 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 411 | 3 | 24292 | 1236 | 0.05088 | 0.0001235 | 15 | 6180 | 2009/2010 | December-2009 | 12 | 2009
22622 | Replace Complete Structure T210 | 2009-12-17 09:36 | 2009-12-17 | 2009-12-17 14:57 | Calculated | 139 | 139 - Fused Link 139 |  | 112SEG139 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 5 | 24292 | 1605 | 0.06607 | 0.00020583 | 75 | 24074 | 2009/2010 | December-2009 | 12 | 2009
22625 | Install New Pole Mid Span - Pole 21/22 | 2009-12-17 09:54 | 2009-12-17 | 2009-12-17 11:16 | Calculated | 549 | 549 - Air Break Switch 549 |  | 111SEG395-549 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 28 | 24292 | 1708 | 0.07031 | 0.0011526 | 225 | 13724 | 2009/2010 | December-2009 | 12 | 2009
22628 | Lower Tap - Huirimu Road | 2009-12-18 08:28 | 2009-12-18 | 2009-12-18 08:58 | Calculated | T1711 | T1711 - 1 Phase : 15.00 kVA : polemnt |  | 121SEG724-425RET | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24292 |  | 0 | 0 |  |  | 2009/2010 | December-2009 | 12 | 2009
22629 | Upgrade T1261 to 3 Phase | 2009-12-18 09:37 | 2009-12-18 | 2009-12-18 14:00 | Calculated | 1760 | 1760 - Fused Link 1760 |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 263 | 3 | 24292 | 789 | 0.03248 | 0.0001235 | 30 | 7890 | 2009/2010 | December-2009 | 12 | 2009
22630 | Replace Xarm on Pole 105/52 | 2009-12-18 10:14 | 2009-12-18 | 2009-12-18 11:59 | Calculated | 210 | 210 - Air Break Switch 210 |  | 108SEG212-210 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 389 | 24292 | 8935 | 0.36782 | 0.016014 | 2485 | 54634 | 2009/2010 | December-2009 | 12 | 2009
22632 | Unknown - Moeatoa Road | 2009-12-18 12:30 | 2009-12-18 | 2009-12-18 15:05 | Calculated | T2539 | T2539 - 1 Phase : 5.00 kVA : POLEMNT |  | 125SEG1536-1535 | Coast 125-06 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 1 | 24292 | 155 | 0.00638 | 4.1166e-05 | 5 | 775 | 2009/2010 | December-2009 | 12 | 2009
22633 | Unknown - Pungarehu Road | 2009-12-19 07:36 | 2009-12-19 | 2009-12-19 09:16 | Calculated | T1639 | T1639 - 1 Phase : 15.00 kVA : POLEMNT |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 2 | 24292 | 200 | 0.00823 | 8.2332e-05 | 15 | 1500 | 2009/2010 | December-2009 | 12 | 2009
22634 | Replace HV Pole for McDonalds Lime | 2009-12-19 08:55 | 2009-12-19 | 2009-12-19 12:43 | Calculated | 757 | 757 - Air Break Switch 757 |  | 208SEG756-757 | No Asset Group | Remote Rural F | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 227 | 5 | 24292 | 1135 | 0.04672 | 0.00020583 | 800 | 181599 | 2009/2010 | December-2009 | 12 | 2009
22717 | RETRY 22648 | 2009-12-20 00:05 | 2009-12-20 | 2009-12-20 05:07 | Calculated | TPTokaanu CB1102 | TPTokaanu CB1102 - 33kV Minimum Oil Circuit Breaker TP1102 |  | No Segment | 515-01 Transpower Tokaanu | Rural D | No Feeder |  |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 2744 | 24292 | 104113 | 4.2859 | 0.11296 | 0 | 0 | 2009/2010 | December-2009 | 12 | 2009
22635 | Burning Pole 235 - By Sawmill (South of Mokau) | 2009-12-20 11:10 | 2009-12-20 | 2009-12-20 13:58 | Calculated | 1634 | 1634 - Air Break Switch 1634 |  | 128SEG1634-REG3 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24292 |  | 0 | 0 |  |  | 2009/2010 | December-2009 | 12 | 2009
22636 | Branch - Kaahu South Road | 2009-12-20 17:55 | 2009-12-20 | 2009-12-20 20:00 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 26 | 24292 | 3250 | 0.13379 | 0.0010703 | 300 | 37500 | 2009/2010 | December-2009 | 12 | 2009
22639 | Remove Branch From Line - Waihaha Road | 2009-12-21 09:46 | 2009-12-21 | 2009-12-21 10:35 | Calculated | 5534 | 5534 - Sectionaliser 5534 |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 14 | 24292 | 686 | 0.02824 | 0.00057632 | 105 | 5145 | 2009/2010 | December-2009 | 12 | 2009
22642 | Ducks - Hangatiki East Road | 2009-12-22 06:20 | 2009-12-22 | 2009-12-22 08:48 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 9 | 24292 | 1332 | 0.05483 | 0.00037049 | 50 | 7399 | 2009/2010 | December-2009 | 12 | 2009
22643 | Fuse Pulled Apart - Rimu Street | 2009-12-22 07:30 | 2009-12-22 | 2009-12-22 08:43 | Calculated | T700 | T700 - 3 Phase : 30.00 kVA : GNDPAD |  | 118SEG1742-463 | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 2 | 24292 | 146 | 0.00601 | 8.2332e-05 | 30 | 2190 | 2009/2010 | December-2009 | 12 | 2009
22644 | Unknown - Grace's Road | 2009-12-22 12:15 | 2009-12-22 | 2009-12-22 15:25 | Calculated | 5731 | 5731 - Fused Link 5731 |  | No Segment | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24292 |  | 0 | 0 |  |  | 2009/2010 | December-2009 | 12 | 2009
22646 | Rotten Xarm - Ohura | 2009-12-22 16:03 | 2009-12-22 | 2009-12-22 18:50 | Calculated | 5758 | 5758 - Sectionaliser 5758 |  | 413SEG5996-5758 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 125 | 24292 | 20875 | 0.85934 | 0.0051457 | 928.5 | 155059 | 2009/2010 | December-2009 | 12 | 2009
22647 | Rotten Xarm - Ohura (Stratford H/Way) | 2009-12-22 16:03 | 2009-12-22 | 2009-12-22 22:15 | Calculated | 5298 | 5298 - Air Break Switch 5298 |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 372 | 82 | 24292 | 30504 | 1.2557 | 0.0033756 | 613 | 228035 | 2009/2010 | December-2009 | 12 | 2009
22645 | Rotten Xarm - Nihoniho | 2009-12-22 17:58 | 2009-12-22 | 2009-12-22 18:27 | Calculated | 5641 | 5641 - Recloser with Bypass & Links 5641 |  | 413SEG6781-5666 | No Asset Group | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 389 | 24292 | 11281 | 0.46439 | 0.016014 | 2672.5 | 77502 | 2009/2010 | December-2009 | 12 | 2009
22649 | Upgrade Speedies Road To 3 Phase | 2009-12-23 09:01 | 2009-12-23 | 2009-12-23 14:37 | Calculated | 285 | 285 - Air Break Switch 285 |  | 125SEG285-1768 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 336 | 3 | 24292 | 1008 | 0.0415 | 0.0001235 | 15 | 5040 | 2009/2010 | December-2009 | 12 | 2009
22651 | Reconfigure Jumpers @ T4042 - Manunui | 2009-12-23 09:33 | 2009-12-23 | 2009-12-23 12:11 | Calculated | 5557 | 5557 - Solid Link 5557 |  | 408SEG5557-5380 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 85 | 36 | 24292 | 1138 | 0.04685 | 0.001482 | 161 | 5837 | 2009/2010 | December-2009 | 12 | 2009
22650 | Replace DDO & Remove Old L.A @ 04J02 | 2009-12-23 09:35 | 2009-12-23 | 2009-12-23 11:11 | Calculated | 5809 | 5809 - Fused Link 5809 |  | 421SEG5809-5363 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 7 | 18 | 24292 | 126 | 0.00519 | 0.00074098 | 85 | 594 | 2009/2010 | December-2009 | 12 | 2009
22652 | Possum x2 - Waitea Road | 2009-12-23 14:00 | 2009-12-23 | 2009-12-23 15:49 | Calculated | 09K05 | 09K05 - 2ph 15kVA POLEMNT |  | 409SEG5134 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 2 | 24292 | 218 | 0.00897 | 8.2332e-05 | 15 | 1635 | 2009/2010 | December-2009 | 12 | 2009
22653 | Unknown - Turongo Street | 2009-12-24 11:55 | 2009-12-24 | 2009-12-24 14:43 | Calculated | 668 | 668 - Fused Link 668 |  | 112SEG668-229 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 39 | 24292 | 6552 | 0.26972 | 0.0016055 | 400 | 67199 | 2009/2010 | December-2009 | 12 | 2009
22655 | Birds - Waituhi Road | 2009-12-25 11:55 | 2009-12-25 | 2009-12-25 12:39 | Calculated | 07J17 | 07J17 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5596-5930 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 1 | 24292 | 44 | 0.00181 | 4.1166e-05 | 15 | 660 | 2009/2010 | December-2009 | 12 | 2009
22656 | Unknown - Karangahape Road | 2009-12-26 08:45 | 2009-12-26 | 2009-12-26 10:09 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 39 | 24292 | 3276 | 0.13486 | 0.0016055 | 353.5 | 29693 | 2009/2010 | December-2009 | 12 | 2009
22657 | Magpie @ 06D02 - Waitewhena Road | 2009-12-26 20:25 | 2009-12-26 | 2009-12-26 22:12 | Calculated | 5281 | 5281 - Recloser with Bypass & Links 5281 |  | 413SEG5281-5283 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 23 | 24292 | 2461 | 0.10131 | 0.00094681 | 158 | 16906 | 2009/2010 | December-2009 | 12 | 2009
22659 | Unknown - Haurua Road | 2009-12-27 19:15 | 2009-12-27 | 2009-12-27 19:58 | Calculated | T82 | T82 - 3 Phase : 25.00 kVA : POLEMNT |  | 101SEG261-519 | Caves 101-02 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 3 | 24292 | 129 | 0.00531 | 0.0001235 | 25 | 1074 | 2009/2010 | December-2009 | 12 | 2009
22660 | Unknown - Pamotumotu Road | 2009-12-28 07:00 | 2009-12-28 | 2009-12-28 09:21 | Calculated | T639 | T639 - 3ph 30kVA polemnt |  | 111SEG551 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 4 | 24292 | 564 | 0.02322 | 0.00016466 | 30 | 4230 | 2009/2010 | December-2009 | 12 | 2009
22661 | Unknown - Hospital Road | 2009-12-28 15:45 | 2009-12-28 | 2009-12-28 16:03 | Calculated | T1339 | T1339 - 3 Phase : 50.00 kVA : POLEMNT |  | 107SEG555 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 11 | 24292 | 198 | 0.00815 | 0.00045282 | 50 | 899 | 2009/2010 | December-2009 | 12 | 2009
22662 | Unknown - Rata Street | 2009-12-28 15:52 | 2009-12-28 | 2009-12-28 16:45 | Calculated | 08J46 | 08J46 - 3ph 200kVA GNDPAD |  | 408SEG5390-5621 | Manunui 408-01 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 26 | 24292 | 1378 | 0.05673 | 0.0010703 | 200 | 10599 | 2009/2010 | December-2009 | 12 | 2009
22664 | Wind - Mangaorongo Road | 2009-12-30 13:05 | 2009-12-30 | 2009-12-30 14:24 | Calculated | T1286 | T1286 - 1 Phase : 25.00 kVA : POLEMNT |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 2 | 24292 | 158 | 0.0065 | 8.2332e-05 | 25 | 1975 | 2009/2010 | December-2009 | 12 | 2009
22666 | Wind - Tahaia Cross Road | 2009-12-30 15:27 | 2009-12-30 | 2009-12-30 17:24 | Calculated | T188 | T188 - 3ph 50kVA POLEMNT |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 3 | 24292 | 351 | 0.01445 | 0.0001235 | 50 | 5849 | 2009/2010 | December-2009 | 12 | 2009
22667 | Wind - Kaahu South Road | 2009-12-30 17:15 | 2009-12-30 | 2009-12-30 17:39 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 26 | 24292 | 624 | 0.02569 | 0.0010703 | 300 | 7200 | 2009/2010 | December-2009 | 12 | 2009
22668 | Wind - Hangatiki | 2009-12-30 18:00 | 2009-12-30 | 2009-12-30 18:05 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24292 |  | 0 | 0 |  |  | 2009/2010 | December-2009 | 12 | 2009
22669 | Wind - Taharoa | 2009-12-30 18:00 | 2009-12-30 | 2009-12-30 18:10 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24292 |  | 0 | 0 |  |  | 2009/2010 | December-2009 | 12 | 2009
22671 | Wind - Ouruwhero Road | 2009-12-30 21:05 | 2009-12-30 | 2009-12-30 22:39 | Calculated | T224 | T224 - 3 Phase : 50.00 kVA : POLEMNT |  | 112SEG637-352 | Otorohanga 112-07 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 5 | 24292 | 470 | 0.01935 | 0.00020583 | 50 | 4700 | 2009/2010 | December-2009 | 12 | 2009
22672 | Wind - Te Anga Road | 2009-12-31 07:59 | 2009-12-31 | 2009-12-31 09:42 | Calculated | T516 | T516 - 3ph 25kVA POL |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 5 | 24292 | 515 | 0.0212 | 0.00020583 | 25 | 2575 | 2009/2010 | December-2009 | 12 | 2009
22673 | Faulty L.A - Desert Road | 2009-12-31 08:30 | 2009-12-31 | 2009-12-31 11:00 | Calculated | 11S09 | 11S09 - 3 Phase : 100.00 kVA : POLEMNT |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLY | FOLY | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 2 | 24292 | 300 | 0.01235 | 8.2332e-05 | 100 | 15000 | 2009/2010 | December-2009 | 12 | 2009
22674 | Replace Pole Using Bulldozer | 2009-12-31 09:29 | 2009-12-31 | 2009-12-31 13:26 | Calculated | 636 | 636 - Air Break Switch 636 |  | 103SEG REG4-636 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 222 | 263 | 24292 | 666 | 0.02742 | 0.010827 | 1960.5 | 3330 | 2009/2010 | December-2009 | 12 | 2009
22675 | Change Tx - Hikumutu Road | 2009-12-31 09:37 | 2009-12-31 | 2009-12-31 11:19 | Calculated | 10K11 | 10K11 - 1 Phase : 15.00 kVA : POLEMNT |  | 409SEG5403-5662RET | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 102 | 2 | 24292 | 204 | 0.0084 | 8.2332e-05 | 15 | 1530 | 2009/2010 | December-2009 | 12 | 2009
22676 | Wind - Main Sth Road Te Kuiti | 2010-01-01 14:17 | 2010-01-01 | 2010-01-01 15:58 | Calculated | T638 | T638 - 3 Phase : 50.00 kVA : POLEMNT |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 1 | 24329 | 101 | 0.00415 | 4.1103e-05 | 50 | 5050 | 2009/2010 | January-2010 | 1 | 2010
22678 | Fuse Pulled Apart - Hapa Road | 2010-01-02 14:10 | 2010-01-02 | 2010-01-02 15:11 | Calculated | 09K08 | 09K08 - 2 Phase : 25.00 kVA : POLEMNT |  | 409SEG5789-5778 | Southern 409-03 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 19 | 24329 | 1159 | 0.04764 | 0.00078096 | 25 | 1524 | 2009/2010 | January-2010 | 1 | 2010
22680 | Unknown - Borough Sub | 2010-01-03 09:05 | 2010-01-03 | 2010-01-03 09:14 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22681 | Broken Xarm - Ranginui Road | 2010-01-04 05:31 | 2010-01-04 | 2010-01-04 05:42 | Calculated | 411 | 411 - Recloser with Bypass & Links 411 |  | No Segment | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 69 | 24329 | 759 | 0.0312 | 0.0028361 | 1388 | 15267 | 2009/2010 | January-2010 | 1 | 2010
22682 | Broken Xarm - Scott Road | 2010-01-04 05:31 | 2010-01-04 | 2010-01-04 06:24 | Calculated | 492 | 492 - Air Break Switch 492 |  | 119SEG492-406RET | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 117 | 24329 | 6201 | 0.25488 | 0.0048091 | 2143 | 113579 | 2009/2010 | January-2010 | 1 | 2010
22683 | Broken Xarm - Maraetai Substation | 2010-01-04 05:31 | 2010-01-04 | 2010-01-04 09:13 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 222 | 147 | 24329 | 32634 | 1.3414 | 0.0060422 | 2633 | 584525 | 2009/2010 | January-2010 | 1 | 2010
22684 | Wind - Ongarue E/W Sub | 2010-01-04 08:30 | 2010-01-04 | 2010-01-04 09:23 | Calculated | 5466 | 5466 - Recloser with Bypass & Links 5466 |  | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 80 | 24329 | 4240 | 0.17428 | 0.0032883 | 548.5 | 29070 | 2009/2010 | January-2010 | 1 | 2010
22685 | Unknown - Hangatiki | 2010-01-04 22:56 | 2010-01-04 | 2010-01-04 22:59 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22686 | Unknown - Taharoa | 2010-01-04 22:56 | 2010-01-04 | 2010-01-04 23:06 | Calculated | 788 | 788 - Circuit Breaker 788 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22687 | Jumper Off - Kohua Road | 2010-01-05 06:20 | 2010-01-05 | 2010-01-05 11:45 | Calculated | 1738 | 1738 - Fused Link 1738 |  | 115SEG1738-1709 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 325 | 14 | 24329 | 4550 | 0.18702 | 0.00057544 | 80 | 25999 | 2009/2010 | January-2010 | 1 | 2010
22690 | Magpie x2 - Ongarue Stream Road | 2010-01-05 09:07 | 2010-01-05 | 2010-01-05 11:35 | Calculated | 02J05 | 02J05 - 1 Phase : 10.00 kVA : POLEMNT |  | 421SEG5468 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 1 | 24329 | 148 | 0.00608 | 4.1103e-05 | 10 | 1480 | 2009/2010 | January-2010 | 1 | 2010
22688 | Jumper Off - Owens Road | 2010-01-05 09:23 | 2010-01-05 | 2010-01-05 11:45 | Calculated | 1708 | 1708 - Fused Link 1708 |  | 115SEG1708-1738 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 18 | 24329 | 2556 | 0.10506 | 0.00073986 | 100 | 14199 | 2009/2010 | January-2010 | 1 | 2010
22691 | Intall HV Pin @ T2845 | 2010-01-05 09:51 | 2010-01-05 | 2010-01-05 11:32 | Calculated | 1329 | 1329 - Air Break Switch 1329 |  | 117SEG1329-1316 | Te Mapara 117-02 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 53 | 30 | 24329 | 1590 | 0.06535 | 0.0012331 | 277.5 | 14707 | 2009/2010 | January-2010 | 1 | 2010
22692 | Fuse Pulled Apart - Beards Road | 2010-01-05 11:00 | 2010-01-05 | 2010-01-05 14:26 | Calculated | 05L01 | 05L01 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5356-5320 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 206 | 2 | 24329 | 412 | 0.01693 | 8.2206e-05 | 15 | 3090 | 2009/2010 | January-2010 | 1 | 2010
22693 | Broken HV Xarm - Napinapi Road | 2010-01-05 13:21 | 2010-01-05 | 2010-01-05 14:49 | Calculated | T1766 | T1766 - 1 Phase : 15.00 kVA : POLEMNT |  | 117SEG1299-1329 | Te Mapara 117-02 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 2 | 24329 | 176 | 0.00723 | 8.2206e-05 | 15 | 1320 | 2009/2010 | January-2010 | 1 | 2010
22694 | Wind - Rangitoto Road | 2010-01-05 19:00 | 2010-01-05 | 2010-01-05 19:54 | Calculated | T2262 | T2262 - 1 Phase : 10.00 kVA : POLEMNT |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 24329 | 54 | 0.00222 | 4.1103e-05 | 10 | 540 | 2009/2010 | January-2010 | 1 | 2010
22695 | Overloaded - McLean Road | 2010-01-06 05:15 | 2010-01-06 | 2010-01-06 06:40 | Calculated | 1151 | 1151 - Fused Link 1151 |  | 119SEG1151 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 5 | 24329 | 425 | 0.01747 | 0.00020552 | 115 | 9775 | 2009/2010 | January-2010 | 1 | 2010
22696 | Fuse Pulled Apart - Main Sth Road Piopio | 2010-01-06 08:20 | 2010-01-06 | 2010-01-06 11:06 | Calculated | T821 | T821 - 1 Phase : 10.00 kVA : POLEMNT |  | 113SEG1337-1650 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 1 | 24329 | 166 | 0.00682 | 4.1103e-05 | 10 | 1660 | 2009/2010 | January-2010 | 1 | 2010
22699 | Upgrade Speedies Road to 3 Phase | 2010-01-07 09:31 | 2010-01-07 | 2010-01-07 12:46 | Calculated | 285 | 285 - Air Break Switch 285 |  | 125SEG285-1768 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 195 | 3 | 24329 | 585 | 0.02405 | 0.00012331 | 15 | 2925 | 2009/2010 | January-2010 | 1 | 2010
22701 | Replace Tx Pole & Hardware - 13I01 | 2010-01-07 09:36 | 2010-01-07 | 2010-01-07 15:28 | Calculated | 5499 | 5499 - Fused Link 5499 |  | 410SEG5499-5559 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 316 | 25 | 24329 | 632 | 0.02598 | 0.0010276 | 138.5 | 4740 | 2009/2010 | January-2010 | 1 | 2010
22702 | Unknown - Waituhi Road | 2010-01-07 17:25 | 2010-01-07 | 2010-01-07 18:13 | Calculated | 07J17 | 07J17 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5596-5930 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 1 | 24329 | 48 | 0.00197 | 4.1103e-05 | 15 | 720 | 2009/2010 | January-2010 | 1 | 2010
22705 | Unknown - Hangatiki | 2010-01-10 02:05 | 2010-01-10 | 2010-01-10 02:08 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22706 | Unknown - Taharoa | 2010-01-10 02:05 | 2010-01-10 | 2010-01-10 02:18 | Calculated | 788 | 788 - Circuit Breaker 788 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22707 | Starling - Waituhi Road | 2010-01-10 07:50 | 2010-01-10 | 2010-01-10 08:45 | Calculated | 07J17 | 07J17 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5596-5930 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 24329 | 55 | 0.00226 | 4.1103e-05 | 15 | 825 | 2009/2010 | January-2010 | 1 | 2010
22708 | Unknown - Ahuroa Road | 2010-01-10 08:30 | 2010-01-10 | 2010-01-10 11:45 | Calculated | 252 | 252 - Fused Link 252 |  | 106SEG252-803 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 195 | 10 | 24329 | 1950 | 0.08015 | 0.00041103 | 50 | 9750 | 2009/2010 | January-2010 | 1 | 2010
22709 | Unknown - Harding Road | 2010-01-10 10:37 | 2010-01-10 | 2010-01-10 17:25 | Calculated | T2835 | T2835 - 3 Phase : 15.00 kVA : POLEMNT |  | 122SEG375 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 408 | 1 | 24329 | 408 | 0.01677 | 4.1103e-05 | 15 | 6120 | 2009/2010 | January-2010 | 1 | 2010
22710 | Gadsby Road 33 kV Feeder Renewal | 2010-01-11 09:17 | 2010-01-11 | 2010-01-11 16:08 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22712 | Broken DDO @ Links 283 - SH30 | 2010-01-11 12:12 | 2010-01-11 | 2010-01-11 12:52 | Calculated | 273 | 273 - Air Break Switch 273 |  | 103SEG723 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 16 | 24329 | 640 | 0.02631 | 0.00065765 | 65 | 2599 | 2009/2010 | January-2010 | 1 | 2010
22715 | Gadsby Road 33kV Feeder Renewal Project | 2010-01-12 09:18 | 2010-01-12 | 2010-01-12 16:27 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24329 | 0 | 0 | 0 | 0 | 0 | 2009/2010 | January-2010 | 1 | 2010
22716 | Bird Strike - Gravel Scoop | 2010-01-12 16:00 | 2010-01-12 | 2010-01-12 17:46 | Calculated | 122 | 122 - Circuit Breaker 122 |  | No Segment | 203-01 Te Waireka Road | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 520 | 24329 | 29111 | 1.1966 | 0.021374 | 4813.5 | 277161 | 2009/2010 | January-2010 | 1 | 2010
22719 | Replace "H" Structures 15,19 and 20 | 2010-01-13 08:29 | 2010-01-13 | 2010-01-13 16:44 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22720 | Gadsby Road Feeder Renewal Project | 2010-01-13 09:08 | 2010-01-13 | 2010-01-13 16:13 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22722 | Overloaded TX, Main Sth Road | 2010-01-14 07:37 | 2010-01-14 | 2010-01-14 08:34 | Calculated | 09K13 | 09K13 - 3ph 30kVA POLEMNT |  | 409SEG5867-5135 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 1 | 24329 | 57 | 0.00234 | 4.1103e-05 | 30 | 1710 | 2009/2010 | January-2010 | 1 | 2010
22723 | Gadsby Rd Feeder Renewal Project | 2010-01-14 09:12 | 2010-01-14 | 2010-01-14 16:34 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22725 | Replace Pole 1/102/19 With New TX Structure- TX3313 | 2010-01-14 10:00 | 2010-01-14 | 2010-01-14 15:35 | Calculated | 440 | 440 - Recloser with Outgoing Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 335 | 117 | 24329 | 37343 | 1.5349 | 0.0048091 | 1048.5 | 324704 | 2009/2010 | January-2010 | 1 | 2010
22727 | Lightning, Beach Road | 2010-01-14 12:40 | 2010-01-14 | 2010-01-14 14:58 | Calculated | 1758 | 1758 - Fused Link 1758 |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 6 | 24329 | 828 | 0.03403 | 0.00024662 | 40 | 5520 | 2009/2010 | January-2010 | 1 | 2010
22729 | Possum- Main South Road, Piopio | 2010-01-15 08:45 | 2010-01-15 | 2010-01-15 10:19 | Calculated | T1715 | T1715 - 1 Phase : 15.00 kVA : POLEMNT |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 4 | 24329 | 376 | 0.01545 | 0.00016441 | 15 | 1410 | 2009/2010 | January-2010 | 1 | 2010
22732 | Fuse Pulled Apart, Maihiihi Road | 2010-01-17 17:00 | 2010-01-17 | 2010-01-17 18:35 | Calculated | T1098 | T1098 - 2ph 15kVA polemnt |  | 111SEG665 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 3 | 24329 | 285 | 0.01171 | 0.00012331 | 15 | 1425 | 2009/2010 | January-2010 | 1 | 2010
22733 | Bird at TX7Q4- Karangahape Road | 2010-01-18 05:30 | 2010-01-18 | 2010-01-18 07:32 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 39 | 24329 | 4758 | 0.19557 | 0.001603 | 353.5 | 43126 | 2009/2010 | January-2010 | 1 | 2010
22734 | Bird at TX7Q4- Karangahape Road West | 2010-01-18 05:30 | 2010-01-18 | 2010-01-18 07:45 | Calculated | 5592 | 5592 - Fused Link 5592 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 32 | 24329 | 4320 | 0.17757 | 0.0013153 | 283.5 | 38272 | 2009/2010 | January-2010 | 1 | 2010
22736 | Possum Main South Road Piopio | 2010-01-18 08:45 | 2010-01-18 | 2010-01-18 09:50 | Calculated | T1715 | T1715 - 1 Phase : 15.00 kVA : POLEMNT |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 4 | 24329 | 260 | 0.01069 | 0.00016441 | 15 | 975 | 2009/2010 | January-2010 | 1 | 2010
22735 | Bird at TX7Q4- Karangahape Road | 2010-01-18 09:12 | 2010-01-18 | 2010-01-18 10:38 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 86 | 39 | 24329 | 3354 | 0.13786 | 0.001603 | 353.5 | 30400 | 2009/2010 | January-2010 | 1 | 2010
22738 | Faulty TX- Wairere Road | 2010-01-18 10:21 | 2010-01-18 | 2010-01-18 11:30 | Calculated | T2548 | T2548 - 3 Phase : 30.00 kVA : POLEMNT |  | 116SEG1327-1340 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24329 | 69 | 0.00284 | 4.1103e-05 | 30 | 2070 | 2009/2010 | January-2010 | 1 | 2010
22741 | Unknown- Kaikara Road | 2010-01-18 13:15 | 2010-01-18 | 2010-01-18 16:39 | Calculated | 10E05 | 10E05 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5308-5794 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 204 | 3 | 24329 | 612 | 0.02516 | 0.00012331 | 15 | 3060 | 2009/2010 | January-2010 | 1 | 2010
22743 | Duck- Raetihi Road | 2010-01-18 14:30 | 2010-01-18 | 2010-01-18 15:11 | Calculated | 20K18 | 20K18 - 3 Phase : 30.00 kVA : POLEMNT |  | 416SEG5956-5672 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 1 | 24329 | 41 | 0.00169 | 4.1103e-05 | 30 | 1230 | 2009/2010 | January-2010 | 1 | 2010
22744 | Replace "H" Structures 15,19 and 20 | 2010-01-19 08:13 | 2010-01-19 | 2010-01-19 16:02 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22745 | Gadsby Road Feeder Renewal Project | 2010-01-19 08:44 | 2010-01-19 | 2010-01-19 15:46 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22746 | Earth Test SH49 | 2010-01-19 11:25 | 2010-01-19 | 2010-01-19 12:00 | Calculated | 21M01 | 21M01 - 3 Phase : 50.00 kVA : POLEMNT |  | 416SEG5690 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 35 | 8 | 24329 | 280 | 0.01151 | 0.00032883 | 50 | 1750 | 2009/2010 | January-2010 | 1 | 2010
22748 | Faulty DDO Fuse Carrier Harbour Road | 2010-01-19 19:15 | 2010-01-19 | 2010-01-19 22:05 | Calculated | T542 | T542 - 3 Phase : 30.00 kVA : POLEMNT |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 6 | 24329 | 1020 | 0.04193 | 0.00024662 | 30 | 5100 | 2009/2010 | January-2010 | 1 | 2010
22749 | Ducks - Hangatiki East Road | 2010-01-20 06:20 | 2010-01-20 | 2010-01-20 08:26 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FIPS1 | Incorrect Protection Settings | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 9 | 24329 | 1134 | 0.04661 | 0.00036993 | 50 | 6299 | 2009/2010 | January-2010 | 1 | 2010
22750 | Possum-Main South Road Piopio | 2010-01-20 06:43 | 2010-01-20 | 2010-01-20 09:40 | Calculated | T1715 | T1715 - 1 Phase : 15.00 kVA : POLEMNT |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 4 | 24329 | 708 | 0.0291 | 0.00016441 | 15 | 2655 | 2009/2010 | January-2010 | 1 | 2010
22751 | Unknown - Wilson Road | 2010-01-20 06:55 | 2010-01-20 | 2010-01-20 10:07 | Calculated | T1690 | T1690 - 1 Phase : 25.00 kVA : POLEMNT |  | 113SEG1547 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 192 | 3 | 24329 | 576 | 0.02368 | 0.00012331 | 25 | 4799 | 2009/2010 | January-2010 | 1 | 2010
22752 | Trees - Hangatiki East Road | 2010-01-20 08:05 | 2010-01-20 | 2010-01-20 09:06 | Calculated | T80 | T80 - 1 Phase : 15.00 kVA : POLEMNT |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 2 | 24329 | 122 | 0.00501 | 8.2206e-05 | 15 | 915 | 2009/2010 | January-2010 | 1 | 2010
22753 | Lightning - Browns Road | 2010-01-20 09:24 | 2010-01-20 | 2010-01-20 11:38 | Calculated | T1539 | T1539 - 1 Phase : 15.00 kVA : POLEMNT |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 2 | 24329 | 268 | 0.01102 | 8.2206e-05 | 15 | 2010 | 2009/2010 | January-2010 | 1 | 2010
22754 | Raise Tap - Kopaki Road | 2010-01-20 11:10 | 2010-01-20 | 2010-01-20 11:20 | Calculated | T1088 | T1088 - 1 Phase : 15.00 kVA : POLEMNT |  | 103SEG641-1350 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 10 | 7 | 24329 | 70 | 0.00288 | 0.00028772 | 15 | 149 | 2009/2010 | January-2010 | 1 | 2010
22756 | Unknown - Makokomiko Road | 2010-01-20 15:50 | 2010-01-20 | 2010-01-20 16:44 | Calculated | T4056 | T4056 - 3 Phase : 5.00 kVA : POLEMNT |  | 409SEG5867-5135 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 24329 | 54 | 0.00222 | 4.1103e-05 | 5 | 270 | 2009/2010 | January-2010 | 1 | 2010
22757 | Branch on Line - Tahaia Cross Road | 2010-01-20 17:55 | 2010-01-20 | 2010-01-20 19:07 | Calculated | T188 | T188 - 3ph 50kVA POLEMNT |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 3 | 24329 | 216 | 0.00888 | 0.00012331 | 50 | 3599 | 2009/2010 | January-2010 | 1 | 2010
22758 | Lightning- Puketawai Road | 2010-01-21 08:05 | 2010-01-21 | 2010-01-21 09:56 | Calculated | T1192 | T1192 - 3ph 25kVA POLEMNT |  | 110SEG642-343 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 3 | 24329 | 333 | 0.01369 | 0.00012331 | 25 | 2774 | 2009/2010 | January-2010 | 1 | 2010
22759 | Lightning- Aotearoa Road | 2010-01-21 09:00 | 2010-01-21 | 2010-01-21 11:12 | Calculated | T1320 | T1320 - 3ph 25kVA POLEMNT |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 5 | 24329 | 660 | 0.02713 | 0.00020552 | 25 | 3300 | 2009/2010 | January-2010 | 1 | 2010
22762 | Lightning Aotearoa Road | 2010-01-21 13:30 | 2010-01-21 | 2010-01-21 14:47 | Calculated | T875 | T875 - 3ph 30kVA POLEMNT |  | 122SEG562 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 6 | 24329 | 462 | 0.01899 | 0.00024662 | 30 | 2310 | 2009/2010 | January-2010 | 1 | 2010
22763 | Fuse Pulled Apart- Noho St | 2010-01-21 13:50 | 2010-01-21 | 2010-01-21 14:24 | Calculated | 09K15 | 09K15 - 2ph 25kVA POLEMNT |  | 409SEG5778 | Southern 409-03 | Rural D | Southern | Manunui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 9 | 24329 | 306 | 0.01258 | 0.00036993 | 25 | 849 | 2009/2010 | January-2010 | 1 | 2010
22764 | Line Down- Kaahu Tee Zone Substation | 2010-01-21 16:31 | 2010-01-21 | 2010-01-21 23:11 | Calculated | 1748 | 1748 - Circuit Breaker 1748 |  | No Segment | 216-01 Kaahu Tee | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22765 | Line Down- Waikino Road | 2010-01-21 16:31 | 2010-01-21 | 2010-01-21 19:07 | Calculated | 426 | 426 - Recloser 426 |  | 129SEG434-426 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22766 | Line Down- Tirohanga Road | 2010-01-21 16:31 | 2010-01-21 | 2010-01-21 19:32 | Calculated | 787 | 787 - Air Break Switch 787 |  | 123SEG460-787 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22767 | Branch on Line- Ngaroma Rd | 2010-01-21 16:50 | 2010-01-21 | 2010-01-21 18:17 | Calculated | T1190 | T1190 - 1 Phase : 15.00 kVA : POLEMNT |  | 122SEG633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22768 | Wind SH1 | 2010-01-21 18:05 | 2010-01-21 | 2010-01-21 18:41 | Calculated | 08V02 | 08V02 - 1 Phase : 25.00 kVA : POLEMNT |  | 417SEG5905 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 9 | 24329 | 324 | 0.01332 | 0.00036993 | 25 | 899 | 2009/2010 | January-2010 | 1 | 2010
22769 | Broken DDO- Waikino Road | 2010-01-21 23:12 | 2010-01-21 | 2010-01-21 23:52 | Calculated | 426 | 426 - Recloser 426 |  | 129SEG434-426 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22770 | Lightning- Poihipi Road | 2010-01-22 04:40 | 2010-01-22 | 2010-02-22 10:48 | Calculated | T933 | T933 - 1 Phase : 15.00 kVA : POLEMNT |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 368 | 3 | 24329 | 1104 | 0.04538 | 0.00012331 | 15 | 5520 | 2009/2010 | January-2010 | 1 | 2010
22771 | Lightning- Marotiri Rd | 2010-01-22 08:45 | 2010-01-22 | 2010-01-22 11:22 | Calculated | T167 | T167 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 3 | 24329 | 471 | 0.01936 | 0.00012331 | 15 | 2355 | 2009/2010 | January-2010 | 1 | 2010
22772 | Lightning- Marotiri Rd | 2010-01-22 10:15 | 2010-01-22 | 2010-01-22 10:57 | Calculated | T1078 | T1078 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 2 | 24329 | 84 | 0.00345 | 8.2206e-05 | 15 | 630 | 2009/2010 | January-2010 | 1 | 2010
22774 | Lightning- Marotiri Road | 2010-01-22 12:25 | 2010-01-22 | 2010-01-22 18:57 | Calculated | T1490 | T1490 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG699-1267 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 392 | 2 | 24329 | 784 | 0.03222 | 8.2206e-05 | 15 | 5880 | 2009/2010 | January-2010 | 1 | 2010
22773 | Lightning- Aotearoa Road | 2010-01-22 22:10 | 2010-01-22 | 2010-01-23 13:03 | Calculated | T916 | T916 - 1 Phase : 10.00 kVA : POLEMNT |  | 122SEG499 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 893 | 2 | 24329 | 1786 | 0.07341 | 8.2206e-05 | 10 | 8930 | 2009/2010 | January-2010 | 1 | 2010
22775 | Denzil Dr | 2010-01-24 08:15 | 2010-01-24 | 2010-01-24 09:08 | Calculated | T4118 | T4118 - 3ph 15kVA POLEMNT |  | 410SEG6766-5141 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 3 | 24329 | 159 | 0.00654 | 0.00012331 | 15 | 795 | 2009/2010 | January-2010 | 1 | 2010
22777 | Te Puke Road | 2010-01-25 10:10 | 2010-01-25 | 2010-01-25 11:17 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 2 | 24329 | 134 | 0.00551 | 8.2206e-05 | 8 | 536 | 2009/2010 | January-2010 | 1 | 2010
22778 | Lightning SH32 | 2010-01-25 14:35 | 2010-01-25 | 2010-01-25 15:13 | Calculated | 04Q13 | 04Q13 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 1 | 24329 | 38 | 0.00156 | 4.1103e-05 | 15 | 570 | 2009/2010 | January-2010 | 1 | 2010
22779 | Broke DDO Tihoi Road | 2010-01-25 17:05 | 2010-01-25 | 2010-01-25 21:28 | Calculated | T745 | T745 - 3 Phase : 25.00 kVA : POLEMNT |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 263 | 2 | 24329 | 526 | 0.02162 | 8.2206e-05 | 25 | 6575 | 2009/2010 | January-2010 | 1 | 2010
22781 | Faulty TX Mangawhero Road | 2010-01-25 17:05 | 2010-01-25 | 2010-01-25 22:55 | Calculated | T2919 | T2919 - 3ph 50kVA POLEMNT |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 350 | 2 | 24329 | 700 | 0.02877 | 8.2206e-05 | 50 | 17500 | 2009/2010 | January-2010 | 1 | 2010
22782 | Lightning Old Te Kuiti Road | 2010-01-25 17:05 | 2010-01-25 | 2010-01-25 18:37 | Calculated | T208 | T208 - 3 Phase : 25.00 kVA : POLEMNT |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 3 | 24329 | 276 | 0.01134 | 0.00012331 | 25 | 2299 | 2009/2010 | January-2010 | 1 | 2010
22783 | Lightning Old Te Kuiti Road | 2010-01-25 17:05 | 2010-01-25 | 2010-01-25 18:48 | Calculated | T1042 | T1042 - 3ph 50kVA POLEMNT |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 3 | 24329 | 309 | 0.0127 | 0.00012331 | 50 | 5149 | 2009/2010 | January-2010 | 1 | 2010
22784 | Lightning Old Te Kuiti Road | 2010-01-25 17:05 | 2010-01-25 | 2010-01-25 18:54 | Calculated | T563 | T563 - 1 Phase : 15.00 kVA : POLEMNT |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 1 | 24329 | 109 | 0.00448 | 4.1103e-05 | 15 | 1635 | 2009/2010 | January-2010 | 1 | 2010
22785 | Lightning Mangawhero Road | 2010-01-25 17:05 | 2010-01-25 | 2010-01-25 19:03 | Calculated | T394 | T394 - 3ph 25kVA POLEMNT |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 3 | 24329 | 354 | 0.01455 | 0.00012331 | 25 | 2949 | 2009/2010 | January-2010 | 1 | 2010
22786 | Lightning Mangawhero Road | 2010-01-25 17:05 | 2010-01-25 | 2010-01-25 19:10 | Calculated | T1044 | T1044 - 3ph 25kVA POLEMNT |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 2 | 24329 | 250 | 0.01028 | 8.2206e-05 | 25 | 3125 | 2009/2010 | January-2010 | 1 | 2010
22787 | Lightning Ahuroa Road | 2010-01-25 17:05 | 2010-01-25 | 2010-01-25 19:12 | Calculated | T1587 | T1587 - 1 Phase : 7.50 kVA : POLEMNT |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 3 | 24329 | 381 | 0.01566 | 0.00012331 | 7.5 | 952 | 2009/2010 | January-2010 | 1 | 2010
22788 | Lightning SH49 | 2010-01-25 18:30 | 2010-01-25 | 2010-01-25 19:34 | Calculated | 21O08 | 21O08 - 1 Phase : 25.00 kVA : POLEMNT |  | 416SEG5780-6608 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 5 | 24329 | 320 | 0.01315 | 0.00020552 | 25 | 1600 | 2009/2010 | January-2010 | 1 | 2010
22789 | Lightning SH46 | 2010-01-25 18:30 | 2010-01-25 | 2010-01-25 21:54 | Calculated | 12R01 | 12R01 - 1 Phase : 10.00 kVA : POLEMNT |  | 418SEG5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 204 | 2 | 24329 | 408 | 0.01677 | 8.2206e-05 | 10 | 2040 | 2009/2010 | January-2010 | 1 | 2010
22790 | Lightning Mangatutu Road | 2010-01-25 19:05 | 2010-01-25 | 2010-01-25 20:30 | Calculated | T996 | T996 - 3ph 25kVA POLEMNT |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 4 | 24329 | 340 | 0.01398 | 0.00016441 | 25 | 2125 | 2009/2010 | January-2010 | 1 | 2010
22791 | Lightning Pukehou Road | 2010-01-25 20:25 | 2010-01-25 | 2010-01-25 20:44 | Calculated | 09L06 | 09L06 - 1 Phase : 10.00 kVA : POLEMNT |  | 408SEG5406 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 5 | 24329 | 95 | 0.0039 | 0.00020552 | 10 | 190 | 2009/2010 | January-2010 | 1 | 2010
22792 | Lightning Burnand Road | 2010-01-25 20:30 | 2010-01-25 | 2010-01-25 21:05 | Calculated | 08K17 | 08K17 - 1 Phase : 10.00 kVA : POLEMNT |  | 408SEG5935-5936 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 1 | 24329 | 35 | 0.00144 | 4.1103e-05 | 10 | 350 | 2009/2010 | January-2010 | 1 | 2010
22780 | Broken DDO Tihoi Road | 2010-01-25 20:33 | 2010-01-25 | 2010-01-25 21:28 | Calculated | 700 | 700 - Air Break Switch 700 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22793 | Lightning Ongarure Stream Road | 2010-01-25 21:10 | 2010-01-25 | 2010-01-25 22:34 | Calculated | 01N01 | 01N01 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5933 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 3 | 24329 | 252 | 0.01036 | 0.00012331 | 15 | 1260 | 2009/2010 | January-2010 | 1 | 2010
22794 | Lightning Waihaha Road | 2010-01-25 21:20 | 2010-01-25 | 2010-01-26 | Calculated | 04Q04 | 04Q04 - 1 Phase : 15.00 kVA : POLEMNT |  | 124SEG5610-5535 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 4 | 24329 | 640 | 0.02631 | 0.00016441 | 15 | 2400 | 2009/2010 | January-2010 | 1 | 2010
22795 | Lightning Ahuroa Road | 2010-01-25 21:55 | 2010-01-25 | 2010-01-26 00:11 | Calculated | T661 | T661 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 2 | 24329 | 272 | 0.01118 | 8.2206e-05 | 15 | 2040 | 2009/2010 | January-2010 | 1 | 2010
22796 | Lightning Oio #1 Road | 2010-01-26 06:48 | 2010-01-26 | 2010-01-26 10:24 | Calculated | 12H06 | 12H06 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 216 | 2 | 24329 | 432 | 0.01776 | 8.2206e-05 | 10 | 2160 | 2009/2010 | January-2010 | 1 | 2010
22797 | Lightning Raetihi Road | 2010-01-26 07:10 | 2010-01-26 | 2010-01-26 08:01 | Calculated | 20K03 | 20K03 - 3 Phase : 50.00 kVA : POLEMNT |  | 416SEG5672-5718 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 8 | 24329 | 408 | 0.01677 | 0.00032883 | 50 | 2550 | 2009/2010 | January-2010 | 1 | 2010
22798 | Lightning SH49 | 2010-01-26 08:05 | 2010-01-26 | 2010-01-26 09:04 | Calculated | 21O17 | 21O17 - 5709-5796ph 5kVA POLEMNT |  | 416SEG5709-5796 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 1 | 24329 | 59 | 0.00243 | 4.1103e-05 | 5 | 295 | 2009/2010 | January-2010 | 1 | 2010
22821 | Xarm & Pole Top On Fire - Mapara Road | 2010-01-26 08:10 | 2010-01-26 | 2010-01-26 10:36 | Calculated | 1297 | 1297 - Fused Link 1297 |  | 117SEG1297-1296 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 73 | 24329 | 10658 | 0.43808 | 0.0030005 | 540.5 | 78912 | 2009/2010 | January-2010 | 1 | 2010
22822 | Xarm & Pole Top On Fire - SH4 | 2010-01-26 08:10 | 2010-01-26 | 2010-01-26 10:38 | Calculated | 1728 | 1728 - Recloser 1728 |  | No Segment | No Asset Group | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 43 | 24329 | 6364 | 0.26158 | 0.0017674 | 335.5 | 49654 | 2009/2010 | January-2010 | 1 | 2010
22823 | Xarm & Pole Top On Fire - Mapara Road | 2010-01-26 08:10 | 2010-01-26 | 2010-01-26 13:38 | Calculated | 1296 | 1296 - Fused Link 1296 |  | 117SEG1296-1273 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 328 | 66 | 24329 | 21648 | 0.8898 | 0.0027128 | 500.5 | 164163 | 2009/2010 | January-2010 | 1 | 2010
22799 | Lightning Raetihi Road | 2010-01-26 08:40 | 2010-01-26 | 2010-01-26 14:11 | Calculated | 20K18 | 20K18 - 3 Phase : 30.00 kVA : POLEMNT |  | 416SEG5956-5672 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 331 | 1 | 24329 | 331 | 0.01361 | 4.1103e-05 | 30 | 9930 | 2009/2010 | January-2010 | 1 | 2010
22800 | Lightning Pukehou Road | 2010-01-26 08:50 | 2010-01-26 | 2010-01-26 09:07 | Calculated | 08K15 | 08K15 - 1 Phase : 10.00 kVA : POLEMNT |  | 407SEG5868-5126 | Manunui 407-01 (was Affco) | Rural B | Manunui | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 3 | 24329 | 51 | 0.0021 | 0.00012331 | 10 | 169 | 2009/2010 | January-2010 | 1 | 2010
22802 | Gadsby Road Feeder Renewal Project | 2010-01-26 09:01 | 2010-01-26 | 2010-01-26 16:19 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22801 | Lightning SH32 | 2010-01-26 09:08 | 2010-01-26 | 2010-01-26 12:49 | Calculated | 02Q05 | 02Q05 - 1 Phase : 3.00 kVA : POLEMNT |  | 124SEG1283 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 1 | 24329 | 221 | 0.00908 | 4.1103e-05 | 3 | 663 | 2009/2010 | January-2010 | 1 | 2010
22804 | Lightning Tahaia Bush Road | 2010-01-26 09:10 | 2010-01-26 | 2010-01-26 09:57 | Calculated | 587 | 587 - Fused Link 587 |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 13 | 24329 | 611 | 0.02511 | 0.00053434 | 100 | 4699 | 2009/2010 | January-2010 | 1 | 2010
22805 | Lightning SH47 | 2010-01-26 09:10 | 2010-01-26 | 2010-01-26 10:31 | Calculated | 12N06 | 12N06 - 3 Phase : 100.00 kVA : POLEMNT |  | 609SEG5159-6761 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 2 | 24329 | 162 | 0.00666 | 8.2206e-05 | 100 | 8100 | 2009/2010 | January-2010 | 1 | 2010
22806 | Lightning Tihoi Road | 2010-01-26 09:10 | 2010-01-26 | 2010-01-26 11:00 | Calculated | 580 | 580 - Fused Link 580 |  | 120SEG481-422 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 8 | 24329 | 880 | 0.03617 | 0.00032883 | 125 | 13749 | 2009/2010 | January-2010 | 1 | 2010
22808 | Lightning Oio #1 Road | 2010-01-26 09:30 | 2010-01-26 | 2010-01-26 12:39 | Calculated | 12H13 | 12H13 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | u | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 189 | 1 | 24329 | 189 | 0.00777 | 4.1103e-05 | 10 | 1890 | 2009/2010 | January-2010 | 1 | 2010
22809 | Lightning SH47 | 2010-01-26 10:15 | 2010-01-26 | 2010-01-26 11:30 | Calculated | 12N05 | 12N05 - 3 Phase : 200.00 kVA : POLEMNT |  | 609SEG5159-6761 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 5 | 24329 | 375 | 0.01541 | 0.00020552 | 200 | 15000 | 2009/2010 | January-2010 | 1 | 2010
22810 | Replace Faulty Link 593 | 2010-01-26 11:13 | 2010-01-26 | 2010-01-26 13:02 | Calculated | 5110 | 5110 - Fused Link 5110 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 109 | 16 | 24329 | 1744 | 0.07168 | 0.00065765 | 135.5 | 14769 | 2009/2010 | January-2010 | 1 | 2010
22811 | Lightning Whangamata Road | 2010-01-26 13:30 | 2010-01-26 | 2010-01-26 14:41 | Calculated | T2925 | T2925 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG744 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 2 | 24329 | 142 | 0.00584 | 8.2206e-05 | 15 | 1065 | 2009/2010 | January-2010 | 1 | 2010
22812 | Lightning - Whangamata Road | 2010-01-26 13:40 | 2010-01-26 | 2010-01-26 14:28 | Calculated | T2998 | T2998 - 3 Phase : 15.00 kVA : POLEMNT |  | 123SEG744 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 1 | 24329 | 48 | 0.00197 | 4.1103e-05 | 15 | 720 | 2009/2010 | January-2010 | 1 | 2010
22813 | Lightning - Huirimu Road | 2010-01-26 13:42 | 2010-01-26 | 2010-01-26 14:53 | Calculated | T2296 | T2296 - 3ph 50kVA polemnt |  | 121SEG724-425RET | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 3 | 24329 | 213 | 0.00875 | 0.00012331 | 50 | 3549 | 2009/2010 | January-2010 | 1 | 2010
22848 | Lightning - Kawakawa Road | 2010-01-26 13:43 | 2010-01-26 | 2010-01-26 20:30 | Calculated | T3056 | T3056 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG468 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 407 | 1 | 24329 | 407 | 0.01673 | 4.1103e-05 | 15 | 6105 | 2009/2010 | January-2010 | 1 | 2010
22849 | Lightning - Kawakawa Road | 2010-01-26 13:43 | 2010-01-26 | 2010-01-26 20:41 | Calculated | T1272 | T1272 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG468 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 418 | 3 | 24329 | 1254 | 0.05154 | 0.00012331 | 15 | 6270 | 2009/2010 | January-2010 | 1 | 2010
22850 | Lightning - Kawakawa Road | 2010-01-26 13:44 | 2010-01-26 | 2010-01-26 20:55 | Calculated | T3246 | T3246 - 3 Phase : 30.00 kVA : POLEMNT |  | 123SEG468 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22814 | Lightning - Whangamata Road | 2010-01-26 13:47 | 2010-01-26 | 2010-01-26 15:22 | Calculated | T1105 | T1105 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 3 | 24329 | 285 | 0.01171 | 0.00012331 | 15 | 1425 | 2009/2010 | January-2010 | 1 | 2010
22815 | Lightning - Whangamata Road | 2010-01-26 13:49 | 2010-01-26 | 2010-01-26 15:51 | Calculated | T2746 | T2746 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 3 | 24329 | 366 | 0.01504 | 0.00012331 | 10 | 1219 | 2009/2010 | January-2010 | 1 | 2010
22816 | Lightning - Whangamata Road | 2010-01-26 13:52 | 2010-01-26 | 2010-01-26 16:11 | Calculated | 145 | 145 - Fused Link 145 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 7 | 24329 | 973 | 0.03999 | 0.00028772 | 25 | 3475 | 2009/2010 | January-2010 | 1 | 2010
22817 | Lightning - Puketawai Road | 2010-01-26 13:55 | 2010-01-26 | 2010-01-26 15:19 | Calculated | T1429 | T1429 - 1 Phase : 10.00 kVA : POLEMNT |  | 110SEG554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 1 | 24329 | 84 | 0.00345 | 4.1103e-05 | 10 | 840 | 2009/2010 | January-2010 | 1 | 2010
22824 | SWER Backfeed - SH4 | 2010-01-26 13:55 | 2010-01-26 | 2010-01-26 13:59 | Calculated | 1728 | 1728 - Recloser 1728 |  | No Segment | No Asset Group | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 43 | 24329 | 172 | 0.00707 | 0.0017674 | 335.5 | 1342 | 2009/2010 | January-2010 | 1 | 2010
22825 | Lightning - Whangamata Road | 2010-01-26 14:15 | 2010-01-26 | 2010-01-26 16:25 | Calculated | T1269 | T1269 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG145-553 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 2 | 24329 | 260 | 0.01069 | 8.2206e-05 | 10 | 1300 | 2009/2010 | January-2010 | 1 | 2010
22826 | Lightning - Waihora Road | 2010-01-26 14:15 | 2010-01-26 | 2010-01-26 18:00 | Calculated | T1103 | T1103 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 225 | 2 | 24329 | 450 | 0.0185 | 8.2206e-05 | 15 | 3375 | 2009/2010 | January-2010 | 1 | 2010
22818 | Lightning - Waitaanga | 2010-01-26 14:30 | 2010-01-26 | 2010-01-26 15:30 | Calculated | 5560 | 5560 - Sectionaliser with Bypass & Links 5560 |  | 413SEG5306-5560 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 25 | 24329 | 1500 | 0.06165 | 0.0010276 | 145 | 8699 | 2009/2010 | January-2010 | 1 | 2010
22827 | Lightning - Burn Street | 2010-01-26 14:35 | 2010-01-26 | 2010-01-26 16:20 | Calculated | 20K02 | 20K02 - 3ph 15kVA POL |  | THUVVK | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 2 | 24329 | 210 | 0.00863 | 8.2206e-05 | 15 | 1575 | 2009/2010 | January-2010 | 1 | 2010
22828 | Lightning - Lower Burns Street | 2010-01-26 14:35 | 2010-01-26 | 2010-01-26 16:30 | Calculated | 397 | 397 - Air Break Switch 397 |  | 109SEG397-345 | Gravel Scoop 109-12 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 104 | 24329 | 11960 | 0.49159 | 0.0042747 | 1035 | 119024 | 2009/2010 | January-2010 | 1 | 2010
22829 | Lightning - Koporotuku Road | 2010-01-26 14:55 | 2010-01-26 | 2010-01-26 16:52 | Calculated | 5694 | 5694 - Fused Link 5694 |  | 416SEG5694 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 9 | 24329 | 1053 | 0.04328 | 0.00036993 | 40 | 4680 | 2009/2010 | January-2010 | 1 | 2010
22830 | Lightning - Koporotuku Road | 2010-01-26 14:55 | 2010-01-26 | 2010-01-26 17:24 | Calculated | 21L04 | 21L04 - 1 Phase : 10.00 kVA : POLEMNT |  | 416SEG5694 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 1 | 24329 | 149 | 0.00612 | 4.1103e-05 | 10 | 1490 | 2009/2010 | January-2010 | 1 | 2010
22819 | Line Down - Otukou | 2010-01-26 15:13 | 2010-01-26 | 2010-01-26 16:07 | Calculated | 5160 | 5160 - Air Break Switch 5160 |  | 609SEG5159-6761 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22820 | Line Down - Tawahi Sub | 2010-01-26 15:13 | 2010-01-26 | 2010-01-26 20:52 | Calculated | 6007 | 6007 - Circuit Breaker 6007 |  | No Segment | 513-01 Tawhai | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22831 | Lightning - Whangamata Road | 2010-01-26 15:35 | 2010-01-26 | 2010-01-26 17:08 | Calculated | T2781 | T2781 - 2ph 15kVA POLEMNT |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 2 | 24329 | 186 | 0.00765 | 8.2206e-05 | 15 | 1395 | 2009/2010 | January-2010 | 1 | 2010
22832 | Lightning - Waihora Road | 2010-01-26 15:45 | 2010-01-26 | 2010-01-26 18:42 | Calculated | T817 | T817 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 2 | 24329 | 354 | 0.01455 | 8.2206e-05 | 10 | 1770 | 2009/2010 | January-2010 | 1 | 2010
22833 | Lightning - Hingarae Road | 2010-01-26 16:10 | 2010-01-26 | 2010-01-26 17:36 | Calculated | T4153 | T4153 - 1 Phase : 15.00 kVA : POLEMNT |  | 124SEG5536 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 1 | 24329 | 86 | 0.00353 | 4.1103e-05 | 15 | 1290 | 2009/2010 | January-2010 | 1 | 2010
22834 | Lightning - Waihora Road | 2010-01-26 16:10 | 2010-01-26 | 2010-01-26 18:56 | Calculated | T930 | T930 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 3 | 24329 | 498 | 0.02047 | 0.00012331 | 10 | 1659 | 2009/2010 | January-2010 | 1 | 2010
22835 | Branch on Line - Wairere Falls | 2010-01-26 16:15 | 2010-01-26 | 2010-01-26 17:52 | Calculated | 682 | 682 - Circuit Breaker 682 |  | No Segment | 207-01 Wairere Falls | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 174 | 24329 | 16878 | 0.69374 | 0.007152 | 1510.5 | 146518 | 2009/2010 | January-2010 | 1 | 2010
22836 | Branch on Line - Kohua Road | 2010-01-26 16:15 | 2010-01-26 | 2010-01-26 18:11 | Calculated | 1701 | 1701 - Air Break Switch 1701 |  | 115SEG1701-1710 | Mokauiti 115-01 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 166 | 24329 | 19256 | 0.79148 | 0.0068231 | 1165.5 | 135197 | 2009/2010 | January-2010 | 1 | 2010
22837 | Branch on Line - Mokauiti Road | 2010-01-26 16:15 | 2010-01-26 | 2010-01-26 18:29 | Calculated | 1710 | 1710 - Air Break Switch 1710 |  | 115SEGTempABS1-1705 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 140 | 24329 | 18760 | 0.7711 | 0.0057544 | 1015.5 | 136076 | 2009/2010 | January-2010 | 1 | 2010
22839 | Branch on Line - Mokauiti Road | 2010-01-26 16:15 | 2010-01-26 | 2010-01-26 19:30 | Calculated | 1705 | 1705 - Air Break Switch 1705 |  | 115SEG1705-1707 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 195 | 120 | 24329 | 23400 | 0.96182 | 0.0049324 | 875.5 | 170722 | 2009/2010 | January-2010 | 1 | 2010
22840 | Branch on Line - Mokauiti Road | 2010-01-26 16:15 | 2010-01-26 | 2010-01-26 19:35 | Calculated | 1707 | 1707 - Air Break Switch 1707 |  | 115SEG1705-1707 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 200 | 79 | 24329 | 15800 | 0.64943 | 0.0032472 | 558 | 111599 | 2009/2010 | January-2010 | 1 | 2010
22841 | Lightning - Tuhua Sub | 2010-01-26 17:14 | 2010-01-26 | 2010-01-26 18:00 | Calculated | 5820 | 5820 - Circuit Breaker 5820 |  | 421SEG5820-5821 | 502-01 Tuhua | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 46 | 261 | 24329 | 12006 | 0.49349 | 0.010728 | 1809.5 | 83236 | 2009/2010 | January-2010 | 1 | 2010
22842 | Lightning - Ohura Road | 2010-01-26 17:14 | 2010-01-26 | 2010-01-26 18:44 | Calculated | 6640 | 6640 - Air Break Switch 6640 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 243 | 24329 | 21870 | 0.89893 | 0.0099881 | 1708.5 | 153764 | 2009/2010 | January-2010 | 1 | 2010
22843 | Lightning - Ongarue/Tapuwahine Sub | 2010-01-26 17:14 | 2010-01-26 | 2010-01-26 18:51 | Calculated | 5462 | 5462 - Sectionaliser with Bypass & Links 5462 |  | 421SEG6554-5462RET | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 120 | 24329 | 11640 | 0.47844 | 0.0049324 | 857.5 | 83177 | 2009/2010 | January-2010 | 1 | 2010
22844 | Lightning - Tapuwahine Sub | 2010-01-26 17:14 | 2010-01-26 | 2010-01-26 19:00 | Calculated | 5465 | 5465 - Recloser 5465 |  | No Segment | No Asset Group | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 38 | 24329 | 4028 | 0.16556 | 0.0015619 | 255.5 | 27083 | 2009/2010 | January-2010 | 1 | 2010
22851 | Lightning - SH32 | 2010-01-26 17:15 | 2010-01-26 | 2010-01-26 22:59 | Calculated | 02Q04 | 02Q04 - 1 Phase : 10.00 kVA : POLEMNT |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 344 | 1 | 24329 | 344 | 0.01414 | 4.1103e-05 | 10 | 3440 | 2009/2010 | January-2010 | 1 | 2010
22846 | Lightning - Raurimu Township | 2010-01-26 17:22 | 2010-01-26 | 2010-01-26 20:05 | Calculated | 5829 | 5829 - Fused Link 5829 |  | 410SEG5829-5545 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 22 | 24329 | 3586 | 0.1474 | 0.00090427 | 115 | 18744 | 2009/2010 | January-2010 | 1 | 2010
22875 | Lightning SH47 | 2010-01-26 17:37 | 2010-01-26 | 2010-01-27 09:13 | Calculated | 14N02 | 14N02 - 3 Phase : 15.00 kVA : POLEMNT |  | 609SEG5158-5159 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 936 | 2 | 24329 | 1872 | 0.07695 | 8.2206e-05 | 15 | 14040 | 2009/2010 | January-2010 | 1 | 2010
22847 | Lightning - Maihiihi Road | 2010-01-26 17:40 | 2010-01-26 | 2010-01-26 20:06 | Calculated | T1335 | T1335 - 3ph 10kVA polemnt |  | 111SEG351-647 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 1 | 24329 | 146 | 0.006 | 4.1103e-05 | 10 | 1460 | 2009/2010 | January-2010 | 1 | 2010
22876 | Lightning Whangamata Road | 2010-01-26 17:41 | 2010-01-26 | 2010-01-27 01:14 | Calculated | T1106 | T1106 - 1 Phase : 5.00 kVA : POLEMNT |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 453 | 1 | 24329 | 453 | 0.01862 | 4.1103e-05 | 5 | 2265 | 2009/2010 | January-2010 | 1 | 2010
22877 | Lightning Mangaotaki Road | 2010-01-26 17:46 | 2010-01-26 | 2010-01-27 09:28 | Calculated | T1693 | T1693 - 1 Phase : 10.00 kVA : POLEMNT |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 942 | 1 | 24329 | 942 | 0.03872 | 4.1103e-05 | 10 | 9420 | 2009/2010 | January-2010 | 1 | 2010
22852 | Lightning - Wall Road | 2010-01-26 17:54 | 2010-01-26 | 2010-01-26 21:12 | Calculated | T372 | T372 - 1 Phase : 5.00 kVA : POLEMNT |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 3 | 24329 | 594 | 0.02442 | 0.00012331 | 5 | 989 | 2009/2010 | January-2010 | 1 | 2010
22853 | Lightning - Wall Road | 2010-01-26 17:54 | 2010-01-26 | 2010-01-26 21:12 | Calculated | T1326 | T1326 - 3ph 25kVA POLEMNT |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 5 | 24329 | 990 | 0.04069 | 0.00020552 | 25 | 4950 | 2009/2010 | January-2010 | 1 | 2010
22878 | Lightning Faulty TX- Whangamata Road | 2010-01-26 17:54 | 2010-01-26 | 2010-01-27 11:34 | Calculated | T1105 | T1105 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1060 | 3 | 24329 | 3180 | 0.13071 | 0.00012331 | 15 | 15900 | 2009/2010 | January-2010 | 1 | 2010
22854 | Lightning - Whangamata Road | 2010-01-26 17:58 | 2010-01-26 | 2010-01-26 21:19 | Calculated | T1128 | T1128 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG744 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 201 | 2 | 24329 | 402 | 0.01652 | 8.2206e-05 | 10 | 2010 | 2009/2010 | January-2010 | 1 | 2010
22855 | Lightning - Mangawhero Road | 2010-01-26 18:05 | 2010-01-26 | 2010-01-26 22:00 | Calculated | 302 | 302 - Fused Link 302 |  | 109SEG302 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 235 | 7 | 24329 | 1645 | 0.06761 | 0.00028772 | 50 | 11750 | 2009/2010 | January-2010 | 1 | 2010
22857 | Lightning - Mangawhero Road | 2010-01-26 18:05 | 2010-01-26 | 2010-01-26 22:21 | Calculated | T492 | T492 - 3ph 25kVA POLEMNT |  | 109SEG302 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 256 | 2 | 24329 | 512 | 0.02104 | 8.2206e-05 | 25 | 6400 | 2009/2010 | January-2010 | 1 | 2010
22838 | Branch on Line - Wairere Falls | 2010-01-26 18:43 | 2010-01-26 | 2010-01-26 19:06 | Calculated | 682 | 682 - Circuit Breaker 682 |  | No Segment | 207-01 Wairere Falls | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 174 | 24329 | 4002 | 0.1645 | 0.007152 | 1510.5 | 34741 | 2009/2010 | January-2010 | 1 | 2010
22879 | Lightning Mangaokewa Road | 2010-01-26 18:53 | 2010-01-26 | 2010-01-27 10:50 | Calculated | T141 | T141 - 1 Phase : 15.00 kVA : POLEMNT |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 957 | 2 | 24329 | 1914 | 0.07867 | 8.2206e-05 | 15 | 14355 | 2009/2010 | January-2010 | 1 | 2010
22845 | Lightning - Hangatiki | 2010-01-26 19:23 | 2010-01-26 | 2010-01-26 19:25 | Calculated | TPHangatiki CB232 | TPHangatiki CB232 - 33kV Minimum Oil Circuit Breaker TP232 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Waitete 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 1930 | 24329 | 3860 | 0.15866 | 0.079329 | 16246.5 | 32493 | 2009/2010 | January-2010 | 1 | 2010
22858 | Lightning - Mahoe Road | 2010-01-26 19:23 | 2010-01-26 | 2010-01-26 22:55 | Calculated | 289 | 289 - Fused Link 289 |  | 101SEG289-552 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 212 | 14 | 24329 | 2968 | 0.12199 | 0.00057544 | 105 | 22259 | 2009/2010 | January-2010 | 1 | 2010
22860 | Lightning - Waitomo Valley Road | 2010-01-26 19:24 | 2010-01-26 | 2010-01-26 22:17 | Calculated | T1399 | T1399 - 3ph 25kVA POLEMNT |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 173 | 3 | 24329 | 519 | 0.02133 | 0.00012331 | 25 | 4324 | 2009/2010 | January-2010 | 1 | 2010
22861 | Lightning - SH30 | 2010-01-26 19:31 | 2010-01-26 | 2010-01-26 22:42 | Calculated | T23 | T23 - 1 Phase : 25.00 kVA : POLEMNT |  | 103SEG282-728 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 5 | 24329 | 955 | 0.03925 | 0.00020552 | 25 | 4775 | 2009/2010 | January-2010 | 1 | 2010
22880 | Lightning Mokauiti Road | 2010-01-26 19:34 | 2010-01-26 | 2010-01-27 01:11 | Calculated | T1993 | T1993 - 3ph 50kVA POLEMNT |  | 114SEG1107-1116 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 337 | 5 | 24329 | 1685 | 0.06926 | 0.00020552 | 50 | 16850 | 2009/2010 | January-2010 | 1 | 2010
22881 | Lightning Te Anga Road | 2010-01-26 19:37 | 2010-01-26 | 2010-01-27 00:31 | Calculated | T508 | T508 - 1 Phase : 15.00 kVA : POLEMNT |  | 101SEG274-506 | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 294 | 3 | 24329 | 882 | 0.03625 | 0.00012331 | 15 | 4410 | 2009/2010 | January-2010 | 1 | 2010
22882 | Lightning Ongarue Road | 2010-01-26 19:44 | 2010-01-26 | 2010-01-27 11:00 | Calculated | 04J07 | 04J07 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5657-5473 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 916 | 2 | 24329 | 1832 | 0.0753 | 8.2206e-05 | 15 | 13740 | 2009/2010 | January-2010 | 1 | 2010
22862 | Lightning - Mangahauhau Valley Road | 2010-01-26 19:48 | 2010-01-26 | 2010-01-26 23:14 | Calculated | 5717 | 5717 - Fused Link 5717 |  | 416SEG5717 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 206 | 5 | 24329 | 1030 | 0.04234 | 0.00020552 | 45 | 9270 | 2009/2010 | January-2010 | 1 | 2010
22863 | Lightning - Ngahape Road | 2010-01-26 19:53 | 2010-01-26 | 2010-01-26 23:47 | Calculated | T607 | T607 - 3ph 25kVA polemnt |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 234 | 7 | 24329 | 1638 | 0.06733 | 0.00028772 | 25 | 5849 | 2009/2010 | January-2010 | 1 | 2010
22864 | Lightning - Te Anga Road | 2010-01-26 20:03 | 2010-01-26 | 2010-01-26 23:54 | Calculated | T510 | T510 - 1 Phase : 15.00 kVA : POLEMNT |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 4 | 24329 | 924 | 0.03798 | 0.00016441 | 15 | 3465 | 2009/2010 | January-2010 | 1 | 2010
22883 | Lightning Kie Kie Road | 2010-01-26 20:07 | 2010-01-26 | 2010-01-27 01:26 | Calculated | 1101 | 1101 - Fused Link 1101 |  | 114SEG1101 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 319 | 9 | 24329 | 2871 | 0.11801 | 0.00036993 | 67.5 | 21532 | 2009/2010 | January-2010 | 1 | 2010
22884 | Lightning Puketapu Road | 2010-01-26 20:33 | 2010-01-26 | 2010-01-27 01:06 | Calculated | T1278 | T1278 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 273 | 2 | 24329 | 546 | 0.02244 | 8.2206e-05 | 10 | 2730 | 2009/2010 | January-2010 | 1 | 2010
22885 | Lightning Mangarongo Road | 2010-01-26 21:19 | 2010-01-26 | 2010-01-27 08:53 | Calculated | T664 | T664 - 3 Phase : 50.00 kVA : POLEMNT |  | 111SEG342-544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 694 | 2 | 24329 | 1388 | 0.05705 | 8.2206e-05 | 7.5 | 5205 | 2009/2010 | January-2010 | 1 | 2010
22886 | Lightning Hangatiki East Road | 2010-01-27 05:45 | 2010-01-27 | 2010-01-27 08:27 | Calculated | T462 | T462 - 3ph 25kVA POLEMNT |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 3 | 24329 | 486 | 0.01998 | 0.00012331 | 25 | 4049 | 2009/2010 | January-2010 | 1 | 2010
22887 | Lightning Hangatiki East Road | 2010-01-27 05:46 | 2010-01-27 | 2010-01-27 10:16 | Calculated | T118 | T118 - 3ph 15kVA POLEMNT |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 3 | 24329 | 810 | 0.03329 | 0.00012331 | 15 | 4050 | 2009/2010 | January-2010 | 1 | 2010
22888 | Lightning Main Sth Road, Otorohanga | 2010-01-27 05:50 | 2010-01-27 | 2010-01-27 09:27 | Calculated | T165 | T165 - 3 Phase : 100.00 kVA : POLEMNT |  | 110SEG1344 | McDonalds 110-01 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 3 | 24329 | 651 | 0.02676 | 0.00012331 | 100 | 21699 | 2009/2010 | January-2010 | 1 | 2010
22906 | Lightning - Scott Road | 2010-01-27 09:20 | 2010-01-27 | 2010-01-27 13:14 | Calculated | T922 | T922 - 3ph 25kVA POLEMNT |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 234 | 2 | 24329 | 468 | 0.01924 | 8.2206e-05 | 25 | 5850 | 2009/2010 | January-2010 | 1 | 2010
22907 | Lightning - Okau Road | 2010-01-27 09:20 | 2010-01-27 | 2010-01-27 14:13 | Calculated | T3190 | T3190 - 1 Phase : 15.00 kVA : POLEMNT |  | 128SEG1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 293 | 1 | 24329 | 293 | 0.01204 | 4.1103e-05 | 15 | 4395 | 2009/2010 | January-2010 | 1 | 2010
22908 | Lightning - Scott Road | 2010-01-27 09:35 | 2010-01-27 | 2010-01-27 12:43 | Calculated | T1802 | T1802 - 3ph 15kVA POLEMNT |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22889 | Broken DDO at Tx1115 Waihora Road | 2010-01-27 09:49 | 2010-01-27 | 2010-01-27 10:16 | Calculated | 436 | 436 - Solid Link 436 |  | 123SEG436 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 4 | 24329 | 108 | 0.00444 | 0.00016441 | 65 | 1755 | 2009/2010 | January-2010 | 1 | 2010
22923 | Lightning - Waihora Road | 2010-01-27 09:50 | 2010-01-27 | 2010-01-27 18:29 | Calculated | T970 | T970 - 3ph 10kVA POLEMNT |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 519 | 1 | 24329 | 519 | 0.02133 | 4.1103e-05 | 10 | 5190 | 2009/2010 | January-2010 | 1 | 2010
22909 | Lightning - Wharepapa Road | 2010-01-27 10:15 | 2010-01-27 | 2010-01-27 12:09 | Calculated | 375 | 375 - Fused Link 375 |  | 122SEG375 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 14 | 24329 | 1596 | 0.0656 | 0.00057544 | 95 | 10829 | 2009/2010 | January-2010 | 1 | 2010
22924 | Lightning - Whangamata Road | 2010-01-27 10:35 | 2010-01-27 | 2010-01-27 16:39 | Calculated | T896 | T896 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG450-469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 364 | 3 | 24329 | 1092 | 0.04488 | 0.00012331 | 15 | 5460 | 2009/2010 | January-2010 | 1 | 2010
22910 | Lightning - Tauraroa Road | 2010-01-27 11:10 | 2010-01-27 | 2010-01-27 12:50 | Calculated | T1362 | T1362 - 3 Phase : 25.00 kVA : POLEMNT |  | 111SEG399-374 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 2 | 24329 | 200 | 0.00822 | 8.2206e-05 | 25 | 2500 | 2009/2010 | January-2010 | 1 | 2010
22911 | Lightning - SH41 | 2010-01-27 11:11 | 2010-01-27 | 2010-01-27 13:13 | Calculated | 08Q04 | 08Q04 - 1 Phase : 5.00 kVA : POLEMNT |  | 406SEG5250-5249 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 1 | 24329 | 122 | 0.00501 | 4.1103e-05 | 5 | 610 | 2009/2010 | January-2010 | 1 | 2010
22925 | Lightning - Waihohonu Road | 2010-01-27 11:15 | 2010-01-27 | 2010-01-27 15:53 | Calculated | T586 | T586 - 3 Phase : 30.00 kVA : POLEMNT |  | 101SEG526 | Caves 101-03 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 278 | 3 | 24329 | 834 | 0.03428 | 0.00012331 | 30 | 8340 | 2009/2010 | January-2010 | 1 | 2010
22912 | Lightning - Scown Road | 2010-01-27 11:20 | 2010-01-27 | 2010-01-27 13:54 | Calculated | T235 | T235 - 3 Phase : 25.00 kVA : POLEMNT |  | 111SEG342-544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 3 | 24329 | 462 | 0.01899 | 0.00012331 | 25 | 3849 | 2009/2010 | January-2010 | 1 | 2010
22926 | Lightning - Hauturu Road | 2010-01-27 11:28 | 2010-01-27 | 2010-01-27 18:43 | Calculated | T1437 | T1437 - 1 Phase : 10.00 kVA : POLEMNT |  | 101SEG289-552 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 435 | 1 | 24329 | 435 | 0.01788 | 4.1103e-05 | 10 | 4350 | 2009/2010 | January-2010 | 1 | 2010
22913 | Broken Xarm - Waihora Road | 2010-01-27 11:57 | 2010-01-27 | 2010-01-27 13:01 | Calculated | 806 | 806 - Air Break Switch 806 |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 119 | 24329 | 7616 | 0.31304 | 0.0048913 | 915 | 58559 | 2009/2010 | January-2010 | 1 | 2010
22914 | Broken Xarm - Waihora Road | 2010-01-27 11:57 | 2010-01-27 | 2010-01-27 15:43 | Calculated | 446 | 446 - Recloser 446 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 226 | 163 | 24329 | 36838 | 1.5142 | 0.0066998 | 1380 | 311879 | 2009/2010 | January-2010 | 1 | 2010
22927 | Lightning/Faulty Tx - Whangamata Road | 2010-01-27 12:15 | 2010-01-27 | 2010-01-27 18:02 | Calculated | T601 | T601 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 347 | 2 | 24329 | 694 | 0.02853 | 8.2206e-05 | 15 | 5205 | 2009/2010 | January-2010 | 1 | 2010
22902 | Broken DDO - Seafund Road | 2010-01-27 13:35 | 2010-01-27 | 2010-01-27 14:51 | Calculated | 372 | 372 - Fused Link 372 |  | 122SEG372 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 21 | 24329 | 1596 | 0.0656 | 0.00086317 | 133 | 10107 | 2009/2010 | January-2010 | 1 | 2010
22868 | Faulty TX 14M4 | 2010-01-27 14:11 | 2010-01-27 | 2010-01-27 16:17 | Calculated | 5148 | 5148 - Air Break Switch 5148 |  | 411SEG5148-5373 | 513-01 Tawhai | Rural D | National Park | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 112 | 24329 | 14112 | 0.58005 | 0.0046036 | 217.9126 | 27456 | 2009/2010 | January-2010 | 1 | 2010
22915 | Line Down - SH32 | 2010-01-27 14:16 | 2010-01-27 | 2010-01-27 20:06 | Calculated | 5531 | 5531 - Sectionaliser 5531 |  | 426SEG5531 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 350 | 13 | 24329 | 4550 | 0.18702 | 0.00053434 | 125 | 43749 | 2009/2010 | January-2010 | 1 | 2010
22928 | Lightning - Ropiha Road | 2010-01-27 15:00 | 2010-01-27 | 2010-01-27 19:00 | Calculated | T1117 | T1117 - 1 Phase : 10.00 kVA : POLEMNT |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 240 | 2 | 24329 | 480 | 0.01973 | 8.2206e-05 | 10 | 2400 | 2009/2010 | January-2010 | 1 | 2010
22929 | Lightning - Moerangi Road | 2010-01-27 15:00 | 2010-01-27 | 2010-01-27 19:04 | Calculated | 10O03 | 10O03 - 1 Phase : 10.00 kVA : POLEMNT |  | 426SEG5242 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 244 | 1 | 24329 | 244 | 0.01003 | 4.1103e-05 | 10 | 2440 | 2009/2010 | January-2010 | 1 | 2010
22865 | Lightning- Ngapaenga Road | 2010-01-27 15:55 | 2010-01-27 | 2010-01-28 10:28 | Calculated | T576 | T576 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1113 | 2 | 24329 | 2226 | 0.0915 | 8.2206e-05 | 10 | 11130 | 2009/2010 | January-2010 | 1 | 2010
22866 | Lightning Ahuroa Road | 2010-01-27 16:00 | 2010-01-27 | 2010-01-28 09:29 | Calculated | T1587 | T1587 - 1 Phase : 7.50 kVA : POLEMNT |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1049 | 3 | 24329 | 3147 | 0.12935 | 0.00012331 | 7.5 | 7867 | 2009/2010 | January-2010 | 1 | 2010
22922 | Broken DDO - SH41 | 2010-01-27 16:36 | 2010-01-27 | 2010-01-27 17:00 | Calculated | 5250 | 5250 - Sectionaliser with Bypass & Links 5250 |  | 406SEG5617-5250 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 12 | 24329 | 288 | 0.01184 | 0.00049324 | 72.5 | 1740 | 2009/2010 | January-2010 | 1 | 2010
22891 | Lightning - Mairoa Road | 2010-01-27 17:00 | 2010-01-27 | 2010-01-28 14:17 | Calculated | T151 | T151 - 3ph 25kVA POLEMNT |  | 107SEG176-269 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1277 | 2 | 24329 | 2554 | 0.10498 | 8.2206e-05 | 25 | 31925 | 2009/2010 | January-2010 | 1 | 2010
22930 | Lightning - SH43 | 2010-01-27 17:00 | 2010-01-27 | 2010-01-27 19:11 | Calculated | 10C04 | 10C04 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 131 | 1 | 24329 | 131 | 0.00538 | 4.1103e-05 | 15 | 1965 | 2009/2010 | January-2010 | 1 | 2010
22916 | Lightning - Whangamata Road | 2010-01-27 17:02 | 2010-01-27 | 2010-01-28 16:32 | Calculated | T1385 | T1385 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1410 | 2 | 24329 | 2820 | 0.11591 | 8.2206e-05 | 10 | 14100 | 2009/2010 | January-2010 | 1 | 2010
22869 | Lightning Waituhi Road | 2010-01-27 17:05 | 2010-01-27 | 2010-01-28 09:01 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 956 | 21 | 24329 | 20076 | 0.82519 | 0.00086317 | 160 | 152960 | 2009/2010 | January-2010 | 1 | 2010
22870 | Lightning Waituhi Road | 2010-01-27 17:05 | 2010-01-27 | 2010-01-28 09:30 | Calculated | 07L06 | 07L06 - 1 Phase : 25.00 kVA : POLEMNT |  | 408SEG5485-5791 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 985 | 2 | 24329 | 1970 | 0.08097 | 8.2206e-05 | 25 | 24625 | 2009/2010 | January-2010 | 1 | 2010
22917 | Lightning - Whangamata Road | 2010-01-27 17:09 | 2010-01-27 | 2010-01-28 16:16 | Calculated | T903 | T903 - 1 Phase : 5.00 kVA : POLEMNT |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1387 | 2 | 24329 | 2774 | 0.11402 | 8.2206e-05 | 5 | 6935 | 2009/2010 | January-2010 | 1 | 2010
22867 | Lightning SH47 | 2010-01-27 17:10 | 2010-01-27 | 2010-01-28 17:10 | Calculated | 14M04 | 14M04 - 1 Phase : 15.00 kVA : POLEMNT |  | 411SEG5148-5373 | National Park 411-02 | Rural D | National Park | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1440 | 1 | 24329 | 1440 | 0.05919 | 4.1103e-05 | 15 | 21600 | 2009/2010 | January-2010 | 1 | 2010
22892 | Lightning - Barclay Road | 2010-01-27 17:12 | 2010-01-27 | 2010-01-28 13:10 | Calculated | T1963 | T1963 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1101 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1198 | 2 | 24329 | 2396 | 0.09848 | 8.2206e-05 | 10 | 11980 | 2009/2010 | January-2010 | 1 | 2010
22893 | Lightning - Paekaka Road | 2010-01-27 17:19 | 2010-01-27 | 2010-01-28 11:51 | Calculated | T1992 | T1992 - 1 Phase : 15.00 kVA : POLEMNT |  | 113SEG1505 | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1112 | 1 | 24329 | 1112 | 0.04571 | 4.1103e-05 | 15 | 16680 | 2009/2010 | January-2010 | 1 | 2010
22918 | Lightning - Okama Road | 2010-01-27 17:21 | 2010-01-27 | 2010-01-28 16:44 | Calculated | T771 | T771 - 3 Phase : 25.00 kVA : POLEMNT |  | 129SEG635-REG23J | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1403 | 4 | 24329 | 5612 | 0.23067 | 0.00016441 | 25 | 35075 | 2009/2010 | January-2010 | 1 | 2010
22871 | Lightning Whangamata Road | 2010-01-27 17:29 | 2010-01-27 | 2010-01-28 01:33 | Calculated | T601 | T601 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 484 | 2 | 24329 | 968 | 0.03979 | 8.2206e-05 | 15 | 7260 | 2009/2010 | January-2010 | 1 | 2010
22931 | Lightning - Raurimu Road | 2010-01-27 17:30 | 2010-01-27 | 2010-01-27 20:05 | Calculated | 13K04 | 13K04 - 1 Phase : 5.00 kVA : POLEMNT |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 1 | 24329 | 155 | 0.00637 | 4.1103e-05 | 5 | 775 | 2009/2010 | January-2010 | 1 | 2010
22919 | Lightning - Okama Road | 2010-01-27 17:35 | 2010-01-27 | 2010-01-28 16:21 | Calculated | T1716 | T1716 - 3 Phase : 25.00 kVA : POLEMNT |  | 129SEG635-451RET | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1366 | 4 | 24329 | 5464 | 0.22459 | 0.00016441 | 25 | 34150 | 2009/2010 | January-2010 | 1 | 2010
22920 | Lightning - Pokuru Road | 2010-01-27 17:36 | 2010-01-27 | 2010-01-28 17:24 | Calculated | T980 | T980 - 1 Phase : 10.00 kVA : POLEMNT |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1428 | 2 | 24329 | 2856 | 0.11739 | 8.2206e-05 | 10 | 14280 | 2009/2010 | January-2010 | 1 | 2010
22894 | Lightning/Faulty Carrier - SH41 | 2010-01-27 17:37 | 2010-01-27 | 2010-01-28 12:17 | Calculated | 08Q05 | 08Q05 - 1 Phase : 7.50 kVA : POLEMNT |  | 406SEG5250-5249 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1120 | 2 | 24329 | 2240 | 0.09207 | 8.2206e-05 | 7.5 | 8400 | 2009/2010 | January-2010 | 1 | 2010
22921 | Lightning - SH41 | 2010-01-27 17:37 | 2010-01-27 | 2010-01-28 17:26 | Calculated | 08Q14 | 08Q14 - 1 Phase : 15.00 kVA : POLEMNT |  | 406SEG5250-5249 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1429 | 1 | 24329 | 1429 | 0.05874 | 4.1103e-05 | 15 | 21435 | 2009/2010 | January-2010 | 1 | 2010
22932 | Lightning - Kaitieke Road | 2010-01-27 17:45 | 2010-01-27 | 2010-01-27 19:23 | Calculated | 13K07 | 13K07 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 2 | 24329 | 196 | 0.00806 | 8.2206e-05 | 10 | 980 | 2009/2010 | January-2010 | 1 | 2010
22895 | Lightning - Ropiha Road | 2010-01-27 18:12 | 2010-01-27 | 2010-01-28 13:42 | Calculated | T1117 | T1117 - 1 Phase : 10.00 kVA : POLEMNT |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1170 | 2 | 24329 | 2340 | 0.09618 | 8.2206e-05 | 10 | 11700 | 2009/2010 | January-2010 | 1 | 2010
22933 | Lightning - Otake Road | 2010-01-27 18:15 | 2010-01-27 | 2010-01-27 18:51 | Calculated | T2586 | T2586 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG528 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 1 | 24329 | 36 | 0.00148 | 4.1103e-05 | 10 | 360 | 2009/2010 | January-2010 | 1 | 2010
22896 | Lightning - Tirohanga Road | 2010-01-27 18:37 | 2010-01-27 | 2010-01-28 15:52 | Calculated | T788 | T788 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1275 | 1 | 24329 | 1275 | 0.05241 | 4.1103e-05 | 10 | 12750 | 2009/2010 | January-2010 | 1 | 2010
22934 | Lightning - Waihohonu Road | 2010-01-27 18:51 | 2010-01-27 | 2010-01-27 20:27 | Calculated | T586 | T586 - 3 Phase : 30.00 kVA : POLEMNT |  | 101SEG526 | Caves 101-03 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 3 | 24329 | 288 | 0.01184 | 0.00012331 | 30 | 2880 | 2009/2010 | January-2010 | 1 | 2010
22897 | Lightning - SH30 | 2010-01-27 18:56 | 2010-01-27 | 2010-01-28 12:54 | Calculated | T714 | T714 - 3 Phase : 30.00 kVA : POLEMNT |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1078 | 3 | 24329 | 3234 | 0.13293 | 0.00012331 | 30 | 32340 | 2009/2010 | January-2010 | 1 | 2010
22898 | Lightning - Aotearoa Road | 2010-01-27 20:14 | 2010-01-27 | 2010-01-28 12:03 | Calculated | T951 | T951 - 1 Phase : 25.00 kVA : POLEMNT |  | 122SEG375 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 949 | 1 | 24329 | 949 | 0.03901 | 4.1103e-05 | 10 | 9490 | 2009/2010 | January-2010 | 1 | 2010
22899 | Lightning - Wharepapa Road | 2010-01-27 20:14 | 2010-01-27 | 2010-01-28 12:03 | Calculated | T952 | T952 - 1 Phase : 25.00 kVA : POLEMNT |  | 122SEG375 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 949 | 6 | 24329 | 5694 | 0.23404 | 0.00024662 | 25 | 23724 | 2009/2010 | January-2010 | 1 | 2010
22900 | Lightning - Duncan Road | 2010-01-27 20:44 | 2010-01-27 | 2010-01-28 11:14 | Calculated | T419 | T419 - 1 Phase : 25.00 kVA : POLEMNT |  | 122SEG678-768 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 870 | 2 | 24329 | 1740 | 0.07152 | 8.2206e-05 | 25 | 21750 | 2009/2010 | January-2010 | 1 | 2010
22901 | Lightning - Newman Road | 2010-01-27 21:14 | 2010-01-27 | 2010-01-28 14:51 | Calculated | T360 | T360 - 3ph 25kVA POLEMNT |  | 122SEG372 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1057 | 3 | 24329 | 3171 | 0.13034 | 0.00012331 | 25 | 26424 | 2009/2010 | January-2010 | 1 | 2010
22903 | Lightning - Mangaokewa Road | 2010-01-27 22:57 | 2010-01-27 | 2010-01-28 11:32 | Calculated | T733 | T733 - 1 Phase : 10.00 kVA : POLEMNT |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 755 | 1 | 24329 | 755 | 0.03103 | 4.1103e-05 | 10 | 7550 | 2009/2010 | January-2010 | 1 | 2010
22904 | Lightning - Barclay Road | 2010-01-27 23:09 | 2010-01-27 | 2010-01-28 12:53 | Calculated | T1994 | T1994 - 1 Phase : 7.50 kVA : POLEMNT |  | 114SEG1101 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 824 | 1 | 24329 | 824 | 0.03387 | 4.1103e-05 | 7.5 | 6180 | 2009/2010 | January-2010 | 1 | 2010
22905 | Lightning - Barclay Road | 2010-01-27 23:10 | 2010-01-27 | 2010-01-28 13:22 | Calculated | T1330 | T1330 - 1 Phase : 5.00 kVA : POLEMNT |  | 114SEG1101 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 852 | 1 | 24329 | 852 | 0.03502 | 4.1103e-05 | 5 | 4260 | 2009/2010 | January-2010 | 1 | 2010
22944 | Lightning - Piawa Road | 2010-01-28 06:30 | 2010-01-28 | 2010-01-28 07:00 | Calculated | 06J04 | 06J04 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 3 | 24329 | 90 | 0.0037 | 0.00012331 | 15 | 450 | 2009/2010 | January-2010 | 1 | 2010
22945 | Lightning - Hauhangaroa | 2010-01-28 07:55 | 2010-01-28 | 2010-01-28 09:32 | Calculated | 5177 | 5177 - Air Break Switch 5177 |  | 426SEG5177 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 1 | 24329 | 97 | 0.00399 | 4.1103e-05 | 5 | 485 | 2009/2010 | January-2010 | 1 | 2010
22946 | Lightning - Waihora Road | 2010-01-28 08:23 | 2010-01-28 | 2010-01-28 10:11 | Calculated | T972 | T972 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 2 | 24329 | 216 | 0.00888 | 8.2206e-05 | 15 | 1620 | 2009/2010 | January-2010 | 1 | 2010
22942 | Broken DDO - Ahuroa Road | 2010-01-28 10:14 | 2010-01-28 | 2010-01-28 11:11 | Calculated | 256 | 256 - Fused Link 256 |  | 106SEG256 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 6 | 24329 | 342 | 0.01406 | 0.00024662 | 35 | 1995 | 2009/2010 | January-2010 | 1 | 2010
22950 | Lightning - Scott Road | 2010-01-28 11:25 | 2010-01-28 | 2010-01-28 12:42 | Calculated | T712 | T712 - 3ph 25kVA POLEMNT |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 3 | 24329 | 231 | 0.00949 | 0.00012331 | 25 | 1924 | 2009/2010 | January-2010 | 1 | 2010
22941 | Lightning - Owaewenga Road | 2010-01-28 11:50 | 2010-01-28 | 2010-01-29 11:11 | Calculated | T751 | T751 - 1 Phase : 5.00 kVA : POLEMNT |  | 106SEG256 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1401 | 1 | 24329 | 1401 | 0.05759 | 4.1103e-05 | 5 | 7005 | 2009/2010 | January-2010 | 1 | 2010
22951 | Lightning - Whangamata Road | 2010-01-28 11:50 | 2010-01-28 | 2010-01-28 14:05 | Calculated | T3298 | T3298 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 1 | 24329 | 135 | 0.00555 | 4.1103e-05 | 15 | 2025 | 2009/2010 | January-2010 | 1 | 2010
22952 | Lightning - Puketapu Road | 2010-01-28 12:45 | 2010-01-28 | 2010-01-28 13:39 | Calculated | T1276 | T1276 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 1 | 24329 | 54 | 0.00222 | 4.1103e-05 | 10 | 540 | 2009/2010 | January-2010 | 1 | 2010
22953 | Lightning - SH47 | 2010-01-28 13:00 | 2010-01-28 | 2010-01-28 14:38 | Calculated | T4065 | T4065 - 3ph 15kVA polemnt |  | 411SEG5146-5148 | National Park 411-02 | Rural D | National Park | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 1 | 24329 | 98 | 0.00403 | 4.1103e-05 | 15 | 1470 | 2009/2010 | January-2010 | 1 | 2010
22943 | Lightning/Faulty Tx - SH30 | 2010-01-28 14:56 | 2010-01-28 | 2010-01-29 14:24 | Calculated | T714 | T714 - 3 Phase : 30.00 kVA : POLEMNT |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1408 | 3 | 24329 | 4224 | 0.17362 | 0.00012331 | 30 | 42240 | 2009/2010 | January-2010 | 1 | 2010
22954 | Lightning - Otake Road | 2010-01-28 15:25 | 2010-01-28 | 2010-01-28 17:10 | Calculated | T819 | T819 - 1 Phase : 5.00 kVA : POLEMNT |  | 123SEG490-528 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 1 | 24329 | 105 | 0.00432 | 4.1103e-05 | 5 | 525 | 2009/2010 | January-2010 | 1 | 2010
22935 | Lightning - SH40 | 2010-01-28 16:55 | 2010-01-28 | 2010-01-28 23:45 | Calculated | 05F19 | 05F19 - 1 Phase : 15.00 kVA : POLEMNT |  | 422SEG5606 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 410 | 2 | 24329 | 820 | 0.0337 | 8.2206e-05 | 15 | 6150 | 2009/2010 | January-2010 | 1 | 2010
22955 | Lightning - Hangatiki (Taharoa A) | 2010-01-28 17:46 | 2010-01-28 | 2010-01-28 17:51 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22956 | Lightning - Hangatiki (Taharoa B) | 2010-01-28 17:46 | 2010-01-28 | 2010-01-28 17:52 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22936 | Lightning - Huirimu Road | 2010-01-28 17:53 | 2010-01-28 | 2010-01-28 22:30 | Calculated | T1711 | T1711 - 1 Phase : 15.00 kVA : polemnt |  | 121SEG724-425RET | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22937 | Lightning - Koiro Road | 2010-01-28 17:58 | 2010-01-28 | 2010-01-28 21:16 | Calculated | 10F03 | 10F03 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5771 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 3 | 24329 | 594 | 0.02442 | 0.00012331 | 15 | 2970 | 2009/2010 | January-2010 | 1 | 2010
22957 | Lightning - SH1 | 2010-01-28 18:00 | 2010-01-28 | 2010-01-28 19:31 | Calculated | 11S10 | 11S10 - 1 Phase : 15.00 kVA : POLEMNT |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 2 | 24329 | 182 | 0.00748 | 8.2206e-05 | 15 | 1365 | 2009/2010 | January-2010 | 1 | 2010
22958 | Lightning - Ngapaenga Road | 2010-01-28 18:00 | 2010-01-28 | 2010-01-28 19:00 | Calculated | T576 | T576 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 2 | 24329 | 120 | 0.00493 | 8.2206e-05 | 10 | 600 | 2009/2010 | January-2010 | 1 | 2010
22959 | Lightning - Ngapaenga Road | 2010-01-28 18:02 | 2010-01-28 | 2010-01-28 19:15 | Calculated | T1440 | T1440 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 1 | 24329 | 73 | 0.003 | 4.1103e-05 | 10 | 730 | 2009/2010 | January-2010 | 1 | 2010
22938 | Lightning - Waipuna Road | 2010-01-28 18:30 | 2010-01-28 | 2010-01-28 21:12 | Calculated | T2744 | T2744 - 1 Phase : 15.00 kVA : POLEMNT |  | 101SEG1272-257 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 1 | 24329 | 162 | 0.00666 | 4.1103e-05 | 15 | 2430 | 2009/2010 | January-2010 | 1 | 2010
22960 | Lightning - Te Anga Road | 2010-01-28 18:39 | 2010-01-28 | 2010-01-28 20:59 | Calculated | T510 | T510 - 1 Phase : 15.00 kVA : POLEMNT |  | 101SEG506-291 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 4 | 24329 | 560 | 0.02302 | 0.00016441 | 15 | 2100 | 2009/2010 | January-2010 | 1 | 2010
22961 | Lightning - Whangamata Road | 2010-01-28 18:50 | 2010-01-28 | 2010-01-28 19:28 | Calculated | T2834 | T2834 - 1 Phase : 5.00 kVA : POLEMNT |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 2 | 24329 | 76 | 0.00312 | 8.2206e-05 | 5 | 190 | 2009/2010 | January-2010 | 1 | 2010
22962 | Lightning - Wairoma Road | 2010-01-28 19:10 | 2010-01-28 | 2010-01-28 20:57 | Calculated | T1905 | T1905 - 1 Phase : 5.00 kVA : POLEMNT |  | 114SEG1106-1105 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24329 | 107 | 0.0044 | 4.1103e-05 | 5 | 535 | 2009/2010 | January-2010 | 1 | 2010
22963 | Lightning - Wairoma Road | 2010-01-28 19:11 | 2010-01-28 | 2010-01-28 20:57 | Calculated | T1906 | T1906 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1118 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 2 | 24329 | 212 | 0.00871 | 8.2206e-05 | 10 | 1060 | 2009/2010 | January-2010 | 1 | 2010
22964 | Lightning - Waitomo | 2010-01-28 19:30 | 2010-01-28 | 2010-01-28 20:42 | Calculated | T2798 | T2798 - 3 Phase : 25.00 kVA : POLEMNT |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 1 | 24329 | 72 | 0.00296 | 4.1103e-05 | 25 | 1800 | 2009/2010 | January-2010 | 1 | 2010
22965 | Jumper Off - Waipuna Road | 2010-01-28 19:52 | 2010-01-28 | 2010-01-28 20:50 | Calculated | 286 | 286 - Air Break Switch 286 |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 10 | 24329 | 580 | 0.02384 | 0.00041103 | 88 | 5104 | 2009/2010 | January-2010 | 1 | 2010
22939 | Lightning - Waitangata Road | 2010-01-28 20:24 | 2010-01-28 | 2010-01-28 23:32 | Calculated | 06E12 | 06E12 - 2ph 5kVA POLEMNT |  | 412SEG5256-5445 | Nihoniho 412-01 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 2 | 24329 | 376 | 0.01545 | 8.2206e-05 | 5 | 940 | 2009/2010 | January-2010 | 1 | 2010
22940 | Lightning - SH40 | 2010-01-28 22:27 | 2010-01-28 | 2010-01-28 23:17 | Calculated | 05F27 | 05F27 - 2 Phase : 15.00 kVA : POLEMNT |  | 412SEG5445-5257 | Nihoniho 412-01 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 3 | 24329 | 150 | 0.00617 | 0.00012331 | 15 | 750 | 2009/2010 | January-2010 | 1 | 2010
22967 | Gadsby Road Feeder Renewal Project | 2010-01-29 08:50 | 2010-01-29 | 2010-01-29 15:52 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22970 | Lightning - Waitanguru Road | 2010-01-29 09:05 | 2010-01-29 | 2010-01-29 12:30 | Calculated | T2480 | T2480 - 1 Phase : 3.00 kVA : POLEMNT |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 205 | 1 | 24329 | 205 | 0.00843 | 4.1103e-05 | 3 | 615 | 2009/2010 | January-2010 | 1 | 2010
22971 | Lightning - Mangaokewa Road | 2010-01-29 09:10 | 2010-01-29 | 2010-01-29 11:11 | Calculated | T733 | T733 - 1 Phase : 10.00 kVA : POLEMNT |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 1 | 24329 | 121 | 0.00497 | 4.1103e-05 | 10 | 1210 | 2009/2010 | January-2010 | 1 | 2010
22969 | Connect New Earth Mat - Hirangi Road | 2010-01-29 10:32 | 2010-01-29 | 2010-01-29 14:26 | Calculated | 10R03 | 10R03 - 1 Phase : 30.00 kVA : POLEMNT |  | 405SEG5519-5488 | Hirangi 405-01 | Rural B | Hirangi | Awamate Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 234 | 4 | 24329 | 936 | 0.03847 | 0.00016441 | 30 | 7020 | 2009/2010 | January-2010 | 1 | 2010
22972 | Lightning - SH40 | 2010-01-29 11:30 | 2010-01-29 | 2010-01-29 13:15 | Calculated | T4050 | T4050 - 1 Phase : 3.00 kVA : POLEMNT |  | 422SEG5727-5259 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24329 |  | 0 | 0 |  |  | 2009/2010 | January-2010 | 1 | 2010
22973 | Lightning - Wharepapa Road | 2010-01-29 12:20 | 2010-01-29 | 2010-01-29 13:52 | Calculated | T2579 | T2579 - 1 Phase : 15.00 kVA : POLEMNT |  | 122SEG376-380 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 24329 | 92 | 0.00378 | 4.1103e-05 | 15 | 1380 | 2009/2010 | January-2010 | 1 | 2010
22974 | Lightning - Karangahape Road | 2010-01-29 12:40 | 2010-01-29 | 2010-01-29 14:18 | Calculated | 07Q08 | 07Q08 - 1 Phase : 10.00 kVA : POLEMNT |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 2 | 24329 | 196 | 0.00806 | 8.2206e-05 | 10 | 980 | 2009/2010 | January-2010 | 1 | 2010
22975 | Lightning - SH43 | 2010-01-29 14:10 | 2010-01-29 | 2010-01-29 15:54 | Calculated | 10C04 | 10C04 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 1 | 24329 | 104 | 0.00427 | 4.1103e-05 | 15 | 1560 | 2009/2010 | January-2010 | 1 | 2010
22966 | Lightning - Waipa Valley Road | 2010-01-29 16:00 | 2010-01-29 | 2010-01-30 10:37 | Calculated | T2320 | T2320 - 1 Phase : 5.00 kVA : POLEMNT |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1117 | 1 | 24329 | 1117 | 0.04591 | 4.1103e-05 | 5 | 5585 | 2009/2010 | January-2010 | 1 | 2010
22976 | Lightning - Ongarue Road | 2010-01-30 07:15 | 2010-01-30 | 2010-01-30 09:43 | Calculated | 06I02 | 06I02 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5472-5343 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 2 | 24329 | 296 | 0.01217 | 8.2206e-05 | 15 | 2220 | 2009/2010 | January-2010 | 1 | 2010
22977 | Dead Bird - Rimu Road | 2010-01-30 08:15 | 2010-01-30 | 2010-01-30 09:43 | Calculated | 5564 | 5564 - Fused Link 5564 |  | 412SEG5785-5263 | Nihoniho 412-01 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 3 | 24329 | 264 | 0.01085 | 0.00012331 | 18 | 1584 | 2009/2010 | January-2010 | 1 | 2010
22978 | Lightning - Te Anga Road | 2010-01-30 08:20 | 2010-01-30 | 2010-01-30 10:25 | Calculated | T1152 | T1152 - 1 Phase : 5.00 kVA : POLEMNT |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 1 | 24329 | 125 | 0.00514 | 4.1103e-05 | 5 | 625 | 2009/2010 | January-2010 | 1 | 2010
22979 | Lightning - Mangaokewa Road | 2010-01-30 10:00 | 2010-01-30 | 2010-01-30 11:04 | Calculated | T1229 | T1229 - 1 Phase : 25.00 kVA : POLEMNT |  | 103SEG294-476 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 1 | 24329 | 64 | 0.00263 | 4.1103e-05 | 25 | 1600 | 2009/2010 | January-2010 | 1 | 2010
22980 | Unknown - Karangahape Road | 2010-01-30 13:00 | 2010-01-30 | 2010-01-30 14:15 | Calculated | 5847 | 5847 - FusedLink 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 39 | 24329 | 2925 | 0.12023 | 0.001603 | 353.5 | 26512 | 2009/2010 | January-2010 | 1 | 2010
22981 | Bird - Mears Road | 2010-01-30 13:55 | 2010-01-30 | 2010-01-30 15:38 | Calculated | 06K02 | 06K02 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5108-5810 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 3 | 24329 | 309 | 0.0127 | 0.00012331 | 15 | 1545 | 2009/2010 | January-2010 | 1 | 2010
22982 | Lightning - Fullerton Road | 2010-01-31 08:00 | 2010-01-31 | 2010-01-31 10:27 | Calculated | T1177 | T1177 - 3 Phase : 50.00 kVA : POLEMNT |  | 101SEG500-186 | Caves 101-07 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 5 | 24329 | 735 | 0.03021 | 0.00020552 | 50 | 7350 | 2009/2010 | January-2010 | 1 | 2010
22983 | Lightning - Fullerton Road | 2010-01-31 08:05 | 2010-01-31 | 2010-01-31 09:30 | Calculated | T654 | T654 - 1 Phase : 10.00 kVA : POLEMNT |  | 101SEG500-186 | Caves 101-07 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 1 | 24329 | 85 | 0.00349 | 4.1103e-05 | 10 | 850 | 2009/2010 | January-2010 | 1 | 2010
22984 | Tree Through Line - Kokomiko Sub | 2010-01-31 12:33 | 2010-01-31 | 2010-01-31 15:29 | Calculated | 5505 | 5505 - Sectionaliser with Bypass 5505 |  | 421SEG5502-5505 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 176 | 29 | 24329 | 5104 | 0.20979 | 0.001192 | 227.5 | 40040 | 2009/2010 | January-2010 | 1 | 2010
22985 | Tree Through Line - Waimiha | 2010-01-31 12:33 | 2010-01-31 | 2010-01-31 17:28 | Calculated | 5349 | 5349 - Fused Link 5349 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 295 | 20 | 24329 | 5900 | 0.24251 | 0.00082206 | 157.5 | 46462 | 2009/2010 | January-2010 | 1 | 2010
22988 | Lightning - Whanagamata Road | 2010-01-31 15:55 | 2010-01-31 | 2010-01-31 18:53 | Calculated | 469 | 469 - Fused Link 469 |  | 123SEG469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 178 | 9 | 24329 | 1602 | 0.06585 | 0.00036993 | 55 | 9790 | 2009/2010 | January-2010 | 1 | 2010
22989 | Lightning - Puketapu Road | 2010-01-31 15:55 | 2010-01-31 | 2010-01-31 19:12 | Calculated | T1279 | T1279 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG469 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 2 | 24329 | 394 | 0.01619 | 8.2206e-05 | 15 | 2955 | 2009/2010 | January-2010 | 1 | 2010
22987 | Unknown - Gadsby Road | 2010-01-31 17:40 | 2010-01-31 | 2010-01-31 17:52 | Calculated | 513 | 513 - Circuit Breaker Gadsby Rd 11 kV Feeder 513 |  | No Segment | 205-01 Gadsby Road | Urban A | Waitomo | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 434 | 24329 | 5208 | 0.21407 | 0.017839 | 3330 | 39959 | 2009/2010 | January-2010 | 1 | 2010
22990 | Lightning - Spencer Road | 2010-01-31 17:55 | 2010-01-31 | 2010-01-31 20:17 | Calculated | T781 | T781 - 1 Phase : 15.00 kVA : POLEMNT |  | 129SEG442-2238 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 2 | 24329 | 284 | 0.01167 | 8.2206e-05 | 15 | 2130 | 2009/2010 | January-2010 | 1 | 2010
22991 | Lightning - Pokuru Road | 2010-01-31 18:00 | 2010-01-31 | 2010-01-31 20:29 | Calculated | T782 | T782 - 1 Phase : 15.00 kVA : POLEMNT |  | 129SEG442-2238 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 5 | 24329 | 745 | 0.03062 | 0.00020552 | 15 | 2235 | 2009/2010 | January-2010 | 1 | 2010
22992 | Lightning - Marotiri Road | 2010-01-31 18:02 | 2010-01-31 | 2010-01-31 21:44 | Calculated | T981 | T981 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 222 | 2 | 24329 | 444 | 0.01825 | 8.2206e-05 | 15 | 3330 | 2009/2010 | January-2010 | 1 | 2010
22993 | Lightning - Poihipi Road | 2010-01-31 19:20 | 2010-01-31 | 2010-01-31 23:26 | Calculated | T933 | T933 - 1 Phase : 15.00 kVA : POLEMNT |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 246 | 3 | 24329 | 738 | 0.03033 | 0.00012331 | 15 | 3690 | 2009/2010 | January-2010 | 1 | 2010
22994 | Lightning - Tirohanga Road | 2010-01-31 20:00 | 2010-01-31 | 2010-01-31 23:41 | Calculated | T240 | T240 - 1 Phase : 30.00 kVA : POLEMNT |  | 129SEG477 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 1 | 24329 | 221 | 0.00908 | 4.1103e-05 | 30 | 6630 | 2009/2010 | January-2010 | 1 | 2010
22995 | Lightning - Fullerton Road | 2010-02-01 07:45 | 2010-02-01 | 2010-02-01 09:14 | Calculated | T2575 | T2575 - 1 Phase : 10.00 kVA : POLEMNT |  | 101SEG500-186 | Caves 101-07 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 3 | 24437 | 267 | 0.01093 | 0.00012276 | 10 | 889 | 2009/2010 | February-2010 | 2 | 2010
22996 | Lightning - Raetihi Road | 2010-02-01 09:34 | 2010-02-01 | 2010-02-01 10:23 | Calculated | 20K18 | 20K18 - 3 Phase : 30.00 kVA : POLEMNT |  | 416SEG5956-5672 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 1 | 24437 | 49 | 0.00201 | 4.0922e-05 | 30 | 1470 | 2009/2010 | February-2010 | 2 | 2010
22997 | Lightning - Oparure Road | 2010-02-01 10:25 | 2010-02-01 | 2010-02-01 12:38 | Calculated | T900 | T900 - 1 Phase : 15.00 kVA : POLEMNT |  | 107SEG262-176 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 1 | 24437 | 133 | 0.00544 | 4.0922e-05 | 15 | 1995 | 2009/2010 | February-2010 | 2 | 2010
22998 | Fuse Pulled Apart - Kaeaea Road | 2010-02-01 17:45 | 2010-02-01 | 2010-02-01 20:15 | Calculated | T2397 | T2397 - 3ph 10kVA POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 1 | 24437 | 150 | 0.00614 | 4.0922e-05 | 10 | 1500 | 2009/2010 | February-2010 | 2 | 2010
22999 | Wind - Mohakatino | 2010-02-01 18:00 | 2010-02-01 | 2010-02-02 15:33 | Calculated | 1625 | 1625 - Recloser with Outgoing Link1625 |  | 128SEG1634-REG3 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1293 | 19 | 24437 | 24567 | 1.0053 | 0.00077751 | 107.5 | 138997 | 2009/2010 | February-2010 | 2 | 2010
23000 | Lightning - Ngahape Road | 2010-02-02 08:55 | 2010-02-02 | 2010-02-02 11:12 | Calculated | T2667 | T2667 - 1 Phase : 10.00 kVA : POLEMNT |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 1 | 24437 | 137 | 0.00561 | 4.0922e-05 | 10 | 1370 | 2009/2010 | February-2010 | 2 | 2010
23001 | Fuse Pulled Apart - Waikaka Road | 2010-02-02 09:25 | 2010-02-02 | 2010-02-02 16:25 | Calculated | 05E08 | 05E08 - 1 Phase : 3.00 kVA : POLEMNT |  | 412SEG5265-5628 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 420 | 1 | 24437 | 420 | 0.01719 | 4.0922e-05 | 3 | 1260 | 2009/2010 | February-2010 | 2 | 2010
23003 | Burning Xarm - Wairere Falls | 2010-02-02 11:09 | 2010-02-02 | 2010-02-02 11:49 | Calculated | 683 | 683 - Circuit Breaker 683 |  | No Segment | 207-01 Wairere Falls | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 286 | 24437 | 11440 | 0.46814 | 0.011704 | 2853.5 | 114140 | 2009/2010 | February-2010 | 2 | 2010
23004 | Burning Xarm - SH3 | 2010-02-02 11:09 | 2010-02-02 | 2010-02-02 12:00 | Calculated | 1312 | 1312 - Air Break Switch 1312 |  | 116SEG1312-1362 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 47 | 24437 | 2397 | 0.09809 | 0.0019233 | 423 | 21572 | 2009/2010 | February-2010 | 2 | 2010
23005 | Burning Xarm - Tui Street | 2010-02-02 11:09 | 2010-02-02 | 2010-02-02 14:07 | Calculated | 1342 | 1342 - Air Break Switch 1342 |  | 116SEG1342-1312 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 178 | 35 | 24437 | 6230 | 0.25494 | 0.0014323 | 663 | 118014 | 2009/2010 | February-2010 | 2 | 2010
23006 | Bird - Wanganui Valley Road | 2010-02-02 12:20 | 2010-02-02 | 2010-02-02 14:23 | Calculated | 09I06 | 09I06 - 1 Phase : 10.00 kVA : POLEMNT |  | 403SEG5981 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 2 | 24437 | 246 | 0.01007 | 8.1843e-05 | 10 | 1230 | 2009/2010 | February-2010 | 2 | 2010
23007 | Lightning - Moerangi Road | 2010-02-02 12:47 | 2010-02-02 | 2010-02-02 14:38 | Calculated | 09O01 | 09O01 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5240-5242 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 1 | 24437 | 111 | 0.00454 | 4.0922e-05 | 15 | 1665 | 2009/2010 | February-2010 | 2 | 2010
23008 | Lightning - Kawakawa Road | 2010-02-02 13:05 | 2010-02-02 | 2010-02-02 16:34 | Calculated | T2912 | T2912 - 3 Phase : 15.00 kVA : POLEMNT |  | 123SEG468 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 209 | 1 | 24437 | 209 | 0.00855 | 4.0922e-05 | 15 | 3135 | 2009/2010 | February-2010 | 2 | 2010
23009 | Lightning - Hewers Road | 2010-02-02 13:42 | 2010-02-02 | 2010-02-02 15:47 | Calculated | T190 | T190 - 3ph 10kVA POLEMNT |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 1 | 24437 | 125 | 0.00512 | 4.0922e-05 | 10 | 1250 | 2009/2010 | February-2010 | 2 | 2010
23011 | Gadsby Road Feeder Renewal Project | 2010-02-03 09:01 | 2010-02-03 | 2010-02-03 17:20 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23012 | Replace "H" Structure 19 | 2010-02-04 08:22 | 2010-02-04 | 2010-02-04 15:51 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23014 | Gadsby Road Feeder Renewal Project | 2010-02-04 08:57 | 2010-02-04 | 2010-02-04 15:37 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23015 | Lightning - SH40 | 2010-02-04 11:30 | 2010-02-04 | 2010-02-04 13:54 | Calculated | 05F01 | 05F01 - 2 Phase : 15.00 kVA : POLEMNT |  | 422SEG5606 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 3 | 24437 | 432 | 0.01768 | 0.00012276 | 15 | 2160 | 2009/2010 | February-2010 | 2 | 2010
23016 | Unknown - Huia Road | 2010-02-05 08:35 | 2010-02-05 | 2010-02-05 09:43 | Calculated | 5287 | 5287 - Recloser with Bypass & Links 5287 |  | 413SEG5288-5287 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 31 | 24437 | 2108 | 0.08626 | 0.0012686 | 213 | 14484 | 2009/2010 | February-2010 | 2 | 2010
23017 | Gadsby Road Feeder Renewal Project | 2010-02-05 09:07 | 2010-02-05 | 2010-02-05 16:14 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23019 | Install Tx Link | 2010-02-05 10:00 | 2010-02-05 | 2010-02-05 12:41 | Calculated | 5527 | 5527 - Air Break Switch 5527 |  | 426SEG5847-5592 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23022 | Replace L.A - Tahae Road | 2010-02-05 12:15 | 2010-02-05 | 2010-02-05 13:00 | Calculated | T3290 | T3290 - 3 Phase : 30.00 kVA : POLEMNT |  | 119SEG241 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 2 | 24437 | 90 | 0.00368 | 8.1843e-05 | 30 | 1350 | 2009/2010 | February-2010 | 2 | 2010
23023 | Xarm Off Pole - McLean Road | 2010-02-05 14:32 | 2010-02-05 | 2010-02-05 15:07 | Calculated | 406 | 406 - Air Break Switch 406 |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 94 | 24437 | 3290 | 0.13463 | 0.0038466 | 1793 | 62754 | 2009/2010 | February-2010 | 2 | 2010
23024 | Jumper Off - SH41 | 2010-02-06 12:16 | 2010-02-06 | 2010-02-06 16:39 | Calculated | 6143 | 6143 - Circuit Breaker Manunui 33kV 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23025 | Pig Opened ABS 5838 - Morero Tce | 2010-02-07 06:30 | 2010-02-07 | 2010-02-07 08:20 | Calculated | 1.7 | 1.7 - Ring Main Unit 1.7 |  | 404SEG1.7-5915 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Birds & Animals | Animals | BANI:ANIM |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 123 | 24437 | 13530 | 0.55367 | 0.0050334 | 620 | 68199 | 2009/2010 | February-2010 | 2 | 2010
23026 | Unknown - SH41 | 2010-02-07 09:50 | 2010-02-07 | 2010-02-07 11:45 | Calculated | 09P02 | 09P02 - 3 Phase : 100.00 kVA : POLEMNT |  | No Segment | National Park / Kuratau 609-01 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 1 | 24437 | 115 | 0.00471 | 4.0922e-05 | 100 | 11500 | 2009/2010 | February-2010 | 2 | 2010
23027 | Change Tx - Kaeaea Road | 2010-02-08 09:49 | 2010-02-08 | 2010-02-08 11:23 | Calculated | T2397 | T2397 - 3ph 10kVA POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 1 | 24437 | 94 | 0.00385 | 4.0922e-05 | 10 | 940 | 2009/2010 | February-2010 | 2 | 2010
23029 | Change Tx - Ohura Road | 2010-02-08 11:38 | 2010-02-08 | 2010-02-08 12:35 | Calculated | T1982 | T1982 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 57 | 1 | 24437 | 57 | 0.00233 | 4.0922e-05 | 10 | 570 | 2009/2010 | February-2010 | 2 | 2010
23031 | Unknown - Kirikau Sub | 2010-02-09 09:35 | 2010-02-09 | 2010-02-09 09:57 | Calculated | 5378 | 5378 - Recloser with Bypass & Links 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 65 | 24437 | 1430 | 0.05852 | 0.0026599 | 383 | 8425 | 2009/2010 | February-2010 | 2 | 2010
23032 | Unknown - Kirikau School | 2010-02-09 09:35 | 2010-02-09 | 2010-02-09 13:46 | Calculated | 5367 | 5367 - Sectionaliser with Bypass 5367 |  | 403SEG5367-5875 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 251 | 20 | 24437 | 5020 | 0.20543 | 0.00081843 | 110 | 27609 | 2009/2010 | February-2010 | 2 | 2010
23033 | Unknown - Jebbs Road | 2010-02-09 10:10 | 2010-02-09 | 2010-02-09 12:17 | Calculated | 05F21 | 05F21 - 1 Phase : 15.00 kVA : POLEMNT |  | 422SEG5273 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 1 | 24437 | 127 | 0.0052 | 4.0922e-05 | 15 | 1905 | 2009/2010 | February-2010 | 2 | 2010
23035 | Faulty Tx - Sandel Road | 2010-02-09 17:40 | 2010-02-09 | 2010-02-09 18:10 | Calculated | T1077 | T1077 - 3 Phase : 30.00 kVA : POLEMNT |  | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 1 | 24437 | 30 | 0.00123 | 4.0922e-05 | 30 | 900 | 2009/2010 | February-2010 | 2 | 2010
23036 | Jumper Off @ T2804 - Wharepapa Road | 2010-02-10 08:38 | 2010-02-10 | 2010-02-10 09:53 | Calculated | 380 | 380 - Air Break Switch 380 |  | 122SEG398-380 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 22 | 24437 | 1650 | 0.06752 | 0.00090027 | 723 | 54225 | 2009/2010 | February-2010 | 2 | 2010
23037 | Gadsby Road Feeder Renewal Project | 2010-02-10 08:45 | 2010-02-10 | 2010-02-10 16:36 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23038 | Unknown - Nukuhakari Tap Off | 2010-02-10 16:10 | 2010-02-10 | 2010-02-10 20:06 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 236 | 16 | 24437 | 3776 | 0.15452 | 0.00065474 | 135 | 31860 | 2009/2010 | February-2010 | 2 | 2010
23039 | Faulty Insulator @ Pole 89 - Otukou Sub | 2010-02-11 07:20 | 2010-02-11 | 2010-02-11 08:18 | Calculated | 5584 | 5584 - Recloser with Bypass & Links 5584 |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 75 | 24437 | 4350 | 0.17801 | 0.0030691 | 336 | 19487 | 2009/2010 | February-2010 | 2 | 2010
23040 | Faulty Insulator @ Pole 89 - by Te Roto School | 2010-02-11 07:20 | 2010-02-11 | 2010-02-11 10:38 | Calculated | 5591 | 5591 - Sectionaliser with Bypass & Links 5591 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 7 | 24437 | 1386 | 0.05672 | 0.00028645 | 208 | 41184 | 2009/2010 | February-2010 | 2 | 2010
23041 | Faulty Insulator @ Pole 89 - Rotoaira Trust | 2010-02-11 07:20 | 2010-02-11 | 2010-02-11 13:49 | Calculated | 5939 | 5939 - Earth Working Link 5939 |  | 418SEG5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 389 | 45 | 24437 | 17505 | 0.71633 | 0.0018415 | 125 | 48624 | 2009/2010 | February-2010 | 2 | 2010
23042 | Gadsby Road Feeder Renewal Project | 2010-02-11 08:31 | 2010-02-11 | 2010-02-11 16:02 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23043 | Tree Through Line - Ahuroa Road | 2010-02-11 20:14 | 2010-02-11 | 2010-02-11 20:44 | Calculated | 112 | 112 - Circuit Breaker with Bypass & Links 112 |  | 106SEG112-REG30 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 159 | 24437 | 4770 | 0.1952 | 0.0065065 | 2047 | 61410 | 2009/2010 | February-2010 | 2 | 2010
23044 | Tree Through Line - Taipairu Road | 2010-02-11 20:14 | 2010-02-11 | 2010-02-11 23:00 | Calculated | 192 | 192 - Air Break Switch 192 |  | 106SEG192-246 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 48 | 24437 | 7968 | 0.32606 | 0.0019642 | 297.5 | 49384 | 2009/2010 | February-2010 | 2 | 2010
23045 | Gadsby Road Feeder Renewal Project | 2010-02-12 08:51 | 2010-02-12 | 2010-02-12 15:54 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23046 | Change Xarm - Rangitoto Road | 2010-02-12 09:11 | 2010-02-12 | 2010-02-12 14:22 | Calculated | T1487 | T1487 - 3ph 30kVA POLEMNT |  | 106SEG389-227 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 311 | 4 | 24437 | 1244 | 0.05091 | 0.00016369 | 30 | 9330 | 2009/2010 | February-2010 | 2 | 2010
23047 | Repair Broken Earth - SH41 | 2010-02-12 10:16 | 2010-02-12 | 2010-02-12 12:37 | Calculated | 08Q11 | 08Q11 - 1 Phase : 15.00 kVA : POLEMNT |  | 406SEG5617-5250 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 4 | 24437 | 564 | 0.02308 | 0.00016369 | 15 | 2115 | 2009/2010 | February-2010 | 2 | 2010
23048 | Magpie - Wanganui Valley Road | 2010-02-12 11:00 | 2010-02-12 | 2010-02-12 11:38 | Calculated | 09I13 | 09I13 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5981 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 1 | 24437 | 38 | 0.00156 | 4.0922e-05 | 15 | 570 | 2009/2010 | February-2010 | 2 | 2010
23049 | Repair Broken Earth - SH41 | 2010-02-12 12:38 | 2010-02-12 | 2010-02-12 14:03 | Calculated | 08Q10 | 08Q10 - 1 Phase : 10.00 kVA : POLEMNT |  | 406SEG5250-5249 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 1 | 24437 | 85 | 0.00348 | 4.0922e-05 | 10 | 850 | 2009/2010 | February-2010 | 2 | 2010
23050 | Unknown - Mangakowhai Road | 2010-02-12 15:00 | 2010-02-12 | 2010-02-12 17:25 | Calculated | T1666 | T1666 - 3ph 25kVA POLEMNT |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 3 | 24437 | 435 | 0.0178 | 0.00012276 | 25 | 3624 | 2009/2010 | February-2010 | 2 | 2010
23051 | Unknown - SH30 | 2010-02-13 05:05 | 2010-02-13 | 2010-02-13 06:32 | Calculated | T3077 | T3077 - 3ph 100kVA POLEMNT |  | 119SEG404 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 1 | 24437 | 87 | 0.00356 | 4.0922e-05 | 100 | 8700 | 2009/2010 | February-2010 | 2 | 2010
23052 | Unknown - Nukuhakari Tap Off | 2010-02-13 08:35 | 2010-02-13 | 2010-02-13 11:30 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 16 | 24437 | 2800 | 0.11458 | 0.00065474 | 135 | 23625 | 2009/2010 | February-2010 | 2 | 2010
23053 | Unknown - Raetihih Road | 2010-02-13 14:12 | 2010-02-13 | 2010-02-13 14:46 | Calculated | 20K18 | 20K18 - 3 Phase : 30.00 kVA : POLEMNT |  | 416SEG5956-5672 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 1 | 24437 | 34 | 0.00139 | 4.0922e-05 | 30 | 1020 | 2009/2010 | February-2010 | 2 | 2010
23054 | Unknown - Nukuhakari Tap Off | 2010-02-13 20:45 | 2010-02-13 | 2010-02-13 22:55 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 16 | 24437 | 2080 | 0.08512 | 0.00065474 | 135 | 17550 | 2009/2010 | February-2010 | 2 | 2010
23057 | Gadsby Road Feeder Renewal Project | 2010-02-15 09:05 | 2010-02-15 | 2010-02-15 15:57 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23058 | Line Down @ Pole 386 - Turakina Valley Road | 2010-02-15 09:57 | 2010-02-15 | 2010-02-15 12:01 | Calculated | 6174 | 6174 - Recloser 6174 |  | 416SEG5711-6174 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 37 | 24437 | 4588 | 0.18775 | 0.0015141 | 360 | 44639 | 2009/2010 | February-2010 | 2 | 2010
23059 | Line Down @ Pole 386 - Tangiwai Railway Station | 2010-02-15 09:57 | 2010-02-15 | 2010-02-15 14:13 | Calculated | 5689 | 5689 - Fused Link 5689 |  | 416SEG5689-5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 256 | 28 | 24437 | 7168 | 0.29333 | 0.0011458 | 290 | 74239 | 2009/2010 | February-2010 | 2 | 2010
23060 | Unknown - Mission Bay Sub | 2010-02-15 12:00 | 2010-02-15 | 2010-02-15 13:05 | Calculated | 5478 | 5478 - Recloser with Bypass 5478 |  | 417SEG5478-5905 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 30 | 24437 | 1950 | 0.0798 | 0.0012276 | 125 | 8124 | 2009/2010 | February-2010 | 2 | 2010
23062 | Gadsby Road Feeder Renewal Project | 2010-02-16 08:42 | 2010-02-16 | 2010-02-16 16:03 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23063 | SWER Backfeed - Kirikau Otunui Sub | 2010-02-16 09:30 | 2010-02-16 | 2010-02-16 09:32 | Calculated | 5886 | 5886 - Solid Link 5886 |  | 403SEG5886-5879 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 2 | 65 | 24437 | 130 | 0.00532 | 0.0026599 | 383 | 765 | 2009/2010 | February-2010 | 2 | 2010
23064 | SWER Backfeed - Kirikau Otunui Sub | 2010-02-16 09:33 | 2010-02-16 | 2010-02-16 09:35 | Calculated | 5887 | 5887 - Earth Working Link 5887 |  | 403SEG5887-5322 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 19 | 24437 | 38 | 0.00156 | 0.00077751 | 105 | 209 | 2009/2010 | February-2010 | 2 | 2010
23065 | SWER Backfeed - SH43 | 2010-02-16 09:48 | 2010-02-16 | 2010-02-16 09:49 | Calculated | 5622 | 5622 - Fused Link 5622 |  | 403SEG5622-5368 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 24 | 24437 | 24 | 0.00098 | 0.00098212 | 150 | 149 | 2009/2010 | February-2010 | 2 | 2010
23066 | Unknown - Taharoa Road | 2010-02-16 20:00 | 2010-02-16 | 2010-02-16 21:49 | Calculated | 525 | 525 - Fused Link 525 |  | 126SEG525 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 43 | 24437 | 4687 | 0.1918 | 0.0017596 | 260 | 28339 | 2009/2010 | February-2010 | 2 | 2010
23067 | Change Tx - Tihoi Road | 2010-02-17 10:42 | 2010-02-17 | 2010-02-17 12:06 | Calculated | T2683 | T2683 - 3 Phase : 30.00 kVA : POLEMNT |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 1 | 24437 | 84 | 0.00344 | 4.0922e-05 | 30 | 2520 | 2009/2010 | February-2010 | 2 | 2010
23070 | Smoking Pole 901/85/102 - Manunui | 2010-02-18 08:25 | 2010-02-18 | 2010-02-18 09:27 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOF | Pole Top Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 37 | 24437 | 2294 | 0.09387 | 0.0015141 | 227.5 | 14105 | 2009/2010 | February-2010 | 2 | 2010
23071 | Smoking Pole 901/85/102 - Hohotaka Road | 2010-02-18 08:25 | 2010-02-18 | 2010-02-18 11:12 | Calculated | 5916 | 5916 - Earth Working Link 5916 |  | 408SEG5916-5241 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOF | Pole Top Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 167 | 23 | 24437 | 3841 | 0.15718 | 0.0009412 | 130 | 21710 | 2009/2010 | February-2010 | 2 | 2010
23072 | Lightning - Waipuna Road | 2010-02-18 08:30 | 2010-02-18 | 2010-02-18 09:43 | Calculated | T511 | T511 - 1 Phase : 10.00 kVA : POLEMNT |  | 101SEG291-752 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 1 | 24437 | 73 | 0.00299 | 4.0922e-05 | 10 | 730 | 2009/2010 | February-2010 | 2 | 2010
23073 | Change Insulator & Repair Conductor on Pole 133/4 | 2010-02-18 08:38 | 2010-02-18 | 2010-02-18 11:00 | Calculated | 5813 | 5813 - Fused Link 5813 |  | 409SEG5813 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23074 | Upgrade Speedies Road to 3 Phase | 2010-02-18 08:49 | 2010-02-18 | 2010-02-18 14:16 | Calculated | T519 | T519 - 3ph 50kVA POL |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 11 | 24437 | 3609 | 0.14769 | 0.00045014 | 65 | 21315 | 2009/2010 | February-2010 | 2 | 2010
23075 | Upgrade HV & LV Terminations on 07R14 | 2010-02-18 09:32 | 2010-02-18 | 2010-02-18 11:47 | Calculated | 5226 | 5226 - Air Break Switch 5226 |  | 426SEG5226RET | Waihaha 426-02 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 135 | 106 | 24437 | 14310 | 0.58559 | 0.0043377 | 600 | 80999 | 2009/2010 | February-2010 | 2 | 2010
23076 | Fuse Pulled Apart - Upper Retaruke Road | 2010-02-18 09:34 | 2010-02-18 | 2010-02-18 10:38 | Calculated | 14I02 | 14I02 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5334-5745 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 1 | 24437 | 64 | 0.00262 | 4.0922e-05 | 10 | 640 | 2009/2010 | February-2010 | 2 | 2010
23078 | Fuse Pulled Apart - Te Waitere Road | 2010-02-19 07:20 | 2010-02-19 | 2010-02-19 10:55 | Calculated | T1474 | T1474 - 3ph 25kVA POLEMNT |  | 125SEG281-298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 215 | 6 | 24437 | 1290 | 0.05279 | 0.00024553 | 25 | 5374 | 2009/2010 | February-2010 | 2 | 2010
23079 | Refurbish Otunui/Kirikau SWER Sub | 2010-02-19 11:53 | 2010-02-19 | 2010-02-19 14:03 | Calculated | 5886 | 5886 - Solid Link 5886 |  | 403SEG5886-5879 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 130 | 37 | 24437 | 148 | 0.00606 | 0.0015141 | 683 | 92990 | 2009/2010 | February-2010 | 2 | 2010
23082 | Jumper off Link 519 - Waitomo Caves Road | 2010-02-20 12:56 | 2010-02-20 | 2010-02-20 13:33 | Calculated | 261 | 261 - Fused Link 261 |  | 101SEG261-519 | Caves 101-02 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 43 | 24437 | 1591 | 0.06511 | 0.0017596 | 507.5 | 18777 | 2009/2010 | February-2010 | 2 | 2010
23084 | E/F? - Borough Sub | 2010-02-21 15:38 | 2010-02-21 | 2010-02-21 15:44 | Calculated | 880 | 880 - Circuit Breaker Hakiaha 880 |  | No Segment | 508-01 Borough |  | Hakiaha | Borough Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 298 | 24437 | 1788 | 0.07317 | 0.012195 | 3580 | 21479 | 2009/2010 | February-2010 | 2 | 2010
23085 | Gadsby Road Feeder Renewal Project | 2010-02-22 09:06 | 2010-02-22 | 2010-02-22 16:43 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23086 | Remove 20K13 & Install GMT & RTE6031 | 2010-02-22 09:32 | 2010-02-22 | 2010-02-22 15:19 | Calculated | 20K13 | 20K13 - 3ph 100kVA POL |  | THUVVK | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 347 | 10 | 24437 | 3490 | 0.14282 | 0.00040922 | 150 | 53049 | 2009/2010 | February-2010 | 2 | 2010
23087 | Gadsby Road Feeder Renewal Project | 2010-02-23 08:54 | 2010-02-23 | 2010-02-23 16:54 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23089 | Fuse Pulled Apart - Whangaehu Valley Road | 2010-02-23 11:10 | 2010-02-23 | 2010-02-23 12:53 | Calculated | 21M10 | 21M10 - 1 Phase : 15.00 kVA : POLEMNT |  | 416SEG5684-5747 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 1 | 24437 | 103 | 0.00421 | 4.0922e-05 | 15 | 1545 | 2009/2010 | February-2010 | 2 | 2010
23090 | Lightning - Maihiihi Road | 2010-02-23 11:55 | 2010-02-23 | 2010-02-23 15:34 | Calculated | T604 | T604 - 3ph 5kVA polemnt |  | 111SEG346-REG6 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 1 | 24437 | 219 | 0.00896 | 4.0922e-05 | 5 | 1095 | 2009/2010 | February-2010 | 2 | 2010
23091 | Raise Tap - Pururu West Road | 2010-02-23 12:56 | 2010-02-23 | 2010-02-23 13:37 | Calculated | T2693 | T2693 - 3ph 50kVA POLEMNT |  | 106SEG173 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 1 | 24437 | 41 | 0.00168 | 4.0922e-05 | 50 | 2050 | 2009/2010 | February-2010 | 2 | 2010
23092 | Unknown - Waihora Road | 2010-02-23 18:10 | 2010-02-23 | 2010-02-23 20:08 | Calculated | T1103 | T1103 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 2 | 24437 | 236 | 0.00966 | 8.1843e-05 | 15 | 1770 | 2009/2010 | February-2010 | 2 | 2010
23093 | Change Poles 4-22 Waihaha Feeder | 2010-02-24 08:34 | 2010-02-24 | 2010-02-24 15:20 | Calculated | 5409 | 5409 - Recloser with Bypass 5409 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 406 | 157 | 24437 | 45310 | 1.8542 | 0.0064247 | 1178.5 | 329266 | 2009/2010 | February-2010 | 2 | 2010
23094 | Gadsby Road Feeder Renewal Project | 2010-02-24 08:55 | 2010-02-24 | 2010-02-24 17:13 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23095 | Unknown - Nukuhakari Tap Off | 2010-02-25 09:35 | 2010-02-25 | 2010-02-25 11:43 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 16 | 24437 | 2048 | 0.08381 | 0.00065474 | 135 | 17280 | 2009/2010 | February-2010 | 2 | 2010
23098 | Magpie - SH32 | 2010-02-25 10:00 | 2010-02-25 | 2010-02-25 11:58 | Calculated | 04Q13 | 04Q13 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 1 | 24437 | 118 | 0.00483 | 4.0922e-05 | 15 | 1770 | 2009/2010 | February-2010 | 2 | 2010
23099 | Bird @ 08V02 - Mission Bay Sub | 2010-02-25 10:30 | 2010-02-25 | 2010-02-25 13:55 | Calculated | 5478 | 5478 - Recloser with Bypass 5478 |  | 417SEG5478-5905 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 205 | 30 | 24437 | 6150 | 0.25167 | 0.0012276 | 125 | 25624 | 2009/2010 | February-2010 | 2 | 2010
23100 | Connect New 11kV Extension to T3318 | 2010-02-25 10:34 | 2010-02-25 | 2010-02-25 17:14 | Calculated | 553 | 553 - Fused Link 553 |  | 123SEG553 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 400 | 3 | 24437 | 1200 | 0.04911 | 0.00012276 | 10 | 4000 | 2009/2010 | February-2010 | 2 | 2010
23101 | Clash-Line Down - King Country Lamb | 2010-02-25 11:21 | 2010-02-25 | 2010-02-25 11:26 | Calculated | 651 | 651 - Fused Link 651 |  | 103SEG651-652 | Pureora 119-03 RETIRED | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 1 | 24437 | 5 | 0.0002 | 4.0922e-05 | 500 | 2500 | 2009/2010 | February-2010 | 2 | 2010
23102 | Clash-Line Down - Mine Road | 2010-02-25 11:21 | 2010-02-25 | 2010-02-25 13:58 | Calculated | 714 | 714 - Recloser with Bypass 714 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 6 | 24437 | 942 | 0.03855 | 0.00024553 | 1028 | 161396 | 2009/2010 | February-2010 | 2 | 2010
23103 | Clash-Line Down - SH30 | 2010-02-25 11:21 | 2010-02-25 | 2010-02-25 14:18 | Calculated | 293 | 293 - Air Break Switch 293 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 6 | 24437 | 1062 | 0.04346 | 0.00024553 | 948 | 167796 | 2009/2010 | February-2010 | 2 | 2010
23104 | Clash-Line Down - Tiroa Road | 2010-02-25 11:21 | 2010-02-25 | 2010-02-25 15:06 | Calculated | 709 | 709 - Air Break Switch 709 |  | No Segment | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 225 | 17 | 24437 | 3825 | 0.15652 | 0.00069567 | 360.5 | 81112 | 2009/2010 | February-2010 | 2 | 2010
23105 | Clash-Line Down - Waipa Valley Road | 2010-02-25 11:21 | 2010-02-25 | 2010-02-25 16:57 | Calculated | 453 | 453 - Air Break Switch 453 |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 336 | 25 | 24437 | 8400 | 0.34374 | 0.001023 | 185.5 | 62328 | 2009/2010 | February-2010 | 2 | 2010
23106 | Fuse Pulled Apart - Pukepoto Microwave | 2010-02-25 12:54 | 2010-02-25 | 2010-02-25 15:47 | Calculated | 05H06 | 05H06 - 3ph 30kVA POLEMNT |  | 421SEG5595 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 173 | 3 | 24437 | 519 | 0.02124 | 0.00012276 | 30 | 5190 | 2009/2010 | February-2010 | 2 | 2010
23096 | Repair Suspect Faults - Nukuhakari Tap Off | 2010-02-25 14:48 | 2010-02-25 | 2010-02-25 16:14 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 16 | 24437 | 1376 | 0.05631 | 0.00065474 | 135 | 11610 | 2009/2010 | February-2010 | 2 | 2010
23113 | Replace 16N15 & Install New Xria LBS to 16N27 | 2010-02-26 08:39 | 2010-02-26 | 2010-02-26 16:31 | Calculated | 5990 | 5990 - Circuit Breaker 5990 |  | 419SEG5990-5991 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 472 | 14 | 24437 | 6438 | 0.26345 | 0.0005729 | 2050 | 925350 | 2009/2010 | February-2010 | 2 | 2010
23114 | Gadsby Road Feeder Renewal Project | 2010-02-26 09:05 | 2010-02-26 | 2010-02-26 16:12 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24437 |  | 0 | 0 |  |  | 2009/2010 | February-2010 | 2 | 2010
23116 | Earth Test for Tx Upgrade - Bonners Road | 2010-02-26 10:19 | 2010-02-26 | 2010-02-26 11:28 | Calculated | T374 | T374 - 3ph 15kVA POLEMNT |  | 110SEG189 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 69 | 1 | 24437 | 69 | 0.00282 | 4.0922e-05 | 15 | 1035 | 2009/2010 | February-2010 | 2 | 2010
23118 | Unknown - Taringamotu Road | 2010-02-28 16:40 | 2010-02-28 | 2010-02-28 16:57 | Calculated | 07J25 | 07J25 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 4 | 24437 | 68 | 0.00278 | 0.00016369 | 15 | 255 | 2009/2010 | February-2010 | 2 | 2010
23119 | Unknown - Kawautahi Road | 2010-03-01 11:24 | 2010-03-01 | 2010-03-01 13:49 | Calculated | 11J04 | 11J04 - 1 Phase : 7.50 kVA : POLEMNT |  | 409SEG5402-5389 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 1 | 24435 | 145 | 0.00593 | 4.0925e-05 | 7.5 | 1087 | 2009/2010 | March-2010 | 3 | 2010
23120 | Unknown - Omaru Road | 2010-03-01 12:00 | 2010-03-01 | 2010-03-01 13:03 | Calculated | 1729 | 1729 - Fused Link 1729 |  | 117SEG1729 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 10 | 24435 | 630 | 0.02578 | 0.00040925 | 65 | 4095 | 2009/2010 | March-2010 | 3 | 2010
23121 | Replace Xarms & Re-Conductor | 2010-03-02 09:31 | 2010-03-02 | 2010-03-02 16:55 | Calculated | 635 | 635 - Air Break Switch 635 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 443 | 48 | 24435 | 21264 | 0.87023 | 0.0019644 | 695 | 307885 | 2009/2010 | March-2010 | 3 | 2010
23122 | Change Tx - Raetihi Road | 2010-03-02 10:13 | 2010-03-02 | 2010-03-02 11:19 | Calculated | 20K18 | 20K18 - 3 Phase : 30.00 kVA : POLEMNT |  | 416SEG5956-5672 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 66 | 1 | 24435 | 66 | 0.0027 | 4.0925e-05 | 30 | 1980 | 2009/2010 | March-2010 | 3 | 2010
23123 | Lightning - Ohura Road | 2010-03-02 11:32 | 2010-03-02 | 2010-03-02 12:47 | Calculated | 05F15 | 05F15 - 1 Phase : 15.00 kVA : POLEMNT |  | 422SEG5618-5272 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 24435 | 75 | 0.00307 | 4.0925e-05 | 15 | 1125 | 2009/2010 | March-2010 | 3 | 2010
23124 | Unknown - Hikurangi Sub | 2010-03-03 04:20 | 2010-03-03 | 2010-03-03 06:57 | Calculated | 5370 | 5370 - Recloser with Bypass & Links 5370 |  | 402SEG5370-5199 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 82 | 24435 | 12874 | 0.52687 | 0.0033558 | 620 | 97339 | 2009/2010 | March-2010 | 3 | 2010
23125 | Replace Rotten Xarms on Poles 46 & 47 | 2010-03-03 09:02 | 2010-03-03 | 2010-03-03 14:03 | Calculated | 5797 | 5797 - Fused Link 5797 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 15 | 24435 | 60 | 0.00246 | 0.00061387 | 112.5 | 450 | 2009/2010 | March-2010 | 3 | 2010
23126 | Change 21M01 - SH4 | 2010-03-04 09:27 | 2010-03-04 | 2010-03-04 16:20 | Calculated | 5690 | 5690 - Fused Link 5690 |  | 416SEG5690 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 413 | 8 | 24435 | 3304 | 0.13522 | 0.0003274 | 50 | 20650 | 2009/2010 | March-2010 | 3 | 2010
23127 | Faulty Tx - Taharoa Road | 2010-03-04 10:05 | 2010-03-04 | 2010-03-04 10:51 | Calculated | T1405 | T1405 - 3 Phase : 15.00 kVA : POLEMNT |  | 126SEG609-2121 | Rural 126-03 | Rural D | Rural | Taharoa Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 1 | 24435 | 46 | 0.00188 | 4.0925e-05 | 15 | 690 | 2009/2010 | March-2010 | 3 | 2010
23128 | Unknown - Ongarue EW Sub | 2010-03-04 17:20 | 2010-03-04 | 2010-03-04 18:41 | Calculated | 5466 | 5466 - Recloser with Bypass & Links 5466 |  | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 30 | 24435 | 2430 | 0.09945 | 0.0012277 | 548.5 | 44428 | 2009/2010 | March-2010 | 3 | 2010
23129 | Broken Xarm - Ongarue Back Road | 2010-03-05 11:30 | 2010-03-05 | 2010-03-05 13:22 | Calculated | 5446 | 5446 - Sectionaliser with Bypass & Links 5446 |  | 402SEG5343-5446 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 37 | 24435 | 4144 | 0.16959 | 0.0015142 | 265.5 | 29736 | 2009/2010 | March-2010 | 3 | 2010
23130 | Broken Xarm - Ongarue Back Road | 2010-03-05 11:30 | 2010-03-05 | 2010-03-05 15:47 | Calculated | 5797 | 5797 - Fused Link 5797 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 257 | 15 | 24435 | 3855 | 0.15777 | 0.00061387 | 112.5 | 28912 | 2009/2010 | March-2010 | 3 | 2010
23131 | Birds - Main Sth Road Te Kuiti | 2010-03-05 14:00 | 2010-03-05 | 2010-03-05 15:21 | Calculated | T147 | T147 - 1 Phase : 10.00 kVA : POLEMNT |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 1 | 24435 | 81 | 0.00331 | 4.0925e-05 | 10 | 810 | 2009/2010 | March-2010 | 3 | 2010
23132 | SH41 | 2010-03-06 11:15 | 2010-03-06 | 2010-03-06 12:13 | Calculated | 08Q10 | 08Q10 - 1 Phase : 10.00 kVA : POLEMNT |  | 406SEG5250-5249 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 1 | 24435 | 58 | 0.00237 | 4.0925e-05 | 10 | 580 | 2009/2010 | March-2010 | 3 | 2010
23134 | Unknown - Te Puke Road | 2010-03-08 07:35 | 2010-03-08 | 2010-03-08 08:17 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause |  | CANT3 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 2 | 24435 | 84 | 0.00344 | 8.185e-05 | 8 | 336 | 2009/2010 | March-2010 | 3 | 2010
23135 | Change Tx - Bonners Road | 2010-03-08 10:30 | 2010-03-08 | 2010-03-08 11:42 | Calculated | T374 | T374 - 3ph 15kVA POLEMNT |  | 110SEG189 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 72 | 1 | 24435 | 72 | 0.00295 | 4.0925e-05 | 15 | 1080 | 2009/2010 | March-2010 | 3 | 2010
23136 | Main South Road | 2010-03-08 10:41 | 2010-03-08 | 2010-03-08 13:51 | Calculated | 09K13 | 09K13 - 3ph 30kVA POLEMNT |  | 409SEG5867-5135 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 1 | 24435 | 190 | 0.00778 | 4.0925e-05 | 30 | 5700 | 2009/2010 | March-2010 | 3 | 2010
23138 | Unknown - Waituhi Road | 2010-03-08 14:35 | 2010-03-08 | 2010-03-08 15:46 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause |  | CANT3 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 21 | 24435 | 1491 | 0.06102 | 0.00085942 | 160 | 11360 | 2009/2010 | March-2010 | 3 | 2010
23137 | Unknown - Te Puke Road | 2010-03-08 18:05 | 2010-03-08 | 2010-03-08 19:14 | Calculated | 08R03 | 08R03 - 1 Phase : 5.00 kVA : POLEMNT |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24435 | 69 | 0.00282 | 4.0925e-05 | 5 | 345 | 2009/2010 | March-2010 | 3 | 2010
23139 | Gadsby Rd Feeder Renewal Project | 2010-03-09 08:45 | 2010-03-09 | 2010-03-09 16:15 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24435 |  | 0 | 0 |  |  | 2009/2010 | March-2010 | 3 | 2010
23141 | Upgrade Speedies Road to 3 Phase | 2010-03-09 09:35 | 2010-03-09 | 2010-03-09 15:08 | Calculated | 285 | 285 - Air Break Switch 285 |  | 125SEG285-1768 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 333 | 3 | 24435 | 999 | 0.04088 | 0.00012277 | 15 | 4995 | 2009/2010 | March-2010 | 3 | 2010
23142 | Scheduled Maintenance - Ngahape Road | 2010-03-09 09:35 | 2010-03-09 | 2010-03-09 15:08 | Calculated | T2516 | T2516 - 3ph 50kVA polemnt |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 333 | 2 | 24435 | 666 | 0.02726 | 8.185e-05 | 50 | 16650 | 2009/2010 | March-2010 | 3 | 2010
23143 | Bird - Waituhi Road | 2010-03-09 12:50 | 2010-03-09 | 2010-03-09 14:15 | Calculated | 07K01 | 07K01 - 1 Phase : 10.00 kVA : POLEMNT |  | 402SEG5930-5756 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 3 | 24435 | 255 | 0.01044 | 0.00012277 | 10 | 849 | 2009/2010 | March-2010 | 3 | 2010
23148 | Gadsby Road Feeder Renewal Project | 2010-03-10 09:03 | 2010-03-10 | 2010-03-10 16:17 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24435 |  | 0 | 0 |  |  | 2009/2010 | March-2010 | 3 | 2010
23147 | Change Tx - Pururu West Road | 2010-03-10 09:05 | 2010-03-10 | 2010-03-10 10:59 | Calculated | T2693 | T2693 - 3ph 50kVA POLEMNT |  | 106SEG173 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 114 | 1 | 24435 | 114 | 0.00467 | 4.0925e-05 | 50 | 5700 | 2009/2010 | March-2010 | 3 | 2010
23149 | Connect New 11kV Diversion | 2010-03-10 10:01 | 2010-03-10 | 2010-03-10 11:40 | Calculated | 110 | 110 - Air Break Switch 110 |  | 101SEG110-109 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 99 | 111 | 24435 | 10989 | 0.44972 | 0.0045427 | 851 | 84248 | 2009/2010 | March-2010 | 3 | 2010
23151 | Gadsby Road Feeder Renewal Project | 2010-03-11 08:55 | 2010-03-11 | 2010-03-11 16:39 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24435 |  | 0 | 0 |  |  | 2009/2010 | March-2010 | 3 | 2010
23152 | Unknown - Rangataua Township | 2010-03-11 13:48 | 2010-03-11 | 2010-03-11 15:22 | Calculated | 5712 | 5712 - Fused Link 5712 |  | 415SEG5712-6323 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24435 |  | 0 | 0 |  |  | 2009/2010 | March-2010 | 3 | 2010
23153 | Gadsby Road Feeder Renewal Project | 2010-03-12 08:52 | 2010-03-12 | 2010-03-12 16:38 | Calculated | TPHangatiki CB252 | TPHangatiki CB252 - 33kV Minimum Oil Circuit Breaker TP252 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 0 | 0 | 24435 |  | 0 | 0 |  |  | 2009/2010 | March-2010 | 3 | 2010
23154 | Unknown - Otunui South Road | 2010-03-12 08:59 | 2010-03-12 | 2010-03-12 12:32 | Calculated | 5740 | 5740 - Sectionaliser with Bypass & Links 5740 |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 213 | 24 | 24435 | 5112 | 0.20921 | 0.0009822 | 135 | 28754 | 2009/2010 | March-2010 | 3 | 2010
23159 | Unknown - Te Puke Road | 2010-03-12 10:10 | 2010-03-12 | 2010-03-12 15:07 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 297 | 2 | 24435 | 594 | 0.02431 | 8.185e-05 | 8 | 2376 | 2009/2010 | March-2010 | 3 | 2010
23157 | Jumper Off @ T4064 - Taringamotu Road | 2010-03-12 11:26 | 2010-03-12 | 2010-03-12 12:11 | Calculated | 5103 | 5103 - Air Break Switch 5103 |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 134 | 24435 | 6030 | 0.24678 | 0.0054839 | 1010 | 45449 | 2009/2010 | March-2010 | 3 | 2010
23158 | Jumper Off @ T4064 - Ongarue Village Road | 2010-03-12 11:26 | 2010-03-12 | 2010-03-12 12:11 | Calculated | 5669 | 5669 - Fused Link 5669 |  | 421SEG5669-5342 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 46 | 24435 | 2070 | 0.08471 | 0.0018825 | 325.5 | 14647 | 2009/2010 | March-2010 | 3 | 2010
23161 | Duck (Line Down) - Taharoa Road | 2010-03-12 16:56 | 2010-03-12 | 2010-03-12 19:08 | Calculated | 277 | 277 - Recloser with Bypass 277 |  | No Segment | No Asset Group | Remote Rural F | Coast | Te Anga Zone Substation (Containerised) |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 120 | 24435 | 15840 | 0.64825 | 0.004911 | 958.5 | 126521 | 2009/2010 | March-2010 | 3 | 2010
23165 | Replace Link 669 & 809 | 2010-03-16 09:35 | 2010-03-16 | 2010-03-16 12:35 | Calculated | 5342 | 5342 - Fused Link 5342 |  | 421SEG5342-5792 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 135 | 79 | 24435 | 10902 | 0.44616 | 0.0032331 | 540.5 | 74588 | 2009/2010 | March-2010 | 3 | 2010
23166 | Change Poles/Tx's & L.A's | 2010-03-16 09:36 | 2010-03-16 | 2010-03-16 14:32 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 296 | 16 | 24435 | 4736 | 0.19382 | 0.0006548 | 135 | 39960 | 2009/2010 | March-2010 | 3 | 2010
23169 | Coast Feeder Renewal Project | 2010-03-17 08:41 | 2010-03-17 | 2010-03-17 08:55 | Calculated | T542 | T542 - 3 Phase : 30.00 kVA : POLEMNT |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 14 | 6 | 24435 | 186 | 0.00761 | 0.00024555 | 30 | 930 | 2009/2010 | March-2010 | 3 | 2010
23170 | Change Poles/Tx's & L.A's | 2010-03-17 09:36 | 2010-03-17 | 2010-03-17 14:11 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 275 | 16 | 24435 | 4400 | 0.18007 | 0.0006548 | 135 | 37125 | 2009/2010 | March-2010 | 3 | 2010
23171 | Replace DDO's - Te Waitere Road | 2010-03-17 10:31 | 2010-03-17 | 2010-03-17 12:31 | Calculated | 281 | 281 - Air Break Switch 281 |  | 125SEG281-298 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 120 | 54 | 24435 | 6480 | 0.26519 | 0.0022099 | 515 | 61799 | 2009/2010 | March-2010 | 3 | 2010
23172 | Unknown - Manunui | 2010-03-17 10:40 | 2010-03-17 | 2010-03-17 11:18 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 37 | 24435 | 1406 | 0.05754 | 0.0015142 | 227.5 | 8645 | 2009/2010 | March-2010 | 3 | 2010
23174 | Line Down - Taharoa | 2010-03-18 06:34 | 2010-03-18 | 2010-03-18 12:11 | Calculated | 609 | 609 - Circuit Breaker 609 (Rural Feeder) 609 |  | No Segment | 201-01 Taharoa | Rural D | Rural | Taharoa Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 337 | 107 | 24435 | 36059 | 1.4757 | 0.004379 | 673 | 226800 | 2009/2010 | March-2010 | 3 | 2010
23175 | Connect Gen Set - Otukou Sub | 2010-03-18 08:34 | 2010-03-18 | 2010-03-18 09:10 | Calculated | 5836 | 5836 - Circuit Breaker 5836 |  | No Segment | 512-01 Otukou | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 99 | 24435 | 3564 | 0.14586 | 0.0040516 | 761 | 27395 | 2009/2010 | March-2010 | 3 | 2010
23176 | Too Cold for Gen Set - By Te Roto School | 2010-03-18 08:34 | 2010-03-18 | 2010-03-18 16:20 | Calculated | 5591 | 5591 - Sectionaliser with Bypass & Links 5591 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 466 | 52 | 24435 | 24232 | 0.99169 | 0.0021281 | 208 | 96927 | 2009/2010 | March-2010 | 3 | 2010
23178 | Change Poles/Tx's & L.A's | 2010-03-18 09:40 | 2010-03-18 | 2010-03-18 12:23 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 163 | 16 | 24435 | 2608 | 0.10673 | 0.0006548 | 135 | 22005 | 2009/2010 | March-2010 | 3 | 2010
23181 | Branch Felled Onto Line - Walker Road | 2010-03-18 15:35 | 2010-03-18 | 2010-03-18 16:46 | Calculated | T163 | T163 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG193RET | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 3 | 24435 | 213 | 0.00872 | 0.00012277 | 15 | 1065 | 2009/2010 | March-2010 | 3 | 2010
23177 | Disconnect Gen Set - Otukou Sub | 2010-03-18 15:42 | 2010-03-18 | 2010-03-18 16:08 | Calculated | 5836 | 5836 - Circuit Breaker 5836 |  | No Segment | 512-01 Otukou | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 26 | 99 | 24435 | 2574 | 0.10534 | 0.0040516 | 761 | 19785 | 2009/2010 | March-2010 | 3 | 2010
23182 | Replace Tx Pole & Upgrade 09K13 | 2010-03-19 08:53 | 2010-03-19 | 2010-03-19 16:20 | Calculated | 5235 | 5235 - Air Break Switch 5235 |  | 409SEG5138-5235 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 386 | 2 | 24435 | 772 | 0.03159 | 8.185e-05 | 30 | 11580 | 2009/2010 | March-2010 | 3 | 2010
23184 | Replace Red Tagged Pole - Mahoenui | 2010-03-19 10:08 | 2010-03-19 | 2010-03-19 15:17 | Calculated | 1516 | 1516 - Air Break Switch 1516 |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 135 | 24435 |  | 0 | 0.0055249 | 853.5 |  | 2009/2010 | March-2010 | 3 | 2010
23183 | Change Tx - Te Marama Road | 2010-03-19 10:09 | 2010-03-19 | 2010-03-19 12:13 | Calculated | T2457 | T2457 - 1 Phase : 15.00 kVA : POLEMNT |  | 128SEG1615-1624 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 124 | 1 | 24435 | 124 | 0.00507 | 4.0925e-05 | 15 | 1860 | 2009/2010 | March-2010 | 3 | 2010
23187 | Unknown - Barbers Road | 2010-03-19 12:00 | 2010-03-19 | 2010-03-19 15:18 | Calculated | T110 | T110 - 1 Phase : 7.50 kVA : POLEMNT |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause |  | CANT3 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 1 | 24435 | 198 | 0.0081 | 4.0925e-05 | 7.5 | 1485 | 2009/2010 | March-2010 | 3 | 2010
23188 | Unknown - Hangatiki | 2010-03-19 23:22 | 2010-03-19 | 2010-03-19 23:29 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause |  | CANT3 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24435 |  | 0 | 0 |  |  | 2009/2010 | March-2010 | 3 | 2010
23189 | Unknown - Taharoa | 2010-03-19 23:22 | 2010-03-19 | 2010-03-19 23:29 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause |  | CANT3 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24435 |  | 0 | 0 |  |  | 2009/2010 | March-2010 | 3 | 2010
23190 | Upgrade 20L66 Including New Magnefix Gear | 2010-03-21 07:06 | 2010-03-21 | 2010-03-21 07:51 | Calculated | 5925 | 5925 - Air Break Switch 5925 |  | 414SEG5715-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 844 | 24435 | 2912 | 0.11917 | 0.034541 | 5650 | 15600 | 2009/2010 | March-2010 | 3 | 2010
23191 | Jumper Burning Up - Transpower Ongarue | 2010-03-21 12:33 | 2010-03-21 | 2010-03-21 16:08 | Calculated | TPOngarue CB202 | TPOngarue CB202 - 33kV Minimum Oil Circuit Breaker TP202 |  | No Segment | 514-01 Transpower Ongarue | Rural D | Nihoniho 33 | Direct from Ongarue Supply |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24435 | 0 | 0 | 0 | 3168.5 | 681227 | 2009/2010 | March-2010 | 3 | 2010
23192 | Unknown - Upper Retaruke Sub | 2010-03-21 21:15 | 2010-03-21 | 2010-03-21 23:05 | Calculated | 5494 | 5494 - Recloser with Bypass 5494 |  | 410SEG5494-5493 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 110 | 46 | 24435 | 5060 | 0.20708 | 0.0018825 | 290 | 31899 | 2009/2010 | March-2010 | 3 | 2010
23193 | Faulty Insulator @ Pole - Kirikau Sub | 2010-03-22 06:45 | 2010-03-22 | 2010-03-22 08:35 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 65 | 24435 | 7150 | 0.29261 | 0.0026601 | 383 | 42129 | 2009/2010 | March-2010 | 3 | 2010
23194 | Faulty Insulator @ Pole - Kirikau School | 2010-03-22 06:45 | 2010-03-22 | 2010-03-22 10:51 | Calculated | 5367 | 5367 - Sectionaliser with Bypass 5367 |  | 403SEG5367-5875 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 246 | 20 | 24435 | 4920 | 0.20135 | 0.0008185 | 110 | 27059 | 2009/2010 | March-2010 | 3 | 2010
23195 | Floating Insulator @ Pole - Upper Retaruke Sub | 2010-03-22 06:50 | 2010-03-22 | 2010-03-22 08:54 | Calculated | 5494 | 5494 - Recloser with Bypass 5494 |  | 410SEG5494-5493 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 124 | 46 | 24435 | 5704 | 0.23344 | 0.0018825 | 290 | 35959 | 2009/2010 | March-2010 | 3 | 2010
23196 | Floating Insulator @ Pole - Upper Retaruke Sub | 2010-03-22 06:50 | 2010-03-22 | 2010-03-22 09:49 | Calculated | 5492 | 5492 - Fused Link 5492 |  | 410SEG5492-5334 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 18 | 24435 | 3222 | 0.13186 | 0.00073665 | 120 | 21479 | 2009/2010 | March-2010 | 3 | 2010
23197 | Floating Insulator @ Pole - Upper Retaruke Sub | 2010-03-22 06:50 | 2010-03-22 | 2010-03-22 12:57 | Calculated | 5334 | 5334 - Fused Link 5334 |  | 410SEG5334-5745 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 367 | 10 | 24435 | 3670 | 0.15019 | 0.00040925 | 65 | 23855 | 2009/2010 | March-2010 | 3 | 2010
23198 | Blackberry in 10S38 - Hinerangi Street | 2010-03-22 16:00 | 2010-03-22 | 2010-03-22 17:12 | Calculated | 6195 | 6195 - Fused Link 6195 |  | 423SEG6193-6710 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 130 | 24435 | 9360 | 0.38306 | 0.0053202 | 500 | 35999 | 2009/2010 | March-2010 | 3 | 2010
23199 | Unknown - Te Puke Road | 2010-03-23 10:07 | 2010-03-23 | 2010-03-23 11:13 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 2 | 24435 | 132 | 0.0054 | 8.185e-05 | 8 | 528 | 2009/2010 | March-2010 | 3 | 2010
23200 | Magpie - SH4 | 2010-03-23 17:30 | 2010-03-23 | 2010-03-23 18:00 | Calculated | 05I06 | 05I06 - 1 Phase : 3.00 kVA : POLEMNT |  | 402SEG5446-5797 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 1 | 24435 | 30 | 0.00123 | 4.0925e-05 | 3 | 90 | 2009/2010 | March-2010 | 3 | 2010
23201 | Unknown - Waitanguru | 2010-03-23 18:15 | 2010-03-23 | 2010-03-23 20:15 | Calculated | 1526 | 1526 - Fused Link 1526 |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 55 | 24435 | 6600 | 0.2701 | 0.0022509 | 365.5 | 43859 | 2009/2010 | March-2010 | 3 | 2010
23202 | Unknown - Te Kawa Street | 2010-03-24 04:30 | 2010-03-24 | 2010-03-24 07:31 | Calculated | T170 | T170 - 3ph 200kVA GNDPAD |  | 112SEG311 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 63 | 24435 | 11403 | 0.46667 | 0.0025783 | 200 | 36199 | 2009/2010 | March-2010 | 3 | 2010
23203 | Magpie @ 12K09 - Oio Sub | 2010-03-24 08:30 | 2010-03-24 | 2010-03-24 09:21 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 25 | 24435 | 1275 | 0.05218 | 0.0010231 | 138.5 | 7063 | 2009/2010 | March-2010 | 3 | 2010
23204 | Magpie @ 12K09 - SH4 Owhanga | 2010-03-24 08:30 | 2010-03-24 | 2010-03-24 09:47 | Calculated | 5113 | 5113 - Fused Link 5113 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 13 | 24435 | 1001 | 0.04097 | 0.00053202 | 65.5 | 5043 | 2009/2010 | March-2010 | 3 | 2010
23205 | Magpie @ 12K09 - SH4 (before Bullians Road) | 2010-03-24 08:30 | 2010-03-24 | 2010-03-24 09:59 | Calculated | 5755 | 5755 - Fused Link 5755 |  | 409SEG5755 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 2 | 24435 | 178 | 0.00728 | 8.185e-05 | 15 | 1335 | 2009/2010 | March-2010 | 3 | 2010
23207 | Unknown - Ruapehu Road | 2010-03-25 05:00 | 2010-03-25 | 2010-03-25 07:54 | Calculated | 20L06 | 20L06 - 3 Phase : 100.00 kVA : GNDPAD |  | 416SEG5678-6564 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 174 | 23 | 24435 | 4002 | 0.16378 | 0.00094127 | 75 | 13049 | 2009/2010 | March-2010 | 3 | 2010
23208 | R.E.F. Relay Operated On Livening T3 - Turangi Sub | 2010-03-25 13:25 | 2010-03-25 | 2010-03-25 13:27 | Calculated | 5198 | 5198 - Circuit Breaker 5198 |  | No Segment | 505-01 Turangi | Rural C | Turangi | Turangi Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 1093 | 24435 | 2186 | 0.08946 | 0.044731 | 5350 | 10699 | 2009/2010 | March-2010 | 3 | 2010
23209 | R.E.F. Relay Operated On Livening T3 - Turangi Sub | 2010-03-25 13:25 | 2010-03-25 | 2010-03-25 13:27 | Calculated | 5200 | 5200 - Circuit Breaker 5200 |  | No Segment | 505-01 Turangi | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 848 | 24435 | 1696 | 0.06941 | 0.034704 | 8055 | 16109 | 2009/2010 | March-2010 | 3 | 2010
23211 | Broken Xarm @ 13F02 - Lower Retaruke | 2010-03-26 13:01 | 2010-03-26 | 2010-03-26 14:35 | Calculated | 5668 | 5668 - Fused Link 5668 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 14 | 24435 | 1316 | 0.05386 | 0.00057295 | 60 | 5640 | 2009/2010 | March-2010 | 3 | 2010
23215 | Removal of Temporary Links | 2010-03-29 10:06 | 2010-03-29 | 2010-03-29 12:39 | Calculated | 268 | 268 - Air Break Switch 268 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 120 | 24435 | 16904 | 0.69179 | 0.004911 | 958.5 | 137046 | 2009/2010 | March-2010 | 3 | 2010
23218 | Upgrade Complete Structure T1054 | 2010-03-30 10:01 | 2010-03-30 | 2010-03-30 14:42 | Calculated | 1746 | 1746 - Fused Link 1746 |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 4 | 24435 | 1124 | 0.046 | 0.0001637 | 85 | 23885 | 2009/2010 | March-2010 | 3 | 2010
23222 | Unknown - Pongahura Road Sub | 2010-03-31 10:20 | 2010-03-31 | 2010-03-31 11:23 | Calculated | 5863 | 5863 - Recloser with Bypass & Links 5863 |  | 403SEG5863-5862 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 39 | 24435 | 2457 | 0.10055 | 0.0015961 | 275 | 17324 | 2009/2010 | March-2010 | 3 | 2010
23223 | Damaged Conductor - Makino Road | 2010-03-31 11:08 | 2010-03-31 | 2010-03-31 13:05 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 28 | 24435 | 3276 | 0.13407 | 0.0011459 | 183.5 | 21469 | 2009/2010 | March-2010 | 3 | 2010
23224 | Remove Branch from Line - SH41 | 2010-03-31 12:47 | 2010-03-31 | 2010-03-31 12:54 | Calculated | 5240 | 5240 - Sectionaliser 5240 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 22 | 24435 | 154 | 0.0063 | 0.00090035 | 95 | 664 | 2009/2010 | March-2010 | 3 | 2010
23225 | Line Down - Otunui South Road | 2010-03-31 13:45 | 2010-03-31 | 2010-03-31 16:14 | Calculated | 5740 | 5740 - Sectionaliser with Bypass & Links 5740 |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 24 | 24435 | 3576 | 0.14635 | 0.0009822 | 135 | 20114 | 2009/2010 | March-2010 | 3 | 2010
23227 | Line Down - Otunui North Road | 2010-03-31 13:45 | 2010-03-31 | 2010-03-31 19:52 | Calculated | 5546 | 5546 - Fused Link 5546 |  | 403SEG5546-5575 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 367 | 13 | 24435 | 4771 | 0.19525 | 0.00053202 | 75 | 27524 | 2009/2010 | March-2010 | 3 | 2010
23226 | Line Down - Otunui South Road | 2010-03-31 18:17 | 2010-03-31 | 2010-03-31 18:39 | Calculated | 5740 | 5740 - Sectionaliser with Bypass & Links 5740 |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 24 | 24435 | 528 | 0.02161 | 0.0009822 | 135 | 2969 | 2009/2010 | March-2010 | 3 | 2010
23230 | Unknown - Hangatiki | 2010-04-03 22:14 | 2010-04-03 | 2010-04-03 22:16 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24436 |  | 0 | 0 |  |  | 2010/2011 | April-2010 | 4 | 2010
23231 | Unknown - Taharoa | 2010-04-03 22:14 | 2010-04-03 | 2010-04-03 22:25 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 244 | 24436 | 488 | 0.01997 | 0.0099853 | 4091 | 8182 | 2010/2011 | April-2010 | 4 | 2010
23232 | Unknown - Irvine Road | 2010-04-04 07:25 | 2010-04-04 | 2010-04-04 08:34 | Calculated | T2767 | T2767 - 3ph 50kVA POLEMNT |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24436 | 69 | 0.00282 | 4.0923e-05 | 50 | 3450 | 2010/2011 | April-2010 | 4 | 2010
23233 | Fuse Pulled Apart - Upper Retaruke Road | 2010-04-06 08:00 | 2010-04-06 | 2010-04-06 09:35 | Calculated | 14I04 | 14I04 - 1 Phase : 15.00 kVA : POLEMNT |  | 410SEG5334-5745 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 5 | 24436 | 475 | 0.01944 | 0.00020462 | 18.75 | 1781 | 2010/2011 | April-2010 | 4 | 2010
23234 | Lightning - Waimiha | 2010-04-06 15:01 | 2010-04-06 | 2010-04-06 16:22 | Calculated | 5355 | 5355 - Sectionaliser with Bypass & Links 5355 |  | 421SEG5355-5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 12 | 24436 | 972 | 0.03978 | 0.00049108 | 150 | 12150 | 2010/2011 | April-2010 | 4 | 2010
23235 | Lightning - Gadsby Road | 2010-04-06 17:10 | 2010-04-06 | 2010-04-06 17:30 | Calculated | 511 | 511 - Circuit Breaker Gadsby Rd 11 kV Local Service 511 |  | No Segment | 205-01 Gadsby Road | Urban A | No Feeder |  |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 1 | 24436 | 20 | 0.00082 | 4.0923e-05 | 100 | 2000 | 2010/2011 | April-2010 | 4 | 2010
23236 | Lightning - Old Golf Road | 2010-04-06 17:40 | 2010-04-06 | 2010-04-06 18:24 | Calculated | T682 | T682 - 3ph 25kVA POLEMNT |  | 112SEG1021-318 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 7 | 24436 | 308 | 0.0126 | 0.00028646 | 25 | 1099 | 2010/2011 | April-2010 | 4 | 2010
23237 | Lightning - Rangitoto Road | 2010-04-06 18:00 | 2010-04-06 | 2010-04-06 20:30 | Calculated | T102 | T102 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 3 | 24436 | 450 | 0.01842 | 0.00012277 | 15 | 2250 | 2010/2011 | April-2010 | 4 | 2010
23241 | Unknown - Piawa Road | 2010-04-06 18:00 | 2010-04-06 | 2010-04-07 16:30 | Calculated | T4171 | T4171 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1350 | 1 | 24436 | 1350 | 0.05525 | 4.0923e-05 | 15 | 20250 | 2010/2011 | April-2010 | 4 | 2010
23242 | Unknown - Piawa Road | 2010-04-06 18:00 | 2010-04-06 | 2010-04-07 16:35 | Calculated | 06J11 | 06J11 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1355 | 2 | 24436 | 2710 | 0.1109 | 8.1846e-05 | 15 | 20325 | 2010/2011 | April-2010 | 4 | 2010
23238 | Lightning - Rangitoto Road | 2010-04-06 18:05 | 2010-04-06 | 2010-04-06 21:10 | Calculated | T616 | T616 - 3ph 15kVA POLEMNT |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 3 | 24436 | 555 | 0.02271 | 0.00012277 | 15 | 2775 | 2010/2011 | April-2010 | 4 | 2010
23239 | Lightning - Rangitoto Road | 2010-04-06 18:05 | 2010-04-06 | 2010-04-06 21:10 | Calculated | T2754 | T2754 - 3ph 50kVA POLEMNT |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 1 | 24436 | 185 | 0.00757 | 4.0923e-05 | 50 | 9250 | 2010/2011 | April-2010 | 4 | 2010
23243 | Lightning - Paekaka Road | 2010-04-06 19:50 | 2010-04-06 | 2010-04-07 11:11 | Calculated | T1708 | T1708 - 1 Phase : 10.00 kVA : POLEMNT |  | 113SEG686-1546 | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 921 | 1 | 24436 | 921 | 0.03769 | 4.0923e-05 | 10 | 9210 | 2010/2011 | April-2010 | 4 | 2010
23244 | Lightning - Whangamata Road | 2010-04-07 06:45 | 2010-04-07 | 2010-04-07 09:29 | Calculated | T2691 | T2691 - 3 Phase : 50.00 kVA : POLEMNT |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 1 | 24436 | 164 | 0.00671 | 4.0923e-05 | 50 | 8200 | 2010/2011 | April-2010 | 4 | 2010
23245 | Contractor vs HV Line - Marotiri Road | 2010-04-07 10:16 | 2010-04-07 | 2010-04-07 12:44 | Calculated | T2848 | T2848 - 3 Phase : 50.00 kVA : POLEMNT |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 1 | 24436 | 148 | 0.00606 | 4.0923e-05 | 50 | 7400 | 2010/2011 | April-2010 | 4 | 2010
23246 | Lightning - Tangitu Road | 2010-04-07 11:10 | 2010-04-07 | 2010-04-07 13:16 | Calculated | T2109 | T2109 - 1 Phase : 10.00 kVA : POLEMNT |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 1 | 24436 | 126 | 0.00516 | 4.0923e-05 | 10 | 1260 | 2010/2011 | April-2010 | 4 | 2010
23247 | Lightning - Mangaokewa Road | 2010-04-07 15:15 | 2010-04-07 | 2010-04-07 16:26 | Calculated | T909 | T909 - 1 Phase : 7.50 kVA : POLEMNT |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 2 | 24436 | 142 | 0.00581 | 8.1846e-05 | 7.5 | 532 | 2010/2011 | April-2010 | 4 | 2010
23248 | Lightning - Whangamata Road | 2010-04-07 18:30 | 2010-04-07 | 2010-04-07 20:14 | Calculated | T1129 | T1129 - 1 Phase : 10.00 kVA : POLEMNT |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 1 | 24436 | 104 | 0.00426 | 4.0923e-05 | 10 | 1040 | 2010/2011 | April-2010 | 4 | 2010
23249 | Magpie - Wanganui Valley Road | 2010-04-08 09:30 | 2010-04-08 | 2010-04-08 10:37 | Calculated | 09I06 | 09I06 - 1 Phase : 10.00 kVA : POLEMNT |  | 403SEG5981 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 2 | 24436 | 134 | 0.00548 | 8.1846e-05 | 10 | 670 | 2010/2011 | April-2010 | 4 | 2010
23250 | LV Fault - Waikune Prison | 2010-04-08 12:05 | 2010-04-08 | 2010-04-08 12:28 | Calculated | 15L03 | 15L03 - 3ph 25kVA polemnt |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 1 | 24436 | 23 | 0.00094 | 4.0923e-05 | 25 | 575 | 2010/2011 | April-2010 | 4 | 2010
23251 | Lightning - Mangaotaki Road | 2010-04-08 15:30 | 2010-04-08 | 2010-04-08 17:48 | Calculated | T2959 | T2959 - 1 Phase : 15.00 kVA : POLEMNT |  | 113SEG1514-1516 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 1 | 24436 | 138 | 0.00565 | 4.0923e-05 | 15 | 2070 | 2010/2011 | April-2010 | 4 | 2010
23252 | Lightning - Waitanguru Road | 2010-04-09 06:54 | 2010-04-09 | 2010-04-09 10:28 | Calculated | T2480 | T2480 - 1 Phase : 3.00 kVA : POLEMNT |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 1 | 24436 | 214 | 0.00876 | 4.0923e-05 | 3 | 642 | 2010/2011 | April-2010 | 4 | 2010
23253 | Old Age Tx - Moore Street | 2010-04-09 07:05 | 2010-04-09 | 2010-04-09 07:24 | Calculated | 20K10 | 20K10 - 3 Phase : 100.00 kVA : POLEMNT |  | 415SEG5704-REG28 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 42 | 24436 | 798 | 0.03266 | 0.0017188 | 100 | 1899 | 2010/2011 | April-2010 | 4 | 2010
23254 | Replace Pole 38/11/31 & Recover 14J02 | 2010-04-09 09:35 | 2010-04-09 | 2010-04-09 15:06 | Calculated | 5793 | 5793 - Fused Link 5793 |  | 410SEG5793-5746 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 267 | 67 | 24436 | 849 | 0.03474 | 0.0027419 | 411.5 | 8482 | 2010/2011 | April-2010 | 4 | 2010
23255 | Unknown - Tokirima Highway | 2010-04-10 08:00 | 2010-04-10 | 2010-04-10 09:48 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 12 | 24436 | 1296 | 0.05304 | 0.00049108 | 100 | 10800 | 2010/2011 | April-2010 | 4 | 2010
23256 | Install New Tx 4289 - Tangiwai Saw Mill | 2010-04-10 09:30 | 2010-04-10 | 2010-04-10 11:33 | Calculated | 6112 | 6112 - Air Break Switch 6112 |  | 428SEG6112-6113 | Tangiwai 416-05 RETIRED | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 123 | 4 | 24436 | 492 | 0.02013 | 0.00016369 | 4100 | 504300 | 2010/2011 | April-2010 | 4 | 2010
23257 | Unknown - Taharoa Road | 2010-04-10 23:33 | 2010-04-10 | 2010-04-10 23:45 | Calculated | 277 | 277 - Recloser with Bypass 277 |  | 125SEG277-268 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 120 | 24436 | 1440 | 0.05893 | 0.0049108 | 958.5 | 11501 | 2010/2011 | April-2010 | 4 | 2010
23259 | Unknown - Hangatiki East Road | 2010-04-12 07:00 | 2010-04-12 | 2010-04-12 09:03 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 9 | 24436 | 1107 | 0.0453 | 0.00036831 | 50 | 6149 | 2010/2011 | April-2010 | 4 | 2010
23260 | Geese/Ducks - Harpers Ave | 2010-04-13 06:30 | 2010-04-13 | 2010-04-13 07:25 | Calculated | 663 | 663 - Fused Link 663 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 6 | 24436 | 330 | 0.0135 | 0.00024554 | 90 | 4950 | 2010/2011 | April-2010 | 4 | 2010
23261 | Possum - Makokomiko Road | 2010-04-13 06:35 | 2010-04-13 | 2010-04-13 07:30 | Calculated | 09I04 | 09I04 - 1 Phase : 10.00 kVA : POLEMNT |  | 409SEG5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 3 | 24436 | 165 | 0.00675 | 0.00012277 | 10 | 549 | 2010/2011 | April-2010 | 4 | 2010
23263 | RAL Maintenance - Turoa Ski Base | 2010-04-13 15:29 | 2010-04-13 | 2010-04-13 16:03 | Calculated | 6586 | 6586 - Ring Main Unit 6586 |  | 415SEG6354-6586 | Turoa 415-03 | Rural B | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 34 | 1 | 24436 | 34 | 0.00139 | 4.0923e-05 | 3050 | 103700 | 2010/2011 | April-2010 | 4 | 2010
23264 | Unknown - Te Puke Road | 2010-04-14 08:40 | 2010-04-14 | 2010-04-14 10:36 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 2 | 24436 | 232 | 0.00949 | 8.1846e-05 | 8 | 928 | 2010/2011 | April-2010 | 4 | 2010
23268 | Broken Xarm @ 07E04 - Nihoniho Sub | 2010-04-14 11:30 | 2010-04-14 | 2010-04-14 16:41 | Calculated | 5609 | 5609 - Fused Link 5609 |  | 413SEG5609 | Ohura 413-01 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 271 | 24436 | 19241 | 0.7874 | 0.01109 | 3089.912 | 219383 | 2010/2011 | April-2010 | 4 | 2010
23269 | Birds - Makokomiko Road | 2010-04-15 17:55 | 2010-04-15 | 2010-04-15 19:23 | Calculated | 09K52 | 09K52 - 3 Phase : 15.00 kVA : POLEMNT |  | 409SEG5757-5761 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 2 | 24436 | 176 | 0.0072 | 8.1846e-05 | 15 | 1320 | 2010/2011 | April-2010 | 4 | 2010
23271 | Changing Main Line Pole - Benneydale | 2010-04-16 10:01 | 2010-04-16 | 2010-04-16 15:32 | Calculated | 1651 | 1651 - Fused Link 1651 |  | 103SEG1651-2227 | Benneydale 103-08 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 331 | 19 | 24436 | 6289 | 0.25737 | 0.00077754 | 90 | 29790 | 2010/2011 | April-2010 | 4 | 2010
23272 | Broken Xarm @ T1499 - Kahorekau Road | 2010-04-16 10:47 | 2010-04-16 | 2010-04-16 12:37 | Calculated | 448 | 448 - Air Break Switch 448 |  | 122SEG448-REG34J | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 42 | 24436 | 3066 | 0.12547 | 0.0017188 | 610 | 44529 | 2010/2011 | April-2010 | 4 | 2010
23274 | Changing Poles & Xarms between 1106 & T1896 | 2010-04-19 09:03 | 2010-04-19 | 2010-04-19 15:43 | Calculated | T1945 | T1945 - 3ph 25kVA POLEMNT |  | 114SEG1106-1105 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 385 | 41 | 24436 | 8963 | 0.36679 | 0.0016779 | 402.5 | 101227 | 2010/2011 | April-2010 | 4 | 2010
23273 | Fuse Fell Out - Mission House Dr | 2010-04-19 09:30 | 2010-04-19 | 2010-04-19 10:54 | Calculated | 09R28 | 09R28 - 3 Phase : 200.00 kVA : POLEMNT |  | 406SEG5896 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 3 | 24436 | 252 | 0.01031 | 0.00012277 | 200 | 16799 | 2010/2011 | April-2010 | 4 | 2010
25267 | Remove Disused Tx06Q04 & Replace X/arm On Pole 60 | 2010-04-19 09:32 | 2010-04-19 | 2010-04-19 11:20 | Calculated | 5588 | 5588 - Air Break Switch 5588 |  | 426SEG5588-5583 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 65 | 9 | 24436 | 585 | 0.02394 | 0.00036831 | 125 | 8124 | 2010/2011 | April-2010 | 4 | 2010
23275 | Changing Poles & Xarms between 1106 & T1896 | 2010-04-20 09:24 | 2010-04-20 | 2010-04-20 15:26 | Calculated | T1945 | T1945 - 3ph 25kVA POLEMNT |  | 114SEG1106-1105 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 347 | 27 | 24436 | 8330 | 0.34089 | 0.0011049 | 307.5 | 94165 | 2010/2011 | April-2010 | 4 | 2010
23278 | Fuse Pulled Apart - Puataata Street | 2010-04-20 13:00 | 2010-04-20 | 2010-04-20 14:15 | Calculated | 10S26 | 10S26 - 3 Phase : 200.00 kVA : GNDPAD |  | 423SEG6182-6183 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 55 | 24436 | 4125 | 0.16881 | 0.0022508 | 200 | 14999 | 2010/2011 | April-2010 | 4 | 2010
23279 | Changing Poles & Xarms between 1106 & T1896 | 2010-04-21 09:32 | 2010-04-21 | 2010-04-21 15:41 | Calculated | 1104 | 1104 - Fused Link 1104 |  | 114SEG1106-1105 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 369 | 5 | 24436 | 1845 | 0.0755 | 0.00020462 | 20 | 7379 | 2010/2011 | April-2010 | 4 | 2010
23289 | Unknown - Ngapuke Sub | 2010-04-22 00:08 | 2010-04-22 | 2010-04-22 01:27 | Calculated | 5218 | 5218 - Recloser with Bypass 5218 |  | 408SEG5275-5218 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 74 | 24436 | 5846 | 0.23924 | 0.0030283 | 493 | 38946 | 2010/2011 | April-2010 | 4 | 2010
23283 | Change T1789 - Tikitiki Road | 2010-04-22 13:40 | 2010-04-22 | 2010-04-22 16:17 | Calculated | T1789 | T1789 - 1 Phase : 15.00 kVA : POLEMNT |  | 117SEG1296-1273 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 157 | 3 | 24436 | 471 | 0.01927 | 0.00012277 | 15 | 2355 | 2010/2011 | April-2010 | 4 | 2010
23285 | Inframax vs LV - Waitete Road | 2010-04-22 14:20 | 2010-04-22 | 2010-04-22 14:36 | Calculated | T4 | T4 - 3ph 100kVA POL |  | 103SEG200-225 | Benneydale 103-01 | Urban A | Benneydale | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 17 | 24436 | 272 | 0.01113 | 0.00069569 | 100 | 1599 | 2010/2011 | April-2010 | 4 | 2010
23286 | Inframax vs LV (LV Off) - Waitete Road | 2010-04-22 14:20 | 2010-04-22 | 2010-04-22 17:02 | Calculated | T4 | T4 - 3ph 100kVA POL |  | 103SEG200-225 | Benneydale 103-01 | Urban A | Benneydale | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 17 | 24436 | 2754 | 0.1127 | 0.00069569 | 100 | 16199 | 2010/2011 | April-2010 | 4 | 2010
23287 | Kids Ball vs Line - Porou Street | 2010-04-22 17:20 | 2010-04-22 | 2010-04-22 18:19 | Calculated | 01B20 | 01B20 - 3ph 300kVA GNDPAD |  | 404SEGL1.20-A1.41 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADP | Other Accidental Damage by Private Individuals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 45 | 24436 | 2655 | 0.10865 | 0.0018415 | 300 | 17699 | 2010/2011 | April-2010 | 4 | 2010
23293 | Change Poles, DDO's & Tx 01B11 | 2010-04-25 09:00 | 2010-04-25 | 2010-04-25 13:42 | Calculated | 5967 | 5967 - Air Break Switch 5967 |  | 401SEG5967-5831 | Hakiaha 401-02 | Rural B | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 282 | 17 | 24436 | 4794 | 0.19619 | 0.00069569 | 680 | 191760 | 2010/2011 | April-2010 | 4 | 2010
23365 | Changing Poles & Xarms Between ABS1105 & T1945 | 2010-04-26 09:33 | 2010-04-26 | 2010-04-26 14:23 | Calculated | 1105 | 1105 - Air Break Switch 1105 |  | 114SEG1105-1118 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 290 | 15 | 24436 | 4350 | 0.17802 | 0.00061385 | 110 | 31899 | 2010/2011 | April-2010 | 4 | 2010
23366 | Replace Pole 58 - 01B25 to be backfed from 01B21 | 2010-04-26 10:27 | 2010-04-26 | 2010-04-26 14:12 | Calculated | 1.33 | 1.33 - Air Break Switch 1.33 |  | 404SEGA1.33-L1.20 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 192 | 147 | 24436 | 28224 | 1.155 | 0.0060157 | 507.3165 | 97404 | 2010/2011 | April-2010 | 4 | 2010
23368 | Bird - Maihiihi Road | 2010-04-27 09:05 | 2010-04-27 | 2010-04-27 10:17 | Calculated | T604 | T604 - 3ph 5kVA polemnt |  | 111SEG346-REG6 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 1 | 24436 | 72 | 0.00295 | 4.0923e-05 | 5 | 360 | 2010/2011 | April-2010 | 4 | 2010
23370 | Changing Poles & Xarms between ABS1105 & T1945 | 2010-04-27 09:32 | 2010-04-27 | 2010-04-27 14:55 | Calculated | 1105 | 1105 - Air Break Switch 1105 |  | 114SEG1105-1118 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 323 | 15 | 24436 | 4845 | 0.19827 | 0.00061385 | 110 | 35529 | 2010/2011 | April-2010 | 4 | 2010
23371 | Trees Line Down - Nihoniho Sub | 2010-04-27 15:55 | 2010-04-27 | 2010-04-27 17:10 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 34 | 24436 | 2550 | 0.10435 | 0.0013914 | 208.5 | 15637 | 2010/2011 | April-2010 | 4 | 2010
23372 | Trees Line Down - Nihoniho Sub | 2010-04-27 15:55 | 2010-04-27 | 2010-04-27 17:23 | Calculated | 5265 | 5265 - Fused Link 5265 |  | 412SEG5265-5628 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 22 | 24436 | 1936 | 0.07923 | 0.00090031 | 166 | 14607 | 2010/2011 | April-2010 | 4 | 2010
23373 | Trees Line Down - Rimu Road | 2010-04-27 15:55 | 2010-04-27 | 2010-04-27 18:48 | Calculated | 5628 | 5628 - Fused Link 5628 |  | 412SEG6741-5227 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 36 | 24436 | 2700 | 0.11049 | 0.0014732 | 219 | 16424 | 2010/2011 | April-2010 | 4 | 2010
23375 | Unknown - Pioi Station | 2010-04-27 17:05 | 2010-04-27 | 2010-04-27 19:32 | Calculated | 1617 | 1617 - Fused Link 1617 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 2 | 24436 | 294 | 0.01203 | 8.1846e-05 | 30 | 4410 | 2010/2011 | April-2010 | 4 | 2010
23376 | Unknown - Makino Road | 2010-04-28 09:40 | 2010-04-28 | 2010-04-28 11:32 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 28 | 24436 | 3136 | 0.12834 | 0.0011459 | 183.5 | 20551 | 2010/2011 | April-2010 | 4 | 2010
23377 | Change 09T05 from Polemount to Groundmount | 2010-04-28 10:01 | 2010-04-28 | 2010-04-28 15:04 | Calculated | 09T05 | 09T05 - 3 Phase : 250.00 kVA : POLEMNT |  | 417SEG5927RET | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 303 | 43 | 24436 | 13029 | 0.53319 | 0.0017597 | 250 | 75749 | 2010/2011 | April-2010 | 4 | 2010
23379 | Unknown - Paro Road | 2010-04-28 17:35 | 2010-04-28 | 2010-04-28 19:15 | Calculated | T2535 | T2535 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 1 | 24436 | 100 | 0.00409 | 4.0923e-05 | 10 | 1000 | 2010/2011 | April-2010 | 4 | 2010
23380 | Unknown - Makino Road | 2010-04-29 05:00 | 2010-04-29 | 2010-04-29 06:35 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 28 | 24436 | 2660 | 0.10886 | 0.0011459 | 183.5 | 17432 | 2010/2011 | April-2010 | 4 | 2010
23382 | Changing Poles & Xarms between ABS1105 & T1945 | 2010-04-29 09:37 | 2010-04-29 | 2010-04-29 14:31 | Calculated | 1105 | 1105 - Air Break Switch 1105 |  | 114SEG1105-1118 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 15 | 24436 | 4410 | 0.18047 | 0.00061385 | 110 | 32339 | 2010/2011 | April-2010 | 4 | 2010
23381 | Shift HV Pole @ 703 Aria Road | 2010-04-29 10:03 | 2010-04-29 | 2010-04-29 15:20 | Calculated | 1289 | 1289 - Air Break Switch 1289 |  | 117SEG1289-1292 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 311 | 5 | 24436 | 1555 | 0.06364 | 0.00020462 | 50 | 15550 | 2010/2011 | April-2010 | 4 | 2010
23383 | Maintenance - Marotiri Road | 2010-04-29 10:40 | 2010-04-29 | 2010-04-29 14:44 | Calculated | T755 | T755 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 244 | 3 | 24436 | 732 | 0.02996 | 0.00012277 | 10 | 2439 | 2010/2011 | April-2010 | 4 | 2010
23384 | Unknown - Mangahauhau Valley Road | 2010-04-29 17:55 | 2010-04-29 | 2010-04-29 18:51 | Calculated | 5717 | 5717 - Fused Link 5717 |  | 416SEG5717 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 5 | 24436 | 280 | 0.01146 | 0.00020462 | 45 | 2520 | 2010/2011 | April-2010 | 4 | 2010
23385 | Magpie @ 16H02 - Makino Road | 2010-04-30 05:30 | 2010-04-30 | 2010-04-30 10:15 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 285 | 28 | 24436 | 7980 | 0.32657 | 0.0011459 | 183.5 | 52297 | 2010/2011 | April-2010 | 4 | 2010
23388 | Unknown - Graces Road | 2010-04-30 10:07 | 2010-04-30 | 2010-04-30 17:55 | Calculated | 5733 | 5733 - Fused Link 5733 |  | 609SEG5163-5544 | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24436 |  | 0 | 0 |  |  | 2010/2011 | April-2010 | 4 | 2010
23389 | Change Red Tagged Pole | 2010-04-30 10:45 | 2010-04-30 | 2010-04-30 16:15 | Calculated | T2793 | T2793 - 3 Phase : 100.00 kVA : POLEMNT |  | 120SEG497-REG31 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 5 | 24436 | 1650 | 0.06752 | 0.00020462 | 125 | 41249 | 2010/2011 | April-2010 | 4 | 2010
23390 | Fuse Pulled Apart - Whakapapa Road | 2010-04-30 11:10 | 2010-04-30 | 2010-04-30 11:27 | Calculated | 10L01 | 10L01 - 1 Phase : 15.00 kVA : POLEMNT |  | 409SEG5319-5114 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 2 | 24436 | 34 | 0.00139 | 8.1846e-05 | 30 | 510 | 2010/2011 | April-2010 | 4 | 2010
23391 | Bird - Whakapapa Road | 2010-04-30 13:05 | 2010-04-30 | 2010-04-30 13:37 | Calculated | 09L11 | 09L11 - 1 Phase : 15.00 kVA : POLEMNT |  | 409SEG5114 | Southern 409-07 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 1 | 24436 | 32 | 0.00131 | 4.0923e-05 | 15 | 480 | 2010/2011 | April-2010 | 4 | 2010
23393 | Trees Auto Dialler Failed - Wairere Falls | 2010-04-30 23:40 | 2010-04-30 | 2010-05-01 01:25 | Calculated | 687 | 687 - Circuit Breaker 687 |  | No Segment | 207-01 Wairere Falls | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 230 | 24436 | 24150 | 0.9883 | 0.0094123 | 1760 | 184799 | 2010/2011 | April-2010 | 4 | 2010
23394 | Trees- Wairere Falls | 2010-05-01 08:25 | 2010-05-01 | 2010-05-01 08:34 | Calculated | 687 | 687 - Circuit Breaker 687 |  | No Segment | 207-01 Wairere Falls | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 230 | 24436 | 2070 | 0.08471 | 0.0094123 | 1760 | 15839 | 2010/2011 | May-2010 | 5 | 2010
23395 | Faulty DDO - Rangiatea Road | 2010-05-01 09:02 | 2010-05-01 | 2010-05-01 09:53 | Calculated | T1100 | T1100 - 3ph 50kVA POLEMNT |  | 109SEG334-396 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 7 | 24436 | 357 | 0.01461 | 0.00028646 | 50 | 2549 | 2010/2011 | May-2010 | 5 | 2010
23396 | Faulty L.A @ 07L07 - Meinga Road | 2010-05-01 12:25 | 2010-05-01 | 2010-05-01 16:43 | Calculated | 5736 | 5736 - Fused Link 5736 |  | 408SEG5736-5341 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 258 | 88 | 24436 | 22704 | 0.92912 | 0.0036012 | 613 | 158153 | 2010/2011 | May-2010 | 5 | 2010
23399 | Magpie - Pukeatua Road | 2010-05-01 14:40 | 2010-05-01 | 2010-05-01 18:32 | Calculated | 12H02 | 12H02 - 1 Phase : 25.00 kVA : POLEMNT |  | 410SEG5611-5400 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 232 | 6 | 24436 | 1392 | 0.05697 | 0.00024554 | 25 | 5799 | 2010/2011 | May-2010 | 5 | 2010
23397 | Faulty Link 5736 - Oruaiwi Road | 2010-05-01 15:50 | 2010-05-01 | 2010-05-01 16:43 | Calculated | 5639 | 5639 - Air Break Switch 5639 |  | 408SEG5639-5485 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 35 | 24436 | 1855 | 0.07591 | 0.0014323 | 918 | 48654 | 2010/2011 | May-2010 | 5 | 2010
23398 | DDO Off Xarm - Pureora Village | 2010-05-01 16:13 | 2010-05-01 | 2010-05-01 17:13 | Calculated | 456 | 456 - Fused Link 456 |  | 119SEG456 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 13 | 24436 | 780 | 0.03192 | 0.000532 | 60 | 3599 | 2010/2011 | May-2010 | 5 | 2010
23401 | Changing Poles & Xarms | 2010-05-03 09:23 | 2010-05-03 | 2010-05-03 15:16 | Calculated | 1339 | 1339 - Air Break Switch 1339 |  | 113SEG1339-1511 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 300 | 20 | 24436 | 6000 | 0.24554 | 0.00081846 | 225 | 67499 | 2010/2011 | May-2010 | 5 | 2010
23402 | Faulty Insulator - Wairere Falls | 2010-05-03 13:15 | 2010-05-03 | 2010-05-03 13:39 | Calculated | 687 | 687 - Circuit Breaker 687 |  | No Segment | 207-01 Wairere Falls | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 230 | 24436 | 5520 | 0.2259 | 0.0094123 | 1760 | 42240 | 2010/2011 | May-2010 | 5 | 2010
23403 | Faulty Insulator - Wairere Falls | 2010-05-03 13:40 | 2010-05-03 | 2010-05-03 14:17 | Calculated | 687 | 687 - Circuit Breaker 687 |  | No Segment | 207-01 Wairere Falls | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 230 | 24436 | 8510 | 0.34826 | 0.0094123 | 1760 | 65119 | 2010/2011 | May-2010 | 5 | 2010
23404 | Faulty Insulator - SH3 | 2010-05-03 15:03 | 2010-05-03 | 2010-05-03 15:38 | Calculated | 1318 | 1318 - Air Break Switch 1318 |  | 117SEG1318-770 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 36 | 24436 | 1260 | 0.05156 | 0.0014732 | 308 | 10779 | 2010/2011 | May-2010 | 5 | 2010
23405 | Faulty DDO - Pureora Village | 2010-05-03 17:32 | 2010-05-03 | 2010-05-03 19:10 | Calculated | 456 | 456 - Fused Link 456 |  | 119SEG456 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 13 | 24436 | 1274 | 0.05214 | 0.000532 | 60 | 5879 | 2010/2011 | May-2010 | 5 | 2010
23407 | Unknown - SH41 | 2010-05-04 12:00 | 2010-05-04 | 2010-05-04 15:40 | Calculated | 09R06 | 09R06 - 1 Phase : 15.00 kVA : POLEMNT |  | 406SEG5897-5481 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 220 | 4 | 24436 | 880 | 0.03601 | 0.00016369 | 15 | 3300 | 2010/2011 | May-2010 | 5 | 2010
23408 | Unknown - Troopers Road | 2010-05-04 13:30 | 2010-05-04 | 2010-05-04 15:51 | Calculated | 1365 | 1365 - Fused Link 1365 |  | 117SEG1365 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 3 | 24436 | 423 | 0.01731 | 0.00012277 | 70 | 9870 | 2010/2011 | May-2010 | 5 | 2010
23412 | Changing Poles & Xarms | 2010-05-05 09:22 | 2010-05-05 | 2010-05-05 15:43 | Calculated | 1339 | 1339 - Air Break Switch 1339 |  | 113SEG1339-1511 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 368 | 9 | 24436 | 3312 | 0.13554 | 0.00036831 | 90 | 33120 | 2010/2011 | May-2010 | 5 | 2010
23414 | Unknown - Graces Road | 2010-05-05 10:30 | 2010-05-05 | 2010-05-05 15:31 | Calculated | 5731 | 5731 - Fused Link 5731 |  | No Segment | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24436 |  | 0 | 0 |  |  | 2010/2011 | May-2010 | 5 | 2010
23415 | Unknown - Graces Road | 2010-05-05 10:30 | 2010-05-05 | 2010-05-05 16:18 | Calculated | 5733 | 5733 - Fused Link 5733 |  | 609SEG5163-5544 | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24436 |  | 0 | 0 |  |  | 2010/2011 | May-2010 | 5 | 2010
23413 | Raise Taps - Main Nth Road Piopio | 2010-05-05 10:39 | 2010-05-05 | 2010-05-05 11:08 | Calculated | T1667 | T1667 - 1 Phase : 15.00 kVA : POLEMNT |  | 116SEG1312-1362 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 3 | 24436 | 87 | 0.00356 | 0.00012277 | 15 | 435 | 2010/2011 | May-2010 | 5 | 2010
23417 | Broken DDO @ T585 - Whibley Road | 2010-05-05 17:18 | 2010-05-05 | 2010-05-05 17:41 | Calculated | 573 | 573 - Air Break Switch 573 |  | 111SEG346-REG6 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 54 | 24436 | 1242 | 0.05083 | 0.0022099 | 550 | 12649 | 2010/2011 | May-2010 | 5 | 2010
23418 | Vehicle vs Pole - SH4 | 2010-05-05 22:30 | 2010-05-05 | 2010-05-05 22:52 | Calculated | 1321 | 1321 - Recloser 1321 |  | 117SEG1314-1324 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 40 | 24436 | 880 | 0.03601 | 0.0016369 | 228.5 | 5026 | 2010/2011 | May-2010 | 5 | 2010
23419 | Vehicle vs Pole - SH4 | 2010-05-05 22:30 | 2010-05-05 | 2010-05-05 22:52 | Calculated | T3293 | T3293 - 3 Phase : 75.00 kVA : POLEMNT |  | 117SEG1314-1324 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24436 |  | 0 | 0 |  |  | 2010/2011 | May-2010 | 5 | 2010
25249 | Line Renewal - Bell Rd | 2010-05-06 09:12 | 2010-05-06 | 2010-05-06 16:14 | Calculated | TF1A81 | TF1A81 - Transformer Fuse: TF1A81 |  | 401SEGA5.19-5967 | Hakiaha 401-02 | Rural B | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 421 | 16 | 24436 | 6828 | 0.27942 | 0.00065477 | 3200 | 1365600 | 2010/2011 | May-2010 | 5 | 2010
23421 | Vehicle vs Pole - SH 4 By Tuhua Rd | 2010-05-06 09:13 | 2010-05-06 | 2010-05-06 13:07 | Calculated | 1315 | 1315 - Sectionaliser 1315 |  | 117SEG1315-1326 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 218 | 40 | 24436 | 5830 | 0.23858 | 0.0016369 | 228.5 | 34723 | 2010/2011 | May-2010 | 5 | 2010
23425 | Changing Poles & Xarms | 2010-05-06 09:24 | 2010-05-06 | 2010-05-06 16:38 | Calculated | 1339 | 1339 - Air Break Switch 1339 |  | 113SEG1339-1511 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 418 | 76 | 24436 | 3762 | 0.15395 | 0.0031102 | 558 | 37620 | 2010/2011 | May-2010 | 5 | 2010
23427 | Unknown - Aotearoa Road | 2010-05-06 11:35 | 2010-05-06 | 2010-05-06 14:16 | Calculated | 562 | 562 - Fused Link 562 |  | 122SEG562 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 13 | 24436 | 2093 | 0.08565 | 0.000532 | 125 | 20124 | 2010/2011 | May-2010 | 5 | 2010
23428 | Unknown - Aotearoa Road | 2010-05-06 15:00 | 2010-05-06 | 2010-05-06 16:26 | Calculated | 562 | 562 - Fused Link 562 |  | 122SEG562 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 13 | 24436 | 1118 | 0.04575 | 0.000532 | 125 | 10749 | 2010/2011 | May-2010 | 5 | 2010
23429 | Lower Tap - Ongarue Village Road | 2010-05-06 15:54 | 2010-05-06 | 2010-05-06 16:17 | Calculated | 04I20 | 04I20 - 1 Phase : 30.00 kVA : POLEMNT |  | 421SEG5809-5363 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 5 | 24436 | 115 | 0.00471 | 0.00020462 | 30 | 690 | 2010/2011 | May-2010 | 5 | 2010
25292 | Line Down - Marotiri Sub | 2010-05-07 04:15 | 2010-05-07 | 2010-05-07 04:26 | Calculated | CB1 | CB1 - Circuit Breaker Mokai Feeder B1 |  | No Segment | 212-01 Marotiri | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 196 | 24436 | 2165 | 0.0886 | 0.008021 | 1700 | 18784 | 2010/2011 | May-2010 | 5 | 2010
23432 | Changing Poles & Xarms | 2010-05-07 09:29 | 2010-05-07 | 2010-05-07 15:06 | Calculated | 1339 | 1339 - Air Break Switch 1339 |  | 113SEG1339-1511 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 329 | 76 | 24436 | 2961 | 0.12117 | 0.0031102 | 558 | 29610 | 2010/2011 | May-2010 | 5 | 2010
23433 | Unknown - Taharoa | 2010-05-07 20:16 | 2010-05-07 | 2010-05-07 20:25 | Calculated | 788 | 788 - Circuit Breaker 788 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24436 |  | 0 | 0 |  |  | 2010/2011 | May-2010 | 5 | 2010
23434 | Unknown - Clarke Street | 2010-05-08 20:25 | 2010-05-08 | 2010-05-08 21:22 | Calculated | T504 | T504 - 3 Phase : 100.00 kVA : POLEMNT |  | 110SEG312-629 | McDonalds 110-01 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 31 | 24436 | 1767 | 0.07231 | 0.0012686 | 100 | 5699 | 2010/2011 | May-2010 | 5 | 2010
23435 | Mokauiti Line Renewal Project | 2010-05-10 09:31 | 2010-05-10 | 2010-05-10 14:04 | Calculated | 1708 | 1708 - Fused Link 1708 |  | 115SEG1708-1738 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 273 | 18 | 24436 | 4914 | 0.2011 | 0.00073662 | 100 | 27299 | 2010/2011 | May-2010 | 5 | 2010
23436 | Replace Tx Pole 01A30 | 2010-05-11 08:23 | 2010-05-11 | 2010-05-11 15:50 | Calculated | 5967 | 5967 - Air Break Switch 5967 |  | 401SEG5967-5831 | Hakiaha 401-02 | Rural B | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 407 | 23 | 24436 | 5451 | 0.22307 | 0.00094123 | 400 | 123699 | 2010/2011 | May-2010 | 5 | 2010
23437 | Changing Poles & Xarms | 2010-05-11 09:33 | 2010-05-11 | 2010-05-11 15:27 | Calculated | 1708 | 1708 - Fused Link 1708 |  | 115SEG1708-1738 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 18 | 24436 | 6372 | 0.26076 | 0.00073662 | 105 | 37169 | 2010/2011 | May-2010 | 5 | 2010
23438 | Changing Poles & Xarms | 2010-05-12 09:33 | 2010-05-12 | 2010-05-12 15:51 | Calculated | 1708 | 1708 - Fused Link 1708 |  | 115SEG1708-1738 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 378 | 18 | 24436 | 6804 | 0.27844 | 0.00073662 | 105 | 39689 | 2010/2011 | May-2010 | 5 | 2010
23440 | Fit New Tx to Existing Structure (PT Power Systems) | 2010-05-12 10:05 | 2010-05-12 | 2010-05-12 10:45 | Calculated | 1106 | 1106 - Air Break Switch 1106 |  | 114SEG1106-1105 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 40 | 39 | 24436 | 1560 | 0.06384 | 0.001596 | 377.5 | 15099 | 2010/2011 | May-2010 | 5 | 2010
23441 | Move Tx & Connect Cabling | 2010-05-12 10:18 | 2010-05-12 | 2010-05-12 16:16 | Calculated | 6340 | 6340 - Ring Main Unit 6340 |  | 419SEG5970-6340 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24436 |  | 0 | 0 |  |  | 2010/2011 | May-2010 | 5 | 2010
23442 | Fuse Pulled Apart - Main North Road | 2010-05-12 10:25 | 2010-05-12 | 2010-05-12 12:30 | Calculated | 04I10 | 04I10 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5345 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 5 | 24436 | 625 | 0.02558 | 0.00020462 | 15 | 1875 | 2010/2011 | May-2010 | 5 | 2010
23448 | Fuse Pulled Apart - Mahoe Road | 2010-05-13 09:08 | 2010-05-13 | 2010-05-13 09:19 | Calculated | 08K14 | 08K14 - 3 Phase : 200.00 kVA : POLEMNT |  | 408SEG5116-5816 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 34 | 24436 | 374 | 0.01531 | 0.0013914 | 200 | 2199 | 2010/2011 | May-2010 | 5 | 2010
23449 | Changing Poles & Xarms | 2010-05-13 09:33 | 2010-05-13 | 2010-05-13 14:11 | Calculated | 1708 | 1708 - Fused Link 1708 |  | 115SEG1708-1738 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 278 | 18 | 24436 | 5004 | 0.20478 | 0.00073662 | 105 | 29189 | 2010/2011 | May-2010 | 5 | 2010
23451 | Jumper Off - Kumara Road | 2010-05-13 10:35 | 2010-05-13 | 2010-05-13 14:14 | Calculated | T1960 | T1960 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1108-1102 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 2 | 24436 | 438 | 0.01792 | 8.1846e-05 | 10 | 2190 | 2010/2011 | May-2010 | 5 | 2010
23452 | Trees in Line - Kururau Road | 2010-05-13 12:08 | 2010-05-13 | 2010-05-13 12:57 | Calculated | 08G09 | 08G09 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 3 | 24436 | 147 | 0.00602 | 0.00012277 | 15 | 735 | 2010/2011 | May-2010 | 5 | 2010
23453 | Jumper Off Links - Borck's Road | 2010-05-13 12:25 | 2010-05-13 | 2010-05-13 15:36 | Calculated | 5339 | 5339 - Fused Link 5339 |  | 402SEG5339 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 10 | 24436 | 1910 | 0.07816 | 0.00040923 | 75 | 14325 | 2010/2011 | May-2010 | 5 | 2010
23455 | Broken Xarm - Ranginui Road | 2010-05-13 13:20 | 2010-05-13 | 2010-05-13 23:25 | Calculated | 1262 | 1262 - Recloser 1262 |  | 121SEG712-1262 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 605 | 165 | 24436 | 47944 | 1.962 | 0.0067523 | 1706.5 | 445562 | 2010/2011 | May-2010 | 5 | 2010
23454 | Jumper Off Links - Okahukura Back Road | 2010-05-13 15:05 | 2010-05-13 | 2010-05-13 15:36 | Calculated | 5645 | 5645 - Air Break Switch 5645 |  | 402SEG5645-5471 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 106 | 24436 | 3286 | 0.13447 | 0.0043379 | 1043 | 32332 | 2010/2011 | May-2010 | 5 | 2010
23461 | Changing Poles & Xarms | 2010-05-14 08:58 | 2010-05-14 | 2010-05-14 14:46 | Calculated | 1339 | 1339 - Air Break Switch 1339 |  | 113SEG1339-1511 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 296 | 9 | 24436 | 2664 | 0.10902 | 0.00036831 | 90 | 26640 | 2010/2011 | May-2010 | 5 | 2010
23462 | Replace Broken Xarm - Mangawhio Road | 2010-05-14 11:25 | 2010-05-14 | 2010-05-14 13:30 | Calculated | 421 | 421 - Air Break Switch 421 |  | 121SEG421-424 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 50 | 24436 | 6250 | 0.25577 | 0.0020462 | 429 | 53624 | 2010/2011 | May-2010 | 5 | 2010
23464 | Unknown - Kaitieke Road | 2010-05-14 17:45 | 2010-05-14 | 2010-05-14 19:58 | Calculated | 13K07 | 13K07 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 2 | 24436 | 266 | 0.01089 | 8.1846e-05 | 10 | 1330 | 2010/2011 | May-2010 | 5 | 2010
23465 | Change Poles 49, 50 & 59 | 2010-05-15 09:03 | 2010-05-15 | 2010-05-15 13:42 | Calculated | 5967 | 5967 - Air Break Switch 5967 |  | 401SEG5967-5831 | Hakiaha 401-02 | Rural B | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 279 | 17 | 24436 | 4743 | 0.1941 | 0.00069569 | 680 | 189720 | 2010/2011 | May-2010 | 5 | 2010
23471 | Faulty Tx - Oio No. 1 Road | 2010-05-16 07:20 | 2010-05-16 | 2010-05-17 14:14 | Calculated | 12H05 | 12H05 - 1 Phase : 15.00 kVA : POLEMNT |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1854 | 1 | 24436 | 1854 | 0.07587 | 4.0923e-05 | 15 | 27810 | 2010/2011 | May-2010 | 5 | 2010
23473 | Magpie @ 04K02 - Ongarue | 2010-05-17 07:40 | 2010-05-17 | 2010-05-17 11:23 | Calculated | 5656 | 5656 - Fused Link 5656 |  | 421SEG5656-5669 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 223 | 85 | 24436 | 15408 | 0.63055 | 0.0034785 | 574.8333 | 103512 | 2010/2011 | May-2010 | 5 | 2010
23477 | SWER Backfeed - Mokauiti Line Renewal Project | 2010-05-17 08:31 | 2010-05-17 | 2010-05-17 08:36 | Calculated | 1716 | 1716 - Recloser with Bypass1716 |  | 115SEG1716-1719 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 33 | 24436 | 165 | 0.00675 | 0.0013505 | 250 | 1249 | 2010/2011 | May-2010 | 5 | 2010
23478 | SWER Backfeed - Mokauiti Line Renewal Project | 2010-05-17 08:37 | 2010-05-17 | 2010-05-17 08:39 | Calculated | 1717 | 1717 - Recloser with Bypass 1717 |  | 115SEG1717-1723 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 23 | 24436 | 46 | 0.00188 | 0.00094123 | 180.5 | 361 | 2010/2011 | May-2010 | 5 | 2010
23479 | Mokauiti Line Renewal Project | 2010-05-17 08:49 | 2010-05-17 | 2010-05-17 16:12 | Calculated | 1708 | 1708 - Fused Link 1708 |  | 115SEG1708-1738 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 410 | 56 | 24436 | 18116 | 0.74137 | 0.0022917 | 355 | 117804 | 2010/2011 | May-2010 | 5 | 2010
23480 | Possum - Sommerville Road | 2010-05-17 09:35 | 2010-05-17 | 2010-05-17 10:03 | Calculated | T1512 | T1512 - 2ph 25kVA POLEMNT |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 1 | 24436 | 28 | 0.00115 | 4.0923e-05 | 25 | 700 | 2010/2011 | May-2010 | 5 | 2010
23482 | Repair Damaged Cable - BDS to High Noon | 2010-05-17 12:48 | 2010-05-17 | 2010-05-17 16:24 | Calculated | 6147 | 6147 - Circuit Breaker 6147 |  | 415SEG6598RET | Turoa 415-03 | Rural B | Turoa | Direct from Ohakune Supply |  | Asset Related | Cable - Underground | FAIL:FCAB |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24436 |  | 0 | 0 |  |  | 2010/2011 | May-2010 | 5 | 2010
23485 | Line Down - Tuamatamaire | 2010-05-18 00:55 | 2010-05-18 | 2010-05-18 05:39 | Calculated | 1640 | 1640 - Recloser 1640 |  | 128SEG REG2-1609 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 284 | 624 | 24436 | 151892 | 6.2159 | 0.025536 | 3731.8233 | 882151 | 2010/2011 | May-2010 | 5 | 2010
23488 | Mokauiti Line Renewal Project | 2010-05-18 08:43 | 2010-05-18 | 2010-05-18 15:50 | Calculated | 1710 | 1710 - Air Break Switch 1710 |  | 115SEGTempABS1-1705 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 380 | 36 | 24436 | 10316 | 0.42216 | 0.0014732 | 215 | 63759 | 2010/2011 | May-2010 | 5 | 2010
23490 | Unknown - Matiere Road | 2010-05-18 16:55 | 2010-05-18 | 2010-05-18 18:30 | Calculated | 1113 | 1113 - Fused Link 1113 |  | 114SEG1113-1122 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 13 | 24436 | 1235 | 0.05054 | 0.000532 | 80 | 7600 | 2010/2011 | May-2010 | 5 | 2010
23492 | Broken DDO @ T2011 - Kohua Road | 2010-05-18 20:38 | 2010-05-18 | 2010-05-18 21:30 | Calculated | 1701 | SEG1701-1710 - 115SEG1701-1710 |  | No Segment | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 183 | 24436 | 9516 | 0.38943 | 0.007489 | 1307.25 | 67976 | 2010/2011 | May-2010 | 5 | 2010
23493 | Mokauiti Line Renewal Project | 2010-05-19 08:58 | 2010-05-19 | 2010-05-19 16:08 | Calculated | 1710 | 1710 - Air Break Switch 1710 |  | 115SEGTempABS1-1705 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 390 | 36 | 24436 | 10628 | 0.43493 | 0.0014732 | 215 | 65704 | 2010/2011 | May-2010 | 5 | 2010
23496 | Mokauiti Line Renewal Project | 2010-05-20 09:01 | 2010-05-20 | 2010-05-20 15:53 | Calculated | 1710 | 1710 - Air Break Switch 1710 |  | 115SEGTempABS1-1705 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 36 | 24436 | 8692 | 0.3557 | 0.0014732 | 215 | 53679 | 2010/2011 | May-2010 | 5 | 2010
23497 | SWER Backfeed - Mokauiti Line Renewal Project | 2010-05-20 16:03 | 2010-05-20 | 2010-05-20 16:05 | Calculated | 1717 | 1717 - Recloser with Bypass 1717 |  | 115SEG1717-1723 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 2 | 23 | 24436 | 46 | 0.00188 | 0.00094123 | 180.5 | 361 | 2010/2011 | May-2010 | 5 | 2010
23498 | SWER Backfeed - Mokauiti Line Renewal Project | 2010-05-20 16:10 | 2010-05-20 | 2010-05-20 16:12 | Calculated | 1716 | 1716 - Recloser with Bypass1716 |  | 115SEG1716-1719 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 33 | 24436 | 66 | 0.0027 | 0.0013505 | 250 | 499 | 2010/2011 | May-2010 | 5 | 2010
23499 | SWER Backfeed - SH4 | 2010-05-21 09:35 | 2010-05-21 | 2010-05-21 09:36 | Calculated | 1728 | 1728 - Recloser 1728 |  | 117SEG1728-1260 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 42 | 24436 | 42 | 0.00172 | 0.0017188 | 335.5 | 335 | 2010/2011 | May-2010 | 5 | 2010
25271 | Change Pole 124/66 - Mapara Rd | 2010-05-21 10:03 | 2010-05-21 | 2010-05-21 15:11 | Calculated | 1728 | 1728 - Recloser 1728 |  | 117SEG1728-1260 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 308 | 18 | 24436 | 5544 | 0.22688 | 0.00073662 | 135 | 41579 | 2010/2011 | May-2010 | 5 | 2010
23501 | National Park Line Renewal Project | 2010-05-21 10:05 | 2010-05-21 | 2010-05-21 14:29 | Calculated | 5162 | 5162 - Fused Link 5162 |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 5 | 24436 | 1320 | 0.05402 | 0.00020462 | 45 | 11880 | 2010/2011 | May-2010 | 5 | 2010
23500 | SWER Backfeed - SH4 | 2010-05-21 15:34 | 2010-05-21 | 2010-05-21 15:35 | Calculated | 1728 | 1728 - Recloser 1728 |  | 117SEG1728-1260 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 43 | 24436 | 43 | 0.00176 | 0.0017597 | 335.5 | 335 | 2010/2011 | May-2010 | 5 | 2010
23503 | Trees Through Lines - Kirikau Valley Road | 2010-05-21 19:25 | 2010-05-21 | 2010-05-21 22:50 | Calculated | SEG5314-5765 | SEG5314-5765 - 403SEG5314-5765 |  | No Segment | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 205 | 15 | 24436 | 3075 | 0.12584 | 0.00061385 | 98 | 20089 | 2010/2011 | May-2010 | 5 | 2010
23504 | Trees Through Lines - Kirikau Valley Road | 2010-05-21 19:25 | 2010-05-21 | 2010-05-22 10:24 | Calculated | 5765 | 5765 - Fused Link 5765 |  | 403SEG5765-5653 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 899 | 6 | 24436 | 5394 | 0.22074 | 0.00024554 | 28 | 25172 | 2010/2011 | May-2010 | 5 | 2010
23505 | Trees Through Lines - Kirikau Valley Road | 2010-05-22 09:40 | 2010-05-22 | 2010-05-22 10:24 | Calculated | SEG5314-5765 | SEG5314-5765 - 403SEG5314-5765 |  | No Segment | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 15 | 24436 | 660 | 0.02701 | 0.00061385 | 98 | 4311 | 2010/2011 | May-2010 | 5 | 2010
23506 | Jumper Off - Rauriki Road | 2010-05-22 12:50 | 2010-05-22 | 2010-05-22 13:45 | Calculated | T1919 | T1919 - 1 Phase : 10.00 kVA : POLEMNT |  | 115SEG1738-1709 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 2 | 24436 | 110 | 0.0045 | 8.1846e-05 | 10 | 550 | 2010/2011 | May-2010 | 5 | 2010
23507 | Unknown - Mairoa Road | 2010-05-22 20:10 | 2010-05-22 | 2010-05-22 20:17 | Calculated | 113 | 113 - Circuit Breaker 113 |  | 107SEG243-113 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 52 | 24436 | 364 | 0.0149 | 0.002128 | 455 | 3184 | 2010/2011 | May-2010 | 5 | 2010
23508 | Cable Fault - Manunui Freezing Works | 2010-05-23 08:50 | 2010-05-23 | 2010-05-24 14:57 | Calculated | 5552 | 5552 - Fused Link 5552 |  | 407SEG5405 | Manunui 407-01 (was Affco) | Rural B | Manunui / AFFCO Retired | Manunui Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1807 | 2 | 24436 | 3614 | 0.1479 | 8.1846e-05 | 550 | 993850 | 2010/2011 | May-2010 | 5 | 2010
23509 | Repair Broken Stay - Ngapaenga Road | 2010-05-25 11:24 | 2010-05-25 | 2010-05-25 11:35 | Calculated | T576 | T576 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 2 | 24436 | 22 | 0.0009 | 8.1846e-05 | 10 | 110 | 2010/2011 | May-2010 | 5 | 2010
23510 | Fuse Pulled Apart - Mangapura Road | 2010-05-25 15:20 | 2010-05-25 | 2010-05-25 17:27 | Calculated | 17H01 | 17H01 - 1 Phase : 15.00 kVA : POLEMNT |  | 410SEG5511-5517 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 4 | 24436 | 508 | 0.02079 | 0.00016369 | 15 | 1905 | 2010/2011 | May-2010 | 5 | 2010
23513 | Wind - Te Raumauku Road | 2010-05-26 01:00 | 2010-05-26 | 2010-05-26 06:58 | Calculated | 355 | 355 - Fused Link 355 |  | 112SEG355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 358 | 10 | 24436 | 3580 | 0.14651 | 0.00040923 | 95 | 34009 | 2010/2011 | May-2010 | 5 | 2010
23514 | Repair Centre Conductor etc | 2010-05-26 10:06 | 2010-05-26 | 2010-05-26 13:11 | Calculated | T72 | T72 - 3ph 30kVA POLEMNT |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 185 | 13 | 24436 | 2342 | 0.09584 | 0.000532 | 80 | 14449 | 2010/2011 | May-2010 | 5 | 2010
23515 | Wind - Mangatea Road | 2010-05-26 10:10 | 2010-05-26 | 2010-05-26 10:23 | Calculated | T1084 | T1084 - 3ph 15kVA POL |  | 104SEG730-547 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 4 | 24436 | 52 | 0.00213 | 0.00016369 | 15 | 195 | 2010/2011 | May-2010 | 5 | 2010
23516 | Insulate HV Tails @ 20L66 - Change Red Tagged Pole? | 2010-05-26 21:53 | 2010-05-26 | 2010-05-27 00:20 | Calculated | 5925 | 5925 - Air Break Switch 5925 |  | 414SEG5715-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 132 | 274 | 24436 | 36168 | 1.4801 | 0.011213 | 1646.2451 | 217304 | 2010/2011 | May-2010 | 5 | 2010
23523 | Replacing Strain Pole 73/6 - Kaahu Road | 2010-05-27 09:16 | 2010-05-27 | 2010-05-27 09:52 | Calculated | T3131 | T3131 - 3 Phase : 50.00 kVA : POLEMNT |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 47 | 24436 | 10306 | 0.42175 | 0.0019234 | 522.5 | 115315 | 2010/2011 | May-2010 | 5 | 2010
23521 | Branch on Line - Awatane Road | 2010-05-27 09:19 | 2010-05-27 | 2010-05-27 09:53 | Calculated | T239 | T239 - 3 Phase : 30.00 kVA : POLEMNT |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 8 | 24436 | 272 | 0.01113 | 0.00032739 | 30 | 1020 | 2010/2011 | May-2010 | 5 | 2010
23519 | Jumper Off - SH3 - Awakau | 2010-05-27 10:17 | 2010-05-27 | 2010-05-27 12:33 | Calculated | 1606 | 1606 - Air Break Switch 1606 |  | 128SEG1600-1623 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 20 | 24436 | 2720 | 0.11131 | 0.00081846 | 125 | 16999 | 2010/2011 | May-2010 | 5 | 2010
23522 | Replace Rotten Xarm on pole 54 | 2010-05-27 10:33 | 2010-05-27 | 2010-05-27 12:07 | Calculated | 1102 | 1102 - Air Break Switch 1102 |  | 114SEG1102-1126RET | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 53 | 24436 | 4982 | 0.20388 | 0.0021689 | 368 | 34591 | 2010/2011 | May-2010 | 5 | 2010
23520 | ABS 1606 Faulty - SH3 Awakau | 2010-05-27 11:12 | 2010-05-27 | 2010-05-27 12:33 | Calculated | T239 | T239 - 3 Phase : 30.00 kVA : POLEMNT |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 8 | 24436 | 648 | 0.02652 | 0.00032739 | 30 | 2430 | 2010/2011 | May-2010 | 5 | 2010
23525 | Unknown - Mahoenui | 2010-05-27 17:38 | 2010-05-27 | 2010-05-27 17:44 | Calculated | 1010 | 1010 - Circuit Breaker Mahoenui 1010 |  | No Segment | 209-01 Mahoenui | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 633 | 24436 | 3798 | 0.15543 | 0.025904 | 3882.5 | 23294 | 2010/2011 | May-2010 | 5 | 2010
23526 | Unknown - Main Nth Road Otorohanga | 2010-05-28 04:20 | 2010-05-28 | 2010-05-28 10:34 | Calculated | T230 | T230 - 3ph 30kVA polemnt |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 374 | 6 | 24436 | 2244 | 0.09183 | 0.00024554 | 30 | 11220 | 2010/2011 | May-2010 | 5 | 2010
23527 | Birds - Waituhi Road | 2010-05-28 06:25 | 2010-05-28 | 2010-05-28 08:02 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 21 | 24436 | 2037 | 0.08336 | 0.00085939 | 160 | 15520 | 2010/2011 | May-2010 | 5 | 2010
23528 | Multiple Worksites - Treescape Also in Area | 2010-05-28 09:08 | 2010-05-28 | 2010-05-28 15:12 | Calculated | T1840 | T1840 - 1 Phase : 15.00 kVA : POLEMNT |  | 128SEG1616 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 49 | 24436 | 16216 | 0.66361 | 0.0020052 | 385.5 | 126984 | 2010/2011 | May-2010 | 5 | 2010
25285 | Jumper Off Tx 2155 - Takarei Tce | 2010-05-29 07:51 | 2010-05-29 | 2010-05-29 11:46 | Calculated | T2155 | T2155 - 3 Phase : 200.00 kVA : GNDPAD |  | 128SEG1523 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 235 | 484 | 24436 | 35630 | 1.4581 | 0.019807 | 2732.0376 | 171269 | 2010/2011 | May-2010 | 5 | 2010
25284 | Replace Link 5619 | 2010-05-29 09:39 | 2010-05-29 | 2010-05-29 10:47 | Calculated | 5619 | 5619 - Fused Link 5619 |  | 426SEG6205-5619 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 86 | 24436 | 5853 | 0.23952 | 0.0035194 | 582.5 | 39648 | 2010/2011 | May-2010 | 5 | 2010
23531 | Line Down (Pole 36) - Turangi Sub | 2010-05-30 10:01 | 2010-05-30 | 2010-05-30 10:56 | Calculated | 5200 | 5200 - Circuit Breaker 5200 |  | No Segment | 505-01 Turangi | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 848 | 24436 | 46640 | 1.9087 | 0.034703 | 8055 | 443024 | 2010/2011 | May-2010 | 5 | 2010
23532 | Line Down (Pole 36) - Tukehu Street | 2010-05-30 10:01 | 2010-05-30 | 2010-05-30 14:34 | Calculated | 5207 | 5207 - Air Break Switch 5207 |  | 424SEG5207-6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 273 | 47 | 24436 | 12831 | 0.52509 | 0.0019234 | 500 | 136499 | 2010/2011 | May-2010 | 5 | 2010
23533 | Burning Line Tap T2155 - SH3 | 2010-05-30 14:52 | 2010-05-30 | 2010-05-30 15:37 | Calculated | 1619 | 1619 - Fused Link 1619 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 449 | 24436 | 20205 | 0.82685 | 0.018375 | 2534 | 114029 | 2010/2011 | May-2010 | 5 | 2010
23534 | Jumper Off - Mangatoa Road | 2010-05-30 18:10 | 2010-05-30 | 2010-05-30 21:41 | Calculated | T1616 | T1616 - 1 Phase : 15.00 kVA : POLEMNT |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 211 | 2 | 24436 | 422 | 0.01727 | 8.1846e-05 | 15 | 3165 | 2010/2011 | May-2010 | 5 | 2010
23535 | Jumper Off - Moana Quay | 2010-05-30 20:50 | 2010-05-30 | 2010-05-30 21:41 | Calculated | 563 | 563 - Air Break Switch 563 |  | 125SEG563-569 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 25 | 24436 | 1275 | 0.05218 | 0.0010231 | 225 | 11475 | 2010/2011 | May-2010 | 5 | 2010
23536 | Unknown - Okau Road | 2010-05-31 08:35 | 2010-05-31 | 2010-05-31 13:49 | Calculated | T3190 | T3190 - 1 Phase : 15.00 kVA : POLEMNT |  | 128SEG1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 314 | 1 | 24436 | 314 | 0.01285 | 4.0923e-05 | 15 | 4710 | 2010/2011 | May-2010 | 5 | 2010
23538 | Line Renewal - National Park | 2010-05-31 09:35 | 2010-05-31 | 2010-05-31 14:42 | Calculated | 5329 | 5329 - Fused Link 5329 |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 19 | 24436 | 5833 | 0.23871 | 0.00077754 | 135.5 | 41598 | 2010/2011 | May-2010 | 5 | 2010
23539 | Unknown - Ruatiti Sub | 2010-06-01 08:30 | 2010-06-01 | 2010-06-01 12:43 | Calculated | 5806 | 5806 - Recloser with Bypass 5806 |  | 410SEG5806-5793 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 253 | 67 | 24506 | 16951 | 0.69171 | 0.002734 | 411.5 | 104109 | 2010/2011 | June-2010 | 6 | 2010
23541 | Burnt Fuse Carrier - Turakina Valley Road | 2010-06-01 13:05 | 2010-06-01 | 2010-06-01 16:04 | Calculated | 22O06 | 22O06 - 1 Phase : 15.00 kVA : POLEMNT |  | 416SEG5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 1 | 24506 | 179 | 0.0073 | 4.0806e-05 | 15 | 2685 | 2010/2011 | June-2010 | 6 | 2010
23542 | Wind - Upper Retaruke | 2010-06-01 14:30 | 2010-06-01 | 2010-06-01 17:32 | Calculated | 5407 | 5407 - Sectionaliser with Bypass 5407 |  | 410SEG5407-5433 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 182 | 45 | 24506 | 8190 | 0.3342 | 0.0018363 | 267.5 | 48684 | 2010/2011 | June-2010 | 6 | 2010
23543 | Tree Through Line - Mairoa Road | 2010-06-01 15:35 | 2010-06-01 | 2010-06-01 16:51 | Calculated | 1334 | 1334 - Air Break Switch 1334 |  | 116SEG1334-269 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 42 | 24506 | 3192 | 0.13025 | 0.0017139 | 252.5 | 19189 | 2010/2011 | June-2010 | 6 | 2010
23544 | Car vs Pole - Golf Road Extension | 2010-06-01 15:40 | 2010-06-01 | 2010-06-01 16:21 | Calculated | 5119 | 5119 - Recloser 5119 |  | No Segment | No Asset Group | Remote Rural F | Northern | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 155 | 24506 | 6355 | 0.25932 | 0.006325 | 1608.5 | 65948 | 2010/2011 | June-2010 | 6 | 2010
23545 | Car vs Pole - Borck's Road | 2010-06-01 15:40 | 2010-06-01 | 2010-06-01 18:14 | Calculated | 5339 | 5339 - Fused Link 5339 |  | 402SEG5339 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 10 | 24506 | 1540 | 0.06284 | 0.00040806 | 75 | 11550 | 2010/2011 | June-2010 | 6 | 2010
23546 | Fuse Fell Out - Mahuri Road | 2010-06-01 15:40 | 2010-06-01 | 2010-06-01 20:00 | Calculated | 06H03 | 06H03 - 2 Phase : 15.00 kVA : POLEMNT |  | 402SEG5339 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 260 | 1 | 24506 | 260 | 0.01061 | 4.0806e-05 | 15 | 3900 | 2010/2011 | June-2010 | 6 | 2010
23547 | Unknown - Pukemapou Road | 2010-06-01 16:35 | 2010-06-01 | 2010-06-01 19:17 | Calculated | 364 | 364 - Fused Link 364 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 31 | 24506 | 5022 | 0.20493 | 0.001265 | 260 | 42119 | 2010/2011 | June-2010 | 6 | 2010
23548 | Jumper Off - Mahoe Road | 2010-06-01 17:06 | 2010-06-01 | 2010-06-01 18:12 | Calculated | 552 | 552 - Air Break Switch 552 |  | 101SEG552-290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 13 | 24506 | 858 | 0.03501 | 0.00053048 | 95 | 6269 | 2010/2011 | June-2010 | 6 | 2010
23552 | Fuse Pulled Apart - Marsack Road | 2010-06-02 13:55 | 2010-06-02 | 2010-06-02 15:18 | Calculated | 08I30 | 08I30 - 2 Phase : 25.00 kVA : POLEMNT |  | 404SEG5915-5838 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 1 | 24506 | 83 | 0.00339 | 4.0806e-05 | 25 | 2075 | 2010/2011 | June-2010 | 6 | 2010
23553 | Cable Fault - Iwiheke Pl | 2010-06-02 21:40 | 2010-06-02 | 2010-06-03 04:30 | Calculated | 10S29 | 10S29 - 3 Phase : 300.00 kVA : GNDPAD |  | 423SEG6182-6183 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 410 | 46 | 24506 | 18860 | 0.76961 | 0.0018771 | 300 | 122999 | 2010/2011 | June-2010 | 6 | 2010
23555 | Replace Poles 1282089 & 1282090 | 2010-06-03 10:41 | 2010-06-03 | 2010-06-03 13:45 | Calculated | 1641 | 1641 - Sectionaliser with Bypass & Links 1641 |  | 128SEGT2208-1645 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 184 | 11 | 24506 | 2024 | 0.08259 | 0.00044887 | 82.5 | 15180 | 2010/2011 | June-2010 | 6 | 2010
23556 | Digger vs LV - Tawata Road | 2010-06-03 11:54 | 2010-06-03 | 2010-06-03 12:22 | Calculated | 11F05 | 11F05 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5367-5875 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 3 | 24506 | 84 | 0.00343 | 0.00012242 | 15 | 420 | 2010/2011 | June-2010 | 6 | 2010
23558 | Disconnect Genset - Cable | 2010-06-03 16:14 | 2010-06-03 | 2010-06-03 16:34 | Calculated | 10S29 | 10S29 - 3 Phase : 300.00 kVA : GNDPAD |  | 423SEG6182-6183 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB:FCBF | Underground Cable Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 46 | 24506 | 920 | 0.03754 | 0.0018771 | 300 | 5999 | 2010/2011 | June-2010 | 6 | 2010
23559 | Change Poles & Xarms - Te Kura Road | 2010-06-04 09:10 | 2010-06-04 | 2010-06-04 15:29 | Calculated | 383 | 383 - Fused Link 383 |  | 110SEG383 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 379 | 14 | 24506 | 5306 | 0.21652 | 0.00057129 | 110 | 41690 | 2010/2011 | June-2010 | 6 | 2010
23560 | Faulty Tx - Marsack Road | 2010-06-04 09:46 | 2010-06-04 | 2010-06-04 12:49 | Calculated | 08I30 | 08I30 - 2 Phase : 25.00 kVA : POLEMNT |  | 404SEG5915-5838 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 1 | 24506 | 183 | 0.00747 | 4.0806e-05 | 25 | 4575 | 2010/2011 | June-2010 | 6 | 2010
23561 | Vehicle vs Pole - Wairere Falls | 2010-06-06 01:56 | 2010-06-06 | 2010-06-06 10:19 | Calculated | 687 | 687 - Circuit Breaker 687 |  | No Segment | 207-01 Wairere Falls | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 503 | 236 | 24506 | 61461 | 2.508 | 0.0096303 | 1796 | 439512 | 2010/2011 | June-2010 | 6 | 2010
25288 | Branch on Line - Hirangi Road | 2010-06-06 14:16 | 2010-06-06 | 2010-06-06 14:29 | Calculated | 6337 | 6337 - Circuit Breaker Waiotaka 11kV 6337 |  | 427SEG6337-6549 | 511-01 Waiotaka | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 13 | 21 | 24506 | 273 | 0.01114 | 0.00085693 | 302.5 | 3932 | 2010/2011 | June-2010 | 6 | 2010
25287 | Branch On Line/Line Down - Tokaanu Sub | 2010-06-06 14:17 | 2010-06-06 | 2010-06-06 16:38 | Calculated | 6623 | 6623 - Solid Link 6623 |  | 606SEG6578-6622 | 519-01 Awamate | Rural B | Lake Taupo 33 | Direct from Tokaanu Supply |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 141 | 383 | 24506 | 54022 | 2.2044 | 0.015629 | 1743.7756 | 245959 | 2010/2011 | June-2010 | 6 | 2010
25291 | Branch On Line / Line Down Hirangi Rd | 2010-06-06 14:17 | 2010-06-06 | 2010-06-07 15:20 | Calculated | 6545 | 6545 - Air Break Switch 6545 |  | 606SEG5212-6545 | Lake Taupo 606-01 | Urban A | Lake Taupo 33 | Direct from Tokaanu Supply |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1503 | 798 | 24506 | 1199526 | 48.9483 | 0.032563 | 4267.9668 | 6415465 | 2010/2011 | June-2010 | 6 | 2010
23566 | Unknown - Marotiri Road | 2010-06-06 23:24 | 2010-06-06 | 2010-06-06 23:38 | Calculated | 474 | 474 - Recloser 474 |  | 123SEG441-474 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 132 | 24506 | 1848 | 0.07541 | 0.0053864 | 1973 | 27622 | 2010/2011 | June-2010 | 6 | 2010
23569 | Pole Down - T2128 (Private) Taumatamaire | 2010-06-07 02:02 | 2010-06-07 | 2010-06-07 02:17 | Calculated | 1640 | 1640 - Recloser 1640 |  | 128SEG REG2-1609 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 582 | 24506 | 8730 | 0.35624 | 0.023749 | 3454.5 | 51817 | 2010/2011 | June-2010 | 6 | 2010
23570 | Pole Down - T2128 (Private) Taumatamaire | 2010-06-07 03:44 | 2010-06-07 | 2010-06-07 03:54 | Calculated | 1640 | 1640 - Recloser 1640 |  | 128SEG REG2-1609 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 582 | 24506 | 5820 | 0.23749 | 0.023749 | 3454.5 | 34544 | 2010/2011 | June-2010 | 6 | 2010
23573 | Line Down - Marotiri Sub | 2010-06-07 04:15 | 2010-06-07 | 2010-06-07 08:45 | Calculated | 474 | 474 - Recloser 474 |  | 123SEG441-474 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 42 | 24506 | 11340 | 0.46274 | 0.0017139 | 387.5 | 104624 | 2010/2011 | June-2010 | 6 | 2010
23574 | Line Down - Poihipi Road | 2010-06-07 04:15 | 2010-06-07 | 2010-06-07 09:10 | Calculated | 470 | 470 - Air Break Switch 470 |  | 123SEG470-2135 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 295 | 11 | 24506 | 3245 | 0.13242 | 0.00044887 | 90 | 26550 | 2010/2011 | June-2010 | 6 | 2010
23576 | Line Down - Tirohanga Road | 2010-06-07 04:15 | 2010-06-07 | 2010-06-07 11:45 | Calculated | 473 | 473 - Air Break Switch 473 |  | 123SEG473-695RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 450 | 30 | 24506 | 13500 | 0.55089 | 0.0012242 | 755 | 339750 | 2010/2011 | June-2010 | 6 | 2010
25293 | Line Down - Tirohanga Road | 2010-06-07 04:15 | 2010-06-07 | 2010-06-07 09:21 | Calculated | 599 | 599 - Air Break Switch 599 |  | 123SEG599-460 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 306 | 21 | 24506 | 6426 | 0.26222 | 0.00085693 | 260.5 | 79713 | 2010/2011 | June-2010 | 6 | 2010
23571 | Pole Down - T2128 (Private) Taumatamaire | 2010-06-07 04:20 | 2010-06-07 | 2010-06-07 04:29 | Calculated | 1640 | 1640 - Recloser 1640 |  | 128SEG REG2-1609 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 582 | 24506 | 5238 | 0.21374 | 0.023749 | 3454.5 | 31090 | 2010/2011 | June-2010 | 6 | 2010
23577 | Broken Xarm - Ranginui Road | 2010-06-07 05:28 | 2010-06-07 | 2010-06-07 05:46 | Calculated | 1262 | 1262 - Recloser 1262 |  | 121SEG712-1262 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 13 | 24506 | 234 | 0.00955 | 0.00053048 | 85 | 1530 | 2010/2011 | June-2010 | 6 | 2010
23578 | Broken Xarm - Arohena Sub | 2010-06-07 05:28 | 2010-06-07 | 2010-06-07 08:54 | Calculated | 1072 | 1072 - Circuit Breaker 1072 Huirimu |  | 121SEG1072-753 | 211-01 Arohena | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 206 | 64 | 24506 | 13184 | 0.53799 | 0.0026116 | 867 | 178601 | 2010/2011 | June-2010 | 6 | 2010
23579 | Broken Xarm - Arohena Road | 2010-06-07 05:28 | 2010-06-07 | 2010-06-07 09:15 | Calculated | SEG425-748 | SEG425-748 - 121SEG425-748 |  | No Segment | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 227 | 10 | 24506 | 2270 | 0.09263 | 0.00040806 | 45 | 10214 | 2010/2011 | June-2010 | 6 | 2010
23580 | Broken Xarm - Wairehi Road | 2010-06-07 05:28 | 2010-06-07 | 2010-06-07 10:00 | Calculated | 748 | 748 - Air Break Switch 748 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 272 | 20 | 24506 | 5440 | 0.22199 | 0.00081613 | 220 | 59840 | 2010/2011 | June-2010 | 6 | 2010
23581 | Broken Xarm - Mangawhio Road | 2010-06-07 05:28 | 2010-06-07 | 2010-06-07 14:15 | Calculated | 421 | 421 - Air Break Switch 421 |  | 121SEG421-424 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 527 | 50 | 24506 | 26350 | 1.0753 | 0.0020403 | 429 | 226082 | 2010/2011 | June-2010 | 6 | 2010
23572 | Pole Down - T2128 (Private) - Awakau | 2010-06-07 06:55 | 2010-06-07 | 2010-06-07 08:26 | Calculated | 1623 | 1623 - Fused Link 1623 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 14 | 24506 | 1274 | 0.05199 | 0.00057129 | 95 | 8645 | 2010/2011 | June-2010 | 6 | 2010
23567 | Remove Branch from 33kV - Waipapa Road | 2010-06-07 07:45 | 2010-06-07 | 2010-06-07 08:03 | Calculated | 5168 | 5168 - Circuit Breaker with Bypass 5168 |  | No Segment | No Asset Group | Remote Rural F | Rangipo / Hautu | Turangi Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 18 | 185 | 24506 | 3330 | 0.13589 | 0.0075492 | 950 | 17099 | 2010/2011 | June-2010 | 6 | 2010
23568 | Remove Branch from 33kV - Waiotaka Sub | 2010-06-07 07:45 | 2010-06-07 | 2010-06-07 08:03 | Calculated | 6337 | 6337 - Circuit Breaker Waiotaka 11kV 6337 |  | 427SEG6337-6549 | 511-01 Waiotaka | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 18 | 7 | 24506 | 126 | 0.00514 | 0.00028564 | 80 | 1440 | 2010/2011 | June-2010 | 6 | 2010
23582 | Wind - Okama Road | 2010-06-07 08:40 | 2010-06-07 | 2010-06-07 12:03 | Calculated | T1716 | T1716 - 3 Phase : 25.00 kVA : POLEMNT |  | 129SEG635-451RET | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 203 | 4 | 24506 | 812 | 0.03313 | 0.00016323 | 25 | 5075 | 2010/2011 | June-2010 | 6 | 2010
23583 | Wind - Whangamata Road | 2010-06-07 09:10 | 2010-06-07 | 2010-06-07 12:45 | Calculated | 744 | 744 - Fused Link 744 |  | 123SEG744 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 215 | 6 | 24506 | 1290 | 0.05264 | 0.00024484 | 55 | 11825 | 2010/2011 | June-2010 | 6 | 2010
23584 | LV Fault - Takarei Tce | 2010-06-07 10:11 | 2010-06-07 | 2010-06-07 11:28 | Calculated | T2155 | T2155 - 3ph 200kVA GNDPAD |  | 128SEG1523 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 61 | 24506 | 4697 | 0.19167 | 0.0024892 | 200 | 15399 | 2010/2011 | June-2010 | 6 | 2010
23585 | Wind - Te Anga Road | 2010-06-07 10:15 | 2010-06-07 | 2010-06-07 11:16 | Calculated | T1057 | T1057 - 1 Phase : 10.00 kVA : POLEMNT |  | 101SEG514 | Caves 101-11 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 1 | 24506 | 61 | 0.00249 | 4.0806e-05 | 10 | 610 | 2010/2011 | June-2010 | 6 | 2010
23586 | Wind - SH3 | 2010-06-07 11:05 | 2010-06-07 | 2010-06-07 12:53 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 6 | 24506 | 648 | 0.02644 | 0.00024484 | 90 | 9719 | 2010/2011 | June-2010 | 6 | 2010
23587 | Wind - Mangaotaki Road | 2010-06-07 11:05 | 2010-06-07 | 2010-06-07 13:22 | Calculated | T1621 | T1621 - 2ph 15kVA POLEMNT |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 4 | 24506 | 548 | 0.02236 | 0.00016323 | 15 | 2055 | 2010/2011 | June-2010 | 6 | 2010
23588 | Wind - Kaahu South Road | 2010-06-07 14:00 | 2010-06-07 | 2010-06-07 15:26 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2:EENW1 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 27 | 24506 | 2322 | 0.09475 | 0.0011018 | 310 | 26660 | 2010/2011 | June-2010 | 6 | 2010
23589 | Wind - Ranginui Road | 2010-06-07 15:55 | 2010-06-07 | 2010-06-07 16:50 | Calculated | T838 | T838 - 1 Phase : 10.00 kVA : polemnt |  | 121SEG487-531 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 2 | 24506 | 110 | 0.00449 | 8.1613e-05 | 10 | 550 | 2010/2011 | June-2010 | 6 | 2010
23592 | Wind - Te Anga Road | 2010-06-08 04:44 | 2010-06-08 | 2010-06-08 07:59 | Calculated | T1145 | T1145 - 1 Phase : 25.00 kVA : POLEMNT |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 195 | 6 | 24506 | 1170 | 0.04774 | 0.00024484 | 25 | 4874 | 2010/2011 | June-2010 | 6 | 2010
23593 | Meter Board Fault - Burn Street | 2010-06-08 08:20 | 2010-06-08 | 2010-06-08 10:49 | Calculated | 20K01 | 20K01 - 1 Phase : 10.00 kVA : POLEMNT |  | 415SEG5397-5670 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Metering | FAIL:FMET2:FMET1 | Metering Equipment Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 1 | 24506 | 149 | 0.00608 | 4.0806e-05 | 10 | 1490 | 2010/2011 | June-2010 | 6 | 2010
23594 | Upgrade Tx - Aria Road | 2010-06-09 09:52 | 2010-06-09 | 2010-06-09 11:45 | Calculated | T3277 | T3277 - 1 Phase : 15.00 kVA : POLEMNT |  | 116SEG805 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 1 | 24506 | 113 | 0.00461 | 4.0806e-05 | 75 | 8475 | 2010/2011 | June-2010 | 6 | 2010
23597 | Repair broken Staywire @ Pole 175/3 | 2010-06-10 09:32 | 2010-06-10 | 2010-06-10 10:51 | Calculated | 1214 | 1214 - Fused Link 1214 |  | 113SEG1214 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 79 | 2 | 24506 | 158 | 0.00645 | 8.1613e-05 | 20 | 1580 | 2010/2011 | June-2010 | 6 | 2010
23599 | Jumper Off @ T1042 - Old Te Kuiti Road | 2010-06-10 12:29 | 2010-06-10 | 2010-06-10 13:12 | Calculated | 320 | 320 - Air Break Switch 320 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 86 | 24506 | 3698 | 0.1509 | 0.0035093 | 430.7051 | 18520 | 2010/2011 | June-2010 | 6 | 2010
23600 | Tree Felled Through Lines - Borough Sub | 2010-06-10 13:13 | 2010-06-10 | 2010-06-10 13:53 | Calculated | 5952 | 5952 - Circuit Breaker Matapuna 5952 |  | No Segment | 508-01 Borough | Rural B | Matapuna | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1042 | 24506 | 41680 | 1.7008 | 0.04252 | 5060 | 202399 | 2010/2011 | June-2010 | 6 | 2010
23601 | Tree Felled Through Lines - Bell Road | 2010-06-10 13:13 | 2010-06-10 | 2010-06-10 13:53 | Calculated | 5.19 | 5.19 - Air Break Switch 5.19 |  | 401SEG5.10-6721 | Hakiaha 401-01 | Urban A | Hakiaha | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 57 | 24506 | 2280 | 0.09304 | 0.002326 | 1280 | 51199 | 2010/2011 | June-2010 | 6 | 2010
23602 | Tree Felled Through Lines - Taumaranui Victory Bridge | 2010-06-10 13:13 | 2010-06-10 | 2010-06-10 16:20 | Calculated | 5915 | 5915 - Air Break Switch 5915 |  | 404SEG5915-5838 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 40 | 24506 | 7480 | 0.30523 | 0.0016323 | 270 | 50489 | 2010/2011 | June-2010 | 6 | 2010
23603 | Leaning Pole - Waitaanga Sub | 2010-06-10 14:25 | 2010-06-10 | 2010-06-10 17:10 | Calculated | 5420 | 5420 - Fused Link 5420 |  | 413SEG5420-5305 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 36 | 24506 | 5940 | 0.24239 | 0.001469 | 233 | 38444 | 2010/2011 | June-2010 | 6 | 2010
23607 | Branch on Line - Smiths Road | 2010-06-14 09:17 | 2010-06-14 | 2010-06-14 09:49 | Calculated | 390 | 390 - Air Break Switch 390 |  | 110SEG390-2144 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 19 | 24506 | 608 | 0.02481 | 0.00077532 | 185 | 5919 | 2010/2011 | June-2010 | 6 | 2010
23608 | Faulty Tx - South of Paekaka Road | 2010-06-14 09:27 | 2010-06-14 | 2010-06-14 13:31 | Calculated | 1343 | 1343 - Recloser 1343 |  | 113SEG1343-1339 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 244 | 97 | 24506 | 13540 | 0.55252 | 0.0039582 | 783 | 116691 | 2010/2011 | June-2010 | 6 | 2010
23614 | Unknown - Puketawai Road | 2010-06-14 13:45 | 2010-06-14 | 2010-06-14 15:42 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 104 | 24506 | 9089 | 0.37089 | 0.0042439 | 1063 | 92913 | 2010/2011 | June-2010 | 6 | 2010
23617 | Fuse Pulled Apart - Whangamata Road | 2010-06-14 19:00 | 2010-06-14 | 2010-06-14 20:47 | Calculated | T1129 | T1129 - 1 Phase : 10.00 kVA : POLEMNT |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24506 | 107 | 0.00437 | 4.0806e-05 | 10 | 1070 | 2010/2011 | June-2010 | 6 | 2010
23618 | Unknown - Mokau River Road | 2010-06-15 10:50 | 2010-06-15 | 2010-06-15 13:00 | Calculated | 1621 | 1621 - Fused Link 1621 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 20 | 24506 | 2600 | 0.1061 | 0.00081613 | 145 | 18849 | 2010/2011 | June-2010 | 6 | 2010
23619 | Unknown - Puketawai Road | 2010-06-15 11:55 | 2010-06-15 | 2010-06-15 12:30 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 104 | 24506 | 3640 | 0.14854 | 0.0042439 | 1063 | 37204 | 2010/2011 | June-2010 | 6 | 2010
23620 | Jumper Shorting on Xarm - Puketawai Road | 2010-06-15 13:25 | 2010-06-15 | 2010-06-15 15:01 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 104 | 24506 | 5298 | 0.21619 | 0.0042439 | 1063 | 54917 | 2010/2011 | June-2010 | 6 | 2010
23625 | Faulty L.A @ T903 - Tihoi Road | 2010-06-15 15:57 | 2010-06-15 | 2010-06-15 16:36 | Calculated | 542 | 542 - Solid Link 542 |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 8 | 24506 | 312 | 0.01273 | 0.00032645 | 90 | 3510 | 2010/2011 | June-2010 | 6 | 2010
23623 | Unknown - Puketawai Road | 2010-06-15 16:15 | 2010-06-15 | 2010-06-15 16:49 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 101 | 24506 | 3434 | 0.14013 | 0.0041214 | 988 | 33591 | 2010/2011 | June-2010 | 6 | 2010
23627 | Unknown - Waitanguru Road | 2010-06-16 08:17 | 2010-06-16 | 2010-06-16 11:12 | Calculated | T2480 | T2480 - 1 Phase : 3.00 kVA : POLEMNT |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 1 | 24506 | 175 | 0.00714 | 4.0806e-05 | 3 | 525 | 2010/2011 | June-2010 | 6 | 2010
23630 | Wire off Insulator - Puketawai Road | 2010-06-16 09:57 | 2010-06-16 | 2010-06-16 10:22 | Calculated | 554 | 554 - Air Break Switch 554 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 15 | 24506 | 375 | 0.0153 | 0.00061209 | 105 | 2625 | 2010/2011 | June-2010 | 6 | 2010
23631 | Wire off Insulator - Puketawai Road | 2010-06-16 11:05 | 2010-06-16 | 2010-06-16 11:19 | Calculated | 554 | 554 - Air Break Switch 554 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 15 | 24506 | 210 | 0.00857 | 0.00061209 | 105 | 1470 | 2010/2011 | June-2010 | 6 | 2010
23632 | Faulty Tx - SH3 Hangatiki | 2010-06-16 13:23 | 2010-06-16 | 2010-06-16 15:58 | Calculated | T2441 | T2441 - 3ph 30kVA POL |  | 101SEG253-295 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 3 | 24506 | 465 | 0.01897 | 0.00012242 | 30 | 4650 | 2010/2011 | June-2010 | 6 | 2010
23633 | Change Poles & Xarms - McDonalds Feeder | 2010-06-17 09:03 | 2010-06-17 | 2010-06-17 12:33 | Calculated | 383 | 383 - Fused Link 383 |  | 110SEG383 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 210 | 14 | 24506 | 2940 | 0.11997 | 0.00057129 | 110 | 23100 | 2010/2011 | June-2010 | 6 | 2010
23635 | Clash - Whataroa Road | 2010-06-17 21:15 | 2010-06-17 | 2010-06-17 22:25 | Calculated | 575 | 575 - Fused Link 575 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 13 | 24506 | 910 | 0.03713 | 0.00053048 | 150 | 10499 | 2010/2011 | June-2010 | 6 | 2010
23637 | Change Poles & Xarms - Maihiihi Feeder | 2010-06-18 09:07 | 2010-06-18 | 2010-06-18 16:02 | Calculated | T286 | T286 - 3 Phase : 10.00 kVA : POLEMNT |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 54 | 24506 | 5171 | 0.21101 | 0.0022035 | 587.5 | 62619 | 2010/2011 | June-2010 | 6 | 2010
23642 | Disconnect Genset - Maihiihi Road | 2010-06-18 15:33 | 2010-06-18 | 2010-06-18 15:38 | Calculated | 368 | 368 - Fused Link 368 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 35 | 24506 | 175 | 0.00714 | 0.0014282 | 352.5 | 1762 | 2010/2011 | June-2010 | 6 | 2010
23639 | Fuse Pulled Apart - Ward Street | 2010-06-20 04:10 | 2010-06-20 | 2010-06-20 05:40 | Calculated | 08I72 | 08I72 - 3 Phase : 50.00 kVA : POLEMNT |  | 402SEG5987-A4.5 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 6 | 24506 | 540 | 0.02204 | 0.00024484 | 50 | 4499 | 2010/2011 | June-2010 | 6 | 2010
23640 | Install Tap Off Fuses to 07I35 | 2010-06-21 09:06 | 2010-06-21 | 2010-06-21 12:59 | Calculated | 5480 | 5480 - Solid Link 5480 |  | 402SEG5480 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 233 | 17 | 24506 | 3961 | 0.16163 | 0.00069371 | 125 | 29125 | 2010/2011 | June-2010 | 6 | 2010
23641 | Change Poles & Xarms - Maihiihi Feeder | 2010-06-21 09:26 | 2010-06-21 | 2010-06-21 15:54 | Calculated | T286 | T286 - 3 Phase : 10.00 kVA : POLEMNT |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 357 | 21 | 24506 | 6120 | 0.24973 | 0.00085693 | 245 | 75119 | 2010/2011 | June-2010 | 6 | 2010
23645 | Raise Tap - SH40 | 2010-06-21 11:45 | 2010-06-21 | 2010-06-21 12:09 | Calculated | 04H04 | 04H04 - 2ph 15kVA POLEMNT |  | 421SEG6640-5462 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 1 | 24506 | 24 | 0.00098 | 4.0806e-05 | 5 | 120 | 2010/2011 | June-2010 | 6 | 2010
23646 | Fuse Pulled Apart - Taringamotu Road | 2010-06-21 14:25 | 2010-06-21 | 2010-06-21 15:08 | Calculated | 06J15 | 06J15 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 2 | 24506 | 86 | 0.00351 | 8.1613e-05 | 15 | 645 | 2010/2011 | June-2010 | 6 | 2010
23647 | Unknown - Mangateka Road | 2010-06-21 14:45 | 2010-06-21 | 2010-06-21 17:44 | Calculated | 1714 | 1714 - Fused Link 1714 |  | 115SEG1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 13 | 24506 | 2327 | 0.09496 | 0.00053048 | 95 | 17005 | 2010/2011 | June-2010 | 6 | 2010
23643 | Disconnect Genset - Maihiihi Road | 2010-06-21 15:34 | 2010-06-21 | 2010-06-21 15:35 | Calculated | 368 | 368 - Fused Link 368 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 33 | 24506 | 33 | 0.00135 | 0.0013466 | 342.5 | 342 | 2010/2011 | June-2010 | 6 | 2010
23650 | Change Poles & Xarms - Maihiihi Feeder | 2010-06-22 09:20 | 2010-06-22 | 2010-06-22 15:51 | Calculated | T286 | T286 - 3 Phase : 10.00 kVA : POLEMNT |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 359 | 21 | 24506 | 6192 | 0.25267 | 0.00085693 | 245 | 76039 | 2010/2011 | June-2010 | 6 | 2010
23649 | Line Renewal - Nationa Park Feeder | 2010-06-22 09:37 | 2010-06-22 | 2010-06-22 15:41 | Calculated | 5329 | 5329 - Fused Link 5329 |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 364 | 19 | 24506 | 6916 | 0.28222 | 0.00077532 | 135.5 | 49321 | 2010/2011 | June-2010 | 6 | 2010
23651 | Disconnect Genset - Maihiihi Road | 2010-06-22 15:31 | 2010-06-22 | 2010-06-22 15:32 | Calculated | 368 | 368 - Fused Link 368 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 35 | 24506 | 35 | 0.00143 | 0.0014282 | 352.5 | 352 | 2010/2011 | June-2010 | 6 | 2010
23652 | Line Down @ Sub - Piri Piri Substation | 2010-06-22 18:04 | 2010-06-22 | 2010-06-22 19:17 | Calculated | 114 | 114 - Circuit Breaker with Bypass 114 |  | No Segment | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 318 | 24506 | 23214 | 0.94728 | 0.012976 | 2393.5 | 174725 | 2010/2011 | June-2010 | 6 | 2010
23655 | Change Poles & Xarms - Maihiihi Feeder | 2010-06-23 09:17 | 2010-06-23 | 2010-06-23 15:47 | Calculated | T286 | T286 - 3 Phase : 10.00 kVA : POLEMNT |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 352 | 54 | 24506 | 6087 | 0.24839 | 0.0022035 | 587.5 | 74609 | 2010/2011 | June-2010 | 6 | 2010
23653 | Replace Complete Structure 05F10 - Tuhua | 2010-06-23 09:38 | 2010-06-23 | 2010-06-23 15:37 | Calculated | 5258 | 5258 - Fused Link 5258 |  | 422SEG5258-5725 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 359 | 38 | 24506 | 13642 | 0.55668 | 0.0015506 | 180 | 64619 | 2010/2011 | June-2010 | 6 | 2010
23657 | Unknown - Nettie Street | 2010-06-23 10:00 | 2010-06-23 | 2010-06-23 10:30 | Calculated | T2 | T2 - 3ph 200kVA GNDPAD |  | 106SEG203-205 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 63 | 24506 | 1890 | 0.07712 | 0.0025708 | 200 | 5999 | 2010/2011 | June-2010 | 6 | 2010
23656 | Disconnect Genset - Maihiihi Road | 2010-06-23 15:31 | 2010-06-23 | 2010-06-23 15:33 | Calculated | 368 | 368 - Fused Link 368 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 35 | 24506 | 70 | 0.00286 | 0.0014282 | 352.5 | 704 | 2010/2011 | June-2010 | 6 | 2010
23658 | Remove Spur from pole 40 & Fit new DDO's to pole46 | 2010-06-24 10:03 | 2010-06-24 | 2010-06-24 12:25 | Calculated | 579 | 579 - Fused Link 579 |  | 111SEG579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 142 | 10 | 24506 | 1420 | 0.05794 | 0.00040806 | 95 | 13490 | 2010/2011 | June-2010 | 6 | 2010
23659 | Unknown - Waimahora Road | 2010-06-24 15:15 | 2010-06-24 | 2010-06-24 17:34 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 21 | 24506 | 2919 | 0.11911 | 0.00085693 | 168 | 23352 | 2010/2011 | June-2010 | 6 | 2010
23660 | Line Down - Kakara Road | 2010-06-25 02:29 | 2010-06-25 | 2010-06-25 05:20 | Calculated | 1730 | 1730 - Fused Link 1730 |  | 115SEG1730 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 9 | 24506 | 1539 | 0.0628 | 0.00036726 | 67.5 | 11542 | 2010/2011 | June-2010 | 6 | 2010
23661 | Replace Faulty ABS707 - Maihiihi Feeder | 2010-06-25 09:18 | 2010-06-25 | 2010-06-25 14:01 | Calculated | T286 | T286 - 3 Phase : 10.00 kVA : POLEMNT |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 239 | 70 | 24506 | 7175 | 0.29279 | 0.0028564 | 732.5 | 77462 | 2010/2011 | June-2010 | 6 | 2010
23665 | Change Faulty Tx - Soundy Road | 2010-06-25 12:08 | 2010-06-25 | 2010-06-25 13:23 | Calculated | T1606 | T1606 - 1 Phase : 10.00 kVA : POLEMNT |  | 125SEG356 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 24506 | 75 | 0.00306 | 4.0806e-05 | 10 | 750 | 2010/2011 | June-2010 | 6 | 2010
23667 | Fit New Spur Links on Main Line Pole 49 | 2010-06-25 13:26 | 2010-06-25 | 2010-06-25 16:12 | Calculated | 706 | 706 - Air Break Switch 706 |  | 107SEG706-243 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 29 | 150 | 24506 | 2842 | 0.11597 | 0.0061209 | 1050 | 17254 | 2010/2011 | June-2010 | 6 | 2010
23666 | Jumper Blown Off - Paewhenua Road | 2010-06-25 13:31 | 2010-06-25 | 2010-06-25 14:36 | Calculated | 399 | 399 - Air Break Switch 399 |  | 111SEG707-399 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 32 | 24506 | 2080 | 0.08488 | 0.0013058 | 455 | 29574 | 2010/2011 | June-2010 | 6 | 2010
23662 | Disconnect Genset - Maihiihi Road | 2010-06-25 13:41 | 2010-06-25 | 2010-06-25 13:42 | Calculated | 368 | 368 - Fused Link 368 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 35 | 24506 | 35 | 0.00143 | 0.0014282 | 352.5 | 352 | 2010/2011 | June-2010 | 6 | 2010
23668 | Phasing Incorrect - Paewhenua Road | 2010-06-26 13:21 | 2010-06-26 | 2010-06-26 13:24 | Calculated | SEG399-373 | SEG399-373 - 111SEG399-373 |  | No Segment | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 32 | 24506 | 96 | 0.00392 | 0.0013058 | 455 | 1364 | 2010/2011 | June-2010 | 6 | 2010
25295 | Phasing Incorrect - Paewhenua Road | 2010-06-26 13:32 | 2010-06-26 | 2010-06-26 15:15 | Calculated | 707 | 707 - Air Break Switch 707 |  | 111SEG707-399 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 54 | 24506 | 5562 | 0.22696 | 0.0022035 | 587.5 | 60512 | 2010/2011 | June-2010 | 6 | 2010
23670 | Change Tx - Paritaniwha Road | 2010-06-28 11:06 | 2010-06-28 | 2010-06-28 13:49 | Calculated | T738 | T738 - 3 Phase : 30.00 kVA : POLEMNT |  | 120SEG580-745 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 163 | 1 | 24506 | 163 | 0.00665 | 4.0806e-05 | 30 | 4890 | 2010/2011 | June-2010 | 6 | 2010
23671 | Fuse Pulled Apart - Oio No 1 Road | 2010-06-28 16:00 | 2010-06-28 | 2010-06-29 09:11 | Calculated | 12J08 | 12J08 - 1 Phase : 15.00 kVA : POLEMNT |  | No Segment | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1031 | 1 | 24506 | 1031 | 0.04207 | 4.0806e-05 | 15 | 15465 | 2010/2011 | June-2010 | 6 | 2010
25296 | Change Poles, X/arms & Install Temp Links | 2010-06-29 09:34 | 2010-06-29 | 2010-06-29 14:55 | Calculated | 466 | 466 - Recloser 466 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 79 | 24506 | 25362 | 1.0349 | 0.0032237 | 550 | 176577 | 2010/2011 | June-2010 | 6 | 2010
23674 | SWER Backfeed - Tokirima Highway | 2010-06-30 09:30 | 2010-06-30 | 2010-06-30 09:40 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 10 | 12 | 24506 | 120 | 0.0049 | 0.00048968 | 100 | 1000 | 2010/2011 | June-2010 | 6 | 2010
23677 | Changing Poles & Xarms - Mokai | 2010-06-30 09:34 | 2010-06-30 | 2010-06-30 15:05 | Calculated | 145 | 145 - Fused Link 145 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 331 | 7 | 24506 | 2317 | 0.09455 | 0.00028564 | 25 | 8275 | 2010/2011 | June-2010 | 6 | 2010
23675 | Install Earth Mat & Change Pole | 2010-06-30 09:40 | 2010-06-30 | 2010-06-30 14:15 | Calculated | 5579 | 5579 - Fused Link 5579 |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 228 | 24 | 24506 | 2736 | 0.11165 | 0.00097935 | 185 | 19380 | 2010/2011 | June-2010 | 6 | 2010
23678 | Urgent Replacement of broken Xarms on Pole 1221339 | 2010-06-30 10:33 | 2010-06-30 | 2010-06-30 13:32 | Calculated | 371 | 371 - Air Break Switch 371 |  | 122SEG371-633 | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 179 | 45 | 24506 | 8055 | 0.3287 | 0.0018363 | 250 | 44749 | 2010/2011 | June-2010 | 6 | 2010
23676 | SWER Backfeed - Tokirima Highway | 2010-06-30 14:09 | 2010-06-30 | 2010-06-30 14:15 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 6 | 12 | 24506 | 72 | 0.00294 | 0.00048968 | 100 | 600 | 2010/2011 | June-2010 | 6 | 2010
23680 | Re-conductor Broken Span & Fit DDO's 08I30 | 2010-07-01 09:06 | 2010-07-01 | 2010-07-01 09:40 | Calculated | SEG1.7-5915 | SEG1.7-5915 - 404SEG1.7-5915 |  | No Segment | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 34 | 42 | 24509 | 1428 | 0.05826 | 0.0017137 | 102.439 | 3482 | 2010/2011 | July-2010 | 7 | 2010
23683 | Changaing Poles & Xarms - Mokai | 2010-07-01 09:33 | 2010-07-01 | 2010-07-01 13:25 | Calculated | 145 | 145 - Fused Link 145 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 8 | 24509 | 1856 | 0.07573 | 0.00032641 | 25 | 5800 | 2010/2011 | July-2010 | 7 | 2010
23681 | Re-conductor Broken Span & Fit DDO's 08I30 | 2010-07-01 10:01 | 2010-07-01 | 2010-07-01 14:45 | Calculated | 5915 | 5915 - Air Break Switch 5915 |  | 404SEG5915-5838 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 284 | 40 | 24509 | 11360 | 0.4635 | 0.0016321 | 270 | 76679 | 2010/2011 | July-2010 | 7 | 2010
23682 | Re-conductor Broken Span & Fit DDO's 08I30 | 2010-07-01 14:51 | 2010-07-01 | 2010-07-01 15:59 | Calculated | SEG1.7-5915 | SEG1.7-5915 - 404SEG1.7-5915 |  | No Segment | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 68 | 42 | 24509 | 2856 | 0.11653 | 0.0017137 | 102.439 | 6965 | 2010/2011 | July-2010 | 7 | 2010
23686 | Jumper Off - Oturu Road | 2010-07-01 16:36 | 2010-07-01 | 2010-07-01 16:55 | Calculated | T1161 | T1161 - 3ph 15kVA POLEMNT |  | 109SEG179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 2 | 24509 | 38 | 0.00155 | 8.1603e-05 | 15 | 285 | 2010/2011 | July-2010 | 7 | 2010
23687 | Unknown - Tihoi Road | 2010-07-01 19:25 | 2010-07-01 | 2010-07-01 21:41 | Calculated | T891 | T891 - 3 Phase : 50.00 kVA : POLEMNT |  | 124SEG457 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 6 | 24509 | 816 | 0.03329 | 0.00024481 | 50 | 6799 | 2010/2011 | July-2010 | 7 | 2010
25301 | COB 1062 - Transpower Tokaanu | 2010-07-01 21:00 | 2010-07-01 | 2010-07-01 21:02 | Calculated | TPTokaanu CB1062 | TPTokaanu CB1062 - 33kV Minimum Oil Circuit Breaker TP1062 |  | No Segment | 515-01 Transpower Tokaanu | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 1501 | 24509 | 3002 | 0.12249 | 0.061243 | 11670.072 | 23340 | 2010/2011 | July-2010 | 7 | 2010
25251 | Line Renewal Disconnect Genset - Kiko Rd | 2010-07-02 15:29 | 2010-07-02 | 2010-07-02 15:30 | Calculated | 6130 | 6130 - Circuit Breaker with Bypass & Links 6130 |  | 606SEG6545-6130 | Lake Taupo 606-02 | Urban A | Lake Taupo 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 775 | 24509 | 775 | 0.03162 | 0.031621 | 4267.9668 | 5690 | 2010/2011 | July-2010 | 7 | 2010
23689 | Wind - Waihi E/W Sub | 2010-07-05 06:00 | 2010-07-05 | 2010-07-05 07:46 | Calculated | 5899 | 5899 - Fused Link 5899 |  | 406SEG09R27-5891 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 48 | 24509 | 5088 | 0.2076 | 0.0019585 | 215 | 22789 | 2010/2011 | July-2010 | 7 | 2010
23690 | Wind - Waihaha Sub | 2010-07-05 07:00 | 2010-07-05 | 2010-07-05 08:38 | Calculated | 5409 | 5409 - Recloser with Bypass 5409 |  | No Segment | No Asset Group | Remote Rural F | Waihaha | Kuratau Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 35 | 24509 | 3430 | 0.13995 | 0.001428 | 272.5 | 26704 | 2010/2011 | July-2010 | 7 | 2010
23691 | Wind - Awatane Road | 2010-07-05 08:30 | 2010-07-05 | 2010-07-05 10:25 | Calculated | T428 | T428 - 3 Phase : 25.00 kVA : POLEMNT |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 2 | 24509 | 230 | 0.00938 | 8.1603e-05 | 25 | 2875 | 2010/2011 | July-2010 | 7 | 2010
23693 | Jumper Off @ DDO - Main South Road Piopio | 2010-07-05 17:14 | 2010-07-05 | 2010-07-05 17:29 | Calculated | T1721 | T1721 - 1 Phase : 15.00 kVA : POLEMNT |  | 116SEG1310-1781 | Piopio 116-03 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 15 | 4 | 24509 | 60 | 0.00245 | 0.00016321 | 15 | 225 | 2010/2011 | July-2010 | 7 | 2010
23694 | Unknown - Taharoa | 2010-07-05 22:59 | 2010-07-05 | 2010-07-05 23:07 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24509 |  | 0 | 0 |  |  | 2010/2011 | July-2010 | 7 | 2010
23695 | Broken DDO - Lairdvale Road | 2010-07-06 07:40 | 2010-07-06 | 2010-07-06 11:26 | Calculated | 07I36 | 07I36 - 2 Phase : 15.00 kVA : POLEMNT |  | 402SEG5358 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 226 | 1 | 24509 | 226 | 0.00922 | 4.0801e-05 | 15 | 3390 | 2010/2011 | July-2010 | 7 | 2010
23697 | Magpie - SH30 Puetutu | 2010-07-06 08:40 | 2010-07-06 | 2010-07-06 09:33 | Calculated | 621 | 621 - Fused Link 621 |  | 103SEG621 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 3 | 24509 | 159 | 0.00649 | 0.0001224 | 25 | 1325 | 2010/2011 | July-2010 | 7 | 2010
23698 | Changing Poles & Xarms - National Park Feeder | 2010-07-06 09:33 | 2010-07-06 | 2010-07-06 15:20 | Calculated | 5329 | 5329 - Fused Link 5329 |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 347 | 18 | 24509 | 6246 | 0.25485 | 0.00073442 | 143 | 49620 | 2010/2011 | July-2010 | 7 | 2010
25235 | Changing Pole & X/arms - Whangamata Rd | 2010-07-06 09:43 | 2010-07-06 | 2010-07-06 15:08 | Calculated | T1267 | T1267 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 325 | 14 | 24509 | 4550 | 0.18565 | 0.00057122 | 115 | 37382 | 2010/2011 | July-2010 | 7 | 2010
23696 | Broken DDO - Kelland's Road | 2010-07-06 09:49 | 2010-07-06 | 2010-07-06 11:26 | Calculated | 5358 | 5358 - Fused Link 5358 |  | 402SEG5358 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 7 | 24509 | 679 | 0.0277 | 0.00028561 | 50 | 4850 | 2010/2011 | July-2010 | 7 | 2010
23701 | Fuse Pulled Apart - Main South Road | 2010-07-06 13:55 | 2010-07-06 | 2010-07-06 15:25 | Calculated | 12K14 | 12K14 - 1 Phase : 150.00 kVA : POLEMNT |  | 409SEG5934 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 3 | 24509 | 270 | 0.01102 | 0.0001224 | 150 | 13500 | 2010/2011 | July-2010 | 7 | 2010
23700 | Change Taps - McDonalds Lime | 2010-07-06 14:12 | 2010-07-06 | 2010-07-06 14:49 | Calculated | 818 | 818 - Circuit Breaker Incoming 818 |  | 110SEG825-818 | McDonalds 110-04 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 37 | 1 | 24509 | 37 | 0.00151 | 4.0801e-05 | 750 | 27750 | 2010/2011 | July-2010 | 7 | 2010
25240 | Changing Pole & X/arms - Whangamata Rd | 2010-07-07 09:39 | 2010-07-07 | 2010-07-07 15:11 | Calculated | T1267 | T1267 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 332 | 14 | 24509 | 4648 | 0.18964 | 0.00057122 | 115 | 38187 | 2010/2011 | July-2010 | 7 | 2010
23704 | Tree Cutting - SH30 Pureora | 2010-07-08 09:10 | 2010-07-08 | 2010-07-08 16:16 | Calculated | T995 | T995 - 1 Phase : 15.00 kVA : POLEMNT |  | 119SEG417-423 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 426 | 2 | 24509 | 852 | 0.03476 | 8.1603e-05 | 15 | 6390 | 2010/2011 | July-2010 | 7 | 2010
25242 | Changing Pole & X/arms - Whangamata Rd | 2010-07-08 09:34 | 2010-07-08 | 2010-07-08 14:43 | Calculated | T1267 | T1267 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 309 | 14 | 24509 | 4326 | 0.17651 | 0.00057122 | 115 | 35542 | 2010/2011 | July-2010 | 7 | 2010
25300 | Replace H/V Fuse at RMU 6334 - Dogleg | 2010-07-08 10:22 | 2010-07-08 | 2010-07-08 13:57 | Calculated | T4175 | T4175 - 3 Phase : 300.00 kVA : GNDPAD |  | 419SEG6332-6333 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 215 | 1 | 24509 | 215 | 0.00877 | 4.0801e-05 | 300 | 64500 | 2010/2011 | July-2010 | 7 | 2010
23706 | Unknown - Oio Sub | 2010-07-08 14:40 | 2010-07-08 | 2010-07-08 15:13 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 47 | 24509 | 1551 | 0.06328 | 0.0019177 | 239.75 | 7911 | 2010/2011 | July-2010 | 7 | 2010
23707 | Unknown - Oio Sub | 2010-07-08 16:45 | 2010-07-08 | 2010-07-08 17:30 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 47 | 24509 | 2115 | 0.08629 | 0.0019177 | 239.75 | 10788 | 2010/2011 | July-2010 | 7 | 2010
23708 | Unknown - Oio Sub | 2010-07-08 19:30 | 2010-07-08 | 2010-07-08 20:11 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 47 | 24509 | 1927 | 0.07862 | 0.0019177 | 239.75 | 9829 | 2010/2011 | July-2010 | 7 | 2010
25236 | Changing Pole & X/arms - Whangamata Rd | 2010-07-09 09:33 | 2010-07-09 | 2010-07-09 14:10 | Calculated | T1267 | T1267 - 1 Phase : 10.00 kVA : POLEMNT |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 277 | 14 | 24509 | 3878 | 0.15823 | 0.00057122 | 115 | 31862 | 2010/2011 | July-2010 | 7 | 2010
23709 | Unknown - Hautu Rangipo Road | 2010-07-09 10:10 | 2010-07-09 | 2010-07-09 14:55 | Calculated | 11T03 | 11T03 - 3 Phase : 50.00 kVA : POLEMNT |  | 427SEG5392-5642 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 285 | 1 | 24509 | 285 | 0.01163 | 4.0801e-05 | 0 | 0 | 2010/2011 | July-2010 | 7 | 2010
23711 | Replacing Pole 73/5 - Tirohanga | 2010-07-09 10:21 | 2010-07-09 | 2010-07-09 14:25 | Calculated | T3131 | T3131 - 3 Phase : 50.00 kVA : POLEMNT |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 178 | 43 | 24509 | 1966 | 0.08022 | 0.0017545 | 482.5 | 24205 | 2010/2011 | July-2010 | 7 | 2010
23713 | Unknown - Tangiwai Timber Mill | 2010-07-10 18:05 | 2010-07-10 | 2010-07-10 22:35 | Calculated | 5780 | 5780 - Fused Link 5780 |  | 416SEG5780-6608 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 21 | 24509 | 5670 | 0.23134 | 0.00085683 | 230 | 62100 | 2010/2011 | July-2010 | 7 | 2010
23714 | Unknown - SH32 | 2010-07-11 09:30 | 2010-07-11 | 2010-07-11 11:50 | Calculated | 5531 | 5531 - Sectionaliser 5531 |  | 426SEG5531 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 13 | 24509 | 1820 | 0.07426 | 0.00053042 | 125 | 17499 | 2010/2011 | July-2010 | 7 | 2010
23715 | Fuse Pulled Apart - Waituhi Road | 2010-07-11 11:25 | 2010-07-11 | 2010-07-11 12:45 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 21 | 24509 | 1680 | 0.06855 | 0.00085683 | 160 | 12800 | 2010/2011 | July-2010 | 7 | 2010
23717 | Line Down - Taharoa Road | 2010-07-11 23:12 | 2010-07-11 | 2010-07-12 00:36 | Calculated | 277 | 277 - Recloser with Bypass 277 |  | 125SEG277-268 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 120 | 24509 | 10080 | 0.41128 | 0.0048962 | 968.5 | 81353 | 2010/2011 | July-2010 | 7 | 2010
23718 | Replace Pole - Ohura | 2010-07-12 09:02 | 2010-07-12 | 2010-07-12 15:05 | Calculated | 5455 | 5455 - Recloser with Bypass & Links 5455 |  | No Segment | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 33 | 24509 | 2436 | 0.09939 | 0.0013464 | 208 | 14969 | 2010/2011 | July-2010 | 7 | 2010
25250 | Replace H/V Fuse -Rangitoto Rd | 2010-07-12 09:25 | 2010-07-12 | 2010-07-12 15:47 | Calculated | TF872 | TF872 - Transformer Fuse: TF872 |  | 103SEG228-226 | Benneydale 103-03 | Urban A | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 381 | 1 | 24509 | 381 | 0.01555 | 4.0801e-05 | 15 | 5718 | 2010/2011 | July-2010 | 7 | 2010
23719 | Fuse Pulled Apart - Echolands Road | 2010-07-12 13:25 | 2010-07-12 | 2010-07-12 13:54 | Calculated | 01B08 | 01B08 - 2ph 10kVA POLEMNT |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 1 | 24509 | 29 | 0.00118 | 4.0801e-05 | 10 | 290 | 2010/2011 | July-2010 | 7 | 2010
23720 | Fuse Pulled Apart - SH41 | 2010-07-13 08:25 | 2010-07-13 | 2010-07-13 08:54 | Calculated | 08K07 | 08K07 - 1 Phase : 10.00 kVA : POLEMNT |  | 408SEG5935-5936 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 2 | 24509 | 58 | 0.00237 | 8.1603e-05 | 10 | 290 | 2010/2011 | July-2010 | 7 | 2010
23722 | Unknown - River Road | 2010-07-13 18:20 | 2010-07-13 | 2010-07-13 20:30 | Calculated | T4059 | T4059 - 3 Phase : 50.00 kVA : POLEMNT |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 1 | 24509 | 130 | 0.0053 | 4.0801e-05 | 50 | 6500 | 2010/2011 | July-2010 | 7 | 2010
23724 | Replace Poles and Xarms - National Park | 2010-07-14 09:01 | 2010-07-14 | 2010-07-14 15:45 | Calculated | 17K02 | 17K02 - 1 Phase : 15.00 kVA : POLEMNT |  | 411SEG5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 390 | 19 | 24509 | 3975 | 0.16219 | 0.00077523 | 135.5 | 32678 | 2010/2011 | July-2010 | 7 | 2010
23726 | Broken DDO @ 16L02 - Waikune Prison | 2010-07-14 16:11 | 2010-07-14 | 2010-07-14 18:45 | Calculated | 16L02 | 16L02 - 3 Phase : 200.00 kVA : POLEMNT |  | 411SEG5775-5329 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 8 | 24509 | 1232 | 0.05027 | 0.00032641 | 100 | 15400 | 2010/2011 | July-2010 | 7 | 2010
23727 | Broken DDO @ 16L02 - Waikune Prison | 2010-07-14 17:14 | 2010-07-14 | 2010-07-14 18:45 | Calculated | 5775 | 5775 - Fused Link 5775 |  | 411SEG5775-5329 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 27 | 24509 | 2457 | 0.10025 | 0.0011016 | 258 | 23477 | 2010/2011 | July-2010 | 7 | 2010
23729 | Change Difficult Poles (Can't Be Done Live Line) | 2010-07-15 08:30 | 2010-07-15 | 2010-07-15 14:40 | Calculated | 320 | 320 - Air Break Switch 320 |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 309 | 94 | 24509 | 29046 | 1.1851 | 0.0038353 | 510.7051 | 157807 | 2010/2011 | July-2010 | 7 | 2010
23731 | Install New Xiria Unit | 2010-07-15 09:35 | 2010-07-15 | 2010-07-15 18:41 | Calculated | 08I15 | 08I15 - 3ph 100kVA POLEMNT |  | 403SEG5404-5243 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 357 | 74 | 24509 | 26418 | 1.0779 | 0.0030193 | 1869 | 4500 | 2010/2011 | July-2010 | 7 | 2010
25298 | Damaged Conductor - Manu Rd | 2010-07-15 16:13 | 2010-07-15 | 2010-07-15 18:10 | Calculated | TF3026 | TF3026 - Transformer Fuse: TF3026 |  | No Segment | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 4 | 24509 | 471 | 0.01922 | 0.00016321 | 30 | 3530 | 2010/2011 | July-2010 | 7 | 2010
23732 | Disconnect Genset - Kururau Road | 2010-07-15 18:05 | 2010-07-15 | 2010-07-15 18:07 | Calculated | 6041 | 6041 - Recloser 6041 |  | No Segment | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 262 | 24509 | 524 | 0.02138 | 0.01069 | 1869 | 3737 | 2010/2011 | July-2010 | 7 | 2010
23733 | Fuse Pulled Apart - Echolands Road | 2010-07-16 12:55 | 2010-07-16 | 2010-07-16 15:18 | Calculated | 07K16 | 07K16 - 3 Phase : 25.00 kVA : POLEMNT |  | 408SEG5385-5624 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 2 | 24509 | 286 | 0.01167 | 8.1603e-05 | 25 | 3575 | 2010/2011 | July-2010 | 7 | 2010
23734 | Broken DDO @ 07k16 | 2010-07-16 14:38 | 2010-07-16 | 2010-07-16 15:18 | Calculated | 5385 | 5385 - Recloser with Bypass 5385 |  | No Segment | No Asset Group | Remote Rural F | Manunui | Manunui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 182 | 24509 | 7280 | 0.29703 | 0.0074258 | 1333 | 53319 | 2010/2011 | July-2010 | 7 | 2010
23735 | Fuse Pulled Apart - Oruakukuru Road | 2010-07-16 19:51 | 2010-07-16 | 2010-07-16 20:46 | Calculated | 22M13 | 22M13 - 1 Phase : 10.00 kVA : POLEMNT |  | 416SEG5684-5747 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 2 | 24509 | 110 | 0.00449 | 8.1603e-05 | 10 | 550 | 2010/2011 | July-2010 | 7 | 2010
23737 | Wind - Fauchelle Road | 2010-07-17 08:20 | 2010-07-17 | 2010-07-17 10:46 | Calculated | 5277 | 5277 - Sectionaliser with Bypass & Links5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 17 | 24509 | 2482 | 0.10127 | 0.00069362 | 150 | 21900 | 2010/2011 | July-2010 | 7 | 2010
23736 | Wind _ Waimahora Road | 2010-07-17 22:40 | 2010-07-17 | 2010-07-18 00:38 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 21 | 24509 | 2478 | 0.10111 | 0.00085683 | 168 | 19824 | 2010/2011 | July-2010 | 7 | 2010
23738 | Fuse Pulled Apart - Old Horopito Station Road | 2010-07-18 08:15 | 2010-07-18 | 2010-07-18 09:22 | Calculated | 20L31 | 20L31 - 3ph 200kVA POL |  | 415SEG5704-REG28 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 6 | 24509 | 402 | 0.0164 | 0.00024481 | 300 | 20100 | 2010/2011 | July-2010 | 7 | 2010
23739 | Changing Poles & Xarms | 2010-07-19 09:34 | 2010-07-19 | 2010-07-19 13:07 | Calculated | 744 | 744 - Fused Link 744 |  | 123SEG744 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 213 | 6 | 24509 | 1278 | 0.05214 | 0.00024481 | 55 | 11715 | 2010/2011 | July-2010 | 7 | 2010
23741 | Unknown - Aukopae E/W Sub | 2010-07-20 08:25 | 2010-07-20 | 2010-07-20 09:51 | Calculated | 5266 | 5266 - Recloser 5266 |  | 413SEG5260-5266 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 17 | 24509 | 1462 | 0.05965 | 0.00069362 | 110 | 9460 | 2010/2011 | July-2010 | 7 | 2010
25252 | Line Renewal - Disconnect Genset - Kiko Road | 2010-07-20 14:44 | 2010-07-20 | 2010-07-20 14:48 | Calculated | 6130 | 6130 - Circuit Breaker with Bypass & Links 6130 |  | 606SEG6545-6130 | Lake Taupo 606-02 | Urban A | Lake Taupo 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 3 | 775 | 24509 | 2325 | 0.09486 | 0.031621 | 4267.9668 | 14511 | 2010/2011 | July-2010 | 7 | 2010
23885 | Genset tripped on planned outage - Line Renewal | 2010-07-21 08:51 | 2010-07-21 | 2010-07-21 08:56 | Calculated | 6130 | 6130 - Circuit Breaker with Bypass & Links 6130 |  | 606SEG6545-6130 | Lake Taupo 606-02 | Urban A | Lake Taupo 33 | Direct from Tokaanu Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 33kV | 33000 |  | 5 | 775 | 24509 | 3875 | 0.15811 | 0.031621 | 4267.9668 | 21339 | 2010/2011 | July-2010 | 7 | 2010
23747 | Broken LV Neutral - McDonald Road | 2010-07-21 12:43 | 2010-07-21 | 2010-07-21 13:26 | Calculated | T2589 | T2589 - 3ph 25kVA POLEMNT |  | 120SEG465-410 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 3 | 24509 | 129 | 0.00526 | 0.0001224 | 25 | 1074 | 2010/2011 | July-2010 | 7 | 2010
23748 | Tidy Inside & Outside Tx Shed - Rota Street | 2010-07-22 09:32 | 2010-07-22 | 2010-07-22 10:26 | Calculated | 10S32 | 10S32 - 3 Phase : 250.00 kVA : GNDPAD |  | 423SEG6184-6185 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 54 | 58 | 24509 | 3132 | 0.12779 | 0.0023665 | 250 | 13499 | 2010/2011 | July-2010 | 7 | 2010
23751 | Faulty L.A - Hautu-Rangipo Road | 2010-07-22 10:10 | 2010-07-22 | 2010-07-22 11:02 | Calculated | T4032 | T4032 - 3 Phase : 100.00 kVA : GNDPAD |  | 427SEG5392-5642 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 1 | 24509 | 52 | 0.00212 | 4.0801e-05 | 0 | 0 | 2010/2011 | July-2010 | 7 | 2010
23755 | Possum - Whawharua | 2010-07-25 18:45 | 2010-07-25 | 2010-07-25 23:40 | Calculated | 343 | 343 - Air Break Switch 343 |  | 110SEG343-554 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 295 | 104 | 24509 | 11454 | 0.46734 | 0.0042433 | 1063 | 129401 | 2010/2011 | July-2010 | 7 | 2010
23758 | Unknown - Kahorekau Road | 2010-07-26 07:55 | 2010-07-26 | 2010-07-26 11:29 | Calculated | T870 | T870 - 3 Phase : 25.00 kVA : POLEMNT |  | 122SEG448-REG34J | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 4 | 24509 | 856 | 0.03493 | 0.00016321 | 25 | 5350 | 2010/2011 | July-2010 | 7 | 2010
23759 | Magpie @ 09E07 - Huia Road | 2010-07-26 08:26 | 2010-07-26 | 2010-07-26 10:13 | Calculated | 5287 | 5287 - Recloser with Bypass & Links 5287 |  | 413SEG5288-5287 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 31 | 24509 | 3317 | 0.13534 | 0.0012648 | 213 | 22791 | 2010/2011 | July-2010 | 7 | 2010
23765 | Clean Inside & Outside Tx Sheds - Hinerangi Street | 2010-07-26 09:32 | 2010-07-26 | 2010-07-26 10:49 | Calculated | 6195 | 6195 - Fused Link 6195 |  | 423SEG6193-6710 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 77 | 130 | 24509 | 10010 | 0.40842 | 0.0053042 | 500 | 38499 | 2010/2011 | July-2010 | 7 | 2010
23766 | Replace Red Tagged Pole - Gribbon Road | 2010-07-26 09:33 | 2010-07-26 | 2010-07-26 15:29 | Calculated | 1543 | 1543 - Fused Link 1543 |  | 113SEG1543 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 3 | 24509 | 1068 | 0.04358 | 0.0001224 | 15 | 5340 | 2010/2011 | July-2010 | 7 | 2010
23767 | Unknown - Kawautahi Road | 2010-07-26 10:35 | 2010-07-26 | 2010-07-26 14:17 | Calculated | 11J04 | 11J04 - 1 Phase : 7.50 kVA : POLEMNT |  | 409SEG5402-5389 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 222 | 1 | 24509 | 222 | 0.00906 | 4.0801e-05 | 7.5 | 1665 | 2010/2011 | July-2010 | 7 | 2010
23760 | Magpie @ 09E07 - Tokirima Highway | 2010-07-26 11:15 | 2010-07-26 | 2010-07-26 11:49 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 12 | 24509 | 408 | 0.01665 | 0.00048962 | 100 | 3400 | 2010/2011 | July-2010 | 7 | 2010
23761 | Magpie @ 09E07 - Huia Road | 2010-07-26 11:15 | 2010-07-26 | 2010-07-26 17:05 | Calculated | 5287 | 5287 - Recloser with Bypass & Links 5287 |  | 413SEG5288-5287 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 224 | 20 | 24509 | 4480 | 0.18279 | 0.00081603 | 123 | 27552 | 2010/2011 | July-2010 | 7 | 2010
23768 | Dismantle Redundant Line & Re-cover T1030 | 2010-07-27 09:36 | 2010-07-27 | 2010-07-27 11:08 | Calculated | 1744 | 1744 - Fused Link 1744 |  | 101SEG519-232 | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 92 | 1 | 24509 | 92 | 0.00375 | 4.0801e-05 | 0 | 0 | 2010/2011 | July-2010 | 7 | 2010
25297 | Faulty Insulator - Mangakowhai Road | 2010-07-27 12:14 | 2010-07-27 | 2010-07-27 16:05 | Calculated | 1313 | 1313 - Air Break Switch 1313 |  | 116SEG1313 | Piopio 116-05 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 208 | 667 | 24509 | 34619 | 1.4125 | 0.027214 | 4280.3677 | 229419 | 2010/2011 | July-2010 | 7 | 2010
23782 | Upgrade Tx - Waikino Road | 2010-07-28 11:10 | 2010-07-28 | 2010-07-28 14:05 | Calculated | T2381 | T2381 - 3 Phase : 15.00 kVA : POLEMNT |  | 129SEG434-426 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 175 | 3 | 24509 | 525 | 0.02142 | 0.0001224 | 15 | 2625 | 2010/2011 | July-2010 | 7 | 2010
23785 | Repalce Red Tagged Pole - Whangamata Road | 2010-07-29 09:39 | 2010-07-29 | 2010-07-29 17:30 | Calculated | T1271 | T1271 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG493-466 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 471 | 4 | 24509 | 1884 | 0.07687 | 0.00016321 | 15 | 7065 | 2010/2011 | July-2010 | 7 | 2010
23788 | Faulty O/H to U/G Connection - Mt Ruapehu | 2010-07-31 02:13 | 2010-07-31 | 2010-07-31 02:25 | Calculated | 5990 | 5990 - Circuit Breaker 5990 |  | 419SEG5990-5991 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 35 | 24509 | 420 | 0.01714 | 0.001428 | 9837.5 | 118050 | 2010/2011 | July-2010 | 7 | 2010
23790 | LBS 6613 Stuck in C/E Position - Mt Ruapehu (Happy Valley) | 2010-07-31 08:25 | 2010-07-31 | 2010-07-31 16:46 | Calculated | 6136 | 6136 - Ring Main Unit 6136 |  | No Segment | No Asset Group | Remote Rural F | Chateau | Tawhai Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 501 | 5 | 24509 | 1701 | 0.0694 | 0.00020401 | 2900 | 890100 | 2010/2011 | July-2010 | 7 | 2010
23791 | Wind/Clash - Mangateitei Road | 2010-08-01 12:15 | 2010-08-01 | 2010-08-01 12:57 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 29 | 24506 | 1218 | 0.0497 | 0.0011834 | 285 | 11969 | 2010/2011 | August-2010 | 8 | 2010
23792 | Faulty Insulator - Marakopa Road (Te Anga) | 2010-08-01 18:09 | 2010-08-01 | 2010-08-01 19:46 | Calculated | 296 | 296 - Recloser with Bypass 296 |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 169 | 24506 | 16393 | 0.66894 | 0.0068963 | 1185 | 114944 | 2010/2011 | August-2010 | 8 | 2010
23793 | Faulty Insulator - Marakopa Road (by Phillips) | 2010-08-01 18:09 | 2010-08-01 | 2010-08-01 20:40 | Calculated | 583 | 583 - Air Break Switch 583 |  | 125SEG296-583 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 145 | 24506 | 21895 | 0.89345 | 0.0059169 | 975 | 147224 | 2010/2011 | August-2010 | 8 | 2010
23797 | Pole Down - Ohura Road | 2010-08-02 15:54 | 2010-08-02 | 2010-08-03 13:22 | Calculated | T1983 | T1983 - 1 Phase : 15.00 kVA : POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1288 | 2 | 24506 | 2576 | 0.10512 | 8.1613e-05 | 15 | 19320 | 2010/2011 | August-2010 | 8 | 2010
23798 | Unknown - Main Sth Road | 2010-08-03 06:38 | 2010-08-03 | 2010-08-03 07:37 | Calculated | 01B16 | 01B16 - 3ph 50kVA POLEMNT |  | 401SEG5967-5831 | Hakiaha 401-02 | Rural B | Hakiaha | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 8 | 24506 | 472 | 0.01926 | 0.00032645 | 50 | 2950 | 2010/2011 | August-2010 | 8 | 2010
23800 | Jumper Off @ T2719 - Tihoi Road | 2010-08-04 20:33 | 2010-08-04 | 2010-08-04 21:40 | Calculated | 700 | 700 - Air Break Switch 700 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 69 | 24506 | 4623 | 0.18865 | 0.0028156 | 637.7778 | 42731 | 2010/2011 | August-2010 | 8 | 2010
23801 | Replace Rotten Poles | 2010-08-05 10:01 | 2010-08-05 | 2010-08-05 15:06 | Calculated | 421 | 421 - Air Break Switch 421 |  | 121SEG421-424 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 50 | 24506 | 15250 | 0.6223 | 0.0020403 | 429 | 130844 | 2010/2011 | August-2010 | 8 | 2010
23802 | Clash - Mangarino Road | 2010-08-05 11:00 | 2010-08-05 | 2010-08-05 11:47 | Calculated | T669 | T669 - 3 Phase : 25.00 kVA : POLEMNT |  | 102SEG340-191 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 3 | 24506 | 141 | 0.00575 | 0.00012242 | 25 | 1174 | 2010/2011 | August-2010 | 8 | 2010
25302 | Replace H/V Fuses Tx09T03 - Scheduled L/V Maintenance | 2010-08-06 09:33 | 2010-08-06 | 2010-08-06 12:14 | Calculated | TF9T3 | TF9T3 - Transformer Fuse: TF9T3 |  | 417SEG5927RET | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 161 | 35 | 24506 | 5635 | 0.22994 | 0.0014282 | 100 | 16099 | 2010/2011 | August-2010 | 8 | 2010
23803 | Fuse Pulled Apart - Manuka St | 2010-08-06 11:10 | 2010-08-06 | 2010-08-06 11:51 | Calculated | 20L41 | 20L41 - 3 Phase : 200.00 kVA : GNDPAD |  | 414SEG6644-5643 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 61 | 24506 | 2501 | 0.10206 | 0.0024892 | 200 | 8199 | 2010/2011 | August-2010 | 8 | 2010
23804 | Unknown - Tokirima Highway | 2010-08-06 11:40 | 2010-08-06 | 2010-08-06 14:38 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 178 | 12 | 24506 | 2136 | 0.08716 | 0.00048968 | 100 | 17800 | 2010/2011 | August-2010 | 8 | 2010
23805 | Broken Xarm - Water Intake Pumps | 2010-08-09 11:32 | 2010-08-09 | 2010-08-09 12:53 | Calculated | T4266 | T4266 - 3 Phase : 200.00 kVA : POLEMNT |  | 416SEG5709-5796 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24506 |  | 0 | 0 |  |  | 2010/2011 | August-2010 | 8 | 2010
23811 | Vibration Fuse Fell Out - Sommerville Road | 2010-08-13 07:15 | 2010-08-13 | 2010-08-13 08:12 | Calculated | T1357 | T1357 - 1 Phase : 15.00 kVA : POLEMNT |  | 108SEG180-182 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 2 | 24506 | 114 | 0.00465 | 8.1613e-05 | 15 | 855 | 2010/2011 | August-2010 | 8 | 2010
23812 | Private Tree Felling - Western Bay Road | 2010-08-13 08:40 | 2010-08-13 | 2010-08-13 11:22 | Calculated | T960 | T960 - 1 Phase : 5.00 kVA : POLEMNT |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 2 | 24506 | 324 | 0.01322 | 8.1613e-05 | 5 | 810 | 2010/2011 | August-2010 | 8 | 2010
23813 | Upgrade Structure - Old Te Kuiti Road | 2010-08-13 09:35 | 2010-08-13 | 2010-08-13 15:41 | Calculated | T431 | T431 - 3ph 30kVA POLEMNT |  | 110SEG383 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 366 | 7 | 24506 | 2562 | 0.10455 | 0.00028564 | 30 | 10979 | 2010/2011 | August-2010 | 8 | 2010
23814 | Wind - SH30 Mangakino | 2010-08-13 10:00 | 2010-08-13 | 2010-08-13 12:51 | Calculated | T714 | T714 - 3 Phase : 30.00 kVA : POLEMNT |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 3 | 24506 | 513 | 0.02093 | 0.00012242 | 30 | 5130 | 2010/2011 | August-2010 | 8 | 2010
23815 | Wind - Sommerville Road | 2010-08-13 12:40 | 2010-08-13 | 2010-08-13 13:27 | Calculated | T1357 | T1357 - 1 Phase : 15.00 kVA : POLEMNT |  | 108SEG180-182 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 2 | 24506 | 94 | 0.00384 | 8.1613e-05 | 15 | 705 | 2010/2011 | August-2010 | 8 | 2010
23817 | Wind - Te Mahoe Road | 2010-08-13 16:25 | 2010-08-13 | 2010-08-13 19:17 | Calculated | T2158 | T2158 - 1 Phase : 10.00 kVA : POLEMNT |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 2 | 24506 | 344 | 0.01404 | 8.1613e-05 | 10 | 1720 | 2010/2011 | August-2010 | 8 | 2010
23818 | Branch on line @ pole 9 - Omaru Road | 2010-08-14 06:45 | 2010-08-14 | 2010-08-14 09:00 | Calculated | 1729 | 1729 - Fused Link 1729 |  | 117SEG1729 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 10 | 24506 | 1350 | 0.05509 | 0.00040806 | 65 | 8775 | 2010/2011 | August-2010 | 8 | 2010
23819 | Bird - SH40 Tongaporutu | 2010-08-14 17:20 | 2010-08-14 | 2010-08-14 19:51 | Calculated | T2207 | T2207 - 3ph 50kVA POLEMNT |  | 128SEG1642-1630 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 4 | 24506 | 604 | 0.02465 | 0.00016323 | 50 | 7550 | 2010/2011 | August-2010 | 8 | 2010
23821 | Unknown - Kuratau | 2010-08-16 10:50 | 2010-08-16 | 2010-08-16 10:53 | Calculated | 6005 | 6005 - Circuit Breaker 6005 |  | 404SEGL1.10 | 509-01 Kuratau | Rural D | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 1631 | 24506 | 4893 | 0.19967 | 0.066555 | 9067.7824 | 27203 | 2010/2011 | August-2010 | 8 | 2010
23823 | Broken Xarm - Kaahu Tee | 2010-08-16 19:59 | 2010-08-16 | 2010-08-16 20:31 | Calculated | 1748 | 1748 - Circuit Breaker 1748 |  | No Segment | 216-01 Kaahu Tee | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 49 | 24506 | 1568 | 0.06398 | 0.0019995 | 527.5 | 16880 | 2010/2011 | August-2010 | 8 | 2010
23824 | Broken Xarm - Okama Road | 2010-08-16 19:59 | 2010-08-16 | 2010-08-16 21:10 | Calculated | 635 | 635 - Air Break Switch 635 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 138 | 24506 | 9798 | 0.39982 | 0.0056313 | 1720.4167 | 122149 | 2010/2011 | August-2010 | 8 | 2010
23825 | Broken Xarm - Pokuru Road | 2010-08-16 19:59 | 2010-08-16 | 2010-08-17 03:33 | Calculated | SEG634-635 | SEG634-635 - 129SEG634-635 |  | No Segment | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 454 | 9 | 24506 | 4086 | 0.16673 | 0.00036726 | 165 | 74910 | 2010/2011 | August-2010 | 8 | 2010
25304 | Broken Xarm - Kahuu Tee Sub 11kv outgoing | 2010-08-16 19:59 | 2010-08-16 | 2010-08-17 12:54 | Calculated | 442 | 442 - Fused Link 442 |  | 129SEG442-2238 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1015 | 29 | 24506 | 29435 | 1.2011 | 0.0011834 | 275 | 279125 | 2010/2011 | August-2010 | 8 | 2010
23827 | Faulty SWER Isolating Tx - Tauranga/Taupo | 2010-08-16 20:50 | 2010-08-16 | 2010-08-17 11:39 | Calculated | T4087 | T4087 - 1ph 50kVA POLEMNT |  | 417SEG5297-5245 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 889 | 1 | 24506 | 889 | 0.03628 | 4.0806e-05 | 15 | 13335 | 2010/2011 | August-2010 | 8 | 2010
23829 | Changing Poles & Xarms | 2010-08-17 09:34 | 2010-08-17 | 2010-08-17 15:19 | Calculated | SEG493-466 | SEG493-466 - 123SEG493-466 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 345 | 28 | 24506 | 9660 | 0.39419 | 0.0011426 | 305 | 105225 | 2010/2011 | August-2010 | 8 | 2010
23830 | Broken DDO @ 06J12 - Hikurangi Sub | 2010-08-17 11:06 | 2010-08-17 | 2010-08-17 11:45 | Calculated | 5370 | 5370 - Recloser with Bypass & Links 5370 |  | 402SEG5370-5199 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 82 | 24506 | 3198 | 0.1305 | 0.0033461 | 620 | 24180 | 2010/2011 | August-2010 | 8 | 2010
23828 | Broken Xarm - Pokuru Road (by Brunt's) | 2010-08-17 12:28 | 2010-08-17 | 2010-08-17 12:54 | Calculated | 634 | 634 - Air Break Switch 634 |  | 129SEG634-2131 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 26 | 24506 | 676 | 0.02759 | 0.001061 | 510 | 13260 | 2010/2011 | August-2010 | 8 | 2010
23831 | Changing Poles & Xarms | 2010-08-18 09:32 | 2010-08-18 | 2010-08-18 15:14 | Calculated | SEG493-466 | SEG493-466 - 123SEG493-466 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 28 | 24506 | 9576 | 0.39076 | 0.0011426 | 305 | 104310 | 2010/2011 | August-2010 | 8 | 2010
23832 | Trees - Paritikona Road | 2010-08-18 13:20 | 2010-08-18 | 2010-08-18 14:08 | Calculated | T1820 | T1820 - 1 Phase : 15.00 kVA : POLEMNT |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 2 | 24506 | 96 | 0.00392 | 8.1613e-05 | 15 | 720 | 2010/2011 | August-2010 | 8 | 2010
23833 | Lightning - Fraser Smith Road | 2010-08-19 08:20 | 2010-08-19 | 2010-08-19 15:21 | Calculated | T2142 | T2142 - 1 Phase : 15.00 kVA : POLEMNT |  | 128SEG1617RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 421 | 1 | 24506 | 421 | 0.01718 | 4.0806e-05 | 15 | 6315 | 2010/2011 | August-2010 | 8 | 2010
23834 | Changing Poles & Xarms | 2010-08-19 09:32 | 2010-08-19 | 2010-08-19 15:19 | Calculated | SEG493-466 | SEG493-466 - 123SEG493-466 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 347 | 28 | 24506 | 9716 | 0.39647 | 0.0011426 | 305 | 105835 | 2010/2011 | August-2010 | 8 | 2010
23836 | Repair Tx Earth - Mahoe Road | 2010-08-19 11:36 | 2010-08-19 | 2010-08-19 16:36 | Calculated | T1530 | T1530 - 1 Phase : 5.00 kVA : POLEMNT |  | 101SEG290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 300 | 1 | 24506 | 300 | 0.01224 | 4.0806e-05 | 5 | 1500 | 2010/2011 | August-2010 | 8 | 2010
23837 | Unknown - Mangarino Road | 2010-08-20 08:30 | 2010-08-20 | 2010-08-20 09:25 | Calculated | T1032 | T1032 - 3ph 30kVA POLEMNT |  | 106SEG224-361 | Rangitoto 106-07 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 6 | 24506 | 330 | 0.01347 | 0.00024484 | 30 | 1650 | 2010/2011 | August-2010 | 8 | 2010
23838 | Changing Poles & Xarms | 2010-08-20 09:37 | 2010-08-20 | 2010-08-20 14:44 | Calculated | SEG493-466 | SEG493-466 - 123SEG493-466 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 28 | 24506 | 8596 | 0.35077 | 0.0011426 | 305 | 93635 | 2010/2011 | August-2010 | 8 | 2010
23839 | Faulty T2142 - Pioi Station | 2010-08-20 10:05 | 2010-08-20 | 2010-08-20 13:05 | Calculated | 1617 | 1617 - Fused Link 1617 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 2 | 24506 | 360 | 0.01469 | 8.1613e-05 | 30 | 5400 | 2010/2011 | August-2010 | 8 | 2010
23842 | Trees Through Line - Turn off to Raurimu | 2010-08-22 01:43 | 2010-08-22 | 2010-08-22 02:58 | Calculated | 5142 | 5142 - Circuit Breaker with Bypass 5142 |  | 410SEG6766-5141 | 501-01 National Park | Rural D | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 989 | 24506 | 186268 | 7.6009 | 0.040357 | 6070.9157 | 1129120 | 2010/2011 | August-2010 | 8 | 2010
23849 | Changing Poles & Xarms | 2010-08-23 09:35 | 2010-08-23 | 2010-08-23 14:56 | Calculated | SEG493-466 | SEG493-466 - 123SEG493-466 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 28 | 24506 | 8988 | 0.36677 | 0.0011426 | 305 | 97905 | 2010/2011 | August-2010 | 8 | 2010
23850 | Fuse Pulled Apart - Pukehou Road | 2010-08-23 17:00 | 2010-08-23 | 2010-08-23 17:16 | Calculated | 08K15 | 08K15 - 1 Phase : 10.00 kVA : POLEMNT |  | 407SEG5868-5126 | Manunui 407-01 (was Affco) | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 3 | 24506 | 48 | 0.00196 | 0.00012242 | 10 | 159 | 2010/2011 | August-2010 | 8 | 2010
23851 | Unknown - Hangatiki | 2010-08-23 23:53 | 2010-08-23 | 2010-08-23 23:55 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24506 |  | 0 | 0 |  |  | 2010/2011 | August-2010 | 8 | 2010
23852 | Unknown - Taharoa | 2010-08-23 23:53 | 2010-08-23 | 2010-08-24 00:10 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24506 |  | 0 | 0 |  |  | 2010/2011 | August-2010 | 8 | 2010
23853 | Unknown - Whibleys Road | 2010-08-24 01:15 | 2010-08-24 | 2010-08-24 06:09 | Calculated | 638 | 638 - Fused Link 638 |  | 111SEG638 | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 294 | 26 | 24506 | 7644 | 0.31192 | 0.001061 | 265 | 77909 | 2010/2011 | August-2010 | 8 | 2010
23854 | Fuse Pulled Apart - Burns Street | 2010-08-24 07:00 | 2010-08-24 | 2010-08-24 07:20 | Calculated | 20K15 | 20K15 - 3 Phase : 200.00 kVA : POLEMNT |  | 415SEG5704-REG28 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 25 | 24506 | 500 | 0.0204 | 0.0010202 | 200 | 4000 | 2010/2011 | August-2010 | 8 | 2010
23856 | Changing Poles & Xarms - Mokai Feeder | 2010-08-24 09:35 | 2010-08-24 | 2010-08-24 14:56 | Calculated | SEG493-466 | SEG493-466 - 123SEG493-466 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 28 | 24506 | 8988 | 0.36677 | 0.0011426 | 305 | 97905 | 2010/2011 | August-2010 | 8 | 2010
23860 | Changing Poles & Xarms - Rangitoto Feeder | 2010-08-25 09:32 | 2010-08-25 | 2010-08-25 13:59 | Calculated | 354 | 354 - Fused Link 354 |  | 106SEG354 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 267 | 4 | 24506 | 1068 | 0.04358 | 0.00016323 | 25 | 6675 | 2010/2011 | August-2010 | 8 | 2010
25306 | CB 594 and CB754 Tripped - Waitete | 2010-08-25 15:52 | 2010-08-25 | 2010-08-25 15:54 | Calculated | 754 | 754 - Circuit Breaker 754 |  | No Segment | 206-01 Waitete | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 2168 | 24506 | 4661 | 0.1902 | 0.088468 | 14937.0436 | 32114 | 2010/2011 | August-2010 | 8 | 2010
23870 | Replace Poles & Xarms - National Park Feeder | 2010-08-27 09:36 | 2010-08-27 | 2010-08-27 14:43 | Calculated | 5329 | 5329 - Fused Link 5329 |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 18 | 24506 | 5526 | 0.2255 | 0.00073451 | 143 | 43900 | 2010/2011 | August-2010 | 8 | 2010
23871 | Fuse Pulled Apart - Pukawa Road | 2010-08-27 12:10 | 2010-08-27 | 2010-08-27 14:32 | Calculated | 09R13 | 09R13 - 1 Phase : 50.00 kVA : POLEMNT |  | 406SEG5896 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 4 | 24506 | 568 | 0.02318 | 0.00016323 | 50 | 7100 | 2010/2011 | August-2010 | 8 | 2010
23873 | Fuse Pulled Apart - Mahuri Road | 2010-08-30 11:25 | 2010-08-30 | 2010-08-30 14:33 | Calculated | 06H03 | 06H03 - 2 Phase : 15.00 kVA : POLEMNT |  | 402SEG5339 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 1 | 24506 | 188 | 0.00767 | 4.0806e-05 | 15 | 2820 | 2010/2011 | August-2010 | 8 | 2010
23875 | Truck vs Line - Whakamaru Road | 2010-08-31 08:45 | 2010-08-31 | 2010-08-31 10:55 | Calculated | 507 | 507 - Fused Link 507 |  | 120SEG507-530 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 2 | 24506 | 260 | 0.01061 | 8.1613e-05 | 150 | 19500 | 2010/2011 | August-2010 | 8 | 2010
23876 | Fuse Pulled Apart - Bayley Road | 2010-08-31 11:00 | 2010-08-31 | 2010-08-31 12:33 | Calculated | T365 | T365 - 3ph 30kVA POLEMNT |  | 122SEG619-REG35 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 5 | 24506 | 465 | 0.01897 | 0.00020403 | 30 | 2790 | 2010/2011 | August-2010 | 8 | 2010
23877 | Check Earth Connections - Punga Punga Valley Road | 2010-08-31 13:13 | 2010-08-31 | 2010-08-31 14:08 | Calculated | 08M04 | 08M04 - 1 Phase : 15.00 kVA : POLEMNT |  | 408SEG5515 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 4 | 24506 | 220 | 0.00898 | 0.00016323 | 15 | 825 | 2010/2011 | August-2010 | 8 | 2010
23878 | Truck vs LV - Ongarue Road | 2010-08-31 14:20 | 2010-08-31 | 2010-08-31 15:21 | Calculated | 06I01 | 06I01 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5472-5343 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 4 | 24506 | 244 | 0.00996 | 0.00016323 | 15 | 915 | 2010/2011 | August-2010 | 8 | 2010
23880 | Upgrade Tx & Fusing - Mangawhero Road | 2010-09-01 09:30 | 2010-09-01 | 2010-09-01 13:27 | Calculated | T2919 | T2919 - 3 Phase : 50.00 kVA : POLEMNT |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 237 | 2 | 24506 | 474 | 0.01934 | 8.1613e-05 | 50 | 11850 | 2010/2011 | September-2010 | 9 | 2010
23881 | Unknown - SH4 | 2010-09-01 12:15 | 2010-09-01 | 2010-09-01 13:48 | Calculated | T3293 | T3293 - 3 Phase : 75.00 kVA : POLEMNT |  | 117SEG1314-1324 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24506 |  | 0 | 0 |  |  | 2010/2011 | September-2010 | 9 | 2010
23882 | Change Tx - Hangatiki Station Road | 2010-09-01 14:03 | 2010-09-01 | 2010-09-01 15:34 | Calculated | T2563 | T2563 - 3ph 10kVA POLEMNT |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 91 | 2 | 24506 | 182 | 0.00743 | 8.1613e-05 | 10 | 910 | 2010/2011 | September-2010 | 9 | 2010
23914 | Lightning - Waitepipi Road | 2010-09-03 06:05 | 2010-09-03 | 2010-09-03 08:23 | Calculated | 258 | 258 - Fused Link 258 |  | 107SEG258 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 10 | 24506 | 1380 | 0.05631 | 0.00040806 | 80 | 11040 | 2010/2011 | September-2010 | 9 | 2010
23915 | Fuse Pulled Apart - River Road | 2010-09-03 06:30 | 2010-09-03 | 2010-09-03 07:06 | Calculated | 08I21 | 08I21 - 1 Phase : 200.00 kVA : POLEMNT |  | 403SEG5280-5779 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 51 | 24506 | 1836 | 0.07492 | 0.0020811 | 371 | 13356 | 2010/2011 | September-2010 | 9 | 2010
23916 | Replace SWER Iso T4087 with a 25kVA | 2010-09-03 09:32 | 2010-09-03 | 2010-09-03 11:30 | Calculated | 5340 | 5340 - Solid Link 5340 |  | 417SEG5340 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | POUT:PSYS2:PSYM | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 1 | 24506 | 114 | 0.00465 | 4.0806e-05 | 15 | 1710 | 2010/2011 | September-2010 | 9 | 2010
23917 | Lightning - Whangamata Road | 2010-09-03 10:55 | 2010-09-03 | 2010-09-03 12:14 | Calculated | 553 | 553 - Fused Link 553 |  | 123SEG553 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 3 | 24506 | 237 | 0.00967 | 0.00012242 | 10 | 790 | 2010/2011 | September-2010 | 9 | 2010
23918 | Sparking Tx - Okahukura Saddle Road | 2010-09-03 14:09 | 2010-09-03 | 2010-09-03 14:32 | Calculated | 06H18 | 06H18 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5776 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 1 | 24506 | 23 | 0.00094 | 4.0806e-05 | 15 | 345 | 2010/2011 | September-2010 | 9 | 2010
23919 | Line Down - Aotearoa Road | 2010-09-03 14:52 | 2010-09-03 | 2010-09-03 18:19 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 207 | 316 | 24506 | 11479 | 0.46842 | 0.012895 | 2602.25 | 76690 | 2010/2011 | September-2010 | 9 | 2010
23923 | LV Fault - Okahukura Saddle Road | 2010-09-03 17:23 | 2010-09-03 | 2010-09-03 19:00 | Calculated | 06H18 | 06H18 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5776 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 1 | 24506 | 97 | 0.00396 | 4.0806e-05 | 15 | 1455 | 2010/2011 | September-2010 | 9 | 2010
23924 | Wind - State Highway 3 | 2010-09-03 18:30 | 2010-09-03 | 2010-09-03 21:05 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 6 | 24506 | 930 | 0.03795 | 0.00024484 | 95 | 14724 | 2010/2011 | September-2010 | 9 | 2010
23925 | Unknown - State Highway 41 | 2010-09-04 21:20 | 2010-09-04 | 2010-09-04 23:44 | Calculated | 08P03 | 08P03 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5892-5240 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 4 | 24506 | 576 | 0.0235 | 0.00016323 | 15 | 2160 | 2010/2011 | September-2010 | 9 | 2010
23927 | Wind - Poihipi Road | 2010-09-06 03:15 | 2010-09-06 | 2010-09-06 03:45 | Calculated | 433 | 433 - Fused Link 433 |  | 124SEG433 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 18 | 24506 | 540 | 0.02204 | 0.00073451 | 140 | 4200 | 2010/2011 | September-2010 | 9 | 2010
23929 | Wind - Ngakonui Road | 2010-09-06 06:50 | 2010-09-06 | 2010-09-06 07:15 | Calculated | 06J02 | 06J02 - 3 Phase : 50.00 kVA : POLEMNT |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 10 | 24506 | 250 | 0.0102 | 0.00040806 | 50 | 1250 | 2010/2011 | September-2010 | 9 | 2010
23930 | Unknown - Rangiatea Road | 2010-09-06 14:23 | 2010-09-06 | 2010-09-06 14:58 | Calculated | T1557 | T1557 - 3ph 50kVA POLEMNT |  | 109SEG396-397 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 2 | 24506 | 70 | 0.00286 | 8.1613e-05 | 50 | 1750 | 2010/2011 | September-2010 | 9 | 2010
23931 | Unknown - Paraheka Road | 2010-09-06 20:31 | 2010-09-06 | 2010-09-06 20:39 | Calculated | 1108 | 1108 - Recloser with Bypass 1108 |  | 114SEG1108-1102 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 61 | 24506 | 488 | 0.01991 | 0.0024892 | 403 | 3223 | 2010/2011 | September-2010 | 9 | 2010
23932 | River washed away bank - Upper Retaruke Road | 2010-09-06 20:55 | 2010-09-06 | 2010-09-06 22:46 | Calculated | 5334 | 5334 - Fused Link 5334 |  | 410SEG5334-5745 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | EENF2 | WEAT:EENF2:EENF1 | Flood / Washout | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 9 | 24506 | 999 | 0.04077 | 0.00036726 | 65 | 7215 | 2010/2011 | September-2010 | 9 | 2010
23886 | Move Pole away from river - Upper Retaruke Road | 2010-09-07 10:03 | 2010-09-07 | 2010-09-07 12:16 | Calculated | 5334 | 5334 - Fused Link 5334 |  | 410SEG5334-5745 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | EENF2 | WEAT:EENF2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 9 | 24506 | 1197 | 0.04885 | 0.00036726 | 65 | 8645 | 2010/2011 | September-2010 | 9 | 2010
23887 | Replace Faulty Tx - Honikiwi Road | 2010-09-07 13:36 | 2010-09-07 | 2010-09-07 14:55 | Calculated | T2256 | T2256 - 1 Phase : 15.00 kVA : POLEMNT |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 2 | 24506 | 158 | 0.00645 | 8.1613e-05 | 15 | 1185 | 2010/2011 | September-2010 | 9 | 2010
23888 | Change Poles & Xarms - Rangitoto Feeder | 2010-09-08 09:29 | 2010-09-08 | 2010-09-08 15:12 | Calculated | SEG247-TempLink210 | SEG247-TempLink210 - 106SEG247-TempLink210 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 319 | 18 | 24506 | 5742 | 0.23431 | 0.00073451 | 165 | 52635 | 2010/2011 | September-2010 | 9 | 2010
23889 | Replace H Structure - Rangitoto Feeder | 2010-09-09 08:52 | 2010-09-09 | 2010-09-09 16:23 | Calculated | 361 | 361 - Air Break Switch 361 |  | 102SEG191-361 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 451 | 18 | 24506 | 8118 | 0.33127 | 0.00073451 | 171.1111 | 77171 | 2010/2011 | September-2010 | 9 | 2010
23891 | Jumper off @ T2519 - Mangawhero Road | 2010-09-09 11:37 | 2010-09-09 | 2010-09-09 12:15 | Calculated | 324 | 324 - Air Break Switch 324 |  | 109SEG324-1755 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 57 | 24506 | 2166 | 0.08839 | 0.002326 | 523 | 19873 | 2010/2011 | September-2010 | 9 | 2010
23895 | Rotten Xarm @ Pole 254/2 - Pukemapou Road | 2010-09-09 12:37 | 2010-09-09 | 2010-09-09 15:05 | Calculated | 362 | 362 - Fused Link 362 |  | 111SEG362 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 215 | 24506 | 13379 | 0.54595 | 0.0087734 | 2130.8333 | 119381 | 2010/2011 | September-2010 | 9 | 2010
23898 | Upgrade LV Fuses - Irvine Road | 2010-09-10 09:09 | 2010-09-10 | 2010-09-10 09:50 | Calculated | T2767 | T2767 - 3ph 50kVA POLEMNT |  | 109SEG333-620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 41 | 1 | 24506 | 41 | 0.00167 | 4.0806e-05 | 50 | 2050 | 2010/2011 | September-2010 | 9 | 2010
23901 | Duck - Gadsby Road | 2010-09-11 05:59 | 2010-09-11 | 2010-09-11 06:10 | Calculated | 513 | 513 - Circuit Breaker Gadsby Rd 11 kV Feeder 513 |  | No Segment | 205-01 Gadsby Road | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 434 | 24506 | 4774 | 0.19481 | 0.01771 | 3330 | 36629 | 2010/2011 | September-2010 | 9 | 2010
23902 | Sheared Off Bolt in 10S30 - Maria Place | 2010-09-11 10:34 | 2010-09-11 | 2010-09-11 11:40 | Calculated | 10S30 | 10S30 - 3 Phase : 300.00 kVA : GNDPAD |  | 423SEG6184-6185 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 87 | 24506 | 5742 | 0.23431 | 0.0035502 | 300 | 19799 | 2010/2011 | September-2010 | 9 | 2010
23903 | Wind - Okama Road | 2010-09-12 06:00 | 2010-09-12 | 2010-09-12 08:14 | Calculated | T1716 | T1716 - 3 Phase : 25.00 kVA : POLEMNT |  | 129SEG635-451RET | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 4 | 24506 | 536 | 0.02187 | 0.00016323 | 25 | 3350 | 2010/2011 | September-2010 | 9 | 2010
23904 | Upgrade Tx - State Highway 1 | 2010-09-13 09:35 | 2010-09-13 | 2010-09-13 13:35 | Calculated | 09U05 | 09U05 - 3 Phase : 100.00 kVA : POLEMNT |  | 417SEG5297-5245 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 240 | 53 | 24506 | 12720 | 0.51906 | 0.0021627 | 100 | 23999 | 2010/2011 | September-2010 | 9 | 2010
23908 | Fuse Pulled Apart - Raetihi Road | 2010-09-13 12:30 | 2010-09-13 | 2010-09-13 13:32 | Calculated | 20K06 | 20K06 - 3ph 15kVA POL |  | THUVVK | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 2 | 24506 | 124 | 0.00506 | 8.1613e-05 | 15 | 930 | 2010/2011 | September-2010 | 9 | 2010
23909 | Faulty Tx - Mangaokewa Road | 2010-09-13 14:50 | 2010-09-13 | 2010-09-13 18:29 | Calculated | T905 | T905 - 1 Phase : 10.00 kVA : POLEMNT |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 2 | 24506 | 438 | 0.01787 | 8.1613e-05 | 10 | 2190 | 2010/2011 | September-2010 | 9 | 2010
23911 | Shift HV Poles for new Earth Works - Mokai Feeder | 2010-09-15 09:35 | 2010-09-15 | 2010-09-15 15:36 | Calculated | 695 | 695 - Air Break Switch 695 |  | 123SEG473-695RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 361 | 5 | 24506 | 1805 | 0.07366 | 0.00020403 | 615 | 222015 | 2010/2011 | September-2010 | 9 | 2010
23913 | Isolate for Treescape - Hohotaka Road | 2010-09-16 09:01 | 2010-09-16 | 2010-09-16 14:59 | Calculated | 09L04 | 09L04 - 1 Phase : 15.00 kVA : POLEMNT |  | 408SEG5916-5241 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 358 | 3 | 24506 | 1074 | 0.04383 | 0.00012242 | 15 | 5370 | 2010/2011 | September-2010 | 9 | 2010
23933 | Extreme Weather - Ouruwhero Road | 2010-09-17 06:30 | 2010-09-17 | 2010-09-17 07:00 | Calculated | T224 | T224 - 3 Phase : 50.00 kVA : POLEMNT |  | 112SEG637-352 | Otorohanga 112-07 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 5 | 24506 | 150 | 0.00612 | 0.00020403 | 50 | 1500 | 2010/2011 | September-2010 | 9 | 2010
23934 | Fuse Pulled Apart - Taupo Road | 2010-09-17 08:45 | 2010-09-17 | 2010-09-17 09:40 | Calculated | 5742 | 5742 - Fused Link 5742 |  | 404SEG5742 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 2 | 24506 | 110 | 0.00449 | 8.1613e-05 | 25 | 1375 | 2010/2011 | September-2010 | 9 | 2010
23935 | Branch on Line - Whakamaro Road | 2010-09-17 11:19 | 2010-09-17 | 2010-09-17 11:41 | Calculated | 5812 | 5812 - Fused Link 5812 |  | 403SEG5812-5321 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 26 | 24506 | 572 | 0.02334 | 0.001061 | 160 | 3519 | 2010/2011 | September-2010 | 9 | 2010
23937 | Extreme Weather - Mapara Road | 2010-09-17 11:30 | 2010-09-17 | 2010-09-17 15:32 | Calculated | 1297 | 1297 - Fused Link 1297 |  | 117SEG1297-1296 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 242 | 72 | 24506 | 17424 | 0.71101 | 0.0029381 | 550.5 | 133220 | 2010/2011 | September-2010 | 9 | 2010
23938 | Extreme Weather - Lurman Road | 2010-09-17 14:35 | 2010-09-17 | 2010-09-17 16:39 | Calculated | 179 | 179 - Fused Link 179 |  | 109SEG179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 20 | 24506 | 2480 | 0.1012 | 0.00081613 | 185 | 22939 | 2010/2011 | September-2010 | 9 | 2010
23939 | Extreme Weather - SH40 | 2010-09-17 16:55 | 2010-09-17 | 2010-09-17 17:00 | Calculated | 05F10 | 05F10 - 3 Phase : 100.00 kVA : POLEMNT |  | 422SEG5258-5725 | Tuhua 422-01 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 20 | 24506 | 100 | 0.00408 | 0.00081613 | 100 | 500 | 2010/2011 | September-2010 | 9 | 2010
23941 | Extreme Weather - Mairoa Road | 2010-09-17 17:15 | 2010-09-17 | 2010-09-17 21:15 | Calculated | T2541 | T2541 - 1 Phase : 15.00 kVA : POLEMNT |  | 116SEG1354-1334 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 240 | 2 | 24506 | 480 | 0.01959 | 8.1613e-05 | 15 | 3600 | 2010/2011 | September-2010 | 9 | 2010
23942 | Extreme Weather - Waimahora Road | 2010-09-17 17:15 | 2010-09-17 | 2010-09-17 21:17 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 242 | 21 | 24506 | 5082 | 0.20738 | 0.00085693 | 168 | 40656 | 2010/2011 | September-2010 | 9 | 2010
23958 | Extreme Weather - Mairoa Road | 2010-09-17 17:15 | 2010-09-17 | 2010-09-17 22:25 | Calculated | T151 | T151 - 3ph 25kVA POLEMNT |  | 107SEG176-269 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 310 | 2 | 24506 | 620 | 0.0253 | 8.1613e-05 | 25 | 7750 | 2010/2011 | September-2010 | 9 | 2010
23943 | Extreme Weather - Barclay Road | 2010-09-17 17:45 | 2010-09-17 | 2010-09-17 22:00 | Calculated | T1963 | T1963 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1101 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 255 | 2 | 24506 | 510 | 0.02081 | 8.1613e-05 | 10 | 2550 | 2010/2011 | September-2010 | 9 | 2010
23944 | Extreme Weather - Hoopers Road | 2010-09-17 17:50 | 2010-09-17 | 2010-09-17 21:38 | Calculated | 1302 | 1302 - Fused Link 1302 |  | 116SEG1302 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 228 | 4 | 24506 | 912 | 0.03722 | 0.00016323 | 40 | 9120 | 2010/2011 | September-2010 | 9 | 2010
23945 | Extreme Weather - Taumatamaire Road | 2010-09-17 17:50 | 2010-09-17 | 2010-09-17 20:14 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 24 | 24506 | 3456 | 0.14103 | 0.00097935 | 165 | 23759 | 2010/2011 | September-2010 | 9 | 2010
23946 | Extreme Weather - Kaitieke Road | 2010-09-17 17:55 | 2010-09-17 | 2010-09-17 18:46 | Calculated | 13K07 | 13K07 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 2 | 24506 | 102 | 0.00416 | 8.1613e-05 | 10 | 510 | 2010/2011 | September-2010 | 9 | 2010
23947 | Extreme Weather - Kaitieke Road | 2010-09-17 17:55 | 2010-09-17 | 2010-09-17 19:36 | Calculated | 13K15 | 13K15 - 2ph 15kVA POLEMNT |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 1 | 24506 | 101 | 0.00412 | 4.0806e-05 | 15 | 1515 | 2010/2011 | September-2010 | 9 | 2010
23948 | Extreme Weather - Raurimu Road | 2010-09-17 17:55 | 2010-09-17 | 2010-09-17 20:13 | Calculated | 13K04 | 13K04 - 1 Phase : 5.00 kVA : POLEMNT |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 1 | 24506 | 138 | 0.00563 | 4.0806e-05 | 5 | 690 | 2010/2011 | September-2010 | 9 | 2010
23959 | Extreme Weather - Ngapaenga Road | 2010-09-17 17:55 | 2010-09-17 | 2010-09-17 22:43 | Calculated | T576 | T576 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 288 | 2 | 24506 | 576 | 0.0235 | 8.1613e-05 | 10 | 2880 | 2010/2011 | September-2010 | 9 | 2010
23949 | Tree on Line - Taipairu Road | 2010-09-17 18:00 | 2010-09-17 | 2010-09-17 18:08 | Calculated | 112 | 112 - Circuit Breaker with Bypass & Links 112 |  | 106SEG112-REG30 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 265 | 24506 | 2120 | 0.08651 | 0.010814 | 2047 | 16375 | 2010/2011 | September-2010 | 9 | 2010
23950 | Tree on Line - Taipairu Road | 2010-09-17 18:00 | 2010-09-17 | 2010-09-17 18:37 | Calculated | 247 | 247 - Air Break Switch 247 |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 54 | 24506 | 1998 | 0.08153 | 0.0022035 | 472.5 | 17482 | 2010/2011 | September-2010 | 9 | 2010
23951 | Tree on Line - Taipairu Road | 2010-09-17 18:00 | 2010-09-17 | 2010-09-17 19:46 | Calculated | 199 | 199 - Air Break Switch 199 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 108 | 24506 | 11448 | 0.46715 | 0.0044071 | 932.5 | 98844 | 2010/2011 | September-2010 | 9 | 2010
23952 | Extreme Weather - Tahaia Road | 2010-09-17 18:15 | 2010-09-17 | 2010-09-17 20:31 | Calculated | 341 | 341 - Fused Link 341 |  | 109SEG341-587 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 40 | 24506 | 5440 | 0.22199 | 0.0016323 | 350 | 47599 | 2010/2011 | September-2010 | 9 | 2010
23960 | Extreme Weather - Okama Road | 2010-09-17 18:15 | 2010-09-17 | 2010-09-17 22:48 | Calculated | T1716 | T1716 - 3 Phase : 25.00 kVA : POLEMNT |  | 129SEG635-451RET | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 273 | 4 | 24506 | 1092 | 0.04456 | 0.00016323 | 25 | 6825 | 2010/2011 | September-2010 | 9 | 2010
23954 | Exterme Weather - Waihaha Road | 2010-09-17 18:30 | 2010-09-17 | 2010-09-17 21:25 | Calculated | 04Q04 | 04Q04 - 1 Phase : 15.00 kVA : POLEMNT |  | 124SEG5610-5535 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 4 | 24506 | 700 | 0.02856 | 0.00016323 | 15 | 2625 | 2010/2011 | September-2010 | 9 | 2010
23961 | Extreme Weather - Ongarue Road | 2010-09-17 18:35 | 2010-09-17 | 2010-09-17 22:26 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 15 | 24506 | 3465 | 0.14139 | 0.00061209 | 112.5 | 25987 | 2010/2011 | September-2010 | 9 | 2010
23957 | Extreme Weather - Poihipi Road | 2010-09-17 19:10 | 2010-09-17 | 2010-09-17 21:48 | Calculated | 471 | 471 - Fused Link 471 |  | 123SEG471 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 10 | 24506 | 1580 | 0.06447 | 0.00040806 | 85 | 13430 | 2010/2011 | September-2010 | 9 | 2010
23962 | Extreme Weather - Kururau Road | 2010-09-17 19:30 | 2010-09-17 | 2010-09-17 23:26 | Calculated | 08F02 | 08F02 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5123 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 236 | 3 | 24506 | 708 | 0.02889 | 0.00012242 | 15 | 3540 | 2010/2011 | September-2010 | 9 | 2010
23963 | Extreme Weather - SH3 | 2010-09-17 20:30 | 2010-09-17 | 2010-09-17 22:31 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 6 | 24506 | 726 | 0.02963 | 0.00024484 | 95 | 11494 | 2010/2011 | September-2010 | 9 | 2010
23965 | Extreme Weather - Kaahu South Road | 2010-09-17 21:30 | 2010-09-17 | 2010-09-18 00:52 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 27 | 24506 | 5454 | 0.22256 | 0.0011018 | 310 | 62620 | 2010/2011 | September-2010 | 9 | 2010
23966 | Extreme Weather - Harpers Ave | 2010-09-17 22:00 | 2010-09-17 | 2010-09-17 23:37 | Calculated | 663 | 663 - Fused Link 663 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 6 | 24506 | 582 | 0.02375 | 0.00024484 | 90 | 8730 | 2010/2011 | September-2010 | 9 | 2010
23969 | Line Down - Hangatiki | 2010-09-17 22:56 | 2010-09-17 | 2010-09-18 14:18 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 922 | 115 | 24506 | 106030 | 4.3267 | 0.0046927 | 720.3751 | 664185 | 2010/2011 | September-2010 | 9 | 2010
23967 | Extreme Weather - Kaitieke Road | 2010-09-17 23:59 | 2010-09-17 | 2010-09-18 00:30 | Calculated | 13J06 | 13J06 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5919 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 1 | 24506 | 31 | 0.00126 | 4.0806e-05 | 10 | 310 | 2010/2011 | September-2010 | 9 | 2010
23970 | Broken Pole - Mangaotaki Road | 2010-09-18 06:15 | 2010-09-18 | 2010-09-18 14:44 | Calculated | T1621 | T1621 - 2ph 15kVA POLEMNT |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 509 | 4 | 24506 | 2036 | 0.08308 | 0.00016323 | 15 | 7635 | 2010/2011 | September-2010 | 9 | 2010
23971 | Extreme Weather - Rangitoto Road | 2010-09-18 07:20 | 2010-09-18 | 2010-09-18 08:50 | Calculated | T1479 | T1479 - 1 Phase : 10.00 kVA : POLEMNT |  | 106SEG548-1550 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 1 | 24506 | 90 | 0.00367 | 4.0806e-05 | 10 | 900 | 2010/2011 | September-2010 | 9 | 2010
23972 | Extreme Weather - SH3 | 2010-09-18 07:20 | 2010-09-18 | 2010-09-18 10:15 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 6 | 24506 | 1050 | 0.04285 | 0.00024484 | 95 | 16624 | 2010/2011 | September-2010 | 9 | 2010
23974 | Extreme Weather - Mangamahoe Road | 2010-09-18 09:20 | 2010-09-18 | 2010-09-18 14:33 | Calculated | T1900 | T1900 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1128 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 313 | 2 | 24506 | 626 | 0.02554 | 8.1613e-05 | 10 | 3130 | 2010/2011 | September-2010 | 9 | 2010
23975 | Extreme Weather - Manganui Road | 2010-09-18 09:30 | 2010-09-18 | 2010-09-18 12:34 | Calculated | T1837 | T1837 - 1 Phase : 10.00 kVA : POLEMNT |  | 128SEG1612-1613 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 2 | 24506 | 368 | 0.01502 | 8.1613e-05 | 10 | 1840 | 2010/2011 | September-2010 | 9 | 2010
23977 | Tree on Line - Tangitu Road | 2010-09-18 09:42 | 2010-09-18 | 2010-09-18 11:37 | Calculated | 1263 | 1263 - Sectionaliser with Incoming Link 1263 |  | 115SEG1356-1725 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 1 | 24506 | 115 | 0.00469 | 4.0806e-05 | 15 | 1725 | 2010/2011 | September-2010 | 9 | 2010
23978 | Extreme Weather - Oio Sub | 2010-09-18 10:40 | 2010-09-18 | 2010-09-18 12:20 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 25 | 24506 | 2500 | 0.10202 | 0.0010202 | 138.5 | 13849 | 2010/2011 | September-2010 | 9 | 2010
23980 | Extreme Weather - SH32 | 2010-09-18 11:00 | 2010-09-18 | 2010-09-18 13:55 | Calculated | 04P03 | 04P03 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 5 | 24506 | 875 | 0.03571 | 0.00020403 | 15 | 2625 | 2010/2011 | September-2010 | 9 | 2010
24134 | Extreme Weather - Main South Road | 2010-09-18 11:50 | 2010-09-18 | 2010-09-18 22:33 | Calculated | 12K07 | 12K07 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5161-5235 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 643 | 1 | 24506 | 643 | 0.02624 | 4.0806e-05 | 10 | 6430 | 2010/2011 | September-2010 | 9 | 2010
23982 | Extreme Weather - Mangateitei Road | 2010-09-18 12:20 | 2010-09-18 | 2010-09-18 16:17 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 237 | 29 | 24506 | 6873 | 0.28046 | 0.0011834 | 285 | 67544 | 2010/2011 | September-2010 | 9 | 2010
23979 | Extreme Weather - Oio Sub | 2010-09-18 13:15 | 2010-09-18 | 2010-09-18 14:43 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 25 | 24506 | 2200 | 0.08977 | 0.0010202 | 138.5 | 12187 | 2010/2011 | September-2010 | 9 | 2010
23983 | Line Down - Taumatatotoro West | 2010-09-18 14:00 | 2010-09-18 | 2010-09-18 15:18 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 8 | 24506 | 624 | 0.02546 | 0.00032645 | 73 | 5694 | 2010/2011 | September-2010 | 9 | 2010
23985 | Extreme Weather - Waituhi Road | 2010-09-18 14:05 | 2010-09-18 | 2010-09-18 16:44 | Calculated | 485 | 485 - Air Break Switch 485 |  | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 27 | 24506 | 4293 | 0.17518 | 0.0011018 | 395 | 62804 | 2010/2011 | September-2010 | 9 | 2010
23986 | Line Down - Mangateka Road | 2010-09-18 14:18 | 2010-09-18 | 2010-09-18 15:33 | Calculated | 682 | 682 - Circuit Breaker 682 |  | No Segment | 207-01 Wairere Falls | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 175 | 24506 | 13125 | 0.53558 | 0.0071411 | 1528 | 114599 | 2010/2011 | September-2010 | 9 | 2010
23987 | Line Down - Mangateka Road | 2010-09-18 14:18 | 2010-09-18 | 2010-09-18 16:15 | Calculated | 1705 | 1705 - Air Break Switch 1705 |  | 115SEG1705-1707 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 121 | 24506 | 14157 | 0.5777 | 0.0049376 | 883 | 103310 | 2010/2011 | September-2010 | 9 | 2010
23988 | Line Down - Mangateka Road | 2010-09-18 14:18 | 2010-09-18 | 2010-09-18 19:29 | Calculated | 1712 | 1712 - Fused Link 1712 |  | 115SEG1712-1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 311 | 28 | 24506 | 8708 | 0.35534 | 0.0011426 | 197.5 | 61422 | 2010/2011 | September-2010 | 9 | 2010
23989 | Extreme Weather - Kaahu South Road | 2010-09-18 14:30 | 2010-09-18 | 2010-09-18 17:26 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 27 | 24506 | 4752 | 0.19391 | 0.0011018 | 310 | 54560 | 2010/2011 | September-2010 | 9 | 2010
24135 | Lines Down - National Park | 2010-09-18 15:15 | 2010-09-18 | 2010-09-18 19:50 | Calculated | 5147 | 5147 - Circuit Breaker with Bypass 5147 |  | No Segment | No Asset Group | Remote Rural F | National Park | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 275 | 37 | 24506 | 10175 | 0.4152 | 0.0015098 | 533 | 146574 | 2010/2011 | September-2010 | 9 | 2010
24136 | Lines Down - National Park | 2010-09-18 15:15 | 2010-09-18 | 2010-09-19 14:13 | Calculated | 5162 | 5162 - Fused Link 5162 |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1378 | 5 | 24506 | 6890 | 0.28116 | 0.00020403 | 45 | 62010 | 2010/2011 | September-2010 | 9 | 2010
24137 | Lines Down - Opatu Sub | 2010-09-18 15:20 | 2010-09-18 | 2010-09-18 20:55 | Calculated | 5417 | 5417 - Recloser 5417 |  | 413SEG5418-5417 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 335 | 61 | 24506 | 20435 | 0.83388 | 0.0024892 | 413 | 138354 | 2010/2011 | September-2010 | 9 | 2010
24138 | Lines Down - Opatu Sub | 2010-09-18 15:20 | 2010-09-18 | 2010-09-19 12:04 | Calculated | 5301 | 5301 - Fused Link 5301 |  | 413SEG5301-5300 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1244 | 6 | 24506 | 7464 | 0.30458 | 0.00024484 | 63 | 78372 | 2010/2011 | September-2010 | 9 | 2010
23990 | Line Down - Western Bay Road | 2010-09-18 16:30 | 2010-09-18 | 2010-09-18 19:30 | Calculated | 454 | 454 - Air Break Switch 454 |  | 124SEG454-475 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 68 | 24506 | 12240 | 0.49947 | 0.0027748 | 655.5 | 117989 | 2010/2011 | September-2010 | 9 | 2010
23991 | Extreme Weather - Kirikau Sub | 2010-09-18 16:30 | 2010-09-18 | 2010-09-18 18:25 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 65 | 24506 | 7475 | 0.30503 | 0.0026524 | 383 | 44044 | 2010/2011 | September-2010 | 9 | 2010
23992 | Extreme Weather - Oparure Road | 2010-09-18 16:40 | 2010-09-18 | 2010-09-18 18:39 | Calculated | T123 | T123 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG113-262 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 2 | 24506 | 238 | 0.00971 | 8.1613e-05 | 10 | 1190 | 2010/2011 | September-2010 | 9 | 2010
23993 | Extreme Weather - Rangitoto Road | 2010-09-18 17:05 | 2010-09-18 | 2010-09-18 19:36 | Calculated | T1479 | T1479 - 1 Phase : 10.00 kVA : POLEMNT |  | 106SEG548-1550 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 1 | 24506 | 151 | 0.00616 | 4.0806e-05 | 10 | 1510 | 2010/2011 | September-2010 | 9 | 2010
24139 | Extreme Weather - Poihipi Road | 2010-09-18 19:00 | 2010-09-18 | 2010-09-18 22:03 | Calculated | 471 | 471 - Fused Link 471 |  | 123SEG471 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 10 | 24506 | 1830 | 0.07468 | 0.00040806 | 85 | 15555 | 2010/2011 | September-2010 | 9 | 2010
24140 | Extreme Weather - Waimahora Road | 2010-09-18 19:30 | 2010-09-18 | 2010-09-18 21:24 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 21 | 24506 | 2394 | 0.09769 | 0.00085693 | 168 | 19152 | 2010/2011 | September-2010 | 9 | 2010
23994 | Wires Wrapped - Hangatiki | 2010-09-19 01:25 | 2010-09-19 | 2010-09-19 02:34 | Calculated | 1272 | 1272 - Circuit Breaker 1272 |  | No Segment | 204-01 Hangatiki | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 310 | 24506 | 21390 | 0.87285 | 0.01265 | 2868.5 | 197926 | 2010/2011 | September-2010 | 9 | 2010
23995 | Lines Down - Kaahu Tee Zone Sub | 2010-09-19 04:40 | 2010-09-19 | 2010-09-19 11:04 | Calculated | 1748 | 1748 - Circuit Breaker 1748 |  | No Segment | 216-01 Kaahu Tee | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 383 | 241 | 24506 | 50883 | 2.0764 | 0.0098343 | 3022.9167 | 633771 | 2010/2011 | September-2010 | 9 | 2010
23998 | Extreme Weather - Kaahu South Road | 2010-09-19 04:45 | 2010-09-19 | 2010-09-19 14:25 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 580 | 27 | 24506 | 15660 | 0.63903 | 0.0011018 | 310 | 179800 | 2010/2011 | September-2010 | 9 | 2010
23999 | Extreme Weather - Wairoma Road | 2010-09-19 06:30 | 2010-09-19 | 2010-09-19 09:43 | Calculated | T1906 | T1906 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1118 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 2 | 24506 | 386 | 0.01575 | 8.1613e-05 | 10 | 1930 | 2010/2011 | September-2010 | 9 | 2010
24002 | Extreme Weather - Oio Sub | 2010-09-19 07:37 | 2010-09-19 | 2010-09-19 12:01 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 264 | 25 | 24506 | 6600 | 0.26932 | 0.0010202 | 138.5 | 36563 | 2010/2011 | September-2010 | 9 | 2010
24003 | Extreme Weather - SH43 | 2010-09-19 09:00 | 2010-09-19 | 2010-09-19 13:12 | Calculated | 09D05 | 09D05 - 1 Phase : 25.00 kVA : POLEMNT |  | 413SEG5562-5437 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 252 | 5 | 24506 | 1260 | 0.05142 | 0.00020403 | 25 | 6300 | 2010/2011 | September-2010 | 9 | 2010
24001 | Jumper off DDO - Soundy Road | 2010-09-19 10:19 | 2010-09-19 | 2010-09-19 12:20 | Calculated | 356 | 356 - Fused Link 356 |  | 125SEG356 | Coast 125-06 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 5 | 24506 | 605 | 0.02469 | 0.00020403 | 55 | 6655 | 2010/2011 | September-2010 | 9 | 2010
24008 | Extreme Weather - Mohakatino Road | 2010-09-19 10:25 | 2010-09-19 | 2010-09-19 15:27 | Calculated | T2162 | T2162 - 1 Phase : 10.00 kVA : POLEMNT |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 302 | 1 | 24506 | 302 | 0.01232 | 4.0806e-05 | 10 | 3020 | 2010/2011 | September-2010 | 9 | 2010
24010 | Line Down - Maihiihi Road | 2010-09-19 14:25 | 2010-09-19 | 2010-09-19 15:26 | Calculated | 117 | 117 - Circuit Breaker 117 |  | 111SEG647-117RET | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 232 | 24506 | 14152 | 0.57749 | 0.0094671 | 2252.5 | 137402 | 2010/2011 | September-2010 | 9 | 2010
24011 | Line Down - Maihiihi Road | 2010-09-19 14:25 | 2010-09-19 | 2010-09-19 17:28 | Calculated | 362 | 362 - Fused Link 362 |  | 111SEG362 | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 17 | 24506 | 3111 | 0.12695 | 0.00069371 | 115 | 21045 | 2010/2011 | September-2010 | 9 | 2010
24012 | Extreme Weather - Kaahu South Road | 2010-09-19 14:30 | 2010-09-19 | 2010-09-19 15:41 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 27 | 24506 | 1917 | 0.07823 | 0.0011018 | 310 | 22010 | 2010/2011 | September-2010 | 9 | 2010
24013 | Wire off Insulator - Waimahora Road | 2010-09-19 17:00 | 2010-09-19 | 2010-09-19 17:30 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 21 | 24506 | 630 | 0.02571 | 0.00085693 | 168 | 5040 | 2010/2011 | September-2010 | 9 | 2010
24014 | Wire off Insulator - Waimahora Road | 2010-09-19 17:00 | 2010-09-19 | 2010-09-20 16:16 | Calculated | 171 | 171 - Fused Link 171 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1396 | 7 | 24506 | 9772 | 0.39876 | 0.00028564 | 85 | 118660 | 2010/2011 | September-2010 | 9 | 2010
24015 | Extreme Weather - Waitanguru Road | 2010-09-20 06:50 | 2010-09-20 | 2010-09-20 14:10 | Calculated | T2480 | T2480 - 1 Phase : 3.00 kVA : POLEMNT |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 440 | 1 | 24506 | 440 | 0.01795 | 4.0806e-05 | 3 | 1320 | 2010/2011 | September-2010 | 9 | 2010
24017 | Rangitoto Feeder Line Renewal Project | 2010-09-20 09:31 | 2010-09-20 | 2010-09-20 14:37 | Calculated | 284 | 284 - Fused Link 284 |  | 106SEG284 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 306 | 4 | 24506 | 1224 | 0.04995 | 0.00016323 | 25 | 7650 | 2010/2011 | September-2010 | 9 | 2010
24018 | Extreme Weather - Echolands Road | 2010-09-20 11:20 | 2010-09-20 | 2010-09-20 11:42 | Calculated | 1.27 | 1.27 - Fused Link 1.27 |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 6 | 24506 | 132 | 0.00539 | 0.00024484 | 25 | 550 | 2010/2011 | September-2010 | 9 | 2010
24020 | Extreme Weather - SH3 | 2010-09-20 21:45 | 2010-09-20 | 2010-09-20 22:45 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 6 | 24506 | 360 | 0.01469 | 0.00024484 | 95 | 5699 | 2010/2011 | September-2010 | 9 | 2010
24021 | Unknown - Kuratau Sub | 2010-09-21 05:09 | 2010-09-21 | 2010-09-21 05:18 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 4 | 24506 | 36 | 0.00147 | 0.00016323 | 450 | 4050 | 2010/2011 | September-2010 | 9 | 2010
24022 | Tree through Line - Tapuiwahine Valley Road | 2010-09-21 05:45 | 2010-09-21 | 2010-09-21 11:52 | Calculated | 5851 | 5851 - Sectionaliser with Bypass & Links 5851 |  | 421SEG5434-5851 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 367 | 16 | 24506 | 5872 | 0.23961 | 0.0006529 | 105 | 38535 | 2010/2011 | September-2010 | 9 | 2010
24023 | Tree through Line - Before Mangatoro Road | 2010-09-21 05:45 | 2010-09-21 | 2010-09-21 11:00 | Calculated | 1631 | 1631 - Sectionaliser with Incoming Link1631 |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 315 | 10 | 24506 | 3150 | 0.12854 | 0.00040806 | 70 | 22049 | 2010/2011 | September-2010 | 9 | 2010
24024 | Wind/Clash - Kaahu South Road | 2010-09-21 05:45 | 2010-09-21 | 2010-09-21 09:15 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 210 | 27 | 24506 | 5670 | 0.23137 | 0.0011018 | 310 | 65100 | 2010/2011 | September-2010 | 9 | 2010
24026 | Wind - Echolands Road | 2010-09-21 07:20 | 2010-09-21 | 2010-09-21 08:25 | Calculated | 1.27 | 1.27 - Fused Link 1.27 |  | 404SEGF1.27 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 8 | 24506 | 520 | 0.02122 | 0.00032645 | 45 | 2925 | 2010/2011 | September-2010 | 9 | 2010
24028 | Install New T/O Pole for New Tx T4275 | 2010-09-21 09:38 | 2010-09-21 | 2010-09-21 10:36 | Calculated | 5904 | 5904 - Fused Link 5904 |  | 409SEG5904-6206 | Southern 409-04 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 58 | 45 | 24506 | 2610 | 0.1065 | 0.0018363 | 200 | 11599 | 2010/2011 | September-2010 | 9 | 2010
24029 | Wind - Ranginui Road | 2010-09-21 11:15 | 2010-09-21 | 2010-09-21 13:28 | Calculated | 414 | 414 - Fused Link 414 |  | 119SEG414-241 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 6 | 24506 | 798 | 0.03256 | 0.00024484 | 65 | 8645 | 2010/2011 | September-2010 | 9 | 2010
24030 | Jumper Off - Hauturu North Road | 2010-09-21 11:49 | 2010-09-21 | 2010-09-21 13:04 | Calculated | 290 | 290 - Air Break Switch 290 |  | 101SEG290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 8 | 24506 | 600 | 0.02448 | 0.00032645 | 65 | 4875 | 2010/2011 | September-2010 | 9 | 2010
24031 | Wind - Western Bay Road | 2010-09-21 12:15 | 2010-09-21 | 2010-09-21 16:40 | Calculated | 445 | 445 - Fused Link 445 |  | 124SEG445-694 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 265 | 11 | 24506 | 2915 | 0.11895 | 0.00044887 | 205 | 54325 | 2010/2011 | September-2010 | 9 | 2010
24032 | Wind/Clash - Kaahu South Road | 2010-09-21 12:20 | 2010-09-21 | 2010-09-21 15:05 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 27 | 24506 | 4455 | 0.18179 | 0.0011018 | 310 | 51150 | 2010/2011 | September-2010 | 9 | 2010
24035 | Trees/Line Down - Nihoniho Sub | 2010-09-22 03:45 | 2010-09-22 | 2010-09-22 07:32 | Calculated | 5264 | 5264 - Fused Link 5264 |  | 412SEG5496-5262RET | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 227 | 12 | 24506 | 2724 | 0.11116 | 0.00048968 | 42.5 | 9647 | 2010/2011 | September-2010 | 9 | 2010
24036 | Trees/Line Down - Nihoniho Sub | 2010-09-22 03:45 | 2010-09-22 | 2010-09-22 09:08 | Calculated | SEG5265-5628 | SEG5265-5628 - 412SEG5265-5628 |  | No Segment | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 323 | 6 | 24506 | 1938 | 0.07908 | 0.00024484 | 48 | 15504 | 2010/2011 | September-2010 | 9 | 2010
24037 | Trees/Line Down - Waikaka Road | 2010-09-22 03:45 | 2010-09-22 | 2010-09-22 09:36 | Calculated | 5227 | 5227 - Fused Link 5227 |  | 412SEG5227-5269 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 351 | 8 | 24506 | 2808 | 0.11458 | 0.00032645 | 50 | 17550 | 2010/2011 | September-2010 | 9 | 2010
24038 | Trees/Line Down - Rimu Road | 2010-09-22 03:45 | 2010-09-22 | 2010-09-22 13:59 | Calculated | 5628 | 5628 - Fused Link 5628 |  | 412SEG6741-5227 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 614 | 13 | 24506 | 7982 | 0.32572 | 0.00053048 | 93 | 57102 | 2010/2011 | September-2010 | 9 | 2010
24040 | Faulty Insulators - Hangatiki | 2010-09-22 04:28 | 2010-09-22 | 2010-09-23 15:15 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24506 |  | 0 | 0 |  |  | 2010/2011 | September-2010 | 9 | 2010
24041 | Trees/Line Down - Golf Road Extension | 2010-09-22 04:39 | 2010-09-22 | 2010-09-22 09:04 | Calculated | 5119 | 5119 - Recloser 5119 |  | No Segment | No Asset Group | Remote Rural F | Northern | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 265 | 155 | 24506 | 41075 | 1.6761 | 0.006325 | 1608.5 | 426252 | 2010/2011 | September-2010 | 9 | 2010
24042 | Extreme Weather - Oio Sub | 2010-09-22 05:40 | 2010-09-22 | 2010-09-22 06:38 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 25 | 24506 | 1450 | 0.05917 | 0.0010202 | 138.5 | 8032 | 2010/2011 | September-2010 | 9 | 2010
24043 | Extreme Weather - Kaahu South Road | 2010-09-22 05:40 | 2010-09-22 | 2010-09-22 08:22 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 27 | 24506 | 4374 | 0.17849 | 0.0011018 | 310 | 50220 | 2010/2011 | September-2010 | 9 | 2010
24044 | Extreme Weather - SH3 | 2010-09-22 06:58 | 2010-09-22 | 2010-09-22 13:15 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 377 | 6 | 24506 | 2262 | 0.0923 | 0.00024484 | 95 | 35814 | 2010/2011 | September-2010 | 9 | 2010
24045 | Extreme Weather - Waitomo Caves Road | 2010-09-22 07:55 | 2010-09-22 | 2010-09-22 09:38 | Calculated | 775 | 775 - Solid Link 775 |  | 101SEG775 | Caves 101-06 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 8 | 24506 | 824 | 0.03362 | 0.00032645 | 95 | 9785 | 2010/2011 | September-2010 | 9 | 2010
24046 | Extreme Weather - Hangatiki | 2010-09-22 08:54 | 2010-09-22 | 2010-09-22 08:56 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 444 | 24506 | 888 | 0.03624 | 0.018118 | 683 | 1366 | 2010/2011 | September-2010 | 9 | 2010
25307 | Extreme Weather - Tree Through Lines - Te Waireka Rd | 2010-09-22 09:35 | 2010-09-22 | 2010-09-22 11:35 | Calculated | 124 | 124 - Circuit Breaker 124 |  | No Segment | 203-01 Te Waireka Road | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 900 | 24506 | 29884 | 1.2195 | 0.036726 | 8634.9019 | 274032 | 2010/2011 | September-2010 | 9 | 2010
24052 | Replace Broken Pole - Mangaotaki Road | 2010-09-22 10:08 | 2010-09-22 | 2010-09-22 15:01 | Calculated | 1548 | 1548 - Air Break Switch 1548 |  | 113SEG1548-1526 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 293 | 98 | 24506 | 28714 | 1.1717 | 0.003999 | 633 | 185468 | 2010/2011 | September-2010 | 9 | 2010
24054 | Faulty Insulator - SH4 | 2010-09-22 10:31 | 2010-09-22 | 2010-09-22 13:15 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-04 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 17 | 24506 | 2788 | 0.11377 | 0.00069371 | 90 | 14760 | 2010/2011 | September-2010 | 9 | 2010
24055 | Extreme Wind - Thompsons Road | 2010-09-22 12:43 | 2010-09-22 | 2010-09-22 16:46 | Calculated | 284 | 284 - Fused Link 284 |  | 106SEG284 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 243 | 4 | 24506 | 972 | 0.03966 | 0.00016323 | 25 | 6075 | 2010/2011 | September-2010 | 9 | 2010
24059 | Jumper Off - Hikumutu | 2010-09-22 13:15 | 2010-09-22 | 2010-09-22 17:44 | Calculated | 5811 | 5811 - Sectionaliser with Incoming Link 5811 |  | 403SEG5811-5315 | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 269 | 26 | 24506 | 6994 | 0.2854 | 0.001061 | 193 | 51917 | 2010/2011 | September-2010 | 9 | 2010
24057 | Extreme Wind - Kaahu South Road | 2010-09-22 13:30 | 2010-09-22 | 2010-09-22 14:00 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 27 | 24506 | 810 | 0.03305 | 0.0011018 | 310 | 9300 | 2010/2011 | September-2010 | 9 | 2010
24056 | Replace Broken Pole - Otewa Road | 2010-09-22 14:06 | 2010-09-22 | 2010-09-22 16:35 | Calculated | SEG559-321 | SEG559-321 - 109SEG559-321 |  | No Segment | Gravel Scoop 109-01 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 37 | 24506 | 5513 | 0.22497 | 0.0015098 | 146.7033 | 21858 | 2010/2011 | September-2010 | 9 | 2010
24039 | Restore SWER Backfeed - Waikaka Road | 2010-09-22 14:13 | 2010-09-22 | 2010-09-22 14:17 | Calculated | 5227 | 5227 - Fused Link 5227 |  | 412SEG5227-5269 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 8 | 24506 | 32 | 0.00131 | 0.00032645 | 50 | 200 | 2010/2011 | September-2010 | 9 | 2010
24060 | Jumper Off - New River Rd Sub | 2010-09-22 14:20 | 2010-09-22 | 2010-09-22 14:40 | Calculated | 5779 | 5779 - Recloser with Bypass 5779 |  | 403SEG5779-5594 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 28 | 24506 | 560 | 0.02285 | 0.0011426 | 209.25 | 4185 | 2010/2011 | September-2010 | 9 | 2010
24058 | Jumper off LA - Tihoi Road | 2010-09-22 16:20 | 2010-09-22 | 2010-09-22 16:42 | Calculated | T1244 | T1244 - 3 Phase : 15.00 kVA : POLEMNT |  | 120SEG481-422 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 3 | 24506 | 66 | 0.00269 | 0.00012242 | 15 | 330 | 2010/2011 | September-2010 | 9 | 2010
24062 | Wind/Clash - Kaahu South Road | 2010-09-22 21:13 | 2010-09-22 | 2010-09-22 22:44 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 27 | 24506 | 2457 | 0.10026 | 0.0011018 | 310 | 28210 | 2010/2011 | September-2010 | 9 | 2010
24063 | Extreme Wind - Kuratau Sub | 2010-09-23 05:19 | 2010-09-23 | 2010-09-23 05:28 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 4 | 24506 | 36 | 0.00147 | 0.00016323 | 450 | 4050 | 2010/2011 | September-2010 | 9 | 2010
24064 | Extreme Wind - Oio Sub | 2010-09-23 05:30 | 2010-09-23 | 2010-09-23 06:29 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 42 | 24506 | 2478 | 0.10112 | 0.0017139 | 228.5 | 13481 | 2010/2011 | September-2010 | 9 | 2010
24065 | Extreme Wind/Clash - River Road | 2010-09-23 05:35 | 2010-09-23 | 2010-09-23 07:31 | Calculated | T4059 | T4059 - 3 Phase : 50.00 kVA : POLEMNT |  | 413SEG5298-5418 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 1 | 24506 | 116 | 0.00473 | 4.0806e-05 | 50 | 5800 | 2010/2011 | September-2010 | 9 | 2010
24066 | Extreme Wind - SH3 | 2010-09-23 06:17 | 2010-09-23 | 2010-09-23 07:44 | Calculated | 1343 | 1343 - Recloser 1343 |  | 113SEG1343-1339 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 89 | 24506 | 7743 | 0.31596 | 0.0036318 | 713 | 62030 | 2010/2011 | September-2010 | 9 | 2010
25309 | Extreme Wind - Oparure Rd | 2010-09-23 06:47 | 2010-09-23 | 2010-09-23 08:22 | Calculated | T123 | T123 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG113-262 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 2 | 24506 | 190 | 0.00775 | 8.1613e-05 | 10 | 950 | 2010/2011 | September-2010 | 9 | 2010
24067 | Extreme Wind - Main South Road | 2010-09-23 06:48 | 2010-09-23 | 2010-09-23 10:28 | Calculated | T1713 | T1713 - 1 Phase : 15.00 kVA : POLEMNT |  | 113SEG1504 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 220 | 4 | 24506 | 880 | 0.03591 | 0.00016323 | 15 | 3300 | 2010/2011 | September-2010 | 9 | 2010
24068 | Extreme Wind - SH3 | 2010-09-23 06:50 | 2010-09-23 | 2010-09-23 11:25 | Calculated | 1504 | 1504 - Fused Link 1504 |  | 113SEG1504 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 275 | 6 | 24506 | 1650 | 0.06733 | 0.00024484 | 30 | 8250 | 2010/2011 | September-2010 | 9 | 2010
24069 | Extreme Wind - Rangiatea Road | 2010-09-23 07:27 | 2010-09-23 | 2010-09-23 07:28 | Calculated | 334 | 334 - Circuit Breaker with Bypass & Links 334 |  | 109SEG303-334 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 157 | 24506 | 157 | 0.00641 | 0.0064066 | 1770 | 1769 | 2010/2011 | September-2010 | 9 | 2010
25319 | Line Down Extreme Weather - Mahoenui Feeder | 2010-09-23 07:53 | 2010-09-23 | 2010-09-23 16:12 | Calculated | 1512 | 1512 - Recloser 1512 |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 499 | 168 | 24506 | 35908 | 1.4653 | 0.0068555 | 1128.0833 | 231515 | 2010/2011 | September-2010 | 9 | 2010
24074 | Extreme Wind - SH3 | 2010-09-23 08:10 | 2010-09-23 | 2010-09-23 12:05 | Calculated | 1539 | 1539 - Fused Link 1539 |  | 113SEG1539 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 235 | 6 | 24506 | 1410 | 0.05754 | 0.00024484 | 95 | 22324 | 2010/2011 | September-2010 | 9 | 2010
24075 | Extreme Wind - Waikawau Road | 2010-09-23 08:12 | 2010-09-23 | 2010-09-23 15:37 | Calculated | 1612 | 1612 - Sectionaliser with Bypass & Links 1612 |  | 128SEG1611-1612 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 445 | 39 | 24506 | 17355 | 0.70819 | 0.0015914 | 295 | 131275 | 2010/2011 | September-2010 | 9 | 2010
24077 | Extreme Wind - Harpers Ave | 2010-09-23 08:50 | 2010-09-23 | 2010-09-23 11:56 | Calculated | 663 | 663 - Fused Link 663 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 6 | 24506 | 1116 | 0.04554 | 0.00024484 | 90 | 16740 | 2010/2011 | September-2010 | 9 | 2010
24078 | Extreme Wind - Marotiri Road | 2010-09-23 08:51 | 2010-09-23 | 2010-09-23 08:52 | Calculated | 474 | 474 - Recloser 474 |  | 123SEG441-474 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 134 | 24506 | 134 | 0.00547 | 0.005468 | 2013 | 2012 | 2010/2011 | September-2010 | 9 | 2010
24079 | Jumper off Iso Tx - SH41 | 2010-09-23 09:04 | 2010-09-23 | 2010-09-23 11:48 | Calculated | 6353 | 6353 - Sectionaliser with Bypass & Links 6353 |  | 406SEG5658-6355 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 359 | 24506 | 58876 | 2.4025 | 0.014649 | 2092.5 | 343169 | 2010/2011 | September-2010 | 9 | 2010
24080 | Extreme Wind - Poro-o-tarao | 2010-09-23 09:50 | 2010-09-23 | 2010-09-23 15:00 | Calculated | 705 | 705 - Recloser with Bypass & Links 705 |  | 103SEG1774-1750 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 310 | 20 | 24506 | 6200 | 0.253 | 0.00081613 | 132.5 | 41075 | 2010/2011 | September-2010 | 9 | 2010
24081 | Extreme Wind - Waimiha Township | 2010-09-23 09:50 | 2010-09-23 | 2010-09-23 15:44 | Calculated | 1726 | 1726 - Fused Link 1726 |  | 103SEG1726-1733 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 354 | 6 | 24506 | 2124 | 0.08667 | 0.00024484 | 30 | 10620 | 2010/2011 | September-2010 | 9 | 2010
24082 | Extreme Wind - Oio Sub | 2010-09-23 10:00 | 2010-09-23 | 2010-09-23 10:32 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 42 | 24506 | 1344 | 0.05484 | 0.0017139 | 228.5 | 7311 | 2010/2011 | September-2010 | 9 | 2010
24083 | Extreme Wind - Taumatatotoro West | 2010-09-23 10:28 | 2010-09-23 | 2010-09-23 14:27 | Calculated | 292 | 292 - Fused Link 292 |  | 125SEG292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 8 | 24506 | 1912 | 0.07802 | 0.00032645 | 73 | 17447 | 2010/2011 | September-2010 | 9 | 2010
24085 | Extreme Wind - Ngapaenga Road | 2010-09-23 10:50 | 2010-09-23 | 2010-09-23 16:10 | Calculated | T576 | T576 - 1 Phase : 10.00 kVA : POLEMNT |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 320 | 2 | 24506 | 640 | 0.02612 | 8.1613e-05 | 10 | 3200 | 2010/2011 | September-2010 | 9 | 2010
24084 | Address Clashing Issue - Kaahu South Road | 2010-09-23 11:43 | 2010-09-23 | 2010-09-23 12:55 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 27 | 24506 | 1944 | 0.07933 | 0.0011018 | 310 | 22320 | 2010/2011 | September-2010 | 9 | 2010
24076 | Extreme Wind - Waikawau EW Sub | 2010-09-23 12:00 | 2010-09-23 | 2010-09-23 12:10 | Calculated | 1610 | 1610 - Recloser 1610 |  | 128SEG1610-1611 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 49 | 24506 | 490 | 0.02 | 0.0019995 | 385.5 | 3855 | 2010/2011 | September-2010 | 9 | 2010
24086 | Iron Rail Leaning Over - Makino Road | 2010-09-23 12:00 | 2010-09-23 | 2010-09-23 14:15 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOL1 | Pole Leaning | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 28 | 24506 | 3780 | 0.15425 | 0.0011426 | 183.5 | 24772 | 2010/2011 | September-2010 | 9 | 2010
25320 | Extreme Wind/Trees - Waitete | 2010-09-23 12:17 | 2010-09-23 | 2010-09-23 20:30 | Calculated | 103 | 103 - Circuit Breaker Te Kuiti South 103 |  | No Segment | 206-01 Waitete | Urban A | Te Kuiti South | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 480 | 616 | 24506 | 29453 | 1.2019 | 0.025137 | 4453.018 | 210025 | 2010/2011 | September-2010 | 9 | 2010
25321 | Extreme Wind - Mokauiti Feeder | 2010-09-23 13:27 | 2010-09-23 | 2010-09-23 15:39 | Calculated | 682 | 682 - Circuit Breaker 682 |  | No Segment | 207-01 Wairere Falls | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 191 | 24506 | 18677 | 0.76214 | 0.007794 | 1652.25 | 155770 | 2010/2011 | September-2010 | 9 | 2010
25322 | Floating Wire and Insulator - Oio Sub | 2010-09-23 14:22 | 2010-09-23 | 2010-09-23 17:31 | Calculated | 5800 | 5800 - Fused Link 5800 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 189 | 47 | 24506 | 6623 | 0.27026 | 0.0019179 | 239.75 | 33936 | 2010/2011 | September-2010 | 9 | 2010
24100 | Extreme Wind - Mangateitei Road | 2010-09-23 16:00 | 2010-09-23 | 2010-09-23 16:52 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 29 | 24506 | 1508 | 0.06154 | 0.0011834 | 285 | 14819 | 2010/2011 | September-2010 | 9 | 2010
24102 | Extreme Wind - Station Road | 2010-09-23 16:55 | 2010-09-23 | 2010-09-23 17:20 | Calculated | 17K04 | 17K04 - 1 Phase : 50.00 kVA : POLEMNT |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 3 | 24506 | 75 | 0.00306 | 0.00012242 | 50 | 1249 | 2010/2011 | September-2010 | 9 | 2010
24103 | Extreme Wind - Whatauri Road | 2010-09-23 18:56 | 2010-09-23 | 2010-09-23 19:30 | Calculated | SEGREG25-376 | SEGREG25-376 - 122SEGREG25-376 |  | No Segment | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 22 | 24506 | 748 | 0.03052 | 0.00089774 | 220 | 7480 | 2010/2011 | September-2010 | 9 | 2010
25323 | Stub Pole vs Car - Ahuroa Rd By Abattoirs | 2010-09-24 05:11 | 2010-09-24 | 2010-09-24 11:01 | Calculated | 104 | 104 - Circuit Breaker Rangitoto 104 |  | No Segment | 206-01 Waitete | Urban A | Rangitoto | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 350 | 740 | 24506 | 43355 | 1.7692 | 0.030197 | 5169.958 | 281908 | 2010/2011 | September-2010 | 9 | 2010
25324 | Tree Felled Through Line - Mangaorongo Rd | 2010-09-24 09:53 | 2010-09-24 | 2010-09-24 11:33 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 597 | 24506 | 31274 | 1.2762 | 0.024361 | 6071 | 319109 | 2010/2011 | September-2010 | 9 | 2010
24115 | Replace Broken Pole - Waitanguru | 2010-09-24 11:36 | 2010-09-24 | 2010-09-24 14:41 | Calculated | 1526 | 1526 - Fused Link 1526 |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 59 | 24506 | 10306 | 0.42055 | 0.0024076 | 378.8333 | 66241 | 2010/2011 | September-2010 | 9 | 2010
24118 | Wind - SH30 | 2010-09-24 15:55 | 2010-09-24 | 2010-09-24 17:37 | Calculated | T2308 | T2308 - 1 Phase : 15.00 kVA : POLEMNT |  | 103SEG623 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 2 | 24506 | 204 | 0.00832 | 8.1613e-05 | 15 | 1530 | 2010/2011 | September-2010 | 9 | 2010
24119 | Jumper off Links - Waipa River Road | 2010-09-24 16:09 | 2010-09-24 | 2010-09-24 17:21 | Calculated | 566 | 566 - Air Break Switch 566 |  | 109SEG566-2068 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 1 | 24506 | 72 | 0.00294 | 4.0806e-05 | 15 | 1080 | 2010/2011 | September-2010 | 9 | 2010
24121 | Fault Current/Sympathy?? - Oio Sub | 2010-09-25 13:30 | 2010-09-25 | 2010-09-25 14:22 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 42 | 24506 | 2184 | 0.08912 | 0.0017139 | 228.5 | 11881 | 2010/2011 | September-2010 | 9 | 2010
24122 | Fuse Pulled Apart - Main South Road | 2010-09-25 13:30 | 2010-09-25 | 2010-09-25 14:38 | Calculated | 12K10 | 12K10 - 1 Phase : 7.50 kVA : POLEMNT |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24506 |  | 0 | 0 |  |  | 2010/2011 | September-2010 | 9 | 2010
24124 | MRP Switching Error - Atiamuri | 2010-09-27 05:26 | 2010-09-27 | 2010-09-27 05:27 | Calculated | 732 | 732 - Circuit Breaker Atiamuri 33 kV Supply 732 |  | No Segment | 215-01 Atiamuri | Rural C | Whakamaru 33 | Direct from Whakamaru Supply |  | Third Party (includeds unauthorised contractors) |  | 3PAR |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24506 |  | 0 | 0 |  |  | 2010/2011 | September-2010 | 9 | 2010
24126 | Install LA on Tx - Old Te Kuiti Road | 2010-09-27 10:20 | 2010-09-27 | 2010-09-27 11:34 | Calculated | T320 | T320 - 3 Phase : 50.00 kVA : POLEMNT |  | 110SEG320-REG11J | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 74 | 12 | 24506 | 888 | 0.03624 | 0.00048968 | 50 | 3699 | 2010/2011 | September-2010 | 9 | 2010
24128 | Repair Broken Earth - Matiere/Aria Road | 2010-09-27 12:23 | 2010-09-27 | 2010-09-27 13:46 | Calculated | 04F02 | 04F02 - 1 Phase : 15.00 kVA : POLEMNT |  | 422SEG5278-5307 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 2 | 24506 | 166 | 0.00677 | 8.1613e-05 | 15 | 1245 | 2010/2011 | September-2010 | 9 | 2010
24129 | Unknown - Scott Road | 2010-09-27 15:31 | 2010-09-27 | 2010-09-27 16:37 | Calculated | 407 | 407 - Fused Link 407 |  | 119SEG407 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 11 | 24506 | 726 | 0.02963 | 0.00044887 | 165 | 10889 | 2010/2011 | September-2010 | 9 | 2010
25247 | Replacing Poles & X/arms - Rangitoto | 2010-09-28 09:49 | 2010-09-28 | 2010-09-28 14:37 | Calculated | 199 | 199 - Air Break Switch 199 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 173 | 32 | 24506 | 5508 | 0.22476 | 0.0013058 | 235 | 40451 | 2010/2011 | September-2010 | 9 | 2010
24130 | Fault on CB190 - Kuratau Sub | 2010-09-28 16:46 | 2010-09-28 | 2010-09-28 19:16 | Calculated | 5189 | 5189 - Circuit Breaker 5189 |  | No Segment | 509-01 Kuratau | Rural D | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24506 |  | 0 | 0 |  |  | 2010/2011 | September-2010 | 9 | 2010
24131 | Fault Zone Extended - SH41 | 2010-09-28 16:51 | 2010-09-28 | 2010-09-28 18:04 | Calculated | 6353 | 6353 - Sectionaliser with Bypass & Links 6353 |  | 406SEG5658-6355 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 359 | 24506 | 26207 | 1.0694 | 0.014649 | 2092.5 | 152752 | 2010/2011 | September-2010 | 9 | 2010
25248 | Replacing Poles & X/arms - Rangitoto | 2010-09-29 09:05 | 2010-09-29 | 2010-09-29 14:54 | Calculated | 199 | 199 - Air Break Switch 199 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 320 | 32 | 24506 | 10212 | 0.41671 | 0.0013058 | 235 | 74996 | 2010/2011 | September-2010 | 9 | 2010
24133 | Fuse Pulled Apart - National Park | 2010-09-29 15:20 | 2010-09-29 | 2010-09-29 16:29 | Calculated | T4033 | T4033 - 1 Phase : 15.00 kVA : POLEMNT |  | 411SEG5144-5769 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 1 | 24506 | 69 | 0.00282 | 4.0806e-05 | 15 | 1035 | 2010/2011 | September-2010 | 9 | 2010
25325 | Replace Link 775 - Waitomo Caves Rd | 2010-09-30 05:01 | 2010-09-30 | 2010-09-30 06:01 | Calculated | 775 | 775 - Solid Link 775 |  | 101SEG775 | Caves 101-06 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 9 | 24506 | 540 | 0.02204 | 0.00036726 | 102.5 | 6155 | 2010/2011 | September-2010 | 9 | 2010
24142 | Replacing poles & xarm | 2010-09-30 09:11 | 2010-09-30 | 2010-09-30 14:17 | Calculated | 199 | 199 - Air Break Switch 199 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 279 | 32 | 24506 | 8928 | 0.36432 | 0.0013058 | 235 | 65565 | 2010/2011 | September-2010 | 9 | 2010
24144 | Unknown Fault - Manunui-Tokaanu Highway | 2010-09-30 12:45 | 2010-09-30 | 2010-09-30 13:05 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 37 | 24506 | 740 | 0.0302 | 0.0015098 | 227.5 | 4550 | 2010/2011 | September-2010 | 9 | 2010
24146 | Unknown Fault - Te Kura Rd | 2010-09-30 15:30 | 2010-09-30 | 2010-09-30 16:27 | Calculated | 383 | 383 - Fused Link 383 |  | 110SEG383 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 14 | 24506 | 798 | 0.03256 | 0.00057129 | 110 | 6270 | 2010/2011 | September-2010 | 9 | 2010
24147 | Unknown Fault - Okama Rd | 2010-10-01 07:30 | 2010-10-01 | 2010-10-01 09:25 | Calculated | T1716 | T1716 - 3 Phase : 25.00 kVA : POLEMNT |  | 129SEG635-451RET | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 4 | 24504 | 460 | 0.01877 | 0.00016324 | 25 | 2875 | 2010/2011 | October-2010 | 10 | 2010
24149 | Unknown Fault - SHW32 | 2010-10-01 08:10 | 2010-10-01 | 2010-10-01 11:00 | Calculated | 5531 | 5531 - Sectionaliser 5531 |  | 426SEG5531 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 13 | 24504 | 2210 | 0.09019 | 0.00053053 | 125 | 21249 | 2010/2011 | October-2010 | 10 | 2010
25326 | Replaceingj Poles and X/arms - Walker Rd | 2010-10-01 08:54 | 2010-10-01 | 2010-10-01 13:41 | Calculated | 199 | 199 - Air Break Switch 199 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 31 | 24504 | 7658 | 0.31252 | 0.0012651 | 255 | 62997 | 2010/2011 | October-2010 | 10 | 2010
24150 | Unknown Fault - Waitomo Valley Rd | 2010-10-01 13:30 | 2010-10-01 | 2010-10-01 15:27 | Calculated | T216 | T216 - 1 Phase : 10.00 kVA : POLEMNT |  | 112SEG331-355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 2 | 24504 | 234 | 0.00955 | 8.1619e-05 | 10 | 1170 | 2010/2011 | October-2010 | 10 | 2010
24908 | Jumper Off Tx187- Veale Rd | 2010-10-02 08:31 | 2010-10-02 | 2010-10-02 11:30 | Calculated | T187 | T187 - 3ph 50kVA POLEMNT |  | 109SEG620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 8 | 24504 | 1210 | 0.04938 | 0.00032648 | 75 | 11582 | 2010/2011 | October-2010 | 10 | 2010
24902 | CB180 Tripped - Kuratau Sub | 2010-10-03 04:56 | 2010-10-03 | 2010-10-03 05:12 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 4 | 24504 | 64 | 0.00261 | 0.00016324 | 450 | 7290 | 2010/2011 | October-2010 | 10 | 2010
24903 | CB1748 Tripped - Kaahu Tee Zone Substation | 2010-10-03 11:18 | 2010-10-03 | 2010-10-03 11:29 | Calculated | 1748 | 1748 - Circuit Breaker 1748 |  | No Segment | 216-01 Kaahu Tee | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 206 | 24504 | 2111 | 0.08615 | 0.0084068 | 2320 | 23779 | 2010/2011 | October-2010 | 10 | 2010
24906 | Pole Down - Gadsby Rd | 2010-10-03 12:22 | 2010-10-03 | 2010-10-03 16:05 | Calculated | 513 | 513 - Circuit Breaker Gadsby Rd 11 kV Feeder 513 |  | No Segment | 205-01 Gadsby Road | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 223 | 434 | 24504 | 20476 | 0.83562 | 0.017711 | 3365 | 166558 | 2010/2011 | October-2010 | 10 | 2010
24905 | Replace Fuse Tx02K10 - Ongarure Stream Rd | 2010-10-03 18:26 | 2010-10-03 | 2010-10-03 20:07 | Calculated | 02K10 | 02K10 - 1 Phase : 30.00 kVA : POLEMNT |  | 421SEG5874-6730 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 3 | 24504 | 303 | 0.01237 | 0.00012243 | 30 | 3035 | 2010/2011 | October-2010 | 10 | 2010
24910 | Replacing Poles & X/arms - Walker Rd | 2010-10-04 09:04 | 2010-10-04 | 2010-10-04 14:02 | Calculated | 199 | 199 - Air Break Switch 199 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 267 | 37 | 24504 | 9862 | 0.40246 | 0.00151 | 325 | 86628 | 2010/2011 | October-2010 | 10 | 2010
24899 | Replace Fuse Tx14I02 - Upper Retaruke Rd | 2010-10-04 09:56 | 2010-10-04 | 2010-10-04 10:37 | Calculated | 14I02 | 14I02 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5334-5745 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 1 | 24504 | 41 | 0.00167 | 4.081e-05 | 10 | 412 | 2010/2011 | October-2010 | 10 | 2010
24898 | Isolate & Earth For Treescape - Whakamaru/108/14 | 2010-10-04 10:05 | 2010-10-04 | 2010-10-04 13:49 | Calculated | 2065 | 2065 - Fused Link 2065 |  | 120SEG482-480 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 224 | 8 | 24504 | 1794 | 0.07321 | 0.00032648 | 135 | 30275 | 2010/2011 | October-2010 | 10 | 2010
24901 | Faulty Insulator On Low Line - Kuratau Power Station | 2010-10-04 15:20 | 2010-10-04 | 2010-10-04 17:49 | Calculated | 5150 | 5150 - Fused Link 5150 |  | 426SEG5150-5737 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 149 | 157 | 24504 | 23421 | 0.9558 | 0.0064071 | 1183.5 | 176558 | 2010/2011 | October-2010 | 10 | 2010
24894 | Replace Poles & X/arms - Main South Highway - South of Erua | 2010-10-05 09:41 | 2010-10-05 | 2010-10-05 15:24 | Calculated | 5329 | 5329 - Fused Link 5329 |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 343 | 18 | 24504 | 6179 | 0.25216 | 0.00073457 | 128 | 43946 | 2010/2011 | October-2010 | 10 | 2010
24895 | Digger vs L/V - Tihoi Rd | 2010-10-05 14:21 | 2010-10-05 | 2010-10-05 15:24 | Calculated | TF735 | TF735 - Transformer Fuse: TF735 |  | 120SEG484-483 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 21 | 24504 | 1329 | 0.05424 | 0.000857 | 50 | 3164 | 2010/2011 | October-2010 | 10 | 2010
24896 | Lines Wrapped - Waitomo Caves Rd | 2010-10-05 16:20 | 2010-10-05 | 2010-10-05 17:13 | Calculated | T132 | T132 - 3ph 15kVA POL |  | 101SEG679-267 | Caves 101-06 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 24504 | 104 | 0.00424 | 8.1619e-05 | 15 | 784 | 2010/2011 | October-2010 | 10 | 2010
24897 | Soccer Ball vs L/V - Taupo Rd | 2010-10-05 20:11 | 2010-10-05 | 2010-10-05 21:14 | Calculated | 01B24 | 01B24 - 3 Phase : 300.00 kVA : GNDPAD |  | 404SEGF1.34-F1.32 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 68 | 24504 | 4303 | 0.1756 | 0.0027751 | 300 | 18984 | 2010/2011 | October-2010 | 10 | 2010
24909 | Replace Poles & X/arms - Walker Rd | 2010-10-06 09:59 | 2010-10-06 | 2010-10-06 14:42 | Calculated | 199 | 199 - Air Break Switch 199 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 288 | 37 | 24504 | 10635 | 0.43401 | 0.00151 | 325 | 93421 | 2010/2011 | October-2010 | 10 | 2010
25327 | Floating Insulator at Pole 123 - Aorearoa Rd - By Walker Rd | 2010-10-06 14:04 | 2010-10-06 | 2010-10-06 17:21 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 316 | 24504 | 9724 | 0.39683 | 0.012896 | 2602.25 | 78833 | 2010/2011 | October-2010 | 10 | 2010
24907 | Replaceing Poles @X/arms - Walker Rd | 2010-10-07 09:04 | 2010-10-07 | 2010-10-07 14:46 | Calculated | 199 | 199 - Air Break Switch 199 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 310 | 37 | 24504 | 11449 | 0.46723 | 0.00151 | 310 | 95924 | 2010/2011 | October-2010 | 10 | 2010
24891 | Digger vs L/V - Paerata Rd | 2010-10-07 14:02 | 2010-10-07 | 2010-10-07 14:41 | Calculated | T1207 | T1207 - 3 Phase : 25.00 kVA : POLEMNT |  | 129SEG402-725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 3 | 24504 | 118 | 0.00482 | 0.00012243 | 25 | 984 | 2010/2011 | October-2010 | 10 | 2010
24912 | Replaceing Poles @X/arms - Walker Rd | 2010-10-08 09:05 | 2010-10-08 | 2010-10-08 14:30 | Calculated | 199 | 199 - Air Break Switch 199 |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 37 | 24504 | 10524 | 0.42948 | 0.00151 | 310 | 88174 | 2010/2011 | October-2010 | 10 | 2010
24885 | Digger vs L/V - Tihoi Rd | 2010-10-08 09:17 | 2010-10-08 | 2010-10-08 11:09 | Calculated | T735 | T735 - 3ph 50kVA POLEMNT |  | 120SEG484-483 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 21 | 24504 | 2356 | 0.09615 | 0.000857 | 50 | 5611 | 2010/2011 | October-2010 | 10 | 2010
24886 | Change Tx - B.P. Rd | 2010-10-08 09:26 | 2010-10-08 | 2010-10-08 17:20 | Calculated | 01B13 | 01B13 - 3 Phase : 30.00 kVA : GNDPAD |  | 404SEG5742 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 474 | 2 | 24504 | 948 | 0.03869 | 8.1619e-05 | 30 | 14229 | 2010/2011 | October-2010 | 10 | 2010
24887 | Line Renewal - Raurimu Rd | 2010-10-08 09:35 | 2010-10-08 | 2010-10-08 12:29 | Calculated | 13K02 | 13K02 - 3 Phase : 200.00 kVA : POLEMNT |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 173 | 16 | 24504 | 2773 | 0.11317 | 0.00065295 | 200 | 34673 | 2010/2011 | October-2010 | 10 | 2010
24888 | Replace L/V Fuse - Mangakahu Rd | 2010-10-08 13:32 | 2010-10-08 | 2010-10-08 13:58 | Calculated | 05K04 | 05K04 - 1 Phase : 30.00 kVA : POLEMNT |  | 402SEG5360-5267 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 5 | 24504 | 130 | 0.00531 | 0.00020405 | 30 | 785 | 2010/2011 | October-2010 | 10 | 2010
24889 | Replace Fuse Tx17K03 - SH 4 | 2010-10-08 14:46 | 2010-10-08 | 2010-10-08 15:46 | Calculated | 17K03 | 17K03 - 1 Phase : 7.50 kVA : POLEMNT |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 1 | 24504 | 60 | 0.00245 | 4.081e-05 | 7.5 | 452 | 2010/2011 | October-2010 | 10 | 2010
24890 | OCB594 &754 Tripped -Gadsby Rd - Line Facing | 2010-10-08 21:13 | 2010-10-08 | 2010-10-08 21:20 | Calculated | 594 | 594 - Circuit Breaker 594 |  | No Segment | 205-01 Gadsby Road | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 2028 | 24504 | 14635 | 0.59725 | 0.082762 | 13909.5 | 100380 | 2010/2011 | October-2010 | 10 | 2010
25328 | Faulty Insulators - Whangamama Rd | 2010-10-09 03:13 | 2010-10-09 | 2010-10-09 18:54 | Calculated | 446 | 446 - Recloser 446 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 514 | 187 | 24504 | 56196 | 2.2933 | 0.0076314 | 1577.5 | 427522 | 2010/2011 | October-2010 | 10 | 2010
25329 | Faulty Insulators - Whangamata Rd | 2010-10-09 12:26 | 2010-10-09 | 2010-10-09 17:23 | Calculated | 446 | 446 - Recloser 446 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLX | Faulty Manufacture | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 297 | 187 | 24504 | 38409 | 1.5675 | 0.0076314 | 1577.5 | 287617 | 2010/2011 | October-2010 | 10 | 2010
24884 | Branch on L/V - Troopers Rd | 2010-10-09 13:31 | 2010-10-09 | 2010-10-09 14:20 | Calculated | T1211 | T1211 - 3 Phase : 25.00 kVA : POLEMNT | Branch on L/V - Troopers Rd | 107SEG266 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 2 | 24504 | 98 | 0.004 | 8.1619e-05 | 25 | 1231 | 2010/2011 | October-2010 | 10 | 2010
24883 | Cable Fault to Tx4208 - Soldiers Rd | 2010-10-10 10:29 | 2010-10-10 | 2010-10-10 10:40 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDI | Conductor Failure - Insulated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 2 | 24504 | 22 | 0.0009 | 8.1619e-05 | 0 | 0 | 2010/2011 | October-2010 | 10 | 2010
24881 | Jumper Off @ Link 302 - Tokirima Rd | 2010-10-10 21:21 | 2010-10-10 | 2010-10-11 07:43 | Calculated | 5302 | 5302 - Fused Link 5302 |  | 413SEG5568-5301 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 622 | 10 | 24504 | 6226 | 0.25408 | 0.0004081 | 93 | 57901 | 2010/2011 | October-2010 | 10 | 2010
24882 | L/V Jumper Off - Findlay St | 2010-10-10 23:31 | 2010-10-10 | 2010-10-11 01:25 | Calculated | 15L06 | 15L06 - 3ph 100kVA polemnt |  | 411SEG5769-5147 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 56 | 24504 | 6397 | 0.26106 | 0.0022853 | 100 | 11423 | 2010/2011 | October-2010 | 10 | 2010
25444 | Trees Through Line - Marotiri Sub | 2010-10-11 06:21 | 2010-10-11 | 2010-10-11 18:59 | Calculated | CB2 | CB2 - Circuit Breaker Tihoi Feeder CB2 |  | No Segment | 212-01 Marotiri | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 660 | 229 | 24504 | 34395 | 1.4037 | 0.0093454 | 2343.2778 | 396937 | 2010/2011 | October-2010 | 10 | 2010
25449 | Extreme Wind - Tangiwai Timber Mill | 2010-10-11 07:31 | 2010-10-11 | 2010-10-11 08:43 | Calculated | 5780 | 5780 - Fused Link 5780 |  | 416SEG5780-6608 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 21 | 24504 | 1517 | 0.06191 | 0.000857 | 230 | 16621 | 2010/2011 | October-2010 | 10 | 2010
24223 | Extreme Wind - SH47 | 2010-10-11 10:42 | 2010-10-11 | 2010-10-11 17:30 | Calculated | 6007 | 6007 - Circuit Breaker 6007 |  | No Segment | 513-01 Tawhai | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 408 | 120 | 24504 | 42075 | 1.7171 | 0.0048972 | 1171 | 415162 | 2010/2011 | October-2010 | 10 | 2010
25445 | Extreme Wind - SH 47 | 2010-10-11 10:42 | 2010-10-11 | 2010-10-11 17:53 | Calculated | TF12P05 | TF12P05 - Transformer Fuse: TF12P05 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 430 | 1 | 24504 | 430 | 0.01755 | 4.081e-05 | 15 | 6454 | 2010/2011 | October-2010 | 10 | 2010
24212 | Magpie - Tapuwae Road | 2010-10-11 10:47 | 2010-10-11 | 2010-10-11 13:51 | Calculated | T2119 | T2119 - 1 Phase : 5.00 kVA : POLEMNT |  | 103SEG705-1736 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 1 | 24504 | 184 | 0.00751 | 4.081e-05 | 5 | 920 | 2010/2011 | October-2010 | 10 | 2010
24213 | Trees (Multiple Poles Down) - Mapara Road | 2010-10-11 12:05 | 2010-10-11 | 2010-10-11 15:57 | Calculated | 1297 | 1297 - Fused Link 1297 |  | 117SEG1297-1296 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 232 | 22 | 24504 | 5104 | 0.20829 | 0.00089781 | 150 | 34800 | 2010/2011 | October-2010 | 10 | 2010
24214 | SWER Backfeed - SH4 | 2010-10-11 12:05 | 2010-10-11 | 2010-10-11 16:45 | Calculated | 1273 | 1273 - Fused Link 1273 |  | 117SEG1296-1273 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation |  | VEGE |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 280 | 42 | 24504 | 11760 | 0.47992 | 0.001714 | 335.5 | 93940 | 2010/2011 | October-2010 | 10 | 2010
24224 | Extreme Wind - Turongo Street | 2010-10-11 12:05 | 2010-10-11 | 2010-10-11 15:00 | Calculated | 668 | 668 - Fused Link 668 |  | 112SEG668-229 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 39 | 24504 | 6825 | 0.27853 | 0.0015916 | 400 | 69999 | 2010/2011 | October-2010 | 10 | 2010
25442 | Trees (Multiple Poles Down) - Mapara Road | 2010-10-11 12:05 | 2010-10-11 | 2010-10-11 16:41 | Calculated | 1273 | 1273 - Fused Link 1273 |  | 117SEG1296-1273 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 276 | 8 | 24504 | 2208 | 0.09011 | 0.00032648 | 65 | 17939 | 2010/2011 | October-2010 | 10 | 2010
25443 | Trees - Tikitiki Rd | 2010-10-11 12:06 | 2010-10-11 | 2010-10-11 22:17 | Calculated | SEG1296-1273 | SEG1296-1273 - 117SEG1296-1273 |  | No Segment | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 611 | 10 | 24504 | 6112 | 0.24943 | 0.0004081 | 70 | 42788 | 2010/2011 | October-2010 | 10 | 2010
24225 | Extreme Wind - SH4 | 2010-10-11 12:40 | 2010-10-11 | 2010-10-11 17:51 | Calculated | 1724 | 1724 - Sectionaliser 1724 |  | No Segment | No Asset Group | Remote Rural F | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 311 | 9 | 24504 | 2799 | 0.11423 | 0.00036729 | 68 | 21148 | 2010/2011 | October-2010 | 10 | 2010
24226 | Extreme Wind - Tangitu | 2010-10-11 12:40 | 2010-10-11 | 2010-10-11 19:54 | Calculated | 1725 | 1725 - Fused Link 1725 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 434 | 6 | 24504 | 2604 | 0.10627 | 0.00024486 | 75 | 32550 | 2010/2011 | October-2010 | 10 | 2010
24227 | Extreme Wind - Waimiha Township | 2010-10-11 12:40 | 2010-10-11 | 2010-10-11 19:54 | Calculated | 1726 | 1726 - Fused Link 1726 |  | 103SEG1726-1733 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 434 | 6 | 24504 | 2604 | 0.10627 | 0.00024486 | 30 | 13020 | 2010/2011 | October-2010 | 10 | 2010
24215 | Lines Down - Kie Kie Road | 2010-10-11 12:43 | 2010-10-11 | 2010-10-11 14:27 | Calculated | 1101 | 1101 - Fused Link 1101 |  | 114SEG1101 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 9 | 24504 | 936 | 0.0382 | 0.00036729 | 67.5 | 7020 | 2010/2011 | October-2010 | 10 | 2010
24228 | Extreme Wind - Findlay Street | 2010-10-11 13:10 | 2010-10-11 | 2010-10-11 17:12 | Calculated | 15L06 | 15L06 - 3ph 100kVA polemnt |  | 411SEG5769-5147 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 242 | 56 | 24504 | 13552 | 0.55305 | 0.0022853 | 100 | 24199 | 2010/2011 | October-2010 | 10 | 2010
25446 | Extreme Wind - Lines Wrapped - Mokauiti Rd | 2010-10-11 14:31 | 2010-10-11 | 2010-10-11 17:32 | Calculated | 682 | 682 - Circuit Breaker 682 |  | No Segment | 207-01 Wairere Falls | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 184 | 24504 | 19892 | 0.81179 | 0.007509 | 1562.25 | 150526 | 2010/2011 | October-2010 | 10 | 2010
24229 | Extreme Wind - View Road | 2010-10-11 14:40 | 2010-10-11 | 2010-10-11 17:57 | Calculated | T1467 | T1467 - 3ph 50kVA POLEMNT |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 7 | 24504 | 1379 | 0.05628 | 0.00028567 | 50 | 9849 | 2010/2011 | October-2010 | 10 | 2010
24230 | Tree on Line - Okaihae Road | 2010-10-11 14:57 | 2010-10-11 | 2010-10-11 17:41 | Calculated | 5480 | 5480 - Solid Link 5480 |  | 402SEG5480 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 164 | 17 | 24504 | 2788 | 0.11378 | 0.00069376 | 125 | 20500 | 2010/2011 | October-2010 | 10 | 2010
25448 | Jumper off @ Pole 22 - Golf Road Extension | 2010-10-11 15:20 | 2010-10-11 | 2010-10-11 17:26 | Calculated | 5119 | 5119 - Recloser 5119 |  | 402SEG5118-5119RET | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 607 | 24504 | 56606 | 2.3101 | 0.024771 | 4825.3749 | 451513 | 2010/2011 | October-2010 | 10 | 2010
24234 | Line Down - Waihaha Road | 2010-10-11 15:48 | 2010-10-11 | 2010-10-11 18:25 | Calculated | 5534 | 5534 - Sectionaliser 5534 |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 14 | 24504 | 2198 | 0.0897 | 0.00057134 | 105 | 16485 | 2010/2011 | October-2010 | 10 | 2010
24235 | Extreme Wind - Amos Road | 2010-10-11 16:50 | 2010-10-11 | 2010-10-11 19:39 | Calculated | 03L01 | 03L01 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 169 | 3 | 24504 | 507 | 0.02069 | 0.00012243 | 15 | 2535 | 2010/2011 | October-2010 | 10 | 2010
24236 | Extreme Wind - Hikumutu | 2010-10-11 17:20 | 2010-10-11 | 2010-10-11 18:58 | Calculated | 5811 | 5811 - Sectionaliser with Incoming Link 5811 |  | 403SEG5811-5315 | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 17 | 24504 | 1666 | 0.06799 | 0.00069376 | 158 | 15484 | 2010/2011 | October-2010 | 10 | 2010
24237 | Extreme Wind - Hikumutu Road | 2010-10-11 17:20 | 2010-10-11 | 2010-10-11 19:59 | Calculated | 5315 | 5315 - Fused Link 5315 |  | 403SEG5315 | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 10 | 24504 | 1590 | 0.06489 | 0.0004081 | 45 | 7155 | 2010/2011 | October-2010 | 10 | 2010
24239 | Extreme Wind - Makokomiko Sub | 2010-10-11 17:20 | 2010-10-11 | 2010-10-11 20:21 | Calculated | 5599 | 5599 - Recloser with Bypass & Links 5599 |  | 409SEG5598-5599 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 44 | 24504 | 7964 | 0.32501 | 0.0017956 | 303 | 54842 | 2010/2011 | October-2010 | 10 | 2010
24880 | Tree Smashed Tx - SH 43 | 2010-10-11 18:00 | 2010-10-11 | 2010-10-13 15:08 | Calculated | 09I03 | 09I03 - 1 Phase : 15.00 kVA : POLEMNT |  | 403SEG5594-5601 | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2707 | 1 | 24504 | 2707 | 0.11047 | 4.081e-05 | 15 | 40617 | 2010/2011 | October-2010 | 10 | 2010
24206 | Trees Through Line - Tihoi Road | 2010-10-11 18:55 | 2010-10-11 | 2010-10-11 18:58 | Calculated | 440 | 440 - Recloser with Outgoing Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 50 | 24504 | 150 | 0.00612 | 0.0020405 | 370.5 | 1111 | 2010/2011 | October-2010 | 10 | 2010
24238 | Extreme Wind - Ongarue Sub | 2010-10-11 19:15 | 2010-10-11 | 2010-10-11 21:10 | Calculated | 5476 | 5476 - Fused Link 5476 |  | 421SEG04I01-5586 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 81 | 24504 | 9315 | 0.38014 | 0.0033056 | 548.5 | 63077 | 2010/2011 | October-2010 | 10 | 2010
24240 | Mulitple Poles Down - Main Road | 2010-10-11 19:25 | 2010-10-11 | 2010-10-11 19:56 | Calculated | 5311 | 5311 - Air Break Switch 5311 |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 97 | 24504 | 3007 | 0.12271 | 0.0039585 | 435 | 13484 | 2010/2011 | October-2010 | 10 | 2010
25450 | Multiple Poles Down - Mill Rd | 2010-10-11 19:26 | 2010-10-11 | 2010-10-12 20:11 | Calculated | 6159 | 6159 - Fused Link 6159 |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1485 | 18 | 24504 | 26733 | 1.091 | 0.00073457 | 75 | 111387 | 2010/2011 | October-2010 | 10 | 2010
24243 | Wind - Amos Road | 2010-10-12 08:27 | 2010-10-12 | 2010-10-12 16:36 | Calculated | 03L01 | 03L01 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 489 | 3 | 24504 | 1467 | 0.05987 | 0.00012243 | 15 | 7335 | 2010/2011 | October-2010 | 10 | 2010
24244 | Wind - Tranzrail | 2010-10-12 08:55 | 2010-10-12 | 2010-10-12 13:51 | Calculated | 15L09 | 15L09 - 3 Phase : 30.00 kVA : POLEMNT |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 296 | 1 | 24504 | 296 | 0.01208 | 4.081e-05 | 30 | 8880 | 2010/2011 | October-2010 | 10 | 2010
24245 | Wind/Clash - Kaahu South Road | 2010-10-12 10:15 | 2010-10-12 | 2010-10-12 11:13 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 27 | 24504 | 1566 | 0.06391 | 0.0011019 | 310 | 17980 | 2010/2011 | October-2010 | 10 | 2010
24247 | Wind - Paerata Road | 2010-10-12 10:23 | 2010-10-12 | 2010-10-12 12:37 | Calculated | 455 | 455 - Fused Link 455 |  | 129SEG455-402 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 45 | 24504 | 6030 | 0.24608 | 0.0018364 | 395 | 52929 | 2010/2011 | October-2010 | 10 | 2010
24246 | Wind/Clash - Kaahu South Road | 2010-10-12 14:50 | 2010-10-12 | 2010-10-12 15:00 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 27 | 24504 | 270 | 0.01102 | 0.0011019 | 310 | 3100 | 2010/2011 | October-2010 | 10 | 2010
24241 | Re-Instate Jumpers - Mapara Road | 2010-10-12 16:04 | 2010-10-12 | 2010-10-12 17:09 | Calculated | 1297 | 1297 - Fused Link 1297 |  | 117SEG1297-1296 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 30 | 24504 | 1950 | 0.07958 | 0.0012243 | 0 | 0 | 2010/2011 | October-2010 | 10 | 2010
24242 | Restore SWER Backfeed - SH4 | 2010-10-12 17:35 | 2010-10-12 | 2010-10-12 17:36 | Calculated | 1728 | 1728 - Recloser 1728 |  | 117SEG1728-1260 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Vegetation |  | VEGE |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 1 | 42 | 24504 | 42 | 0.00171 | 0.001714 | 335.5 | 335 | 2010/2011 | October-2010 | 10 | 2010
24253 | Broken Neutral - SH47 | 2010-10-12 19:06 | 2010-10-12 | 2010-10-12 20:05 | Calculated | 12N05 | 12N05 - 3 Phase : 200.00 kVA : POLEMNT |  | 609SEG5159-6761 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 5 | 24504 | 295 | 0.01204 | 0.00020405 | 200 | 11800 | 2010/2011 | October-2010 | 10 | 2010
24254 | Wind - Tahaia Bush Road | 2010-10-13 06:25 | 2010-10-13 | 2010-10-13 07:40 | Calculated | 587 | 587 - Fused Link 587 |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 13 | 24504 | 975 | 0.03979 | 0.00053053 | 100 | 7499 | 2010/2011 | October-2010 | 10 | 2010
24255 | Wind - Paewhenua Road | 2010-10-13 07:15 | 2010-10-13 | 2010-10-13 08:44 | Calculated | T283 | T283 - 3 Phase : 25.00 kVA : POLEMNT |  | 111SEG399-374 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 6 | 24504 | 534 | 0.02179 | 0.00024486 | 25 | 2224 | 2010/2011 | October-2010 | 10 | 2010
24257 | Jumper off @ T2804 - Wharepapa Road | 2010-10-13 09:44 | 2010-10-13 | 2010-10-13 10:31 | Calculated | 380 | 380 - Air Break Switch 380 |  | 122SEG398-380 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 36 | 24504 | 1692 | 0.06905 | 0.0014691 | 307.5 | 14452 | 2010/2011 | October-2010 | 10 | 2010
24258 | Wind - Ropiha Road | 2010-10-13 12:10 | 2010-10-13 | 2010-10-13 14:18 | Calculated | T1117 | T1117 - 1 Phase : 10.00 kVA : POLEMNT |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 2 | 24504 | 256 | 0.01045 | 8.1619e-05 | 10 | 1280 | 2010/2011 | October-2010 | 10 | 2010
24259 | CT Metering - Ranfurly Street | 2010-10-14 08:27 | 2010-10-14 | 2010-10-14 09:18 | Calculated | T1257 | T1257 - 3 Phase : 50.00 kVA : GNDPAD |  | 112SEG300-646 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 51 | 1 | 24504 | 51 | 0.00208 | 4.081e-05 | 50 | 2550 | 2010/2011 | October-2010 | 10 | 2010
24260 | Broken Xarm - Pukawa Sub | 2010-10-14 09:27 | 2010-10-14 | 2010-10-14 10:27 | Calculated | 5617 | 5617 - Fused Link 5617 |  | 406SEG5617-5250 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 23 | 24504 | 1380 | 0.05632 | 0.00093862 | 117.5 | 7050 | 2010/2011 | October-2010 | 10 | 2010
24261 | Broken Xarm - Te Waitere Road | 2010-10-14 11:28 | 2010-10-14 | 2010-10-14 13:06 | Calculated | 298 | 298 - Fused Link 298 |  | 125SEG298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 9 | 24504 | 882 | 0.03599 | 0.00036729 | 45 | 4409 | 2010/2011 | October-2010 | 10 | 2010
25453 | Disconnect Gen Set - Mill Rd | 2010-10-14 12:26 | 2010-10-14 | 2010-10-14 16:51 | Calculated | 6159 | 6159 - Fused Link 6159 |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 265 | 18 | 24504 | 4774 | 0.19483 | 0.00073457 | 75 | 19894 | 2010/2011 | October-2010 | 10 | 2010
24262 | Fit New T/O Links - Main Road | 2010-10-14 13:03 | 2010-10-14 | 2010-10-14 13:29 | Calculated | 5311 | 5311 - Air Break Switch 5311 |  | 409SEG5311-5452 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 84 | 24504 | 2184 | 0.08913 | 0.003428 | 387.9094 | 10085 | 2010/2011 | October-2010 | 10 | 2010
24264 | Changing Poles & Xarms - Maihiihi Feeder | 2010-10-15 09:06 | 2010-10-15 | 2010-10-15 14:52 | Calculated | 707 | 707 - Air Break Switch 707 |  | 111SEG707-399 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 306 | 33 | 24504 | 10098 | 0.4121 | 0.0013467 | 260 | 79559 | 2010/2011 | October-2010 | 10 | 2010
24267 | Wire on Xarm - Waitomo Valley Road | 2010-10-15 10:28 | 2010-10-15 | 2010-10-15 12:59 | Calculated | 1021 | 1021 - Recloser 1021 |  | 112SEG314-1021 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 173 | 24504 | 10597 | 0.43246 | 0.0070601 | 1675.0833 | 102121 | 2010/2011 | October-2010 | 10 | 2010
24270 | Line Down @ Link 1736 - Poro-o-tarao | 2010-10-17 13:10 | 2010-10-17 | 2010-10-17 16:00 | Calculated | 705 | 705 - Recloser with Bypass & Links 705 |  | 103SEG1774-1750 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 20 | 24504 | 3400 | 0.13875 | 0.00081619 | 132.5 | 22525 | 2010/2011 | October-2010 | 10 | 2010
24271 | Branch on Line - Ruapehu Road | 2010-10-17 14:17 | 2010-10-17 | 2010-10-17 14:33 | Calculated | 5677 | 5677 - Recloser with Bypass 5677 |  | 416SEG5677-5681 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 16 | 230 | 24504 | 3680 | 0.15018 | 0.0093862 | 7770 | 124319 | 2010/2011 | October-2010 | 10 | 2010
24272 | Replace L.A - Mahoenui (Re-work) | 2010-10-18 10:35 | 2010-10-18 | 2010-10-18 11:58 | Calculated | 1543 | 1543 - Fused Link 1543 |  | 113SEG1543 | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 83 | 3 | 24504 | 249 | 0.01016 | 0.00012243 | 15 | 1245 | 2010/2011 | October-2010 | 10 | 2010
24273 | Wind - Tahaia Bush Road | 2010-10-18 12:15 | 2010-10-18 | 2010-10-18 13:48 | Calculated | 587 | 587 - Fused Link 587 |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 13 | 24504 | 1209 | 0.04934 | 0.00053053 | 100 | 9299 | 2010/2011 | October-2010 | 10 | 2010
24274 | Wind - Oio Sub | 2010-10-18 13:14 | 2010-10-18 | 2010-10-18 14:08 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 54 | 25 | 24504 | 1350 | 0.05509 | 0.0010202 | 138.5 | 7478 | 2010/2011 | October-2010 | 10 | 2010
24276 | Wind - Haurua Road | 2010-10-18 17:30 | 2010-10-18 | 2010-10-18 18:36 | Calculated | 519 | 519 - Fused Link 519 |  | 101SEG519-232 | Caves 101-02 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 19 | 24504 | 1254 | 0.05118 | 0.00077538 | 235 | 15509 | 2010/2011 | October-2010 | 10 | 2010
24277 | Jumper Off - Maihiihi Road | 2010-10-18 17:50 | 2010-10-18 | 2010-10-18 18:22 | Calculated | 662 | 662 - Fused Link 662 |  | 111SEG662 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 4 | 24504 | 128 | 0.00522 | 0.00016324 | 45 | 1440 | 2010/2011 | October-2010 | 10 | 2010
24279 | Faulty Tx - SH43 | 2010-10-19 19:30 | 2010-10-19 | 2010-10-19 21:42 | Calculated | 09G10 | 09G10 - no label |  | 403SEG5932-5649 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 2 | 24504 | 264 | 0.01077 | 8.1619e-05 | 15 | 1980 | 2010/2011 | October-2010 | 10 | 2010
24280 | Changing Poles & Xarms - Maihiihi Feeder | 2010-10-20 09:10 | 2010-10-20 | 2010-10-20 14:45 | Calculated | 358 | 358 - Air Break Switch 358 |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 274 | 9 | 24504 | 2466 | 0.10064 | 0.00036729 | 115 | 31509 | 2010/2011 | October-2010 | 10 | 2010
24281 | Floating Insulator - Haurua Road | 2010-10-20 11:38 | 2010-10-20 | 2010-10-20 13:02 | Calculated | 519 | 519 - Fused Link 519 |  | 101SEG519-232 | Caves 101-02 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 19 | 24504 | 1596 | 0.06513 | 0.00077538 | 235 | 19739 | 2010/2011 | October-2010 | 10 | 2010
24283 | Wind - Taharoa | 2010-10-21 03:58 | 2010-10-21 | 2010-10-21 07:17 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 321 | 24504 | 963 | 0.0393 | 0.0131 | 2511 | 7533 | 2010/2011 | October-2010 | 10 | 2010
24284 | Changing Poles & Xarms - Maihiihi Feeder | 2010-10-21 09:13 | 2010-10-21 | 2010-10-21 14:59 | Calculated | 358 | 358 - Air Break Switch 358 |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 9 | 24504 | 2718 | 0.11092 | 0.00036729 | 115 | 34729 | 2010/2011 | October-2010 | 10 | 2010
24285 | Wind - Oio Sub | 2010-10-21 13:45 | 2010-10-21 | 2010-10-21 14:04 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 25 | 24504 | 475 | 0.01938 | 0.0010202 | 138.5 | 2631 | 2010/2011 | October-2010 | 10 | 2010
24286 | Wind - Oio Sub | 2010-10-21 14:19 | 2010-10-21 | 2010-10-21 15:04 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 25 | 24504 | 1125 | 0.04591 | 0.0010202 | 138.5 | 6232 | 2010/2011 | October-2010 | 10 | 2010
24287 | Wind - Tahaia Bush Road | 2010-10-21 15:35 | 2010-10-21 | 2010-10-21 18:54 | Calculated | 587 | 587 - Fused Link 587 |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 14 | 24504 | 2577 | 0.10517 | 0.00057134 | 107.5 | 19824 | 2010/2011 | October-2010 | 10 | 2010
24289 | Wind - Paekaka Road | 2010-10-21 19:42 | 2010-10-21 | 2010-10-21 19:51 | Calculated | 1512 | 1512 - Recloser 1512 |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 160 | 24504 | 1440 | 0.05877 | 0.0065295 | 1063.5 | 9571 | 2010/2011 | October-2010 | 10 | 2010
24879 | Wind - Waimahora Rd | 2010-10-22 08:30 | 2010-10-22 | 2010-10-22 12:49 | Calculated | T1290 | T1290 - 1 Phase : 5.00 kVA : POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 258 | 4 | 24504 | 1034 | 0.0422 | 0.00016324 | 65 | 16815 | 2010/2011 | October-2010 | 10 | 2010
24291 | Changing Poles & Xarms - Maihiihi Feeder | 2010-10-22 09:06 | 2010-10-22 | 2010-10-22 15:14 | Calculated | 358 | 358 - Air Break Switch 358 |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 317 | 9 | 24504 | 2853 | 0.11643 | 0.00036729 | 115 | 36454 | 2010/2011 | October-2010 | 10 | 2010
24290 | Cut Clear P/L LV Fault | 2010-10-22 09:36 | 2010-10-22 | 2010-10-22 10:32 | Calculated | T284 | T284 - 3 Phase : 50.00 kVA : POLEMNT |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 7 | 24504 | 392 | 0.016 | 0.00028567 | 50 | 2799 | 2010/2011 | October-2010 | 10 | 2010
24293 | Big Span Down - Kokakoriki Road | 2010-10-22 12:10 | 2010-10-22 | 2010-10-22 18:57 | Calculated | 5603 | 5603 - Fused Link 5603 |  | 403SEG5603-5883 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 407 | 12 | 24504 | 4884 | 0.19931 | 0.00048972 | 75 | 30525 | 2010/2011 | October-2010 | 10 | 2010
24294 | Fuse Pulled Apart - Waitomo Valley Road | 2010-10-22 14:40 | 2010-10-22 | 2010-10-22 16:44 | Calculated | T1216 | T1216 - 1 Phase : 10.00 kVA : POLEMNT |  | 112SEG326-288 | Otorohanga 112-06 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 3 | 24504 | 372 | 0.01518 | 0.00012243 | 10 | 1239 | 2010/2011 | October-2010 | 10 | 2010
24297 | Ducks - Karioi Sports Ground | 2010-10-23 10:07 | 2010-10-23 | 2010-10-23 11:50 | Calculated | 5722 | 5722 - Fused Link 5722 |  | 416SEG5722 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 3 | 24504 | 309 | 0.01261 | 0.00012243 | 55 | 5665 | 2010/2011 | October-2010 | 10 | 2010
24299 | Unknown - Lower Retaruke Road | 2010-10-25 09:10 | 2010-10-25 | 2010-10-25 14:50 | Calculated | 5396 | 5396 - Sectionaliser 5396 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 340 | 74 | 24504 | 17214 | 0.7025 | 0.0030199 | 421.75 | 78182 | 2010/2011 | October-2010 | 10 | 2010
24300 | Faulty Tx - McBeth Road | 2010-10-25 10:12 | 2010-10-25 | 2010-10-25 11:27 | Calculated | T2053 | T2053 - 1 Phase : 15.00 kVA : POLEMNT |  | 115SEG1717-1723 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 3 | 24504 | 225 | 0.00918 | 0.00012243 | 22.5 | 1687 | 2010/2011 | October-2010 | 10 | 2010
25458 | Line Down @ Tx 1A35 (Outside School) - Borough Sub | 2010-10-26 11:18 | 2010-10-26 | 2010-10-26 13:27 | Calculated | 5952 | 5952 - Circuit Breaker Matapuna 5952 |  | No Segment | 508-01 Borough | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 1101 | 24504 | 27391 | 1.1178 | 0.044931 | 9438.1835 | 235438 | 2010/2011 | October-2010 | 10 | 2010
24307 | Install new Tx Pole - Mokau Feeder | 2010-10-26 13:28 | 2010-10-26 | 2010-10-26 17:14 | Calculated | 1616 | 1616 - Sectionaliser with Bypass & Links 1616 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 226 | 15 | 24504 | 3390 | 0.13834 | 0.00061214 | 120 | 27120 | 2010/2011 | October-2010 | 10 | 2010
24310 | Magpie - SH32 | 2010-10-27 09:15 | 2010-10-27 | 2010-10-27 10:58 | Calculated | 02R02 | 02R02 - 1 Phase : 10.00 kVA : POLEMNT |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 2 | 24504 | 206 | 0.00841 | 8.1619e-05 | 10 | 1030 | 2010/2011 | October-2010 | 10 | 2010
24309 | Fit Links for New Tx Extension - Maihiihi | 2010-10-27 10:10 | 2010-10-27 | 2010-10-27 12:12 | Calculated | 551 | 551 - Fused Link 551 |  | 111SEG551 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 122 | 9 | 24504 | 1098 | 0.04481 | 0.00036729 | 75 | 9150 | 2010/2011 | October-2010 | 10 | 2010
25459 | Ducks - SH 49 - Coner of Lakes Rd | 2010-10-28 06:00 | 2010-10-28 | 2010-10-28 10:00 | Calculated | 5673 | 5673 - Fused Link 5673 |  | 416SEG5673-5675 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 45 | 24504 | 5576 | 0.22755 | 0.0018364 | 301.25 | 44110 | 2010/2011 | October-2010 | 10 | 2010
24316 | Unknown - Otapouri Sub | 2010-10-28 06:15 | 2010-10-28 | 2010-10-28 07:36 | Calculated | 5428 | 5428 - Fused Link 5428 |  | 409SEG5428-5427 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 42 | 24504 | 3402 | 0.13883 | 0.001714 | 371 | 30050 | 2010/2011 | October-2010 | 10 | 2010
24317 | Changing Poles & Xarms - Maihiihi Feeder | 2010-10-28 09:07 | 2010-10-28 | 2010-10-28 14:46 | Calculated | 707 | 707 - Air Break Switch 707 |  | 111SEG707-399 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 303 | 25 | 24504 | 7575 | 0.30913 | 0.0010202 | 155 | 46964 | 2010/2011 | October-2010 | 10 | 2010
24318 | Line Renewal - Raurimu Road | 2010-10-28 09:30 | 2010-10-28 | 2010-10-28 15:35 | Calculated | 13K02 | 13K02 - 3 Phase : 200.00 kVA : POLEMNT |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 365 | 16 | 24504 | 5840 | 0.23833 | 0.00065295 | 200 | 73000 | 2010/2011 | October-2010 | 10 | 2010
24321 | - Oruatua Ave | 2010-10-28 11:00 | 2010-10-28 | 2010-10-28 11:45 | Calculated | 09T05 | 09T05 - 3 Phase : 250.00 kVA : POLEMNT |  | 417SEG5927RET | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 44 | 24504 | 1980 | 0.0808 | 0.0017956 | 250 | 11249 | 2010/2011 | October-2010 | 10 | 2010
24322 | Change Poles & Xarms - Pureora Feeder | 2010-10-28 11:53 | 2010-10-28 | 2010-10-28 15:07 | Calculated | 407 | 407 - Fused Link 407 |  | 119SEG407 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 194 | 11 | 24504 | 2134 | 0.08709 | 0.00044891 | 165 | 32009 | 2010/2011 | October-2010 | 10 | 2010
24323 | Changing Poles & Xarms - Maihiihi Feeder | 2010-10-29 09:08 | 2010-10-29 | 2010-10-29 15:20 | Calculated | 707 | 707 - Air Break Switch 707 |  | 111SEG707-399 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 330 | 25 | 24504 | 8250 | 0.33668 | 0.0010202 | 155 | 51149 | 2010/2011 | October-2010 | 10 | 2010
24324 | Raise Taps - Aotearoa Road | 2010-10-29 10:06 | 2010-10-29 | 2010-10-29 10:57 | Calculated | T3170 | T3170 - 3 Phase : 50.00 kVA : POLEMNT |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 1 | 24504 | 51 | 0.00208 | 4.081e-05 | 50 | 2550 | 2010/2011 | October-2010 | 10 | 2010
24325 | Fell Tree Clear of Line - Borough Sub | 2010-10-29 10:19 | 2010-10-29 | 2010-10-29 10:30 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24504 |  | 0 | 0 |  |  | 2010/2011 | October-2010 | 10 | 2010
25463 | Change Poles & X/arms, Run 3rd Phase & Erect New 3 Phase Tx | 2010-10-29 10:23 | 2010-10-29 | 2010-10-29 16:13 | Calculated | TF3336 | TF3336 - Transformer Fuse TF3336 |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 349 | 3 | 24504 | 1047 | 0.04273 | 0.00012243 | 35 | 12222 | 2010/2011 | October-2010 | 10 | 2010
24326 | Unknown - Mangawhitiwhiti Road | 2010-10-29 11:05 | 2010-10-29 | 2010-10-29 12:19 | Calculated | 11S13 | 11S13 - 1 Phase : 15.00 kVA : POLEMNT |  | 427SEG5524 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 2 | 24504 | 148 | 0.00604 | 8.1619e-05 | 15 | 1110 | 2010/2011 | October-2010 | 10 | 2010
24328 | Vehicle vs LV - Tutunui Street | 2010-10-29 13:27 | 2010-10-29 | 2010-10-29 15:45 | Calculated | T351 | T351 - 3 Phase : 200.00 kVA : GNDPAD |  | 112SEG307-314 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 64 | 24504 | 8832 | 0.36043 | 0.0026118 | 200 | 27600 | 2010/2011 | October-2010 | 10 | 2010
24329 | Isolation for Safety - Timber Mill | 2010-10-29 14:55 | 2010-10-29 | 2010-10-29 17:45 | Calculated | 21O02 | 21O02 - 3 Phase : 1000.00 kVA : POLEMNT |  | 428SEG6638 | Tangiwai 416-05 RETIRED | Remote Rural F | Tangiwai | Direct from Ohakune Supply |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 170 | 1 | 24504 | 170 | 0.00694 | 4.081e-05 | 1000 | 170000 | 2010/2011 | October-2010 | 10 | 2010
24331 | Magpie - Kaitieke Road | 2010-10-30 17:20 | 2010-10-30 | 2010-10-30 18:30 | Calculated | 13J04 | 13J04 - 1 Phase : 7.50 kVA : POLEMNT |  | 410SEG5919 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 1 | 24504 | 70 | 0.00286 | 4.081e-05 | 7.5 | 525 | 2010/2011 | October-2010 | 10 | 2010
24332 | Possum - Mangawhero Road | 2010-10-31 07:13 | 2010-10-31 | 2010-10-31 08:12 | Calculated | T201 | T201 - 3ph 25kVA POLEMNT |  | 109SEG302 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 5 | 24504 | 295 | 0.01204 | 0.00020405 | 25 | 1475 | 2010/2011 | October-2010 | 10 | 2010
24333 | Unknown - Ahuroa Road | 2010-11-01 06:37 | 2010-11-01 | 2010-11-01 08:03 | Calculated | T597 | T597 - 1 Phase : 10.00 kVA : POLEMNT |  | 106SEG192-246 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 3 | 24487 | 258 | 0.01054 | 0.00012251 | 10 | 859 | 2010/2011 | November-2010 | 11 | 2010
24334 | Unlnown - Otukou | 2010-11-01 08:00 | 2010-11-01 | 2010-11-01 09:45 | Calculated | 5835 | 5835 - Fused Link 5835 |  | 418SEG5835-6544 | 512-01 Otukou | Rural D | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 19 | 24487 | 1995 | 0.08147 | 0.00077592 | 225 | 23624 | 2010/2011 | November-2010 | 11 | 2010
24336 | Raise Tap - Bonners Road | 2010-11-03 10:22 | 2010-11-03 | 2010-11-03 11:38 | Calculated | T374 | T374 - 3 Phase : 15.00 kVA : POLEMNT |  | 110SEG189 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 1 | 24487 | 76 | 0.0031 | 4.0838e-05 | 50 | 3800 | 2010/2011 | November-2010 | 11 | 2010
24337 | Unknown - Waitomo Valley Road | 2010-11-03 15:00 | 2010-11-03 | 2010-11-03 16:21 | Calculated | T703 | T703 - 3 Phase : 3.00 kVA : POLEMNT |  | 112SEG545-326 | Otorohanga 112-05 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 1 | 24487 | 81 | 0.00331 | 4.0838e-05 | 3 | 243 | 2010/2011 | November-2010 | 11 | 2010
24340 | Straighten/Tidy Poles & Xarms - Pureora Feeder | 2010-11-04 10:36 | 2010-11-04 | 2010-11-04 15:26 | Calculated | 407 | 407 - Fused Link 407 |  | 119SEG407 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 290 | 11 | 24487 | 1454 | 0.05938 | 0.00044922 | 165 | 19639 | 2010/2011 | November-2010 | 11 | 2010
24341 | Lower Tap - Western Bay Road | 2010-11-04 14:44 | 2010-11-04 | 2010-11-04 15:46 | Calculated | T1353 | T1353 - 1 Phase : 15.00 kVA : POLEMNT |  | 124SEG437-1764 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 4 | 24487 | 248 | 0.01013 | 0.00016335 | 15 | 930 | 2010/2011 | November-2010 | 11 | 2010
24342 | Urgent Replacement of Pole - Rangitoto Feeder | 2010-11-05 10:02 | 2010-11-05 | 2010-11-05 14:11 | Calculated | 659 | 659 - Air Break Switch 659 |  | 106SEG659-194 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 249 | 32 | 24487 | 7968 | 0.3254 | 0.0013068 | 250.5 | 62374 | 2010/2011 | November-2010 | 11 | 2010
24343 | Pull Up Slack Span - Ngapuke Road | 2010-11-05 10:14 | 2010-11-05 | 2010-11-05 11:53 | Calculated | 08L09 | 08L09 - 1 Phase : 25.00 kVA : POLEMNT |  | 408SEG5233-5514 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 7 | 24487 | 693 | 0.0283 | 0.00028587 | 25 | 2474 | 2010/2011 | November-2010 | 11 | 2010
24344 | Fuse Pulled Apart - Turakina Valley Road | 2010-11-05 12:05 | 2010-11-05 | 2010-11-05 13:58 | Calculated | 22O06 | 22O06 - 1 Phase : 15.00 kVA : POLEMNT |  | 416SEG5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 1 | 24487 | 113 | 0.00461 | 4.0838e-05 | 15 | 1695 | 2010/2011 | November-2010 | 11 | 2010
24345 | Line Down - Lower Retaruke Road | 2010-11-06 05:00 | 2010-11-06 | 2010-11-06 13:11 | Calculated | 5396 | 5396 - Sectionaliser 5396 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 491 | 45 | 24487 | 21675 | 0.88516 | 0.0018377 | 183.75 | 88541 | 2010/2011 | November-2010 | 11 | 2010
24347 | Possum - Rimu Road | 2010-11-06 07:30 | 2010-11-06 | 2010-11-06 11:17 | Calculated | 06E06 | 06E06 - 1 Phase : 15.00 kVA : POLEMNT |  | 412SEG5564 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 227 | 2 | 24487 | 454 | 0.01854 | 8.1676e-05 | 15 | 3405 | 2010/2011 | November-2010 | 11 | 2010
25465 | Replace Link 6150 - Karangahape Rd Pole 38/34 | 2010-11-07 07:16 | 2010-11-07 | 2010-11-07 09:49 | Calculated | 6150 | 6150 - Fused Link 6150 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 153 | 5 | 24487 | 766 | 0.03128 | 0.00020419 | 30 | 4601 | 2010/2011 | November-2010 | 11 | 2010
24349 | Possum - Marotiri Road | 2010-11-07 09:30 | 2010-11-07 | 2010-11-07 10:49 | Calculated | T981 | T981 - 1 Phase : 15.00 kVA : POLEMNT |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 2 | 24487 | 158 | 0.00645 | 8.1676e-05 | 15 | 1185 | 2010/2011 | November-2010 | 11 | 2010
24350 | Shifting Poles - Whakamaru Feeder | 2010-11-08 10:16 | 2010-11-08 | 2010-11-08 15:57 | Calculated | 481 | 481 - Air Break Switch 481 |  | 120SEG483-482 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 341 | 11 | 24487 | 3751 | 0.15318 | 0.00044922 | 60 | 20460 | 2010/2011 | November-2010 | 11 | 2010
24351 | Truck vs LV - Troopers Road | 2010-11-08 11:46 | 2010-11-08 | 2010-11-08 15:54 | Calculated | T1752 | T1752 - 1 Phase : 15.00 kVA : POLEMNT |  | 117SEG1318-770 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 248 | 6 | 24487 | 1488 | 0.06077 | 0.00024503 | 15 | 3720 | 2010/2011 | November-2010 | 11 | 2010
24355 | Shifting Poles - Whakamaru Feeder | 2010-11-09 09:34 | 2010-11-09 | 2010-11-09 16:06 | Calculated | 481 | 481 - Air Break Switch 481 |  | 120SEG483-482 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 378 | 11 | 24487 | 4158 | 0.1698 | 0.00044922 | 60 | 22680 | 2010/2011 | November-2010 | 11 | 2010
25467 | Replace I/R 4131130 - bENT @ 45 Degrees | 2010-11-09 09:38 | 2010-11-09 | 2010-11-09 15:17 | Calculated | 5455 | 5455 - Recloser with Bypass & Links 5455 |  | 413SEG5454-5455 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 36 | 24487 | 3349 | 0.13677 | 0.0014702 | 235.5 | 20779 | 2010/2011 | November-2010 | 11 | 2010
24358 | Unknown - Karangahape Road | 2010-11-11 05:40 | 2010-11-11 | 2010-11-11 07:47 | Calculated | 6150 | 6150 - Fused Link 6150 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 5 | 24487 | 635 | 0.02593 | 0.00020419 | 30 | 3810 | 2010/2011 | November-2010 | 11 | 2010
24359 | Unknown - Karangahape Road | 2010-11-11 05:40 | 2010-11-11 | 2010-11-11 08:42 | Calculated | 07R19 | 07R19 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 182 | 1 | 24487 | 182 | 0.00743 | 4.0838e-05 | 15 | 2730 | 2010/2011 | November-2010 | 11 | 2010
24360 | SWER Backfeed - Kiritihere | 2010-11-11 08:33 | 2010-11-11 | 2010-11-11 08:35 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 2 | 16 | 24487 | 32 | 0.00131 | 0.00065341 | 140 | 280 | 2010/2011 | November-2010 | 11 | 2010
24361 | Changing Poles & Xarms & Running New Conductor - Coast Feeder | 2010-11-11 09:36 | 2010-11-11 | 2010-11-11 15:21 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 345 | 15 | 24487 | 5175 | 0.21134 | 0.00061257 | 85 | 29325 | 2010/2011 | November-2010 | 11 | 2010
24362 | Run New Conductor After Fault - Western Feeder | 2010-11-11 10:08 | 2010-11-11 | 2010-11-11 15:05 | Calculated | 5603 | 5603 - Fused Link 5603 |  | 403SEG5603-5883 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 246 | 20 | 24487 | 4154 | 0.16964 | 0.00081676 | 120 | 25650 | 2010/2011 | November-2010 | 11 | 2010
24364 | Changing Poles & Xarms & Running New Conductor - Coast Feeder | 2010-11-12 08:53 | 2010-11-12 | 2010-11-12 14:54 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 361 | 15 | 24487 | 5415 | 0.22114 | 0.00061257 | 85 | 30685 | 2010/2011 | November-2010 | 11 | 2010
24365 | SWER Backfeed - Kiritihere | 2010-11-12 15:34 | 2010-11-12 | 2010-11-12 15:40 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 6 | 16 | 24487 | 96 | 0.00392 | 0.00065341 | 140 | 840 | 2010/2011 | November-2010 | 11 | 2010
24367 | Unknown - Makino Road | 2010-11-12 16:40 | 2010-11-12 | 2010-11-12 17:45 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 28 | 24487 | 1820 | 0.07433 | 0.0011435 | 183.5 | 11927 | 2010/2011 | November-2010 | 11 | 2010
24368 | Bolt Out of Xarm - Waihora Road | 2010-11-14 15:19 | 2010-11-14 | 2010-11-14 16:23 | Calculated | 436 | 436 - Solid Link 436 |  | 123SEG436 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 4 | 24487 | 256 | 0.01045 | 0.00016335 | 65 | 4160 | 2010/2011 | November-2010 | 11 | 2010
24370 | Magpie - Mangakahu Road | 2010-11-16 08:30 | 2010-11-16 | 2010-11-16 10:13 | Calculated | 04J10 | 04J10 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5669-5342 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 3 | 24487 | 309 | 0.01262 | 0.00012251 | 15 | 1545 | 2010/2011 | November-2010 | 11 | 2010
24371 | Urgent Replacement of Pole in Maize | 2010-11-16 08:54 | 2010-11-16 | 2010-11-16 15:10 | Calculated | T689 | T689 - 1 Phase : 25.00 kVA : POLEMNT |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 376 | 1 | 24487 | 376 | 0.01536 | 4.0838e-05 | 25 | 9400 | 2010/2011 | November-2010 | 11 | 2010
24373 | Unknown - Mokau River Road | 2010-11-16 11:15 | 2010-11-16 | 2010-11-16 12:48 | Calculated | 1621 | 1621 - Fused Link 1621 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 20 | 24487 | 1860 | 0.07596 | 0.00081676 | 145 | 13484 | 2010/2011 | November-2010 | 11 | 2010
24372 | New Tx Structure | 2010-11-16 12:02 | 2010-11-16 | 2010-11-16 14:24 | Calculated | 379 | 379 - Air Break Switch 379 |  | 122SEG379 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 142 | 10 | 24487 | 1420 | 0.05799 | 0.00040838 | 60 | 8520 | 2010/2011 | November-2010 | 11 | 2010
24375 | Unknown - Wairere | 2010-11-17 06:34 | 2010-11-17 | 2010-11-17 06:43 | Calculated | 793 | 793 - Circuit Breaker 793 |  | No Segment | 207-01 Wairere Falls | Rural D | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24487 |  | 0 | 0 |  |  | 2010/2011 | November-2010 | 11 | 2010
24376 | Upgrade Tx Structure - Rangitoto Road | 2010-11-17 09:33 | 2010-11-17 | 2010-11-17 14:27 | Calculated | T104 | T104 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 4 | 24487 | 1176 | 0.04803 | 0.00016335 | 15 | 4410 | 2010/2011 | November-2010 | 11 | 2010
24377 | Suspect Fault @ T4230 - Omori Road | 2010-11-17 13:00 | 2010-11-17 | 2010-11-17 17:39 | Calculated | 6018 | 6018 - Solid Link 6018 |  | 406SEG6018-5009 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 279 | 1310 | 24487 | 5041 | 0.20586 | 0.053498 | 6623.4261 | 159946 | 2010/2011 | November-2010 | 11 | 2010
24379 | Fuse Pulled Apart - Rangataua Road | 2010-11-17 17:35 | 2010-11-17 | 2010-11-17 17:56 | Calculated | 20L09 | 20L09 - 3 Phase : 30.00 kVA : POLEMNT |  | 416SEG5677-5681 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 3 | 24487 | 63 | 0.00257 | 0.00012251 | 30 | 630 | 2010/2011 | November-2010 | 11 | 2010
24384 | Install Channel Steel to Support HV Cable Under Bridge | 2010-11-19 09:21 | 2010-11-19 | 2010-11-19 15:23 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 362 | 2 | 24487 | 724 | 0.02957 | 8.1676e-05 | 0 | 0 | 2010/2011 | November-2010 | 11 | 2010
24385 | Unknown - Ohakune Sub | 2010-11-19 09:46 | 2010-11-19 | 2010-11-19 09:58 | Calculated | 5003 | 5003 - Circuit Breaker 5003 |  | No Segment | 517-01 Transpower Ohakune | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 429 | 24487 | 5148 | 0.21023 | 0.01752 | 2808 | 33695 | 2010/2011 | November-2010 | 11 | 2010
24386 | Magpie - SH4 | 2010-11-19 13:00 | 2010-11-19 | 2010-11-19 13:50 | Calculated | 05I06 | 05I06 - 1 Phase : 3.00 kVA : POLEMNT |  | 402SEG5446-5797 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FOOB | Other Birds | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 1 | 24487 | 50 | 0.00204 | 4.0838e-05 | 3 | 150 | 2010/2011 | November-2010 | 11 | 2010
24387 | Ducks - SH4 | 2010-11-19 15:43 | 2010-11-19 | 2010-11-19 16:19 | Calculated | 5690 | 5690 - Fused Link 5690 |  | 416SEG5690 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 8 | 24487 | 288 | 0.01176 | 0.0003267 | 50 | 1800 | 2010/2011 | November-2010 | 11 | 2010
24388 | Clash - Pukemapou Road | 2010-11-20 05:50 | 2010-11-20 | 2010-11-20 07:49 | Calculated | 364 | 364 - Fused Link 364 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 31 | 24487 | 3689 | 0.15065 | 0.001266 | 260 | 30939 | 2010/2011 | November-2010 | 11 | 2010
24389 | Unknown - Stewart Road | 2010-11-20 07:10 | 2010-11-20 | 2010-11-20 09:44 | Calculated | 5360 | 5360 - Sectionaliser with Bypass & Links 5360 |  | 402SEG5360-5267 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 14 | 24487 | 2156 | 0.08805 | 0.00057173 | 90 | 13860 | 2010/2011 | November-2010 | 11 | 2010
24390 | Lightning vs Insulator - Manunui Sub | 2010-11-21 00:36 | 2010-11-21 | 2010-11-21 11:40 | Calculated | 6143 | 6143 - Circuit Breaker Manunui 33kV 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQS | Lightning Damage to Switch-gear | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 4 | 24487 | 44 | 0.0018 | 0.00016335 | 450 | 4950 | 2010/2011 | November-2010 | 11 | 2010
24391 | Car vs Tx - Waiotaka Road | 2010-11-21 12:23 | 2010-11-21 | 2010-11-21 13:09 | Calculated | T4040 | T4040 - 3 Phase : 15.00 kVA : POLEMNT |  | 424SEG5010-T4172 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 1 | 24487 | 46 | 0.00188 | 4.0838e-05 | 15 | 690 | 2010/2011 | November-2010 | 11 | 2010
24392 | Tx Change - SH1 | 2010-11-22 10:06 | 2010-11-22 | 2010-11-22 10:53 | Calculated | 09U05 | 09U05 - 3 Phase : 100.00 kVA : POLEMNT |  | 417SEG5297-5245 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 47 | 53 | 24487 | 2491 | 0.10173 | 0.0021644 | 100 | 4699 | 2010/2011 | November-2010 | 11 | 2010
24393 | Re-Work - Mokau Feeder | 2010-11-22 10:31 | 2010-11-22 | 2010-11-22 14:03 | Calculated | 1616 | 1616 - Sectionaliser with Bypass & Links 1616 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 212 | 15 | 24487 | 3180 | 0.12986 | 0.00061257 | 120 | 25440 | 2010/2011 | November-2010 | 11 | 2010
24394 | Upgrade Tx - Whakamaru Feeder | 2010-11-22 11:04 | 2010-11-22 | 2010-11-22 13:37 | Calculated | 530 | 530 - Air Break Switch 530 |  | 120SEG530RET | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 1 | 24487 | 153 | 0.00625 | 4.0838e-05 | 100 | 15300 | 2010/2011 | November-2010 | 11 | 2010
24396 | Jumper vs Stay @ Link 537 - Tihoi Road | 2010-11-22 14:51 | 2010-11-22 | 2010-11-22 15:00 | Calculated | 440 | 440 - Recloser with Outgoing Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 50 | 24487 | 450 | 0.01838 | 0.0020419 | 370.5 | 3334 | 2010/2011 | November-2010 | 11 | 2010
24399 | Tree Through Line - Tahaia Bush Road | 2010-11-22 15:29 | 2010-11-22 | 2010-11-22 17:00 | Calculated | 587 | 587 - Fused Link 587 |  | 109SEG587-2218 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 13 | 24487 | 1183 | 0.04831 | 0.00053089 | 100 | 9099 | 2010/2011 | November-2010 | 11 | 2010
24397 | Jumper vs Stay @ Link 537 - Tihoi Road | 2010-11-22 15:55 | 2010-11-22 | 2010-11-22 16:20 | Calculated | 440 | 440 - Recloser with Outgoing Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 50 | 24487 | 1250 | 0.05105 | 0.0020419 | 370.5 | 9262 | 2010/2011 | November-2010 | 11 | 2010
24398 | Jumper vs Stay @ Link 537 - Tihoi Road | 2010-11-22 16:56 | 2010-11-22 | 2010-11-22 17:10 | Calculated | 440 | 440 - Recloser with Outgoing Link 440 |  | 124SEG440-5581 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 50 | 24487 | 700 | 0.02859 | 0.0020419 | 370.5 | 5186 | 2010/2011 | November-2010 | 11 | 2010
24400 | Replace Rusty Tx - Waihaha Feeder | 2010-11-23 10:04 | 2010-11-23 | 2010-11-23 12:05 | Calculated | 5924 | 5924 - Earth Working Link 5924 |  | 426SEG5924 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 3 | 24487 | 363 | 0.01482 | 0.00012251 | 25 | 3025 | 2010/2011 | November-2010 | 11 | 2010
24403 | Broken Binder - Walker Road | 2010-11-23 17:44 | 2010-11-23 | 2010-11-23 17:58 | Calculated | 659 | 659 - Air Break Switch 659 |  | 106SEG659-194 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 32 | 24487 | 448 | 0.0183 | 0.0013068 | 250.5 | 3506 | 2010/2011 | November-2010 | 11 | 2010
24405 | Unknown - Whareroa Sub | 2010-11-24 06:55 | 2010-11-24 | 2010-11-24 09:38 | Calculated | 5619 | 5619 - Fused Link 5619 |  | 426SEGT07Q14-5268 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 81 | 24487 | 13203 | 0.53918 | 0.0033079 | 527.5 | 85982 | 2010/2011 | November-2010 | 11 | 2010
24404 | Changing Poles & Xarms - Rangitoto Feeder | 2010-11-24 09:32 | 2010-11-24 | 2010-11-24 14:09 | Calculated | 284 | 284 - Fused Link 284 |  | 106SEG284 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 277 | 4 | 24487 | 1108 | 0.04525 | 0.00016335 | 25 | 6925 | 2010/2011 | November-2010 | 11 | 2010
24406 | Changing Poles & Xarms - Rangitoto Feeder | 2010-11-25 09:30 | 2010-11-25 | 2010-11-25 14:35 | Calculated | 284 | 284 - Fused Link 284 |  | 106SEG284 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 4 | 24487 | 1220 | 0.04982 | 0.00016335 | 25 | 7625 | 2010/2011 | November-2010 | 11 | 2010
24408 | Replace Structures - Turoa Feeder | 2010-11-26 09:03 | 2010-11-26 | 2010-11-26 15:57 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 414 | 2 | 24487 | 828 | 0.03381 | 8.1676e-05 | 0 | 0 | 2010/2011 | November-2010 | 11 | 2010
24409 | Upgrade Tx - Rangitoto Road | 2010-11-26 09:30 | 2010-11-26 | 2010-11-26 14:23 | Calculated | T104 | T104 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG199-247 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 293 | 4 | 24487 | 1172 | 0.04786 | 0.00016335 | 15 | 4395 | 2010/2011 | November-2010 | 11 | 2010
24410 | Replace Poles - Turoa Feeder | 2010-11-26 09:35 | 2010-11-26 | 2010-11-26 13:32 | Calculated | 5397 | 5397 - Fused Link 5397 |  | THUVVK | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 237 | 9 | 24487 | 2133 | 0.08711 | 0.00036754 | 70 | 16590 | 2010/2011 | November-2010 | 11 | 2010
24412 | Suspect Fault - Hingarae Road | 2010-11-26 19:28 | 2010-11-26 | 2010-11-26 19:30 | Calculated | 5537 | 5537 - Fused Link 5537 |  | 124SEG5537-5324 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 31 | 24487 | 62 | 0.00253 | 0.001266 | 217.5 | 434 | 2010/2011 | November-2010 | 11 | 2010
24413 | Unknown - Te Mahoe Road | 2010-11-26 19:30 | 2010-11-26 | 2010-11-26 22:15 | Calculated | T2158 | T2158 - 1 Phase : 10.00 kVA : POLEMNT |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 2 | 24487 | 330 | 0.01348 | 8.1676e-05 | 10 | 1650 | 2010/2011 | November-2010 | 11 | 2010
24414 | Unknown - Tihoi Road | 2010-11-26 22:30 | 2010-11-26 | 2010-11-27 00:30 | Calculated | T891 | T891 - 3 Phase : 50.00 kVA : POLEMNT |  | 124SEG457 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 6 | 24487 | 720 | 0.0294 | 0.00024503 | 50 | 5999 | 2010/2011 | November-2010 | 11 | 2010
24415 | Unknown - Tihoi Road | 2010-11-27 06:00 | 2010-11-27 | 2010-11-27 08:00 | Calculated | 457 | 457 - Air Break Switch 457 |  | 124SEG457 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 7 | 24487 | 840 | 0.0343 | 0.00028587 | 100 | 11999 | 2010/2011 | November-2010 | 11 | 2010
24417 | Unknown - Te Puke Road | 2010-11-28 11:00 | 2010-11-28 | 2010-11-28 12:32 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 24487 | 92 | 0.00376 | 4.0838e-05 | 5 | 460 | 2010/2011 | November-2010 | 11 | 2010
24418 | Upgrade Tx 01A44 - Hakiaha Feeder | 2010-11-28 22:06 | 2010-11-28 | 2010-11-29 05:30 | Calculated | 5.23 | 5.23 - Ring Main Unit 5.23 |  | No Segment | No Asset Group | Remote Rural F | Hakiaha | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 444 | 26 | 24487 | 11544 | 0.47143 | 0.0010618 | 300 | 133199 | 2010/2011 | November-2010 | 11 | 2010
24419 | Repair Broken Tx Earth - Hangatiki East Road | 2010-11-29 09:17 | 2010-11-29 | 2010-11-29 10:29 | Calculated | T689 | T689 - 1 Phase : 25.00 kVA : POLEMNT |  | 108SEG182-505 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 72 | 1 | 24487 | 72 | 0.00294 | 4.0838e-05 | 25 | 1800 | 2010/2011 | November-2010 | 11 | 2010
24420 | SWER Backfeed - Waimiha Township | 2010-11-29 10:08 | 2010-11-29 | 2010-11-29 10:23 | Calculated | 1726 | 1726 - Fused Link 1726 |  | 103SEG1726-1733 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 15 | 6 | 24487 | 90 | 0.00368 | 0.00024503 | 30 | 450 | 2010/2011 | November-2010 | 11 | 2010
24421 | Replace Swinging Insulator - Mokauiti Feeder | 2010-11-29 10:44 | 2010-11-29 | 2010-11-29 12:21 | Calculated | 1725 | 1725 - Fused Link 1725 |  | 115SEG1725-2177 | Mokauiti 115-06 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 97 | 6 | 24487 | 582 | 0.02377 | 0.00024503 | 75 | 7275 | 2010/2011 | November-2010 | 11 | 2010
24422 | Fuse Pulled Apart - Foyle Street | 2010-11-29 11:15 | 2010-11-29 | 2010-11-29 12:50 | Calculated | 20L35 | 20L35 - 3ph 300kVA GMT |  | 103SEG453- Temp Link between Pole 544 & Pole 538 | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 49 | 24487 | 4655 | 0.1901 | 0.0020011 | 300 | 28499 | 2010/2011 | November-2010 | 11 | 2010
24423 | Rotten Xarm - Hingarae Road | 2010-11-29 17:20 | 2010-11-29 | 2010-11-29 19:15 | Calculated | 5537 | 5537 - Fused Link 5537 |  | 124SEG5537-5324 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 31 | 24487 | 3565 | 0.14559 | 0.001266 | 217.5 | 25012 | 2010/2011 | November-2010 | 11 | 2010
24426 | Lightning - Tokirima Road | 2010-11-30 12:53 | 2010-11-30 | 2010-11-30 14:49 | Calculated | 09E16 | 09E16 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5569-5437 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 1 | 24487 | 116 | 0.00474 | 4.0838e-05 | 15 | 1740 | 2010/2011 | November-2010 | 11 | 2010
24428 | Replace Pole & Redo Connections - Wharepapa Road | 2010-12-01 10:06 | 2010-12-01 | 2010-12-01 14:13 | Calculated | 376 | 376 - Air Break Switch 376 |  | 122SEG376-380 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 225 | 25 | 24487 | 5625 | 0.22971 | 0.0010209 | 250 | 56250 | 2010/2011 | December-2010 | 12 | 2010
24433 | Unknown - Mahoe Road | 2010-12-01 21:23 | 2010-12-01 | 2010-12-02 12:43 | Calculated | 109 | 109 - Recloser with bypass 109 |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 920 | 102 | 24487 | 21108 | 0.86201 | 0.0041655 | 787 | 145689 | 2010/2011 | December-2010 | 12 | 2010
24434 | Line Down Through Forest - Kopaki Road | 2010-12-01 22:22 | 2010-12-01 | 2010-12-02 12:04 | Calculated | 669 | 669 - Recloser with Bypass & Links 669 |  | 103SEG731-REG14 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 812 | 358 | 24487 | 34617 | 1.4137 | 0.01462 | 2652.138 | 189488 | 2010/2011 | December-2010 | 12 | 2010
24439 | Line Down - Kirikau Valley Road | 2010-12-02 04:25 | 2010-12-02 | 2010-12-02 07:50 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 205 | 15 | 24487 | 3075 | 0.12558 | 0.00061257 | 98 | 20089 | 2010/2011 | December-2010 | 12 | 2010
24440 | Truck vs Line - Scott Road | 2010-12-02 11:46 | 2010-12-02 | 2010-12-02 16:17 | Calculated | 407 | 407 - Fused Link 407 |  | 119SEG407 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 271 | 11 | 24487 | 2981 | 0.12174 | 0.00044922 | 165 | 44714 | 2010/2011 | December-2010 | 12 | 2010
24441 | Lower Tap - Whangamata Road | 2010-12-03 09:24 | 2010-12-03 | 2010-12-03 09:51 | Calculated | T903 | T903 - 1 Phase : 5.00 kVA : POLEMNT |  | 124SEG542-786 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 2 | 24487 | 54 | 0.00221 | 8.1676e-05 | 5 | 135 | 2010/2011 | December-2010 | 12 | 2010
24443 | Replace Structure - Happy Valley Road | 2010-12-03 09:43 | 2010-12-03 | 2010-12-03 15:38 | Calculated | T269 | T269 - 3ph 25kVA polemnt |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 355 | 2 | 24487 | 710 | 0.02899 | 8.1676e-05 | 25 | 8875 | 2010/2011 | December-2010 | 12 | 2010
24444 | Unknown - Lower Burns Street | 2010-12-04 06:29 | 2010-12-04 | 2010-12-04 07:12 | Calculated | 5397 | 5397 - Fused Link 5397 |  | THUVVK | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 9 | 24487 | 387 | 0.0158 | 0.00036754 | 70 | 3010 | 2010/2011 | December-2010 | 12 | 2010
24445 | Clash - Harpers Ave | 2010-12-05 21:07 | 2010-12-05 | 2010-12-05 21:55 | Calculated | 663 | 663 - Fused Link 663 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 6 | 24487 | 288 | 0.01176 | 0.00024503 | 90 | 4320 | 2010/2011 | December-2010 | 12 | 2010
24448 | LV Neutral Copper Theft - Whakamaru Road | 2010-12-06 04:40 | 2010-12-06 | 2010-12-06 06:52 | Calculated | T1066 | T1066 - 1 Phase : 30.00 kVA : POLEMNT |  | 120SEG497-REG31 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 3 | 24487 | 396 | 0.01617 | 0.00012251 | 30 | 3960 | 2010/2011 | December-2010 | 12 | 2010
24446 | Replace Tx Structure - Paewhenua Road | 2010-12-06 09:41 | 2010-12-06 | 2010-12-06 14:37 | Calculated | T452 | T452 - 3ph 15kVA polemnt |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 296 | 3 | 24487 | 888 | 0.03626 | 0.00012251 | 15 | 4440 | 2010/2011 | December-2010 | 12 | 2010
24447 | Line Down - Mangaotaki Road | 2010-12-06 10:13 | 2010-12-06 | 2010-12-06 12:14 | Calculated | 1516 | 1516 - Air Break Switch 1516 |  | 113SEG1516-1548 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 135 | 24487 | 16335 | 0.66709 | 0.0055131 | 858.5 | 103878 | 2010/2011 | December-2010 | 12 | 2010
24449 | Unknown - Oio No 1 Road | 2010-12-07 09:05 | 2010-12-07 | 2010-12-07 12:37 | Calculated | 12J04 | 12J04 - 1 Phase : 7.50 kVA : POLEMNT |  | 409SEG5748-5743 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 212 | 2 | 24487 | 424 | 0.01732 | 8.1676e-05 | 7.5 | 1590 | 2010/2011 | December-2010 | 12 | 2010
25470 | Change Tx11S15 to GMT & Replace Tx11S20 | 2010-12-07 09:13 | 2010-12-07 | 2010-12-07 16:17 | Calculated | 6016 | 6016 - Fused Link: 6016 |  | 424SEG6650-6651 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 424 | 138 | 24487 | 58408 | 2.3853 | 0.0056356 | 604.3478 | 255784 | 2010/2011 | December-2010 | 12 | 2010
24451 | Faulty Tx - Tutu Road | 2010-12-07 10:38 | 2010-12-07 | 2010-12-07 12:14 | Calculated | T145 | T145 - 3ph 15kVA POL |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 1 | 24487 | 96 | 0.00392 | 4.0838e-05 | 15 | 1440 | 2010/2011 | December-2010 | 12 | 2010
24453 | Jumper Off - SH3 | 2010-12-07 16:07 | 2010-12-07 | 2010-12-07 16:49 | Calculated | T2140 | T2140 - 3ph 100kVA GNDPAD |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 24 | 24487 | 1008 | 0.04116 | 0.00098011 | 100 | 4199 | 2010/2011 | December-2010 | 12 | 2010
24454 | Tree Felling with Digger - Kie Kie Road | 2010-12-08 09:04 | 2010-12-08 | 2010-12-08 15:15 | Calculated | 1101 | 1101 - Fused Link 1101 |  | 114SEG1101 | Aria 114-01 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 371 | 9 | 24487 | 3339 | 0.13636 | 0.00036754 | 67.5 | 25042 | 2010/2011 | December-2010 | 12 | 2010
24455 | Change Poles & Xarms - Maihiihi Road | 2010-12-08 10:04 | 2010-12-08 | 2010-12-08 14:13 | Calculated | 1148 | 1148 - Fused Link 1148 |  | 111SEG148 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 249 | 6 | 24487 | 1494 | 0.06101 | 0.00024503 | 80 | 19919 | 2010/2011 | December-2010 | 12 | 2010
24456 | Faulty Tx - Mangarino Road | 2010-12-08 13:00 | 2010-12-08 | 2010-12-08 16:08 | Calculated | T2791 | T2791 - 3ph 15kVA POLEMNT |  | 106SEG224-361 | Rangitoto 106-07 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 188 | 1 | 24487 | 188 | 0.00768 | 4.0838e-05 | 15 | 2820 | 2010/2011 | December-2010 | 12 | 2010
24458 | Unknown - Huia Street | 2010-12-09 07:00 | 2010-12-09 | 2010-12-09 08:33 | Calculated | 1.36 | 1.36 - Fused Link 1.36 |  | 404SEGF1.36 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 42 | 24487 | 3906 | 0.15951 | 0.0017152 | 100 | 9299 | 2010/2011 | December-2010 | 12 | 2010
24459 | Fuse Pulled Apart - SH49 | 2010-12-09 07:30 | 2010-12-09 | 2010-12-09 08:45 | Calculated | 21M07 | 21M07 - 1 Phase : 15.00 kVA : POLEMNT |  | 416SEG5677-5681 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 1 | 24487 | 75 | 0.00306 | 4.0838e-05 | 15 | 1125 | 2010/2011 | December-2010 | 12 | 2010
24460 | Line Renewal - National Park Feeder | 2010-12-09 08:17 | 2010-12-09 | 2010-12-09 16:11 | Calculated | 16L02 | 16L02 - 3 Phase : 200.00 kVA : POLEMNT |  | 411SEG5775-5329 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 453 | 18 | 24487 | 4364 | 0.17822 | 0.00073508 | 375 | 110050 | 2010/2011 | December-2010 | 12 | 2010
24465 | Line Renewal - National Park Feeder | 2010-12-10 08:16 | 2010-12-10 | 2010-12-10 15:07 | Calculated | 16L02 | 16L02 - 3 Phase : 200.00 kVA : POLEMNT |  | 411SEG5775-5329 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 361 | 18 | 24487 | 3536 | 0.1444 | 0.00073508 | 375 | 92800 | 2010/2011 | December-2010 | 12 | 2010
24466 | Install New Links 2061 @ Pole 20 - Harpers Ave | 2010-12-10 09:32 | 2010-12-10 | 2010-12-10 11:54 | Calculated | 663 | 663 - Fused Link 663 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 142 | 6 | 24487 | 852 | 0.03479 | 0.00024503 | 90 | 12780 | 2010/2011 | December-2010 | 12 | 2010
24467 | Lower Line for Tree Felling - Tihoi Feeder | 2010-12-10 10:33 | 2010-12-10 | 2010-12-10 15:25 | Calculated | 457 | 457 - Air Break Switch 457 |  | 124SEG457 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 7 | 24487 | 2044 | 0.08347 | 0.00028587 | 100 | 29199 | 2010/2011 | December-2010 | 12 | 2010
24469 | Replace Rotten Xarms on T1131 | 2010-12-10 12:38 | 2010-12-10 | 2010-12-10 13:47 | Calculated | 193 | 193 - Air Break Switch 193 |  | 106SEG193RET | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 69 | 10 | 24487 | 690 | 0.02818 | 0.00040838 | 90 | 6210 | 2010/2011 | December-2010 | 12 | 2010
24470 | Replace Xarm on Pole 1062041 - Rangitoto Feeder | 2010-12-10 14:31 | 2010-12-10 | 2010-12-10 15:38 | Calculated | 659 | 659 - Air Break Switch 659 |  | 106SEG659-194 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 67 | 25 | 24487 | 1675 | 0.0684 | 0.0010209 | 178.8333 | 11981 | 2010/2011 | December-2010 | 12 | 2010
24472 | Jumper off @ ABS 5721 - SH49 | 2010-12-11 07:35 | 2010-12-11 | 2010-12-11 10:32 | Calculated | 5684 | 5684 - Recloser 5684 |  | 416SEG5721-5684 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 179 | 24487 | 16627 | 0.67901 | 0.00731 | 6382 | 334805 | 2010/2011 | December-2010 | 12 | 2010
24475 | Faulty L.A - Phillips Ave | 2010-12-11 10:30 | 2010-12-11 | 2010-12-11 12:30 | Calculated | T1552 | T1552 - 3 Phase : 300.00 kVA : GNDPAD |  | 112SEG300-646 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 3 | 24487 | 360 | 0.0147 | 0.00012251 | 300 | 36000 | 2010/2011 | December-2010 | 12 | 2010
24477 | Branch on Line - Hikumutu Road | 2010-12-12 06:00 | 2010-12-12 | 2010-12-12 07:30 | Calculated | 5623 | 5623 - Sectionaliser with Bypass 5623 |  | 409SEG5411-5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 15 | 24487 | 1350 | 0.05513 | 0.00061257 | 72.5 | 6525 | 2010/2011 | December-2010 | 12 | 2010
24479 | Possum - Otewa Road | 2010-12-13 05:35 | 2010-12-13 | 2010-12-13 06:15 | Calculated | T2708 | T2708 - 3ph 30kVA POLEMNT |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1 | 24487 | 40 | 0.00163 | 4.0838e-05 | 30 | 1200 | 2010/2011 | December-2010 | 12 | 2010
24480 | Branch - Ongarue Road | 2010-12-13 08:15 | 2010-12-13 | 2010-12-13 09:43 | Calculated | 04J07 | 04J07 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5657-5473 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 2 | 24487 | 176 | 0.00719 | 8.1676e-05 | 15 | 1320 | 2010/2011 | December-2010 | 12 | 2010
24478 | Unknown - SH1 | 2010-12-13 21:20 | 2010-12-13 | 2010-12-14 09:08 | Calculated | 12S04 | 12S04 - 1 Phase : 7.50 kVA : POLEMNT |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 708 | 1 | 24487 | 708 | 0.02891 | 4.0838e-05 | 7.5 | 5310 | 2010/2011 | December-2010 | 12 | 2010
24482 | Trees On Line - Manunui Sub | 2010-12-14 07:59 | 2010-12-14 | 2010-12-14 14:24 | Calculated | 6143 | 6143 - Circuit Breaker Manunui 33kV 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 4 | 24487 | 100 | 0.00408 | 0.00016335 | 450 | 11250 | 2010/2011 | December-2010 | 12 | 2010
24485 | Replace Tx Structure - Paewhenua Road | 2010-12-14 09:30 | 2010-12-14 | 2010-12-14 15:18 | Calculated | T278 | T278 - 3 Phase : 25.00 kVA : POLEMNT |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 348 | 7 | 24487 | 2436 | 0.09948 | 0.00028587 | 25 | 8699 | 2010/2011 | December-2010 | 12 | 2010
24486 | Burnt Xarm - Mangatutu Road | 2010-12-14 09:55 | 2010-12-14 | 2010-12-14 11:17 | Calculated | 625 | 625 - Air Break Switch 625 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 2 | 24487 | 164 | 0.0067 | 8.1676e-05 | 30 | 2460 | 2010/2011 | December-2010 | 12 | 2010
24488 | Unknown - Te Puke Road | 2010-12-15 19:51 | 2010-12-15 | 2010-12-15 21:37 | Calculated | 08R03 | 08R03 - 1 Phase : 5.00 kVA : POLEMNT |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 1 | 24487 | 106 | 0.00433 | 4.0838e-05 | 5 | 530 | 2010/2011 | December-2010 | 12 | 2010
24489 | Faulty SWER Iso Tx - Tapuwahine Sub | 2010-12-15 19:55 | 2010-12-15 | 2010-12-15 22:26 | Calculated | 5464 | 5464 - Fused Link 5464 |  | 421SEGT4128-5448 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 151 | 39 | 24487 | 5889 | 0.24049 | 0.0015927 | 255.5 | 38580 | 2010/2011 | December-2010 | 12 | 2010
24491 | Unknown - Tirohanga Road | 2010-12-17 17:05 | 2010-12-17 | 2010-12-17 18:43 | Calculated | T780 | T780 - 3 Phase : 50.00 kVA : POLEMNT |  | 129SEG451-787 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 5 | 24487 | 490 | 0.02001 | 0.00020419 | 50 | 4900 | 2010/2011 | December-2010 | 12 | 2010
24492 | Tree Through Line - Kawautahi Road | 2010-12-18 05:56 | 2010-12-18 | 2010-12-18 11:00 | Calculated | 5885 | 5885 - Recloser 5885 |  | 409SEG5884-5403 | Southern 409-08 | Rural D | Southern | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 304 | 24 | 24487 | 7296 | 0.29795 | 0.00098011 | 200.5 | 60952 | 2010/2011 | December-2010 | 12 | 2010
24493 | Unknown - Lower Retaruke Road | 2010-12-18 17:20 | 2010-12-18 | 2010-12-18 19:39 | Calculated | 5170 | 5170 - Sectionaliser 5170 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 21 | 24487 | 2919 | 0.11921 | 0.0008576 | 168 | 23351 | 2010/2011 | December-2010 | 12 | 2010
24494 | Lightning - Ngatarawa Road | 2010-12-18 17:45 | 2010-12-18 | 2010-12-18 19:50 | Calculated | T1892 | T1892 - 1 Phase : 15.00 kVA : POLEMNT |  | 114SEG1100 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 3 | 24487 | 375 | 0.01531 | 0.00012251 | 15 | 1875 | 2010/2011 | December-2010 | 12 | 2010
24495 | Lightning - Ruatiti Erua Road | 2010-12-18 19:20 | 2010-12-18 | 2010-12-18 21:00 | Calculated | 16H03 | 16H03 - 1 Phase : 15.00 kVA : POLEMNT |  | 410SEG5517-6750 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 4 | 24487 | 400 | 0.01634 | 0.00016335 | 15 | 1500 | 2010/2011 | December-2010 | 12 | 2010
24496 | Unknown - Te Waireka Road | 2010-12-19 06:23 | 2010-12-19 | 2010-12-19 06:31 | Calculated | 123 | 123 - Circuit Breaker 123 |  | No Segment | 203-01 Te Waireka Road | Urban A | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 1142 | 24487 | 9136 | 0.3731 | 0.046637 | 7368 | 58943 | 2010/2011 | December-2010 | 12 | 2010
24497 | Lightning Makino Road | 2010-12-19 10:02 | 2010-12-19 | 2010-12-19 14:11 | Calculated | 17I01 | 17I01 - 1 Phase : 3.00 kVA : POLEMNT |  | 410SEG5510-5511 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 249 | 1 | 24487 | 249 | 0.01017 | 4.0838e-05 | 3 | 747 | 2010/2011 | December-2010 | 12 | 2010
24498 | Lightning - Waitaanga Road | 2010-12-19 10:17 | 2010-12-19 | 2010-12-19 13:43 | Calculated | 07C01 | 07C01 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5420-5305 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 206 | 1 | 24487 | 206 | 0.00841 | 4.0838e-05 | 15 | 3090 | 2010/2011 | December-2010 | 12 | 2010
24500 | Bird - SH1 | 2010-12-19 11:45 | 2010-12-19 | 2010-12-19 14:49 | Calculated | 08V02 | 08V02 - 1 Phase : 25.00 kVA : POLEMNT |  | 417SEG5905 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 9 | 24487 | 1656 | 0.06763 | 0.00036754 | 25 | 4599 | 2010/2011 | December-2010 | 12 | 2010
24501 | Unknown - Hangatiki | 2010-12-19 12:50 | 2010-12-19 | 2010-12-19 13:01 | Calculated | 1272 | 1272 - Circuit Breaker 1272 |  | No Segment | 204-01 Hangatiki | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 310 | 24487 | 3410 | 0.13926 | 0.01266 | 2873.5 | 31608 | 2010/2011 | December-2010 | 12 | 2010
24503 | Faulty Insulator - Oururwhero Road | 2010-12-19 13:59 | 2010-12-19 | 2010-12-19 18:26 | Calculated | 123 | 123 - Circuit Breaker 123 |  | No Segment | 203-01 Te Waireka Road | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 267 | 1204 | 24487 | 48681 | 1.988 | 0.049169 | 7764.2932 | 312222 | 2010/2011 | December-2010 | 12 | 2010
24508 | Faulty Insulator - Tirohanga Road | 2010-12-19 17:38 | 2010-12-19 | 2010-12-19 21:48 | Calculated | 474 | 474 - Recloser 474 |  | 123SEG441-474 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 250 | 149 | 24487 | 8766 | 0.35799 | 0.0060849 | 2029.25 | 126114 | 2010/2011 | December-2010 | 12 | 2010
24509 | Unknown - Haurua Road | 2010-12-19 18:30 | 2010-12-19 | 2010-12-19 19:18 | Calculated | 1359 | 1359 - Fused Link 1359 |  | 112SEG1359 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 4 | 24487 | 192 | 0.00784 | 0.00016335 | 45 | 2160 | 2010/2011 | December-2010 | 12 | 2010
24510 | Unknown - Manunui | 2010-12-19 20:49 | 2010-12-19 | 2010-12-19 22:16 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 37 | 24487 | 3219 | 0.13146 | 0.001511 | 227.5 | 19792 | 2010/2011 | December-2010 | 12 | 2010
24511 | Unknown - Hohotaka Road | 2010-12-19 20:49 | 2010-12-19 | 2010-12-19 22:45 | Calculated | 5916 | 5916 - Earth Working Link 5916 |  | 408SEG5916-5241 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 23 | 24487 | 2668 | 0.10896 | 0.00093927 | 130 | 15080 | 2010/2011 | December-2010 | 12 | 2010
24512 | Faulty Batch of Insulators - Waihora Road | 2010-12-20 00:05 | 2010-12-20 | 2010-12-20 14:00 | Calculated | 446 | 446 - Recloser 446 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 534 | 218 | 24487 | 65429 | 2.672 | 0.0089027 | 1696.2037 | 480982 | 2010/2011 | December-2010 | 12 | 2010
24517 | Faulty Disc Insulator - Manunui | 2010-12-20 04:45 | 2010-12-20 | 2010-12-20 07:05 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 37 | 24487 | 5180 | 0.21154 | 0.001511 | 227.5 | 31850 | 2010/2011 | December-2010 | 12 | 2010
25474 | T 2 Buchholz Trip - Hangatiki | 2010-12-20 07:51 | 2010-12-20 | 2010-12-20 07:54 | Calculated | TPHangatiki CB232 | TPHangatiki CB232 - 33kV Minimum Oil Circuit Breaker TP232 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Waitete 33 | Direct from Hangatiki Supply |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 2056 | 24487 | 5996 | 0.24486 | 0.083963 | 17128.0864 | 49956 | 2010/2011 | December-2010 | 12 | 2010
24520 | T2 Buchholz Trip - Waitete | 2010-12-20 07:57 | 2010-12-20 | 2010-12-20 08:07 | Calculated | 1404 | 1404 - Circuit Breaker 1404 |  | 306SEGTP236-153 | 206-01 Waitete | Urban A | Benneydale | Waitete Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 466 | 24487 | 4660 | 0.19031 | 0.019031 | 5609.5 | 56094 | 2010/2011 | December-2010 | 12 | 2010
24522 | Change Poles & Xarms - Rangitoto Feeder | 2010-12-20 09:32 | 2010-12-20 | 2010-12-20 14:31 | Calculated | SEG247-TempLink210 | SEG247-TempLink210 - 106SEG247-TempLink210 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 260 | 25 | 24487 | 6500 | 0.26545 | 0.0010209 | 165 | 42900 | 2010/2011 | December-2010 | 12 | 2010
24518 | Faulty Disc Insulator - Manunui | 2010-12-20 13:45 | 2010-12-20 | 2010-12-20 15:22 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 37 | 24487 | 3589 | 0.14657 | 0.001511 | 227.5 | 22067 | 2010/2011 | December-2010 | 12 | 2010
24523 | Tree On Line - Kirikau Valley Road | 2010-12-20 14:25 | 2010-12-20 | 2010-12-20 20:21 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 356 | 15 | 24487 | 5340 | 0.21807 | 0.00061257 | 98 | 34887 | 2010/2011 | December-2010 | 12 | 2010
25475 | T 2 Buchholz Trip - Hangatiki | 2010-12-20 19:17 | 2010-12-20 | 2010-12-20 19:18 | Calculated | TPHangatiki CB232 | TPHangatiki CB232 - 33kV Minimum Oil Circuit Breaker TP232 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Waitete 33 | Direct from Hangatiki Supply |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 2056 | 24487 | 2056 | 0.08396 | 0.083963 | 17128.0864 | 15700 | 2010/2011 | December-2010 | 12 | 2010
24878 | H/V Pole Replacement - Ailsa St T8 | 2010-12-21 09:06 | 2010-12-21 | 2010-12-21 12:28 | Calculated | 201 | 201 - RTE Switch 201 |  | No Segment | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 202 | 100 | 24487 | 20226 | 0.82599 | 0.0040838 | 400 | 80906 | 2010/2011 | December-2010 | 12 | 2010
25243 | Change Poles & X/arms - Rangitoto | 2010-12-21 09:41 | 2010-12-21 | 2010-12-21 14:26 | Calculated | SEGTempLink210-2068 | SEGTempLink210-2068 - 106SEGTempLink210-2068 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 261 | 25 | 24487 | 6502 | 0.26553 | 0.0010209 | 165 | 42913 | 2010/2011 | December-2010 | 12 | 2010
24526 | Unknown - Lower Retaruke Road | 2010-12-21 14:15 | 2010-12-21 | 2010-12-21 16:14 | Calculated | 5170 | 5170 - Sectionaliser 5170 |  | 410SEG5170-5611 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 21 | 24487 | 2499 | 0.10205 | 0.0008576 | 168 | 19991 | 2010/2011 | December-2010 | 12 | 2010
24527 | Lightning - Erua Road | 2010-12-21 21:50 | 2010-12-21 | 2010-12-21 22:38 | Calculated | 16J01 | 16J01 - 1 Phase : 3.00 kVA : POLEMNT |  | 410SEG5631 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 2 | 24487 | 96 | 0.00392 | 8.1676e-05 | 3 | 144 | 2010/2011 | December-2010 | 12 | 2010
24528 | Lightning - SH3 | 2010-12-21 22:35 | 2010-12-21 | 2010-12-22 01:10 | Calculated | T2204 | T2204 - 3 Phase : 30.00 kVA : POLEMNT |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 155 | 5 | 24487 | 775 | 0.03165 | 0.00020419 | 30 | 4650 | 2010/2011 | December-2010 | 12 | 2010
24529 | Jumper off DDO - SH40 | 2010-12-21 22:35 | 2010-12-21 | 2010-12-22 00:31 | Calculated | T2210 | T2210 - 1 Phase : 15.00 kVA : POLEMNT |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 2 | 24487 | 232 | 0.00947 | 8.1676e-05 | 15 | 1740 | 2010/2011 | December-2010 | 12 | 2010
24530 | Jumper off DDO - SH40 | 2010-12-21 23:33 | 2010-12-21 | 2010-12-22 00:31 | Calculated | 1645 | 1645 - Solid Link 1645 |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 34 | 24487 | 1972 | 0.08053 | 0.0013885 | 228 | 13223 | 2010/2011 | December-2010 | 12 | 2010
24531 | Unknown - Paerata Road | 2010-12-22 00:20 | 2010-12-22 | 2010-12-22 02:16 | Calculated | 455 | 455 - Fused Link 455 |  | 129SEG455-402 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 45 | 24487 | 5220 | 0.21317 | 0.0018377 | 400 | 46399 | 2010/2011 | December-2010 | 12 | 2010
24532 | Remove Pine Tree Burning on Line - | 2010-12-22 10:00 | 2010-12-22 | 2010-12-22 11:53 | Calculated | 5615 | 5615 - Solid Link 5615 |  | 417SEG5615 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 39 | 24487 | 4407 | 0.17997 | 0.0015927 | 502.7778 | 56813 | 2010/2011 | December-2010 | 12 | 2010
24534 | Fuse Pulled Apart - Dekker Road | 2010-12-23 09:00 | 2010-12-23 | 2010-12-23 09:23 | Calculated | 11S19 | 11S19 - 3 Phase : 50.00 kVA : POLEMNT |  | 424SEG5228 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 2 | 24487 | 46 | 0.00188 | 8.1676e-05 | 50 | 1150 | 2010/2011 | December-2010 | 12 | 2010
24533 | Replace Faulty Batch of Insulators | 2010-12-23 09:01 | 2010-12-23 | 2010-12-23 13:38 | Calculated | 493 | 493 - Air Break Switch 493 |  | 123SEG493-466 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 277 | 101 | 24487 | 27977 | 1.1425 | 0.0041246 | 790 | 218829 | 2010/2011 | December-2010 | 12 | 2010
24536 | Magpie - Oio No.1 Road | 2010-12-23 16:30 | 2010-12-23 | 2010-12-23 18:00 | Calculated | 12I03 | 12I03 - 1 Phase : 15.00 kVA : POLEMNT |  | 409SEG5748-5743 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 2 | 24487 | 180 | 0.00735 | 8.1676e-05 | 0 | 0 | 2010/2011 | December-2010 | 12 | 2010
24537 | Ducks - Te Kumi Station Road | 2010-12-24 10:30 | 2010-12-24 | 2010-12-24 11:01 | Calculated | 763 | 763 - Fused Link 763 |  | 108SEG763-2140 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 2 | 24487 | 62 | 0.00253 | 8.1676e-05 | 330 | 10230 | 2010/2011 | December-2010 | 12 | 2010
24538 | Broken Xarm - McLean Road | 2010-12-24 10:52 | 2010-12-24 | 2010-12-24 14:16 | Calculated | 406 | 406 - Air Break Switch 406 |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 106 | 24487 | 2336 | 0.0954 | 0.0043288 | 1855.5 | 35799 | 2010/2011 | December-2010 | 12 | 2010
24539 | Fuse Pulled Apart - SH4 | 2010-12-26 08:15 | 2010-12-26 | 2010-12-26 09:10 | Calculated | 05I11 | 05I11 - 1 Phase : 15.00 kVA : POLEMNT |  | 402SEG5782 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 24487 | 55 | 0.00225 | 4.0838e-05 | 15 | 825 | 2010/2011 | December-2010 | 12 | 2010
24541 | Unknown - Waitaanga Road (0800 crashed unable to phone) | 2010-12-27 16:00 | 2010-12-27 | 2010-12-28 14:50 | Calculated | 5734 | 5734 - Fused Link 5734 |  | 413SEG5734 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1370 | 29 | 24487 | 38650 | 1.5784 | 0.0011843 | 160.8333 | 213391 | 2010/2011 | December-2010 | 12 | 2010
24542 | Unknown - Mangateitei Road | 2010-12-28 05:10 | 2010-12-28 | 2010-12-28 09:45 | Calculated | 5693 | 5693 - Fused Link 5693 |  | 415SEG5693-6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 275 | 29 | 24487 | 7975 | 0.32568 | 0.0011843 | 285 | 78374 | 2010/2011 | December-2010 | 12 | 2010
24543 | Unknown - SH3 | 2010-12-28 07:45 | 2010-12-28 | 2010-12-28 14:23 | Calculated | T2204 | T2204 - 3 Phase : 30.00 kVA : POLEMNT |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 398 | 5 | 24487 | 1990 | 0.08127 | 0.00020419 | 30 | 11940 | 2010/2011 | December-2010 | 12 | 2010
24544 | Unknown - Karangahape Road | 2010-12-28 11:04 | 2010-12-28 | 2010-12-28 12:27 | Calculated | 5847 | 5847 - Recloser w Bypass & Links 5847 |  | 426SEGT4193-5847 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 24 | 24487 | 1992 | 0.08135 | 0.00098011 | 233 | 19339 | 2010/2011 | December-2010 | 12 | 2010
24545 | Unknown - Karangahape Road | 2010-12-28 11:04 | 2010-12-28 | 2010-12-28 13:03 | Calculated | 5110 | 5110 - Fused Link 5110 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 16 | 24487 | 1904 | 0.07776 | 0.00065341 | 135.5 | 16124 | 2010/2011 | December-2010 | 12 | 2010
24546 | Unknown - Karangahape Road West | 2010-12-28 11:04 | 2010-12-28 | 2010-12-28 16:17 | Calculated | 5593 | 5593 - Fused Link 5593 |  | 426SEG5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 313 | 4 | 24487 | 1252 | 0.05113 | 0.00016335 | 40 | 12520 | 2010/2011 | December-2010 | 12 | 2010
24547 | Wind - Hangatiki | 2010-12-28 11:40 | 2010-12-28 | 2010-12-28 11:52 | Calculated | 1272 | 1272 - Circuit Breaker 1272 |  | No Segment | 204-01 Hangatiki | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 310 | 24487 | 3720 | 0.15192 | 0.01266 | 2873.5 | 34481 | 2010/2011 | December-2010 | 12 | 2010
24548 | Wind - Waitomo Caves Road | 2010-12-28 11:40 | 2010-12-28 | 2010-12-28 12:09 | Calculated | 679 | 679 - Air Break Switch 679 |  | 101SEG679-267 | Caves 101-05 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 178 | 24487 | 5162 | 0.21081 | 0.0072692 | 1781 | 51648 | 2010/2011 | December-2010 | 12 | 2010
24549 | Wind - Top Caves Road | 2010-12-28 11:40 | 2010-12-28 | 2010-12-28 14:19 | Calculated | 110 | 110 - Air Break Switch 110 |  | 101SEG110-109 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 111 | 24487 | 17649 | 0.72075 | 0.004533 | 851 | 135308 | 2010/2011 | December-2010 | 12 | 2010
25477 | Wind - Hangatiki | 2010-12-28 11:41 | 2010-12-28 | 2010-12-28 14:20 | Calculated | 1272 | 1272 - Circuit Breaker 1272 |  | No Segment | 204-01 Hangatiki | Urban A | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 336 | 24487 | 23132 | 0.94466 | 0.013722 | 3243.9372 | 194332 | 2010/2011 | December-2010 | 12 | 2010
24550 | Wind - Kaahu South Road | 2010-12-28 11:45 | 2010-12-28 | 2010-12-28 13:13 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 27 | 24487 | 2376 | 0.09703 | 0.0011026 | 310 | 27280 | 2010/2011 | December-2010 | 12 | 2010
24551 | Wind - Marotiri Road | 2010-12-28 12:15 | 2010-12-28 | 2010-12-28 13:36 | Calculated | T1203 | T1203 - 3ph 15kVA POLEMNT |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 3 | 24487 | 243 | 0.00992 | 0.00012251 | 15 | 1215 | 2010/2011 | December-2010 | 12 | 2010
24553 | Unknown - Pungarehu Road | 2010-12-28 12:53 | 2010-12-28 | 2010-12-28 13:21 | Calculated | T1643 | T1643 - 2ph 10kVA POLEMNT |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 2 | 24487 | 56 | 0.00229 | 8.1676e-05 | 10 | 280 | 2010/2011 | December-2010 | 12 | 2010
24555 | Unknown - Whangaehu Valley Road | 2010-12-28 12:55 | 2010-12-28 | 2010-12-28 18:43 | Calculated | 5684 | 5684 - Recloser 5684 |  | 416SEG5721-5684 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 348 | 72 | 24487 | 10756 | 0.43925 | 0.0029403 | 567 | 81486 | 2010/2011 | December-2010 | 12 | 2010
24556 | Wind - SH46 | 2010-12-28 13:15 | 2010-12-28 | 2010-12-28 14:39 | Calculated | 12P03 | 12P03 - 1 Phase : 15.00 kVA : POLEMNT |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 4 | 24487 | 336 | 0.01372 | 0.00016335 | 15 | 1260 | 2010/2011 | December-2010 | 12 | 2010
24558 | Faulty Tx @ Zone Sub - Piripiri Substation | 2010-12-28 15:30 | 2010-12-28 | 2010-12-28 18:37 | Calculated | 797 | 797 - Circuit Breaker 797 |  | No Segment | 202-01 Piripiri | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 318 | 24487 | 59466 | 2.4285 | 0.012986 | 2398.5 | 448519 | 2010/2011 | December-2010 | 12 | 2010
24559 | Unknown - Oturu Road | 2010-12-28 16:40 | 2010-12-28 | 2010-12-28 17:39 | Calculated | T347 | T347 - 3ph 25kVA POLEMNT |  | 109SEG179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 2 | 24487 | 118 | 0.00482 | 8.1676e-05 | 25 | 1475 | 2010/2011 | December-2010 | 12 | 2010
24560 | Unknown - Lower Retaruke Road | 2010-12-28 16:50 | 2010-12-28 | 2010-12-28 19:04 | Calculated | 5490 | 5490 - Recloser with Bypass 5490 |  | 410SEG5490-5438 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 74 | 24487 | 6683 | 0.27292 | 0.003022 | 421.75 | 41035 | 2010/2011 | December-2010 | 12 | 2010
24562 | Unknown - Oio Sub | 2010-12-28 17:00 | 2010-12-28 | 2010-12-28 19:27 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 147 | 25 | 24487 | 3675 | 0.15008 | 0.0010209 | 138.5 | 20359 | 2010/2011 | December-2010 | 12 | 2010
24563 | Tree Work - SH4 | 2010-12-29 11:22 | 2010-12-29 | 2010-12-29 13:26 | Calculated | 03H12 | 03H12 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5436-5434 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 124 | 3 | 24487 | 372 | 0.01519 | 0.00012251 | 15 | 1860 | 2010/2011 | December-2010 | 12 | 2010
24565 | Jumper off @ Tx - Waipuna Road | 2010-12-30 12:45 | 2010-12-30 | 2010-12-30 13:05 | Calculated | T2553 | T2553 - 1 Phase : 3.00 kVA : POLEMNT |  | 101SEG1272-257 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 1 | 24487 | 20 | 0.00082 | 4.0838e-05 | 3 | 60 | 2010/2011 | December-2010 | 12 | 2010
24566 | Ducks - Harpers Ave | 2010-12-31 06:55 | 2010-12-31 | 2010-12-31 08:14 | Calculated | 663 | 663 - Fused Link 663 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 6 | 24487 | 474 | 0.01936 | 0.00024503 | 90 | 7110 | 2010/2011 | December-2010 | 12 | 2010
24568 | SWER Backfeed - Ongarue Back Road | 2011-01-02 09:15 | 2011-01-02 | 2011-01-02 11:35 | Calculated | 5777 | 5777 - Fused Link 5777 |  | No Segment | No Asset Group | Remote Rural F | Northern | Borough Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 18 | 24487 | 955 | 0.039 | 0.00073508 | 132.5 | 7962 | 2010/2011 | January-2011 | 1 | 2011
24570 | Possum - Oparure Road | 2011-01-03 06:30 | 2011-01-03 | 2011-01-03 08:17 | Calculated | T900 | T900 - 1 Phase : 15.00 kVA : POLEMNT |  | 107SEG262-176 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24487 | 107 | 0.00437 | 4.0838e-05 | 15 | 1605 | 2010/2011 | January-2011 | 1 | 2011
24571 | Unknown - Old Te Kuiti Road | 2011-01-03 20:16 | 2011-01-03 | 2011-01-03 21:18 | Calculated | T177 | T177 - 3ph 15kVA POLEMNT |  | 102SEG1271-336 | Hangatiki East 102-01 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 4 | 24487 | 248 | 0.01013 | 0.00016335 | 15 | 930 | 2010/2011 | January-2011 | 1 | 2011
24573 | Unknown - Borough Sub | 2011-01-05 05:05 | 2011-01-05 | 2011-01-05 05:17 | Calculated | 5952 | 5952 - Circuit Breaker Matapuna 5952 |  | No Segment | 508-01 Borough | Rural B | Matapuna | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 1042 | 24487 | 12504 | 0.51064 | 0.042553 | 5065 | 60779 | 2010/2011 | January-2011 | 1 | 2011
24574 | Trees - Waipapa | 2011-01-05 07:00 | 2011-01-05 | 2011-01-05 08:15 | Calculated | T673 | T673 - 3ph 15kVA POLEMNT |  | 107SEG250-254 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 2 | 24487 | 150 | 0.00613 | 8.1676e-05 | 15 | 1125 | 2010/2011 | January-2011 | 1 | 2011
24576 | Unknown - Soldiers Road | 2011-01-06 09:53 | 2011-01-06 | 2011-01-06 16:31 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 398 | 1 | 24487 | 398 | 0.01625 | 4.0838e-05 | 3360 | 1337280 | 2010/2011 | January-2011 | 1 | 2011
24587 | Trees Through Line - Mapara South Rd | 2011-01-07 05:31 | 2011-01-07 | 2011-01-07 14:44 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 553 | 15 | 24487 | 8303 | 0.33908 | 0.00061257 | 133 | 73624 | 2010/2011 | January-2011 | 1 | 2011
24589 | Scheduled Tree Cutting - Lower Retaruke | 2011-01-07 09:29 | 2011-01-07 | 2011-01-07 13:18 | Calculated | 5396 | 5396 - Sectionaliser 5396 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 | Vegetation Plantation | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 228 | 44 | 24487 | 10045 | 0.41022 | 0.0017969 | 180 | 41096 | 2010/2011 | January-2011 | 1 | 2011
24590 | Replace Link 5895 - Te Puke Rd | 2011-01-08 07:30 | 2011-01-08 | 2011-01-08 08:48 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related |  |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 1 | 24487 | 77 | 0.00314 | 4.0838e-05 | 5 | 387 | 2010/2011 | January-2011 | 1 | 2011
24602 | Maintenance in Oparure Sub - Also Replace 11kv Pole in Quarry | 2011-01-10 09:06 | 2011-01-10 | 2011-01-10 16:05 | Calculated | 658 | 658 - Air Break Switch 658 |  | No Segment | 208-01 Oparure | Remote Rural E | Gadsby Rd 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 418 | 5 | 24487 | 2091 | 0.08539 | 0.00020419 | 800 | 334679 | 2010/2011 | January-2011 | 1 | 2011
24604 | Fuse Pulled Apart - Waitomo Caves Rd | 2011-01-11 08:08 | 2011-01-11 | 2011-01-11 09:57 | Calculated | T95 | T95 - 1 Phase : 15.00 kVA : POLEMNT |  | 101SEG577-679 | Caves 101-05 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related |  |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 1 | 24487 | 109 | 0.00445 | 4.0838e-05 | 15 | 1637 | 2010/2011 | January-2011 | 1 | 2011
24605 | Replace Poles 4152006 & 4152052 | 2011-01-11 09:33 | 2011-01-11 | 2011-01-11 14:35 | Calculated | 5705 | 5705 - Fused Link 5705 |  | 415SEG5705 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 12 | 24487 | 3628 | 0.14816 | 0.00049006 | 65.8333 | 19905 | 2010/2011 | January-2011 | 1 | 2011
24607 | Ducks - Hangatiki East Rd | 2011-01-11 21:33 | 2011-01-11 | 2011-01-11 22:31 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals |  |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 9 | 24487 | 524 | 0.0214 | 0.00036754 | 50 | 2915 | 2010/2011 | January-2011 | 1 | 2011
24608 | Replace Poles 4152006 & 4152052 | 2011-01-12 09:33 | 2011-01-12 | 2011-01-12 14:28 | Calculated | 5705 | 5705 - Fused Link 5705 |  | 415SEG5705 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 12 | 24487 | 3533 | 0.14428 | 0.00049006 | 65.8333 | 19384 | 2010/2011 | January-2011 | 1 | 2011
24609 | Update Earth Bank - SH 30 Pureora | 2011-01-12 11:20 | 2011-01-12 | 2011-01-12 13:16 | Calculated | T983 | T983 - 1 Phase : 5.00 kVA : POLEMNT |  | 119SEG404 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 1 | 24487 | 115 | 0.0047 | 4.0838e-05 | 25 | 2879 | 2010/2011 | January-2011 | 1 | 2011
24610 | High Voltage - Lower Taps - Paerata | 2011-01-12 13:55 | 2011-01-12 | 2011-01-12 16:04 | Calculated | T1969 | T1969 - 3 Phase : 25.00 kVA : POLEMNT |  | 129SEG455-402 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related |  |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 3 | 24487 | 387 | 0.0158 | 0.00012251 | 25 | 3229 | 2010/2011 | January-2011 | 1 | 2011
24611 | Change Faulty Transformer | 2011-01-12 17:31 | 2011-01-12 | 2011-01-12 19:20 | Calculated | T1969 | T1969 - 3 Phase : 25.00 kVA : POLEMNT |  | 129SEG455-402 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related |  |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 109 | 3 | 24487 | 327 | 0.01335 | 0.00012251 | 25 | 2730 | 2010/2011 | January-2011 | 1 | 2011
24612 | Change Poles and Xarms - Sommerville Rd | 2011-01-13 09:35 | 2011-01-13 | 2011-01-13 16:42 | Calculated | SEG182-505 | SEG182-505 - 108SEG182-505 |  | No Segment | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage |  |  |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 427 | 33 | 24487 | 14124 | 0.5768 | 0.0013477 | 369.1667 | 157855 | 2010/2011 | January-2011 | 1 | 2011
24622 | Replace Poles & Xarms - Main South Highway - South of Erua Township | 2011-01-13 09:35 | 2011-01-13 | 2011-01-13 14:38 | Calculated | 5329 | 5329 - Fused Link 5329 |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 302 | 19 | 24487 | 5752 | 0.2349 | 0.00077592 | 135.5 | 41027 | 2010/2011 | January-2011 | 1 | 2011
24620 | Ducks - Hangatiki East Rd | 2011-01-14 07:00 | 2011-01-14 | 2011-01-14 08:12 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 10 | 24487 | 711 | 0.02904 | 0.00040838 | 54.1667 | 3853 | 2010/2011 | January-2011 | 1 | 2011
24621 | Unknown | 2011-01-14 08:30 | 2011-01-14 | 2011-01-14 16:35 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Asset Related |  |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 485 | 1 | 24487 | 485 | 0.01981 | 4.0838e-05 | 5 | 2426 | 2010/2011 | January-2011 | 1 | 2011
24626 | Change Poles & Xarms - Sommerville Rd | 2011-01-14 09:32 | 2011-01-14 | 2011-01-14 14:31 | Calculated | SEG182-505 | SEG182-505 - 108SEG182-505 |  | No Segment | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 298 | 33 | 24487 | 9834 | 0.4016 | 0.0013477 | 369.1667 | 110103 | 2010/2011 | January-2011 | 1 | 2011
24627 | Upgrade Tx11s20 from 200kva to 300kva - Taupahi Rd | 2011-01-14 09:43 | 2011-01-14 | 2011-01-14 16:07 | Calculated | 6648 | 6648 - Magnefix Switch 6648 |  | 424SEG6648 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 383 | 70 | 24487 | 26821 | 1.0953 | 0.0028587 | 304.3478 | 116615 | 2010/2011 | January-2011 | 1 | 2011
24631 | Burn out H/V Fuse Carrier - Turongo St | 2011-01-14 11:30 | 2011-01-14 | 2011-01-14 12:49 | Calculated | 668 | 668 - Fused Link 668 |  | 112SEG668-229 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related |  |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 39 | 24487 | 3050 | 0.12456 | 0.0015927 | 400 | 31286 | 2010/2011 | January-2011 | 1 | 2011
24632 | Birds Nest In L/V Bushings - Kururau Rd | 2011-01-14 12:16 | 2011-01-14 | 2011-01-14 13:49 | Calculated | 08G03 | 08G03 - 1 Phase : 10.00 kVA : POLEMNT |  | 403SEG5812-5321 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 1 | 24487 | 93 | 0.0038 | 4.0838e-05 | 10 | 934 | 2010/2011 | January-2011 | 1 | 2011
24633 | Magpie - S.H.41 | 2011-01-15 08:20 | 2011-01-15 | 2011-01-15 09:59 | Calculated | 09R06 | 09R06 - 1 Phase : 15.00 kVA : POLEMNT |  | 406SEG5897-5481 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 4 | 24487 | 397 | 0.01621 | 0.00016335 | 15 | 1489 | 2010/2011 | January-2011 | 1 | 2011
24637 | Replace H/V Fuse Tx4056 | 2011-01-17 09:00 | 2011-01-17 | 2011-01-17 11:20 | Calculated | T4056 | T4056 - 3 Phase : 5.00 kVA : POLEMNT |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 1 | 24487 | 140 | 0.00572 | 4.0838e-05 | 5 | 700 | 2010/2011 | January-2011 | 1 | 2011
24638 | Fit links on tap off pole to T2548 - Wairere Rd - South of Kahuwera Rd | 2011-01-17 09:31 | 2011-01-17 | 2011-01-17 11:32 | Calculated | 1327 | 1327 - Air Break Switch 1327 | Fit links on tap off pole to T2548 - Wairere Rd - South of Kahuwera Rd | 116SEG1327-1340 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 24 | 24487 | 2910 | 0.11884 | 0.00098011 | 170 | 20612 | 2010/2011 | January-2011 | 1 | 2011
24639 | Changing Poles & X/arms - Taipairu Rd | 2011-01-17 09:37 | 2011-01-17 | 2011-01-17 14:44 | Calculated | SEGTempLink210-2068 | SEGTempLink210-2068 - 106SEGTempLink210-2068 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 25 | 24487 | 7680 | 0.31364 | 0.0010209 | 290 | 89092 | 2010/2011 | January-2011 | 1 | 2011
24641 | Install T/O Fuse To Tx12P1 For Future Upgrade - Otukou Sub | 2011-01-17 10:02 | 2011-01-17 | 2011-01-17 11:04 | Calculated | 5584 | 5584 - Recloser with Bypass & Links 5584 |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 62 | 75 | 24487 | 4675 | 0.19092 | 0.0030628 | 336 | 20943 | 2010/2011 | January-2011 | 1 | 2011
24642 | Replace Blown L/A & Reconnect Earth - Omori Rd | 2011-01-17 10:06 | 2011-01-17 | 2011-01-17 12:03 | Calculated | 6018 | 6018 - Solid Link 6018 |  | 406SEG6018-5009 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 7 | 24487 | 815 | 0.03328 | 0.00028587 | 400 | 46580 | 2010/2011 | January-2011 | 1 | 2011
24643 | Replace H/V fuse Tx2573 - SH 30 Waipa Valley | 2011-01-17 11:25 | 2011-01-17 | 2011-01-17 13:38 | Calculated | T2573 | T2573 - 3 Phase : 100.00 kVA : POLEMNT |  | 119SEG432-653 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 133 | 3 | 24487 | 399 | 0.01629 | 0.00012251 | 100 | 13324 | 2010/2011 | January-2011 | 1 | 2011
24645 | Faulty Insulator Across N/O Link 5861 - Tunanui Sub | 2011-01-17 12:53 | 2011-01-17 | 2011-01-17 16:24 | Calculated | 5861 | 5861 - Earth Working Link 5861 |  | 409SEG5599-5600 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 211 | 78 | 24487 | 15778 | 0.64434 | 0.0031854 | 545.5 | 110598 | 2010/2011 | January-2011 | 1 | 2011
24646 | Replace H/V fuse Tx115 - Mapara Rd | 2011-01-17 15:26 | 2011-01-17 | 2011-01-17 16:49 | Calculated | T115 | T115 - 1 Phase : 5.00 kVA : POLEMNT |  | 117SEG1297-1296 | Te Mapara 117-03 | Rural D | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 1 | 24487 | 83 | 0.00339 | 4.0838e-05 | 15 | 1248 | 2010/2011 | January-2011 | 1 | 2011
24647 | Faulty DDO@Tx3J5 - Ongarue/Waimiha Rd | 2011-01-17 17:43 | 2011-01-17 | 2011-01-17 18:06 | Calculated | 5473 | 5473 - Fused Link 5473 |  | 421SEG5473 | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 5 | 24487 | 116 | 0.00474 | 0.00020419 | 60 | 1394 | 2010/2011 | January-2011 | 1 | 2011
24648 | L/V Jumper Off - Tx2963 - Mangawhero Rd | 2011-01-17 20:10 | 2011-01-17 | 2011-01-17 20:54 | Calculated | T2963 | T2963 - 3ph 15kVA POLEMNT |  | 109SEG324-1755 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 1 | 24487 | 44 | 0.0018 | 4.0838e-05 | 15 | 662 | 2010/2011 | January-2011 | 1 | 2011
24649 | H/V Cable Jointing & Re-Instatement - Eketone Street | 2011-01-18 09:17 | 2011-01-18 | 2011-01-18 15:33 | Calculated | 649 | 649 - Fused Link 649 |  | 107SEG299-218 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 376 | 53 | 24487 | 19946 | 0.81455 | 0.0021644 | 400 | 150539 | 2010/2011 | January-2011 | 1 | 2011
24650 | Changing poles & x/arms - Taipairu Rd - before Thompson's Rd | 2011-01-18 09:35 | 2011-01-18 | 2011-01-18 14:45 | Calculated | 247 | 247 - Air Break Switch 247 |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 310 | 24 | 24487 | 7445 | 0.30404 | 0.00098011 | 277.5 | 86085 | 2010/2011 | January-2011 | 1 | 2011
24653 | Replace H/V fuse Tx4p3 - SH 32 | 2011-01-18 12:30 | 2011-01-18 | 2011-01-18 15:12 | Calculated | 04P03 | 04P03 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 5 | 24487 | 806 | 0.03292 | 0.00020419 | 15 | 2419 | 2010/2011 | January-2011 | 1 | 2011
24655 | Wind - Racecourse Rd | 2011-01-18 19:15 | 2011-01-18 | 2011-01-18 20:45 | Calculated | 08J12 | 08J12 - 3 Phase : 50.00 kVA : POLEMNT |  | 404SEG5165 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 9 | 24487 | 803 | 0.03279 | 0.00036754 | 50 | 4465 | 2010/2011 | January-2011 | 1 | 2011
24656 | Branch on line Tx1211 - Troopers Rd | 2011-01-18 20:20 | 2011-01-18 | 2011-01-18 20:46 | Calculated | T1211 | T1211 - 3 Phase : 25.00 kVA : POLEMNT |  | 107SEG266 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 2 | 24487 | 50 | 0.00204 | 8.1676e-05 | 25 | 630 | 2010/2011 | January-2011 | 1 | 2011
24663 | Trees through line - Mapara South Rd | 2011-01-18 20:26 | 2011-01-18 | 2011-01-19 12:23 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 956 | 15 | 24487 | 14342 | 0.5857 | 0.00061257 | 133 | 127172 | 2010/2011 | January-2011 | 1 | 2011
24657 | OCB tripped - Maraetai Substation | 2011-01-18 21:52 | 2011-01-18 | 2011-01-18 22:03 | Calculated | 2062 | 2062 - Circuit Breaker Maraetai 11 kV 2062 |  | No Segment | 210-01 Maraetai | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 1210 | 24487 | 12483 | 0.50978 | 0.049414 | 8906 | 91880 | 2010/2011 | January-2011 | 1 | 2011
24665 | Wind - Marotiri Sub | 2011-01-19 00:15 | 2011-01-19 | 2011-01-19 00:24 | Calculated | CB2 | CB2 - Circuit Breaker Tihoi Feeder CB2 |  | No Segment | 212-01 Marotiri | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 208 | 24487 | 1920 | 0.07841 | 0.0084943 | 2025.5 | 18702 | 2010/2011 | January-2011 | 1 | 2011
24776 |  | 2011-01-19 00:15 | 2011-01-19 | 2011-01-19 00:23 | Calculated | CB2 | CB2 - Circuit Breaker Tihoi Feeder CB2 |  | No Segment | 212-01 Marotiri | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 208 | 24487 | 1764 | 0.07204 | 0.0084943 | 2025.5 | 17182 | 2010/2011 | January-2011 | 1 | 2011
24666 | Jumper off at Tx105 - Pururu West Rd | 2011-01-19 00:59 | 2011-01-19 | 2011-01-19 01:40 | Calculated | 173 | 173 - Fused Link 173 |  | 106SEG173 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 7 | 24487 | 288 | 0.01176 | 0.00028587 | 90 | 3708 | 2010/2011 | January-2011 | 1 | 2011
24669 | Wind - Replace H/V fuse Tx04H08 - SH 40 | 2011-01-19 06:31 | 2011-01-19 | 2011-01-19 07:38 | Calculated | 04H08 | 04H08 - 1 Phase : 15.00 kVA : POLEMNT |  | 421SEG5448-5436 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 1 | 24487 | 67 | 0.00274 | 4.0838e-05 | 15 | 1007 | 2010/2011 | January-2011 | 1 | 2011
24671 | Replace Tx Structure - Tx12P1 -SH 46 | 2011-01-19 09:31 | 2011-01-19 | 2011-01-19 14:30 | Calculated | 12P01 | 12P01 - 1 Phase : 30.00 kVA : POLEMNT |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 299 | 8 | 24487 | 2394 | 0.09777 | 0.0003267 | 30 | 8977 | 2010/2011 | January-2011 | 1 | 2011
24672 | Change X/arm &Insulator at Tx17H7 - Also bolt down Tx17H2 - Makino Rd | 2011-01-19 10:21 | 2011-01-19 | 2011-01-19 13:15 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | 410SEG5511-5517 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 174 | 28 | 24487 | 4876 | 0.19913 | 0.0011435 | 183.5 | 31959 | 2010/2011 | January-2011 | 1 | 2011
24675 | Jumper Off at Tx 1905 - Wairoma Rd | 2011-01-19 12:46 | 2011-01-19 | 2011-01-19 13:47 | Calculated | 1118 | 1118 - Fused Link 1118 |  | 114SEG1118 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 3 | 24487 | 180 | 0.00735 | 0.00012251 | 15 | 902 | 2010/2011 | January-2011 | 1 | 2011
24676 | H/V fuse at Tx 2601 fell out - vibration- Hangatiki Rd | 2011-01-20 08:07 | 2011-01-20 | 2011-01-20 10:11 | Calculated | T2601 | T2601 - 3ph 50kVA POLEMNT |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 5 | 24487 | 621 | 0.02536 | 0.00020419 | 50 | 6210 | 2010/2011 | January-2011 | 1 | 2011
24678 | SWER Backfeed - Kiritihere Rd | 2011-01-20 08:36 | 2011-01-20 | 2011-01-20 08:38 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | PTRN2 | POUT:PTRN2:PTRN1 | PTRN1 | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 2 | 16 | 24487 | 34 | 0.00139 | 0.00065341 | 140 | 303 | 2010/2011 | January-2011 | 1 | 2011
24681 | Changing Poles & X/arms - Running New Conductor - Refer 2011/23 | 2011-01-20 08:37 | 2011-01-20 | 2011-01-20 16:19 | Calculated | 740 | 740 - Fused Link 740 |  | 125SEG740 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 462 | 1 | 24487 | 462 | 0.01887 | 4.0838e-05 | 200 | 92433 | 2010/2011 | January-2011 | 1 | 2011
24682 | Changing Poles & X/arms - Running New Conductor - Refer 2011/23 | 2011-01-20 09:36 | 2011-01-20 | 2011-01-20 16:01 | Calculated | 296 | 296 - Recloser with Bypass 296 |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 385 | 12 | 24487 | 4623 | 0.18879 | 0.00049006 | 75 | 28893 | 2010/2011 | January-2011 | 1 | 2011
24684 | Connect New Earth, Replace DDO & X/arm @Tx9C9 - Refer 2011/25 - Tatu Sub | 2011-01-20 10:04 | 2011-01-20 | 2011-01-20 10:25 | Calculated | 5456 | 5456 - Fused Link 5456 |  | 413SEG5456-5461 | Ohura 413-07 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PCUS2:PCUS1 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 20 | 18 | 24487 | 363 | 0.01482 | 0.00073508 | 125 | 2522 | 2010/2011 | January-2011 | 1 | 2011
24687 | L/V tree work - SH 4 | 2011-01-20 10:08 | 2011-01-20 | 2011-01-20 11:58 | Calculated | 05I05 | 05I05 - 1 Phase : 25.00 kVA : POLEMNT |  | 402SEG5782 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 110 | 4 | 24487 | 441 | 0.01801 | 0.00016335 | 25 | 2757 | 2010/2011 | January-2011 | 1 | 2011
24688 | Replace H/V fuse at Tx5H16 - Opotiki Rd | 2011-01-20 13:11 | 2011-01-20 | 2011-01-20 15:18 | Calculated | 05H16 | 05H16 - 1 Phase : 15.00 kVA : POLEMNT |  | 422SEG5105-5279 | Tuhua 422-02 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 1 | 24487 | 127 | 0.00519 | 4.0838e-05 | 15 | 1907 | 2010/2011 | January-2011 | 1 | 2011
24683 | SWER backfeed - Refer 2011/23 | 2011-01-20 16:44 | 2011-01-20 | 2011-01-20 16:49 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 16 | 24487 | 83 | 0.00339 | 0.00065341 | 140 | 730 | 2010/2011 | January-2011 | 1 | 2011
24689 | Replace H/V Fuse Tx2062 - Mokauiti Rd | 2011-01-21 07:00 | 2011-01-21 | 2011-01-21 10:00 | Calculated | T2062 | T2062 - 1 Phase : 25.00 kVA : POLEMNT |  | 115SEG1712-1714 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 4 | 24487 | 717 | 0.02928 | 0.00016335 | 25 | 4482 | 2010/2011 | January-2011 | 1 | 2011
24690 | Sect 277 tripped - Fauchelle Rd | 2011-01-21 17:51 | 2011-01-21 | 2011-01-21 18:31 | Calculated | 5277 | 5277 - Sectionaliser with Bypass & Links5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 16 | 24487 | 642 | 0.02622 | 0.00065341 | 135 | 5422 | 2010/2011 | January-2011 | 1 | 2011
24701 | Replace fuses Tx 2091 after trees cut - Maihiihi Rd | 2011-01-23 06:11 | 2011-01-23 | 2011-01-23 14:30 | Calculated | T2091 | T2091 - 3ph 30kVA polemnt |  | 111SEG346-REG6 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 499 | 3 | 24487 | 1497 | 0.06113 | 0.00012251 | 30 | 14979 | 2010/2011 | January-2011 | 1 | 2011
24696 | RT&T Link 246 - Trees in line- Ahuroa Rd | 2011-01-23 07:31 | 2011-01-23 | 2011-01-23 11:35 | Calculated | 246 | 246 - Fused Link 246 |  | 106SEG246-252 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 244 | 28 | 24487 | 6837 | 0.27921 | 0.0011435 | 162.5 | 39682 | 2010/2011 | January-2011 | 1 | 2011
24702 | Replace Link 260 - SH 30 Kopaki | 2011-01-23 07:55 | 2011-01-23 | 2011-01-23 11:36 | Calculated | 260 | 260 - Circuit Breaker 260 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 220 | 20 | 24487 | 4403 | 0.17981 | 0.00081676 | 185.5 | 40837 | 2010/2011 | January-2011 | 1 | 2011
24703 | Replace fuses Tx1111 - Mangaokewa Rd | 2011-01-23 09:00 | 2011-01-23 | 2011-01-23 12:20 | Calculated | T1111 | T1111 - 1 Phase : 15.00 kVA : POLEMNT |  | 103SEG459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 1 | 24487 | 199 | 0.00813 | 4.0838e-05 | 15 | 2991 | 2010/2011 | January-2011 | 1 | 2011
24699 | Isolation Tx1587, Tx661 - Ahuroa Rd | 2011-01-23 11:34 | 2011-01-23 | 2011-01-24 12:00 | Calculated | T661 | T661 - 1 Phase : 15.00 kVA : POLEMNT |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1466 | 5 | 24487 | 7330 | 0.29934 | 0.00020419 | 22.5 | 32989 | 2010/2011 | January-2011 | 1 | 2011
24704 | Sect 489 -Trees - Upper Retaruke Rd | 2011-01-23 14:30 | 2011-01-23 | 2011-01-23 16:40 | Calculated | 5489J | 5489J - Incoming Link 5489J |  | 410SEG5489-5901 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 29 | 24487 | 3776 | 0.1542 | 0.0011843 | 170 | 22139 | 2010/2011 | January-2011 | 1 | 2011
24705 | Sect 1335 tripped - Fault on line - Road flooded - Mapara South Rd | 2011-01-23 18:40 | 2011-01-23 | 2011-01-24 09:54 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | EENF2 | WEAT:EENF2:EENF1 | Flood / Washout | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 914 | 15 | 24487 | 13713 | 0.56001 | 0.00061257 | 133 | 121590 | 2010/2011 | January-2011 | 1 | 2011
24800 | Floating Wire & Broken X/arm - Tokaanu Sub | 2011-01-24 02:56 | 2011-01-24 | 2011-01-24 03:10 | Calculated | 6576 | 6576 - Circuit Breaker Tokaanu POS 33kV 6576 |  | No Segment | 515-01 Transpower Tokaanu | Rural D | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 47 | 24487 | 658 | 0.02687 | 0.0019194 | 450 | 6299 | 2010/2011 | January-2011 | 1 | 2011
24804 | Floating Wire & Broken X/arm - Kuratau 33/11kv Sub | 2011-01-24 02:56 | 2011-01-24 | 2011-01-24 04:22 | Calculated | 6001 | 6001 - Air Break Switch 6001 |  | No Segment | 509-01 Kuratau | Rural D | No Feeder |  |  | Cant Find a Cause |  | CANT3 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 1590 | 24487 | 136740 | 5.5842 | 0.064932 | 8596 | 739255 | 2010/2011 | January-2011 | 1 | 2011
24818 | Floating Wire & Broken X/arm - Tokaanu Sub | 2011-01-24 02:56 | 2011-01-24 | 2011-01-24 03:10 | Calculated | 5032 | 5032 - Circuit Breaker Incomer 5032 |  | No Segment | Tokaanu 420-01 | Rural C | Tokaanu | Tokaanu Village Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 89 | 24487 | 1246 | 0.05088 | 0.0036346 | 650 | 9099 | 2010/2011 | January-2011 | 1 | 2011
24819 | Floating Wire & Broken X/arm - Tokaanu 33kV | 2011-01-24 02:56 | 2011-01-24 | 2011-01-25 23:28 | Calculated | 6604 | 6604 - Circuit Breaker Tokaanu 33 kV 6604 |  | No Segment | No Asset Group | Remote Rural F | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24487 |  | 0 | 0 |  |  | 2010/2011 | January-2011 | 1 | 2011
24709 | Replace Link 457 - Tihoi Rd | 2011-01-24 06:50 | 2011-01-24 | 2011-01-24 09:42 | Calculated | 457 | 457 - Air Break Switch 457 |  | 124SEG454-475 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 7 | 24487 | 1198 | 0.04892 | 0.00028587 | 100 | 17123 | 2010/2011 | January-2011 | 1 | 2011
24706 | Line Down - Mapara South Rd | 2011-01-24 09:55 | 2011-01-24 | 2011-01-24 11:35 | Calculated | 1325 | 1325 - Fused Link 1325 |  | 103SEG1301-1307 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 3 | 24487 | 301 | 0.01229 | 0.00012251 | 30 | 3012 | 2010/2011 | January-2011 | 1 | 2011
24710 | Replace H/V fuse Tx05I01 - Ongarue Rd | 2011-01-24 10:12 | 2011-01-24 | 2011-01-24 14:44 | Calculated | 05I01 | 05I01 - 1 Phase : 7.50 kVA : POLEMNT |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 272 | 1 | 24487 | 272 | 0.01111 | 4.0838e-05 | 7.5 | 2041 | 2010/2011 | January-2011 | 1 | 2011
24700 | Reconnect Jumpers - Ahuroa Rd - Refer Key 24699 | 2011-01-24 12:00 | 2011-01-24 | 2011-01-24 13:00 | Calculated | 246 | 246 - Fused Link 246 |  | 106SEG246-252 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 28 | 24487 | 1690 | 0.06902 | 0.0011435 | 162.5 | 9809 | 2010/2011 | January-2011 | 1 | 2011
24712 | Sect 281 tripped - Waitewhena Rd | 2011-01-25 07:10 | 2011-01-25 | 2011-01-25 09:42 | Calculated | 5282 | 5282 - Fused Link 5282 |  | 413SEG5282-5281 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 23 | 24487 | 3478 | 0.14203 | 0.00093927 | 158 | 23894 | 2010/2011 | January-2011 | 1 | 2011
24715 | Bolt Out of Arm Brace - Honikiwi Rd | 2011-01-25 11:52 | 2011-01-25 | 2011-01-25 12:24 | Calculated | T3157 | T3157 - 1 Phase : 30.00 kVA : POLEMNT |  | 112SEG209-674 | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 2 | 24487 | 62 | 0.00253 | 8.1676e-05 | 30 | 938 | 2010/2011 | January-2011 | 1 | 2011
24717 | L/V Line Down - Happy Valley Rd | 2011-01-25 13:17 | 2011-01-25 | 2011-01-25 14:53 | Calculated | T421 | T421 - 3ph 10kVA polemnt |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 2 | 24487 | 192 | 0.00784 | 8.1676e-05 | 10 | 961 | 2010/2011 | January-2011 | 1 | 2011
24718 | Upgrade Tx - Hangatiki East Rd | 2011-01-26 07:25 | 2011-01-26 | 2011-01-26 15:55 | Calculated | T2926 | T2926 - 3ph 300kVA GNDPAD |  | 102SEG327 | Hangatiki East 102-03 | Rural C | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 509 | 1 | 24487 | 509 | 0.02079 | 4.0838e-05 | 300 | 152795 | 2010/2011 | January-2011 | 1 | 2011
24723 | Blown Link 526 - Clash - Waihohonui Rd | 2011-01-26 09:10 | 2011-01-26 | 2011-01-26 11:05 | Calculated | 526 | 526 - Fused Link 526 |  | 101SEG526 | Caves 101-03 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 10 | 24487 | 1142 | 0.04664 | 0.00040838 | 102.5 | 11712 | 2010/2011 | January-2011 | 1 | 2011
24820 | Change Poles - 33 & 11 kV On Same Poles - Taharoa | 2011-01-26 10:07 | 2011-01-26 | 2011-01-26 15:31 | Calculated | 609 | 609 - Circuit Breaker 609 (Rural Feeder) 609 |  | No Segment | 201-01 Taharoa | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 324 | 11 | 24487 | 3564 | 0.14555 | 0.00044922 | 83 | 26892 | 2010/2011 | January-2011 | 1 | 2011
24821 | Disconnect Gen Set - Taharoa on Sand | 2011-01-26 15:31 | 2011-01-26 | 2011-01-26 15:33 | Calculated | 504 | 504 - Air Break Switch 504 |  | 126SEG504-578 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 1 | 96 | 24487 | 171 | 0.00698 | 0.0039204 | 590 | 1052 | 2010/2011 | January-2011 | 1 | 2011
24728 | Replace H/V Link 1617 - Pioi Station Spru by Estuary | 2011-01-27 09:05 | 2011-01-27 | 2011-01-27 15:46 | Calculated | 1617 | 1617 - Fused Link 1617 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 400 | 2 | 24487 | 800 | 0.03267 | 8.1676e-05 | 30 | 12009 | 2010/2011 | January-2011 | 1 | 2011
24731 | Burnt Out Fuse Holder Tx2417 - Turongo St | 2011-01-27 09:18 | 2011-01-27 | 2011-01-27 10:38 | Calculated | 668 | 668 - Fused Link 668 |  | 112SEG668-229 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 39 | 24487 | 3094 | 0.12635 | 0.0015927 | 400 | 31733 | 2010/2011 | January-2011 | 1 | 2011
24732 | Replacement of Tx 20L51 - Arawa St | 2011-01-27 09:35 | 2011-01-27 | 2011-01-27 13:43 | Calculated | 20L51 | 20L51 - 3 Phase : 200.00 kVA : GNDPAD |  | 414SEG5715-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 50 | 24487 | 12416 | 0.50704 | 0.0020419 | 200 | 49666 | 2010/2011 | January-2011 | 1 | 2011
24734 | Change Pole 1090296 & Tx 2722 - Waimahora Rd | 2011-01-27 09:45 | 2011-01-27 | 2011-01-27 14:56 | Calculated | T2722 | T2722 - 1 Phase : 5.00 kVA : POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 311 | 4 | 24487 | 1244 | 0.0508 | 0.00016335 | 55 | 17112 | 2010/2011 | January-2011 | 1 | 2011
25180 | Switching Error - 20l51 Pole 30 | 2011-01-27 14:01 | 2011-01-27 | 2011-01-27 15:19 | Calculated | 6632 | 6632 - RTE Switch 6632 |  | 414SEG6351-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 797 | 24487 | 61594 | 2.5154 | 0.032548 | 5450 | 421194 | 2010/2011 | January-2011 | 1 | 2011
24737 | Tree Cutting - Otukou Rd | 2011-01-28 10:09 | 2011-01-28 | 2011-01-28 18:19 | Calculated | 5217 | 5217 - Fused Link 5217 |  | 418SEG5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 490 | 6 | 24487 | 2941 | 0.1201 | 0.00024503 | 50 | 24515 | 2010/2011 | January-2011 | 1 | 2011
24741 | Broken DDO @ Link 217 - Pihanga Saddle Rd | 2011-01-28 17:19 | 2011-01-28 | 2011-01-28 18:19 | Calculated | SEG5590-5217 | SEG5590-5217 - 418SEG5590-5217 |  | No Segment | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 3 | 24487 | 178 | 0.00727 | 0.00012251 | 18 | 1068 | 2010/2011 | January-2011 | 1 | 2011
24743 | Branch On Line - Walker Rd | 2011-01-29 08:20 | 2011-01-29 | 2011-01-29 09:15 | Calculated | T2614 | T2614 - 1 Phase : 10.00 kVA : POLEMNT |  | 106SEG195-659 | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 24487 | 55 | 0.00225 | 4.0838e-05 | 10 | 552 | 2010/2011 | January-2011 | 1 | 2011
24744 | Replace H/V fuse Tx 17H5 - Mangapura Rd | 2011-01-29 09:25 | 2011-01-29 | 2011-01-29 10:48 | Calculated | 17H05 | 17H05 - 1 Phase : 10.00 kVA : POLEMNT |  | 410SEG5511-5517 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 2 | 24487 | 166 | 0.00678 | 8.1676e-05 | 10 | 831 | 2010/2011 | January-2011 | 1 | 2011
24745 | OCB 242 tripped - Hangatiki | 2011-01-29 10:19 | 2011-01-29 | 2011-01-29 10:20 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 318 | 24487 | 408 | 0.01666 | 0.012986 | 2398.5 | 3078 | 2010/2011 | January-2011 | 1 | 2011
24746 | Extreme Wind - Hangatiki | 2011-01-29 10:52 | 2011-01-29 | 2011-01-29 10:53 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 318 | 24487 | 392 | 0.01601 | 0.012986 | 2398.5 | 2958 | 2010/2011 | January-2011 | 1 | 2011
24747 | Replace H/V Fuse - Wind- Clash - Arataki Rd | 2011-01-29 11:15 | 2011-01-29 | 2011-01-29 12:06 | Calculated | T1313 | T1313 - 3 Phase : 30.00 kVA : POLEMNT |  | 120SEG419 | Whakamaru 120-05 (was part 124-01) | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 5 | 24487 | 256 | 0.01045 | 0.00020419 | 30 | 1536 | 2010/2011 | January-2011 | 1 | 2011
24749 | Branch On Line - McRaes Rd - Rangiatea | 2011-01-29 12:39 | 2011-01-29 | 2011-01-29 13:04 | Calculated | 622 | 622 - Fused Link 622 |  | 109SEG622 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 12 | 24487 | 303 | 0.01237 | 0.00049006 | 85 | 2150 | 2010/2011 | January-2011 | 1 | 2011
24748 | Extreme Wind - Piripiri Substation | 2011-01-29 12:40 | 2011-01-29 | 2011-01-29 12:48 | Calculated | 114 | 114 - Circuit Breaker with Bypass 114 |  | No Segment | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 318 | 24487 | 2612 | 0.10667 | 0.012986 | 2398.5 | 19707 | 2010/2011 | January-2011 | 1 | 2011
24750 | Extreme Wind - Waimahora Rd | 2011-01-29 13:06 | 2011-01-29 | 2011-01-29 13:53 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 21 | 24487 | 990 | 0.04043 | 0.0008576 | 168 | 7926 | 2010/2011 | January-2011 | 1 | 2011
24751 | Recloser 799 tripped - Oio Sub | 2011-01-29 13:29 | 2011-01-29 | 2011-01-29 14:07 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 42 | 24487 | 1607 | 0.06563 | 0.0017152 | 228.5 | 8743 | 2010/2011 | January-2011 | 1 | 2011
24829 | Recloser 799 tripped - Oio Sub | 2011-01-29 15:01 | 2011-01-29 | 2011-01-29 15:24 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 42 | 24487 | 934 | 0.03814 | 0.0017152 | 228.5 | 5084 | 2010/2011 | January-2011 | 1 | 2011
24758 | Replace Temp Link @ Pole 289 - Waimahora Rd - Extreme Wind | 2011-01-29 19:45 | 2011-01-29 | 2011-01-30 11:04 | Calculated | T1290 | T1290 - 1 Phase : 5.00 kVA : POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 919 | 4 | 24487 | 3677 | 0.15016 | 0.00016335 | 55 | 50566 | 2010/2011 | January-2011 | 1 | 2011
24753 | Replace Fuse 5604 - Taranui St - Cnr Hihi St | 2011-01-29 20:51 | 2011-01-29 | 2011-01-29 22:31 | Calculated | 5604 | 5604 - Fused Link 5604 |  | 413SEG5604 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 21 | 24487 | 2104 | 0.08592 | 0.0008576 | 50 | 5009 | 2010/2011 | January-2011 | 1 | 2011
24766 | Line Let Go From Sleeve - Taharoa Rd by Old Quarry | 2011-01-30 10:35 | 2011-01-30 | 2011-01-30 12:22 | Calculated | 280 | 280 - Fused Link 280 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 12 | 24487 | 1275 | 0.05207 | 0.00049006 | 118 | 12545 | 2010/2011 | January-2011 | 1 | 2011
24772 | Line Let Go From Sleeve - Taharoa Rd By Old Quarry | 2011-01-30 10:35 | 2011-01-30 | 2011-01-30 15:16 | Calculated | 268 | 268 - Air Break Switch 268 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 280 | 95 | 24487 | 26615 | 1.0869 | 0.0038796 | 750.5 | 210265 | 2010/2011 | January-2011 | 1 | 2011
24767 | Line Let Go From Sleeve - Taharoa Rd by Old Quarry | 2011-01-30 10:36 | 2011-01-30 | 2011-01-30 12:21 | Calculated | SEG277-268 | SEG277-268 - 125SEG277-268 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 13 | 24487 | 1367 | 0.05583 | 0.00053089 | 100 | 10516 | 2010/2011 | January-2011 | 1 | 2011
24773 | Broken L/V X/arm - Kahorekau Rd | 2011-01-30 12:02 | 2011-01-30 | 2011-01-30 16:05 | Calculated | T869 | T869 - 3ph 25kVA POLEMNT |  | 122SEG448-REG34J | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 242 | 3 | 24487 | 726 | 0.02965 | 0.00012251 | 25 | 6057 | 2010/2011 | January-2011 | 1 | 2011
24770 | Line Let Go From Sleeve - Taharoa Rd by Old Quarry | 2011-01-30 12:50 | 2011-01-30 | 2011-01-30 12:52 | Calculated | SEG277-268 | SEG277-268 - 125SEG277-268 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 13 | 24487 | 28 | 0.00114 | 0.00053089 | 100 | 218 | 2010/2011 | January-2011 | 1 | 2011
24769 | Line Let Go From Sleeve - Taharoa Rd by Old Quarry | 2011-01-30 12:51 | 2011-01-30 | 2011-01-30 12:53 | Calculated | 280 | 280 - Fused Link 280 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 12 | 24487 | 25 | 0.00102 | 0.00049006 | 118 | 253 | 2010/2011 | January-2011 | 1 | 2011
24774 | Replace Link 655 - Kuratahi St | 2011-01-30 14:38 | 2011-01-30 | 2011-01-30 15:20 | Calculated | 655 | 655 - Fused Link 655 |  | 116SEG655 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 2 | 24487 | 82 | 0.00335 | 8.1676e-05 | 65 | 2675 | 2010/2011 | January-2011 | 1 | 2011
24779 | Replace Fuse Link 5640 - Taranui Rd | 2011-01-30 18:56 | 2011-01-30 | 2011-01-30 20:50 | Calculated | 5604 | 5604 - Fused Link 5604 |  | 413SEG5604 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation | OH Lines : Pole - Untreated Softwood / Larch | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 21 | 24487 | 2399 | 0.09797 | 0.0008576 | 50 | 5714 | 2010/2011 | January-2011 | 1 | 2011
24780 | OCB 5152 tripped - Ongarue Sub - Transpower | 2011-01-31 05:12 | 2011-01-31 | 2011-01-31 05:22 | Calculated | 5152 | 5152 - Circuit Breaker 5152 |  | No Segment | 514-01 Transpower Ongarue | Rural D | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24487 |  | 0 | 0 |  |  | 2010/2011 | January-2011 | 1 | 2011
24791 | Replace Fuse @Tx 2160 - SH 3 Mokau | 2011-01-31 06:59 | 2011-01-31 | 2011-01-31 08:40 | Calculated | TF2160 | TF2160 - Transformer Fuse: TF2160 |  | 128SEG1620-1634 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 1 | 24487 | 101 | 0.00412 | 4.0838e-05 | 3 | 303 | 2010/2011 | January-2011 | 1 | 2011
24781 | Recloser 474 tripped - Marotiri Rd | 2011-01-31 14:00 | 2011-01-31 | 2011-01-31 14:13 | Calculated | 474 | 474 - Recloser 474 |  | 123SEG441-474 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 134 | 24487 | 1648 | 0.0673 | 0.0054723 | 2013 | 24759 | 2010/2011 | January-2011 | 1 | 2011
24782 | Line Down - Tirohanga Rd | 2011-01-31 14:56 | 2011-01-31 | 2011-01-31 16:24 | Calculated | 473 | 473 - Air Break Switch 473 |  | 123SEG473-695RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 31 | 24487 | 2733 | 0.11161 | 0.001266 | 785 | 69223 | 2010/2011 | January-2011 | 1 | 2011
24794 | Replace H/C Fuse Tx7L1 - Meringa Rd | 2011-02-01 09:15 | 2011-02-01 | 2011-02-01 10:18 | Calculated | 07L01 | 07L01 - 1 Phase : 50.00 kVA : POLEMNT |  | 408SEG5639-5485 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 7 | 24484 | 441 | 0.01801 | 0.0002859 | 50 | 3149 | 2010/2011 | February-2011 | 2 | 2011
24795 | Magpie - Karangahape Rd | 2011-02-01 09:31 | 2011-02-01 | 2011-02-01 13:04 | Calculated | 06S03 | 06S03 - 1 Phase : 15.00 kVA : POLEMNT |  | 426SEG5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 213 | 1 | 24484 | 213 | 0.0087 | 4.0843e-05 | 15 | 3200 | 2010/2011 | February-2011 | 2 | 2011
24797 | Change Leaking Tx8v2 - Mission Bay Sub - at Youth Hostel | 2011-02-01 10:04 | 2011-02-01 | 2011-02-01 11:39 | Calculated | 5905 | 5905 - Earth Working Link 5905 |  | 417SEG5905 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 95 | 30 | 24484 | 2850 | 0.1164 | 0.0012253 | 125 | 11874 | 2010/2011 | February-2011 | 2 | 2011
24822 | Faulty L/A - Oparure Rd | 2011-02-02 05:25 | 2011-02-02 | 2011-02-02 07:16 | Calculated | T2707 | T2707 - 3ph 100kVA POLEMNT |  | 107SEG706-243 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 1 | 24484 | 111 | 0.00453 | 4.0843e-05 | 100 | 11123 | 2010/2011 | February-2011 | 2 | 2011
24824 | Fuse Pulled Apart - Hangatiki East Rd | 2011-02-02 07:46 | 2011-02-02 | 2011-02-02 09:45 | Calculated | T2601 | T2601 - 3ph 50kVA POLEMNT |  | 102SEG175-521 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 5 | 24484 | 595 | 0.0243 | 0.00020421 | 50 | 5958 | 2010/2011 | February-2011 | 2 | 2011
24825 | Possum@Tx 12N5 - SH 47 | 2011-02-02 10:00 | 2011-02-02 | 2011-02-02 12:10 | Calculated | 12N05 | 12N05 - 3 Phase : 200.00 kVA : POLEMNT |  | 609SEG5159-6761 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 130 | 5 | 24484 | 650 | 0.02655 | 0.00020421 | 200 | 26030 | 2010/2011 | February-2011 | 2 | 2011
24826 | Wind - Waitete Rd | 2011-02-02 13:55 | 2011-02-02 | 2011-02-02 14:35 | Calculated | T2504 | T2504 - 3ph 15kVA POL |  | 103SEG1226 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 1 | 24484 | 40 | 0.00163 | 4.0843e-05 | 15 | 604 | 2010/2011 | February-2011 | 2 | 2011
24827 | Faulty Tx - Waitomo Valley Rd | 2011-02-02 18:09 | 2011-02-02 | 2011-02-02 22:56 | Calculated | T214 | T214 - 3ph 30kVA POLEMNT |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 286 | 5 | 24484 | 1431 | 0.05845 | 0.00020421 | 30 | 8586 | 2010/2011 | February-2011 | 2 | 2011
25010 | Replace Fuse @Tx2160 - SH 3 Mokau | 2011-02-03 06:59 | 2011-02-03 | 2011-02-03 08:40 | Calculated | TF2160 | TF2160 - Transformer Fuse: TF2160 |  | 128SEG1620-1634 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 1 | 24484 | 101 | 0.00413 | 4.0843e-05 | 15 | 1518 | 2010/2011 | February-2011 | 2 | 2011
24835 | Magpie - Kururau Rd | 2011-02-04 08:28 | 2011-02-04 | 2011-02-04 10:35 | Calculated | 08F02 | 08F02 - 1 Phase : 15.00 kVA : POLEMNT |  | 413SEG5123 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 3 | 24484 | 381 | 0.01556 | 0.00012253 | 15 | 1907 | 2010/2011 | February-2011 | 2 | 2011
24837 | Fuse Pulled Apart Tx12S02 - Mt View Cres | 2011-02-04 10:44 | 2011-02-04 | 2011-02-04 11:24 | Calculated | 12S02 | 12S02 - 3 Phase : 100.00 kVA : POLEMNT |  | 424SEG5963 | Rangipo / Hautu 424-03 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 4 | 24484 | 157 | 0.00641 | 0.00016337 | 100 | 3925 | 2010/2011 | February-2011 | 2 | 2011
24838 | Fuse Pulled Apart Tx1646 - Maire Rd | 2011-02-04 12:08 | 2011-02-04 | 2011-02-04 14:58 | Calculated | T1646 | T1646 - 2ph 15kVA POLEMNT |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 4 | 24484 | 681 | 0.02781 | 0.00016337 | 15 | 2554 | 2010/2011 | February-2011 | 2 | 2011
24839 | Replace Link 655 - Kuratahi St | 2011-02-04 21:13 | 2011-02-04 | 2011-02-04 21:42 | Calculated | 655 | 655 - Fused Link 655 |  | 116SEG655 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 2 | 24484 | 58 | 0.00237 | 8.1686e-05 | 65 | 1895 | 2010/2011 | February-2011 | 2 | 2011
24840 | Recloser 277 tripped - Earth Fault - Taharoa Rd by Old Quarry | 2011-02-04 22:57 | 2011-02-04 | 2011-02-04 23:03 | Calculated | 277 | 277 - Recloser with Bypass 277 |  | 125SEG277-268 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 6 | 120 | 24484 | 744 | 0.03039 | 0.0049012 | 968.5 | 6004 | 2010/2011 | February-2011 | 2 | 2011
24857 | Faulty Tx - SH 3 - Mokau | 2011-02-05 06:40 | 2011-02-05 | 2011-02-05 10:05 | Calculated | T2160 | T2160 - 1 Phase : 15.00 kVA : POLEMNT |  | 128SEG1620-1634 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 204 | 1 | 24484 | 204 | 0.00833 | 4.0843e-05 | 15 | 3064 | 2010/2011 | February-2011 | 2 | 2011
24842 | Replace Link 1317 - SH 3 Arapae Spur | 2011-02-05 15:20 | 2011-02-05 | 2011-02-05 15:42 | Calculated | 1317 | 1317 - Fused Link 1317 |  | 117SEG1317 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 22 | 8 | 24484 | 179 | 0.00731 | 0.00032674 | 70 | 1571 | 2010/2011 | February-2011 | 2 | 2011
24843 | Broken Stay - Poihipi Rd | 2011-02-05 17:20 | 2011-02-05 | 2011-02-05 17:57 | Calculated | T3209 | T3209 - 3 Phase : 100.00 kVA : POLEMNT |  | 123SEG699-1267 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 3 | 24484 | 108 | 0.00441 | 0.00012253 | 100 | 3626 | 2010/2011 | February-2011 | 2 | 2011
24844 | CB242 Tripped - Hangatiki | 2011-02-05 23:57 | 2011-02-05 | 2011-02-06 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 318 | 24484 | 688 | 0.0281 | 0.012988 | 2398.5 | 5196 | 2010/2011 | February-2011 | 2 | 2011
24845 | Replace Fuse Tx07I06 - Kellands Rd | 2011-02-06 17:03 | 2011-02-06 | 2011-02-06 18:00 | Calculated | 07I06 | 07I06 - 2 Phase : 10.00 kVA : POLEMNT |  | 402SEG5358 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 2 | 24484 | 114 | 0.00466 | 8.1686e-05 | 10 | 572 | 2010/2011 | February-2011 | 2 | 2011
24848 | Splice in New Conductor @ Pole 1282096 before Mangatoro | 2011-02-07 10:44 | 2011-02-07 | 2011-02-07 16:27 | Calculated | 1631J | 1631J - Incoming Link 1631J |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 10 | 24484 | 3421 | 0.13972 | 0.00040843 | 60 | 20531 | 2010/2011 | February-2011 | 2 | 2011
24846 | Clash - Tihoi Rd - For Barker Rd | 2011-02-07 13:17 | 2011-02-07 | 2011-02-07 15:33 | Calculated | 557 | 557 - Air Break Switch 557 |  | 120SEG557 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 7 | 24484 | 946 | 0.03864 | 0.0002859 | 40 | 5408 | 2010/2011 | February-2011 | 2 | 2011
24849 | Faulty Tx745 - Tihoi Rd | 2011-02-07 15:57 | 2011-02-07 | 2011-02-07 21:51 | Calculated | T745 | T745 - 3 Phase : 30.00 kVA : POLEMNT |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 353 | 70 | 24484 | 5973 | 0.24396 | 0.002859 | 650 | 58622 | 2010/2011 | February-2011 | 2 | 2011
24847 | Faulty Tx745 - Tihoi Rd | 2011-02-07 15:57 | 2011-02-07 | 2011-02-07 21:51 | Calculated | T745 | T745 - 3 Phase : 30.00 kVA : POLEMNT |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 353 | 2 | 24484 | 706 | 0.02884 | 8.1686e-05 | 30 | 10597 | 2010/2011 | February-2011 | 2 | 2011
24913 | Change Poles & X/arms - Paewhenua Rd - By Miller's | 2011-02-08 09:13 | 2011-02-08 | 2011-02-08 16:52 | Calculated | SEG358-TempLink17 | SEG358-TempLink17 - 111SEG358-TempLink17 |  | No Segment | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 436 | 24 | 24484 | 8370 | 0.34186 | 0.00098023 | 150 | 51937 | 2010/2011 | February-2011 | 2 | 2011
24853 | Line Renewal Maintenance - By Waikune Prison | 2011-02-08 09:42 | 2011-02-08 | 2011-02-08 15:55 | Calculated | 5775 | 5775 - Fused Link 5775 |  | 411SEG5775-5329 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 372 | 27 | 24484 | 10051 | 0.41051 | 0.0011028 | 243 | 90460 | 2010/2011 | February-2011 | 2 | 2011
24851 | Pole 131 - Burnt X/arm & Pole - SH 3 South of Junction S/S | 2011-02-08 20:49 | 2011-02-08 | 2011-02-08 21:51 | Calculated | 1619 | 1619 - Fused Link 1619 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAU | Cross-Arm Burnt | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 452 | 24484 | 28129 | 1.1489 | 0.018461 | 2534 | 157699 | 2010/2011 | February-2011 | 2 | 2011
24854 | Replace H/V fuse Tx11E02 - Tokirima Rd | 2011-02-09 04:28 | 2011-02-09 | 2011-02-09 10:34 | Calculated | 11E02 | 11E02 - 1 Phase : 10.00 kVA : POLEMNT |  | 413SEG5646-5883 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 366 | 1 | 24484 | 366 | 0.01495 | 4.0843e-05 | 10 | 3661 | 2010/2011 | February-2011 | 2 | 2011
24915 | Change Poles & X/arms - Paewhenua Rd - By Miller's | 2011-02-09 09:07 | 2011-02-09 | 2011-02-09 14:48 | Calculated | SEGTempLink17-707 | SEG358-TempLink17 - 111SEG358-TempLink17 |  | No Segment | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 298 | 25 | 24484 | 7431 | 0.3035 | 0.0010211 | 155 | 46073 | 2010/2011 | February-2011 | 2 | 2011
24916 | Move Poles for Road Widening - Ngakonui Rd | 2011-02-09 09:54 | 2011-02-09 | 2011-02-09 15:06 | Calculated | SEGTempLink71-5369 | SEGTempLink71-5369 - 402SEGTempLink71-5369 |  | No Segment | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 94 | 24484 | 4304 | 0.17579 | 0.0038392 | 710 | 34422 | 2010/2011 | February-2011 | 2 | 2011
24855 | Replace H/V Fuse Tx938 - Forest Rd | 2011-02-09 17:25 | 2011-02-09 | 2011-02-09 19:21 | Calculated | T938 | T938 - 3 Phase : 15.00 kVA : POLEMNT |  | 123SEG473-695RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 1 | 24484 | 115 | 0.0047 | 4.0843e-05 | 15 | 1729 | 2010/2011 | February-2011 | 2 | 2011
24936 | Changing Poles & X/arms - Taipairu Rd- Before Thompson's Rd | 2011-02-10 09:09 | 2011-02-10 | 2011-02-10 15:23 | Calculated | 247 | 247 - Air Break Switch 247 |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 343 | 50 | 24484 | 8569 | 0.34998 | 0.0020421 | 455 | 99407 | 2010/2011 | February-2011 | 2 | 2011
24856 | Truck vs Line - Pirongia Rd | 2011-02-10 14:54 | 2011-02-10 | 2011-02-10 19:20 | Calculated | 1021X | 1021X - Outgoing Link 1021X |  | 112SEG314-1021 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 236 | 864 | 24484 | 78330 | 3.1992 | 0.035288 | 5518 | 434780 | 2010/2011 | February-2011 | 2 | 2011
24935 | Changing Poles & X/arms - Taipairu Rd - Before Thompson's Rd | 2011-02-11 09:10 | 2011-02-11 | 2011-02-11 14:11 | Calculated | 247 | 247 - Air Break Switch 247 |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 272 | 50 | 24484 | 6782 | 0.277 | 0.0020421 | 455 | 78672 | 2010/2011 | February-2011 | 2 | 2011
24860 | Install New Tx3348 - Otake Rd | 2011-02-11 09:27 | 2011-02-11 | 2011-02-11 15:08 | Calculated | 528 | 528 - Air Break Switch 528 |  | 123SEG490-528 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 341 | 8 | 24484 | 2728 | 0.11142 | 0.00032674 | 80 | 27284 | 2010/2011 | February-2011 | 2 | 2011
24862 | Repair Faulty ABS 5159 - Opposite Chateau Turnoff | 2011-02-11 10:07 | 2011-02-11 | 2011-02-11 13:22 | Calculated | 5158 | 5158 - Air Break Switch 5158 |  | 609SEG5158-5159 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 195 | 113 | 24484 | 22080 | 0.90181 | 0.0046153 | 1136 | 221974 | 2010/2011 | February-2011 | 2 | 2011
24864 | Replace Rotten X/arm On Pole 1111463 - Pukemapou Rd | 2011-02-14 10:08 | 2011-02-14 | 2011-02-14 12:13 | Calculated | 364 | 364 - Fused Link 364 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 124 | 31 | 24484 | 3853 | 0.15737 | 0.0012661 | 260 | 32317 | 2010/2011 | February-2011 | 2 | 2011
24865 | Replace Fuse Tx3268 - Kaeaea Rd | 2011-02-14 11:33 | 2011-02-14 | 2011-02-14 14:09 | Calculated | T3268 | T3268 - 1 Phase : 15.00 kVA : POLEMNT |  | 114SEG1759 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24484 |  | 0 | 0 |  |  | 2010/2011 | February-2011 | 2 | 2011
24867 | Replace H/V Fuses Tx2296 - Huirimu Rd | 2011-02-14 15:25 | 2011-02-14 | 2011-02-14 18:36 | Calculated | T2296 | T2296 - 3ph 50kVA polemnt |  | 121SEG724-425RET | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 3 | 24484 | 573 | 0.0234 | 0.00012253 | 50 | 9556 | 2010/2011 | February-2011 | 2 | 2011
24868 | Replace Fuse Link 5895 - Te Puke Rd | 2011-02-15 08:31 | 2011-02-15 | 2011-02-15 11:10 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 1 | 24484 | 159 | 0.00649 | 4.0843e-05 | 5 | 796 | 2010/2011 | February-2011 | 2 | 2011
24869 | Upgrade Tx - Waikune Prison | 2011-02-15 09:40 | 2011-02-15 | 2011-02-15 15:36 | Calculated | 16L02 | 16L02 - 3 Phase : 200.00 kVA : POLEMNT |  | 411SEG5775-5329 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 8 | 24484 | 2850 | 0.1164 | 0.00032674 | 100 | 35626 | 2010/2011 | February-2011 | 2 | 2011
24872 | Jumper Off @Tx 599 - Mangaorongo Rd | 2011-02-15 13:40 | 2011-02-15 | 2011-02-15 14:42 | Calculated | T599 | T599 - 3ph 25kVA polemnt |  | 111SEG339-346 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 47 | 24484 | 1424 | 0.05816 | 0.0019196 | 498 | 15089 | 2010/2011 | February-2011 | 2 | 2011
24873 | Jumper Off @ Tx04I02 - Tapuwahine Sub | 2011-02-16 17:13 | 2011-02-16 | 2011-02-16 17:48 | Calculated | 5465 | 5465 - Recloser 5465 |  | No Segment | No Asset Group | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 39 | 24484 | 1340 | 0.05473 | 0.0015929 | 255.5 | 8780 | 2010/2011 | February-2011 | 2 | 2011
24875 | Replace Poles 4100002 - 4100018 - National Park North | 2011-02-17 08:22 | 2011-02-17 | 2011-02-17 15:44 | Calculated | 5141 | 5141 - Air Break Switch 5141 |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 403 | 8 | 24484 | 3219 | 0.13147 | 0.00032674 | 37.5 | 15090 | 2010/2011 | February-2011 | 2 | 2011
24874 | Unknown E/F - Kuratau 33s | 2011-02-17 08:40 | 2011-02-17 | 2011-02-17 08:43 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 1275 | 24484 | 2851 | 0.11644 | 0.052075 | 9845.0558 | 22437 | 2010/2011 | February-2011 | 2 | 2011
24917 | Earth Fault - CB992,CB876 and CB180 Tripped | 2011-02-17 08:40 | 2011-02-17 | 2011-02-17 08:44 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 1694 | 24484 | 4995 | 0.20401 | 0.069188 | 23034 | 71638 | 2010/2011 | February-2011 | 2 | 2011
24933 | Change Pole 27, Fit Temp Links@Pole 28 &Reconductor Span - By Ohakune Sub | 2011-02-17 09:13 | 2011-02-17 | 2011-02-17 15:45 | Calculated | SEG5983-TempLink33 | SEG5983-TempLink33 - 415SEG5983-TempLink33 |  | No Segment | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 371 | 429 | 24484 | 5195 | 0.21218 | 0.017522 | 2808 | 32369 | 2010/2011 | February-2011 | 2 | 2011
25003 | Replace 2 Pole Structure Tx656 & Pole 5 | 2011-02-18 09:04 | 2011-02-18 | 2011-02-18 15:56 | Calculated | 216 | 216 - Air Break Switch 216 |  | 104SEG216 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 412 | 30 | 24484 | 12367 | 0.50511 | 0.0012253 | 200 | 82453 | 2010/2011 | February-2011 | 2 | 2011
25008 | Replacing Pole 28 - Burnts St | 2011-02-18 10:06 | 2011-02-18 | 2011-02-18 10:43 | Calculated | Temp Link 33 | Temp Link 33 - Temp Link On Pole 33 |  | THUVVK | No Asset Group | Remote Rural F | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 23 | 24484 | 835 | 0.0341 | 0.00093939 | 155 | 5629 | 2010/2011 | February-2011 | 2 | 2011
25007 | Replace H/V Fuse Tx11S13 - Mangamawhitiwhiti Rd | 2011-02-18 10:11 | 2011-02-18 | 2011-02-18 15:59 | Calculated | TF11S13 | TF11S13 - Transformer Fuse: TF11S13 |  | 427SEG5524 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 348 | 2 | 24484 | 696 | 0.02843 | 8.1686e-05 | 15 | 5222 | 2010/2011 | February-2011 | 2 | 2011
25009 | Replacing Pole 28 - Burnts St | 2011-02-18 15:18 | 2011-02-18 | 2011-02-18 16:08 | Calculated | Temp Link 33 | Temp Link 33 - Temp Link On Pole 33 |  | THUVVK | No Asset Group | Remote Rural F | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 49 | 23 | 24484 | 1134 | 0.04632 | 0.00093939 | 155 | 7644 | 2010/2011 | February-2011 | 2 | 2011
24994 | Install New Tx Structure & Move Tx917 - Allens Rd - Off Waipa Valley | 2011-02-21 10:05 | 2011-02-21 | 2011-02-21 16:07 | Calculated | 449 | 449 - Air Break Switch 449 |  | 103SEG709-453 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 362 | 5 | 24484 | 1812 | 0.07401 | 0.00020421 | 45 | 16308 | 2010/2011 | February-2011 | 2 | 2011
24997 | Fuse Pulled Apart - Ngaroma Rd | 2011-02-21 13:28 | 2011-02-21 | 2011-02-21 15:44 | Calculated | T2299 | T2299 - 1 Phase : 10.00 kVA : POLEMNT |  | 122SEG371-633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 1 | 24484 | 136 | 0.00555 | 4.0843e-05 | 10 | 1362 | 2010/2011 | February-2011 | 2 | 2011
24996 | Stock Rubbing - Waitomo Valley Rd | 2011-02-21 14:02 | 2011-02-21 | 2011-02-21 15:00 | Calculated | TF703 | TF703 - Transformer Fuse: TF703 |  | 112SEG545-326 | Otorohanga 112-05 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AFAR | Farm Animals | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 1 | 24484 | 58 | 0.00237 | 4.0843e-05 | 3 | 174 | 2010/2011 | February-2011 | 2 | 2011
25002 | Tree On Line - Tirohanga Rd | 2011-02-21 15:47 | 2011-02-21 | 2011-02-21 16:23 | Calculated | 477 | 477 - Air Break Switch 477 |  | 129SEG477 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 13 | 24484 | 471 | 0.01924 | 0.00053096 | 115 | 4168 | 2010/2011 | February-2011 | 2 | 2011
24990 | L/V Maintenance - Waikawau Rd | 2011-02-22 10:05 | 2011-02-22 | 2011-02-22 13:42 | Calculated | TF1848 | TF1848 - Transformer Fuse: TF1848 |  | 128SEG1616 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 217 | 5 | 24484 | 1086 | 0.04436 | 0.00020421 | 30 | 6516 | 2010/2011 | February-2011 | 2 | 2011
24991 | Urgent Pole Change - Red Tagged & Rotten X/arm - Mokauiti Rd | 2011-02-22 11:39 | 2011-02-22 | 2011-02-22 16:37 | Calculated | 1716 | 1716 - Recloser with Bypass1716 |  | 115SEG1716-1719 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 141 | 24484 | 9367 | 0.38258 | 0.0057589 | 1023 | 65423 | 2010/2011 | February-2011 | 2 | 2011
24993 | Faulty Tx & Jumper Off The Tx - Rotongata Rd, Wharepapa Rd | 2011-02-22 14:09 | 2011-02-22 | 2011-02-22 16:07 | Calculated | TF1301 | TF1301 - Transformer Fuse: TF1301 |  | 122SEG568-702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 41 | 24484 | 1654 | 0.06755 | 0.0016746 | 435 | 16144 | 2010/2011 | February-2011 | 2 | 2011
24992 | Replace Fuse Tx1514 - Awakino Rd | 2011-02-22 19:48 | 2011-02-22 | 2011-02-22 20:09 | Calculated | TF1514 | TF1514 - Transformer Fuse: TF1514 |  | 104SEG217-730 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 1 | 24484 | 20 | 0.00082 | 4.0843e-05 | 15 | 306 | 2010/2011 | February-2011 | 2 | 2011
24986 | D/C For Safety - Waipapa Rd | 2011-02-23 09:24 | 2011-02-23 | 2011-02-23 16:23 | Calculated | TF673 | TF673 - Transformer Fuse: TF673 |  | No Segment | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 419 | 3 | 24484 | 1257 | 0.05134 | 0.00012253 | 15 | 6289 | 2010/2011 | February-2011 | 2 | 2011
24987 | Changing Poles & X/arms - Rangitoto | 2011-02-23 09:38 | 2011-02-23 | 2011-02-23 14:07 | Calculated | Temp Link 210 | Temp Link 210 - Temp Link On Pole 210 Rangitoto Feeder |  | No Segment | No Asset Group | Remote Rural F | No Feeder |  |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 25 | 24484 | 6729 | 0.27483 | 0.0010211 | 165 | 44415 | 2010/2011 | February-2011 | 2 | 2011
24988 | Re-sag Low Line - Mohakatino - E/W Sub | 2011-02-23 10:35 | 2011-02-23 | 2011-02-23 14:27 | Calculated | 1625 | 1625 - Recloser with Outgoing Link1625 |  | 128SEG1634-REG3 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 232 | 21 | 24484 | 4876 | 0.19915 | 0.0008577 | 122.5 | 28448 | 2010/2011 | February-2011 | 2 | 2011
24982 | Replace Fuse @Tx1775 - Tuhua Rd | 2011-02-24 03:57 | 2011-02-24 | 2011-02-24 04:53 | Calculated | T1775 | T1775 - 1 Phase : 10.00 kVA : POLEMNT |  | 117SEG1298-810 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 3 | 24484 | 168 | 0.00686 | 0.00012253 | 10 | 561 | 2010/2011 | February-2011 | 2 | 2011
24983 | Tree Cutting By Taumata Forestry Contractors | 2011-02-24 09:03 | 2011-02-24 | 2011-02-24 16:10 | Calculated | 5349 | 5349 - Fused Link 5349 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 427 | 20 | 24484 | 8546 | 0.34904 | 0.00081686 | 157.5 | 67299 | 2010/2011 | February-2011 | 2 | 2011
24984 | Changing Poles & X/arms - Taipairu Rd Before Thompson's Rd | 2011-02-24 09:07 | 2011-02-24 | 2011-02-24 15:09 | Calculated | 247 | 247 - Air Break Switch 247 |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 335 | 16 | 24484 | 5348 | 0.21843 | 0.00065349 | 133.3333 | 44566 | 2010/2011 | February-2011 | 2 | 2011
24985 | Fit DDO's & Connect Spur To New Tx3347 - Arataki Rd | 2011-02-24 10:03 | 2011-02-24 | 2011-02-24 13:12 | Calculated | 419 | 419 - Air Break Switch 419 |  | 120SEG419 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 189 | 23 | 24484 | 4350 | 0.17767 | 0.00093939 | 170 | 32158 | 2010/2011 | February-2011 | 2 | 2011
24978 | High Load - Tirohanga Rd | 2011-02-25 06:15 | 2011-02-25 | 2011-02-25 06:35 | Calculated | 473 | 473 - Air Break Switch 473 |  | 123SEG473-695RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 20 | 31 | 24484 | 630 | 0.02573 | 0.0012661 | 785 | 15961 | 2010/2011 | February-2011 | 2 | 2011
24979 | Changing Poles & X/arms - Pururu East Rd | 2011-02-25 09:32 | 2011-02-25 | 2011-02-25 14:17 | Calculated | 675 | 675 - Fused Link 675 |  | 106SEG675 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 6 | 24484 | 1712 | 0.06992 | 0.00024506 | 55 | 15700 | 2010/2011 | February-2011 | 2 | 2011
24981 | Lighting - Waimahora Rd | 2011-02-25 12:43 | 2011-02-25 | 2011-02-25 17:00 | Calculated | T1547 | T1547 - 1 Phase : 30.00 kVA : POLEMNT |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 256 | 1 | 24484 | 256 | 0.01046 | 4.0843e-05 | 30 | 7693 | 2010/2011 | February-2011 | 2 | 2011
24977 | Lighting - Ruru St | 2011-02-26 19:01 | 2011-02-26 | 2011-02-26 20:46 | Calculated | 07D07 | 07D07 - 3ph 50kVA POLEMNT |  | 413SEG5420-5305 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 21 | 24484 | 2189 | 0.08941 | 0.0008577 | 50 | 5214 | 2010/2011 | February-2011 | 2 | 2011
24976 | Lighting - Behind Whakapapa Tavern | 2011-02-27 09:13 | 2011-02-27 | 2011-02-27 10:04 | Calculated | 5330 | 5330 - Fused Link 5330 |  | 419SEG5330 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 30 | 24484 | 1538 | 0.06282 | 0.0012253 | 1525 | 78207 | 2010/2011 | February-2011 | 2 | 2011
24967 | Lighting - Kopaki Rd | 2011-02-28 08:23 | 2011-02-28 | 2011-02-28 09:24 | Calculated | T1833 | T1833 - 1 Phase : 10.00 kVA : POLEMNT |  | 103SEG1335-1301 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 2 | 24484 | 120 | 0.0049 | 8.1686e-05 | 10 | 602 | 2010/2011 | February-2011 | 2 | 2011
24968 | Replace Pole 2 - National Park North | 2011-02-28 08:29 | 2011-02-28 | 2011-02-28 17:14 | Calculated | 5141 | 5141 - Air Break Switch 5141 |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 445 | 8 | 24484 | 3556 | 0.14524 | 0.00032674 | 37.5 | 16671 | 2010/2011 | February-2011 | 2 | 2011
24970 | Changing Poles & X/arms - Sommerville Rd By Symond's | 2011-02-28 09:34 | 2011-02-28 | 2011-02-28 14:33 | Calculated | SEG182-505 | SEG182-505 - 108SEG182-505 |  | No Segment | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 33 | 24484 | 9603 | 0.39222 | 0.0013478 | 369.1667 | 107562 | 2010/2011 | February-2011 | 2 | 2011
24971 | Tree Cutting - Upper Retaruke Rd | 2011-02-28 10:00 | 2011-02-28 | 2011-02-28 12:47 | Calculated | 5334 | 5334 - Fused Link 5334 |  | 410SEG5334-5745 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 151 | 9 | 24484 | 1354 | 0.0553 | 0.00036759 | 65 | 9781 | 2010/2011 | February-2011 | 2 | 2011
24972 | Urgent Pole Replacement - Mokauiti Pole 114 | 2011-02-28 10:46 | 2011-02-28 | 2011-02-28 14:09 | Calculated | 1704 | 1704 - Fused Link 1704 |  | 115SEGTempABS1-1705 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 4 | 24484 | 810 | 0.03308 | 0.00016337 | 35 | 7093 | 2010/2011 | February-2011 | 2 | 2011
24973 | Faulty L/A @ Mahoenui Sub - Wairere | 2011-02-28 12:09 | 2011-02-28 | 2011-02-28 12:10 | Calculated | 798 | 798 - Circuit Breaker 798 |  | No Segment | 207-01 Wairere Falls | Rural D | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Asset Related | Protection | FAIL:FPRO |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 633 | 24484 | 759 | 0.031 | 0.025854 | 3882.5 | 4658 | 2010/2011 | February-2011 | 2 | 2011
24974 | Replace Link 575 - Whataroa Rd | 2011-02-28 14:49 | 2011-02-28 | 2011-02-28 16:55 | Calculated | 575 | 575 - Fused Link 575 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 13 | 24484 | 1641 | 0.06702 | 0.00053096 | 150 | 18937 | 2010/2011 | February-2011 | 2 | 2011
24975 | Replace Fuse @ Tx09K22 - Burnand Rd | 2011-02-28 18:00 | 2011-02-28 | 2011-02-28 18:42 | Calculated | 09K22 | 09K22 - 2ph 10kVA POLEMNT |  | 409SEG5549 | Southern 409-02 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 3 | 24484 | 126 | 0.00515 | 0.00012253 | 10 | 421 | 2010/2011 | February-2011 | 2 | 2011
25081 | Wind - Mangaokewa Rd | 2011-03-01 08:17 | 2011-03-01 | 2011-03-01 10:13 | Calculated | TF1111 | TF1111 - Transformer Fuse: TF1111 |  | 103SEG459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 1 | 24474 | 116 | 0.00474 | 4.086e-05 | 15 | 1743 | 2010/2011 | March-2011 | 3 | 2011
25083 | Tree Cutting By Taumata Forestry Contractors - Whakamaro Rd | 2011-03-01 08:45 | 2011-03-01 | 2011-03-01 16:05 | Calculated | 5321 | 5321 - Fused Link 5321 |  | 403SEG5321-5740 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 419 | 26 | 24474 | 926 | 0.03784 | 0.0010624 | 160 | 10925 | 2010/2011 | March-2011 | 3 | 2011
25084 | Changing Poles & X/arms - Sommerville Rd - By Symond's | 2011-03-01 09:32 | 2011-03-01 | 2011-03-01 15:23 | Calculated | SEG182-505 | SEG182-505 - 108SEG182-505 |  | No Segment | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 351 | 33 | 24474 | 11583 | 0.47328 | 0.0013484 | 369.1667 | 129620 | 2010/2011 | March-2011 | 3 | 2011
24962 | Replace H/V Fuse at Tx06E18 - Waikaka Rd | 2011-03-02 07:53 | 2011-03-02 | 2011-03-02 10:10 | Calculated | 06E18 | 06E18 - 1 Phase : 15.00 kVA : POLEMNT |  | 412SEG6741-5227 | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 137 | 1 | 24474 | 137 | 0.0056 | 4.086e-05 | 15 | 2057 | 2010/2011 | March-2011 | 3 | 2011
25077 | Tractor vs Pillar Box - Harpers Ave | 2011-03-02 11:47 | 2011-03-02 | 2011-03-02 14:21 | Calculated | TF3047 | TF3047 - Transformer Fuse: TF3047 |  | No Segment | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 2 | 24474 | 308 | 0.01258 | 8.1719e-05 | 30 | 4633 | 2010/2011 | March-2011 | 3 | 2011
24965 | Upgrade Tx2662 - Poihipi Rd | 2011-03-02 12:31 | 2011-03-02 | 2011-03-02 14:17 | Calculated | T2662 | T2662 - 3 Phase : 30.00 kVA : POLEMNT |  | 123SEG472-698 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 106 | 2 | 24474 | 212 | 0.00866 | 8.1719e-05 | 30 | 3185 | 2010/2011 | March-2011 | 3 | 2011
25078 | Blown Link 6564 - 2 Phasing - Soldiers Rd | 2011-03-02 16:43 | 2011-03-02 | 2011-03-02 17:07 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 1 | 24474 | 23 | 0.00094 | 4.086e-05 | 3345 | 76935 | 2010/2011 | March-2011 | 3 | 2011
25079 | Pole Down On Sand - Hangatiki | 2011-03-02 17:10 | 2011-03-02 | 2011-03-02 17:12 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24474 |  | 0 | 0 |  |  | 2010/2011 | March-2011 | 3 | 2011
25080 | Suspect Cable/Tx Fault | 2011-03-02 17:30 | 2011-03-02 | 2011-03-02 18:18 | Calculated | TF1463 | TF1463 - Transformer Fuse: TF1463 |  | 112SEG311 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 62 | 24474 | 2988 | 0.12209 | 0.0025333 | 200 | 9639 | 2010/2011 | March-2011 | 3 | 2011
24955 | Scheduled Maintenance - Takarei Tce | 2011-03-03 09:08 | 2011-03-03 | 2011-03-03 16:07 | Calculated | T2155 | T2155 - 3ph 200kVA GNDPAD |  | 128SEG1523 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 419 | 62 | 24474 | 25986 | 1.0618 | 0.0025333 | 200 | 83826 | 2010/2011 | March-2011 | 3 | 2011
24956 | Tree Cutting By Taumata Forestry Contactors - Main North Highway - Past Tapuwahine Rd | 2011-03-03 09:09 | 2011-03-03 | 2011-03-03 16:08 | Calculated | 5434 | 5434 - Fused Link 5434 |  | 421SEG5434-5851 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 418 | 18 | 24474 | 7530 | 0.30767 | 0.00073547 | 115 | 48114 | 2010/2011 | March-2011 | 3 | 2011
24959 | Fuse Pulled Apart - Ongarue Stream Rd | 2011-03-03 13:07 | 2011-03-03 | 2011-03-03 15:42 | Calculated | 01M04 | 01M04 - 1 Phase : 10.00 kVA : POLEMNT |  | 421SEG5362-5933 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 2 | 24474 | 308 | 0.01258 | 8.1719e-05 | 10 | 1542 | 2010/2011 | March-2011 | 3 | 2011
24960 | Replace H/V Fuse @Tx2535 - Paro Rd | 2011-03-03 20:31 | 2011-03-03 | 2011-03-03 22:06 | Calculated | T2535 | T2535 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 1 | 24474 | 95 | 0.00388 | 4.086e-05 | 10 | 952 | 2010/2011 | March-2011 | 3 | 2011
24961 | Line Down @ Pole 101 - Marakopa Rd | 2011-03-03 22:22 | 2011-03-03 | 2011-03-03 23:38 | Calculated | 296 | 296 - Recloser with Bypass 296 |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 169 | 24474 | 12866 | 0.5257 | 0.0069053 | 1185 | 90217 | 2010/2011 | March-2011 | 3 | 2011
24953 | Road Side Incoming Solid Out - Mangaorongo Rd | 2011-03-04 07:05 | 2011-03-04 | 2011-03-04 07:06 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 596 | 24474 | 685 | 0.02799 | 0.024352 | 6021 | 6924 | 2010/2011 | March-2011 | 3 | 2011
24951 | Install New ABS For New Cable To New Tx Site - SH 30 McDonalds Rd | 2011-03-04 11:19 | 2011-03-04 | 2011-03-04 13:19 | Calculated | 413 | 413 - Air Break Switch 413 |  | 120SEG465-410 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 78 | 11 | 24474 | 855 | 0.03494 | 0.00044946 | 80 | 6220 | 2010/2011 | March-2011 | 3 | 2011
24954 | Sec5571 Tripped - Tokirima Highway | 2011-03-04 17:11 | 2011-03-04 | 2011-03-04 18:15 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 12 | 24474 | 769 | 0.03142 | 0.00049032 | 100 | 6415 | 2010/2011 | March-2011 | 3 | 2011
24947 | Magpie@Tx8F5 - Tokirima Highway | 2011-03-05 07:06 | 2011-03-05 | 2011-03-05 09:00 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 31 | 24474 | 1831 | 0.07481 | 0.0012667 | 213 | 14165 | 2010/2011 | March-2011 | 3 | 2011
24950 | Replace Insulators on Taharoa B - Hangatiki | 2011-03-05 09:37 | 2011-03-05 | 2011-03-05 14:57 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24474 |  | 0 | 0 |  |  | 2010/2011 | March-2011 | 3 | 2011
24949 | Birds - Paro Rd | 2011-03-05 14:06 | 2011-03-05 | 2011-03-05 16:20 | Calculated | T2535 | T2535 - 1 Phase : 10.00 kVA : POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 134 | 1 | 24474 | 134 | 0.00548 | 4.086e-05 | 10 | 1341 | 2010/2011 | March-2011 | 3 | 2011
24948 | Magpie@Tx8F5 - Tokirima Highway | 2011-03-05 18:16 | 2011-03-05 | 2011-03-05 19:53 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 12 | 24474 | 1166 | 0.04764 | 0.00049032 | 100 | 9716 | 2010/2011 | March-2011 | 3 | 2011
25086 | Magpie @ Tx08F05 & 08F02 @ Tokirima Highway | 2011-03-07 08:11 | 2011-03-07 | 2011-03-07 09:24 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 12 | 24474 | 868 | 0.03547 | 0.00049032 | 100 | 7233 | 2010/2011 | March-2011 | 3 | 2011
25087 | Change Tx 2135 - Awakau Rd | 2011-03-07 09:10 | 2011-03-07 | 2011-03-07 10:25 | Calculated | TF2135 | TF2135 - Transformer Fuse: TF2135 |  | 128SEG1623-1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 75 | 3 | 24474 | 225 | 0.00919 | 0.00012258 | 15 | 1127 | 2010/2011 | March-2011 | 3 | 2011
25091 | Change Rec 5799 & Reconfigure To Secondary Side - Oio Sub | 2011-03-07 09:35 | 2011-03-07 | 2011-03-07 14:00 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 265 | 42 | 24474 | 11138 | 0.4551 | 0.0017161 | 228.5 | 60598 | 2010/2011 | March-2011 | 3 | 2011
25092 | Replace Fused Link 5895 - Te Puke Rd | 2011-03-07 10:13 | 2011-03-07 | 2011-03-07 14:38 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 265 | 1 | 24474 | 265 | 0.01083 | 4.086e-05 | 5 | 1328 | 2010/2011 | March-2011 | 3 | 2011
25093 | Change Tx 2161 - SH 3 Mokau | 2011-03-07 11:42 | 2011-03-07 | 2011-03-07 13:16 | Calculated | TF2161 | TF2161 - Transformer Fuse: TF2161 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 6 | 24474 | 565 | 0.02309 | 0.00024516 | 10 | 941 | 2010/2011 | March-2011 | 3 | 2011
25094 | Change Faulty Tx - Paro Rd | 2011-03-07 14:07 | 2011-03-07 | 2011-03-07 15:41 | Calculated | T2535 | T2535 - 1 Phase : 15.00 kVA : POLEMNT |  | 114SEG1117-1121 | Aria 114-06 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 93 | 1 | 24474 | 93 | 0.0038 | 4.086e-05 | 15 | 1397 | 2010/2011 | March-2011 | 3 | 2011
25095 | Change Tx - Mangatoro Rd | 2011-03-07 14:41 | 2011-03-07 | 2011-03-07 16:09 | Calculated | T2213 | T2213 - 1 Phase : 5.00 kVA : POLEMNT |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 1 | 24474 | 88 | 0.0036 | 4.086e-05 | 5 | 440 | 2010/2011 | March-2011 | 3 | 2011
25096 | Jumper Off @Tx1328 - Pukemapou Rd | 2011-03-07 18:19 | 2011-03-07 | 2011-03-07 18:51 | Calculated | 364 | 364 - Fused Link 364 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 31 | 24474 | 999 | 0.04082 | 0.0012667 | 260 | 8384 | 2010/2011 | March-2011 | 3 | 2011
25104 | Replace Link 458 - Tirohanga Rd | 2011-03-08 03:31 | 2011-03-08 | 2011-03-08 06:22 | Calculated | 458 | 458 - Fused Link 458 |  | 129SEG458 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORC | Cold / Snow Loading | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 6 | 24474 | 1027 | 0.04196 | 0.00024516 | 80 | 13701 | 2010/2011 | March-2011 | 3 | 2011
25105 | Changing Poles 28,29,30 & 31 - Walker Rd By Venn's | 2011-03-08 09:02 | 2011-03-08 | 2011-03-08 15:48 | Calculated | 193 | 193 - Air Break Switch 193 |  | 106SEG193RET | Rangitoto 106-03 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 406 | 9 | 24474 | 3655 | 0.14934 | 0.00036774 | 80 | 32492 | 2010/2011 | March-2011 | 3 | 2011
25101 | L/V Line Down - Kawakawa Rd | 2011-03-09 08:57 | 2011-03-09 | 2011-03-09 09:50 | Calculated | TF1274 | TF1274 - Transformer Fuse: TF1274 |  | 123SEG468 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 3 | 24474 | 159 | 0.0065 | 0.00012258 | 15 | 799 | 2010/2011 | March-2011 | 3 | 2011
25102 | Replace Pole 1071044 - Te Kumi Nth of Tregoweth's Mill | 2011-03-09 09:28 | 2011-03-09 | 2011-03-09 12:20 | Calculated | 223 | 223 - Air Break Switch 223 |  | 107SEG223-233 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 122 | 9 | 24474 | 1092 | 0.04462 | 0.00036774 | 65 | 7888 | 2010/2011 | March-2011 | 3 | 2011
25103 | Connect New L/V Cable Into Tx 20k24 - Mangarewa Rd | 2011-03-09 10:04 | 2011-03-09 | 2011-03-09 10:39 | Calculated | 5670 | 5670 - Fused Link 5670 |  | 415SEG5670 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 34 | 8 | 24474 | 273 | 0.01115 | 0.00032688 | 60 | 2052 | 2010/2011 | March-2011 | 3 | 2011
25122 | Fault Zone Extended - Borough Sub | 2011-03-09 22:14 | 2011-03-09 | 2011-03-09 22:42 | Calculated | 5951 | 5951 - Circuit Breaker T2 Incomer 5951 |  | No Segment | 508-01 Borough | Rural B | No Feeder |  |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 27 | 3021 | 24474 | 80235 | 3.2784 | 0.12344 | 20280.5 | 538086 | 2010/2011 | March-2011 | 3 | 2011
25114 | T1 & T2 Income - Borough Sub | 2011-03-09 22:15 | 2011-03-09 | 2011-03-09 22:41 | Calculated | 5955 | 5955 - Circuit Breaker Northern 5955 |  | No Segment | 508-01 Borough | Rural B | Northern | Borough Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 3092 | 24474 | 79493 | 3.2481 | 0.12634 | 24070.3484 | 616955 | 2010/2011 | March-2011 | 3 | 2011
25097 | Replace Links 705 & 397 - Ducks | 2011-03-10 07:00 | 2011-03-10 | 2011-03-10 07:44 | Calculated | 5705 | 5705 - Fused Link 5705 |  | 415SEG5705 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 19 | 24474 | 826 | 0.03375 | 0.00077633 | 125 | 5437 | 2010/2011 | March-2011 | 3 | 2011
25098 | Replace Rotten X/arm On Pole 70/70 - Ongarue Back Rd | 2011-03-10 08:59 | 2011-03-10 | 2011-03-10 09:28 | Calculated | 5777 | 5777 - Fused Link 5777 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 29 | 11 | 24474 | 323 | 0.0132 | 0.00044946 | 70 | 2055 | 2010/2011 | March-2011 | 3 | 2011
25099 | Replace H/V Fuse @Tx2470 - Fraser Smith Rd | 2011-03-10 09:34 | 2011-03-10 | 2011-03-10 11:46 | Calculated | TF2470 | TF2470 - Transformer Fuse: TF2470 |  | 128SEG1609-1619 | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 1 | 24474 | 132 | 0.00539 | 4.086e-05 | 10 | 1322 | 2010/2011 | March-2011 | 3 | 2011
25187 | Rangipo/Hautu Feeder Renewal Project - Tuapehi Rd | 2011-03-10 14:48 | 2011-03-10 | 2011-03-11 03:01 | Calculated | SEG5963 | SEG5963 - 424SEG5963 |  | No Segment | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 197 | 340 | 24474 | 60330 | 2.4651 | 0.013892 | 1750 | 305191 | 2010/2011 | March-2011 | 3 | 2011
25100 | Trees - Waipa Valley Rd | 2011-03-10 18:48 | 2011-03-10 | 2011-03-10 20:34 | Calculated | TF2320 | TF2320 - Transformer Fuse: TF2320 |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 1 | 24474 | 106 | 0.00433 | 4.086e-05 | 5 | 531 | 2010/2011 | March-2011 | 3 | 2011
25125 | Broken DDO @ Tx 08I63 - Main North Rd | 2011-03-11 12:43 | 2011-03-11 | 2011-03-11 14:25 | Calculated | 5482 | 5482 - Fused Link 5482 |  | 402SEG5984-5484 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 12 | 24474 | 1225 | 0.05005 | 0.00049032 | 68 | 6943 | 2010/2011 | March-2011 | 3 | 2011
25126 | Replace H/V Fuse Tx 703 - Waitomo Valley Rd | 2011-03-11 15:52 | 2011-03-11 | 2011-03-11 18:58 | Calculated | TF703 | TF703 - Transformer Fuse: TF703 |  | 112SEG545-326 | Otorohanga 112-05 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 1 | 24474 | 185 | 0.00756 | 4.086e-05 | 3 | 556 | 2010/2011 | March-2011 | 3 | 2011
25127 | Broken DDO @ Link 256 - Ahuroa Rd | 2011-03-12 10:26 | 2011-03-12 | 2011-03-12 11:31 | Calculated | 803 | 803 - Fused Link 803 |  | 106SEG252-803 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 6 | 24474 | 384 | 0.01569 | 0.00024516 | 35 | 2244 | 2010/2011 | March-2011 | 3 | 2011
25128 | Magpie - Tokirima Highway | 2011-03-13 07:50 | 2011-03-13 | 2011-03-13 09:58 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 128 | 12 | 24474 | 1538 | 0.06284 | 0.00049032 | 100 | 12818 | 2010/2011 | March-2011 | 3 | 2011
25129 | Bird - Mangapapa Rd | 2011-03-13 16:31 | 2011-03-13 | 2011-03-13 16:44 | Calculated | TF3G4 | TF3G4 - Transformer Fuse: TF3G4 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 5 | 24474 | 64 | 0.00262 | 0.0002043 | 30 | 389 | 2010/2011 | March-2011 | 3 | 2011
25130 | Replace H/V Fuses Tx 13I09 - Kouturoa Rd | 2011-03-14 08:27 | 2011-03-14 | 2011-03-14 10:04 | Calculated | TF13I09 | TF13I09 - Transformer Fuse: TF13I09 |  | 410SEG5492-5334 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 1 | 24474 | 96 | 0.00392 | 4.086e-05 | 10 | 961 | 2010/2011 | March-2011 | 3 | 2011
25131 | Scheduled Maintenance - Barber Rd | 2011-03-14 09:32 | 2011-03-14 | 2011-03-14 14:38 | Calculated | TF494 | TF494 - Transformer Fuse: TF494 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 3 | 24474 | 916 | 0.03743 | 0.00012258 | 25 | 7635 | 2010/2011 | March-2011 | 3 | 2011
25132 | Line Renewal Maintenance - Replace Pole With Helicopter - By Waikune Prison | 2011-03-14 09:36 | 2011-03-14 | 2011-03-14 13:45 | Calculated | 5775 | 5775 - Fused Link 5775 |  | 411SEG5775-5329 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 27 | 24474 | 6705 | 0.27396 | 0.0011032 | 243 | 60353 | 2010/2011 | March-2011 | 3 | 2011
25133 | Lightning - Blown L/A - Taringamotu Rd | 2011-03-14 10:07 | 2011-03-14 | 2011-03-14 11:30 | Calculated | TF7J21 | TF7J21 - Transformer Fuse: TF7J21 |  | 402SEG5103-5369 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 1 | 24474 | 83 | 0.00339 | 4.086e-05 | 50 | 4162 | 2010/2011 | March-2011 | 3 | 2011
25134 | Bird - Rewa St | 2011-03-14 10:39 | 2011-03-14 | 2011-03-14 11:42 | Calculated | TF973 | TF973 - Transformer Fuse: TF973 |  | No Segment | Mangakino 118-01 | Rural D | Mangakino | Maraetai Zone Substation |  | Birds & Animals | Birds | BANI:BIRD |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 13 | 24474 | 821 | 0.03355 | 0.00053118 | 100 | 6318 | 2010/2011 | March-2011 | 3 | 2011
25135 | Replace H/V Fuse Tx2533 - Tirohanga Rd | 2011-03-15 07:30 | 2011-03-15 | 2011-03-15 08:23 | Calculated | TF2533 | TF2533 - Transformer Fuse: TF2533 |  | 123SEG460-787 | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 2 | 24474 | 104 | 0.00425 | 8.1719e-05 | 30 | 1566 | 2010/2011 | March-2011 | 3 | 2011
25171 | Replace Poles 201 To 201/4 - SH 3 Mokau | 2011-03-15 07:41 | 2011-03-15 | 2011-03-15 17:28 | Calculated | 1620 | 1620 - Recloser 1620 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 472 | 220 | 24474 | 82008 | 3.3508 | 0.0089891 | 990 | 328471 | 2010/2011 | March-2011 | 3 | 2011
25136 | Tree Cutting By Hancock Forestry Contractors - Waimiha | 2011-03-15 08:40 | 2011-03-15 | 2011-03-15 16:01 | Calculated | 5349 | 5349 - Fused Link 5349 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 441 | 20 | 24474 | 8822 | 0.36046 | 0.00081719 | 157.5 | 69481 | 2010/2011 | March-2011 | 3 | 2011
25137 | Pole & X/arm Replacements - SH 49 By Ohakune Sub | 2011-03-15 08:41 | 2011-03-15 | 2011-03-15 17:17 | Calculated | 5702 | 5702 - Air Break Switch 5702 |  | 414SEG5715-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 440 | 431 | 24474 | 878 | 0.03587 | 0.017611 | 2815.5 | 3295 | 2010/2011 | March-2011 | 3 | 2011
25138 | L/V Line Down - Bayley Rd | 2011-03-15 13:22 | 2011-03-15 | 2011-03-15 14:12 | Calculated | TF308 | TF308 - Transformer Fuse: TF308 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 2 | 24474 | 100 | 0.00409 | 8.1719e-05 | 25 | 1255 | 2010/2011 | March-2011 | 3 | 2011
25139 | Low L/V Line - Mangawhio Rd | 2011-03-16 06:49 | 2011-03-16 | 2011-03-16 07:01 | Calculated | TF836 | TF836 - Transformer Fuse: TF836 |  | No Segment | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DICL | Conductor Low - Incorrect Clearances | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 2 | 24474 | 24 | 0.00098 | 8.1719e-05 | 25 | 302 | 2010/2011 | March-2011 | 3 | 2011
25141 | Relocate Pole 225 To Prevent From Slipping - Tapuiwahine Valley Rd | 2011-03-16 07:24 | 2011-03-16 | 2011-03-16 14:52 | Calculated | 1634 | 1634 - Air Break Switch 1634 |  | 128SEG1634-REG3 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 322 | 194 | 24474 | 2118 | 0.08654 | 0.0079268 | 1326 | 38210 | 2010/2011 | March-2011 | 3 | 2011
25140 | Tree Cutting By Hancock Forestry Contractors - Tapuiwahine Rd | 2011-03-16 08:34 | 2011-03-16 | 2011-03-16 16:31 | Calculated | 5739 | 5739 - Sectionaliser with Bypass & Links 5739 |  | 421SEG5436-5434 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 465 | 2 | 24474 | 930 | 0.038 | 8.1719e-05 | 3 | 1395 | 2010/2011 | March-2011 | 3 | 2011
25142 | Replace Red Tagged Pole - Mangawhio Rd | 2011-03-16 11:40 | 2011-03-16 | 2011-03-16 13:38 | Calculated | 421 | 421 - Air Break Switch 421 |  | 121SEG421-424 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 117 | 50 | 24474 | 5890 | 0.24066 | 0.002043 | 429 | 50543 | 2010/2011 | March-2011 | 3 | 2011
25143 | L/V Wrapped in H/V - Marotiri Rd | 2011-03-16 12:29 | 2011-03-16 | 2011-03-23 13:42 | Calculated | CB2 | CB2 - Circuit Breaker Tihoi Feeder CB2 |  | No Segment | 212-01 Marotiri | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10152 | 208 | 24474 | 30156 | 1.2322 | 0.0084988 | 2030.5 | 347461 | 2010/2011 | March-2011 | 3 | 2011
25144 | Rock Dropped On Cable - Soldiers Rd | 2011-03-16 14:40 | 2011-03-16 | 2011-03-17 15:00 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Cable - Underground | FAIL:FCAB |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 1460 | 24474 | 1460 | 0.05966 | 0.059655 | 3345 | 3345 | 2010/2011 | March-2011 | 3 | 2011
25145 | Replace Link 5899 - Waihi E/W Sub | 2011-03-17 06:28 | 2011-03-17 | 2011-03-17 07:00 | Calculated | 5899 | 5899 - Fused Link 5899 |  | 406SEG09R27-5891 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 48 | 24474 | 1544 | 0.06309 | 0.0019613 | 215 | 6915 | 2010/2011 | March-2011 | 3 | 2011
25146 | Replace Pole 138/28 - Mahoe Rd - Past Piggeries | 2011-03-17 09:37 | 2011-03-17 | 2011-03-17 15:30 | Calculated | 552 | 552 - Air Break Switch 552 |  | 101SEG552-290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 352 | 13 | 24474 | 4581 | 0.18718 | 0.00053118 | 95 | 33481 | 2010/2011 | March-2011 | 3 | 2011
25148 | 5417 Tripped - Opatu Sub | 2011-03-19 09:09 | 2011-03-19 | 2011-03-19 10:14 | Calculated | 5417 | 5417 - Recloser 5417 |  | 413SEG5418-5417 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 61 | 24474 | 3976 | 0.16246 | 0.0024924 | 413 | 26920 | 2010/2011 | March-2011 | 3 | 2011
25149 | L/V Fault - Troopers Rd | 2011-03-19 09:22 | 2011-03-19 | 2011-03-19 09:53 | Calculated | TF2723 | TF2723 - Transformer Fuse: TF2723 |  | 107SEG231 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Third Party (includeds unauthorised contractors) |  | 3PAR |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 1 | 24474 | 30 | 0.00123 | 4.086e-05 | 15 | 453 | 2010/2011 | March-2011 | 3 | 2011
25151 | Fuse Pulled Apart - Tunanui Rd | 2011-03-20 13:32 | 2011-03-20 | 2011-03-20 14:09 | Calculated | TF10K1 | TF10K1 - Transformer Fuse: TF10K1 |  | 409SEG5411-5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 1 | 24474 | 37 | 0.00151 | 4.086e-05 | 10 | 372 | 2010/2011 | March-2011 | 3 | 2011
25152 | CB5005 Tripped - Ohakune Sub | 2011-03-20 18:00 | 2011-03-20 | 2011-03-20 18:07 | Calculated | 5005 | 5005 - Circuit Breaker 5005 |  | No Segment | 517-01 Transpower Ohakune | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 876 | 24474 | 6351 | 0.2595 | 0.035793 | 5957.5 | 43191 | 2010/2011 | March-2011 | 3 | 2011
25155 | Replace Poles 104/9 &49 - Remove ABS 1606 - Taumatamaire Rd | 2011-03-21 09:23 | 2011-03-21 | 2011-03-21 13:46 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 262 | 28 | 24474 | 7341 | 0.29995 | 0.0011441 | 195 | 51128 | 2010/2011 | March-2011 | 3 | 2011
25156 | Install 2 New Poles With Links For Cable Terminations | 2011-03-21 10:42 | 2011-03-21 | 2011-03-21 14:49 | Calculated | 5712 | 5712 - Fused Link 5712 |  | 415SEG5712-6323 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 0 | 0 | 24474 |  | 0 | 0 |  |  | 2010/2011 | March-2011 | 3 | 2011
25157 | Bird - Hikumutu Rd | 2011-03-21 11:28 | 2011-03-21 | 2011-03-21 12:54 | Calculated | TF9I17 | TF9I17 - Transformer Fuse: TF9I17 |  | No Segment | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 1 | 24474 | 86 | 0.00351 | 4.086e-05 | 15 | 1292 | 2010/2011 | March-2011 | 3 | 2011
25158 | Broken X/arm To Tx 1469 - Waipa River Rd | 2011-03-21 13:03 | 2011-03-21 | 2011-03-21 14:21 | Calculated | 529 | 529 - Air Break Switch 529 |  | 109SEG529-1727 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 35 | 24474 | 2739 | 0.11191 | 0.0014301 | 358 | 28025 | 2010/2011 | March-2011 | 3 | 2011
25159 | Sectionaliser 5591 Tripped - By Te Roto School | 2011-03-21 20:14 | 2011-03-21 | 2011-03-21 20:59 | Calculated | 5591 | 5591 - Sectionaliser with Bypass & Links 5591 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 52 | 24474 | 2354 | 0.09618 | 0.0021247 | 208 | 9418 | 2010/2011 | March-2011 | 3 | 2011
25160 | H/V Change Over - Turangi | 2011-03-22 08:49 | 2011-03-22 | 2011-03-22 10:56 | Calculated | TF4022 | TF4022 - Transformer Fuse: TF4022 |  | 424SEG5200-5168RET | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 127 | 1 | 24474 | 127 | 0.00519 | 4.086e-05 | 100 | 12716 | 2010/2011 | March-2011 | 3 | 2011
25162 | Replace H/V Fuse Tx8F6 - Kururau St | 2011-03-22 10:28 | 2011-03-22 | 2011-03-22 12:05 | Calculated | TF8F6 | TF8F6 - Transformer Fuse: TF8F6 |  | No Segment | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 1 | 24474 | 96 | 0.00392 | 4.086e-05 | 5 | 480 | 2010/2011 | March-2011 | 3 | 2011
25163 | Replace Rotten X/arms on Pole 57 & 60 - Ongarue Back Rd | 2011-03-23 08:50 | 2011-03-23 | 2011-03-23 14:54 | Calculated | 5777 | 5777 - Fused Link 5777 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 347 | 15 | 24474 | 1857 | 0.07588 | 0.0006129 | 112.5 | 15425 | 2010/2011 | March-2011 | 3 | 2011
25164 | Tree Felling - Upper Retaruke | 2011-03-23 09:01 | 2011-03-23 | 2011-03-23 13:16 | Calculated | 5431 | 5431 - Fused Link 5431 |  | 410SEG5431-5407 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 254 | 58 | 24474 | 14752 | 0.60276 | 0.0023699 | 336 | 85461 | 2010/2011 | March-2011 | 3 | 2011
25165 | H/V Change Over - Club Habitat | 2011-03-23 12:00 | 2011-03-23 | 2011-03-23 13:53 | Calculated | TF10S49 | TF10S49 - Transformer Fuse: TF10S49 |  | 424SEG5200-5168RET | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 1 | 24474 | 113 | 0.00462 | 4.086e-05 | 300 | 33905 | 2010/2011 | March-2011 | 3 | 2011
25166 | Faulty L/A - Tihoi Rd | 2011-03-23 12:20 | 2011-03-23 | 2011-03-23 16:30 | Calculated | TF3349 | TF3349 - Transformer Fuse: TF3349 |  | 124SEG1417 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Protection | FAIL:FPRO |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 251 | 1 | 24474 | 251 | 0.01026 | 4.086e-05 | 50 | 12550 | 2010/2011 | March-2011 | 3 | 2011
25167 | Line Down/Historical Clash - Mahoenui | 2011-03-23 20:13 | 2011-03-23 | 2011-03-24 00:17 | Calculated | 1010 | 1010 - Circuit Breaker Mahoenui 1010 |  | No Segment | 209-01 Mahoenui | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 234 | 633 | 24474 | 92601 | 3.7837 | 0.025864 | 3909.5 | 581543 | 2010/2011 | March-2011 | 3 | 2011
25168 | Replace H/V Fuse Tx2048 - Omaru Rd | 2011-03-24 10:30 | 2011-03-24 | 2011-03-24 12:23 | Calculated | TF2048 | TF2048 - Transformer Fuse: TF2048 |  | 117SEG1729 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 2 | 24474 | 224 | 0.00915 | 8.1719e-05 | 10 | 1122 | 2010/2011 | March-2011 | 3 | 2011
25170 | Connect Gen Set - Rangitoto Rd | 2011-03-24 14:45 | 2011-03-24 | 2011-03-24 14:59 | Calculated | TF3081 | TF3081 - Transformer Fuse: TF3081 |  | No Segment | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 14 | 3 | 24474 | 42 | 0.00172 | 0.00012258 | 15 | 212 | 2010/2011 | March-2011 | 3 | 2011
25174 | Change Poles & X/arms - Waitete | 2011-03-25 08:43 | 2011-03-25 | 2011-03-25 16:40 | Calculated | SEG104-389 | SEG104-389 - 106SEG104-389 |  | No Segment | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 386 | 43 | 24474 | 16550 | 0.67623 | 0.001757 | 140 | 53766 | 2010/2011 | March-2011 | 3 | 2011
25175 | Replace Link 604 - Taranui St By Hihi St | 2011-03-25 15:56 | 2011-03-25 | 2011-03-25 17:42 | Calculated | 5604 | 5604 - Fused Link 5604 |  | 413SEG5604 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 21 | 24474 | 2229 | 0.09108 | 0.00085805 | 50 | 5309 | 2010/2011 | March-2011 | 3 | 2011
25176 | Tree On Line - Haurua Rd | 2011-03-27 05:37 | 2011-03-27 | 2011-03-27 07:31 | Calculated | 1359 | 1359 - Fused Link 1359 |  | 112SEG1359 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 4 | 24474 | 456 | 0.01863 | 0.00016344 | 45 | 5136 | 2010/2011 | March-2011 | 3 | 2011
25177 | Broken X/arm and Line Down - Bell Rd | 2011-03-27 12:48 | 2011-03-27 | 2011-03-27 16:39 | Calculated | 5385 | 5385 - Recloser with Bypass 5385 |  | No Segment | No Asset Group | Remote Rural F | Manunui | Manunui Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 181 | 24474 | 32116 | 1.3122 | 0.0073956 | 1318 | 236438 | 2010/2011 | March-2011 | 3 | 2011
25179 | L/V Line Down - Oturu Rd | 2011-03-28 17:56 | 2011-03-28 | 2011-03-28 19:00 | Calculated | TF1430 | TF1430 - Transformer Fuse: TF1430 |  | 109SEG179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 5 | 24474 | 320 | 0.01308 | 0.0002043 | 15 | 962 | 2010/2011 | March-2011 | 3 | 2011
25181 | Replace 5673 5694 - SH 49 By Lakes Rd | 2011-03-29 08:20 | 2011-03-29 | 2011-03-29 09:13 | Calculated | 5694 | 5694 - Fused Link 5694 |  | 416SEG5694 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 42 | 24474 | 1804 | 0.07371 | 0.0017161 | 280 | 11766 | 2010/2011 | March-2011 | 3 | 2011
25184 | Lower Tap - Waimiha Valley Rd | 2011-03-29 10:57 | 2011-03-29 | 2011-03-29 11:29 | Calculated | TF1J3 | TF1J3 - Transformer Fuse: TF1J3 |  | No Segment | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLI | Faulty Construction or Installation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 1 | 24474 | 32 | 0.00131 | 4.086e-05 | 15 | 486 | 2010/2011 | March-2011 | 3 | 2011
25185 | Magpie - Huia Rd | 2011-03-29 16:27 | 2011-03-29 | 2011-03-29 17:58 | Calculated | 5287 | 5287 - Recloser with Bypass & Links 5287 |  | 413SEG5288-5287 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 31 | 24474 | 2828 | 0.11555 | 0.0012667 | 213 | 19432 | 2010/2011 | March-2011 | 3 | 2011
25186 | Replace H/V Fuse Tx1739 - Kahuwera Rd | 2011-03-29 19:15 | 2011-03-29 | 2011-03-29 20:36 | Calculated | TF1739 | TF1739 - Transformer Fuse: TF1739 |  | 116SEG1306-1303 | Piopio 116-01 | Rural D | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 3 | 24474 | 243 | 0.00993 | 0.00012258 | 25 | 2029 | 2010/2011 | March-2011 | 3 | 2011
25188 | Tree Cutting By Hancock Forestry Contractors - Tapuiwahine Valley Rd | 2011-03-30 08:37 | 2011-03-30 | 2011-03-30 16:21 | Calculated | 5739 | 5739 - Sectionaliser with Bypass & Links 5739 |  | 421SEG5436-5434 | Ongarue 421-02 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 464 | 2 | 24474 | 928 | 0.03792 | 8.1719e-05 | 3 | 1392 | 2010/2011 | March-2011 | 3 | 2011
25189 | Cable Change Over - Raukura St North | 2011-03-30 09:01 | 2011-03-30 | 2011-03-30 10:36 | Calculated | TF11S26 | TF11S26 - Transformer Fuse: TF11S26 |  | 424SEG5200-5168RET | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 67 | 24474 | 6344 | 0.25921 | 0.0027376 | 200 | 18939 | 2010/2011 | March-2011 | 3 | 2011
25190 | Possum - Borough Sub | 2011-03-30 09:16 | 2011-03-30 | 2011-03-30 09:30 | Calculated | 5992 | 5992 - (RC) Circuit Breaker 5992 |  | No Segment | 508-01 Borough | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 14 | 1234 | 24474 | 17522 | 0.71594 | 0.050421 | 9569.5 | 135886 | 2010/2011 | March-2011 | 3 | 2011
25193 | L/V Neutral Fault - Te Anga Rd | 2011-03-30 12:09 | 2011-03-30 | 2011-03-30 13:29 | Calculated | TF624 | TF624 - Transformer Fuse: TF624 |  | No Segment | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 4 | 24474 | 321 | 0.01312 | 0.00016344 | 15 | 1205 | 2010/2011 | March-2011 | 3 | 2011
25196 | Cable Change Over - Raukura St South | 2011-03-31 09:01 | 2011-03-31 | 2011-03-31 10:31 | Calculated | TF11S27 | TF11S27 - Transformer Fuse: TF11S27 |  | 424SEG6650-6651 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 47 | 24474 | 4240 | 0.17325 | 0.0019204 | 200 | 18043 | 2010/2011 | March-2011 | 3 | 2011
25198 | Tree Cutting - Otukou Pa | 2011-03-31 10:13 | 2011-03-31 | 2011-03-31 15:59 | Calculated | 5217 | 5217 - Fused Link 5217 |  | 418SEG5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 346 | 6 | 24474 | 2076 | 0.08482 | 0.00024516 | 50 | 17304 | 2010/2011 | March-2011 | 3 | 2011
25199 | Replace Pole 73/20/2 & Resag Line | 2011-04-01 09:04 | 2011-04-01 | 2011-04-01 12:24 | Calculated | 429 | 429 - Fused Link 429 |  | 129SEG429-721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 200 | 27 | 24519 | 5404 | 0.2204 | 0.0011012 | 310 | 62051 | 2011/2012 | April-2011 | 4 | 2011
25200 | L/V Line Down - Main Nth Rd - Otorohanga | 2011-04-02 16:51 | 2011-04-02 | 2011-04-02 17:16 | Calculated | TF1028 | TF1028 - Transformer Fuse: TF1028 |  | 111SEG335-338 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 4 | 24519 | 96 | 0.00392 | 0.00016314 | 30 | 725 | 2011/2012 | April-2011 | 4 | 2011
25203 | Replace Link 5895 - Te Puke Rd | 2011-04-04 10:23 | 2011-04-04 | 2011-04-04 11:14 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 1 | 24519 | 51 | 0.00208 | 4.0785e-05 | 5 | 255 | 2011/2012 | April-2011 | 4 | 2011
25207 | Broken X/arm @ Tx 830 - Ranginui Rd | 2011-04-05 11:52 | 2011-04-05 | 2011-04-05 13:35 | Calculated | 412 | 412 - Fused Link 412 |  | 121SEG412 | Huirimu 121-04 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 5 | 24519 | 515 | 0.021 | 0.00020392 | 40 | 4124 | 2011/2012 | April-2011 | 4 | 2011
25206 | Broken DDO @Tx2645 - Tihoi Rd - Marotiri Corner | 2011-04-05 18:54 | 2011-04-05 | 2011-04-05 19:13 | Calculated | 700 | 700 - Air Break Switch 700 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 18 | 67 | 24519 | 1267 | 0.05167 | 0.0027326 | 635 | 12012 | 2011/2012 | April-2011 | 4 | 2011
25210 | L/V Maintenance - Waiotaka Rd | 2011-04-06 09:01 | 2011-04-06 | 2011-04-06 11:30 | Calculated | TF10T04 | TF10T04 - Transformer Fuse: TF10T04 |  | 424SEG5917 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 16 | 24519 | 2370 | 0.09666 | 0.00065256 | 50 | 7407 | 2011/2012 | April-2011 | 4 | 2011
25212 | Replace Stub Pole, Pole 11 & X/arm @Pole 10 - SH 49 By Ohakune Sub | 2011-04-06 09:06 | 2011-04-06 | 2011-04-06 18:12 | Calculated | 5005 | 5005 - Circuit Breaker 5005 |  | No Segment | 517-01 Transpower Ohakune | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 512 | 1305 | 24519 | 2797 | 0.11407 | 0.053224 | 8765.5 | 15797 | 2011/2012 | April-2011 | 4 | 2011
25213 | Replace Faulty DDO @ T3R1 - Hingarae Rd | 2011-04-06 09:40 | 2011-04-06 | 2011-04-06 10:23 | Calculated | 5536 | 5536 - Sectionaliser 5536 |  | 124SEG5536 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 43 | 11 | 24519 | 474 | 0.01933 | 0.00044863 | 77.5 | 3342 | 2011/2012 | April-2011 | 4 | 2011
25214 | Replace Blown Link 6564 - Soldiers Rd | 2011-04-06 10:39 | 2011-04-06 | 2011-04-06 11:18 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 2 | 24519 | 78 | 0.00318 | 8.1569e-05 | 0 | 0 | 2011/2012 | April-2011 | 4 | 2011
25215 | Jumper Off @ Tx 2752 - Before Mokau Bridge | 2011-04-06 10:41 | 2011-04-06 | 2011-04-06 10:58 | Calculated | 1620 | 1620 - Recloser 1620 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 232 | 24519 | 3978 | 0.16224 | 0.009462 | 1571 | 26942 | 2011/2012 | April-2011 | 4 | 2011
25216 | Replace Link 5217 - Otukou Pa | 2011-04-06 15:24 | 2011-04-06 | 2011-04-06 16:13 | Calculated | 5217 | 5217 - Fused Link 5217 |  | 418SEG5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 6 | 24519 | 295 | 0.01203 | 0.00024471 | 50 | 2459 | 2011/2012 | April-2011 | 4 | 2011
25217 | Replace Link 6564 - Soldiers Rd | 2011-04-06 17:27 | 2011-04-06 | 2011-04-06 17:39 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 1 | 24519 | 12 | 0.00049 | 4.0785e-05 | 3360 | 40320 | 2011/2012 | April-2011 | 4 | 2011
25218 | OCB 242, 796 Tripped - Hangatiki | 2011-04-07 02:58 | 2011-04-07 | 2011-04-07 03:08 | Calculated | 796 | 796 - Circuit Breaker 796 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24519 |  | 0 | 0 |  |  | 2011/2012 | April-2011 | 4 | 2011
25219 | Recloser 5799 Tripped - Oio Sub | 2011-04-07 07:30 | 2011-04-07 | 2011-04-07 08:47 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 42 | 24519 | 3200 | 0.13051 | 0.001713 | 228.5 | 17411 | 2011/2012 | April-2011 | 4 | 2011
25220 | Replace H/V Fuse Tx 9K16 - Waitea Rd | 2011-04-07 07:45 | 2011-04-07 | 2011-04-07 09:43 | Calculated | TF9K16 | TF9K16 - Transformer Fuse: TF9K16 |  | No Segment | Southern 409-03 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 3 | 24519 | 354 | 0.01444 | 0.00012235 | 15 | 1773 | 2011/2012 | April-2011 | 4 | 2011
25221 | Tree Cutting By Hancock Forestry - Whakamaro Rd | 2011-04-07 08:04 | 2011-04-07 | 2011-04-07 16:33 | Calculated | SEG5812-5321 | SEG5812-5321 - 403SEG5812-5321 |  | No Segment | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 451 | 26 | 24519 | 900 | 0.03671 | 0.0010604 | 160 | 11254 | 2011/2012 | April-2011 | 4 | 2011
25222 | Replace H/V Fuse Tx4H8 - SH 40 | 2011-04-07 08:43 | 2011-04-07 | 2011-04-07 10:33 | Calculated | TF4H8 | TF4H8 - Transformer Fuse: TF4H8 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 1 | 24519 | 110 | 0.00449 | 4.0785e-05 | 15 | 1652 | 2011/2012 | April-2011 | 4 | 2011
25223 | Replace H/V Fuse Tx214 - Tree In L/V | 2011-04-07 13:28 | 2011-04-07 | 2011-04-07 14:24 | Calculated | TF214 | TF214 - Transformer Fuse: TF214 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 5 | 24519 | 280 | 0.01142 | 0.00020392 | 30 | 1684 | 2011/2012 | April-2011 | 4 | 2011
25225 | Faulty ABS 550 - Waitomo Valley Rd | 2011-04-08 04:50 | 2011-04-08 | 2011-04-08 06:02 | Calculated | 318 | 318 - Air Break Switch 318 |  | 112SEG318-550 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 80 | 24519 | 5777 | 0.23561 | 0.0032628 | 728 | 52573 | 2011/2012 | April-2011 | 4 | 2011
25227 | Replace H/V Fuse Tx12K1 (Old Age) - Main South Rd | 2011-04-08 05:46 | 2011-04-08 | 2011-04-08 06:30 | Calculated | TF12K1 | TF12K1 - Transformer Fuse: TF12K1 |  | 410SEG5457 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWF | Service Fuse Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 4 | 24519 | 176 | 0.00718 | 0.00016314 | 15 | 662 | 2011/2012 | April-2011 | 4 | 2011
25228 | L/V Lines Wrapped - Replace H/V Fuse Tx214 - Waitomo Valley Rd | 2011-04-08 09:01 | 2011-04-08 | 2011-04-08 12:14 | Calculated | TF214 | TF214 - Transformer Fuse: TF214 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 5 | 24519 | 966 | 0.0394 | 0.00020392 | 30 | 5798 | 2011/2012 | April-2011 | 4 | 2011
25229 | Replace H/V Fuse Tx11s12 - Magpie Mangamawhitiwhiti Rd | 2011-04-08 09:04 | 2011-04-08 | 2011-04-08 13:03 | Calculated | TF11S12 | TF11S12 - Transformer Fuse: TF11S12 |  | 427SEG5524 | Waiotaka 427-01 | Rural C | Waiotaka | Waiotaka Zone Substation (Containerised) |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 1 | 24519 | 239 | 0.00975 | 4.0785e-05 | 5 | 1195 | 2011/2012 | April-2011 | 4 | 2011
25231 | Vibration -Fuse Fell Out - Ranginui Rd - Lower End | 2011-04-09 12:41 | 2011-04-09 | 2011-04-09 14:32 | Calculated | 412 | 412 - Fused Link 412 |  | 121SEG412 | Huirimu 121-04 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLM | Mechanical Shock or Vibration | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 111 | 5 | 24519 | 556 | 0.02268 | 0.00020392 | 40 | 4450 | 2011/2012 | April-2011 | 4 | 2011
25232 | Replace H/V Fuse Tx7I3 - Golf Rd | 2011-04-11 11:35 | 2011-04-11 | 2011-04-11 11:47 | Calculated | TF7I3 | TF7I3 - Transformer Fuse: TF7I3 |  | 402SEG5484-5118 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 21 | 24519 | 234 | 0.00954 | 0.00085648 | 300 | 3344 | 2011/2012 | April-2011 | 4 | 2011
25480 | Pole 49/67/16 On Fire - Paraheka Rd - Near Aria Township | 2011-04-12 06:10 | 2011-04-12 | 2011-04-12 11:53 | Calculated | 1108 | 1108 - Recloser with Bypass 1108 |  | 114SEG1108-1102 | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOF | Pole Top Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 343 | 63 | 24519 | 11075 | 0.45169 | 0.0025694 | 428 | 79991 | 2011/2012 | April-2011 | 4 | 2011
25482 | Tree Cutting By Hancock Forestry Contractor | 2011-04-13 08:36 | 2011-04-13 | 2011-04-13 16:40 | Calculated | 5349 | 5349 - Fused Link 5349 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 483 | 23 | 24519 | 11123 | 0.45365 | 0.00093805 | 180 | 87057 | 2011/2012 | April-2011 | 4 | 2011
25483 | Remove Pole 4151051 From Edge Of Bank - Soldiers Rd | 2011-04-13 09:31 | 2011-04-13 | 2011-04-13 14:24 | Calculated | 5947 | 5947 - Air Break Switch 5947 |  | 415SEG5947-6617 | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 17 | 24519 | 4967 | 0.20258 | 0.00069334 | 153.3333 | 44809 | 2011/2012 | April-2011 | 4 | 2011
25484 | Replace Link 499 - Aotearoa Rd - Kahorekau Rd | 2011-04-13 11:01 | 2011-04-13 | 2011-04-13 16:09 | Calculated | 499 | 499 - Fused Link 499 |  | 122SEG499 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 308 | 7 | 24519 | 2158 | 0.08801 | 0.00028549 | 52.5 | 16191 | 2011/2012 | April-2011 | 4 | 2011
25485 | Digger vs Line - Tihoi Rd to Paritaniwha Rd | 2011-04-13 12:01 | 2011-04-13 | 2011-04-13 17:10 | Calculated | 580 | 580 - Fused Link 580 |  | 120SEG481-422 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 309 | 9 | 24519 | 2785 | 0.11359 | 0.00036706 | 153.3333 | 47448 | 2011/2012 | April-2011 | 4 | 2011
25486 | Replace Link 6573 - Atirau Road | 2011-04-14 07:50 | 2011-04-14 | 2011-04-14 09:34 | Calculated | 6573 | 6573 - Fused Link 6573 |  | 423SEG5198-5881 | Turangi 423-01 | Rural C | Turangi | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 11 | 24519 | 1146 | 0.04674 | 0.00044863 | 330 | 34391 | 2011/2012 | April-2011 | 4 | 2011
25487 | Repair Damaged Conductor & Run New Span - Hangatiki East Rd | 2011-04-14 10:34 | 2011-04-14 | 2011-04-14 15:07 | Calculated | 764 | 764 - Solid Link 764 |  | 108SEG764 | Waitomo 108-02 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 273 | 14 | 24519 | 3770 | 0.15376 | 0.00057099 | 84.1667 | 22584 | 2011/2012 | April-2011 | 4 | 2011
25488 | Repair Damaged Conductor - Tihio Rd | 2011-04-14 11:46 | 2011-04-14 | 2011-04-14 12:31 | Calculated | 580 | 580 - Fused Link 580 |  | 120SEG481-422 | Whakamaru 120-06 (was 124-02) | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 9 | 24519 | 404 | 0.01648 | 0.00036706 | 153.3333 | 6884 | 2011/2012 | April-2011 | 4 | 2011
25489 | Suspected Overloading - Waiotaka Substation | 2011-04-14 17:54 | 2011-04-14 | 2011-04-14 17:57 | Calculated | 6336 | 6336 - Circuit Breaker Waiotaka 33kV 6336 |  | 606SEG6546-6336 | Lake Taupo 606-01 | Urban A | Lake Taupo 33 | Direct from Tokaanu Supply |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 744 | 24519 | 2418 | 0.09862 | 0.030344 | 5080 | 16509 | 2011/2012 | April-2011 | 4 | 2011
25491 | Replace H/V Fuse - Tx796 - Maraetai Rd | 2011-04-15 07:46 | 2011-04-15 | 2011-04-15 09:06 | Calculated | TF796 | TF796 - Transformer Fuse: TF796 |  | No Segment | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 2 | 24519 | 160 | 0.00653 | 8.1569e-05 | 25 | 2005 | 2011/2012 | April-2011 | 4 | 2011
25493 | Broken DDO@Tx08G07 - Otunui South Rd | 2011-04-16 09:55 | 2011-04-16 | 2011-04-16 11:29 | Calculated | 5740 | 5740 - Sectionaliser with Bypass & Links 5740 |  | 403SEG5740-5546 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 25 | 24519 | 2355 | 0.09605 | 0.0010196 | 138.75 | 13072 | 2011/2012 | April-2011 | 4 | 2011
25494 | Recloser 5378 Tripped - Kirikau Sub | 2011-04-16 11:00 | 2011-04-16 | 2011-04-16 11:37 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 70 | 24519 | 2601 | 0.10608 | 0.0028549 | 430.5 | 16000 | 2011/2012 | April-2011 | 4 | 2011
25495 | Goose at Tx3295 - Seafund Rd | 2011-04-17 06:21 | 2011-04-17 | 2011-04-17 07:42 | Calculated | 1652 | 1652 - Fused Link 1652 |  | 122SEG398-380 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 2 | 24519 | 162 | 0.00661 | 8.1569e-05 | 30 | 2442 | 2011/2012 | April-2011 | 4 | 2011
25496 | Tree Cutting - Haurua Rd | 2011-04-18 08:13 | 2011-04-18 | 2011-04-18 09:19 | Calculated | 1359 | 1359 - Fused Link 1359 |  | 112SEG1359 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 66 | 4 | 24519 | 264 | 0.01077 | 0.00016314 | 45 | 2970 | 2011/2012 | April-2011 | 4 | 2011
25498 | Replace HV Fuse at Tx900 - Oparure Rd | 2011-04-18 09:20 | 2011-04-18 | 2011-04-18 14:30 | Calculated | TF900 | TF900 - Transformer Fuse: TF900 |  | 107SEG262-176 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 310 | 1 | 24519 | 310 | 0.01264 | 4.0785e-05 | 15 | 4650 | 2011/2012 | April-2011 | 4 | 2011
25499 | LV Line Down - Main North Rd | 2011-04-18 09:47 | 2011-04-18 | 2011-04-18 10:26 | Calculated | TF7I30 | TF7I30 - Transformer Fuse: TF7I30 |  | 402SEG5480 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:EFPL | Fault on Private Line - Affecting Network | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 8 | 24519 | 312 | 0.01272 | 0.00032628 | 50 | 1950 | 2011/2012 | April-2011 | 4 | 2011
25501 | Broken Pole at Tx1601 - Nukuhakari Tap Off - On Hill Before School | 2011-04-18 10:01 | 2011-04-18 | 2011-04-18 23:36 | Calculated | 1615 | 1615 - Sectionaliser with Bypass & Links 1615 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 815 | 41 | 24519 | 15783 | 0.6437 | 0.0016722 | 302.5 | 128998 | 2011/2012 | April-2011 | 4 | 2011
25502 | Wind - Tirohanga Rd | 2011-04-18 14:23 | 2011-04-18 | 2011-04-18 15:57 | Calculated | TF722 | TF722 - Transformer Fuse: TF722 |  | 120SEG408-465 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 3 | 24519 | 279 | 0.01138 | 0.00012235 | 22.5 | 2097 | 2011/2012 | April-2011 | 4 | 2011
25503 | Line Down - Opatu Sub | 2011-04-18 14:51 | 2011-04-18 | 2011-04-18 18:09 | Calculated | 5417 | 5417 - Recloser 5417 |  | 413SEG5418-5417 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 197 | 68 | 24519 | 7387 | 0.30128 | 0.0027734 | 459.5556 | 53155 | 2011/2012 | April-2011 | 4 | 2011
25504 | High Wind - Oruruwhero Rd | 2011-04-18 15:53 | 2011-04-18 | 2011-04-18 17:15 | Calculated | TF224 | TF224 - Transformer Fuse: TF224 |  | 112SEG637-352 | Otorohanga 112-07 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 5 | 24519 | 411 | 0.01676 | 0.00020392 | 50 | 4114 | 2011/2012 | April-2011 | 4 | 2011
25505 | High Winds - Hikurangi Sub | 2011-04-18 18:41 | 2011-04-18 | 2011-04-18 19:49 | Calculated | 5370 | 5370 - Recloser with Bypass & Links 5370 |  | 402SEG5370-5199 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 84 | 24519 | 5733 | 0.23382 | 0.0034259 | 632.5 | 43168 | 2011/2012 | April-2011 | 4 | 2011
25506 | High Winds - Oio Sub | 2011-04-18 19:21 | 2011-04-18 | 2011-04-18 20:09 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 47 | 24519 | 2266 | 0.09242 | 0.0019169 | 239.75 | 11563 | 2011/2012 | April-2011 | 4 | 2011
25511 | Broken Insulator/Tree/Line Down - Huirimu Feeder | 2011-04-18 23:30 | 2011-04-18 | 2011-04-19 05:48 | Calculated | 1072 | 1072 - Circuit Breaker 1072 Huirimu |  | 121SEG1072-753 | 211-01 Arohena | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 378 | 159 | 24519 | 32581 | 1.3288 | 0.0064848 | 1668.1667 | 332052 | 2011/2012 | April-2011 | 4 | 2011
25512 | Replace Red Tagged Pole 1031269 | 2011-04-19 10:11 | 2011-04-19 | 2011-04-19 14:35 | Calculated | 1733 | 1733 - Fused Link 1733 |  | 103SEG1726-1733 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 248 | 7 | 24519 | 1730 | 0.07056 | 0.00028549 | 30 | 7414 | 2011/2012 | April-2011 | 4 | 2011
25518 | Replace Stub Pole, Pole 11 & X/arm @ Pole 10 - SH 49 By Ohakune | 2011-04-20 08:39 | 2011-04-20 | 2011-04-20 16:19 | Calculated | 5702 | 5702 - Air Break Switch 5702 |  | 414SEG5715-5925RET | Ohakune Town 414-01 | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 356 | 26 | 24519 | 9192 | 0.37489 | 0.0010604 | 600 | 212839 | 2011/2012 | April-2011 | 4 | 2011
25513 | Replace LV Pole - Te Kawa St | 2011-04-20 09:33 | 2011-04-20 | 2011-04-20 15:00 | Calculated | TF170 | TF170 - Transformer Fuse: TF170 |  | 112SEG311 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 64 | 24519 | 20945 | 0.85424 | 0.0026102 | 203.1746 | 66492 | 2011/2012 | April-2011 | 4 | 2011
25520 | Recloser 564 Tripped - Kiritihere - By Junction | 2011-04-20 10:30 | 2011-04-20 | 2011-04-20 12:42 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 19 | 24519 | 2509 | 0.10233 | 0.00077491 | 160 | 21133 | 2011/2012 | April-2011 | 4 | 2011
25260 | Tree On Line @ Tx08I40 - Kururau Rd | 2011-04-21 14:31 | 2011-04-21 | 2011-04-21 18:28 | Calculated | 6041 | 6041 - Recloser 6041 |  | 403SEG6041-6037 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 237 | 277 | 24519 | 48582 | 1.9814 | 0.011297 | 2026.619 | 359015 | 2011/2012 | April-2011 | 4 | 2011
25258 | Replace H/V Fuse Tx08R12 - Tukino St | 2011-04-22 17:55 | 2011-04-22 | 2011-04-22 19:23 | Calculated | TF8R12 | TF8R12 - Transformer Fuse: TF8R12 |  | 406SEG6558-5921 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 52 | 24519 | 4586 | 0.18704 | 0.0021208 | 200 | 17639 | 2011/2012 | April-2011 | 4 | 2011
25255 | Sect 5277 Tripped - Fauchelle Rd | 2011-04-23 13:31 | 2011-04-23 | 2011-04-23 14:56 | Calculated | 5277 | 5277 - Sectionaliser with Bypass & Links5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 17 | 24519 | 1448 | 0.05906 | 0.00069334 | 150 | 12784 | 2011/2012 | April-2011 | 4 | 2011
25256 | L/V Cable Fault - Awakino Rd | 2011-04-23 17:09 | 2011-04-23 | 2011-04-23 17:57 | Calculated | TF2464 | TF2464 - Transformer Fuse: TF2464 |  | 104SEG214-639 | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 27 | 24519 | 1304 | 0.05318 | 0.0011012 | 207.6923 | 10034 | 2011/2012 | April-2011 | 4 | 2011
25257 | Replace Link 485 - Waituhi Rd | 2011-04-23 17:21 | 2011-04-23 | 2011-04-23 18:18 | Calculated | 5485 | 5485 - Fused Link 5485 |  | 408SEG5485-5791 | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 22 | 24519 | 1256 | 0.05123 | 0.00089726 | 172.5 | 9852 | 2011/2012 | April-2011 | 4 | 2011
25254 | Suspect Faulty Sect 5277 - Fauchelle Rd | 2011-04-24 18:21 | 2011-04-24 | 2011-04-24 20:22 | Calculated | 5277 | 5277 - Sectionaliser with Bypass & Links5277 |  | 422SEG5277-5929 | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 17 | 24519 | 2060 | 0.08402 | 0.00069334 | 150 | 18177 | 2011/2012 | April-2011 | 4 | 2011
25253 | Bolt Out Of X/arm @P33 - Tuhua Sub | 2011-04-25 06:25 | 2011-04-25 | 2011-04-25 09:30 | Calculated | 6640 | 6640 - Air Break Switch 6640 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAN | Cross-Arm Nut Missing/Loose | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 285 | 24519 | 50824 | 2.0728 | 0.011624 | 1965.75 | 352998 | 2011/2012 | April-2011 | 4 | 2011
25334 | Extreme Wind - Tree On Line - Paewhenua Rd | 2011-04-26 07:30 | 2011-04-26 | 2011-04-26 11:35 | Calculated | 399 | 399 - Air Break Switch 399 |  | 111SEG707-399 | Maihiihi 111-14 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 245 | 33 | 24519 | 8087 | 0.32983 | 0.0013459 | 459.1667 | 112534 | 2011/2012 | April-2011 | 4 | 2011
25335 | Extreme Wind - Tree On Line - Paewhenua Rd | 2011-04-26 07:30 | 2011-04-26 | 2011-04-26 14:56 | Calculated | SEG707-399 | SEG707-399 - 111SEG707-399 |  | No Segment | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 446 | 19 | 24519 | 8475 | 0.34565 | 0.00077491 | 235 | 104829 | 2011/2012 | April-2011 | 4 | 2011
25336 | Extreme Wind - Tree On Line - Paewhenua Rd | 2011-04-26 07:30 | 2011-04-26 | 2011-04-26 16:36 | Calculated | 368 | 368 - Fused Link 368 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 546 | 15 | 24519 | 8191 | 0.33407 | 0.00061177 | 132.5 | 72356 | 2011/2012 | April-2011 | 4 | 2011
25337 | Extreme Wind - Pole Down - Paewhenua Rd | 2011-04-26 07:30 | 2011-04-26 | 2011-04-26 20:53 | Calculated | 368 | 368 - Fused Link 368 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 803 | 22 | 24519 | 17667 | 0.72054 | 0.00089726 | 230 | 184709 | 2011/2012 | April-2011 | 4 | 2011
25333 | Extreme Wind - Tree On Line - Paewhenua Rd | 2011-04-26 07:30 | 2011-04-26 | 2011-04-26 08:47 | Calculated | 117 | 117 - Circuit Breaker 117 |  | 111SEG647-117RET | Maihiihi 111-10 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 128 | 24519 | 9866 | 0.40238 | 0.0052204 | 1084.1667 | 83571 | 2011/2012 | April-2011 | 4 | 2011
25331 | Extreme Wind Line Down - Sandel Rd | 2011-04-26 07:30 | 2011-04-26 | 2011-04-26 14:28 | Calculated | 2102 | 2102 - Circuit Breaker Mareatai 11 kV 2102 |  | No Segment | 210-01 Maraetai | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 417 | 601 | 24519 | 26736 | 1.0904 | 0.024512 | 4681.8889 | 289850 | 2011/2012 | April-2011 | 4 | 2011
25332 | Extreme Wind - Tree Down x 2 - Mangaorongo Rd | 2011-04-26 07:58 | 2011-04-26 | 2011-04-26 16:08 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 490 | 373 | 24519 | 45364 | 1.8502 | 0.015213 | 4038.5 | 524190 | 2011/2012 | April-2011 | 4 | 2011
25338 | Extreme Wind - Pole Down - Otewa Rd | 2011-04-26 08:14 | 2011-04-26 | 2011-04-26 10:33 | Calculated | 116 | 116 - Recloser with Bypass 116 |  | 109SEG541-116 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 25 | 24519 | 3478 | 0.14185 | 0.0010196 | 260 | 36174 | 2011/2012 | April-2011 | 4 | 2011
25339 | Extreme Wind - Pole Down - Otewa Rd | 2011-04-26 08:14 | 2011-04-26 | 2011-04-27 13:02 | Calculated | 171 | 171 - Fused Link 171 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1728 | 15 | 24519 | 25922 | 1.0572 | 0.00061177 | 145 | 250579 | 2011/2012 | April-2011 | 4 | 2011
25340 | Extreme Wind - Pole Down - Otewa Rd | 2011-04-26 08:14 | 2011-04-26 | 2011-04-29 14:48 | Calculated | T839 | T839 - 1 Phase : 15.00 kVA : POLEMNT |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4714 | 6 | 24519 | 28284 | 1.1536 | 0.00024471 | 40 | 188565 | 2011/2012 | April-2011 | 4 | 2011
25341 | Extreme Wind - Line Down - Wharepapa Feeder | 2011-04-26 08:37 | 2011-04-26 | 2011-04-26 14:55 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 378 | 316 | 24519 | 28417 | 1.159 | 0.012888 | 2602.25 | 217049 | 2011/2012 | April-2011 | 4 | 2011
25343 | Extreme Wind - Recloser 467 Tripped - Okahukura Sub | 2011-04-26 08:41 | 2011-04-26 | 2011-04-26 09:38 | Calculated | 5467 | 5467 - Recloser with Bypass & Links 5467 |  | 402SEG5467-5472 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 72 | 24519 | 4099 | 0.16718 | 0.0029365 | 486.75 | 27712 | 2011/2012 | April-2011 | 4 | 2011
25342 | Bark at ABS 1029 - Waihora Rd | 2011-04-26 09:15 | 2011-04-26 | 2011-04-26 11:32 | Calculated | 446 | 446 - Recloser 446 |  | 123SEG466-145 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 187 | 24519 | 24066 | 0.98152 | 0.0076267 | 1577.5 | 201729 | 2011/2012 | April-2011 | 4 | 2011
25344 | Extreme Wind - P/L L/V Poles Leaning | 2011-04-26 09:27 | 2011-04-26 | 2011-04-27 15:03 | Calculated | TF282 | TF282 - Transformer Fuse: TF282 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1776 | 4 | 24519 | 7104 | 0.28973 | 0.00016314 | 30 | 53287 | 2011/2012 | April-2011 | 4 | 2011
25348 | Extreme Wind - Poles Down - Turangi Sub | 2011-04-26 09:34 | 2011-04-26 | 2011-04-26 10:20 | Calculated | 5200 | 5200 - Circuit Breaker 5200 |  | No Segment | 505-01 Turangi | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 636 | 24519 | 29298 | 1.1949 | 0.025939 | 7017.6 | 323277 | 2011/2012 | April-2011 | 4 | 2011
25346 | Extreme Wind - Poles Down - Turangi Sub | 2011-04-26 09:34 | 2011-04-26 | 2011-04-26 10:06 | Calculated | 5198 | 5198 - Circuit Breaker 5198 |  | No Segment | 505-01 Turangi | Rural C | Turangi | Turangi Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 1119 | 24519 | 35882 | 1.4634 | 0.045638 | 5508.3097 | 176633 | 2011/2012 | April-2011 | 4 | 2011
25345 | Extreme Wind - Poles Down - Turangi Sub | 2011-04-26 09:34 | 2011-04-26 | 2011-04-26 09:46 | Calculated | 5168 | 5168 - Circuit Breaker with Bypass 5168 |  | 424SEG6652-5168 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 196 | 24519 | 2195 | 0.08952 | 0.0079938 | 1050.0264 | 11760 | 2011/2012 | April-2011 | 4 | 2011
25349 | Extreme Wind - Poles Down - Turangi Sub | 2011-04-26 09:35 | 2011-04-26 | 2011-04-26 17:25 | Calculated | 5207 | 5207 - Air Break Switch 5207 |  | 424SEG5207-6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 470 | 43 | 24519 | 20211 | 0.8243 | 0.0017537 | 447.5 | 210339 | 2011/2012 | April-2011 | 4 | 2011
25350 | Extreme Wind - Line Down - Mount Pihanga | 2011-04-26 09:35 | 2011-04-26 | 2011-04-28 18:00 | Calculated | 11R03 | 11R03 - 1 Phase : 15.00 kVA : POLEMNT |  | 424SEG5207-6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3385 | 8 | 24519 | 27081 | 1.1045 | 0.00032628 | 90 | 304665 | 2011/2012 | April-2011 | 4 | 2011
25353 | Tree Through Line - Tawhai Sub | 2011-04-26 10:02 | 2011-04-26 | 2011-04-26 14:51 | Calculated | SEG5158-5159 | SEG5158-5159 - 609SEG5158-5159 |  | No Segment | National Park / Kuratau 609-02 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 289 | 10 | 24519 | 2893 | 0.11799 | 0.00040785 | 80 | 23144 | 2011/2012 | April-2011 | 4 | 2011
25352 | Tree Through Line - Otukau Sub | 2011-04-26 10:02 | 2011-04-26 | 2011-04-26 14:01 | Calculated | 5834 | 5834 - Solid Link 5834 |  | 418SEG512T1-5836 | 512-01 Otukou | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 239 | 96 | 24519 | 22951 | 0.93605 | 0.0039153 | 681 | 162815 | 2011/2012 | April-2011 | 4 | 2011
25354 | Tree Through Line - Tauwera | 2011-04-26 10:03 | 2011-04-26 | 2011-04-27 14:36 | Calculated | 12N05 | 12N05 - 3 Phase : 200.00 kVA : POLEMNT |  | 609SEG5159-6761 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1713 | 8 | 24519 | 13704 | 0.55891 | 0.00032628 | 340 | 582437 | 2011/2012 | April-2011 | 4 | 2011
25351 | Tree Through Line - National Park Sub | 2011-04-26 10:03 | 2011-04-26 | 2011-04-26 11:55 | Calculated | TPN/Park 232 | TPN/Park 232 - 33kV Minimum Oil Circuit Breaker TPN/Park 232 |  | No Segment | 516-01 Transpower National Park | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 112 | 133 | 24519 | 14909 | 0.60806 | 0.0054244 | 13602.5 | 1524840 | 2011/2012 | April-2011 | 4 | 2011
25361 | Extreme Wind - Line Down | 2011-04-26 10:07 | 2011-04-26 | 2011-04-26 23:12 | Calculated | 334 | 334 - Circuit Breaker with Bypass & Links 334 |  | 109SEG303-334 | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 785 | 172 | 24519 | 67004 | 2.7327 | 0.007015 | 2137.1429 | 799529 | 2011/2012 | April-2011 | 4 | 2011
25362 | Tree Through Line Tx145 - King Country Lamb - West Side | 2011-04-26 10:19 | 2011-04-26 | 2011-04-26 16:30 | Calculated | 714 | 714 - Recloser with Bypass 714 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 371 | 66 | 24519 | 11185 | 0.45618 | 0.0026918 | 1099.25 | 117201 | 2011/2012 | April-2011 | 4 | 2011
25370 | Extreme Wind - Ngahape Rd | 2011-04-26 10:48 | 2011-04-26 | 2011-04-26 16:21 | Calculated | TF618 | TF618 - Transformer Fuse: TF618 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 333 | 7 | 24519 | 2332 | 0.09511 | 0.00028549 | 50 | 16657 | 2011/2012 | April-2011 | 4 | 2011
25364 | Branches In Line - Mangaorongo Rd | 2011-04-26 10:55 | 2011-04-26 | 2011-04-26 11:00 | Calculated | 127 | 127 - Circuit Breaker 127 |  | 111SEG127-339 | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 5 | 601 | 24519 | 3105 | 0.12664 | 0.024512 | 6299.75 | 32548 | 2011/2012 | April-2011 | 4 | 2011
25365 | Extreme Wind -Clash - Bayley Rd | 2011-04-26 11:17 | 2011-04-26 | 2011-04-26 15:28 | Calculated | TF2982 | TF2982 - Transformer Fuse: TF2982 |  | No Segment | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 250 | 1 | 24519 | 250 | 0.0102 | 4.0785e-05 | 30 | 7508 | 2011/2012 | April-2011 | 4 | 2011
25366 | Extreme Wind - Hikurangi Sub | 2011-04-26 11:33 | 2011-04-26 | 2011-04-26 13:01 | Calculated | 5370 | 5370 - Recloser with Bypass & Links 5370 |  | 402SEG5370-5199 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 84 | 24519 | 7404 | 0.30197 | 0.0034259 | 632.5 | 55754 | 2011/2012 | April-2011 | 4 | 2011
25371 | Extreme Wind - Te Puke Rd | 2011-04-26 11:53 | 2011-04-26 | 2011-04-26 17:57 | Calculated | 5895 | 5895 - Earth Working Link 5895 |  | 406SEG5895-5252 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 364 | 1 | 24519 | 364 | 0.01485 | 4.0785e-05 | 5 | 1820 | 2011/2012 | April-2011 | 4 | 2011
25367 | Tree Through Line - SH 1 Turangi | 2011-04-26 12:42 | 2011-04-26 | 2011-04-26 17:03 | Calculated | 6650 | 6650 - Load Break Switch 6650 |  | 424SEG5200-6650 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 261 | 250 | 24519 | 65316 | 2.6639 | 0.010196 | 1000 | 261266 | 2011/2012 | April-2011 | 4 | 2011
25372 | Extreme Wind - Aotearoa Rd | 2011-04-26 12:51 | 2011-04-26 | 2011-04-26 22:36 | Calculated | 562 | 562 - Fused Link 562 |  | 122SEG562 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 585 | 14 | 24519 | 8191 | 0.33407 | 0.00057099 | 125 | 73141 | 2011/2012 | April-2011 | 4 | 2011
25373 | Extreme Wind - Kaitieke Rd | 2011-04-26 13:25 | 2011-04-26 | 2011-04-26 17:43 | Calculated | TF13K07 | TF13K07 - Transformer Fuse: TF13K07 |  | 410SEG5703-5805 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 258 | 3 | 24519 | 774 | 0.03157 | 0.00012235 | 15 | 3872 | 2011/2012 | April-2011 | 4 | 2011
25369 | L/V Line Down - Happy Valley Rd | 2011-04-26 15:14 | 2011-04-26 | 2011-04-26 15:45 | Calculated | TF423 | TF423 - Transformer Fuse: TF423 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 6 | 24519 | 187 | 0.00763 | 0.00024471 | 30 | 938 | 2011/2012 | April-2011 | 4 | 2011
25374 | Extreme Wind - Aotearoa Rd | 2011-04-26 15:48 | 2011-04-26 | 2011-04-26 23:16 | Calculated | TF3284 | TF3284 - Transformer Fuse: T3284 |  | 122SEG807 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 448 | 1 | 24519 | 448 | 0.01827 | 4.0785e-05 | 0 | 0 | 2011/2012 | April-2011 | 4 | 2011
25375 | L/V Line Down - Sandel Rd | 2011-04-26 16:06 | 2011-04-26 | 2011-04-26 17:57 | Calculated | TF2944 | TF2944 - Transformer Fuse: TF2944 |  | 120SEG410-632 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 110 | 2 | 24519 | 220 | 0.00897 | 8.1569e-05 | 30 | 3309 | 2011/2012 | April-2011 | 4 | 2011
25377 | Extreme Wind - Tree On Line - Rangitoto Rd | 2011-04-26 16:22 | 2011-04-26 | 2011-04-27 11:13 | Calculated | 112 | 112 - Circuit Breaker with Bypass & Links 112 |  | 106SEG112-REG30 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1075 | 258 | 24519 | 76585 | 3.1235 | 0.010522 | 1878.6667 | 564167 | 2011/2012 | April-2011 | 4 | 2011
25378 | Broken X/arm - Ngahape Rd | 2011-04-26 17:02 | 2011-04-26 | 2011-04-26 20:14 | Calculated | 359 | 359 - Fused Link 359 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 192 | 20 | 24519 | 3843 | 0.15674 | 0.00081569 | 235 | 45155 | 2011/2012 | April-2011 | 4 | 2011
25380 | Extreme Wind - Cottles Rd | 2011-04-26 17:12 | 2011-04-26 | 2011-04-26 21:17 | Calculated | TF273 | TF273 - Transformer Fuse: TF273 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 245 | 2 | 24519 | 490 | 0.01998 | 8.1569e-05 | 15 | 3678 | 2011/2012 | April-2011 | 4 | 2011
25379 | Extreme Wind - Trees In Line - Otukou Sub | 2011-04-26 17:26 | 2011-04-26 | 2011-04-27 17:04 | Calculated | 5584 | 5584 - Recloser with Bypass & Links 5584 |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1418 | 74 | 24519 | 13274 | 0.54138 | 0.0030181 | 346 | 104560 | 2011/2012 | April-2011 | 4 | 2011
25381 | Faulty Tx - Happy Valley Rd | 2011-04-26 17:41 | 2011-04-26 | 2011-04-27 17:48 | Calculated | T270 | T270 - 3 Phase : 30.00 kVA : POLEMNT |  | 111SEG357-579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1446 | 3 | 24519 | 4340 | 0.17701 | 0.00012235 | 30 | 43400 | 2011/2012 | April-2011 | 4 | 2011
25382 | Extreme Wind -Bayley Rd | 2011-04-26 18:34 | 2011-04-26 | 2011-04-26 21:35 | Calculated | TF2982 | TF2982 - Transformer Fuse: TF2982 |  | No Segment | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 1 | 24519 | 181 | 0.00738 | 4.0785e-05 | 30 | 5431 | 2011/2012 | April-2011 | 4 | 2011
25383 | L/V Line Down - SH 30 Pureora | 2011-04-26 18:54 | 2011-04-26 | 2011-04-27 14:20 | Calculated | TF2357 | TF2357 - Transformer Fuse: TF2357 |  | 119SEG432-653 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1166 | 1 | 24519 | 1166 | 0.04755 | 4.0785e-05 | 10 | 11663 | 2011/2012 | April-2011 | 4 | 2011
25384 | L/V Line Down - Wharepuhunga Rd | 2011-04-26 18:57 | 2011-04-26 | 2011-04-26 20:13 | Calculated | TF295 | TF295 - Transformer Fuse: TF295 |  | No Segment | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 5 | 24519 | 380 | 0.0155 | 0.00020392 | 25 | 1904 | 2011/2012 | April-2011 | 4 | 2011
25385 | Pole On Fire - Tx 2766 - Mangatutu Rd | 2011-04-26 19:36 | 2011-04-26 | 2011-04-27 14:38 | Calculated | 2063 | 2063 - Fused Link 2063 |  | 111SEG395-551RET | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOF | Pole Top Fire | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1142 | 7 | 24519 | 7997 | 0.32616 | 0.00028549 | 105 | 119957 | 2011/2012 | April-2011 | 4 | 2011
25386 | Pole Down and Leaning - Maihiihi Rd | 2011-04-26 20:00 | 2011-04-26 | 2011-04-27 12:28 | Calculated | 172 | 172 - Fused Link 172 |  | 111SEG172 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 987 | 15 | 24519 | 14807 | 0.6039 | 0.00061177 | 115 | 113526 | 2011/2012 | April-2011 | 4 | 2011
25387 | Broken L/V Neutral - Pukeiti Rd | 2011-04-26 20:28 | 2011-04-26 | 2011-04-26 21:16 | Calculated | TF1772 | TF1772 - Transformer Fuse: TF1772 |  | 117SEG1298-810 | Te Mapara 117-01 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 2 | 24519 | 96 | 0.00392 | 8.1569e-05 | 5 | 240 | 2011/2012 | April-2011 | 4 | 2011
25388 | L/V Line Down - Aotearoa Rd | 2011-04-26 21:48 | 2011-04-26 | 2011-04-27 16:28 | Calculated | TF1320 | TF1320 - Transformer Fuse: TF1320 |  | 122SEG702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1120 | 5 | 24519 | 5601 | 0.22844 | 0.00020392 | 25 | 28005 | 2011/2012 | April-2011 | 4 | 2011
25390 | L/V Line Down - Ngahape Rd | 2011-04-27 00:16 | 2011-04-27 | 2011-04-27 01:42 | Calculated | TF15 | TF15 - Transformer Fuse: TF15 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 86 | 4 | 24519 | 344 | 0.01403 | 0.00016314 | 50 | 4310 | 2011/2012 | April-2011 | 4 | 2011
25391 | Extreme Wind - Tauraroa Rd | 2011-04-27 06:15 | 2011-04-27 | 2011-04-27 11:02 | Calculated | TF1469 | TF1469 - Transformer Fuse: TF1469 |  | 109SEG529-1727 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 287 | 3 | 24519 | 861 | 0.03512 | 0.00012235 | 50 | 14359 | 2011/2012 | April-2011 | 4 | 2011
25403 | Extreme Wind - SH 47 | 2011-04-27 07:29 | 2011-04-27 | 2011-04-27 15:20 | Calculated | TF12P05 | TF12P05 - Transformer Fuse: TF12P05 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 471 | 1 | 24519 | 471 | 0.01921 | 4.0785e-05 | 15 | 7067 | 2011/2012 | April-2011 | 4 | 2011
25404 | Extreme Wind - Scown Rd | 2011-04-27 08:00 | 2011-04-27 | 2011-04-27 15:13 | Calculated | TF1004 | TF1004 - Transformer Fuse: TF1004 |  | 111SEG544 | Maihiihi 111-04 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 433 | 5 | 24519 | 2165 | 0.0883 | 0.00020392 | 30 | 12994 | 2011/2012 | April-2011 | 4 | 2011
25405 | Extreme Wind - Paewhenua Rd | 2011-04-27 08:20 | 2011-04-27 | 2011-04-27 13:45 | Calculated | TF278 | TF278 - Transformer Fuse: TF278 |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 325 | 7 | 24519 | 2276 | 0.09283 | 0.00028549 | 30 | 9755 | 2011/2012 | April-2011 | 4 | 2011
25392 | Trees In Line - Mapara South Rd | 2011-04-27 08:58 | 2011-04-27 | 2011-04-27 13:45 | Calculated | 1325 | 1325 - Fused Link 1325 |  | 103SEG1301-1307 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 287 | 4 | 24519 | 1148 | 0.04682 | 0.00016314 | 37.5 | 10769 | 2011/2012 | April-2011 | 4 | 2011
25393 | Broken X/arm @ Link 171 - Ongarue Back Rd | 2011-04-27 08:59 | 2011-04-27 | 2011-04-27 11:07 | Calculated | 5797 | 5797 - Fused Link 5797 |  | 402SEG5797-5777 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 18 | 24519 | 2289 | 0.09336 | 0.00073412 | 132.5 | 16856 | 2011/2012 | April-2011 | 4 | 2011
25394 | L/V Fault - Happy Valley Rd | 2011-04-27 11:00 | 2011-04-27 | 2011-04-27 12:09 | Calculated | TF423 | TF423 - Transformer Fuse: TF423 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 69 | 6 | 24519 | 415 | 0.01693 | 0.00024471 | 30 | 2075 | 2011/2012 | April-2011 | 4 | 2011
25395 | Extreme Wind - Maihiihi Rd | 2011-04-27 11:19 | 2011-04-27 | 2011-04-27 12:33 | Calculated | 665 | 665 - Fused Link 665 |  | 111SEG665 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 9 | 24519 | 667 | 0.0272 | 0.00036706 | 75 | 5561 | 2011/2012 | April-2011 | 4 | 2011
25396 | L/V Fault - Rangitoto Rd | 2011-04-27 11:26 | 2011-04-27 | 2011-04-27 11:54 | Calculated | TF101 | TF101 - Transformer Fuse: TF101 |  | Segment between 199 and Temp ABS 2 @ Pole 146 RET | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 4 | 24519 | 112 | 0.00457 | 0.00016314 | 0 | 0 | 2011/2012 | April-2011 | 4 | 2011
25407 | Extreme Wind - Mangatutu Rd | 2011-04-27 11:31 | 2011-04-27 | 2011-04-27 15:57 | Calculated | TF996 | TF996 - Transformer Fuse: TF996 |  | No Segment | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 266 | 4 | 24519 | 1064 | 0.04339 | 0.00016314 | 25 | 6655 | 2011/2012 | April-2011 | 4 | 2011
25399 | Extreme Wind - Pokuru Rd | 2011-04-27 11:33 | 2011-04-27 | 2011-04-27 12:19 | Calculated | 447 | 447 - Fused Link 447 |  | 129SEG447 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 13 | 24519 | 599 | 0.02443 | 0.0005302 | 145 | 6686 | 2011/2012 | April-2011 | 4 | 2011
25409 | Extreme Wind - Whatauri Rd | 2011-04-27 11:44 | 2011-04-27 | 2011-04-27 17:09 | Calculated | TF1590 | TF1590 - Transformer Fuse: TF1590 |  | 122SEG619-REG35 | Wharepapa 122-06 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 325 | 2 | 24519 | 650 | 0.02651 | 8.1569e-05 | 25 | 8130 | 2011/2012 | April-2011 | 4 | 2011
25410 | Extreme Wind - Wharepapa Rd | 2011-04-27 12:37 | 2011-04-27 | 2011-04-27 17:14 | Calculated | TF952 | TF952 - Transformer Fuse: TF952 |  | No Segment | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 277 | 6 | 24519 | 1663 | 0.06782 | 0.00024471 | 25 | 6929 | 2011/2012 | April-2011 | 4 | 2011
25411 | Extreme Wind - Marotiri Rd | 2011-04-27 12:53 | 2011-04-27 | 2011-04-27 17:51 | Calculated | TF1203 | TF1203 - Transformer Fuse: TF1203 |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 298 | 3 | 24519 | 894 | 0.03646 | 0.00012235 | 15 | 4473 | 2011/2012 | April-2011 | 4 | 2011
25400 | Tree On L/V - Maihiihi Rd | 2011-04-27 13:15 | 2011-04-27 | 2011-04-27 14:02 | Calculated | TF1098 | TF1098 - Transformer Fuse: TF1098 |  | 111SEG665 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 3 | 24519 | 141 | 0.00575 | 0.00012235 | 15 | 707 | 2011/2012 | April-2011 | 4 | 2011
25401 | Broken DDO @ Tx1308 - Mitchell Rd Off Scott Rd | 2011-04-27 13:17 | 2011-04-27 | 2011-04-27 13:55 | Calculated | 495 | 495 - Fused Link 495 |  | 119SEG495 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 6 | 24519 | 223 | 0.00909 | 0.00024471 | 85 | 3164 | 2011/2012 | April-2011 | 4 | 2011
25402 | L/V Line Down - Oturu Rd | 2011-04-27 13:19 | 2011-04-27 | 2011-04-27 17:00 | Calculated | TF347 | TF347 - Transformer Fuse: TF347 |  | No Segment | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 221 | 3 | 24519 | 663 | 0.02704 | 0.00012235 | 37.5 | 8294 | 2011/2012 | April-2011 | 4 | 2011
25389 | Tree Through Line - SH 47 Towards Wanganui | 2011-04-27 13:57 | 2011-04-27 | 2011-04-27 14:35 | Calculated | 5834 | 5834 - Solid Link 5834 |  | 418SEG512T1-5836 | 512-01 Otukou | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 96 | 24519 | 3659 | 0.14923 | 0.0039153 | 681 | 25957 | 2011/2012 | April-2011 | 4 | 2011
25413 | Extreme Wind - Omatane Rd | 2011-04-27 15:41 | 2011-04-27 | 2011-04-27 17:01 | Calculated | TF10K16 | TF10K16 - Transformer Fuse: TF10K16 |  | 409SEG5904-6206 | Southern 409-04 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 25 | 24519 | 2005 | 0.08177 | 0.0010196 | 104.1667 | 8354 | 2011/2012 | April-2011 | 4 | 2011
25414 | Extreme Wind - Mangaorongo Rd | 2011-04-27 16:40 | 2011-04-27 | 2011-04-28 10:30 | Calculated | TF1231 | TF1231 - Transformer Fuse: TF1231 |  | 111SEG339-346 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1070 | 1 | 24519 | 1070 | 0.04364 | 4.0785e-05 | 15 | 16053 | 2011/2012 | April-2011 | 4 | 2011
25415 | Trees In Line - Otukou Sub | 2011-04-27 17:21 | 2011-04-27 | 2011-04-27 20:12 | Calculated | 5584 | 5584 - Recloser with Bypass & Links 5584 |  | 418SEG5584-5591 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 74 | 24519 | 2560 | 0.10441 | 0.0030181 | 346 | 16655 | 2011/2012 | April-2011 | 4 | 2011
25419 | Replace H/V Fuse Tx1096- L/V Fault - Sircombe Rd | 2011-04-28 07:44 | 2011-04-28 | 2011-04-28 09:15 | Calculated | TF1096 | TF1096 - Transformer Fuse: TF1096 |  | 109SEG522-179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 4 | 24519 | 364 | 0.01485 | 0.00016314 | 40 | 3642 | 2011/2012 | April-2011 | 4 | 2011
25420 | Upgrade Tx10S51 - Tongariro High School | 2011-04-28 10:08 | 2011-04-28 | 2011-04-28 17:55 | Calculated | TF10S51 | TF10S51 - Transformer Fuse: TF10S51 |  | 424SEG6158 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 467 | 2 | 24519 | 934 | 0.03809 | 8.1569e-05 | 400 | 186826 | 2011/2012 | April-2011 | 4 | 2011
25422 | Relocate Pole In River - Taharoa Rd - By Old Quarry | 2011-04-28 10:21 | 2011-04-28 | 2011-04-28 12:04 | Calculated | 277 | 277 - Recloser with Bypass 277 |  | 125SEG277-268 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 125 | 24519 | 12893 | 0.52584 | 0.0050981 | 989.2895 | 102045 | 2011/2012 | April-2011 | 4 | 2011
25416 | Extreme Wind - Pole Down - Maihiihi Rd | 2011-04-28 11:16 | 2011-04-28 | 2011-04-28 12:51 | Calculated | T285 | T285 - 3 Phase : 25.00 kVA : POLEMNT |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 20 | 24519 | 1906 | 0.07774 | 0.00081569 | 220 | 20976 | 2011/2012 | April-2011 | 4 | 2011
25417 | Extreme Wind - Pole Down - Maihiihi Rd | 2011-04-28 11:20 | 2011-04-28 | 2011-04-28 12:51 | Calculated | T469 | T469 - 3 Phase : 25.00 kVA : POLEMNT |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 15 | 24519 | 1370 | 0.05588 | 0.00061177 | 132.5 | 12103 | 2011/2012 | April-2011 | 4 | 2011
25425 | Replace 359 - Ngahape Rd | 2011-04-28 14:53 | 2011-04-28 | 2011-04-28 15:53 | Calculated | 359 | 359 - Fused Link 359 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 20 | 24519 | 1202 | 0.04902 | 0.00081569 | 235 | 14131 | 2011/2012 | April-2011 | 4 | 2011
25426 | Replace H/V Fuse Tx3284 - Aotearoa Rd | 2011-04-28 15:48 | 2011-04-28 | 2011-04-28 17:00 | Calculated | TF3284 | TF3284 - Transformer Fuse: T3284 |  | 122SEG807 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 1 | 24519 | 72 | 0.00294 | 4.0785e-05 | 0 | 0 | 2011/2012 | April-2011 | 4 | 2011
25427 | Broken Insulator - Lurman Rd | 2011-04-28 16:02 | 2011-04-28 | 2011-04-28 16:55 | Calculated | 179 | 179 - Fused Link 179 |  | 109SEG179 | Gravel Scoop 109-14 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 21 | 24519 | 1116 | 0.04552 | 0.00085648 | 197.5 | 10500 | 2011/2012 | April-2011 | 4 | 2011
25418 | Restore Jumper - Tukehu St - Corner Atirau Rd | 2011-04-28 17:27 | 2011-04-28 | 2011-04-28 18:00 | Calculated | 5207 | 5207 - Air Break Switch 5207 |  | 424SEG5207-6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 43 | 24519 | 1427 | 0.0582 | 0.0017537 | 447.5 | 14856 | 2011/2012 | April-2011 | 4 | 2011
25431 | Faulty Tx - Arohena Substation | 2011-04-28 22:12 | 2011-04-28 | 2011-04-28 22:21 | Calculated | 1072 | 1072 - Circuit Breaker 1072 Huirimu |  | 121SEG1072-753 | 211-01 Arohena | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 169 | 24519 | 1543 | 0.06293 | 0.0068926 | 1711.5 | 15631 | 2011/2012 | April-2011 | 4 | 2011
25434 | Tree Fell Into Line - Manunui Sub | 2011-04-29 06:43 | 2011-04-29 | 2011-04-29 06:51 | Calculated | 6143 | 6143 - Circuit Breaker Manunui 33kV 6143 |  | No Segment | 510-01 Manunui | Rural B | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 4 | 24519 | 33 | 0.00135 | 0.00016314 | 450 | 3727 | 2011/2012 | April-2011 | 4 | 2011
25433 | Extreme Wind - Pole Down | 2011-04-29 09:21 | 2011-04-29 | 2011-04-29 14:48 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 327 | 15 | 24519 | 4906 | 0.20009 | 0.00061177 | 168 | 54958 | 2011/2012 | April-2011 | 4 | 2011
25435 | L/V Fault - Cottles Rd | 2011-04-29 10:39 | 2011-04-29 | 2011-04-29 12:35 | Calculated | TF273 | TF273 - Transformer Fuse: TF273 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 2 | 24519 | 232 | 0.00946 | 8.1569e-05 | 15 | 1742 | 2011/2012 | April-2011 | 4 | 2011
25436 | Replace H/V Fuse At Tx13332 - Kiokio Station Rd | 2011-04-29 11:04 | 2011-04-29 | 2011-04-29 11:47 | Calculated | TF1332 | TF1332 - Transformer Fuse: TF1332 |  | 112SEG674RET | Otorohanga 112-03 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 1 | 24519 | 43 | 0.00175 | 4.0785e-05 | 10 | 431 | 2011/2012 | April-2011 | 4 | 2011
25437 | Insulator out of X/arm - Cottles Rd | 2011-04-29 12:47 | 2011-04-29 | 2011-04-29 15:19 | Calculated | TF1541 | TF1541 - Transformer Fuse: TF1541 |  | 111SEG579 | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Insulator | FAIL:FINS2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 1 | 24519 | 152 | 0.0062 | 4.0785e-05 | 25 | 3805 | 2011/2012 | April-2011 | 4 | 2011
25438 | L/V Maintenance - Maihiihi Rd | 2011-04-29 13:00 | 2011-04-29 | 2011-04-29 14:08 | Calculated | TF2091 | TF2091 - Transformer Fuse: TF2091 |  | No Segment | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 68 | 3 | 24519 | 204 | 0.00832 | 0.00012235 | 30 | 2044 | 2011/2012 | April-2011 | 4 | 2011
25439 | Repair Fault From Tuesday - Ngahape Rd | 2011-04-29 14:09 | 2011-04-29 | 2011-04-29 15:11 | Calculated | 359 | 359 - Fused Link 359 |  | 111SEG359RET | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 20 | 24519 | 1223 | 0.04988 | 0.00081569 | 235 | 14370 | 2011/2012 | April-2011 | 4 | 2011
25440 | Replace Fuse 829 - Raurimu Township | 2011-04-29 18:00 | 2011-04-29 | 2011-04-29 19:32 | Calculated | 5829 | 5829 - Fused Link 5829 |  | 410SEG5829-5545 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 23 | 24519 | 2119 | 0.08642 | 0.00093805 | 118.3333 | 10904 | 2011/2012 | April-2011 | 4 | 2011
25523 | Replace HV Fuse at Tx8R19 - Te Waaka Tec | 2011-05-01 08:00 | 2011-05-01 | 2011-05-01 10:20 | Calculated | TF8R19 | TF8R19 - Transformer Fuse: TF8R19 |  | 406SEG6558-5921 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 59 | 24418 | 8266 | 0.33852 | 0.0024163 | 218.5185 | 30618 | 2011/2012 | May-2011 | 5 | 2011
25521 | Replace HV Fuse at Tx13K12 - Main South Rd | 2011-05-01 08:01 | 2011-05-01 | 2011-05-01 09:13 | Calculated | TF13K12 | TF13K12 - Transformer Fuse: TF13K12 |  | 410SEG5161-5235 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 1 | 24418 | 72 | 0.00295 | 4.0953e-05 | 7.5 | 540 | 2011/2012 | May-2011 | 5 | 2011
25524 | Recloser 642 Tripped - Puketawai Rd - Cnr Old Te Kuiti Rd | 2011-05-01 12:56 | 2011-05-01 | 2011-05-01 13:36 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 103 | 24418 | 4029 | 0.165 | 0.0042182 | 988 | 38647 | 2011/2012 | May-2011 | 5 | 2011
25525 | OCB 5955 Tripped - Borough Sub | 2011-05-02 01:27 | 2011-05-02 | 2011-05-02 01:38 | Calculated | 5955 | 5955 - Circuit Breaker Northern 5955 |  | No Segment | 508-01 Borough | Rural B | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 1241 | 24418 | 13816 | 0.56581 | 0.050823 | 7773.108 | 86540 | 2011/2012 | May-2011 | 5 | 2011
25526 | LV Fault - Maihiihi Rd | 2011-05-02 11:49 | 2011-05-02 | 2011-05-02 12:15 | Calculated | TF275 | TF275 - Transformer Fuse: TF275 |  | No Segment | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 2 | 24418 | 52 | 0.00213 | 8.1907e-05 | 15 | 392 | 2011/2012 | May-2011 | 5 | 2011
25529 | Faulty Recloser - Lower Retaruke Sub | 2011-05-02 12:52 | 2011-05-02 | 2011-05-06 11:07 | Calculated | 5490 | 5490 - Recloser with Bypass 5490 |  | 410SEG5490-5438 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 206 | 74 | 24418 | 15149 | 0.6204 | 0.0030306 | 421.75 | 86062 | 2011/2012 | May-2011 | 5 | 2011
25530 | Lower Taps at Tx776 - Paerata Rd | 2011-05-02 13:26 | 2011-05-02 | 2011-05-02 14:05 | Calculated | TF776 | TF776 - Transformer Fuse: TF776 |  | 129SEG402-725 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 4 | 24418 | 156 | 0.00639 | 0.00016381 | 25 | 979 | 2011/2012 | May-2011 | 5 | 2011
25531 | LV Fault - Barbers Rd | 2011-05-02 13:28 | 2011-05-02 | 2011-05-02 14:02 | Calculated | TF112 | TF112 - Transformer Fuse: TF112 |  | 106SEG247-2068 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 34 | 3 | 24418 | 102 | 0.00418 | 0.00012286 | 30 | 1025 | 2011/2012 | May-2011 | 5 | 2011
25532 | Replace HV Fuse at Tx1469 - Tauraroa Rd | 2011-05-03 06:31 | 2011-05-03 | 2011-05-03 07:09 | Calculated | TF1469 | TF1469 - Transformer Fuse: TF1469 |  | 109SEG529-1727 | Gravel Scoop 109-06 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 3 | 24418 | 114 | 0.00467 | 0.00012286 | 50 | 1908 | 2011/2012 | May-2011 | 5 | 2011
25533 | Replace 11Kv Poles & Hardware - Tangiwai Railway Station | 2011-05-03 09:06 | 2011-05-03 | 2011-05-03 15:56 | Calculated | 5689 | 5689 - Fused Link 5689 |  | 416SEG5689-5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 410 | 29 | 24418 | 11896 | 0.48718 | 0.0011876 | 300 | 123064 | 2011/2012 | May-2011 | 5 | 2011
25534 | Replace HV Fuse at Tx05I12 - Ongarue Rd | 2011-05-03 09:07 | 2011-05-03 | 2011-05-03 10:00 | Calculated | TF5I12 | TF5I12 - Transformer Fuse: TF5I12 |  | 402SEG5798 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 1 | 24418 | 53 | 0.00217 | 4.0953e-05 | 5 | 265 | 2011/2012 | May-2011 | 5 | 2011
25536 | Upgrade Existing Line To Tx1117 & Beyond To 3 Phase - Pureora | 2011-05-04 08:39 | 2011-05-04 | 2011-05-04 16:29 | Calculated | TF3336 | TF3336 - Transformer Fuse TF3336 |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 469 | 3 | 24418 | 1408 | 0.05766 | 0.00012286 | 35 | 16430 | 2011/2012 | May-2011 | 5 | 2011
25538 | Fuse Pulled Apart - Henderson Rd | 2011-05-04 08:46 | 2011-05-04 | 2011-05-04 12:37 | Calculated | TF2819 | TF2819 - Transformer Fuse: TF2819 |  | 120SEG416-479 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 1 | 24418 | 231 | 0.00946 | 4.0953e-05 | 10 | 2311 | 2011/2012 | May-2011 | 5 | 2011
25539 | Replace 11Kv Pole & Hardware Poles 345 - 401 - Tangiwai Railway Station | 2011-05-04 09:01 | 2011-05-04 | 2011-05-04 15:48 | Calculated | 5689 | 5689 - Fused Link 5689 |  | 416SEG5689-5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 407 | 29 | 24418 | 11807 | 0.48354 | 0.0011876 | 300 | 122144 | 2011/2012 | May-2011 | 5 | 2011
25540 | Line Clash - Waverley Rd | 2011-05-04 15:41 | 2011-05-04 | 2011-05-04 16:46 | Calculated | TF414 | TF414 - Transformer Fuse: TF414 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 2 | 24418 | 130 | 0.00532 | 8.1907e-05 | 30 | 1954 | 2011/2012 | May-2011 | 5 | 2011
25541 | Upgrade Existing Line To Tx1117 and Beyond To 3 Phase - Pureora | 2011-05-05 09:02 | 2011-05-05 | 2011-05-05 18:29 | Calculated | TF3336 | TF3336 - Transformer Fuse TF3336 |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 567 | 3 | 24418 | 1701 | 0.06966 | 0.00012286 | 35 | 19854 | 2011/2012 | May-2011 | 5 | 2011
25543 | Upgrade Tx2930 - Whakamaru Rd | 2011-05-05 10:04 | 2011-05-05 | 2011-05-05 17:04 | Calculated | 507 | 507 - Fused Link 507 |  | 120SEG507-530 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 420 | 2 | 24418 | 840 | 0.0344 | 8.1907e-05 | 300 | 126065 | 2011/2012 | May-2011 | 5 | 2011
25544 | Replace Link 6608 - SH 49 | 2011-05-05 16:23 | 2011-05-05 | 2011-05-05 17:12 | Calculated | 6608 | 6608 - Fused Link 6608 |  | 416SEG5780-6608 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 2 | 24418 | 98 | 0.00401 | 8.1907e-05 | 100 | 4926 | 2011/2012 | May-2011 | 5 | 2011
25545 | Upgrade Existing Line To Tx1117 and Beyond To 3 Phase | 2011-05-06 08:30 | 2011-05-06 | 2011-05-06 13:35 | Calculated | TF3336 | TF3336 - Transformer Fuse TF3336 |  | 119SEG407 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 3 | 24418 | 915 | 0.03747 | 0.00012286 | 35 | 10682 | 2011/2012 | May-2011 | 5 | 2011
25548 | Fuse Pulled Apart at Tx2284 - Scott Rd | 2011-05-06 10:32 | 2011-05-06 | 2011-05-06 11:49 | Calculated | TF2284 | TF2284 - Transformer Fuse: TF2284 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 5 | 24418 | 380 | 0.01556 | 0.00020477 | 25 | 1904 | 2011/2012 | May-2011 | 5 | 2011
25549 | Fuse Pulled Apart - Te Kumi Rd | 2011-05-06 10:34 | 2011-05-06 | 2011-05-06 11:02 | Calculated | TF2610 | TF2610 - Transformer Fuse: TF2610 |  | 107SEG233-1020 | Oparure 107-03 | Rural C | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 1 | 24418 | 28 | 0.00115 | 4.0953e-05 | 25 | 702 | 2011/2012 | May-2011 | 5 | 2011
25550 | Replace H/V Fuse - Were Rd | 2011-05-06 20:45 | 2011-05-06 | 2011-05-06 22:20 | Calculated | TF1651 | TF1651 - Transformer Fuse: TF1651 |  | 113SEG1549-1530 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 2 | 24418 | 190 | 0.00778 | 8.1907e-05 | 15 | 1428 | 2011/2012 | May-2011 | 5 | 2011
25551 | Wind/Clash - Marokopa | 2011-05-07 13:08 | 2011-05-07 | 2011-05-07 15:53 | Calculated | TF2822 | TF2822 - Transformer Fuse: TF2822 |  | No Segment | Coast 125-06 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Conductor - Overhead | FAIL:FCDT:DCLS1 | Conductor Clashing due to Wind | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 1 | 24418 | 165 | 0.00676 | 4.0953e-05 | 15 | 2477 | 2011/2012 | May-2011 | 5 | 2011
25552 | Jumper Off at Pole 32/8 - Taitua St | 2011-05-07 22:30 | 2011-05-07 | 2011-05-07 22:40 | Calculated | 5920 | 5920 - Air Break Switch 5920 |  | 409SEG5920-5383 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 77 | 24418 | 786 | 0.03219 | 0.0031534 | 402.5 | 4112 | 2011/2012 | May-2011 | 5 | 2011
25553 | Replace H/V Fuse at Tx581 - Rangiatea Rd | 2011-05-09 08:41 | 2011-05-09 | 2011-05-09 10:09 | Calculated | TF581 | TF581 - Transformer Fuse: TF581 |  | No Segment | Gravel Scoop 109-11 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 2 | 24418 | 174 | 0.00713 | 8.1907e-05 | 25 | 2182 | 2011/2012 | May-2011 | 5 | 2011
25555 | Broken L/A Earth - Porou St | 2011-05-09 13:17 | 2011-05-09 | 2011-05-09 14:03 | Calculated | 1.22 | 1.22 - Fused Link 1.22 |  | 404SEGL1.20-A1.41 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Protection | FAIL:FPRO |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 99 | 24418 | 4466 | 0.1829 | 0.0040544 | 503.7736 | 22728 | 2011/2012 | May-2011 | 5 | 2011
25556 | Replace H/V Fuse at Tx7L5 - Oruaiwi Rd | 2011-05-09 13:39 | 2011-05-09 | 2011-05-09 16:05 | Calculated | TF7L5 | TF7L5 - Transformer Fuse: TF7L5 |  | No Segment | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:AOTH | Other Animal | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 1 | 24418 | 146 | 0.00598 | 4.0953e-05 | 15 | 2192 | 2011/2012 | May-2011 | 5 | 2011
25557 | Fuse Pull Apart at Tx2J14- Tangitu Rd | 2011-05-09 14:01 | 2011-05-09 | 2011-05-09 16:52 | Calculated | TF2J14 | TF2J14 - Transformer Fuse: TF2J14 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 1 | 24418 | 170 | 0.00696 | 4.0953e-05 | 15 | 2552 | 2011/2012 | May-2011 | 5 | 2011
25558 | Replace H/V Fuse at Tx6R1 - Karangahape Rd | 2011-05-09 14:10 | 2011-05-09 | 2011-05-09 18:35 | Calculated | TF6R1 | TF6R1 - Transformer Fuse: TF6R1 |  | 426SEG5847-5592 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 265 | 1 | 24418 | 265 | 0.01085 | 4.0953e-05 | 15 | 3977 | 2011/2012 | May-2011 | 5 | 2011
25560 | Broken X/arm - Mangaohutu Rd | 2011-05-10 09:50 | 2011-05-10 | 2011-05-10 14:41 | Calculated | TF12F03 | TF12F03 - Transformer Fuse: TF12F03 |  | 403SEG5541 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 290 | 3 | 24418 | 870 | 0.03563 | 0.00012286 | 15 | 4352 | 2011/2012 | May-2011 | 5 | 2011
25561 | Magpie - Upper Retaruke Rd | 2011-05-10 11:37 | 2011-05-10 | 2011-05-10 12:14 | Calculated | TF13I03 | TF13I03 - Transformer Fuse: TF13I03 |  | 410SEG5492-5334 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 1 | 24418 | 37 | 0.00152 | 4.0953e-05 | 15 | 557 | 2011/2012 | May-2011 | 5 | 2011
25562 | Recloser 5266 Tripped - Aukopae E/W Sub | 2011-05-10 14:33 | 2011-05-10 | 2011-05-10 16:01 | Calculated | 5266 | 5266 - Recloser 5266 |  | 413SEG5260-5266 | Ohura 413-09 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 19 | 24418 | 1674 | 0.06856 | 0.00077811 | 122.5 | 10798 | 2011/2012 | May-2011 | 5 | 2011
25564 | Wind - Forest Rd | 2011-05-11 09:31 | 2011-05-11 | 2011-05-11 10:22 | Calculated | TF1615 | TF1615 - Transformer Fuse: TF1615 |  | 123SEG695RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 1 | 24418 | 51 | 0.00209 | 4.0953e-05 | 50 | 2556 | 2011/2012 | May-2011 | 5 | 2011
25565 | Replace Old Type Of Link and Fit Fuse Elements - Oio Sub | 2011-05-11 10:07 | 2011-05-11 | 2011-05-11 11:28 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 81 | 47 | 24418 | 3816 | 0.15628 | 0.0019248 | 239.75 | 19467 | 2011/2012 | May-2011 | 5 | 2011
25567 | Broken Link 5373- Turangi Highway | 2011-05-11 11:18 | 2011-05-11 | 2011-05-11 12:16 | Calculated | 5148 | 5148 - Air Break Switch 5148 |  | 411SEG5148-5373 | 513-01 Tawhai | Rural D | National Park | National Park Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 12 | 24418 | 697 | 0.02854 | 0.00049144 | 215 | 12498 | 2011/2012 | May-2011 | 5 | 2011
25568 | Replace H/V Fuse at Tx11H02 - Kirikau Valley Rd | 2011-05-11 16:37 | 2011-05-11 | 2011-05-11 18:30 | Calculated | TF11H02 | TF11H02 - Transformer Fuse: TF11H02 |  | 403SEG5765-5653 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 5 | 24418 | 565 | 0.02314 | 0.00020477 | 25 | 2827 | 2011/2012 | May-2011 | 5 | 2011
25569 | Faulty Tx2688 - Gadsby Rd | 2011-05-12 00:42 | 2011-05-12 | 2011-05-12 13:05 | Calculated | 512 | 512 - Circuit Breaker Gadsby Rd 11 kV Feeder512 |  | No Segment | 205-01 Gadsby Road | Urban A | Oparure | Gadsby Road Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 742 | 529 | 24418 | 44286 | 1.8137 | 0.021664 | 4779.9604 | 377896 | 2011/2012 | May-2011 | 5 | 2011
25570 | Replace H/V Fuses - Turoa Feeder | 2011-05-12 06:50 | 2011-05-12 | 2011-05-12 08:00 | Calculated | TF19K4 | TF19K4 - Transformer Fuse: TF19K4 |  | No Segment | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 1 | 24418 | 40 | 0.00164 | 4.0953e-05 | 15 | 603 | 2011/2012 | May-2011 | 5 | 2011
25571 | Drop SWER Line For Tree Felling - Hikumutu Rd | 2011-05-12 08:38 | 2011-05-12 | 2011-05-12 16:22 | Calculated | 5623 | 5623 - Sectionaliser with Bypass 5623 |  | 409SEG5411-5623 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 464 | 16 | 24418 | 7426 | 0.30412 | 0.00065525 | 73.75 | 34232 | 2011/2012 | May-2011 | 5 | 2011
25573 | Fuse Pulled Apart at Tx1A75 - Blair Rd | 2011-05-12 12:26 | 2011-05-12 | 2011-05-12 13:43 | Calculated | TF1A75 | TF1A75 - Transformer Fuse: TF1A75 |  | 404SEG5022-L1.10 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 21 | 24418 | 1620 | 0.06634 | 0.00086002 | 110.5263 | 8527 | 2011/2012 | May-2011 | 5 | 2011
25574 | Vehicle vs Line - Ohirea Rd | 2011-05-13 07:15 | 2011-05-13 | 2011-05-13 12:25 | Calculated | T410 | T410 - 1 Phase : 25.00 kVA : POLEMNT |  | 103SEG283 | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 310 | 3 | 24418 | 930 | 0.03809 | 0.00012286 | 25 | 7755 | 2011/2012 | May-2011 | 5 | 2011
25576 | Scheduled Maintenance - Tx04P03 | 2011-05-13 10:28 | 2011-05-13 | 2011-05-13 11:43 | Calculated | TF4P3 | TF4P3 - Transformer Fuse: TF4P3 |  | 426SEG5333-5532 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 74 | 6 | 24418 | 445 | 0.01822 | 0.00024572 | 18 | 1338 | 2011/2012 | May-2011 | 5 | 2011
25577 | Replace H/V Fuse at Tx244 - Rangiatea Rd | 2011-05-13 11:43 | 2011-05-13 | 2011-05-13 13:18 | Calculated | TF244 | TF244 - Transformer Fuse: TF244 |  | No Segment | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 2 | 24418 | 190 | 0.00778 | 8.1907e-05 | 25 | 2379 | 2011/2012 | May-2011 | 5 | 2011
25578 | Broken X/arm -Te Waitere Rd By Scott's | 2011-05-13 15:39 | 2011-05-13 | 2011-05-13 17:26 | Calculated | 281 | 281 - Air Break Switch 281 |  | 125SEG281-298 | 202-01 Piripiri | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 55 | 24418 | 5901 | 0.24167 | 0.0022524 | 530.7895 | 56953 | 2011/2012 | May-2011 | 5 | 2011
25579 | Replace H/V Fuse at Tx20L32 - Ruapehu Rd | 2011-05-13 17:02 | 2011-05-13 | 2011-05-13 17:19 | Calculated | TF20L32 | TF20L32 - Transformer Fuse: TF20L32 |  | No Segment | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 11 | 24418 | 188 | 0.0077 | 0.00045049 | 55 | 944 | 2011/2012 | May-2011 | 5 | 2011
25580 | L/V Fault - Taharoa Rd | 2011-05-15 10:26 | 2011-05-15 | 2011-05-15 11:40 | Calculated | TF1411 | TF1411 - Transformer Fuse: TF1411 |  | 125SEG298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 3 | 24418 | 222 | 0.00909 | 0.00012286 | 10 | 742 | 2011/2012 | May-2011 | 5 | 2011
25581 | Replace H/V Fuse at Tx772 - Tirohanga Rd | 2011-05-15 15:29 | 2011-05-15 | 2011-05-15 16:17 | Calculated | TF772 | TF772 - Transformer Fuse: TF772 |  | 129SEG451-787 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 5 | 24418 | 240 | 0.00983 | 0.00020477 | 62.5 | 3011 | 2011/2012 | May-2011 | 5 | 2011
25582 | Line Clash due to Wind - Taranui St corner of Hihi St | 2011-05-16 09:08 | 2011-05-16 | 2011-05-16 10:35 | Calculated | 5604 | 5604 - Fused Link 5604 |  | 413SEG5604 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 22 | 24418 | 1916 | 0.07847 | 0.00090097 | 52.381 | 4564 | 2011/2012 | May-2011 | 5 | 2011
25583 | Wind - Hangatiki | 2011-05-16 09:42 | 2011-05-16 | 2011-05-16 09:45 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 114 | 24418 | 256 | 0.01048 | 0.0046687 | 3229.4228 | 7266 | 2011/2012 | May-2011 | 5 | 2011
25584 | Clash due to Wind - Main South Rd - Piopio | 2011-05-16 11:16 | 2011-05-16 | 2011-05-16 12:26 | Calculated | TF821 | TF821 - Transformer Fuse: TF821 |  | No Segment | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 2 | 24418 | 140 | 0.00573 | 8.1907e-05 | 10 | 701 | 2011/2012 | May-2011 | 5 | 2011
25585 | L/V Wrapped - Tirohanga Rd | 2011-05-16 12:41 | 2011-05-16 | 2011-05-16 14:56 | Calculated | TF772 | TF772 - Transformer Fuse: TF772 |  | 129SEG451-787 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 5 | 24418 | 675 | 0.02764 | 0.00020477 | 62.5 | 8445 | 2011/2012 | May-2011 | 5 | 2011
25588 | Broken Pole 138/37 - Mahoe Rd - Past Piggeries | 2011-05-17 11:36 | 2011-05-17 | 2011-05-17 13:42 | Calculated | 552 | 552 - Air Break Switch 552 |  | 101SEG552-290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 126 | 15 | 24418 | 1893 | 0.07752 | 0.0006143 | 95 | 11988 | 2011/2012 | May-2011 | 5 | 2011
25639 | Binder Off at Pole 48 - Tokaanu/Kurakau 33 | 2011-05-17 11:42 | 2011-05-17 | 2011-05-17 11:44 | Calculated | 6576 | 6576 - Circuit Breaker Tokaanu POS 33kV 6576 |  | 607SEG6576-6604 | Tokaanu / Kuratau 607-02 | Urban A | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 1628 | 24418 | 3492 | 0.14301 | 0.066672 | 8942.25 | 18922 | 2011/2012 | May-2011 | 5 | 2011
25768 | BINDER OFF AT POLE 48 - TOKAANU RD | 2011-05-17 11:43 | 2011-05-17 | 2011-05-17 15:28 | Calculated | 6576 | 6576 - Circuit Breaker Tokaanu POS 33kV 6576 |  | 607SEG6576-6604 | Tokaanu / Kuratau 607-02 | Urban A | Tokaanu / Kuratau 33 | Direct from Tokaanu Supply |  | Asset Related | Conductor Ties | FAIL:FCOT:FCOB | Binder Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4 | 1628 | 24418 | 3364 | 0.13777 | 0.066672 | 8942.25 | 18796 | 2011/2012 | May-2011 | 5 | 2011
25591 | Treescape vs Line - National Park North | 2011-05-17 12:47 | 2011-05-17 | 2011-05-17 14:00 | Calculated | 5142 | 5142 - Circuit Breaker with Bypass 5142 |  | 410SEG6766-5141 | 501-01 National Park | Rural D | Raurimu | National Park Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EADA | Other Accidental Damage by Authorities, Utillities, Contractors | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 333 | 24418 | 24370 | 0.99803 | 0.013637 | 2118.0833 | 155008 | 2011/2012 | May-2011 | 5 | 2011
25598 | Recloser 5180 Tripped - Kuratau St | 2011-05-17 14:18 | 2011-05-17 | 2011-05-17 14:19 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 253 | 24418 | 333 | 0.01364 | 0.010361 | 13551 | 17842 | 2011/2012 | May-2011 | 5 | 2011
25599 | Replace Tx15N1 With ETEL RTE & Replace O/H Joints - Mt Ruapehu | 2011-05-18 09:20 | 2011-05-18 | 2011-05-18 15:05 | Calculated | 5990 | 5990 - Circuit Breaker 5990 |  | 419SEG5990-5991 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 344 | 82 | 24418 | 27748 | 1.1364 | 0.0033582 | 11591.7857 | 3973690 | 2011/2012 | May-2011 | 5 | 2011
25593 | Replace H/V Fuse at Pole 196 and Resag L/V Off Tx2J2 - Waihuka Rd | 2011-05-18 10:12 | 2011-05-18 | 2011-05-18 14:34 | Calculated | 5366 | 5366 - Solid Link 5366 |  | 421SEG5366 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 262 | 5 | 24418 | 1311 | 0.05369 | 0.00020477 | 16.6667 | 4370 | 2011/2012 | May-2011 | 5 | 2011
25595 | Fuse Pulled Apart - Pehi Rd | 2011-05-18 15:23 | 2011-05-18 | 2011-05-18 17:09 | Calculated | TF15K04 | TF15K04 - Transformer Fuse: TF15K04 |  | 411SEG5162-5145 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 2 | 24418 | 212 | 0.00868 | 8.1907e-05 | 30 | 3185 | 2011/2012 | May-2011 | 5 | 2011
25596 | Line Down - Main Rd - South of National Park | 2011-05-19 08:39 | 2011-05-19 | 2011-05-19 15:44 | Calculated | 5162 | 5162 - Fused Link 5162 |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 425 | 7 | 24418 | 2977 | 0.12192 | 0.00028667 | 50 | 21266 | 2011/2012 | May-2011 | 5 | 2011
25601 | Truck vs L/V - SH 3 Mahoenui | 2011-05-19 16:25 | 2011-05-19 | 2011-05-19 17:44 | Calculated | TF1891 | TF1891 - Transformer Fuse: TF1891 |  | 128SEG1358-1602 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 2 | 24418 | 158 | 0.00647 | 8.1907e-05 | 30 | 2380 | 2011/2012 | May-2011 | 5 | 2011
25602 | Duck - Harpers Avenue - Pole 1/4/20 | 2011-05-19 18:44 | 2011-05-19 | 2011-05-19 20:21 | Calculated | 2061 | 2061 - Fused Link 2061 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 2 | 24418 | 194 | 0.00794 | 8.1907e-05 | 45 | 4374 | 2011/2012 | May-2011 | 5 | 2011
25603 | Jumper Off at Tx1644 = Waitanguru - By Reed's | 2011-05-19 19:38 | 2011-05-19 | 2011-05-19 20:08 | Calculated | 1526 | 1526 - Fused Link 1526 |  | 113SEG1526-1525 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 59 | 24418 | 1776 | 0.07273 | 0.0024163 | 378.8333 | 11409 | 2011/2012 | May-2011 | 5 | 2011
25604 | Livening New 11kV Line To Open ABS 2076 and Remove Links 2074 - Tirohonga Road | 2011-05-20 10:00 | 2011-05-20 | 2011-05-20 14:45 | Calculated | 1751 | 1751 - Fused Link 1751 |  | 123SEG1751-765RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 3 | 24418 | 855 | 0.03502 | 0.00012286 | 100 | 28520 | 2011/2012 | May-2011 | 5 | 2011
25605 | Jumper Off Pole 190 - Tirohanga Rd | 2011-05-22 13:30 | 2011-05-22 | 2011-05-22 14:18 | Calculated | 451 | 451 - Air Break Switch 451 |  | 129SEG451-787 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 102 | 24418 | 4913 | 0.2012 | 0.0041772 | 1335 | 64302 | 2011/2012 | May-2011 | 5 | 2011
25606 | L/V Fuse Box - Waimanoa Rd | 2011-05-22 15:37 | 2011-05-22 | 2011-05-22 15:55 | Calculated | TF924 | TF924 - Transformer Fuse: TF924 |  | 124SEG445-694 | Tihoi 124-02 (was Tihoi 124-05) | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 17 | 2 | 24418 | 34 | 0.00139 | 8.1907e-05 | 30 | 518 | 2011/2012 | May-2011 | 5 | 2011
25607 | L/V Line Down - Waikawau Rd | 2011-05-22 18:17 | 2011-05-22 | 2011-05-22 19:15 | Calculated | TF1840 | TF1840 - Transformer Fuse: TF1840 |  | 128SEG1616 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 4 | 24418 | 232 | 0.0095 | 0.00016381 | 15 | 872 | 2011/2012 | May-2011 | 5 | 2011
25608 | Faulty Sect/Bark On Private Line - SH 32 | 2011-05-22 18:55 | 2011-05-22 | 2011-05-22 21:38 | Calculated | 5531 | 5531 - Sectionaliser 5531 |  | 426SEG5531 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 163 | 13 | 24418 | 2121 | 0.08686 | 0.00053239 | 125 | 20399 | 2011/2012 | May-2011 | 5 | 2011
25609 | Recloser 5867 Tripped On Eearth Fault - Mokomiko Sub | 2011-05-22 21:17 | 2011-05-22 | 2011-05-22 21:24 | Calculated | 5867 | 5867 - Recloser with Bypass 5867 |  | 409SEG5761-5867 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 510 | 24418 | 3629 | 0.14862 | 0.020886 | 3470.2308 | 24696 | 2011/2012 | May-2011 | 5 | 2011
25610 | Possum at Tx363 - Haurua Rd | 2011-05-23 08:53 | 2011-05-23 | 2011-05-23 10:11 | Calculated | TF363 | TF363 - Transformer Fuse: TF363 |  | 112SEG1359 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24418 | 156 | 0.00639 | 8.1907e-05 | 30 | 2345 | 2011/2012 | May-2011 | 5 | 2011
25612 | Line Down @ Pole 52/141/12/8 - Waitanguru For Pungarehu Rd | 2011-05-24 07:26 | 2011-05-24 | 2011-05-24 11:26 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 239 | 12 | 24418 | 1419 | 0.05811 | 0.00049144 | 58 | 8077 | 2011/2012 | May-2011 | 5 | 2011
25613 | Private Tree Felling - Herekiekie St | 2011-05-24 07:51 | 2011-05-24 | 2011-05-24 09:27 | Calculated | 6003 | 6003 - Fault Thrower Switch Isolator 6003 |  | 424SEG6003-6559 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Third Party (includeds unauthorised contractors) |  | 3PAR |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 118 | 24418 | 11349 | 0.46478 | 0.0048325 | 521.3657 | 50146 | 2011/2012 | May-2011 | 5 | 2011
25615 | Re-Arrange Jumpers To Tx19K04 and 4082 - Fit Numbers - Burns St | 2011-05-24 10:02 | 2011-05-24 | 2011-05-24 11:42 | Calculated | 5705 | 5705 - Fused Link 5705 |  | 415SEG5705 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 99 | 13 | 24418 | 1288 | 0.05275 | 0.00053239 | 69.1667 | 6857 | 2011/2012 | May-2011 | 5 | 2011
25616 | Total Dismantle Of Tx12N03 - H/V Cable To Be Cut Away - Otukou | 2011-05-24 10:06 | 2011-05-24 | 2011-05-24 12:06 | Calculated | 5835 | 5835 - Fused Link 5835 |  | 418SEG5835-6544 | 512-01 Otukou | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 119 | 18 | 24418 | 2147 | 0.08793 | 0.00073716 | 175 | 20877 | 2011/2012 | May-2011 | 5 | 2011
25617 | Recloser 1512 Tripped - Faulty Iso Tx1453 | 2011-05-24 14:46 | 2011-05-24 | 2011-05-24 19:23 | Calculated | 1512 | 1512 - Recloser 1512 |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 276 | 165 | 24418 | 15268 | 0.62528 | 0.0067573 | 1090.5 | 97955 | 2011/2012 | May-2011 | 5 | 2011
25619 | Replace Tx15N01 With ETEL RTE and Replace O/H Joints - Chateau | 2011-05-25 09:04 | 2011-05-25 | 2011-05-25 16:06 | Calculated | 6631 | 6631 - Ring Main Unit 6631 |  | No Segment | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 422 | 82 | 24418 | 34649 | 1.419 | 0.0033582 | 11591.7857 | 4898109 | 2011/2012 | May-2011 | 5 | 2011
25618 | Replace 11kV Poles and Hardware at Pole 324-401 - Tangiwai | 2011-05-25 09:05 | 2011-05-25 | 2011-05-25 16:01 | Calculated | 5711 | 5711 - Air Break Switch 5711 |  | 416SEG5711-6174 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 416 | 40 | 24418 | 16648 | 0.68179 | 0.0016381 | 387.5 | 161277 | 2011/2012 | May-2011 | 5 | 2011
25620 | Fuse Pulled Apart at Tx2265 - SH 30 Pureora | 2011-05-25 12:31 | 2011-05-25 | 2011-05-25 14:13 | Calculated | TF2265 | TF2265 - Transformer Fuse: TF2265 |  | 119SEG710 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 1 | 24418 | 101 | 0.00414 | 4.0953e-05 | 10 | 1011 | 2011/2012 | May-2011 | 5 | 2011
25623 | Line Down - Te Mapara Feeder | 2011-05-25 21:23 | 2011-05-25 | 2011-05-26 10:32 | Calculated | 1728 | 1728 - Recloser 1728 |  | 117SEG1728-1260 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 789 | 44 | 24418 | 16924 | 0.6931 | 0.0018019 | 346.5 | 126796 | 2011/2012 | May-2011 | 5 | 2011
25622 | Recloser 5867 Tripped - By Makomiko Sub | 2011-05-25 22:13 | 2011-05-25 | 2011-05-25 22:21 | Calculated | 5867 | 5867 - Recloser with Bypass 5867 |  | 409SEG5761-5867 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 510 | 24418 | 4156 | 0.1702 | 0.020886 | 3470.2308 | 28282 | 2011/2012 | May-2011 | 5 | 2011
25630 | Recloser 5867 Tripped - Faulty Insulator | 2011-05-26 04:30 | 2011-05-26 | 2011-05-26 04:41 | Calculated | 5867 | 5867 - Recloser with Bypass 5867 |  | 409SEG5761-5867 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 11 | 510 | 24418 | 5703 | 0.23356 | 0.020886 | 3470.2308 | 38808 | 2011/2012 | May-2011 | 5 | 2011
25631 | Recloser 5867 Tripped - Faulty Insulator | 2011-05-26 05:23 | 2011-05-26 | 2011-05-26 05:25 | Calculated | 5867 | 5867 - Recloser with Bypass 5867 |  | 409SEG5761-5867 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 510 | 24418 | 1113 | 0.04558 | 0.020886 | 3470.2308 | 7576 | 2011/2012 | May-2011 | 5 | 2011
25637 | Recloser 5867 Tripped - Faulty Insulator | 2011-05-26 08:38 | 2011-05-26 | 2011-05-26 09:20 | Calculated | 5867 | 5867 - Recloser with Bypass 5867 |  | 409SEG5761-5867 | Southern 409-01 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 510 | 24418 | 21505 | 0.8807 | 0.020886 | 3470.2308 | 146328 | 2011/2012 | May-2011 | 5 | 2011
25635 | Faulty Insulator - SH 4 Before Bullians Rd | 2011-05-26 11:18 | 2011-05-26 | 2011-05-26 12:29 | Calculated | 5934 | 5934 - Air Break Switch 5934 |  | 409SEG5934 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 50 | 24418 | 2099 | 0.08596 | 0.0020477 | 389.75 | 20291 | 2011/2012 | May-2011 | 5 | 2011
25626 | Fuse Pulled Apart at Tx1083 - Maire Rd | 2011-05-26 14:32 | 2011-05-26 | 2011-05-26 16:10 | Calculated | TF1083 | TF1083 - Transformer Fuse: TF1083 |  | 113SEG1529 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 1 | 24418 | 98 | 0.00401 | 4.0953e-05 | 3 | 294 | 2011/2012 | May-2011 | 5 | 2011
25627 | Replace H/V Fuse at Tx2318 - Potaka Rd | 2011-05-26 15:35 | 2011-05-26 | 2011-05-26 17:23 | Calculated | TF2318 | TF2318 - Transformer Fuse: TF2318 |  | 114SEG1105-1118 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 1 | 24418 | 107 | 0.00438 | 4.0953e-05 | 10 | 1071 | 2011/2012 | May-2011 | 5 | 2011
25628 | L/V Fault - Mathers Rd | 2011-05-26 15:46 | 2011-05-26 | 2011-05-26 17:50 | Calculated | TF1744 | TF1744 - Transformer Fuse: TF1744 |  | 117SEG770-1787 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 4 | 24418 | 496 | 0.02031 | 0.00016381 | 25 | 3103 | 2011/2012 | May-2011 | 5 | 2011
25629 | Fuse Pulled Apart at Tx21O08 - SH 49 | 2011-05-26 20:27 | 2011-05-26 | 2011-05-26 21:58 | Calculated | TF21O8 | TF21O8 - Transformer Fuse: TF21O8 |  | 416SEG5780-6608 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 5 | 24418 | 455 | 0.01863 | 0.00020477 | 25 | 2278 | 2011/2012 | May-2011 | 5 | 2011
25647 | Faulty Insulator - Oio Rd | 2011-05-27 07:12 | 2011-05-27 | 2011-05-27 16:24 | Calculated | 5440 | 5440 - Recloser with Bypass & Links 5440 |  | 409SEG5439-5440 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 551 | 32 | 24418 | 11470 | 0.46974 | 0.0013105 | 221.25 | 83692 | 2011/2012 | May-2011 | 5 | 2011
25645 | Fuse Pulled Apart at Tx741 - Tihoi Rd | 2011-05-27 08:38 | 2011-05-27 | 2011-05-27 09:48 | Calculated | TF741 | TF741 - Transformer Fuse: TF741 |  | 124SEG700-428 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 3 | 24418 | 210 | 0.0086 | 0.00012286 | 30 | 2103 | 2011/2012 | May-2011 | 5 | 2011
25646 | Broken Earth - Amos Rd | 2011-05-27 14:14 | 2011-05-27 | 2011-05-27 16:08 | Calculated | TF3K3 | TF3K3 - Transformer Fuse: TF3K3 |  | No Segment | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 1 | 24418 | 114 | 0.00467 | 4.0953e-05 | 15 | 1712 | 2011/2012 | May-2011 | 5 | 2011
25649 | L/V Line Down - Tihoi Rd | 2011-05-30 11:26 | 2011-05-30 | 2011-05-30 12:49 | Calculated | TF1256 | TF1256 - Transformer Fuse: TF1256 |  | 120SEG484-483 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 2 | 24418 | 166 | 0.0068 | 8.1907e-05 | 30 | 2494 | 2011/2012 | May-2011 | 5 | 2011
25651 | Change Tx - Waitomo Caves Rd | 2011-05-31 10:15 | 2011-05-31 | 2011-05-31 14:44 | Calculated | T88A | T88A - 3 Phase : 200.00 kVA : GNDPAD |  | 101SEG746-1656 | Caves 101-08 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 269 | 1 | 24418 | 269 | 0.01102 | 4.0953e-05 | 200 | 53836 | 2011/2012 | May-2011 | 5 | 2011
25652 | Replace H/V Fuse at Tx16J3 - Erua Rd | 2011-05-31 15:53 | 2011-05-31 | 2011-05-31 18:00 | Calculated | TF16J03 | TF16J03 - Transformer Fuse: TF16J03 |  | 410SEG5631 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 1 | 24418 | 127 | 0.0052 | 4.0953e-05 | 5 | 635 | 2011/2012 | May-2011 | 5 | 2011
25655 | Remove SWER Line For Tree Cutting - Taumarunnui - Tokirima | 2011-06-01 08:48 | 2011-06-01 | 2011-06-01 16:19 | Calculated | 5300 | 5300 - Fused Link 5300 |  | 413SEG5300-5570 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 441 | 7 | 24417 | 2562 | 0.10493 | 0.00028669 | 78 | 31873 | 2011/2012 | June-2011 | 6 | 2011
25656 | Gen Set Connection and Disconnection - Burns St | 2011-06-01 09:33 | 2011-06-01 | 2011-06-01 16:06 | Calculated | TF20K15 | TF20K15 - Transformer Fuse: TF20K15 |  | 415SEG5704-REG28 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 47 | 26 | 24417 | 1204 | 0.04931 | 0.0010648 | 208 | 9637 | 2011/2012 | June-2011 | 6 | 2011
25658 | Broken Earth - Waione Rd | 2011-06-01 16:12 | 2011-06-01 | 2011-06-01 17:32 | Calculated | TF2K6 | TF2K6 - Transformer Fuse: TF2K6 |  | No Segment | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Protection | FAIL:FPRO |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 1 | 24417 | 80 | 0.00328 | 4.0955e-05 | 15 | 1202 | 2011/2012 | June-2011 | 6 | 2011
25659 | Fuse Pulled Apart at Tx8I71 - SH 43 | 2011-06-01 16:21 | 2011-06-01 | 2011-06-01 17:13 | Calculated | TF8I71 | TF8I71 - Transformer Fuse: TF8I71 |  | No Segment | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLA | Accidental Contact, Damage or Interference by TLC Staff | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 1 | 24417 | 52 | 0.00213 | 4.0955e-05 | 15 | 782 | 2011/2012 | June-2011 | 6 | 2011
25661 | New 11kV Extension For Paerata Rd - Forest Rd | 2011-06-02 08:42 | 2011-06-02 | 2011-06-02 15:17 | Calculated | TF2695 | TF2695 - Transformer Fuse: TF2695 |  | No Segment | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 395 | 1 | 24417 | 395 | 0.01618 | 4.0955e-05 | 50 | 19778 | 2011/2012 | June-2011 | 6 | 2011
25660 | Replace Rotten X/arm On Pole 162 - Main South Highway | 2011-06-02 09:03 | 2011-06-02 | 2011-06-02 10:27 | Calculated | 5329 | 5329 - Fused Link 5329 |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 84 | 19 | 24417 | 1599 | 0.06549 | 0.00077815 | 135.5 | 11406 | 2011/2012 | June-2011 | 6 | 2011
25662 | Install Structure For New RG28 - Turoa Feeder | 2011-06-02 10:04 | 2011-06-02 | 2011-06-02 16:22 | Calculated | 5704 | 5704 - Air Break Switch 5704 |  | 415SEG5704-REG28 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 17 | 26 | 24417 | 798 | 0.03268 | 0.0010648 | 208 | 6385 | 2011/2012 | June-2011 | 6 | 2011
25668 | RAL Maintenance - To Tower 3 | 2011-06-03 14:33 | 2011-06-03 | 2011-06-03 15:04 | Calculated | 6614 | 6614 - Ring Main Unit 6614 |  | 419SEG6614-6138 | Chateau 419-01 | Rural D | Chateau | Tawhai Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 31 | 25 | 24417 | 779 | 0.0319 | 0.0010239 | 6337.5 | 197624 | 2011/2012 | June-2011 | 6 | 2011
25669 | Line Down - Tapuwahine Sub | 2011-06-03 15:07 | 2011-06-03 | 2011-06-03 17:49 | Calculated | 5465 | 5465 - Recloser 5465 |  | No Segment | No Asset Group | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 41 | 24417 | 6635 | 0.27174 | 0.0016792 | 270.5 | 43780 | 2011/2012 | June-2011 | 6 | 2011
25670 | Fuse Pulled Apart - Bledisloe Avenue | 2011-06-03 15:51 | 2011-06-03 | 2011-06-03 16:53 | Calculated | TF2566 | TF2566 - Transformer Fuse: TF2566 |  | 112SEG310-628 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 36 | 24417 | 2237 | 0.09162 | 0.0014744 | 205.7143 | 12785 | 2011/2012 | June-2011 | 6 | 2011
25671 | Wind - Whakapirau Rd | 2011-06-03 17:52 | 2011-06-03 | 2011-06-03 21:53 | Calculated | TF2540 | TF2540 - Transformer Fuse: TF2540 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 241 | 2 | 24417 | 482 | 0.01974 | 8.191e-05 | 5 | 1205 | 2011/2012 | June-2011 | 6 | 2011
25672 | Fuse Pulled Apart - Te Maire Valley Rd | 2011-06-04 11:21 | 2011-06-04 | 2011-06-04 12:30 | Calculated | TF10H03 | TF10H03 - Transformer Fuse: TF10H3 |  | 403SEG5368-5230 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 2 | 24417 | 136 | 0.00557 | 8.191e-05 | 10 | 681 | 2011/2012 | June-2011 | 6 | 2011
25674 | Jumper Off at P49/67/17/7 - Paraheka Sub | 2011-06-04 15:38 | 2011-06-04 | 2011-06-04 16:15 | Calculated | 1126 | 1126 - Recloser with Bypass & Links 1126 |  | 114SEG1126-1127 | Aria 114-04 | Rural D | Aria | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 31 | 24417 | 1152 | 0.04718 | 0.0012696 | 225 | 8362 | 2011/2012 | June-2011 | 6 | 2011
25675 | Sectionalisor 5505 - Kokomiko Sub | 2011-06-04 22:21 | 2011-06-04 | 2011-06-04 23:50 | Calculated | 5505 | 5505 - Sectionaliser with Bypass 5505 |  | 421SEG5502-5505 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 33 | 24417 | 2946 | 0.12065 | 0.0013515 | 262.5 | 23441 | 2011/2012 | June-2011 | 6 | 2011
25676 | Faulty Polymer - Ongarue Feeder | 2011-06-05 08:26 | 2011-06-05 | 2011-06-05 17:59 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 572 | 33 | 24417 | 10599 | 0.43408 | 0.0013515 | 262.5 | 79787 | 2011/2012 | June-2011 | 6 | 2011
25677 | Tree Cutting - Manunui - Tokaanu Highway | 2011-06-07 08:43 | 2011-06-07 | 2011-06-07 15:25 | Calculated | 5379 | 5379 - Sectionaliser with Bypass 5379 |  | 408SEG5514-5379 | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 401 | 40 | 24417 | 16068 | 0.65807 | 0.0016382 | 255 | 102437 | 2011/2012 | June-2011 | 6 | 2011
25678 | Broken DDO at Tx5i12 - Ongarue Rd | 2011-06-07 09:24 | 2011-06-07 | 2011-06-07 12:02 | Calculated | TF5I12 | TF5I12 - Transformer Fuse: TF5I12 |  | 402SEG5798 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 13 | 24417 | 1025 | 0.04198 | 0.00053242 | 70 | 5486 | 2011/2012 | June-2011 | 6 | 2011
25679 | Fuse Pulled Apart - Forest Rd | 2011-06-07 14:12 | 2011-06-07 | 2011-06-07 15:20 | Calculated | TF939 | TF939 - Transformer Fuse: TF939 |  | 123SEG473-695RET | Mokai 123-04 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 1 | 24417 | 67 | 0.00274 | 4.0955e-05 | 15 | 1017 | 2011/2012 | June-2011 | 6 | 2011
25680 | Broken X/arm at Pole 299 - Taharoa | 2011-06-07 15:38 | 2011-06-07 | 2011-06-07 17:57 | Calculated | 609 | 609 - Circuit Breaker 609 (Rural Feeder) 609 |  | No Segment | 201-01 Taharoa | Rural D | Rural | Taharoa Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 109 | 24417 | 15167 | 0.62117 | 0.0044641 | 765.8571 | 106569 | 2011/2012 | June-2011 | 6 | 2011
25681 | Fuse Pulled Apart - Ngamokai Rd | 2011-06-07 16:44 | 2011-06-07 | 2011-06-07 17:37 | Calculated | TF22M4 | TF22M4 - Transformer Fuse: TF22M4 |  | 416SEG5965 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 4 | 24417 | 208 | 0.00852 | 0.00016382 | 20 | 1043 | 2011/2012 | June-2011 | 6 | 2011
25682 | Changing Poles and X/arms - Paewhenua Rd | 2011-06-09 09:29 | 2011-06-09 | 2011-06-09 14:35 | Calculated | 707 | 707 - Air Break Switch 707 |  | 111SEG707-399 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 267 | 26 | 24417 | 6921 | 0.28345 | 0.0010648 | 155 | 41263 | 2011/2012 | June-2011 | 6 | 2011
25683 | Maintenance For RAL - Soldiers Rd | 2011-06-09 10:47 | 2011-06-09 | 2011-06-09 14:17 | Calculated | 5949 | 5949 - Circuit Breaker with Bypass 5949 |  | 415SEG5949RET | Turoa 415-02 | Urban A | Turoa | Direct from Ohakune Supply |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 210 | 2 | 24417 | 420 | 0.0172 | 8.191e-05 | 0 | 0 | 2011/2012 | June-2011 | 6 | 2011
25685 | Tree Scape vs Line - Manunui Sub and Kuratau Sub | 2011-06-09 11:55 | 2011-06-09 | 2011-06-09 12:15 | Calculated | 5189 | 5189 - Circuit Breaker 5189 |  | 608SEG5193-5189 | 509-01 Kuratau | Rural D | Taumarunui / Kuratau 33 | Borough Zone Substation |  | Third Party (includeds unauthorised contractors) | ETRE2 | 3PAR:ETRE2:ETRE1 | Tree Clearing/Trimming Activities | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 10 | 4 | 24417 | 40 | 0.00164 | 0.00016382 | 450 | 4500 | 2011/2012 | June-2011 | 6 | 2011
25688 | L/V Maintenance - Waihora Rd | 2011-06-10 11:19 | 2011-06-10 | 2011-06-10 12:35 | Calculated | TF972 | TF972 - Transformer Fuse: TF972 |  | 123SEG446-806 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 76 | 3 | 24417 | 228 | 0.00934 | 0.00012287 | 22.5 | 1714 | 2011/2012 | June-2011 | 6 | 2011
25689 | Fuse Pulled Apart - Tx22O4 - Kurakina Valley Rd | 2011-06-10 17:18 | 2011-06-10 | 2011-06-10 18:29 | Calculated | TF22O4 | TF22O4 - Transformer Fuse: TF22O4 |  | 416SEG5555 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 1 | 24417 | 71 | 0.00291 | 4.0955e-05 | 15 | 1067 | 2011/2012 | June-2011 | 6 | 2011
25690 | Lightning - Tx148 - Main South Rd | 2011-06-11 08:38 | 2011-06-11 | 2011-06-11 10:07 | Calculated | TF148 | TF148 - Transformer Fuse: TF148 |  | 104SEG547-444 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 4 | 24417 | 356 | 0.01458 | 0.00016382 | 25 | 2230 | 2011/2012 | June-2011 | 6 | 2011
25692 | Line Down In River - Okau E/W Sub | 2011-06-12 16:02 | 2011-06-12 | 2011-06-13 13:44 | Calculated | 1630 | 1630 - Recloser 1630 |  | No Segment | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1302 | 49 | 24417 | 27620 | 1.1312 | 0.0020068 | 358 | 227868 | 2011/2012 | June-2011 | 6 | 2011
25694 | L/V Clash - Hangatiki Caves Rd | 2011-06-13 08:00 | 2011-06-13 | 2011-06-13 09:23 | Calculated | TF81 | TF81 - Transformer Fuse: TF81 |  | 101SEG1272-257 | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 12 | 24417 | 986 | 0.04038 | 0.00049146 | 81.8182 | 6726 | 2011/2012 | June-2011 | 6 | 2011
25695 | L/V Line Down - John St | 2011-06-13 10:40 | 2011-06-13 | 2011-06-13 12:14 | Calculated | TF559 | TF559 - Transformer Fuse: TF559 |  | No Segment | Te Kuiti South 104-01 | Urban A | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 56 | 24417 | 5272 | 0.21592 | 0.0022935 | 305.4545 | 28758 | 2011/2012 | June-2011 | 6 | 2011
25696 | Possum - Waipapa Rd | 2011-06-13 11:50 | 2011-06-13 | 2011-06-13 14:40 | Calculated | 254 | 254 - Fused Link 254 |  | 107SEG254 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 2 | 24417 | 340 | 0.01392 | 8.191e-05 | 15 | 2554 | 2011/2012 | June-2011 | 6 | 2011
25697 | Fault Zone Extended - Borough Sub and Manunui Sub | 2011-06-13 16:29 | 2011-06-13 | 2011-06-13 16:32 | Calculated | 5876 | 5876 - Circuit Breaker Manunui SF6 5876 |  | No Segment | 510-01 Manunui | Rural B | Manunui / AFFCO Retired | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 1230 | 24417 | 3812 | 0.15612 | 0.050375 | 9011.4251 | 27935 | 2011/2012 | June-2011 | 6 | 2011
25699 | Replaced Red Tagged Pole - Gradara Ave | 2011-06-14 10:09 | 2011-06-14 | 2011-06-14 16:02 | Calculated | TF1072 | TF1072 - Transformer Fuse: TF1072 |  | 112SEG391-627 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 6 | 24417 | 2118 | 0.08674 | 0.00024573 | 50 | 17655 | 2011/2012 | June-2011 | 6 | 2011
25701 | Possum - Makokomiko Rd | 2011-06-14 16:01 | 2011-06-14 | 2011-06-14 17:30 | Calculated | TF9J15 | TF9J15 - Transformer Fuse: TF9J15 |  | No Segment | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 2 | 24417 | 178 | 0.00729 | 8.191e-05 | 15 | 1337 | 2011/2012 | June-2011 | 6 | 2011
25703 | Bolt Down Tx02J10 - Waimiha Rd | 2011-06-15 09:52 | 2011-06-15 | 2011-06-15 09:58 | Calculated | TF2J10 | TF2J10 - Transformer Fuse: TF2J10 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 6 | 3 | 24417 | 18 | 0.00074 | 0.00012287 | 5 | 30 | 2011/2012 | June-2011 | 6 | 2011
25704 | Bolt Down Tx02J07 - Waimiha Rd | 2011-06-15 10:10 | 2011-06-15 | 2011-06-15 10:15 | Calculated | TF2J7 | TF2J7 - Transformer Fuse: TF2J7 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 5 | 2 | 24417 | 10 | 0.00041 | 8.191e-05 | 20 | 103 | 2011/2012 | June-2011 | 6 | 2011
25707 | Bolt Down Tx2J6 - Paraketu Rd | 2011-06-15 10:55 | 2011-06-15 | 2011-06-15 11:04 | Calculated | TF2J6 | TF2J6 - Transformer Fuse: TF2J6 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 9 | 2 | 24417 | 18 | 0.00074 | 8.191e-05 | 10 | 92 | 2011/2012 | June-2011 | 6 | 2011
25709 | Bolt Down Tx2J2 - Waimiha Rd | 2011-06-15 12:45 | 2011-06-15 | 2011-06-15 12:53 | Calculated | TF2J2 | TF2J2 - Transformer Fuse: TF2J2 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 8 | 5 | 24417 | 41 | 0.00168 | 0.00020478 | 16.6667 | 136 | 2011/2012 | June-2011 | 6 | 2011
25712 | Bolt Down Tx4I8 - SH 4 | 2011-06-15 14:27 | 2011-06-15 | 2011-06-15 14:31 | Calculated | TF4I8 | TF4I8 - Transformer Fuse: TF4I8 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 4 | 3 | 24417 | 12 | 0.00049 | 0.00012287 | 15 | 63 | 2011/2012 | June-2011 | 6 | 2011
25713 | Replace H/V Fuse at Tx364 - Veale Rd | 2011-06-16 07:03 | 2011-06-16 | 2011-06-16 08:21 | Calculated | TF364 | TF364 - Transformer Fuse: TF364 |  | No Segment | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24417 | 156 | 0.00639 | 8.191e-05 | 15 | 1175 | 2011/2012 | June-2011 | 6 | 2011
25714 | Scheduled Maintenance - Tukehu St | 2011-06-16 09:16 | 2011-06-16 | 2011-06-16 15:23 | Calculated | TF11S01 | TF11S01 - Transformer Fuse: TF11S01 |  | 424SEG5207-6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage |  | POUT |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 366 | 5 | 24417 | 1831 | 0.07499 | 0.00020478 | 30 | 10991 | 2011/2012 | June-2011 | 6 | 2011
25716 | UPGRADE TX1400 TO A 30KVA - FORD RD | 2011-06-16 10:34 | 2011-06-16 | 2011-06-16 15:43 | Calculated | 654 | 654 - Fused Link 654 |  | 120SEG654 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 309 | 5 | 24417 | 1246 | 0.05103 | 0.00020478 | 65 | 15101 | 2011/2012 | June-2011 | 6 | 2011
25717 | BOLT DOWN TX4I13 - SH 4 | 2011-06-16 10:40 | 2011-06-16 | 2011-06-16 10:58 | Calculated | TF4I13 | TF4I13 - Transformer Fuse: TF4I13 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 18 | 1 | 24417 | 18 | 0.00074 | 4.0955e-05 | 15 | 272 | 2011/2012 | June-2011 | 6 | 2011
25718 | L/V LINE DOWN - ALEXANDRA ST | 2011-06-16 11:24 | 2011-06-16 | 2011-06-16 12:06 | Calculated | TF603 | TF603 - Transformer Fuse: TF603 |  | 108SEG211-212 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 42 | 55 | 24417 | 2319 | 0.09497 | 0.0022525 | 364.7959 | 15382 | 2011/2012 | June-2011 | 6 | 2011
25720 | BOLT DOWN TX 5H8 - SH 40 | 2011-06-16 14:04 | 2011-06-16 | 2011-06-16 14:25 | Calculated | TF5H8 | TF5H8 - Transformer Fuse: TF5H8 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 21 | 1 | 24417 | 21 | 0.00086 | 4.0955e-05 | 10 | 211 | 2011/2012 | June-2011 | 6 | 2011
25721 | JUMPER OFF TX2279 - TAUMATAMAIRE RD | 2011-06-16 14:57 | 2011-06-16 | 2011-06-16 16:02 | Calculated | TF2279 | TF2279 - Transformer Fuse: TF2279 |  | 128SEG1523 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 2 | 24417 | 128 | 0.00524 | 8.191e-05 | 10 | 644 | 2011/2012 | June-2011 | 6 | 2011
25722 | BOTL DOWN TX4H5 - SH 40 | 2011-06-17 09:16 | 2011-06-17 | 2011-06-17 09:24 | Calculated | TF4H5 | TF4H5 - Transformer Fuse: TF4H5 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 8 | 2 | 24417 | 16 | 0.00066 | 8.191e-05 | 15 | 122 | 2011/2012 | June-2011 | 6 | 2011
25723 | Relocate Pole - Tx2059 - Mapiu South | 2011-06-17 09:17 | 2011-06-17 | 2011-06-17 13:50 | Calculated | 1647 | 1647 - Fused Link 1647 |  | 115SEG1647-1646 | Mokauiti 115-05 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 31 | 24417 | 2024 | 0.08289 | 0.0012696 | 243 | 12848 | 2011/2012 | June-2011 | 6 | 2011
25725 | WRONG .LINK REMOVED - SH 4 BY NEAL'S | 2011-06-17 09:35 | 2011-06-17 | 2011-06-17 12:29 | Calculated | 1723 | 1723 - Fused Link 1723 |  | 115SEG1723-1724 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 174 | 17 | 24417 | 2961 | 0.12127 | 0.00069624 | 143 | 24915 | 2011/2012 | June-2011 | 6 | 2011
25726 | TREE VS LINE - TAHAROA ON SAND | 2011-06-17 20:22 | 2011-06-17 | 2011-06-17 23:52 | Calculated | 509 | 509 - Fused Link 509 |  | 126SEG509 | Rural 126-02 | Rural D | Rural | Taharoa Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 210 | 109 | 24417 | 7869 | 0.32228 | 0.0044641 | 765.8571 | 54947 | 2011/2012 | June-2011 | 6 | 2011
25728 | TREE THROUGH LINE P119 -120 - NATIONAL PARK BEHIND SERVICE STATION | 2011-06-18 01:32 | 2011-06-18 | 2011-06-18 07:41 | Calculated | 5147 | 5147 - Circuit Breaker with Bypass 5147 |  | No Segment | No Asset Group | Remote Rural F | National Park | National Park Zone Substation |  | Vegetation |  |  |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 369 | 42 | 24417 | 10722 | 0.43912 | 0.0017201 | 630.5 | 129820 | 2011/2012 | June-2011 | 6 | 2011
25729 | ROTTEN X/ARM AT POLE 79 - RAURIMU FEEDER | 2011-06-19 06:26 | 2011-06-19 | 2011-06-19 10:32 | Calculated | 5142 | 5142 - Circuit Breaker with Bypass 5142 |  | 410SEG6766-5141 | 501-01 National Park | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 245 | 333 | 24417 | 28659 | 1.1737 | 0.013638 | 2118.0833 | 188462 | 2011/2012 | June-2011 | 6 | 2011
25730 | TREE THROUGH LINE - MAPARA SOUTH | 2011-06-19 16:20 | 2011-06-19 | 2011-06-19 19:51 | Calculated | 1335 | 1335 - Sectionaliser 1335 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 210 | 17 | 24417 | 3575 | 0.14641 | 0.00069624 | 140.5 | 29554 | 2011/2012 | June-2011 | 6 | 2011
25731 | FAULTY INSULATOR - P4211026 - SH 40 | 2011-06-20 09:36 | 2011-06-20 | 2011-06-20 10:50 | Calculated | 5574 | 5574 - Fused Link 5574 |  | 421SEG5574 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLX | Faulty Manufacture | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 5 | 24417 | 371 | 0.01519 | 0.00020478 | 22.5 | 1670 | 2011/2012 | June-2011 | 6 | 2011
25732 | MAGPIE - SH 47 | 2011-06-20 10:01 | 2011-06-20 | 2011-06-20 11:18 | Calculated | TF14N02 | TF14N02 - Transformer Fuse: TF14N02 |  | 609SEG5787-6007 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 2 | 24417 | 154 | 0.00631 | 8.191e-05 | 15 | 1157 | 2011/2012 | June-2011 | 6 | 2011
25733 | FAULTY TX 821 - MAIN STH RD - PIOPIO | 2011-06-21 11:18 | 2011-06-21 | 2011-06-21 13:23 | Calculated | TF821 | TF821 - Transformer Fuse: TF821 |  | No Segment | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:O7IITG | Transformer - Ageing of Associated Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 2 | 24417 | 248 | 0.01016 | 8.191e-05 | 10 | 1241 | 2011/2012 | June-2011 | 6 | 2011
25734 | TURKEY UP POLE AT TX 1403 - SH 30 | 2011-06-21 11:27 | 2011-06-21 | 2011-06-21 11:40 | Calculated | TF1403 | TF1403 - Transformer Fuse: TF1403 |  | 103SEG728 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:BBOP | Bird Contact at Pole | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 2 | 24417 | 26 | 0.00106 | 8.191e-05 | 15 | 196 | 2011/2012 | June-2011 | 6 | 2011
25737 | REPLACE X/ARM AND REPAIR CONDUCTOR AT POLE 1130232 | 2011-06-22 09:58 | 2011-06-22 | 2011-06-22 15:32 | Calculated | 1524 | 1524 - Air Break Switch 1524 |  | 128SEG1524-1261 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 245 | 23 | 24417 | 5618 | 0.23009 | 0.00094197 | 250 | 61066 | 2011/2012 | June-2011 | 6 | 2011
25736 | REPLACE SWER POLE - MANGATIKI RD TE MAPARA | 2011-06-22 10:04 | 2011-06-22 | 2011-06-22 14:45 | Calculated | 1721 | 1721 - Sectionaliser 1721 |  | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 15 | 24417 | 4227 | 0.17312 | 0.00061433 | 109 | 30718 | 2011/2012 | June-2011 | 6 | 2011
25738 | LOWER TAP AT TX3225 - PAERATA RD | 2011-06-22 13:03 | 2011-06-22 | 2011-06-22 13:20 | Calculated | TF3225 | TF3225 - Transformer Fuse: TF3225 |  | 129SEG1407 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 17 | 4 | 24417 | 68 | 0.00278 | 0.00016382 | 400 | 6860 | 2011/2012 | June-2011 | 6 | 2011
25739 | FUSE PULLED APART TX5H2 - SH 40 | 2011-06-22 15:31 | 2011-06-22 | 2011-06-22 17:11 | Calculated | TF5H2 | TF5H2 - Transformer Fuse: TF5H2 |  | No Segment | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 3 | 24417 | 300 | 0.01229 | 0.00012287 | 11.25 | 1127 | 2011/2012 | June-2011 | 6 | 2011
25740 | REPLACE POLE AND POLYMERS - INSTALL T/O LINK FOR TX11G5 - WESTERN FEEDER | 2011-06-23 09:44 | 2011-06-23 | 2011-06-23 12:56 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 192 | 19 | 24417 | 3653 | 0.14961 | 0.00077815 | 130.5 | 25090 | 2011/2012 | June-2011 | 6 | 2011
25741 | CONNECT NEW EARTH MAT AT TX8I14 - TUNAKOTEKOTE RD | 2011-06-23 10:03 | 2011-06-23 | 2011-06-23 13:10 | Calculated | TF8I14 | TF8I14 - Transformer Fuse: TF8I14 |  | 403SEG5811-5315 | Western 403-03 | Rural B | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 187 | 3 | 24417 | 561 | 0.02298 | 0.00012287 | 15 | 2807 | 2011/2012 | June-2011 | 6 | 2011
25742 | FAULTY L/A AT TX7D4 - NIHONIHO | 2011-06-24 01:29 | 2011-06-24 | 2011-06-24 04:20 | Calculated | 5641 | 5641 - Recloser with Bypass & Links 5641 |  | 413SEG6781-5666 | No Asset Group | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 171 | 381 | 24417 | 50680 | 2.0756 | 0.015604 | 2600.4048 | 345506 | 2011/2012 | June-2011 | 6 | 2011
25743 | REPLACE POLES AND X/ARMS - RANGIPO/HAUTU | 2011-06-24 09:13 | 2011-06-24 | 2011-06-24 14:31 | Calculated | TF11S02 | TF11S02 - Transformer Fuse: TF11S02 |  | 424SEG5207-6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 317 | 9 | 24417 | 2855 | 0.11693 | 0.0003686 | 100 | 31726 | 2011/2012 | June-2011 | 6 | 2011
25745 | L/V NEUTRAL FAULT-RIVER RD | 2011-06-24 09:30 | 2011-06-24 | 2011-06-24 10:41 | Calculated | TF7D4 | TF7D4 - Transformer Fuse: TF7D4 |  | 413SEG5996-5758 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 8 | 24417 | 562 | 0.02302 | 0.00032764 | 44.4444 | 3122 | 2011/2012 | June-2011 | 6 | 2011
25746 | REPLACE X/ARM AT POLE 1141143 ALSO POLE TX2620 - ARIA FEEDER | 2011-06-24 09:33 | 2011-06-24 | 2011-06-24 16:10 | Calculated | 1102 | 1102 - Air Break Switch 1102 |  | 114SEG1102-1126RET | Aria 114-03 | Rural D | Aria | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 397 | 57 | 24417 | 22638 | 0.92714 | 0.0023344 | 408 | 162043 | 2011/2012 | June-2011 | 6 | 2011
25747 | L/V FAULT - MANGATOA RD | 2011-06-24 10:14 | 2011-06-24 | 2011-06-24 11:24 | Calculated | TF1616 | TF1616 - Transformer Fuse: TF1616 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 2 | 24417 | 140 | 0.00573 | 8.191e-05 | 15 | 1053 | 2011/2012 | June-2011 | 6 | 2011
25748 | L/V FAULT - PONGAHURA RD | 2011-06-24 11:03 | 2011-06-24 | 2011-06-24 11:30 | Calculated | TF8H1 | TF8H1 - Transformer Fuse: TF8H1 |  | 403SEG5316-5622 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 27 | 2 | 24417 | 54 | 0.00221 | 8.191e-05 | 15 | 406 | 2011/2012 | June-2011 | 6 | 2011
25749 | VEHICLE VS LINE - SH 30 - KOPAKI | 2011-06-24 12:45 | 2011-06-24 | 2011-06-24 14:00 | Calculated | TF32 | TF32 - Transformer Fuse: TF32 |  | No Segment | Benneydale 103-06 | Rural D | Benneydale | Waitete Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 4 | 24417 | 300 | 0.01229 | 0.00016382 | 25 | 1880 | 2011/2012 | June-2011 | 6 | 2011
25750 | REPLACE H/V FUSE AT TX7Q16 - SH 32 | 2011-06-28 08:27 | 2011-06-28 | 2011-06-28 11:00 | Calculated | TF7Q16 | TF7Q16 - Transformer Fuse: TF7Q16 |  | 426SEG5847-5592 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 152 | 1 | 24417 | 152 | 0.00623 | 4.0955e-05 | 15 | 2282 | 2011/2012 | June-2011 | 6 | 2011
25751 | UPGRADE TX1316 - PUKETAWAI RD | 2011-06-28 10:39 | 2011-06-28 | 2011-06-28 16:50 | Calculated | TF1316 | TF1316 - Transformer Fuse: TF1316 |  | 110SEG387-328 | McDonalds 110-04 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 371 | 2 | 24417 | 742 | 0.03039 | 8.191e-05 | 15 | 5566 | 2011/2012 | June-2011 | 6 | 2011
25752 | SCHEDULED MAINTENANCE - DEKKER DR | 2011-06-28 13:09 | 2011-06-28 | 2011-06-28 15:01 | Calculated | TF11S16 | TF11S16 - Transformer Fuse: TF11S16 |  | 424SEG5910 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 112 | 1 | 24417 | 112 | 0.00459 | 4.0955e-05 | 100 | 11215 | 2011/2012 | June-2011 | 6 | 2011
25753 | RECLOSER 474 TRIPPED - MAROTIRI RD | 2011-06-28 14:48 | 2011-06-28 | 2011-06-28 14:49 | Calculated | 474 | 474 - Recloser 474 |  | 123SEG441-474 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 149 | 24417 | 173 | 0.00709 | 0.0061023 | 2099.25 | 2449 | 2011/2012 | June-2011 | 6 | 2011
25755 | FUSE PULLED APART - MAIROA RD | 2011-06-29 07:00 | 2011-06-29 | 2011-06-29 09:48 | Calculated | TF2541 | TF2541 - Transformer Fuse: TF2541 |  | 116SEG1354-1334 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 2 | 24417 | 336 | 0.01376 | 8.191e-05 | 15 | 2522 | 2011/2012 | June-2011 | 6 | 2011
25757 | REPLACE TWO OLD "H" STRUCTURE - 14/13 &14 - MATAPUNA | 2011-06-29 09:02 | 2011-06-29 | 2011-06-29 14:04 | Calculated | 5915 | 5915 - Air Break Switch 5915 |  | 404SEG5915-5838 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 43 | 24417 | 12606 | 0.51628 | 0.0017611 | 279.3056 | 81887 | 2011/2012 | June-2011 | 6 | 2011
25758 | REPLACE POLE - LINKS 519 - CAVES | 2011-06-29 09:35 | 2011-06-29 | 2011-06-29 14:21 | Calculated | 261 | 261 - Fused Link 261 |  | 101SEG261-519 | Caves 101-02 | Urban A | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 286 | 44 | 24417 | 12592 | 0.51571 | 0.001802 | 497.5 | 142384 | 2011/2012 | June-2011 | 6 | 2011
25759 | UPGRADE TX424 - NGAHAPE RD | 2011-06-29 10:12 | 2011-06-29 | 2011-06-29 15:07 | Calculated | TF424 | TF424 - Transformer Fuse: TF424 |  | No Segment | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 5 | 24417 | 1472 | 0.06029 | 0.00020478 | 50 | 14722 | 2011/2012 | June-2011 | 6 | 2011
25760 | REPLACE POLES FOR NEW 3 PHASE EXTENSION - ONGARUE | 2011-06-29 10:48 | 2011-06-29 | 2011-06-29 15:40 | Calculated | 5355 | 5355 - Sectionaliser with Bypass & Links 5355 |  | 421SEG5355-5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 292 | 21 | 24417 | 6136 | 0.2513 | 0.00086006 | 150 | 43832 | 2011/2012 | June-2011 | 6 | 2011
25761 | REPLACE POLES AND X/ARMS - RANGIPO/HAUTU | 2011-06-30 09:05 | 2011-06-30 | 2011-06-30 16:01 | Calculated | 5207 | 5207 - Air Break Switch 5207 |  | 424SEG5200-6650 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 416 | 51 | 24417 | 21225 | 0.86927 | 0.0020887 | 537.5 | 223698 | 2011/2012 | June-2011 | 6 | 2011
25763 | REPLACE POLES AND X/ARMS - RANGIPO/HAUTU | 2011-07-01 09:06 | 2011-07-01 | 2011-07-01 15:13 | Calculated | 6657 | 6657 - Fused Link 6657 |  | 424SEG5207-6657 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 367 | 9 | 24415 | 3304 | 0.13533 | 0.00036863 | 100 | 36716 | 2011/2012 | July-2011 | 7 | 2011
25764 | REPLACE STAY STRAPS ON POLE 58 - HUIRIMU | 2011-07-01 12:26 | 2011-07-01 | 2011-07-01 14:22 | Calculated | 724 | 724 - Air Break Switch 724 |  | 121SEG724-425RET | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 64 | 30 | 24415 | 1895 | 0.07762 | 0.0012288 | 515 | 32530 | 2011/2012 | July-2011 | 7 | 2011
25766 | FAULTY L/A AT TX650 - TUMUTUMU RD | 2011-07-01 13:47 | 2011-07-01 | 2011-07-01 17:56 | Calculated | 109 | 109 - Recloser with bypass 109 |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Protection | FAIL:FPRO:FPRB | Protection Malfunction | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 249 | 102 | 24415 | 10074 | 0.41262 | 0.0041778 | 787 | 84148 | 2011/2012 | July-2011 | 7 | 2011
25769 | RED TAGGED L/V POLES - MERRINS AVE | 2011-07-04 09:40 | 2011-07-04 | 2011-07-04 15:21 | Calculated | TF379 | TF379 - Transformer Fuse: TF379 |  | No Segment | Gravel Scoop 109-10 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 341 | 23 | 24415 | 7846 | 0.32136 | 0.00094204 | 52.2727 | 17833 | 2011/2012 | July-2011 | 7 | 2011
25770 | REPLACE I/R POLE AND FIT DDO FOR TX7R10 - WAIHAHA | 2011-07-04 11:08 | 2011-07-04 | 2011-07-04 13:24 | Calculated | 5110 | 5110 - Fused Link 5110 |  | 426SEG5110-5593 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 135 | 16 | 24415 | 2162 | 0.08855 | 0.00065533 | 135.5 | 18317 | 2011/2012 | July-2011 | 7 | 2011
25771 | L/V FAULT - PORO ST | 2011-07-04 13:07 | 2011-07-04 | 2011-07-04 14:23 | Calculated | TF13L1 | TF13L1 - Transformer Fuse: TF13L1 |  | 410SEG5139-5829 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 21 | 24415 | 1598 | 0.06545 | 0.00086013 | 52.5 | 3997 | 2011/2012 | July-2011 | 7 | 2011
25772 | REPLACE H/V FUSE AT TX7K15 - WAITUHI | 2011-07-04 14:38 | 2011-07-04 | 2011-07-04 16:17 | Calculated | TF7K15 | TF7K15 - Transformer Fuse: TF7K15 |  | 402SEG5756 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 2 | 24415 | 198 | 0.00811 | 8.1917e-05 | 30 | 2974 | 2011/2012 | July-2011 | 7 | 2011
25773 | L/V FAULT AT SERVICE BOX - KIRIKAU VALLEY RD | 2011-07-05 09:34 | 2011-07-05 | 2011-07-05 10:00 | Calculated | TF11H02 | TF11H02 - Transformer Fuse: TF11H02 |  | 403SEG5765-5653 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 26 | 5 | 24415 | 131 | 0.00537 | 0.00020479 | 25 | 657 | 2011/2012 | July-2011 | 7 | 2011
25774 | L/V POLE CHANGES -PAEWHENUA RD | 2011-07-05 09:35 | 2011-07-05 | 2011-07-05 16:02 | Calculated | TF282 | TF282 - Transformer Fuse: TF282 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 387 | 4 | 24415 | 1548 | 0.0634 | 0.00016383 | 30 | 11613 | 2011/2012 | July-2011 | 7 | 2011
25775 | LINE DOWN/SPLICE LET DO - MAROTIRI SUB | 2011-07-06 07:34 | 2011-07-06 | 2011-07-06 11:04 | Calculated | CB1 | CB1 - Circuit Breaker Mokai Feeder B1 |  | No Segment | 212-01 Marotiri | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 210 | 346 | 24415 | 24073 | 0.98599 | 0.014172 | 3838.4167 | 359968 | 2011/2012 | July-2011 | 7 | 2011
25780 | HIGH WINDS - BAYLEY RD | 2011-07-06 11:31 | 2011-07-06 | 2011-07-06 17:15 | Calculated | TF610 | TF610 - Transformer Fuse: TF610 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 344 | 2 | 24415 | 688 | 0.02818 | 8.1917e-05 | 10 | 3441 | 2011/2012 | July-2011 | 7 | 2011
25782 | HIGH WINDS - MOHAKATINO RD | 2011-07-06 12:36 | 2011-07-06 | 2011-07-06 14:36 | Calculated | TF2185 | TF2185 - Transformer Fuse: TF2185 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 2 | 24415 | 240 | 0.00983 | 8.1917e-05 | 10 | 1202 | 2011/2012 | July-2011 | 7 | 2011
25783 | HIGH WINDS - ONGARUE SUB | 2011-07-06 13:08 | 2011-07-06 | 2011-07-06 15:15 | Calculated | TPOngarue CB192 | TPOngarue CB192 - 33kV Minimum Oil Circuit Breaker TP192 |  | No Segment | 514-01 Transpower Ongarue | Rural D | Ongarue / Taumarunui 33 | Direct from Ongarue Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 25 | 5167 | 24415 | 27567 | 1.1291 | 0.21163 | 47564.2755 | 301482 | 2011/2012 | July-2011 | 7 | 2011
25781 | 11KV X/ARM LAYING ON L/V - TOKAANU VILLAGE FEEDER | 2011-07-06 13:13 | 2011-07-06 | 2011-07-06 15:06 | Calculated | 5033 | 5033 - Circuit Breaker 5033 |  | No Segment | Tokaanu 420-01 | Rural C | Tokaanu | Tokaanu Village Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAB | Cross-Arm Bent | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 113 | 65 | 24415 | 7362 | 0.30154 | 0.0026623 | 400 | 45306 | 2011/2012 | July-2011 | 7 | 2011
25784 | HIGH WINDS - WAIKAWAU RD | 2011-07-06 13:23 | 2011-07-06 | 2011-07-06 15:20 | Calculated | 1612 | 1612 - Sectionaliser with Bypass & Links 1612 |  | 128SEG1611-1612 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 117 | 41 | 24415 | 4804 | 0.19676 | 0.0016793 | 302.5 | 35447 | 2011/2012 | July-2011 | 7 | 2011
25790 | TREES THROUGH LINES - TUMUTUMU RD | 2011-07-06 15:31 | 2011-07-06 | 2011-07-07 12:18 | Calculated | 109 | 109 - Recloser with bypass 109 |  | 101SEG110-109 | Caves 101-09 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1247 | 102 | 24415 | 20438 | 0.83711 | 0.0041778 | 787 | 140612 | 2011/2012 | July-2011 | 7 | 2011
25785 | HIGH WINDS TX306 - BAYLEY RD | 2011-07-06 15:56 | 2011-07-06 | 2011-07-06 17:36 | Calculated | TF306 | TF306 - Transformer Fuse: TF306 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 4 | 24415 | 402 | 0.01647 | 0.00016383 | 30 | 3015 | 2011/2012 | July-2011 | 7 | 2011
25786 | HIGH WINDS AT TX56 - OPARURE RD | 2011-07-06 16:28 | 2011-07-06 | 2011-07-06 18:29 | Calculated | TF56 | TF56 - Transformer Fuse: TF56 |  | 107SEG706-243 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 4 | 24415 | 484 | 0.01982 | 0.00016383 | 30 | 3636 | 2011/2012 | July-2011 | 7 | 2011
25787 | BROKEN DDO AT TX1844 - PAST WAIKAWAU SCHOOL - ISOLATION | 2011-07-06 16:55 | 2011-07-06 | 2011-07-07 11:35 | Calculated | 1616 | 1616 - Sectionaliser with Bypass & Links 1616 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related |  | FAIL |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1120 | 16 | 24415 | 17929 | 0.73434 | 0.00065533 | 120 | 134470 | 2011/2012 | July-2011 | 7 | 2011
25788 | HIGH WINDS - HANGATIKI | 2011-07-06 17:11 | 2011-07-06 | 2011-07-06 17:14 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 3 | 111 | 24415 | 353 | 0.01446 | 0.0045464 | 3280.8571 | 10444 | 2011/2012 | July-2011 | 7 | 2011
25789 | HIGH WINDS - HANGATIKI | 2011-07-06 20:09 | 2011-07-06 | 2011-07-06 20:11 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 111 | 24415 | 242 | 0.00991 | 0.0045464 | 3280.8571 | 7163 | 2011/2012 | July-2011 | 7 | 2011
25791 | HIGH WINDS - TIROHANGA RD | 2011-07-07 05:49 | 2011-07-07 | 2011-07-07 08:28 | Calculated | TF772 | TF772 - Transformer Fuse: TF772 |  | 129SEG451-787 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 159 | 5 | 24415 | 795 | 0.03256 | 0.00020479 | 62.5 | 9946 | 2011/2012 | July-2011 | 7 | 2011
25792 | LIGHTING - MANGAOKEWA RD | 2011-07-07 09:06 | 2011-07-07 | 2011-07-07 11:04 | Calculated | TF910 | TF910 - Transformer Fuse: TF910 |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 118 | 4 | 24415 | 473 | 0.01937 | 0.00016383 | 25 | 2957 | 2011/2012 | July-2011 | 7 | 2011
25793 | WIND/TREES - TE MAHOE RD | 2011-07-07 10:08 | 2011-07-07 | 2011-07-07 14:03 | Calculated | TF2158 | TF2158 - Transformer Fuse: TF2158 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 235 | 2 | 24415 | 470 | 0.01925 | 8.1917e-05 | 10 | 2352 | 2011/2012 | July-2011 | 7 | 2011
25794 | TREE THROUGH L/V - HAPPY VALLEY RD | 2011-07-07 11:23 | 2011-07-07 | 2011-07-07 13:00 | Calculated | TF270 | TF270 - Transformer Fuse: TF270 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 3 | 24415 | 291 | 0.01192 | 0.00012288 | 30 | 2914 | 2011/2012 | July-2011 | 7 | 2011
25797 | LIGHTING - TE MAHOE RD | 2011-07-07 20:51 | 2011-07-07 | 2011-07-07 23:51 | Calculated | TF2180 | TF2180 - Transformer Fuse: TF2180 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 2 | 24415 | 360 | 0.01475 | 8.1917e-05 | 25 | 4502 | 2011/2012 | July-2011 | 7 | 2011
25795 | LIGHTING BODDIES RD | 2011-07-07 21:31 | 2011-07-07 | 2011-07-07 22:45 | Calculated | TF2469 | TF2469 - Transformer Fuse: TF2469 |  | No Segment | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 74 | 1 | 24415 | 74 | 0.00303 | 4.0958e-05 | 10 | 741 | 2011/2012 | July-2011 | 7 | 2011
25796 | LIGHTING - OLD TE KUITI RD | 2011-07-07 21:46 | 2011-07-07 | 2011-07-07 22:30 | Calculated | TF389 | TF389 - Transformer Fuse: TF389 |  | No Segment | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 2 | 24415 | 88 | 0.0036 | 8.1917e-05 | 0 | 0 | 2011/2012 | July-2011 | 7 | 2011
25844 | FAULTY TX2230 PROBABLY DUE TO LIGHTNING - MANGATORO RD | 2011-07-08 07:30 | 2011-07-08 | 2011-07-11 14:01 | Calculated | 1631 | 1631 - Sectionaliser with Incoming Link1631 |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4710 | 10 | 24415 | 8520 | 0.34897 | 0.00040958 | 70 | 93937 | 2011/2012 | July-2011 | 7 | 2011
25798 | FAULTY TX2230 - POLE 22 BEFORE MANGATORO RD | 2011-07-08 07:31 | 2011-07-08 | 2011-07-11 14:01 | Calculated | 1631 | 1631 - Sectionaliser with Incoming Link1631 |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 4710 | 10 | 24415 | 8519 | 0.34892 | 0.00040958 | 70 | 93928 | 2011/2012 | July-2011 | 7 | 2011
25799 | OCB 242 PLUS 788 TRIPPED - HANGATIKI | 2011-07-08 07:35 | 2011-07-08 | 2011-07-08 07:38 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 111 | 24415 | 240 | 0.00983 | 0.0045464 | 3280.8571 | 7108 | 2011/2012 | July-2011 | 7 | 2011
25800 | LIGHTING - FULLERTON RD | 2011-07-08 07:55 | 2011-07-08 | 2011-07-08 09:00 | Calculated | TF1177 | TF1177 - Transformer Fuse: TF1177 |  | 101SEG500-186 | Caves 101-07 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 5 | 24415 | 325 | 0.01331 | 0.00020479 | 50 | 3259 | 2011/2012 | July-2011 | 7 | 2011
25801 | HIGH WINDS - TE MAHOE RD | 2011-07-08 07:56 | 2011-07-08 | 2011-07-08 10:17 | Calculated | TF2158 | TF2158 - Transformer Fuse: TF2158 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 2 | 24415 | 282 | 0.01155 | 8.1917e-05 | 10 | 1411 | 2011/2012 | July-2011 | 7 | 2011
25802 | LIGHTING - BODDIES TD | 2011-07-08 08:51 | 2011-07-08 | 2011-07-08 09:49 | Calculated | TF60 | TF60 - Transformer Fuse: TF60 |  | No Segment | Oparure 107-05 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 2 | 24415 | 116 | 0.00475 | 8.1917e-05 | 10 | 581 | 2011/2012 | July-2011 | 7 | 2011
25803 | REPLACE 11KV POLES AND HARDWARE - TURAKINA VALLEY RD | 2011-07-08 09:11 | 2011-07-08 | 2011-07-08 13:36 | Calculated | 5691 | 5691 - Fused Link 5691 |  | 416SEG5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 264 | 5 | 24415 | 1320 | 0.05407 | 0.00020479 | 45 | 11886 | 2011/2012 | July-2011 | 7 | 2011
25804 | BROKEN DDO AT TX2768 - SH 3 MOKAU | 2011-07-08 09:44 | 2011-07-08 | 2011-07-08 12:50 | Calculated | TF2768 | TF2768 - Transformer Fuse: TF2768 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Cable - Underground | FAIL:FCAB |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 3 | 24415 | 558 | 0.02285 | 0.00012288 | 25 | 4653 | 2011/2012 | July-2011 | 7 | 2011
25806 | LIGHTING - SANDEL RD | 2011-07-08 15:25 | 2011-07-08 | 2011-07-08 18:21 | Calculated | TF1077 | TF1077 - Transformer Fuse: TF1077 |  | 120SEG485-413 | Whakamaru 120-01 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 2 | 24415 | 352 | 0.01442 | 8.1917e-05 | 100 | 17615 | 2011/2012 | July-2011 | 7 | 2011
25807 | WIRE ACROSS LINE - BURN ST | 2011-07-08 17:20 | 2011-07-08 | 2011-07-08 18:55 | Calculated | TF20K13 | TF20K13 - Transformer Fuse: TF20K13 |  | 415SEGTempLink33-5704RET | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Conductor - Overhead | FAIL:FCDT |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 11 | 24415 | 1046 | 0.04284 | 0.00045054 | 110 | 10466 | 2011/2012 | July-2011 | 7 | 2011
25808 | LIGHTING - SH 3 MAHOENUI | 2011-07-08 19:14 | 2011-07-08 | 2011-07-08 21:44 | Calculated | TF1889 | TF1889 - Transformer Fuse: TF1889 |  | 128SEG1358-1602 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 2 | 24415 | 300 | 0.01229 | 8.1917e-05 | 15 | 2251 | 2011/2012 | July-2011 | 7 | 2011
25809 | LIGHTING - WHAWHARUA RD | 2011-07-09 14:56 | 2011-07-09 | 2011-07-09 15:32 | Calculated | TF2538 | TF2538 - Transformer Fuse: TF2538 |  | No Segment | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 2 | 24415 | 72 | 0.00295 | 8.1917e-05 | 25 | 910 | 2011/2012 | July-2011 | 7 | 2011
25810 | LIGHTING - OPATU SUB | 2011-07-09 15:30 | 2011-07-09 | 2011-07-09 17:04 | Calculated | 5417 | 5417 - Recloser 5417 |  | 413SEG5418-5417 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 68 | 24415 | 6337 | 0.25955 | 0.0027852 | 459.5556 | 42830 | 2011/2012 | July-2011 | 7 | 2011
25811 | HIGH WINDS - LINE DOWN - KAHOREKAU RD | 2011-07-09 16:00 | 2011-07-09 | 2011-07-09 17:54 | Calculated | 593 | 593 - Fused Link 593 |  | 122SEG593-595 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 26 | 24415 | 2969 | 0.12161 | 0.0010649 | 222.5 | 25413 | 2011/2012 | July-2011 | 7 | 2011
25812 | LIGHTING - KAITEKE SUB | 2011-07-09 16:10 | 2011-07-09 | 2011-07-09 17:00 | Calculated | 5439 | 5439 - Fused Link 5439 |  | 409SEG5439-5440 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 32 | 24415 | 1572 | 0.06439 | 0.0013107 | 221.25 | 10874 | 2011/2012 | July-2011 | 7 | 2011
25813 | LIGHTING - WAITOMO VALLEY RD | 2011-07-09 19:46 | 2011-07-09 | 2011-07-09 21:04 | Calculated | TF214 | TF214 - Transformer Fuse: TF214 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 5 | 24415 | 390 | 0.01597 | 0.00020479 | 30 | 2343 | 2011/2012 | July-2011 | 7 | 2011
25814 | LIGHTING - MARAETAI SUBSTATION | 2011-07-09 22:49 | 2011-07-09 | 2011-07-09 22:58 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 8 | 167 | 24415 | 1361 | 0.05574 | 0.0068401 | 2740.5 | 22335 | 2011/2012 | July-2011 | 7 | 2011
25815 | LIGHTING - MCLEAN RD | 2011-07-09 23:15 | 2011-07-09 | 2011-07-10 06:31 | Calculated | TF1348 | TF1348 - Transformer Fuse: TF1348 |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 435 | 2 | 24415 | 870 | 0.03563 | 8.1917e-05 | 15 | 6527 | 2011/2012 | July-2011 | 7 | 2011
25816 | LIGHTING - MCREADY RD | 2011-07-09 23:36 | 2011-07-09 | 2011-07-10 00:16 | Calculated | TF171 | TF171 - Transformer Fuse: TF171 |  | 114SEG1104 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 4 | 24415 | 160 | 0.00655 | 0.00016383 | 33.3333 | 1339 | 2011/2012 | July-2011 | 7 | 2011
25817 | LIGHTING - POKURU RD - AT OKAMA BLOCK | 2011-07-09 23:50 | 2011-07-09 | 2011-07-10 08:10 | Calculated | 442 | 442 - Fused Link 442 |  | 129SEG442-2238 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 499 | 28 | 24415 | 13976 | 0.57243 | 0.0011468 | 265 | 132279 | 2011/2012 | July-2011 | 7 | 2011
25818 | LIGHTNING - DUNCAN RD | 2011-07-10 06:55 | 2011-07-10 | 2011-07-10 09:47 | Calculated | TF419 | TF419 - Transformer Fuse: TF419 |  | No Segment | Wharepapa 122-08 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 172 | 2 | 24415 | 344 | 0.01409 | 8.1917e-05 | 25 | 4307 | 2011/2012 | July-2011 | 7 | 2011
25819 | LIGHTNING - MAIHIIHI RD | 2011-07-10 07:16 | 2011-07-10 | 2011-07-10 09:20 | Calculated | TF482 | TF482 - Transformer Fuse: TF482 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 124 | 2 | 24415 | 248 | 0.01016 | 8.1917e-05 | 30 | 3724 | 2011/2012 | July-2011 | 7 | 2011
25820 | LIGHTNING - MANGAOTAKI RD | 2011-07-10 07:46 | 2011-07-10 | 2011-07-10 11:09 | Calculated | TF1627 | TF1627 - Transformer Fuse: TF1627 |  | 113SEG1548-1526 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 203 | 2 | 24415 | 406 | 0.01663 | 8.1917e-05 | 7.5 | 1523 | 2011/2012 | July-2011 | 7 | 2011
25821 | LIGHTNING - TAUPAKI RD | 2011-07-10 07:56 | 2011-07-10 | 2011-07-10 12:46 | Calculated | TF1075 | TF1075 - Transformer Fuse: TF1075 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 290 | 2 | 24415 | 580 | 0.02376 | 8.1917e-05 | 15 | 4351 | 2011/2012 | July-2011 | 7 | 2011
25822 | LIGHTNING - AOTEAROA RD | 2011-07-10 08:31 | 2011-07-10 | 2011-07-10 11:20 | Calculated | TF916 | TF916 - Transformer Fuse: TF916 |  | No Segment | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 169 | 2 | 24415 | 338 | 0.01384 | 8.1917e-05 | 10 | 1691 | 2011/2012 | July-2011 | 7 | 2011
25823 | LIGHTNING - NGAPAENGA RD | 2011-07-10 08:40 | 2011-07-10 | 2011-07-10 10:40 | Calculated | TF576 | TF576 - Transformer Fuse: TF576 |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 2 | 24415 | 240 | 0.00983 | 8.1917e-05 | 10 | 1202 | 2011/2012 | July-2011 | 7 | 2011
25824 | LIGHTNING - NGAPAENGA RD | 2011-07-10 08:40 | 2011-07-10 | 2011-07-10 11:00 | Calculated | TF322 | TF322 - Transformer Fuse: TF322 |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 139 | 1 | 24415 | 139 | 0.00569 | 4.0958e-05 | 10 | 1391 | 2011/2012 | July-2011 | 7 | 2011
25825 | LIGHTNING - NGAROMA RD | 2011-07-10 09:00 | 2011-07-10 | 2011-07-10 10:20 | Calculated | TF1190 | TF1190 - Transformer Fuse: TF1190 |  | 122SEG633 | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 3 | 24415 | 237 | 0.00971 | 0.00012288 | 15 | 1187 | 2011/2012 | July-2011 | 7 | 2011
25826 | LIGHTNING - DREADNOUGHT RD | 2011-07-10 09:05 | 2011-07-10 | 2011-07-10 11:48 | Calculated | 5613 | 5613 - Fused Link 5613 |  | 415SEG5695-5692 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 162 | 3 | 24415 | 486 | 0.01991 | 0.00012288 | 50 | 8107 | 2011/2012 | July-2011 | 7 | 2011
25827 | LIGHTNING - RANGATAUA RD | 2011-07-10 09:45 | 2011-07-10 | 2011-07-10 12:26 | Calculated | TF20L11 | TF20L11 - Transformer Fuse: TF20L11 |  | 416SEG5677-5681 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 3 | 24415 | 483 | 0.01978 | 0.00012288 | 15 | 2419 | 2011/2012 | July-2011 | 7 | 2011
25828 | LIGHTNING - RANGATAUA RD | 2011-07-10 09:45 | 2011-07-10 | 2011-07-10 13:04 | Calculated | TF20L63 | TF20L63 - Transformer Fuse: TF20L63 |  | 416SEG5677-5681 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 4 | 24415 | 797 | 0.03264 | 0.00016383 | 20 | 3986 | 2011/2012 | July-2011 | 7 | 2011
25829 | LIGHTNING - RANGATAUA RD | 2011-07-10 09:45 | 2011-07-10 | 2011-07-10 13:06 | Calculated | TF20L9 | TF20L9 - Transformer Fuse: TF20L9 |  | 416SEG5677-5681 | Tangiwai 416-03 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 201 | 2 | 24415 | 402 | 0.01647 | 8.1917e-05 | 20 | 4026 | 2011/2012 | July-2011 | 7 | 2011
25831 | LIGHTNING - MANGAOKEWA RD | 2011-07-10 11:09 | 2011-07-10 | 2011-07-10 13:05 | Calculated | TF141 | TF141 - Transformer Fuse: TF141 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 116 | 2 | 24415 | 232 | 0.0095 | 8.1917e-05 | 15 | 1744 | 2011/2012 | July-2011 | 7 | 2011
25830 | LIGHTNING - MANGAOKEWA NTH RD | 2011-07-10 11:10 | 2011-07-10 | 2011-07-10 13:04 | Calculated | TF138 | TF138 - Transformer Fuse: TF138 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 4 | 24415 | 456 | 0.01868 | 0.00016383 | 33.3333 | 3806 | 2011/2012 | July-2011 | 7 | 2011
25832 | LIGHTNING - RIMU RD | 2011-07-10 12:03 | 2011-07-10 | 2011-07-10 14:03 | Calculated | TF5E4 | TF5E4 - Transformer Fuse: TF5E4 |  | No Segment | Nihoniho 412-02 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 1 | 24415 | 120 | 0.00492 | 4.0958e-05 | 3 | 360 | 2011/2012 | July-2011 | 7 | 2011
25833 | LIGHTNING - SH 41 | 2011-07-10 12:58 | 2011-07-10 | 2011-07-10 15:46 | Calculated | TF4013 | TF4013 - Transformer Fuse: TF4013 |  | No Segment | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 168 | 5 | 24415 | 841 | 0.03445 | 0.00020479 | 25 | 4205 | 2011/2012 | July-2011 | 7 | 2011
25845 | FAULTY TX DUE TO LIGHTNING - MCLEAN RD | 2011-07-10 13:25 | 2011-07-10 | 2011-07-11 12:08 | Calculated | T2974 | T2974 - 3 Phase : 50.00 kVA : POLEMNT |  | 119SEG406-411 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1362 | 1 | 24415 | 1362 | 0.05579 | 4.0958e-05 | 50 | 68134 | 2011/2012 | July-2011 | 7 | 2011
25834 | LIGHTNING - PONGAHURA RD | 2011-07-10 13:30 | 2011-07-10 | 2011-07-10 15:48 | Calculated | TF8H1 | TF8H1 - Transformer Fuse: TF8H1 |  | 403SEG5316-5622 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 138 | 2 | 24415 | 276 | 0.0113 | 8.1917e-05 | 15 | 2073 | 2011/2012 | July-2011 | 7 | 2011
25840 | LIGHTNING - LOWER RETARUKE RD | 2011-07-10 14:03 | 2011-07-10 | 2011-07-10 16:24 | Calculated | 5396 | 5396 - Sectionaliser 5396 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 140 | 45 | 24415 | 6311 | 0.25849 | 0.0018431 | 183.75 | 25773 | 2011/2012 | July-2011 | 7 | 2011
25841 | LIGHTNING - TIHOI RD | 2011-07-10 14:25 | 2011-07-10 | 2011-07-10 17:36 | Calculated | 1132 | 1132 - Fused Link 1132 |  | 124SEG475-440 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 63 | 24415 | 11986 | 0.49093 | 0.0025804 | 595.5 | 113303 | 2011/2012 | July-2011 | 7 | 2011
25835 | FLOATING X/ARM - WAIHI SUB | 2011-07-10 14:26 | 2011-07-10 | 2011-07-10 15:30 | Calculated | 5897 | 5897 - Earth Working Link 5897 |  | 406SEG5897-5481 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 19 | 24415 | 1219 | 0.04993 | 0.00077821 | 108.75 | 6979 | 2011/2012 | July-2011 | 7 | 2011
25836 | LIGHTNING - MANGAOKEWA RD | 2011-07-10 14:42 | 2011-07-10 | 2011-07-10 16:02 | Calculated | TF31 | TF31 - Transformer Fuse: TF31 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 3 | 24415 | 240 | 0.00983 | 0.00012288 | 37.5 | 3011 | 2011/2012 | July-2011 | 7 | 2011
25838 | LIGHTNING - SH 46 | 2011-07-10 15:21 | 2011-07-10 | 2011-07-10 19:36 | Calculated | TF12P03 | TF12P03 - Transformer Fuse: TF12P03 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 254 | 5 | 24415 | 1271 | 0.05206 | 0.00020479 | 18.75 | 4767 | 2011/2012 | July-2011 | 7 | 2011
25837 | LIGHTNING - WAIKINO RD | 2011-07-10 15:22 | 2011-07-10 | 2011-07-10 16:02 | Calculated | TF742 | TF742 - Transformer Fuse: TF742 |  | 129SEG434-426 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 2 | 24415 | 78 | 0.00319 | 8.1917e-05 | 15 | 587 | 2011/2012 | July-2011 | 7 | 2011
25884 | L/V FAULT - OIO RD | 2011-07-10 16:40 | 2011-07-10 | 2011-07-12 13:53 | Calculated | TF13G02 | TF13G02 - Transformer Fuse: TF13G02 |  | 410SEG5396-5668 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2712 | 5 | 24415 | 13561 | 0.55544 | 0.00020479 | 15 | 40685 | 2011/2012 | July-2011 | 7 | 2011
25842 | LIGHTNING - MANGATEITEI RD | 2011-07-10 17:06 | 2011-07-10 | 2011-07-10 17:39 | Calculated | TF20M12 | TF20M12 - Transformer Fuse: TF20M12 |  | No Segment | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 32 | 1 | 24415 | 32 | 0.00131 | 4.0958e-05 | 10 | 322 | 2011/2012 | July-2011 | 7 | 2011
25843 | LIGHTNING - MANGATEITEI RD | 2011-07-10 17:06 | 2011-07-10 | 2011-07-10 18:34 | Calculated | 6012 | 6012 - Air Break Switch 6012 |  | 415SEG6012 | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 29 | 24415 | 597 | 0.02445 | 0.0011878 | 286.875 | 8680 | 2011/2012 | July-2011 | 7 | 2011
25847 | LIGHTNING - MANGAOKEWA NTH RD | 2011-07-10 20:56 | 2011-07-10 | 2011-07-11 08:02 | Calculated | TF138 | TF138 - Transformer Fuse: TF138 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 666 | 4 | 24415 | 2665 | 0.10915 | 0.00016383 | 33.3333 | 22211 | 2011/2012 | July-2011 | 7 | 2011
25848 | LIGHTNING - MANGAOTAKI RD | 2011-07-11 06:20 | 2011-07-11 | 2011-07-11 08:06 | Calculated | 1517 | 1517 - Fused Link 1517 |  | 116SEG1517 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 5 | 24415 | 530 | 0.02171 | 0.00020479 | 52.5 | 5574 | 2011/2012 | July-2011 | 7 | 2011
25849 | LIGHTNING - PAEKAKA RD | 2011-07-11 07:35 | 2011-07-11 | 2011-07-11 09:14 | Calculated | TF1992 | TF1992 - Transformer Fuse: TF1992 |  | No Segment | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 1 | 24415 | 99 | 0.00405 | 4.0958e-05 | 15 | 1487 | 2011/2012 | July-2011 | 7 | 2011
25850 | LIGHTNING - PAEKAKA RD | 2011-07-11 07:35 | 2011-07-11 | 2011-07-11 09:14 | Calculated | TF1991 | TF1991 - Transformer Fuse: TF1991 |  | No Segment | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 1 | 24415 | 99 | 0.00405 | 4.0958e-05 | 15 | 1487 | 2011/2012 | July-2011 | 7 | 2011
25852 | LIGHTNING - SH 32 | 2011-07-11 08:40 | 2011-07-11 | 2011-07-11 10:43 | Calculated | TF5Q8 | TF5Q8 - Transformer Fuse: TF5Q8 |  | 426SEG5847-5592 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 3 | 24415 | 369 | 0.01511 | 0.00012288 | 10 | 1231 | 2011/2012 | July-2011 | 7 | 2011
25853 | LIGHTNING - KOUTUROA RD | 2011-07-11 11:37 | 2011-07-11 | 2011-07-11 14:17 | Calculated | TF13H02 | TF13H02 - Transformer Fuse: TF13H02 |  | 410SEG5597-5396 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 160 | 4 | 24415 | 640 | 0.02621 | 0.00016383 | 20 | 3203 | 2011/2012 | July-2011 | 7 | 2011
25854 | LIGHTNING STRIKE TX557 - TE WAIREKA RD | 2011-07-11 12:22 | 2011-07-11 | 2011-07-11 16:05 | Calculated | 123 | 123 - Circuit Breaker 123 |  | No Segment | 203-01 Te Waireka Road | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 223 | 1171 | 24415 | 59465 | 2.4356 | 0.047962 | 7505.6587 | 411001 | 2011/2012 | July-2011 | 7 | 2011
25862 | LINE DOWN - TE MAPARA | 2011-07-11 12:51 | 2011-07-11 | 2011-07-12 16:06 | Calculated | 687 | 687 - Circuit Breaker 687 |  | No Segment | 207-01 Wairere Falls | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 196 | 239 | 24415 | 25173 | 1.0311 | 0.0097891 | 1806 | 190514 | 2011/2012 | July-2011 | 7 | 2011
25855 | EARTH REPAIRS AT TX13G2 - LOWER RETARUKE RD | 2011-07-11 13:06 | 2011-07-11 | 2011-07-11 14:47 | Calculated | 5396 | 5396 - Sectionaliser 5396 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 101 | 45 | 24415 | 4552 | 0.18644 | 0.0018431 | 183.75 | 18589 | 2011/2012 | July-2011 | 7 | 2011
25856 | LIGHTNING - RANGITOTO RD | 2011-07-11 13:36 | 2011-07-11 | 2011-07-11 15:13 | Calculated | TF2860 | TF2860 - Transformer Fuse: TF2860 |  | No Segment | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 1 | 24415 | 97 | 0.00397 | 4.0958e-05 | 15 | 1457 | 2011/2012 | July-2011 | 7 | 2011
25857 | LIGHTNING -AHUROA RD | 2011-07-11 13:36 | 2011-07-11 | 2011-07-11 16:58 | Calculated | TF2831 | TF2831 - Transformer Fuse: TF2831 |  | No Segment | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 2 | 24415 | 404 | 0.01655 | 8.1917e-05 | 30 | 6065 | 2011/2012 | July-2011 | 7 | 2011
25858 | LIGHTNING -ARATAKI RD | 2011-07-11 13:41 | 2011-07-11 | 2011-07-11 17:05 | Calculated | TF2756 | TF2756 - Transformer Fuse: TF2756 |  | 120SEG422-428 | Whakamaru 120-05 (was part 124-01) | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 204 | 1 | 24415 | 204 | 0.00836 | 4.0958e-05 | 15 | 3062 | 2011/2012 | July-2011 | 7 | 2011
25859 | LIGHTNING -TE KUMI RD | 2011-07-11 13:45 | 2011-07-11 | 2011-07-11 14:24 | Calculated | TF2479 | TF2479 - Transformer Fuse: TF2479 |  | 107SEG1020-515 | Oparure 107-03 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 1 | 24415 | 39 | 0.0016 | 4.0958e-05 | 15 | 587 | 2011/2012 | July-2011 | 7 | 2011
25860 | LIGHTNING -WHAREPAPA RD | 2011-07-11 14:52 | 2011-07-11 | 2011-07-11 16:59 | Calculated | 392 | 392 - Recloser with Bypass 392 |  | 122SEG376-380 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 127 | 74 | 24415 | 9411 | 0.38546 | 0.0030309 | 695 | 88392 | 2011/2012 | July-2011 | 7 | 2011
25863 | LIGHTNING - MAIROA RD | 2011-07-11 15:30 | 2011-07-11 | 2011-07-11 18:49 | Calculated | TF151 | TF151 - Transformer Fuse: TF151 |  | 107SEG176-269 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 199 | 2 | 24415 | 398 | 0.0163 | 8.1917e-05 | 25 | 4980 | 2011/2012 | July-2011 | 7 | 2011
25864 | LIGHTNING - MOHAKATINO RD | 2011-07-11 15:34 | 2011-07-11 | 2011-07-11 17:55 | Calculated | TF2185 | TF2185 - Transformer Fuse: TF2185 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 2 | 24415 | 282 | 0.01155 | 8.1917e-05 | 10 | 1412 | 2011/2012 | July-2011 | 7 | 2011
25865 | LIGHTNING - WAIPUNA RD | 2011-07-11 16:09 | 2011-07-11 | 2011-07-11 17:54 | Calculated | TF293 | TF293 - Transformer Fuse: TF293 |  | 101SEG1272-257 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 2 | 24415 | 210 | 0.0086 | 8.1917e-05 | 15 | 1578 | 2011/2012 | July-2011 | 7 | 2011
25861 | LIGHTNING - WAIPUNA RD | 2011-07-11 16:10 | 2011-07-11 | 2011-07-11 17:33 | Calculated | TF691 | TF691 - Transformer Fuse: TF691 |  | No Segment | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 2 | 24415 | 166 | 0.0068 | 8.1917e-05 | 0 | 0 | 2011/2012 | July-2011 | 7 | 2011
25866 | LIGHTNING - MANGATEA RD | 2011-07-11 16:35 | 2011-07-11 | 2011-07-11 19:35 | Calculated | TF43 | TF43 - Transformer Fuse: TF43 |  | No Segment | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 2 | 24415 | 360 | 0.01475 | 8.1917e-05 | 15 | 2703 | 2011/2012 | July-2011 | 7 | 2011
25867 | LIGHTNING - MANGATEA RD OFF SH 3 | 2011-07-11 16:35 | 2011-07-11 | 2011-07-11 19:48 | Calculated | 235 | 235 - Fused Link 235 |  | 104SEG235 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 20 | 24415 | 3864 | 0.15826 | 0.00081917 | 90 | 17389 | 2011/2012 | July-2011 | 7 | 2011
25868 | LIGHTNING - MAIN STH RD - PIOPIO | 2011-07-11 16:45 | 2011-07-11 | 2011-07-11 21:09 | Calculated | TF1709 | TF1709 - Transformer Fuse: TF1709 |  | 113SEG1343-1339 | Mahoenui 113-02 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 264 | 3 | 24415 | 792 | 0.03244 | 0.00012288 | 15 | 3963 | 2011/2012 | July-2011 | 7 | 2011
25869 | LIGHTNING - WAIPA VALLEY RD | 2011-07-11 17:03 | 2011-07-11 | 2011-07-11 19:39 | Calculated | TF2320 | TF2320 - Transformer Fuse: TF2320 |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 156 | 1 | 24415 | 156 | 0.00639 | 4.0958e-05 | 5 | 781 | 2011/2012 | July-2011 | 7 | 2011
25885 | LIGHTNING - WAIPA VALLEY RD | 2011-07-11 17:03 | 2011-07-11 | 2011-07-12 15:34 | Calculated | TF915 | TF915 - Transformer Fuse: TF915 |  | No Segment | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1350 | 6 | 24415 | 2782 | 0.11395 | 0.00024575 | 65 | 14626 | 2011/2012 | July-2011 | 7 | 2011
25870 | LIGHTNING - NGAPAENGA RD | 2011-07-11 17:04 | 2011-07-11 | 2011-07-11 18:32 | Calculated | TF576 | TF576 - Transformer Fuse: TF576 |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 2 | 24415 | 176 | 0.00721 | 8.1917e-05 | 10 | 882 | 2011/2012 | July-2011 | 7 | 2011
25871 | LIGHTNING - MANGAOKEWA RD | 2011-07-11 17:06 | 2011-07-11 | 2011-07-11 19:08 | Calculated | TF910 | TF910 - Transformer Fuse: TF910 |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 4 | 24415 | 488 | 0.01999 | 0.00016383 | 25 | 3055 | 2011/2012 | July-2011 | 7 | 2011
25872 | LIGHTNING - BAYLEY RD | 2011-07-11 17:12 | 2011-07-11 | 2011-07-11 17:49 | Calculated | TF343 | TF343 - Transformer Fuse: TF343 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 2 | 24415 | 74 | 0.00303 | 8.1917e-05 | 15 | 558 | 2011/2012 | July-2011 | 7 | 2011
25873 | LIGHTNING - SEAFUND RD | 2011-07-11 17:12 | 2011-07-11 | 2011-07-11 19:40 | Calculated | 372 | 372 - Fused Link 372 |  | 122SEG372 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 148 | 25 | 24415 | 3705 | 0.15175 | 0.001024 | 143.5 | 21269 | 2011/2012 | July-2011 | 7 | 2011
25881 | LIGHTNING -RANGITOTO RD POLE 117 | 2011-07-11 17:29 | 2011-07-11 | 2011-07-11 21:21 | Calculated | 823 | 823 - Fused Link 823 |  | 106SEG193RET | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 231 | 4 | 24415 | 924 | 0.03785 | 0.00016383 | 65 | 15023 | 2011/2012 | July-2011 | 7 | 2011
25875 | LIGHTNING - SH 3 MAHOENUI | 2011-07-11 17:38 | 2011-07-11 | 2011-07-11 20:28 | Calculated | TF1889 | TF1889 - Transformer Fuse: TF1889 |  | 128SEG1358-1602 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 170 | 2 | 24415 | 340 | 0.01393 | 8.1917e-05 | 15 | 2553 | 2011/2012 | July-2011 | 7 | 2011
25877 | LIGHTNING - NEWMAN RD | 2011-07-11 18:18 | 2011-07-11 | 2011-07-11 20:10 | Calculated | TF360 | TF360 - Transformer Fuse: TF360 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 3 | 24415 | 336 | 0.01376 | 0.00012288 | 25 | 2803 | 2011/2012 | July-2011 | 7 | 2011
25878 | LIGHTNING - TAHAIA BUSH RD | 2011-07-11 18:25 | 2011-07-11 | 2011-07-11 20:56 | Calculated | TF1178 | TF1178 - Transformer Fuse: TF1178 |  | 109SEG341-587 | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 2 | 24415 | 300 | 0.01229 | 8.1917e-05 | 25 | 3753 | 2011/2012 | July-2011 | 7 | 2011
25879 | LIGHTNING - OTEWA RD | 2011-07-11 18:25 | 2011-07-11 | 2011-07-11 21:22 | Calculated | TF1160 | TF1160 - Transformer Fuse: TF1160 |  | 109SEG329-539 | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 176 | 2 | 24415 | 352 | 0.01442 | 8.1917e-05 | 10 | 1761 | 2011/2012 | July-2011 | 7 | 2011
25919 | LIGHTNING - KURATAU SUB | 2011-07-11 20:03 | 2011-07-11 | 2011-07-12 07:44 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 701 | 4 | 24415 | 2804 | 0.11485 | 0.00016383 | 450 | 315510 | 2011/2012 | July-2011 | 7 | 2011
25880 | LIGHTNING -SH 3 NEAR TUNNEL | 2011-07-11 20:05 | 2011-07-11 | 2011-07-11 22:42 | Calculated | 1601 | 1601 - Air Break Switch 1601 |  | 128SEG1601 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 156 | 3 | 24415 | 468 | 0.01917 | 0.00012288 | 25 | 3903 | 2011/2012 | July-2011 | 7 | 2011
25904 | LIGHTNING - MOKAU VALLEY RD | 2011-07-11 20:06 | 2011-07-11 | 2011-07-12 15:52 | Calculated | TF2093 | TF2093 - Transformer Fuse: TF2093 |  | 128SEG1623-1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1186 | 2 | 24415 | 2373 | 0.09719 | 8.1917e-05 | 15 | 17798 | 2011/2012 | July-2011 | 7 | 2011
25905 | LIGHTNING - AWAKAU RD | 2011-07-11 20:06 | 2011-07-11 | 2011-07-12 17:17 | Calculated | TF2135 | TF2135 - Transformer Fuse: TF2135 |  | 128SEG1623-1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1271 | 3 | 24415 | 3814 | 0.15622 | 0.00012288 | 15 | 19073 | 2011/2012 | July-2011 | 7 | 2011
25906 | LIGHTNING - MODAU VALLEY RD | 2011-07-11 20:06 | 2011-07-11 | 2011-07-12 17:17 | Calculated | TF2134 | TF2134 - Transformer Fuse: TF2134 |  | 128SEG1623-1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1271 | 3 | 24415 | 3814 | 0.15622 | 0.00012288 | 15 | 19073 | 2011/2012 | July-2011 | 7 | 2011
25907 | LIGHTNING - MODAU VALLEY RD | 2011-07-11 20:06 | 2011-07-11 | 2011-07-12 15:52 | Calculated | TF2133 | TF2133 - Transformer Fuse: TF2133 |  | 128SEG1623-1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1186 | 2 | 24415 | 2373 | 0.09719 | 8.1917e-05 | 15 | 17798 | 2011/2012 | July-2011 | 7 | 2011
25886 | LIGHTNING - TAUMATAMAIRE RD | 2011-07-11 20:06 | 2011-07-11 | 2011-07-12 15:07 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1141 | 28 | 24415 | 31957 | 1.3089 | 0.0011468 | 195 | 222563 | 2011/2012 | July-2011 | 7 | 2011
25887 | LIGHTNING - GRIBBON RD | 2011-07-11 21:44 | 2011-07-11 | 2011-07-12 11:35 | Calculated | TF1863 | TF1863 - Transformer Fuse: TF1863 |  | No Segment | Mahoenui 113-04 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 831 | 2 | 24415 | 1662 | 0.06807 | 8.1917e-05 | 15 | 12470 | 2011/2012 | July-2011 | 7 | 2011
25883 | ROTTEN POLE DOWN - WHAREPAPA | 2011-07-11 23:14 | 2011-07-11 | 2011-07-12 06:07 | Calculated | 1052 | 1052 - Circuit Breaker 1052 Wharepapa |  | 122SEG1052-524 | 211-01 Arohena | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Pole | FAIL:FPOL2:FPOR | Pole Down - Rotten | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 412 | 419 | 24415 | 32523 | 1.3321 | 0.017162 | 3443.5 | 269581 | 2011/2012 | July-2011 | 7 | 2011
25882 | TAHAROA "A" - HANGATIKI | 2011-07-12 03:52 | 2011-07-12 | 2011-07-12 03:54 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 111 | 24415 | 251 | 0.01028 | 0.0045464 | 3280.8571 | 7436 | 2011/2012 | July-2011 | 7 | 2011
25888 | LIGHTNING/FAULTY L/A - TE MAHOE RD | 2011-07-12 05:21 | 2011-07-12 | 2011-07-12 10:51 | Calculated | TF2158 | TF2158 - Transformer Fuse: TF2158 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 330 | 2 | 24415 | 660 | 0.02703 | 8.1917e-05 | 10 | 3303 | 2011/2012 | July-2011 | 7 | 2011
25889 | LIGHTNING - PIAWA RD | 2011-07-12 06:05 | 2011-07-12 | 2011-07-12 07:00 | Calculated | TF6J17 | TF6J17 - Transformer Fuse: TF6J17 |  | 402SEG5354 | Northern 402-04 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 1 | 24415 | 55 | 0.00225 | 4.0958e-05 | 7.5 | 414 | 2011/2012 | July-2011 | 7 | 2011
25890 | LIGHTNING - TE WAITERE RD | 2011-07-12 06:19 | 2011-07-12 | 2011-07-12 10:23 | Calculated | TF545 | TF545 - Transformer Fuse: TF545 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 244 | 2 | 24415 | 488 | 0.01999 | 8.1917e-05 | 25 | 6103 | 2011/2012 | July-2011 | 7 | 2011
25891 | LIGHTNING - SH 4 PAST OIO RD | 2011-07-12 06:31 | 2011-07-12 | 2011-07-12 07:37 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 18 | 24415 | 1190 | 0.04874 | 0.00073725 | 93.75 | 6201 | 2011/2012 | July-2011 | 7 | 2011
25892 | LIGHTNING - HUIRIMU RD | 2011-07-12 07:10 | 2011-07-12 | 2011-07-12 15:05 | Calculated | TF1329 | TF1329 - Transformer Fuse: TF1329 |  | 121SEG425-748 | Huirimu 121-02 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 475 | 2 | 24415 | 950 | 0.03891 | 8.1917e-05 | 10 | 4751 | 2011/2012 | July-2011 | 7 | 2011
25893 | LIGHTNING - RANGITOTO RD POLE 117 | 2011-07-12 08:06 | 2011-07-12 | 2011-07-12 09:39 | Calculated | 823 | 823 - Fused Link 823 |  | 106SEG193RET | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 4 | 24415 | 372 | 0.01524 | 0.00016383 | 65 | 6054 | 2011/2012 | July-2011 | 7 | 2011
25894 | LIGHTNING - RANGITOTO RD | 2011-07-12 08:06 | 2011-07-12 | 2011-07-12 10:06 | Calculated | TF2754 | TF2754 - Transformer Fuse: TF2754 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 1 | 24415 | 120 | 0.00492 | 4.0958e-05 | 50 | 6007 | 2011/2012 | July-2011 | 7 | 2011
25895 | LIGHTNING - TE WAITERE RD | 2011-07-12 08:10 | 2011-07-12 | 2011-07-12 11:07 | Calculated | 298 | 298 - Fused Link 298 |  | 125SEG298 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 177 | 9 | 24415 | 1594 | 0.06529 | 0.00036863 | 45 | 7971 | 2011/2012 | July-2011 | 7 | 2011
25908 | LIGHTNING - SH 3 AWAKAU | 2011-07-12 09:13 | 2011-07-12 | 2011-07-12 18:17 | Calculated | TF2129 | TF2129 - Transformer Fuse: TF2129 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 544 | 2 | 24415 | 1089 | 0.0446 | 8.1917e-05 | 15 | 8168 | 2011/2012 | July-2011 | 7 | 2011
25896 | LIGHTNING - WALL RD | 2011-07-12 09:22 | 2011-07-12 | 2011-07-12 13:24 | Calculated | TF372 | TF372 - Transformer Fuse: TF372 |  | No Segment | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 242 | 3 | 24415 | 726 | 0.02974 | 0.00012288 | 5 | 1210 | 2011/2012 | July-2011 | 7 | 2011
25897 | LIGHTNING/BROKEN EARTH -MANGAOKEWA | 2011-07-12 09:30 | 2011-07-12 | 2011-07-12 14:11 | Calculated | TF914 | TF914 - Transformer Fuse: TF914 |  | No Segment | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 281 | 1 | 24415 | 281 | 0.01151 | 4.0958e-05 | 10 | 2811 | 2011/2012 | July-2011 | 7 | 2011
25898 | LIGHTNING - WALL RD | 2011-07-12 09:49 | 2011-07-12 | 2011-07-12 13:26 | Calculated | TF1326 | TF1326 - Transformer Fuse: TF1326 |  | 111SEG364-625 | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 217 | 5 | 24415 | 1085 | 0.04444 | 0.00020479 | 25 | 5428 | 2011/2012 | July-2011 | 7 | 2011
25899 | BOLT DOWN TX9I10 - HIKUMUTU RD | 2011-07-12 10:56 | 2011-07-12 | 2011-07-12 11:59 | Calculated | TF9I10 | TF9I10 - Transformer Fuse: TF9I10 |  | No Segment | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 63 | 3 | 24415 | 189 | 0.00774 | 0.00012288 | 25 | 1579 | 2011/2012 | July-2011 | 7 | 2011
25900 | LIGHTNING - SH 3 | 2011-07-12 11:39 | 2011-07-12 | 2011-07-12 13:27 | Calculated | TF1414 | TF1414 - Transformer Fuse: TF1414 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 1 | 24415 | 108 | 0.00442 | 4.0958e-05 | 15 | 1621 | 2011/2012 | July-2011 | 7 | 2011
25909 | LIGHTNING - TAUMATATOTARA EAST RD | 2011-07-12 12:56 | 2011-07-12 | 2011-07-12 18:49 | Calculated | TF2396 | TF2396 - Transformer Fuse: TF2396 |  | No Segment | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 353 | 1 | 24415 | 353 | 0.01446 | 4.0958e-05 | 10 | 3535 | 2011/2012 | July-2011 | 7 | 2011
25910 | LIGHTNING - SH 3 MAHOENUI | 2011-07-12 13:03 | 2011-07-12 | 2011-07-12 17:18 | Calculated | TF2518 | TF2518 - Transformer Fuse: TF2518 |  | No Segment | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 255 | 1 | 24415 | 255 | 0.01044 | 4.0958e-05 | 5 | 1277 | 2011/2012 | July-2011 | 7 | 2011
25901 | LIGHTNING - WAITAANGA BY TERRILL'S | 2011-07-12 14:44 | 2011-07-12 | 2011-07-12 16:56 | Calculated | 5560 | 5560 - Sectionaliser with Bypass & Links 5560 |  | 413SEG5306-5560 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 132 | 29 | 24415 | 3831 | 0.15691 | 0.0011878 | 160.8333 | 21251 | 2011/2012 | July-2011 | 7 | 2011
25911 | LIGHTNING - POMARANGAI RD | 2011-07-12 14:59 | 2011-07-12 | 2011-07-12 16:44 | Calculated | TF1620 | TF1620 - Transformer Fuse: TF1620 |  | 113SEG1533-1534 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 105 | 1 | 24415 | 105 | 0.0043 | 4.0958e-05 | 15 | 1583 | 2011/2012 | July-2011 | 7 | 2011
25902 | LIGHTNING CONNECT BIGGER GEN SET - WAHANUI CRES | 2011-07-12 15:01 | 2011-07-12 | 2011-07-12 15:15 | Calculated | TF1174 | TF1174 - Transformer Fuse: TF1174 |  | 112SEG313-645 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 24 | 24415 | 339 | 0.01388 | 0.000983 | 228.5714 | 3230 | 2011/2012 | July-2011 | 7 | 2011
25912 | LIGHTNING -MAIN STH RE TE KUITI | 2011-07-12 15:13 | 2011-07-12 | 2011-07-12 17:15 | Calculated | TF46 | TF46 - Transformer Fuse: TF46 |  | No Segment | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 3 | 24415 | 367 | 0.01503 | 0.00012288 | 15 | 1838 | 2011/2012 | July-2011 | 7 | 2011
25903 | BROKEN INSULATOR - FAULTY ZONE EXTENDED - BOROUGH SUB | 2011-07-12 15:36 | 2011-07-12 | 2011-07-12 17:13 | Calculated | 5951 | 5951 - Circuit Breaker T2 Incomer 5951 |  | No Segment | 508-01 Borough | Rural B | No Feeder |  |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 97 | 4232 | 24415 | 107809 | 4.4157 | 0.17334 | 29175.6663 | 765365 | 2011/2012 | July-2011 | 7 | 2011
25914 | LIGHTNING - WHAKAPIRAU RD | 2011-07-12 15:42 | 2011-07-12 | 2011-07-12 17:58 | Calculated | TF550 | TF550 - Transformer Fuse: TF550 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 2 | 24415 | 270 | 0.01106 | 8.1917e-05 | 15 | 2029 | 2011/2012 | July-2011 | 7 | 2011
25915 | LIGHTNING - SH 4 PAST OIO RD | 2011-07-12 16:30 | 2011-07-12 | 2011-07-12 18:08 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 18 | 24415 | 1751 | 0.07172 | 0.00073725 | 93.75 | 9121 | 2011/2012 | July-2011 | 7 | 2011
25916 | LIGHTNING - OHURA | 2011-07-12 16:59 | 2011-07-12 | 2011-07-12 17:56 | Calculated | 5758 | 5758 - Sectionaliser 5758 |  | 413SEG5996-5758 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 139 | 24415 | 7941 | 0.32525 | 0.0056932 | 1040.0556 | 59421 | 2011/2012 | July-2011 | 7 | 2011
25917 | LIGHTNING - TIROHANGA RD | 2011-07-12 17:32 | 2011-07-12 | 2011-07-12 18:20 | Calculated | TF772 | TF772 - Transformer Fuse: TF772 |  | 129SEG451-787 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 5 | 24415 | 240 | 0.00983 | 0.00020479 | 62.5 | 3008 | 2011/2012 | July-2011 | 7 | 2011
25918 | LIGHTNING - RIVER RD TOKIRIMA | 2011-07-12 18:31 | 2011-07-12 | 2011-07-12 19:55 | Calculated | TF4059 | TF4059 - Transformer Fuse: TF4059 |  | No Segment | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 1 | 24415 | 84 | 0.00344 | 4.0958e-05 | 50 | 4206 | 2011/2012 | July-2011 | 7 | 2011
25920 | LIGHTNING - MOKAU VALLEY RD | 2011-07-12 20:05 | 2011-07-12 | 2011-07-13 15:39 | Calculated | TF2285 | TF2285 - Transformer Fuse: TF2285 |  | 128SEG1623-1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1034 | 1 | 24415 | 1033 | 0.04231 | 4.0958e-05 | 5 | 5166 | 2011/2012 | July-2011 | 7 | 2011
25921 | LIGHTNING - MOKAU VALLEY RD | 2011-07-12 20:06 | 2011-07-12 | 2011-07-13 13:19 | Calculated | TF2128 | TF2128 - Transformer Fuse: TF2128 |  | 128SEG1623-1540 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1033 | 4 | 24415 | 4132 | 0.16924 | 0.00016383 | 30 | 30996 | 2011/2012 | July-2011 | 7 | 2011
25922 | FAULTY TX21M7 - RUAPEHU RD | 2011-07-13 08:02 | 2011-07-13 | 2011-07-13 09:43 | Calculated | 5677 | 5677 - Recloser with Bypass 5677 |  | 416SEG5677-5681 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 45 | 24415 | 2844 | 0.11649 | 0.0018431 | 332.5 | 21019 | 2011/2012 | July-2011 | 7 | 2011
25923 | LIGHTNING - TE WAITERE RD | 2011-07-13 08:30 | 2011-07-13 | 2011-07-13 11:35 | Calculated | TF2841 | TF2841 - Transformer Fuse: TF2841 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 185 | 2 | 24415 | 370 | 0.01515 | 8.1917e-05 | 10 | 1851 | 2011/2012 | July-2011 | 7 | 2011
25924 | LIGHTNING - MANGARE RD | 2011-07-13 08:33 | 2011-07-13 | 2011-07-13 13:06 | Calculated | TF1059 | TF1059 - Transformer Fuse: TF1059 |  | 121SEG435 | Huirimu 121-01 | Rural D | Huirimu | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 273 | 3 | 24415 | 819 | 0.03354 | 0.00012288 | 30 | 8194 | 2011/2012 | July-2011 | 7 | 2011
25925 | LIGHTNING - MOKAUITI RD | 2011-07-13 08:50 | 2011-07-13 | 2011-07-13 12:00 | Calculated | TF2050 | TF2050 - Transformer Fuse: TF2050 |  | 115SEG1707-1648 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 190 | 2 | 24415 | 380 | 0.01556 | 8.1917e-05 | 15 | 2852 | 2011/2012 | July-2011 | 7 | 2011
25926 | LIGHTNING - MANGAOKEWA RD | 2011-07-13 10:32 | 2011-07-13 | 2011-07-13 12:34 | Calculated | TF914 | TF914 - Transformer Fuse: TF914 |  | No Segment | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 122 | 1 | 24415 | 122 | 0.005 | 4.0958e-05 | 10 | 1221 | 2011/2012 | July-2011 | 7 | 2011
25929 | JUMPER OFF AT TX1869 - SH 3 BEFORE MANGAORONGA RD | 2011-07-13 10:32 | 2011-07-13 | 2011-07-13 11:49 | Calculated | 1336 | 1336 - Air Break Switch 1336 |  | 113SEG1336-1337 | Mahoenui 113-03 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 46 | 24415 | 2259 | 0.09253 | 0.0018841 | 338 | 16601 | 2011/2012 | July-2011 | 7 | 2011
25927 | FAULTY DDO TX915 - WAIPA VALLEY RD | 2011-07-13 10:36 | 2011-07-13 | 2011-07-13 12:01 | Calculated | 459 | 459 - Air Break Switch 459 |  | 103SEG459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 5 | 24415 | 425 | 0.01741 | 0.00020479 | 55 | 4682 | 2011/2012 | July-2011 | 7 | 2011
25928 | LIGHTNING - WAITANGURU RD | 2011-07-13 10:47 | 2011-07-13 | 2011-07-13 13:54 | Calculated | TF2480 | TF2480 - Transformer Fuse: TF2480 |  | No Segment | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 187 | 1 | 24415 | 187 | 0.00766 | 4.0958e-05 | 3 | 561 | 2011/2012 | July-2011 | 7 | 2011
25930 | LIGHTNING - NEWMAN RD | 2011-07-13 10:57 | 2011-07-13 | 2011-07-13 14:10 | Calculated | TF2943 | TF2943 - Transformer Fuse: TF2943 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 193 | 1 | 24415 | 193 | 0.0079 | 4.0958e-05 | 10 | 1931 | 2011/2012 | July-2011 | 7 | 2011
25931 | LOW VOLTAGE LINE DOWN - PAEWHENUA RD | 2011-07-13 11:01 | 2011-07-13 | 2011-07-13 12:07 | Calculated | TF452 | TF452 - Transformer Fuse: TF452 |  | 111SEG358-707 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 3 | 24415 | 198 | 0.00811 | 0.00012288 | 15 | 992 | 2011/2012 | July-2011 | 7 | 2011
25933 | LIGHTNING/BROKEN POLE - AWAKAU BY COPPELSTONE'S | 2011-07-13 13:21 | 2011-07-13 | 2011-07-13 15:27 | Calculated | 1623 | 1623 - Fused Link 1623 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 125 | 16 | 24415 | 2002 | 0.082 | 0.00065533 | 105 | 13140 | 2011/2012 | July-2011 | 7 | 2011
25936 | LIGHTNING / TWO FAULTS - WESTERN FEEDER | 2011-07-14 06:21 | 2011-07-14 | 2011-07-14 16:58 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 590 | 70 | 24415 | 16783 | 0.68741 | 0.0028671 | 430.5 | 104345 | 2011/2012 | July-2011 | 7 | 2011
25937 | LIGHTNING - TE ANGA RD | 2011-07-14 08:24 | 2011-07-14 | 2011-07-14 08:46 | Calculated | TF508 | TF508 - Transformer Fuse: TF508 |  | No Segment | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 21 | 3 | 24415 | 65 | 0.00266 | 0.00012288 | 15 | 327 | 2011/2012 | July-2011 | 7 | 2011
25938 | LIGHTNING - MANGAKARA RD | 2011-07-14 08:27 | 2011-07-14 | 2011-07-14 10:54 | Calculated | TF6C4 | TF6C4 - Transformer Fuse: TF6C4 |  | 413SEG5304 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 2 | 24415 | 293 | 0.012 | 8.1917e-05 | 7.5 | 1101 | 2011/2012 | July-2011 | 7 | 2011
25939 | LIGHTNING - SH 47 | 2011-07-14 08:35 | 2011-07-14 | 2011-07-14 10:11 | Calculated | TF14N02 | TF14N02 - Transformer Fuse: TF14N02 |  | 609SEG5787-6007 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 2 | 24415 | 190 | 0.00778 | 8.1917e-05 | 15 | 1427 | 2011/2012 | July-2011 | 7 | 2011
25940 | LIGHTNING - SH 47 | 2011-07-14 08:35 | 2011-07-14 | 2011-07-14 10:11 | Calculated | TF14N02 | TF14N02 - Transformer Fuse: TF14N02 |  | 609SEG5787-6007 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 2 | 24415 | 190 | 0.00778 | 8.1917e-05 | 15 | 1427 | 2011/2012 | July-2011 | 7 | 2011
25941 | LIGHTNING - NGAPAENGA RD | 2011-07-14 08:38 | 2011-07-14 | 2011-07-14 09:59 | Calculated | TF576 | TF576 - Transformer Fuse: TF576 |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 2 | 24415 | 160 | 0.00655 | 8.1917e-05 | 10 | 801 | 2011/2012 | July-2011 | 7 | 2011
25942 | LIGHTNING - SH 40 MANGAKARA | 2011-07-14 09:27 | 2011-07-14 | 2011-07-14 14:08 | Calculated | 5305 | 5305 - Sectionaliser with Bypass & Links 5305 |  | 413SEG5305-5306 | Ohura 413-04 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 281 | 29 | 24415 | 7420 | 0.30391 | 0.0011878 | 160.8333 | 40390 | 2011/2012 | July-2011 | 7 | 2011
25943 | LIGHTNING - TOTORO RD | 2011-07-14 09:46 | 2011-07-14 | 2011-07-14 11:11 | Calculated | TF1902 | TF1902 - Transformer Fuse: TF1902 |  | 114SEG1106-1105 | Aria 114-02 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 1 | 24415 | 85 | 0.00348 | 4.0958e-05 | 15 | 1277 | 2011/2012 | July-2011 | 7 | 2011
25944 | LIGHTNING - UPPER RETARUKE RD | 2011-07-14 11:19 | 2011-07-14 | 2011-07-14 13:49 | Calculated | TF13I15 | TF13I15 - Transformer Fuse: TF13I15 |  | 410SEG5901-5399 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 2 | 24415 | 300 | 0.01229 | 8.1917e-05 | 15 | 2252 | 2011/2012 | July-2011 | 7 | 2011
25945 | LIGHTNING - MANGAITI RD | 2011-07-14 11:26 | 2011-07-14 | 2011-07-14 12:29 | Calculated | TF2076 | TF2076 - Transformer Fuse: TF2076 |  | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 1 | 24415 | 63 | 0.00258 | 4.0958e-05 | 3 | 189 | 2011/2012 | July-2011 | 7 | 2011
25946 | LIGHTNING - OHURA/MOKAU RD | 2011-07-14 12:44 | 2011-07-14 | 2011-07-14 15:55 | Calculated | TF4F1 | TF4F1 - Transformer Fuse: TF4F1 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 191 | 1 | 24415 | 191 | 0.00782 | 4.0958e-05 | 7.5 | 1433 | 2011/2012 | July-2011 | 7 | 2011
25947 | LIGHTNING/FAULTY L/A - MARAKOPA RD - TE ANGA | 2011-07-14 13:37 | 2011-07-14 | 2011-07-14 15:35 | Calculated | 296 | 296 - Recloser with Bypass 296 |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 112 | 177 | 24415 | 18425 | 0.75466 | 0.0072496 | 1264.5455 | 129651 | 2011/2012 | July-2011 | 7 | 2011
25948 | LINE DOWN IN RIVER -OKAU - E/W SUB | 2011-07-14 16:00 | 2011-07-14 | 2011-07-15 14:23 | Calculated | 1630 | 1630 - Recloser 1630 |  | No Segment | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1343 | 49 | 24415 | 28586 | 1.1708 | 0.002007 | 358 | 241229 | 2011/2012 | July-2011 | 7 | 2011
25978 | LIGHTNING/FAULTY TX14M05 - SH 4 | 2011-07-15 12:47 | 2011-07-15 | 2011-07-22 14:56 | Calculated | TF14M05 | TF14M05 - Transformer Fuse: TF14M05 |  | 609SEG5787-6007 | National Park / Kuratau 609-03 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10208 | 2 | 24415 | 20416 | 0.83621 | 8.1917e-05 | 30 | 306249 | 2011/2012 | July-2011 | 7 | 2011
25949 | POLES AND LINES DOWN - BROWNS RD | 2011-07-15 12:48 | 2011-07-15 | 2011-07-15 14:09 | Calculated | 1268 | 1268 - Fused Link 1268 |  | 125SEG561-1758 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 7 | 24415 | 568 | 0.02326 | 0.00028671 | 30 | 2436 | 2011/2012 | July-2011 | 7 | 2011
25950 | LIGHTNING - HAUHANGAROA | 2011-07-15 13:47 | 2011-07-15 | 2011-07-15 16:26 | Calculated | 5177 | 5177 - Air Break Switch 5177 |  | 426SEG5177 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 158 | 1 | 24415 | 158 | 0.00647 | 4.0958e-05 | 5 | 791 | 2011/2012 | July-2011 | 7 | 2011
25951 | LIGHTNING - SH 4 ARAMATAI | 2011-07-15 14:02 | 2011-07-15 | 2011-07-15 18:05 | Calculated | TF2080 | TF2080 - Transformer Fuse: TF2080 |  | No Segment | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 243 | 2 | 24415 | 486 | 0.01991 | 8.1917e-05 | 10 | 2431 | 2011/2012 | July-2011 | 7 | 2011
25952 | LOWER TAP AT TX4249 - WHAREROA RD | 2011-07-15 15:55 | 2011-07-15 | 2011-07-15 16:34 | Calculated | TF4249 | TF4249 - Transformer Fuse: TF4249 |  | No Segment | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 1 | 24415 | 39 | 0.0016 | 4.0958e-05 | 15 | 587 | 2011/2012 | July-2011 | 7 | 2011
25953 | LIGHTNING - WAIMAHORA RD | 2011-07-16 08:01 | 2011-07-16 | 2011-07-16 17:05 | Calculated | 2041 | 2041 - Fused Link 2041 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 544 | 4 | 24415 | 2176 | 0.08913 | 0.00016383 | 65 | 35369 | 2011/2012 | July-2011 | 7 | 2011
25954 | LIGHTNING - PARITIKONA | 2011-07-16 10:31 | 2011-07-16 | 2011-07-16 12:01 | Calculated | TF2994 | TF2994 - Transformer Fuse: TF2994 |  | 103SEG1345-1346 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 1 | 24415 | 90 | 0.00369 | 4.0958e-05 | 5 | 450 | 2011/2012 | July-2011 | 7 | 2011
25955 | LIGHTNING/FAULTY TX - WAITOMO VALLEY RD | 2011-07-16 11:26 | 2011-07-16 | 2011-07-16 18:31 | Calculated | TF214 | TF214 - Transformer Fuse: TF214 |  | 112SEG318-550 | Otorohanga 112-02 | Rural C | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 425 | 5 | 24415 | 2125 | 0.08704 | 0.00020479 | 30 | 12754 | 2011/2012 | July-2011 | 7 | 2011
25956 | L/V LINE DOWN - COTTLES RD | 2011-07-16 17:44 | 2011-07-16 | 2011-07-16 18:23 | Calculated | TF273 | TF273 - Transformer Fuse: TF273 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 2 | 24415 | 76 | 0.00311 | 8.1917e-05 | 15 | 571 | 2011/2012 | July-2011 | 7 | 2011
25958 | Replace Pole 1061300 - Ahuroa Rd Opposite Templeton's | 2011-07-18 09:34 | 2011-07-18 | 2011-07-18 14:22 | Calculated | 246 | 246 - Fused Link 246 |  | 106SEG246-252 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 287 | 28 | 24415 | 8039 | 0.32926 | 0.0011468 | 162.5 | 46659 | 2011/2012 | July-2011 | 7 | 2011
25959 | L/V CLASH - OPARURE RD | 2011-07-18 11:28 | 2011-07-18 | 2011-07-18 13:27 | Calculated | TF149 | TF149 - Transformer Fuse: TF149 |  | 107SEG262-176 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 3 | 24415 | 357 | 0.01462 | 0.00012288 | 25 | 2978 | 2011/2012 | July-2011 | 7 | 2011
25960 | L/V LINE DOWN ACROSS RD - MILLAR ST | 2011-07-18 22:16 | 2011-07-18 | 2011-07-18 23:06 | Calculated | TF15L14 | TF15L14 - Transformer Fuse: TF15L14 |  | 411SEG5769-5147 | National Park 411-01 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 40 | 24415 | 2004 | 0.08208 | 0.0016383 | 300 | 15035 | 2011/2012 | July-2011 | 7 | 2011
25962 | REPLACE H/V FUSE - THOMPSON RD | 2011-07-19 07:58 | 2011-07-19 | 2011-07-19 09:11 | Calculated | TF2273 | TF2273 - Transformer Fuse: TF2273 |  | No Segment | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 72 | 2 | 24415 | 145 | 0.00594 | 8.1917e-05 | 10 | 726 | 2011/2012 | July-2011 | 7 | 2011
25963 | REPLACE YELLOW TAGGED POLE 1171185 | 2011-07-19 09:29 | 2011-07-19 | 2011-07-19 14:58 | Calculated | 1721 | 1721 - Sectionaliser 1721 |  | 117SEG1721-1307 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 270 | 15 | 24415 | 4040 | 0.16547 | 0.00061438 | 109 | 29357 | 2011/2012 | July-2011 | 7 | 2011
25964 | LIGHTNING - RAUTITI RD | 2011-07-19 10:56 | 2011-07-19 | 2011-07-19 14:46 | Calculated | TF4093 | TF4093 - Transformer Fuse: TF4093 |  | No Segment | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 230 | 1 | 24415 | 230 | 0.00942 | 4.0958e-05 | 5 | 1150 | 2011/2012 | July-2011 | 7 | 2011
25965 | FUSED PULLED APART - PAERATA RD | 2011-07-19 13:51 | 2011-07-19 | 2011-07-19 15:08 | Calculated | TF774 | TF774 - Transformer Fuse: TF774 |  | 129SEG455-402 | Tirohanga 129-03 (was 123-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 3 | 24415 | 231 | 0.00946 | 0.00012288 | 30 | 2315 | 2011/2012 | July-2011 | 7 | 2011
25966 | FUSE PULLED APART - TAUMATAMAIRE RD | 2011-07-19 14:11 | 2011-07-19 | 2011-07-19 19:15 | Calculated | 1600 | 1600 - Air Break Switch 1600 |  | 128SEG1600-1606RET | Mokau 128-02 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 304 | 27 | 24415 | 8212 | 0.33635 | 0.0011059 | 190 | 57788 | 2011/2012 | July-2011 | 7 | 2011
25967 | INSTALL NEW MAGNAFIX GEAR AND TX3361 - AILSA ST | 2011-07-20 09:24 | 2011-07-20 | 2011-07-20 16:19 | Calculated | TF8 | TF8 - Transformer Fuse: TF8 |  | 107SEG201 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 102 | 24415 | 8897 | 0.36441 | 0.0041778 | 408.0808 | 35598 | 2011/2012 | July-2011 | 7 | 2011
25968 | REPLACE COMPLETE STRUCTURE - TX587 | 2011-07-20 09:43 | 2011-07-20 | 2011-07-20 16:16 | Calculated | 382 | 382 - Fused Link 382 |  | 111SEG382 | Maihiihi 111-12 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 393 | 14 | 24415 | 5504 | 0.22544 | 0.00057342 | 125 | 49150 | 2011/2012 | July-2011 | 7 | 2011
25969 | LOWER TAP AT TX862 - NGATAPUWAE RD | 2011-07-20 09:45 | 2011-07-20 | 2011-07-20 10:15 | Calculated | TF862 | TF862 - Transformer Fuse: TF862 |  | No Segment | Caves 101-11 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 29 | 2 | 24415 | 58 | 0.00238 | 8.1917e-05 | 15 | 436 | 2011/2012 | July-2011 | 7 | 2011
25970 | REPLACE H/V FUSE AT TX5L1 - BEARDS RD | 2011-07-20 09:51 | 2011-07-20 | 2011-07-20 10:58 | Calculated | TF5L1 | TF5L1 - Transformer Fuse: TF5L1 |  | 421SEG5356-5320 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 2 | 24415 | 134 | 0.00549 | 8.1917e-05 | 15 | 1006 | 2011/2012 | July-2011 | 7 | 2011
25971 | L/V LINE DOWN - OPARURE RD | 2011-07-20 12:04 | 2011-07-20 | 2011-07-20 13:05 | Calculated | TF59 | TF59 - Transformer Fuse: TF59 |  | 107SEG384-706 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 10 | 24415 | 612 | 0.02507 | 0.00040958 | 50 | 3060 | 2011/2012 | July-2011 | 7 | 2011
25972 | CHANGE OVER FROM GENERATION TRUCK - WAHANUI CRES REFER PREVIOUS 25902 | 2011-07-20 17:30 | 2011-07-20 | 2011-07-20 17:57 | Calculated | TF1174 | TF1174 - Transformer Fuse: TF1174 |  | 112SEG313-645 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 27 | 23 | 24415 | 625 | 0.0256 | 0.00094204 | 191.6667 | 5216 | 2011/2012 | July-2011 | 7 | 2011
25973 | OIO SWER FAULT - CLIMB EVERY POLE AND CHANGE SUSPECT HARDWARE | 2011-07-21 08:56 | 2011-07-21 | 2011-07-21 15:04 | Calculated | 5440 | 5440 - Recloser with Bypass & Links 5440 |  | 409SEG5439-5440 | Southern 409-09 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 307 | 54 | 24415 | 5888 | 0.24116 | 0.0022118 | 330 | 29135 | 2011/2012 | July-2011 | 7 | 2011
25974 | REPLACE POLE 1241167 - ALSO REPLACE X/ARMS - TIHOI | 2011-07-21 09:34 | 2011-07-21 | 2011-07-21 14:22 | Calculated | 433 | 433 - Fused Link 433 |  | 124SEG433 | Tihoi 124-01 | Rural C | Tihoi | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 288 | 17 | 24415 | 4898 | 0.20061 | 0.00069629 | 125 | 36018 | 2011/2012 | July-2011 | 7 | 2011
25975 | L/V MAINTENANCE - PUKERIMU RD | 2011-07-21 09:46 | 2011-07-21 | 2011-07-21 12:14 | Calculated | TF1815 | TF1815 - Transformer Fuse: TF1815 |  | 117SEG1315-1326 | Te Mapara 117-06 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 148 | 2 | 24415 | 296 | 0.01212 | 8.1917e-05 | 15 | 2223 | 2011/2012 | July-2011 | 7 | 2011
25976 | LOWER TAPS AT TX2950 - WAIPAPA RD | 2011-07-21 11:53 | 2011-07-21 | 2011-07-21 12:45 | Calculated | TF2950 | TF2950 - Transformer Fuse: TF2950 |  | No Segment | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2 |  | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 52 | 1 | 24415 | 52 | 0.00213 | 4.0958e-05 | 10 | 521 | 2011/2012 | July-2011 | 7 | 2011
25979 | REPLACE LINK 302 - MANGAWHERO RD | 2011-07-22 05:49 | 2011-07-22 | 2011-07-22 08:04 | Calculated | 302 | 302 - Fused Link 302 |  | 109SEG302 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 135 | 8 | 24415 | 1081 | 0.04428 | 0.00032767 | 55 | 7434 | 2011/2012 | July-2011 | 7 | 2011
25980 | REPLACE STRUCTURE TX2504 - WAITETE RD - BOYLE'S SPUR | 2011-07-22 09:02 | 2011-07-22 | 2011-07-22 15:33 | Calculated | 1226 | 1226 - Solid Link 1226 |  | 103SEG1226 | Benneydale 103-04 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 391 | 3 | 24415 | 1173 | 0.04804 | 0.00012288 | 30 | 11737 | 2011/2012 | July-2011 | 7 | 2011
25981 | L/V MAINTENANCE - TUTUNUI ST | 2011-07-22 09:31 | 2011-07-22 | 2011-07-22 10:31 | Calculated | TF351 | TF351 - Transformer Fuse: TF351 |  | 112SEG307-314 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 65 | 24415 | 3914 | 0.16031 | 0.0026623 | 203.125 | 12231 | 2011/2012 | July-2011 | 7 | 2011
25984 | WIND - ONGARUE BACK RD | 2011-07-22 11:28 | 2011-07-22 | 2011-07-22 13:28 | Calculated | 5446 | 5446 - Sectionaliser with Bypass & Links 5446 |  | 402SEG5343-5446 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 120 | 43 | 24415 | 5167 | 0.21163 | 0.0017612 | 306.75 | 36866 | 2011/2012 | July-2011 | 7 | 2011
25982 | WIND - UPPER RETARUKE SUB | 2011-07-22 11:50 | 2011-07-22 | 2011-07-22 13:03 | Calculated | 5494 | 5494 - Recloser with Bypass 5494 |  | 410SEG5494-5493 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 50 | 24415 | 3657 | 0.14978 | 0.0020479 | 315.5833 | 23084 | 2011/2012 | July-2011 | 7 | 2011
25983 | WIND - PUKETAWAI RD - CORNER OLD TE KUITI | 2011-07-22 12:29 | 2011-07-22 | 2011-07-22 13:14 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 103 | 24415 | 4647 | 0.19033 | 0.0042187 | 988 | 44575 | 2011/2012 | July-2011 | 7 | 2011
25986 | REPLACE POLE - BENNEYDALE FEEDER | 2011-07-22 15:10 | 2011-07-22 | 2011-07-22 18:17 | Calculated | 714 | 714 - Recloser with Bypass 714 |  | 103SEG714-293 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 176 | 8 | 24415 | 1402 | 0.05742 | 0.00032767 | 110 | 19279 | 2011/2012 | July-2011 | 7 | 2011
25987 | WIND - WAIMIHA SUB | 2011-07-22 15:34 | 2011-07-22 | 2011-07-22 16:39 | Calculated | 5475 | 5475 - Recloser with Bypass & Links 5475 |  | 421SEG5470-5475 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 49 | 24415 | 3190 | 0.13066 | 0.002007 | 387.5 | 25232 | 2011/2012 | July-2011 | 7 | 2011
25985 | WIND - ONGARUE BACK RD | 2011-07-22 19:19 | 2011-07-22 | 2011-07-22 20:29 | Calculated | 5446 | 5446 - Sectionaliser with Bypass & Links 5446 |  | 402SEG5343-5446 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 43 | 24415 | 3017 | 0.12357 | 0.0017612 | 306.75 | 21528 | 2011/2012 | July-2011 | 7 | 2011
25988 | JUMPER OFF AT TX297 - SEAFUND RD BY STORER'S | 2011-07-24 09:54 | 2011-07-24 | 2011-07-24 11:35 | Calculated | 366 | 366 - Air Break Switch 366 |  | 122SEG366-549RET | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 60 | 24415 | 5591 | 0.229 | 0.0024575 | 441 | 41101 | 2011/2012 | July-2011 | 7 | 2011
25991 | REPLACE RED TAGGED POLE TX1063 AND ROTTEN X/ARMS ON POLE 122022 - WHAREPAPA FEEDER | 2011-07-25 09:36 | 2011-07-25 | 2011-07-25 15:13 | Calculated | 398 | 398 - Air Break Switch 398 |  | 122SEG366-398 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 294 | 60 | 24415 | 17589 | 0.72042 | 0.0024575 | 441 | 129286 | 2011/2012 | July-2011 | 7 | 2011
25990 | WIND - MANGANUI RD | 2011-07-25 09:51 | 2011-07-25 | 2011-07-25 12:52 | Calculated | TF1838 | TF1838 - Transformer Fuse: TF1838 |  | 128SEG1614-1615 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | Wind | WEAT:EENW2 |  | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 181 | 2 | 24415 | 362 | 0.01483 | 8.1917e-05 | 15 | 2717 | 2011/2012 | July-2011 | 7 | 2011
25992 | JUMPER OFF AT TX2193 - TONFAPORUTU | 2011-07-25 17:14 | 2011-07-25 | 2011-07-25 17:42 | Calculated | 1635 | 1635 - Air Break Switch 1635 |  | 128SEG1635-1626 | Mokau 128-06 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 149 | 24415 | 4214 | 0.1726 | 0.0061028 | 916.5 | 25921 | 2011/2012 | July-2011 | 7 | 2011
25989 | REPLACE H/V FUSE - MANGATORO RD | 2011-07-25 22:35 | 2011-07-25 | 2011-07-26 02:42 | Calculated | TF2231 | TF2231 - Transformer Fuse: TF2231 |  | 128SEG1631 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 247 | 3 | 24415 | 741 | 0.03035 | 0.00012288 | 15 | 3707 | 2011/2012 | July-2011 | 7 | 2011
25993 | REINSTATE STAY WIRE AT POLE 1090289 AND INSTALL NEW 11KV PINS ON POLE 1090277 | 2011-07-26 09:47 | 2011-07-26 | 2011-07-26 13:51 | Calculated | 171 | 171 - Fused Link 171 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 244 | 8 | 24415 | 1953 | 0.07999 | 0.00032767 | 105 | 25637 | 2011/2012 | July-2011 | 7 | 2011
25994 | REPLACE HARDWARE AT TX13I04 - 5559 | 2011-07-26 10:22 | 2011-07-26 | 2011-07-26 14:02 | Calculated | 5559 | 5559 - Fused Link 5559 |  | 410SEG5559-5582 | Raurimu 410-03 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 219 | 22 | 24415 | 4822 | 0.1975 | 0.00090109 | 121.8333 | 26707 | 2011/2012 | July-2011 | 7 | 2011
25995 | L/V FAULT - SCOTT RD | 2011-07-26 12:09 | 2011-07-26 | 2011-07-26 14:44 | Calculated | TF711 | TF711 - Transformer Fuse: TF711 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 3 | 24415 | 462 | 0.01892 | 0.00012288 | 25 | 3854 | 2011/2012 | July-2011 | 7 | 2011
25997 | REPLACE FUSE LINK 256 - SH 4 | 2011-07-27 07:31 | 2011-07-27 | 2011-07-27 14:17 | Calculated | 256 | 256 - Fused Link 256 |  | 106SEG256 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 406 | 6 | 24415 | 2436 | 0.09977 | 0.00024575 | 35 | 14215 | 2011/2012 | July-2011 | 7 | 2011
25996 | REPLACE POLE AND RECLOSER 168 - RANGIPO/HAUTU FEEDER | 2011-07-27 07:33 | 2011-07-27 | 2011-07-27 15:28 | Calculated | TF10S15 | TF10S15 - Transformer Fuse: TF10S15 |  | 424SEG5168-5010 | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 426 | 9 | 24415 | 2451 | 0.10039 | 0.00036863 | 700 | 220418 | 2011/2012 | July-2011 | 7 | 2011
25998 | FAULTY TX17K6 - SH 4 | 2011-07-27 08:23 | 2011-07-27 | 2011-07-27 13:30 | Calculated | TF17K06 | TF17K06 - Transformer Fuse: TF17K06 |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 307 | 3 | 24415 | 921 | 0.03772 | 0.00012288 | 7.5 | 2303 | 2011/2012 | July-2011 | 7 | 2011
25999 | REPLACE HV FUSE AT TX7D5 - MANGAPARA RD | 2011-07-28 07:29 | 2011-07-28 | 2011-07-28 08:27 | Calculated | TF7D5 | TF7D5 - Transformer Fuse: TF7D5 |  | 413SEG5299 | Ohura 413-06 | Rural D | Ohura | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 2 | 24415 | 116 | 0.00475 | 8.1917e-05 | 20 | 1165 | 2011/2012 | July-2011 | 7 | 2011
26000 | DUCKS - LOWER BURNS ST | 2011-07-28 07:31 | 2011-07-28 | 2011-07-28 08:36 | Calculated | 5397 | 5397 - Fused Link 5397 |  | 415SEG5397-5670 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Birds & Animals | FODU1 | BANI:FODU1:FODU2 | Ducks or Geese | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 22 | 24415 | 1423 | 0.05828 | 0.00090109 | 143.3333 | 9273 | 2011/2012 | July-2011 | 7 | 2011
26001 | RE-SAG CONDUCTORS AFTER POLE CHANGES - MATAPUNA FEEDER | 2011-07-28 09:00 | 2011-07-28 | 2011-07-28 12:14 | Calculated | 5915 | 5915 - Air Break Switch 5915 |  | 404SEG5915-5838 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 43 | 24415 | 8187 | 0.33533 | 0.0017612 | 279.3056 | 53179 | 2011/2012 | July-2011 | 7 | 2011
26002 | NEW 11KV EXTENSION P16 T/O LINKS TX3369 - CAVES FEEDER | 2011-07-28 09:59 | 2011-07-28 | 2011-07-28 14:21 | Calculated | 514 | 514 - Fused Link 514 |  | 101SEG514 | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 262 | 26 | 24415 | 6818 | 0.27925 | 0.0010649 | 175 | 45890 | 2011/2012 | July-2011 | 7 | 2011
26003 | REPLACE BROKEN POLE - CHOPPER REQUIRED - NOT ORGANIZED - JOB CANCELLED - MOKAU FEEDER | 2011-07-28 10:53 | 2011-07-28 | 2011-07-28 13:25 | Calculated | 1623 | 1623 - Fused Link 1623 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 152 | 17 | 24415 | 2586 | 0.10592 | 0.00069629 | 95 | 14455 | 2011/2012 | July-2011 | 7 | 2011
26006 | 11KV METERING WORK - MCDONALDS FEEDER | 2011-07-30 08:50 | 2011-07-30 | 2011-07-30 11:37 | Calculated | 809 | 809 - Solid Links 809 |  | 110SEG387-328 | McDonalds 110-04 | Urban A | McDonalds | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 167 | 2 | 24415 | 334 | 0.01368 | 8.1917e-05 | 1500 | 250750 | 2011/2012 | July-2011 | 7 | 2011
26007 | 11KV METERING WORK - BENNEYDALE FEEDER | 2011-07-30 13:23 | 2011-07-30 | 2011-07-30 14:52 | Calculated | 723 | 723 - Air Break Switch 723 |  | 103SEG723 | Benneydale 103-02 | Urban A | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 88 | 1 | 24415 | 88 | 0.0036 | 4.0958e-05 | 750 | 66162 | 2011/2012 | July-2011 | 7 | 2011
26008 | FUSE PULLED APART TX1046 - MCRAE RD | 2011-07-30 18:07 | 2011-07-30 | 2011-07-30 19:00 | Calculated | TF1046 | TF1046 - Transformer Fuse: TF1046 |  | 109SEG622 | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 53 | 4 | 24415 | 212 | 0.00868 | 0.00016383 | 30 | 1595 | 2011/2012 | July-2011 | 7 | 2011
26009 | REPLACE POLE 7 AND ABS 614 - ORUATUA FEEDER | 2011-08-01 09:08 | 2011-08-01 | 2011-08-01 15:03 | Calculated | TF9T7 | TF9T7 - Transformer Fuse: TF9T7 |  | 417SEG5614 | Oruatua 417-01 | Rural D | Oruatua | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 354 | 2 | 24415 | 708 | 0.029 | 8.1917e-05 | 100 | 35418 | 2011/2012 | August-2011 | 8 | 2011
26011 | BROKEN DDO AT TX8G12 - KURUAU RD | 2011-08-02 09:50 | 2011-08-02 | 2011-08-02 13:30 | Calculated | 5575 | 5575 - Fused Link 5575 |  | 403SEG5546-5575 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 219 | 1 | 24415 | 219 | 0.00897 | 4.0958e-05 | 15 | 3287 | 2011/2012 | August-2011 | 8 | 2011
26012 | CHANGE TX755 - MAROTIRI RD | 2011-08-02 10:41 | 2011-08-02 | 2011-08-02 12:15 | Calculated | TF755 | TF755 - Transformer Fuse: TF755 |  | 123SEG474-2134 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 93 | 3 | 24415 | 281 | 0.01151 | 0.00012288 | 10 | 937 | 2011/2012 | August-2011 | 8 | 2011
26013 | REPLACE TX STRUCTURE - AOTEAROA RD | 2011-08-02 10:56 | 2011-08-02 | 2011-08-02 16:49 | Calculated | TF885 | TF885 - Transformer Fuse: TF885 |  | No Segment | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 353 | 2 | 24415 | 706 | 0.02892 | 8.1917e-05 | 30 | 10595 | 2011/2012 | August-2011 | 8 | 2011
26014 | BOLT DOWN TX9I16 - HIKUMUTU RD | 2011-08-02 11:04 | 2011-08-02 | 2011-08-02 11:16 | Calculated | TF9I16 | TF9I16 - Transformer Fuse: TF9I16 |  | No Segment | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 12 | 1 | 24415 | 12 | 0.00049 | 4.0958e-05 | 25 | 303 | 2011/2012 | August-2011 | 8 | 2011
26015 | BOLT DOWN TX9I22 - HIKUMUTU RD | 2011-08-02 11:16 | 2011-08-02 | 2011-08-02 11:30 | Calculated | TF9I22 | TF9I22 - Transformer Fuse: TF9I22 |  | No Segment | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 14 | 2 | 24415 | 28 | 0.00115 | 8.1917e-05 | 10 | 141 | 2011/2012 | August-2011 | 8 | 2011
26016 | BOLT DOWN TX9I5 - HIKUMUTU RD | 2011-08-02 11:37 | 2011-08-02 | 2011-08-02 11:56 | Calculated | TF9I5 | TF9I5 - Transformer Fuse: TF9I5 |  | No Segment | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 19 | 1 | 24415 | 19 | 0.00078 | 4.0958e-05 | 15 | 287 | 2011/2012 | August-2011 | 8 | 2011
26020 | FUSE PULLED APART AT TX20M10 - MANGATEITEI RD | 2011-08-02 14:18 | 2011-08-02 | 2011-08-02 15:28 | Calculated | TF20M10 | TF20M10 - Transformer Fuse: TF20M10 |  | No Segment | Turoa 415-04 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 7 | 24415 | 490 | 0.02007 | 0.00028671 | 21.875 | 1533 | 2011/2012 | August-2011 | 8 | 2011
26017 | BOLT DOWN TX4056 - MAKOKOMIKO RD | 2011-08-02 14:39 | 2011-08-02 | 2011-08-02 14:56 | Calculated | TF4056 | TF4056 - Transformer Fuse: TF4056 |  | No Segment | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 16 | 1 | 24415 | 16 | 0.00066 | 4.0958e-05 | 5 | 80 | 2011/2012 | August-2011 | 8 | 2011
26021 | REPLACE HV FUSE LINK 685 - WHANGAEHU VALLEY RD | 2011-08-02 15:18 | 2011-08-02 | 2011-08-02 16:26 | Calculated | 5685 | 5685 - Fused Link 5685 |  | 416SEG5685-5716 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 22 | 24415 | 1500 | 0.06144 | 0.00090109 | 162 | 11048 | 2011/2012 | August-2011 | 8 | 2011
26022 | OLD STYLE FUSE LINK - JUST FELL OUT - WHANGAEHU VALLEY RD | 2011-08-03 04:17 | 2011-08-03 | 2011-08-03 06:58 | Calculated | 5685 | 5685 - Fused Link 5685 |  | 416SEG5685-5716 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 161 | 22 | 24415 | 3545 | 0.1452 | 0.00090109 | 162 | 26106 | 2011/2012 | August-2011 | 8 | 2011
26024 | FUSE PULLED APART AT TX9I8 - WANGANUI VALLEY RD | 2011-08-03 10:59 | 2011-08-03 | 2011-08-03 13:21 | Calculated | TF9I8 | TF9I8 - Transformer Fuse: TF9I8 |  | No Segment | Western 403-04 | Rural D | Western | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 1 | 24415 | 142 | 0.00582 | 4.0958e-05 | 10 | 1421 | 2011/2012 | August-2011 | 8 | 2011
26028 | FAULTY LINK/FELL OUT - WHANGAEHU VALLEY RD | 2011-08-04 04:11 | 2011-08-04 | 2011-08-04 05:43 | Calculated | 5685 | 5685 - Fused Link 5685 |  | 416SEG5685-5716 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 22 | 24415 | 2026 | 0.08298 | 0.00090109 | 162 | 14922 | 2011/2012 | August-2011 | 8 | 2011
26029 | RECONNECT NEW EARTH MAT - ONGARUE RD | 2011-08-04 09:24 | 2011-08-04 | 2011-08-04 13:55 | Calculated | TF4J6 | TF4J6 - Transformer Fuse: TF4J6 |  | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 271 | 3 | 24415 | 813 | 0.0333 | 0.00012288 | 15 | 4068 | 2011/2012 | August-2011 | 8 | 2011
26030 | UPGRADE TX2693 AND FIT L/A'S - RANGITOTO FEEDER | 2011-08-04 09:34 | 2011-08-04 | 2011-08-04 14:24 | Calculated | 173 | 173 - Fused Link 173 |  | 106SEG173 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 289 | 7 | 24415 | 2024 | 0.0829 | 0.00028671 | 90 | 26035 | 2011/2012 | August-2011 | 8 | 2011
26034 | HARDWARE UPGRADE ON MAKOKOMIKO SWER - SOUTHERN FEEDER | 2011-08-04 10:09 | 2011-08-04 | 2011-08-04 14:57 | Calculated | 5599 | 5599 - Recloser with Bypass & Links 5599 |  | 409SEG5598-5599 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 287 | 44 | 24415 | 12633 | 0.51743 | 0.0018022 | 299.7857 | 86078 | 2011/2012 | August-2011 | 8 | 2011
26035 | REPLACE T/O POLE AND OLD LATTICE POLE FOR TX2K18 - ONGARUE RD | 2011-08-04 10:10 | 2011-08-04 | 2011-08-04 14:06 | Calculated | 5763 | 5763 - Fused Link 5763 |  | 421SEG5763 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 235 | 13 | 24415 | 3061 | 0.12537 | 0.00053246 | 95 | 22372 | 2011/2012 | August-2011 | 8 | 2011
26036 | REPLACE FAULTY LINK 5685 - FIELDS TRACK | 2011-08-04 12:29 | 2011-08-04 | 2011-08-04 13:32 | Calculated | 5721 | 5721 - Air Break Switch 5721 |  | 416SEG5721-5684 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 62 | 66 | 24415 | 4102 | 0.16801 | 0.0027033 | 632.5 | 39320 | 2011/2012 | August-2011 | 8 | 2011
26043 | REPLACE FLOATING INSULTOR AT POLE 8 - ALSO REPLACE FAULTY SECT 314 - WESTERN FEEDER | 2011-08-05 10:02 | 2011-08-05 | 2011-08-05 11:02 | Calculated | 5314 | 5314 - Sectionaliser with Bypass 5314 |  | 403SEG5314-5765 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 60 | 19 | 24415 | 1143 | 0.04682 | 0.00077821 | 130.5 | 7853 | 2011/2012 | August-2011 | 8 | 2011
26049 | REPLACE I/R POLE 52 - FITTED WITH T/O DDO - ONGARUE FEEDER | 2011-08-05 10:40 | 2011-08-05 | 2011-08-05 14:08 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 207 | 18 | 24415 | 3732 | 0.15286 | 0.00073725 | 135 | 27996 | 2011/2012 | August-2011 | 8 | 2011
26050 | POLE DOWN (17) - TAHAROA RD - BY OLD QUARRY | 2011-08-05 10:41 | 2011-08-05 | 2011-08-05 15:57 | Calculated | 277 | 277 - Recloser with Bypass 277 |  | 125SEG277-268 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 316 | 124 | 24415 | 39200 | 1.6056 | 0.0050788 | 981.7895 | 310376 | 2011/2012 | August-2011 | 8 | 2011
26051 | FAULTY TX1374 - TE ANGA RD | 2011-08-06 10:01 | 2011-08-06 | 2011-08-06 14:46 | Calculated | TF1347 | TF1347 - Transformer Fuse: TF1347 |  | 125SEG2182-518 | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 285 | 1 | 24415 | 285 | 0.01167 | 4.0958e-05 | 10 | 2851 | 2011/2012 | August-2011 | 8 | 2011
26052 | REPLACE HV FUSE TF871 - AOTEAROA RD | 2011-08-06 14:26 | 2011-08-06 | 2011-08-06 15:24 | Calculated | TF871 | TF871 - Transformer Fuse: TF871 |  | No Segment | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 4 | 24415 | 232 | 0.0095 | 0.00016383 | 30 | 1746 | 2011/2012 | August-2011 | 8 | 2011
26054 | LIGHTNING - SH 4 PAST OIO RD | 2011-08-07 09:24 | 2011-08-07 | 2011-08-07 10:33 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 68 | 18 | 24415 | 1227 | 0.05026 | 0.00073725 | 93.75 | 6395 | 2011/2012 | August-2011 | 8 | 2011
26101 | FAULTY TX - LIGHTNING - SH 3 TONGAPORUTU | 2011-08-07 09:34 | 2011-08-07 | 2011-08-08 11:58 | Calculated | TF2204 | TF2204 - Transformer Fuse: TF2204 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1583 | 5 | 24415 | 7916 | 0.32423 | 0.00020479 | 30 | 47501 | 2011/2012 | August-2011 | 8 | 2011
26076 | LIGHTNING - TROOPERS RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 14:30 | Calculated | TF54 | TF54 - Transformer Fuse: TF54 |  | 107SEG266 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 4 | 24415 | 1080 | 0.04424 | 0.00016383 | 25 | 6754 | 2011/2012 | August-2011 | 8 | 2011
26078 | LIGHTNING - WHATAROA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 15:30 | Calculated | 575 | 575 - Fused Link 575 |  | 107SEG575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 330 | 14 | 24415 | 4622 | 0.18931 | 0.00057342 | 153.75 | 50763 | 2011/2012 | August-2011 | 8 | 2011
26079 | LIGHTNING - WHATAROA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 16:00 | Calculated | TF2423 | TF2423 - Transformer Fuse: TF2423 |  | No Segment | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 360 | 5 | 24415 | 1800 | 0.07373 | 0.00020479 | 18.75 | 6753 | 2011/2012 | August-2011 | 8 | 2011
26080 | LIGHTNING - OPARURE | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 16:30 | Calculated | TF3063 | TF3063 - Transformer Fuse: TF3063 |  | 107SEG231 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 390 | 1 | 24415 | 390 | 0.01597 | 4.0958e-05 | 50 | 19508 | 2011/2012 | August-2011 | 8 | 2011
26081 | LIGHTNING -TROOPERS RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 17:00 | Calculated | TF2723 | TF2723 - Transformer Fuse: TF2723 |  | 107SEG231 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 420 | 1 | 24415 | 420 | 0.0172 | 4.0958e-05 | 15 | 6302 | 2011/2012 | August-2011 | 8 | 2011
26082 | LIGHTNING -OPARURE RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 17:30 | Calculated | TF56 | TF56 - Transformer Fuse: TF56 |  | 107SEG706-243 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 450 | 4 | 24415 | 1800 | 0.07373 | 0.00016383 | 30 | 13505 | 2011/2012 | August-2011 | 8 | 2011
26083 | LIGHTNING -WAIPUNA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 18:00 | Calculated | TF691 | TF691 - Transformer Fuse: TF691 |  | No Segment | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 480 | 2 | 24415 | 960 | 0.03932 | 8.1917e-05 | 0 | 0 | 2011/2012 | August-2011 | 8 | 2011
26084 | LIGHTNING -WAIPUNA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 13:00 | Calculated | TF2757 | TF2757 - Transformer Fuse: TF2757 |  | 101SEG1272-257 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 2 | 24415 | 360 | 0.01475 | 8.1917e-05 | 20 | 3603 | 2011/2012 | August-2011 | 8 | 2011
26085 | LIGHTNING - NGAPAENGA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 11:30 | Calculated | TF576 | TF576 - Transformer Fuse: TF576 |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 2 | 24415 | 180 | 0.00737 | 8.1917e-05 | 10 | 901 | 2011/2012 | August-2011 | 8 | 2011
26086 | LIGHTNING - WAIPUNA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 13:00 | Calculated | TF160 | TF160 - Transformer Fuse: TF160 |  | 107SEG263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 2 | 24415 | 360 | 0.01475 | 8.1917e-05 | 10 | 1801 | 2011/2012 | August-2011 | 8 | 2011
26087 | LIGHTNING - TE ANGA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 11:30 | Calculated | TF508 | TF508 - Transformer Fuse: TF508 |  | No Segment | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 3 | 24415 | 270 | 0.01106 | 0.00012288 | 15 | 1352 | 2011/2012 | August-2011 | 8 | 2011
26088 | LIGHTNING - TE WAITETE RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 13:00 | Calculated | TF541 | TF541 - Transformer Fuse: TF541 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 180 | 1 | 24415 | 180 | 0.00737 | 4.0958e-05 | 10 | 1801 | 2011/2012 | August-2011 | 8 | 2011
26090 | LIGHTNING - TE WAITETE RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 14:00 | Calculated | TF537 | TF537 - Transformer Fuse: TF537 |  | No Segment | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 240 | 4 | 24415 | 960 | 0.03932 | 0.00016383 | 25 | 6004 | 2011/2012 | August-2011 | 8 | 2011
26091 | LIGHTNING - TAHAROA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 14:30 | Calculated | TF535 | TF535 - Transformer Fuse: TF535 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 3 | 24415 | 810 | 0.03318 | 0.00012288 | 15 | 4052 | 2011/2012 | August-2011 | 8 | 2011
26092 | LIGHTNING - TAHAROA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 15:00 | Calculated | TF534 | TF534 - Transformer Fuse: TF534 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 300 | 1 | 24415 | 300 | 0.01229 | 4.0958e-05 | 15 | 4502 | 2011/2012 | August-2011 | 8 | 2011
26093 | LIGHTNING - TAUMATATOTARA EAST RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 15:30 | Calculated | TF2396 | TF2396 - Transformer Fuse: TF2396 |  | No Segment | Coast 125-01 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 330 | 1 | 24415 | 330 | 0.01352 | 4.0958e-05 | 10 | 3301 | 2011/2012 | August-2011 | 8 | 2011
26095 | LIGHTNING - TE ANGA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 16:00 | Calculated | TF510 | TF510 - Transformer Fuse: TF510 |  | No Segment | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 360 | 4 | 24415 | 1440 | 0.05898 | 0.00016383 | 15 | 5402 | 2011/2012 | August-2011 | 8 | 2011
26096 | LIGHTNING - WAITOMO | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 17:30 | Calculated | TF2798 | TF2798 - Transformer Fuse: TF2798 |  | No Segment | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 450 | 1 | 24415 | 450 | 0.01843 | 4.0958e-05 | 25 | 11254 | 2011/2012 | August-2011 | 8 | 2011
26097 | LIGHTNING - WAITOMO CAVES RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 19:00 | Calculated | TF85 | TF85 - Transformer Fuse: TF85 |  | 101SEG679-267 | Caves 101-06 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 540 | 9 | 24415 | 4861 | 0.1991 | 0.00036863 | 33.75 | 18230 | 2011/2012 | August-2011 | 8 | 2011
26098 | LIGHTNING -TAHAROA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 19:30 | Calculated | TF535 | TF535 - Transformer Fuse: TF535 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 570 | 3 | 24415 | 1710 | 0.07004 | 0.00012288 | 15 | 8552 | 2011/2012 | August-2011 | 8 | 2011
26099 | LIGHTNING -TAHAROA RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 21:15 | Calculated | TF536 | TF536 - Transformer Fuse: TF536 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 675 | 3 | 24415 | 2025 | 0.08294 | 0.00012288 | 25 | 16879 | 2011/2012 | August-2011 | 8 | 2011
26055 | LIGHTNING - KOIRO RD | 2011-08-07 10:00 | 2011-08-07 | 2011-08-07 11:35 | Calculated | TF10F01 | TF10F01 - Transformer Fuse: TF10F01 |  | 403SEG5771 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 94 | 3 | 24415 | 282 | 0.01155 | 0.00012288 | 25 | 2354 | 2011/2012 | August-2011 | 8 | 2011
26060 | LIGHTNING - WAIPUNA RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 14:14 | Calculated | TF2757 | TF2757 - Transformer Fuse: TF2757 |  | 101SEG1272-257 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 253 | 2 | 24415 | 507 | 0.02077 | 8.1917e-05 | 20 | 5075 | 2011/2012 | August-2011 | 8 | 2011
26061 | LIGHTNING - TROOPERS RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 17:19 | Calculated | 231 | 231 - Fused Link 231 |  | 107SEG244-575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 438 | 2 | 24415 | 877 | 0.03592 | 8.1917e-05 | 65 | 28518 | 2011/2012 | August-2011 | 8 | 2011
26062 | LIGHTNING - TROOPERS RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 17:40 | Calculated | TF1211 | TF1211 - Transformer Fuse: TF1211 |  | 107SEG266 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 459 | 2 | 24415 | 919 | 0.03764 | 8.1917e-05 | 25 | 11493 | 2011/2012 | August-2011 | 8 | 2011
26063 | LIGHTNING - MANGAORONGO RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 14:10 | Calculated | TF3058 | TF3058 - Transformer Fuse: TF3058 |  | No Segment | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 249 | 4 | 24415 | 999 | 0.04092 | 0.00016383 | 30 | 7492 | 2011/2012 | August-2011 | 8 | 2011
26064 | LIGHTNING - RANGIATEA RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 14:50 | Calculated | TF244 | TF244 - Transformer Fuse: TF244 |  | No Segment | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 289 | 2 | 24415 | 579 | 0.02371 | 8.1917e-05 | 25 | 7243 | 2011/2012 | August-2011 | 8 | 2011
26065 | LIGHTNING - RANGIATEA RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 15:15 | Calculated | TF402 | TF402 - Transformer Fuse: TF402 |  | No Segment | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 314 | 6 | 24415 | 1888 | 0.07733 | 0.00024575 | 30 | 9442 | 2011/2012 | August-2011 | 8 | 2011
26066 | LIGHTNING - TE RAUMAUKU RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 15:55 | Calculated | TF219 | TF219 - Transformer Fuse: TF219 |  | 112SEG209-674 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 354 | 4 | 24415 | 1419 | 0.05812 | 0.00016383 | 33.3333 | 11824 | 2011/2012 | August-2011 | 8 | 2011
26067 | LIGHTNING - OPARURE RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 10:15 | Calculated | TF117 | TF117 - Transformer Fuse: TF117 |  | 107SEG243-113 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 14 | 3 | 24415 | 44 | 0.0018 | 0.00012288 | 15 | 221 | 2011/2012 | August-2011 | 8 | 2011
26068 | LIGHTNING - TROOPERS RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 11:00 | Calculated | TF51 | TF51 - Transformer Fuse: TF51 |  | No Segment | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 6 | 24415 | 358 | 0.01466 | 0.00024575 | 30 | 1792 | 2011/2012 | August-2011 | 8 | 2011
26069 | LIGHTNING - TROOPERS RD | 2011-08-07 10:01 | 2011-08-07 | 2011-08-07 17:00 | Calculated | TF52 | TF52 - Transformer Fuse: TF52 |  | No Segment | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 419 | 3 | 24415 | 1259 | 0.05157 | 0.00012288 | 30 | 12592 | 2011/2012 | August-2011 | 8 | 2011
26053 | LIGHTNING - TAHAROA FEEDER | 2011-08-07 10:06 | 2011-08-07 | 2011-08-07 10:21 | Calculated | 796 | 796 - Circuit Breaker 796 |  | 301SEG1418-796 | Taharoa A 301-02 | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 14 | 111 | 24415 | 1646 | 0.06742 | 0.0045464 | 3280.8571 | 48666 | 2011/2012 | August-2011 | 8 | 2011
26056 | LIGHTNING - TE ANGA RD | 2011-08-07 10:06 | 2011-08-07 | 2011-08-07 11:47 | Calculated | TF508 | TF508 - Transformer Fuse: TF508 |  | No Segment | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 3 | 24415 | 300 | 0.01229 | 0.00012288 | 15 | 1503 | 2011/2012 | August-2011 | 8 | 2011
26058 | BROKEN XARM ON WESTERN FEEDER - FAULT EXTENDED - BOROUGH SUB | 2011-08-07 12:29 | 2011-08-07 | 2011-08-07 15:16 | Calculated | 5951 | 5951 - Circuit Breaker T2 Incomer 5951 |  | No Segment | 508-01 Borough | Rural B | No Feeder |  |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 3002 | 24415 | 101200 | 4.145 | 0.12296 | 20164.2412 | 762227 | 2011/2012 | August-2011 | 8 | 2011
26057 | LINE DOWN/EXTREME WEATHER- TROOPERS RD | 2011-08-07 12:33 | 2011-08-07 | 2011-08-07 15:36 | Calculated | 244 | 244 - Air Break Switch 244 |  | 107SEG244-575 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 183 | 44 | 24415 | 8061 | 0.33017 | 0.0018022 | 428.75 | 78554 | 2011/2012 | August-2011 | 8 | 2011
26059 | FAULT ON NORTHERN FEEDER - FAULT ZONE EXTENDED - BOROUGH SUB | 2011-08-07 13:32 | 2011-08-07 | 2011-08-07 18:54 | Calculated | 5951 | 5951 - Circuit Breaker T2 Incomer 5951 |  | No Segment | 508-01 Borough | Rural B | No Feeder |  |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 299 | 2552 | 24415 | 267143 | 10.9418 | 0.10453 | 16512.073 | 1614955 | 2011/2012 | August-2011 | 8 | 2011
26100 | LIGHTNING -SH 4 PAST OIO RD | 2011-08-07 18:14 | 2011-08-07 | 2011-08-07 19:27 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 18 | 24415 | 1317 | 0.05394 | 0.00073725 | 93.75 | 6859 | 2011/2012 | August-2011 | 8 | 2011
26074 | LIGHTNING - OPATURE RD | 2011-08-07 19:51 | 2011-08-07 | 2011-08-07 20:00 | Calculated | TF430 | TF430 - Transformer Fuse: TF430 |  | No Segment | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 9 | 3 | 24415 | 27 | 0.00111 | 0.00012288 | 15 | 137 | 2011/2012 | August-2011 | 8 | 2011
26075 | LIGHTNING - TROOPERS RD | 2011-08-07 19:51 | 2011-08-07 | 2011-08-07 21:30 | Calculated | TF1224 | TF1224 - Transformer Fuse: TF1224 |  | 107SEG244-575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 3 | 24415 | 297 | 0.01216 | 0.00012288 | 15 | 1487 | 2011/2012 | August-2011 | 8 | 2011
26102 | LIGHTNING - TROOPERS RD | 2011-08-07 21:36 | 2011-08-07 | 2011-08-08 09:44 | Calculated | TF2688 | TF2688 - Transformer Fuse: TF2688 |  | 107SEG706-243 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 727 | 1 | 24415 | 727 | 0.02978 | 4.0958e-05 | 15 | 10910 | 2011/2012 | August-2011 | 8 | 2011
26103 | LIGHTNING - MCRAE RD | 2011-08-08 05:23 | 2011-08-08 | 2011-08-08 07:01 | Calculated | TF333 | TF333 - Transformer Fuse: TF333 |  | No Segment | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 97 | 4 | 24415 | 389 | 0.01593 | 0.00016383 | 25 | 2434 | 2011/2012 | August-2011 | 8 | 2011
26109 | LIGHTNING - TAHAROA RD | 2011-08-08 08:30 | 2011-08-08 | 2011-08-08 12:34 | Calculated | 280 | 280 - Fused Link 280 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 244 | 12 | 24415 | 2773 | 0.11358 | 0.0004915 | 118 | 27052 | 2011/2012 | August-2011 | 8 | 2011
26110 | LIGHTNING - SH 3 AWAKAU | 2011-08-08 08:46 | 2011-08-08 | 2011-08-08 12:08 | Calculated | TF2130 | TF2130 - Transformer Fuse: TF2130 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 202 | 1 | 24415 | 202 | 0.00827 | 4.0958e-05 | 5 | 1010 | 2011/2012 | August-2011 | 8 | 2011
26108 | LIGHTNING - TAUMATATOTARA WEST RD | 2011-08-08 08:54 | 2011-08-08 | 2011-08-08 11:03 | Calculated | TF1079 | TF1079 - Transformer Fuse: TF1079 |  | 125SEG280-292 | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 129 | 1 | 24415 | 129 | 0.00528 | 4.0958e-05 | 15 | 1937 | 2011/2012 | August-2011 | 8 | 2011
26106 | REPLACE DDO'S AT TX 2158 - MAOKAU FEEDER | 2011-08-08 10:02 | 2011-08-08 | 2011-08-08 11:09 | Calculated | 726 | 726 - Fused Link 726 |  | 128SEG726-1621 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 66 | 36 | 24415 | 2380 | 0.09748 | 0.0014745 | 191.25 | 12647 | 2011/2012 | August-2011 | 8 | 2011
26104 | REPLACE XARMS ON POLE 401 - TANGIWAI FEEDER | 2011-08-08 10:09 | 2011-08-08 | 2011-08-08 12:39 | Calculated | 5691 | 5691 - Fused Link 5691 |  | 416SEG5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 150 | 5 | 24415 | 750 | 0.03072 | 0.00020479 | 45 | 6758 | 2011/2012 | August-2011 | 8 | 2011
26107 | CHANGE TX265 - NAGHAPE RD | 2011-08-08 10:21 | 2011-08-08 | 2011-08-08 13:18 | Calculated | TF265 | TF265 - Transformer Fuse: TF265 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 176 | 5 | 24415 | 880 | 0.03604 | 0.00020479 | 30 | 5285 | 2011/2012 | August-2011 | 8 | 2011
26111 | LV FAULT AT TX525 - MAROKOPA RD | 2011-08-08 13:27 | 2011-08-08 | 2011-08-08 18:09 | Calculated | TF525 | TF525 - Transformer Fuse: TF525 |  | No Segment | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 281 | 4 | 24415 | 1124 | 0.04604 | 0.00016383 | 25 | 7030 | 2011/2012 | August-2011 | 8 | 2011
26112 | LIGHTNING - FAULTY TX 85 - WAITOMO CAVES RD | 2011-08-08 16:25 | 2011-08-08 | 2011-08-08 20:21 | Calculated | TF85 | TF85 - Transformer Fuse: TF85 |  | 101SEG679-267 | Caves 101-06 | Urban A | Caves | Hangatiki Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 235 | 9 | 24415 | 2118 | 0.08675 | 0.00036863 | 33.75 | 7942 | 2011/2012 | August-2011 | 8 | 2011
26115 | LIGHTNING - TAUMATATOTORA WEST RD | 2011-08-09 07:05 | 2011-08-09 | 2011-08-09 14:58 | Calculated | TF627 | TF627 - Transformer Fuse: TF627 |  | No Segment | Coast 125-02 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 473 | 3 | 24415 | 1419 | 0.05812 | 0.00012288 | 30 | 14194 | 2011/2012 | August-2011 | 8 | 2011
26113 | HARDWARE UPGRADE ON MAKOKOMIKO SWER - SOUTHERN FEEDER | 2011-08-09 09:12 | 2011-08-09 | 2011-08-09 15:29 | Calculated | 5599 | 5599 - Recloser with Bypass & Links 5599 |  | 409SEG5598-5599 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 377 | 44 | 24415 | 16603 | 0.68003 | 0.0018022 | 299.7857 | 113124 | 2011/2012 | August-2011 | 8 | 2011
26114 | LV MAINTENANCE - MANGAWHIO RD | 2011-08-09 10:05 | 2011-08-09 | 2011-08-09 11:26 | Calculated | TF1396 | TF1396 - Transformer Fuse: TF1396 |  | 121SEG421-424 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 2 | 24415 | 162 | 0.00664 | 8.1917e-05 | 10 | 811 | 2011/2012 | August-2011 | 8 | 2011
26116 | LIGHTNING - TROOPERS RD | 2011-08-09 15:47 | 2011-08-09 | 2011-08-09 18:47 | Calculated | TF50 | TF50 - Transformer Fuse: TF50 |  | No Segment | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 179 | 1 | 24415 | 179 | 0.00733 | 4.0958e-05 | 5 | 895 | 2011/2012 | August-2011 | 8 | 2011
26117 | REPLACE HV FUSE LINK 1528 - WAITANGURU | 2011-08-10 07:59 | 2011-08-10 | 2011-08-10 09:29 | Calculated | 1528 | 1528 - Fused Link 1528 |  | 113SEG1528-1527 | Mahoenui 113-06 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 12 | 24415 | 1081 | 0.04428 | 0.0004915 | 58 | 5229 | 2011/2012 | August-2011 | 8 | 2011
26119 | REPLACE POLE AT ABS 459 - PUREORA FEEDER | 2011-08-10 08:47 | 2011-08-10 | 2011-08-10 16:55 | Calculated | 405 | 405 - Air Break Switch 405 |  | 119SEG2205-489 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 429 | 36 | 24415 | 15392 | 0.63043 | 0.0014745 | 480.5 | 205414 | 2011/2012 | August-2011 | 8 | 2011
26118 | HARDWARE UPGRADE ON MAKOKOMIKO SWER - SOUTHERN FEEDER | 2011-08-10 09:08 | 2011-08-10 | 2011-08-10 12:46 | Calculated | 5599 | 5599 - Recloser with Bypass & Links 5599 |  | 409SEG5598-5599 | Southern 409-06 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 218 | 44 | 24415 | 9597 | 0.39308 | 0.0018022 | 299.7857 | 65393 | 2011/2012 | August-2011 | 8 | 2011
26120 | REPLACE HV FUSE - SH 3 HANGATIKI | 2011-08-10 12:44 | 2011-08-10 | 2011-08-10 15:57 | Calculated | TF998 | TF998 - Transformer Fuse: TF998 |  | No Segment | Caves 101-01 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 192 | 4 | 24415 | 768 | 0.03146 | 0.00016383 | 50 | 9611 | 2011/2012 | August-2011 | 8 | 2011
26121 | BLOWN LA - TE KAWA ST | 2011-08-10 22:31 | 2011-08-10 | 2011-08-10 22:43 | Calculated | TF170 | TF170 - Transformer Fuse: TF170 |  | 112SEG311 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 12 | 63 | 24415 | 764 | 0.03129 | 0.0025804 | 200 | 2426 | 2011/2012 | August-2011 | 8 | 2011
26123 | UNKNOWN FAULT - NIHONIHO SUB | 2011-08-11 10:52 | 2011-08-11 | 2011-08-11 13:38 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 166 | 36 | 24415 | 2969 | 0.12161 | 0.0014745 | 219 | 18968 | 2011/2012 | August-2011 | 8 | 2011
26122 | LV MAINTENANCE - NGATAMAHINE RD | 2011-08-11 13:42 | 2011-08-11 | 2011-08-11 14:30 | Calculated | TF2001 | TF2001 - Transformer Fuse: TF2001 |  | No Segment | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUS1 | Planned Outage for Customer Work | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 48 | 3 | 24415 | 144 | 0.0059 | 0.00012288 | 10 | 481 | 2011/2012 | August-2011 | 8 | 2011
26129 | WIRE OFF INSULATOR PLUS LINE DOWN - NIHONIHO FEEDER | 2011-08-12 03:50 | 2011-08-12 | 2011-08-12 11:42 | Calculated | 5262 | 5262 - Recloser with Bypass & Links 5262 |  | 412SEG5263-5262 | No Asset Group | Remote Rural F | Nihoniho | Nihoniho Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 463 | 69 | 24415 | 16600 | 0.67991 | 0.0028261 | 391.5 | 96033 | 2011/2012 | August-2011 | 8 | 2011
26132 | LIGHTNING FAULTY TX2870 - TROOPERS RD | 2011-08-12 06:20 | 2011-08-12 | 2011-08-12 11:31 | Calculated | TF2870 | TF2870 - Transformer Fuse: TF2870 |  | No Segment | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 310 | 1 | 24415 | 310 | 0.0127 | 4.0958e-05 | 30 | 9308 | 2011/2012 | August-2011 | 8 | 2011
26134 | LIGHTNING - TROOPERS RD | 2011-08-12 06:20 | 2011-08-12 | 2011-08-12 12:56 | Calculated | TF52 | TF52 - Transformer Fuse: TF52 |  | No Segment | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 395 | 3 | 24415 | 1185 | 0.04854 | 0.00012288 | 30 | 11858 | 2011/2012 | August-2011 | 8 | 2011
26131 | LIGHTNING - TROOPERS RD | 2011-08-12 06:20 | 2011-08-12 | 2011-08-12 07:16 | Calculated | TF1224 | TF1224 - Transformer Fuse: TF1224 |  | 107SEG244-575 | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 3 | 24415 | 165 | 0.00676 | 0.00012288 | 15 | 829 | 2011/2012 | August-2011 | 8 | 2011
26130 | LIGHTNING - TROOPERS RD | 2011-08-12 06:21 | 2011-08-12 | 2011-08-12 07:00 | Calculated | TF51 | TF51 - Transformer Fuse: TF51 |  | No Segment | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 6 | 24415 | 236 | 0.00967 | 0.00024575 | 30 | 1181 | 2011/2012 | August-2011 | 8 | 2011
26135 | MOVE POLE OUT OF BOG - COAST FEEDER | 2011-08-12 08:30 | 2011-08-12 | 2011-08-12 15:51 | Calculated | 268 | 268 - Air Break Switch 268 |  | 125SEG268-281 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 265 | 31 | 24415 | 5784 | 0.2369 | 0.0012697 | 248 | 49493 | 2011/2012 | August-2011 | 8 | 2011
26136 | JUMPER OFF TX 2804 - WHAREPAPA RD | 2011-08-12 10:02 | 2011-08-12 | 2011-08-12 11:17 | Calculated | 380 | 380 - Air Break Switch 380 |  | 122SEG398-380 | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 46 | 36 | 24415 | 1637 | 0.06705 | 0.0014745 | 307.5 | 13986 | 2011/2012 | August-2011 | 8 | 2011
26137 | REPLACE BROKEN POLE - MOKAU FEEDER | 2011-08-12 10:30 | 2011-08-12 | 2011-08-12 15:15 | Calculated | 1623 | 1623 - Fused Link 1623 |  | 128SEG1600-1623 | Mokau 128-04 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 285 | 17 | 24415 | 4849 | 0.19861 | 0.00069629 | 95 | 27101 | 2011/2012 | August-2011 | 8 | 2011
26138 | REPLACE HV FUSE TX 7M2 - EASTWOOD RD | 2011-08-12 12:41 | 2011-08-12 | 2011-08-12 13:30 | Calculated | TF7M2 | TF7M2 - Transformer Fuse: TF7M2 |  | No Segment | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 5 | 24415 | 241 | 0.00987 | 0.00020479 | 15 | 723 | 2011/2012 | August-2011 | 8 | 2011
26139 | BRANCH ON LINE - LOWER RETARUKE RD | 2011-08-12 15:46 | 2011-08-12 | 2011-08-12 16:25 | Calculated | 5398 | 5398 - Fused Link 5398 |  | 410SEG5398 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 39 | 4 | 24415 | 156 | 0.00639 | 0.00016383 | 43 | 1684 | 2011/2012 | August-2011 | 8 | 2011
26140 | LIGHTNING - REPLACE FAULTY TX - TROOPERS RD | 2011-08-12 17:56 | 2011-08-12 | 2011-08-12 19:22 | Calculated | TF52 | TF52 - Transformer Fuse: TF52 |  | No Segment | Oparure 107-06 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | Lightning | WEAT:LIGH:LEQT | Lightning Damage to Transformer | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 3 | 24415 | 255 | 0.01044 | 0.00012288 | 30 | 2554 | 2011/2012 | August-2011 | 8 | 2011
26141 | POSSUM - PURURU EAST ROAD | 2011-08-12 19:41 | 2011-08-12 | 2011-08-12 20:10 | Calculated | 675 | 675 - Fused Link 675 |  | 106SEG675 | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 7 | 24415 | 204 | 0.00836 | 0.00028671 | 63.3333 | 1846 | 2011/2012 | August-2011 | 8 | 2011
26124 | OCB 242 -788 TRIPPED - HANGATIKI A LINE | 2011-08-14 11:05 | 2011-08-14 | 2011-08-14 11:08 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 116 | 24415 | 448 | 0.01835 | 0.0047512 | 3228.2323 | 12482 | 2011/2012 | August-2011 | 8 | 2011
26125 | OCB 242 -788 TRIPPED - HANGATIKI A LINE | 2011-08-14 12:23 | 2011-08-14 | 2011-08-14 12:23 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 1 | 111 | 24415 | 111 | 0.00455 | 0.0045464 | 3280.8571 | 2843 | 2011/2012 | August-2011 | 8 | 2011
26126 | CB 788 TRIPPED - TAHAROA | 2011-08-14 13:01 | 2011-08-14 | 2011-08-14 13:04 | Calculated | 788 | 788 - Circuit Breaker 788 |  | No Segment | 201-01 Taharoa | Rural D | Taharoa B 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 111 | 24415 | 349 | 0.01429 | 0.0045464 | 3280.8571 | 10334 | 2011/2012 | August-2011 | 8 | 2011
26127 | REPLACE 5432 - SH 4 PAST OIO RD | 2011-08-14 17:16 | 2011-08-14 | 2011-08-14 17:52 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 36 | 18 | 24415 | 657 | 0.02691 | 0.00073725 | 93.75 | 3423 | 2011/2012 | August-2011 | 8 | 2011
26128 | REPLACE 5432 - SH 4 PAST OIO RD | 2011-08-14 19:16 | 2011-08-14 | 2011-08-14 19:47 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 18 | 24415 | 567 | 0.02322 | 0.00073725 | 93.75 | 2954 | 2011/2012 | August-2011 | 8 | 2011
26143 | REPLACE LINK 289 - MAHOE RD - PUTAKI SPUR | 2011-08-15 06:10 | 2011-08-15 | 2011-08-15 08:05 | Calculated | 289 | 289 - Fused Link 289 |  | 101SEG289-552 | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 115 | 16 | 24415 | 1842 | 0.07545 | 0.00065533 | 105 | 12090 | 2011/2012 | August-2011 | 8 | 2011
26144 | Sect 5511 Tripped - Makino Rd | 2011-08-15 07:11 | 2011-08-15 | 2011-08-15 09:11 | Calculated | 5511 | 5511 - Sectionaliser with Bypass 5511 |  | 410SEG5511-5517 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 29 | 24415 | 3487 | 0.14282 | 0.0011878 | 186.5 | 22426 | 2011/2012 | August-2011 | 8 | 2011
26147 | DISCONNECTION FOR SAFETY - MAIHIIHI RD | 2011-08-15 08:17 | 2011-08-15 | 2011-08-15 11:50 | Calculated | TF1989 | TF1989 - Transformer Fuse: TF1989 |  | No Segment | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 213 | 3 | 24415 | 639 | 0.02617 | 0.00012288 | 15 | 3199 | 2011/2012 | August-2011 | 8 | 2011
26149 | REPLACE HV FUSE AT TX2480 - WAITANGURU RD | 2011-08-15 11:41 | 2011-08-15 | 2011-08-15 13:01 | Calculated | TF2408 | TF2408 - Transformer Fuse: TF2408 |  | No Segment | Caves 101-03 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 80 | 1 | 24415 | 80 | 0.00328 | 4.0958e-05 | 7.5 | 601 | 2011/2012 | August-2011 | 8 | 2011
26150 | OCB 378 TRIPPED - AOTEAROA RD | 2011-08-15 19:50 | 2011-08-15 | 2011-08-15 19:57 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 7 | 316 | 24415 | 2254 | 0.09232 | 0.012943 | 2603.5 | 18571 | 2011/2012 | August-2011 | 8 | 2011
26151 | REPLACE HV FUSE AT TX1176 - MARAETAUA RD | 2011-08-15 21:09 | 2011-08-15 | 2011-08-15 21:57 | Calculated | TF1176 | TF1176 - Transformer Fuse: TF1176 |  | 104SEG245 | Te Kuiti South 104-02 | Rural C | Te Kuiti South | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 48 | 2 | 24415 | 97 | 0.00397 | 8.1917e-05 | 30 | 1458 | 2011/2012 | August-2011 | 8 | 2011
26152 | CHANGE RED TAGGED LV POLE - BROADFOOT PL | 2011-08-16 09:37 | 2011-08-16 | 2011-08-16 14:36 | Calculated | TF466 | TF466 - Transformer Fuse: TF466 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 299 | 28 | 24415 | 8376 | 0.34307 | 0.0011468 | 103.7037 | 31022 | 2011/2012 | August-2011 | 8 | 2011
26153 | UPGRADE TX2750 - SCOTT RD | 2011-08-16 10:00 | 2011-08-16 | 2011-08-16 15:22 | Calculated | TF2750 | TF2750 - Transformer Fuse: TF2750 |  | 119SEG403-492 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 322 | 4 | 24415 | 1288 | 0.05275 | 0.00016383 | 40 | 12887 | 2011/2012 | August-2011 | 8 | 2011
26154 | LINE DOWN - MOKAU FEEDER | 2011-08-16 19:05 | 2011-08-16 | 2011-08-17 00:23 | Calculated | 1627 | 1627 - Recloser with Incoming Link1627 |  | 128SEG1626-1642 | Mokau 128-08 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 317 | 9 | 24415 | 2369 | 0.09703 | 0.00036863 | 80 | 21128 | 2011/2012 | August-2011 | 8 | 2011
26157 | REPLACE HV FUSE AT TX901 - HENDERSON RD | 2011-08-17 06:58 | 2011-08-17 | 2011-08-17 09:21 | Calculated | TF901 | TF901 - Transformer Fuse: TF901 |  | 120SEG416-479 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 143 | 1 | 24415 | 143 | 0.00586 | 4.0958e-05 | 25 | 3579 | 2011/2012 | August-2011 | 8 | 2011
26158 | LIGHTNING - WAIPUNA RD | 2011-08-17 08:01 | 2011-08-17 | 2011-08-17 09:11 | Calculated | TF511 | TF511 - Transformer Fuse: TF511 |  | No Segment | Caves 101-13 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 70 | 1 | 24415 | 70 | 0.00287 | 4.0958e-05 | 10 | 702 | 2011/2012 | August-2011 | 8 | 2011
26159 | REPLACE INSULATORS - SOUTHERN FEEDER | 2011-08-17 09:05 | 2011-08-17 | 2011-08-17 12:54 | Calculated | 5113 | 5113 - Fused Link 5113 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 229 | 34 | 24415 | 5216 | 0.21364 | 0.0013926 | 159.25 | 25951 | 2011/2012 | August-2011 | 8 | 2011
26160 | FUSE PULLED APART - RANGIPARE ST | 2011-08-17 10:25 | 2011-08-17 | 2011-08-17 11:40 | Calculated | TF1377 | TF1377 - Transformer Fuse: TF1377 |  | 112SEG307-314 | Otorohanga 112-01 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 75 | 57 | 24415 | 4282 | 0.17538 | 0.0023346 | 219.2308 | 16471 | 2011/2012 | August-2011 | 8 | 2011
26165 | WIND - SH 4 PAST OIO RD | 2011-08-18 00:02 | 2011-08-18 | 2011-08-18 00:31 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Weather | Wind | WEAT:EENW2:EENW1 | Wind Borne Material - Vegetation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 29 | 18 | 24415 | 525 | 0.0215 | 0.00073725 | 90 | 2624 | 2011/2012 | August-2011 | 8 | 2011
26166 | REPLACE HV FUSE AT TX151 - MAIROA RD | 2011-08-18 08:31 | 2011-08-18 | 2011-08-18 10:57 | Calculated | TF151 | TF151 - Transformer Fuse: TF151 |  | 107SEG176-269 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 2 | 24415 | 290 | 0.01188 | 8.1917e-05 | 25 | 3636 | 2011/2012 | August-2011 | 8 | 2011
26167 | REPLACE POLE - ONGARUE FEEDER | 2011-08-18 09:34 | 2011-08-18 | 2011-08-18 13:46 | Calculated | 5574 | 5574 - Fused Link 5574 |  | 421SEG5574 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 252 | 5 | 24415 | 1261 | 0.05165 | 0.00020479 | 22.5 | 5676 | 2011/2012 | August-2011 | 8 | 2011
26168 | CHANGE TX POLE - NORTHERN FEEDER | 2011-08-18 09:34 | 2011-08-18 | 2011-08-18 16:10 | Calculated | 5339 | 5339 - Fused Link 5339 |  | 402SEG5339 | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 396 | 10 | 24415 | 3962 | 0.16228 | 0.00040958 | 75 | 29716 | 2011/2012 | August-2011 | 8 | 2011
26169 | REPLACE HV FUSE AT TX 120 - HAURUA RD | 2011-08-18 14:22 | 2011-08-18 | 2011-08-18 16:43 | Calculated | TF120 | TF120 - Transformer Fuse: TF120 |  | 101SEG519-232 | Caves 101-04 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 141 | 2 | 24415 | 282 | 0.01155 | 8.1917e-05 | 15 | 2117 | 2011/2012 | August-2011 | 8 | 2011
26170 | FAULTY LINK 5936 - MANUNUI FEEDER | 2011-08-18 16:28 | 2011-08-18 | 2011-08-18 19:22 | Calculated | 5936 | 5936 - Fuse Switch 5936 |  | 408SEG5936-5557 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Asset Related | Switch-gear | FAIL:FSWG2:FSWP | Switch-gear Failure High Voltage | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 174 | 49 | 24415 | 6713 | 0.27495 | 0.002007 | 234 | 30130 | 2011/2012 | August-2011 | 8 | 2011
26171 | BRANCH ON LINE - WAITEPIPI RD | 2011-08-19 08:11 | 2011-08-19 | 2011-08-19 10:41 | Calculated | TF321 | TF321 - Transformer Fuse: TF321 |  | No Segment | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 2 | 24415 | 300 | 0.01229 | 8.1917e-05 | 25 | 3755 | 2011/2012 | August-2011 | 8 | 2011
26172 | REPLACE POLES - RURAL FEEDER | 2011-08-19 09:36 | 2011-08-19 | 2011-08-19 16:01 | Calculated | 509 | 509 - Fused Link 509 |  | 126SEG509 | Rural 126-02 | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 384 | 10 | 24415 | 3841 | 0.15732 | 0.00040958 | 68 | 26122 | 2011/2012 | August-2011 | 8 | 2011
26173 | REPLACE FAULTY ABS 5548 WITH LINKS - NORTHERN FEEDER | 2011-08-19 10:04 | 2011-08-19 | 2011-08-19 11:38 | Calculated | 5351 | 5351 - Air Break Switch 5351 |  | 402SEG5351-5548 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 94 | 197 | 24415 | 18550 | 0.75978 | 0.0080688 | 879.322 | 82802 | 2011/2012 | August-2011 | 8 | 2011
26174 | REPLACE POLES - WESTERN FEEDER | 2011-08-19 10:07 | 2011-08-19 | 2011-08-19 11:49 | Calculated | 5887 | 5887 - Earth Working Link 5887 |  | 403SEG5887-5322 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 102 | 19 | 24415 | 1944 | 0.07962 | 0.00077821 | 110 | 11258 | 2011/2012 | August-2011 | 8 | 2011
26175 | REPLACE HV FUSE AT TX2959 - MANGAOTAKI RD | 2011-08-19 11:04 | 2011-08-19 | 2011-08-19 16:01 | Calculated | TF2959 | TF2959 - Transformer Fuse: TF2959 |  | No Segment | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 297 | 1 | 24415 | 297 | 0.01216 | 4.0958e-05 | 15 | 4457 | 2011/2012 | August-2011 | 8 | 2011
26176 | DUCKS - SH 49 | 2011-08-20 10:02 | 2011-08-20 | 2011-08-20 10:45 | Calculated | TF4082 | TF4082 - Transformer Fuse: TF4082 |  | No Segment | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Asset Related | Other | FAIL:FOLD:FIPS1 | Incorrect Protection Settings | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24415 |  | 0 | 0 |  |  | 2011/2012 | August-2011 | 8 | 2011
26179 | INSTALL LIVE LINE BREAKS AT POLES 24 AND 14 - OPARURE FEEDER | 2011-08-22 09:04 | 2011-08-22 | 2011-08-22 09:49 | Calculated | TF1219 | TF1219 - Transformer Fuse: TF1219 |  | 107SEG213-242 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 45 | 41 | 24415 | 1851 | 0.07581 | 0.0016793 | 113.8889 | 5143 | 2011/2012 | August-2011 | 8 | 2011
26178 | REPLACE XARM TO PTF ON POLE 47 AND PL MAINTENANCE - MAHOENUI FEEDER | 2011-08-22 10:16 | 2011-08-22 | 2011-08-22 15:01 | Calculated | 1636 | 1636 - Recloser 1636 |  | 113SEG1636-1537 | Mahoenui 113-07 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 284 | 16 | 24415 | 2756 | 0.11288 | 0.00065533 | 100 | 17978 | 2011/2012 | August-2011 | 8 | 2011
26177 | REPLACING POLES - RURAL FEEDER | 2011-08-22 10:36 | 2011-08-22 | 2011-08-22 14:25 | Calculated | 509 | 509 - Fused Link 509 |  | 126SEG509 | Rural 126-02 | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 229 | 10 | 24415 | 2292 | 0.09388 | 0.00040958 | 68 | 15589 | 2011/2012 | August-2011 | 8 | 2011
26180 | LV FAULT - WAIHORA RD | 2011-08-23 09:19 | 2011-08-23 | 2011-08-23 10:36 | Calculated | TF3285 | TF3285 - Transformer Fuse: TF3285 |  | 123SEG1760 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 76 | 1 | 24415 | 76 | 0.00311 | 4.0958e-05 | 0 | 0 | 2011/2012 | August-2011 | 8 | 2011
26182 | LET LINES DOWN AND EARTH FOR TREE WORK - RANGITOTO FEEDER | 2011-08-23 09:32 | 2011-08-23 | 2011-08-23 14:55 | Calculated | 246 | 246 - Fused Link 246 |  | 106SEG246-252 | Rangitoto 106-04 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 323 | 28 | 24415 | 9058 | 0.371 | 0.0011468 | 162.5 | 52574 | 2011/2012 | August-2011 | 8 | 2011
26183 | UPGRADE TX 8R18 TO AN RTE TYPE (ETEL) - KURATAU FEEDER | 2011-08-23 09:33 | 2011-08-23 | 2011-08-23 15:42 | Calculated | 5913 | 5913 - Solid Link 5913 |  | 406SEG5913-6599 | Kuratau 406-03 | Rural D | Kuratau | Kuratau Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 369 | 211 | 24415 | 77890 | 3.1902 | 0.0086422 | 800 | 295319 | 2011/2012 | August-2011 | 8 | 2011
26181 | REPLACING POLES - RURAL FEEDER | 2011-08-23 10:36 | 2011-08-23 | 2011-08-23 14:42 | Calculated | 509 | 509 - Fused Link 509 |  | 126SEG509 | Rural 126-02 | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 246 | 10 | 24415 | 2462 | 0.10084 | 0.00040958 | 68 | 16746 | 2011/2012 | August-2011 | 8 | 2011
26184 | RECLOSER 5935 TRIPPED - MAGPIE - KIRTONS RD | 2011-08-23 14:00 | 2011-08-23 | 2011-08-23 15:57 | Calculated | 5768 | 5768 - Recloser with Bypass 5768 |  | No Segment | No Asset Group | Remote Rural F | Manunui | Manunui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 104 | 71 | 24415 | 5799 | 0.23752 | 0.002908 | 382.75 | 32208 | 2011/2012 | August-2011 | 8 | 2011
26185 | REPLACE HV FUSE AT TX 1098 - MAIHIIHI RD | 2011-08-24 08:19 | 2011-08-24 | 2011-08-24 10:06 | Calculated | TF1098 | TF1098 - Transformer Fuse: TF1098 |  | 111SEG665 | Maihiihi 111-08 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 107 | 3 | 24415 | 321 | 0.01315 | 0.00012288 | 15 | 1609 | 2011/2012 | August-2011 | 8 | 2011
26186 | STILL SEARCHING FOR THE PHANTOM FAULT - SOUTHERN FEEDER | 2011-08-24 09:21 | 2011-08-24 | 2011-08-24 13:50 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 268 | 18 | 24415 | 2454 | 0.10051 | 0.00073725 | 90 | 11185 | 2011/2012 | August-2011 | 8 | 2011
26187 | REPLACE YELLOW TAGGED POLE - SECT 1721 - TE MAPARA FEEDER | 2011-08-24 10:09 | 2011-08-24 | 2011-08-24 16:08 | Calculated | 1722 | 1722 - Fused Link 1722 |  | 117SEG1722-1721 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 358 | 31 | 24415 | 11109 | 0.45501 | 0.0012697 | 214 | 76690 | 2011/2012 | August-2011 | 8 | 2011
26188 | LET LINES DOWN AND EARTH FOR TREE WORK - RANGITOTO FEEDER | 2011-08-24 10:13 | 2011-08-24 | 2011-08-24 15:50 | Calculated | 2093 | 2093 - Fused Link 2093 |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 337 | 5 | 24415 | 1688 | 0.06914 | 0.00020479 | 22.5 | 7599 | 2011/2012 | August-2011 | 8 | 2011
26189 | BROKEN FUSE HOLDER - WILSON RD | 2011-08-24 11:09 | 2011-08-24 | 2011-08-24 13:44 | Calculated | TF2783 | TF2783 - Transformer Fuse: TF2783 |  | No Segment | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation | Switchgear : Fuse Carriers | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 154 | 1 | 24415 | 154 | 0.00631 | 4.0958e-05 | 5 | 774 | 2011/2012 | August-2011 | 8 | 2011
26190 | REPLACE HV FUSE AT TX 82 - HAURUA RD | 2011-08-24 11:30 | 2011-08-24 | 2011-08-24 13:03 | Calculated | TF82 | TF82 - Transformer Fuse: TF82 |  | No Segment | Caves 101-02 | Urban A | Caves | Hangatiki Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 3 | 24415 | 279 | 0.01143 | 0.00012288 | 25 | 2327 | 2011/2012 | August-2011 | 8 | 2011
26192 | BROKEN XARM AT TX 2028 - MAKAUITI TD | 2011-08-24 15:55 | 2011-08-24 | 2011-08-24 17:41 | Calculated | 1713 | 1713 - Fused Link 1713 |  | 115SEG1713 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 106 | 7 | 24415 | 742 | 0.03039 | 0.00028671 | 60 | 6367 | 2011/2012 | August-2011 | 8 | 2011
26193 | FAULTY TX 2216 - MANGATORO RD | 2011-08-24 19:15 | 2011-08-24 | 2011-08-24 20:42 | Calculated | TF2216 | TF2216 - Transformer Fuse: TF2216 |  | 128SEG1645-1632 | Mokau 128-10 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 87 | 2 | 24415 | 174 | 0.00713 | 8.1917e-05 | 15 | 1306 | 2011/2012 | August-2011 | 8 | 2011
26197 | OPARURE - CHANGING POLES AND XARMS | 2011-08-25 09:34 | 2011-08-25 | 2011-08-25 14:55 | Calculated | 630 | 630 - Air Break Switch 630 |  | 107SEG630-677 | Oparure 107-01 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 321 | 31 | 24415 | 9956 | 0.40778 | 0.0012697 | 365 | 117231 | 2011/2012 | August-2011 | 8 | 2011
26198 | UPGRADE TX 1090 - MANGAORONGO RD | 2011-08-25 11:23 | 2011-08-25 | 2011-08-25 15:48 | Calculated | TF1090 | TF1090 - Transformer Fuse: TF1090 |  | 111SEG339-346 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 265 | 1 | 24415 | 265 | 0.01085 | 4.0958e-05 | 15 | 3978 | 2011/2012 | August-2011 | 8 | 2011
26200 | LINE DOWN - KAKARA RD | 2011-08-26 12:47 | 2011-08-26 | 2011-08-26 15:18 | Calculated | 1730 | 1730 - Fused Link 1730 |  | 115SEG1730 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation | OH Lines : Conductor - Bare Copper | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 9 | 24415 | 1360 | 0.0557 | 0.00036863 | 67.5 | 10203 | 2011/2012 | August-2011 | 8 | 2011
26202 | UNKNOWN - B PHASE ER - KURATAU SUB | 2011-08-28 06:53 | 2011-08-28 | 2011-08-28 07:03 | Calculated | 5180 | 5180 - Circuit Breaker 5180 |  | No Segment | 509-01 Kuratau | Rural D | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 10 | 4 | 24415 | 40 | 0.00164 | 0.00016383 | 450 | 4575 | 2011/2012 | August-2011 | 8 | 2011
26203 | LV FAULT - RERENGA ST | 2011-08-28 20:29 | 2011-08-28 | 2011-08-28 21:36 | Calculated | TF2154 | TF2154 - Transformer Fuse: TF2154 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 58 | 24415 | 3893 | 0.15945 | 0.0023756 | 218.8679 | 14693 | 2011/2012 | August-2011 | 8 | 2011
26205 | BROKEN XARM AND LINK - ROTO RD | 2011-08-29 14:58 | 2011-08-29 | 2011-08-29 18:38 | Calculated | 5579 | 5579 - Fused Link 5579 |  | 413SEG5579-5571 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 180 | 12 | 24415 | 2151 | 0.0881 | 0.0004915 | 85 | 15239 | 2011/2012 | August-2011 | 8 | 2011
26206 | REPLACE FUSE LINK 980 - OLD HOROPITO RD | 2011-08-29 15:22 | 2011-08-29 | 2011-08-29 16:30 | Calculated | 5980 | 5980 - Fused Link 5980 |  | 415SEG5980 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 67 | 4 | 24415 | 268 | 0.01098 | 0.00016383 | 20 | 1342 | 2011/2012 | August-2011 | 8 | 2011
26208 | CHANGING POLES AND XARMS - MOKAUITI FEEDER | 2011-08-30 08:09 | 2011-08-30 | 2011-08-30 15:57 | Calculated | 1710 | 1710 - Air Break Switch 1710 |  | 115SEGTempABS1-1705 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 425 | 146 | 24415 | 4241 | 0.1737 | 0.0059799 | 1005.5 | 30700 | 2011/2012 | August-2011 | 8 | 2011
26209 | UNKNOWN O/C EVENT - OHAKUNE SUB | 2011-08-30 15:55 | 2011-08-30 | 2011-08-30 16:51 | Calculated | 5005 | 5005 - Circuit Breaker 5005 |  | No Segment | 517-01 Transpower Ohakune | Urban A | Ohakune Town | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 925 | 24415 | 25553 | 1.0466 | 0.037887 | 6347.1859 | 196526 | 2011/2012 | August-2011 | 8 | 2011
26211 | REPLACE ROTTEN SWER POLE TO TX2053 - MOKAUITI FEEDER | 2011-08-31 12:31 | 2011-08-31 | 2011-08-31 15:24 | Calculated | 1719 | 1719 - Fused Link 1719 |  | 115SEG1719-1647 | Mokauiti 115-04 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 125 | 37 | 24415 | 1851 | 0.07581 | 0.0015155 | 280.5 | 13741 | 2011/2012 | August-2011 | 8 | 2011
26215 | DUCKS - AT TX404 - AILSA ST | 2011-08-31 18:37 | 2011-08-31 | 2011-08-31 18:57 | Calculated | TF404 | TF404 - Transformer Fuse: TF404 |  | 107SEG299-218 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Asset Related | Other | FAIL:FOLD:FIPS1 | Incorrect Protection Settings | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 20 | 1 | 24415 | 20 | 0.00082 | 4.0958e-05 | 300 | 6050 | 2011/2012 | August-2011 | 8 | 2011
26216 | TREE THROUGH LINE - CB5168 TRIPPED - RANGIPO/HAUTU | 2011-08-31 23:13 | 2011-08-31 | 2011-09-01 04:56 | Calculated | 5168 | 5168 - Circuit Breaker with Bypass 5168 |  | 424SEG6652-5168 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VOCL1 | Vegetation Non Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 343 | 196 | 24415 | 52996 | 2.1706 | 0.0080279 | 1050.0264 | 263641 | 2011/2012 | August-2011 | 8 | 2011
26220 | CHANGING POLES AND XARMS - MOKAUITI FEEDER | 2011-09-01 08:06 | 2011-09-01 | 2011-09-01 15:57 | Calculated | 1710 | 1710 - Air Break Switch 1710 |  | 115SEGTempABS1-1705 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 383 | 146 | 24424 | 4026 | 0.16484 | 0.0059777 | 1005.5 | 29045 | 2011/2012 | September-2011 | 9 | 2011
26218 | CLEAN, CHECK AND SERVICE REC 6041 - WESTERN FEEDER | 2011-09-01 08:25 | 2011-09-01 | 2011-09-01 15:25 | Calculated | 5997 | 5997 - Air Break Switch 5997 |  | 403SEG5997-5547RET | Western 403-01 | Urban A | Western | Borough Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 308 | 340 | 24424 | 11889 | 0.48678 | 0.013921 | 2179.9459 | 73416 | 2011/2012 | September-2011 | 9 | 2011
26217 | UPGRADE LV FUSING - ARAPAE RD | 2011-09-01 09:37 | 2011-09-01 | 2011-09-01 10:49 | Calculated | TF1760 | TF1760 - Transformer Fuse: TF1760 |  | 117SEG1317 | Te Mapara 117-05 | Rural C | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 72 | 3 | 24424 | 216 | 0.00884 | 0.00012283 | 50 | 3608 | 2011/2012 | September-2011 | 9 | 2011
26221 | Line Down - Te Waireka Rd | 2011-09-02 05:14 | 2011-09-02 | 2011-09-02 11:13 | Calculated | 124 | 124 - Circuit Breaker 124 |  | No Segment | 203-01 Te Waireka Road | Urban A | Maihiihi | Te Waireka Zone Substation | OH Lines : Conductor - Bare ACSR | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 341 | 1091 | 24424 | 184760 | 7.5647 | 0.044669 | 10765.9 | 1717296 | 2011/2012 | September-2011 | 9 | 2011
26222 | LV LINE DOWN - BAYLEY RD | 2011-09-02 12:22 | 2011-09-02 | 2011-09-02 13:12 | Calculated | TF373 | TF373 - Transformer Fuse: TF373 |  | No Segment | Wharepapa 122-05 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 50 | 3 | 24424 | 150 | 0.00614 | 0.00012283 | 25 | 1255 | 2011/2012 | September-2011 | 9 | 2011
26223 | LV FAULT - OURUWHERO RD | 2011-09-02 16:01 | 2011-09-02 | 2011-09-02 17:26 | Calculated | TF224 | TF224 - Transformer Fuse: TF224 |  | 112SEG637-352 | Otorohanga 112-07 | Urban A | Otorohanga | Te Waireka Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 5 | 24424 | 425 | 0.0174 | 0.00020472 | 50 | 4259 | 2011/2012 | September-2011 | 9 | 2011
26224 | REPLACE HV FUSE AT TX154 - MAIROA RD | 2011-09-02 17:37 | 2011-09-02 | 2011-09-02 18:21 | Calculated | TF154 | TF154 - Transformer Fuse: TF154 |  | 116SEG1334-269 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 44 | 2 | 24424 | 88 | 0.0036 | 8.1887e-05 | 25 | 1102 | 2011/2012 | September-2011 | 9 | 2011
26225 | REPLACE HV FUSE AT LOCAL SERVICE TX 4078 - TAWHAI SUB | 2011-09-05 08:00 | 2011-09-05 | 2011-09-05 10:31 | Calculated | Fuse513-1 | Fuse513-1 - 11kv local service fuses |  | No Segment | 513-01 Tawhai | Rural D | No Feeder |  |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24424 |  | 0 | 0 |  |  | 2011/2012 | September-2011 | 9 | 2011
26226 | LV FAULT - AOTEAROA RD | 2011-09-06 21:19 | 2011-09-06 | 2011-09-06 22:08 | Calculated | TF3284 | TF3284 - Transformer Fuse: T3284 |  | 122SEG807 | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 1 | 24424 | 49 | 0.00201 | 4.0943e-05 | 0 | 0 | 2011/2012 | September-2011 | 9 | 2011
26228 | INSTALL NEW TX POLE AT TX 3371 - MOKAI FEEDER | 2011-09-07 09:50 | 2011-09-07 | 2011-09-07 12:09 | Calculated | 528 | 528 - Air Break Switch 528 |  | 123SEG490-528 | Mokai 123-02 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 139 | 7 | 24424 | 974 | 0.03988 | 0.0002866 | 80 | 11132 | 2011/2012 | September-2011 | 9 | 2011
26240 | REPLACE LINK 471 - POIHIPI RD | 2011-09-08 06:41 | 2011-09-08 | 2011-09-08 10:48 | Calculated | 471 | 471 - Fused Link 471 |  | 123SEG471 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 247 | 10 | 24424 | 2472 | 0.10121 | 0.00040943 | 85 | 21016 | 2011/2012 | September-2011 | 9 | 2011
26238 | REPLACE HV FUSE AT TX 9P2 - SH 41 | 2011-09-08 08:15 | 2011-09-08 | 2011-09-08 10:15 | Calculated | TF09P02 | TF09P02 - Transformer Fuse: TF09P02 |  | 609SEG5839-5163 | National Park / Kuratau 609-01 | Urban A | National Park / Kuratau 33 | Direct from National Park Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 119 | 1 | 24424 | 119 | 0.00487 | 4.0943e-05 | 100 | 11920 | 2011/2012 | September-2011 | 9 | 2011
26239 | REPLACE POLE 1111291 WITH NEW POLE AND HARDWARE - NGAHAPE RD | 2011-09-08 09:46 | 2011-09-08 | 2011-09-08 14:26 | Calculated | TF618 | TF618 - Transformer Fuse: TF618 |  | No Segment | Maihiihi 111-07 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 280 | 7 | 24424 | 1961 | 0.08029 | 0.0002866 | 50 | 14009 | 2011/2012 | September-2011 | 9 | 2011
26241 | BROKEN XARM - MANGAWHIO RD | 2011-09-08 12:40 | 2011-09-08 | 2011-09-08 15:13 | Calculated | TF824 | TF824 - Transformer Fuse: TF824 |  | No Segment | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation | OH Lines : Crossarm - Wood | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 153 | 2 | 24424 | 306 | 0.01253 | 8.1887e-05 | 5 | 766 | 2011/2012 | September-2011 | 9 | 2011
26244 | CAR VS POLE - KURATAU | 2011-09-10 00:20 | 2011-09-10 | 2011-09-10 09:20 | Calculated | 6125 | 6125 - Circuit Breaker 6125 |  | 406SEG6125-5658 | 509-01 Kuratau | Rural D | Kuratau | Kuratau Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUP | Vehicle Accident/Collision | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 410 | 1310 | 24424 | 11513 | 0.47138 | 0.053636 | 6617.9758 | 108494 | 2011/2012 | September-2011 | 9 | 2011
26246 | WIND - TURAKINA VALLEY RD | 2011-09-11 09:40 | 2011-09-11 | 2011-09-11 11:23 | Calculated | TF22O5 | TF22O5 - Transformer Fuse: TF22O5 |  | 416SEG5689-5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 102 | 3 | 24424 | 307 | 0.01257 | 0.00012283 | 15 | 1535 | 2011/2012 | September-2011 | 9 | 2011
26247 | WIND - TOKIRIMA HIGHWAY | 2011-09-11 11:06 | 2011-09-11 | 2011-09-11 12:51 | Calculated | 5571 | 5571 - Sectionaliser with Bypass & Links 5571 |  | 413SEG5571-5570 | Ohura 413-05 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 105 | 12 | 24424 | 1263 | 0.05171 | 0.00049132 | 100 | 10528 | 2011/2012 | September-2011 | 9 | 2011
26248 | WIND - OKAHUKURA SUB | 2011-09-11 11:51 | 2011-09-11 | 2011-09-11 12:45 | Calculated | 5467 | 5467 - Recloser with Bypass & Links 5467 |  | 402SEG5467-5472 | Northern 402-05 | Remote Rural E | Northern | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 54 | 72 | 24424 | 3908 | 0.16001 | 0.0029479 | 486.75 | 26422 | 2011/2012 | September-2011 | 9 | 2011
26249 | WIND -TREE THROUGH LINE - RUAPEHU RD | 2011-09-11 13:00 | 2011-09-11 | 2011-09-11 15:39 | Calculated | 5677 | 5677 - Recloser with Bypass 5677 |  | 416SEG5677-5681 | Tangiwai 416-02 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 145 | 220 | 24424 | 24873 | 1.0184 | 0.0090075 | 2129 | 258467 | 2011/2012 | September-2011 | 9 | 2011
26251 | TREE THROUGH LV LINE - MANGAHAUHAU VALLEY RD | 2011-09-11 18:31 | 2011-09-11 | 2011-09-11 19:11 | Calculated | 5717 | 5717 - Fused Link 5717 |  | 416SEG5717 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 40 | 7 | 24424 | 282 | 0.01155 | 0.0002866 | 60 | 2422 | 2011/2012 | September-2011 | 9 | 2011
26252 | LIGHTNING - NGAPAENGA RD | 2011-09-12 07:36 | 2011-09-12 | 2011-09-12 08:58 | Calculated | TF576 | TF576 - Transformer Fuse: TF576 |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 2 | 24424 | 164 | 0.00671 | 8.1887e-05 | 10 | 822 | 2011/2012 | September-2011 | 9 | 2011
26253 | OIO SWER FAULT - RECONFIGURE 3 PHASE AND SWER | 2011-09-12 09:08 | 2011-09-12 | 2011-09-12 13:04 | Calculated | 5432 | 5432 - Fused Link 5432 |  | 409SEG5113-5432 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 186 | 54 | 24424 | 3833 | 0.15694 | 0.0022109 | 326.25 | 18511 | 2011/2012 | September-2011 | 9 | 2011
26254 | BROKEN XARM - KAHOREKAU RD | 2011-09-12 10:00 | 2011-09-12 | 2011-09-12 11:11 | Calculated | TF1511 | TF1511 - Transformer Fuse: TF1511 |  | 122SEG448-REG34J | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 3 | 24424 | 213 | 0.00872 | 0.00012283 | 25 | 1780 | 2011/2012 | September-2011 | 9 | 2011
26255 | REPLACE LA - TAWA ST | 2011-09-12 10:04 | 2011-09-12 | 2011-09-12 11:01 | Calculated | TF7D24 | TF7D24 - Transformer Fuse: TF7D24 |  | 413SEG6543-5996 | Ohura 413-02 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 57 | 39 | 24424 | 2233 | 0.09143 | 0.0015968 | 513.1579 | 29386 | 2011/2012 | September-2011 | 9 | 2011
26258 | LIGHTNING - NGAPAENGA RD | 2011-09-12 11:42 | 2011-09-12 | 2011-09-12 14:13 | Calculated | TF1440 | TF1440 - Transformer Fuse: TF1440 |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 1 | 24424 | 151 | 0.00618 | 4.0943e-05 | 10 | 1511 | 2011/2012 | September-2011 | 9 | 2011
26256 | WIND / CLASH - WAITOMO VALLEY RD | 2011-09-12 11:43 | 2011-09-12 | 2011-09-12 13:10 | Calculated | TF216 | TF216 - Transformer Fuse: TF216 |  | 112SEG331-355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 2 | 24424 | 174 | 0.00712 | 8.1887e-05 | 10 | 871 | 2011/2012 | September-2011 | 9 | 2011
26257 | WIND - UPPER RETARUKE SUB | 2011-09-12 12:49 | 2011-09-12 | 2011-09-12 13:25 | Calculated | 5494 | 5494 - Recloser with Bypass 5494 |  | 410SEG5494-5493 | Raurimu 410-04 | Remote Rural F | Raurimu | National Park Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 36 | 50 | 24424 | 1807 | 0.07398 | 0.0020472 | 309.5833 | 11191 | 2011/2012 | September-2011 | 9 | 2011
26259 | WIND - SUNSHINE DR | 2011-09-12 15:07 | 2011-09-12 | 2011-09-12 15:56 | Calculated | TF8I58 | TF8I58 - Transformer Fuse: TF8I58 |  | 404SEG5022-L1.10 | Matapuna 404-01 | Rural B | Matapuna | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 10 | 24424 | 491 | 0.0201 | 0.00040943 | 50 | 2457 | 2011/2012 | September-2011 | 9 | 2011
26260 | WIND - AOTEAROA RD | 2011-09-12 15:44 | 2011-09-12 | 2011-09-12 18:00 | Calculated | TF2379 | TF2379 - Transformer Fuse: TF2379 |  | No Segment | Wharepapa 122-02 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 136 | 2 | 24424 | 272 | 0.01114 | 8.1887e-05 | 25 | 3403 | 2011/2012 | September-2011 | 9 | 2011
26261 | WIND - TREE ON LINE - NIHONIHO | 2011-09-12 17:55 | 2011-09-12 | 2011-09-12 21:53 | Calculated | 5641 | 5641 - Recloser with Bypass & Links 5641 |  | 413SEG6781-5666 | No Asset Group | Remote Rural F | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 238 | 381 | 24424 | 90792 | 3.7173 | 0.015599 | 2600.4048 | 619676 | 2011/2012 | September-2011 | 9 | 2011
26264 | CHANGING POLES AND XARMS - MOKAUITI FEEDER | 2011-09-13 08:03 | 2011-09-13 | 2011-09-13 15:28 | Calculated | 1710 | 1710 - Air Break Switch 1710 |  | 115SEGTempABS1-1705 | Mokauiti 115-02 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 381 | 86 | 24424 | 7195 | 0.29459 | 0.0035211 | 590.5 | 51156 | 2011/2012 | September-2011 | 9 | 2011
26265 | LV MAINTENANCE - PAREKAWA DR | 2011-09-13 09:00 | 2011-09-13 | 2011-09-13 11:59 | Calculated | TF4157 | TF4157 - Transformer Fuse: TF4157 |  | 425SEG6552-6550 | Motuoapa 425-01 | Rural D | Motuoapa | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 178 | 36 | 24424 | 6414 | 0.26261 | 0.001474 | 327.2727 | 58309 | 2011/2012 | September-2011 | 9 | 2011
26266 | WIND - MANGAHOUHOU RD | 2011-09-13 09:43 | 2011-09-13 | 2011-09-13 10:56 | Calculated | TF21K4 | TF21K4 - Transformer Fuse: TF21K4 |  | 416SEG5717 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 4 | 24424 | 293 | 0.012 | 0.00016377 | 30 | 2201 | 2011/2012 | September-2011 | 9 | 2011
26268 | WIND - TREE ON LINE -WHAKAMARO RD | 2011-09-13 13:39 | 2011-09-13 | 2011-09-18 14:38 | Calculated | 5460 | 5460 - Fused Link 5460 |  | 403SEG5460-5812 | Western 403-05 | Rural B | Western | Borough Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 113 | 42 | 24424 | 3856 | 0.15788 | 0.0017196 | 323.75 | 29557 | 2011/2012 | September-2011 | 9 | 2011
26269 | WIND - WAIMAHORA RD | 2011-09-13 16:25 | 2011-09-13 | 2011-09-13 18:56 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 150 | 22 | 24424 | 2940 | 0.12037 | 0.00090075 | 188 | 26076 | 2011/2012 | September-2011 | 9 | 2011
26270 | WIND - BROWNS RD | 2011-09-13 16:30 | 2011-09-13 | 2011-09-13 17:58 | Calculated | TF1539 | TF1539 - Transformer Fuse: TF1539 |  | 125SEG1268 | Coast 125-03 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 2 | 24424 | 176 | 0.00721 | 8.1887e-05 | 15 | 1322 | 2011/2012 | September-2011 | 9 | 2011
26271 | LIGHTNING - SH 30 PUREORA | 2011-09-13 16:51 | 2011-09-13 | 2011-09-13 17:57 | Calculated | TF964 | TF964 - Transformer Fuse: TF964 |  | 119SEG432-653 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 66 | 2 | 24424 | 132 | 0.0054 | 8.1887e-05 | 30 | 1985 | 2011/2012 | September-2011 | 9 | 2011
26272 | LINE DOWN - MOKAUITI RD | 2011-09-13 19:49 | 2011-09-13 | 2011-09-13 21:25 | Calculated | 1713 | 1713 - Fused Link 1713 |  | 115SEG1713 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 7 | 24424 | 673 | 0.02755 | 0.0002866 | 60 | 5770 | 2011/2012 | September-2011 | 9 | 2011
26273 | WIND - PAEKAKA RD | 2011-09-13 19:49 | 2011-09-13 | 2011-09-13 20:02 | Calculated | 1512 | 1512 - Recloser 1512 |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 13 | 165 | 24424 | 2172 | 0.08893 | 0.0067557 | 1090.5 | 14358 | 2011/2012 | September-2011 | 9 | 2011
26274 | LINE DOWN AT POLE 254 - BEFORE MOKAU BRIDGE | 2011-09-13 20:49 | 2011-09-13 | 2011-09-14 02:32 | Calculated | 1620 | 1620 - Recloser 1620 |  | 128SEG1619-1620 | Mokau 128-05 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 342 | 246 | 24424 | 73660 | 3.0159 | 0.010072 | 1617.5577 | 476269 | 2011/2012 | September-2011 | 9 | 2011
26275 | LINE DOWN AT POLE 125/160 - WHAREPAPA FEEDER | 2011-09-13 22:14 | 2011-09-13 | 2011-09-14 11:23 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation | OH Lines : Conductor - Bare ACSR | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 770 | 316 | 24424 | 27174 | 1.1126 | 0.012938 | 2603.5 | 157103 | 2011/2012 | September-2011 | 9 | 2011
26277 | WIND/TREE THROUGH LINE - TAWA ST | 2011-09-14 02:40 | 2011-09-14 | 2011-09-14 12:21 | Calculated | 5641 | 5641 - Recloser with Bypass & Links 5641 |  | 413SEG6781-5666 | Ohura 413-01 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 580 | 381 | 24424 | 73612 | 3.0139 | 0.015599 | 2600.4048 | 615472 | 2011/2012 | September-2011 | 9 | 2011
26276 | WIND - MOHAKATINO RD | 2011-09-14 07:04 | 2011-09-14 | 2011-09-14 12:10 | Calculated | TF2180 | TF2180 - Transformer Fuse: TF2180 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 305 | 2 | 24424 | 610 | 0.02498 | 8.1887e-05 | 25 | 7631 | 2011/2012 | September-2011 | 9 | 2011
26278 | WIND - KIRITIHERE - BY ROAD JUNCTION | 2011-09-14 07:12 | 2011-09-14 | 2011-09-14 10:21 | Calculated | 564 | 564 - Recloser 564 |  | 125SEG563-569 | Coast 125-05 | Rural D | Coast | Te Anga Zone Substation (Containerised) |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 189 | 19 | 24424 | 3596 | 0.14723 | 0.00077792 | 160 | 30288 | 2011/2012 | September-2011 | 9 | 2011
26279 | FAULTY LA - MCDONALD RD | 2011-09-14 08:22 | 2011-09-14 | 2011-09-14 14:06 | Calculated | TF722 | TF722 - Transformer Fuse: TF722 |  | 120SEG408-465 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 343 | 3 | 24424 | 1029 | 0.04213 | 0.00012283 | 22.5 | 7721 | 2011/2012 | September-2011 | 9 | 2011
26280 | WIND - NGAPAENGA RD | 2011-09-14 08:32 | 2011-09-14 | 2011-09-14 08:51 | Calculated | TF576 | TF576 - Transformer Fuse: TF576 |  | 107SEG265-263 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 19 | 2 | 24424 | 38 | 0.00156 | 8.1887e-05 | 10 | 193 | 2011/2012 | September-2011 | 9 | 2011
26281 | WIND - MAIROA RD | 2011-09-14 09:32 | 2011-09-14 | 2011-09-14 13:08 | Calculated | TF1138 | TF1138 - Transformer Fuse: TF1138 |  | 116SEG1334-269 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 216 | 1 | 24424 | 216 | 0.00884 | 4.0943e-05 | 25 | 5403 | 2011/2012 | September-2011 | 9 | 2011
26282 | OCB 242 AND OCB 788 TRIPPED - TAHAROA A FEEDER | 2011-09-14 11:58 | 2011-09-14 | 2011-09-14 12:00 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 2 | 111 | 24424 | 240 | 0.00983 | 0.0045447 | 3280.8571 | 7108 | 2011/2012 | September-2011 | 9 | 2011
26283 | WIND - LINE DOWN - MOHAKATINO | 2011-09-14 13:04 | 2011-09-14 | 2011-09-14 14:50 | Calculated | 1639 | 1639 - Fused Link 1639 |  | 128SEG1639 | Mokau 128-07 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 106 | 21 | 24424 | 2231 | 0.09134 | 0.00085981 | 122.5 | 13017 | 2011/2012 | September-2011 | 9 | 2011
26284 | WIND - WAIMAHORA RD | 2011-09-14 13:55 | 2011-09-14 | 2011-09-14 16:59 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 184 | 22 | 24424 | 4056 | 0.16607 | 0.00090075 | 188 | 34660 | 2011/2012 | September-2011 | 9 | 2011
26286 | WIND - WAIMAHORA RD | 2011-09-15 08:26 | 2011-09-15 | 2011-09-15 14:43 | Calculated | 2041 | 2041 - Fused Link 2041 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 377 | 4 | 24424 | 1509 | 0.06178 | 0.00016377 | 65 | 24529 | 2011/2012 | September-2011 | 9 | 2011
26287 | REPLACE HV FUSE AT TX 2342 - WHANGAMATA RD | 2011-09-15 15:47 | 2011-09-15 | 2011-09-15 19:05 | Calculated | TF2342 | TF2342 - Transformer Fuse: TF2342 |  | 123SEG145-553 | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 198 | 1 | 24424 | 198 | 0.00811 | 4.0943e-05 | 2.5 | 495 | 2011/2012 | September-2011 | 9 | 2011
26288 | LIGHTNING - HANGATIKI | 2011-09-15 16:20 | 2011-09-15 | 2011-09-15 16:23 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 441 | 24424 | 992 | 0.04062 | 0.018056 | 5744.0402 | 12924 | 2011/2012 | September-2011 | 9 | 2011
26289 | LIGHTNING - TAHAROA RD | 2011-09-15 16:21 | 2011-09-15 | 2011-09-15 20:11 | Calculated | TF1367 | TF1367 - Transformer Fuse: TF1367 |  | 126SEG525 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 230 | 15 | 24424 | 3452 | 0.14134 | 0.00061415 | 107.1429 | 24662 | 2011/2012 | September-2011 | 9 | 2011
26290 | WIND - SH 49 - CNR LAKES RD | 2011-09-15 18:54 | 2011-09-15 | 2011-09-15 20:15 | Calculated | 5673 | 5673 - Fused Link 5673 |  | 416SEG5673-5675 | Tangiwai 416-01 | Urban A | Tangiwai | Direct from Ohakune Supply |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 43 | 24424 | 1042 | 0.04266 | 0.0017606 | 287.5 | 7870 | 2011/2012 | September-2011 | 9 | 2011
26291 | FAULTY LA - TAHAROA RD | 2011-09-15 19:10 | 2011-09-15 | 2011-09-15 19:43 | Calculated | TF680 | TF680 - Transformer Fuse: TF680 |  | 126SEG525 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 1 | 24424 | 33 | 0.00135 | 4.0943e-05 | 30 | 996 | 2011/2012 | September-2011 | 9 | 2011
26293 | TREE CONTRACTORS - DIGGER VS LINE - WHAKAMARU - ATIAMURI LEG | 2011-09-16 12:18 | 2011-09-16 | 2011-09-16 13:29 | Calculated | 1720 | 1720 - Circuit Breaker 1720 |  | 310SEG1025X-2196 | 214-01 Whakamaru | Rural D | Whakamaru 33 | Direct from Whakamaru Supply |  | Third Party (includeds unauthorised contractors) | ETRE2 | 3PAR:ETRE2:ETRE1 | Tree Clearing/Trimming Activities | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 67 | 762 | 24424 | 29418 | 1.2045 | 0.031199 | 8752.6667 | 331127 | 2011/2012 | September-2011 | 9 | 2011
26294 | WIND - MOKAUITI RD - FOR PATOTO RD | 2011-09-16 12:42 | 2011-09-16 | 2011-09-16 14:13 | Calculated | 1713 | 1713 - Fused Link 1713 |  | 115SEG1713 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 91 | 7 | 24424 | 638 | 0.02612 | 0.0002866 | 60 | 5473 | 2011/2012 | September-2011 | 9 | 2011
26296 | LIGHTNING - MANGAOKEWA RD | 2011-09-16 12:43 | 2011-09-16 | 2011-09-16 14:13 | Calculated | TF910 | TF910 - Transformer Fuse: TF910 |  | 103SEG453-459 | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 89 | 4 | 24424 | 357 | 0.01462 | 0.00016377 | 25 | 2236 | 2011/2012 | September-2011 | 9 | 2011
26297 | LIGHTNING - WAIPA VALLEY RD | 2011-09-16 14:05 | 2011-09-16 | 2011-09-16 15:38 | Calculated | TF2958 | TF2958 - Transformer Fuse: TF2958 |  | No Segment | Benneydale 103-09 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 92 | 1 | 24424 | 92 | 0.00377 | 4.0943e-05 | 15 | 1386 | 2011/2012 | September-2011 | 9 | 2011
26299 | LIGHTNING - ONAIO RD | 2011-09-16 16:30 | 2011-09-16 | 2011-09-16 17:41 | Calculated | TF2046 | TF2046 - Transformer Fuse: TF2046 |  | 114SEG1114 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 71 | 2 | 24424 | 142 | 0.00581 | 8.1887e-05 | 15 | 1068 | 2011/2012 | September-2011 | 9 | 2011
26300 | REPLACE HV FUSE AT TX 2359 - MAIN STH RD - OTOROHANGA | 2011-09-17 21:38 | 2011-09-17 | 2011-09-17 22:24 | Calculated | TF2359 | TF2359 - Transformer Fuse: TF2359 |  | No Segment | McDonalds 110-03 | Urban A | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 3 | 24424 | 135 | 0.00553 | 0.00012283 | 30 | 1356 | 2011/2012 | September-2011 | 9 | 2011
26301 | JUMPER OFF DDO - TE ANGA RD | 2011-09-18 08:15 | 2011-09-18 | 2011-09-18 11:00 | Calculated | 514 | 514 - Fused Link 514 |  | 101SEG514 | Caves 101-10 | Remote Rural E | Caves | Hangatiki Zone Substation | OH Lines : Jumper - Bare Copper | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 165 | 26 | 24424 | 2509 | 0.10273 | 0.0010645 | 175 | 15307 | 2011/2012 | September-2011 | 9 | 2011
26302 | REPLACE HV FUSE AT TX 21M08 - DOMAIN RD | 2011-09-18 15:07 | 2011-09-18 | 2011-09-18 15:41 | Calculated | TF21M8 | TF21M8 - Transformer Fuse: TF21M8 |  | 416SEG5722 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 33 | 1 | 24424 | 33 | 0.00135 | 4.0943e-05 | 10 | 331 | 2011/2012 | September-2011 | 9 | 2011
26303 | REPLACE HV FUSE AT TX 157 - PUNGAREHU RD | 2011-09-19 08:00 | 2011-09-19 | 2011-09-19 09:01 | Calculated | TF157 | TF157 - Transformer Fuse: TF157 |  | 116SEG272 | Piopio 116-04 | Rural D | Piopio | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 60 | 3 | 24424 | 180 | 0.00737 | 0.00012283 | 10 | 601 | 2011/2012 | September-2011 | 9 | 2011
26304 | LINE DOWN AT POLE 331 - HANGATIKI | 2011-09-19 08:52 | 2011-09-19 | 2011-09-19 21:28 | Calculated | TPHangatiki CB262 | TPHangatiki CB262 - 33kV Minimum Oil Circuit Breaker TP262 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa B 33 | Direct from Hangatiki Supply | OH Lines : Conductor - Bare ACSR | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 85 | 441 | 24424 | 28296 | 1.1585 | 0.018056 | 5744.0402 | 221754 | 2011/2012 | September-2011 | 9 | 2011
26305 | FAULTY INSULATOR - BY TE ROTO SCHOOL | 2011-09-19 17:31 | 2011-09-19 | 2011-09-19 22:39 | Calculated | 5591 | 5591 - Sectionaliser with Bypass & Links 5591 |  | 418SEG5591-5939 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation | OH Lines : Insulator - Disc | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 308 | 54 | 24424 | 16654 | 0.68187 | 0.0022109 | 215.5 | 66463 | 2011/2012 | September-2011 | 9 | 2011
26308 | HV MAINTENANCE - RAURIMU FEEDER | 2011-09-20 09:16 | 2011-09-20 | 2011-09-20 15:04 | Calculated | 5161 | 5161 - Fused Link 5161 |  | 410SEG5161-5235 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 347 | 14 | 24424 | 4861 | 0.19903 | 0.00057321 | 142.5 | 49480 | 2011/2012 | September-2011 | 9 | 2011
26306 | REPLACE FAULTY TX 82 - HAURUA RD | 2011-09-20 10:19 | 2011-09-20 | 2011-09-20 11:20 | Calculated | TF82 | TF82 - Transformer Fuse: TF82 |  | No Segment | Caves 101-02 | Urban A | Caves | Hangatiki Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 61 | 3 | 24424 | 183 | 0.00749 | 0.00012283 | 25 | 1530 | 2011/2012 | September-2011 | 9 | 2011
26307 | WIND - MOKAUITI RD - FOR PATOTO RD | 2011-09-20 11:39 | 2011-09-20 | 2011-09-20 12:53 | Calculated | 1713 | 1713 - Fused Link 1713 |  | 115SEG1713 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 73 | 7 | 24424 | 512 | 0.02096 | 0.0002866 | 60 | 4392 | 2011/2012 | September-2011 | 9 | 2011
26310 | REPLACE ABS 331 AND POLE EITHER SIDE OF - ALSO FIT TAP OFF LINKS TO MULIPLE TX - OTOROHANGA FEEDER | 2011-09-21 08:47 | 2011-09-21 | 2011-09-21 15:36 | Calculated | 550 | 550 - Air Break Switch 550 |  | 112SEG550-545 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 348 | 30 | 24424 | 10419 | 0.42659 | 0.0012283 | 300.8333 | 104484 | 2011/2012 | September-2011 | 9 | 2011
26312 | RAISE TAPS - KAAHU RD | 2011-09-21 11:40 | 2011-09-21 | 2011-09-21 13:15 | Calculated | TF3167 | TF3167 - Transformer Fuse: TF3167 |  | 129SEG721 | Tirohanga 129-01 (was 124-03) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 1 | 24424 | 95 | 0.00389 | 4.0943e-05 | 100 | 9513 | 2011/2012 | September-2011 | 9 | 2011
26313 | REPLACE HV FUSE AT TX 8G2 - KURURAU RD | 2011-09-21 11:49 | 2011-09-21 | 2011-09-21 13:18 | Calculated | TF8G2 | TF8G2 - Transformer Fuse: TF8G2 |  | 403SEG5316-5622 | Western 403-06 | Rural D | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 89 | 5 | 24424 | 445 | 0.01822 | 0.00020472 | 18.75 | 1671 | 2011/2012 | September-2011 | 9 | 2011
26309 | BROKEN INSULATOR AT ABS 5161 - TURN OFF TO RAURIMU TOWNSHIP | 2011-09-21 15:23 | 2011-09-21 | 2011-09-21 15:51 | Calculated | 5543 | 5543 - Fused Link 5543 |  | 410SEG5543-5161 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 28 | 99 | 24424 | 2788 | 0.11415 | 0.0040534 | 638.3333 | 17979 | 2011/2012 | September-2011 | 9 | 2011
26314 | SCHEDULED MAINTENANCE - MAIHIIHI RD | 2011-09-22 09:35 | 2011-09-22 | 2011-09-22 14:40 | Calculated | 368 | 368 - Fused Link 368 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 305 | 34 | 24424 | 10376 | 0.42483 | 0.0013921 | 345 | 105293 | 2011/2012 | September-2011 | 9 | 2011
26316 | RECLOSER 5119 TRIPPED - UNKNOWN - E/F AND O/C - GOLF RD EXTENSION | 2011-09-22 16:15 | 2011-09-22 | 2011-09-22 16:17 | Calculated | 5119 | 5119 - Recloser 5119 |  | 402SEG5118-5119RET | Northern 402-02 | Rural C | Northern | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 2 | 159 | 24424 | 344 | 0.01408 | 0.00651 | 1623.5 | 3517 | 2011/2012 | September-2011 | 9 | 2011
26318 | CHANGE FAULTY TX 2480 - WAITANGURU RD | 2011-09-23 10:49 | 2011-09-23 | 2011-09-23 12:19 | Calculated | TF2480 | TF2480 - Transformer Fuse: TF2480 |  | No Segment | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 90 | 1 | 24424 | 90 | 0.00368 | 4.0943e-05 | 3 | 270 | 2011/2012 | September-2011 | 9 | 2011
26319 | BROKEN XARM - BORCK'S RD - FOR OPOTIKI RD | 2011-09-23 18:46 | 2011-09-23 | 2011-09-23 20:15 | Calculated | 5339 | 5339 - Fused Link 5339 |  | 402SEG5339 | Northern 402-02 | Rural C | Northern | Borough Zone Substation | OH Lines : Crossarm - Wood | Asset Related | Cross-arm | FAIL:FXAR:FXAX | Cross-Arm Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 88 | 10 | 24424 | 883 | 0.03615 | 0.00040943 | 75 | 6623 | 2011/2012 | September-2011 | 9 | 2011
26320 | OCB 222 TRIPPED - HANGAKITI | 2011-09-24 14:56 | 2011-09-24 | 2011-09-24 14:58 | Calculated | TPHangatikiCB222 | TPHangatikiCB222 - 33kV Minimum Oil Circuit Breaker TP222 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Te Waireka Rd 33 | Direct from Hangatiki Supply |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 0 | 0 | 24424 |  | 0 | 0 |  |  | 2011/2012 | September-2011 | 9 | 2011
26808 | OCB 5198 AND 5200 TRIPPED - TURANGI SUB | 2011-09-27 08:13 | 2011-09-27 | 2011-09-28 21:30 | Calculated | 5198 | 5198 - Circuit Breaker 5198 |  | No Segment | 505-01 Turangi | Rural C | Turangi | Turangi Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 186 | 1968 | 24424 | 79754 | 3.2654 | 0.080576 | 13805 | 469679 | 2011/2012 | September-2011 | 9 | 2011
26323 | REPLACE POLES - ONGARUE FEEDER | 2011-09-27 09:39 | 2011-09-27 | 2011-09-27 15:00 | Calculated | 5595 | 5595 - Solid Link 5595 |  | 421SEG5595 | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 321 | 4 | 24424 | 1284 | 0.05257 | 0.00016377 | 40 | 12848 | 2011/2012 | September-2011 | 9 | 2011
26322 | REPLACE POLES - OTOROHANGA FEEDER | 2011-09-27 09:41 | 2011-09-27 | 2011-09-27 16:15 | Calculated | 355 | 355 - Fused Link 355 |  | 112SEG355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 394 | 11 | 24424 | 4340 | 0.17769 | 0.00045038 | 112.5 | 44386 | 2011/2012 | September-2011 | 9 | 2011
26325 | OVERLOAD - WAIOTAKA SUBSTATION | 2011-09-28 21:43 | 2011-09-28 | 2011-09-28 21:47 | Calculated | 6336 | 6336 - Circuit Breaker Waiotaka 33kV 6336 |  | 606SEG6546-6336 | Lake Taupo 606-01 | Urban A | Lake Taupo 33 | Direct from Tokaanu Supply |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 3 | 744 | 24424 | 1711 | 0.07005 | 0.030462 | 5080 | 11683 | 2011/2012 | September-2011 | 9 | 2011
26327 | LIGHTNING - MAIHIIHI RD - BY FOOTBALL CLUB | 2011-10-02 05:18 | 2011-10-02 | 2011-10-02 07:44 | Calculated | 1148 | 1148 - Fused Link 1148 |  | 111SEG148 | Maihiihi 111-09 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 146 | 6 | 24464 | 877 | 0.03585 | 0.00024526 | 80 | 11705 | 2011/2012 | October-2011 | 10 | 2011
26331 | REPLACE COMPLETE STRUCTURE TX1339 - OPARURE FEEDER | 2011-10-03 09:20 | 2011-10-03 | 2011-10-03 15:04 | Calculated | TF1339 | TF1339 - Transformer Fuse: TF1339 |  | 107SEG649-160 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 344 | 12 | 24464 | 4129 | 0.16878 | 0.00049052 | 54.5455 | 18772 | 2011/2012 | October-2011 | 10 | 2011
26332 | LIGHTNING - FAULTY TX676 - WHAREPAPA RD | 2011-10-03 11:34 | 2011-10-03 | 2011-10-03 21:52 | Calculated | 378 | 378 - Recloser 378 |  | 122SEG448-REG34J | Wharepapa 122-03 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | WOLD | WEAT:WOLD:WORE | WORE | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 478 | 317 | 24464 | 33011 | 1.3494 | 0.012958 | 2616 | 307335 | 2011/2012 | October-2011 | 10 | 2011
26333 | LIGHTNING - MAIHIIHI RD | 2011-10-03 12:07 | 2011-10-03 | 2011-10-03 14:01 | Calculated | TF483 | TF483 - Transformer Fuse: TF483 |  | 111SEG363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 114 | 2 | 24464 | 228 | 0.00932 | 8.1753e-05 | 10 | 1142 | 2011/2012 | October-2011 | 10 | 2011
26334 | LIGHTNING - MAIHIIHI RD | 2011-10-03 12:09 | 2011-10-03 | 2011-10-03 14:31 | Calculated | TF2878 | TF2878 - Transformer Fuse: TF2878 |  | 111SEG363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 142 | 1 | 24464 | 142 | 0.0058 | 4.0876e-05 | 50 | 7109 | 2011/2012 | October-2011 | 10 | 2011
26335 | LIGHTNING - MAIHIIHI RD | 2011-10-03 12:11 | 2011-10-03 | 2011-10-03 15:06 | Calculated | TF286 | TF286 - Transformer Fuse: TF286 |  | 111SEG368-363 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 175 | 2 | 24464 | 350 | 0.01431 | 8.1753e-05 | 10 | 1751 | 2011/2012 | October-2011 | 10 | 2011
26336 | LIGHTNING - WAIMAHORA RD | 2011-10-03 15:01 | 2011-10-03 | 2011-10-03 15:46 | Calculated | 170 | 170 - Sectionaliser 170 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 45 | 22 | 24464 | 994 | 0.04063 | 0.00089928 | 188 | 8494 | 2011/2012 | October-2011 | 10 | 2011
26337 | LIGHTNING - WALL RD | 2011-10-03 16:41 | 2011-10-03 | 2011-10-03 18:17 | Calculated | TF372 | TF372 - Transformer Fuse: TF372 |  | No Segment | Maihiihi 111-11 | Remote Rural E | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 96 | 3 | 24464 | 288 | 0.01177 | 0.00012263 | 5 | 480 | 2011/2012 | October-2011 | 10 | 2011
26338 | BIRD ON TX9E2 - OPATU SUB | 2011-10-03 16:50 | 2011-10-03 | 2011-10-03 18:44 | Calculated | 5417 | 5417 - Recloser 5417 |  | 413SEG5418-5417 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 114 | 68 | 24464 | 6451 | 0.26369 | 0.0027796 | 459.5556 | 45575 | 2011/2012 | October-2011 | 10 | 2011
26339 | LIGHTNING - TIROHANGA RD | 2011-10-03 17:59 | 2011-10-03 | 2011-10-03 19:39 | Calculated | TF240 | TF240 - Transformer Fuse: TF240 |  | 129SEG477 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 2 | 24464 | 200 | 0.00818 | 8.1753e-05 | 60 | 6015 | 2011/2012 | October-2011 | 10 | 2011
26343 | LIGHTNING - JULIAN ST | 2011-10-03 18:04 | 2011-10-03 | 2011-10-03 19:28 | Calculated | TF1501 | TF1501 - Transformer Fuse: TF1501 |  | 106SEG543-224 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 84 | 1 | 24464 | 84 | 0.00343 | 4.0876e-05 | 10 | 842 | 2011/2012 | October-2011 | 10 | 2011
26340 | LIGHTNING - JULIAN ST | 2011-10-03 18:05 | 2011-10-03 | 2011-10-03 19:28 | Calculated | TF1501 | TF1501 - Transformer Fuse: TF1501 |  | 106SEG543-224 | Rangitoto 106-01 | Urban A | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 83 | 1 | 24464 | 83 | 0.00339 | 4.0876e-05 | 10 | 832 | 2011/2012 | October-2011 | 10 | 2011
26344 | LIGHTNING - VEALES RD - TAHAIA | 2011-10-03 19:49 | 2011-10-03 | 2011-10-03 20:53 | Calculated | 620 | 620 - Fused Link 620 |  | 109SEG620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 8 | 24464 | 513 | 0.02097 | 0.00032701 | 75 | 4815 | 2011/2012 | October-2011 | 10 | 2011
26345 | LIGHTNING - GRIFFITHS RD | 2011-10-03 19:52 | 2011-10-03 | 2011-10-03 21:30 | Calculated | TF945 | TF945 - Transformer Fuse: TF945 |  | No Segment | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 98 | 5 | 24464 | 491 | 0.02007 | 0.00020438 | 25 | 2455 | 2011/2012 | October-2011 | 10 | 2011
26348 | LINE DOWN TO TX8Q4 - SH 41 - PUKAWA E/W SUB | 2011-10-03 20:37 | 2011-10-03 | 2011-10-04 00:39 | Calculated | 5248 | 5248 - Recloser with Bypass 5248 |  | 406SEG09R02-5248 | Kuratau 406-02 | Rural D | Kuratau | Kuratau Zone Substation | OH Lines : Conductor - Bare Copper | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDB | Conductor Failure - Bare Wire - Al | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 242 | 35 | 24464 | 8475 | 0.34643 | 0.0014307 | 182.5 | 44195 | 2011/2012 | October-2011 | 10 | 2011
26346 | TREE ON LINE - AROHENA RD | 2011-10-03 21:31 | 2011-10-03 | 2011-10-03 23:33 | Calculated | 1072 | 1072 - Circuit Breaker 1072 Huirimu |  | 121SEG1072-753 | 211-01 Arohena | Rural D | Huirimu | Arohena Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 121 | 168 | 24464 | 15473 | 0.63248 | 0.0068672 | 1693.1667 | 144938 | 2011/2012 | October-2011 | 10 | 2011
26347 | LIGHTNING - TE KURA RD | 2011-10-03 22:00 | 2011-10-03 | 2011-10-03 22:49 | Calculated | 383 | 383 - Fused Link 383 |  | 110SEG383 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 16 | 24464 | 786 | 0.03213 | 0.00065402 | 115 | 5654 | 2011/2012 | October-2011 | 10 | 2011
26350 | LIGHTNING - TE KURA RD | 2011-10-03 22:00 | 2011-10-03 | 2011-10-03 23:33 | Calculated | TF994 | TF994 - Transformer Fuse: TF994 |  | 110SEG383 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 93 | 7 | 24464 | 652 | 0.02665 | 0.00028613 | 35 | 3260 | 2011/2012 | October-2011 | 10 | 2011
26351 | LIGHTNING - TE KURA RD | 2011-10-03 22:01 | 2011-10-03 | 2011-10-04 01:03 | Calculated | TF200 | TF200 - Transformer Fuse: TF200 |  | 110SEG383 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 182 | 3 | 24464 | 546 | 0.02232 | 0.00012263 | 30 | 5464 | 2011/2012 | October-2011 | 10 | 2011
26352 | LIGHTNING - MANGAWHERO RD | 2011-10-04 03:42 | 2011-10-04 | 2011-10-04 05:30 | Calculated | 302 | 302 - Fused Link 302 |  | 109SEG302 | Gravel Scoop 109-03 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 108 | 8 | 24464 | 866 | 0.0354 | 0.00032701 | 55 | 5955 | 2011/2012 | October-2011 | 10 | 2011
26353 | LIGHTNING - MCRAE RD | 2011-10-04 04:38 | 2011-10-04 | 2011-10-04 07:15 | Calculated | TF333 | TF333 - Transformer Fuse: TF333 |  | No Segment | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 157 | 4 | 24464 | 629 | 0.02571 | 0.00016351 | 25 | 3932 | 2011/2012 | October-2011 | 10 | 2011
26354 | LIGHTNING - OTEWA RD | 2011-10-04 04:58 | 2011-10-04 | 2011-10-04 06:15 | Calculated | TF643 | TF643 - Transformer Fuse: TF643 |  | No Segment | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 77 | 3 | 24464 | 231 | 0.00944 | 0.00012263 | 25 | 1932 | 2011/2012 | October-2011 | 10 | 2011
26355 | LIGHTNING - TE KURA RD | 2011-10-04 05:56 | 2011-10-04 | 2011-10-04 08:27 | Calculated | 383 | 383 - Fused Link 383 |  | 110SEG383 | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 151 | 16 | 24464 | 2315 | 0.09463 | 0.00065402 | 115 | 16658 | 2011/2012 | October-2011 | 10 | 2011
26356 | LIGHTNING - ROTONGATA RD | 2011-10-04 06:01 | 2011-10-04 | 2011-10-04 11:07 | Calculated | TF1301 | TF1301 - Transformer Fuse: TF1301 |  | 122SEG568-702 | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 306 | 3 | 24464 | 918 | 0.03752 | 0.00012263 | 15 | 4593 | 2011/2012 | October-2011 | 10 | 2011
26357 | LIGHTNING - OWAEWENGA RD | 2011-10-04 06:36 | 2011-10-04 | 2011-10-04 10:10 | Calculated | TF1432 | TF1432 - Transformer Fuse: TF1432 |  | 109SEG170-171 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 214 | 2 | 24464 | 428 | 0.0175 | 8.1753e-05 | 15 | 3213 | 2011/2012 | October-2011 | 10 | 2011
26358 | LIGHTNING - OLD TE KUITI RD | 2011-10-04 07:17 | 2011-10-04 | 2011-10-04 07:46 | Calculated | TF208 | TF208 - Transformer Fuse: TF208 |  | No Segment | McDonalds 110-02 | Urban A | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 3 | 24464 | 87 | 0.00356 | 0.00012263 | 25 | 732 | 2011/2012 | October-2011 | 10 | 2011
26359 | LIGHTNING - SH 32 - KURATAU | 2011-10-04 07:26 | 2011-10-04 | 2011-10-04 10:25 | Calculated | TF8P12 | TF8P12 - Transformer Fuse: TF8P12 |  | 426SEG5359-5237 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 179 | 2 | 24464 | 358 | 0.01463 | 8.1753e-05 | 0 | 0 | 2011/2012 | October-2011 | 10 | 2011
26365 | LIGHTNING - ONGARUE RD | 2011-10-04 07:50 | 2011-10-04 | 2011-10-04 09:45 | Calculated | 5362 | 5362 - Sectionaliser with Bypass & Links 5362 |  | 421SEG5349-5362 | Ongarue 421-04 | Remote Rural F | Ongarue | Tuhua Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 114 | 18 | 24464 | 2057 | 0.08408 | 0.00073578 | 135 | 15428 | 2011/2012 | October-2011 | 10 | 2011
26366 | MAGPIE - SH 32 | 2011-10-04 08:00 | 2011-10-04 | 2011-10-04 11:13 | Calculated | 5020 | 5020 - Air Break Switch 5020 |  | 426SEG5020 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 193 | 2 | 24464 | 406 | 0.0166 | 8.1753e-05 | 60 | 12193 | 2011/2012 | October-2011 | 10 | 2011
26367 | LIGHTNING - GRIFFITHS RD | 2011-10-04 08:11 | 2011-10-04 | 2011-10-04 11:36 | Calculated | TF890 | TF890 - Transformer Fuse: TF890 |  | No Segment | Wharepapa 122-04 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 205 | 4 | 24464 | 821 | 0.03356 | 0.00016351 | 15 | 3081 | 2011/2012 | October-2011 | 10 | 2011
26368 | LIGHTNING - OTEWA RD | 2011-10-04 08:45 | 2011-10-04 | 2011-10-04 10:04 | Calculated | TF2280 | TF2280 - Transformer Fuse: TF2280 |  | No Segment | Gravel Scoop 109-02 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 3 | 24464 | 238 | 0.00973 | 0.00012263 | 25 | 1985 | 2011/2012 | October-2011 | 10 | 2011
26369 | LIGHTNING - VEALE RD | 2011-10-04 09:11 | 2011-10-04 | 2011-10-04 10:51 | Calculated | TF1422 | TF1422 - Transformer Fuse: TF1422 |  | 109SEG620 | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 100 | 1 | 24464 | 100 | 0.00409 | 4.0876e-05 | 10 | 1004 | 2011/2012 | October-2011 | 10 | 2011
26370 | LIGHTNING - MANGAOKEWA NORTH RD | 2011-10-04 09:35 | 2011-10-04 | 2011-10-04 13:47 | Calculated | TF138 | TF138 - Transformer Fuse: TF138 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 252 | 5 | 24464 | 1262 | 0.05159 | 0.00020438 | 41.6667 | 10518 | 2011/2012 | October-2011 | 10 | 2011
26371 | LIGHTNING - WARD ST | 2011-10-04 09:41 | 2011-10-04 | 2011-10-04 11:24 | Calculated | TF1A52 | TF1A52 - Transformer Fuse: TF1A52 |  | 402SEGA4.6-5351 | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 103 | 41 | 24464 | 4240 | 0.17332 | 0.0016759 | 205 | 21203 | 2011/2012 | October-2011 | 10 | 2011
26372 | LV FUSING FAULT - KAWAKAWA RD | 2011-10-04 10:44 | 2011-10-04 | 2011-10-04 12:03 | Calculated | TF2721 | TF2721 - Transformer Fuse: TF2721 |  | No Segment | Mokai 123-03 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 78 | 2 | 24464 | 156 | 0.00638 | 8.1753e-05 | 30 | 2346 | 2011/2012 | October-2011 | 10 | 2011
26373 | LIGHTNING - BELL RD | 2011-10-04 11:05 | 2011-10-04 | 2011-10-04 11:56 | Calculated | TF1A45 | TF1A45 - Transformer Fuse: TF1A45 |  | No Segment | Northern 402-01 | Rural B | Northern | Borough Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 51 | 2 | 24464 | 102 | 0.00417 | 8.1753e-05 | 100 | 5116 | 2011/2012 | October-2011 | 10 | 2011
26374 | LIGHTNING - SH 32 | 2011-10-04 12:32 | 2011-10-04 | 2011-10-04 14:05 | Calculated | TF7Q10 | TF7Q10 - Transformer Fuse: TF7Q10 |  | 426SEG5526-5359 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 93 | 3 | 24464 | 279 | 0.0114 | 0.00012263 | 15 | 1397 | 2011/2012 | October-2011 | 10 | 2011
26375 | LIGHTNING - PAEWHENUA RD | 2011-10-04 14:35 | 2011-10-04 | 2011-10-04 15:38 | Calculated | TF416 | TF416 - Transformer Fuse: TF416 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 3 | 24464 | 189 | 0.00773 | 0.00012263 | 30 | 1895 | 2011/2012 | October-2011 | 10 | 2011
26376 | LIGHTNING - PAEWHENUA RD | 2011-10-04 14:35 | 2011-10-04 | 2011-10-04 15:38 | Calculated | TF2638 | TF2638 - Transformer Fuse: TF2638 |  | 111SEG707-399 | Maihiihi 111-13 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 63 | 1 | 24464 | 63 | 0.00258 | 4.0876e-05 | 25 | 1579 | 2011/2012 | October-2011 | 10 | 2011
26385 | LIGHTNING - WAITEWHENA RD | 2011-10-05 07:51 | 2011-10-05 | 2011-10-05 09:55 | Calculated | TF5D2 | TF5D2 - Transformer Fuse: TF5D2 |  | No Segment | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 124 | 4 | 24464 | 496 | 0.02027 | 0.00016351 | 25 | 3104 | 2011/2012 | October-2011 | 10 | 2011
26380 | LIGHTNING - RANGIATEA RD | 2011-10-05 11:07 | 2011-10-05 | 2011-10-05 12:08 | Calculated | TF435 | TF435 - Transformer Fuse: TF435 |  | No Segment | Gravel Scoop 109-13 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 4 | 24464 | 245 | 0.01001 | 0.00016351 | 30 | 1839 | 2011/2012 | October-2011 | 10 | 2011
26381 | LIGHTNING - WHAWHARUA RD | 2011-10-05 15:48 | 2011-10-05 | 2011-10-05 16:37 | Calculated | TF2538 | TF2538 - Transformer Fuse: TF2538 |  | No Segment | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 49 | 3 | 24464 | 147 | 0.00601 | 0.00012263 | 37.5 | 1849 | 2011/2012 | October-2011 | 10 | 2011
26382 | LIGHTNING - VEALE RD | 2011-10-05 15:54 | 2011-10-05 | 2011-10-05 16:58 | Calculated | TF467 | TF467 - Transformer Fuse: TF467 |  | No Segment | Gravel Scoop 109-04 | Urban A | Gravel Scoop | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 64 | 1 | 24464 | 64 | 0.00262 | 4.0876e-05 | 10 | 643 | 2011/2012 | October-2011 | 10 | 2011
26383 | LIGHTNING - PUKETAWAI RD | 2011-10-05 16:25 | 2011-10-05 | 2011-10-05 17:24 | Calculated | TF475 | TF475 - Transformer Fuse: TF475 |  | No Segment | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 59 | 4 | 24464 | 237 | 0.00969 | 0.00016351 | 25 | 1482 | 2011/2012 | October-2011 | 10 | 2011
26384 | LIGHTNING - AHUROA RD | 2011-10-05 17:02 | 2011-10-05 | 2011-10-05 18:00 | Calculated | 2093 | 2093 - Fused Link 2093 |  | 106SEG246-252 | Rangitoto 106-05 | Rural C | Rangitoto | Waitete Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 58 | 5 | 24464 | 290 | 0.01185 | 0.00020438 | 22.5 | 1309 | 2011/2012 | October-2011 | 10 | 2011
26390 | REPLACE POLES AND XARMS - TANGIWAI FEEDER | 2011-10-06 09:25 | 2011-10-06 | 2011-10-06 14:33 | Calculated | 5686 | 5686 - Fused Link 5686 |  | 416SEG5686 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 308 | 17 | 24464 | 5238 | 0.21411 | 0.0006949 | 137.5 | 42372 | 2011/2012 | October-2011 | 10 | 2011
26389 | LIGHTNING - DEVIATION RD | 2011-10-06 10:11 | 2011-10-06 | 2011-10-06 12:14 | Calculated | TF2687 | TF2687 - Transformer Fuse: TF2687 |  | No Segment | Wharepapa 122-07 | Rural D | Wharepapa | Arohena Zone Substation |  | Weather | Lightning | WEAT:LIGH:LFBL | Lightning - Protection Operated | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 123 | 1 | 24464 | 123 | 0.00503 | 4.0876e-05 | 10 | 1232 | 2011/2012 | October-2011 | 10 | 2011
26386 | MAINTAIN 11KV CABLE BRACKET - RURAL FEEDER | 2011-10-06 10:51 | 2011-10-06 | 2011-10-06 16:27 | Calculated | 609 | 609 - Circuit Breaker 609 (Rural Feeder) 609 |  | No Segment | 201-01 Taharoa | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 250 | 12 | 24464 | 2993 | 0.12234 | 0.00049052 | 83 | 20704 | 2011/2012 | October-2011 | 10 | 2011
26391 | REPLACE POLE AFTER TREE HIT IT - NATIONAL PARK | 2011-10-07 09:32 | 2011-10-07 | 2011-10-07 13:36 | Calculated | 5329 | 5329 - Fused Link 5329 |  | 411SEG5329-5310 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 244 | 16 | 24464 | 3907 | 0.1597 | 0.00065402 | 128 | 31257 | 2011/2012 | October-2011 | 10 | 2011
26392 | REPLACE FUSE HOLDER AT TX1620 - MAHOENUI FEEDER | 2011-10-07 10:10 | 2011-10-07 | 2011-10-07 12:04 | Calculated | 1533 | 1533 - Fused Link 1533 |  | 113SEG1533-1534 | Mahoenui 113-08 | Rural D | Mahoenui | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 89 | 3 | 24464 | 264 | 0.01079 | 0.00012263 | 22.5 | 1984 | 2011/2012 | October-2011 | 10 | 2011
26393 | LV MAINTENANCE - PAREKAWA DR | 2011-10-10 08:02 | 2011-10-10 | 2011-10-10 11:12 | Calculated | TF4157 | TF4157 - Transformer Fuse: TF4157 |  | 425SEG6552-6550 | Motuoapa 425-01 | Rural D | Motuoapa | Kiko Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 190 | 36 | 24464 | 6845 | 0.2798 | 0.0014716 | 327.2727 | 62230 | 2011/2012 | October-2011 | 10 | 2011
26394 | REPLACE FALULTY LINK 5936 - MANUNUI FEEDER | 2011-10-10 09:01 | 2011-10-10 | 2011-10-10 12:11 | Calculated | 5935 | 5935 - Fuse Switch 5935 |  | 408SEG5935-5936 | Manunui 408-04 | Rural B | Manunui | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 135 | 49 | 24464 | 3002 | 0.12271 | 0.0020029 | 234 | 17240 | 2011/2012 | October-2011 | 10 | 2011
26395 | INSTALL NEW LA ON TX 576 - OPARURE FEEDER | 2011-10-10 11:03 | 2011-10-10 | 2011-10-10 13:04 | Calculated | 265 | 265 - Sectionaliser with Bypass & Links 265 |  | 107SEG262-176 | Oparure 107-08 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 121 | 14 | 24464 | 1697 | 0.06937 | 0.00057227 | 135 | 16366 | 2011/2012 | October-2011 | 10 | 2011
26396 | FUSE PULLED APART - TARINGAMOTU RD | 2011-10-11 07:40 | 2011-10-11 | 2011-10-11 12:40 | Calculated | TF7I19 | TF7I19 - Transformer Fuse: TF7I19 |  | 402SEG5164-5923 | Northern 402-03 | Rural C | Northern | Borough Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 299 | 8 | 24464 | 2394 | 0.09786 | 0.00032701 | 30 | 8977 | 2011/2012 | October-2011 | 10 | 2011
26399 | LOWER LINE FOR TREE CUTTING - OTUKOU FEEDER | 2011-10-11 09:40 | 2011-10-11 | 2011-10-11 12:15 | Calculated | 5217 | 5217 - Fused Link 5217 |  | 418SEG5217 | Otukou 418-01 | Rural D | Otukou | Otukou Zone Substation |  | Planned Outage | PVEG2 | POUT:PVEG2:PVEG1 | Vegetation Work Planned Outage | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 155 | 6 | 24464 | 930 | 0.03802 | 0.00024526 | 50 | 7758 | 2011/2012 | October-2011 | 10 | 2011
26397 | LV FAULT - INSULATOR - MAIN SOUTH RD | 2011-10-11 21:33 | 2011-10-11 | 2011-10-11 22:04 | Calculated | TF1710 | TF1710 - Transformer Fuse: TF1710 |  | 113SEG1512-1514 | Mahoenui 113-05 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 31 | 3 | 24464 | 93 | 0.0038 | 0.00012263 | 45 | 1401 | 2011/2012 | October-2011 | 10 | 2011
26403 | TREE ON LINE - KIRIKAU VALLEY RD | 2011-10-12 12:15 | 2011-10-12 | 2011-10-12 17:31 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Vegetation | Vegetation | VEGE:VICL2:VICL1 | Vegetation Plantation | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 316 | 70 | 24464 | 10349 | 0.42303 | 0.0028613 | 430.5 | 61520 | 2011/2012 | October-2011 | 10 | 2011
26400 | EARTH TESTING - POWER RD | 2011-10-12 13:35 | 2011-10-12 | 2011-10-12 15:03 | Calculated | TF15I01 | TF15I01 - Transformer Fuse: TF15I01 |  | 410SEG5431-5407 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 88 | 3 | 24464 | 264 | 0.01079 | 0.00012263 | 15 | 1323 | 2011/2012 | October-2011 | 10 | 2011
26401 | FUSE LINK FALLEN OUT - WEST TAUPO RD | 2011-10-12 13:36 | 2011-10-12 | 2011-10-12 15:37 | Calculated | 5580 | 5580 - Fused Link 5580 |  | 426SEG5526-5359 | Waihaha 426-04 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 121 | 12 | 24464 | 1454 | 0.05943 | 0.00049052 | 100 | 12123 | 2011/2012 | October-2011 | 10 | 2011
26402 | BROKEN DDO AT TX 15I01 - UPPER RETARUKE | 2011-10-12 14:18 | 2011-10-12 | 2011-10-12 15:03 | Calculated | 5431 | 5431 - Fused Link 5431 |  | 410SEG5431-5407 | Raurimu 410-02 | Remote Rural F | Raurimu | National Park Zone Substation | Switchgear : Fuse Carriers | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 45 | 66 | 24464 | 2979 | 0.12177 | 0.0026978 | 364 | 16434 | 2011/2012 | October-2011 | 10 | 2011
26404 | LV LINE DOWN - MCDONALD RD | 2011-10-13 08:01 | 2011-10-13 | 2011-10-13 09:06 | Calculated | TF721 | TF721 - Transformer Fuse: TF721 |  | 120SEG498-408 | Whakamaru 120-04 | Rural D | Whakamaru | Maraetai Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 65 | 7 | 24464 | 456 | 0.01864 | 0.00028613 | 29.1667 | 1901 | 2011/2012 | October-2011 | 10 | 2011
26405 | REPLACE TX STRUCTURE - TIHOI RD | 2011-10-13 09:31 | 2011-10-13 | 2011-10-13 15:13 | Calculated | TF1256 | TF1256 - Transformer Fuse: TF1256 |  | 120SEG484-483 | Whakamaru 120-03 | Rural D | Whakamaru | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 2 | 24464 | 684 | 0.02796 | 8.1753e-05 | 30 | 10265 | 2011/2012 | October-2011 | 10 | 2011
26406 | REPLACE HV FUSE AT TX730 - ARATAKI RD | 2011-10-13 10:36 | 2011-10-13 | 2011-10-13 12:15 | Calculated | TF730 | TF730 - Transformer Fuse: TF730 |  | 120SEG419 | Whakamaru 120-05 (was part 124-01) | Rural D | Whakamaru | Maraetai Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 99 | 6 | 24464 | 595 | 0.02432 | 0.00024526 | 36 | 3570 | 2011/2012 | October-2011 | 10 | 2011
26407 | FIT TAP OFF DDO'S - POKURU RD | 2011-10-13 10:41 | 2011-10-13 | 2011-10-13 12:36 | Calculated | TF1026 | TF1026 - Transformer Fuse: TF1026 |  | 129SEG634-2131 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 115 | 2 | 24464 | 230 | 0.0094 | 8.1753e-05 | 15 | 1727 | 2011/2012 | October-2011 | 10 | 2011
26410 | JUMPER OFF AT LINKS 1712 - MOKAUITI RD | 2011-10-13 14:30 | 2011-10-13 | 2011-10-13 14:53 | Calculated | 1705 | 1705 - Air Break Switch 1705 |  | 115SEG1705-1707 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 23 | 126 | 24464 | 2921 | 0.1194 | 0.0051504 | 860.5 | 19949 | 2011/2012 | October-2011 | 10 | 2011
26408 | REPLACE HV FUSE AT TX 2481 -MATIERE RD | 2011-10-13 16:28 | 2011-10-13 | 2011-10-13 17:50 | Calculated | TF2481 | TF2481 - Transformer Fuse: TF2481 |  | 114SEG1107-1116 | Aria 114-05 | Rural D | Aria | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 82 | 1 | 24464 | 82 | 0.00335 | 4.0876e-05 | 15 | 1232 | 2011/2012 | October-2011 | 10 | 2011
26409 | BROKEN EARTH - OPARURE RD | 2011-10-14 09:36 | 2011-10-14 | 2011-10-14 10:07 | Calculated | TF571 | TF571 - Transformer Fuse: TF571 |  | 107SEG113-262 | Oparure 107-07 | Remote Rural E | Oparure | Gadsby Road Zone Substation |  | Asset Related | Conductor - Overhead | FAIL:FCDT:FCDC | Conductor Failure - Bare Wire - Cu | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 1 | 24464 | 30 | 0.00123 | 4.0876e-05 | 10 | 301 | 2011/2012 | October-2011 | 10 | 2011
26413 | JUMPER OFF - NGAHAPE RD | 2011-10-15 10:41 | 2011-10-15 | 2011-10-15 11:24 | Calculated | TF424 | TF424 - Transformer Fuse: TF424 |  | No Segment | Maihiihi 111-06 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 5 | 24464 | 216 | 0.00883 | 0.00020438 | 100 | 4320 | 2011/2012 | October-2011 | 10 | 2011
26414 | REPLACE HV FUSE AT TX 07K14 - ECHOLANDS RD | 2011-10-15 11:30 | 2011-10-15 | 2011-10-15 12:27 | Calculated | TF7K14 | TF7K14 - Transformer Fuse: TF7K14 |  | No Segment | Manunui 408-02 | Rural B | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 57 | 3 | 24464 | 171 | 0.00699 | 0.00012263 | 15 | 857 | 2011/2012 | October-2011 | 10 | 2011
26416 | FELL OUT FUSES - WAITANGATA RD | 2011-10-18 06:33 | 2011-10-18 | 2011-10-18 08:00 | Calculated | TF6E12 | TF6E12 - Transformer Fuse: TF6E12 |  | No Segment | Nihoniho 412-01 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 87 | 2 | 24464 | 175 | 0.00715 | 8.1753e-05 | 5 | 437 | 2011/2012 | October-2011 | 10 | 2011
26418 | REPLACE POLES 1230217 AND 218 - TIHOI FEEDER | 2011-10-18 08:40 | 2011-10-18 | 2011-10-18 16:00 | Calculated | 451 | 451 - Air Break Switch 451 |  | 129SEG451-787 | Tirohanga 129-02 (was 124-04) | Rural C | Tirohanga | Kaahu Tee Zone Substation (Containerised) |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 342 | 4 | 24464 | 1364 | 0.05576 | 0.00016351 | 66.6667 | 22747 | 2011/2012 | October-2011 | 10 | 2011
26417 | DEVIATE LINE AND INSTALL NEW STRUCTURE TX 3373 - OPARURE FEEDER | 2011-10-18 09:33 | 2011-10-18 | 2011-10-18 14:31 | Calculated | 244 | 244 - Air Break Switch 244 |  | 107SEG244-575 | Oparure 107-04 | Rural C | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYE | Extension/Capacity Increase for System | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 298 | 42 | 24464 | 12523 | 0.5119 | 0.0017168 | 431.25 | 128591 | 2011/2012 | October-2011 | 10 | 2011
26420 | RECLOSER 642 TRIPPED - PUKETAWAI RD | 2011-10-18 11:00 | 2011-10-18 | 2011-10-18 11:57 | Calculated | 642 | 642 - Recloser with Bypass & Links 642 |  | 110SEG328-336 | McDonalds 110-05 | Rural C | McDonalds | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 56 | 103 | 24464 | 5785 | 0.23647 | 0.0042103 | 988 | 55492 | 2011/2012 | October-2011 | 10 | 2011
26421 | OVERLOADED - MAROTIRI RD | 2011-10-18 15:33 | 2011-10-18 | 2011-10-18 15:34 | Calculated | 474 | 474 - Recloser 474 |  | 123SEG441-474 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Asset Related | Overload | FAIL:OOVL2:OOVL1 | Overload | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 1 | 129 | 24464 | 150 | 0.00613 | 0.0052731 | 1508.9167 | 1760 | 2011/2012 | October-2011 | 10 | 2011
26422 | REPLACE ABS POLE 418 - HUIRIMU FEEDER | 2011-10-19 09:01 | 2011-10-19 | 2011-10-19 15:57 | Calculated | 748 | 748 - Air Break Switch 748 |  | 121SEG748-418 | Huirimu 121-03 | Rural D | Huirimu | Arohena Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 384 | 74 | 24464 | 6651 | 0.27187 | 0.0030249 | 671 | 76540 | 2011/2012 | October-2011 | 10 | 2011
26423 | EARTH TEST - MANGAORONGO RD | 2011-10-19 10:09 | 2011-10-19 | 2011-10-19 11:30 | Calculated | TF328 | TF328 - Transformer Fuse: TF328 |  | No Segment | Maihiihi 111-03 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Third Party (includeds unauthorised contractors) | Customer Installation Fault | 3PAR:ECUS2:ECUS1 | Customer Installation Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 81 | 7 | 24464 | 568 | 0.02322 | 0.00028613 | 50 | 4062 | 2011/2012 | October-2011 | 10 | 2011
26424 | SCHEDULED MAINTENANCE - HILL ST | 2011-10-19 10:41 | 2011-10-19 | 2011-10-19 11:18 | Calculated | TF1219 | TF1219 - Transformer Fuse: TF1219 |  | 107SEG213-242 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 36 | 36 | 24464 | 1306 | 0.05338 | 0.0014716 | 116.129 | 4213 | 2011/2012 | October-2011 | 10 | 2011
26425 | REPLACE XARMS AT TX2263 - HOSPITAL RD | 2011-10-20 09:28 | 2011-10-20 | 2011-10-20 16:26 | Calculated | TF2263 | TF2263 - Transformer Fuse: TF2263 |  | 107SEG555 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 418 | 3 | 24464 | 1254 | 0.05126 | 0.00012263 | 15 | 6274 | 2011/2012 | October-2011 | 10 | 2011
26426 | LV NEUTRAL FAULT - PUKERIMU RD | 2011-10-20 10:50 | 2011-10-20 | 2011-10-20 11:37 | Calculated | TF1817 | TF1817 - Transformer Fuse: TF1817 |  | 103SEG1346-1326 | Benneydale 103-10 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLF | LV Fault | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 47 | 1 | 24464 | 47 | 0.00192 | 4.0876e-05 | 7.5 | 353 | 2011/2012 | October-2011 | 10 | 2011
26427 | REPLACE HV FUSE AT TX 9L1 - PA RD | 2011-10-20 11:05 | 2011-10-20 | 2011-10-20 13:08 | Calculated | TF9L1 | TF9L1 - Transformer Fuse: TF9L1 |  | No Segment | Manunui 408-05 | Rural D | Manunui | Manunui Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 123 | 4 | 24464 | 492 | 0.02011 | 0.00016351 | 40 | 4929 | 2011/2012 | October-2011 | 10 | 2011
26428 | REPLACE 11KV POLE FOR TX11K22 - SOUTHERN FEEDER | 2011-10-20 12:06 | 2011-10-20 | 2011-10-20 13:50 | Calculated | 5735 | 5735 - Fused Link 5735 |  | 409SEG5735 | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 104 | 11 | 24464 | 1146 | 0.04684 | 0.00044964 | 45 | 4688 | 2011/2012 | October-2011 | 10 | 2011
26429 | REPLACE STRUCTURE AT TX 1454 - BENNEYDALE FEEDER | 2011-10-21 09:18 | 2011-10-21 | 2011-10-21 16:05 | Calculated | 1736 | 1736 - Fused Link 1736 |  | 103SEG1736-1737 | Benneydale 103-11 | Rural D | Benneydale | Waitete Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 382 | 26 | 24464 | 5715 | 0.23361 | 0.0010628 | 177.5 | 41849 | 2011/2012 | October-2011 | 10 | 2011
26430 | REPLACE HV FUSE AT TX 1467 - VIEW RD | 2011-10-21 12:05 | 2011-10-21 | 2011-10-21 12:30 | Calculated | TF1467 | TF1467 - Transformer Fuse: TF1467 |  | 108SEG219-501 | Waitomo 108-03 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 24 | 7 | 24464 | 171 | 0.00699 | 0.00028613 | 58.3333 | 1425 | 2011/2012 | October-2011 | 10 | 2011
26431 | SECTIONALISOR 5534 TRIPPED - WAIHAHA RD | 2011-10-21 12:37 | 2011-10-21 | 2011-10-21 14:36 | Calculated | 5534 | 5534 - Sectionaliser 5534 |  | 124SEG5534-5610 | Tihoi 124-03 (was Tihoi 124-06) | Rural C | Tihoi | Marotiri Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 118 | 15 | 24464 | 1772 | 0.07243 | 0.00061315 | 120 | 14176 | 2011/2012 | October-2011 | 10 | 2011
26432 | REPLACE LINK 6150 - KARANGAHAPE RD | 2011-10-22 09:08 | 2011-10-22 | 2011-10-22 11:09 | Calculated | 6150 | 6150 - Fused Link 6150 |  | 426SEG5592-5110 | Waihaha 426-03 | Remote Rural E | Waihaha | Kuratau Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 5 | 24464 | 601 | 0.02457 | 0.00020438 | 30 | 3610 | 2011/2012 | October-2011 | 10 | 2011
26433 | RECLOSER 5863 TRIPPED - PNGGAHURA RD SUB | 2011-10-22 13:55 | 2011-10-22 | 2011-10-22 15:55 | Calculated | 5863 | 5863 - Recloser with Bypass & Links 5863 |  | 403SEG5863-5862 | Western 403-02 | Rural B | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 120 | 42 | 24464 | 5047 | 0.2063 | 0.0017168 | 323.75 | 38903 | 2011/2012 | October-2011 | 10 | 2011
26437 | BIRDS CONTACT - TAHAIA RD | 2011-10-24 15:56 | 2011-10-24 | 2011-10-24 18:20 | Calculated | TF385 | TF385 - Transformer Fuse: TF385 |  | No Segment | Gravel Scoop 109-05 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 144 | 2 | 24464 | 288 | 0.01177 | 8.1753e-05 | 25 | 3609 | 2011/2012 | October-2011 | 10 | 2011
26439 | REPLACE COMPLETE STRUCTURE AT TX 15L04 - NATIONAL PARK FEEDER | 2011-10-25 09:16 | 2011-10-25 | 2011-10-25 15:08 | Calculated | TF15L04 | TF15L04 - Transformer Fuse: TF15L04 |  | 411SEG5147-5775 | National Park 411-03 | Rural D | National Park | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 351 | 2 | 24464 | 703 | 0.02874 | 8.1753e-05 | 0 | 0 | 2011/2012 | October-2011 | 10 | 2011
26440 | CHANGING POLES AND XARMS - OTOROHANGA FEEDER | 2011-10-25 09:38 | 2011-10-25 | 2011-10-25 15:05 | Calculated | 331 | 331 - Air Break Switch 331 |  | 112SEG331-355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 327 | 22 | 24464 | 7194 | 0.29406 | 0.00089928 | 257.5 | 84202 | 2011/2012 | October-2011 | 10 | 2011
26441 | MAGPIE - TAUMATAMAIRE RD | 2011-10-25 12:57 | 2011-10-25 | 2011-10-25 14:27 | Calculated | TF1888 | TF1888 - Transformer Fuse: TF1888 |  | 128SEG1523 | Mokau 128-01 | Remote Rural F | Mokau | Mahoenui Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 90 | 1 | 24464 | 90 | 0.00368 | 4.0876e-05 | 3 | 270 | 2011/2012 | October-2011 | 10 | 2011
26442 | VANDALISM TO ENCLOSURE - WAIOTAKA RD | 2011-10-25 16:40 | 2011-10-25 | 2011-10-25 17:23 | Calculated | TF4040 | TF4040 - Transformer Fuse: TF4040 |  | No Segment | Rangipo / Hautu 424-02 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Third Party (includeds unauthorised contractors) | Human Interference | 3PAR:EHUM:EHUV | Wilful Damage or Interference | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 43 | 1 | 24464 | 43 | 0.00176 | 4.0876e-05 | 15 | 645 | 2011/2012 | October-2011 | 10 | 2011
26443 | BIRD CLASH - PUREORA FEEDER | 2011-10-25 20:45 | 2011-10-25 | 2011-10-26 01:15 | Calculated | 2092 | 2092 - Circuit Breaker Maraetai 11 kV 2092 |  | No Segment | 210-01 Maraetai | Rural D | Pureora | Maraetai Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 270 | 163 | 24464 | 3400 | 0.13898 | 0.0066629 | 2775.5 | 32683 | 2011/2012 | October-2011 | 10 | 2011
26444 | CONNECT AND DISCONNECT GEN SET - REPLACE POLE 16/12 TURANGI NEW WORLD | 2011-10-26 06:00 | 2011-10-26 | 2011-10-26 14:54 | Calculated | TF4218 | TF4218 - Transformer Fuse: TF4218 |  | 424SEG6651-6652 | Rangipo / Hautu 424-01 | Rural C | Rangipo / Hautu | Turangi Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 25 | 1 | 24464 | 25 | 0.00102 | 4.0876e-05 | 500 | 12500 | 2011/2012 | October-2011 | 10 | 2011
26445 | CHANGING POLES AND XARMS - OTOROHANGA FEEDER | 2011-10-26 09:32 | 2011-10-26 | 2011-10-26 14:55 | Calculated | 331 | 331 - Air Break Switch 331 |  | 112SEG331-355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 323 | 22 | 24464 | 7106 | 0.29047 | 0.00089928 | 257.5 | 83172 | 2011/2012 | October-2011 | 10 | 2011
26446 | MAINTENANCE - RAURIMU FEEDER | 2011-10-26 09:34 | 2011-10-26 | 2011-10-26 15:52 | Calculated | 5161 | 5161 - Fused Link 5161 |  | 410SEG5161-5235 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 378 | 14 | 24464 | 5292 | 0.21632 | 0.00057227 | 142.5 | 53865 | 2011/2012 | October-2011 | 10 | 2011
26448 | REPLACE HV FUSE AT TX 1707 - PAEKAKA RD | 2011-10-27 09:53 | 2011-10-27 | 2011-10-27 11:12 | Calculated | TF1707 | TF1707 - Transformer Fuse: TF1707 |  | 113SEG686-1546 | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 79 | 1 | 24464 | 79 | 0.00323 | 4.0876e-05 | 10 | 790 | 2011/2012 | October-2011 | 10 | 2011
26449 | JUMPER OFF TX 12K11 - OIO SUB | 2011-10-27 12:25 | 2011-10-27 | 2011-10-27 13:16 | Calculated | 5799 | 5799 - Recloser with Bypass & Links 5799 |  | 409SEG5800-5799RET | Southern 409-05 | Rural D | Southern | Manunui Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 51 | 45 | 24464 | 2295 | 0.09381 | 0.0018394 | 243.5 | 12418 | 2011/2012 | October-2011 | 10 | 2011
26452 | JUMPERS OFF AT TX 1530 - HAUTURU NORTH RD | 2011-10-27 18:30 | 2011-10-27 | 2011-10-27 19:08 | Calculated | 290 | 290 - Air Break Switch 290 |  | 101SEG290 | Caves 101-12 | Remote Rural E | Caves | Hangatiki Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 38 | 8 | 24464 | 304 | 0.01243 | 0.00032701 | 65 | 2470 | 2011/2012 | October-2011 | 10 | 2011
26453 | REPLACE POLE 1150184 WITH A 12M POLE - MOKAUITI FEEDDER | 2011-10-28 09:31 | 2011-10-28 | 2011-10-28 15:16 | Calculated | 1648 | 1648 - Fused Link 1648 |  | 115SEG1648-1716 | Mokauiti 115-03 | Rural D | Mokauiti | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 233 | 59 | 24464 | 2835 | 0.11588 | 0.0024117 | 415.5 | 14590 | 2011/2012 | October-2011 | 10 | 2011
26454 | FAULTY TX 1707 - PAEKAKA RD | 2011-10-28 10:33 | 2011-10-28 | 2011-10-28 12:08 | Calculated | TF1707 | TF1707 - Transformer Fuse: TF1707 |  | 113SEG686-1546 | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Transformer | FAIL:FTX2:FTX1 | Transformer Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 95 | 1 | 24464 | 95 | 0.00388 | 4.0876e-05 | 10 | 950 | 2011/2012 | October-2011 | 10 | 2011
26455 | BLOWN SKIRT AT POLE 203 - WAIRERE | 2011-10-29 16:29 | 2011-10-29 | 2011-10-29 16:38 | Calculated | 594 | 594 - Circuit Breaker 594 |  | No Segment | 205-01 Gadsby Road | Urban A | Gadsby Rd / Wairere 33 | Gadsby Road Zone Substation |  | Asset Related | Insulator | FAIL:FINS2:FINC | Insulator Broken/Damaged | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 9 | 2104 | 24464 | 18936 | 0.77404 | 0.086004 | 14351 | 129158 | 2011/2012 | October-2011 | 10 | 2011
26458 | PUKEKO - KURATAHI ST | 2011-10-29 23:28 | 2011-10-29 | 2011-10-30 00:20 | Calculated | TF1673 | TF1673 - Transformer Fuse: TF1673 |  | 116SEG655 | Piopio 116-02 | Rural D | Piopio | Wairere Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 52 | 1 | 24464 | 52 | 0.00213 | 4.0876e-05 | 50 | 2600 | 2011/2012 | October-2011 | 10 | 2011
26456 | REPLCE POLE 1041014 - OPARURE FEEDER | 2011-10-30 09:02 | 2011-10-30 | 2011-10-30 12:27 | Calculated | TF401 | TF401 - Transformer Fuse: TF401 |  | 107SEG503-208 | Oparure 107-02 | Urban A | Oparure | Gadsby Road Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 205 | 49 | 24464 | 10045 | 0.4106 | 0.0020029 | 200 | 40999 | 2011/2012 | October-2011 | 10 | 2011
26461 | REPLACE LINK 2061 - HARPERS AVE | 2011-10-30 21:00 | 2011-10-30 | 2011-10-30 21:30 | Calculated | 2061 | 2061 - Fused Link 2061 |  | 111SEG663-2061 | Maihiihi 111-01 | Urban A | Maihiihi | Te Waireka Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 30 | 2 | 24464 | 60 | 0.00245 | 8.1753e-05 | 45 | 1350 | 2011/2012 | October-2011 | 10 | 2011
26462 | REPLACE YELLOW TAGGED POLE 124/138 - TE MAPARA FEEDER | 2011-10-31 09:14 | 2011-10-31 | 2011-10-31 15:32 | Calculated | 1259 | 1259 - Solid Link 1259 |  | 117SEG1259-1722 | Te Mapara 117-04 | Rural D | Te Mapara | Wairere Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYO | Safety Related Work (includes Red Tag poles & SMS) | Planned | Planned - TLC : Class B | Overhead | 11kV SWER | 9000 |  | 335 | 40 | 24464 | 8355 | 0.34152 | 0.0016351 | 329 | 73478 | 2011/2012 | October-2011 | 10 | 2011
26463 | REPLACE LA AT TX 1290 - GRAVEL SCOOP FEEDER | 2011-10-31 10:05 | 2011-10-31 | 2011-10-31 12:31 | Calculated | 2041 | 2041 - Fused Link 2041 |  | 109SEG171-2041 | Gravel Scoop 109-07 | Rural C | Gravel Scoop | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 146 | 4 | 24464 | 584 | 0.02387 | 0.00016351 | 65 | 9490 | 2011/2012 | October-2011 | 10 | 2011
26464 | REPLACE HV FUSE AT TX05F03 - SH 40 | 2011-10-31 12:00 | 2011-10-31 | 2011-10-31 15:38 | Calculated | TF5F3 | TF5F3 - Transformer Fuse: TF5F3 |  | No Segment | Nihoniho 412-01 | Rural D | Nihoniho | Nihoniho Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 218 | 3 | 24464 | 654 | 0.02673 | 0.00012263 | 15 | 3272 | 2011/2012 | October-2011 | 10 | 2011
26465 | FUSE PULLED APART AT TX 10E06 - OPATU RD | 2011-10-31 17:07 | 2011-10-31 | 2011-10-31 18:15 | Calculated | TF10E06 | TF10E06 - Transformer Fuse: TF10E06 |  | 413SEG5647-5646 | Ohura 413-08 | Rural D | Ohura | Nihoniho Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 68 | 4 | 24464 | 273 | 0.01116 | 0.00016351 | 15 | 1024 | 2011/2012 | October-2011 | 10 | 2011
26467 | RAURIMU FEEDER MAINTENANCE PROJECT - RAURIMU FEEDER | 2011-11-01 08:04 | 2011-11-01 | 2011-11-01 16:18 | Calculated | 5141 | 5141 - Air Break Switch 5141 |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 449 | 213 | 24466 | 11548 | 0.472 | 0.008706 | 1434.5833 | 118815 | 2011/2012 | November-2011 | 11 | 2011
26468 | POLE 104/936 DOWN - WAIKAWAU - E/W SUB | 2011-11-02 07:21 | 2011-11-02 | 2011-11-02 14:44 | Calculated | 1610 | 1610 - Recloser 1610 |  | 128SEG1610-1611 | Mokau 128-03 | Remote Rural F | Mokau | Mahoenui Zone Substation | OH Lines : Pole - Hardwood | Asset Related | Pole | FAIL:FPOL2:FPOD | Pole Down - Broken | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 443 | 54 | 24466 | 23931 | 0.97813 | 0.0022071 | 413 | 183034 | 2011/2012 | November-2011 | 11 | 2011
26469 | RAURIMU FEEDER MAINTENANCE PROJECT - RAURIMU FEEDER | 2011-11-02 08:02 | 2011-11-02 | 2011-11-02 15:42 | Calculated | 5141 | 5141 - Air Break Switch 5141 |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 328 | 309 | 24466 | 8651 | 0.35359 | 0.01263 | 2073.5495 | 93554 | 2011/2012 | November-2011 | 11 | 2011
26470 | UPGRADE LV FUSING - MANAORONGO RD | 2011-11-02 10:18 | 2011-11-02 | 2011-11-02 12:11 | Calculated | TF1210 | TF1210 - Transformer Fuse: TF1210 |  | 111SEG339-346 | Maihiihi 111-05 | Rural C | Maihiihi | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 113 | 1 | 24466 | 113 | 0.00462 | 4.0873e-05 | 15 | 1697 | 2011/2012 | November-2011 | 11 | 2011
26471 | FAULTY DDO - OLD HOROPITO STATION RD | 2011-11-02 15:12 | 2011-11-02 | 2011-11-02 15:47 | Calculated | TF20L30 | TF20L30 - Transformer Fuse: TF20L30 |  | 415SEGREG28-6788 | Turoa 415-01 | Urban A | Turoa | Direct from Ohakune Supply | Switchgear : Fuse Carriers | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 35 | 1 | 24466 | 35 | 0.00143 | 4.0873e-05 | 15 | 528 | 2011/2012 | November-2011 | 11 | 2011
26472 | SECTIONALISER 5489 TRIPPED - UPPER RETARUKE RD | 2011-11-02 17:07 | 2011-11-02 | 2011-11-02 17:52 | Calculated | 5489 | 5489 - Sectionaliser with Bypass 5489 |  | No Segment | No Asset Group | Remote Rural F | Raurimu | National Park Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 45 | 28 | 24466 | 1263 | 0.05162 | 0.0011444 | 178.3333 | 8045 | 2011/2012 | November-2011 | 11 | 2011
26473 | RAURIMU FEEDER MAINTENANCE - RAURIMU FEEDER | 2011-11-03 08:02 | 2011-11-03 | 2011-11-03 16:03 | Calculated | 5141 | 5141 - Air Break Switch 5141 |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 423 | 211 | 24466 | 11408 | 0.46628 | 0.0086242 | 1395.3333 | 111921 | 2011/2012 | November-2011 | 11 | 2011
26476 | LV MAINTENANCE - TAHAROA | 2011-11-03 10:22 | 2011-11-03 | 2011-11-03 16:02 | Calculated | TF1404 | TF1404 - Transformer Fuse: TF1404 |  | 126SEG504-578 | Rural 126-01 | Rural D | Rural | Taharoa Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 340 | 5 | 24466 | 1700 | 0.06948 | 0.00020437 | 50 | 17006 | 2011/2012 | November-2011 | 11 | 2011
26477 | BIRD / CLASH - TURAKINA VALLEY RD | 2011-11-03 10:58 | 2011-11-03 | 2011-11-03 18:28 | Calculated | TF22O7 | TF22O7 - Transformer Fuse: TF22O7 |  | 416SEG5689-5691 | Tangiwai 416-04 | Rural C | Tangiwai | Direct from Ohakune Supply |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 450 | 1 | 24466 | 450 | 0.01839 | 4.0873e-05 | 10 | 4501 | 2011/2012 | November-2011 | 11 | 2011
26485 | POSSUM - HAHAROA A | 2011-11-04 05:07 | 2011-11-04 | 2011-11-04 05:16 | Calculated | TPHangatiki CB242 | TPHangatiki CB242 - 33kV Minimum Oil Circuit Breaker TP242 |  | No Segment | 213-01 Transpower Hangatiki | Urban A | Taharoa A 33 | Direct from Hangatiki Supply |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 33kV | 33000 |  | 0 | 0 | 24466 |  | 0 | 0 |  |  | 2011/2012 | November-2011 | 11 | 2011
26486 | RAURIMU FEEDER MAINTENANCE PROJECT - RAURIMU FEEDER | 2011-11-04 08:13 | 2011-11-04 | 2011-11-04 15:07 | Calculated | 5141 | 5141 - Air Break Switch 5141 |  | 410SEG5141-5543 | Raurimu 410-01 | Rural D | Raurimu | National Park Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 378 | 213 | 24466 | 7920 | 0.32371 | 0.008706 | 1434.5833 | 86039 | 2011/2012 | November-2011 | 11 | 2011
26488 | ROTTEN XARM LINE DOWN - HAPARUA RD | 2011-11-04 08:23 | 2011-11-04 | 2011-11-04 15:09 | Calculated | 5506 | 5506 - Sectionaliser with Bypass & Links 5506 |  | 413SEG5506 | Ohura 413-03 | Rural D | Ohura | Nihoniho Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 405 | 7 | 24466 | 2836 | 0.11592 | 0.00028611 | 58 | 23501 | 2011/2012 | November-2011 | 11 | 2011
26489 | REPLACE HV FUSE AT TX06Q02 - SH 32 | 2011-11-04 09:07 | 2011-11-04 | 2011-11-04 10:31 | Calculated | TF6Q2 | TF6Q2 - Transformer Fuse: TF6Q2 |  | 426SEG6028 | Northern 402-03 | Rural C | Waihaha | Kuratau Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 84 | 1 | 24466 | 84 | 0.00343 | 4.0873e-05 | 5 | 420 | 2011/2012 | November-2011 | 11 | 2011
26490 | REPLACE POLES - OTOROHANG FEEDER | 2011-11-04 09:38 | 2011-11-04 | 2011-11-04 15:59 | Calculated | 355 | 355 - Fused Link 355 |  | 112SEG355 | Otorohanga 112-04 | Remote Rural E | Otorohanga | Te Waireka Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 380 | 10 | 24466 | 3802 | 0.1554 | 0.00040873 | 125 | 47527 | 2011/2012 | November-2011 | 11 | 2011
26491 | FUSE PULLED APART - MANGAOKEWA RD | 2011-11-04 15:37 | 2011-11-04 | 2011-11-04 16:14 | Calculated | TF141 | TF141 - Transformer Fuse: TF141 |  | 103SEG260 | Benneydale 103-05 | Rural D | Benneydale | Waitete Zone Substation |  | Asset Related | Other | FAIL:FOLD:FOLW | Ageing or Wear of Equipment | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 37 | 2 | 24466 | 74 | 0.00302 | 8.1746e-05 | 15 | 561 | 2011/2012 | November-2011 | 11 | 2011
26493 | BIRD CLASH - RANGITOTO RD POLE 17 | 2011-11-05 20:49 | 2011-11-05 | 2011-11-05 21:30 | Calculated | 823 | 823 - Fused Link 823 |  | 106SEG193RET | Rangitoto 106-06 | Rural C | Rangitoto | Waitete Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 41 | 4 | 24466 | 164 | 0.0067 | 0.00016349 | 65 | 2673 | 2011/2012 | November-2011 | 11 | 2011
26494 | JUMPER OFF(GEN SET PROVIDED)- PAEKAKA RD | 2011-11-06 09:38 | 2011-11-06 | 2011-11-06 10:39 | Calculated | TF1913 | TF1913 - Transformer Fuse: TF1913 |  | No Segment | Mahoenui 113-01 | Rural D | Mahoenui | Wairere Zone Substation |  | Asset Related | Connection Failure | FAIL:FCON:FCOF | Connector Failure | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 61 | 1 | 24466 | 61 | 0.00249 | 4.0873e-05 | 10 | 611 | 2011/2012 | November-2011 | 11 | 2011
26495 | BIRD CLASH - TE KUMI STATION RD | 2011-11-06 09:45 | 2011-11-06 | 2011-11-06 10:40 | Calculated | 763 | 763 - Fused Link 763 |  | 108SEG763-2140 | Waitomo 108-01 | Urban A | Waitomo | Gadsby Road Zone Substation |  | Birds & Animals | Birds | BANI:BIRD:84KUQ6 | Bird Contact | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 55 | 2 | 24466 | 110 | 0.0045 | 8.1746e-05 | 330 | 18205 | 2011/2012 | November-2011 | 11 | 2011
26496 | UPGRADE LV FUSING - POIHIPI RD | 2011-11-07 08:28 | 2011-11-07 | 2011-11-07 09:36 | Calculated | TF2662 | TF2662 - Transformer Fuse: TF2662 |  | 123SEG472-698 | Mokai 123-01 | Rural C | Mokai | Marotiri Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYL | Maintenance General (LV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 68 | 2 | 24466 | 136 | 0.00556 | 8.1746e-05 | 100 | 6815 | 2011/2012 | November-2011 | 11 | 2011
26502 | HV FUSE AT TX04G07 REPLACED - MANGAPAPA RD | 2011-11-07 08:48 | 2011-11-07 | 2011-11-07 10:09 | Calculated | TF4G7 | TF4G7 - Transformer Fuse: TF4G7 |  | No Segment | Tuhua 422-03 | Rural D | Tuhua | Tuhua Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 81 | 2 | 24466 | 162 | 0.00662 | 8.1746e-05 | 15 | 1217 | 2011/2012 | November-2011 | 11 | 2011
26498 | RECLOSER 5378 TRIPPED - KIRIKAU SUB | 2011-11-07 09:16 | 2011-11-07 | 2011-11-07 09:51 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 35 | 65 | 24466 | 2285 | 0.09339 | 0.0026567 | 398 | 13996 | 2011/2012 | November-2011 | 11 | 2011
26501 | RECLOSER 5378 TRIPPED - KIRIKAU SUB | 2011-11-07 09:16 | 2011-11-07 | 2011-11-07 11:24 | Calculated | 5378 | 5378 - Recloser 5378 |  | 403SEG5378-5886 | Western 403-07 | Remote Rural E | Western | Borough Zone Substation |  | Cant Find a Cause | Cant Find A Cause | CANT3:CANT2:CANT1 | Cant Find a Cause | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 128 | 65 | 24466 | 8330 | 0.34047 | 0.0026567 | 398 | 51010 | 2011/2012 | November-2011 | 11 | 2011
26504 | REPLACE POLES 42100008,21 24 - ONGARUE FEEDER | 2011-11-08 08:36 | 2011-11-08 | 2011-11-08 15:41 | Calculated | 6554 | 6554 - Solid Link 6554 |  | 421SEG6554-5462RET | Ongarue 421-01 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 351 | 269 | 24466 | 4989 | 0.20392 | 0.010995 | 1937.5 | 31143 | 2011/2012 | November-2011 | 11 | 2011
26503 | LINE MAINTENANCE - MICHELL RD - OFF SCOTT RD | 2011-11-08 09:08 | 2011-11-08 | 2011-11-08 13:29 | Calculated | 495 | 495 - Fused Link 495 |  | 119SEG495 | Pureora 119-01 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 261 | 6 | 24466 | 1566 | 0.06401 | 0.00024524 | 85 | 22196 | 2011/2012 | November-2011 | 11 | 2011
26505 | REPLACE POLE 40 AND FIT TO FUSES FOR NEW TX3376 - HANGATIKI STATION RD | 2011-11-08 10:16 | 2011-11-08 | 2011-11-08 14:50 | Calculated | 175 | 175 - Air Break Switch 175 |  | 102SEG1271-336 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 239 | 32 | 24466 | 7617 | 0.31133 | 0.0013079 | 285 | 67844 | 2011/2012 | November-2011 | 11 | 2011
26506 | FIELD STUFF SWITCHING ERROR - HANGATIKI EAST RD | 2011-11-08 10:23 | 2011-11-08 | 2011-11-08 10:52 | Calculated | 521 | 521 - Air Break Switch 521 |  | 102SEG521-505 | Hangatiki East 102-02 | Urban A | Hangatiki East | Hangatiki Zone Substation |  | Asset Related | TLC Operator & Authorised Contractor Error | FAIL:EHUO2:EHUF | Field Operator Error | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV | 11000 |  | 29 | 7 | 24466 | 204 | 0.00834 | 0.00028611 | 1030 | 30041 | 2011/2012 | November-2011 | 11 | 2011
26507 | POSSUM - ONGARUE VILLAGE RD | 2011-11-08 23:03 | 2011-11-08 | 2011-11-08 23:44 | Calculated | TF4I20 | TF4I20 - Transformer Fuse: TF4I20 |  | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Birds & Animals | Animals | BANI:ANIM:APOS | Possums | Unplanned | Unplanned - TLC : Class C | Overhead | 11kV SWER | 9000 |  | 41 | 5 | 24466 | 205 | 0.00838 | 0.00020437 | 30 | 1234 | 2011/2012 | November-2011 | 11 | 2011
26508 | REPLACE POLES 42100 27,30 AND 37 - ONGARUE FEEDER | 2011-11-09 08:47 | 2011-11-09 | 2011-11-09 15:58 | Calculated | 5466 | 5466 - Recloser with Bypass & Links 5466 |  | No Segment | Ongarue 421-03 | Rural D | Ongarue | Tuhua Zone Substation |  | Planned Outage | Planned Outage for System Work | POUT:PSYS2:PSYM | Maintenance General (HV) | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 281 | 210 | 24466 | 1591 | 0.06503 | 0.0085833 | 1558.5 | 15076 | 2011/2012 | November-2011 | 11 | 2011
26510 | BUILDING NEW 3 PHASE EXTENSION - SH 30 | 2011-11-09 09:39 | 2011-11-09 | 2011-11-09 14:15 | Calculated | 785 | 785 - Fused Link 785 |  | 119SEG785 | Pureora 119-02 | Rural D | Pureora | Maraetai Zone Substation |  | Planned Outage | Planned Outage for Customer Work | POUT:PCUS2:PCUE | Extension/Capacity Increase for Customer | Planned | Planned - TLC : Class B | Overhead | 11kV | 11000 |  | 276 | 3 | 24466 | 828 | 0.03384 | 0.00012262 | 45 | 12428 | 2011/2012 | November-2011 | 11 | 2011